[7 empty] | 12718 | 4312 | 1210607 | 2015-02-15 15:11 | 2015-02-15 16:59 | 108 | 11kV | 133905 | 1569 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | At ZN2196 Milperra Panel 5 "Marigold Amour No.4" tripped, reclosed and locked out on: Relays: C phase timed, C phase instantaneous, EFI, lockout, fault check Signals: 11kv trip, Zone Earth, No.3 Group Earth EFI's: S8696, S5487, S35865 Remarks: lightning/surge arrestor. Lightning strike caused damage to surge arrestor at PT 1896 Zonnebeke Cres | February | 2015 | 2015Q3 | 2015 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-02-15 | N | 85.3442 | N | 6 | N | N | 1.1101 | 39.4971 | 97853.8245
[7 empty] | 14286 | 17126 | 1210615 | 2015-02-15 16:22 | 2015-02-15 18:35 | 133 | 11kV | 23674 | 178 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | Previous Storm | N | S 10783 Boundary Martin - Entire kiosk isolated for safety. Kiosk was hit by a motor vehicle. Kiosk housing and RMI are damaged. ME: 1210619. GIS: 1210621, 3, 5, 6. Withdrawn: 1210615, 22. CC1: 22-"Refer to SOp" | February | 2015 | 2015Q3 | 2015 | ZN10994:PA18 | ZN10994:PA18 | ZN10994/000018 | GEORGES RIVER | Unknown | Not Veg | 2015-02-15 | N | 133 | N | 6 | N | N | 1.1101 | 39.4971 | 17300.2609
[7 empty] | 13004 | 6851 | 1210620 | 2015-02-15 16:31 | 2015-02-15 20:15 | 223.7667 | 11kV | 3580.2667 | 16 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 150683 Tail burnt off at ABS 62965. Outage extended to abs 62818 for clearance. No Protection operations. | February | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2015-02-15 | N | 223.7667 | N | 6 | N | N | 1.1101 | 39.4971 | 2616.3533
[7 empty] | 13009 | 6868 | 1210671 | 2015-02-15 23:07 | 2015-02-16 00:15 | 68 | 11kV | 78419 | 1905 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150686 1 fault operation 3 Phase Overcurrent; Earth Fault A live possum near sub 12238 Tapping burnt off at pole IV-31308. Repairs required Monday Excluded oms 1210671 | February | 2015 | 2015Q3 | 2015 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2015-02-15 | N | 41.1648 | N | 6 | N | N | 1.1101 | 39.4971 | 57306.2922
[7 empty] | 13232 | 8595 | 1210723 | 2015-02-16 08:00 | 2015-02-16 08:27 | 27 | 11kV | 1107 | 41 | HV | Staff Other | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Planned LID 150687 SINO 50061 Planned job cancelled and not communicated to control room hence unplanned interruption | February | 2015 | 2015Q3 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2015-02-16 | N | 27 | N | 1 | N | N | 1.1101 | 39.4971 | 808.9629
[7 empty] | 13513 | 11042 | 1211347 | 2015-02-17 15:15 | 2015-02-17 16:30 | 75 | 11kV | 825 | 11 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 150706 Fdr interupted to repair broken strands on OHM near pole 9L-70427. CC1: 06-"Urgent - O.H Mains - No others" | February | 2015 | 2015Q3 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2015-02-17 | N | 75 | N | 1 | N | N | 1.1101 | 39.4971 | 602.8857
[7 empty] | 12538 | 2669 | 1211461 | 2015-02-18 04:49 | 2015-02-18 06:05 | 76 | 11kV | 100320 | 1320 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn1193 Lindfield Panel 12 Tripped reclosed tripped and locked out on Relays: B and C phase OC + B and C phase IOC Cause Not ascertained for outage | February | 2015 | 2015Q3 | 2015 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Veg | 2015-02-18 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 73310.8971
[7 empty] | 13008 | 6867 | 1212018 | 2015-02-18 16:59 | 2015-02-18 17:03 | 4 | 11kV | 2872 | 718 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12660 woy woy panel 16 "st huberts" fdr tripped on relays: B phase overcurrent signals: 11kv trip EFI's S11997 S14604 S11459 S11458 S11242 Abnormal: S11997:A closed S11242:B opened After DAROS 354687 replace HV cable job completed. Failed on energisation. Suspect cable fault between S11242 & S48128. See 1212018 LV// 1216608 | February | 2015 | 2015Q3 | 2015 | ZN36200:PA11 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | UG | Not Veg | 2015-02-18 | N | 4 | N | 3 | N | N | 1.1101 | 39.4971 | 2098.7729
[7 empty] | 13317 | 9422 | 1211780 | 2015-02-18 16:54 | 2015-02-18 17:40 | 46 | 11kV | 322 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150724 B phase DOLF : 50 Amp Excluded OMS 1211780 | February | 2015 | 2015Q3 | 2015 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2015-02-18 | N | 46 | N | 3 | N | N | 1.1101 | 39.4971 | 235.3081
[7 empty] | 13839 | 13519 | 1212003 | 2015-02-19 12:32 | 2015-02-19 12:55 | 23 | 11kV | 1035 | 45 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150737 C phase DOLF : 20 Amp Excluded OMS 1212003 No Cause Found | February | 2015 | 2015Q3 | 2015 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Veg | 2015-02-19 | N | 23 | N | 3 | N | N | 1.1101 | 39.4971 | 756.3475
[7 empty] | 13748 | 12900 | 1212009 | 2015-02-19 12:42 | 2015-02-19 12:55 | 13 | 11kV | 195 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Replaced blown DOLF 20A C phase Excludes OMS 1212009 | February | 2015 | 2015Q3 | 2015 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Veg | 2015-02-19 | N | 13 | N | 3 | N | N | 1.1101 | 39.4971 | 142.5002
[7 empty] | 13452 | 10571 | 1212155 | 2015-02-19 23:33 | 2015-02-20 10:40 | 667 | 11kV | 148253 | 701 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Panel 28 Tripped on Relays: Earth Fault C phase Timed Overcurrent, C phase IOC Signals: 11kV Trip Abnormal Switching: Section of feeder out of service from S531 to S859 S61562 in LV parallel Cause: Section of 11kv feeder from S5268 Princes Boronia Park to S4372 to S859 tee S4671 defective RMI at S61562 Burns Bay defective and under A/P to be fixed See OMS 1213801 1213804 1213805 1213808 1213807 | February | 2015 | 2015Q3 | 2015 | ZN129:PA28 | ZN129:PA52 | ZN00129/000052 | RYDE | UG | Not Veg | 2015-02-19 | N | 211.4879 | N | 3 | N | N | 1.1101 | 39.4971 | 108338.9197
[7 empty] | 14264 | 16987 | 1212282 | 2015-02-20 12:19 | 2015-02-20 12:46 | 27 | 11kV | 1647 | 61 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | LID 150742 1 fault operation Fdr 34238 tripped but only Perkins St sub 19126 interrupted. Supply restored to customers at 12.46hrs. Sw 34238 -- Intertrip receive. | February | 2015 | 2015Q3 | 2015 | 202:34238 43 48 | 202:34238 43 48 | ZN00202/34238 43 48 | NEWCASTLE | UG | Not Veg | 2015-02-20 | N | 27 | N | 5 | N | N | 1.1101 | 39.4971 | 1203.579
[7 empty] | 14623 | 19910 | 1212169 | 2015-02-20 07:01 | 2015-02-20 14:05 | 424 | 11kV | 424 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 150747 Single phase DOLF assembly ; 10 Amp DOLF porcelain failed due to old age or being faulty | February | 2015 | 2015Q3 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2015-02-20 | N | 424 | N | 5 | N | N | 1.1101 | 39.4971 | 309.8467
[7 empty] | 13002 | 6831 | 1212353 | 2015-02-20 16:16 | 2015-02-20 16:52 | 36 | 11kV | 22716 | 1179 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150750 A & C phase DOLF : 40 Amp Tree branch on 11kV bushings at sub 47935 | February | 2015 | 2015Q3 | 2015 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Veg | 2015-02-20 | N | 19.2672 | N | 5 | N | N | 1.1101 | 39.4971 | 16600.1828
[7 empty] | 12281 | 231 | 1212404 | 2015-02-20 20:33 | 2015-02-20 22:18 | 105 | 11kV | 105 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150752 A phase DOLF : 10 Amp Excluded OMS 1212404 | February | 2015 | 2015Q3 | 2015 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2015-02-20 | N | 105 | N | 5 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 13850 | 13669 | 1212424 | 2015-02-20 23:18 | 2015-02-21 00:39 | 81 | 11kV | 810 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Ex Zn12600 Lisarow section of Pa9 At PT11671 Oliver Taylors 10Amp HDO footpath phase fuse blown Tree branch contact - other Made safe and restored supply See 1213250 exclude 1212424,5 | February | 2015 | 2015Q3 | 2015 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2015-02-20 | N | 81 | N | 5 | N | N | 1.1101 | 39.4971 | 591.9241
[7 empty] | 14435 | 18197 | 1212496 | 2015-02-21 10:03 | 2015-02-21 11:40 | 97 | 11kV | 291 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150755 A & C Phase DOLF : 16 Amp excluded OMS 1212496 | February | 2015 | 2015Q3 | 2015 | 513:48056 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2015-02-21 | N | 97 | N | 4 | N | N | 1.1101 | 39.4971 | 212.6542
[7 empty] | 12986 | 6725 | 1212486 | 2015-02-21 09:36 | 2015-02-21 12:15 | 159 | 11kV | 318 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150756 C phase DOLF : 16 Amp Excluded 1212486 | February | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-02-21 | N | 159 | N | 4 | N | N | 1.1101 | 39.4971 | 232.385
[7 empty] | 12601 | 3230 | 1212477 | 2015-02-21 09:09 | 2015-02-21 13:10 | 241 | 11kV | 241 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150757 Single phase DOLF : 10 Amp Excluded OMS 1212477 | February | 2015 | 2015Q3 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2015-02-21 | N | 241 | N | 4 | N | N | 1.1101 | 39.4971 | 176.1157
[7 empty] | 13726 | 12748 | 1212532 | 2015-02-21 11:36 | 2015-02-21 14:00 | 144 | 11kV | 144 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150758 Single phase DOLF : 10 Amp Excluded OMS 1212532 | February | 2015 | 2015Q3 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2015-02-21 | N | 144 | N | 4 | N | N | 1.1101 | 39.4971 | 105.231
[7 empty] | 13981 | 14791 | 1212712 | 2015-02-22 13:22 | 2015-02-22 15:10 | 108 | 11kV | 37584 | 348 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford Zone section of Pa9 "Wyoming" At LB43610 footpath side HV bond burnt off. See 1213275 exclude 1212712 | February | 2015 | 2015Q3 | 2015 | ZN12650:PA9 | ZN12650:PA9 | ZN12650/000009 | CENTRAL COAST | OH | Not Veg | 2015-02-22 | N | 108 | N | 5 | N | N | 1.1101 | 39.4971 | 27465.2787
[7 empty] | 13039 | 7071 | 1212731 | 2015-02-22 14:36 | 2015-02-22 18:00 | 203.6667 | 11kV | 6721 | 33 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | 150765 Single phase DOLF : 16 Amp Magpie found on trans bushings at sub 72941, DOLF 10A fuse blown but did not drop open. | February | 2015 | 2015Q3 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2015-02-22 | N | 203.6667 | N | 5 | N | N | 1.1101 | 39.4971 | 4911.5086
[7 empty] | 12451 | 1792 | 1212638 | 2015-02-22 06:02 | 2015-02-22 20:37 | 875 | 11kV | 22147 | 243 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 150763 1 fault operation A & B phase Overcurrent Excluded OMS 1212638; 1212640 & 1212652 | February | 2015 | 2015Q3 | 2015 | 203:8089 | 204:82703 | ZN00204/082703 | NEWCASTLE | Unknown | Unknown | 2015-02-22 | N | 91.1399 | N | 5 | N | N | 1.1101 | 39.4971 | 16184.3744
[7 empty] | 12436 | 1693 | 1212772 | 2015-02-22 21:25 | 2015-02-22 23:00 | 95 | 11kV | 1235 | 13 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 150768 Customer felled tree & broke crossarm CUSTOMER PUSHED A TREE OVER WITH A TRACTO AND CONTACTED THE 11KV OH MAINS. THERE IS NOW A BROKEN 11KV CROSS ARM AND DAMAGE TO 11KV CONDUCTOR AT SUB 48845, POLE HV6-7088. - 5 CRANFORD RD AWABA Excluded oms 1212772 | February | 2015 | 2015Q3 | 2015 | 239:82131 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Veg | 2015-02-22 | N | 95 | N | 5 | N | N | 1.1101 | 39.4971 | 902.5016
[7 empty] | 13069 | 7391 | 1213057 | 2015-02-22 19:47 | 2015-02-23 03:15 | 448 | 11kV | 106697 | 2126 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 150767 pole fire OS-20268 33kV/11kV | February | 2015 | 2015Q3 | 2015 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2015-02-22 | N | 50.1867 | N | 5 | N | N | 1.1101 | 39.4971 | 77971.0206
[7 empty] | 12663 | 3845 | 1212824 | 2015-02-23 07:50 | 2015-02-23 12:55 | 305 | 11kV | 610 | 2 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | No Weather Impact | N | @S8103 Derby Suttor No.3, 11kv RMCB tripped due to water penetrating into O/C relay. Section of 11kv Panel 17 "S.8103 Derby Suttor No.3" feeder at Zn.167 Auburn. Remarks: other - details provided. Water ingress into O/C relay caused RMCB to trip | February | 2015 | 2015Q3 | 2015 | ZN167:PA17 | ZN167:PA17 | ZN00167/000017 | PARRAMATTA | UG | Not Veg | 2015-02-23 | N | 305 | N | 3 | N | N | 1.1101 | 39.4971 | 445.77
[7 empty] | 12494 | 2205 | 1213035 | 2015-02-23 13:50 | 2015-02-23 15:00 | 70 | 11kV | 70 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150778 Single phase DOLF : 10 Amp | February | 2015 | 2015Q3 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2015-02-23 | N | 70 | N | 3 | N | N | 1.1101 | 39.4971 | 51.1539
[7 empty] | 13029 | 7025 | 1213189 | 2015-02-24 03:06 | 2015-02-24 04:43 | 97 | 11kV | 127943 | 1319 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1193 Lindfield Panel 12 Tripped - reclosed - tripped and locked out on Relays: B and C phase IOC Cause: Loud explosion outside 81 stanhope Rd Killara - Suspect Possum See OMS 1213190 1213189 | February | 2015 | 2015Q3 | 2015 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Not Veg | 2015-02-24 | N | 97 | N | 5 | N | N | 1.1101 | 39.4971 | 93496.9707
[7 empty] | 14175 | 16296 | 1213229 | 2015-02-24 08:42 | 2015-02-24 10:42 | 120 | 11kV | 89640 | 747 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN35800 Bankstown 11kv VCB panel 22 "S-6352 Bonds Martin" feeder tripped on: Relays: B phase IOC, EFI, Fault Check Field EFI's: S-8320 Signals: GE, ZNE, 11kv Trip Remarks: UG fault. 11kv U/G feeder fault from ZN35800 Bankstown panel 22 to S-6352 Bonds Martin | February | 2015 | 2015Q3 | 2015 | ZN35800:PA22 | ZN35800:PA22 | ZN35800/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-02-24 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 65506.2681
[7 empty] | 13237 | 8622 | 1213111 | 2015-02-23 16:17 | 2015-02-24 16:40 | 1463 | 11kV | 189139 | 143 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | Section of ZN.15014 Mona Vale 11kV Panel 12 from S.16529 to extent of feeder (3 DC's supplied by generator) Affected DC's:- S.16529 Elivina bay North, S.16530 Lovett Bay, S.16419 Towlers Bay Cause:- MG set tripped off on low volts, Aggreko generator has faile and is defective. Replacement to arrive next day. ME:-1213633 RS:-1213635, 1213634 Withdrawn:-1213111 | February | 2015 | 2015Q3 | 2015 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | UG | Not Veg | 2015-02-23 | N | 1322.6503 | N | 3 | N | N | 1.1101 | 39.4971 | 138217.2025
[7 empty] | 13083 | 7488 | 1213410 | 2015-02-24 13:47 | 2015-02-24 20:20 | 393 | 11kV | 11342 | 168 | HV | Vegetation Blow/Fall In | Vegetation | Air Break Switch | Unplanned | No Weather Impact | N | Ex ZN12690 Berkeley Vale section of Pa26R "Wyong Rd" Recloser 50096 Tonkiss Pacific - tripped, reclosed and locked out on timed overcurrent Tree branch on LB44750 causing bond to burn off to PT14761 see seperate interruption for recloser 47878 Pacific Palmdale See 1213765,6 2nd 1213769 exclude 1213410,44 | February | 2015 | 2015Q3 | 2015 | ZN12690:PA26 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Veg | 2015-02-24 | N | 67.5119 | N | 5 | N | N | 1.1101 | 39.4971 | 8288.3991
[7 empty] | 13986 | 14806 | 1213568 | 2015-02-24 22:14 | 2015-02-25 00:24 | 130 | 11kV | 134270 | 1549 | HV | Equipment Failed in Service | Equipment Failure | Enclosed Load Break Switch | Unplanned | No Weather Impact | N | Zn12650 West Gosford Panel 20 fdr tripped & locked out on Relays - A&B phase overcurrnt, EFI, Lockout, TIming Signals: 11kv trip IR49608 Frederick Auburn Failed & caught alight . HV bond Burnt off @ UGOH to S61185/SwA See 1213813,5 Exclude 1213568,9,70,1,2,3,8 | February | 2015 | 2015Q3 | 2015 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | OH | Not Veg | 2015-02-24 | N | 86.6817 | N | 5 | N | N | 1.1101 | 39.4971 | 98120.5557
[7 empty] | 13534 | 11155 | 1213591 | 2015-02-25 02:31 | 2015-02-25 04:15 | 104 | 11kV | 936 | 9 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S35900 Potts Hill Panel 11 "S7929 North Muir No 2" fdr tripped on Relays - 50TN Timed EF, 51IN EF & OC, EFI Signals: 11kv trip, Tx1 GE Remarks: UG fault. 11kv UG from S64056 Worth Muir No 4 to S2611 Hume Shellcote No 1 to S4477 Tennyson Hume | February | 2015 | 2015Q3 | 2015 | ZN35900:PA11 | ZN35900:PA11 | ZN35900/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-02-25 | N | 104 | N | 6 | N | N | 1.1101 | 39.4971 | 684.0012
[7 empty] | 14176 | 16297 | 1213581 | 2015-02-24 20:18 | 2015-02-25 04:30 | 492 | 11kV | 1778 | 302 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | Zn14143 Somersby 11kv Panel 10 "Somersby East" fdr tripped and recloed Relays: EFI, B&C phase overload Signals: 11kv trip, No.1 Group Earth EFI's: S46875 Overhead wire down See 1213782,3 | February | 2015 | 2015Q3 | 2015 | ZN14143:PA10 | ZN14143:PA12 | ZN14143/000012 | CENTRAL COAST | OH | Not Veg | 2015-02-24 | N | 5.8874 | N | 5 | N | N | 1.1101 | 39.4971 | 1299.31
[7 empty] | 13112 | 7729 | 1213590 | 2015-02-25 02:05 | 2015-02-25 09:52 | 466.9333 | 11kV | 23297.5833 | 50 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | PT 62154 Deepwater Estate - Centre phase HDO (63A). Cause not ascertained. ME: 1213590. Withdrawn: 1213640. CC1: 22-"Refer to SOp" | February | 2015 | 2015Q3 | 2015 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | OH | Veg | 2015-02-25 | N | 465.9517 | N | 6 | N | N | 1.1101 | 39.4971 | 17025.1867
[7 empty] | 14453 | 18332 | 1213723 | 2015-02-25 10:50 | 2015-02-25 12:14 | 84 | 11kV | 1702 | 23 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn.2568 St Peters - Pnl.6 triped on Earth Fault with Fault Check Field EFIs: S816 and S8178 Abnormal: S6103 (Sw A) CLOSED - S47663 (Sw A) OPEN & S8539 (Sw A) CLOSED - Pnl.8 OPEN UG Cable fault between S87178 Elizabeth Richard #2 and S7757 RPA Salisbury Temp see 1214030 1214032 | February | 2015 | 2015Q3 | 2015 | ZN2568:PA6 | ZN2568:PA6 | ZN02568/000006 | SYDNEY | UG | Not Veg | 2015-02-25 | N | 74 | N | 6 | N | N | 1.1101 | 39.4971 | 1243.7714
[7 empty] | 13230 | 8588 | 1213870 | 2015-02-25 14:54 | 2015-02-25 16:35 | 101 | 11kV | 1010 | 10 | HV | Vegetation Blow/Fall In | Vegetation | Lightning Arrestor | Unplanned | Rain Light | N | Ex Zn12600 Lisarow section of Pa2 PT11410 Wingrove Talbingo 11kv 16Amp Centre and roadside dropout fuses operated Tree branch on surge arrestors. Rmoved by Dop. See 1214108 exclude 1213870,1,99 | February | 2015 | 2015Q3 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2015-02-25 | N | 101 | N | 6 | N | N | 1.1101 | 39.4971 | 738.0782
[7 empty] | 13223 | 8552 | 1213681 | 2015-02-25 09:40 | 2015-02-25 18:00 | 500 | 11kV | 500 | 1 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 150815 Single phase Sub isolated for safety. Staff advised stay wire fell away to within clearances of TX. Staff also reported STAY WIRE WAS NOT REPLACED, PLEASE HAVE LOACAL STAFF CONFIRM IF THE STAY WIRE SHOULD OR SHOULD NOT BE REPLACED. Staff reported all crossarms are in very poor condition and probably need replacing. Excluded OMS 1213681 | February | 2015 | 2015Q3 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2015-02-25 | N | 500 | N | 6 | N | N | 1.1101 | 39.4971 | 365.3853
[7 empty] | 13790 | 13198 | 1213952 | 2015-02-25 19:09 | 2015-02-25 20:40 | 91 | 11kV | 91 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150816 C Phase DOLF : 16 Amp Excluded OMS 1213952 | February | 2015 | 2015Q3 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2015-02-25 | N | 91 | N | 6 | N | N | 1.1101 | 39.4971 | 66.5001
[7 empty] | 12458 | 1832 | 1214177 | 2015-02-26 15:45 | 2015-02-26 17:07 | 81.9 | 11kV | 9009 | 110 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150833 2 fault operations Pole mounted RAGCB, OVercurrent | February | 2015 | 2015Q3 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-02-26 | N | 81.9 | N | 25 | Y | Y | 1.1101 | 39.4971 | 6583.5115
[7 empty] | 14564 | 19179 | 1214067 | 2015-02-26 13:30 | 2015-02-26 17:45 | 255 | 11kV | 255 | 1 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 1509840 Earths Stolen from pole Excluded OMS 1214067 | February | 2015 | 2015Q3 | 2015 |  |  |  |  | OH | Not Veg | 2015-02-26 | N | 255 | N | 25 | Y | Y | 1.1101 | 39.4971 | 186.3465
[7 empty] | 13131 | 7846 | 1214212 | 2015-02-26 17:20 | 2015-02-26 18:30 | 70 | 11kV | 70 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | No LID - details based on field crew report Lightning storm Excludes OMS 1214212 | February | 2015 | 2015Q3 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2015-02-26 | N | 70 | N | 25 | Y | Y | 1.1101 | 39.4971 | 51.1539
[7 empty] | 13968 | 14680 | 1214173 | 2015-02-26 15:35 | 2015-02-26 18:45 | 190.0333 | 11kV | 1330.2333 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150843 20 AMP FUSE LINE DOLF, SUBSTATION DOLF EXCLUDES 1214176 Blown Spur fuses 75479. Replaced OK 20A Blown Sub DOLFS Sub 64461. Replaced OK 10A CC1: 22-"Refer to SOp" | February | 2015 | 2015Q3 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-02-26 | N | 190.0333 | N | 25 | Y | Y | 1.1101 | 39.4971 | 972.0953
[7 empty] | 12367 | 1045 | 1214236 | 2015-02-26 18:06 | 2015-02-26 21:20 | 194 | 11kV | 135994 | 701 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 150861 Wires down between ABS 74091 & P. 8M-30086. | February | 2015 | 2015Q3 | 2015 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2015-02-26 | N | 194 | N | 25 | Y | Y | 1.1101 | 39.4971 | 99380.4041
[7 empty] | 12769 | 4715 | 1214299 | 2015-02-26 21:32 | 2015-02-26 22:40 | 68 | 11kV | 68 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150846 10 amp fuse Substatoin DOLF Excludes OMS 1214299 | February | 2015 | 2015Q3 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2015-02-26 | N | 68 | N | 25 | Y | Y | 1.1101 | 39.4971 | 49.6924
[7 empty] | 12977 | 6620 | 1214245 | 2015-02-26 18:37 | 2015-02-26 22:53 | 256 | 11kV | 83527 | 472 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 150865 4 fault operation Cable faulty between Sw 39024 tech College sub & Sw 11024 MBK South P/S sub. Excluded OMS 1214245 | February | 2015 | 2015Q3 | 2015 | 801:74120 | 801:74120 | ZN00801/074120 | MUSWELLBROOK | UG | Not Veg | 2015-02-26 | N | 176.964 | N | 25 | Y | Y | 1.1101 | 39.4971 | 61039.068
[7 empty] | 13614 | 11820 | 1214467 | 2015-02-26 22:00 | 2015-02-26 22:53 | 53 | 11kV | 4890 | 2008 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 150866 See LID 150865 4 fault operation Cable faulty between Sw 39024 tech College sub & Sw 11024 MBK South P/S sub. Excluded OMS 1214245 | February | 2015 | 2015Q3 | 2015 | 801:74120 | 801:74120 | ZN00801/074120 | MUSWELLBROOK | OH | Not Veg | 2015-02-26 | N | 2.4353 | N | 25 | Y | Y | 1.1101 | 39.4971 | 3573.4678
[7 empty] | 13788 | 13193 | 1214472 | 2015-02-26 22:15 | 2015-02-26 22:53 | 38 | 11kV | 2033 | 1959 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 150867 see LID 150865 4 fault operation Cable faulty between Sw 39024 tech College sub & Sw 11024 MBK South P/S sub. Excluded OMS 1214245 | February | 2015 | 2015Q3 | 2015 | 801:74120 | 801:74120 | ZN00801/074120 | MUSWELLBROOK | UG | Not Veg | 2015-02-26 | N | 1.0378 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1485.6564
[7 empty] | 14562 | 19176 | 1214628 | 2015-02-26 19:30 | 2015-02-26 23:30 | 240 | 11kV | 2640 | 11 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 150870 OMS 1214321 No Protection. Isolated to make repairs. See # 150869 | February | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2015-02-26 | N | 240 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1929.2341
[7 empty] | 14082 | 15676 | 1214276 | 2015-02-26 19:33 | 2015-02-27 00:05 | 272 | 11kV | 1360 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150854 A & C phase DOLF : 10 Amp | February | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-02-26 | N | 272 | N | 25 | Y | Y | 1.1101 | 39.4971 | 993.8479
[7 empty] | 12378 | 1158 | 1214296 | 2015-02-26 21:12 | 2015-02-27 00:05 | 173 | 11kV | 865 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150856 10 amp fuse Substation DOLF Excludes OMS 1214296 | February | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-02-26 | N | 173 | N | 25 | Y | Y | 1.1101 | 39.4971 | 632.1165
[7 empty] | 13984 | 14804 | 1214235 | 2015-02-26 18:09 | 2015-02-27 00:30 | 381 | 11kV | 27368 | 142 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 150920 A phase Overcurrent Wires down at Merton Spur recloser | February | 2015 | 2015Q3 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2015-02-26 | N | 192.7324 | N | 25 | Y | Y | 1.1101 | 39.4971 | 19999.7272
[7 empty] | 14317 | 17328 | 1214302 | 2015-02-26 21:37 | 2015-02-27 00:30 | 173 | 11kV | 173 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Electrical Storm | N | LID 150855 3 amp fuse Substation DOLF Excludes oMS 1214302 | February | 2015 | 2015Q3 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2015-02-26 | N | 173 | N | 25 | Y | Y | 1.1101 | 39.4971 | 126.4233
[7 empty] | 13632 | 11975 | 1214326 | 2015-02-26 23:45 | 2015-02-27 00:49 | 64 | 11kV | 62656 | 979 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN7900 Campbell St - Pnl.16 tripped on: B & C phase O/C, EF, EF Check, Trip LED, EF time out, O/C Time out, EFI Signals: Tx 2 GE, 11kv Trip Field EFIs: S3368, 36065, 8799 8430 UG Cable fault from S8430 Pelican Waine No.1 to S6222 Brisbane Poplar Sections of feeder restored at the same time (0:49) via Panels 4 & 16 see 1214387 1214388 | February | 2015 | 2015Q3 | 2015 | ZN7900:PA16 | ZN7900:PA16 | ZN07900/000016 | SYDNEY | UG | Not Veg | 2015-02-26 | N | 64 | N | 25 | Y | Y | 1.1101 | 39.4971 | 45787.1568
[7 empty] | 12823 | 5272 | 1214310 | 2015-02-26 21:46 | 2015-02-27 01:00 | 194 | 11kV | 194 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150857 Substation DOLF Excludes OMS 1214310 | February | 2015 | 2015Q3 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2015-02-26 | N | 194 | N | 25 | Y | Y | 1.1101 | 39.4971 | 141.7695
[7 empty] | 13282 | 8991 | 1214306 | 2015-02-26 21:42 | 2015-02-27 01:20 | 218 | 11kV | 218 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150858 10 amp fuse Substation DOLF Excludes OMS 1214306 | February | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-02-26 | N | 218 | N | 25 | Y | Y | 1.1101 | 39.4971 | 159.308
[7 empty] | 13593 | 11642 | 1214323 | 2015-02-26 23:43 | 2015-02-27 01:24 | 101 | 11kV | 96152 | 952 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn80 Chatswood Pa25 fdr tripped, reclosed, tripped & locked out on Relays: A & C phase IOC, EF, EFI Siganls: 11kv trip, Zone Earth, Tx 11 Group Earth EFI: S35000 Cause: Underground Frontline feeder fault from Zn80 Chatswood Pa25 to S3451. See also HV interruption to Chatswood Tx11. | February | 2015 | 2015Q3 | 2015 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | UG | Not Veg | 2015-02-26 | N | 101 | N | 25 | Y | Y | 1.1101 | 39.4971 | 70265.0456
[7 empty] | 13012 | 6896 | 1214331 | 2015-02-26 18:42 | 2015-02-27 01:35 | 413 | 11kV | 50799 | 123 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150860 1 fault operation Pole mounted RAGCB, Overcurrent Excludes OMS 1214612 | February | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2015-02-26 | N | 413 | N | 25 | Y | Y | 1.1101 | 39.4971 | 37122.4109
[7 empty] | 14439 | 18219 | 1214312 | 2015-02-26 19:00 | 2015-02-27 03:00 | 480 | 11kV | 960 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 150884 replaced LL Clamp Excludes OMS 1214312 | February | 2015 | 2015Q3 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2015-02-26 | N | 480 | N | 25 | Y | Y | 1.1101 | 39.4971 | 701.5397
[7 empty] | 14436 | 18205 | 1214339 | 2015-02-26 18:42 | 2015-02-27 04:25 | 583 | 11kV | 43770 | 380 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Electrical Storm | N | LID 150869 2 fault operations Overcurrent, Earth Fault ABS 43226 Faulty. Bonds tied back. ABS Black pinned. Excludes OMS 1216736 Also refer to related job 1216741 - 16 amp fuse Line DOLF 74067 also blew | February | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2015-02-26 | N | 115.1842 | N | 25 | Y | Y | 1.1101 | 39.4971 | 31985.825
[7 empty] | 13675 | 12340 | 1214375 | 2015-02-26 19:00 | 2015-02-27 09:05 | 845 | 11kV | 5915 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150887 DOLF : 10 Amp Excluded OMS 1214375 | February | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-02-26 | N | 845 | N | 25 | Y | Y | 1.1101 | 39.4971 | 4322.5075
[7 empty] | 14437 | 18206 | 1214402 | 2015-02-27 08:25 | 2015-02-27 09:30 | 65 | 11kV | 1430 | 22 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | No LID - based on field crew report Replaced 16Amp Spur fuse 74067 Excludes OMS 1214402 | February | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2015-02-27 | N | 65 | N | 11 | N | N | 1.1101 | 39.4971 | 1045.0018
[7 empty] | 13792 | 13232 | 1215855 | 2015-02-26 19:00 | 2015-02-27 09:45 | 885 | 11kV | 885 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Lightning Arrestor | Unplanned | Previous Storm | N | LID 150881 Repolaced blown Lightning Arrestor Excluded OMS 1215855 | February | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-02-26 | N | 885 | N | 25 | Y | Y | 1.1101 | 39.4971 | 646.7319
[7 empty] | 13628 | 11934 | 1214478 | 2015-02-27 10:22 | 2015-02-27 11:03 | 41 | 11kV | 71873 | 1753 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn2310 Punchbowl 11kv Pnl 38 (S5076, AB893 etc) tripped, reclosed and tripped on: Relays: IOC A phase, EFI, Earth fault, Timing Relay, Lockout Signals: 11kv trip, Zone Earth, Group Earth Tx 5 Remarks: Crane hit OH, Excavator hit OH 11kv feeder outside 91 Wattle St, Mt Lewis (Mount Lewis Bowling Club) No damage to OH conductors. | February | 2015 | 2015Q3 | 2015 | ZN2310:PA38 | ZN2310:PA23 | ZN02310/000023 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-02-27 | N | 41 | N | 11 | N | N | 1.1101 | 39.4971 | 52522.6685
[7 empty] | 13548 | 11300 | 1216328 | 2015-02-26 16:33 | 2015-02-27 11:20 | 1127 | 11kV | 12839 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150879 3 fault operations excluded OMS 1214194 | February | 2015 | 2015Q3 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-02-26 | N | 755.2353 | N | 25 | Y | Y | 1.1101 | 39.4971 | 9382.3625
[7 empty] | 14400 | 17947 | 1214342 | 2015-02-27 08:00 | 2015-02-27 11:55 | 235 | 11kV | 470 | 2 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 150897 REPLACED 11kV BRIDGE LL LEAD ON POLE 8N-30413 Excxludes OMS 1214342 | February | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2015-02-27 | N | 235 | N | 11 | N | N | 1.1101 | 39.4971 | 343.4621
[7 empty] | 13512 | 11039 | 1214348 | 2015-02-27 06:25 | 2015-02-27 12:10 | 345 | 11kV | 2415 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150898 20 amp fuse Line DOLF | February | 2015 | 2015Q3 | 2015 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2015-02-27 | N | 345 | N | 11 | N | N | 1.1101 | 39.4971 | 1764.8108
[7 empty] | 12559 | 2923 | 1214358 | 2015-02-27 12:20 | 2015-02-27 12:25 | 5 | 11kV | 15 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 150914 Substation DOLF Replace Arrestors | February | 2015 | 2015Q3 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2015-02-27 | N | 5 | N | 11 | N | N | 1.1101 | 39.4971 | 10.9616
[7 empty] | 12288 | 325 | 1214512 | 2015-02-26 22:28 | 2015-02-27 14:10 | 942 | 11kV | 1884 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 150911 Replaced Tx | February | 2015 | 2015Q3 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2015-02-26 | N | 942 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1376.7716
[7 empty] | 12904 | 6016 | 1214380 | 2015-02-27 07:56 | 2015-02-27 14:45 | 408.8333 | 11kV | 408.8333 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150912 Single phase 10 amp fuse Substation DOLF HV DOLF REPLACED ON A & C PHASE | February | 2015 | 2015Q3 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2015-02-27 | N | 408.8333 | N | 11 | N | N | 1.1101 | 39.4971 | 298.7633
[7 empty] | 12438 | 1696 | 1214359 | 2015-02-27 07:01 | 2015-02-27 15:15 | 494 | 11kV | 988 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Previous Storm | N | LID 150903 3 amp fuse Substation DOLF Excludes OMS 1214359 | February | 2015 | 2015Q3 | 2015 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2015-02-27 | N | 494 | N | 11 | N | N | 1.1101 | 39.4971 | 722.0013
[7 empty] | 13626 | 11926 | 1214511 | 2015-02-27 11:36 | 2015-02-27 15:25 | 229 | 11kV | 229 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150904 replaced DOLF sub 71289 B phase 16A | February | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-02-27 | N | 229 | N | 11 | N | N | 1.1101 | 39.4971 | 167.3464
[7 empty] | 13494 | 10907 | 1214487 | 2015-02-27 11:00 | 2015-02-27 15:35 | 275 | 11kV | 825 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 150916 | February | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2015-02-27 | N | 275 | N | 11 | N | N | 1.1101 | 39.4971 | 602.8857
[7 empty] | 13571 | 11468 | 1214584 | 2015-02-27 14:02 | 2015-02-27 16:30 | 148 | 11kV | 148 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150905 10 amp fuseSubstation DOLF Excludes OMS 1214584 | February | 2015 | 2015Q3 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2015-02-27 | N | 148 | N | 11 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 14081 | 15674 | 1214662 | 2015-02-27 19:21 | 2015-02-27 21:50 | 149 | 11kV | 298 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 1215584 10 amp fuse Substation DOLF Excludes OMS 1214662 | February | 2015 | 2015Q3 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2015-02-27 | N | 149 | N | 11 | N | N | 1.1101 | 39.4971 | 217.7696
[7 empty] | 14578 | 19326 | 1214691 | 2015-02-28 06:00 | 2015-02-28 06:35 | 35 | 11kV | 35 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150923 40 AMP FUSE SUBSTATION DOLF No cause found 240V per phase as left. EXCLUDES OMS 1214691 | February | 2015 | 2015Q3 | 2015 | 233:82821 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Veg | 2015-02-28 | N | 35 | N | 7 | N | N | 1.1101 | 39.4971 | 25.577
[7 empty] | 14647 | 20122 | 1214698 | 2015-02-28 08:35 | 2015-02-28 12:00 | 205 | 11kV | 205 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150927 10 amp fuse Substation DOLF Excludes OMS 1214698 | February | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-02-28 | N | 205 | N | 7 | N | N | 1.1101 | 39.4971 | 149.808
[7 empty] | 13095 | 7617 | 1216131 | 2015-02-28 00:34 | 2015-02-28 12:02 | 688 | 11kV | 8256 | 12 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 150928 A phase Aph tapping burnt off pole BL-60262. Excluded OMS No. 1214682 + 1214693 | February | 2015 | 2015Q3 | 2015 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2015-02-28 | N | 688 | N | 7 | N | N | 1.1101 | 39.4971 | 6033.2413
[7 empty] | 12315 | 580 | 1214717 | 2015-02-28 10:44 | 2015-02-28 13:35 | 171 | 11kV | 513 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150930 10 amp fuse Substation DOLF Tx Volts: Aph - 236V, Bph - 236V, Cph - 238V | February | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2015-02-28 | N | 171 | N | 7 | N | N | 1.1101 | 39.4971 | 374.8853
[7 empty] | 13623 | 11920 | 1214729 | 2015-02-28 16:25 | 2015-02-28 16:50 | 25 | 11kV | 675 | 27 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S.16694 Old Pittwater Rd 84 Cause:- Fluctuating voltage, no fuses blown, D/Op reported transformer maing unusual noises and interrupted Tx. To be repaced on 1/3/15, LV// by D/Op USL.45918 and USL.37257 to restore supply. ME:-1215479 Withdrawn:-1214744, 1214729 | February | 2015 | 2015Q3 | 2015 | ZN15001:PA11 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | UG | Not Veg | 2015-02-28 | N | 25 | N | 7 | N | N | 1.1101 | 39.4971 | 493.2701
[7 empty] | 13658 | 12168 | 1214753 | 2015-02-28 13:41 | 2015-02-28 18:00 | 259 | 11kV | 517.5667 | 2 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of Panel 26R "Wyong Rd" PT14761 Pacific Old Tuggerah 1.1 11kv centre phase HDO has blown and has a borken insulator that requires replacement. See 1215575 GIS 1214753 | February | 2015 | 2015Q3 | 2015 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2015-02-28 | N | 258.7833 | N | 7 | N | N | 1.1101 | 39.4971 | 378.2225
[7 empty] | 14401 | 17950 | 1214821 | 2015-02-28 21:59 | 2015-03-01 09:44 | 704.5333 | 11kV | 37340.2667 | 53 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | LID 150933 3 fault operations Pole mounted RAGCB Excludes OMS 1214823 | February | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2015-02-28 | N | 704.5333 | N | 7 | N | N | 1.1101 | 39.4971 | 27287.1655
[7 empty] | 12694 | 4084 | 1214904 | 2015-03-01 13:21 | 2015-03-01 14:05 | 43.7667 | 11kV | 30417.8333 | 695 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 150939 1 fault operation Overcurrent, Earth fault Blown UGOH at pole IV-31001. Excludes OMS 1214908/912 | March | 2015 | 2015Q3 | 2015 | 217:33608 | 217:33608 | ZN00217/033608 | LAKE MACQUARIE | Unknown | Unknown | 2015-03-01 | N | 43.7667 | N | 32 | Y | Y | 1.1101 | 39.4971 | 22228.4554
[7 empty] | 12401 | 1428 | 1214905 | 2015-03-01 13:23 | 2015-03-01 14:26 | 63 | 11kV | 87786 | 1396 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ZN 10997 Sans Souci - Pnl 12 - SEL left. AB 31158 Bond off. ME: 1216786. Rest Step: 1216789. Withdrawn: 1214905. | March | 2015 | 2015Q3 | 2015 | ZN10997:PA12 | ZN10997:PA12 | ZN10997/000012 | BAYSIDE | OH | Not Veg | 2015-03-01 | N | 62.884 | N | 32 | Y | Y | 1.1101 | 39.4971 | 64151.4196
[7 empty] | 14457 | 18376 | 1214991 | 2015-03-01 16:04 | 2015-03-01 17:08 | 64 | 11kV | 53888 | 842 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At Zn1673 Turramurra Pa13 tripped on B phase IOC Cause: Tree on OH O/S 35 Holt St Wahroonga | March | 2015 | 2015Q3 | 2015 | ZN1673:PA13 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | OH | Veg | 2015-03-01 | N | 64 | N | 32 | Y | Y | 1.1101 | 39.4971 | 39379.761
[7 empty] | 12851 | 5556 | 1215103 | 2015-03-01 17:28 | 2015-03-01 18:45 | 77 | 11kV | 4851 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 150951 300 amp fuse Distribution LV fuse Excludes OMS 1215103 | March | 2015 | 2015Q3 | 2015 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Veg | 2015-03-01 | N | 77 | N | 32 | Y | Y | 1.1101 | 39.4971 | 3544.9677
[7 empty] | 13712 | 12628 | 1214965 | 2015-03-01 15:54 | 2015-03-01 19:00 | 186 | 11kV | 99073 | 728 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Rain Wind Storm | N | ZN 10994 Mortdale - Pnl 11 - Trip/reclose/trip, A & B phase IOC, Earth fault and EFI, lockout. PT 10958 blew 2 fuses, hit by lightning. ME: 1216809. Rest STeps: 1216812, 3. Withdrawn: 1214965. | March | 2015 | 2015Q3 | 2015 | ZN10994:PA11 | ZN10994:PA11 | ZN10994/000011 | GEORGES RIVER | OH | Not Veg | 2015-03-01 | N | 136.0893 | N | 32 | Y | Y | 1.1101 | 39.4971 | 72399.6262
[7 empty] | 13715 | 12636 | 1215118 | 2015-03-01 17:31 | 2015-03-01 19:04 | 93 | 11kV | 102519 | 1359 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | zn14891 Wyong 11kv Pa8 fdr tripped Relays: timed OC, E/F check EFI Signals: 11kv trip EFI's Nil Weather related. DOp patrolled, no cause found See 1215661,2 Exclude 1215118,275 | March | 2015 | 2015Q3 | 2015 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2015-03-01 | N | 75.4371 | N | 32 | Y | Y | 1.1101 | 39.4971 | 74917.8614
[7 empty] | 13493 | 10906 | 1214960 | 2015-03-01 15:51 | 2015-03-01 19:19 | 208 | 11kV | 169650 | 1138 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | N | ZN 10991 Blakehurst - Pnl 13 - Trip/reclose/trip, A phase timed and IOC and C phase, timing, lockout. DOp Stanborough patrolled feeder. Tree branch removed by mains on Terry Rd. ME: 1216799. Rest STep: 1216800. Withdrawn: 1214960. | March | 2015 | 2015Q3 | 2015 | ZN10991:PA13 | ZN10991:PA13 | ZN10991/000013 | GEORGES RIVER | OH | Veg | 2015-03-01 | N | 149.0773 | N | 32 | Y | Y | 1.1101 | 39.4971 | 123975.2162
[7 empty] | 12427 | 1610 | 1215261 | 2015-03-01 18:44 | 2015-03-01 19:56 | 72 | 11kV | 112752 | 1566 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150954 Overcurrent, Earth fault targets 51N | March | 2015 | 2015Q3 | 2015 | 233:82815 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2015-03-01 | N | 72 | N | 32 | Y | Y | 1.1101 | 39.4971 | 82395.836
[7 empty] | 13717 | 12652 | 1215188 | 2015-03-01 17:57 | 2015-03-01 20:13 | 135.7 | 11kV | 8142 | 60 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn12600 Lisarow section fo Pa3 PT12083 Freen Oaks Baree. 11kv roadside 31.5A HDO fuse blown No cause found. Weather related See 1215163 exclude 1215188 | March | 2015 | 2015Q3 | 2015 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2015-03-01 | N | 135.7 | N | 32 | Y | Y | 1.1101 | 39.4971 | 5949.9335
[7 empty] | 14496 | 18653 | 1216354 | 2015-03-01 18:15 | 2015-03-01 20:30 | 135 | 11kV | 5805 | 43 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150953 1 fault operation Did not reclose due to previous trip 1 minute earlier | March | 2015 | 2015Q3 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2015-03-01 | N | 135 | N | 32 | Y | Y | 1.1101 | 39.4971 | 4242.1228
[7 empty] | 14212 | 16595 | 1215216 | 2015-03-01 18:24 | 2015-03-01 20:45 | 141.4 | 11kV | 2913.75 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 150961 Wire reported hanging just off ground No Protection Operation. Opened for Safety | March | 2015 | 2015Q3 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2015-03-01 | N | 72.8438 | N | 32 | Y | Y | 1.1101 | 39.4971 | 2129.2826
[7 empty] | 13990 | 14851 | 1216274 | 2015-03-01 18:47 | 2015-03-01 20:48 | 121 | 11kV | 55055 | 455 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 150960 3 fault operations C phase Earth fault Blown UGOH pole IT-80370 Excluded oms 1215265 | March | 2015 | 2015Q3 | 2015 | 213:33777 | 213:33777 | ZN00213/033777 | NEWCASTLE | Unknown | Unknown | 2015-03-01 | N | 121 | N | 32 | Y | Y | 1.1101 | 39.4971 | 40232.5702
[7 empty] | 14143 | 16136 | 1214987 | 2015-03-01 15:43 | 2015-03-01 22:00 | 377 | 11kV | 19981 | 53 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150969 20 amp fuse Line DOLF WIres on ground. Also includes LID 150948 downstream LVF sub fuse pulled to isolate Private LV damaged pole. Job is part of bigger outage #150969 Excludes OMS 1214987 | March | 2015 | 2015Q3 | 2015 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2015-03-01 | N | 377 | N | 32 | Y | Y | 1.1101 | 39.4971 | 14601.5255
[7 empty] | 14606 | 19732 | 1214934 | 2015-03-01 15:29 | 2015-03-01 22:19 | 410 | 11kV | 1640 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150971 & 150947 OMS 1215378 Burnt off tapping to LF 75290 No Protection operated. Excluded OMS 1214934 Wrong sub number. This job is incorrect. | March | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-03-01 | N | 410 | N | 32 | Y | Y | 1.1101 | 39.4971 | 1198.4636
[7 empty] | 13472 | 10709 | 1215303 | 2015-03-01 19:24 | 2015-03-01 22:55 | 211 | 11kV | 211 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID150972 10 amp fuse Substation DOLF Replace DOLF. M.Cartwright Excludes OMS 1215303 | March | 2015 | 2015Q3 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2015-03-01 | N | 211 | N | 32 | Y | Y | 1.1101 | 39.4971 | 154.1926
[7 empty] | 12794 | 4958 | 1215271 | 2015-03-01 18:56 | 2015-03-01 23:00 | 243.95 | 11kV | 93676.8 | 384 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 150962 1 fault operation Overcurrent Not a complete outage. Part supply. Tapping Blown on 11kV. P Holland patrolling. At Sw 42049 A= 28A B= 0A C= 28A | March | 2015 | 2015Q3 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2015-03-01 | N | 243.95 | N | 32 | Y | Y | 1.1101 | 39.4971 | 68456.2424
[7 empty] | 13638 | 12028 | 1215387 | 2015-03-01 21:29 | 2015-03-01 23:00 | 91 | 11kV | 364 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 150970 10 amp fuse Substation DOLF Blown Arrestors Excludes OMS 1215387 | March | 2015 | 2015Q3 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2015-03-01 | N | 91 | N | 32 | Y | Y | 1.1101 | 39.4971 | 266.0005
[7 empty] | 13302 | 9169 | 1215413 | 2015-03-01 22:46 | 2015-03-01 23:30 | 44 | 11kV | 3051 | 170 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Wind Storm | N | Section of ZN.15002 Narrabeen feeder from IR.48460 to extent of feeder (2 DC's):- tripped and reclosed Cause:- @ PT.15139 a possum came into contact with it, no vissible damage - Footpath 31.5A HDO replaced ME:-1215612 RS:-1215617 Withdrawn:-1215413 | March | 2015 | 2015Q3 | 2015 | ZN15002:PA4 | ZN15002:PA4 | ZN15002/000004 | NORTHERN BEACHES | OH | Not Veg | 2015-03-01 | N | 17.9471 | N | 32 | Y | Y | 1.1101 | 39.4971 | 2229.5808
[7 empty] | 14349 | 17544 | 1216299 | 2015-03-01 22:50 | 2015-03-01 23:45 | 55 | 11kV | 1705 | 31 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | LID 150973 Emerg SI P0123. No protection operations. Section isolated to remove tree from mains & restring Lv conductor pole VP-57006. | March | 2015 | 2015Q3 | 2015 | 243:80080 | 243:80080 | ZN00243/080080 | LAKE MACQUARIE | OH | Veg | 2015-03-01 | N | 55 | N | 32 | Y | Y | 1.1101 | 39.4971 | 1245.9637
[7 empty] | 12446 | 1778 | 1215286 | 2015-03-01 19:12 | 2015-03-01 23:55 | 282.7 | 11kV | 7067.5 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150975 10 amp fuse Line DOLF | March | 2015 | 2015Q3 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-03-01 | N | 282.7 | N | 32 | Y | Y | 1.1101 | 39.4971 | 5164.7205
[7 empty] | 13837 | 13512 | 1215229 | 2015-03-01 18:29 | 2015-03-02 00:10 | 341.0167 | 11kV | 5115.25 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 150977 16 amp fuse Line DOLF | March | 2015 | 2015Q3 | 2015 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2015-03-01 | N | 341.0167 | N | 32 | Y | Y | 1.1101 | 39.4971 | 3738.0738
[7 empty] | 12975 | 6603 | 1217733 | 2015-03-02 00:15 | 2015-03-02 00:50 | 35 | 11kV | 560 | 16 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | LID 150978 No protection operations. Section isolated to remove branch from mains pole GW-17015 Excluded OMS 1215422. | March | 2015 | 2015Q3 | 2015 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2015-03-02 | N | 35 | N | 11 | N | N | 1.1101 | 39.4971 | 409.2315
[7 empty] | 14299 | 17217 | 1216566 | 2015-03-01 18:23 | 2015-03-02 03:38 | 555 | 11kV | 55150 | 142 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 150958 2 fault operations Reports or wires down Lot 133 Wollombi Rd. | March | 2015 | 2015Q3 | 2015 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2015-03-01 | N | 388.3803 | N | 32 | Y | Y | 1.1101 | 39.4971 | 40301.9934
[7 empty] | 12265 | 75 | 1215357 | 2015-03-01 20:16 | 2015-03-02 04:10 | 473.55 | 11kV | 3788.4 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | LID 150984 20 amp fuse Line DOLF Patrol and Replace blown fuses M.Cartwright, G.Luxon | March | 2015 | 2015Q3 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2015-03-01 | N | 473.55 | N | 32 | Y | Y | 1.1101 | 39.4971 | 2768.451
[7 empty] | 12898 | 5946 | 1215765 | 2015-03-02 03:10 | 2015-03-02 05:05 | 115 | 11kV | 2070 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa13 "Brush rd" fdr Beyond LB40982 to normally open LB41264 interrupted by DOp for safety. Large tree on Overhead Mains. | March | 2015 | 2015Q3 | 2015 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2015-03-02 | N | 115 | N | 11 | N | N | 1.1101 | 39.4971 | 1512.6949
[7 empty] | 14536 | 18990 | 1215368 | 2015-03-01 18:21 | 2015-03-02 05:20 | 659.3667 | 11kV | 18462.2667 | 28 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | LID 150985 20 amp fuse Line DOLF Patrolled feeder and replace fuses M.Cartwright, G.Luxon | March | 2015 | 2015Q3 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2015-03-01 | N | 659.3667 | N | 32 | Y | Y | 1.1101 | 39.4971 | 13491.6799
[7 empty] | 12897 | 5933 | 1215369 | 2015-03-01 18:21 | 2015-03-02 05:40 | 679.3667 | 11kV | 4076.2 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 150986 Line DOLF | March | 2015 | 2015Q3 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2015-03-01 | N | 679.3667 | N | 32 | Y | Y | 1.1101 | 39.4971 | 2978.7667
[7 empty] | 13845 | 13633 | 1215290 | 2015-03-01 19:04 | 2015-03-02 06:58 | 714 | 11kV | 574807 | 1853 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Electrical Storm | N | LID 150983 linesman believe car possibly hit pole or-90076 Excluded oms 1215421 1215392 | March | 2015 | 2015Q3 | 2015 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2015-03-01 | N | 310.2035 | N | 32 | Y | Y | 1.1101 | 39.4971 | 420052.0017
[7 empty] | 13782 | 13176 | 1216217 | 2015-03-02 09:30 | 2015-03-02 09:40 | 10 | 11kV | 1350 | 135 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Zn14144 Wamberal Pa7 fdr tripped on: Relays: EF, EFI Signals: Tx2 Group Earth Abnormal: S11697 Sw/B closed Sw/A open, LB40803 closed, S11934 Sw/A open, fdr from s11697:A to S11934:A to AB41389 tee PT12915, PT11286, PT13549 remains off for scheduled interruption. While isolating fdr from S11697:A to S11934:A to AB41389 tee PT12915, PT11286, PT13549. The AB41389 failed failed to open on all 3 phases causing suspected ferroresonance. | March | 2015 | 2015Q3 | 2015 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Not Veg | 2015-03-02 | N | 10 | N | 11 | N | N | 1.1101 | 39.4971 | 986.5402
[7 empty] | 14660 | 20220 | 1215485 | 2015-03-02 07:46 | 2015-03-02 10:33 | 167 | 11kV | 1336 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150991 16 amp fuse Line DOLF Excludes OMS 1215485 | March | 2015 | 2015Q3 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2015-03-02 | N | 167 | N | 11 | N | N | 1.1101 | 39.4971 | 976.3094
[7 empty] | 14029 | 15272 | 1215421 | 2015-03-01 19:04 | 2015-03-02 10:45 | 941 | 11kV | 1882 | 2 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 150993 Sub earthing found stolen when isolated for emerg repairs refer to job 1219783 vehicle hit pole Operator reported no customers off sub. DO attended after subsequent calls & closed LV link 45041 to restore supply to customers. Excluded OMS 1215421. also see report # 150983. | March | 2015 | 2015Q3 | 2015 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2015-03-01 | N | 941 | N | 32 | Y | Y | 1.1101 | 39.4971 | 1375.3101
[7 empty] | 12913 | 6079 | 1215506 | 2015-03-02 08:15 | 2015-03-02 11:00 | 164.6667 | 11kV | 823.3333 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150995 5 amp fuse Line DOLF | March | 2015 | 2015Q3 | 2015 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2015-03-02 | N | 164.6667 | N | 11 | N | N | 1.1101 | 39.4971 | 601.6677
[7 empty] | 13953 | 14592 | 1215474 | 2015-03-02 07:30 | 2015-03-02 11:25 | 235 | 11kV | 705 | 3 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 150997 10 amp fuse Substation Dolf Excludes OMS No. 1215474 + 1215477 Dead magpie found at sub. | March | 2015 | 2015Q3 | 2015 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2015-03-02 | N | 235 | N | 11 | N | N | 1.1101 | 39.4971 | 515.1932
[7 empty] | 14651 | 20138 | 1215510 | 2015-03-02 | 2015-03-02 11:50 | 710 | 11kV | 2130 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150996 10 amp fuse Substation DOLF Excludes OMS 1215510 + 1215420 | March | 2015 | 2015Q3 | 2015 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2015-03-02 | N | 710 | N | 11 | N | N | 1.1101 | 39.4971 | 1556.5412
[7 empty] | 12742 | 4577 | 1215643 | 2015-03-02 10:12 | 2015-03-02 13:15 | 183 | 11kV | 183 | 1 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | Installed new crossarm & 11KV pins Reinstated 11KV mains onto new crossarm Excludes OMS 1215643 | March | 2015 | 2015Q3 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2015-03-02 | N | 183 | N | 11 | N | N | 1.1101 | 39.4971 | 133.731
[7 empty] | 12814 | 5135 | 1215437 | 2015-03-02 06:34 | 2015-03-02 13:45 | 431 | 11kV | 6806 | 16 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | Ex Zn12600 Lisarow section of Pa2 "Holgate" 11kv fdr from LK41345 to PT11410 to PT11409 was interrupted for repairs to PT11410 after storm Repairs complete. See 1216207,8 exclude 1215437 | March | 2015 | 2015Q3 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | UG | Not Veg | 2015-03-02 | N | 425.375 | N | 11 | N | N | 1.1101 | 39.4971 | 4973.6241
[7 empty] | 14628 | 19974 | 1216347 | 2015-03-01 18:20 | 2015-03-02 14:00 | 1180 | 11kV | 57341 | 112 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150980 Earth fault | March | 2015 | 2015Q3 | 2015 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2015-03-01 | N | 511.9732 | N | 32 | Y | Y | 1.1101 | 39.4971 | 41903.1115
[7 empty] | 12280 | 225 | 1215237 | 2015-03-01 18:32 | 2015-03-02 14:03 | 1171 | 11kV | 23420 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150979 Excluded OMS 1215237 | March | 2015 | 2015Q3 | 2015 | 233:82812 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2015-03-01 | N | 1171 | N | 32 | Y | Y | 1.1101 | 39.4971 | 17114.6452
[7 empty] | 14661 | 20225 | 1215091 | 2015-03-01 17:15 | 2015-03-02 14:10 | 1255 | 11kV | 199618 | 166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn14143 Somersby section of Pa17 "Somersby Falls" Relays: EFI Singals: Tx2 Group Earth EFI's: Nil RE45012 VBar Point tripped and locked out Relays: Lockout, Overcurrent Trip Cause: Weather related Remarks: Mains repaired. Repairs Complete. Tree removed Lineworker Supervisoer Tony Fiore advises not to patrol in dark (water crossing) will attend first thing in the morning. See 1216145,6 Exclude 1215091 | March | 2015 | 2015Q3 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2015-03-01 | N | 1202.5181 | N | 32 | Y | Y | 1.1101 | 39.4971 | 145874.9467
[7 empty] | 12620 | 3392 | 1215820 | 2015-03-02 13:39 | 2015-03-02 14:58 | 79 | 11kV | 79 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150999 10 amp fuse Substation DOLF EXcludes OMS 1215820 | March | 2015 | 2015Q3 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-03-02 | N | 79 | N | 11 | N | N | 1.1101 | 39.4971 | 57.7309
[7 empty] | 14515 | 18818 | 1219151 | 2015-03-01 17:18 | 2015-03-02 15:30 | 1332 | 11kV | 114303 | 316 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150964 2 fault operations conductor | March | 2015 | 2015Q3 | 2015 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2015-03-01 | N | 361.7184 | N | 32 | Y | Y | 1.1101 | 39.4971 | 83529.261
[7 empty] | 13789 | 13196 | 1216263 | 2015-03-01 17:56 | 2015-03-02 17:40 | 1424 | 11kV | 23208 | 117 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 150967 2 fault operations C phase Overcurrent OHM down from GV-90180 to GV-90184 Excluded oms1215165/329. | March | 2015 | 2015Q3 | 2015 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Not Veg | 2015-03-01 | N | 198.359 | N | 32 | Y | Y | 1.1101 | 39.4971 | 16959.7219
[7 empty] | 13621 | 11889 | 1215958 | 2015-03-02 17:24 | 2015-03-02 20:00 | 156 | 11kV | 156 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | No LID report | March | 2015 | 2015Q3 | 2015 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2015-03-02 | N | 156 | N | 11 | N | N | 1.1101 | 39.4971 | 114.0002
[7 empty] | 13197 | 8437 | 1216191 | 2015-03-03 11:38 | 2015-03-03 14:00 | 142 | 11kV | 142 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 151013 Broken lead to LL clamp. Excluded OMS 1216191 | March | 2015 | 2015Q3 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-03-03 | N | 142 | N | 4 | N | N | 1.1101 | 39.4971 | 103.7694
[7 empty] | 13442 | 10511 | 1216404 | 2015-03-03 16:47 | 2015-03-03 19:10 | 143 | 11kV | 286 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151017 A & B Phase DOLF : 16 Amp A & B phase sub dolfs at sub 52592 were also replaced Excluded oms 1216404 | March | 2015 | 2015Q3 | 2015 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2015-03-03 | N | 143 | N | 4 | N | N | 1.1101 | 39.4971 | 209.0004
[7 empty] | 14024 | 15191 | 1216437 | 2015-03-03 21:31 | 2015-03-03 23:35 | 124 | 11kV | 144624 | 1326 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S1193 LindfieldPanel 12 Tripped Reclosed Tripped and Locked out on B phase Timed Overcurrent Cause Not ascertained for outage See OMS 1217655 1217662 1217660 1216441 1216437 1216447 | March | 2015 | 2015Q3 | 2015 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Veg | 2015-03-03 | N | 109.0679 | N | 4 | N | N | 1.1101 | 39.4971 | 105686.9535
[7 empty] | 14123 | 16016 | 1216428 | 2015-03-03 21:10 | 2015-03-03 23:50 | 160 | 11kV | 2560 | 16 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 151018 Section isolated to replace defective pole JR-54425 reported by Maitland ERC | March | 2015 | 2015Q3 | 2015 | 264:81240 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Not Veg | 2015-03-03 | N | 160 | N | 4 | N | N | 1.1101 | 39.4971 | 1870.7725
[7 empty] | 14339 | 17456 | 1216522 | 2015-03-04 08:38 | 2015-03-04 10:09 | 91 | 11kV | 148148 | 1628 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15011 Beacon Hill Pa2 "Allambie rd 252" fdr has tripped Signals: 11kv trip Relays: A&C phase overcurrent, timer and Lockout EFI's:Nil Abnormal: Defective between S16691:B to S15180:5934. S46675:B closed Mains found twisted together Oh cables adjacent LB64953 See 1217029 exclude 1216522,6,9,31,5,41 | March | 2015 | 2015Q3 | 2015 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Not Veg | 2015-03-04 | N | 91 | N | 6 | N | N | 1.1101 | 39.4971 | 108262.1888
[7 empty] | 12587 | 3137 | 1216547 | 2015-03-04 09:24 | 2015-03-04 11:08 | 104 | 11kV | 10920 | 105 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S3472 Section of Panel 11 "Marjorie st Feeder" beyond AB 2104 (Burnt Bond) Remarks: bond off AB2104 | March | 2015 | 2015Q3 | 2015 | ZN3472:PA11 | ZN3472:PA11 | ZN03472/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-03-04 | N | 104 | N | 6 | N | N | 1.1101 | 39.4971 | 7980.0139
[7 empty] | 12932 | 6242 | 1216653 | 2015-03-04 12:00 | 2015-03-04 13:53 | 113 | 11kV | 157775 | 1559 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn.7481 Darling Harbour - Pnl.0 tripped on: Panel 9 E/F trip, 9L O/C & E/F trip Signals: 11kV Trip, Tx No.11 Group Earth Field EFIs: S4199, S8111, S8013, S8014 UG Cable fault between S.8014 Refinery Bowman No.2 and S.8460 Refinery Bowman No.1 see 1216965 1216968 1216966 GSI: 1216671 | March | 2015 | 2015Q3 | 2015 | ZN7481:PA9 | ZN7481:PA9 | ZN07481/000009 | SYDNEY | UG | Not Veg | 2015-03-04 | N | 101.2027 | N | 6 | N | N | 1.1101 | 39.4971 | 115297.3164
[7 empty] | 14545 | 19030 | 1216785 | 2015-03-04 15:09 | 2015-03-04 17:15 | 126 | 11kV | 13860 | 110 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn180 Mosman section of Pa24 "Brady Ourimbah No.2" S1620 Courallie Road 60Amp OQFRN HV fuse operated Appears that truck hit Telco cable and OH as per callers comment on OMS 1216765. Restored via LV// then HV fuse replaced & LV// removed. See 1217050 GIS 1216861 exclude 1216767,85 | March | 2015 | 2015Q3 | 2015 | ZN180:PA24 | ZN180:PA24 | ZN00180/000024 | WILLOUGHBY | OH | Not Veg | 2015-03-04 | N | 126 | N | 6 | N | N | 1.1101 | 39.4971 | 10128.4792
[7 empty] | 12595 | 3196 | 1217715 | 2015-03-04 14:51 | 2015-03-04 17:21 | 150 | 11kV | 124500 | 830 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 151032 fdr 19071 tripped on SEF. sub 72778 treatment works fuses found down after second trip - refer to OMS 1217716 sub isolated and fdr restored | March | 2015 | 2015Q3 | 2015 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2015-03-04 | N | 150 | N | 6 | N | N | 1.1101 | 39.4971 | 90980.9279
[7 empty] | 13511 | 11035 | 1217532 | 2015-03-04 08:05 | 2015-03-04 18:10 | 605 | 11kV | 11766 | 110 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 150024 1 fault operation Earth fault Wire down at pole AH-42128 Nandowra Rd subs 71259, 71548 and 71549 isolated for repairs restored at 1810hrs Excluded OMS 1216499 | March | 2015 | 2015Q3 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2015-03-04 | N | 106.9636 | N | 6 | N | N | 1.1101 | 39.4971 | 8598.2458
[7 empty] | 12402 | 1444 | 1216917 | 2015-03-05 03:49 | 2015-03-05 04:45 | 56 | 11kV | 112 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151035 B phase DOLF : 10 Amp Excluded OMS 1216917 | March | 2015 | 2015Q3 | 2015 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2015-03-05 | N | 56 | N | 6 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 13526 | 11103 | 1217031 | 2015-03-05 09:34 | 2015-03-05 12:05 | 151 | 11kV | 453 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151042 A phase DOLF : 10 Amp | March | 2015 | 2015Q3 | 2015 | 814:82285 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Veg | 2015-03-05 | N | 151 | N | 6 | N | N | 1.1101 | 39.4971 | 331.039
[7 empty] | 12821 | 5245 | 1217018 | 2015-03-05 09:02 | 2015-03-05 12:25 | 203 | 11kV | 203 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151043 C phase DOLF : 10 Amp Excluded OMS 1217018 | March | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-03-05 | N | 203 | N | 6 | N | N | 1.1101 | 39.4971 | 148.3464
[7 empty] | 13718 | 12653 | 1217153 | 2015-03-05 12:08 | 2015-03-05 17:27 | 319 | 11kV | 155466 | 1809 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Pa19 fdr tripped reclosed & locked out Relays: B & C phase timed overcurrent, reclose, timing & lockout relays Signals: 11kv trip EFI's: Nil Cause: Pole Fire REamrks: Cause by borken crossarm, one psan from AB42782 PT12647 & PT13590 interrupted to carry out repairs due to low network volts PT12656 placed in LV// to extend isolation for access permit See 1217591,2,3 Exclude 1217153,64,84,272,7 | March | 2015 | 2015Q3 | 2015 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | OH | Not Veg | 2015-03-05 | N | 85.9403 | N | 6 | N | N | 1.1101 | 39.4971 | 113609.9673
[7 empty] | 14084 | 15686 | 1217237 | 2015-03-05 13:48 | 2015-03-05 17:30 | 222 | 11kV | 84735 | 1050 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.21 tripped on IOC Signals: 11kV trip with EFI Field EFIs: S10364 Tree branch brought down OH in Woodlands Ave - DOp and lineworker made safe and restored supply see 1217494 1217495 1217497 | March | 2015 | 2015Q3 | 2015 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Veg | 2015-03-05 | N | 80.7 | N | 6 | N | N | 1.1101 | 39.4971 | 61921.8387
[7 empty] | 14592 | 19528 | 1217280 | 2015-03-05 15:01 | 2015-03-06 01:02 | 601 | 11kV | 85249 | 1278 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12580 Erina Pa16 fdr tripped/closed/tripped & locked out on: Relays: 16R - Timing, Lockout, SEL, IOC, EFI, OC&EF Signals: 11kv trip EFI's: S14330 S18039 Tree/Branch brought down OH. Repair work required on section of 11kv fdr from S18039/SwB to LB61009 tee to PT14208. HV & LV mains to be replaced. Customer report fire. Fire Brigade report fire spreading towards properties. See 1219126,7,8,9 GIS 1217346 Exclude 1217280,90,318,9 | March | 2015 | 2015Q3 | 2015 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2015-03-05 | N | 66.705 | N | 6 | N | N | 1.1101 | 39.4971 | 62297.4548
[7 empty] | 12737 | 4537 | 1217598 | 2015-03-06 10:36 | 2015-03-06 12:00 | 84 | 11kV | 168 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | No Weather Impact | N | Repaired 11Kv Dropper cable lug. Excludes OMS 1217598 | March | 2015 | 2015Q3 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2015-03-06 | N | 84 | N | 3 | N | N | 1.1101 | 39.4971 | 122.7694
[7 empty] | 12980 | 6651 | 1217778 | 2015-03-06 15:18 | 2015-03-06 23:40 | 502 | 11kV | 2664 | 47 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 151071 3 fault operations A & B phase Earth fault E/FAULT AT SW 3098 BEN EAN RAGCB. FAULTY UGOH AT POLE ES-62997. GENERATOR INSTALLED SUB 29290. Excluded OMS 1217780 & 1217799 | March | 2015 | 2015Q3 | 2015 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | Unknown | Unknown | 2015-03-06 | N | 56.6809 | N | 3 | N | N | 1.1101 | 39.4971 | 1946.7726
[7 empty] | 14234 | 16797 | 1217856 | 2015-03-06 21:12 | 2015-03-07 00:06 | 174 | 11kV | 173874 | 1732 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn4545 Meadowbank 11kV Panel 29 tripped on A, B and C phase Timed Overcurrent and Earth Fault, Fault Check, EFI, Tx2 Fault Check and UV Signals: Group Earth Zone Earth and 11kV Trip Cause: UGOH Fault - 11kV feeder from SW/B to S36078 Lincoln Vimera Tee PT1501 to LB1477 See OMS 1218899 1218902 1218903 1218904 1219122 1219116 1219117 1217856/69/59/66/63/58/64/61/60 | March | 2015 | 2015Q3 | 2015 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | Unknown | Unknown | 2015-03-06 | N | 100.3891 | N | 3 | N | N | 1.1101 | 39.4971 | 127061.9908
[7 empty] | 14480 | 18551 | 1218018 | 2015-03-08 05:40 | 2015-03-08 08:00 | 140 | 11kV | 103740 | 741 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN.36300 Balgowlah North 11kV Panel 17 tripped on:- Relays:- B & C phase IOC Signals:-11kV trip with EFI Field EFI's:- S.46665 Cause:- UG cable fault between S.46665 SW/B and S.48110 SW/A, also found bond burnt between S.15107 and PT.15524 Link St ME:-1218155 RS:-1218156 Withdrawn:-1218018, 1218026, 1218028, 1218030, 1218031, 1218032, 1218034, 1218036 | March | 2015 | 2015Q3 | 2015 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | UG | Not Veg | 2015-03-08 | N | 140 | N | 2 | N | N | 1.1101 | 39.4971 | 75810.1322
[7 empty] | 12733 | 4508 | 1218128 | 2015-03-08 20:14 | 2015-03-08 22:30 | 136 | 11kV | 1088 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151088 A phase DOLF : 10 Amp No cause found. Readings as left 3A, 31A, 13A @ 240v Excluded OMS 1218128. | March | 2015 | 2015Q3 | 2015 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2015-03-08 | N | 136 | N | 2 | N | N | 1.1101 | 39.4971 | 795.0783
[7 empty] | 13796 | 13255 | 1218319 | 2015-03-09 11:36 | 2015-03-09 12:52 | 76 | 11kV | 9728 | 128 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Section of Panel 32 ex Top Ryde Zone Fluctuating Supply Beyond AB239 _ No Protection Operated Cuase Footpath Phase Burnt off at CP239 See OMS 1221938 1218319 1218349 1218322 | March | 2015 | 2015Q3 | 2015 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Not Veg | 2015-03-09 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 7108.9355
[7 empty] | 13368 | 9851 | 1218416 | 2015-03-09 14:09 | 2015-03-09 15:45 | 96 | 11kV | 672 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151100 B Phase DOLF : 10 Amp Excluded OMS 1218416 | March | 2015 | 2015Q3 | 2015 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2015-03-09 | N | 96 | N | 3 | N | N | 1.1101 | 39.4971 | 491.0778
[7 empty] | 12715 | 4288 | 1218580 | 2015-03-09 22:50 | 2015-03-09 23:38 | 48 | 11kV | 13488 | 281 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa2 "holgate" @RE41020 Wattle Tree rd Nth tripped and relcosed on overload. Due to Tree/branch on OH Mains @RE41845 11kv Link bond burnt off. See 1219075 exclude 1218580,1,3,4 | March | 2015 | 2015Q3 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2015-03-09 | N | 48 | N | 3 | N | N | 1.1101 | 39.4971 | 9856.6326
[7 empty] | 13592 | 11634 | 1218844 | 2015-03-10 14:07 | 2015-03-10 15:21 | 74 | 11kV | 173194 | 2627 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At Zn80 Chatswood Panel 80 Tripped on Relays: Earth Fault, EFI and Fault Check Signals: 11kV Trip Cause: Borer Hit UG cable O/S 19 Rosenthal Ave. (Section of 11kV between S50303 to S277 to S5184) GERARD MOON 19 ROSENTHAL AVE LANE COVE "gerard thinks he has hit u.ground cables with a borer machine" - see OMS 1218849 See OMS 1221601 1221602 1218849 1218844 1218852 | March | 2015 | 2015Q3 | 2015 | ZN80:PA40 | ZN80:PA40 | ZN00080/000040 | LANE COVE | UG | Not Veg | 2015-03-10 | N | 65.9284 | N | 4 | N | N | 1.1101 | 39.4971 | 126565.0668
[7 empty] | 13169 | 8116 | 1218871 | 2015-03-10 14:56 | 2015-03-10 21:17 | 381 | 11kV | 8847 | 317 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge Pa4 "Kulnura" opened by AOp DOp reported car hit pole CM345. Car details BMW Rego VAE13K. See 1219189,91 Exclude 1218871 | March | 2015 | 2015Q3 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2015-03-10 | N | 27.9085 | N | 4 | N | N | 1.1101 | 39.4971 | 6465.1267
[7 empty] | 13651 | 12144 | 1218965 | 2015-03-10 20:10 | 2015-03-10 22:11 | 121 | 11kV | 186237 | 2157 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ZN.15008 Harbord 11kV Panel 9 feeder tripped & reclosed on:- Relays:- Lock-out & Timing, O/C B+C phase Tx.2 Panel:- O/C + EF relay, O/C pick-up B+C phase Signals:- Tx.2 Cooling supply fail, 11kV trip Cause:- Open Bond above LBS.62773 ME:-1219024 RS:-1219026, [1218982 (Known Outage in Area)] Withdrawn:-[1218967 (Duplication)], [1218966, 1218965, 1218985 (Reporting Hazard)] | March | 2015 | 2015Q3 | 2015 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Not Veg | 2015-03-10 | N | 86.3408 | N | 4 | N | N | 1.1101 | 39.4971 | 136096.5065
[7 empty] | 14308 | 17289 | 1218994 | 2015-03-10 20:49 | 2015-03-10 22:55 | 126 | 11kV | 52089 | 485 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 Matraville Pnl.11 tripped on: B phase timed + Inst O/C, EFI Signals: 11kV trip, Tx4 GE, ZE, Thermal Signal Field EFIs: S8708 - Faulty EFIs @ S61524 & S4556 - EFI needs to be installed at CP1113 (Sw B) UG Cable fault between S61524 (Sw B) and S2870 (Sw A) See also interruption to Pnl.14 due to defective EFIs not operating. See 1219087 1219088 1219084 | March | 2015 | 2015Q3 | 2015 | ZN1788:PA11 | ZN35700:PA10 | ZN35700/000010 | RANDWICK | UG | Not Veg | 2015-03-10 | N | 107.4 | N | 4 | N | N | 1.1101 | 39.4971 | 38065.1048
[7 empty] | 13040 | 7074 | 1219311 | 2015-03-11 17:00 | 2015-03-11 19:15 | 135 | 11kV | 270 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 151133 C phase DOLF : 10 Amp Excluded OMS 1219311 | March | 2015 | 2015Q3 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-03-11 | N | 135 | N | 5 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 14199 | 16485 | 1219374 | 2015-03-11 19:30 | 2015-03-11 21:11 | 101 | 11kV | 49282 | 488 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | At Zn847 Hornsby Panel 45 Tripped on A and B phase Overcurrent Signals: 11kV Trip Group Earth Cause: Lightning Storm See OMS 1221582 1221583 1219374 1219406 | March | 2015 | 2015Q3 | 2015 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2015-03-11 | N | 100.9877 | N | 5 | N | N | 1.1101 | 39.4971 | 36013.832
[7 empty] | 12709 | 4215 | 1219407 | 2015-03-11 20:08 | 2015-03-11 22:10 | 121.95 | 11kV | 12438.9 | 102 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | At PT734 Rotherwood Ave Roadside HVDO fuse operated Cause: Weather Related - Lightning See OMS 1219407 1219438/440/442 | March | 2015 | 2015Q3 | 2015 | ZN847:PA46 | ZN847:PA46 | ZN00847/000046 | HORNSBY | OH | Veg | 2015-03-11 | N | 121.95 | N | 5 | N | N | 1.1101 | 39.4971 | 9089.9812
[7 empty] | 12724 | 4416 | 1219359 | 2015-03-11 19:02 | 2015-03-12 01:40 | 398 | 11kV | 9552 | 24 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 151140 A & B phase DOLF : 20 Amp branch on Fdr at BQ-90145 Excluded OMS 1219359 | March | 2015 | 2015Q3 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2015-03-11 | N | 398 | N | 5 | N | N | 1.1101 | 39.4971 | 6980.3199
[7 empty] | 13669 | 12264 | 1219494 | 2015-03-12 01:33 | 2015-03-12 04:38 | 185 | 11kV | 173922 | 1220 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Previous Storm | N | @ZN9900 Menai 11kv Panel #1 labelled "S.9002, S9930 + S9044" tripped & reclosed & locked out: Relays: OC + EF Relay - trip, EF, EFI Timed + lockout Signals: 11kv trip, Zone Earth, Group Earth Field EFI's S9002 (No access), S9443, S9429, S9949, S9428 1st Attempt Relays: O/C + EF Relay - Trip, EF, EFI Signals: Group Earth, Zone Earth, Field EFI's S9002 (No access), S9443, S9429 Remarks: 11kv underground feeder fault from Sw/B @ S9429 Lawson Old Illawarra to Sw/A @ S9949 Australia New Illawarra | March | 2015 | 2015Q3 | 2015 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | UG | Not Veg | 2015-03-12 | N | 142.559 | N | 16 | N | N | 1.1101 | 39.4971 | 127097.0678
[7 empty] | 13701 | 12549 | 1219377 | 2015-03-11 19:31 | 2015-03-12 08:30 | 779 | 11kV | 15648 | 67 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 151132 Broken crossarm found at CS30053 possible high into low 3 fault operations Earth fault | March | 2015 | 2015Q3 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2015-03-11 | N | 233.5522 | N | 5 | N | N | 1.1101 | 39.4971 | 11435.0969
[7 empty] | 14577 | 19303 | 1219528 | 2015-03-12 07:53 | 2015-03-12 12:15 | 262 | 11kV | 786 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 151146 A phase DOLF : 16 Amp Excluded OMS 1219528 | March | 2015 | 2015Q3 | 2015 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Not Veg | 2015-03-12 | N | 262 | N | 16 | N | N | 1.1101 | 39.4971 | 574.3856
[7 empty] | 13540 | 11180 | 1219501 | 2015-03-12 06:28 | 2015-03-12 12:20 | 352 | 11kV | 704 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 151150 Single phase DOLF : 10 Amp replicated job see OMS 1219501 | March | 2015 | 2015Q3 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2015-03-12 | N | 352 | N | 16 | N | N | 1.1101 | 39.4971 | 514.4624
[7 empty] | 14363 | 17618 | 1219600 | 2015-03-12 10:40 | 2015-03-12 12:25 | 105 | 11kV | 1785 | 17 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Lightning | N | At PT2022 Arcadia Wylds 11kV HDO footpath and roadside Phase fuse blown Abnormal Switching: AB130 Open, LB62109 Closed AB451 Open, AB2063 Closed. Cause: TX Defective, Winding Test Required. Note: PT tried back and Tripped upstream recloser (Suspect Grading Issue) See OMS 1222205 1222202 1219600 Excludes OMS 1222205 | March | 2015 | 2015Q3 | 2015 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2015-03-12 | N | 105 | N | 16 | N | N | 1.1101 | 39.4971 | 1304.4254
[7 empty] | 13965 | 14674 | 1219620 | 2015-03-12 10:24 | 2015-03-12 14:52 | 268 | 11kV | 268 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | replaced hv fuse Incorporates LID 151158 Excludes OMS 1220183 | March | 2015 | 2015Q3 | 2015 | 801:74117 | 801:74117 | ZN00801/074117 | MUSWELLBROOK | OH | Veg | 2015-03-12 | N | 268 | N | 16 | N | N | 1.1101 | 39.4971 | 195.8465
[7 empty] | 14124 | 16020 | 1220223 | 2015-03-12 16:00 | 2015-03-12 16:45 | 45 | 11kV | 90 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 151167 C phase DOLF : 20 Amp Call in to Micheal Judge. Excludes OMS 1220223 | March | 2015 | 2015Q3 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-03-12 | N | 45 | N | 16 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 14089 | 15710 | 1219828 | 2015-03-12 15:23 | 2015-03-12 18:21 | 178 | 11kV | 20029 | 142 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 151176 and LID 151172 Earth fault Excluded OMS 1219828 & 1219834 | March | 2015 | 2015Q3 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-03-12 | N | 141.0493 | N | 16 | N | N | 1.1101 | 39.4971 | 14636.6024
[7 empty] | 13381 | 9976 | 1219918 | 2015-03-12 18:00 | 2015-03-12 19:45 | 105 | 11kV | 420 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 151179 A phase DOLF : 10 Amp Excluded OMS 1219918 | March | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2015-03-12 | N | 105 | N | 16 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 12738 | 4538 | 1219920 | 2015-03-12 18:44 | 2015-03-12 19:50 | 66 | 11kV | 66 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 121182 A phase DOLF : 10 Amp Excluded OMS 1219920 | March | 2015 | 2015Q3 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2015-03-12 | N | 66 | N | 16 | N | N | 1.1101 | 39.4971 | 48.2309
[7 empty] | 14095 | 15754 | 1219910 | 2015-03-12 16:00 | 2015-03-12 22:00 | 360 | 11kV | 360 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 151188 A phase DOLF : 10 Amp Excluded OMS 1219910 | March | 2015 | 2015Q3 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2015-03-12 | N | 360 | N | 16 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 13551 | 11316 | 1219947 | 2015-03-12 19:49 | 2015-03-12 22:25 | 156 | 11kV | 780 | 5 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Lightning | N | LID 151194 C Phase 10A Substation DOLF Operated during storm | March | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2015-03-12 | N | 156 | N | 16 | N | N | 1.1101 | 39.4971 | 570.001
[7 empty] | 14172 | 16275 | 1219915 | 2015-03-12 20:36 | 2015-03-12 22:44 | 128 | 11kV | 6628 | 53 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 151189 A phase burnt off tapping near sub 50510 Excluded OMS 1219915 | March | 2015 | 2015Q3 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2015-03-12 | N | 125.0566 | N | 16 | N | N | 1.1101 | 39.4971 | 4843.5469
[7 empty] | 13078 | 7460 | 1219868 | 2015-03-12 16:00 | 2015-03-12 23:35 | 455 | 11kV | 1365 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 151191 A phase DOLF : 5 Amp LF 15226 was also blown Excluded OMS 1219868 + 1220113 | March | 2015 | 2015Q3 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-03-12 | N | 455 | N | 16 | N | N | 1.1101 | 39.4971 | 997.5017
[7 empty] | 13093 | 7608 | 1219851 | 2015-03-12 16:11 | 2015-03-13 00:01 | 470 | 11kV | 940 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 151192 10A A Phase DOLF operated during electrical storm | March | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-03-12 | N | 470 | N | 16 | N | N | 1.1101 | 39.4971 | 686.9243
[7 empty] | 12857 | 5607 | 1219844 | 2015-03-12 15:54 | 2015-03-13 01:00 | 546 | 11kV | 131549.7 | 683 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 151183 A & C phase Overcurrent; Earth fault | March | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | UPPER HUNTER | OH | Not Veg | 2015-03-12 | N | 192.6057 | N | 16 | N | N | 1.1101 | 39.4971 | 96132.6407
[7 empty] | 14002 | 14948 | 1219978 | 2015-03-12 22:27 | 2015-03-13 01:35 | 188 | 11kV | 142433 | 1039 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S3154 St Ives Panel 19 tripped on Relays: Timed Earth Fault With EFI Cause: DOp patrolled nothing found - At PT1260 Narelle Avenue distributor 2 tripped on A phase of distributor 2. At PT1140 Pearson Ave 400A fuse blown on B phase of distributor 1 Cause: LV parallel failure during feeder trip. See OMS1221192 1221193 1221194 1221196 1221197 1221204 1221202 | March | 2015 | 2015Q3 | 2015 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | OH | Veg | 2015-03-12 | N | 137.0866 | N | 16 | N | N | 1.1101 | 39.4971 | 104085.8353
[7 empty] | 13786 | 13184 | 1220003 | 2015-03-13 03:48 | 2015-03-13 05:16 | 88 | 11kV | 109032 | 1239 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn12660 Woy Woy Panel 14 Tripped , Reclosed, Tripped and Lcoked out on C phase IOC and Timed O/C with Earth Fault Tree branch on OH beyond AB41623 removed by DOp. Protection did not grade, T/PE to investigate | March | 2015 | 2015Q3 | 2015 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Veg | 2015-03-13 | N | 88 | N | 15 | N | N | 1.1101 | 39.4971 | 79677.3697
[7 empty] | 12802 | 5040 | 1219999 | 2015-03-13 03:19 | 2015-03-13 08:20 | 301 | 11kV | 1505 | 5 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Blown HV Fuses A & C 16A Ecxludes OMS 1219999 + 1220898 | March | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2015-03-13 | N | 301 | N | 15 | N | N | 1.1101 | 39.4971 | 1099.8096
[7 empty] | 12567 | 2996 | 1220000 | 2015-03-13 03:38 | 2015-03-13 08:50 | 312 | 11kV | 936 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 151199 10 amp fuse Substation DOLF Excludes OMS 1220000 | March | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2015-03-13 | N | 312 | N | 15 | N | N | 1.1101 | 39.4971 | 684.0012
[7 empty] | 12266 | 79 | 1220031 | 2015-03-13 07:12 | 2015-03-13 09:05 | 113 | 11kV | 226 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 151200 10 amp fuse Substation DOLF Tx Volts: 242V TX Load: 20A Excludes OMS 1220031 | March | 2015 | 2015Q3 | 2015 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2015-03-13 | N | 113 | N | 15 | N | N | 1.1101 | 39.4971 | 165.1541
[7 empty] | 12693 | 4075 | 1220041 | 2015-03-13 07:29 | 2015-03-13 10:36 | 187 | 11kV | 187 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 151210 10 amp fuse Substation DOLF Excludes OMS 1220041 | March | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-03-13 | N | 187 | N | 15 | N | N | 1.1101 | 39.4971 | 136.6541
[7 empty] | 13528 | 11105 | 1220133 | 2015-03-13 09:40 | 2015-03-13 11:00 | 80 | 11kV | 160 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 151209 10 amp fuse Substation DOLF Excludes OMS 1220133 | March | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2015-03-13 | N | 80 | N | 15 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 13993 | 14859 | 1220173 | 2015-03-13 10:20 | 2015-03-13 11:30 | 70 | 11kV | 85993 | 1851 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 151207 2 fault operations Earth fault Nothing found Excluded OMS 1220173 | March | 2015 | 2015Q3 | 2015 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Veg | 2015-03-13 | N | 46.4576 | N | 15 | N | N | 1.1101 | 39.4971 | 62841.148
[7 empty] | 14208 | 16559 | 1220158 | 2015-03-13 10:07 | 2015-03-13 12:15 | 128 | 11kV | 128 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 151212 C Phase 20 A Fuse Operated during storms Excludes OMS 1220158 | March | 2015 | 2015Q3 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2015-03-13 | N | 128 | N | 15 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 12454 | 1808 | 1220225 | 2015-03-13 11:39 | 2015-03-13 12:16 | 37 | 11kV | 78381 | 2135 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | LID 151211 6 fault operations A & C phase Overcurrent 11kV cable failure Excluded OMS 1220225 | March | 2015 | 2015Q3 | 2015 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | UG | Not Veg | 2015-03-13 | N | 36.7124 | N | 15 | N | N | 1.1101 | 39.4971 | 57278.523
[7 empty] | 14681 | 20372 | 1220188 | 2015-03-13 10:51 | 2015-03-13 12:23 | 92 | 11kV | 184 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 151213 10 amp fuse Substation DOLF Excludes OMS 1220188 | March | 2015 | 2015Q3 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-03-13 | N | 92 | N | 15 | N | N | 1.1101 | 39.4971 | 134.4618
[7 empty] | 14677 | 20342 | 1220132 | 2015-03-13 09:39 | 2015-03-13 12:50 | 191 | 11kV | 764 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID151215 10 amp fuse Substation DOLF Excludes OMS 1220132 | March | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-03-13 | N | 191 | N | 15 | N | N | 1.1101 | 39.4971 | 558.3087
[7 empty] | 12993 | 6780 | 1222366 | 2015-03-13 12:23 | 2015-03-13 13:24 | 61 | 11kV | 4270 | 70 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge Panel 13 Recloser CP49206 Mangrove Mtn West Tripped and Reclosed on Overcurrent Cause not ascertained Mains to Patrol | March | 2015 | 2015Q3 | 2015 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2015-03-13 | N | 61 | N | 15 | N | N | 1.1101 | 39.4971 | 3120.3901
[7 empty] | 12456 | 1821 | 1220052 | 2015-03-13 07:49 | 2015-03-13 14:10 | 381 | 11kV | 4566 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn 12650 West Gosford CP: 45010 Palm Grove Tripped, Reclosed Tripped and Locked out on Relays: Overcurrent, Earth Fault Cause: Tree branch brought down HV mains 11kV feeder from LB48486 to LK43168 to LK43082 tee PT13274 See OMS 1222391 1222393 1220052 | March | 2015 | 2015Q3 | 2015 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2015-03-13 | N | 268.5882 | N | 15 | N | N | 1.1101 | 39.4971 | 3336.6981
[7 empty] | 13035 | 7053 | 1220461 | 2015-03-13 19:05 | 2015-03-13 21:19 | 134 | 11kV | 106843 | 1851 | HV | Vandalism | 3rd Party Impact | O/H Conductor Bare | Unplanned | Rain Light | N | LID 151220 3 fault operation Earth fault Targets E/F, BGN, NC!, NC3. Copper wire found & removed from 11kV main at Tomaree National Park No 3 Caps. Excluded OMS 1220461 | March | 2015 | 2015Q3 | 2015 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2015-03-13 | N | 57.7218 | N | 15 | N | N | 1.1101 | 39.4971 | 78077.7131
[7 empty] | 13024 | 6988 | 1221216 | 2015-03-13 22:01 | 2015-03-14 00:56 | 175 | 11kV | 52537 | 1851 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 151223 2 fault operation Earth fault 3rd trip today,Detailed Fdr patrol required 11454 to 61222 Was raining each time Fdr tripped Excluded OMS 1220488 | March | 2015 | 2015Q3 | 2015 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Veg | 2015-03-13 | N | 28.383 | N | 15 | N | N | 1.1101 | 39.4971 | 38392.49
[7 empty] | 12670 | 3901 | 1220500 | 2015-03-14 02:07 | 2015-03-14 05:27 | 200 | 11kV | 369232 | 1849 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 151224 3 fault operations 5th trip since 13/3/15 Excluded OMS 1220500 | March | 2015 | 2015Q3 | 2015 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Veg | 2015-03-14 | N | 199.6928 | N | 2 | N | N | 1.1101 | 39.4971 | 269823.8551
[7 empty] | 13417 | 10298 | 1220604 | 2015-03-14 19:40 | 2015-03-14 20:21 | 41 | 11kV | 4993 | 143 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2835 Burwood Panel 17 'S2931' Feeder has tripped Signals: 11kv trip, No4 Tx GE, ZE Relays: Timed EF, EFI, FC EFI: S2931 Remarks: UG fault. UG fault between Sw/B @ Sub 2931 Burwood Wilga and Sw/A @ Sub 7650 Victoria Burwood No.1 | March | 2015 | 2015Q3 | 2015 | ZN2835:PA17 | ZN2835:PA17 | ZN02835/000017 | BURWOOD | UG | Not Veg | 2015-03-14 | N | 34.9161 | N | 2 | N | N | 1.1101 | 39.4971 | 3648.7371
[7 empty] | 13280 | 8978 | 1259696 | 2015-03-15 01:10 | 2015-03-15 11:00 | 590 | 11kV | 3846 | 8 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S1290 leightonfield Panel 11 "Bileola Gurr No.2" fdr tripped, reclosed, tripped and locked out Relays - C phase IOC and timed, reclose timer, lockout, EFI Signals: 11kv trip, Zone earth, Tx 3 Group earth EFI's: S7614, S3081. NO access at sub 3399 Dop Required to check and reset EFI Remarks: UG fault. Fault between Sw/B @ Sub 3081 Biloela St, AB 24 tee Sub 5911 Shaddock Metal Polisher (N//) Feeder unable to be resotred due to access inssues at S7614, S3399, S3081. Access was gained sun morning to Sub 7614 | March | 2015 | 2015Q3 | 2015 | ZN1290:PA11 | ZN1290:PA11 | ZN01290/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-03-15 | N | 480.75 | N | 12 | N | N | 1.1101 | 39.4971 | 2810.5434
[7 empty] | 12950 | 6453 | 1220676 | 2015-03-15 11:20 | 2015-03-15 13:23 | 123 | 11kV | 13284 | 108 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | CP44602 Ourimbah Ck Rd Tripped Reclosed Tripped and locked out on O/C Trip Cause: Tree branch on OH mains O/S 644 Ourimbah Creek Rd - Emso to check for earthing issues at Customer premisis | March | 2015 | 2015Q3 | 2015 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2015-03-15 | N | 123 | N | 12 | N | N | 1.1101 | 39.4971 | 9707.5554
[7 empty] | 12990 | 6748 | 1220701 | 2015-03-15 12:23 | 2015-03-15 13:45 | 82 | 11kV | 410 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151233 10 amp fuse Substation DOLF Excludes OMS 1220701 | March | 2015 | 2015Q3 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2015-03-15 | N | 82 | N | 12 | N | N | 1.1101 | 39.4971 | 299.6159
[7 empty] | 14209 | 16579 | 1220678 | 2015-03-15 11:42 | 2015-03-15 14:00 | 138 | 11kV | 167118 | 1211 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 151232 2 fault operations Overcurrent tree branch removed from OHM at pole IW-10570 Excluded oms # 1220678 | March | 2015 | 2015Q3 | 2015 | 239:82132 | 239:82132 | ZN00239/082132 | LAKE MACQUARIE | OH | Veg | 2015-03-15 | N | 138 | N | 12 | N | N | 1.1101 | 39.4971 | 122124.9053
[7 empty] | 13744 | 12869 | 1220671 | 2015-03-15 11:06 | 2015-03-15 14:10 | 184 | 11kV | 184 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 151235 10 amp fuse Substation DOLF Excludes OMS 1220671 | March | 2015 | 2015Q3 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2015-03-15 | N | 184 | N | 12 | N | N | 1.1101 | 39.4971 | 134.4618
[7 empty] | 13354 | 9758 | 1220720 | 2015-03-15 13:11 | 2015-03-15 14:53 | 102 | 11kV | 24888 | 244 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Rain Wind Storm | N | Recloser CP421 Crosslands tripped and reclosed tripped and locked out Cause: Tree branch found on 11kV CCT adjacent to PT2438 See OMS 1220720 1220730 1220721 | March | 2015 | 2015Q3 | 2015 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2015-03-15 | N | 102 | N | 12 | N | N | 1.1101 | 39.4971 | 18187.4163
[7 empty] | 12831 | 5326 | 1220711 | 2015-03-15 12:57 | 2015-03-15 15:14 | 137 | 11kV | 183113 | 1474 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | At S12600 Lisarow Panel 9 tripped on Relays: A phase timed and OC, EFI, Lockout Signals: 11kV Trip Cause not ascertained for outage See OMS 1222684 1222686 1222688 1222691 1222689 1220711 | March | 2015 | 2015Q3 | 2015 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2015-03-15 | N | 124.2286 | N | 12 | N | N | 1.1101 | 39.4971 | 133813.5795
[7 empty] | 12604 | 3249 | 1220677 | 2015-03-15 11:34 | 2015-03-15 17:45 | 371 | 11kV | 283986 | 1356 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 151231 Broken Xarm pole SW-40007 Excluded OMS 1220677 | March | 2015 | 2015Q3 | 2015 | 239:82129 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2015-03-15 | N | 209.4292 | N | 12 | N | N | 1.1101 | 39.4971 | 207528.5926
[7 empty] | 14211 | 16583 | 1220796 | 2015-03-15 17:42 | 2015-03-15 20:10 | 148 | 11kV | 148 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 1221164 100 amp fuse Excludes OMS 1220796 | March | 2015 | 2015Q3 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-03-15 | N | 148 | N | 12 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 12577 | 3060 | 1220793 | 2015-03-15 17:29 | 2015-03-15 20:13 | 164 | 11kV | 492 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151244 100 amp fuse Excludes OMS 1220793 | March | 2015 | 2015Q3 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2015-03-15 | N | 164 | N | 12 | N | N | 1.1101 | 39.4971 | 359.5391
[7 empty] | 14471 | 18500 | 1220685 | 2015-03-15 11:34 | 2015-03-15 22:40 | 666 | 11kV | 34632 | 52 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 151242 Sub Isolated B & C phase LV mains wrapped together 1 conductor replaced | March | 2015 | 2015Q3 | 2015 | 239:82129 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2015-03-15 | N | 666 | N | 12 | N | N | 1.1101 | 39.4971 | 25308.0441
[7 empty] | 13578 | 11531 | 1221409 | 2015-03-15 19:42 | 2015-03-16 05:30 | 588 | 11kV | 219879 | 1849 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 151247 2 fault operations Multiple trips since Fri 13/3/15 detailed patrol required Cap bank 62224 - Replaced faulty CT post insulator with standard post insulator. Cap bank left isolated Excluded OMS 1220754 & 1220844 | March | 2015 | 2015Q3 | 2015 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2015-03-15 | N | 118.9178 | N | 12 | N | N | 1.1101 | 39.4971 | 160681.0879
[7 empty] | 13139 | 7898 | 1220882 | 2015-03-16 06:54 | 2015-03-16 08:50 | 116 | 11kV | 2320 | 20 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151250 A Phase DOLF : 10 Amp Possum on Transformer removed | March | 2015 | 2015Q3 | 2015 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2015-03-16 | N | 116 | N | 4 | N | N | 1.1101 | 39.4971 | 1695.3876
[7 empty] | 13428 | 10384 | 1220922 | 2015-03-16 08:47 | 2015-03-16 10:47 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151252 B & C phase DOLF : 20 Amp Excluded OMS 1220922 | March | 2015 | 2015Q3 | 2015 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2015-03-16 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 12564 | 2956 | 1220958 | 2015-03-16 09:52 | 2015-03-16 11:55 | 123 | 11kV | 123 | 1 | HV | Animal Frog | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151253 Single phase DOLF : 10 Amp Excluded OMS 120958 | March | 2015 | 2015Q3 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2015-03-16 | N | 123 | N | 4 | N | N | 1.1101 | 39.4971 | 89.8848
[7 empty] | 12350 | 891 | 1221272 | 2015-03-16 17:13 | 2015-03-16 19:30 | 137 | 11kV | 685 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151256 DOLF excluded OMS 1221272 | March | 2015 | 2015Q3 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2015-03-16 | N | 137 | N | 4 | N | N | 1.1101 | 39.4971 | 500.5778
[7 empty] | 14547 | 19044 | 1221680 | 2015-03-17 17:46 | 2015-03-17 17:57 | 11 | 11kV | 8041 | 731 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty - iR62166 Watkins Thompson - tripped on: SEF and OC Protection malfunction - while switching across panel 6 and 22, DOp made iR62166 non tripping manually (Due to iR being in scan fail). After switching was completed DOp restored iR to normal operation and iR then tripped on SEF and OC. No cause was found and iR closed again OK. | March | 2015 | 2015Q3 | 2015 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Not Veg | 2015-03-17 | N | 11 | N | 1 | N | N | 1.1101 | 39.4971 | 5876.1256
[7 empty] | 14115 | 15942 | 1221720 | 2015-03-18 06:16 | 2015-03-18 07:20 | 64 | 11kV | 4352 | 68 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT49203 Reeves Pildarra 11kV HDO fuse operated Cause:11kV HDO fuse bluew and fell in a way that caused that pole to catch fire. PT was isolated and supply was restored via LV parallel See OMS 1222658 1221726 1221725 1221720 | March | 2015 | 2015Q3 | 2015 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2015-03-18 | N | 64 | N | 11 | N | N | 1.1101 | 39.4971 | 3180.3132
[7 empty] | 14543 | 19028 | 1221717 | 2015-03-18 05:52 | 2015-03-18 07:35 | 103 | 11kV | 7725 | 75 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Section of ZN.3154 St Ives 11kV from PT.1703 Nomurra Somerset to extent of Feeder (1 DC) - Centre phase 50K HDO operated Cause:- Not ascertained, HDO replaced successfully ME:-1222144 Withdrawn:-1221733, 1221717 | March | 2015 | 2015Q3 | 2015 | ZN3154:PA11 | ZN3154:PA11 | ZN03154/000011 | KU-RING-GAI | OH | Veg | 2015-03-18 | N | 103 | N | 11 | N | N | 1.1101 | 39.4971 | 5645.2022
[7 empty] | 14079 | 15667 | 1221785 | 2015-03-18 08:54 | 2015-03-18 14:30 | 336 | 11kV | 336 | 1 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 2 PHASES FOUND DOWN ALIVE ON BACKFEED THROUGH TX 72012. NO PROTECTION OPERATED. TRIPPED the night before. Possibility that farmer hit stay with plough. Excludes OMS 1221785 + 1222226 | March | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2015-03-18 | N | 336 | N | 11 | N | N | 1.1101 | 39.4971 | 245.5389
[7 empty] | 14452 | 18312 | 1221930 | 2015-03-18 14:24 | 2015-03-18 18:15 | 231 | 11kV | 12890 | 84 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | Zn1788 Matraville Pnl.7 tripped on: A phase timed O/C and EFI - No field EFIs flagged - assumed frontline feeder fault, isolated and attempted restore from S35741 ( P22 Botany). @ 16:04 Zn340 Botany P22 tripped on: ABC timed O/C and EFI - Field EFIs at S35741, S35742, S35094, S667 Cause: S667 McPherson Champ - 11kV RMI failure. See 1222157 1222158 | March | 2015 | 2015Q3 | 2015 | ZN1788:PA7 | ZN1788:PA67 | ZN01788/000067 | BAYSIDE | UG | Not Veg | 2015-03-18 | N | 153.4524 | N | 11 | N | N | 1.1101 | 39.4971 | 9419.6318
[7 empty] | 13866 | 13835 | 1222059 | 2015-03-18 17:45 | 2015-03-18 18:36 | 51 | 11kV | 112557 | 2207 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Lightning | N | ZN.15001 Brookvale 11kV Panel 18 feeder tripped on:- Relays:- 18L IOC, EFI, Fault Check, Reclose Signals:- 11kV Trip All EFI's operated on Panel 18L side Cause:- Lightning struck pole FF-46087 (O/S 24 Princess Mary St Beacon Hill), Mains ton inspect in daylight ME:-1222059 GIS Model Error:-1222067 (Known Outage in Area) Withdrawn:-1222070 | March | 2015 | 2015Q3 | 2015 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | OH | Not Veg | 2015-03-18 | N | 51 | N | 11 | N | N | 1.1101 | 39.4971 | 82253.3357
[7 empty] | 14279 | 17072 | 1222024 | 2015-03-18 16:44 | 2015-03-18 21:15 | 271 | 11kV | 11007 | 244 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Wind Strong | N | LID 151298 3 fault operations A phase Overcurrent LB 26930 left open on request of customer due to internal defect Excluded OMS 1222024 | March | 2015 | 2015Q3 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | Unknown | Not Veg | 2015-03-18 | N | 45.1107 | N | 11 | N | N | 1.1101 | 39.4971 | 8043.5909
[7 empty] | 14513 | 18811 | 1222098 | 2015-03-18 19:38 | 2015-03-18 22:10 | 152 | 11kV | 152 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID151302 No protection Op. HV dropper lead came lose. Excludes OMS 1222098 | March | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2015-03-18 | N | 152 | N | 11 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 13507 | 10989 | 1222032 | 2015-03-18 16:55 | 2015-03-18 22:58 | 363 | 11kV | 2178 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Rain Light | N | LID 151305 Single phase DOLF : 5 Amp DOLF carrier burnt in half Excluded OMS 1222032 & 1222060 | March | 2015 | 2015Q3 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-03-18 | N | 363 | N | 11 | N | N | 1.1101 | 39.4971 | 1591.6182
[7 empty] | 13041 | 7078 | 1222121 | 2015-03-18 21:55 | 2015-03-18 23:00 | 65 | 11kV | 58789 | 1211 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | LID 151306 2 fault operations Blown UGOH pole IV-70609. Requires replacement. Excluded OMS 1222121, 1222123, 1222128, 1222130. | March | 2015 | 2015Q3 | 2015 | 239:82132 | 239:82132 | ZN00239/082132 | LAKE MACQUARIE | Unknown | Unknown | 2015-03-18 | N | 48.5458 | N | 11 | N | N | 1.1101 | 39.4971 | 42961.2672
[7 empty] | 13579 | 11532 | 1222176 | 2015-03-18 23:10 | 2015-03-18 23:14 | 4 | 11kV | 2244 | 561 | HV | Staff Operation | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 151307 1 fault operation Sensitive Earth Fault During RSI 4821 SEF not disabled when energising cable from 11kV links 7264. Interruption betweem Sw 11455 and Sw 20199. Intellirupter Sw 20199 installed 17/3/15. | March | 2015 | 2015Q3 | 2015 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Not Veg | 2015-03-18 | N | 4 | N | 11 | N | N | 1.1101 | 39.4971 | 1639.849
[7 empty] | 14397 | 17899 | 1222132 | 2015-03-19 02:10 | 2015-03-19 03:20 | 70 | 11kV | 280 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 151308 No protection operation. Sub 54689 isolated to cut away faulty 11kV arrestors. New arrestors required. Excluded OMS 1222132. | March | 2015 | 2015Q3 | 2015 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2015-03-19 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 13662 | 12219 | 1222248 | 2015-03-18 17:12 | 2015-03-19 12:40 | 1168 | 11kV | 27258 | 70 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind Strong | N | LID 151300 1 fault operation Wire Down between GN-50016 & GN 50017 | March | 2015 | 2015Q3 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-03-18 | N | 389.4 | N | 11 | N | N | 1.1101 | 39.4971 | 19919.3424
[7 empty] | 13775 | 13111 | 1222156 | 2015-03-19 07:41 | 2015-03-19 12:50 | 309.5 | 11kV | 5571 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151323 2 amp fuse LIne DOLF CC1: 22-"Refer to SOp" | March | 2015 | 2015Q3 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | SINGLETON | OH | Veg | 2015-03-19 | N | 309.5 | N | 4 | N | N | 1.1101 | 39.4971 | 4071.1225
[7 empty] | 12888 | 5907 | 1222504 | 2015-03-19 17:51 | 2015-03-19 19:23 | 92 | 11kV | 49800 | 569 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn.931 Darlinghurst Pnl.18 tripped on: Left leg translay & EFI No Field EFIs UG Cable fault - frontline feeder from Pnl.18 to S35424 to S36107 to S46974 see 1222607 GIS: 1222509 1222506 | March | 2015 | 2015Q3 | 2015 | ZN931:PA18 | ZN931:PA18 | ZN00931/000018 | SYDNEY | UG | Not Veg | 2015-03-19 | N | 87.522 | N | 4 | N | N | 1.1101 | 39.4971 | 36392.3711
[7 empty] | 13771 | 13084 | 1222532 | 2015-03-19 20:21 | 2015-03-19 23:17 | 176 | 11kV | 142403 | 1018 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At ZN35500 Top Ryde Panel 34 tripped on A phase IOC and Earth Fault Signals: 11kV Trip, EFI, Group Earth and Fault Check Cause Not ascertained for outage See OMS 1223728 1223730 1223729 1222553 1222546 1222541 1222532 1222536 1222537 | March | 2015 | 2015Q3 | 2015 | ZN35500:PA34 | ZN35500:PA36 | ZN35500/000036 | RYDE | OH | Veg | 2015-03-19 | N | 139.8851 | N | 4 | N | N | 1.1101 | 39.4971 | 104063.9122
[7 empty] | 14173 | 16278 | 1222557 | 2015-03-20 00:13 | 2015-03-20 01:35 | 82 | 11kV | 7708 | 94 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151328 A phase DOLF : 2-0 Amp Excluded OMS 1222557 & 1222559 | March | 2015 | 2015Q3 | 2015 | 239:82132 | 239:82132 | ZN00239/082132 | LAKE MACQUARIE | OH | Veg | 2015-03-20 | N | 82 | N | 7 | N | N | 1.1101 | 39.4971 | 5632.7791
[7 empty] | 14654 | 20150 | 1222558 | 2015-03-20 00:21 | 2015-03-20 02:45 | 144 | 11kV | 9936 | 69 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At PT9357 Pacific Maianbar Ex S9118 Cronulla Panel 3 the center phase HDO blew Remark: Transformer failure. Dop replaced HDO and fuse blew again. Transformer isolated on HV and LV. Supply restored via LV// | March | 2015 | 2015Q3 | 2015 | ZN9118:PA3 | ZN9118:PA3 | ZN09118/000003 | SUTHERLAND | UG | Not Veg | 2015-03-20 | N | 144 | N | 7 | N | N | 1.1101 | 39.4971 | 7260.9357
[7 empty] | 14498 | 18664 | 1222619 | 2015-03-20 08:22 | 2015-03-20 10:51 | 149 | 11kV | 298 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | No Weather Impact | N | LID 151336 Single phase Conductor had broken off top of DOLF. | March | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2015-03-20 | N | 149 | N | 7 | N | N | 1.1101 | 39.4971 | 217.7696
[7 empty] | 14413 | 18006 | 1222896 | 2015-03-20 17:16 | 2015-03-20 18:16 | 60 | 11kV | 127620 | 2127 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca Pa37 "Picketts Scenic" fdr tripped Signals: 11kv trip Relays: 51 A and B EFI:Nil Tree branch on 11kv near LB49195 See 1222896 exclude 1222921,4 | March | 2015 | 2015Q3 | 2015 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2015-03-20 | N | 60 | N | 7 | N | N | 1.1101 | 39.4971 | 93260.9318
[7 empty] | 13487 | 10857 | 1222904 | 2015-03-20 17:10 | 2015-03-20 18:18 | 68 | 11kV | 4776 | 823 | HV | Vegetation Blow/Fall In | Vegetation | Lightning Arrestor | Unplanned | Rain Light | N | Zn14144 Wamberal Pa4L has tripped and reclosed Signals: 11kv trip Relays: 51A&B @PT12632 Hastings Aspen A 7 B phase 40Amp HDO fuses blown due to tree branch found across lightning arrestors. See 1224113,4 Exclude 1222904,5,6,18,28 | March | 2015 | 2015Q3 | 2015 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2015-03-20 | N | 5.8032 | N | 7 | N | N | 1.1101 | 39.4971 | 3490.1599
[7 empty] | 13361 | 9805 | 1223002 | 2015-03-20 22:15 | 2015-03-20 23:15 | 60.35 | 11kV | 6336.75 | 105 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn12640 Umina section of Pa10 @PT11892 Onslow Mackenzie footpath & centre phase 31.5Amp HDO fuses operated Possum fried itself See 1223001 exclude 1223002,3 | March | 2015 | 2015Q3 | 2015 | ZN12640:PA10 | ZN12640:PA10 | ZN12640/000010 | CENTRAL COAST | OH | Not Veg | 2015-03-20 | N | 60.35 | N | 7 | N | N | 1.1101 | 39.4971 | 4630.71
[7 empty] | 12591 | 3166 | 1223009 | 2015-03-20 22:47 | 2015-03-20 23:36 | 49 | 11kV | 49882 | 1018 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S965 Pennant HIlls Panel 43 tripped on Relays - B and C phase O/C Signals: 11kV Trip Cause: Found dead bat in Quarter Sessions Rd - Near Duffy | March | 2015 | 2015Q3 | 2015 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Not Veg | 2015-03-20 | N | 49 | N | 7 | N | N | 1.1101 | 39.4971 | 36452.2943
[7 empty] | 13909 | 14192 | 1223017 | 2015-03-21 00:06 | 2015-03-21 01:07 | 61 | 11kV | 11529 | 189 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | IR 50015 Quarry Old Northern Tripped Reclosed Tripped Reclosed Tripped and locked out on overcurrent Cause: Branch removed by DOp adjacent to PT2108 See OMS 1223721 1223017 1223025 | March | 2015 | 2015Q3 | 2015 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2015-03-21 | N | 61 | N | 4 | N | N | 1.1101 | 39.4971 | 8425.0532
[7 empty] | 13010 | 6881 | 1223092 | 2015-03-21 09:49 | 2015-03-21 13:15 | 206 | 11kV | 618 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | PT13616 Fishermans Point No,1 HDO 10Amp fuse blown Second time in 2 weeks. Suspect trasnformer failing. Cause not ascertained See 1224514 Exclude 1223092 | March | 2015 | 2015Q3 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | HORNSBY | OH | Not Veg | 2015-03-21 | N | 206 | N | 4 | N | N | 1.1101 | 39.4971 | 451.6162
[7 empty] | 13226 | 8566 | 1223178 | 2015-03-21 05:32 | 2015-03-21 19:20 | 828 | 11kV | 8280 | 10 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | PT.15238 Cross Roads Cause:- B phase LV Tail burnt at transformer bushing D/Op isolated and restored via LV// ME:-1223460 Withdrawn:-1223178 Excludes OMS 1223460 | March | 2015 | 2015Q3 | 2015 | ZN15013:PA2 | ZN15013:PA2 | ZN15013/000002 | NORTHERN BEACHES | OH | Not Veg | 2015-03-21 | N | 828 | N | 4 | N | N | 1.1101 | 39.4971 | 6050.7798
[7 empty] | 12765 | 4701 | 1223219 | 2015-03-21 21:45 | 2015-03-21 22:20 | 35 | 11kV | 35 | 1 | HV | Arcing | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 151353 sub isolated to repair damaged service Excluded OMS 1223219 | March | 2015 | 2015Q3 | 2015 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2015-03-21 | N | 35 | N | 4 | N | N | 1.1101 | 39.4971 | 25.577
[7 empty] | 12363 | 1028 | 1223254 | 2015-03-22 01:50 | 2015-03-22 03:10 | 80 | 11kV | 720 | 9 | HV | Arcing | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 151354 section isolated to make repairs at sub 27386 Excluded oms 1223254 | March | 2015 | 2015Q3 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2015-03-22 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 12766 | 4703 | 1223359 | 2015-03-22 12:18 | 2015-03-22 14:25 | 127 | 11kV | 147933 | 2091 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Panel 16 "Charmhaven San Remo" fdr tripped, reclosed, tripped & Lock out Relays: EF, Fault Check, Lock Out, EFI Signals: Tx2 GE, 11kv trip EFI's Nil Underground Frontline feeder fault See 1224515,6 exclude 1223359 | March | 2015 | 2015Q3 | 2015 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | UG | Not Veg | 2015-03-22 | N | 70.7475 | N | 3 | N | N | 1.1101 | 39.4971 | 108105.0731
[7 empty] | 13933 | 14444 | 1223420 | 2015-03-22 20:27 | 2015-03-22 23:10 | 163 | 11kV | 222975 | 1373 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn13000 Lake Munmorah Panel 7 "Summerland Point" @RE45061 Chain Valley Bay tripped and locked out on SEF Trip Bond Burnt off at AB43825 See 1224519,20 Exclude 1223420 | March | 2015 | 2015Q3 | 2015 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2015-03-22 | N | 162.3999 | N | 3 | N | N | 1.1101 | 39.4971 | 162943.5534
[7 empty] | 14146 | 16162 | 1223809 | 2015-03-23 23:31 | 2015-03-24 01:02 | 91 | 11kV | 99190 | 1090 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 42 Tripped on O/C and Earth Fault and A and B phase Overcurrent Cause not ascertained for outage NOTE: At the time of interruption only 30A of load on feeder. Feeder appears to be backfed by LV parallel. | March | 2015 | 2015Q3 | 2015 | ZN4545:PA42 | ZN4545:PA42 | ZN04545/000042 | RYDE | OH | Veg | 2015-03-23 | N | 91 | N | 2 | N | N | 1.1101 | 39.4971 | 72485.1264
[7 empty] | 13279 | 8970 | 1223808 | 2015-03-23 23:41 | 2015-03-24 01:49 | 128 | 11kV | 5437 | 44 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14143 Somersby Pa6 tripped on Earth fault EFI Faulty section of UG fdr between S18454:B to S18253:A See 1224529,30,1,2,3 Exclude 1223808 | March | 2015 | 2015Q3 | 2015 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | UG | Not Veg | 2015-03-23 | N | 123.5682 | N | 2 | N | N | 1.1101 | 39.4971 | 3973.1992
[7 empty] | 12702 | 4176 | 1223819 | 2015-03-24 06:16 | 2015-03-24 09:20 | 184 | 11kV | 2208 | 12 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn14142 Somersby section of Pa21 "Somersby" PT14454 Debenham Chivers 0.2 11kv roadside HDO fuse found blown (31.5k) Possum found at base of pole transformer See 1224703 exclude 1223819 | March | 2015 | 2015Q3 | 2015 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2015-03-24 | N | 184 | N | 12 | N | N | 1.1101 | 39.4971 | 1613.5413
[7 empty] | 12429 | 1634 | 1223973 | 2015-03-24 12:02 | 2015-03-24 12:27 | 25 | 11kV | 275 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Replace blown HV fuse on sub 51887 Excludes OMS 1223973 | March | 2015 | 2015Q3 | 2015 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2015-03-24 | N | 25 | N | 12 | N | N | 1.1101 | 39.4971 | 200.9619
[7 empty] | 14454 | 18341 | 1224074 | 2015-03-24 14:46 | 2015-03-24 15:11 | 25 | 11kV | 40700 | 1628 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN.150011 Beacon Hill 11kV Panel 2 feeder tripped, re-closed, tripped and locked out on:- Relays:- Inst A+C phase, recloser, timing, lock out Field EFI's: Nil Signals: 11kV trip Cause:- Tree branch on 11kV OH mains removed by D/Op adjacent to PT.15164 in Darmour Ave ME:-1224074 Withdrawn:-1224078, 1224084, 1224086, 1224091 | March | 2015 | 2015Q3 | 2015 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Veg | 2015-03-24 | N | 25 | N | 12 | N | N | 1.1101 | 39.4971 | 29742.3596
[7 empty] | 13538 | 11168 | 1224108 | 2015-03-24 15:20 | 2015-03-24 16:16 | 56 | 11kV | 56 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 151379 2 fault operations Overcurrent Aph 4.191kA, Bph 4.246kA, Cph 4.878kA, EF 2.207kA. see UPO report # 151378 also. Excluded 1224108 | March | 2015 | 2015Q3 | 2015 |  |  |  | SINGLETON | OH | Veg | 2015-03-24 | N | 56 | N | 12 | N | N | 1.1101 | 39.4971 | 40.9231
[7 empty] | 14601 | 19632 | 1224112 | 2015-03-24 15:31 | 2015-03-24 16:50 | 79 | 11kV | 474 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151381 A & B phase DOLF : 10 Amp Excluded OMS 1224112 | March | 2015 | 2015Q3 | 2015 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Veg | 2015-03-24 | N | 79 | N | 12 | N | N | 1.1101 | 39.4971 | 346.3852
[7 empty] | 14093 | 15737 | 1224153 | 2015-03-24 16:48 | 2015-03-24 18:05 | 77 | 11kV | 6622 | 86 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Ex Zn12570 Avoca Pa29 "Bensville" @PT11799 Meridan Valencia 11kv HDO fuse 31.5 A & C phase footpath side Dist 2 "Valencia st" A phase fuse blown DW down Tree branch fell onto DW outside 1 Emma st Bensville See 1224155 exclude 1224153 | March | 2015 | 2015Q3 | 2015 | ZN12570:PA29 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2015-03-24 | N | 77 | N | 12 | N | N | 1.1101 | 39.4971 | 4839.1623
[7 empty] | 14319 | 17331 | 1224196 | 2015-03-24 17:49 | 2015-03-24 19:00 | 71 | 11kV | 71 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 151382 C phase DOLF : 10 Amp Excluded OMS 1224196 | March | 2015 | 2015Q3 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2015-03-24 | N | 71 | N | 12 | N | N | 1.1101 | 39.4971 | 51.8847
[7 empty] | 13431 | 10432 | 1224201 | 2015-03-24 17:43 | 2015-03-24 19:20 | 96.65 | 11kV | 7248.75 | 75 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Heavy | N | At PT51 Culloden Abuklea footpath phase surge arrestor was found blown after possible lightning strike | March | 2015 | 2015Q3 | 2015 | ZN2635:PA46 | ZN2635:PA46 | ZN02635/000046 | RYDE | OH | Not Veg | 2015-03-24 | N | 96.65 | N | 12 | N | N | 1.1101 | 39.4971 | 5297.1727
[7 empty] | 13828 | 13473 | 1224066 | 2015-03-24 14:23 | 2015-03-24 19:30 | 307 | 11kV | 60047 | 352 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | At Zn847 Hornsby Panel 22 Tripped reclosed tripped and locked out on Overcurrent Cause: AB3193 Has busted and insulator on footpath side of PT1994 Side See oMS 1225746 1225747 1224054/066/166 | March | 2015 | 2015Q3 | 2015 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Not Veg | 2015-03-24 | N | 170.5881 | N | 12 | N | N | 1.1101 | 39.4971 | 43880.5765
[7 empty] | 13373 | 9886 | 1224106 | 2015-03-24 15:17 | 2015-03-24 20:32 | 315 | 11kV | 22662 | 98 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 151380 1 fault operation single phase Sensitive Earth Fault Main off pin pole SF-50055 Excluded OMS 1224106 | March | 2015 | 2015Q3 | 2015 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2015-03-24 | N | 231.2449 | N | 12 | N | N | 1.1101 | 39.4971 | 16560.7212
[7 empty] | 13455 | 10579 | 1224233 | 2015-03-24 19:37 | 2015-03-24 21:00 | 83 | 11kV | 581 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151383 C Phase DOLF : 20 Amp Excvluded OMS 1224233 | March | 2015 | 2015Q3 | 2015 | 508:82576 | 508:82576 | ZN00508/082576 | PORT STEPHENS | OH | Veg | 2015-03-24 | N | 83 | N | 12 | N | N | 1.1101 | 39.4971 | 424.5777
[7 empty] | 14524 | 18906 | 1224269 | 2015-03-24 22:03 | 2015-03-25 00:40 | 157 | 11kV | 122475 | 1039 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 151384 Prot = Cph O/C, E/F Blown L/A on UGOH at pole CH-20192 Excluded OMS 1224269 | March | 2015 | 2015Q3 | 2015 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | Unknown | Unknown | 2015-03-24 | N | 117.8778 | N | 12 | N | N | 1.1101 | 39.4971 | 89501.1176
[7 empty] | 13092 | 7607 | 1224596 | 2015-03-25 18:22 | 2015-03-25 19:00 | 38 | 11kV | 76 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 151399 A phase DOLF : 10 Amp Excluded OMS 1224596 | March | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-03-25 | N | 38 | N | 2 | N | N | 1.1101 | 39.4971 | 55.5386
[7 empty] | 13293 | 9049 | 1224589 | 2015-03-25 17:54 | 2015-03-25 23:59 | 365 | 11kV | 7381 | 34 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | PT13242 Yarramalong Lauffs Dist 1 "Yarramalong rd" ABC fuses blown. Broken Cross arm outside 403 Yarramalong Rd , Wyong Creek OH Cables twisted together. Also Ex Zn14891 Wyong section of Pa12 feeder section between LK43741 to LB41276 interrupted for safety reasons. Excludes OMS 1224858/60 | March | 2015 | 2015Q3 | 2015 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2015-03-25 | N | 217.0882 | N | 2 | N | N | 1.1101 | 39.4971 | 5393.8171
[7 empty] | 13610 | 11775 | 1225038 | 2015-03-26 19:46 | 2015-03-26 21:05 | 79 | 11kV | 869 | 11 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa33 "Macmasters Beach" PT18856 Abundance Scenic Footpath phase 31.5Amp HDO fuse operated due to fuse fatigue See 1225187 exclude 1225038 | March | 2015 | 2015Q3 | 2015 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2015-03-26 | N | 79 | N | 1 | N | N | 1.1101 | 39.4971 | 635.0396
[7 empty] | 13177 | 8184 | 1225185 | 2015-03-27 11:00 | 2015-03-27 11:50 | 50 | 11kV | 50 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151428 B Phase DOLF : 10 Amp dead magpie found at sub Excluded oms 1225185 | March | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2015-03-27 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 13910 | 14204 | 1225268 | 2015-03-27 13:09 | 2015-03-27 15:40 | 151 | 11kV | 132683 | 1067 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN.3154 St Ives 11kV Panel 18 feeder tripped on:- Relays:- IOC, Earth Fault, EFI Signals:- 11kV trip, No.3 Group Earth, Zone Earth Field EFI's:- S.35629, S.62714, S.4903, S.35308 Cause:- 11kV UG Cable Fault from S.35308 SW/B to S.7324 SW/b to S.35920 SW/A N/O tee PT.1143 ME:-1225624 RS:-1225625, 1225626 Withdrawn:-1225268 | March | 2015 | 2015Q3 | 2015 | ZN3154:PA18 | ZN3154:PA18 | ZN03154/000018 | KU-RING-GAI | UG | Not Veg | 2015-03-27 | N | 124.3515 | N | 4 | N | N | 1.1101 | 39.4971 | 96960.8229
[7 empty] | 12499 | 2242 | 1225376 | 2015-03-27 18:13 | 2015-03-28 04:15 | 602 | 11kV | 602 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At S62905 Balfour Balfour Two 11KV 100A fuses operated interrupting Sub Cause: Suspect Tx Failure - Transformer replaced. Excludes OMS 1225376 | March | 2015 | 2015Q3 | 2015 | ZN1193:PA17 | ZN1193:PA17 | ZN01193/000017 | KU-RING-GAI | UG | Not Veg | 2015-03-27 | N | 602 | N | 4 | N | N | 1.1101 | 39.4971 | 439.9238
[7 empty] | 14303 | 17245 | 1225405 | 2015-03-28 02:56 | 2015-03-28 05:55 | 179 | 11kV | 180740 | 1101 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 18 Tripped Reclosed Tripped and Locked out on Signals: 11kV Trip, Zone Earth, TX2 Group Earth Relays: A phase IOC and Timed A phase, Timing Relays and Lockout Cause: Suspect UG cable fault between Pa18 Hornsby and S4526 SW/A See OMS 1226112 1225405 | March | 2015 | 2015Q3 | 2015 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | UG | Not Veg | 2015-03-28 | N | 164.1599 | N | 4 | N | N | 1.1101 | 39.4971 | 132079.4611
[7 empty] | 13188 | 8306 | 1225391 | 2015-03-27 19:24 | 2015-03-28 11:50 | 986 | 11kV | 4860 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | At ZN35370 Galston ex Panel 4L High Voltage Line Connector failed between tee off to PT1890 Vision Arcadia and tee off to PT1941 Vision Valley See OMS 1226141 1226139 1226138 1225395 1225391 | March | 2015 | 2015Q3 | 2015 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2015-03-27 | N | 972 | N | 4 | N | N | 1.1101 | 39.4971 | 3551.5447
[7 empty] | 14360 | 17601 | 1225449 | 2015-03-28 10:57 | 2015-03-28 12:03 | 66 | 11kV | 66 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151433 C phase DOLF : 10 Amp Volts = 242 V | March | 2015 | 2015Q3 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2015-03-28 | N | 66 | N | 4 | N | N | 1.1101 | 39.4971 | 48.2309
[7 empty] | 12524 | 2508 | 1225506 | 2015-03-28 19:30 | 2015-03-28 21:30 | 120 | 11kV | 3240 | 27 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 151439 pole fire JT-10093 no protection operation section isolated Excluded oms # 1225499 | March | 2015 | 2015Q3 | 2015 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2015-03-28 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 2367.6964
[7 empty] | 12343 | 828 | 1225515 | 2015-03-28 22:55 | 2015-03-28 23:53 | 57.9167 | 11kV | 4922.9167 | 85 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151440 C phase DOLF : 40 Amp Possum Excluded OMS 1225515 & 1225518 | March | 2015 | 2015Q3 | 2015 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2015-03-28 | N | 57.9167 | N | 4 | N | N | 1.1101 | 39.4971 | 3597.5223
[7 empty] | 12650 | 3758 | 1226058 | 2015-03-30 21:43 | 2015-03-30 22:30 | 47 | 11kV | 33981 | 723 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn3425 Castle Cove Panel 22 tripped Relays: Timed Earth Fault, Fault Check and EFI Signals: 11kV Trip Cause: 11kV UG fault from S3538 Orara Douglas to S49097 Gibbes Smith No2 | March | 2015 | 2015Q3 | 2015 | ZN3425:PA22 | ZN3425:PA22 | ZN03425/000022 | WILLOUGHBY | UG | Not Veg | 2015-03-30 | N | 47 | N | 3 | N | N | 1.1101 | 39.4971 | 24832.3125
[7 empty] | 13414 | 10251 | 1226051 | 2015-03-30 20:57 | 2015-03-30 22:38 | 101 | 11kV | 48045 | 519 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S35800 Bankstown the Panel 19 "Bristish Paints, etc" feeder tripped on: Relays: 61N-EF, 50TN-EFC,FLP-Frame leakage prohibition relay Signals: Tx 12 Group Earth Field EFIs: Nil Remarks: UG fault. 11kv fdr fault from Panel 19 @ S35800 Bankstown to S3050 British paints No2 to S6696 Fairford Gow South | March | 2015 | 2015Q3 | 2015 | ZN35800:PA19 | ZN35800:PA19 | ZN35800/000019 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-03-30 | N | 92.5723 | N | 3 | N | N | 1.1101 | 39.4971 | 35109.8689
[7 empty] | 13114 | 7751 | 1226068 | 2015-03-30 23:42 | 2015-03-31 03:15 | 213 | 11kV | 32702 | 154 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2483 North Sydney Panel 22 tripped on Relays: B phase overcuurrent, with EFI Signals: 11kV Trip, TX3 Group Earth Cause:11kV UG cable fault from Panel 22 North Sydney to S6643 Hipwood High to S2758 Clark Kurraba Note: LV parallel found in for S6443 Hipwood High backfeeding into the fault and stopped auto closing at S6642 Bradfield Park See OMS 1227063 1227112 1226068 | March | 2015 | 2015Q3 | 2015 | ZN2473:PA22 | ZN35400:PA53 | ZN35400/000053 | NORTH SYDNEY | UG | Not Veg | 2015-03-30 | N | 212.3506 | N | 3 | N | N | 1.1101 | 39.4971 | 23897.6571
[7 empty] | 13515 | 11067 | 1226149 | 2015-03-31 08:55 | 2015-03-31 10:06 | 71 | 11kV | 118710 | 1845 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At Zn12640 Umina Pa19 fdr has tripped Signals: 11kv trip Relays: A & C phase IOC Cause not ascertained See 1226208,87 Exclude 1226149 | March | 2015 | 2015Q3 | 2015 | ZN12640:PA19 | ZN12640:PA14 | ZN12640/000014 | CENTRAL COAST | OH | Veg | 2015-03-31 | N | 64.3415 | N | 3 | N | N | 1.1101 | 39.4971 | 86749.7666
[7 empty] | 13952 | 14590 | 1226069 | 2015-03-31 | 2015-03-31 15:55 | 955 | 11kV | 29130 | 180 | HV | 3rd Party Vehicle | 3rd Party Impact | Bond | Unplanned | Rain Heavy | N | LID 151455 2 fault operations 3 phase Truck hit and broke pole DN-30295. Txf & mains down. Broke taps to sub 53263. 2nd outage required to reconnect tappings. Excluded OMS 1226069. | March | 2015 | 2015Q3 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2015-03-31 | N | 161.8333 | N | 3 | N | N | 1.1101 | 39.4971 | 21287.3448
[7 empty] | 14373 | 17702 | 1226291 | 2015-03-31 12:19 | 2015-03-31 19:40 | 441 | 11kV | 82250 | 1102 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S1193 Lindfield Panel 27 Tripped, Reclosed Tripped and Locked out on SEF with EFI Cause: 11kV Down in Wellington Ave See OMS 1227019 1227023 1227024 1226279 1226283 1226291 1226295 1226299 1226304 1226305 1226322 | March | 2015 | 2015Q3 | 2015 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Not Veg | 2015-03-31 | N | 74.637 | N | 3 | N | N | 1.1101 | 39.4971 | 60105.874
[7 empty] | 14001 | 14944 | 1226484 | 2015-04-01 00:53 | 2015-04-01 01:50 | 57 | 11kV | 23712 | 416 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN.3154 St Ives 11kV Panel feeder tripped and locked out on:- Relays:- B Phase IOC & EFI Signals:- 11kV Trip Zone Earth, Tx.1 Group Earth Field EFI's:- S.4264 Cause:- Desd possum found on ground @ PT.1258 Benaroon Avenue ME:-1226484 Withdrawn:-1226486 | April | 2015 | 2015Q4 | 2015 | ZN3154:PA14 | ZN3154:PA14 | ZN03154/000014 | KU-RING-GAI | OH | Not Veg | 2015-04-01 | N | 57 | N | 9 | N | N | 1.1101 | 39.4971 | 17328.0302
[7 empty] | 12657 | 3814 | 1226485 | 2015-04-01 01:11 | 2015-04-01 02:20 | 69 | 11kV | 97566 | 1414 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | ZN 9252 Jannali - Pnl 31 - A & B phase IOC, EFI. Possum at first UGOH on RH leg. | April | 2015 | 2015Q4 | 2015 | ZN9252:PA31 | ZN9252:PA31 | ZN09252/000031 | SUTHERLAND | OH | Not Veg | 2015-04-01 | N | 69 | N | 9 | N | N | 1.1101 | 39.4971 | 71298.3551
[7 empty] | 14018 | 15160 | 1226537 | 2015-04-01 07:42 | 2015-04-01 08:42 | 60 | 11kV | 138120 | 2302 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S2635 Panel 58 Chambridge Chester tripped on A phase IOC Reclose T/D Lockout with EFI. Cause: Mains twisted together near AB1906 Cause Unknown. See OMS 1226526 1226537 | April | 2015 | 2015Q4 | 2015 | ZN2635:PA58 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | OH | Not Veg | 2015-04-01 | N | 60 | N | 9 | N | N | 1.1101 | 39.4971 | 100934.0221
[7 empty] | 13804 | 13314 | 1226542 | 2015-04-01 08:15 | 2015-04-01 09:55 | 100.5 | 11kV | 100.5 | 1 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa2 PT13305 The Ridgeway Cutrock N 11kv roadside dropout fuse opened Vehicle Hit Pole See 1226542 exclude 1226541 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2015-04-01 | N | 100.5 | N | 9 | N | N | 1.1101 | 39.4971 | 73.4424
[7 empty] | 13757 | 12945 | 1226515 | 2015-04-01 07:34 | 2015-04-01 13:55 | 381.3667 | 11kV | 5720.5 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 151474 repaired mains wire down at sub 25777 Excludes OMS 1226534 | April | 2015 | 2015Q4 | 2015 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2015-04-01 | N | 381.3667 | N | 9 | N | N | 1.1101 | 39.4971 | 4180.3727
[7 empty] | 14198 | 16481 | 1226677 | 2015-04-01 11:44 | 2015-04-01 14:13 | 149 | 11kV | 311087 | 2317 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn7481 Darling Harbour - Pnl.17 tripped on: O/C + E/F Field EFIs: NIL UG cable fault - frontline feeder damaged by customer excavator outside 298 Pyrmont Bridge Rd, Camperdown see 1228260 | April | 2015 | 2015Q4 | 2015 | ZN7481:PA17 | ZN384:PA76 | ZN00384/000076 | SYDNEY | UG | Not Veg | 2015-04-01 | N | 134.2628 | N | 9 | N | N | 1.1101 | 39.4971 | 227333.2041
[7 empty] | 13608 | 11768 | 1226827 | 2015-04-01 15:12 | 2015-04-01 16:36 | 84 | 11kV | 124488 | 1482 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN.15011 Beacon Hill 11kV Panel 10 Feeder tripped on:- Relays 10R:- A, B, C Phase Overcurrent, EFI Signals:- 11kV Trip, Zone Earth Field EFI's:- S.16679, S.16399, S.46678, S.26679 NOTE:- Abnormal switching - S.16726 SW/A Closed / LBS.63021 Open Cause:- Bird contacted OH 11kV mains on HV T-Pole on corner of Oxford Falls Rd & Broker Ave, Beacon Hill ME:-1228705 GIS Model Error:-1226845 Withdrawn:-1226834, 1226827, 1226843, 1226856, 1226839, 1226838, 1226833 | April | 2015 | 2015Q4 | 2015 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Not Veg | 2015-04-01 | N | 84 | N | 9 | N | N | 1.1101 | 39.4971 | 90972.1586
[7 empty] | 13545 | 11269 | 1226713 | 2015-04-01 15:10 | 2015-04-01 17:15 | 125 | 11kV | 43250 | 346 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 151480 11kV dropper broken at top of dolf at sub 54304 and resting on crossarm. Excludes OMS 1226713,1226829 | April | 2015 | 2015Q4 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2015-04-01 | N | 125 | N | 9 | N | N | 1.1101 | 39.4971 | 31605.8243
[7 empty] | 13827 | 13471 | 1226862 | 2015-04-01 16:30 | 2015-04-01 17:30 | 60 | 11kV | 655 | 11 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | No Weather Impact | N | Ex Zn12600 section of Pa2 "Holgate" fdr Interrupted for safety reasons for lineworkers to retie CCT conductor back onto pin insulator See 1227122,4,5,6 exclude 1226862 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2015-04-01 | N | 59.5455 | N | 9 | N | N | 1.1101 | 39.4971 | 478.6547
[7 empty] | 12836 | 5394 | 1226959 | 2015-04-02 07:07 | 2015-04-02 07:50 | 43 | 11kV | 5332 | 124 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151482 40 amp fuse Substation DOLF Readings as left = 239V, 238V, 240V. No Load readings taken (white ant pole) LVF isolated at 0740hrs supply on 0750hrs. Excludes OMS 1226959/962/967 CC1: 22-"Refer to SOp" | April | 2015 | 2015Q4 | 2015 | 258:80784 | 258:80784 | ZN00258/080784 | NEWCASTLE | OH | Veg | 2015-04-02 | N | 43 | N | 4 | N | N | 1.1101 | 39.4971 | 3896.4683
[7 empty] | 14187 | 16394 | 1227061 | 2015-04-02 03:22 | 2015-04-02 11:05 | 463 | 11kV | 4630 | 10 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa20 RE45203 Butt Gass Generator tripped @03:22 RE476302 Hue Hue Sparks 0.1 opened @ 9:55 to carry out repairs to feeder 11kv bond past RE47302 Hue Hue Sparks 0.1 burnt off | April | 2015 | 2015Q4 | 2015 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2015-04-02 | N | 463 | N | 4 | N | N | 1.1101 | 39.4971 | 3383.4674
[7 empty] | 13945 | 14570 | 1227317 | 2015-04-02 15:09 | 2015-04-02 17:25 | 136 | 11kV | 272 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 151498 20 amp fuse Substation DOLF HV fuse carrier had burnt up and R Cook had to replace the fuse and fuse carrier. It appears the fuse carrier had degraded in the weather. Excludes OMS # 1227318 & 1227317. | April | 2015 | 2015Q4 | 2015 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2015-04-02 | N | 136 | N | 4 | N | N | 1.1101 | 39.4971 | 198.7696
[7 empty] | 13843 | 13627 | 1227357 | 2015-04-02 17:00 | 2015-04-02 18:15 | 75 | 11kV | 3600 | 48 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID151499 No protection operated. Local staff advised damaged conductor at pole EM-20216 only had a few strands left and had to be attended to immediately. Interuption was solely to allow access to complete repairs. In addition to repairing the damaged conductor 11kV cross arm defects were also repaired at this pole. Excludes OMS 1227357 | April | 2015 | 2015Q4 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-04-02 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 2630.7738
[7 empty] | 13922 | 14391 | 1227407 | 2015-04-03 06:50 | 2015-04-03 07:00 | 10 | 11kV | 3260 | 326 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn12620 Noraville section of Pa13 "Wallarah" LK42034 opened interrupting 5 centres to AB41000 ABNORMAL: AB40129 is closed wiht AB41000 open Feeder required to be isolated from S14497 to LK42034 tee to PT11860 due to car hit pole Interrupted to change 11kv supply as it does not phase See 1229076 2nd 1229080 GIS 1227496 exclude 1227406,8826 | April | 2015 | 2015Q4 | 2015 | ZN12620:PA13 | ZN12620:PA13 | ZN12620/000013 | CENTRAL COAST | OH | Not Veg | 2015-04-03 | N | 10 | N | 2 | N | N | 1.1101 | 39.4971 | 2382.3118
[7 empty] | 12622 | 3405 | 1227435 | 2015-04-03 10:00 | 2015-04-03 10:38 | 38 | 11kV | 26828 | 706 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S35370 Galston Panel 8 Tripped and reclosed on A and C phase IOC Cause: Tree branch removed by DOp See OMS 1228408 1227435 - 1227463 | April | 2015 | 2015Q4 | 2015 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2015-04-03 | N | 38 | N | 2 | N | N | 1.1101 | 39.4971 | 19605.1111
[7 empty] | 13685 | 12410 | 1228879 | 2015-04-04 00:01 | 2015-04-04 01:23 | 82 | 11kV | 61428 | 794 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | LID 151504 1 fault operation A phase Overcurrent; Earth fault Cable fault between Sw 55705 & 36663. Excluded OMS 1227529 | April | 2015 | 2015Q4 | 2015 | 202:34262 | 202:34262 | ZN00202/034262 | NEWCASTLE | UG | Not Veg | 2015-04-04 | N | 77.3652 | N | 6 | N | N | 1.1101 | 39.4971 | 44889.7706
[7 empty] | 13071 | 7397 | 1227570 | 2015-04-04 08:57 | 2015-04-04 10:30 | 93 | 11kV | 93 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 151505 10 amp fuse Substation DOLF Excludes OMS 1227570 | April | 2015 | 2015Q4 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-04-04 | N | 93 | N | 6 | N | N | 1.1101 | 39.4971 | 67.9617
[7 empty] | 13032 | 7046 | 1227703 | 2015-04-04 15:45 | 2015-04-05 01:10 | 565 | 11kV | 11570 | 42 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 151507 2 fault operations Earth fault Mans knocked down by falling tree between sub 54276 and sub 52791. | April | 2015 | 2015Q4 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2015-04-04 | N | 275.4762 | N | 6 | N | N | 1.1101 | 39.4971 | 8455.0147
[7 empty] | 14221 | 16673 | 1227716 | 2015-04-04 16:32 | 2015-04-05 08:10 | 938 | 11kV | 53492 | 149 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn14891 Wyong section of Pa12 "Yarramalong" fdr from CP44753 bunnings creek tripped reclosed and locked out (in scan fail) Branch found on overhead mains near PT12164 Ravensdale End 0.5 See 1229099,100,1 Exclude 1227716,63 | April | 2015 | 2015Q4 | 2015 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2015-04-04 | N | 359.0067 | N | 6 | N | N | 1.1101 | 39.4971 | 39090.3759
[7 empty] | 14678 | 20343 | 1227762 | 2015-04-04 20:43 | 2015-04-05 09:46 | 782.65 | 11kV | 3130.6 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 151508 10 amp fuse Substation DOLF Staff suspect fuse blew in a previous storm. LA replaced. Excludes OMS 1227804 CC1: 22-"Refer to SOp" FRC1: 328-"High Voltage Fuse - Replaced - Specify Detail By Voice" | April | 2015 | 2015Q4 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2015-04-04 | N | 782.65 | N | 6 | N | N | 1.1101 | 39.4971 | 2287.7501
[7 empty] | 14258 | 16955 | 1227781 | 2015-04-04 23:41 | 2015-04-05 15:00 | 919 | 11kV | 58031 | 281 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Ex Zn12600 Lisarow section of Pa2 "Holgate Feeder" RE44605 Ridgeway rd tripped on earth fault ABNORMAL: RE41845 North Erina opened (Defective) and Recloser 44605 Ridgeway Rd closed Tree brought down mains corner Wattle Tree and Pollard Close in Matcham See 1229475,6 Exclude 1227779,81 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2015-04-04 | N | 206.516 | N | 6 | N | N | 1.1101 | 39.4971 | 42407.3432
[7 empty] | 14626 | 19947 | 1227924 | 2015-04-05 22:55 | 2015-04-06 00:50 | 115 | 11kV | 145215 | 1557 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn12640 Umina Pa8 "Woolworths Bullion" tripped, reclosed and locked out on: Relays: IOC (No Phase), EFI, Lockout Signals: 11kv trip, Zone Earth EFI's: S46539 S18321 S13010 Picnic Oveanview Sw/B End Box failed See 1229492,3,4 Exclude 1227924 | April | 2015 | 2015Q4 | 2015 | ZN12640:PA8 | ZN12640:PA8 | ZN12640/000008 | CENTRAL COAST | UG | Not Veg | 2015-04-05 | N | 93.2659 | N | 1 | N | N | 1.1101 | 39.4971 | 106118.8389
[7 empty] | 14551 | 19077 | 1227928 | 2015-04-06 02:49 | 2015-04-06 14:55 | 726 | 11kV | 220977 | 1623 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 151511 2 fault operations 3 phase Earth fault X arm broke at pole JU-30638. HV into LV. Excluded OMS 1227928 | April | 2015 | 2015Q4 | 2015 | 203:8085 | 204:82705 | ZN00204/082705 | NEWCASTLE | OH | Not Veg | 2015-04-06 | N | 136.1534 | N | 6 | N | N | 1.1101 | 39.4971 | 161483.4739
[7 empty] | 13483 | 10800 | 1228003 | 2015-04-06 14:29 | 2015-04-06 16:00 | 91 | 11kV | 25025 | 275 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Zn14144 Wamberal Zone Pa5 "The Beaufort Blue View" fdr tripped, reclosed and locked out on BC phase timed and instantaneous overcurrent, reclose lockout Removed by DOp unable to close circuit breaker 5. Permit Issued | April | 2015 | 2015Q4 | 2015 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2015-04-06 | N | 91 | N | 6 | N | N | 1.1101 | 39.4971 | 18287.5319
[7 empty] | 12463 | 1847 | 1228005 | 2015-04-06 14:42 | 2015-04-06 16:25 | 103.25 | 11kV | 5265.75 | 51 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 151523 3 fault operations Overcurrent Vehicle hit tree near pole AN-60509 Jerrys Plains. | April | 2015 | 2015Q4 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Not Veg | 2015-04-06 | N | 103.25 | N | 6 | N | N | 1.1101 | 39.4971 | 3848.0548
[7 empty] | 13911 | 14211 | 1228251 | 2015-04-06 14:32 | 2015-04-06 17:03 | 151 | 11kV | 10327 | 69 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 151524 3 fault operations Overcurrent no fault found Excludes OMS 1228004/8251 | April | 2015 | 2015Q4 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2015-04-06 | N | 149.6667 | N | 6 | N | N | 1.1101 | 39.4971 | 7546.667
[7 empty] | 13768 | 13054 | 1228017 | 2015-04-06 15:52 | 2015-04-06 18:20 | 148 | 11kV | 148 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 151527 10 amp fuse Substation DOLF VOLTS =251 LOAD 3A excludes OMS 1228017. | April | 2015 | 2015Q4 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2015-04-06 | N | 148 | N | 6 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 12961 | 6509 | 1228032 | 2015-04-06 16:28 | 2015-04-06 20:20 | 232 | 11kV | 8410 | 51 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 151525 3 fault operations 3 phase Overcurrent; Earth fault MAINS DOWN BETWEEN SUB 70481 & POLE 9L-70382. Excluded OMS 1228032; 1223036 & 1223073 | April | 2015 | 2015Q4 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2015-04-06 | N | 164.902 | N | 6 | N | N | 1.1101 | 39.4971 | 6145.7799
[7 empty] | 13849 | 13668 | 1229068 | 2015-04-07 06:29 | 2015-04-07 09:55 | 206 | 11kV | 402 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151532 Single phase DOLF : 10 Amp Replaced blown LA's at sub 72904 (sub DOLF 10A). Replaced Line Fuse 43790 (10A). Excluded OMS No. 1228135 | April | 2015 | 2015Q4 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-04-07 | N | 201 | N | 11 | N | N | 1.1101 | 39.4971 | 293.7697
[7 empty] | 14636 | 20036 | 1228129 | 2015-04-07 06:01 | 2015-04-07 10:45 | 284 | 11kV | 2863 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151528 3 fault operation B & C Phase Overcurrent Excluded OMS 1228129 | April | 2015 | 2015Q4 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2015-04-07 | N | 204.5 | N | 11 | N | N | 1.1101 | 39.4971 | 2092.196
[7 empty] | 13564 | 11424 | 1229077 | 2015-04-07 07:58 | 2015-04-07 10:55 | 177 | 11kV | 885 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 151539 3 phase DOLFs : 20 Amp please patrol Excluded OMS 1228168 | April | 2015 | 2015Q4 | 2015 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2015-04-07 | N | 177 | N | 11 | N | N | 1.1101 | 39.4971 | 646.7319
[7 empty] | 12300 | 461 | 1228131 | 2015-04-07 06:07 | 2015-04-07 13:10 | 423 | 11kV | 22975 | 55 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 151534 2 fault operations Tree on OHM near sub 52418. Excluded OMS No. 1228131 | April | 2015 | 2015Q4 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2015-04-07 | N | 417.7273 | N | 11 | N | N | 1.1101 | 39.4971 | 16789.4524
[7 empty] | 13664 | 12231 | 1228274 | 2015-04-07 10:02 | 2015-04-07 15:15 | 313 | 11kV | 313 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | No Weather Impact | N | LID 151541 A phase LL clamp broken away from DOLF Excluded OMS 1228274 | April | 2015 | 2015Q4 | 2015 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2015-04-07 | N | 313 | N | 11 | N | N | 1.1101 | 39.4971 | 228.7312
[7 empty] | 14152 | 16189 | 1228569 | 2015-04-07 14:52 | 2015-04-07 15:47 | 55 | 11kV | 33880 | 616 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Section of ZN.3154 St Ives 11kV panel 16 from RE-1622 eatsern Arterial to estent of feeder (10 DC's) tripped & locked out on OC, EF Signals:- ZE, TX3 GE Cause:- Not ascertained - section of feeder patrolled and cleared by D/Op except gully crossing ME:-1228569 | April | 2015 | 2015Q4 | 2015 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Veg | 2015-04-07 | N | 55 | N | 11 | N | N | 1.1101 | 39.4971 | 24758.5047
[7 empty] | 12662 | 3838 | 1228558 | 2015-04-07 14:48 | 2015-04-07 16:10 | 82 | 11kV | 164 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 151544 Single phase DOLF : 10 Amp Excluded OMS 1228558 | April | 2015 | 2015Q4 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2015-04-07 | N | 82 | N | 11 | N | N | 1.1101 | 39.4971 | 119.8464
[7 empty] | 13711 | 12625 | 1228442 | 2015-04-07 12:55 | 2015-04-07 17:02 | 247 | 11kV | 137361 | 1406 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn2400 Berowra Pa22 Crawford Glenview tripped reclosed tripped and locked out Relays: Cause not ascertained for outage.thunderstorm See OMS 1219864 1229867 1228462 1228463 1228442 | April | 2015 | 2015Q4 | 2015 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Veg | 2015-04-07 | N | 97.6963 | N | 11 | N | N | 1.1101 | 39.4971 | 100379.3673
[7 empty] | 13742 | 12854 | 1228583 | 2015-04-07 15:08 | 2015-04-07 17:10 | 122 | 11kV | 854 | 7 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | Wind Strong | N | LID 151545 B phase Live Line Lead B PH HV LEAD BROKEN OFF. Excluded OMS REPORT NO 1228583. | April | 2015 | 2015Q4 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-04-07 | N | 122 | N | 11 | N | N | 1.1101 | 39.4971 | 624.078
[7 empty] | 12270 | 102 | 1228485 | 2015-04-07 13:34 | 2015-04-07 18:05 | 271 | 11kV | 51504 | 319 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Light | N | LID 151543 2 fault operations Tree on mains near sub 18858. Excluded OMS 1228485 | April | 2015 | 2015Q4 | 2015 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2015-04-07 | N | 161.4545 | N | 11 | N | N | 1.1101 | 39.4971 | 37637.6041
[7 empty] | 12676 | 3942 | 1228459 | 2015-04-07 13:11 | 2015-04-07 19:00 | 349 | 11kV | 105403 | 1190 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | Zn14892 Charmhaven Pa3 "Oxford Gorokan" fdr tripped, reclosed, tripped and locked out on timed overcurrent, reclose time delay and lockout, AC prohibition, EFI Large tree brought down mains Malvina Pde See 1229515,8 Exclude 1228459,658 | April | 2015 | 2015Q4 | 2015 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Veg | 2015-04-07 | N | 88.5739 | N | 11 | N | N | 1.1101 | 39.4971 | 77025.4035
[7 empty] | 12392 | 1331 | 1228691 | 2015-04-08 02:12 | 2015-04-08 04:01 | 109 | 11kV | 106384 | 976 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 151549 burnt off tapping in section of feeder between tee to ocean pitt sub 42398 and john st sub 2143. Location could not be found OHM required to find in daylight. dq Excluded OMS 1228691 | April | 2015 | 2015Q4 | 2015 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Not Veg | 2015-04-08 | N | 109 | N | 7 | N | N | 1.1101 | 39.4971 | 77742.2894
[7 empty] | 13072 | 7404 | 1228944 | 2015-04-08 11:54 | 2015-04-08 12:35 | 41 | 11kV | 21202 | 616 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Section of ZN.3154 St Ives 11kV Panel 16 from RE-1622 Eastern Arterial (10 DC's) to extent of feeder tripped & reclosed on:- EF Signals:- Zone Earth & Tx.3 Group Earth SC LBS.62189 & LBS.62190 OC A phase & EF Cause:- Surge Arrestor @ LBS.62190 found defective - 11kV Feeder isolated from LBS.62190 to ABS.2062 tee PT.2154 - PT.2154 in LV//, links closed #11596, 11598, 11594 ME:-1229204 RS:-1229205, 1229206 Withdrawn:-1228944 Note:- See also OMS-1229202 for interruption @ 11:23 hrs | April | 2015 | 2015Q4 | 2015 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Not Veg | 2015-04-08 | N | 34.4188 | N | 7 | N | N | 1.1101 | 39.4971 | 15493.7962
[7 empty] | 13568 | 11444 | 1228989 | 2015-04-08 12:45 | 2015-04-08 12:52 | 7 | 11kV | 15309 | 2187 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 22 Tripped on Overcurrent and Earth Fault Relays C phase Timed 11kV Trip and Zone Earth Abnormal Switching:SW/A open At S5600, SW/A Open at S5160, SW/A Closed at S8018 and SW/A Open at S4526 Cause: Off duty DOp Nigel Lasheras witnessed tree branch come in contact and blow clear adjacent to PT1490 See OMS 1231687 1228989 | April | 2015 | 2015Q4 | 2015 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Veg | 2015-04-08 | N | 7 | N | 7 | N | N | 1.1101 | 39.4971 | 11187.3657
[7 empty] | 14494 | 18640 | 1228701 | 2015-04-08 06:11 | 2015-04-08 13:55 | 464 | 11kV | 928 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Wind Strong | N | LID 151550 B & C phase DOLF : 10 Amp Replaced damaged transformer. Excluded OMS 1228701 | April | 2015 | 2015Q4 | 2015 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2015-04-08 | N | 464 | N | 7 | N | N | 1.1101 | 39.4971 | 678.155
[7 empty] | 12925 | 6170 | 1228976 | 2015-04-08 12:30 | 2015-04-08 14:30 | 120 | 11kV | 4440 | 37 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 151559 isolate to remove tree branch from ohm | April | 2015 | 2015Q4 | 2015 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2015-04-08 | N | 120 | N | 7 | N | N | 1.1101 | 39.4971 | 3244.621
[7 empty] | 14304 | 17269 | 1228950 | 2015-04-08 12:05 | 2015-04-08 15:45 | 220 | 11kV | 12540 | 57 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Appears there's a intermittent h/v fault in area, Barrie St, Warrington Ave, Koola Av. affected also customer towards end of Saiala Rd lost power last night. Killara High School multiple outages over past week, Koola Ave side affected but not Wentworth Ave side (seperate supplys). Excludes OMS 122950 | April | 2015 | 2015Q4 | 2015 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Veg | 2015-04-08 | N | 220 | N | 7 | N | N | 1.1101 | 39.4971 | 9163.8621
[7 empty] | 13559 | 11381 | 1229162 | 2015-04-08 17:15 | 2015-04-08 21:55 | 280 | 11kV | 2477 | 14 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 151561 3 fault operations A & B phase Overcurrent MAIN OFF PIN AT POLE 9N-60334. Excluded OMS REPORT NO 1229162. | April | 2015 | 2015Q4 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2015-04-08 | N | 176.9286 | N | 7 | N | N | 1.1101 | 39.4971 | 1810.1185
[7 empty] | 14204 | 16525 | 1230023 | 2015-04-11 08:15 | 2015-04-11 10:16 | 121 | 11kV | 119129 | 1031 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 41 tripped on IOC and EFI with fault check Cause: private works contractor dug through 11kV cable cnr Shaftsbury and Terry Rd Eastwood Between S35110 and S8530 See OMS 1230590 1230585 1230023 1230030 | April | 2015 | 2015Q4 | 2015 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | UG | Not Veg | 2015-04-11 | N | 115.547 | N | 3 | N | N | 1.1101 | 39.4971 | 87055.9595
[7 empty] | 12269 | 97 | 1230082 | 2015-04-11 11:25 | 2015-04-11 13:30 | 125 | 11kV | 125 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151587 DOLF : 20 Amp Excluded OMS 1230082 | April | 2015 | 2015Q4 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-04-11 | N | 125 | N | 3 | N | N | 1.1101 | 39.4971 | 91.3463
[7 empty] | 13940 | 14489 | 1230147 | 2015-04-11 22:06 | 2015-04-12 02:45 | 279 | 11kV | 134624 | 1581 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn13000 Lake Munmorah Pa11 fdr tripped, reclosed and locked out Relays: Earth Fault, EFI, Reclose, Timing and Lockout Relays Signals: 11kv trip EFI's S61297 Car hit pole brought 11kv mains down near PT12722 Colongra Kimilaroo See 1230336,7 Exclude 1230147 | April | 2015 | 2015Q4 | 2015 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2015-04-11 | N | 85.1512 | N | 3 | N | N | 1.1101 | 39.4971 | 98379.2485
[7 empty] | 13003 | 6842 | 1230192 | 2015-04-12 09:48 | 2015-04-12 11:01 | 73 | 11kV | 98185 | 1345 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 21 Tripped on C hase IOC and TImed, Lockout with EFI Cause: Tree on OH mains OS 17 Manor St Hornsby See OMS 1230192 1230610 1230608 1230199 1230200 1230201 | April | 2015 | 2015Q4 | 2015 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Veg | 2015-04-12 | N | 73 | N | 5 | N | N | 1.1101 | 39.4971 | 71750.702
[7 empty] | 14492 | 18632 | 1230194 | 2015-04-12 09:51 | 2015-04-12 11:30 | 99 | 11kV | 13761 | 139 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 151590 Boom Irrigator frame hit 11kV OHM while being moved. Located at sub 47508 Brindley Park. 165 Willow tree Rd, Merriwa. Excluded OMS 1230205 | April | 2015 | 2015Q4 | 2015 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2015-04-12 | N | 99 | N | 5 | N | N | 1.1101 | 39.4971 | 10056.1329
[7 empty] | 13291 | 9039 | 1230214 | 2015-04-12 11:17 | 2015-04-12 13:00 | 103 | 11kV | 103 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151591 A phase DOLF : 20 Amp Apparently this is the fourth time in four days that this fuse has blown. Sw 50113 Faulte Detectors. C Ph OC & EF Excluded OMS 1230214 | April | 2015 | 2015Q4 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-04-12 | N | 103 | N | 5 | N | N | 1.1101 | 39.4971 | 75.2694
[7 empty] | 12713 | 4257 | 1230228 | 2015-04-12 12:35 | 2015-04-12 13:15 | 40 | 11kV | 40200 | 1005 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN.3154 St Ives 11kV Panel 19 tripped on:- Relays:- Earth fault, EFI Signals:- 11kV trip, Zone Earth, Tx.3 Group Earth, CB No.19 Open, Tx.2 Thermal Alarm Field EFI's:- S.4456, S.484, S.46581, S.4935 Field EFI that did not drop at S.1724 @ PT.1260 Narelle Ave - A phase (footpath phase) 31.5A fuse replaced Cause:-Tree branch on HV mains adjacent PT.1260 ME:-1230228 Withdrawn:-1230229, 1220235 | April | 2015 | 2015Q4 | 2015 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | OH | Veg | 2015-04-12 | N | 40 | N | 5 | N | N | 1.1101 | 39.4971 | 29376.9743
[7 empty] | 13454 | 10574 | 1230276 | 2015-04-12 23:26 | 2015-04-13 06:00 | 394 | 11kV | 21276 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151595 EF C phase to earth 128Amps Please Patroll ALSO trip & reclose 12/04/2015 0113 report 15189 | April | 2015 | 2015Q4 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2015-04-12 | N | 394 | N | 5 | N | N | 1.1101 | 39.4971 | 15547.8733
[7 empty] | 14201 | 16487 | 1230395 | 2015-04-13 09:57 | 2015-04-13 11:20 | 83 | 11kV | 36738 | 453 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At Zn3425 Castle Cove Panel 33 tripped on A phase Timed Overcurrent, Earth Fault and Fault Check With EFI Signals: 11kV Trip Cause: Cable Damaged outside 3 Deepwater Rd - UG cable damaged by contactor (from call by resident appears it could have been a plumber) See OMS 1231723 1231725 1230395 1231723 1230412 | April | 2015 | 2015Q4 | 2015 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | UG | Not Veg | 2015-04-13 | N | 81.0993 | N | 7 | N | N | 1.1101 | 39.4971 | 26847.0468
[7 empty] | 14137 | 16096 | 1230360 | 2015-04-13 09:05 | 2015-04-13 13:45 | 280 | 11kV | 280 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 151603 C Phase DOLF : 10 Amp Replace blown lightning arrestor Excluded OMS 1230360 | April | 2015 | 2015Q4 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2015-04-13 | N | 280 | N | 7 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 13132 | 7847 | 1230534 | 2015-04-13 12:54 | 2015-04-13 14:13 | 79 | 11kV | 2749 | 75 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 151605 Hand glider into LV OHM. Emergency isolation to remove Excluded oms1230534/37. | April | 2015 | 2015Q4 | 2015 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | OH | Not Veg | 2015-04-13 | N | 36.6533 | N | 7 | N | N | 1.1101 | 39.4971 | 2008.8881
[7 empty] | 14431 | 18146 | 1230485 | 2015-04-13 10:22 | 2015-04-13 16:15 | 353 | 11kV | 221286 | 1760 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN35900 Potts Hill 11kv Panel 17 "17L S1265 Hill Rd" tripped, closed, tripped & locked out on: Relays: earth fault, EFI, reclose timing relay, lockout relay Signals: Tx2 group earth, 11kv trip Field EFI's: Nil Remarks: UG fault. 11kv Cable fault from ZN35900 Potts Hill (Panel 17 "S1265 Hill Rd") to Sw/A @ S1265 Hill Rd. See DMA | April | 2015 | 2015Q4 | 2015 | ZN35900:PA17 | ZN35900:PA17 | ZN35900/000017 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-04-13 | N | 125.7307 | N | 7 | N | N | 1.1101 | 39.4971 | 161709.282
[7 empty] | 14162 | 16244 | 1230542 | 2015-04-13 13:32 | 2015-04-13 17:03 | 211 | 11kV | 9564 | 72 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 151606 2 fault operations B & C phase Earth fault Centre phase 11kV OHM down from sub 72372 to pole 8J-80112. Excluded OMS 1230542 + 1230648 | April | 2015 | 2015Q4 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2015-04-13 | N | 132.8333 | N | 7 | N | N | 1.1101 | 39.4971 | 6989.0891
[7 empty] | 13128 | 7822 | 1230678 | 2015-04-13 16:59 | 2015-04-13 17:30 | 31 | 11kV | 31 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151608 B phase DOLF : 10 Amp Dead bird found at sub Excluded OMS 1230678 | April | 2015 | 2015Q4 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-04-13 | N | 31 | N | 7 | N | N | 1.1101 | 39.4971 | 22.6539
[7 empty] | 13068 | 7367 | 1230641 | 2015-04-13 15:58 | 2015-04-13 22:07 | 369 | 11kV | 205044 | 1594 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 151609 3 fault operations A phase Earth fault Tree cut onto fdr outside 31 Bushland Road Cooranbong between poles GW-50231 & GW-50232 Excluded OMS 1230694 & 1230698 | April | 2015 | 2015Q4 | 2015 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2015-04-13 | N | 128.6349 | N | 7 | N | N | 1.1101 | 39.4971 | 149840.1074
[7 empty] | 13575 | 11509 | 1230717 | 2015-04-14 06:30 | 2015-04-14 08:20 | 110 | 11kV | 30900 | 622 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn340 Botany - Pnl.2 tripped on: Short Translay with EFI Field EFIs down @ S1420, S35616, S2966 11kV End box (Sw A) failed at S6804 Hale Underwood. see 1231160 1231158 | April | 2015 | 2015Q4 | 2015 | ZN340:PA2 | ZN340:PA45 | ZN00340/000045 | BAYSIDE | UG | Not Veg | 2015-04-14 | N | 49.6785 | N | 3 | N | N | 1.1101 | 39.4971 | 22580.8086
[7 empty] | 12310 | 529 | 1231046 | 2015-04-14 15:20 | 2015-04-14 16:32 | 72 | 11kV | 37158 | 522 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2473 North Sydney Pa11 fdr tripped on earth fault Signals: 11kv trip with EFI EFI's: Nil 11kv frontline feeder fault from Zn2473:pa11 to S6063 to CP1337 See 1231443,4 Exclude 1231046,55 | April | 2015 | 2015Q4 | 2015 | ZN2473:PA11 | ZN35400:PA68 | ZN35400/000068 | NORTH SYDNEY | UG | Not Veg | 2015-04-14 | N | 71.1839 | N | 3 | N | N | 1.1101 | 39.4971 | 27153.9704
[7 empty] | 13017 | 6923 | 1231101 | 2015-04-14 18:40 | 2015-04-14 19:45 | 65 | 11kV | 63776 | 1008 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @Sub 1287 Revesby Zn Panel #22 labelled sub 3939 tripped on C phase timed OC Fault check and EFI 11kv trip Remarks: animals/birds. Bat into mains | April | 2015 | 2015Q4 | 2015 | ZN1287:PA22 | ZN1287:PA22 | ZN01287/000022 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-04-14 | N | 63.2698 | N | 3 | N | N | 1.1101 | 39.4971 | 46605.6197
[7 empty] | 12867 | 5682 | 1231493 | 2015-04-15 20:44 | 2015-04-15 23:00 | 136 | 11kV | 78775 | 743 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | At CP863 Rosetta Arterial Tripped reclosed tripped and locked out on B phase timed O/C Abnormal Switching AB62191 Closed With AB2062 Open Cause:Insulator failed at ZB2860 C phase road side insulator disks broken See OMS 1231782 1231784 1231785 1231492 | April | 2015 | 2015Q4 | 2015 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Not Veg | 2015-04-15 | N | 106.0229 | N | 3 | N | N | 1.1101 | 39.4971 | 57566.4465
[7 empty] | 12626 | 3439 | 1231515 | 2015-04-15 22:00 | 2015-04-16 00:26 | 146 | 11kV | 438 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151639 B & C phase DOLF : 16 Amp Excluded OMS 1231515 | April | 2015 | 2015Q4 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2015-04-15 | N | 146 | N | 3 | N | N | 1.1101 | 39.4971 | 320.0775
[7 empty] | 13239 | 8659 | 1231520 | 2015-04-16 01:57 | 2015-04-16 04:16 | 139 | 11kV | 47438 | 369 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S35370 Galston Panel 2 Tripped reclosed tripped and locked out on 51A Earth Fault Timing Relay/lockout Cause not ascertained 1231818 1231820 1231819 | April | 2015 | 2015Q4 | 2015 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2015-04-16 | N | 128.5583 | N | 6 | N | N | 1.1101 | 39.4971 | 34666.2912
[7 empty] | 12619 | 3373 | 1231536 | 2015-04-16 07:18 | 2015-04-16 09:38 | 140 | 11kV | 280 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Previous Storm | N | Replace 10amp A phase HV fuse on sub 51813 Excludes OMS 1231536 | April | 2015 | 2015Q4 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-04-16 | N | 140 | N | 6 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 13563 | 11414 | 1231579 | 2015-04-16 08:27 | 2015-04-16 10:25 | 118 | 11kV | 6608 | 56 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | No Weather Impact | N | LID 151641 A phase DOLF : 40 Amp Excluded OMS 1231579; 1231580 & 1231583 | April | 2015 | 2015Q4 | 2015 | 513:48057 | 513:83497 | ZN00513/083497 | SINGLETON | UG | Not Veg | 2015-04-16 | N | 118 | N | 6 | N | N | 1.1101 | 39.4971 | 4828.9315
[7 empty] | 12680 | 3961 | 1231746 | 2015-04-16 12:31 | 2015-04-16 13:35 | 64 | 11kV | 50601 | 1039 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | ZN 9037 Miranda - Pnl 2 - Trip/reclose/trip, C phase IOC, EF, EFI, Timer, lockout, Field EFIs. Road side surge arrestor failed at PT9732. ME: 1232122. Rest Step: 1232123. Withdrawn: 1231746, 53. | April | 2015 | 2015Q4 | 2015 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Not Veg | 2015-04-16 | N | 48.7016 | N | 6 | N | N | 1.1101 | 39.4971 | 36977.7183
[7 empty] | 12681 | 3984 | 1231675 | 2015-04-16 10:00 | 2015-04-16 15:40 | 340 | 11kV | 340 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151657 A & B phase DOLF : 10 Amp | April | 2015 | 2015Q4 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2015-04-16 | N | 340 | N | 6 | N | N | 1.1101 | 39.4971 | 248.462
[7 empty] | 13501 | 10944 | 1231512 | 2015-04-15 21:57 | 2015-04-16 16:00 | 1083 | 11kV | 5415 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | Ex Zn12660 Woy Woy section of Pa14 RE45093 Wondabyne tripped and locked out on: Sensitive Earth Leakage Single Phase Overhead wire down adjacenet PT13544 Woy Woy Bambarra 4.3 | April | 2015 | 2015Q4 | 2015 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2015-04-15 | N | 1083 | N | 3 | N | N | 1.1101 | 39.4971 | 3957.1223
[7 empty] | 14532 | 18966 | 1231888 | 2015-04-16 18:24 | 2015-04-16 21:00 | 156 | 11kV | 39502 | 369 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At Zn35370 Galston Panel 2 Tripped Reclosed Tripped and Locked Out on Relays: A Phase Overcurrent, Earth Faulkt, EFI Reclose Lockout and Timing Signals: Tx1 group Earth Cause:11KV footpath Phase Surge Arrestors Found Blown See OMS 1232014 1232017 1232018 1231888 | April | 2015 | 2015Q4 | 2015 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2015-04-16 | N | 107.0515 | N | 6 | N | N | 1.1101 | 39.4971 | 28866.8965
[7 empty] | 12476 | 1959 | 1231915 | 2015-04-17 03:27 | 2015-04-17 04:53 | 86.1333 | 11kV | 25840 | 300 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | CP428 Bayfield Rd tripped and locked out tree branch found and removed from OH mains . See OMS 1231916 1231915 | April | 2015 | 2015Q4 | 2015 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2015-04-17 | N | 86.1333 | N | 4 | N | N | 1.1101 | 39.4971 | 18883.1098
[7 empty] | 13749 | 12903 | 1232177 | 2015-04-17 17:30 | 2015-04-17 19:15 | 105 | 11kV | 1365 | 13 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 151669 interrupt to install new pole to rectify Low Ground Clearence | April | 2015 | 2015Q4 | 2015 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2015-04-17 | N | 105 | N | 4 | N | N | 1.1101 | 39.4971 | 997.5017
[7 empty] | 13481 | 10778 | 1232208 | 2015-04-17 22:07 | 2015-04-17 23:10 | 63 | 11kV | 4095 | 65 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn 12640 Umina Pa13 "Patinga" fdr PT18648 Patonga Bay 63Amp middle phase fuse blew due to fuse fatigue See 1232577 GIS 1232210 Exclude 1232208 | April | 2015 | 2015Q4 | 2015 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2015-04-17 | N | 63 | N | 4 | N | N | 1.1101 | 39.4971 | 2992.5052
[7 empty] | 13023 | 6978 | 1232202 | 2015-04-17 21:05 | 2015-04-18 03:07 | 362 | 11kV | 11692 | 100 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 151672 Isolate to replace broken C phase line dolf 47027 | April | 2015 | 2015Q4 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2015-04-17 | N | 116.92 | N | 4 | N | N | 1.1101 | 39.4971 | 8544.1687
[7 empty] | 14122 | 16009 | 1232219 | 2015-04-18 06:25 | 2015-04-18 07:50 | 85 | 11kV | 85 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151675 Single phase DOLF : 10 Amp Excluded OMS 1232219 | April | 2015 | 2015Q4 | 2015 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2015-04-18 | N | 85 | N | 1 | N | N | 1.1101 | 39.4971 | 62.1155
[7 empty] | 13527 | 11104 | 1232442 | 2015-04-19 12:45 | 2015-04-19 14:05 | 80 | 11kV | 160 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 151685 C phase DOLF : 10 Amp Excluded OMS 1232442 | April | 2015 | 2015Q4 | 2015 | 814:82283 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2015-04-19 | N | 80 | N | 2 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 13832 | 13494 | 1232479 | 2015-04-19 17:14 | 2015-04-19 20:26 | 192 | 11kV | 1912.5 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind Strong | N | At PT134 Fishburn End 31.5A HDO fuse Operated Cause: HDO appears fatigues - No other damage visible See OMS 1232478 1232479 | April | 2015 | 2015Q4 | 2015 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2015-04-19 | N | 191.25 | N | 2 | N | N | 1.1101 | 39.4971 | 1397.5986
[7 empty] | 14516 | 18823 | 1242425 | 2015-04-20 08:35 | 2015-04-20 10:05 | 90 | 11kV | 4410 | 49 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 151687 BURNT OFF TAPPING AT ABS 65217. SWITCHED AROUND FAULT. | April | 2015 | 2015Q4 | 2015 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2015-04-20 | N | 90 | N | 8 | N | N | 1.1101 | 39.4971 | 3222.6979
[7 empty] | 13655 | 12163 | 1232717 | 2015-04-20 11:23 | 2015-04-20 13:20 | 117.3833 | 11kV | 1995.5167 | 17 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 151689 Tree branch on mains at pole SS-70013 | April | 2015 | 2015Q4 | 2015 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2015-04-20 | N | 117.3833 | N | 8 | N | N | 1.1101 | 39.4971 | 1458.2647
[7 empty] | 14505 | 18740 | 1232969 | 2015-04-20 15:20 | 2015-04-20 16:08 | 48.1167 | 11kV | 3223.8167 | 67 | HV | Vegetation Blow/Fall In | Vegetation | Fuse | Unplanned | Rain Wind Storm | Y | @ PT.14306 River Muloora - 11kV 50A roadside dropout operated Cause:- Tree branch on OH mains removed by D/Op ME:-1232954 Withdrawn:-1232969, 1232980 CC1: 22-"Refer to SOp" | April | 2015 | 2015Q4 | 2015 | ZN12580:PA16 | ZN12580:PA8 | ZN12580/000008 | CENTRAL COAST | OH | Veg | 2015-04-20 | Y | 48.1167 | N | 8 | N | Y | 1.1101 | 39.4971 | 2355.8701
[7 empty] | 12637 | 3574 | 1232882 | 2015-04-20 14:03 | 2015-04-20 16:10 | 127 | 11kV | 635 | 5 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | PT14550 Ilbery Sileta - A phase HDO operated Tree branch on mains Adj PT14550 | April | 2015 | 2015Q4 | 2015 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2015-04-20 | Y | 127 | N | 8 | N | Y | 1.1101 | 39.4971 | 464.0393
[7 empty] | 12896 | 5928 | 1232912 | 2015-04-20 14:29 | 2015-04-20 16:25 | 116 | 11kV | 37686 | 327 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S15014 Monave Ex Panel 14 recloser 22381 Lane Cover Walter Tripped on Overcurrent and IOC Cause: Storm - Patrolled By DOp See OMS 1255582 1255592 1232912 | April | 2015 | 2015Q4 | 2015 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Not Veg | 2015-04-20 | Y | 115.2477 | N | 8 | N | Y | 1.1101 | 39.4971 | 27539.8173
[7 empty] | 14302 | 17244 | 1233059 | 2015-04-20 16:16 | 2015-04-20 17:15 | 59 | 11kV | 79119 | 1341 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn847 Hornsby Panel 21 Tripped reclosed Tripped and Locked out on C phase IOC and OC, A phase Timing Relay and Lockout Cause: Tree branch landed on HV OH, Mains outside 15 NManor Rd Hornsby | April | 2015 | 2015Q4 | 2015 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Not Veg | 2015-04-20 | N | 59 | N | 8 | N | N | 1.1101 | 39.4971 | 57817.8316
[7 empty] | 13405 | 10188 | 1233011 | 2015-04-20 15:55 | 2015-04-20 17:17 | 82 | 11kV | 144320 | 1760 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | @S1287 Revesby Panel 15 'S47211 Eastern Tomp etc' fdr tripped, reclosed, tripped & locked out on Relays - A phase O/C, IOC Reclose, Lockout Signals - 11kv trip Remarks: tree/branch on OH mains. Branch removed by Dop adj AB1869 | April | 2015 | 2015Q4 | 2015 | ZN1287:PA15 | ZN1287:PA15 | ZN01287/000015 | CANTERBURY-BANKSTOWN | OH | Veg | 2015-04-20 | N | 82 | N | 8 | N | N | 1.1101 | 39.4971 | 105464.7993
[7 empty] | 12954 | 6480 | 1232836 | 2015-04-20 13:19 | 2015-04-20 17:50 | 271 | 11kV | 12083 | 130 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12600 Lisarow ex Pnl.2 - REC41020 Wattle Tree Rd North tripped, reclosed & locked out on: O/C trip & lockout Tree branch on mains adj LB45186 see 1257601 1257602 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2015-04-20 | Y | 92.9462 | N | 8 | N | Y | 1.1101 | 39.4971 | 8829.9
[7 empty] | 12455 | 1817 | 1242507 | 2015-04-20 17:25 | 2015-04-20 18:15 | 50 | 11kV | 100 | 2 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 151692 Conductor off pin pole BI-90014 off Rouchel Rd | April | 2015 | 2015Q4 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2015-04-20 | N | 50 | N | 8 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 12536 | 2654 | 1258255 | 2015-04-20 18:49 | 2015-04-20 19:51 | 62 | 11kV | 45818 | 739 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn14143 Somersby Pnl.17 tripped, reclosed and locked out Storm | April | 2015 | 2015Q4 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2015-04-20 | Y | 62 | N | 8 | N | Y | 1.1101 | 39.4971 | 33482.443
[7 empty] | 13425 | 10367 | 1233326 | 2015-04-20 18:33 | 2015-04-20 20:04 | 91 | 11kV | 34412 | 452 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | Y | @S1610 Homebush Bay Panel 12 'S8703 Bennelong Australia' feeder tripped on Relays - C phase O/C, EFI Signals - 11kv trip, TX1 GE No field EFIS operated Remarks: UG fault. 11kv UG fdr fault from Panel 12 @ S1610 Homebush Bay to S8703 Bennelong Australia | April | 2015 | 2015Q4 | 2015 | ZN1610:PA12 | ZN1610:PA14 | ZN01610/000014 | PARRAMATTA | UG | Not Veg | 2015-04-20 | Y | 76.1327 | N | 8 | N | Y | 1.1101 | 39.4971 | 25147.2746
[7 empty] | 13980 | 14776 | 1233269 | 2015-04-20 18:02 | 2015-04-20 20:43 | 161 | 11kV | 18193 | 113 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15013 Terrey Hills Pa6 "Cooyong Rd" tripped on ABNORMAL: RE20828 Cooyong Rd open (see interrutpion report @ 1738) HV contacted LV in Myoora Rd. See 1255619 seperate interruption report for PT15804 on pa2 | April | 2015 | 2015Q4 | 2015 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2015-04-20 | Y | 161 | N | 8 | N | Y | 1.1101 | 39.4971 | 13294.9078
[7 empty] | 12607 | 3266 | 1257479 | 2015-04-20 19:31 | 2015-04-20 21:28 | 117 | 11kV | 100620 | 860 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12600 Lisarow Pnl.13 tripped on: B & C phase O/C, L/O Tree branch on mains adj LK44897 further extended outage to Pnl13 on Tues 21/4 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2015-04-20 | Y | 117 | N | 8 | N | Y | 1.1101 | 39.4971 | 73530.1282
[7 empty] | 13236 | 8620 | 1255462 | 2015-04-20 17:35 | 2015-04-20 23:25 | 350 | 11kV | 518501 | 1774 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S9700 Kirrawee Oanel 20 The cook Glencoe North feeder tripped , reclosed tripped and locked out on b and c phase ioc with timed and reclose lockout. OH down near AB36016 after branch on feeder at PT9194 Arcadia Princes See OMS 1255462 1255472 1255469 1255473 | April | 2015 | 2015Q4 | 2015 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2015-04-20 | N | 292.2779 | N | 8 | N | N | 1.1101 | 39.4971 | 378905.2376
[7 empty] | 12336 | 799 | 1233839 | 2015-04-20 21:57 | 2015-04-21 00:15 | 138 | 11kV | 95046 | 1849 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 151698 Tree in mains at sub 15551 | April | 2015 | 2015Q4 | 2015 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Veg | 2015-04-20 | Y | 51.404 | N | 8 | N | Y | 1.1101 | 39.4971 | 69456.8134
[7 empty] | 13491 | 10878 | 1233793 | 2015-04-20 21:48 | 2015-04-21 00:31 | 163 | 11kV | 218909 | 1343 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S847 Hornsby Panel 21 Tripped on A and C phase Overcurrent, Timing and Lockout Relays Patrolled, Cleared By DOps | April | 2015 | 2015Q4 | 2015 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Veg | 2015-04-20 | N | 163 | N | 8 | N | N | 1.1101 | 39.4971 | 159972.2405
[7 empty] | 12798 | 5022 | 1267045 | 2015-04-20 23:33 | 2015-04-21 00:50 | 77 | 11kV | 78967 | 1331 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Fault beyond Wahganyah Intelliruptor. Initial feeder section restoration within 1 hour. Section of feeder beyond ELB61643 was fed abnormally from Nelsons Bay ZS after initial fault. This section then appears to have seen a sustained outage when the Nelsons bay Feeder tripped Several individual substation outages per calls Entries based on swtiching sheets, SCADA logs and operational OMS jobs. No information as to cause on switching sheets | April | 2015 | 2015Q4 | 2015 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2015-04-20 | Y | 59.3291 | N | 8 | N | Y | 1.1101 | 39.4971 | 57706.7545
[7 empty] | 13958 | 14609 | 1233077 | 2015-04-20 22:02 | 2015-04-21 01:38 | 216 | 11kV | 295596 | 1721 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZN2196 Milperra Panel 25 tripped on: "Turvey River" feeder Relays: A & B phase overcurrent Signals: 11kv trip Remarks: tree/branch on OH mains. Dop found tree branch on OH 11kv mains. | April | 2015 | 2015Q4 | 2015 | ZN2196:PA25 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2015-04-20 | N | 171.7583 | N | 8 | N | N | 1.1101 | 39.4971 | 216012.8382
[7 empty] | 12947 | 6402 | 1233948 | 2015-04-20 22:51 | 2015-04-21 01:42 | 171 | 11kV | 65682 | 389 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | At Zn167 Auburn Panel 20L "S1338 Adderley Station" tripped on: Relays: 20L trip, earth fault left, EFI left Signals: 11kv trip, Tx5 Group Earth Field EFI's: S2951, S7377, S63792, S6877 Remarks: UG fault. Suspect 11kv UG feeder fault between S63792 Aquitch Melton Sw/B & S6877 Asquith Stubbs Sw/A | April | 2015 | 2015Q4 | 2015 | ZN167:PA20 | ZN167:PA20 | ZN00167/000020 | PARRAMATTA | UG | Not Veg | 2015-04-20 | Y | 168.8483 | N | 8 | N | Y | 1.1101 | 39.4971 | 47998.4683
[7 empty] | 13498 | 10940 | 1266036 | 2015-04-20 19:19 | 2015-04-21 02:30 | 431 | 11kV | 67667 | 157 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn12630 Peats Ridge ex Panel 5 'Somersby' @IR61082 Briesees Peats Ridge 0.3 tripped and locked out on: Relays: SEF & OC Abnormal: RE46803 tripped at 19:19 Major Storm. See 1266036,9 | April | 2015 | 2015Q4 | 2015 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2015-04-20 | Y | 431 | N | 8 | N | Y | 1.1101 | 39.4971 | 49449.0478
[7 empty] | 13475 | 10737 | 1257825 | 2015-04-21 02:28 | 2015-04-21 04:06 | 98 | 11kV | 39396 | 402 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | EX ZN 14891 Wyong - Pnl 5 - REC 40082 Opened due to wires down and was restored as part of a major outage. This is an outage covering customers from the time this device opened to when the Panel opened. | April | 2015 | 2015Q4 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 98 | N | 3 | N | Y | 1.1101 | 39.4971 | 28789.4348
[7 empty] | 13535 | 11158 | 1234165 | 2015-04-21 01:01 | 2015-04-21 05:21 | 260 | 11kV | 74360 | 286 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | No LID report Branch on mains Thomas St | April | 2015 | 2015Q4 | 2015 | 502:48001 | 502:48001 | ZN00502/048001 | MAITLAND | OH | Veg | 2015-04-21 | Y | 260 | N | 3 | N | Y | 1.1101 | 39.4971 | 54340.0948
[7 empty] | 13101 | 7662 | 1234329 | 2015-04-21 02:21 | 2015-04-21 07:24 | 303 | 11kV | 63630 | 210 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN.12610 Long Jetty 11kV Panel 5 feeder tripped and locked out on:- Relays:- B & C phase IOC, EFI, EFcheck, Reclose timing, Lockout Signals:- 11kV trip Cause:- STORM, tree branch removed by D/Op from 11kV on tee S.12000 ME:-1234329 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA5 | ZN12610:PA5 | ZN12610/000005 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 303 | N | 3 | N | Y | 1.1101 | 39.4971 | 46498.9272
[7 empty] | 13311 | 9247 | 1259439 | 2015-04-21 05:21 | 2015-04-21 07:33 | 132 | 11kV | 107844 | 817 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | EX ZN 14891 Wyong - Pnl 16 - REC40118 Murrawal Kilpa 0.2 Trip/reclose/trip, OC. Major storm in the area. | April | 2015 | 2015Q4 | 2015 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 132 | N | 3 | N | Y | 1.1101 | 39.4971 | 78809.2143
[7 empty] | 13090 | 7568 | 1234508 | 2015-04-21 03:39 | 2015-04-21 08:06 | 267 | 11kV | 193041 | 723 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15002 Narrabeen Pa6 fdr has tripped Signals: 11kv Relays: Timed overcurrent C phase, Timer, Lockout Tree into mains near LK24808. THen bond off at UGOH near S49277. Tree branch brought down OH See 1256291,4 exclude 1234508 | April | 2015 | 2015Q4 | 2015 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 267 | N | 3 | N | Y | 1.1101 | 39.4971 | 141068.6691
[7 empty] | 12903 | 5997 | 1234657 | 2015-04-21 03:39 | 2015-04-21 08:07 | 268 | 33kV Distribution | 8732 | 33 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled from emergency switching sheet mains down pole KT-70184 and tapping KT-72440 mains down span to ABS 46803 - pole KT-40007 trip of both 80500 & 80507 | April | 2015 | 2015Q4 | 2015 |  |  |  | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 264.6061 | N | 3 | N | Y | 1.1101 | 39.4971 | 6381.088
[7 empty] | 14125 | 16030 | 1234913 | 2015-04-21 06:29 | 2015-04-21 09:00 | 151 | 11kV | 111891 | 741 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Ex ZN 195 Pymble - Pnl 30 - REC 46113 Trip/reclose/trip, OC trip. Tree branch on OH mains in Beaumont Rd. | April | 2015 | 2015Q4 | 2015 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2015-04-21 | Y | 151 | N | 3 | N | Y | 1.1101 | 39.4971 | 81766.6426
[7 empty] | 14202 | 16490 | 1254953 | 2015-04-21 08:15 | 2015-04-21 09:14 | 59 | 11kV | 86317 | 1463 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | At Zn10991 Blakehurst Panel 1 trpped Reclosed Tripped and locked out on A Phase O/C and IOC, Timinf relay and Lockout Signals: 11kV trip Cause: Tree branch on OH mains Abnormal Switching: Defective Section of Feeder USL30493 to Normally Open AB31021 See OMS 1254953 1235349 | April | 2015 | 2015Q4 | 2015 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2015-04-21 | Y | 59 | N | 3 | N | Y | 1.1101 | 39.4971 | 63077.9177
[7 empty] | 13250 | 8761 | 1256724 | 2015-04-21 05:40 | 2015-04-21 09:35 | 235 | 11kV | 42300 | 180 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Wind Storm | Y | At Zn35370 Galston Panel 8 CP554 Arcadia Rosscommon Has tripped on IOC and OC trip Cause: Tree on mains Abnormal Switching CP559 Open CP2063 Closed (Implied By outage 12565101,1256514,1256517) | April | 2015 | 2015Q4 | 2015 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2015-04-21 | Y | 235 | N | 3 | N | Y | 1.1101 | 39.4971 | 30911.5924
[7 empty] | 13973 | 14708 | 1261108 | 2015-04-21 08:32 | 2015-04-21 09:45 | 73 | 11kV | 47450 | 650 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | Ex Zn12610 Long Jetty section of Pa10 IR61729 The Entrance Cresthaven tripped & locked out on overcurrent Brnach removed from 11kv OH by DOp near S14803 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 73 | N | 3 | N | Y | 1.1101 | 39.4971 | 34675.0605
[7 empty] | 13964 | 14661 | 1234302 | 2015-04-21 02:08 | 2015-04-21 10:20 | 492 | 11kV | 87298 | 877 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn10996 Rockdlae Panel 10 Tripped Reclosed Tripped and locked out on Relays: A phase OC and A phase IOC, timing and lockout Signals: 11kV trip Cause: Large Palm tree in HV mains between S1019 and LB30119 tee S10624 near UGOH to S10109. See OMS 1255056 1255059 1255063 1234685 1234302 | April | 2015 | 2015Q4 | 2015 | ZN10996:PA10 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Veg | 2015-04-21 | Y | 99.5416 | N | 3 | N | Y | 1.1101 | 39.4971 | 63794.8035
[7 empty] | 13585 | 11586 | 1257803 | 2015-04-21 08:19 | 2015-04-21 10:24 | 125 | 11kV | 167750 | 1342 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | No LID report Compiled from emergency switching sheets | April | 2015 | 2015Q4 | 2015 | 216:10729 | 216:10729 | ZN00216/010729 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 125 | N | 3 | N | Y | 1.1101 | 39.4971 | 122586.7522
[7 empty] | 14468 | 18477 | 1254677 | 2015-04-21 09:29 | 2015-04-21 11:27 | 118 | 11kV | 178509 | 1605 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | S2310 Punchbowl Panel 40 "Berring Avenue" tripped Relays - A phase overcurrent, earth fault, EFI, Signals - 11kv trip, Zone earth, Tx Group Earth EFI's: S1039, S3543, S1094, S2027, S3529 Remarks: UG fault. Underground fault from S3529 Myers St Sw/B to S3831 Legge St Sw/A. Requires Hayzemers extension. sw/tag at S7745 | April | 2015 | 2015Q4 | 2015 | ZN2310:PA40 | ZN2310:PA19 | ZN02310/000019 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-04-21 | N | 111.2206 | N | 3 | N | N | 1.1101 | 39.4971 | 130449.1121
[7 empty] | 13555 | 11361 | 1235092 | 2015-04-21 07:10 | 2015-04-21 11:54 | 284 | 11kV | 377152 | 1328 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN.12610 Long Jetty 11kV Panel 25 feeder tripped and locked out on:- Relays:- A, B phase O/C, reclose timing, lockout, group 3 EF Signals:- 11kV trip Cause:- STORM, tree branch on OH mains removed by D/Op in Nolfolk near Tuggerah Pde ME:-1235092 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 284 | N | 3 | N | Y | 1.1101 | 39.4971 | 275611.5575
[7 empty] | 12965 | 6532 | 1237097 | 2015-04-21 11:53 | 2015-04-21 12:22 | 29 | 11kV | 4988 | 172 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Wind Storm | Y | Ex Zn80 Chatswood section of Pa32 S4221 Helen Burley HV fuse blown. Fuse failure. Unable to isolate due to defective RMI at S5278 and also S4221 is a L&C fuse switch. Restored via LV parallel. Also at same time S4221 Helen Burley Dist 3 "Helen St W/S UG & Burley St UG & ... " ABC phase fuses blown due to underground fault in Ralston Rd | April | 2015 | 2015Q4 | 2015 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | OH | Not Veg | 2015-04-21 | N | 29 | N | 3 | N | N | 1.1101 | 39.4971 | 3645.0833
[7 empty] | 13826 | 13459 | 1236226 | 2015-04-21 10:05 | 2015-04-21 12:24 | 139 | 11kV | 121528 | 904 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | Y | At S10994 Mortdale Panel 19 Tripped on SEF Signals: 11kV Trip Cause: HV bond burnt of between CP31183 and UGOH to S10954 See INS 125539 1255140 1236226 | April | 2015 | 2015Q4 | 2015 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2015-04-21 | Y | 134.4336 | N | 3 | N | Y | 1.1101 | 39.4971 | 88809.0779
[7 empty] | 13397 | 10136 | 1234536 | 2015-04-21 03:54 | 2015-04-21 12:38 | 524 | 11kV | 566444 | 1081 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | @S14892 Charmhaven Panel 13 "S11408 Stanley Phillis Etc" fdr tripped & Locked out on Relays: A & B phase, O/C Remarks: tree/branch on OH mains. Branch removed by dop nr ugoh to S14725 | April | 2015 | 2015Q4 | 2015 | ZN14892:PA13 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 524 | N | 3 | N | Y | 1.1101 | 39.4971 | 413940.5679
[7 empty] | 12260 | 39 | 1235064 | 2015-04-21 02:43 | 2015-04-21 12:40 | 597 | 11kV | 1014086 | 2271 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | No LID report compiled from Emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Veg | 2015-04-21 | Y | 446.5372 | N | 3 | N | Y | 1.1101 | 39.4971 | 741064.1383
[7 empty] | 12597 | 3210 | 1234156 | 2015-04-21 01:04 | 2015-04-21 13:33 | 749.6333 | 11kV | 1300613.8333 | 1735 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12600 Lisarow Pnl.3 tripped on : B phase IOC, L/O Weather related - patrolled and restored - tripped again @ 16:23 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 749.6333 | N | 3 | N | Y | 1.1101 | 39.4971 | 950450.2278
[7 empty] | 13278 | 8968 | 1236506 | 2015-04-21 10:37 | 2015-04-21 13:41 | 184 | 11kV | 488854 | 3335 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | At Zn9245 Engadine Panel 15 Tripped on 11 KV trip, Tx3 Group Earth and Zone Earth Relays: C Phase O/C and Lockout Relays Abnrormal Swicthing: S9818 SW/B closed and Ab35813 Ope, _Earlier Fault on Pa20 Kirrawee Cause:Suspect UG fault between UGOH adjacent AB35746 and S9460 Dobell Rd See OMS 1253953 1253960 1236506 | April | 2015 | 2015Q4 | 2015 | ZN9245:PA15 | ZN9245:PA10 | ZN09245/000010 | SUTHERLAND | UG | Not Veg | 2015-04-21 | Y | 146.5829 | N | 3 | N | Y | 1.1101 | 39.4971 | 357240.0844
[7 empty] | 14427 | 18122 | 1234575 | 2015-04-21 04:09 | 2015-04-21 14:20 | 611 | 11kV | 241625 | 955 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | AT Zn4545 Meadowbank, ex Panel 40, Rec 1437 Shaftsbury Morven has tripped. Relays: IOC trip. OC trip Remarks: tree/branch brought down OH. See OMS | April | 2015 | 2015Q4 | 2015 | ZN4545:PA40 | ZN4545:PA40 | ZN04545/000040 | RYDE | OH | Veg | 2015-04-21 | Y | 253.0105 | N | 3 | N | Y | 1.1101 | 39.4971 | 176572.4233
[7 empty] | 14622 | 19900 | 1238525 | 2015-04-21 07:42 | 2015-04-21 14:22 | 400 | 11kV | 760866 | 1932 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | No LID report Tree pulled mains down to ground at ABS 40327 | April | 2015 | 2015Q4 | 2015 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2015-04-21 | Y | 393.823 | N | 3 | N | Y | 1.1101 | 39.4971 | 556018.4311
[7 empty] | 14300 | 17221 | 1265496 | 2015-04-21 01:44 | 2015-04-21 14:30 | 766 | 11kV | 729998 | 953 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn12690 Berkeley Vale Pa 6 fdr tripped 7 locked out on Relays: L1, L2, trip, auto reclose, lockout, EFI Major Storm. See 1265496 exclude 1234239 | April | 2015 | 2015Q4 | 2015 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 766 | N | 3 | N | Y | 1.1101 | 39.4971 | 533461.0071
[7 empty] | 13465 | 10663 | 1236151 | 2015-04-21 06:28 | 2015-04-21 14:39 | 491.3833 | 11kV | 140535.6333 | 286 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | no further information supplied from control room start and end time and device left as operated by control room | April | 2015 | 2015Q4 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2015-04-21 | Y | 491.3833 | N | 3 | N | Y | 1.1101 | 39.4971 | 102699.2957
[7 empty] | 12502 | 2295 | 1237123 | 2015-04-21 11:56 | 2015-04-21 15:02 | 186 | 11kV | 233971 | 1459 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn2400 Berowra Pa21 "yallambee Pacific" tripped on Relays: SEL Signals: 11kv trip Tree Branch on Overhead Mains See 1257026,9,31 exclude 1237123,497 | April | 2015 | 2015Q4 | 2015 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Veg | 2015-04-21 | Y | 160.3639 | N | 3 | N | Y | 1.1101 | 39.4971 | 170979.1058
[7 empty] | 13022 | 6957 | 1234713 | 2015-04-21 03:11 | 2015-04-21 15:10 | 719 | 11kV | 69024 | 96 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled via emergency switching sheets Excludes OMS 1234713 + 1241325 | April | 2015 | 2015Q4 | 2015 | 224:80335 | 224:80335 | ZN00224/080335 | LAKE MACQUARIE | Unknown | Unknown | 2015-04-21 | Y | 719 | Y | 3 | N | Y | 1.1101 | 39.4971 | 50440.7033
[7 empty] | 12976 | 6610 | 1234439 | 2015-04-21 02:37 | 2015-04-21 15:41 | 784 | 11kV | 81536 | 104 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | Y | Rec 45061 Chain vally bay Mulloway Tripped reclosed tripped and locked out on: Relays: overcurrent Ex Panel 7 "Summerland Point" feeder @ Zn13000 Lake Munmorah Abnormal: AB43825 Opened, LB 40172 Closed, AB40428 Opened, AB 44265 Closed Remarks: weather realated. HV down near LK41687 | April | 2015 | 2015Q4 | 2015 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 784 | N | 3 | N | Y | 1.1101 | 39.4971 | 59584.1039
[7 empty] | 13519 | 11076 | 1234658 | 2015-04-21 04:47 | 2015-04-21 15:58 | 671 | 11kV | 49654 | 74 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Ex ZN 14891 Wyong - Pnl 8 - REC 48425 Trip/reclose/trip, OC and IOC. Tree on HV mains during major storm in the area. | April | 2015 | 2015Q4 | 2015 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 671 | N | 3 | N | Y | 1.1101 | 39.4971 | 36285.6787
[7 empty] | 14486 | 18566 | 1233768 | 2015-04-20 21:38 | 2015-04-21 16:15 | 1117 | 11kV | 1686249 | 1513 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN.12580 Erina 11kV Panel 10 tripped on:- Relays:- A phase IOC & Timed, EFI Field EFI's:- S.13682, S.12866, S.14189, S.18183 Cause:- Tree on HV mains just beyond S.18183 ME:-1257222 RS:-1257226 Withdrawn:-1234448, 1233768 | April | 2015 | 2015Q4 | 2015 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Veg | 2015-04-20 | Y | 1114.5069 | N | 8 | N | Y | 1.1101 | 39.4971 | 1232261.0333
[7 empty] | 13334 | 9603 | 1257728 | 2015-04-21 15:35 | 2015-04-21 16:43 | 68 | 11kV | 16508 | 274 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12600 Lisarow Pnl.12 tripped on: A phase IOC + timed O/C, EFI, L/O 11kV OH down between S180778 and S18011 See 1257728 1257729 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA12 | ZN12600:PA12 | ZN12600/000012 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 60.2482 | N | 3 | N | Y | 1.1101 | 39.4971 | 12063.5595
[7 empty] | 13253 | 8788 | 1234385 | 2015-04-21 01:48 | 2015-04-21 17:00 | 912 | 11kV | 70452 | 86 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn35370 Galston ex Panel 8 Reclsoer CP559 Cobar Rd Tripped Abnormal Switching AB2063 Open and Defective, CP3343 Closed. See OMS 1234385/48691/47843/42556 1256510/1256514/1256517 | April | 2015 | 2015Q4 | 2015 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2015-04-21 | Y | 819.2093 | Y | 3 | N | Y | 1.1101 | 39.4971 | 51484.2436
[7 empty] | 12537 | 2660 | 1238746 | 2015-04-21 08:12 | 2015-04-21 17:24 | 552 | 11kV | 135240 | 245 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S847 Hornsby Panel 45 CP421 Crosslands has tripped Relays: Overload Trip with lockout Cause: Storm | April | 2015 | 2015Q4 | 2015 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2015-04-21 | Y | 552 | Y | 3 | N | Y | 1.1101 | 39.4971 | 98829.4031
[7 empty] | 13247 | 8708 | 1234104 | 2015-04-21 00:32 | 2015-04-21 17:35 | 1023 | 11kV | 170419 | 937 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn3425 Castle Cove - Pnl.44 tripped on: C phase timed O/C Tree touching HV in The High Tor o/s #13 see 1256635 1256637 1256638 | April | 2015 | 2015Q4 | 2015 | ZN3425:PA44 | ZN3425:PA44 | ZN03425/000044 | WILLOUGHBY | OH | Veg | 2015-04-21 | Y | 181.8773 | N | 3 | N | Y | 1.1101 | 39.4971 | 124537.1787
[7 empty] | 13583 | 11571 | 1239167 | 2015-04-21 16:54 | 2015-04-21 17:37 | 42.9 | 11kV | 56499.3 | 1317 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | ZN 2400 Berowra - Pnl 22 - Trip/reclose/trip, All phases Timed OC, lockout. Tree branch on mains near PT 2211 during major storm in the area. | April | 2015 | 2015Q4 | 2015 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Veg | 2015-04-21 | Y | 42.9 | N | 3 | N | Y | 1.1101 | 39.4971 | 41288.022
[7 empty] | 13007 | 6862 | 1276489 | 2015-04-21 17:34 | 2015-04-21 17:41 | 7 | 11kV | 8148 | 1164 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor ABC | Unplanned | Rain Wind Storm | Y | No information in blue forms Additional entry based off SCADA for Pa8 at Noraville. Note PT 61844 was already off supply at this time. | April | 2015 | 2015Q4 | 2015 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 7 | N | 3 | N | Y | 1.1101 | 39.4971 | 5954.3181
[7 empty] | 14119 | 15996 | 1254895 | 2015-04-21 12:31 | 2015-04-21 18:16 | 345 | 11kV | 179151 | 2359 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S10991 Blakehurst Panel 12 the King Georges rd Feeder Tripped Reclosed Tripped and Locked out on C phase IOC and Timed O/C, Lockout and Timing Relay. Tree Branch on OH mains Near HV link 30534 Abnormal Switching: SW/B Closed At S10846 Panel 13 Open - Defective AB30508 See OMS 1254895 1254902 1254901 | April | 2015 | 2015Q4 | 2015 | ZN10991:PA12 | ZN10991:PA12 | ZN10991/000012 | GEORGES RIVER | OH | Veg | 2015-04-21 | Y | 75.9436 | N | 3 | N | Y | 1.1101 | 39.4971 | 130918.2667
[7 empty] | 12371 | 1072 | 1279679 | 2015-04-21 16:41 | 2015-04-21 18:42 | 121 | 11kV | 41140 | 340 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | NO LID report, Compiled via SCADA trends, emergency switching sheets and OMS jobs Feeder load carried by 35198 to restore customers | April | 2015 | 2015Q4 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2015-04-21 | Y | 121 | N | 3 | N | Y | 1.1101 | 39.4971 | 30063.8986
[7 empty] | 13627 | 11930 | 1233271 | 2015-04-21 08:47 | 2015-04-21 18:50 | 603 | 11kV | 269497 | 1162 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | ZN 1673 Turramurra - Pnl 18 - Trip/reclose/trip, A&B phase IOC, lock out. Tree branch on OH mains near AB 1840 durning major storm in the area. ME: 1256782. Rest Steps: 1256785, 6. Withdrawn: 1235576. | April | 2015 | 2015Q4 | 2015 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Veg | 2015-04-21 | Y | 231.9251 | N | 3 | N | Y | 1.1101 | 39.4971 | 196940.4588
[7 empty] | 13149 | 7986 | 1256753 | 2015-04-21 14:42 | 2015-04-21 19:35 | 293 | 11kV | 47481 | 369 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S35370 Galston Panel 2 Tripped Reclosed Tripped and Locked out on Relays: A and B phase OC Cause: Tree branches on OH mains See OMS 1256753 1256754 1234986 | April | 2015 | 2015Q4 | 2015 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2015-04-21 | Y | 128.6748 | N | 3 | N | Y | 1.1101 | 39.4971 | 34697.7143
[7 empty] | 13413 | 10245 | 1240099 | 2015-04-21 02:42 | 2015-04-21 19:45 | 1023 | 11kV | 18414 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor ABC | Unplanned | Rain Wind Storm | Y | At Zn35370 Galston Panel 8 CP560 Peeble Nollands from LB47745 Cause: Tree branch brought down 11kV See OMS1256596 1240099 | April | 2015 | 2015Q4 | 2015 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2015-04-21 | Y | 1023 | Y | 3 | N | Y | 1.1101 | 39.4971 | 13456.4081
[7 empty] | 14667 | 20261 | 1239482 | 2015-04-21 17:39 | 2015-04-21 19:47 | 128 | 11kV | 172544 | 1348 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn15001 Brookvale Pa6 fdr has tripped Signals: 11kv Relays: 50T A&C ABNORMAL: S16245/SwB closed, S16821/SwB Open Cause: Major Event Storm. Mains to Patrol See 1255699 exclude 1239482 | April | 2015 | 2015Q4 | 2015 | ZN15001:PA6 | ZN15001:PA6 | ZN15001/000006 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 128 | N | 3 | N | Y | 1.1101 | 39.4971 | 126090.066
[7 empty] | 13103 | 7677 | 1234141 | 2015-04-21 00:43 | 2015-04-21 19:51 | 1148 | 11kV | 1897644 | 1653 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12640 Umina Pa10 "Mcevoy Bapaume" tripped on Aphase instantaneous overcurrent, timing, lockout Tree/Branch on mains. repaired by overhead crew. Major Event Storm | April | 2015 | 2015Q4 | 2015 | ZN12640:PA10 | ZN12640:PA10 | ZN12640/000010 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 1148 | N | 3 | N | Y | 1.1101 | 39.4971 | 1386742.2642
[7 empty] | 12971 | 6580 | 1257836 | 2015-04-21 15:00 | 2015-04-21 20:10 | 310 | 11kV | 13820 | 60 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | NO LID report compiled from emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-04-21 | N | 230.3333 | N | 3 | N | N | 1.1101 | 39.4971 | 10099.2484
[7 empty] | 12286 | 313 | 1238568 | 2015-04-21 12:04 | 2015-04-21 20:21 | 497 | 11kV | 112137 | 293 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled via emergency switching sheets Includes OMS 1262430/31/34/36/37/39 | April | 2015 | 2015Q4 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2015-04-21 | Y | 382.7201 | N | 3 | N | Y | 1.1101 | 39.4971 | 81946.4121
[7 empty] | 13644 | 12083 | 1239580 | 2015-04-21 18:02 | 2015-04-21 20:25 | 143 | 11kV | 5291 | 37 | HV | Vegetation Blow/Fall In | Vegetation | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | Y | At Zn 1193 Lindfield, ex Panel 12, Rec 863 Rosetta Arteria has tripped Relays: IOC trip, OC trip Abnormal: AB 2860 open due to defective Remarks: storm, tree on mains | April | 2015 | 2015Q4 | 2015 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Veg | 2015-04-21 | Y | 143 | N | 3 | N | Y | 1.1101 | 39.4971 | 3866.5067
[7 empty] | 14165 | 16260 | 1239504 | 2015-04-21 17:43 | 2015-04-21 21:00 | 197 | 11kV | 226120 | 1448 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN.15005 Belrose 11kV Panel 12 tripped on:- Relays:- B phase timed OC, FC timer LO Signals:- 11kV Trip EFI's:- Nil Cause:- STORM, Tree against mains in Forest Way near Belrose Zone. Located between ZN.15005 Belrose Panel 12 to ABS.25739 to ABS.21063 to S16533 ME:-1255549 RS:-1255556 Withdrawn:-1239504 | April | 2015 | 2015Q4 | 2015 | ZN15005:PA12 | ZN15005:PA12 | ZN15005/000012 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 156.1602 | N | 3 | N | Y | 1.1101 | 39.4971 | 165241.8266
[7 empty] | 12833 | 5347 | 1236329 | 2015-04-21 10:19 | 2015-04-21 21:00 | 641 | 11kV | 73685 | 289 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Wind Storm | Y | S35900 Potts Hill Panel 6 "Lewis St" tripped, reclosed, tripped and locked out Relays - A and B phase overcurrent, EFI Signals: 11kv trip EFI's: S3860 Remarks: pole defective/failure. Sydney Trains 33kv pole fell and tangled with 11kv mains either side of S62911 Eucalyptus Church | April | 2015 | 2015Q4 | 2015 | ZN35900:PA6 | ZN35900:PA6 | ZN35900/000006 | CUMBERLAND | OH | Not Veg | 2015-04-21 | Y | 254.9654 | N | 3 | N | Y | 1.1101 | 39.4971 | 53846.8247
[7 empty] | 14350 | 17553 | 1235214 | 2015-04-21 07:53 | 2015-04-21 21:25 | 812 | 11kV | 1284584 | 1582 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15009 Manly Pa7 has tripped Signals: 11kv trip Relays: Overcurrent, Timer, Lockout Tree on Mains near 21 Kangaroo st near s15095 Kangaroo st 41. Located between Zn15009 Pa7, S16452:A, LK23505 & S16923:SwA tee S15905 Major Event Storm | April | 2015 | 2015Q4 | 2015 | ZN15009:PA7 | ZN15009:PA7 | ZN15009/000007 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 812 | N | 3 | N | Y | 1.1101 | 39.4971 | 938736.0984
[7 empty] | 12370 | 1069 | 1276476 | 2015-04-21 17:08 | 2015-04-21 21:25 | 257 | 11kV | 160625 | 625 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Entered based off SCADA records and feeder loads. No blue form. Section beyond CP62773 was off due to prior fault at this time | April | 2015 | 2015Q4 | 2015 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Not Veg | 2015-04-21 | Y | 257 | N | 3 | N | Y | 1.1101 | 39.4971 | 117380.0124
[7 empty] | 12576 | 3054 | 1235854 | 2015-04-21 05:41 | 2015-04-21 21:27 | 946 | 11kV | 696236 | 1352 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report compiled from emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 528:83014 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Not Veg | 2015-04-21 | Y | 514.9675 | N | 3 | N | Y | 1.1101 | 39.4971 | 508788.7333
[7 empty] | 14045 | 15395 | 1260913 | 2015-04-21 18:25 | 2015-04-21 21:35 | 190 | 11kV | 274496 | 2122 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | ZN 9245 Engadine - Pnl 13 - Trip/reclose/trip, C phase OC and EF. Branch on 11kV OH mains between AB 35951 and UGOH. ME: 1260913. Rest Step: 1260914. Withdrawn: 1239784. | April | 2015 | 2015Q4 | 2015 | ZN9245:PA13 | ZN9245:PA21 | ZN09245/000021 | SUTHERLAND | OH | Veg | 2015-04-21 | Y | 129.3572 | N | 3 | N | Y | 1.1101 | 39.4971 | 200593.5805
[7 empty] | 13406 | 10190 | 1234133 | 2015-04-21 00:50 | 2015-04-21 21:53 | 1263.3667 | 11kV | 1340432.0333 | 1061 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | Y | ZN.15002 Narrabeen 11kV Panel 8 feeder tripped on C phase overcurrent Cause:- Storm caused burnt bonds at UGOH beyond S.15366 to ABS.26122 ME:-1234133 | April | 2015 | 2015Q4 | 2015 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | OH | Not Veg | 2015-04-21 | Y | 1263.3667 | N | 3 | N | Y | 1.1101 | 39.4971 | 979548.1939
[7 empty] | 13536 | 11162 | 1234637 | 2015-04-21 04:29 | 2015-04-21 21:55 | 1046 | 11kV | 2195564 | 2149 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn12640 Umina 11kv Pa19 fdr tripped Relays: A & B phase IOC, EFI ABNORMAL: DMA S14488 SwB closed S18026 SwA Open Dop patrolled and supply restored. Major Storm Event See 1257611,2,3 exclude 1234637 | April | 2015 | 2015Q4 | 2015 | ZN12640:PA19 | ZN12640:PA14 | ZN12640/000014 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 1021.6678 | N | 3 | N | Y | 1.1101 | 39.4971 | 1604453.413
[7 empty] | 13831 | 13492 | 1239821 | 2015-04-21 18:55 | 2015-04-22 | 305 | 11kV | 131701 | 965 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn847 Hornsby Panel 44 tripped reclosed tripped and locked out on SEF, TX# Group Earth and Zone Earth Cause: Large Tree brough down 11 KkV above AB1305 on Pa44 Side. See OMS 1255874 1255877 1239821 | April | 2015 | 2015Q4 | 2015 | ZN847:PA44 | ZN847:PA44 | ZN00847/000044 | HORNSBY | OH | Veg | 2015-04-21 | Y | 136.4777 | N | 3 | N | Y | 1.1101 | 39.4971 | 96243.2063
[7 empty] | 13595 | 11665 | 1240509 | 2015-04-21 22:33 | 2015-04-22 01:06 | 153 | 11kV | 405297 | 2649 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn10999 Kogarah Pa12 "Queen Vic Washington etc" tripped, reclosed, tripped on: A & B phase IOC, EFI, E/F check, Lockout Branch on mains near PT10367 | April | 2015 | 2015Q4 | 2015 | ZN10999:PA12 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | OH | Veg | 2015-04-21 | Y | 153 | N | 3 | N | Y | 1.1101 | 39.4971 | 296179.0934
[7 empty] | 13889 | 13987 | 1240514 | 2015-04-21 22:43 | 2015-04-22 01:10 | 147 | 11kV | 88470 | 1220 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S9700 Kirrawee Oanel 17 Tripped Reclosed Tripped and locked out on C phase IOC and Timed O/C with Lockout Cause: tree on mains Near PT9543 Cobargo Rd See OMS 1255409 1255414 1255417 1240514 | April | 2015 | 2015Q4 | 2015 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Veg | 2015-04-21 | Y | 72.5164 | N | 3 | N | Y | 1.1101 | 39.4971 | 64651.2666
[7 empty] | 13305 | 9172 | 1235958 | 2015-04-21 05:07 | 2015-04-22 02:50 | 1303 | 11kV | 1951522 | 1587 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | Y | NO LID Report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | Unknown | Unknown | 2015-04-21 | Y | 1229.6925 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1426114.7174
[7 empty] | 14200 | 16486 | 1255099 | 2015-04-21 23:12 | 2015-04-22 03:20 | 248 | 11kV | 644552 | 2599 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn15006 Harbord Pa9L DOp patrolled and found no cause. Suspect Weather. Major Event Storm | April | 2015 | 2015Q4 | 2015 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 248 | N | 3 | N | Y | 1.1101 | 39.4971 | 471019.5905
[7 empty] | 12608 | 3267 | 1276477 | 2015-04-21 23:12 | 2015-04-22 03:26 | 254 | 11kV | 158750 | 625 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Entered based off SCADA records and feeder loads. No blue form. Section beyond CP62773 was off due to prior fault at this time. | April | 2015 | 2015Q4 | 2015 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Not Veg | 2015-04-21 | Y | 254 | N | 3 | N | Y | 1.1101 | 39.4971 | 116009.8177
[7 empty] | 14650 | 20131 | 1243079 | 2015-04-21 05:31 | 2015-04-22 04:00 | 1349 | 11kV | 597232 | 589 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | No LID Compiled from emergency switching sheet. | April | 2015 | 2015Q4 | 2015 | 206:34438 | 206:34438 | ZN00206/034438 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 1013.9762 | Y | 3 | N | Y | 1.1101 | 39.4971 | 436439.5302
[7 empty] | 13979 | 14753 | 1240727 | 2015-04-22 00:50 | 2015-04-22 04:39 | 229 | 11kV | 141174 | 620 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | At Zn8000 Marquarie Park 11kv Panel 38 "S8180" tripped on: Relays: Earth fault (51N), EFI, Fault Check, Fault Check (Tx3) Signals: 11kv trip Field EFI's operated: S8180, S5758, S6015, S4431 (S4431 was incorrect operation) Remarks: UG fault. Suspect UG 11kv fault between S6015/Sw: B & S4431/SW:A. Ex Panel 38 ZN8000 Macquarie | April | 2015 | 2015Q4 | 2015 | ZN8000:PA38 | ZN8000:PA38 | ZN08000/000038 | RYDE | UG | Not Veg | 2015-04-22 | N | 227.7 | N | 10 | N | N | 1.1101 | 39.4971 | 103165.7953
[7 empty] | 13376 | 9946 | 1274962 | 2015-04-21 03:41 | 2015-04-22 07:58 | 1697 | 11kV | 1961732 | 1156 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | NO LID report Compiled from emergency switching sheets and scada data | April | 2015 | 2015Q4 | 2015 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2015-04-21 | Y | 1697 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1433575.8843
[7 empty] | 12683 | 4013 | 1254766 | 2015-04-22 05:52 | 2015-04-22 08:04 | 132 | 11kV | 233960 | 1962 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN.15011 Beacon Hill 11kV Panel 6 tripped, reclosed, tripped and locked out on:- Relays:- A phase IOC & Timed OC, Reclose, Timed, Tx2 Fault Check Signals:- 11kV Trip EFI's:- Nil Cause:- Tree/branch on OH mains at 11kV UGOH to S.15311 ME:-1254766 Withdrawn:-1240813, 1241228 | April | 2015 | 2015Q4 | 2015 | ZN15011:PA6 | ZN15011:PA4 | ZN15011/000004 | NORTHERN BEACHES | OH | Veg | 2015-04-22 | Y | 119.2457 | N | 10 | N | Y | 1.1101 | 39.4971 | 170971.0673
[7 empty] | 13065 | 7344 | 1240743 | 2015-04-22 03:57 | 2015-04-22 08:10 | 253 | 11kV | 398269 | 1725 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | At S2196 Milperra - 11kv Panel 25 "Turvey River" tripped Relays: A & B phase timed O/C Signals: 11kv trip, No.3 Group earth, Zone earth EFI's: Nil Remarks: Storm. Feeder patrolled by DOp. All clear | April | 2015 | 2015Q4 | 2015 | ZN2196:PA25 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2015-04-22 | N | 230.8806 | N | 10 | N | N | 1.1101 | 39.4971 | 291043.2383
[7 empty] | 12636 | 3570 | 1259229 | 2015-04-21 19:37 | 2015-04-22 08:45 | 788 | 11kV | 485408 | 616 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Section of ZN.12610 Long Jetty from RE.62165 (5 DC's) to extent of feeder tripped and locked out Cause:- Tree/branch brought down OH mains near CP.41159 ME:-1259229 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 788 | N | 3 | N | Y | 1.1101 | 39.4971 | 354721.8493
[7 empty] | 13111 | 7728 | 1237215 | 2015-04-21 08:16 | 2015-04-22 09:00 | 1484 | 11kV | 595977 | 1199 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn36300 Balgowlah North Pa13 fdr has tripped Signals: 11kv trip Relays: A 7 C phase overcurrent. Timer, Lockout Tree branch between LK24403 and S15008 tee S15372 See 1255249,51 exclude 1237215 | April | 2015 | 2015Q4 | 2015 | ZN36300:PA13 | ZN36300:PA13 | ZN36300/000013 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 497.0617 | N | 3 | N | Y | 1.1101 | 39.4971 | 435522.4133
[7 empty] | 13399 | 10160 | 1279137 | 2015-04-21 01:28 | 2015-04-22 10:38 | 1990 | 11kV | 3605880 | 1812 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | Y | No LID report Compiled via scada trends; emergency switching sheets and OMS jobs | April | 2015 | 2015Q4 | 2015 | 224:80332 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | Unknown | Unknown | 2015-04-21 | Y | 1990 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2635070.7485
[7 empty] | 14352 | 17577 | 1241812 | 2015-04-22 09:57 | 2015-04-22 11:50 | 113 | 11kV | 205158 | 2256 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S9700 Kirrawee Panel 17 Tripped and Locked out on C phase time OC Cause: Weather Related See OMS 1255176 1255178 1241812 | April | 2015 | 2015Q4 | 2015 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Not Veg | 2015-04-22 | N | 90.9388 | N | 10 | N | N | 1.1101 | 39.4971 | 149923.4153
[7 empty] | 12391 | 1321 | 1240840 | 2015-04-21 16:25 | 2015-04-22 11:54 | 1169 | 11kV | 54053 | 55 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID Excludes OMS 1259503, 1259499, 1259497, 1259486, 1259483, 1259481, 1259479, 1259478, 1259476 and 1240840 | April | 2015 | 2015Q4 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2015-04-21 | Y | 982.7818 | Y | 3 | N | Y | 1.1101 | 39.4971 | 39500.3381
[7 empty] | 13606 | 11749 | 1235649 | 2015-04-21 09:00 | 2015-04-22 11:55 | 1615 | 11kV | 92220 | 189 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | At CP50015 Quarray Old Northern Tripped and Locked out on Cause: Tree branches on OH mains See OMS 1256735 1256741 | April | 2015 | 2015Q4 | 2015 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2015-04-21 | Y | 487.9365 | N | 3 | N | Y | 1.1101 | 39.4971 | 67391.656
[7 empty] | 13277 | 8959 | 1256951 | 2015-04-21 18:49 | 2015-04-22 11:55 | 1026 | 11kV | 97470 | 95 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | REC 45055 - Trip/reclose/trip, OC & EF. Trees in the area during major storm. | April | 2015 | 2015Q4 | 2015 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 1026 | N | 3 | N | Y | 1.1101 | 39.4971 | 71228.2011
[7 empty] | 12374 | 1117 | 1234314 | 2015-04-21 02:10 | 2015-04-22 12:00 | 2030 | 11kV | 1898491 | 1042 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn12570 Avoca 11kv Pa25 "Hillcrest st' fdr tripped Relays: 51 AB phase Lock Out Weather related. See 1258123,6,7,8,9 Exclude 1234314 | April | 2015 | 2015Q4 | 2015 | ZN12570:PA25 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 1821.9683 | N | 3 | N | Y | 1.1101 | 39.4971 | 1387361.2268
[7 empty] | 14251 | 16910 | 1240666 | 2015-04-21 18:03 | 2015-04-22 12:23 | 1100 | 11kV | 1111100 | 1016 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN.12610 Long Jetty 11kV Panel 23 has tripped and locked out on:- Relays:- A & C phase OC Signals:- 11kV trip Field EFI's:- Nil Cause:- STORM ME:-1259315 RS:-1259318 Withdrawn:-1240666 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA23 | ZN12610:PA23 | ZN12610/000023 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 1093.6024 | N | 3 | N | Y | 1.1101 | 39.4971 | 811959.1081
[7 empty] | 12357 | 1003 | 1257874 | 2015-04-21 12:48 | 2015-04-22 12:42 | 1434 | 11kV | 104543 | 98 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | No LID report Compiled from emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2015-04-21 | Y | 1066.7653 | Y | 3 | N | Y | 1.1101 | 39.4971 | 76396.9409
[7 empty] | 14589 | 19477 | 1234345 | 2015-04-21 02:10 | 2015-04-22 12:49 | 2079 | 11kV | 2632014 | 1266 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2015-04-21 | Y | 2079 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1923398.1999
[7 empty] | 13031 | 7028 | 1236331 | 2015-04-21 09:20 | 2015-04-22 12:56 | 1656 | 11kV | 47335 | 133 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | Y | No LID report Pole on ground Compiled from emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-04-21 | Y | 355.9023 | N | 3 | N | Y | 1.1101 | 39.4971 | 34591.0219
[7 empty] | 14633 | 20010 | 1258411 | 2015-04-21 19:40 | 2015-04-22 13:07 | 1047 | 11kV | 197883 | 189 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID Sustained outage entered based on SCADA times and trends | April | 2015 | 2015Q4 | 2015 | 225:13444 | 270:83593 | ZN00270/083593 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 1047 | Y | 3 | N | Y | 1.1101 | 39.4971 | 144607.0598
[7 empty] | 14046 | 15398 | 1242763 | 2015-04-22 12:05 | 2015-04-22 13:25 | 80 | 11kV | 640 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 151700 B & C phase DOLF : 31: Amp Tree branch hit B & C phase on DOLF's Removed tree branch from Sub 53592 and replaced 31.5amp B and C phase HV fuses. Supply restored. | April | 2015 | 2015Q4 | 2015 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Veg | 2015-04-22 | N | 80 | N | 10 | N | N | 1.1101 | 39.4971 | 467.6931
[7 empty] | 12883 | 5863 | 1234668 | 2015-04-21 04:52 | 2015-04-22 13:27 | 1955 | 11kV | 1640181 | 951 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | @S14892 Charmhaven Panel 14 'Submarine Cable' fdr tripped & locked out on Relays - SEF, O/C, EF Remarks: tree/branch on OH mains. tree branch on mains near LK 41200 | April | 2015 | 2015Q4 | 2015 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 1724.6909 | N | 3 | N | Y | 1.1101 | 39.4971 | 1198595.8977
[7 empty] | 13050 | 7158 | 1235007 | 2015-04-21 03:10 | 2015-04-22 13:31 | 2061.2167 | 11kV | 2278861.7667 | 1112 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID Report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 507:80931 | 507:80931 | ZN00507/080931 | CESSNOCK | OH | Veg | 2015-04-21 | Y | 2049.3361 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1665324.964
[7 empty] | 12864 | 5655 | 1246024 | 2015-04-21 03:26 | 2015-04-22 13:40 | 2054 | 11kV | 371774 | 181 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | Y | No LID Report, Compiled via SCADA, Emergency switching sheets and OMS Pole IV-10285 Fallen Based on SCADA information feeder tripped about 30 minutes after the ZS outage at Toronto was resolved for this feeder | April | 2015 | 2015Q4 | 2015 | 225:33676 | 270:83593 | ZN00270/083593 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 2054 | Y | 3 | N | Y | 1.1101 | 39.4971 | 271681.4737
[7 empty] | 14462 | 18423 | 1235160 | 2015-04-21 03:23 | 2015-04-22 13:42 | 2059 | 11kV | 1208633 | 587 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | NO LID report Compiled via emergency switching sheet Tree branch removed from 11kV at JV-61149 | April | 2015 | 2015Q4 | 2015 | 202:34253 | 202:34253 | ZN00202/034253 | NEWCASTLE | OH | Veg | 2015-04-21 | Y | 2059 | Y | 3 | N | Y | 1.1101 | 39.4971 | 883233.3478
[7 empty] | 12939 | 6310 | 1234742 | 2015-04-21 05:24 | 2015-04-22 14:00 | 1956 | 11kV | 2084854 | 1152 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12650 West Gosford Pnl.9 feeder tripped on: A & B phase O/C, LO/O, timing Weather related storm damage see 1257124 1257127 1257126 1257129 1257130 | April | 2015 | 2015Q4 | 2015 | ZN12650:PA9 | ZN12650:PA9 | ZN12650/000009 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 1809.7691 | N | 3 | N | Y | 1.1101 | 39.4971 | 1523549.8104
[7 empty] | 13500 | 10943 | 1234753 | 2015-04-21 05:29 | 2015-04-22 14:00 | 1951 | 11kV | 157680 | 84 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Section of ZN.15005 Belrose 11kV Panel 10 from RE.24722 (13 DC's) to extent of feeder tripped, reclosed and trippied on:- Cause:- STORM ME:-1261382 RS:-1261385 Withdrawn:-1234753 | April | 2015 | 2015Q4 | 2015 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Not Veg | 2015-04-21 | Y | 1877.1429 | N | 3 | N | Y | 1.1101 | 39.4971 | 115227.8932
[7 empty] | 12704 | 4186 | 1235729 | 2015-04-21 08:19 | 2015-04-22 14:05 | 1786 | 11kV | 358995 | 1557 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled via emergency switching sheets Includes OMS 1266615/16 Excludes OMS 1235729, 1244547 | April | 2015 | 2015Q4 | 2015 | 216:10727 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 230.5684 | N | 3 | N | Y | 1.1101 | 39.4971 | 262342.9574
[7 empty] | 14609 | 19784 | 1240903 | 2015-04-22 07:21 | 2015-04-22 14:23 | 422 | 11kV | 216486 | 513 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | ZN9252 Jannali - IR63275 Washington Lincoln - Trip (In scan fail) Storm in the area. | April | 2015 | 2015Q4 | 2015 | ZN9252:PA24 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Veg | 2015-04-22 | N | 422 | N | 10 | N | N | 1.1101 | 39.4971 | 158201.5835
[7 empty] | 14576 | 19302 | 1256295 | 2015-04-22 08:59 | 2015-04-22 14:30 | 331 | 11kV | 662 | 2 | HV | Equipment Failed in Service | Equipment Failure | Unselected | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled via emergency switching sheets Excludes OMS 1256295 | April | 2015 | 2015Q4 | 2015 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | Unknown | Not Veg | 2015-04-22 | N | 331 | N | 10 | N | N | 1.1101 | 39.4971 | 483.7701
[7 empty] | 13254 | 8789 | 1233295 | 2015-04-20 18:21 | 2015-04-22 14:42 | 2661 | 11kV | 2523361 | 1529 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn15008 harbord Pnl.9 - REC 62774 Kentwell Pittwater tripped on: OC Trip Tree in Kentwell St - EMSO made safe. Note: LB62773 (New ELBS type) above Rec62774 was found open but indicting closed. see 1256520 1256523 GIS: 1233295 | April | 2015 | 2015Q4 | 2015 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Veg | 2015-04-20 | Y | 1650.3342 | N | 8 | N | Y | 1.1101 | 39.4971 | 1843997.7923
[7 empty] | 13106 | 7699 | 1237803 | 2015-04-21 19:48 | 2015-04-22 14:54 | 1146 | 11kV | 1526472 | 1332 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | No LID report compiled from emergency switching sheets Based on SCADA logs appears feeder was interrupted at time of Maryland Zone Sub outage. There was an extended delay to the supply to this feeder after the zone was restored (assumed due to seperate feeder fault) | April | 2015 | 2015Q4 | 2015 | 213:33774 | 213:33774 | ZN00213/033774 | NEWCASTLE | OH | Veg | 2015-04-21 | Y | 1146 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1115500.7143
[7 empty] | 13668 | 12256 | 1234592 | 2015-04-21 04:20 | 2015-04-22 15:00 | 2080 | 11kV | 1174300 | 820 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Recloser CP45054 Noraville Tripped and Locked out Cause not ascertained for outage. Tree branch on mains Near LB40970 See OMS 1258618 1258620 1242739 1234592 1243720 | April | 2015 | 2015Q4 | 2015 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 1432.0732 | N | 3 | N | Y | 1.1101 | 39.4971 | 858143.804
[7 empty] | 14133 | 16074 | 1234795 | 2015-04-21 05:47 | 2015-04-22 15:01 | 1993.9167 | 11kV | 747718.75 | 375 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | Y | Section of ZN.15005 Belrose 11kV Panel 4 from RE.21818 tripped on:- Relays:- EF trip Cause:- STORM, RE.22588 will not close locally or remotely ME:-1234795 | April | 2015 | 2015Q4 | 2015 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Not Veg | 2015-04-21 | Y | 1993.9167 | N | 3 | N | Y | 1.1101 | 39.4971 | 546410.8085
[7 empty] | 13604 | 11733 | 1234513 | 2015-04-21 03:07 | 2015-04-22 15:06 | 2159 | 11kV | 705993 | 327 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn15014 Mona Vale ex Panel 4 Recloser Cp22381 Lane Cove Walter tripped on IOC and OC trip Cause: Tree branch brought down OH | April | 2015 | 2015Q4 | 2015 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 2159 | N | 3 | N | Y | 1.1101 | 39.4971 | 515918.8611
[7 empty] | 12352 | 915 | 1240356 | 2015-04-21 21:21 | 2015-04-22 15:20 | 1078.9 | 11kV | 110107.2667 | 136 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID report Compiled via emergency switching sheet no further information supplied via the control room | April | 2015 | 2015Q4 | 2015 | 526:34641 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Veg | 2015-04-21 | Y | 809.6123 | Y | 3 | N | Y | 1.1101 | 39.4971 | 80463.1429
[7 empty] | 12648 | 3731 | 1234987 | 2015-04-21 01:45 | 2015-04-22 15:43 | 2278 | 11kV | 3391942 | 1489 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | No LID report Information via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 2278 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2478731.1682
[7 empty] | 14239 | 16840 | 1243228 | 2015-04-21 18:32 | 2015-04-22 15:45 | 1273 | 11kV | 1923503 | 1511 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Tree between ABS 10545 & SW 35785 at pole IV-50351 Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 206:34434 | 206:34434 | ZN00206/034434 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 1273 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1405639.2587
[7 empty] | 12318 | 605 | 1278788 | 2015-04-22 13:47 | 2015-04-22 15:51 | 124 | 11kV | 92008 | 742 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID report compiled from emergency switching sheets | April | 2015 | 2015Q4 | 2015 | 256:80653 | 256:80653 | ZN00256/080653 | NEWCASTLE | OH | Not Veg | 2015-04-22 | N | 124 | N | 10 | N | N | 1.1101 | 39.4971 | 67236.7326
[7 empty] | 14440 | 18231 | 1237043 | 2015-04-21 10:11 | 2015-04-22 16:52 | 1841 | 11kV | 554141 | 301 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID 11kV wires on ground Excludes OMS 1237043 | April | 2015 | 2015Q4 | 2015 | 512:48048 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Veg | 2015-04-21 | Y | 1841 | Y | 3 | N | Y | 1.1101 | 39.4971 | 404949.8984
[7 empty] | 14632 | 20006 | 1235535 | 2015-04-21 04:32 | 2015-04-22 17:12 | 2200 | 11kV | 1918400 | 872 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID Restore time updated from emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 205:12206 | 205:12206 | ZN00205/012206 | NEWCASTLE | OH | Veg | 2015-04-21 | Y | 2200 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1401910.1368
[7 empty] | 12658 | 3825 | 1234241 | 2015-04-21 01:38 | 2015-04-22 17:20 | 2382 | 11kV | 2156080 | 1208 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN 12690 Berkeley Vale - Pnl 19 - Trip/reclose/trip, Right Leg, Trip Alarm, A & B phase IOC. Trees brought down section of 11kV feeder from LB 44768 to USL 41116 to AB 42957 tee PT 12947. Also brought down section from LV42130 to LV 42132 to normally open points. ME: 1257175. Rest Steps: 1257177, 8, 9. Withdrawn: 1234241, 1243351, 1245027. | April | 2015 | 2015Q4 | 2015 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 1784.8344 | N | 3 | N | Y | 1.1101 | 39.4971 | 1575599.6704
[7 empty] | 12845 | 5514 | 1244725 | 2015-04-22 16:29 | 2015-04-22 18:35 | 126 | 11kV | 182506 | 1674 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | Y | @ S72 Five Dock Panel 23 'S2826 West Croydon' Fdr tripped on Relays - A & C phase O/C, EF, EFI Signals - Tx2 GE, ZE, 11kv trip Field EFI's operated @ S2826, 3562, 2558, 35720, 4214, 3259 Remarks: UG fault. 11kv UG cable fault from S4214 Margaret St South to S49607 Frederick Mackay | April | 2015 | 2015Q4 | 2015 | ZN72:PA23 | ZN35555:PA16 | ZN35555/000016 | INNER WEST | UG | Not Veg | 2015-04-22 | N | 109.0239 | N | 10 | N | N | 1.1101 | 39.4971 | 133370.0018
[7 empty] | 13708 | 12599 | 1263000 | 2015-04-21 17:21 | 2015-04-22 18:42 | 1521 | 11kV | 3479095 | 2529 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15014 Mona Vale Pa5 tripped Relays: A & C Phase IOC ABNORMAL: S49277:A Open S49908:B Closed Distributor wires down in area @ S49874 See 126300,1,5,6 | April | 2015 | 2015Q4 | 2015 | ZN15014:PA5 | ZN15014:PA5 | ZN15014/000005 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 1375.6801 | N | 3 | N | Y | 1.1101 | 39.4971 | 2542420.0101
[7 empty] | 13643 | 12080 | 1233249 | 2015-04-20 17:38 | 2015-04-22 18:57 | 2959 | 11kV | 67053 | 121 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Section of ZN.15013 Terrey Hills 11kV panel 6 from RE.20828 (9 DC's) to extent of feeder tripped on SEL Cause:- Tree/branch on OH mains causing HV to contact LV near PT.17116 Killawarra Weemala located between CP.26242 and CP.48729 ME:-1261294 RS:-1261298, 1261297 Withdrawn:-1233249, 12333277, 12334420 | April | 2015 | 2015Q4 | 2015 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2015-04-20 | Y | 554.157 | N | 8 | N | Y | 1.1101 | 39.4971 | 49000.3547
[7 empty] | 13848 | 13662 | 1241348 | 2015-04-21 17:05 | 2015-04-22 19:15 | 1570 | 11kV | 1863655 | 1191 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14144 Wamberal Pnl.1L tripped on: A & B phase O/C, L/O, EFI Field EFI down @ S14897 Weather - storm See 1258005 1258006 1258007 1258009 | April | 2015 | 2015Q4 | 2015 | ZN14144:PA1 | ZN14144:PA1 | ZN14144/000001 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 1564.7817 | N | 3 | N | Y | 1.1101 | 39.4971 | 1361904.1055
[7 empty] | 14493 | 18635 | 1238877 | 2015-04-21 01:49 | 2015-04-22 19:20 | 2491 | 11kV | 1812002 | 1012 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S15014 Mona Vale Panel 11 Recloser20397 Pittwater Cabbage Tree has tripped Relays: IOC OC trip. Section of 11kV OM Mains brought down AB20597 to S15214 tee S16250 See OMS 1255672 1255654 1234258/42565/50502/39755/49235 | April | 2015 | 2015Q4 | 2015 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 1790.5158 | N | 3 | N | Y | 1.1101 | 39.4971 | 1324157.6166
[7 empty] | 13546 | 11271 | 1244436 | 2015-04-22 14:40 | 2015-04-22 19:50 | 310 | 11kV | 8564 | 29 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled fvia emergency switching sheets | April | 2015 | 2015Q4 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2015-04-22 | N | 295.3103 | N | 10 | N | N | 1.1101 | 39.4971 | 6258.3186
[7 empty] | 14160 | 16228 | 1234248 | 2015-04-21 01:50 | 2015-04-22 19:57 | 2527.1 | 11kV | 1771497.1 | 701 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | ZN 12690 Berkeley Vale - Pnl 10 - Trip/reclose/trip, L1, L2, lockout. Large tree on mains near PT 12789. | April | 2015 | 2015Q4 | 2015 | ZN12690:PA10 | ZN12690:PA10 | ZN12690/000010 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 2527.1 | N | 3 | N | Y | 1.1101 | 39.4971 | 1294557.8304
[7 empty] | 13928 | 14436 | 1234207 | 2015-04-21 01:29 | 2015-04-22 20:25 | 2576 | 11kV | 2662693 | 1092 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Wind Storm | Y | At S12620 Noraville Panel 10 tripped and locked out on Relays: A and B phase timed O/C Signals: 11kV Trip Cause: Broken HV crossarm Cnr of Scenic and Phillip St See OMS 1257996 1257994 1257990 1243754 1234207 | April | 2015 | 2015Q4 | 2015 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 2438.3636 | N | 3 | N | Y | 1.1101 | 39.4971 | 1945817.5083
[7 empty] | 13233 | 8596 | 1240096 | 2015-04-21 09:26 | 2015-04-22 21:40 | 2174 | 11kV | 2358790 | 1085 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | Y | EX Zn14891 Wyong section of Pa1 "Minnesota" RE49433 Pacific Minnesota 0.5 tripped and locked out UGOH between, wallbaord indicates all DC's restored. Major Event Storm See 1240096,5711 | April | 2015 | 2015Q4 | 2015 | ZN14891:PA1 | ZN14891:PA1 | ZN14891/000001 | CENTRAL COAST | Unknown | Unknown | 2015-04-21 | Y | 2174 | N | 3 | N | Y | 1.1101 | 39.4971 | 1723734.1595
[7 empty] | 12675 | 3933 | 1245417 | 2015-04-22 20:15 | 2015-04-22 21:53 | 98 | 11kV | 42836 | 446 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | At Zn965 Pennant Hills 11kv Pnl 37 "Railway Pennant" feeder tripped on earth fault Signals: 11kv trip, efi, group and and zone earth Field EFI's: nil Remarks: UG fault. Cable fault between Zn965 (pnl 37) to Sub 62023 Railway Pennant | April | 2015 | 2015Q4 | 2015 | ZN965:PA37 | ZN965:PA37 | ZN00965/000037 | HORNSBY | UG | Not Veg | 2015-04-22 | N | 96.0448 | N | 10 | N | N | 1.1101 | 39.4971 | 31303.2854
[7 empty] | 14679 | 20352 | 1244054 | 2015-04-21 14:23 | 2015-04-22 22:30 | 1927 | 11kV | 1063276 | 608 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN.12610 Long Jetty 11kV Panel 18 Feeder tripped, reclosed, tripped and locked out on:- Relays:- A & C phase OC Field EFI's S.18070 Abnormal Switching: RE.50249 Open, see ME-1259375 Cause:- STORM, tree on OH mains near PT.11743. ME:-1259530 RS:-1259533, 1259537, 1259539 Withdrawn:-1240665, 1245637, 1244054 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 1748.8092 | N | 3 | N | Y | 1.1101 | 39.4971 | 777010.7395
[7 empty] | 14141 | 16126 | 1281571 | 2015-04-21 06:56 | 2015-04-22 22:51 | 2395 | 11kV | 1892525 | 1139 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | No LID report Compiled via SCADA, Emergency switching sheet and OMS 22/04/15 09:01 t44510: CUST CONN ATTENDED : MF/MH/TL 21.04.15 HOUSE NOS. 100 & 102 MADE SAFE : HOUSE NO. 102 POA DAMAGE BY TREE : POLE REQUIRES URGENT MAINTENANCE 21/04/15 04:09 CASS: Job referred by Tgwrdes in CASS | April | 2015 | 2015Q4 | 2015 | 214:8667 | 224:80326 | ZN00224/080326 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 1661.5672 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1383001.45
[7 empty] | 14395 | 17880 | 1234299 | 2015-04-21 04:45 | 2015-04-22 23:50 | 2585 | 11kV | 3048355 | 1363 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Ex Zn13000 Lake Munmorah Pa2 "Acacia Ave" fdr tripped 7 locked out on Relays: Right leg EFi, Under frequency, trip Left Leg B phase overucrrent, efi Branch on mains at time of storm, wallbaord indicates system normal. Times and dates per SCADA See 1265459,60,1 Exclude 1234299,45467,8,52885 | April | 2015 | 2015Q4 | 2015 | ZN13000:PA2 | ZN13000:PA2 | ZN13000/000002 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 2236.504 | N | 3 | N | Y | 1.1101 | 39.4971 | 2227647.9227
[7 empty] | 12415 | 1526 | 1240834 | 2015-04-21 11:05 | 2015-04-23 00:37 | 2252 | 11kV | 47292 | 21 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID Report compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 203:8082 | 204:82708 | ZN00204/082708 | NEWCASTLE | OH | Veg | 2015-04-21 | Y | 2252 | Y | 3 | N | Y | 1.1101 | 39.4971 | 34559.5987
[7 empty] | 14028 | 15271 | 1237414 | 2015-04-21 12:50 | 2015-04-23 02:45 | 2275 | 11kV | 2088220 | 965 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC 45025 Wagstaffe tripped to Lockout (ex Pnl.8 Umina) Tree branch removed adj PT11917 see 1259069 1259067 | April | 2015 | 2015Q4 | 2015 | ZN12640:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 2163.9585 | N | 3 | N | Y | 1.1101 | 39.4971 | 1526009.5839
[7 empty] | 14520 | 18839 | 1235284 | 2015-04-21 04:42 | 2015-04-23 02:45 | 2763 | 11kV | 885164 | 328 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID Report Compiled from emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Veg | 2015-04-21 | Y | 2698.6707 | N | 3 | N | Y | 1.1101 | 39.4971 | 646851.7433
[7 empty] | 13915 | 14220 | 1242895 | 2015-04-22 12:20 | 2015-04-23 04:00 | 940 | 11kV | 62980 | 67 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Rain Wind Storm | Y | S 4700 Finlay Monteith - A phase HV fuse (40A) Major storm in the area. Supply restored and no cause found. ME: 1256407. Withdrawn: 1243006. | April | 2015 | 2015Q4 | 2015 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | OH | Not Veg | 2015-04-22 | Y | 940 | N | 10 | N | Y | 1.1101 | 39.4971 | 46023.9264
[7 empty] | 14003 | 14951 | 1236570 | 2015-04-21 09:09 | 2015-04-23 04:10 | 2581 | 11kV | 1302743 | 553 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Wind Storm | Y | Section of ZN.12610 Long Jetty 11kV Panel 18 from RE.50249 (10 DC's) extent of feeder tripped, reclosed, tripped and locked out on:- Relays:- OC Cause:- STORM, OH mains doen beyond RE.50249, 11kV broken cross arm near CP.42954 ME:-1259375 RS:-1259380, 1259381 Withdrawn:-1236570 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 2355.774 | N | 3 | N | Y | 1.1101 | 39.4971 | 952006.16
[7 empty] | 13961 | 14656 | 1239679 | 2015-04-21 18:24 | 2015-04-23 04:15 | 2031 | 11kV | 444849 | 1147 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | ZN 3154 St Ives - Pnl 5 - Trip/reclose, A & C phase OC, Timing, Lockout. Large tree on 11kV adjacent to PT 1539. ME: 1255588. Rest Steps: 1255596, 7. Withdrawn: 1239679, 1241338, 41. | April | 2015 | 2015Q4 | 2015 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | OH | Veg | 2015-04-21 | Y | 387.837 | N | 3 | N | Y | 1.1101 | 39.4971 | 325082.5284
[7 empty] | 13333 | 9595 | 1241742 | 2015-04-22 09:46 | 2015-04-23 08:22 | 1356.4333 | 11kV | 535791.1667 | 395 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | no information supplied by the control room customer advising no supply, assuming start and end times are as per control room operation of OMS | April | 2015 | 2015Q4 | 2015 | 503:48016 | 532:83314 | ZN00532/083314 | MAITLAND | OH | Veg | 2015-04-22 | Y | 1356.4333 | N | 10 | N | Y | 1.1101 | 39.4971 | 391540.3814
[7 empty] | 12301 | 467 | 1261038 | 2015-04-21 12:41 | 2015-04-23 08:41 | 2640 | 11kV | 2640 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID Job details obtained from emergency switching sheet | April | 2015 | 2015Q4 | 2015 |  |  |  | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 2640 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1929.2341
[7 empty] | 14016 | 15099 | 1238100 | 2015-04-21 10:09 | 2015-04-23 08:56 | 2806.8333 | 11kV | 3323290.6667 | 1184 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No information supplied by control room assuming that switching in OMS is correct by control room | April | 2015 | 2015Q4 | 2015 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2015-04-21 | Y | 2806.8333 | N | 3 | N | Y | 1.1101 | 39.4971 | 2428562.7987
[7 empty] | 12848 | 5538 | 1237092 | 2015-04-21 06:06 | 2015-04-23 09:00 | 3054.05 | 11kV | 2721158.55 | 891 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | no information supplied from control room assumed to be feeder level outage as per control room switching of OMS | April | 2015 | 2015Q4 | 2015 | 238:34137 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Veg | 2015-04-21 | Y | 3054.05 | N | 3 | N | Y | 1.1101 | 39.4971 | 1988542.4078
[7 empty] | 12423 | 1587 | 1236955 | 2015-04-21 11:36 | 2015-04-23 09:42 | 2766.25 | 11kV | 398340 | 144 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2015-04-21 | Y | 2766.25 | N | 3 | N | Y | 1.1101 | 39.4971 | 291095.123
[7 empty] | 13514 | 11043 | 1235281 | 2015-04-21 05:08 | 2015-04-23 10:30 | 3202 | 11kV | 3782550 | 1200 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Tree on mains ABS 42821 Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 223:14397 | 223:14397 | ZN00223/014397 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 3152.125 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2764175.9737
[7 empty] | 13222 | 8550 | 1235415 | 2015-04-21 03:50 | 2015-04-23 12:00 | 3370 | 11kV | 1902402 | 1701 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Fdr 48017 Locked out during cyclonic storm | April | 2015 | 2015Q4 | 2015 | 503:48017 | 532:83300 | ZN00532/083300 | MAITLAND | OH | Veg | 2015-04-21 | Y | 1118.4021 | N | 3 | N | Y | 1.1101 | 39.4971 | 1390219.2702
[7 empty] | 12478 | 2000 | 1235356 | 2015-04-21 07:02 | 2015-04-23 12:01 | 3179 | 11kV | 4549149 | 1431 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID Information derived from emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 258:80779 | 258:80779 | ZN00258/080779 | NEWCASTLE | OH | Veg | 2015-04-21 | Y | 3179 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3324383.912
[7 empty] | 14605 | 19731 | 1254759 | 2015-04-23 10:45 | 2015-04-23 12:15 | 90 | 11kV | 68400 | 760 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | Y | Section of Panel 15 Railway Mananga Feeder Interrupted at SW9069 to effect emergency repairs to UGOH above PT9395 Abnormal Swicthing AB35746 Open LB35754 Closed Cause: 11kV on UGOH - UGOH on Fire See OMS 1254759 1246904 Abnormal Switching AB35746 Open and LB35754 Closed | April | 2015 | 2015Q4 | 2015 | ZN9245:PA15 | ZN9245:PA10 | ZN09245/000010 | SUTHERLAND | Unknown | Unknown | 2015-04-23 | N | 90 | N | 4 | N | N | 1.1101 | 39.4971 | 49984.7025
[7 empty] | 14544 | 19029 | 1246117 | 2015-04-23 08:36 | 2015-04-23 12:48 | 252 | 11kV | 756 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Replaced blown HV fuse on Sub 51791. exclude OMS 1246117 | April | 2015 | 2015Q4 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2015-04-23 | N | 252 | N | 4 | N | N | 1.1101 | 39.4971 | 552.4625
[7 empty] | 13590 | 11626 | 1234256 | 2015-04-21 02:42 | 2015-04-23 13:00 | 3498 | 11kV | 884229 | 750 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn35370 Galston Panel 4L has tripped Signals: 11kV trip Relays: 51 A and C phase Reclose Relay. Trees on Mains between AB25 and AB2894 tee S6666 PT2220 and PT2179 Abnormals Switching: AB334 Open and Defective, AB2063 Closed See OMS 1262510 1262512 1262514 1262516 1234385 | April | 2015 | 2015Q4 | 2015 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2015-04-21 | Y | 1178.972 | Y | 3 | N | Y | 1.1101 | 39.4971 | 646168.4729
[7 empty] | 13052 | 7186 | 1234624 | 2015-04-21 05:50 | 2015-04-23 13:25 | 3335 | 11kV | 590257 | 935 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | @S14892 Charmhaven Panel 1 "S18361 Mataram Haven" fdr tripped & locked out on Relays: O/C & EF, EFI, fault check, reclose timing, lockout Remarks: UG fault. 11kv UG fdr fault from S18081 Hillcroft Ridgewood to S14946 Apple Blossom paperbark to S62857 Sparks Minnesotta 0.2 tee PT50106 Sparks Nicco | April | 2015 | 2015Q4 | 2015 | ZN14892:PA1 | ZN14892:PA1 | ZN14892/000001 | CENTRAL COAST | UG | Not Veg | 2015-04-21 | Y | 631.2909 | N | 3 | N | Y | 1.1101 | 39.4971 | 431342.406
[7 empty] | 14109 | 15852 | 1242620 | 2015-04-22 11:50 | 2015-04-23 13:44 | 1553.7167 | 11kV | 1444774.9333 | 1025 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2015-04-22 | Y | 1409.5365 | N | 10 | N | Y | 1.1101 | 39.4971 | 1055798.9076
[7 empty] | 14595 | 19584 | 1242820 | 2015-04-22 20:30 | 2015-04-23 14:20 | 1070 | 11kV | 211860 | 198 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Section of ZN.12610 Long Jetty 11kV Panel 2 from CP.41159 (3 DC's) to extent of feeder:- interrupted to allow reapirs after storm Cause:- STORM, OH mains down ME:-1259638 Withdrawn:-1242820, 1244828 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Not Veg | 2015-04-22 | Y | 1070 | Y | 10 | N | Y | 1.1101 | 39.4971 | 154821.0392
[7 empty] | 13270 | 8920 | 1258814 | 2015-04-20 23:54 | 2015-04-23 15:48 | 3834 | 11kV | 1561380 | 431 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | Rain Wind Storm | Y | Recloser CP44289 Berkeley Vale 0.3 Tripped and Locked out Cause; Rain Wind Storm See OMS 1258814 1258816 | April | 2015 | 2015Q4 | 2015 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2015-04-20 | Y | 3622.6914 | N | 8 | N | Y | 1.1101 | 39.4971 | 1141010.4511
[7 empty] | 13082 | 7487 | 1246053 | 2015-04-23 08:24 | 2015-04-23 16:00 | 456.3667 | 11kV | 7758.2333 | 17 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 151706 A & C phase DOLF : 31 Amp | April | 2015 | 2015Q4 | 2015 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2015-04-23 | N | 456.3667 | N | 4 | N | N | 1.1101 | 39.4971 | 5669.4881
[7 empty] | 12988 | 6728 | 1235941 | 2015-04-21 05:06 | 2015-04-23 16:08 | 3541.7 | 11kV | 3301830.8667 | 1056 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet P0174 | April | 2015 | 2015Q4 | 2015 | 203:8084 | 204:82689 | ZN00204/082689 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 3126.7338 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2412880.6098
[7 empty] | 12872 | 5734 | 1235784 | 2015-04-21 09:17 | 2015-04-23 16:20 | 3303 | 11kV | 1073507 | 490 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | @S13000 Lake Munmorah Panel 5 "S14743 Bay Vista Pinaroo Etc" fdr tripped & locked out on Abnormal: Rec 45140 Pinnaroo Colledina opened @ 0324 see seperate interruption Relays - Right leg A & B phase O/C, EFI, Trip, UF Remarks: weather related. Several trees on mains | April | 2015 | 2015Q4 | 2015 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 2190.8306 | N | 3 | N | Y | 1.1101 | 39.4971 | 784487.2525
[7 empty] | 13994 | 14879 | 1237486 | 2015-04-21 12:05 | 2015-04-23 16:50 | 3165 | 11kV | 6047532 | 2101 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14892 Charmhaven Pa16 "Charmhaven San Remo" fdr tripped & locked out Tree on mains at LB44340. Restoration of PT11240 unknown. Central Coast storm room may have info? See 1263723,5,6,7,30,1 exclude 1237486,47155 | April | 2015 | 2015Q4 | 2015 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 2878.4065 | N | 3 | N | Y | 1.1101 | 39.4971 | 4419358.0136
[7 empty] | 13531 | 11127 | 1237492 | 2015-04-21 12:47 | 2015-04-23 17:05 | 3138.05 | 11kV | 4010168.05 | 1443 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID 11kV mains on ground to ABS 301 (live on other side) Excludes OMS 1261719, 1261722, 1261723, 1261725, 1261727, 1261729, 1247754 information supplied via emergency switching sheets and operations of OMS by control room | April | 2015 | 2015Q4 | 2015 | 258:80793 | 258:80793 | ZN00258/080793 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 2779.0492 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2930512.531
[7 empty] | 14396 | 17881 | 1237050 | 2015-04-21 11:47 | 2015-04-23 17:07 | 3200 | 11kV | 723391 | 346 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | @S13000 Lake Munmorah Panel 4 "LB62014" fdr tripped & Locked out on Relays - A & B phase O/C, trip, EFI, UF Abnormal: Ab43825 open and defective, LB 40172 closed. AB44265 closed, AB40428 open. See separate interruption for recloser 45138 (open prior) Remarks: tree/branch brought down OH. Section of 11kv OH fdr down from LB46170 tee PTs 46139, 11177, 64431, unable to patrol fdr beyond S64260 | April | 2015 | 2015Q4 | 2015 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 2090.7254 | N | 3 | N | Y | 1.1101 | 39.4971 | 528632.8064
[7 empty] | 13110 | 7727 | 1238081 | 2015-04-21 08:07 | 2015-04-23 18:10 | 3483 | 11kV | 1403701.1667 | 431 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled from Emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Not Veg | 2015-04-21 | Y | 3256.8473 | N | 3 | N | Y | 1.1101 | 39.4971 | 1025783.4104
[7 empty] | 13061 | 7325 | 1234579 | 2015-04-21 04:09 | 2015-04-23 18:16 | 3727 | 11kV | 600866 | 192 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Section of ZN.15013 Terrey Hills from RE.21350 tripped, reclosed and tripped on:- Relays:- OC trip Abnormal Switching:- CP.25194 closed & CP.26242 to CP.48729 tee PT.17116 OOS due to defect - see ME:-1261294 for Panel 6 RE.20828 outage Cause:- STORM ME:-1261349 Withdrawn:-1234579 | April | 2015 | 2015Q4 | 2015 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Not Veg | 2015-04-21 | Y | 3129.5104 | N | 3 | N | Y | 1.1101 | 39.4971 | 439095.1503
[7 empty] | 14188 | 16409 | 1234008 | 2015-04-21 02:36 | 2015-04-23 18:30 | 3834 | 11kV | 9171422.25 | 2554 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID Report Compiled via emergency switching sheet Tree in Mains Tripped when tried to restore after zone sub outage CC1: 22-"Refer to SOp" | April | 2015 | 2015Q4 | 2015 | 225:13446 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 3591.0032 | Y | 3 | N | Y | 1.1101 | 39.4971 | 6702204.8691
[7 empty] | 13049 | 7156 | 1234777 | 2015-04-21 05:38 | 2015-04-23 18:32 | 3654 | 11kV | 4364007 | 1207 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Recloser CP40185 Frevent Tripped and Reclosed Tripped and Locked out on overcurrent Cause Not ascertained for outage See OMS 1258055 1258077 1258078 1258079 1234777 1248520 | April | 2015 | 2015Q4 | 2015 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 3615.5816 | N | 3 | N | Y | 1.1101 | 39.4971 | 3189087.5992
[7 empty] | 14305 | 17275 | 1234445 | 2015-04-21 03:22 | 2015-04-23 18:40 | 3798 | 11kV | 4255866 | 1132 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Rec 45140 Pinnaroo Colledina Tripped mains to patrol wallbaord indicates normal. restoration times and date per DNMS events Recloser tripped before subsequent feeder fault. Restored as part of feeder restorations | April | 2015 | 2015Q4 | 2015 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 3759.5989 | N | 3 | N | Y | 1.1101 | 39.4971 | 3110061.346
[7 empty] | 14558 | 19142 | 1236557 | 2015-04-21 10:46 | 2015-04-23 18:45 | 3359 | 11kV | 1651984 | 1717 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Recloser CP41873 Woolana Woodlawn tripped and locked out Blue Form Identified Abnormal switching: CP40747 Opened, LB40928 Closed, CP61845 Opened AB43864 Closed, LB41870 and Link 40245 Opened See OMS 125770 125775 125774 Re-entered to remove overlap with earlier Panel 8 outage. Panel 8 outage did not identify same abnormal configurations so portion normally connected to Panel 8 not included in this new record | April | 2015 | 2015Q4 | 2015 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 962.134 | N | 3 | N | Y | 1.1101 | 39.4971 | 1207221.1819
[7 empty] | 14614 | 19813 | 1234588 | 2015-04-21 04:17 | 2015-04-23 19:06 | 3769 | 11kV | 2567143 | 743 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12690 Berkely Vale Pa12 "Craftsman ave" fdr tripped & locked out on Relays - L1 L2 l3 trip, auto reclose, lockout, efi Abnormal: RE449999 Warner Ave opened @ 0331 see seperate interruption Multiple trees down. Major Event Storm See 1263655,6,7,8,9,60,1 Exclude 1234588,46494 | April | 2015 | 2015Q4 | 2015 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 3455.105 | N | 3 | N | Y | 1.1101 | 39.4971 | 1875992.3865
[7 empty] | 12935 | 6258 | 1234593 | 2015-04-21 04:18 | 2015-04-23 19:30 | 3792 | 11kV | 954442 | 1803 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12610 Long Jetty Pa10 "Wamberal" fdr tripped & locked out on Relays: C phase IOC ,EF, EFI, EF check, reclose timing, lockout Signals: 11kv trip 11kv of pin outside 11 mosman ave bateau bay See 1261099,105,6 exclude 1234593,7798,45657,8386 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 529.3633 | N | 3 | N | Y | 1.1101 | 39.4971 | 697478.0623
[7 empty] | 14337 | 17453 | 1234175 | 2015-04-21 01:07 | 2015-04-23 20:08 | 4021 | 11kV | 2018864 | 635 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12640 Umina Pa1 tripped on A& B phase IOC EFI Storm damage at various locations. Weather related. See 1257163 exclude 1234175 Major Event Storm | April | 2015 | 2015Q4 | 2015 | ZN12640:PA1 | ZN12640:PA1 | ZN12640/000001 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 3179.3134 | N | 3 | N | Y | 1.1101 | 39.4971 | 1475326.2648
[7 empty] | 13138 | 7888 | 1235666 | 2015-04-21 08:15 | 2015-04-23 20:10 | 3595 | 11kV | 5380113 | 1501 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 205:12210 | 205:12210 | ZN00205/012210 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 3584.3524 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3931627.8939
[7 empty] | 14191 | 16425 | 1248856 | 2015-04-23 12:18 | 2015-04-23 21:34 | 556.5333 | 11kV | 2782.6667 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | major storm, no further information supplied via the control room restoration time as per control room operations in OMS | April | 2015 | 2015Q4 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2015-04-23 | N | 556.5333 | Y | 4 | N | Y | 1.1101 | 39.4971 | 2033.4907
[7 empty] | 13642 | 12067 | 1248811 | 2015-04-23 20:46 | 2015-04-23 22:30 | 104 | 11kV | 102794 | 1571 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | Y | Zn10999 Kogarah Pa17 fdr tripped on 51 M O/C reclose t/d lockout EFI F/C UGOH fault short circuit. UGOH below USL 30592 failed See 1253214,6,7 exclude 1248811 | April | 2015 | 2015Q4 | 2015 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | Unknown | Unknown | 2015-04-23 | N | 65.4322 | N | 4 | N | N | 1.1101 | 39.4971 | 75118.8233
[7 empty] | 12763 | 4674 | 1240552 | 2015-04-21 23:43 | 2015-04-23 23:47 | 2884 | 11kV | 201884 | 738 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15002 Narrabeen 11kv Pa6 tripped, closed, tripped & locked out on: Relays A&C IOC, Lockout, Timing Signals: 11kv trip ABNORMAL: S49277:SwA Open S49908:SwB Closed DOp reports tree on mains adjacent PT15877 Tatiara Cr. Left isoalted form AB23508 to PT15877 See outage on Mona Vale Pa5l in conjunction 1263000 See 1263002,4 Exclude 1240552,3367,6507 | April | 2015 | 2015Q4 | 2015 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 273.5556 | N | 3 | N | Y | 1.1101 | 39.4971 | 147530.8726
[7 empty] | 13228 | 8576 | 1235294 | 2015-04-21 07:30 | 2015-04-24 00:24 | 3894 | 11kV | 1157395 | 1318 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN.15006 Dee Why West 11kV Panel 13 tripped on:- Relays:- 51AC Signals:- 11kV Trip Cause:- Tree near PT.15330 / Storm ME:-1255372 RS:-1255384, 1255385, 1255391 Withdrawn:-1235294, 1236295, 1236732, 1236732, 1242901, 1242369 | April | 2015 | 2015Q4 | 2015 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 878.1449 | N | 3 | N | Y | 1.1101 | 39.4971 | 845790.1286
[7 empty] | 13925 | 14409 | 1235052 | 2015-04-21 02:32 | 2015-04-24 00:43 | 4211 | 11kV | 4102758 | 990 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | No LID report Compiled from emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 257:81985 | 257:81985 | ZN00257/081985 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 4144.2 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2998174.5355
[7 empty] | 14325 | 17347 | 1241518 | 2015-04-22 09:12 | 2015-04-24 02:30 | 2478 | 11kV | 166026 | 67 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | PT15258 The Fairway Kywong the middle HDO was found blown. 22/04/15 17:32 t47273: Clash LV mains by fallen tree on mains. Phase & Neutral. Required OH crew. See 1255789 exclude 1240348,1518 | April | 2015 | 2015Q4 | 2015 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2015-04-22 | Y | 2478 | Y | 10 | N | Y | 1.1101 | 39.4971 | 121326.9039
[7 empty] | 13781 | 13171 | 1234152 | 2015-04-21 01:00 | 2015-04-24 07:12 | 4691.95 | 11kV | 2564081.8667 | 697 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency wsitching sheet | April | 2015 | 2015Q4 | 2015 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 3678.7401 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1873755.4005
[7 empty] | 12931 | 6239 | 1262989 | 2015-04-20 23:55 | 2015-04-24 07:55 | 4800 | 11kV | 5716800 | 1191 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Removed branch from vacinity of ABS 2896 compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 221:11900 | 221:11900 | ZN00221/011900 | LAKE MACQUARIE | OH | Veg | 2015-04-20 | Y | 4800 | N | 8 | N | Y | 1.1101 | 39.4971 | 4177668.8229
[7 empty] | 14138 | 16103 | 1236767 | 2015-04-21 10:19 | 2015-04-24 08:06 | 4186.95 | 11kV | 979063.5333 | 312 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Major storm, no LID report Restoration time as per control room operations of OMS | April | 2015 | 2015Q4 | 2015 | 239:82131 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 3138.0241 | Y | 3 | N | Y | 1.1101 | 39.4971 | 715470.7527
[7 empty] | 12493 | 2200 | 1235668 | 2015-04-21 06:03 | 2015-04-24 08:15 | 4452 | 11kV | 299217 | 306 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID Report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2015-04-21 | Y | 977.8333 | Y | 3 | N | Y | 1.1101 | 39.4971 | 218658.9582
[7 empty] | 12551 | 2824 | 1234755 | 2015-04-21 07:24 | 2015-04-24 09:07 | 4423 | 11kV | 3289247 | 915 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | @ ZN.36200 Empire Bay 11kV Panel 4 tripped:- Relays:- 50T AB phase, SEL Cause:- Storm damage ME:-1258106 RS:-1258130, 1258131, 1258132, 1258134, 1258136 Withdrawn:-1234755, 1240836, 1249371, 1249467, 1249545, 1249564 | April | 2015 | 2015Q4 | 2015 | ZN12570:PA29 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 3594.8055 | N | 3 | N | Y | 1.1101 | 39.4971 | 2403684.6912
[7 empty] | 12585 | 3125 | 1238606 | 2015-04-21 09:07 | 2015-04-24 09:37 | 4350 | 11kV | 1220112 | 833 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | No LID Excluded OMS 1238606, 1247764 & 1258451 | April | 2015 | 2015Q4 | 2015 | 503:48078 | 532:83314 | ZN00532/083314 | MAITLAND | OH | Veg | 2015-04-21 | Y | 1464.7203 | N | 3 | N | Y | 1.1101 | 39.4971 | 891621.8624
[7 empty] | 13938 | 14479 | 1241299 | 2015-04-22 08:39 | 2015-04-24 09:56 | 2956.6333 | 11kV | 1183152 | 510 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | no further information supplied from control room, no LID report records completed in OMS as per OMS switching by control room | April | 2015 | 2015Q4 | 2015 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Veg | 2015-04-22 | Y | 2319.9059 | N | 10 | N | Y | 1.1101 | 39.4971 | 864612.5845
[7 empty] | 14240 | 16842 | 1249535 | 2015-04-24 09:40 | 2015-04-24 10:55 | 75 | 11kV | 33532 | 485 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | Zn3155 Double Bay - 11kV Pnl.21 tripped on: Earth Fault, EFI, Fault Check Field EFIs down @ : S1696, S63099, S7755 UG cable fault between S7755 (Sw B) to S35420 (Sw A) to S35323 (Sw B) 1255433 1255435 1255440 | April | 2015 | 2015Q4 | 2015 | ZN3155:PA21 | ZN3155:PA21 | ZN03155/000021 | WOOLLAHRA | UG | Not Veg | 2015-04-24 | N | 69.1381 | N | 3 | N | N | 1.1101 | 39.4971 | 24504.1966
[7 empty] | 12868 | 5699 | 1235748 | 2015-04-21 08:56 | 2015-04-24 11:35 | 4479 | 11kV | 680808 | 152 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 151714 Sub isolated due to defects from storm | April | 2015 | 2015Q4 | 2015 | 210:8681 | 210:83473 | ZN00210/083473 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 4479 | Y | 3 | N | Y | 1.1101 | 39.4971 | 497514.406
[7 empty] | 12479 | 2015 | 1238576 | 2015-04-21 08:53 | 2015-04-24 11:35 | 4482 | 11kV | 35038 | 300 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | NO LID report compiled via emergency switching sheet 11kV mains down JV-41466 | April | 2015 | 2015Q4 | 2015 | 221:11898 | 221:11898 | ZN00221/011898 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 116.7933 | N | 3 | N | Y | 1.1101 | 39.4971 | 25604.737
[7 empty] | 13935 | 14466 | 1234806 | 2015-04-21 07:20 | 2015-04-24 11:56 | 4596 | 11kV | 652985 | 1246 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S12620 Noraville Panel 8 tripped and locked out on Relays: SEF and EFI Cause: Section of 11kV OH from AB40355 to LB41870 to LB61845 tee PT61844 Isolated See OMS 1257738 1257744 1257745 1234806 | April | 2015 | 2015Q4 | 2015 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 524.065 | N | 3 | N | Y | 1.1101 | 39.4971 | 477182.1782
[7 empty] | 13419 | 10307 | 1234584 | 2015-04-21 04:15 | 2015-04-24 12:00 | 4785 | 11kV | 2567330 | 958 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN 12690 Berkeley Vale - Pnl 8 - Trip/reclose/trip, Trip, alarm, T1>. Tree brought down OH between LB41744 to USL41114 to AB42279 tee PT11972. Tree also on mains tee PT11466. ME: 1257019. Rest Step: 1257023, 4, 7, 8. Withdrawn: 1234584, 1243462, 1248770, 1. | April | 2015 | 2015Q4 | 2015 | ZN12690:PA8 | ZN12690:PA8 | ZN12690/000008 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 2679.8852 | N | 3 | N | Y | 1.1101 | 39.4971 | 1876129.0406
[7 empty] | 14223 | 16691 | 1234930 | 2015-04-21 05:21 | 2015-04-24 12:06 | 4725 | 11kV | 3091435 | 919 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 221:11894 | 221:11894 | ZN00221/011894 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 3363.9119 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2259129.5161
[7 empty] | 12640 | 3628 | 1235721 | 2015-04-21 04:39 | 2015-04-24 12:09 | 4770 | 11kV | 3890898 | 851 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID report Compiled via SCADA, emergency switching sheet and OMS | April | 2015 | 2015Q4 | 2015 | 243:80078 | 243:80078 | ZN00243/080078 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 4572.1481 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2843353.4963
[7 empty] | 12417 | 1557 | 1240386 | 2015-04-21 17:31 | 2015-04-24 12:18 | 4007 | 11kV | 6128805.15 | 1530 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID Report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 242:81535 | 242:81535 | ZN00242/081535 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 4005.755 | Y | 3 | N | Y | 1.1101 | 39.4971 | 4478750.0345
[7 empty] | 14365 | 17627 | 1235050 | 2015-04-21 07:13 | 2015-04-24 13:00 | 4667 | 11kV | 1315300 | 370 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | ZN 12690 Berkeley Vale - Pnl 16 - Trip/reclose/trip, IOC, lockout. Weather related outage as major storm in the area. ME: 1257055. Rest Steps: 1257060, 1, 2, 6. Withdrawn: 1235050, 1243332, 1248476, 666. | April | 2015 | 2015Q4 | 2015 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 3554.8649 | N | 3 | N | Y | 1.1101 | 39.4971 | 961182.4452
[7 empty] | 13480 | 10766 | 1234596 | 2015-04-21 04:20 | 2015-04-24 13:34 | 4874 | 11kV | 1953333 | 1197 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | @S14892 Charhaven Panel 3 "S14575 Oxford Gorakan" Fdr Tripped & Locked out on Relays: O/C & EF, EFI, Fault Check, Reclose Timing, Lockout Remarks: Storm. 1)Large branch on pT12191, section of feeder from AB41001 to AB41274 tee PT12191 Isolated Only 2) Inspect PT11198 24/04/15 - Secton fof feeder interrupted from LB 42772 to repair 2 x HV bonds | April | 2015 | 2015Q4 | 2015 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 1631.8571 | N | 3 | N | Y | 1.1101 | 39.4971 | 1427438.1428
[7 empty] | 12810 | 5095 | 1236547 | 2015-04-21 10:41 | 2015-04-24 13:45 | 4504 | 11kV | 2326658 | 627 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | At S13000 Lake Munmorah Panel 1 Lake Munmorah Aux feeder tripped on: A & C phase O/C Remarks: tree/branch on OH mains. | April | 2015 | 2015Q4 | 2015 | ZN13000:PA1 | ZN13000:PA1 | ZN13000/000001 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 3710.7783 | N | 3 | N | Y | 1.1101 | 39.4971 | 1700253.0416
[7 empty] | 12926 | 6212 | 1235687 | 2015-04-21 04:20 | 2015-04-24 13:50 | 4890 | 11kV | 6914621 | 1497 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled via emergency switching sheets Includes OMS 1266706/09/10/15/16/17 Excludes OMS 1235687, 1249290/91 | April | 2015 | 2015Q4 | 2015 | 240:34840 | 240:34840 | ZN00240/034840 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 4618.9853 | Y | 3 | N | Y | 1.1101 | 39.4971 | 5053001.08
[7 empty] | 14061 | 15480 | 1233287 | 2015-04-21 23:25 | 2015-04-24 13:53 | 3748 | 11kV | 89820 | 43 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Section of ZN.15011 Beacon Hill 11kV Panel 2L from LBS.20329 to extent of feeder (1 DC) Cause:- Interrupted for safety reasons, isolated by D/Op due to large tree contacting and arcing HV/LV mains outside 32 Kokoda Cres Note:- See also ME:-1254986 ME:-1240582 | April | 2015 | 2015Q4 | 2015 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 2088.8372 | N | 3 | N | Y | 1.1101 | 39.4971 | 65637.8068
[7 empty] | 14120 | 16002 | 1235429 | 2015-04-21 03:57 | 2015-04-24 14:13 | 4936.2 | 11kV | 208255.3 | 61 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 511:29872 | 511:29872 | ZN00511/029872 | MAITLAND | OH | Not Veg | 2015-04-21 | Y | 3414.0213 | N | 3 | N | Y | 1.1101 | 39.4971 | 152186.8307
[7 empty] | 13859 | 13765 | 1244432 | 2015-04-22 15:46 | 2015-04-24 14:18 | 2791.5667 | 11kV | 340571.1333 | 122 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | PT13793 Angler Waratah - HDO operated Weather | April | 2015 | 2015Q4 | 2015 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | OH | Not Veg | 2015-04-22 | Y | 2791.5667 | Y | 10 | N | Y | 1.1101 | 39.4971 | 248879.3391
[7 empty] | 14346 | 17518 | 1234042 | 2015-04-20 23:48 | 2015-04-24 14:28 | 5200 | 11kV | 7727200 | 1486 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 242:81541 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Veg | 2015-04-20 | Y | 5200 | N | 8 | N | Y | 1.1101 | 39.4971 | 5646809.8462
[7 empty] | 12617 | 3343 | 1236972 | 2015-04-21 05:59 | 2015-04-24 14:36 | 4837 | 11kV | 49836 | 46 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Tree blow in and damage to ABS27950. Excludes jobs 1236972, 1247925, 1257826 and 1257829. | April | 2015 | 2015Q4 | 2015 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2015-04-21 | Y | 1083.3913 | Y | 3 | N | Y | 1.1101 | 39.4971 | 36418.6789
[7 empty] | 14574 | 19292 | 1234421 | 2015-04-21 02:51 | 2015-04-24 14:40 | 5029 | 11kV | 265496 | 176 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn124891 Wyong Pa20 "Warnervale west railway" fdr tripped 7 locked out on Relays: A&B phase overcurrent, fault check, reclose timing, lockout Abnormal: RE47302 Hue Hue Sparks Open, RE50560 Hue Hue Sandra Open both tripped prior to feeder tripped. Tree branch brought down OH. DMA on section of adjacent feeder Wyong Pa21, closed through RE45070 to defective mains See separate interruption reports fro reclose re47302 and re50560 See 1259896,900,1 | April | 2015 | 2015Q4 | 2015 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 1508.5 | N | 3 | N | Y | 1.1101 | 39.4971 | 194016.646
[7 empty] | 13079 | 7472 | 1240669 | 2015-04-21 15:58 | 2015-04-24 14:42 | 4244 | 11kV | 3896077 | 1363 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN 14891 Wyong - Pnl 8 - Trip/reclose/trip, OC, Earth fault, EFI. Major storm in the area. ME: 1258049. Rest Steps: 1258050, 1, 3, 4. Withdrawn: 1240669. | April | 2015 | 2015Q4 | 2015 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 2858.4571 | N | 3 | N | Y | 1.1101 | 39.4971 | 2847138.1568
[7 empty] | 12785 | 4893 | 1234947 | 2015-04-21 06:40 | 2015-04-24 14:54 | 4814 | 11kV | 974044 | 289 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14892 Charmhaven Pa5 fdr tripped 7 locked out on Relays - B & C phase IOC, EFI, Fault check, reclose timing, lockout Failed during storm. extent of feeder all restored, no details available of extent of damage See 1263676,8,80,1,2 exclude 1234947,48543 | April | 2015 | 2015Q4 | 2015 | ZN14892:PA5 | ZN14892:PA5 | ZN14892/000005 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 3370.3945 | N | 3 | N | Y | 1.1101 | 39.4971 | 711802.6258
[7 empty] | 13014 | 6900 | 1246302 | 2015-04-21 07:00 | 2015-04-24 15:43 | 4843 | 11kV | 5761892 | 1205 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn12570 Avoca section of 11kv Pa39 @RE44855 Lake Tramway tripped on overcurrent + Lockout Weather realted. Major Storm Damage. See 1258805,7,8,9,10 Exclude 1246302 | April | 2015 | 2015Q4 | 2015 | ZN12570:PA39 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 4781.6531 | N | 3 | N | Y | 1.1101 | 39.4971 | 4210620.7266
[7 empty] | 13058 | 7272 | 1243595 | 2015-04-21 03:12 | 2015-04-24 15:45 | 5073 | 11kV | 4883059 | 1068 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | Y | Rec45138 Yeramba Illawong tripped reclosed tripped and locked out on: Relays: Overcurrent Ex Panel 7 "Summerland Point" feeder @ Zn13000 Lake Munmorah Remarks: weather related. Access Permit issued @ 0930 to L/W from LB45141 to AB42910 tee to PT12233 Kullaoo Cudgee tee to PT13690 Cams Yeramba. HV + LV Mains down | April | 2015 | 2015Q4 | 2015 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 4572.1526 | N | 3 | N | Y | 1.1101 | 39.4971 | 3568395.4913
[7 empty] | 12521 | 2482 | 1236805 | 2015-04-21 11:15 | 2015-04-24 15:45 | 4590 | 11kV | 358020 | 78 | HV | Arcing | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 151723 3 phase Excluded OMS 1236805 | April | 2015 | 2015Q4 | 2015 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 4590 | Y | 3 | N | Y | 1.1101 | 39.4971 | 261630.4562
[7 empty] | 13862 | 13782 | 1249338 | 2015-04-24 08:54 | 2015-04-24 16:24 | 450.1167 | 11kV | 42761.0833 | 95 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 151725 sub isolated due to storm damage | April | 2015 | 2015Q4 | 2015 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Veg | 2015-04-24 | N | 450.1167 | N | 3 | N | N | 1.1101 | 39.4971 | 31248.5385
[7 empty] | 14473 | 18507 | 1249133 | 2015-04-24 07:52 | 2015-04-24 16:42 | 529.5 | 11kV | 41830.5 | 79 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | Y | LID 151746 Pole FP-60749 on fire Excludes OMS 1257952 | April | 2015 | 2015Q4 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2015-04-24 | N | 529.5 | Y | 3 | N | Y | 1.1101 | 39.4971 | 30568.4956
[7 empty] | 12638 | 3591 | 1241794 | 2015-04-21 06:15 | 2015-04-24 17:00 | 4965 | 11kV | 181189 | 41 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled from switching sheets Excludes OMS 1261774/75 1241794 1249575 | April | 2015 | 2015Q4 | 2015 | 229:34983 | 233:82818 | ZN00233/082818 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 4419.2439 | Y | 3 | N | Y | 1.1101 | 39.4971 | 132407.577
[7 empty] | 12639 | 3598 | 1249631 | 2015-04-23 13:58 | 2015-04-24 17:01 | 1623.0167 | 11kV | 24345.25 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 151747 Isolated due to storm damage | April | 2015 | 2015Q4 | 2015 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2015-04-23 | Y | 1623.0167 | Y | 4 | N | Y | 1.1101 | 39.4971 | 17790.7906
[7 empty] | 12273 | 141 | 1235427 | 2015-04-21 03:53 | 2015-04-24 17:18 | 5125 | 11kV | 6865281.8667 | 1623 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | NO LID report no emergency switching sheet provided, compliled from OMS swithcing by control room no additional information available | April | 2015 | 2015Q4 | 2015 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 4229.995 | Y | 3 | N | Y | 1.1101 | 39.4971 | 5016945.4966
[7 empty] | 13441 | 10500 | 1233254 | 2015-04-20 17:54 | 2015-04-24 17:21 | 5727 | 11kV | 1118239 | 1365 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15002 Narrabeen Panel 2 "Rickard Anana" Fdr tripped, reclosed and tripped on Signals: 11kv trip Relays: Earth Fault EFI, Recloser, lockout, timing Frame Leakage. Zone Earth 11kv trip ABNORMAL: LB20234 closed, LB20693 is open and defective Highe voltage fell fown into low voltage mains near PT15798 See 1255915,20,1,4,7 exclude 1233254,804,40879 | April | 2015 | 2015Q4 | 2015 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Not Veg | 2015-04-20 | Y | 819.2227 | N | 8 | N | Y | 1.1101 | 39.4971 | 817176.0787
[7 empty] | 13699 | 12520 | 1247428 | 2015-04-23 12:56 | 2015-04-24 17:30 | 1714.1333 | 11kV | 527953.0667 | 308 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor ABC | Unplanned | Rain Wind Storm | Y | Section of feeder from CP24701 Scotland Island was opened due to reports tha HV ABC were on the ground CC1: 23-"Mains Required" FRC1: 300-"Specify details by voice" | April | 2015 | 2015Q4 | 2015 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | OH | Not Veg | 2015-04-23 | Y | 1714.1333 | N | 4 | N | Y | 1.1101 | 39.4971 | 385812.5291
[7 empty] | 13991 | 14852 | 1235438 | 2015-04-21 03:59 | 2015-04-24 17:35 | 5136 | 11kV | 5446321 | 1536 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | No LID report Compiled via Emergency switching sheet and corporate client | April | 2015 | 2015Q4 | 2015 | 213:33771 | 213:33771 | ZN00213/033771 | NEWCASTLE | OH | Veg | 2015-04-21 | Y | 3545.7819 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3980010.7475
[7 empty] | 13875 | 13900 | 1237522 | 2015-04-21 12:27 | 2015-04-24 17:42 | 4635 | 11kV | 454230 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No information supplied by control room, information gathered from related records and customer comments. Customers reporting wires on ground, wires hanging low, and wires brought down by trees and vegetation on wires, both DW and SW start time is as per first customer call and end time was deduced from SO Comments | April | 2015 | 2015Q4 | 2015 | ZN15010:PA5 | ZN15010:PA29 | ZN15010/000029 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 4635 | N | 3 | N | Y | 1.1101 | 39.4971 | 331937.8865
[7 empty] | 14238 | 16815 | 1234127 | 2015-04-21 00:44 | 2015-04-24 17:45 | 5341 | 11kV | 6419990 | 1744 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12570 Avoca Pa24 fdr tripped Relays: 50T BC phase Lockout Weather related. Multiple trees on mains See 1259724,8,9,31,2,3,4 Exclude 1234127,41672,4026,8566,98,9443,726 | April | 2015 | 2015Q4 | 2015 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 3681.1869 | N | 3 | N | Y | 1.1101 | 39.4971 | 4691539.3344
[7 empty] | 13276 | 8955 | 1233695 | 2015-04-20 20:59 | 2015-04-24 18:00 | 5581 | 11kV | 1485951 | 284 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | First event: section of 11kV Feeder Pnl 2, rec 41020 Wattle Tree Rd Noth Tripped Reclosed and locked out 2nd Event 21/04/2015 09:15Ex Zn12600 Lisarow P2 - REC 41845 North Erina tripped on: O/C & L/O Weather related - storm damage see 1257662 1257665 1257666 1257669 have combined the events into one, as per control room switching | April | 2015 | 2015Q4 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2015-04-20 | Y | 5232.2218 | N | 8 | N | Y | 1.1101 | 39.4971 | 1085889.1627
[7 empty] | 13963 | 14660 | 1236632 | 2015-04-21 08:36 | 2015-04-24 18:05 | 4889 | 11kV | 1107787 | 227 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Ex ZN 12690 Berkeley Vale - REC 41630 Keren Bundilla - Trip/reclose/trip. Tree on 11kV mains adjacent to PT 14432. ME: 1257099. Rest Step: 1257101. Withdrawn: 1236632. | April | 2015 | 2015Q4 | 2015 | ZN12690:PA3 | ZN12690:PA3 | ZN12690/000003 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 4880.1189 | N | 3 | N | Y | 1.1101 | 39.4971 | 809538.0654
[7 empty] | 12882 | 5856 | 1266873 | 2015-04-21 02:34 | 2015-04-24 18:14 | 5260 | 11kV | 2051400 | 390 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Entered based on switching sheets Multiple faults. Tree in sub 8504 and 11kV down at sub 10712 Subsequent to this fault on feeder section 48962 feeder 80081 tripped See OMS 1266873 for details on the feeder restoration activities | April | 2015 | 2015Q4 | 2015 | 243:80081 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 5260 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1499102.6139
[7 empty] | 14197 | 16480 | 1235153 | 2015-04-21 03:23 | 2015-04-24 18:20 | 5217 | 11kV | 618615 | 119 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | completed based on switching sheets and operational OMS records Fault on both 8684 & 2121 feeders See OMS 1255734 for feeder 2121 Mains down at Hexham Bowling Club Site | April | 2015 | 2015Q4 | 2015 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 5198.4454 | Y | 3 | N | Y | 1.1101 | 39.4971 | 452065.5959
[7 empty] | 12901 | 5971 | 1239311 | 2015-04-21 17:19 | 2015-04-24 18:27 | 4388 | 11kV | 453105 | 1008 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Wind Storm | Y | Zn2635 Epping Pa38 fdr has tripped Signals: 11kv trip Relays: ABC phase overcurrent (50T), EF (150N), Reclose, EFI EFI:S4566 S5536 S36219 S4550 11kv pole snapped and mains down on span to PT64637 Nirimba Roma. Isolated from LB1261 to AB767 tee to PT64637 See 1256416,8,9 exclude 1239311,44318 | April | 2015 | 2015Q4 | 2015 | ZN2635:PA38 | ZN2635:PA38 | ZN02635/000038 | HORNSBY | OH | Not Veg | 2015-04-21 | Y | 449.5089 | N | 3 | N | Y | 1.1101 | 39.4971 | 331115.7697
[7 empty] | 12816 | 5158 | 1235471 | 2015-04-22 08:38 | 2015-04-24 18:32 | 3473.7667 | 11kV | 368219.2667 | 106 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | S16188 York Raymond - Dist #1 & 2 - B & C phase fuses blown Tree on OH mains No restore time given from Subs who replaced fuses - left as CR incomplete time | April | 2015 | 2015Q4 | 2015 | ZN15004:PA3 | ZN15004:PA3 | ZN15004/000003 | NORTHERN BEACHES | OH | Veg | 2015-04-22 | Y | 3473.7667 | Y | 10 | N | Y | 1.1101 | 39.4971 | 269083.7795
[7 empty] | 12849 | 5540 | 1235086 | 2015-04-21 07:26 | 2015-04-24 18:44 | 4998 | 11kV | 3360012 | 1553 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12650 West Gosford Pnl.20 tripped on: B & C phase O/C, EFI Abnormal: S18104 Dunn Albany Sw B CLOSED with Sw A OPEN Weather related - major storm see 1258725 1258727 1258729 | April | 2015 | 2015Q4 | 2015 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 2163.5621 | N | 3 | N | Y | 1.1101 | 39.4971 | 2455397.666
[7 empty] | 13916 | 14269 | 1259861 | 2015-04-21 02:42 | 2015-04-24 18:50 | 5288 | 11kV | 1925899 | 378 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | EX ZN 14891 Wyong - Pnl 20 - REC 50560 Hue Hue Sandra - Trip/reclose/trip, OC. Weather related outage as major storm in the area. ME: 1259861. Rest Step: 1259862, 4, 7. | April | 2015 | 2015Q4 | 2015 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 5094.9709 | N | 3 | N | Y | 1.1101 | 39.4971 | 1407390.1848
[7 empty] | 14355 | 17583 | 1235030 | 2015-04-21 02:15 | 2015-04-24 18:50 | 5315 | 11kV | 558240 | 108 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID Report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2015-04-21 | Y | 5168.8889 | Y | 3 | N | Y | 1.1101 | 39.4971 | 407945.3267
[7 empty] | 14575 | 19293 | 1234490 | 2015-04-21 03:29 | 2015-04-24 19:10 | 5261 | 11kV | 1395691 | 319 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN 14891 Wyong - Pnl 21 - Trip/reclose/trip, All phases OC, fault check, timing, lockout. Tree branch brought down OH between USL44007 to AB44347. Also section between USL44668 tee PT14665. ME: 1258020. Rest Step: 1258024, 6, 7, 33. Withdrawn: 1234490, 1248862. | April | 2015 | 2015Q4 | 2015 | ZN14891:PA21 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 4375.2069 | N | 3 | N | Y | 1.1101 | 39.4971 | 1019929.8169
[7 empty] | 12777 | 4832 | 1240103 | 2015-04-21 16:23 | 2015-04-24 19:41 | 4518 | 11kV | 7511091 | 1742 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12600 Lisarow Pnl.3 tripped on: A & C phase O/L Weather related - OH down in various locations see 1257696 1257700 1257704 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 4311.7629 | N | 3 | N | Y | 1.1101 | 39.4971 | 5488883.7631
[7 empty] | 14023 | 15181 | 1234376 | 2015-04-21 02:34 | 2015-04-24 19:45 | 5351 | 11kV | 6614220 | 1294 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Entered based on switching sheet Tree on 11kV mains at VP-20266 on Fishery Pt RD 11kV Recloser 48962 tripped before feeder fault - see OMS 1266873 for details on recloser section restoration | April | 2015 | 2015Q4 | 2015 | 243:80081 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 5111.4529 | Y | 3 | N | Y | 1.1101 | 39.4971 | 4833476.8895
[7 empty] | 14579 | 19329 | 1235135 | 2015-04-21 03:40 | 2015-04-24 19:56 | 5296 | 11kV | 2673533.7667 | 671 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | no information supplied from the control room assume switching as per control room operation of OMS | April | 2015 | 2015Q4 | 2015 | 238:34150 | 238:34150 | ZN00238/034150 | NEWCASTLE | OH | Veg | 2015-04-21 | Y | 3984.402 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1953739.6208
[7 empty] | 14230 | 16753 | 1233549 | 2015-04-20 23:57 | 2015-04-24 20:00 | 5523 | 11kV | 3712953 | 4463 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15008 Harbord - Pnl.7 tripped on B & C phase IOC, Timing, L/O relays, F/C relay Weather related - 1. LK23521 Defective 2.Insulator off x-arm @ CNR Admas St & Carrington Pde 3.Insulators off x-arm CNR Griffin Rd & Austin Ave 4. 1 Bay S/L cut away Pitt Rd between Ross & Playfair. During restoration Pnl.10 tripped @ 5:17 21/4/15 which had partly restored P7 see P7: 1256365 1256372 P10: 1256375 1256381 1256382 | April | 2015 | 2015Q4 | 2015 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2015-04-20 | Y | 831.9411 | N | 8 | N | Y | 1.1101 | 39.4971 | 2713316.5388
[7 empty] | 13143 | 7950 | 1249183 | 2015-04-24 07:59 | 2015-04-24 20:00 | 721 | 11kV | 373442 | 883 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | Zn12650 West Gosford Pnl.20 tripped on: Earth Fault , EFI Field EFIs @ S18737 18121 12794 18498 11142 18143 Abnormal: LB61991 OPEN - S18104 Sw B CLOSED with Sw A OPEN - LB49607 CLOSED UG cable fault from S18143 Sw B to S18104 tee PT12727 see 1257199 1257201 | April | 2015 | 2015Q4 | 2015 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | UG | Not Veg | 2015-04-24 | Y | 422.9241 | N | 3 | N | Y | 1.1101 | 39.4971 | 272900.3989
[7 empty] | 13015 | 6904 | 1250483 | 2015-04-21 02:51 | 2015-04-24 20:00 | 5349 | 11kV | 181866 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 151750 Sub isolated due to storm damage | April | 2015 | 2015Q4 | 2015 | 528:83014 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2015-04-21 | Y | 5349 | N | 3 | N | Y | 1.1101 | 39.4971 | 132902.3087
[7 empty] | 13182 | 8262 | 1234826 | 2015-04-21 05:54 | 2015-04-24 20:25 | 5191 | 11kV | 1068493 | 221 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Section of ZN.12610 Long Jetty 11kV from RE.45000 tripped, reclosed, tripped and loced out on:- Relays:- EF Cause:- STORM, multiple sections of 11kV OH mains down Notes:- Access Permit issued to Line Worker @ 10:20hrs from CP.40862 to CP.45131 to S.18758 SW/A, cancelled @ 12:00hrs - Access Permit issued to Line Worker @ 13:15hrs from CP.45130 to CP.50562 and inclusive ME:-1259216 RS:-1259218 Withdrawn:-1234826 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 4834.81 | N | 3 | N | Y | 1.1101 | 39.4971 | 780823.1692
[7 empty] | 12900 | 5964 | 1240437 | 2015-04-21 21:24 | 2015-04-24 21:20 | 4316 | 11kV | 1076571 | 2891 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN.15005 Belrose Panel 8 tripped on:- Signals:- 11kV trip Relays:- OC 50TAB, EFI, Trip LED, FC, Timer, LO Abnormal Switching:- LBS.26243 closed, ABS.25739 open Cause:- STORM, Tree into mains located between LBS.64765 to LBS.25623 N/O tee S.16613, tee S.15754 ME:-1255643 RS:-1255646, 1255645 Withdrawn:-1240437 | April | 2015 | 2015Q4 | 2015 | ZN15005:PA8 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | OH | Veg | 2015-04-21 | Y | 372.3871 | N | 3 | N | Y | 1.1101 | 39.4971 | 786726.3333
[7 empty] | 14236 | 16805 | 1241639 | 2015-04-21 06:10 | 2015-04-24 22:15 | 5285 | 11kV | 1789033 | 1322 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn2400 Berowra ex Pa18 RE3281 Bay Cooper has tripped Relays: Overcurrent trip OH down between AB298 7 LB62158 tee associated PT's From AB714 through to RE349 gully not patrolled PT678 PT2155 de-energised Zn2400 Berowra Pa18 fdr tripped on Relays: IOC Earth Fault, A 7 C Instant Over Current, EFI and lock out Signals: 11kv trip Tree/branch brought down 11kv Over head. See 1256874,81,91 2nd 1256875 Exclude 1234866,9981,8,40267,90,464,74,540,949,1639,5094,120,7424 | April | 2015 | 2015Q4 | 2015 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2015-04-21 | Y | 1353.2776 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1307372.5489
[7 empty] | 12550 | 2816 | 1251281 | 2015-04-24 20:47 | 2015-04-24 22:46 | 119.0333 | 11kV | 15831.4333 | 133 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | Y | Pole fire, no further information supplied | April | 2015 | 2015Q4 | 2015 | 222:33600 | 222:33600 | ZN00222/033600 | LAKE MACQUARIE | OH | Not Veg | 2015-04-24 | N | 119.0333 | N | 3 | N | N | 1.1101 | 39.4971 | 11569.1445
[7 empty] | 14586 | 19426 | 1249365 | 2015-04-24 09:02 | 2015-04-24 23:22 | 860 | 11kV | 20640 | 24 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | Y | ZN 14891 Wyong - Pnl 10 - Trip/reclose/trip, A & B phase OC, All phases IOC, EFI, Fault Check, Timing, Lockout. 11kV UG fault from S 14857 to LB 40095 tee S 14785. exclude OMS 1249365 | April | 2015 | 2015Q4 | 2015 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | UG | Not Veg | 2015-04-24 | Y | 860 | Y | 3 | N | Y | 1.1101 | 39.4971 | 15083.1032
[7 empty] | 13383 | 10008 | 1248963 | 2015-04-24 03:48 | 2015-04-24 23:45 | 1197 | 11kV | 347385 | 717 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | @Zn9900 Menai Panel 6 "S9295" fdr has tripped ABNORMAL: Fault between S9429 & S9949. S9270:B closed, S9949:B Open Signals: 11kv trip, Zone Earth, Group Earth Relays: Earth Fault EFI: S9210 S49220 S9155 S9597 S9211. S9295 did not operate Suspect UG fault between S9211:B Dunmore Daivd to S9074:A tee PT9544 See 1254156,6 exclude 1249863,9134 | April | 2015 | 2015Q4 | 2015 | ZN9900:PA6 | ZN9900:PA6 | ZN09900/000006 | SUTHERLAND | UG | Not Veg | 2015-04-24 | Y | 484.4979 | N | 3 | N | Y | 1.1101 | 39.4971 | 253858.7119
[7 empty] | 13170 | 8117 | 1241579 | 2015-04-21 10:50 | 2015-04-25 00:27 | 5137 | 11kV | 1612750 | 1006 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | Y | No LID Report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 208:58 | 257:81987 | ZN00257/081987 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 1603.1312 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1178550.1319
[7 empty] | 14483 | 18560 | 1256579 | 2015-04-21 09:35 | 2015-04-25 01:00 | 5245 | 11kV | 13010 | 16 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Rain Wind Storm | Y | Ex Zn35370 Galston Panel 8 Cause: Transformer Defective and Required a Rebuild. See OMS 1256579 1256584 Note: start time amended to align with prior consecutive outage OMS 1256724 | April | 2015 | 2015Q4 | 2015 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2015-04-21 | Y | 813.125 | Y | 3 | N | Y | 1.1101 | 39.4971 | 9507.3243
[7 empty] | 13547 | 11279 | 1248960 | 2015-04-24 03:54 | 2015-04-25 06:39 | 1604.65 | 11kV | 489418.25 | 305 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | Major storm in the area. Multiple feeder faults in the area. May have been covered by some of the region completed jobs as well. ME: 1248960. Withdrawn: 1249052, 193. | April | 2015 | 2015Q4 | 2015 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | UG | Not Veg | 2015-04-24 | Y | 1604.65 | Y | 3 | N | Y | 1.1101 | 39.4971 | 357652.4217
[7 empty] | 14510 | 18788 | 1234638 | 2015-04-21 04:42 | 2015-04-25 07:20 | 5918 | 11kV | 4837982 | 873 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12600 Lisarow - Pnl.11 tripped on: B Phase IOC, C phase timed O/C, L/O, EFI Weather related - 11kV down between Ab44030 to AB44963 tee PT11370 See 1257756 1257757 1257758 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA11 | ZN12600:PA11 | ZN12600/000011 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 5541.7892 | N | 3 | N | Y | 1.1101 | 39.4971 | 3535454.5493
[7 empty] | 12915 | 6094 | 1233999 | 2015-04-20 23:32 | 2015-04-25 09:10 | 6338 | 11kV | 6244360 | 1858 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Entered based on switching sheet Multiple faults. JV-10760 tree on LV ans mains down JV-12187 JU-30532 tree on HV feeder Feeder tripped again at 05:58 on 24/4 during restoration switching | April | 2015 | 2015Q4 | 2015 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Veg | 2015-04-20 | Y | 3360.7966 | N | 8 | N | Y | 1.1101 | 39.4971 | 4563194.1106
[7 empty] | 14369 | 17656 | 1233778 | 2015-04-20 21:44 | 2015-04-25 10:20 | 6516 | 11kV | 2410498 | 388 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | REC50247 Blackett Faunce - tripped on: O/C & L/O Storm damage see 1257014 1257017 1257020 1257021 | April | 2015 | 2015Q4 | 2015 | ZN12650:PA2 | ZN12650:PA2 | ZN12650/000002 | CENTRAL COAST | OH | Not Veg | 2015-04-20 | Y | 6212.6237 | N | 8 | N | Y | 1.1101 | 39.4971 | 1761520.8407
[7 empty] | 13450 | 10566 | 1251167 | 2015-04-21 09:54 | 2015-04-25 10:26 | 5792 | 11kV | 57108.3 | 42 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | appears as though post storm isolation, customers advised had no power issues prior to today no information supplied from control room | April | 2015 | 2015Q4 | 2015 | 205:12203 | 205:12203 | ZN00205/012203 | NEWCASTLE | OH | Veg | 2015-04-21 | Y | 1359.7214 | Y | 3 | N | Y | 1.1101 | 39.4971 | 41733.0612
[7 empty] | 12522 | 2488 | 1233574 | 2015-04-20 20:21 | 2015-04-25 10:28 | 6606.95 | 11kV | 4115580.15 | 780 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12570 Avoca Pa34 "Terrigal" fdr tripped Relays: 50T, 150TN, Lockout, EFI Weather related. See 1233574,45281,2 Exclude 1233239 | April | 2015 | 2015Q4 | 2015 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Not Veg | 2015-04-20 | Y | 5276.3848 | N | 8 | N | Y | 1.1101 | 39.4971 | 3007544.5846
[7 empty] | 13340 | 9652 | 1233751 | 2015-04-20 21:46 | 2015-04-25 10:35 | 6529.25 | 11kV | 417064.75 | 1304 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 151699 Tree fell into mains at pole JV-20029 - JV-20031 High into Low at pole JV-20033 | April | 2015 | 2015Q4 | 2015 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Veg | 2015-04-20 | Y | 319.8349 | N | 8 | N | Y | 1.1101 | 39.4971 | 304778.618
[7 empty] | 14309 | 17290 | 1235709 | 2015-04-21 04:28 | 2015-04-25 10:43 | 6135 | 11kV | 146210 | 25 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | completed based on switching sheets and operational OMS records Fault on both 8684 & 2121 feeders See OMS 1255733 for feeder 8684 Fault location for feeder 2121 not noted on swtiching sheet | April | 2015 | 2015Q4 | 2015 | 235:2121 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 5848.4 | Y | 3 | N | Y | 1.1101 | 39.4971 | 106845.9555
[7 empty] | 12920 | 6117 | 1239934 | 2015-04-21 09:00 | 2015-04-25 11:00 | 5880 | 11kV | 559278 | 1138 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID Report compiled from emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2015-04-21 | Y | 491.4569 | N | 3 | N | Y | 1.1101 | 39.4971 | 408703.8665
[7 empty] | 12911 | 6058 | 1234498 | 2015-04-21 03:31 | 2015-04-25 11:13 | 6222 | 11kV | 1510336 | 318 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | EX ZN 12690 Berkeley Vale - REC 44999 - Trip/reclose/trip, OC and IOC. Major storm in the area. ME: 1257139. Rest Steps: 1257143, 6. | April | 2015 | 2015Q4 | 2015 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 4749.4843 | N | 3 | N | Y | 1.1101 | 39.4971 | 1103709.0014
[7 empty] | 14083 | 15684 | 1233379 | 2015-04-20 18:35 | 2015-04-25 12:24 | 6829 | 11kV | 4965943 | 814 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Section of ZN.12610 Long Jetty 11kV from RE.61580 to extent of feeder tripped:- Note:- RE.61580 in scan fail at time of trip Cause:- STORM, 11kV down beyond CP.42098 to CP.43262 and also beyond CP.44709 to CP.44708 ME:-1259180 RS:-1259183, 1259182 Withdrawn:-1250941, 1233367, 1233379, 1233404, 1233411, 1233906, 1244784, 1245109, 1245422, 1247765, 1248988, 1250939, 1251149, 1254600, 1257054 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2015-04-20 | Y | 6100.6671 | N | 8 | N | Y | 1.1101 | 39.4971 | 3628964.6739
[7 empty] | 12907 | 6035 | 1234943 | 2015-04-21 06:49 | 2015-04-25 13:09 | 6140 | 11kV | 6340355 | 1588 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12570 Avoca 11kv Pa33 "Macmasters Beach" tripped Relays: 150 TN,51 C, 51 N, Lockout Multiple Trees on Mains. Wires down LK41453 Open, RE45133 Open, S12740:B Closed See 1259376,84,7,8,90,6,7 Exclude 1233882,4315,943,5330,6262,8319,9750,41549,2318,5951,6041 | April | 2015 | 2015Q4 | 2015 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 3992.6669 | N | 3 | N | Y | 1.1101 | 39.4971 | 4633344.4252
[7 empty] | 13549 | 11312 | 1236742 | 2015-04-21 07:34 | 2015-04-25 13:30 | 6116 | 11kV | 1351379 | 1463 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | ZN 14891 Wyong - Pnl 16 - Trip/reclose/trip, All phases IOC and Timed OC, Fault Check, Timing, lockout. Large tree on mains between S14849 to S64798, also between USL40139 to LB45068 tee PTs 11813 and 13098. ME: 1259399. Rest Steps: 1259400, 1. Withdrawn: 1234805, 1236742, 1243144, 1244566, 1248424, 1248987, 1253507, 8, 9, 10, 11, 12, 77. | April | 2015 | 2015Q4 | 2015 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 923.704 | N | 3 | N | Y | 1.1101 | 39.4971 | 987547.9143
[7 empty] | 14627 | 19965 | 1235053 | 2015-04-21 03:10 | 2015-04-25 14:10 | 6420 | 11kV | 3566945 | 1134 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 239:82128 | 239:82136 | ZN00239/082136 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 3145.4541 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2606618.1989
[7 empty] | 12780 | 4863 | 1236601 | 2015-04-21 11:22 | 2015-04-25 14:22 | 5940 | 11kV | 9704329 | 1750 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12650 West Gosford Pnl.13 tripped on: A & B phase IOC, A & B phase O/C, L/O Storm see 1250644 1257150 1257151 1257154 1257155 1257168 CC1: 06-"Urgent - O.H Mains - No others" FRC1: 340-"Overhead Service Line Connection at POA or Pole -Defective/Detached -Isolated & made safe" | April | 2015 | 2015Q4 | 2015 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 5545.3309 | N | 3 | N | Y | 1.1101 | 39.4971 | 7091637.404
[7 empty] | 13122 | 7797 | 1257396 | 2015-04-21 02:07 | 2015-04-25 14:35 | 6508 | 11kV | 65080 | 10 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | EX ZN 14891 Wyong - Pnl 20 - REC 47302 Hue Hue Sparks Trip/reclose/trip, Earth fault. 11kV wires down during major storm in the area. PT 14257 still interrupted due to LV cross arm broken see 1257217. | April | 2015 | 2015Q4 | 2015 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 6508 | N | 3 | N | Y | 1.1101 | 39.4971 | 47558.5445
[7 empty] | 13064 | 7341 | 1234721 | 2015-04-21 05:16 | 2015-04-25 14:37 | 6321 | 11kV | 6427581 | 1123 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Pnl 12 West Gosford Zn - REC 46928 Collard Brisbane Water tripped on: O/C and Lockout relay Storm damage beyond R46928 see 1257103 1257104 1257105 1257106 1257107 1257108 | April | 2015 | 2015Q4 | 2015 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 5723.5806 | N | 3 | N | Y | 1.1101 | 39.4971 | 4697086.6133
[7 empty] | 12299 | 435 | 1251581 | 2015-04-25 09:17 | 2015-04-25 15:20 | 363 | 11kV | 8712 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | HV fuse replaced as per cass completion comments exclude OMS 1251581 | April | 2015 | 2015Q4 | 2015 | 216:10727 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Veg | 2015-04-25 | Y | 363 | N | 5 | N | Y | 1.1101 | 39.4971 | 6366.4726
[7 empty] | 12339 | 815 | 1251325 | 2015-04-24 21:42 | 2015-04-25 15:28 | 1066 | 11kV | 189656.5 | 270 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via Emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2015-04-24 | Y | 702.4315 | Y | 3 | N | Y | 1.1101 | 39.4971 | 138595.3763
[7 empty] | 12543 | 2702 | 1252308 | 2015-04-25 14:49 | 2015-04-25 15:30 | 41.3333 | 11kV | 7150.6667 | 173 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 151758 No details in report | April | 2015 | 2015Q4 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-04-25 | N | 41.3333 | N | 5 | N | N | 1.1101 | 39.4971 | 5225.4963
[7 empty] | 13434 | 10452 | 1236188 | 2015-04-21 05:15 | 2015-04-25 15:46 | 6391 | 11kV | 7281234 | 1671 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 205:12205 | 205:12205 | ZN00205/012205 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 4357.4111 | Y | 3 | N | Y | 1.1101 | 39.4971 | 5320911.0472
[7 empty] | 14580 | 19352 | 1246026 | 2015-04-22 18:13 | 2015-04-25 15:51 | 4178.45 | 11kV | 313383.75 | 75 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Major storm event, no further information supplied via the control room | April | 2015 | 2015Q4 | 2015 | 528:83024 | 528:83024 | ZN00528/083024 | MAITLAND | OH | Veg | 2015-04-22 | Y | 4178.45 | N | 10 | N | Y | 1.1101 | 39.4971 | 229011.6012
[7 empty] | 14006 | 14980 | 1234149 | 2015-04-22 16:25 | 2015-04-25 16:05 | 4300 | 11kV | 931329 | 417 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12630 Peats Ridge 11kv pa3 "Mangrove Mtn" fdr Relays: nil Peats Ridge Zone Interrupted on loss of 33kv '720' fdr. Trees into OH and 11kv down Due to severity of storms and duration, restoration times are best estimate from bluey. IONS may prove more accurate. See 1265201,5,6,7,9,12,3,4,5,6 Exclude 1234149,49989,90,1,2,52240,3157 | April | 2015 | 2015Q4 | 2015 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2015-04-22 | Y | 2233.4029 | Y | 10 | N | Y | 1.1101 | 39.4971 | 680587.7636
[7 empty] | 12283 | 287 | 1235101 | 2015-04-21 07:33 | 2015-04-25 16:13 | 6279.7 | 11kV | 3089612.4 | 492 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | no further information supplied from control room. OMS and recored switching left as swithed by control room | April | 2015 | 2015Q4 | 2015 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 6279.7 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2257797.6138
[7 empty] | 13613 | 11818 | 1234570 | 2015-04-21 04:02 | 2015-04-25 17:00 | 6538 | 11kV | 6116434 | 1281 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn12650 West Gosford Pnl.6 tripped on: E/F timed, L/O, timing EFI Field EFI @ S11794 Weather related no cause found see 1257072 1257080 1257075 1257085 1257086 1257090 1257085 1257089 | April | 2015 | 2015Q4 | 2015 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 4774.7338 | N | 3 | N | Y | 1.1101 | 39.4971 | 4469709.5629
[7 empty] | 12856 | 5599 | 1234695 | 2015-04-21 05:06 | 2015-04-25 17:10 | 6484 | 11kV | 2879123 | 1041 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12570 Avoca Pa35 "Kincumber" fdr trippeed on 51ABC, lockout relays, EFI Trees on OH beyond CP61952 See 1259026,7,8 exclude 1234695 | April | 2015 | 2015Q4 | 2015 | ZN12570:PA35 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 2765.7281 | N | 3 | N | Y | 1.1101 | 39.4971 | 2103978.1686
[7 empty] | 12518 | 2446 | 1233644 | 2015-04-21 03:41 | 2015-04-25 17:19 | 6578 | 11kV | 5216080 | 968 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12660 Woy Woy Pnl.6 tripped on: C phase timed O/C, L/O Weather realted see 1258058 1258062 1258063 1258065 | April | 2015 | 2015Q4 | 2015 | ZN12660:PA6 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 5388.5124 | N | 3 | N | Y | 1.1101 | 39.4971 | 3811757.4157
[7 empty] | 14525 | 18926 | 1252536 | 2015-04-25 16:51 | 2015-04-25 18:13 | 82.25 | 11kV | 3125.5 | 38 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | LID 151760 Repair storm damage | April | 2015 | 2015Q4 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-04-25 | N | 82.25 | N | 5 | N | N | 1.1101 | 39.4971 | 2284.0232
[7 empty] | 13586 | 11588 | 1242355 | 2015-04-21 18:06 | 2015-04-25 18:18 | 5772 | 11kV | 8721492 | 1511 | HV | Vegetation Blow/Fall In | Vegetation | Air Break Switch | Unplanned | Rain Wind Storm | Y | Entered based on switching sheet Tree on ABS 23002 | April | 2015 | 2015Q4 | 2015 | 223:14394 | 223:14394 | ZN00223/014394 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 5772 | Y | 3 | N | Y | 1.1101 | 39.4971 | 6373409.1131
[7 empty] | 13696 | 12462 | 1241494 | 2015-04-22 09:08 | 2015-04-25 18:49 | 4900.5833 | 11kV | 749789.25 | 153 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | PT13065 Ashton Oakland Dist 1 "Duncan st" & Dist 2 "Ashton Oakland" blown due to Storm Damage Major Event Storm See 1241494 exclude 1239305,45613 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2015-04-22 | Y | 4900.5833 | Y | 10 | N | Y | 1.1101 | 39.4971 | 547923.8689
[7 empty] | 12293 | 365 | 1238123 | 2015-04-21 18:16 | 2015-04-25 18:54 | 5798 | 11kV | 2707666 | 467 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Ex ZN 14891 Wyong - REC 48838 - Trip/reclose/trip, OC. Weather related outage. See 1257229 exclude 1238123,53708,990 | April | 2015 | 2015Q4 | 2015 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 5798 | N | 3 | N | Y | 1.1101 | 39.4971 | 1978682.4502
[7 empty] | 13887 | 13966 | 1242287 | 2015-04-23 12:46 | 2015-04-25 18:57 | 3251 | 11kV | 1566404 | 644 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Flood | Y | Note this group of customer experienced delayed restoration due to flooding refer to primary event 1262867 (all customers lost supply approx 12:55 on the 20th April DIFFICULT_ACCESS due to flooding, as per Brett Burchill Note also - minor overlap in times with OMS 1262867 | April | 2015 | 2015Q4 | 2015 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Veg | 2015-04-23 | Y | 2432.3043 | Y | 4 | N | Y | 1.1101 | 39.4971 | 1144681.8421
[7 empty] | 13673 | 12309 | 1235145 | 2015-04-21 03:20 | 2015-04-25 19:10 | 6710 | 11kV | 4329252 | 2167 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Mains down at pole JV81961 compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 1997.809 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3163689.6703
[7 empty] | 14156 | 16204 | 1233997 | 2015-04-21 02:36 | 2015-04-25 19:41 | 6785 | 11kV | 3728432.75 | 793 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID Report Tree on Mains Compiled via emergency switching sheet also not sub 19327:LV was affected by LV mains on ground at pole IV-40239 Feeder tripped on restore after zone outage | April | 2015 | 2015Q4 | 2015 | 225:33670 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 4701.6806 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2724628.6836
[7 empty] | 14103 | 15807 | 1252383 | 2015-04-25 13:35 | 2015-04-25 20:17 | 402 | 11kV | 3618 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | no information supplied from control room. Appears from the operation of OMS from the Control Room, that both subs was isolated post storm | April | 2015 | 2015Q4 | 2015 | 503:48017 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Veg | 2015-04-25 | N | 402 | N | 5 | N | N | 1.1101 | 39.4971 | 2643.9277
[7 empty] | 14385 | 17789 | 1262432 | 2015-04-21 | 2015-04-25 20:20 | 6980 | 11kV | 700162 | 191 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID Report compiled via emergency switching sheet Note: customers also affected by outages on records 1261826 and 1261827 which carry on from 21/04/2015 02:08:00 | April | 2015 | 2015Q4 | 2015 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 3665.7696 | Y | 3 | N | Y | 1.1101 | 39.4971 | 511657.7383
[7 empty] | 13833 | 13497 | 1252819 | 2015-04-25 18:45 | 2015-04-25 20:30 | 105 | 11kV | 9135 | 87 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | PT15630 Hudson Georgia Lee - Interrupted on HV side To removed tree adjacent to PT | April | 2015 | 2015Q4 | 2015 | ZN15004:PA5 | ZN15004:PA5 | ZN15004/000005 | NORTHERN BEACHES | OH | Veg | 2015-04-25 | N | 105 | N | 5 | N | N | 1.1101 | 39.4971 | 6675.5886
[7 empty] | 12890 | 5912 | 1234429 | 2015-04-21 02:49 | 2015-04-25 20:40 | 6831 | 11kV | 2614381 | 829 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14144 Wamberal Pnl.4 tripped on: B phase IOC, L/O, EFI Storm See 1257954 1257956 1257957 1257959 1257961 | April | 2015 | 2015Q4 | 2015 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 3153.6562 | N | 3 | N | Y | 1.1101 | 39.4971 | 1910512.5236
[7 empty] | 13892 | 14047 | 1246284 | 2015-04-21 09:06 | 2015-04-25 20:52 | 6466.2167 | 11kV | 420304.0833 | 65 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | advised by customer - No power since Tuesday 21st April. Possible uncornfirmed damage to mains on Virgo St. no further information supplied via the control room | April | 2015 | 2015Q4 | 2015 | 258:80785 | 258:80785 | ZN00258/080785 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 6466.2167 | Y | 3 | N | Y | 1.1101 | 39.4971 | 307145.8272
[7 empty] | 13119 | 7780 | 1245628 | 2015-04-23 10:57 | 2015-04-25 21:00 | 3483 | 11kV | 2606144 | 764 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | Y | NO LID Conductor on crossarm Compile from emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 228:7491 | 228:85415 | ZN00228/085415 | NEWCASTLE | OH | Not Veg | 2015-04-23 | Y | 3411.1832 | Y | 4 | N | Y | 1.1101 | 39.4971 | 1904493.167
[7 empty] | 14591 | 19485 | 1252112 | 2015-04-25 20:54 | 2015-04-25 22:30 | 96 | 11kV | 123069 | 1623 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | NO LID report compiled via emergency switching sheets no additional information available | April | 2015 | 2015Q4 | 2015 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Veg | 2015-04-25 | Y | 75.8281 | N | 5 | N | Y | 1.1101 | 39.4971 | 89935.1953
[7 empty] | 14066 | 15540 | 1252622 | 2015-04-25 22:20 | 2015-04-25 23:53 | 93 | 11kV | 56729 | 701 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | Y | ZN 12690 Berkeley Vale - Pnl 10 - Trip/reclose/trip, A phase Timed OC, RTD, lockout. Lightning arrestor blown at PT 12642. ME: 1257109. Rest Steps: 1257112, 3. Withdrawn: 1252622, 830. | April | 2015 | 2015Q4 | 2015 | ZN12690:PA10 | ZN12690:PA10 | ZN12690/000010 | CENTRAL COAST | OH | Not Veg | 2015-04-25 | N | 80.9258 | N | 5 | N | N | 1.1101 | 39.4971 | 41455.88
[7 empty] | 14121 | 16003 | 1246919 | 2015-04-21 07:07 | 2015-04-26 08:13 | 7266 | 11kV | 6551970 | 1636 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID report Compiled via SCADA, emergency switching sheet and OMS | April | 2015 | 2015Q4 | 2015 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 4004.8716 | Y | 3 | N | Y | 1.1101 | 39.4971 | 4787986.4256
[7 empty] | 13677 | 12362 | 1234693 | 2015-04-20 23:32 | 2015-04-26 08:30 | 7738 | 11kV | 5746171 | 1930 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | Y | Zn15004 Newport Pnl.9 tripped on: A & B phase O/C 11kV UGOH below PT15467 is defective short circuit. Isolated from AB21783 to S16868 to S16681 tee PT15467. PT15467 restored 24/4/15 16:00 Weather related - See also multiple LV dist issues which occured during Pnl.9 outage which extended their outage Pnl 9 Outage: 1256140 1256143 1256151 LV dist issues (SE): 1256144 1256145 1256146 1256138 | April | 2015 | 2015Q4 | 2015 | ZN15004:PA9 | ZN15004:PA9 | ZN15004/000009 | NORTHERN BEACHES | Unknown | Unknown | 2015-04-20 | Y | 2977.2907 | N | 8 | N | Y | 1.1101 | 39.4971 | 4199132.2834
[7 empty] | 13482 | 10790 | 1241435 | 2015-04-21 19:38 | 2015-04-26 09:15 | 6577 | 11kV | 1449589 | 1097 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled via emergency switching sheets Excludes OMS 1241435 | April | 2015 | 2015Q4 | 2015 | 213:33775 | 213:33775 | ZN00213/033775 | NEWCASTLE | OH | Veg | 2015-04-21 | Y | 1321.412 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1059316.8856
[7 empty] | 12914 | 6083 | 1256417 | 2015-04-25 20:36 | 2015-04-26 10:41 | 845 | 11kV | 168155 | 199 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Electrical Storm | Y | LID 151762 CAr hit sub pole 50884 Mercury sub Excludes OMS 1252952 | April | 2015 | 2015Q4 | 2015 | 528:83024 | 528:83024 | ZN00528/083024 | MAITLAND | OH | Not Veg | 2015-04-25 | Y | 845 | N | 5 | N | Y | 1.1101 | 39.4971 | 122882.7143
[7 empty] | 14196 | 16475 | 1234348 | 2015-04-21 02:28 | 2015-04-26 10:46 | 7698 | 11kV | 1316279 | 985 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN 14891 Wyong - Pnl 10 - Trip/reclose/trip, A & B phase OC, All phases IOC, EFI Fault Check, Timing, Lockout. 11kV UG cable fault from S 14857 to LV 40095 tee S 14785. Also, HV down beyond AB44472. ME: 1260890. Rest Steps: 1260893, 4. Withdrawn: 1234348, 1243769, 1248432. | April | 2015 | 2015Q4 | 2015 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 1336.3239 | N | 3 | N | Y | 1.1101 | 39.4971 | 961897.8695
[7 empty] | 13682 | 12396 | 1235072 | 2015-04-21 02:45 | 2015-04-26 11:20 | 7715 | 11kV | 2466503 | 468 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled via emergency switching sheets Includes OMS 1262696/98/99 Excludes OMS 1235072, 1258570 | April | 2015 | 2015Q4 | 2015 | 213:33777 | 213:33777 | ZN00213/033777 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 5270.3056 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1802447.6429
[7 empty] | 12923 | 6132 | 1234544 | 2015-04-21 09:38 | 2015-04-26 11:30 | 7312 | 11kV | 10787799 | 2120 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN.12580 Erina 11kV Panel 4 tripped:- Cause:- STORM, OH mains down reported on PT.11621 & PT12779 interruption reports ME:-1259010 RS:-1259019, 1259021, 1259023, 1259022, 1259034, 1259020, 1259035, 1259024, 1259038, 1259039 Withdrawn:-1249806, 1249333, 1248340, 1248149, 1246876, 1245358, 1244534, 1242990, 1251919, 1234544, 1251810, 1251809, 1251808, 1251811 | April | 2015 | 2015Q4 | 2015 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 5088.5844 | N | 3 | N | Y | 1.1101 | 39.4971 | 7883405.323
[7 empty] | 14260 | 16966 | 1234157 | 2015-04-21 01:01 | 2015-04-26 12:15 | 7874 | 11kV | 180299 | 33 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn12600 Lisarow P2 - REC42120 Holgate tripped on O/C & L/O Weather related - storm see 1257642 1257646 1257648 1257649 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 5463.6061 | N | 3 | N | Y | 1.1101 | 39.4971 | 131757.1913
[7 empty] | 12992 | 6769 | 1253425 | 2015-04-26 10:41 | 2015-04-26 12:25 | 104 | 11kV | 520 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 151763 B & C phase DOLF : 10 Amp | April | 2015 | 2015Q4 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-04-26 | N | 104 | N | 3 | N | N | 1.1101 | 39.4971 | 380.0007
[7 empty] | 14469 | 18490 | 1253197 | 2015-04-21 16:33 | 2015-04-26 12:27 | 6954 | 11kV | 4704352 | 1026 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14144 Wamberal Pnl.7 tripped Major storm See 1258802 1258804 1258806 | April | 2015 | 2015Q4 | 2015 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 4585.1384 | N | 3 | N | Y | 1.1101 | 39.4971 | 3437801.6867
[7 empty] | 13295 | 9063 | 1234028 | 2015-04-20 23:44 | 2015-04-26 12:43 | 7979 | 11kV | 4280294 | 577 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Section of ZN.12580 Erina 11kV Panel 16 from RE.46673 to extent of feeder (14 DC's) tripped and locked out on:- Relays:- I/O/C, O/C, L/O Cause:- STORM, tree branch on OH mains near ABS.40402, PT.11274 damaged by tree and HV down ME:-1257656 RS:-1257664, 1257667 Withdrawn:-1248536, 1234028, 1252513, 1252577, 1253139 | April | 2015 | 2015Q4 | 2015 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2015-04-20 | Y | 7418.1872 | N | 8 | N | Y | 1.1101 | 39.4971 | 3127912.6079
[7 empty] | 13458 | 10614 | 1253624 | 2015-04-25 21:01 | 2015-04-26 13:03 | 962 | 11kV | 962 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | no further information supplied by control room operation of OMS by control room, record left as is | April | 2015 | 2015Q4 | 2015 |  |  |  | NEWCASTLE | OH | Veg | 2015-04-25 | Y | 962 | Y | 5 | N | Y | 1.1101 | 39.4971 | 703.0012
[7 empty] | 12835 | 5392 | 1234295 | 2015-04-21 02:08 | 2015-04-26 14:00 | 7912 | 11kV | 1199347 | 162 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled from switching sheets Excludes OMS 1261827, 1249034, 1253000, 1254085/86/87 | April | 2015 | 2015Q4 | 2015 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Veg | 2015-04-21 | Y | 7403.3765 | Y | 3 | N | Y | 1.1101 | 39.4971 | 876447.4129
[7 empty] | 13385 | 10032 | 1236441 | 2015-04-21 20:22 | 2015-04-26 14:03 | 6821 | 11kV | 600248 | 88 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | R.Cook opened LV and HV fused. LV mains down No LID report, major storm, no further information supplied start + restore times adjusted per OMS 1240189 CC1: 06-"Urgent - O.H Mains - No others" | April | 2015 | 2015Q4 | 2015 | 222:33601 | 222:33601 | ZN00222/033601 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 6821 | Y | 3 | N | Y | 1.1101 | 39.4971 | 438643.5341
[7 empty] | 14634 | 20021 | 1240586 | 2015-04-21 03:34 | 2015-04-26 14:15 | 7841 | 11kV | 2040624 | 991 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Entered based on switching sheets. No cause listed on switching sheets | April | 2015 | 2015Q4 | 2015 | 242:81538 | 242:81538 | ZN00242/081538 | PORT STEPHENS | OH | Veg | 2015-04-21 | Y | 2059.1564 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1491227.831
[7 empty] | 13847 | 13650 | 1246046 | 2015-04-23 08:21 | 2015-04-26 14:34 | 4693.0667 | 11kV | 6748629.8667 | 1438 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Major storm, no further information supplied by control room. assuming record is correct as per customer calls, and operation of OMS from control room staff customers also impacted by event 1259341 | April | 2015 | 2015Q4 | 2015 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2015-04-23 | Y | 4693.0667 | Y | 4 | N | Y | 1.1101 | 39.4971 | 4931699.6557
[7 empty] | 14320 | 17334 | 1237085 | 2015-04-21 03:32 | 2015-04-26 14:46 | 7874 | 11kV | 2198150 | 1178 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2015-04-21 | Y | 1866.0017 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1606343.1856
[7 empty] | 14528 | 18932 | 1246194 | 2015-04-23 08:52 | 2015-04-26 14:49 | 4677.1167 | 11kV | 14031.35 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | no information supplied from control room. Appears from the operation of OMS from the Control Room, that sub was isolated during storm | April | 2015 | 2015Q4 | 2015 | 216:10724 | 216:10724 | ZN00216/010724 | NEWCASTLE | OH | Veg | 2015-04-23 | Y | 4677.1167 | Y | 4 | N | Y | 1.1101 | 39.4971 | 10253.6967
[7 empty] | 14021 | 15167 | 1242505 | 2015-04-22 11:36 | 2015-04-26 15:40 | 6004.4333 | 11kV | 120088.6667 | 20 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled from switching sheets | April | 2015 | 2015Q4 | 2015 | 265:81649 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Not Veg | 2015-04-22 | Y | 6004.4333 | Y | 10 | N | Y | 1.1101 | 39.4971 | 87757.2556
[7 empty] | 12425 | 1595 | 1234110 | 2015-04-21 07:07 | 2015-04-26 15:50 | 7723 | 11kV | 3585241 | 1760 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching report | April | 2015 | 2015Q4 | 2015 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 2037.0687 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2619988.3761
[7 empty] | 12408 | 1470 | 1259825 | 2015-04-20 22:34 | 2015-04-26 16:06 | 8252 | 11kV | 57764 | 7 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | 11Kv recloser CP61084 bushells peats tripped Cause: Thunderstorm | April | 2015 | 2015Q4 | 2015 | ZN12630:PA5 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2015-04-20 | Y | 8252 | N | 8 | N | Y | 1.1101 | 39.4971 | 42212.2275
[7 empty] | 12311 | 532 | 1242495 | 2015-04-21 01:39 | 2015-04-26 16:42 | 8103 | 11kV | 324671 | 41 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 265:81645 | 265:81645 | ZN00265/081645 | PORT STEPHENS | OH | Veg | 2015-04-21 | Y | 7918.8049 | Y | 3 | N | Y | 1.1101 | 39.4971 | 237259.9906
[7 empty] | 13567 | 11441 | 1234847 | 2015-04-21 06:07 | 2015-04-26 16:48 | 7841 | 11kV | 3920554 | 1017 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S14144 Wamberal The Glen Eagles Firway Panel 2 tripped reclosed tripped and locked out on overcurrent Cause: rain wind strom See OMS 1257505 1257510 1257511 1257515 1234078 1252410 1252411 1252412 1252413 1234847 1249207 | April | 2015 | 2015Q4 | 2015 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 3855.0187 | N | 3 | N | Y | 1.1101 | 39.4971 | 2865025.2264
[7 empty] | 13056 | 7223 | 1243913 | 2015-04-21 13:52 | 2015-04-26 17:10 | 7398 | 11kV | 379986 | 57 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn2400 Berowra section of pa11 "Brooklyn" Re1238 Milsons Passage tripped on overcurrent Mains to Patrol feeder on 25/4/15 AM HV wires down. Boat Access only. See 1256963,70,1 Exclude 1243913,7745,9976,50649,1543 | April | 2015 | 2015Q4 | 2015 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2015-04-21 | Y | 6666.4211 | Y | 3 | N | Y | 1.1101 | 39.4971 | 277682.5611
[7 empty] | 14272 | 17039 | 1233898 | 2015-04-20 22:36 | 2015-04-26 17:13 | 8316.5333 | 11kV | 7856389.7333 | 2408 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled from emergency switching sheets Includes OMS 1263531/35/36/38/40/42/44/46/49/50/52/53/54 Excludes OMS 1233898 | April | 2015 | 2015Q4 | 2015 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2015-04-20 | Y | 3262.6203 | N | 8 | N | Y | 1.1101 | 39.4971 | 5741217.8929
[7 empty] | 14254 | 16933 | 1242091 | 2015-04-22 00:53 | 2015-04-26 17:31 | 6758 | 11kV | 7854439 | 1166 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | Y | No LID report Major storm Compiled via emergency switching sheets Includes OMS 1255758/63/64/65 Excludes OMS 1241933/2091/2130, 1251257/58/60, 1254185/211/212/213 | April | 2015 | 2015Q4 | 2015 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2015-04-22 | Y | 6736.2256 | N | 10 | N | Y | 1.1101 | 39.4971 | 5739792.3545
[7 empty] | 12774 | 4807 | 1233456 | 2015-04-20 22:20 | 2015-04-26 17:35 | 8355 | 11kV | 4829763 | 860 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12600 Lisarow Pnl.13 tripped on: B Phase O/C, L/O Storm See 1257507 1257513 1257514 12575181257519 1257525 1257526 1257527 1257528 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2015-04-20 | Y | 5616.0035 | N | 8 | N | Y | 1.1101 | 39.4971 | 3529448.3465
[7 empty] | 13185 | 8282 | 1233364 | 2015-04-21 01:35 | 2015-04-26 17:50 | 8175 | 11kV | 5742208 | 740 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14143 Somersby Pnl.17 tripped and locked out Weather related - multiple issues along feeder see 1258215 1258216 1258221 1258222 1258224 1258226 1258228 1258231 1258232 1258233 1258234 | April | 2015 | 2015Q4 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 7759.7405 | N | 3 | N | Y | 1.1101 | 39.4971 | 4196236.2399
[7 empty] | 13635 | 12007 | 1234767 | 2015-04-21 05:36 | 2015-04-26 18:00 | 7944 | 11kV | 1706898 | 326 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | @ ZN.12580 Erina 11kV Panel 12 feeder tripped, reclosed, tripped and locked out Relays:- A & B phase timed O/C, reclose and lockout Cause:- 11kV down at (1. tee to ABS.44966) & (2. tee S.12035) Note:- No interruption report for S.18172 LV Dist.3, estimated restoration time made at 8 hours from last call of NS, 26/04/15 @ 18:00hrs - OMS:1252627 ME:-1257766 RS:-1257781, 1257789 Withdrawn:-1234767, 1252106, 1252627 | April | 2015 | 2015Q4 | 2015 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 5235.8834 | N | 3 | N | Y | 1.1101 | 39.4971 | 1247350.7134
[7 empty] | 12679 | 3954 | 1234312 | 2015-04-21 02:09 | 2015-04-26 19:50 | 8261 | 11kV | 636097 | 77 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn14891 Wyong section of pa5 "Wyong" fdr RE45017 Witeman tripped reclosed tripped and locked out on relays: Overcurrent Major Storm. | April | 2015 | 2015Q4 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 8261 | N | 3 | N | Y | 1.1101 | 39.4971 | 464840.9259
[7 empty] | 13821 | 13408 | 1235919 | 2015-04-21 08:30 | 2015-04-26 20:20 | 7910 | 11kV | 1187397 | 823 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | ZN 12690 Berkeley Vale - Pnl 24 - Trip/reclose/trip, Right Leg, Trip, alarm, A & B phase IOC, EFI. Branch removed from mains near LB49513. ME: 1257195. Rest Steps: 1257195, 7, 8, 202, 5, 7, 8, 9, 11. Withdrawn: 1234026, 1235437, 919, 1245396, 1278775, 6, 1255679. | April | 2015 | 2015Q4 | 2015 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 1442.7667 | N | 3 | N | Y | 1.1101 | 39.4971 | 867714.7053
[7 empty] | 13449 | 10554 | 1234980 | 2015-04-21 02:56 | 2015-04-26 20:55 | 8279 | 11kV | 8963405 | 1862 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID Tree on mains between 21998-42754-501, tree into mains IV-80218 Excludes OMS 1234980, 1263017, 1263018, 1263019, 1263020, 1263021, 1263022, 1263026, 1263027, 1263028, 1263029 | April | 2015 | 2015Q4 | 2015 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 4813.8588 | Y | 3 | N | Y | 1.1101 | 39.4971 | 6550191.9983
[7 empty] | 13656 | 12166 | 1243607 | 2015-04-21 11:54 | 2015-04-26 21:00 | 7746 | 11kV | 9235193 | 1948 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN.36200 Empire Bay 11kV Panel 11 tripped:- Relays:- B phase IOC Cause:- STORM, storm damag along feeder - ABS.43208 closed and S.14569 SW/B opened to restore previous switching ME:-1258249 RS:-1258251, 1258257, 1258250, 1258252, 1258256 Withdrawn:-1243607, 1244075, 1244219, 1244341, 1244863, 1246253, 1248985, 1251162, 1251554, 1251722 | April | 2015 | 2015Q4 | 2015 | ZN36200:PA11 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 4740.8588 | N | 3 | N | Y | 1.1101 | 39.4971 | 6748806.6523
[7 empty] | 13631 | 11940 | 1263103 | 2015-04-21 01:45 | 2015-04-26 21:02 | 8357.45 | 11kV | 4409704.45 | 692 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 6372.4053 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3222481.9478
[7 empty] | 14506 | 18765 | 1251389 | 2015-04-25 20:14 | 2015-04-26 23:15 | 1621 | 11kV | 608451 | 704 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN 14891 Wyong - Pnl 12 - SEL. Tree brought 11kV mains down near tee of to PT 13285. ME: 1257848. Rest Steps: 1257849, 53, 6, 8, 9, 63, 4, 5. Withdrawn: 1251389, 1252939. | April | 2015 | 2015Q4 | 2015 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2015-04-25 | Y | 864.277 | Y | 5 | N | Y | 1.1101 | 39.4971 | 444638.0445
[7 empty] | 14105 | 15829 | 1254118 | 2015-04-26 17:49 | 2015-04-27 03:24 | 575 | 11kV | 28597 | 205 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | LID 151766 Sensitive Earth Fault SEF 16 Amp. Excludes OMS 1254118, 1254324, 1262458, 1262459, 1262460, 1262462, 1262464, 1262465, 1262466, 1262469, 1262470 | April | 2015 | 2015Q4 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2015-04-26 | N | 139.4976 | N | 3 | N | N | 1.1101 | 39.4971 | 20897.8441
[7 empty] | 13375 | 9930 | 1252462 | 2015-04-25 16:10 | 2015-04-27 09:08 | 2458.1167 | 11kV | 27039.2833 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | no further information supplied, appears sub fuse blown post storm assuming operation of OMS from the control room is correct | April | 2015 | 2015Q4 | 2015 | 243:80080 | 243:80080 | ZN00243/080080 | LAKE MACQUARIE | OH | Veg | 2015-04-25 | Y | 2458.1167 | Y | 5 | N | Y | 1.1101 | 39.4971 | 19759.5107
[7 empty] | 13998 | 14924 | 1265373 | 2015-04-21 16:30 | 2015-04-27 09:38 | 8228 | 11kV | 6068324 | 1598 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report compiled via emergency switching sheet 11kV mains in LV pole GW 50022-23 | April | 2015 | 2015Q4 | 2015 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 3797.4493 | Y | 3 | N | Y | 1.1101 | 39.4971 | 4434552.1939
[7 empty] | 13140 | 7908 | 1235347 | 2015-04-21 08:19 | 2015-04-27 10:08 | 8748.6667 | 11kV | 3302240.3333 | 847 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | NO LID report Compiled from emergency switching sheet Tree in mains JU-20917 | April | 2015 | 2015Q4 | 2015 | 210:8681 | 210:83473 | ZN00210/083473 | NEWCASTLE | OH | Veg | 2015-04-21 | Y | 3898.7489 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2413179.836
[7 empty] | 12928 | 6222 | 1234218 | 2015-04-21 01:32 | 2015-04-27 10:20 | 9168 | 11kV | 7705640 | 1487 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12600 Lisarow Pnl.9 tripped on: A phase O/C & L/O Weather related - storm see 1257713 1257714 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 5182.004 | N | 3 | N | Y | 1.1101 | 39.4971 | 5631054.4341
[7 empty] | 12973 | 6590 | 1252624 | 2015-04-25 17:26 | 2015-04-27 11:49 | 2543 | 11kV | 7629 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | LID 151765 Single phase DOLF : 10 Amp Replaced DOLF at sub 43804& repaired hanging LL lead at sub 70506 Excluded OMS 1253535 Mrs Grainger conf power back on - High Voltage Fuse - Replaced also refer to OMS 1252624 | April | 2015 | 2015Q4 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-04-25 | Y | 2543 | N | 5 | N | Y | 1.1101 | 39.4971 | 5575.0482
[7 empty] | 13818 | 13394 | 1236099 | 2015-04-21 09:53 | 2015-04-27 12:00 | 8767 | 11kV | 1437788 | 164 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No infomration from control room, 14 calls from customers on DC advising NO Supply and wires down. Assumption made fuse blown | April | 2015 | 2015Q4 | 2015 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 8767 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1050693.0628
[7 empty] | 12899 | 5956 | 1234567 | 2015-04-21 04:06 | 2015-04-27 12:10 | 9124 | 11kV | 6432511 | 1434 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN 14891 Wyong - Pnl 5 - Trip/reclose/trip, B phase OC, OC & EF, Fault check, timing, lockout. Multiple wires down during major storm in the area. ME: 1257795. Rest Step: 1257797, 8, 800, 2, 4, 5, 7, 8, 9. Withdrawn: 1234312, 46, 567, 1248872, 1253562, 3, 608. | April | 2015 | 2015Q4 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 4485.712 | N | 3 | N | Y | 1.1101 | 39.4971 | 4700689.3118
[7 empty] | 13042 | 7098 | 1248961 | 2015-04-21 04:48 | 2015-04-27 12:20 | 9092 | 11kV | 472900 | 89 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID - entered based off switching sheets and operational OMS records. Assumed multiple faults on feeder section - no information as to faults on switching sheets | April | 2015 | 2015Q4 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | OH | Veg | 2015-04-21 | Y | 5313.4831 | Y | 3 | N | Y | 1.1101 | 39.4971 | 345581.3718
[7 empty] | 13195 | 8406 | 1234338 | 2015-04-21 07:45 | 2015-04-27 12:30 | 8925 | 11kV | 6543687 | 1045 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Entered based on swithcing sheets. Multiple faults on feeder 14395 after severe storms | April | 2015 | 2015Q4 | 2015 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 6261.9014 | Y | 3 | N | Y | 1.1101 | 39.4971 | 4781933.4535
[7 empty] | 14166 | 16261 | 1234239 | 2015-04-21 21:45 | 2015-04-27 12:30 | 8085 | 11kV | 2252928 | 396 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Ex Zn12690 Berkeley Vale section of Pa6 IR44444 Geoffrey Boyle tripped and lock out on Relays: Overcurrent Major Storm See 1243433,7292,52380 | April | 2015 | 2015Q4 | 2015 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 5689.2121 | N | 3 | N | Y | 1.1101 | 39.4971 | 1646373.3323
[7 empty] | 13905 | 14172 | 1257466 | 2015-04-21 21:45 | 2015-04-27 12:30 | 8085 | 11kV | 2252373 | 396 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | EX ZN 12690 Berkeley Vale - Pnl 6 - IR44444 Geoffrey Royle - Trip/reclose/trip, OC. Major storm in the area. ME: 1257466. Rest Steps: 1257470, 1. | April | 2015 | 2015Q4 | 2015 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 5687.8106 | N | 3 | N | Y | 1.1101 | 39.4971 | 1645967.7546
[7 empty] | 13043 | 7104 | 1235930 | 2015-04-21 04:52 | 2015-04-27 12:36 | 9104 | 11kV | 1003504 | 128 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Completed from switching sheets - no LID | April | 2015 | 2015Q4 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2015-04-21 | Y | 7839.875 | N | 3 | N | Y | 1.1101 | 39.4971 | 733331.1248
[7 empty] | 13714 | 12632 | 1254536 | 2015-04-27 09:04 | 2015-04-27 12:40 | 216 | 11kV | 36168 | 635 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn12640 Umina Pa1 tripped and locked out Relays: Timed Earth Fault, EFI, Reclose & Lockout Signals: 11kv trip Vehicle Hit Poel Near PT133356 Hillview Veron White BMW. Rego BWU39D See 1257233,4,5,6 Exclude 1254536,796 | April | 2015 | 2015Q4 | 2015 | ZN12640:PA1 | ZN12640:PA1 | ZN12640/000001 | CENTRAL COAST | OH | Not Veg | 2015-04-27 | N | 56.9575 | N | 8 | N | N | 1.1101 | 39.4971 | 26430.5076
[7 empty] | 14442 | 18239 | 1245820 | 2015-04-22 16:25 | 2015-04-27 13:10 | 7005 | 11kV | 1940014 | 320 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S12360 Peats Ridge Panel 4 - A and C phase OC Timing Reclose and Lockout See OMS 1262255/1262658/1262656/1262659 see excluded OMS 1245820 | April | 2015 | 2015Q4 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2015-04-22 | Y | 6062.5437 | Y | 10 | N | Y | 1.1101 | 39.4971 | 1417705.0105
[7 empty] | 14130 | 16065 | 1255412 | 2015-04-25 19:34 | 2015-04-27 13:15 | 2501 | 11kV | 147559 | 59 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | Y | No LID report Compiled via emergency switching sheet Pole Transformer failed in service | April | 2015 | 2015Q4 | 2015 | 228:7491 | 228:85415 | ZN00228/085415 | NEWCASTLE | OH | Not Veg | 2015-04-25 | Y | 2501 | Y | 5 | N | Y | 1.1101 | 39.4971 | 107831.7649
[7 empty] | 12873 | 5737 | 1251370 | 2015-04-23 11:59 | 2015-04-27 13:25 | 5845.85 | 11kV | 719039.55 | 123 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | 27/04/15 07:36 t44650: Dop attended all on - distributor issues - no bluey 24/04/15 12:02 t39745: associated 11kv feeder restored 21/4 @2155 | April | 2015 | 2015Q4 | 2015 | ZN12640:PA19 | ZN12660:PA5 | ZN12660/000005 | CENTRAL COAST | OH | Not Veg | 2015-04-23 | Y | 5845.85 | Y | 4 | N | Y | 1.1101 | 39.4971 | 525452.8951
[7 empty] | 12405 | 1458 | 1252785 | 2015-04-25 18:43 | 2015-04-27 13:28 | 2565.45 | 11kV | 102618 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | appears customer lost supply again at DC level no further information supplied by control room | April | 2015 | 2015Q4 | 2015 | 256:80632 | 256:80632 | ZN00256/080632 | NEWCASTLE | OH | Veg | 2015-04-25 | Y | 2565.45 | Y | 5 | N | Y | 1.1101 | 39.4971 | 74990.2077
[7 empty] | 13836 | 13511 | 1234201 | 2015-04-21 01:53 | 2015-04-27 13:45 | 9352 | 11kV | 757462 | 118 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching | April | 2015 | 2015Q4 | 2015 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 6419.1695 | Y | 3 | N | Y | 1.1101 | 39.4971 | 553530.8883
[7 empty] | 12855 | 5596 | 1234585 | 2015-04-21 04:16 | 2015-04-27 13:55 | 9219 | 11kV | 8729685 | 2016 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12640 Umina 11kv Pa13 "Patonga" tripped Relays: A 7 C phase IOC, EF, EFI Weather related. Many Trees on mains. See 1257535 1257539 1257541 1257542 1257544 Exclude 1234585 1244087 1245197 1245738 1248129 1248461 1248814 1249650 1252679 1252689 | April | 2015 | 2015Q4 | 2015 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 4330.2009 | N | 3 | N | Y | 1.1101 | 39.4971 | 6379396.3159
[7 empty] | 12723 | 4392 | 1258646 | 2015-04-21 04:59 | 2015-04-27 14:24 | 9205 | 11kV | 5445866 | 1472 | HV | Vegetation Blow/Fall In | Vegetation | UGOH | Unplanned | Electrical Storm | Y | NO LID reoprt Compiled from emergency switching sheets various subs with storm damage | April | 2015 | 2015Q4 | 2015 | 220:8687 | 220:8687 | ZN00220/008687 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 3699.6372 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3979678.2469
[7 empty] | 12879 | 5831 | 1256278 | 2015-04-27 13:01 | 2015-04-27 14:33 | 92 | 11kV | 193702 | 2152 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2466 Flemington 11kv Pnl 41 "Parramatta Alban, etc" feeder tripped on A and B phase IOC with fault check Signals: 11kv trip, Tx 3 gorup and zone earth with efi Field efis: Sub 7703, 7742 and 8323 Abnormal: sw/A closed at S35056 and sw/A opened at S3407 (cable fault) Remarks: UG fault. Cable fault between S7742 Percy Hall #4 to Sub 8323 Station Raw #2. Also efi oeprated incorrectly at S8323 | April | 2015 | 2015Q4 | 2015 | ZN2466:PA25 | ZN167:PA13 | ZN00167/000013 | CUMBERLAND | UG | Not Veg | 2015-04-27 | N | 90.0102 | N | 8 | N | N | 1.1101 | 39.4971 | 141551.7084
[7 empty] | 13603 | 11726 | 1237353 | 2015-04-21 12:27 | 2015-04-27 14:35 | 8768 | 11kV | 4588606 | 933 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | No LID report compiled via emergency switching sheets. Various subs sustained storm damage | April | 2015 | 2015Q4 | 2015 | 221:11895 | 221:11895 | ZN00221/011895 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 4918.12 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3353217.9238
[7 empty] | 13155 | 8020 | 1262482 | 2015-04-21 02:23 | 2015-04-27 14:42 | 9379 | 11kV | 114007.75 | 39 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID report Compiled via SCADA, Emergency switching sheets and OMS This record is for a feeder outage that preceeded the Zone outage at Raymond Terrace | April | 2015 | 2015Q4 | 2015 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 2923.2756 | Y | 3 | N | Y | 1.1101 | 39.4971 | 83313.501
[7 empty] | 13825 | 13452 | 1254991 | 2015-04-27 13:01 | 2015-04-27 14:51 | 110 | 11kV | 14520 | 132 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2466 Flemington 11kv Pnl 41 "Parramatta Alban, etc" feeder tripped on A and B phase IOC with fault check Signals: 11kv trip, Tx 3 gorup and zone earth with efi Field efis: Sub 7703, 7742 and 8323 Abnormal: sw/A closed at S35056 and sw/A opened at S3407 (cable fault) Remarks: UG fault. Cable fault between S7742 Percy Hall #4 to Sub 8323 Station Raw #2. Also efi oeprated incorrectly at S8323 | April | 2015 | 2015Q4 | 2015 | ZN2466:PA41 | ZN36000:PA24 | ZN36000/000024 | CUMBERLAND | UG | Not Veg | 2015-04-27 | N | 110 | N | 8 | N | N | 1.1101 | 39.4971 | 10610.7877
[7 empty] | 13834 | 13499 | 1259431 | 2015-04-22 16:25 | 2015-04-27 15:20 | 7135 | 11kV | 608056 | 136 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S12630 Peats Ridge Panel 1 Tripped on A and C phase Timed O/C, With reclose and lockout relays Cause: Trees and OH down - Major storm See OMS 1259431/433/435/436/444/449/432/456/460/450/467/466/465/454/463 1234310/942/52175/52174/49943/5818/53075/53137/54166 | April | 2015 | 2015Q4 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2015-04-22 | Y | 4471 | Y | 10 | N | Y | 1.1101 | 39.4971 | 444349.3902
[7 empty] | 12353 | 928 | 1235138 | 2015-04-21 03:20 | 2015-04-27 15:53 | 9393 | 11kV | 4057347 | 889 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 4563.9449 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2964989.5161
[7 empty] | 12316 | 591 | 1240280 | 2015-04-21 20:29 | 2015-04-27 16:10 | 8381 | 11kV | 120693 | 158 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switch sheet | April | 2015 | 2015Q4 | 2015 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2015-04-21 | Y | 763.8797 | Y | 3 | N | Y | 1.1101 | 39.4971 | 88198.8846
[7 empty] | 13184 | 8280 | 1238238 | 2015-04-21 13:21 | 2015-04-27 16:19 | 8817.75 | 11kV | 458523 | 52 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | works all complete CC1: 22-"Refer to SOp" | April | 2015 | 2015Q4 | 2015 | ZN1193:PA10 | ZN1193:PA10 | ZN01193/000010 | KU-RING-GAI | OH | Veg | 2015-04-21 | Y | 8817.75 | Y | 3 | N | Y | 1.1101 | 39.4971 | 335075.0843
[7 empty] | 12552 | 2825 | 1238502 | 2015-04-21 07:17 | 2015-04-27 16:21 | 9184 | 11kV | 403319 | 66 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled via emergency switching sheets | April | 2015 | 2015Q4 | 2015 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 6110.8939 | Y | 3 | N | Y | 1.1101 | 39.4971 | 294733.6293
[7 empty] | 13026 | 6996 | 1250537 | 2015-04-24 05:45 | 2015-04-27 16:25 | 4960 | 11kV | 768800 | 155 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | Electrical Storm | Y | No LID Report Damaged 11kV dropper cpompiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 256:80644 | 257:81999 | ZN00257/081999 | NEWCASTLE | OH | Not Veg | 2015-04-24 | Y | 4960 | Y | 3 | N | Y | 1.1101 | 39.4971 | 561816.3642
[7 empty] | 12797 | 5020 | 1255732 | 2015-04-27 16:26 | 2015-04-27 16:34 | 8 | 11kV | 2560 | 320 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 151772 1 fault operation RAGCB on one shot for fuse replacement when tree fell into mains at ABS 18855 | April | 2015 | 2015Q4 | 2015 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2015-04-27 | N | 8 | N | 8 | N | N | 1.1101 | 39.4971 | 1870.7725
[7 empty] | 14455 | 18353 | 1250110 | 2015-04-21 21:29 | 2015-04-27 17:26 | 8396.7833 | 11kV | 654949.1 | 78 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | appears as though sub isolated during the storm and customers received extended outage no information received from the control room | April | 2015 | 2015Q4 | 2015 | 242:81535 | 242:81535 | ZN00242/081535 | PORT STEPHENS | OH | Veg | 2015-04-21 | Y | 8396.7833 | Y | 3 | N | Y | 1.1101 | 39.4971 | 478617.4846
[7 empty] | 13636 | 12009 | 1251251 | 2015-04-21 16:20 | 2015-04-27 17:42 | 8722.1 | 11kV | 14818389.7 | 2590 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | NO LID report compiled via emergency switching sheet various hazards reported | April | 2015 | 2015Q4 | 2015 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 5721.386 | Y | 3 | N | Y | 1.1101 | 39.4971 | 10828842.1243
[7 empty] | 13950 | 14581 | 1253116 | 2015-04-26 07:40 | 2015-04-27 17:58 | 2058.8167 | 11kV | 298528.4167 | 145 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | appears from customer calls that supply was restored, see event 1265906 then supply isolated at sub. no further information supplied from control room or field | April | 2015 | 2015Q4 | 2015 | 230:81434 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Veg | 2015-04-26 | N | 2058.8167 | Y | 3 | N | Y | 1.1101 | 39.4971 | 218155.7618
[7 empty] | 12623 | 3410 | 1265367 | 2015-04-21 05:35 | 2015-04-27 18:06 | 9391 | 11kV | 2628576 | 351 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 7488.8205 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1920885.8109
[7 empty] | 12908 | 6038 | 1233855 | 2015-04-21 01:16 | 2015-04-27 18:28 | 9672 | 11kV | 6925748 | 1592 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12570 avoca 11kv pa22 fdr tripped Relays: 51 AB, Lockout Weather related. Multiple tree down. OH Down See 1259820,4,6,8,9 Exclude 1233855,4073,4010,1,2 | April | 2015 | 2015Q4 | 2015 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 4350.3442 | N | 3 | N | Y | 1.1101 | 39.4971 | 5061132.3634
[7 empty] | 14192 | 16434 | 1234160 | 2015-04-21 00:19 | 2015-04-27 18:29 | 9730 | 11kV | 3303460 | 592 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled via emergency switching sheets Includes OMS 1262526/28/29/30/31/32/33/34/35 Excludes OMS 1234160, 1248494, 1249083 | April | 2015 | 2015Q4 | 2015 | 227:13018 | 227:13018 | ZN00227/013018 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 5580.1689 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2414071.1324
[7 empty] | 13190 | 8326 | 1235450 | 2015-04-21 04:07 | 2015-04-27 18:41 | 9514 | 11kV | 4649176 | 1001 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 239:82132 | 239:82132 | ZN00239/082132 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 4644.5315 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3397480.6933
[7 empty] | 14470 | 18499 | 1235049 | 2015-04-21 02:32 | 2015-04-27 19:11 | 9639 | 11kV | 11646354 | 2497 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled via emergency switching sheets Includes OMS 1262802/4/5/6/7 Excludes 1235049/405, 1249299/424/612, 1251249/2178/2865/2866 | April | 2015 | 2015Q4 | 2015 | 233:82815 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2015-04-21 | Y | 4664.1386 | Y | 3 | N | Y | 1.1101 | 39.4971 | 8510811.9939
[7 empty] | 12395 | 1391 | 1261693 | 2015-04-27 14:00 | 2015-04-27 19:20 | 320 | 11kV | 1600 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Previous Storm | N | No LID report compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2015-04-27 | N | 320 | N | 8 | N | N | 1.1101 | 39.4971 | 1169.2328
[7 empty] | 13648 | 12103 | 1249282 | 2015-04-20 23:33 | 2015-04-27 19:30 | 9837 | 11kV | 4671552 | 677 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Rain Wind Storm | Y | restore time based on operational OMS job secondary event on this sub based on OMS records | April | 2015 | 2015Q4 | 2015 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2015-04-20 | Y | 6900.3722 | N | 8 | N | Y | 1.1101 | 39.4971 | 3413832.4141
[7 empty] | 13025 | 6990 | 1234691 | 2015-04-21 05:04 | 2015-04-27 19:35 | 9511 | 11kV | 2060052 | 303 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14143 Somersby Pnl.10 tripped/ reclosed / tripped & locked out on: A & B phase IOC, SEL Storm - Pnl tripped again 25/4/15 18:17 in next storm Multiple issues along feeder - some restoration steps were missed in the blueys and have been estimated as best as possible based on trends see 1259536 1259531 1259524 | April | 2015 | 2015Q4 | 2015 | ZN14143:PA10 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 6798.8515 | N | 3 | N | Y | 1.1101 | 39.4971 | 1505425.2404
[7 empty] | 12644 | 3692 | 1253225 | 2015-04-22 01:08 | 2015-04-27 19:37 | 8309 | 11kV | 132944 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | according to IONs CP48045 experienced outage. Cause not ascertained. Major Storm Event. | April | 2015 | 2015Q4 | 2015 | ZN14143:PA6 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | OH | Veg | 2015-04-22 | Y | 8309 | Y | 10 | N | Y | 1.1101 | 39.4971 | 97151.554
[7 empty] | 13597 | 11670 | 1254606 | 2015-04-27 09:33 | 2015-04-27 19:50 | 617 | 11kV | 162145 | 1201 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn 2466 Flemington 11kv Pnl 25 "Carter Hill #6" feeder tripped on B phase IOC. Signals: 11kv trip, zone and group 3 earth with efi Field efi's: Sub 62932 remarks: UG fault. Cable fault between S62932 Carter Hill #6 to Sub 3407 Hill Dartbrook tee Zn167 Auburn (Pnl 13) | April | 2015 | 2015Q4 | 2015 | ZN2466:PA25 | ZN167:PA13 | ZN00167/000013 | CUMBERLAND | UG | Not Veg | 2015-04-27 | N | 135.0083 | N | 8 | N | N | 1.1101 | 39.4971 | 118490.7835
[7 empty] | 13000 | 6822 | 1278715 | 2015-04-21 01:48 | 2015-04-27 20:00 | 9732 | 11kV | 4535937 | 814 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID - entered based on SCADA logs, switching sheets & OMS entries This feeder tripped prior to Raymond Terracse Zone Outage | April | 2015 | 2015Q4 | 2015 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 5572.4042 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3314728.9721
[7 empty] | 13415 | 10289 | 1248437 | 2015-04-21 06:12 | 2015-04-27 20:00 | 9468 | 11kV | 2649294 | 1016 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Wind Storm | Y | Section of ZN.12580 Erina 11kV Panel 14 from IR.62391 Wells Brougham tripped:- Relays:- O/C trip, L/O Cause:- STORM, @ PT.11160 Waratah Denver (leaking oil) 11kV LK.41456 open & defective B phase link broken on PT side ME:-1257939 RS:-1257941 GIS Model Error:-1248437 Withdrawn:-1247842 | April | 2015 | 2015Q4 | 2015 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 2607.5728 | N | 3 | N | Y | 1.1101 | 39.4971 | 1936025.9143
[7 empty] | 12527 | 2544 | 1254194 | 2015-04-25 09:14 | 2015-04-27 20:00 | 3526 | 11kV | 42312 | 12 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | PT12879 Bellevue Tanderra 11kv centre fuse blown due to tree branch on mains See 1259988 exclude 1254194 1255633, 1254866 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Veg | 2015-04-25 | Y | 3526 | Y | 5 | N | Y | 1.1101 | 39.4971 | 30920.3616
[7 empty] | 13274 | 8947 | 1236076 | 2015-04-21 05:34 | 2015-04-27 20:05 | 9511 | 11kV | 5225906 | 930 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Entered based on SCADA, Swtiching Sheet & Operational OMS records Assumed multiple faults based on restoration switching - no information on switching sheets as to fault details | April | 2015 | 2015Q4 | 2015 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Veg | 2015-04-21 | Y | 5619.2538 | N | 3 | N | Y | 1.1101 | 39.4971 | 3818937.9667
[7 empty] | 13689 | 12424 | 1240649 | 2015-04-21 19:12 | 2015-04-27 20:15 | 8703 | 11kV | 2635283 | 1586 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn13000 Lake Munmorah Panel 11 "Lake Munmorah Aux No.2" feeder has tripped and locked Remarks: storm. Trees in 11kv Based on SCADA logs & trends Trip & Reclose at 06:098 and then lockout at 19:12 | April | 2015 | 2015Q4 | 2015 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 1661.5908 | N | 3 | N | Y | 1.1101 | 39.4971 | 1925787.0887
[7 empty] | 14657 | 20168 | 1245787 | 2015-04-23 07:26 | 2015-04-27 20:20 | 6534 | 11kV | 463914 | 71 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Previous Storm | Y | PT14096 interrupted on 27/4 17:20 for safety to remove tree branch on PT. See 1259984 exclude 1245787 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA24 | ZN12610:PA24 | ZN12610/000024 | CENTRAL COAST | OH | Veg | 2015-04-23 | Y | 6534 | Y | 4 | N | Y | 1.1101 | 39.4971 | 339014.6681
[7 empty] | 14075 | 15606 | 1249856 | 2015-04-24 11:13 | 2015-04-27 20:30 | 4877 | 11kV | 453561 | 93 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | Y | PT13790 Moss Yaralla suspected transformer fault. Restored via LV parallel See 1267330 exclude 1249856,54511 | April | 2015 | 2015Q4 | 2015 | ZN12620:PA3 | ZN12620:PA3 | ZN12620/000003 | CENTRAL COAST | OH | Not Veg | 2015-04-24 | Y | 4877 | Y | 3 | N | Y | 1.1101 | 39.4971 | 331449.001
[7 empty] | 13125 | 7804 | 1235434 | 2015-04-21 03:56 | 2015-04-27 20:50 | 9654 | 11kV | 3211785 | 391 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Compiled from switching sheets Lockout of 34148 feeder after 3 earlier trip & reclose operations Hinton Intellirupter 50356 had locked out earlier Access issues delayed overall response | April | 2015 | 2015Q4 | 2015 | 238:34148 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2015-04-21 | Y | 8214.2839 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2347077.7464
[7 empty] | 13908 | 14189 | 1249054 | 2015-04-24 07:21 | 2015-04-27 21:21 | 5159.2833 | 11kV | 5159.2833 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | Y | Lost power at 07:15 on Friday, 24th April. Possibly a service wire problem. Appears to be the only premise in the the street with no power. 24/04/15 08:42: Jerremy rang 0411 041 943. reported HV line supying single phase Tx was swinging in the breeze - disconnected from Tx bushing. Ground soggy, hard to access with a heavy. No further information supplied from control room | April | 2015 | 2015Q4 | 2015 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2015-04-24 | Y | 5159.2833 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3770.2521
[7 empty] | 13488 | 10858 | 1256051 | 2015-04-27 22:58 | 2015-04-28 01:15 | 137 | 11kV | 29340 | 358 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | ZN 10994 Mortdale - Pnl 8L - Trip/reclose/trip, A & B phase OC, Earth Fault Check, EFI. Dead possum found at the base of PT 10580 which had 3 HDOs blown. T/Con to inspect PT. Bond burnt of UGOH and cable tie on mains on main line near tee to PT loose and need repairs. ME: 1261118. Rest Step: 1261121. Withdrawn: 1256050, 1, 2. | April | 2015 | 2015Q4 | 2015 | ZN10994:PA8 | ZN10994:PA8 | ZN10994/000008 | GEORGES RIVER | OH | Not Veg | 2015-04-27 | N | 81.9553 | N | 8 | N | N | 1.1101 | 39.4971 | 21440.8066
[7 empty] | 14655 | 20152 | 1238382 | 2015-04-21 09:07 | 2015-04-28 07:37 | 9990 | 11kV | 6249810.4667 | 1762 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LOID report Compiled via switching sheet | April | 2015 | 2015Q4 | 2015 | 503:48011 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2015-04-21 | Y | 3546.998 | N | 3 | N | Y | 1.1101 | 39.4971 | 4567177.1508
[7 empty] | 13087 | 7514 | 1235972 | 2015-04-21 09:40 | 2015-04-28 07:37 | 9956.8667 | 11kV | 67433.2667 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | no information supplied from control room records left and assumed correct as per switching of OMS by control room | April | 2015 | 2015Q4 | 2015 | 229:34989 | 229:34989 | ZN00229/034989 | PORT STEPHENS | OH | Veg | 2015-04-21 | Y | 7492.5852 | Y | 3 | N | Y | 1.1101 | 39.4971 | 49278.2423
[7 empty] | 14033 | 15310 | 1252184 | 2015-04-26 07:15 | 2015-04-28 08:40 | 2965.0667 | 11kV | 127497.8667 | 43 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | PT12041 Munong Kurrawa Dist 1 "kurrawa av" Based on custoemr calls. Major Storm Event previously | April | 2015 | 2015Q4 | 2015 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Veg | 2015-04-26 | N | 2965.0667 | Y | 3 | N | Y | 1.1101 | 39.4971 | 93171.6804
[7 empty] | 13173 | 8146 | 1257344 | 2015-04-28 08:31 | 2015-04-28 08:45 | 14 | 11kV | 28 | 2 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 151779 ABS OPENED FOR CLEARANCE ONLY | April | 2015 | 2015Q4 | 2015 | 238:34151 | 238:34151 | ZN00238/034151 | MAITLAND | OH | Not Veg | 2015-04-28 | N | 14 | N | 10 | N | N | 1.1101 | 39.4971 | 20.4616
[7 empty] | 14423 | 18093 | 1235956 | 2015-04-21 09:39 | 2015-04-28 09:30 | 10071.4833 | 11kV | 2331705.7167 | 251 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | LH LVF Isolated LV OHM damage - no further information supplied via control room also refer to related record 1254150 | April | 2015 | 2015Q4 | 2015 | 240:34849 | 240:34849 | ZN00240/034849 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 9289.6642 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1703941.7641
[7 empty] | 13641 | 12066 | 1234408 | 2015-04-21 02:43 | 2015-04-28 11:31 | 10608 | 11kV | 7915341.3167 | 1629 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 203:8085 | 204:82705 | ZN00204/082705 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 4859.0186 | Y | 3 | N | Y | 1.1101 | 39.4971 | 5784297.9712
[7 empty] | 12958 | 6503 | 1233946 | 2015-04-20 23:12 | 2015-04-28 11:38 | 10825.5833 | 11kV | 7944865.0833 | 1411 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 239:82129 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2015-04-20 | Y | 5630.6627 | N | 8 | N | Y | 1.1101 | 39.4971 | 5805873.0691
[7 empty] | 14307 | 17284 | 1242966 | 2015-04-21 06:56 | 2015-04-28 11:40 | 10364 | 11kV | 2193994 | 459 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC49684 Brisbane Water Lara tripped and locked out on: OC trip Weather - tree down on mains beyond LB41147 see 1258087 1258089 1258090 | April | 2015 | 2015Q4 | 2015 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 4779.9434 | N | 3 | N | Y | 1.1101 | 39.4971 | 1603306.1033
[7 empty] | 14149 | 16170 | 1235130 | 2015-04-21 03:15 | 2015-04-28 11:41 | 10586 | 11kV | 582784.4 | 79 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet Wire down (about 200m, opposite side of her proerty) between properties 260-290 Cabbage Tree Rd, from corner of Nelson Bay Rd. no further information supplied via control room | April | 2015 | 2015Q4 | 2015 | 229:34986 | 229:34986 | ZN00229/034986 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 7377.0177 | Y | 3 | N | Y | 1.1101 | 39.4971 | 425881.6503
[7 empty] | 13999 | 14925 | 1240846 | 2015-04-21 06:29 | 2015-04-28 11:46 | 10397 | 11kV | 1629790 | 635 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID report Compiled via SCADA trend; Emergency switching sheets and OMS jobs | April | 2015 | 2015Q4 | 2015 | 203:8088 | 204:82703 | ZN00204/082703 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 2566.5984 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1191002.4613
[7 empty] | 13868 | 13854 | 1233845 | 2015-04-21 05:23 | 2015-04-28 11:50 | 10467 | 11kV | 12578697 | 1666 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12650 Westgosford Panel 1 "Dog Traprd" fdr tripped and locked out on relays. Trees on HV and overhead down at numerous locations. Major Event Storm See 1262612,7,6,9,20,1,2,3,4,6,7,8 Exclude 1233392,845,4208,736,54034,5,96,322 based off SCADA & trending start time 21/4 05:23 | April | 2015 | 2015Q4 | 2015 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 7550.2383 | N | 3 | N | Y | 1.1101 | 39.4971 | 9192140.7588
[7 empty] | 13199 | 8441 | 1235028 | 2015-04-21 07:00 | 2015-04-28 12:00 | 10380 | 11kV | 1362578 | 170 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID 11kV mains down JR-25091 and tree on mains Noongah Rd Excludes 1253980, 1253981, 1253982, 1235028, 1261810, 1261812, 1261813, 1261814, 1261816, 1261817, 1261818 | April | 2015 | 2015Q4 | 2015 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2015-04-21 | Y | 8015.1647 | Y | 3 | N | Y | 1.1101 | 39.4971 | 995731.8132
[7 empty] | 14459 | 18382 | 1235443 | 2015-04-21 04:05 | 2015-04-28 12:07 | 10562 | 11kV | 3002540.9167 | 394 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via Emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 7620.6622 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2194168.3419
[7 empty] | 14404 | 17967 | 1235398 | 2015-04-21 03:39 | 2015-04-28 12:17 | 10598 | 11kV | 758346.9 | 152 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | No LID report compiled from emergency switch sheets | April | 2015 | 2015Q4 | 2015 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2015-04-21 | Y | 4989.1243 | Y | 3 | N | Y | 1.1101 | 39.4971 | 554177.5471
[7 empty] | 12994 | 6787 | 1248642 | 2015-04-23 18:55 | 2015-04-28 12:19 | 6804.4 | 11kV | 428677.2 | 63 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Rain Wind Storm | Y | switching as per control room operations of OMS assuming sub was isolated or defect detected post storm no information supplied | April | 2015 | 2015Q4 | 2015 | 503:48011 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2015-04-23 | Y | 6804.4 | N | 4 | N | Y | 1.1101 | 39.4971 | 313264.6539
[7 empty] | 13649 | 12119 | 1261879 | 2015-04-28 10:40 | 2015-04-28 12:20 | 100 | 11kV | 5300 | 53 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor ABC | Unplanned | Rain Wind Storm | N | No LID report Major storm Compiled from switching sheets Previous event 1255732 (wires down), temp reconnection - this outage to fix | April | 2015 | 2015Q4 | 2015 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2015-04-28 | N | 100 | N | 10 | N | N | 1.1101 | 39.4971 | 3873.0837
[7 empty] | 14540 | 19015 | 1248272 | 2015-04-23 16:31 | 2015-04-28 12:21 | 6949.85 | 11kV | 20849.55 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Rain Wind Storm | Y | LID 1517995 SUB 52331 ISOLATED FOR REPAIRS TO L/LINE LEADS. also refer to 1258423 and 1256674 note unsure of correct isolation time as control room operated OMS as device isolated on the 23/04/15 16:31. The sub was fixed in the field on the 29th as per LID | April | 2015 | 2015Q4 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2015-04-23 | Y | 6949.85 | N | 4 | N | Y | 1.1101 | 39.4971 | 15236.2362
[7 empty] | 13313 | 9348 | 1252934 | 2015-04-21 08:31 | 2015-04-28 12:36 | 10324.85 | 11kV | 61949.1 | 6 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Rain Wind Storm | Y | replace kiosk shell sub 68666 No LID report, compiled from emergency switching sheet NOTE kiosk shell replaced on the 29th, customers not interrupted again due to closing of LVL 68952 | April | 2015 | 2015Q4 | 2015 | 239:82133 | 239:82133 | ZN00239/082133 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 10324.85 | Y | 3 | N | Y | 1.1101 | 39.4971 | 45270.5751
[7 empty] | 14630 | 19982 | 1256123 | 2015-04-21 15:00 | 2015-04-28 12:47 | 9947 | 11kV | 29841 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | REPLACED LV FUSE BLOWN ON TX | April | 2015 | 2015Q4 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-04-21 | Y | 9947 | Y | 3 | N | Y | 1.1101 | 39.4971 | 21806.9226
[7 empty] | 14561 | 19172 | 1262358 | 2015-04-21 03:23 | 2015-04-28 13:21 | 10678 | 11kV | 3053814 | 553 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report compiled via emergency switching sheet Feeder 48031 tripped before subtransmission faults impacting Cessnock Zone | April | 2015 | 2015Q4 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2015-04-21 | Y | 5522.2676 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2231637.1989
[7 empty] | 13261 | 8837 | 1238438 | 2015-04-21 01:22 | 2015-04-28 13:40 | 10818 | 11kV | 3326914 | 1080 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet Tree on sub and 3 span mains down beyond 49779 | April | 2015 | 2015Q4 | 2015 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 3080.4759 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2431210.6238
[7 empty] | 12483 | 2105 | 1248917 | 2015-04-21 20:48 | 2015-04-28 13:40 | 9652 | 11kV | 2115540 | 1880 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14143 Somersby Pnl.12 tripped: DOP Unable to read relays Weather related see 1258263 1258264 1258265 1258267 1258269 1258270 1258271 1258273 | April | 2015 | 2015Q4 | 2015 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 1125.2872 | N | 3 | N | Y | 1.1101 | 39.4971 | 1545974.2341
[7 empty] | 14050 | 15419 | 1233749 | 2015-04-20 21:20 | 2015-04-28 14:00 | 11080 | 11kV | 2402341 | 671 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14144 Wamberal Pnl.10 tripped on: SEL Weather related see 1257818 1257819 | April | 2015 | 2015Q4 | 2015 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2015-04-20 | Y | 3580.2399 | N | 8 | N | Y | 1.1101 | 39.4971 | 1755559.9457
[7 empty] | 13728 | 12759 | 1255376 | 2015-04-27 11:48 | 2015-04-28 14:29 | 1601 | 11kV | 12808 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | no information supplied from control room. Appears from the operation of OMS from the Control Room, that sub was isolated post storm | April | 2015 | 2015Q4 | 2015 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2015-04-27 | N | 1601 | Y | 8 | N | Y | 1.1101 | 39.4971 | 9359.7086
[7 empty] | 13102 | 7673 | 1263621 | 2015-04-28 12:45 | 2015-04-28 14:35 | 110 | 11kV | 1870 | 17 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Previous Storm | N | No LID Report Compiled via Emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Not Veg | 2015-04-28 | N | 110 | N | 10 | N | N | 1.1101 | 39.4971 | 1366.5408
[7 empty] | 12852 | 5563 | 1256090 | 2015-04-28 07:15 | 2015-04-28 14:45 | 450 | 11kV | 182700 | 406 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Rain Wind Storm | N | Ex Pnl.17 Somersby Zn - Live Line Connector to USL 43276 Open circuit - damaged interrupted for repair | April | 2015 | 2015Q4 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2015-04-28 | N | 450 | N | 10 | N | N | 1.1101 | 39.4971 | 133511.7713
[7 empty] | 14447 | 18267 | 1235071 | 2015-04-21 07:10 | 2015-04-28 15:15 | 10565 | 11kV | 10492724 | 2132 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12570 Avoca Pa37 "Avoca Beach" fdr tripped Relays: 51B & C phase overload, EFI Storm damage along feeder See1258876,7,9,80,1,4,5,6 Exclude 1235071,44049,51177,8,9 | April | 2015 | 2015Q4 | 2015 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 4921.5403 | N | 3 | N | Y | 1.1101 | 39.4971 | 7667773.2162
[7 empty] | 14213 | 16606 | 1252892 | 2015-04-25 19:49 | 2015-04-28 15:32 | 4063.2667 | 11kV | 4063.2667 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | Potential for DIFFICULT_ACCESS due to flooding, as per Brett Burchill Sub isolated. LAs need replacing. EWP required due to termite treated pole. Customer notified. also refer to 1259364 and 1259683 | April | 2015 | 2015Q4 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2015-04-25 | Y | 4063.2667 | Y | 5 | N | Y | 1.1101 | 39.4971 | 2969.3154
[7 empty] | 12453 | 1798 | 1257365 | 2015-04-21 14:00 | 2015-04-28 16:35 | 10235 | 11kV | 71645 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 151789 A & B phase DOLF : 16 Amp | April | 2015 | 2015Q4 | 2015 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2015-04-21 | Y | 10235 | N | 3 | N | Y | 1.1101 | 39.4971 | 52356.0528
[7 empty] | 12571 | 3029 | 1234778 | 2015-04-21 05:14 | 2015-04-28 16:45 | 10771 | 11kV | 4233090.9667 | 1038 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Wire down adjacent ABS 11218 toward 1417 | April | 2015 | 2015Q4 | 2015 | 210:8682 | 210:83465 | ZN00210/083465 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 4078.1223 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3093418.0234
[7 empty] | 13794 | 13244 | 1247418 | 2015-04-21 05:51 | 2015-04-28 16:47 | 10735.5167 | 11kV | 6559540.4 | 1210 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | NO LID reoprt Compiled from emergency switching sheets various subs with storm damage | April | 2015 | 2015Q4 | 2015 | 220:8691 | 220:8691 | ZN00220/008691 | LAKE MACQUARIE | OH | Veg | 2015-04-21 | Y | 5421.1078 | Y | 3 | N | Y | 1.1101 | 39.4971 | 4793518.6506
[7 empty] | 14375 | 17732 | 1235936 | 2015-04-21 05:03 | 2015-04-28 16:57 | 10794 | 11kV | 4751827 | 883 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Entered from Switching Sheet Feeder 8692 tripped. OHM down between pole JV41062 to Sub 13275 Multiple faults on LV network | April | 2015 | 2015Q4 | 2015 | 220:8692 | 220:8692 | ZN00220/008692 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 5381.4575 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3472495.0164
[7 empty] | 13736 | 12822 | 1245523 | 2015-04-22 16:25 | 2015-04-28 17:10 | 8685 | 11kV | 4328671 | 903 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12630 Peats Ridge Pa2 "Guinderman' fdr opened by control room relays: nil Interrupted on loss of 33kv '720' fdr. multiple sections of 11kv and LV found down after patrols See 1265398,400,2,3,4,5,6,7,10,1,2 exclude 1233687,965,45819,52405,6,3146,7,8,9 | April | 2015 | 2015Q4 | 2015 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2015-04-22 | Y | 4793.6556 | Y | 10 | N | Y | 1.1101 | 39.4971 | 3163265.0926
[7 empty] | 12909 | 6049 | 1257097 | 2015-04-28 16:58 | 2015-04-28 17:27 | 28.9333 | 11kV | 4542.5333 | 157 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 151781 Sect interrupted to remove tree in 11kV OHM near sub 10002 | April | 2015 | 2015Q4 | 2015 | 217:33612 | 217:33605 | ZN00217/033605 | LAKE MACQUARIE | OH | Not Veg | 2015-04-28 | N | 28.9333 | N | 10 | N | N | 1.1101 | 39.4971 | 3319.5494
[7 empty] | 12948 | 6423 | 1240628 | 2015-04-22 01:50 | 2015-04-28 17:42 | 9591.6333 | 11kV | 96518.6333 | 29 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID Tree on OHM at pole ER-85424 Info derived from emergency switching sheet Excludes OMS 1261123, 1240628 | April | 2015 | 2015Q4 | 2015 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2015-04-22 | Y | 3328.2287 | Y | 10 | N | Y | 1.1101 | 39.4971 | 70532.9704
[7 empty] | 14422 | 18092 | 1248645 | 2015-04-23 18:56 | 2015-04-28 17:54 | 7138.1167 | 11kV | 1070717.5 | 150 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Rain Wind Storm | Y | switching as per control room operations of OMS assuming sub was isolated or defect detected post storm no information supplied | April | 2015 | 2015Q4 | 2015 | 503:48011 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2015-04-23 | Y | 7138.1167 | N | 4 | N | Y | 1.1101 | 39.4971 | 782448.7682
[7 empty] | 13124 | 7803 | 1235455 | 2015-04-21 04:09 | 2015-04-28 18:00 | 10911 | 11kV | 2908810.0667 | 1511 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled from switching sheets | April | 2015 | 2015Q4 | 2015 | 238:34147 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Veg | 2015-04-21 | Y | 1925.0894 | N | 3 | N | Y | 1.1101 | 39.4971 | 2125672.6013
[7 empty] | 14190 | 16420 | 1257180 | 2015-04-28 17:30 | 2015-04-28 18:50 | 80 | 11kV | 1760 | 22 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 151782 11kV Fdr section isolated to repair broken Cph bridging insulator at pole SM-70028. | April | 2015 | 2015Q4 | 2015 | 814:82283 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2015-04-28 | N | 80 | N | 10 | N | N | 1.1101 | 39.4971 | 1286.1561
[7 empty] | 13858 | 13750 | 1264424 | 2015-04-21 06:14 | 2015-04-28 19:18 | 10864 | 11kV | 3071811 | 374 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID Report Compiled via emergecy switching sheet Flooding | April | 2015 | 2015Q4 | 2015 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 8213.3984 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2244788.8757
[7 empty] | 13923 | 14392 | 1236766 | 2015-04-21 02:51 | 2015-04-28 19:51 | 11100 | 11kV | 4627761 | 770 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Interruption entered based on Switching sheet - No LID Feeder Breaker tripped, preceeded by lockouts on Kirrang Dr and Grahamstown Dam Reclosers Feeder Breaker fault due to 5 Spans HV down near sub 5195 Multiple other faults | April | 2015 | 2015Q4 | 2015 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2015-04-21 | Y | 6010.0792 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3381831.243
[7 empty] | 12664 | 3865 | 1233888 | 2015-04-20 20:41 | 2015-04-28 20:00 | 11479 | 11kV | 2015656 | 278 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At CP61085 peats Ridge 0.3 Tripped and locked out on SEF and OC At CP46803 Wise Ferry Dog Trap 0.1 Tripped Reclosed tripped and locked on Relays: IOC and EF trip Cause: Storm See OMS 1259626/1259620/1259619/1259618/1259616/1259612/1259602/1259614 1254075/1254485/12338881233427 | April | 2015 | 2015Q4 | 2015 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2015-04-20 | Y | 7250.5612 | N | 8 | N | Y | 1.1101 | 39.4971 | 1472981.953
[7 empty] | 13113 | 7741 | 1257042 | 2015-04-28 16:26 | 2015-04-28 20:10 | 224 | 11kV | 224 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 151791 A phase DOLF : 10 Amp Tx Volts = 246V Excluded OMS 1257042 | April | 2015 | 2015Q4 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-04-28 | N | 224 | N | 10 | N | N | 1.1101 | 39.4971 | 163.6926
[7 empty] | 13411 | 10240 | 1250880 | 2015-04-24 17:20 | 2015-04-28 20:10 | 5930.3333 | 11kV | 195701 | 33 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | WIND STORM; Job complete CC1: 06-"Urgent - O.H Mains - No others" | April | 2015 | 2015Q4 | 2015 | 233:82821 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Veg | 2015-04-24 | Y | 5930.3333 | Y | 3 | N | Y | 1.1101 | 39.4971 | 143012.5186
[7 empty] | 13888 | 13970 | 1234173 | 2015-04-21 01:10 | 2015-04-28 20:14 | 11223.8833 | 11kV | 56118.4167 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | no further information available | April | 2015 | 2015Q4 | 2015 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Veg | 2015-04-21 | Y | 11223.6833 | Y | 3 | N | Y | 1.1101 | 39.4971 | 41009.6837
[7 empty] | 12385 | 1224 | 1256497 | 2015-04-28 08:30 | 2015-04-28 20:45 | 735 | 11kV | 735 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Entered based on switching sheet Outage to repair broken tappings on pole JS-70222 | April | 2015 | 2015Q4 | 2015 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2015-04-28 | N | 735 | N | 10 | N | N | 1.1101 | 39.4971 | 537.1163
[7 empty] | 12886 | 5894 | 1248644 | 2015-04-23 18:55 | 2015-04-28 20:46 | 7310.4 | 11kV | 731040 | 100 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Rain Wind Storm | Y | switching as per control room operations of OMS assuming sub was isolated or defect detected post storm no information supplied | April | 2015 | 2015Q4 | 2015 | 503:48011 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2015-04-23 | Y | 7310.4 | N | 4 | N | Y | 1.1101 | 39.4971 | 534222.47
[7 empty] | 12413 | 1518 | 1250164 | 2015-04-24 12:53 | 2015-04-28 21:02 | 6249.1667 | 11kV | 226221.4833 | 78 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | no information supplied from the control room | April | 2015 | 2015Q4 | 2015 | 228:7490 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Veg | 2015-04-24 | Y | 2900.2754 | Y | 3 | N | Y | 1.1101 | 39.4971 | 165315.9876
[7 empty] | 13891 | 14039 | 1246265 | 2015-04-28 22:00 | 2015-04-28 23:00 | 60 | 11kV | 1200 | 20 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Previous Storm | N | LID 151793 Sub isolated to replace LV fuse assembly | April | 2015 | 2015Q4 | 2015 | 238:34137 | 238:34137 | ZN00238/034137 | MAITLAND | OH | Not Veg | 2015-04-28 | N | 60 | N | 10 | N | N | 1.1101 | 39.4971 | 876.9246
[7 empty] | 12991 | 6750 | 1240837 | 2015-04-21 08:10 | 2015-04-28 23:40 | 11010 | 11kV | 2363645 | 672 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn36200 Empire Bay Pa8 'S49860 Poole Belrose' fdr tripped Relays: 51 ABC phase, lockout Weather related. Storm Damage. See 1262364,5,6,7,70,1,2 Exclude 1240837,8657,9941,54493,5143 | April | 2015 | 2015Q4 | 2015 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 3517.3289 | N | 3 | N | Y | 1.1101 | 39.4971 | 1727282.0503
[7 empty] | 12653 | 3776 | 1257289 | 2015-04-28 22:46 | 2015-04-29 00:35 | 109 | 11kV | 87517 | 993 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 28 Tripped on earth Fault with EFI and 11kV Trip Section of 11kV feeder from S129 Hunters Hill Pa28 to S6209 Pittwater Thompson to S62084 Pittwater Auburn tee S5267 Short Thompson See OMS 1257464 1257459 1257289 | April | 2015 | 2015Q4 | 2015 | ZN129:PA28 | ZN129:PA52 | ZN00129/000052 | LANE COVE | UG | Not Veg | 2015-04-28 | N | 88.1339 | N | 10 | N | N | 1.1101 | 39.4971 | 63954.8423
[7 empty] | 13841 | 13608 | 1257293 | 2015-04-29 00:01 | 2015-04-29 01:10 | 69 | 11kV | 690 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | PT12344 Sunnybank Sylvania - Footpath phase HDO let go a crimp Batch 552 | April | 2015 | 2015Q4 | 2015 | ZN12600:PA12 | ZN12600:PA12 | ZN12600/000012 | CENTRAL COAST | OH | Not Veg | 2015-04-29 | N | 69 | N | 11 | N | N | 1.1101 | 39.4971 | 504.2316
[7 empty] | 12326 | 676 | 1253103 | 2015-04-21 03:15 | 2015-04-29 07:21 | 11766 | 11kV | 2476692 | 393 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | Y | No LID report Compiled via scada trends; emergency switching sheets and OMS jobs | April | 2015 | 2015Q4 | 2015 | 224:80329 | 224:80329 | ZN00224/080329 | LAKE MACQUARIE | Unknown | Unknown | 2015-04-21 | Y | 6302.0153 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1809893.4636
[7 empty] | 13639 | 12045 | 1254346 | 2015-04-29 06:46 | 2015-04-29 10:40 | 234 | 11kV | 23166 | 99 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 151797 250 amp fuse Distribution LV fuse Excludes OMS 1254346 | April | 2015 | 2015Q4 | 2015 | 503:48017 | 532:83300 | ZN00532/083300 | MAITLAND | OH | Not Veg | 2015-04-29 | N | 234 | N | 11 | N | N | 1.1101 | 39.4971 | 16929.0295
[7 empty] | 13510 | 11009 | 1259605 | 2015-04-21 09:53 | 2015-04-29 12:00 | 11647 | 11kV | 717426 | 254 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn36200 Empire Bay Pnl.1 tripped on A phase IOC Weahter related - PT12286 LV interrupted due to LV mains down See 1259605 1259607 1259608 | April | 2015 | 2015Q4 | 2015 | ZN36200:PA1 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2015-04-21 | Y | 2824.5118 | N | 3 | N | Y | 1.1101 | 39.4971 | 524273.7603
[7 empty] | 14265 | 16991 | 1235422 | 2015-04-21 03:53 | 2015-04-29 12:12 | 12018.55 | 11kV | 10159658.25 | 1653 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 239:82133 | 239:82133 | ZN00239/082133 | LAKE MACQUARIE | OH | Not Veg | 2015-04-21 | Y | 6146.1937 | Y | 3 | N | Y | 1.1101 | 39.4971 | 7424378.5899
[7 empty] | 13678 | 12368 | 1254234 | 2015-04-26 17:57 | 2015-04-29 13:20 | 4043 | 11kV | 8638 | 48 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | No LID report Major storm Compiled from switching sheets Excludes OMS 1261988, 1242505, 1254053/54 | April | 2015 | 2015Q4 | 2015 | 265:81649 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Not Veg | 2015-04-26 | N | 179.9583 | N | 3 | N | N | 1.1101 | 39.4971 | 6312.3956
[7 empty] | 14271 | 17038 | 1255260 | 2015-04-28 13:09 | 2015-04-29 14:19 | 1510.2833 | 11kV | 3020.5667 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | Previous Storm | N | LID 151803 B phase Live line lead burnt off at Sub 42757 | April | 2015 | 2015Q4 | 2015 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2015-04-28 | N | 1510.2833 | Y | 10 | N | Y | 1.1101 | 39.4971 | 2207.341
[7 empty] | 12889 | 5910 | 1257040 | 2015-04-29 14:45 | 2015-04-29 15:15 | 30 | 11kV | 7620 | 254 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Previous Storm | N | Ex Zn12620 Noraville Panel 13 was opened due to not phasing CP14497 Opened | April | 2015 | 2015Q4 | 2015 | ZN12620:PA13 | ZN12620:PA13 | ZN12620/000013 | CENTRAL COAST | UG | Not Veg | 2015-04-29 | N | 30 | N | 11 | N | N | 1.1101 | 39.4971 | 5568.4712
[7 empty] | 13758 | 12950 | 1240306 | 2015-04-21 16:15 | 2015-04-29 15:45 | 11490 | 11kV | 7062547 | 1655 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled via emergency switching sheets Includes OMS 1262587/89/91 Excludes OMS 1240306, 1250312/491 | April | 2015 | 2015Q4 | 2015 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 4267.4 | Y | 3 | N | Y | 1.1101 | 39.4971 | 5161101.0377
[7 empty] | 13724 | 12738 | 1249227 | 2015-04-21 05:10 | 2015-04-29 16:03 | 12172.6667 | 11kV | 2600802.85 | 687 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Entered based on Swtiching sheets, operational OMS records and SCADA logs Assumed multiple faults based on restoration switching. Details on faults not known | April | 2015 | 2015Q4 | 2015 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | OH | Veg | 2015-04-21 | Y | 3785.7392 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1900590.0121
[7 empty] | 12542 | 2701 | 1254994 | 2015-04-25 11:05 | 2015-04-29 16:06 | 6060.5833 | 11kV | 78787.5833 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | appears as though customer experienced delayed restoration in respect to remainder of feeder at sub level refer to 1263138/ | April | 2015 | 2015Q4 | 2015 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Veg | 2015-04-25 | Y | 6060.5833 | Y | 5 | N | Y | 1.1101 | 39.4971 | 57575.6421
[7 empty] | 13245 | 8705 | 1256654 | 2015-04-28 12:27 | 2015-04-29 16:06 | 1659.6833 | 11kV | 1659.6833 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Previous Storm | N | HUNTER WATER CORPORATION 2160 Nelson Bay Rd. Supply needed to manage water quality in the Tomago to Tomaree Peninsula pipeline. We are testing water quality in the line today with the view to bring the line back into service from tomorrow onwards no information supplied from control room, assuming post storm issue with PT | April | 2015 | 2015Q4 | 2015 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2015-04-28 | N | 1659.6833 | Y | 10 | N | Y | 1.1101 | 39.4971 | 1212.8476
[7 empty] | 12841 | 5433 | 1269034 | 2015-04-29 12:03 | 2015-04-29 16:20 | 257 | 11kV | 1285 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 151806 B & C phase tappings burnt off at links 41276. Suspect SUB volts: 214v, 214v, 10V Excluded OMS No. 1256630 | April | 2015 | 2015Q4 | 2015 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2015-04-29 | N | 257 | N | 11 | N | N | 1.1101 | 39.4971 | 939.0401
[7 empty] | 12781 | 4867 | 1234443 | 2015-04-21 02:31 | 2015-04-29 16:21 | 12350 | 11kV | 4446519 | 1246 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12660 Woy Woy Pnl.14 tripped on: C phase O/C Weather - multiple defectives trees down between AB41632 and LK41791 After AB40774 required patrolling see 1258761 1258762 1258765 1258766 1258768 1258769 1258771 | April | 2015 | 2015Q4 | 2015 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Veg | 2015-04-21 | Y | 3568.6348 | N | 3 | N | Y | 1.1101 | 39.4971 | 3249384.9351
[7 empty] | 14314 | 17306 | 1256530 | 2015-04-24 09:20 | 2015-04-29 16:45 | 7645 | 11kV | 8800 | 22 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Compiled via emergency switching sheets ## sub 4797 opened per time OMS operated by control room Includes OMS 1262453 Excludes OMS 1256530/8810 | April | 2015 | 2015Q4 | 2015 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2015-04-24 | Y | 400 | N | 3 | N | Y | 1.1101 | 39.4971 | 6430.7804
[7 empty] | 13346 | 9715 | 1254247 | 2015-04-26 20:20 | 2015-04-29 16:50 | 4110 | 11kV | 32865 | 9 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Wind Storm | N | Ex Zn14891 Wyong section of Pa12 "Yarramlong feeder" Feeder interrupted between AB44874 and AB40078 to repair storm damaged PT13247 See 1259863 2nd 1259856 exclude 1254247,8191 | April | 2015 | 2015Q4 | 2015 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2015-04-26 | N | 3651.6667 | Y | 3 | N | Y | 1.1101 | 39.4971 | 24016.7726
[7 empty] | 12319 | 615 | 1258111 | 2015-04-29 15:47 | 2015-04-29 17:08 | 81 | 11kV | 68121 | 841 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36100 Rose Bay Pnl.1 tripped on: E/F, EFI, E/F UG cable fault - front line feeder fault Pnl.1 | April | 2015 | 2015Q4 | 2015 | ZN36100:PA1 | ZN36100:PA1 | ZN36100/000001 | WOOLLAHRA | UG | Not Veg | 2015-04-29 | N | 81 | N | 11 | N | N | 1.1101 | 39.4971 | 49780.8176
[7 empty] | 13694 | 12454 | 1238210 | 2015-04-21 06:24 | 2015-04-29 18:05 | 12221 | 11kV | 4357557.5833 | 1285 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Entered based on swtiching sheets - no LID After patrol both cables identified as exposed at sub 69583 Assumed other faults on overhead network | April | 2015 | 2015Q4 | 2015 | 238:34141 | 238:34136 | ZN00238/034136 | MAITLAND | OH | Veg | 2015-04-21 | Y | 3391.0954 | N | 3 | N | Y | 1.1101 | 39.4971 | 3184374.5557
[7 empty] | 13844 | 13632 | 1259873 | 2015-04-29 15:15 | 2015-04-29 18:10 | 175 | 11kV | 27650 | 158 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn14891 Wyong Pa12 "Yarramlong Feeder" Feeder interrupted from AB44980 to LB40905 to extent of feeder to repair storm damage | April | 2015 | 2015Q4 | 2015 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2015-04-29 | N | 175 | N | 11 | N | N | 1.1101 | 39.4971 | 20205.8045
[7 empty] | 13686 | 12411 | 1235096 | 2015-04-21 02:56 | 2015-04-29 18:28 | 12452 | 11kV | 6388966.85 | 863 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via Emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2015-04-21 | Y | 7403.2061 | Y | 3 | N | Y | 1.1101 | 39.4971 | 4668868.5314
[7 empty] | 12917 | 6101 | 1257699 | 2015-04-29 10:52 | 2015-04-29 18:41 | 469.1 | 11kV | 13603.9 | 29 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | Storm effected sub appears as though subs were isolated during the storm and customers experienced an extended outage Information via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Not Veg | 2015-04-29 | N | 469.1 | N | 11 | N | N | 1.1101 | 39.4971 | 9941.3289
[7 empty] | 13503 | 10957 | 1258243 | 2015-04-29 17:30 | 2015-04-29 19:00 | 90 | 11kV | 2230 | 31 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | No LID report Major storm Compiled via emergency switching sheets Includes OMS 1262562 Excludes OMS 1258243 | April | 2015 | 2015Q4 | 2015 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2015-04-29 | N | 71.9355 | N | 11 | N | N | 1.1101 | 39.4971 | 1629.6182
[7 empty] | 12921 | 6118 | 1251222 | 2015-04-24 17:09 | 2015-04-29 20:30 | 7401 | 11kV | 7401 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | Y | LID 151808 Sub isolated by C. Jones. Cph LA blown. No protection details recorded. LAs replaced by P.Lee. Excluded OMS No. 1257489 entered based on switching sheet start time assumed from operational job 1251222 lightning arresters replaced 29/4/15 | April | 2015 | 2015Q4 | 2015 | 238:34150 | 238:34150 | ZN00238/034150 | NEWCASTLE | OH | Not Veg | 2015-04-24 | Y | 7401 | Y | 3 | N | Y | 1.1101 | 39.4971 | 5408.4325
[7 empty] | 14101 | 15802 | 1235221 | 2015-04-21 03:15 | 2015-04-29 20:40 | 12565 | 11kV | 15404575 | 3730 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report 11kV Mains down between sub 10498 & ABS 25164 | April | 2015 | 2015Q4 | 2015 | 256:80646 | 256:80646 | ZN00256/080646 | NEWCASTLE | OH | Veg | 2015-04-21 | Y | 4129.9129 | Y | 3 | N | Y | 1.1101 | 39.4971 | 11257209.052
[7 empty] | 12259 | 38 | 1258332 | 2015-04-29 19:49 | 2015-04-29 20:41 | 52 | 11kV | 32032 | 616 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | ZN12600 Lisarow Pnl.1 tripped, reclosed and locked out on: B & C phase IOC, L/O, timing Tree branch removed from CNR Cambourn & Excelsior | April | 2015 | 2015Q4 | 2015 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Veg | 2015-04-29 | N | 52 | N | 11 | N | N | 1.1101 | 39.4971 | 23408.0408
[7 empty] | 13650 | 12124 | 1258268 | 2015-04-29 19:42 | 2015-04-29 20:44 | 62 | 11kV | 67518 | 1089 | HV | Equipment Failed in Service | Equipment Failure | Enclosed Load Break Switch | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty Pa2 "Bateau Bay" fdr RE62165 Point Lakin could not be interogated ABNORMAL: LK44277 defective and open, AB44645 open, AB41760 closed DOp was opening defective LK44277 when RE62165 opened. Protection was non auto. Cause not ascertained. Feeder patrolled prior to restoring. T/PE to check operation of RE62165. See 1261152 exclude 1258268,307,8 | April | 2015 | 2015Q4 | 2015 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Not Veg | 2015-04-29 | N | 62 | N | 11 | N | N | 1.1101 | 39.4971 | 49340.163
[7 empty] | 13262 | 8838 | 1279141 | 2015-04-27 15:41 | 2015-04-29 20:45 | 3184 | 11kV | 49384 | 2201 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | N | No LID report Compiled via scada trends; emergency switching sheets and OMS jobs | April | 2015 | 2015Q4 | 2015 | 224:80332 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | Unknown | Unknown | 2015-04-27 | N | 22.4371 | N | 8 | N | N | 1.1101 | 39.4971 | 36088.3706
[7 empty] | 12471 | 1929 | 1258360 | 2015-04-29 22:08 | 2015-04-30 00:07 | 119 | 11kV | 145656 | 1224 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S129 Hunters Hill Panel 8 Tripped on A phase O/C Cause: Bat removed from tee off to PT1170 Huntleys Pt Rd See OMS 1258360 1258361 | April | 2015 | 2015Q4 | 2015 | ZN129:PA8 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Not Veg | 2015-04-29 | N | 119 | N | 11 | N | N | 1.1101 | 39.4971 | 106441.1087
[7 empty] | 14074 | 15594 | 1258373 | 2015-04-30 03:23 | 2015-04-30 04:29 | 66 | 11kV | 5148 | 78 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Zn12690 Berkeley Vale section of Pa24L RE45117 Glenning Valley tripped and reclosed and locked out on IOC, OC Cause not ascertained. Patrolled by DOps no cause. | April | 2015 | 2015Q4 | 2015 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2015-04-30 | N | 66 | N | 8 | N | N | 1.1101 | 39.4971 | 3762.0066
[7 empty] | 12444 | 1761 | 1265903 | 2015-04-21 02:10 | 2015-04-30 06:30 | 13220 | 11kV | 9232112 | 3025 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID Report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 3051.9379 | Y | 3 | N | Y | 1.1101 | 39.4971 | 6746555.1484
[7 empty] | 13183 | 8271 | 1235001 | 2015-04-21 04:50 | 2015-04-30 07:44 | 13134 | 11kV | 1360274 | 309 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID report Compiled via scada trends emergency switching sheet and oms jobs | April | 2015 | 2015Q4 | 2015 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 4402.1812 | Y | 3 | N | Y | 1.1101 | 39.4971 | 994048.1179
[7 empty] | 14642 | 20095 | 1245895 | 2015-04-22 20:35 | 2015-04-30 09:35 | 10860 | 11kV | 857940 | 79 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | 2 BAYS OF D/W DOWN Excludes OMS 1241161/45438/45895/48074/48753/49768/52241/55279/55830 | April | 2015 | 2015Q4 | 2015 | ZN12620:PA13 | ZN12620:PA13 | ZN12620/000013 | CENTRAL COAST | OH | Not Veg | 2015-04-22 | Y | 10860 | Y | 10 | N | Y | 1.1101 | 39.4971 | 626957.2471
[7 empty] | 13797 | 13257 | 1246562 | 2015-04-21 00:26 | 2015-04-30 09:50 | 13524.1667 | 11kV | 10095129.15 | 2192 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID report compiled from emergency switching sheets This record is for HV feeder outage that occured prior to the zone outage at Raymond Terrace | April | 2015 | 2015Q4 | 2015 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 4605.4421 | Y | 3 | N | Y | 1.1101 | 39.4971 | 7377222.6269
[7 empty] | 12535 | 2647 | 1266051 | 2015-04-21 04:45 | 2015-04-30 10:05 | 13280 | 11kV | 6796038 | 1197 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Compiled via emergency switching sheets | April | 2015 | 2015Q4 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2015-04-21 | Y | 5677.5589 | Y | 3 | N | Y | 1.1101 | 39.4971 | 4966344.1212
[7 empty] | 12506 | 2307 | 1254649 | 2015-04-20 18:00 | 2015-04-30 10:25 | 13945 | 11kV | 153395 | 11 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | Y | LID 151770 Replace x-arms and TX 12662 Excludes OMS 1254649 | April | 2015 | 2015Q4 | 2015 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2015-04-20 | Y | 13945 | N | 8 | N | Y | 1.1101 | 39.4971 | 112096.5416
[7 empty] | 14610 | 19803 | 1259317 | 2015-04-30 09:10 | 2015-04-30 11:40 | 150 | 11kV | 1050 | 7 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | LID 151812 11KV LINKS 40881 OPENED FOR REPAIRS ON SUB 65630. | April | 2015 | 2015Q4 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2015-04-30 | N | 150 | N | 8 | N | N | 1.1101 | 39.4971 | 767.309
[7 empty] | 13285 | 9008 | 1258606 | 2015-04-30 10:08 | 2015-04-30 12:40 | 152 | 11kV | 912 | 6 | HV | Vegetation Blow/Fall In | Vegetation | Lightning Arrestor | Unplanned | Rain Heavy | N | PT12499 Brush Anderson HVDO 16Amp roadside fuse operated Bark on surge arrestor See 1260902 exclude 1258606,8,74 | April | 2015 | 2015Q4 | 2015 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2015-04-30 | N | 152 | N | 8 | N | N | 1.1101 | 39.4971 | 666.4627
[7 empty] | 12351 | 892 | 1268096 | 2015-04-21 01:49 | 2015-04-30 13:01 | 13632 | 11kV | 1062856 | 176 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 265:81648 | 265:81648 | ZN00265/081648 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 6038.9545 | Y | 3 | N | Y | 1.1101 | 39.4971 | 776703.8159
[7 empty] | 12397 | 1393 | 1251319 | 2015-04-24 21:11 | 2015-04-30 13:42 | 8191.4667 | 11kV | 43919.4667 | 29 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via Emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2015-04-24 | Y | 1514.4644 | Y | 3 | N | Y | 1.1101 | 39.4971 | 32095.0508
[7 empty] | 13412 | 10241 | 1258566 | 2015-04-30 08:50 | 2015-04-30 14:25 | 335 | 11kV | 7930 | 29 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 151817 100 AMP FUSE Distribution LV fuse replace LV x-arm at sub 15933. Excludes OMS No. 1258566 + 1258630 | April | 2015 | 2015Q4 | 2015 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Not Veg | 2015-04-30 | N | 273.4483 | N | 8 | N | N | 1.1101 | 39.4971 | 5795.0101
[7 empty] | 12691 | 4054 | 1256461 | 2015-04-21 06:18 | 2015-04-30 18:15 | 13677 | 11kV | 15502074 | 2104 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No LID report Major storm Complied via emergency switching sheets Includes OMS 1266985/86/88/89/90/91/92/93/97 Wxcludes OMS1238202, 1255122, 1256462/664/610/725 | April | 2015 | 2015Q4 | 2015 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2015-04-21 | Y | 7367.9059 | N | 3 | N | Y | 1.1101 | 39.4971 | 11328458.4454
[7 empty] | 14546 | 19041 | 1258578 | 2015-04-30 09:44 | 2015-04-30 18:30 | 526 | 11kV | 1052 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | PT63074 Wise Ferry Laven 16.9 Footpath HDO operation Fuse fatigue See 1263889 exclude 1258578 | April | 2015 | 2015Q4 | 2015 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2015-04-30 | N | 526 | N | 8 | N | N | 1.1101 | 39.4971 | 768.7706
[7 empty] | 12381 | 1199 | 1259139 | 2015-04-30 16:24 | 2015-04-30 20:30 | 246 | 11kV | 984 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 151820 16 amp fuse Substation DOLF Excludes OMS 1259139 | April | 2015 | 2015Q4 | 2015 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2015-04-30 | N | 246 | N | 8 | N | N | 1.1101 | 39.4971 | 719.0782
[7 empty] | 12989 | 6738 | 1258908 | 2015-04-30 13:43 | 2015-05-01 02:25 | 762 | 11kV | 263475.0167 | 2467 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Heavy | N | ZN 10994 Mortdale - Pnl 4L - A & C phase OC, EFI, Timing, Lockout, Field EFIs. Pole fire on corner of Morts and Forest. Pole on fire and 11kV in LV. Wires down. ME: 1261149. Rest Steps: 1261150, 1. SE: 1258908, 22, 35, 75. GIS: 1258959. Withdrawn: 1258905, 57, 60. | April | 2015 | 2015Q4 | 2015 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | OH | Not Veg | 2015-04-30 | N | 106.7998 | N | 8 | N | N | 1.1101 | 39.4971 | 192539.771
[7 empty] | 13156 | 8021 | 1259271 | 2015-05-01 01:05 | 2015-05-01 03:20 | 135 | 11kV | 7114 | 54 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 151822 4 fault operations Overcurrent, Pole mounted RAGCB Removed bat from OHM at pole DG-60114. Excludes OMS 1259271, 1261022/1024 | May | 2015 | 2015Q4 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2015-05-01 | N | 131.7407 | N | 5 | N | N | 1.1101 | 39.4971 | 5198.7014
[7 empty] | 12678 | 3953 | 1259264 | 2015-04-30 22:35 | 2015-05-01 11:55 | 800 | 11kV | 47510 | 77 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | N | Ex Zn45017 Wyong section of Pa 5 "Wyong" RE45017 Whiteman tripped, reclosed, tripped & locked out on overcurrent See 1261230,4,5,6, Exclude 1259264 | April | 2015 | 2015Q4 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2015-04-30 | N | 617.013 | N | 8 | N | N | 1.1101 | 39.4971 | 34718.9067
[7 empty] | 13328 | 9543 | 1259712 | 2015-05-01 12:32 | 2015-05-01 15:05 | 153 | 11kV | 20349 | 133 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | LID 151827 interrupt to remove falllen tree from mains near sub 21707 brandy hill no5 Excludes OMS 1259712 | May | 2015 | 2015Q4 | 2015 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2015-05-01 | N | 153 | N | 5 | N | N | 1.1101 | 39.4971 | 14870.449
[7 empty] | 14414 | 18018 | 1259869 | 2015-04-23 09:01 | 2015-05-01 17:15 | 12014 | 11kV | 120140 | 10 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Previous Storm | Y | LID 151829 Isolated 11kV section to reconnect sub 52500 that was disconnected during storms. Excludes OMS 1259869 Note: amended start time as per customer calls refer to related rcord 1261071 | April | 2015 | 2015Q4 | 2015 | 238:34137 | 532:83301 | ZN00532/083301 | MAITLAND | UG | Not Veg | 2015-04-23 | Y | 12014 | N | 4 | N | Y | 1.1101 | 39.4971 | 87794.7685
[7 empty] | 12407 | 1469 | 1259964 | 2015-05-01 14:25 | 2015-05-01 17:40 | 195 | 11kV | 7995 | 41 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | LID 151830 Broken LL dropper to sub 47530. | May | 2015 | 2015Q4 | 2015 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2015-05-01 | N | 195 | N | 5 | N | N | 1.1101 | 39.4971 | 5842.5102
[7 empty] | 12832 | 5330 | 1260015 | 2015-05-01 17:57 | 2015-05-01 19:00 | 63 | 11kV | 99855 | 1585 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Ex Zn12610 Long Jetty section of Pa2 "Bateau Bay" 11kv bond off adj LK43644 ABNORMAL: AB41760 closed, defective LK44277 open, AB44645 open See 1261251 exclude 1260015,7,31,41 | May | 2015 | 2015Q4 | 2015 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Not Veg | 2015-05-01 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 72971.0888
[7 empty] | 14210 | 16581 | 1260132 | 2015-05-02 07:37 | 2015-05-02 09:25 | 108 | 11kV | 108 | 1 | HV | Animal Flying Fox | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 151833 10 amp fuse Substation DOLF Flying fox contacted HV surge arrestor and DOLF blew Excludes OMS # 1240132. | May | 2015 | 2015Q4 | 2015 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Not Veg | 2015-05-02 | N | 108 | N | 5 | N | N | 1.1101 | 39.4971 | 78.9232
[7 empty] | 13598 | 11674 | 1260123 | 2015-05-02 07:17 | 2015-05-02 10:00 | 163 | 11kV | 31626 | 418 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn340 Botany Pnl.3 tripped on: B phase IOC and EFI Field EFI @ S5444 Abnormal: S7520 (Sw B ) OPEN + Defective from 27/12/14 - S3807 (Sw A) CLOSED UG cable fault from S5444 to S7520 to S50299 see 1261780 1261782 | May | 2015 | 2015Q4 | 2015 | ZN340:PA3 | ZN340:PA3 | ZN00340/000003 | BAYSIDE | UG | Not Veg | 2015-05-02 | N | 75.6603 | N | 5 | N | N | 1.1101 | 39.4971 | 23111.348
[7 empty] | 12695 | 4094 | 1260278 | 2015-05-02 13:02 | 2015-05-02 13:35 | 33.3333 | 11kV | 26066.6667 | 782 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn80 Chatswood Panel 31 Tripped, Reclosed, Tripped and Locked out on Signals: 11kV trip Relays: B and C phase IOC Timing and Lockout Cause: Tree branch on OH mains Outside 7 Sharland Ave Chatswood See OMS 1260278 1260282 | May | 2015 | 2015Q4 | 2015 | ZN80:PA31 | ZN1193:PA15 | ZN01193/000015 | WILLOUGHBY | OH | Veg | 2015-05-02 | N | 33.3333 | N | 5 | N | N | 1.1101 | 39.4971 | 19048.7512
[7 empty] | 14237 | 16806 | 1260061 | 2015-05-01 20:16 | 2015-05-02 14:30 | 1094 | 11kV | 280979 | 690 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Berowra, Section of Panel 11 Brooklyn Feeder CP3282 Alberta Ave Tripped and Locked out Cause: Wires Down in bush between PT2386 and Recloser CP1772 See OMS 1262595 /596/597/605/604/602/603/601/600/606/607 1260061/075/105/106 | May | 2015 | 2015Q4 | 2015 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2015-05-01 | N | 407.2159 | N | 5 | N | N | 1.1101 | 39.4971 | 205331.1657
[7 empty] | 13186 | 8300 | 1260173 | 2015-05-02 09:18 | 2015-05-02 16:05 | 407 | 11kV | 105413 | 259 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Rain Heavy | N | Ex Zn12570 Avoca section of Pa22 "Davies Wilima" S14647 Bungoona Retirement C phase 11kv fuse B&S OQFRN 40A operated HV fuse operated when customer contractor removed Switch baord cover which disturbed iron filings. Customer contractor cleaned up main switch. See 1261274 exclude 1260173 | May | 2015 | 2015Q4 | 2015 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | Unknown | Not Veg | 2015-05-02 | N | 407 | N | 5 | N | N | 1.1101 | 39.4971 | 77032.7112
[7 empty] | 12807 | 5064 | 1260306 | 2015-05-02 14:21 | 2015-05-02 21:35 | 434 | 11kV | 434 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 151836 10 amp fuse Substation DOLF Excludes OMS 1260306 | May | 2015 | 2015Q4 | 2015 | 528:83014 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Veg | 2015-05-02 | N | 434 | N | 5 | N | N | 1.1101 | 39.4971 | 317.1544
[7 empty] | 12881 | 5854 | 1260457 | 2015-05-03 00:33 | 2015-05-03 02:52 | 139 | 11kV | 4161 | 35 | HV | Animal Possum | Animal | O/H Conductor ABC | Unplanned | No Weather Impact | N | LID 151840 1 fault operation Sensitive earth fault, Pole mounted RAGCB Removed possum from sub 2382 Excludes OMS 1260457/460, 1261035 | May | 2015 | 2015Q4 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-05-03 | N | 118.8857 | N | 5 | N | N | 1.1101 | 39.4971 | 3040.7361
[7 empty] | 14278 | 17059 | 1260470 | 2015-05-03 04:00 | 2015-05-03 07:35 | 215 | 11kV | 131440 | 1553 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Rain Heavy | N | Zn12650 West Gosford 11kv Pa22 "Central Moore" tripped on: Relays: ABC phase IOC, EFI EFI's S18737 S18121 Zn12790 Mason Shortland endbox failed explosively See 1261333,4,5 Exclude 1260470,5 | May | 2015 | 2015Q4 | 2015 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | UG | Not Veg | 2015-05-03 | N | 84.6362 | N | 5 | N | N | 1.1101 | 39.4971 | 96052.4752
[7 empty] | 14163 | 16247 | 1260462 | 2015-05-03 01:50 | 2015-05-03 15:05 | 795 | 11kV | 13072 | 78 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | Ex Zn12690 Berkeley Vale section of pa24L "Berkely rd" tripped and locked out Possible lightning arrestor failure on Pole BV1898 (EFI pole below LB44419) See 1261390,1,2,3 Exclude 1260463,7,8,522 | May | 2015 | 2015Q4 | 2015 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2015-05-03 | N | 167.5897 | N | 5 | N | N | 1.1101 | 39.4971 | 9552.632
[7 empty] | 14070 | 15584 | 1260679 | 2015-05-03 13:19 | 2015-05-03 22:20 | 541 | 11kV | 57185 | 1285 | HV | Animal Bird | Animal | O/H Conductor ABC | Unplanned | No Weather Impact | N | LID 151844 Earth fault Bird hit fdr bringing OHM down between JR-84103 and JR-80138 Excludes OMS 1261179/80/81/82 &1260686/689/710/743 | May | 2015 | 2015Q4 | 2015 | 238:34141 | 238:34136 | ZN00238/034136 | MAITLAND | OH | Not Veg | 2015-05-03 | N | 44.5019 | N | 5 | N | N | 1.1101 | 39.4971 | 41789.1113
[7 empty] | 14179 | 16335 | 1260811 | 2015-05-03 23:56 | 2015-05-04 01:48 | 111.6333 | 11kV | 4353.7 | 39 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Light | N | LID 151846 Isolated 11kV section 7111/62924 to trim tree in OHM, sub 20385 interrupted only. Excludes OMS 1260769 | May | 2015 | 2015Q4 | 2015 | 239:82129 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Veg | 2015-05-03 | N | 111.6333 | N | 5 | N | N | 1.1101 | 39.4971 | 3181.5555
[7 empty] | 13956 | 14606 | 1261039 | 2015-05-04 10:32 | 2015-05-04 11:28 | 56 | 11kV | 99120 | 1770 | HV | 3rd Party Vehicle | 3rd Party Impact | Air Break Switch | Unplanned | No Weather Impact | N | Zn12570 Avoca section of Pa37 "Avoca Beach" fdr (No protection operation) @AB43386 bottom down rod has been broken by truck. No truck on site. Witnesses advised local council removing tree in Cheswick St See 1263062 GIS 1261050,63,75 exclude 1261039 | May | 2015 | 2015Q4 | 2015 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2015-05-04 | N | 56 | N | 5 | N | N | 1.1101 | 39.4971 | 72433.9725
[7 empty] | 14603 | 19686 | 1260847 | 2015-05-04 09:30 | 2015-05-04 13:30 | 240 | 11kV | 1200 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 151849 33kV pole fire IQ-92833 report 151850 11kV isolation follows T/R Sw 82579 report 151848 Note 11kV system abnormal 41444 closed 43101 open | May | 2015 | 2015Q4 | 2015 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2015-05-04 | N | 240 | N | 5 | N | N | 1.1101 | 39.4971 | 876.9246
[7 empty] | 12853 | 5588 | 1261528 | 2015-05-04 16:50 | 2015-05-04 19:50 | 180 | 11kV | 8460 | 47 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn14144 Wamberal Zone section of Pa10L "Wamberal Aux No2" fdr from AB45403 to rest of fdr Broken cross arm at PT11815 Matcham Impala 0.4. outside 303 matcham rd matcham isolated for emergency repairs See 1263120 exclude 1261528,33 | May | 2015 | 2015Q4 | 2015 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2015-05-04 | N | 180 | N | 5 | N | N | 1.1101 | 39.4971 | 6182.3185
[7 empty] | 13148 | 7973 | 1260817 | 2015-05-04 03:27 | 2015-05-04 21:12 | 1065 | 11kV | 318472 | 3596 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | LID 151847 2 fault operations earth fault and LID 151855 Overcurrent, Earth fault, Sensitive earth fault Includes OMS1265340/45/47/48/49/56/58 Excludes OMS 1260817, 1261474/78/79/80 | May | 2015 | 2015Q4 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | CESSNOCK | OH | Not Veg | 2015-05-04 | N | 88.5628 | N | 5 | N | N | 1.1101 | 39.4971 | 232729.9443
[7 empty] | 13810 | 13340 | 1261281 | 2015-05-04 13:23 | 2015-05-04 23:55 | 632 | 11kV | 13272 | 21 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 151858 Conductor Excludes OMS 1261281 | May | 2015 | 2015Q4 | 2015 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2015-05-04 | N | 632 | N | 5 | N | N | 1.1101 | 39.4971 | 9698.7861
[7 empty] | 12330 | 722 | 1261633 | 2015-05-05 06:31 | 2015-05-05 10:30 | 239 | 11kV | 10038 | 42 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT13613 Bar Point HDO Blown 10 Amp fuse blown due to fuse fatigue. See 1262719 exclude 1261633,4 | May | 2015 | 2015Q4 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2015-05-05 | N | 239 | N | 7 | N | N | 1.1101 | 39.4971 | 7335.4743
[7 empty] | 13805 | 13324 | 1261659 | 2015-05-05 08:10 | 2015-05-05 11:48 | 218 | 11kV | 698 | 5 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 151864 20 amp line DOLF Broken stay at sub 71321 Excludes OMS 1261659 + 1262359 | May | 2015 | 2015Q4 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2015-05-05 | N | 139.6 | N | 7 | N | N | 1.1101 | 39.4971 | 510.0778
[7 empty] | 14451 | 18309 | 1261949 | 2015-05-05 13:17 | 2015-05-05 17:19 | 241.8 | 11kV | 65769.6 | 272 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 151866 2 fault opersations Overcurrent tree on mains near sub 17034 Prot = 50TAC | May | 2015 | 2015Q4 | 2015 | 240:34843 | 240:34843 | ZN00240/034843 | NEWCASTLE | OH | Veg | 2015-05-05 | N | 241.8 | N | 7 | N | N | 1.1101 | 39.4971 | 48062.4838
[7 empty] | 12826 | 5279 | 1262132 | 2015-05-05 18:10 | 2015-05-05 20:45 | 155 | 11kV | 4650 | 30 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | No Weather Impact | N | LID 151873 CCT hanging adjacent to LV mains at pole KQ-10042 Italia Rd. | May | 2015 | 2015Q4 | 2015 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2015-05-05 | N | 155 | N | 7 | N | N | 1.1101 | 39.4971 | 3398.0828
[7 empty] | 13453 | 10572 | 1262136 | 2015-05-05 18:13 | 2015-05-05 20:50 | 157 | 11kV | 314 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151872 10 amp fuse Substation DOLF Excludes OMS 1262136 | May | 2015 | 2015Q4 | 2015 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2015-05-05 | N | 157 | N | 7 | N | N | 1.1101 | 39.4971 | 229.4619
[7 empty] | 14313 | 17304 | 1261624 | 2015-05-05 23:41 | 2015-05-06 00:47 | 66 | 11kV | 5742 | 87 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S8000 Macquarie Park Panel 15 Tripped on 51N Earth Fault, Fault Check E/F Check and No2 Tx Group EFI Abnormal Switching: S65035 toi S1958 to S7488 O/O/S Cause: UG Cable Fault See OMS 1262550 1261624 | May | 2015 | 2015Q4 | 2015 | ZN8000:PA15 | ZN8000:PA15 | ZN08000/000015 | RYDE | UG | Not Veg | 2015-05-05 | N | 66 | N | 7 | N | N | 1.1101 | 39.4971 | 4196.0842
[7 empty] | 13289 | 9035 | 1261989 | 2015-05-05 15:15 | 2015-05-06 12:00 | 1245 | 11kV | 19505 | 167 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14143 Someersby section of pa17 "Somersby Falls" RE45012 Bar Point. No protection operation. RE45012 opened by AOp @ 15:15. 11kv wires down to PT13617 RE45012 previously tripped on Earth Fault @ 12:57. See 1263141,3 Exclude 1261989,2002,122 | May | 2015 | 2015Q4 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2015-05-05 | N | 116.7964 | N | 7 | N | N | 1.1101 | 39.4971 | 14253.6787
[7 empty] | 14102 | 15803 | 1262518 | 2015-05-06 14:10 | 2015-05-06 14:20 | 10 | 11kV | 870 | 87 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 151878 faulty dolf burning up. CAW to replace Excludes OMS 1262518 | May | 2015 | 2015Q4 | 2015 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | OH | Not Veg | 2015-05-06 | N | 10 | N | 3 | N | N | 1.1101 | 39.4971 | 635.7703
[7 empty] | 13219 | 8538 | 1262773 | 2015-05-06 18:19 | 2015-05-06 19:15 | 55.8833 | 11kV | 1620.6167 | 29 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14144 Wamberal section of pa10 "wamberal" fdr beyond USL40062 interrupted to allow emergency tree removal 43 brush rd See 1262773 exclude 1262728 | May | 2015 | 2015Q4 | 2015 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2015-05-06 | N | 55.8833 | N | 3 | N | N | 1.1101 | 39.4971 | 1184.2989
[7 empty] | 12813 | 5123 | 1262782 | 2015-05-06 18:39 | 2015-05-06 19:20 | 40.95 | 11kV | 1760.85 | 43 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 151880 section deenergised to repair xarm at pole IU-30675 no protection operation Excludes OMS 1262786/87 | May | 2015 | 2015Q4 | 2015 | 213:33771 | 213:33771 | ZN00213/033771 | NEWCASTLE | OH | Not Veg | 2015-05-06 | N | 40.95 | N | 3 | N | N | 1.1101 | 39.4971 | 1286.7772
[7 empty] | 14548 | 19052 | 1263036 | 2015-05-07 10:55 | 2015-05-07 11:35 | 40 | 11kV | 40 | 1 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN384 Camperdown Pnl.30 tripped on: Earth Fault & EFI. UG cable fault. Recently returned to service on 7/5/15 after defective repairs. #360527 Only received bluey from control room 6/7/15 also refer to 1263036 | May | 2015 | 2015Q4 | 2015 | ZN384:PA30 | ZN7481:PA20 | ZN07481/000020 | SYDNEY | UG | Not Veg | 2015-05-07 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 29.2308
[7 empty] | 14549 | 19053 | 1262845 | 2015-05-07 07:28 | 2015-05-07 12:45 | 317 | 11kV | 634 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 151890 HV Dropper broken away from dolf Excludes OMS 1262845 | May | 2015 | 2015Q4 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2015-05-07 | N | 317 | N | 4 | N | N | 1.1101 | 39.4971 | 463.3085
[7 empty] | 14631 | 19989 | 1263096 | 2015-05-07 12:29 | 2015-05-07 18:45 | 376 | 11kV | 3384 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151894 100 amp fuse Distribution LV fuse Excludes OMS 1263096 | May | 2015 | 2015Q4 | 2015 | 512:48046 | 512:83741 | ZN00512/083741 | CESSNOCK | OH | Veg | 2015-05-07 | N | 376 | N | 4 | N | N | 1.1101 | 39.4971 | 2472.9274
[7 empty] | 12956 | 6496 | 1263193 | 2015-05-07 13:00 | 2015-05-07 19:00 | 360 | 11kV | 9630 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 151895 2 fault operations Pole mounted RAGCB, Sectionaliser Includes OMS 1263430 Excludes OMS 1263306 | May | 2015 | 2015Q4 | 2015 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2015-05-07 | N | 343.9286 | N | 4 | N | N | 1.1101 | 39.4971 | 7037.32
[7 empty] | 13835 | 13505 | 1234446 | 2015-04-21 01:41 | 2015-05-08 09:13 | 24931.6167 | 11kV | 6124507 | 1997 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Compiled off switching sheets - no LID Two seperate fault operations on feeder 80775 First fault due to wire down at pole JT 72211 between subs 43129 & 13755 Part feeder restored and then a second fault - pole at JU14763 moved (due to tree contact?) | April | 2015 | 2015Q4 | 2015 | 258:80775 | 258:80775 | ZN00258/080775 | NEWCASTLE | OH | Not Veg | 2015-04-21 | Y | 3066.8538 | Y | 3 | N | Y | 1.1101 | 39.4971 | 4475609.0732
[7 empty] | 13243 | 8703 | 1263439 | 2015-05-08 08:31 | 2015-05-08 13:10 | 279 | 11kV | 1953 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 151906 Burnt off tapping P AF-40020 No Protection Excludes OMS 1263439, 1263526, 1264366 | May | 2015 | 2015Q4 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2015-05-08 | N | 279 | N | 3 | N | N | 1.1101 | 39.4971 | 1427.1948
[7 empty] | 12751 | 4606 | 1263913 | 2015-05-08 19:00 | 2015-05-08 20:50 | 110 | 11kV | 4180 | 38 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 151908 11kV Mains hanging Low. | May | 2015 | 2015Q4 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2015-05-08 | N | 110 | N | 3 | N | N | 1.1101 | 39.4971 | 3054.6207
[7 empty] | 13330 | 9581 | 1263564 | 2015-05-08 09:59 | 2015-05-09 00:15 | 856 | 11kV | 164979 | 703 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN 9900 Menai - Pnl 19 - Trip/reclose/trip, All phases OC, SEL, Lockout, EFI, Field EFIs. Tree brought down HV and LV mains adjacent to AB 35364. High into low. ME: 1264455. Rest Step: 1264458. Withdrawn: 1263834, 564, 569, 898, 934. | May | 2015 | 2015Q4 | 2015 | ZN9900:PA19 | ZN9900:PA19 | ZN09900/000019 | SUTHERLAND | OH | Veg | 2015-05-08 | N | 234.6785 | N | 3 | N | N | 1.1101 | 39.4971 | 120561.7871
[7 empty] | 12654 | 3784 | 1263932 | 2015-05-09 00:01 | 2015-05-09 08:50 | 529 | 11kV | 42850 | 111 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 151909 5 fault operations Pole mounted RAGCB tree over mains & Broken xarm at pole MG-20140 Includes OMS 1267278/79/80 Excludes OMS 1263942 | May | 2015 | 2015Q4 | 2015 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2015-05-09 | N | 386.036 | N | 3 | N | N | 1.1101 | 39.4971 | 31313.5161
[7 empty] | 13281 | 8983 | 1264023 | 2015-05-09 11:58 | 2015-05-09 19:00 | 422 | 11kV | 55733 | 479 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | EX ZN 9550 Gwawley Bay - Pnl 43 - Beyond LB 35904 interrupted for safety reasons. Car hit pole CRO-8872 - police job number 393457. Lineworker reported pole OK, but 11kV mains had come away from pin insulators and rested on HV crossarms. DOp interrupted feeder for safety. ME: 1264426. Rest Steps: 1264427, 8. Withdrawn: 1264023, 45, 69, 95. | May | 2015 | 2015Q4 | 2015 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Not Veg | 2015-05-09 | N | 116.3528 | N | 3 | N | N | 1.1101 | 39.4971 | 40728.0326
[7 empty] | 14161 | 16229 | 1264103 | 2015-05-09 21:14 | 2015-05-09 23:24 | 130 | 11kV | 5616 | 46 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14143 Somersby Pa6 fdr tripped on Relats - EFI Tx1 Earth Fault Check Relay EFI's S18379 S14634 S18540 S18454 S18253 S18339 S18636 S18256 S14278 S18084 Signals - Group Earth UG fault from S18084:B to RE44948 Myoora Somersby 0.1 tripped on earth fault trip See 1264872.4 exclude 1264103 | May | 2015 | 2015Q4 | 2015 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | UG | Not Veg | 2015-05-09 | N | 122.087 | N | 3 | N | N | 1.1101 | 39.4971 | 4104.0072
[7 empty] | 12325 | 671 | 1264145 | 2015-05-10 10:46 | 2015-05-10 12:02 | 76 | 11kV | 32756 | 431 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 151913 2 fault op[erations Overcurrent tree branch removed from OHM adjacent sub 3750 | May | 2015 | 2015Q4 | 2015 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Veg | 2015-05-10 | N | 76 | N | 8 | N | N | 1.1101 | 39.4971 | 23937.1187
[7 empty] | 14281 | 17095 | 1264133 | 2015-05-10 09:38 | 2015-05-10 12:55 | 196.9167 | 11kV | 1181.5 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 151914 20 amp fuse Line DOLF Feeder patrolled. No cause found. | May | 2015 | 2015Q4 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2015-05-10 | N | 196.9167 | N | 8 | N | N | 1.1101 | 39.4971 | 863.4054
[7 empty] | 14359 | 17599 | 1264149 | 2015-05-10 11:08 | 2015-05-10 13:34 | 146 | 11kV | 47451 | 519 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S35370 Galston Panel 10 tripped on A and C phase IOC with efi Signals: 11kV trip See OMS1264568 1264554 1264567 1264149 | May | 2015 | 2015Q4 | 2015 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2015-05-10 | N | 91.4277 | N | 8 | N | N | 1.1101 | 39.4971 | 34675.7912
[7 empty] | 14113 | 15897 | 1264194 | 2015-05-10 14:04 | 2015-05-10 14:46 | 42 | 11kV | 26292 | 626 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | ZN.15013 Terrey Hills 11kV Panel 10 feeder tripped and locked out on:- C phase timed and inst OC, reclose timedelay and lock out relay, EFI Cause:- Tree/branch on OH mains outside Mona Vale Rd, Mona Vale ME:-1264194 GIS Model Error:-1264202 Withdrawn:-1264197 | May | 2015 | 2015Q4 | 2015 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2015-05-10 | N | 42 | N | 8 | N | N | 1.1101 | 39.4971 | 19213.4181
[7 empty] | 13476 | 10743 | 1264203 | 2015-05-10 14:29 | 2015-05-10 15:37 | 68 | 11kV | 36392 | 3007 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 151916 2 fault operations Instantaneous overcurrent Fdr 81541 switched abnormally ABS 46083 closed & ABS 4629 open. Removed tree branch on mains at pole NB-10177. Targets Sw 81541 = 51 ABC. Includes OMS 1265283 Excludes OMS 1264203/205. | May | 2015 | 2015Q4 | 2015 | 242:81541 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Veg | 2015-05-10 | N | 12.1024 | N | 8 | N | N | 1.1101 | 39.4971 | 26594.2002
[7 empty] | 12517 | 2416 | 1264175 | 2015-05-10 12:30 | 2015-05-10 16:20 | 230 | 11kV | 690 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 151919 LL lead hanging. No heatshrink fetted at lug. Excludes OMS 1264175/76/200 | May | 2015 | 2015Q4 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-05-10 | N | 230 | N | 8 | N | N | 1.1101 | 39.4971 | 504.2316
[7 empty] | 13764 | 13010 | 1264261 | 2015-05-10 19:58 | 2015-05-10 21:30 | 92 | 11kV | 919.75 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12600 lisarow section of Pa13 PT14182 Pryor Cutrock 0.3 11kv 16amp roadside dropout fuse operated Fuse fatigue See 1264262 GIS 1264261 CC1: 22-"Refer to SOp" | May | 2015 | 2015Q4 | 2015 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2015-05-10 | N | 91.975 | N | 8 | N | N | 1.1101 | 39.4971 | 672.1262
[7 empty] | 12495 | 2208 | 1264265 | 2015-05-10 20:14 | 2015-05-10 22:25 | 131 | 11kV | 34846 | 266 | HV | Burnt Contacts | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Section of he 'O' Donnell Ave' feeder panel No.33 at S1285 Greenacre Park, beyond AB.2034 Remarks: Air break switch - details below. AB 2034, Roadside phase contact burnt off | May | 2015 | 2015Q4 | 2015 | ZN1285:PA33 | ZN1285:PA33 | ZN01285/000033 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-05-10 | N | 131 | N | 8 | N | N | 1.1101 | 39.4971 | 25464.429
[7 empty] | 12764 | 4688 | 1264278 | 2015-05-11 02:05 | 2015-05-11 03:00 | 55 | 11kV | 605 | 11 | HV | Animal Possum | Animal | DC Transformer | Unplanned | No Weather Impact | Y | PT13235 Brieses Peats Ridge 0.8 B & C phase 11kv fuses blown due to Possum across tx bushing See 1264918 exclude 1264278,9 | May | 2015 | 2015Q4 | 2015 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2015-05-11 | Y | 55 | N |  | N | Y | 1.1101 | 39.4971 | 442.1162
[7 empty] | 14195 | 16474 | 1264285 | 2015-05-11 04:54 | 2015-05-11 07:22 | 148 | 11kV | 10920 | 111 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | LID 151920 3 fault operations Pole mounted RAGCB tree removed from OHM adjacent sub 47367 Include OMS 1267029 Excludes OMS 1264285 | May | 2015 | 2015Q4 | 2015 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2015-05-11 | Y | 98.3784 | N |  | N | Y | 1.1101 | 39.4971 | 7980.0139
[7 empty] | 14132 | 16073 | 1264286 | 2015-05-11 04:57 | 2015-05-11 08:23 | 206 | 11kV | 24926 | 121 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | Section of ZN.15013 11kV Panel 6 from RE.20828 (9 DC's) to extent of feeder tripped on OC with lockout Abnormal Switching:- CP.25194 closed, CP.26217 open Cause:- Tree/branch on OH mains, removed by D/Op adjacent to CP.21895 ME:-1265151 Withdrawn:-1264286 | May | 2015 | 2015Q4 | 2015 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2015-05-11 | Y | 206 | N |  | N | Y | 1.1101 | 39.4971 | 18215.1856
[7 empty] | 12984 | 6713 | 1264297 | 2015-05-11 06:08 | 2015-05-11 12:23 | 375 | 11kV | 444704 | 2132 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Wind Strong | Y | Zn12570 Avoca Pa37L "Avoca Beach" tripped on Relays: A 7 b phase timed OC Signals: 11kv trip ABNORMAL: AB43386 open and defective. AB43387 Closed 11kv UGOH fault short circuit adjacent CP45180 Avoca beach. Fault current also caused an 11kv bond off the main line between PT63507 and PT11071 See 1266296,8 Exclude 1264297,532 | May | 2015 | 2015Q4 | 2015 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | Unknown | Unknown | 2015-05-11 | Y | 208.5854 | N |  | N | Y | 1.1101 | 39.4971 | 324976.5667
[7 empty] | 12943 | 6359 | 1264459 | 2015-05-11 04:38 | 2015-05-11 12:25 | 467 | 11kV | 109867 | 419 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | Section of ZN.15002 Narrabeen 11kV Panel 2L from RE.20112 (16 DC's) to extent of feeder tripped, reclosed and tripped on:- Relays:- OC trip, lockout Abnormal Switching:- CP.20234 closed, CP.20693 open and defective Cause:- Tree/branch on OH HV & LV mains at 220 Powder Works Rd ME:-1265165 RS:-1265167 Withdrwan:-1264283, 1264284, 1264323, 1264336, 1264377, 1264411, 1264430, 1264470, 1264471, 1264519 | May | 2015 | 2015Q4 | 2015 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2015-05-11 | Y | 262.2124 | N |  | N | Y | 1.1101 | 39.4971 | 80287.5631
[7 empty] | 14296 | 17209 | 1264714 | 2015-05-11 12:13 | 2015-05-11 12:54 | 41 | 11kV | 50102 | 1222 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | Y | ZN 9700 Kirrawee - Pnl 15 - Trip/reclose/trip, A phase IOC and Timed OC, Timing, lockout. Tree branch on 11kV mains opposite 3 Serpentine Rd, Gymea. ME: 1264714. Withdrawn: 1264722, 62. | May | 2015 | 2015Q4 | 2015 | ZN9700:PA15 | ZN9700:PA15 | ZN09700/000015 | SUTHERLAND | OH | Veg | 2015-05-11 | Y | 41 | N |  | N | Y | 1.1101 | 39.4971 | 36613.0638
[7 empty] | 13731 | 12776 | 1264643 | 2015-05-11 11:19 | 2015-05-11 13:00 | 101 | 11kV | 303 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Wind Strong | Y | LID 151925 20 amp fuse Substation DOLF Replaced blown LA. Excludes OMS No. 1264643 | May | 2015 | 2015Q4 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2015-05-11 | Y | 101 | N |  | N | Y | 1.1101 | 39.4971 | 221.4235
[7 empty] | 13681 | 12373 | 1264649 | 2015-05-11 11:21 | 2015-05-11 13:13 | 112 | 11kV | 59312 | 3007 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | LID 151924 2 fault operations Overcurrent Fdr abnormal 46083 closed 4629 open section patrolled OK, tree branch pole NB-10177 Magnus St. Prot = 51ab Includes OMS 1265210 Excludes OMS 1264649/55/59/60/70/706/728 | May | 2015 | 2015Q4 | 2015 | 242:81541 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Veg | 2015-05-11 | Y | 19.7246 | N |  | N | Y | 1.1101 | 39.4971 | 43343.4602
[7 empty] | 12348 | 867 | 1264646 | 2015-05-11 11:21 | 2015-05-11 13:21 | 120 | 11kV | 2400 | 20 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | Y | LID 151926 Repair broken LL Clamp lead. Excludes OMS No. 1264646 | May | 2015 | 2015Q4 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2015-05-11 | Y | 120 | N |  | N | Y | 1.1101 | 39.4971 | 1753.8492
[7 empty] | 13521 | 11081 | 1264621 | 2015-05-11 11:06 | 2015-05-11 14:51 | 225 | 11kV | 675 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | Y | LID 151928 Repair broken LL Clamp lead. Excludes OMS No. 1264621 | May | 2015 | 2015Q4 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2015-05-11 | Y | 225 | N |  | N | Y | 1.1101 | 39.4971 | 493.2701
[7 empty] | 14415 | 18028 | 1264910 | 2015-05-11 15:50 | 2015-05-11 17:45 | 115 | 11kV | 920 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | Ex Zn12630 Peats Ridge Pa1 "Grants rd" fdr LK47842 interrupted for safety. Large tree broke 11kv cross arm leaving 11kv alive and just out of reach above ground. | May | 2015 | 2015Q4 | 2015 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2015-05-11 | Y | 115 | N |  | N | Y | 1.1101 | 39.4971 | 672.3089
[7 empty] | 13541 | 11200 | 1265061 | 2015-05-11 12:19 | 2015-05-11 18:50 | 391 | 11kV | 2346 | 6 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | LID 151929 Overcurrent Helicopter hit AGL 132 fdr 95b bringing down mains onto ausgrid Swer line Excludes oms 1264802,1265074,1265061 | May | 2015 | 2015Q4 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2015-05-11 | Y | 391 | N |  | N | Y | 1.1101 | 39.4971 | 1714.3876
[7 empty] | 12918 | 6104 | 1265051 | 2015-05-11 16:32 | 2015-05-11 22:00 | 328 | 11kV | 328 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | Y | LID 151932 burnt off tapping at dolf 23178. dq Excludes OMS 1265051 | May | 2015 | 2015Q4 | 2015 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2015-05-11 | Y | 328 | N |  | N | Y | 1.1101 | 39.4971 | 239.6927
[7 empty] | 13432 | 10442 | 1264958 | 2015-05-11 16:24 | 2015-05-11 23:10 | 406 | 11kV | 34338 | 163 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | Y | Ex Zn12570 Avoca section of Pa37L "Avoca Beach" fdr section of 11kv mains from LB41678 to S18698 Ficus Avoca interrupted for safety DOp interrupted section of mains due to broken LV cross arm and 11kv pins. See 126636,7 exclude 1264958,5056 | May | 2015 | 2015Q4 | 2015 | ZN12570:PA37 | ZN12570:PA39 | ZN12570/000039 | CENTRAL COAST | OH | Not Veg | 2015-05-11 | Y | 210.6626 | N |  | N | Y | 1.1101 | 39.4971 | 25093.1976
[7 empty] | 12806 | 5061 | 1265138 | 2015-05-12 04:31 | 2015-05-12 05:30 | 59 | 11kV | 649 | 11 | HV | Animal Possum | Animal | Fuse | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge 0.8 section of "Gunderman" fdr PT13235 Briesses Peats Ridge 0.8 centre and roadside HDO's blew Possum across centre phase tx bushing, second time in 24hrs See 1266669 exclude 1265138,9,40 | May | 2015 | 2015Q4 | 2015 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2015-05-12 | N | 59 | N | 6 | N | N | 1.1101 | 39.4971 | 474.2701
[7 empty] | 14266 | 16996 | 1265256 | 2015-05-12 09:03 | 2015-05-12 13:05 | 242 | 11kV | 484 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 151946 Replace broken LL clamp lead at pole DI-60097. Excludes OMS 1265256 | May | 2015 | 2015Q4 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2015-05-12 | N | 242 | N | 6 | N | N | 1.1101 | 39.4971 | 353.6929
[7 empty] | 12753 | 4615 | 1265355 | 2015-05-12 10:56 | 2015-05-12 13:35 | 159 | 11kV | 477 | 3 | HV | Staff Operation | Utility Process Issue | Fuse | Unplanned | No Weather Impact | N | LID 151953 31 amp fuse Substation DOLF 3.15 installed previously instead of 31.5A Excludes OMS 1265355 | May | 2015 | 2015Q4 | 2015 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2015-05-12 | N | 159 | N | 6 | N | N | 1.1101 | 39.4971 | 348.5775
[7 empty] | 12435 | 1692 | 1265645 | 2015-05-12 17:45 | 2015-05-12 19:40 | 115 | 11kV | 345 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | No Weather Impact | N | LID 151954 CCT resting on crossarm | May | 2015 | 2015Q4 | 2015 | 503:48017 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Not Veg | 2015-05-12 | N | 115 | N | 6 | N | N | 1.1101 | 39.4971 | 252.1158
[7 empty] | 12399 | 1398 | 1265617 | 2015-05-12 18:00 | 2015-05-12 20:50 | 170 | 11kV | 680 | 4 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 151955 No Protection Broken xarm P HS30005 Excludes OMS 1265617/18/69 | May | 2015 | 2015Q4 | 2015 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2015-05-12 | N | 170 | N | 6 | N | N | 1.1101 | 39.4971 | 496.9239
[7 empty] | 13341 | 9664 | 1265656 | 2015-05-12 18:18 | 2015-05-12 22:27 | 248.8167 | 11kV | 91680.2667 | 974 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex ZN 10991 Blakehurst - Pnl 12 - AB 30050 one phase open circuit. Bond burnt off at AB 30050. ME: 1265812. GIS: 1265668. Withdrawn: 1265654, 56, 62. | May | 2015 | 2015Q4 | 2015 | ZN10991:PA12 | ZN10991:PA12 | ZN10991/000012 | GEORGES RIVER | OH | Not Veg | 2015-05-12 | N | 94.1276 | N | 6 | N | N | 1.1101 | 39.4971 | 66997.2348
[7 empty] | 13474 | 10720 | 1265778 | 2015-05-13 06:34 | 2015-05-13 07:30 | 56 | 11kV | 29004 | 519 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | At Zn35370 Galston Panel 10 Tripped on Relays: SEL Signals 11kV Trip Cause: Middle Phase Bond Load Side Burnt Off at AB2270 See OMS 1268748 1268749 1265778/786/798/781 | May | 2015 | 2015Q4 | 2015 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2015-05-13 | N | 55.8844 | N | 5 | N | N | 1.1101 | 39.4971 | 21195.2677
[7 empty] | 13468 | 10676 | 1265808 | 2015-05-13 07:48 | 2015-05-13 08:27 | 38.3 | 11kV | 56071.2 | 1464 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12620 Noraville section of Pa1L "Noraville Aux" ABNORMAL: LB63530 closed with LB40197 opened and LB44447 closed with AB41549 opened (D/R 360073) Middle phase bond bunrt at LB63530 CC1: 22-"Refer to SOp" | May | 2015 | 2015Q4 | 2015 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2015-05-13 | N | 38.3 | N | 5 | N | N | 1.1101 | 39.4971 | 40975.1791
[7 empty] | 13948 | 14575 | 1266143 | 2015-05-13 13:34 | 2015-05-13 14:58 | 84 | 11kV | 36457 | 439 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 151972 1 fault operation Overcurrent stick on ohm nr abs 18583 Include OMS 1267049 Exclude OMS 1266110 | May | 2015 | 2015Q4 | 2015 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2015-05-13 | N | 83.0456 | N | 5 | N | N | 1.1101 | 39.4971 | 26641.7003
[7 empty] | 14058 | 15458 | 1266351 | 2015-05-13 21:30 | 2015-05-13 22:10 | 40 | 11kV | 13000 | 325 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 151977 No protection operation. Isolated to repair high resistance joint pole JU-61266 . Outage area extended due to ABS 17513 not opening. Excludes OMS - 1266351/54/55 | May | 2015 | 2015Q4 | 2015 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2015-05-13 | N | 40 | N | 5 | N | N | 1.1101 | 39.4971 | 9500.0166
[7 empty] | 12834 | 5357 | 1266335 | 2015-05-13 20:05 | 2015-05-14 01:35 | 330 | 11kV | 14567 | 70 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 151975 1 fault operation Pole mounted RAGCB, Sensitive earth fault B phase 11kV main on ground between poles GP-32906 & GP-32907. Includes OMS 1266452/53 Excludes OMS No. 1266335 + 1266336 + 1266362 | May | 2015 | 2015Q4 | 2015 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2015-05-13 | N | 208.1 | N | 5 | N | N | 1.1101 | 39.4971 | 10645.1339
[7 empty] | 12698 | 4145 | 1266366 | 2015-05-14 05:45 | 2015-05-14 08:32 | 167 | 11kV | 5229 | 62 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | LID 151979 2 fault operations Overcurrent, Earth fault Pelican into OHM near sub 51405 Includes OMS 1267120/21/22/23/24 Excludes OMS 1266366, 1266381 | May | 2015 | 2015Q4 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2015-05-14 | Y | 84.3387 | N |  | N | Y | 1.1101 | 39.4971 | 3821.199
[7 empty] | 13187 | 8301 | 1238195 | 2015-04-21 06:15 | 2015-05-14 10:00 | 33345.15 | 11kV | 1632314.8333 | 200 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | No LID report Compiled via emergency switching sheet | April | 2015 | 2015Q4 | 2015 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2015-04-21 | Y | 8161.5742 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1192847.5351
[7 empty] | 13861 | 13781 | 1266673 | 2015-05-14 11:50 | 2015-05-14 12:30 | 40 | 11kV | 1080 | 27 | HV | 3rd Party Vehicle | 3rd Party Impact | Pillar | Unplanned | No Weather Impact | Y | LID 151990 sub isolated after truck reversed over pillar box IV-90113. | May | 2015 | 2015Q4 | 2015 | 220:8687 | 220:8687 | ZN00220/008687 | LAKE MACQUARIE | UG | Not Veg | 2015-05-14 | Y | 40 | N |  | N | Y | 1.1101 | 39.4971 | 789.2321
[7 empty] | 14060 | 15479 | 1266439 | 2015-05-14 08:15 | 2015-05-14 13:00 | 285 | 11kV | 2280 | 8 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | Bird brought down 11kV mains at pole DR40142. Isolated at 11kV links HC02898 and power restored to the rest of the feeder. Excludes OMS 1266426/439 | May | 2015 | 2015Q4 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2015-05-14 | Y | 285 | N |  | N | Y | 1.1101 | 39.4971 | 1666.1568
[7 empty] | 12902 | 5990 | 1266399 | 2015-05-14 07:46 | 2015-05-14 13:20 | 334 | 11kV | 105544 | 316 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | LID 151991 1 fault operation Bird into OHM at ABS 64605 Excludes OMS 1266563 | May | 2015 | 2015Q4 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2015-05-14 | Y | 334 | N |  | N | Y | 1.1101 | 39.4971 | 77128.4422
[7 empty] | 13091 | 7594 | 1266642 | 2015-05-14 11:19 | 2015-05-14 15:40 | 261.45 | 11kV | 4706.1 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | Y | LID 151992 HV into LV @ sub51909 11kv conductor broken at Sub 51909. Conductor repaired and supply restored. | May | 2015 | 2015Q4 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-05-14 | Y | 261.45 | N |  | N | Y | 1.1101 | 39.4971 | 3439.0791
[7 empty] | 12327 | 678 | 1267026 | 2015-05-15 08:44 | 2015-05-15 09:42 | 58 | 11kV | 77894 | 1343 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn847 Hornsby Panel 21 Tripped Signals: 11kV Trip. Tree branch O/S 49 Manor Rd Hornsby | May | 2015 | 2015Q4 | 2015 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Veg | 2015-05-15 | N | 58 | N | 7 | N | N | 1.1101 | 39.4971 | 56922.6377
[7 empty] | 14688 | 20431 | 1267198 | 2015-05-15 12:17 | 2015-05-15 13:27 | 70 | 11kV | 71258 | 1738 | HV | 3rd Party Action | 3rd Party Impact | UGOH | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Panel 19 "the Gorokin" feeder tripped, reclosed and locked out on IOC, Earth Fault, Fault CHeck, reclose timing delay and lockout relays, EFI Tx2 Earth Fault check EFI's: S1809 S14816 Pole inspector damaged cable at UGOH to S14816 Sw B Wallarah Rita See 1268603,4,5,6,7 exclude 1267198,293 | May | 2015 | 2015Q4 | 2015 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | Unknown | Not Veg | 2015-05-15 | N | 41 | N | 7 | N | N | 1.1101 | 39.4971 | 52073.2446
[7 empty] | 13591 | 11629 | 1267237 | 2015-05-15 13:05 | 2015-05-15 15:45 | 160 | 11kV | 39415 | 288 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35800 Bankstown Panel 21 "Bankstown Aus No.2" fdr tripped/ Relays: Earth fault, EFI, Signals: Tx #12 Group Earth, CB#21 Open, AC Board AC Supply Fail, Zone AC Board CB trip, EFI's: S46109, S3094, S3095, S1108 Remarks: UG fault. Underground fault from "Sw.E" @ S1108 Wiggs Rd o "Sw B" @ S1091 Moxon Rd to "Sw.B" @ S49434 Tusmore Torrens | May | 2015 | 2015Q4 | 2015 | ZN35800:PA21 | ZN35800:PA21 | ZN35800/000021 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-05-15 | N | 136.8576 | N | 7 | N | N | 1.1101 | 39.4971 | 28803.3195
[7 empty] | 13830 | 13487 | 1267293 | 2015-05-15 14:49 | 2015-05-15 16:00 | 71 | 11kV | 4899 | 69 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT11340 Skyline Glendale B phase HDO blown 31.5 Amps DOp reports fuse was not hanging when he arrived on site. Fuse Fatigue See 1268615 exclude 1267293 | May | 2015 | 2015Q4 | 2015 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | OH | Not Veg | 2015-05-15 | N | 71 | N | 7 | N | N | 1.1101 | 39.4971 | 3580.0447
[7 empty] | 13200 | 8442 | 1267387 | 2015-05-15 20:45 | 2015-05-15 22:15 | 90 | 11kV | 90 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 152008 10 amp fuse Substation DOLF volts 243, amps 12 Excludes oms # 1267387 | May | 2015 | 2015Q4 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2015-05-15 | N | 90 | N | 7 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 12714 | 4273 | 1267377 | 2015-05-15 18:46 | 2015-05-15 23:00 | 254 | 11kV | 1196 | 14 | HV | Staff Operation | Utility Process Issue | Air Break Switch | Unplanned | No Weather Impact | N | LID 152009 1 fault operation Sensitive earth fault ABS 74629 FOUND CLOSED.PERFORMED OPEN & CLOSE RETURNING SYSTEM TO NORMAL. Includes OMS 1267952/54 Excludes OMS 1267377 | May | 2015 | 2015Q4 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2015-05-15 | N | 85.4286 | N | 7 | N | N | 1.1101 | 39.4971 | 874.0015
[7 empty] | 13574 | 11497 | 1267404 | 2015-05-16 01:53 | 2015-05-16 03:02 | 69 | 11kV | 138345 | 2005 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North - Pnl.3 tripped on : A & B phase IOC, EFI, Fault Check relay Field EFIs: S17040, S16927, S16944 Possum on 11kV UGOH below LB22355 No Damage to UGOH | May | 2015 | 2015Q4 | 2015 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2015-05-16 | N | 69 | N | 6 | N | N | 1.1101 | 39.4971 | 101098.4455
[7 empty] | 13218 | 8522 | 1267361 | 2015-05-15 17:01 | 2015-05-16 09:17 | 976 | 11kV | 976 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 152011 10 amp fuse Substation DOLF It appears a contractor identified this yesterday and requested an appointment for today to restore supply, hence the extended outage period. Exclides OMS # 1267361. | May | 2015 | 2015Q4 | 2015 | 814:82283 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2015-05-15 | N | 976 | N | 7 | N | N | 1.1101 | 39.4971 | 713.232
[7 empty] | 13424 | 10366 | 1267442 | 2015-05-16 09:09 | 2015-05-16 11:48 | 159 | 11kV | 194466 | 1234 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S.1610 Homebush Bay Panel 11 "RAS Showring Nth, Aux No.1" fdr tripped Relays - Earth fault, EFI Signals - 11kv trip EFI's - all to and including S.4251 Remarks: UG fault. 11kv feeder fault from S.4251 Melrose Abbot Sw/B to S.40 Rochester St. Sw/C | May | 2015 | 2015Q4 | 2015 | ZN1610:PA11 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | UG | Not Veg | 2015-05-16 | N | 157.59 | N | 6 | N | N | 1.1101 | 39.4971 | 142110.017
[7 empty] | 14421 | 18081 | 1267436 | 2015-05-16 06:32 | 2015-05-16 15:40 | 548 | 11kV | 33464 | 82 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 152012 tree on OHM in Euwylong Cl, Medowie Includes OMS 1267790/91 Excludes OMS 1267411/36/79 | May | 2015 | 2015Q4 | 2015 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Veg | 2015-05-16 | N | 408.0976 | N | 6 | N | N | 1.1101 | 39.4971 | 24454.5042
[7 empty] | 14537 | 19002 | 1267583 | 2015-05-16 23:32 | 2015-05-17 01:05 | 93 | 11kV | 4185 | 45 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn13000 Lake Munmorah section of Pa7 PT12233 Kullaroo Cudgee 11kv HDO operated C phase 20 Amp ABB Replaced HDO, supply restored. Excludes OMS 1267583 | May | 2015 | 2015Q4 | 2015 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2015-05-16 | N | 93 | N | 6 | N | N | 1.1101 | 39.4971 | 3058.2746
[7 empty] | 13570 | 11466 | 1267574 | 2015-05-16 21:14 | 2015-05-17 08:02 | 648 | 11kV | 87451 | 176 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152016 2 fault operations Earth fault Cause was 11kV on the ground adjacent to sub 54002. Includes OMS 1267849/51/52/53/54 Excludes OMS 1267574 | May | 2015 | 2015Q4 | 2015 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2015-05-16 | N | 496.8807 | N | 6 | N | N | 1.1101 | 39.4971 | 63906.6114
[7 empty] | 13198 | 8438 | 1267593 | 2015-05-17 06:36 | 2015-05-17 08:20 | 104 | 11kV | 104 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 152017 10 amp fuse Substation DOLF The Opertor said he has replaced this fuse a few times and it might be prudent for Muswellbrok Depot to further investigate the cause. Excludes OMS # 1267593 | May | 2015 | 2015Q4 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-05-17 | N | 104 | N | 2 | N | N | 1.1101 | 39.4971 | 76.0001
[7 empty] | 12317 | 603 | 1267554 | 2015-05-16 18:40 | 2015-05-17 09:25 | 885 | 11kV | 184771 | 530 | HV | Animal Possum | Animal | UGOH | Unplanned | Rain Light | N | LID 152013 4 fault operations Sensitive earth fault, Earth fault possum on sub 25075 blown UGOH at pole JU-63095 Includes OMS 1267826 Excludes OMS 1267554/55/56 | May | 2015 | 2015Q4 | 2015 | 256:80635 | 256:80635 | ZN00256/080635 | NEWCASTLE | OH | Not Veg | 2015-05-16 | N | 348.6245 | N | 6 | N | N | 1.1101 | 39.4971 | 135025.197
[7 empty] | 14620 | 19892 | 1267662 | 2015-05-17 15:09 | 2015-05-17 16:18 | 69 | 11kV | 79994 | 1246 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Zn12620 Noraville Pa8 "Manda Av" tripped on Relays: OC & EF Signals: 11kv trip Feeder Surge Arrestors defective between S18799 Boomerang Budgewoi and LB63770 tee PT11951 Natuna Scenic See 1268625,6,7 exclude 1268662,3,5 | May | 2015 | 2015Q4 | 2015 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2015-05-17 | N | 64.2006 | N | 2 | N | N | 1.1101 | 39.4971 | 58457.2558
[7 empty] | 12257 | 26 | 1267787 | 2015-05-18 08:55 | 2015-05-18 10:15 | 80 | 11kV | 720 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | B and C Phase 63A HDO's Blown F1835 Caravan Plassey Cause: Feeder Patrolled and nothing found. See OMS 1268768 1267787 1267795 | May | 2015 | 2015Q4 | 2015 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Veg | 2015-05-18 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 13303 | 9170 | 1268024 | 2015-05-18 13:06 | 2015-05-18 14:00 | 54 | 11kV | 54 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | LID 152033 31 amp fuse Substation DOLF Fuse fatigued. Volts = 250. Amps = 8,2,0. Excludes OMS 1268024. | May | 2015 | 2015Q4 | 2015 | 235:2121 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2015-05-18 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 39.4616
[7 empty] | 12624 | 3434 | 1267973 | 2015-05-18 11:43 | 2015-05-18 16:05 | 262 | 11kV | 4192 | 16 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | No 1 Transfomrer at S6345 Ernest Park Section of Panel 31 See OMS 1268831 1267973 1267986 1267974/975/979/980/074/079 | May | 2015 | 2015Q4 | 2015 | ZN2473:PA31 | ZN35400:PA81 | ZN35400/000081 | NORTH SYDNEY | UG | Not Veg | 2015-05-18 | N | 262 | N | 4 | N | N | 1.1101 | 39.4971 | 3063.39
[7 empty] | 13126 | 7807 | 1268235 | 2015-05-18 21:17 | 2015-05-18 22:55 | 97.5 | 11kV | 74273 | 850 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 9900 Menai - Pnl 13 - Trip/reclose/trip, Earth Fault, EFI, Timing, Lockout. 11kV Underground cable fault from S 9254 to S 9817 to S 9667. ME: 1268300. GIS: 1268239. Withdrawn: 1268235. | May | 2015 | 2015Q4 | 2015 | ZN9900:PA13 | ZN9900:PA13 | ZN09900/000013 | SUTHERLAND | UG | Not Veg | 2015-05-18 | N | 87.38 | N | 4 | N | N | 1.1101 | 39.4971 | 54276.5177
[7 empty] | 13423 | 10365 | 1268492 | 2015-05-19 13:20 | 2015-05-19 15:20 | 120 | 11kV | 109420 | 912 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn1610 Homebush Bay 11kv Panel #2 labelled "S.7057 Bennelong 2SM" tripped on: Relays: A and C phase OC, Tx GE, Signals, 11kv trip Field EF: Sub 7075 Remarks: UG fault. Section of 11kv feeder from Sub 7075 Bennalong 2SM to Sub 63790 Hill park #1 tee to Sub 3281 Lumber Services | May | 2015 | 2015Q4 | 2015 | ZN1610:PA2 | ZN1610:PA22 | ZN01610/000022 | PARRAMATTA | UG | Not Veg | 2015-05-19 | N | 119.9781 | N | 2 | N | N | 1.1101 | 39.4971 | 79960.9087
[7 empty] | 12290 | 337 | 1268245 | 2015-05-19 06:09 | 2015-05-19 21:30 | 920.9667 | 11kV | 920.9667 | 1 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | @Zn1290 Leightonfield exiting Panel #17 S.736 Taubmans RMCB tripped on low gas Remarks: Low SF6 Gas in RMCB @ S736 Taubmans. RMCB requires replacement. Refer DMA CC1: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" | May | 2015 | 2015Q4 | 2015 |  |  |  | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2015-05-19 | N | 920.9667 | N | 2 | N | N | 1.1101 | 39.4971 | 673.0153
[7 empty] | 13680 | 12372 | 1268723 | 2015-05-20 08:50 | 2015-05-20 09:07 | 17 | 11kV | 340 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Panel 22 AB43330 opened for safety to remove tree ABNORMAL: AB61929 closed, AB40338 opened Tree branch outside 400 Avoca Drive See 1269481 exclude 1268710,23 | May | 2015 | 2015Q4 | 2015 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2015-05-20 | N | 17 | N | 4 | N | N | 1.1101 | 39.4971 | 248.462
[7 empty] | 12396 | 1392 | 1269016 | 2015-05-20 14:55 | 2015-05-20 16:00 | 65 | 11kV | 455 | 7 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 152057 interrupt to repair wire off pin at pole CK-70018 near sub 72772 (B Webber) | May | 2015 | 2015Q4 | 2015 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2015-05-20 | N | 65 | N | 4 | N | N | 1.1101 | 39.4971 | 332.5006
[7 empty] | 13670 | 12280 | 1269101 | 2015-05-20 21:30 | 2015-05-21 00:15 | 165 | 11kV | 33000 | 200 | HV | Equipment Failed in Service | Equipment Failure | Pillar | Unplanned | No Weather Impact | N | LID 152961 No protection Ops. Section isolated - pole fire SI-90865, also damage at SI-90867 Opened taps at poles SI-90865 & SI-90867 Excluded OMS 1269101. | May | 2015 | 2015Q4 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | UG | Not Veg | 2015-05-20 | N | 165 | N | 4 | N | N | 1.1101 | 39.4971 | 24115.4267
[7 empty] | 13616 | 11843 | 1269144 | 2015-05-21 03:41 | 2015-05-21 05:51 | 130 | 11kV | 6328 | 56 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12650 West Gsoford Ex Panel 1 "Dog Trap rd" RE44604 Dog trap Rd tripped on Overucrrent and locked out Cause not ascertained. DOp patrolled fdr and found no cause See 1269698,9 exclude 1269144 | May | 2015 | 2015Q4 | 2015 | ZN12630:PA5 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2015-05-21 | N | 113 | N | 4 | N | N | 1.1101 | 39.4971 | 4624.3158
[7 empty] | 13335 | 9618 | 1269159 | 2015-05-21 07:07 | 2015-05-21 09:50 | 163 | 11kV | 2771 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152072 C phase DOLF :20 Amp Excluded OMS 1269159 | May | 2015 | 2015Q4 | 2015 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2015-05-21 | N | 163 | N | 4 | N | N | 1.1101 | 39.4971 | 2024.9651
[7 empty] | 13372 | 9871 | 1269149 | 2015-05-20 21:42 | 2015-05-21 12:20 | 878 | 11kV | 878 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of pa4 11kv USL44228 to LB44229 tee to PT12319. Interrupted for safety. Tree branch on 11kv OH mains on tee off to PT12319 Switching tag left on LB44229 Excludes OMS 1269149 | May | 2015 | 2015Q4 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2015-05-20 | N | 878 | N | 4 | N | N | 1.1101 | 39.4971 | 641.6165
[7 empty] | 12323 | 669 | 1269508 | 2015-05-21 16:25 | 2015-05-21 18:15 | 110.25 | 11kV | 330.75 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 152080 A phase DOLF : 10 Amp | May | 2015 | 2015Q4 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-05-21 | N | 110.25 | N | 4 | N | N | 1.1101 | 39.4971 | 241.7023
[7 empty] | 13542 | 11225 | 1269516 | 2015-05-21 21:30 | 2015-05-21 23:31 | 121 | 11kV | 121 | 1 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 152081 No protection operations. Fdr isolated to replace xarm SW-30625. Excluded OMS 1269516. | May | 2015 | 2015Q4 | 2015 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2015-05-21 | N | 121 | N | 4 | N | N | 1.1101 | 39.4971 | 88.4232
[7 empty] | 13256 | 8801 | 1269591 | 2015-05-22 07:31 | 2015-05-22 12:03 | 272 | 11kV | 391963 | 1671 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S965 Pennant Hills Panel 4 tripped on C phase timed O/C , Timing Relay and Lockout Cause: SW/A at S8401 Closed, AB2270 Open and Defective Branch Removed from 11kV OH Near PT2103 LB62157 is closed With CP3280 Open 1274470 1274472 1274475 1269591 1269593 1261269750 1269594 1269747 1269478 | May | 2015 | 2015Q4 | 2015 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | OH | Veg | 2015-05-22 | N | 234.5679 | N | 11 | N | N | 1.1101 | 39.4971 | 286434.9994
[7 empty] | 14389 | 17848 | 1269920 | 2015-05-22 13:36 | 2015-05-22 16:00 | 144 | 11kV | 59804 | 419 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Ex Narrabeen Zn Pnl.2L - REC 20112 Kalang Rd - Tripped and locked out Weather related - no cause found. Strong wind in the area see 1270585 1270586 | May | 2015 | 2015Q4 | 2015 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2015-05-22 | N | 142.7303 | N | 11 | N | N | 1.1101 | 39.4971 | 43702.9993
[7 empty] | 13369 | 9854 | 1269753 | 2015-05-22 11:03 | 2015-05-22 16:10 | 307 | 11kV | 307 | 1 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At PT2102 Galston Arcadia footpath side 16A HDO fuse operated. Possum Caused Flash Over on Roadside HDO Cause: animals/Birds See OMS1269834 1269753 | May | 2015 | 2015Q4 | 2015 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2015-05-22 | N | 307 | N | 11 | N | N | 1.1101 | 39.4971 | 224.3465
[7 empty] | 12580 | 3093 | 1269779 | 2015-05-22 11:26 | 2015-05-22 16:45 | 319 | 11kV | 118512 | 1047 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S35500 Top Ryde Panel 22 Feeder tripped and reclosed on Signals: 11kV trip Relays IOC A and B phase 50T AB Lockout Cause: Tree brought down HV conductors at 252 Quarry Rd Ryde. See OMS 1273513 1273514 1269922 1269783 1269787 | May | 2015 | 2015Q4 | 2015 | ZN35500:PA22 | ZN35500:PA22 | ZN35500/000022 | RYDE | OH | Veg | 2015-05-22 | N | 113.192 | N | 11 | N | N | 1.1101 | 39.4971 | 86605.0741
[7 empty] | 14403 | 17966 | 1269671 | 2015-05-22 09:33 | 2015-05-22 16:53 | 440 | 11kV | 188330 | 1209 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 152096 & 152097 Termination pulled away at ABS 9176 sub 15676 & 55148 isolated for repairs at 9176 | May | 2015 | 2015Q4 | 2015 | 220:8691 | 220:8691 | ZN00220/008691 | LAKE MACQUARIE | OH | Not Veg | 2015-05-22 | N | 155.7734 | N | 11 | N | N | 1.1101 | 39.4971 | 137626.0092
[7 empty] | 13130 | 7835 | 1269868 | 2015-05-22 12:40 | 2015-05-22 16:53 | 253 | 11kV | 17457 | 69 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152097 Overhead Mains Conductor. sub 15676 & 55148 isolated for repairs at 9176 See also LID 152096 and OMS 1270621 | May | 2015 | 2015Q4 | 2015 | 220:8687 | 220:8687 | ZN00220/008687 | LAKE MACQUARIE | OH | Not Veg | 2015-05-22 | N | 253 | N | 11 | N | N | 1.1101 | 39.4971 | 12757.0607
[7 empty] | 14030 | 15290 | 1270044 | 2015-05-22 16:01 | 2015-05-22 17:48 | 107 | 11kV | 21448 | 368 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | LID 152099 no targets at sub for 11 kv fdr 81240 targets reported from dnms Excluded OMS 1270044 | May | 2015 | 2015Q4 | 2015 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2015-05-22 | N | 58.2826 | N | 11 | N | N | 1.1101 | 39.4971 | 15673.5658
[7 empty] | 14159 | 16224 | 1270079 | 2015-05-22 16:46 | 2015-05-22 18:01 | 75 | 11kV | 82200 | 1096 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 152098 2 fault operations B & C phase Protection Overcurrent Excluded OMS 1270079 B-C O/C 5.6kA | May | 2015 | 2015Q4 | 2015 | 213:33775 | 213:33775 | ZN00213/033775 | NEWCASTLE | OH | Veg | 2015-05-22 | N | 75 | N | 11 | N | N | 1.1101 | 39.4971 | 60069.3355
[7 empty] | 13983 | 14798 | 1269825 | 2015-05-22 12:09 | 2015-05-22 21:20 | 551 | 11kV | 20717 | 319 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | Zn12630 Peats Ridge Pa4 "kulnura" fdr has been opend for safety Truck hit pole near PT11396 See 1272329 exclude 1269825 | May | 2015 | 2015Q4 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2015-05-22 | N | 64.9436 | N | 11 | N | N | 1.1101 | 39.4971 | 15139.3726
[7 empty] | 13920 | 14292 | 1270763 | 2015-05-23 11:30 | 2015-05-23 12:35 | 65 | 11kV | 65 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 152109 SW3473 control box found rusted through. Dop suggests water ingress may have caused switch operation. | May | 2015 | 2015Q4 | 2015 |  |  |  | LAKE MACQUARIE | OH | Veg | 2015-05-23 | N | 65 | N | 3 | N | N | 1.1101 | 39.4971 | 47.5001
[7 empty] | 12830 | 5320 | 1270192 | 2015-05-22 22:16 | 2015-05-23 13:00 | 884 | 11kV | 7956 | 9 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex Zn12620 Noraville section of Pa8 "Manoa av' PT14655 Macleay Kalele 1.6 31.5Amp centre phase fuse blown 11kv LK40245 open. PT11787 PT14655 PT11879 interrupted 1040 for reapirs to PT14655 tx bushings See 1272341 exclude 1270192,1270305 | May | 2015 | 2015Q4 | 2015 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2015-05-22 | N | 884 | N | 11 | N | N | 1.1101 | 39.4971 | 5814.0101
[7 empty] | 12296 | 410 | 1270231 | 2015-05-23 08:00 | 2015-05-23 13:30 | 329.9 | 11kV | 38158.4667 | 418 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | LID 152108 1 fault operation mains down between subs 1233 & sub 52842 tocal rd section isolated for repair | May | 2015 | 2015Q4 | 2015 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2015-05-23 | N | 91.2882 | N | 3 | N | N | 1.1101 | 39.4971 | 27885.082
[7 empty] | 14128 | 16060 | 1270075 | 2015-05-22 16:45 | 2015-05-23 14:20 | 1295 | 11kV | 218880 | 1863 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | LID 152102 Trees blown onto mains HV reported down Prot. O/C & E/F BCn Excluded OMS 1270075 | May | 2015 | 2015Q4 | 2015 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Veg | 2015-05-22 | N | 117.4879 | N | 11 | N | N | 1.1101 | 39.4971 | 159951.0481
[7 empty] | 14474 | 18513 | 1270440 | 2015-05-24 00:17 | 2015-05-24 04:21 | 244 | 11kV | 54900 | 225 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 152113 3 fault operations 3 phase Overcurrent truck hit pole LV reported down | May | 2015 | 2015Q4 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2015-05-24 | N | 244 | N | 3 | N | N | 1.1101 | 39.4971 | 40119.3007
[7 empty] | 12995 | 6788 | 1270426 | 2015-05-23 22:17 | 2015-05-24 05:35 | 438 | 11kV | 45443 | 418 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 152111 tree brought mains down at pole iq-41141. Possible protection malgrade email sent to L Archer/JD dq | May | 2015 | 2015Q4 | 2015 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2015-05-23 | N | 108.7153 | N | 3 | N | N | 1.1101 | 39.4971 | 33208.4041
[7 empty] | 13252 | 8777 | 1270451 | 2015-05-24 07:51 | 2015-05-24 12:40 | 289 | 11kV | 3085 | 25 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn2466 Flemington 11kv VCB panel 19 "S2306" feeder tripped on - Relays - B phase O/C, F check, EFI Field EFI's: S7306, S2898 @S986 Egg Board Sw/B tripped on T/lay Remarks: UG fault. 11kv front line feeder fault from ZN2466 flemington to S7306 Carter hill no.2 | May | 2015 | 2015Q4 | 2015 | ZN2466:PA19 | ZN2466:PA19 | ZN02466/000019 | CUMBERLAND | UG | Not Veg | 2015-05-24 | N | 123.4 | N | 3 | N | N | 1.1101 | 39.4971 | 2254.427
[7 empty] | 14183 | 16369 | 1271083 | 2015-05-25 22:50 | 2015-05-26 00:04 | 74 | 11kV | 3996 | 54 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 152128 3 fault operations bat removed at pole BG-60114 | May | 2015 | 2015Q4 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2015-05-25 | N | 74 | N | 1 | N | N | 1.1101 | 39.4971 | 2920.1589
[7 empty] | 13954 | 14594 | 1271424 | 2015-05-26 15:40 | 2015-05-26 17:45 | 125 | 11kV | 750 | 6 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 152142 Isolated to repair defective crossarm on pole DN-20216 | May | 2015 | 2015Q4 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2015-05-26 | N | 125 | N | 2 | N | N | 1.1101 | 39.4971 | 548.0779
[7 empty] | 14104 | 15809 | 1271520 | 2015-05-26 22:17 | 2015-05-27 02:00 | 222.6667 | 11kV | 32490.5 | 146 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S4241 Marshall Pacific HV centre phase fuse operated Section of 11kV feeder Panel No 9 ex S1673 Turramurra Tripped Cause: Truck hit Telco Mains sending into OH LV. Appears LV fuses failed to Grade See OMS 1271518 1271517 1271520 | May | 2015 | 2015Q4 | 2015 | ZN1673:PA9 | ZN1673:PA9 | ZN01673/000009 | KU-RING-GAI | OH | Not Veg | 2015-05-26 | N | 222.5377 | N | 2 | N | N | 1.1101 | 39.4971 | 23743.0991
[7 empty] | 12289 | 331 | 1271601 | 2015-05-27 08:36 | 2015-05-27 09:45 | 69 | 11kV | 11571 | 210 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | LID 152149 3 phase Overcurrent, Earth fault RMI Failed Excluded OMS 1271601; 1271602 | May | 2015 | 2015Q4 | 2015 | 523:33500 | 523:33500 | ZN00523/033500 | SINGLETON | Unknown | Not Veg | 2015-05-27 | N | 55.1 | N | 4 | N | N | 1.1101 | 39.4971 | 8455.7455
[7 empty] | 14376 | 17733 | 1271832 | 2015-05-27 13:50 | 2015-05-27 15:14 | 84 | 11kV | 51240 | 610 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12640 Umina Pa8 11kv bnd burnt at AB41033 11kv centre phase (load side) bond burnt at AB41033 See 1272513 exclude 1271832,42 | May | 2015 | 2015Q4 | 2015 | ZN12640:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2015-05-27 | N | 84 | N | 4 | N | N | 1.1101 | 39.4971 | 37444.6807
[7 empty] | 13912 | 14215 | 1271989 | 2015-05-27 23:00 | 2015-05-28 01:00 | 120 | 11kV | 6480 | 54 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152159 4 fault operations bat removed at pole DG-60131 see report # 152160 | May | 2015 | 2015Q4 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2015-05-27 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 4735.3929
[7 empty] | 13246 | 8706 | 1270539 | 2015-05-24 18:24 | 2015-05-28 04:23 | 4919.2833 | 11kV | 1753.45 | 16 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | At Zn2473 North Sydney: Zone Earth, TX4 Group Earth with Pa31 EFI Field EFI;sS5995 S5460 S6345 Cause; Transformer or RMI Fuse Switch Failure. DOp heard arcing/grugling noise when SW/C closed on No2 RMI Both No1 RMI and NO2 have very black oil See OMS 1272324 1270539 1270542 1270543 | May | 2015 | 2015Q4 | 2015 | ZN2473:PA31 | ZN35400:PA81 | ZN35400/000081 | NORTH SYDNEY | UG | Not Veg | 2015-05-24 | N | 109.5906 | N | 3 | N | N | 1.1101 | 39.4971 | 1281.3695
[7 empty] | 13085 | 7506 | 1271995 | 2015-05-28 04:06 | 2015-05-28 06:58 | 172 | 11kV | 114625 | 861 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12600 Lisarow Pa13 "Brush rd" tripped on Pa13 Relays 51ABC, rec time delay, lockout, EFI , SEF Signals: 11kv trip EFI's: Brush Rd west of PT12251 DOp found EFI down at Brush rd west of PT12251. Patrolled and could not see any visual fault. Possible intermittant fault in section of 11kv ABC Cause not ascertained See 1272551,2,3,4,5,6,7 exclude 1271995 | May | 2015 | 2015Q4 | 2015 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2015-05-28 | N | 133.1301 | N | 4 | N | N | 1.1101 | 39.4971 | 83764.5691
[7 empty] | 13924 | 14394 | 1272124 | 2015-05-28 09:56 | 2015-05-28 10:51 | 55 | 11kV | 123090 | 2238 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor ABC | Unplanned | No Weather Impact | N | LID 152169 1 fault operation A & B phase Overcurrent TARGETS = 51AB, Tree on 11kV fell by tree trimer see OMS report 1272136. Fdr abnormally switched see SI 6304. Excluded OMS 1272136, 1272124. | May | 2015 | 2015Q4 | 2015 | 233:82815 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2015-05-28 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 89950.5415
[7 empty] | 12492 | 2186 | 1271894 | 2015-05-27 15:28 | 2015-05-28 11:25 | 1197 | 11kV | 1197 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | replaced 11kv arrestor Excludes OMS 1271894 | May | 2015 | 2015Q4 | 2015 | 801:74117 | 801:74117 | ZN00801/074117 | MUSWELLBROOK | OH | Not Veg | 2015-05-27 | N | 1197 | N | 4 | N | N | 1.1101 | 39.4971 | 874.7323
[7 empty] | 13773 | 13094 | 1272386 | 2015-05-28 19:37 | 2015-05-28 21:01 | 84 | 11kV | 61770 | 739 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S262 Marrickville Zn P39 the Meeks Central fdr tripped on Earth fault and fault check relays, EFI EFI at S35264 EFI at S35035 meeks Central defective Remarks: UG fault. S35264 Mees Central No2 to S2050 Frampton Ave | May | 2015 | 2015Q4 | 2015 | ZN262:PA39 | ZN262:PA39 | ZN00262/000039 | INNER WEST | UG | Not Veg | 2015-05-28 | N | 83.5859 | N | 4 | N | N | 1.1101 | 39.4971 | 45139.6941
[7 empty] | 12815 | 5136 | 1272392 | 2015-05-28 20:41 | 2015-05-28 23:12 | 151 | 11kV | 8154 | 54 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 152181 2 fault operations B & C phases Overcurrent Bat | May | 2015 | 2015Q4 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2015-05-28 | N | 151 | N | 4 | N | N | 1.1101 | 39.4971 | 5958.7027
[7 empty] | 13874 | 13892 | 1272433 | 2015-05-29 08:13 | 2015-05-29 15:00 | 407 | 11kV | 24827 | 61 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 152185 Earth fault Staff could not find the cause of the outage but found the eye bolt had fallen from 11kV cross arm at pole EM-40089 and it required immediate repairs. | May | 2015 | 2015Q4 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2015-05-29 | N | 407 | N | 2 | N | N | 1.1101 | 39.4971 | 18142.8393
[7 empty] | 13652 | 12155 | 1272700 | 2015-05-29 16:30 | 2015-05-29 17:30 | 60 | 11kV | 3360 | 56 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of Pa10 "Somersby East" fdr 11kv centre phase bond off feeder on line side of AB42044 See 1273127 GIS 1273133 exclude 1272700 | May | 2015 | 2015Q4 | 2015 | ZN14143:PA10 | ZN14143:PA10 | ZN14143/000010 | CENTRAL COAST | OH | Not Veg | 2015-05-29 | N | 60 | N | 2 | N | N | 1.1101 | 39.4971 | 2455.3889
[7 empty] | 13702 | 12554 | 1272775 | 2015-05-30 07:36 | 2015-05-30 08:35 | 59 | 11kV | 59 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152203 DOLF : 10 Amp Amps = 105 Volts = 235 Excluded oms 1272775 was wrong customer | May | 2015 | 2015Q4 | 2015 | 238:34137 | 238:34137 | ZN00238/034137 | MAITLAND | OH | Veg | 2015-05-30 | N | 59 | N | 1 | N | N | 1.1101 | 39.4971 | 43.1155
[7 empty] | 12369 | 1064 | 1272893 | 2015-05-31 03:00 | 2015-05-31 03:35 | 35 | 11kV | 38430 | 1098 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 3 Has tripped Signals: 11kV Trip, UV TX1, Zone Earth and Tx1 Group Earth Relays: A phase IOC, A phase Timed, EFI At PT1096 Gunbalanua St a Pair of Possums have contacted 11kV See OMS 1272893 1272895 1272896 | May | 2015 | 2015Q4 | 2015 | ZN965:PA3 | ZN965:PA3 | ZN00965/000003 | HORNSBY | OH | Veg | 2015-05-31 | N | 35 | N | 5 | N | N | 1.1101 | 39.4971 | 28083.5105
[7 empty] | 12398 | 1396 | 1272897 | 2015-05-31 03:50 | 2015-05-31 10:05 | 375 | 11kV | 93400 | 686 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 152207 2 fault operations 3 phase Overcurrent Sw 48705. Tree into mains NR-60518. HV into LV. Excluded OMS 1272897. | May | 2015 | 2015Q4 | 2015 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2015-05-31 | N | 136.1516 | N | 5 | N | N | 1.1101 | 39.4971 | 68253.9652
[7 empty] | 12953 | 6476 | 1272925 | 2015-05-31 08:43 | 2015-05-31 12:35 | 232 | 11kV | 3206 | 14 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 152208 Overcurrent Sw 74622 open L/O 2 x wire off pin at pole near sub 72473 couldn't enter report properly - indexing issue Excluded OMS 1272925 | May | 2015 | 2015Q4 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2015-05-31 | N | 229 | N | 5 | N | N | 1.1101 | 39.4971 | 2342.8502
[7 empty] | 12358 | 1005 | 1272929 | 2015-05-31 09:05 | 2015-05-31 12:55 | 230 | 11kV | 690 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 152209 LLC off at pole BI-60350 | May | 2015 | 2015Q4 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2015-05-31 | N | 230 | N | 5 | N | N | 1.1101 | 39.4971 | 504.2316
[7 empty] | 13235 | 8611 | 1273041 | 2015-05-31 21:23 | 2015-05-31 23:20 | 117 | 11kV | 585 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12630 PEats Ridge section of Pa3 PT11814 Bunyah Peats Ridge 16Amp footpath fuse operated See 1273163 exclude 1273041 | May | 2015 | 2015Q4 | 2015 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2015-05-31 | N | 117 | N | 5 | N | N | 1.1101 | 39.4971 | 427.5007
[7 empty] | 14408 | 17980 | 1273059 | 2015-06-01 05:16 | 2015-06-01 06:29 | 73 | 11kV | 462 | 7 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S874 Concord, 11kv Panel 16 "Pomeroy Underwood No.1 etc" tripped: Relays: Earth Fault, EFI Signals: 11kv trp, ZE, Tx3 GE Field EFI's: S35176 Remarks: UG fault. 11kv feeder at/from S.35176 Pomeroy Underwood No.1 to S.8321 Underwood Bellona No.1 to S.55 Underwood Rd. Isolated & Earthed | June | 2015 | 2015Q4 | 2015 | ZN874:PA16 | ZN874:PA16 | ZN00874/000016 | STRATHFIELD | UG | Not Veg | 2015-06-01 | N | 66 | N | 5 | N | N | 1.1101 | 39.4971 | 337.616
[7 empty] | 12922 | 6130 | 1273053 | 2015-06-01 01:13 | 2015-06-01 07:10 | 357 | 11kV | 134017 | 955 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12690 Berkely Vale Pa6 "Krone Enterprise" tripped and reclosed on Relays: B & C phase overcurrent Signals: 11kv trip, Zone Earth, Group Earth No13, EFI, Reclose, Lockout EFI's: S18124 HV into LV. HV alive on load side of AB41187 see 1273789,90,1 exclude 1273053,8 | June | 2015 | 2015Q4 | 2015 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2015-06-01 | N | 140.3319 | N | 5 | N | N | 1.1101 | 39.4971 | 97935.6708
[7 empty] | 14465 | 18454 | 1273180 | 2015-06-01 10:02 | 2015-06-01 15:35 | 333 | 11kV | 20062 | 101 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa1 "Grants Rd" fdr RE44995 Kulnura tripped reclosed tripped and locked out Tree brought down 1 phase of 11kv onto 415v mains outside 1266 George Downs Drive. See 1273804,7,8 exclude 1273180,96 | June | 2015 | 2015Q4 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2015-06-01 | N | 198.6337 | N | 5 | N | N | 1.1101 | 39.4971 | 14660.7179
[7 empty] | 13107 | 7702 | 1273816 | 2015-06-01 18:13 | 2015-06-01 18:17 | 4 | 11kV | 4884 | 1221 | HV | Staff Operation | Utility Process Issue | Circuit Breaker | Unplanned | Cold <10C | N | Zn12610 Long Jetty Pa22 "Shelley beach" tripped on SEL AOp inadvertantly closed incorrect scada controlled LV61959 during switching for high current alarm | June | 2015 | 2015Q4 | 2015 | ZN12610:PA22 | ZN12610:PA22 | ZN12610/000022 | CENTRAL COAST | Unknown | Not Veg | 2015-06-01 | N | 4 | N | 5 | N | N | 1.1101 | 39.4971 | 3569.0831
[7 empty] | 14053 | 15438 | 1273815 | 2015-06-01 18:13 | 2015-06-01 18:18 | 5 | 11kV | 10415 | 2083 | HV | Staff Operation | Utility Process Issue | Enclosed Load Break Switch | Unplanned | Cold <10C | N | Zn12610 Pa13 "the entrance" tripped on SEL Area Operaor switching closed wrong scada controlled Load Break Switch during high current overload situation | June | 2015 | 2015Q4 | 2015 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2015-06-01 | N | 5 | N | 5 | N | N | 1.1101 | 39.4971 | 7610.9748
[7 empty] | 13401 | 10168 | 1273979 | 2015-06-02 15:41 | 2015-06-02 16:45 | 64 | 11kV | 6344 | 111 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S 8000 Macquarie Park Panel 7 Talavera Macquarie Tripped on Relays: EFI, Earth Fault, O/C and Fault Check. Signals: 11kV Trip and Tx1 Group Earth Cause: 11kV Cable Fault from S48451 to S48540 to S4283 to S7469 1276286 1276287 1273979 | June | 2015 | 2015Q4 | 2015 | ZN8000:PA7 | ZN8000:PA7 | ZN08000/000007 | RYDE | UG | Not Veg | 2015-06-02 | N | 57.1532 | N | 2 | N | N | 1.1101 | 39.4971 | 4636.0081
[7 empty] | 14004 | 14960 | 1274158 | 2015-06-02 22:13 | 2015-06-02 23:52 | 99 | 11kV | 354 | 4 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | Zn1788 Matraville -Pnl.26 tripped on: Earth Fault, EFI Field EFIs: S47353, S1176, S5382 Customer's installation fault. 11kV umbillical cord supplying crane did not retract and crane crushed cable. Customers switchgear did not operate. Maintenance required. Manager Mark Swavley 0421 613 174 see 1274215 1274216 | June | 2015 | 2015Q4 | 2015 | ZN1788:PA26 | ZN35700:PA8 | ZN35700/000008 | RANDWICK | Unknown | Not Veg | 2015-06-02 | N | 88.5 | N | 2 | N | N | 1.1101 | 39.4971 | 258.6928
[7 empty] | 12575 | 3053 | 1274169 | 2015-06-03 06:51 | 2015-06-03 10:10 | 199.4667 | 11kV | 2992 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 152239 C phase DOLF : 16 Amp Excluded OMS 1274169 | June | 2015 | 2015Q4 | 2015 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2015-06-03 | N | 199.4667 | N | 5 | N | N | 1.1101 | 39.4971 | 2186.4654
[7 empty] | 13251 | 8776 | 1274292 | 2015-06-03 09:59 | 2015-06-03 11:00 | 61 | 11kV | 61 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | 11kv/415V Tx @ S.7969 Derby Day No.3 - defective Ex Panel 23 'S.7566 Derby St East' feeder @ Zn.610 Homebush Bay Remarks: Transformer failure. 11kv/415v tx @ S7969 Derby Day No.3 - defective Volts ok when Tx is un-loaded. Volts fluctuating when Tx is on-load. LV//: Dist #3 400A fuses @ S.7566 Derby St East | June | 2015 | 2015Q4 | 2015 | ZN1610:PA23 | ZN1610:PA23 | ZN01610/000023 | PARRAMATTA | UG | Not Veg | 2015-06-03 | N | 61 | N | 5 | N | N | 1.1101 | 39.4971 | 44.577
[7 empty] | 12651 | 3759 | 1274244 | 2015-06-03 09:23 | 2015-06-03 18:05 | 522 | 11kV | 1566 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 152244 A phase DOLF : 31 Amp Faulty transformer SAO required. Excluded OMS 1274244 | June | 2015 | 2015Q4 | 2015 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2015-06-03 | N | 522 | N | 5 | N | N | 1.1101 | 39.4971 | 1144.3866
[7 empty] | 12805 | 5059 | 1274589 | 2015-06-03 18:28 | 2015-06-03 19:30 | 62 | 11kV | 6448 | 104 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn13000 Lake Munmorah section of Pa7 Operator interrupted section of feeder from AB43823 to AB43824 Abnormal: AB43824 open and defective with LB40172 closed SECTION OF 11KV FEEDER BETWEEN AB 43824 AND AB 43825 STOLEN COPPER THEFT See 1275407 exclude 1274589 | June | 2015 | 2015Q4 | 2015 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2015-06-03 | N | 62 | N | 5 | N | N | 1.1101 | 39.4971 | 4712.0082
[7 empty] | 14565 | 19187 | 1274599 | 2015-06-03 19:09 | 2015-06-03 20:19 | 70 | 11kV | 31316 | 500 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn711 Blackwattle Bay Pnl.15 tripped on: A phase O/C, E/F, EFI Field EFIs: NIL Abnormal: S7026 (Sw A) CLOSED with (Sw F) OPENED - Sw B Closed @ S7549 with Pnl.12 OPEN defective. Frontline feeder UG cable fault from Pnl 15 to S7527 (Sw A) to S7026 (Sw F) | June | 2015 | 2015Q4 | 2015 | ZN711:PA12 | ZN7481:PA6R | ZN07481/000006 | SYDNEY | UG | Not Veg | 2015-06-03 | N | 62.632 | N | 5 | N | N | 1.1101 | 39.4971 | 22884.8091
[7 empty] | 14151 | 16185 | 1274704 | 2015-06-04 08:26 | 2015-06-04 09:25 | 59 | 11kV | 118 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152257 Single phase DOLF : 10 Amp Excluded OMS 1274704 | June | 2015 | 2015Q4 | 2015 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2015-06-04 | N | 59 | N | 3 | N | N | 1.1101 | 39.4971 | 86.2309
[7 empty] | 13783 | 13177 | 1275072 | 2015-06-04 18:00 | 2015-06-04 20:27 | 147 | 11kV | 149796 | 1279 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly Pnl.18 tripped on: EFI, E/F, Fault Check Field EFIs: S3663, S3230 UG cable fault from S3230 (Sw B) to S2677 (Sw A) to S3439 (Sw A) see 1275271 1275272 1275273 | June | 2015 | 2015Q4 | 2015 | ZN2602:PA18 | ZN2602:PA30 | ZN02602/000030 | RANDWICK | UG | Not Veg | 2015-06-04 | N | 117.1196 | N | 3 | N | N | 1.1101 | 39.4971 | 109466.4986
[7 empty] | 12667 | 3883 | 1275115 | 2015-06-04 23:38 | 2015-06-05 01:02 | 84 | 11kV | 167399 | 2006 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn36300 Balgowlah Pa3 "Jackson White" tripped on 51N earth fault, EFI, 11kv trip Cause not sacertained. mains to patrol See 1275462,3 exclude 1275115 | June | 2015 | 2015Q4 | 2015 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Veg | 2015-06-04 | N | 83.4492 | N | 3 | N | N | 1.1101 | 39.4971 | 122330.2518
[7 empty] | 13244 | 8704 | 1275423 | 2015-04-21 07:41 | 2015-06-05 14:29 | 65208.25 | 11kV | 7079299 | 1264 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No LID report Compiled from emergency switching sheets and scada | April | 2015 | 2015Q4 | 2015 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2015-04-21 | Y | 5600.7112 | Y | 3 | N | Y | 1.1101 | 39.4971 | 5173342.9052
[7 empty] | 13544 | 11260 | 1275675 | 2015-06-06 14:11 | 2015-06-06 15:35 | 84 | 11kV | 84 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 152281 1 fault operation Earth fault Customer's installation | June | 2015 | 2015Q4 | 2015 |  |  |  | SINGLETON | Unknown | Not Veg | 2015-06-06 | N | 84 | N | 4 | N | N | 1.1101 | 39.4971 | 61.3847
[7 empty] | 12606 | 3259 | 1275749 | 2015-06-06 22:22 | 2015-06-06 23:23 | 61 | 11kV | 12332 | 208 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn8100 Green Square - Pnl.2 tripped on: A & B phase O/C, Earth Fault. Field EFIs: S3667, S5690, S3721 & S6798 UG cable fault between S6798 and S2804 see 1276216 1276218 GIS: 1276224 | June | 2015 | 2015Q4 | 2015 | ZN8100:PA2 | ZN8100:PA2 | ZN08100/000002 | SYDNEY | UG | Not Veg | 2015-06-06 | N | 59.2885 | N | 4 | N | N | 1.1101 | 39.4971 | 9011.8619
[7 empty] | 14341 | 17459 | 1275715 | 2015-06-06 19:25 | 2015-06-06 23:45 | 260 | 11kV | 301583 | 3527 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 40 Tripped on Overcurrent and EFI Cause: Switch B Closed at S8740 Shaftsbury Victoria and Panel 32 Open Cause: Bat Flew into HV at 1129 Victoria Rd West Ryde See OMS 1276422 1276426 1275730 1275715 1275721 1275728 | June | 2015 | 2015Q4 | 2015 | ZN4545:PA40 | ZN4545:PA40 | ZN04545/000040 | RYDE | OH | Not Veg | 2015-06-06 | N | 85.5069 | N | 4 | N | N | 1.1101 | 39.4971 | 220387.9612
[7 empty] | 12276 | 182 | 1275757 | 2015-06-07 | 2015-06-07 04:50 | 290 | 11kV | 15660 | 54 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152284 2 fault operations B & C phase Overcurrent Bats pole DG-60114 | June | 2015 | 2015Q4 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2015-06-07 | N | 290 | N | 3 | N | N | 1.1101 | 39.4971 | 11443.8661
[7 empty] | 14126 | 16036 | 1275753 | 2015-06-06 23:30 | 2015-06-07 07:22 | 472 | 11kV | 99356 | 907 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 152283 2 fault operations A phase Earth fault MVA pole JU-11153. HV into LV. Excluded OMS 1275753. | June | 2015 | 2015Q4 | 2015 | 210:8682 | 210:83465 | ZN00210/083465 | NEWCASTLE | OH | Not Veg | 2015-06-06 | N | 109.5436 | N | 4 | N | N | 1.1101 | 39.4971 | 72606.4343
[7 empty] | 14333 | 17423 | 1275792 | 2015-06-07 10:11 | 2015-06-07 11:30 | 79 | 11kV | 158 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152287 Single phase DOLF : 10 Amp D Meyers reports this sub keeps blowing DOLFS or Line DOLFS on a regular basis. The customer said the sub took a direct lightning strike and it is possible there is an internal fault. This probably needs further investigation Excluded OMS 1275792 | June | 2015 | 2015Q4 | 2015 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2015-06-07 | N | 79 | N | 3 | N | N | 1.1101 | 39.4971 | 115.4617
[7 empty] | 12929 | 6227 | 1275833 | 2015-06-07 16:16 | 2015-06-07 18:20 | 124 | 11kV | 7259 | 77 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35800 Bankstown Panel 4 'S7397' feeder has tripped Signals: 11kv trip, Relays: EF, EFI, FC EFI's: 7397, 8888, 8188, 36154, 4852, 1734 (no access) Remarks: UG fault. UG fault between sw/D @ Sub 4852 Gow Sebel No.1 and Sw/A @ Sub 1091 Moxon Rd | June | 2015 | 2015Q4 | 2015 | ZN35800:PA4 | ZN35800:PA4 | ZN35800/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-06-07 | N | 94.2727 | N | 3 | N | N | 1.1101 | 39.4971 | 5304.6631
[7 empty] | 12842 | 5454 | 1275884 | 2015-06-08 08:36 | 2015-06-08 16:30 | 474 | 11kV | 15508 | 70 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152289 4 fault operation Earth fault mains down pole GP-82906 near sub 52680 Fernhill Rd 4 trips. 2 Initial trips (Auto Reclose) then 2 other separate trips when re-energising. (No Auto Reclose). Mains down at GP-82917 tpo GP-82909. | June | 2015 | 2015Q4 | 2015 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2015-06-08 | N | 221.5429 | N | 4 | N | N | 1.1101 | 39.4971 | 11332.789
[7 empty] | 12820 | 5204 | 1275975 | 2015-06-08 15:22 | 2015-06-08 16:35 | 73 | 11kV | 16863 | 231 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152291 2 fault operations 3 phase branch on fdr near KR-90079 blown clear by auto re close | June | 2015 | 2015Q4 | 2015 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2015-06-08 | N | 73 | N | 4 | N | N | 1.1101 | 39.4971 | 12322.983
[7 empty] | 14602 | 19648 | 1275989 | 2015-06-08 16:54 | 2015-06-08 19:36 | 162 | 11kV | 4536 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 152292 3 phase sectionaliser Recloser had two trips. Sectionaliser cleared Fault. | June | 2015 | 2015Q4 | 2015 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2015-06-08 | N | 162 | N | 4 | N | N | 1.1101 | 39.4971 | 3314.775
[7 empty] | 14535 | 18985 | 1275997 | 2015-06-08 18:06 | 2015-06-08 19:52 | 106 | 11kV | 146096 | 1607 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN116 Leichhardt 11kv Panel #44 labelled "S.2156 & S.47860" tripped: Relays: Panel #44R B phase overcurrent, fault check, efi Signals: 11kv trip, Tx#3 Group earth, Zone earth, CB #44 open Field EFI's. Remarks: UG fault. Defective section of 11kv feeder from: "Sw.B" @ S.6088 Ainsworth Piper to "Sw.B" @ S.4615 O'Neill Cecily to "Sw.A" @ S.1435 Burt St to "Sw.A" @ S.8311 Cambridge Darling. | June | 2015 | 2015Q4 | 2015 | ZN116:PA44 | ZN116:PA31 | ZN00116/000031 | INNER WEST | UG | Not Veg | 2015-06-08 | N | 90.9123 | N | 4 | N | N | 1.1101 | 39.4971 | 106762.6477
[7 empty] | 13374 | 9927 | 1276040 | 2015-06-09 07:18 | 2015-06-09 07:56 | 38 | 11kV | 85690 | 2255 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca Pa33 IR50407 The Scenice Bounty tripped on overcurrent ABNORMAL: AB44523 closed, LB42288 open, LB40439 closed, AB43718 open Interruption caused during switching for D&R 361358. IR50407 tripped whilst placed in non tripping. TPE to investigate settings. See 1276835 exclude 1276040,8 | June | 2015 | 2015Q4 | 2015 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | Unknown | Not Veg | 2015-06-09 | N | 38 | N | 2 | N | N | 1.1101 | 39.4971 | 62619.7246
[7 empty] | 12799 | 5027 | 1276541 | 2015-06-09 23:30 | 2015-06-10 00:15 | 45 | 11kV | 89603 | 2171 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 152300 2 fault operations B & C phase Overcurrent Excluded OMS 1276541 | June | 2015 | 2015Q4 | 2015 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Veg | 2015-06-09 | N | 41.2727 | N | 2 | N | N | 1.1101 | 39.4971 | 65479.2296
[7 empty] | 14511 | 18796 | 1277091 | 2015-06-10 09:12 | 2015-06-10 09:56 | 44 | 11kV | 46684 | 1061 | HV | Staff Other | Utility Process Issue | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152307 1 fault operation 3 phase Earth fault Cause was due to a labelling error, in the field the location of Switch No's 29549 and 29550 did not match the system diagram. Excluded OMS # 1276619 , 1276669. | June | 2015 | 2015Q4 | 2015 | 503:48017 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Not Veg | 2015-06-10 | N | 44 | N | 5 | N | N | 1.1101 | 39.4971 | 34115.2903
[7 empty] | 14282 | 17101 | 1277092 | 2015-06-10 09:12 | 2015-06-10 10:03 | 51 | 11kV | 48042 | 942 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | LID 152307/2 Feeder was abnormally switched Sw 28405 closed and sw 37972 open at time of the interruption. This section was supplied from Sw 48017 at the time Sw 48017 opened. also refer to OMS 1277091 | June | 2015 | 2015Q4 | 2015 | 503:48017 | 532:83300 | ZN00532/083300 | MAITLAND | UG | Not Veg | 2015-06-10 | N | 51 | N | 5 | N | N | 1.1101 | 39.4971 | 35107.6766
[7 empty] | 12652 | 3770 | 1276972 | 2015-06-10 16:56 | 2015-06-10 17:48 | 52 | 11kV | 45286 | 1037 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | ZN 35900 Potts Hill - Pnl 23 - Instantaneous Earth Fault, EFI, Field EFIs. Underground feeder fault between S 35026 and S 2904. ME: 1277305. Rest Step: 1277306. Withdrawn: 1276972. | June | 2015 | 2015Q4 | 2015 | ZN35900:PA23 | ZN3472:PA19 | ZN03472/000019 | CUMBERLAND | UG | Not Veg | 2015-06-10 | N | 43.6702 | N | 5 | N | N | 1.1101 | 39.4971 | 33093.6731
[7 empty] | 14588 | 19469 | 1276985 | 2015-06-10 17:47 | 2015-06-10 18:38 | 51 | 11kV | 22245 | 453 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 9550 Gwawley Bay - Pnl 4L - Timed Earth Fault, EFI, FIeld EFI. UG fault between S 9831 and S 9456. ME: 1277008. Rest Step: 1277072. Withdrawn: 1276985. | June | 2015 | 2015Q4 | 2015 | ZN9550:PA4 | ZN9550:PA4 | ZN09550/000004 | SUTHERLAND | UG | Not Veg | 2015-06-10 | N | 49.106 | N | 5 | N | N | 1.1101 | 39.4971 | 16255.9899
[7 empty] | 13485 | 10833 | 1277688 | 2015-06-10 16:55 | 2015-06-10 19:13 | 138 | 11kV | 293244 | 2330 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S180 Mosman Panel 18 tripped on B phase Earth Fault. Sealing Contactor. EFI fault Check EFI's operated at S48587, S1930 S5591 S3578 and S4322 EFI's defective at S48689 S5977 NO EFI's at S7434 and S7435 PA42 Tripped on on Restoration of Pa18 - B phase Earth fault EFI and Fault Check. Cause: UG cable fault S48689 to S2922 See OMS 1277688 1277689 1277691 1277688 | June | 2015 | 2015Q4 | 2015 | ZN180:PA18 | ZN180:PA22 | ZN00180/000022 | NORTH SYDNEY | UG | Not Veg | 2015-06-10 | N | 125.8558 | N | 5 | N | N | 1.1101 | 39.4971 | 214294.066
[7 empty] | 12308 | 518 | 1277024 | 2015-06-11 00:07 | 2015-06-11 01:33 | 86 | 11kV | 88482 | 1289 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12580 Erina Zn 11kv VCB Pa16R "Baralong Rd" fdr tripped, reclosed, tripped and locked out Relays: BC phase IOC, EFI, reclose timing lockout EFI's: S14330 S18039 Signals: 11kv trip See 1277280,1 Exclude 1277024 | June | 2015 | 2015Q4 | 2015 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2015-06-11 | N | 68.6439 | N | 3 | N | N | 1.1101 | 39.4971 | 64660.0358
[7 empty] | 14464 | 18451 | 1277259 | 2015-06-11 13:12 | 2015-06-11 14:55 | 103 | 11kV | 87172 | 1034 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 41 Tripped on Relays: IOC Signals: Pa41 Trip TX3 Group Earth and Zone Earth Cause: Cable hit by concreter, Reitsman Construction Group See OMS 1277599 1277603 1277601 | June | 2015 | 2015Q4 | 2015 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | UG | Not Veg | 2015-06-11 | N | 84.3056 | N | 3 | N | N | 1.1101 | 39.4971 | 63702.7265
[7 empty] | 14287 | 17134 | 1277493 | 2015-06-11 16:15 | 2015-06-11 17:11 | 56 | 11kV | 168 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 152324 A phase 11kV main was off pin. NO OMS, NO PROTECTION OPERATED, LIDAR FOUND MAIN OFF PIN AT POLE 5I-50177, DEPOT STAFF ADVISED JOB URGENT. 1 | June | 2015 | 2015Q4 | 2015 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Not Veg | 2015-06-11 | N | 56 | N | 3 | N | N | 1.1101 | 39.4971 | 122.7694
[7 empty] | 12773 | 4780 | 1278612 | 2015-06-12 22:55 | 2015-06-13 00:10 | 75 | 11kV | 1650 | 22 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Insulated | Unplanned | No Weather Impact | N | Zn14144 Wamberal section of Pa10 "Wmaberal Auxilliary No.2" LB45095 opened to remove tree branch from 11kv OH Tree branch on OH mains near Clyde rd Holgate | June | 2015 | 2015Q4 | 2015 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2015-06-12 | N | 75 | N | 1 | N | N | 1.1101 | 39.4971 | 1205.7713
[7 empty] | 12404 | 1457 | 1277780 | 2015-06-13 09:11 | 2015-06-13 12:15 | 184 | 11kV | 552 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152345 Single phase DOLF : 10 Amp Excluded OMS 1277780 | June | 2015 | 2015Q4 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-06-13 | N | 184 | N | 2 | N | N | 1.1101 | 39.4971 | 403.3853
[7 empty] | 13822 | 13415 | 1277770 | 2015-06-13 08:33 | 2015-06-13 15:30 | 417 | 11kV | 834 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 152347 DOLF FUSE CARRIER HAD BURNT UP. Excluded OMS # 1277770 | June | 2015 | 2015Q4 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | LAKE MACQUARIE | OH | Not Veg | 2015-06-13 | N | 417 | N | 2 | N | N | 1.1101 | 39.4971 | 609.4626
[7 empty] | 12940 | 6320 | 1277924 | 2015-06-14 15:03 | 2015-06-14 15:42 | 39 | 11kV | 39819 | 1021 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14144 Wamberal Pa2 "Glen Eagles Fairway" fdr tripped, reclosed, tripped and locked out Relays: B phase IOC Signals: 11kv trip Tree branch on 11kv mains near PT18753 | June | 2015 | 2015Q4 | 2015 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2015-06-14 | N | 39 | N | 1 | N | N | 1.1101 | 39.4971 | 29098.5507
[7 empty] | 14348 | 17535 | 1278068 | 2015-06-15 09:51 | 2015-06-15 10:56 | 65 | 11kV | 55651 | 1439 | HV | Equipment Failed in Service | Equipment Failure | Pillar | Unplanned | No Weather Impact | N | LID 152368 2 fault operations A phase Overcurrent; Earth fault Krone switch failed in service "kiosk in front of 7 Kentmere has exploded" Sub 23424 held up by generator | June | 2015 | 2015Q4 | 2015 | 214:8670 | 214:8670 | ZN00214/008670 | LAKE MACQUARIE | UG | Not Veg | 2015-06-15 | N | 38.6734 | N | 3 | N | N | 1.1101 | 39.4971 | 40668.1094
[7 empty] | 12430 | 1651 | 1278197 | 2015-06-15 12:24 | 2015-06-15 14:00 | 96 | 11kV | 192 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 152370 A phase DOLF : 10 Amp Excluded OMS 1278197 | June | 2015 | 2015Q4 | 2015 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2015-06-15 | N | 96 | N | 3 | N | N | 1.1101 | 39.4971 | 140.3079
[7 empty] | 13812 | 13358 | 1278330 | 2015-06-15 15:46 | 2015-06-15 19:11 | 205 | 11kV | 1017 | 8 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 152371 1 fault operation A phase Earth fault Sw 74200 opened when trying back DOLF at sub 70214. Arrestor replaced. Excluded OMS 1278330. | June | 2015 | 2015Q4 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2015-06-15 | N | 127.125 | N | 3 | N | N | 1.1101 | 39.4971 | 743.1936
[7 empty] | 12504 | 2299 | 1278971 | 2015-06-16 10:17 | 2015-06-16 10:37 | 20 | 11kV | 7120 | 356 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152381 bat at ABS 63583 See UnPlanned Outage 152379, 152380 & 152384 also | June | 2015 | 2015Q4 | 2015 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Not Veg | 2015-06-16 | N | 20 | N | 4 | N | N | 1.1101 | 39.4971 | 5203.086
[7 empty] | 13931 | 14442 | 1278609 | 2015-06-16 11:30 | 2015-06-16 11:44 | 14 | 11kV | 1106 | 79 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152384 bats at pole AK 60203 See UPO 152379,152380 & 152381 also | June | 2015 | 2015Q4 | 2015 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Not Veg | 2015-06-16 | N | 14 | N | 4 | N | N | 1.1101 | 39.4971 | 808.2322
[7 empty] | 13840 | 13551 | 1278743 | 2015-06-16 14:15 | 2015-06-16 15:15 | 60 | 11kV | 1200 | 20 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 152386 interrupt to put wire back on pin at pole AH-11786 near H Porter sub 70928. Excluded oms 1278743 | June | 2015 | 2015Q4 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2015-06-16 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 876.9246
[7 empty] | 13492 | 10891 | 1278614 | 2015-06-16 11:29 | 2015-06-16 22:30 | 661 | 11kV | 127292 | 1392 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Wind Strong | N | @ZN10999 Kogarah 11kv Panel 16 "S10844 Jubilee Park's feeder tripped, reclosed, tripped Relays: A, B & C phase IOC. Fault check, timing, lockout relays, EFI Signals: 11kv trip Field efis: S10844, S10983 Remarks: low sf6 gas. RMCB failure at S10277 Princess Jubilee. 11kv bond burnt off at UGOH adj. S10983 Jubilee Princes. LV// for PT10363: usl 807, 840 | June | 2015 | 2015Q4 | 2015 | ZN10999:PA16 | ZN10999:PA16 | ZN10999/000016 | GEORGES RIVER | UG | Not Veg | 2015-06-16 | N | 91.4454 | N | 4 | N | N | 1.1101 | 39.4971 | 93021.2391
[7 empty] | 14673 | 20302 | 1278992 | 2015-06-17 09:33 | 2015-06-17 11:25 | 112 | 11kV | 89550 | 973 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Rain Light | N | Ex Zn12620 Noraville section of Pa1 "Hutton rd" 11kv RE47818 Wilfred Barrett Terilbah tripped on Earth Fault, Lockout EFI's: S14653 S14652 S14651 S14650 S14649 S18236 S18287 DIRECTIONAL DRILLING company has hit UG cable on the corner of Florida St & Hutton Rd Damaged section of 11kv UG cable from S18798:B to S14654:B to S12807:B See 1279582,3,5,6,7 exclude 1278992,9012 | June | 2015 | 2015Q4 | 2015 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | UG | Not Veg | 2015-06-17 | N | 92.0349 | N | 2 | N | N | 1.1101 | 39.4971 | 65440.4987
[7 empty] | 13362 | 9807 | 1279125 | 2015-06-17 12:21 | 2015-06-17 13:35 | 74 | 11kV | 74 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 152389 Single phase DOLF : 10 Amp Fuse was not blown. Fuse holder fell open. Fuse holder replaced. Excluded OMS No. 1279125 | June | 2015 | 2015Q4 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Veg | 2015-06-17 | N | 74 | N | 2 | N | N | 1.1101 | 39.4971 | 54.077
[7 empty] | 14012 | 15044 | 1279982 | 2015-06-19 07:34 | 2015-06-19 08:28 | 54 | 11kV | 22302 | 413 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | Ex Zn36200 Empire Bay section of Pa8 "Poole Beerlorse" Below AB43265 11kv bond burnt off at UGOH. Opencircuit fault See 1280770 exclude 1279982 | June | 2015 | 2015Q4 | 2015 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | Unknown | Unknown | 2015-06-19 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 16297.6438
[7 empty] | 13504 | 10958 | 1280081 | 2015-06-19 10:30 | 2015-06-19 13:30 | 180 | 11kV | 900 | 5 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 152405 Pole AN-40112 found energised, replaced insulators. Excluded OMS No. 1280081 | June | 2015 | 2015Q4 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2015-06-19 | N | 180 | N | 4 | N | N | 1.1101 | 39.4971 | 657.6935
[7 empty] | 13927 | 14435 | 1280292 | 2015-06-19 17:03 | 2015-06-19 18:48 | 105 | 11kV | 145879 | 1519 | HV | Burnt Contacts | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | AT Zn2196 Milperra, 11kv Panel 5 "Marigold Amour No.4" feeder tripped on: Relays: SEF Signals: 11kv trip EFI's: Nil Remarks: Air break switch. 11kv ABS3077 Middle Phase moving contact burnt open due to HR. Defective & Open (requires replacement) | June | 2015 | 2015Q4 | 2015 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-06-19 | N | 96.0362 | N | 4 | N | N | 1.1101 | 39.4971 | 106604.0705
[7 empty] | 13886 | 13964 | 1281538 | 2015-06-19 20:52 | 2015-06-19 23:25 | 153 | 11kV | 43113 | 348 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Section of Panel 8 Junction Victoria 11kV Conductor down between LB1802 and AB2160 Cause not ascertained 1281538 1251539 | June | 2015 | 2015Q4 | 2015 | ZN129:PA8 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Veg | 2015-06-19 | N | 123.8879 | N | 4 | N | N | 1.1101 | 39.4971 | 31505.7088
[7 empty] | 12534 | 2595 | 1280481 | 2015-06-20 16:11 | 2015-06-20 18:45 | 154 | 11kV | 154 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 152413 Single phase DOLF : 10 Amp sub isolated to replace arrestor Excluded OMS 1280481 | June | 2015 | 2015Q4 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2015-06-20 | N | 154 | N | 2 | N | N | 1.1101 | 39.4971 | 112.5387
[7 empty] | 12756 | 4634 | 1280494 | 2015-06-20 19:32 | 2015-06-20 21:05 | 93 | 11kV | 93 | 1 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152414 Single phase DOLF : 10 Amp Possum found at sub Excluded OMS 1280494 | June | 2015 | 2015Q4 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-06-20 | N | 93 | N | 2 | N | N | 1.1101 | 39.4971 | 67.9617
[7 empty] | 14174 | 16285 | 1280524 | 2015-06-21 07:30 | 2015-06-21 08:45 | 75 | 11kV | 75 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152417 A phase DOLF : 5 Amp Excluded OMS 1280524 | June | 2015 | 2015Q4 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2015-06-21 | N | 75 | N | 1 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 12496 | 2217 | 1281182 | 2015-06-22 17:31 | 2015-06-22 18:35 | 64 | 11kV | 35554 | 636 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15009 Manly Pa9 fdr tripped on Relays: 50TN EFI:s S15092 S16259 S16643 UG Cable fault in 11kv UG mains between S16643 and S16623 See 1282449,80 exclude 1281182,4 | June | 2015 | 2015Q4 | 2015 | ZN15009:PA9 | ZN15009:PA9 | ZN15009/000009 | NORTHERN BEACHES | UG | Not Veg | 2015-06-22 | N | 55.9025 | N | 1 | N | N | 1.1101 | 39.4971 | 25981.8145
[7 empty] | 13489 | 10865 | 1281235 | 2015-06-23 03:53 | 2015-06-23 05:02 | 69 | 11kV | 44091 | 639 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Sub 72 Five Dock Zn Panel #22 labelled "Wolseley Parra" tripped on: C phase O/C and earth fault. EFI 11kv trip change over switch operated at Sub 5972 Remarks: UG fault. Front line feeder fault from S72 Five Dock Zn pnl 22 to S6318 Wolseley Parra Sw/A tee to Sub 5972 Parramatta Croydon | June | 2015 | 2015Q4 | 2015 | ZN72:PA22 | ZN35555:PA20 | ZN35555/000020 | INNER WEST | UG | Not Veg | 2015-06-23 | N | 69 | N | 2 | N | N | 1.1101 | 39.4971 | 32220.4023
[7 empty] | 13798 | 13274 | 1281618 | 2015-06-23 13:55 | 2015-06-23 16:19 | 143.5833 | 11kV | 12009.3333 | 152 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | ZN 9550 Gwawley Bay - Pnl 27 - 11kV Frame Leakage Prohibition, Earth Fault, EFI, Field EFIs. Underground 11kV feeder struck by an Electrician digging for an underground service to 10 Shirley Rd, Miranda. SCC brick found dislodged. ME: 1282087. Rest Step: 1282088. GIS: 1281628. Withdrawn: 1281618, 32. | June | 2015 | 2015Q4 | 2015 | ZN9550:PA27 | ZN9550:PA27 | ZN09550/000027 | SUTHERLAND | UG | Not Veg | 2015-06-23 | N | 79.0088 | N | 2 | N | N | 1.1101 | 39.4971 | 8776.0666
[7 empty] | 14499 | 18677 | 1284746 | 2015-06-24 20:51 | 2015-06-24 21:31 | 40 | 11kV | 17707 | 445 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 37 tripped on Relays: A and C phase O/C and EFI Signals: 11kV Trip, Zone Earth and Tx2 Group Earth 11kV UG cable fault from S8388 Pennant George to S6272 Pennant Hills Toyota See OMS 1284746 1284747 1282184 | June | 2015 | 2015Q4 | 2015 | ZN965:PA37 | ZN965:PA37 | ZN00965/000037 | HORNSBY | UG | Not Veg | 2015-06-24 | N | 39.791 | N | 2 | N | N | 1.1101 | 39.4971 | 12939.7533
[7 empty] | 14637 | 20038 | 1282193 | 2015-06-24 22:52 | 2015-06-24 23:59 | 67 | 11kV | 134 | 2 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152461 10 amp fuse Substation DOLF excludes OMS 1282193 | June | 2015 | 2015Q4 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-06-24 | N | 67 | N | 2 | N | N | 1.1101 | 39.4971 | 97.9232
[7 empty] | 14598 | 19599 | 1282266 | 2015-06-25 08:57 | 2015-06-25 09:45 | 48 | 11kV | 48 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 152464 16 amp fuse Substation DOLF suspect fatigue excludes OMS 1282266 | June | 2015 | 2015Q4 | 2015 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2015-06-25 | N | 48 | N | 6 | N | N | 1.1101 | 39.4971 | 35.077
[7 empty] | 13930 | 14438 | 1282275 | 2015-06-25 09:06 | 2015-06-25 12:20 | 194 | 11kV | 582 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID152465 10 amp fuse Line DOLF Excludes OMS 1282275 Replaced blown SWER spur fuse 10A 65145 | June | 2015 | 2015Q4 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-06-25 | N | 194 | N | 6 | N | N | 1.1101 | 39.4971 | 425.3084
[7 empty] | 12641 | 3631 | 1282564 | 2015-06-25 17:35 | 2015-06-25 18:00 | 25 | 11kV | 600 | 24 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 152471 interrupt to retie wire on to pin at pole AH-72251 near Gwandalan sub 71658 | June | 2015 | 2015Q4 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2015-06-25 | N | 25 | N | 6 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 12812 | 5122 | 1282475 | 2015-06-25 15:01 | 2015-06-25 18:35 | 214 | 11kV | 428 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 152472 10 amp fuse Substation DOLF excludes OMS 1282475 | June | 2015 | 2015Q4 | 2015 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2015-06-25 | N | 214 | N | 6 | N | N | 1.1101 | 39.4971 | 312.7698
[7 empty] | 12941 | 6326 | 1282577 | 2015-06-25 17:24 | 2015-06-25 20:15 | 171 | 11kV | 124609 | 809 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | protection malfunction Rec 48234 tripped and locked - no load volts, no load current. See 1282782,91,4 exclude 1282577, 1282585, 1282580, 1282579, 1282578, 1282595 | June | 2015 | 2015Q4 | 2015 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Not Veg | 2015-06-25 | N | 154.0284 | N | 6 | N | N | 1.1101 | 39.4971 | 91060.5819
[7 empty] | 14274 | 17041 | 1282619 | 2015-06-25 22:44 | 2015-06-26 03:08 | 264 | 11kV | 100331 | 1196 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 12 tripped on Earth Leakage with EFI All field EFI's down to S3170 with S47769 EFI defective Cause: Note: Panel 12 CB at Hunters Hills was shooting through giving the impression that was was still present after faulty section was isolated hence panel 21 Tripped see OMS 1284519/521/526 1282619 | June | 2015 | 2015Q4 | 2015 | ZN129:PA12 | ZN129:PA56 | ZN00129/000056 | LANE COVE | UG | Not Veg | 2015-06-25 | N | 83.8888 | N | 6 | N | N | 1.1101 | 39.4971 | 73318.9355
[7 empty] | 14026 | 15228 | 1283001 | 2015-06-27 00:56 | 2015-06-27 02:40 | 104 | 11kV | 30368 | 292 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152483 B phase 11kV link 74668 found open. Excluded OMS 1283001 & 1283002 | June | 2015 | 2015Q4 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2015-06-27 | N | 104 | N | 5 | N | N | 1.1101 | 39.4971 | 22192.0387
[7 empty] | 12359 | 1017 | 1283343 | 2015-06-27 08:02 | 2015-06-27 09:00 | 58 | 11kV | 49474 | 853 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | Zn4990 City Central - 55/56 "G" feeder tripped on: Buchholz Buchholz trip at S2477 Red Cross Ken St - 56G TX Gas alarm. T/PE to top up oil S5695 restored via LV bus section to 56H TX See 1283343 1283345 | June | 2015 | 2015Q4 | 2015 | ZN4990:PA55 56GHJ | ZN4990:PA55 56GHJ | ZN04990/55 56GHJ | SYDNEY | UG | Not Veg | 2015-06-27 | N | 58 | N | 5 | N | N | 1.1101 | 39.4971 | 36154.14
[7 empty] | 13853 | 13698 | 1283008 | 2015-06-27 06:32 | 2015-06-27 11:15 | 283 | 11kV | 196370 | 1128 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn847 Hornsby Panel 18 has tripped reclosed tripped and locked out on Signals: 11kVTrip, Tx2 Group Earth and Zone Earth Relays: Timed Earth Fault, Timing, Lockout, Fault Check EFI Cause: Suspect 11kV UG feeder fault between SW/B at S8018 and associated 11kV UGOH See OMS 1284734 1284736 1284737 1283008 1283044 | June | 2015 | 2015Q4 | 2015 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | UG | Not Veg | 2015-06-27 | N | 174.0869 | N | 5 | N | N | 1.1101 | 39.4971 | 143501.4041
[7 empty] | 13377 | 9953 | 1283067 | 2015-06-27 11:27 | 2015-06-27 13:35 | 128 | 11kV | 76160 | 595 | HV | Vandalism | 3rd Party Impact | DC Not Transformer | Unplanned | No Weather Impact | N | @S1732 Balamain leagues Club, forced entry into sub and 11kv RMI switches were opened. Section of 11kv Panel 35 "S2051 Lilyfield Rd" feeder @ Zn.116 Leichhardt Remarks: Phantom Operator. @ S1732 Balmain Leagues Club, forced entry into Sub and 11kv RMI switches were opened. Dop has locked the RMI switches in the 'ON' position and placed operating handle on Top of Tx. | June | 2015 | 2015Q4 | 2015 | ZN116:PA35 | ZN116:PA31 | ZN00116/000031 | INNER WEST | Unknown | Not Veg | 2015-06-27 | N | 128 | N | 5 | N | N | 1.1101 | 39.4971 | 55655.4817
[7 empty] | 13429 | 10413 | 1283124 | 2015-06-27 17:44 | 2015-06-27 20:30 | 166 | 11kV | 332 | 2 | HV | Animal Possum | Animal | Fuse | Unplanned | No Weather Impact | N | Zn14891 Wyong Zone section of Pa12 "the yarramalong" @PT18352 Ravensdale Brush 0.3 footpath 16Amp HDO operated. Possum See 1283379 exclude 1283124 | June | 2015 | 2015Q4 | 2015 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2015-06-27 | N | 166 | N | 5 | N | N | 1.1101 | 39.4971 | 242.6158
[7 empty] | 13506 | 10977 | 1283160 | 2015-06-28 03:51 | 2015-06-28 06:07 | 136 | 11kV | 179463 | 1659 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | @Sub 9037 Miranda Zn Panel #8 labelled Sylvania Kingsway tripped and locked out on A phase IOC lockout/timing EFI, earthfault, ZE, 11kv trip Remarks: cause not ascertained. Mains to patrol in daylight | June | 2015 | 2015Q4 | 2015 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Veg | 2015-06-28 | N | 108.1754 | N | 2 | N | N | 1.1101 | 39.4971 | 131146.2671
[7 empty] | 14534 | 18984 | 1283296 | 2015-06-28 23:45 | 2015-06-29 02:45 | 180 | 11kV | 190080 | 1896 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly Pnl.30 tripped on: EF, EFI, FC FIeld EFIs: S46847, S8981, S2132, S8570, S2928, S8851 UG cable fault from S8851 Farrely Denham to S4017 Glen Dind to S3355 Denham St see 1283308 1283366 | June | 2015 | 2015Q4 | 2015 | ZN2602:PA30 | ZN36800:PA58 | ZN36800/000058 | WAVERLEY | UG | Not Veg | 2015-06-28 | N | 100.2532 | N | 2 | N | N | 1.1101 | 39.4971 | 138904.8576
[7 empty] | 12646 | 3718 | 1283759 | 2015-06-29 15:49 | 2015-06-29 18:40 | 171 | 11kV | 141930 | 830 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 152512 Overcurrent OMS 1283759,1283757,1283788,1283793,1283816 system was abnormal due to SI 6903 33kV TM9 was open due to safety with reports of car hit pole petrol leaking sparks at pole refer report | June | 2015 | 2015Q4 | 2015 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2015-06-29 | N | 171 | N | 4 | N | N | 1.1101 | 39.4971 | 103718.2578
[7 empty] | 13120 | 7783 | 1283844 | 2015-06-29 17:50 | 2015-06-29 19:16 | 86 | 11kV | 66473 | 778 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Pa7 "Wyuong Mingara etc" tripped Relays: EFI E/F B&C phase overucrrent EFI's: S14805 Fault to be located in section of 11kfdr from S14805:D Wyong Mingara to AB40295 to LB62465 to S14821:A Mingara Wyong. Isolated only. Switching tag left @ S14805 See 1284560,1,2 exclude 1283844 | June | 2015 | 2015Q4 | 2015 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | UG | Not Veg | 2015-06-29 | N | 85.4409 | N | 4 | N | N | 1.1101 | 39.4971 | 48576.5078
[7 empty] | 14062 | 15501 | 1283861 | 2015-06-29 18:50 | 2015-06-29 20:25 | 95 | 11kV | 151195 | 1625 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn195 Pymble Panel 9 tripped on Earth Fault with EFI Signals: 11kV Trip Field EFI's Nil Cause: Front line feeder fault at Panel 9 Pymble Abnormal Switching: LVB62192 Closed, CP2326 Open See OMS 1284642 1284643 1283861 | June | 2015 | 2015Q4 | 2015 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | UG | Not Veg | 2015-06-29 | N | 93.0431 | N | 4 | N | N | 1.1101 | 39.4971 | 110488.8465
[7 empty] | 12968 | 6549 | 1283850 | 2015-06-29 18:29 | 2015-06-30 11:55 | 1046 | 11kV | 15036.0667 | 26 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 "Wyong" CP44781 Auto link section of fdr interrupted for safety, danger HV falling 11kv OH in danger of fallin near auto link 44781 dunks lane See 1283852 2nd 1283850 exclude 1283912 CC1: 22-"Refer to SOp" | June | 2015 | 2015Q4 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2015-06-29 | N | 578.3103 | N | 4 | N | N | 1.1101 | 39.4971 | 10987.914
[7 empty] | 10808 | 5549 | 1284797 | 2015-07-01 16:20 | 2015-07-01 20:40 | 260 | 11kV | 82693 | 936 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Zone Pa1 "Matarm" tripped and locked out 51N Bassler EF, EFI, fault check relay & lockout/timing, F/C #1 Transformer, 11kv trip HV endbox fault at S18105. Note Endbox labelling was incorrect causiong LV// fuses to blow See 1284950,1,2 exclude 1284797,804,19 | July | 2015 | 2016Q1 | 2016 | ZN14892:PA1 | ZN14892:PA1 | ZN14892/000001 | CENTRAL COAST | UG | Not Veg | 2015-07-01 | N | 88.3472 | N | 3 | N | N | 1.1101 | 39.4971 | 60429.6054
[7 empty] | 10694 | 4388 | 1284577 | 2015-07-01 11:21 | 2015-07-01 23:05 | 704 | 11kV | 36194 | 1780 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 152538 B & C phase Overcurrent; Earth fault UGOH JR-97139 fault feed to sub 8484 | July | 2015 | 2016Q1 | 2016 | 264:81236 | 264:81236 | ZN00264/081236 | PORT STEPHENS | Unknown | Unknown | 2015-07-01 | N | 20.3337 | N | 3 | N | N | 1.1101 | 39.4971 | 26449.5077
[7 empty] | 12077 | 18734 | 1284660 | 2015-07-01 13:24 | 2015-07-02 11:45 | 1341 | 11kV | 381817 | 1632 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | ZN 9245 Engadine - Pnl 34 - Trip/reclose/trip, C phase OC, Earth fault, EFI, Field EFIs. Pt 9649 pole snapped during service work and fell onto property. Due to HV into LV all switchboards on distributors from PT 9649 required inspection by Installation Inspectors. ME: 1286920. Rest Steps: 1286921, 2. Withdrawn: 1284660, 8, 73, 82, 84, 91, 92, 93. | July | 2015 | 2016Q1 | 2016 | ZN9245:PA34 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | OH | Not Veg | 2015-07-01 | N | 233.9565 | N | 3 | N | N | 1.1101 | 39.4971 | 279020.6019
[7 empty] | 11301 | 10968 | 1285033 | 2015-07-02 10:14 | 2015-07-02 12:45 | 151 | 11kV | 18724 | 124 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Sub 2835 Panel No.17 "Burwood Wilga" feeder CB was found in the Open posiion with no Relay operation or signals Abnormal: sub 2931 sw/b to sub 7560 sw/A defective. sw/A closed @ sub 7648 Remarks: cause not ascertained. Ausgrid staff working in Burwood Zn did not see or hear anything. | July | 2015 | 2016Q1 | 2016 | ZN2835:PA17 | ZN2835:PA17 | ZN02835/000017 | BURWOOD | OH | Veg | 2015-07-02 | N | 151 | N | 2 | N | N | 1.1101 | 39.4971 | 13682.9469
[7 empty] | 12226 | 20201 | 1285359 | 2015-07-02 17:36 | 2015-07-02 18:57 | 81 | 11kV | 55728 | 688 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | 11kV Footpath side HV bond burnt off at AB1718 See OMS 1288292 1285364 1285365 1285374 1285375 1285376 | July | 2015 | 2016Q1 | 2016 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Not Veg | 2015-07-02 | N | 81 | N | 2 | N | N | 1.1101 | 39.4971 | 40724.3787
[7 empty] | 11012 | 7692 | 1285799 | 2015-07-03 17:23 | 2015-07-03 18:20 | 57 | 11kV | 2514 | 46 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14143 Somersby 11kv Pa6 fdr tripped Relays: Earth Fault, EFI Signals: Group Earth No.1 EFI's: S18379 S14634 S18540 S18454 11kv UG Fault from S18454 to S18253 See 1289198,9 Exclue 1285799 | July | 2015 | 2016Q1 | 2016 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | UG | Not Veg | 2015-07-03 | N | 54.6522 | N | 2 | N | N | 1.1101 | 39.4971 | 1837.157
[7 empty] | 10802 | 5501 | 1285805 | 2015-07-03 18:06 | 2015-07-03 19:15 | 69 | 11kV | 11656 | 1406 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 152565 DOLF on fire at sub 7648 Excluded OMS 1285805 | July | 2015 | 2016Q1 | 2016 | 258:80793 | 258:80793 | ZN00258/080793 | NEWCASTLE | OH | Not Veg | 2015-07-03 | N | 8.2902 | N | 2 | N | N | 1.1101 | 39.4971 | 8517.861
[7 empty] | 12025 | 18296 | 1285858 | 2015-07-04 08:57 | 2015-07-04 17:00 | 483 | 11kV | 966 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 152568 A Phase DOLF : 10 Amp Transformer replaced Excluded OMS 1285858 | July | 2015 | 2016Q1 | 2016 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2015-07-04 | N | 483 | N | 2 | N | N | 1.1101 | 39.4971 | 705.9243
[7 empty] | 12203 | 19884 | 1288327 | 2015-07-04 17:41 | 2015-07-04 19:18 | 97 | 11kV | 37263 | 439 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn1489 Wyong Pa14 R fdr has tripped Signals: 11kv trip ¦ Relays: 51 AB, EFI ¦ EFI: nil RE45181 Mcpherson rd has tripped and reclosed no supply restored Relays: OC See 1288327,30,1 exclude 1285986 | July | 2015 | 2016Q1 | 2016 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | OH | Veg | 2015-07-04 | N | 84.8815 | N | 2 | N | N | 1.1101 | 39.4971 | 27230.7013
[7 empty] | 12023 | 18273 | 1286148 | 2015-07-05 19:44 | 2015-07-05 21:02 | 78 | 11kV | 77751 | 1022 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 43 tripped on Relays: Earth Fault +EFT Signals: 11kV trip, Zone Earth and No2 Group Earth Cause: 11kV UG fron line feeder fault See OMS 1288126 1286148 1286157 | July | 2015 | 2016Q1 | 2016 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | UG | Not Veg | 2015-07-05 | N | 76.0773 | N | 1 | N | N | 1.1101 | 39.4971 | 56818.1375
[7 empty] | 10666 | 4047 | 1286170 | 2015-07-06 02:59 | 2015-07-06 04:40 | 101 | 11kV | 150592 | 1492 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 152574 2 fault operations 3 phase Earth fault U/G Cable fault excluded OMS 1286170 | July | 2015 | 2016Q1 | 2016 | 240:34840 | 240:34840 | ZN00240/034840 | NEWCASTLE | UG | Not Veg | 2015-07-06 | N | 100.933 | N | 3 | N | N | 1.1101 | 39.4971 | 110048.1919
[7 empty] | 10640 | 3766 | 1286216 | 2015-07-06 09:03 | 2015-07-06 10:03 | 60 | 11kV | 8280 | 138 | HV | Staff Operation | Utility Process Issue | DC Not Transformer | Unplanned | No Weather Impact | N | S61425 HV tee off tripped on RMI. Abnormal: 11kV FDR O/O/S from S61425 to S49955 for jointing work to commission a new sub. Staff Error: Jointer accidently tripped the TX HV switch on the RMI whilst working on D/O #362914 | July | 2015 | 2016Q1 | 2016 | ZN384:PA70 | ZN384:PA80 | ZN00384/000080 | SYDNEY | UG | Not Veg | 2015-07-06 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 6050.7798
[7 empty] | 11976 | 17771 | 1286454 | 2015-07-06 13:59 | 2015-07-06 16:06 | 127 | 11kV | 211221 | 1845 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 690 Campsie - Pnl 18 - 11kV trip, Field EFI. Underground cable failed in service from S 5608 to S 2947 to S 274 to S 356. ME: 1287144. Rest Steps: 1287145, 8. Withdrawn: 1286454. | July | 2015 | 2016Q1 | 2016 | ZN690:PA18 | ZN690:PA18 | ZN00690/000018 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-07-06 | N | 114.4829 | N | 3 | N | N | 1.1101 | 39.4971 | 154354.0768
[7 empty] | 10387 | 266 | 1286724 | 2015-07-07 08:30 | 2015-07-07 09:59 | 89 | 11kV | 267 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152584 A phase DOLF : 10 Amp Excluded OMS 1286724 | July | 2015 | 2016Q1 | 2016 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2015-07-07 | N | 89 | N | 5 | N | N | 1.1101 | 39.4971 | 195.1157
[7 empty] | 10655 | 3931 | 1286859 | 2015-07-07 12:59 | 2015-07-07 14:41 | 102 | 11kV | 181474 | 2072 | HV | Excavation Ausgrid Staff | Utility Process Issue | U/G Cable | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 4 tripped and Reclosed Tripped and locked out on C Phase IOC and Time O/C, Reclose Time delay and lockout At Zn965 Pennant Hills Panel 38 Tripped on Relays: Earth Fault with EFI Cause: UG cable damaged by Ausgrid Staff See OMS 1288097 1288100 1286859 1286860 | July | 2015 | 2016Q1 | 2016 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | UG | Not Veg | 2015-07-07 | N | 87.584 | N | 5 | N | N | 1.1101 | 39.4971 | 132615.8466
[7 empty] | 11283 | 10726 | 1287022 | 2015-07-07 17:59 | 2015-07-07 18:45 | 46 | 11kV | 5317 | 116 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT12775 Boomerang Eloora - Centre phase 31.5A HV Drop Out fuse operated Fuse fatigue See 1287022 1287036(GIS) | July | 2015 | 2016Q1 | 2016 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Not Veg | 2015-07-07 | N | 45.8362 | N | 5 | N | N | 1.1101 | 39.4971 | 3885.5068
[7 empty] | 10750 | 5001 | 1287055 | 2015-07-07 20:15 | 2015-07-07 21:30 | 75.45 | 11kV | 75.45 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 152590 1 fault operation Rang Ian O'Brien. His staff are patrolling their network looking for problem. | July | 2015 | 2016Q1 | 2016 |  |  |  | SINGLETON | Unknown | Not Veg | 2015-07-07 | N | 75.45 | N | 5 | N | N | 1.1101 | 39.4971 | 55.1366
[7 empty] | 11376 | 11672 | 1287067 | 2015-07-07 23:28 | 2015-07-08 02:30 | 182 | 11kV | 203109 | 1341 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S847 Hornsby Panel 21 Tripped and Reclosed on A and C phase IOC, EFI, Fault Check, Timing and Lockout Cause: 11kV front line feeder fault NOTE: Feeder tripped on restoration see OMS 1288296 1284419 1287076 | July | 2015 | 2016Q1 | 2016 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | UG | Not Veg | 2015-07-07 | N | 151.4609 | N | 5 | N | N | 1.1101 | 39.4971 | 148426.0665
[7 empty] | 11611 | 13858 | 1287068 | 2015-07-08 05:15 | 2015-07-08 06:40 | 85 | 11kV | 2210 | 26 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 152591 B phase DOLF : 31 Amp V 233/34/34 Right load 92/27/48 Left load 31/20/11 Fuse fatigue. Excluded OMS 1287068 | July | 2015 | 2016Q1 | 2016 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2015-07-08 | N | 85 | N | 3 | N | N | 1.1101 | 39.4971 | 1615.0028
[7 empty] | 11542 | 13040 | 1287286 | 2015-07-08 12:25 | 2015-07-08 18:50 | 385 | 11kV | 97585 | 2146 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 152604 2 fault operations UGOH fault at pole OR-57029 Excluded OMS 1287349 | July | 2015 | 2016Q1 | 2016 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | Unknown | Unknown | 2015-07-08 | N | 45.473 | N | 3 | N | N | 1.1101 | 39.4971 | 71312.2397
[7 empty] | 11043 | 7969 | 1287498 | 2015-07-08 18:28 | 2015-07-08 20:50 | 142 | 11kV | 26554 | 187 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S 9620 Excellsior Burraneer - All phases Fuse switch. Suspected transformer failure resulting in a tripped fuse switch. Dist also in LV//. also refer to 1287498 | July | 2015 | 2016Q1 | 2016 | ZN9118:PA12 | ZN9118:PA12 | ZN09118/000012 | SUTHERLAND | UG | Not Veg | 2015-07-08 | N | 142 | N | 3 | N | N | 1.1101 | 39.4971 | 19404.88
[7 empty] | 11676 | 14547 | 1287538 | 2015-07-09 02:43 | 2015-07-09 03:30 | 47.4167 | 11kV | 7207.3333 | 152 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152606 C phase DOLF : 31 Amp Excluded OMS 1287538 CC1: 22-"Refer to SOp" | July | 2015 | 2016Q1 | 2016 | 213:33771 | 213:33771 | ZN00213/033771 | NEWCASTLE | OH | Veg | 2015-07-09 | N | 47.4167 | N | 4 | N | N | 1.1101 | 39.4971 | 5266.9066
[7 empty] | 11412 | 11952 | 1287541 | 2015-07-09 03:38 | 2015-07-09 06:12 | 154 | 11kV | 245014 | 1681 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15002 Narrabeen Pnl.6 tripped, reclosed and locked out on: C phase timed O/C, Reclose/timing relay/lockout. Second fault bond burnt off: tripped on SEF Dead possum found near PT15196. Fault current caused second fault with bond burnt off on CNR Pittwater Rd and Namona St see 1287579 1287576 1287578 | July | 2015 | 2016Q1 | 2016 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | OH | Not Veg | 2015-07-09 | N | 145.7549 | N | 4 | N | N | 1.1101 | 39.4971 | 179049.0045
[7 empty] | 11377 | 11701 | 1285986 | 2015-07-09 07:43 | 2015-07-09 07:51 | 8 | 11kV | 712 | 89 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | Recloser CP45181 MCPherson Rd tripped on O/C Cause: Switching for Daros363586 (Cross Tx Circulating Current) see OMS1288306 1285986 | July | 2015 | 2016Q1 | 2016 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | OH | Not Veg | 2015-07-09 | N | 8 | N | 4 | N | N | 1.1101 | 39.4971 | 520.3086
[7 empty] | 11922 | 17156 | 1287681 | 2015-07-09 10:20 | 2015-07-09 12:35 | 135 | 11kV | 945 | 7 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 152610 isolated for safety. Pole broken HV-70040. exclude OMS 1287681 | July | 2015 | 2016Q1 | 2016 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Not Veg | 2015-07-09 | N | 135 | N | 4 | N | N | 1.1101 | 39.4971 | 690.5781
[7 empty] | 10544 | 2520 | 1288284 | 2015-07-10 14:43 | 2015-07-10 16:50 | 126.85 | 11kV | 634.25 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 152622 emergency switching, broken cross-arm at pole 4k-40033. | July | 2015 | 2016Q1 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2015-07-10 | N | 126.85 | N | 3 | N | N | 1.1101 | 39.4971 | 463.4912
[7 empty] | 11995 | 18021 | 1288351 | 2015-07-10 16:39 | 2015-07-10 19:25 | 166 | 11kV | 34919 | 495 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Lightning | N | Zn12650 West Gosford Pa14 "Kariong/ Erina St" tripped on Relays: 51N Earth Fault, 150N - EFI, Lockout & Timing Signals: Nil EFI's: Nil Note: Some EFI's on the HV UGOH's would help Abnormal: Closed LB46579 S18014/SwA Open Lightning Strike caused damage to commercial switchboard @ JusFrute Drive West Gosford S14172 Jusfrute Nippon Dist 3 interrupted for safety. Service Cut awau to commercial premises corner of Jusfrute Drive adjacent LV USL 18982 See 1289211,5,6 2nd 1288393 Exclude 1288351,64 | July | 2015 | 2016Q1 | 2016 | ZN12650:PA14 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | Unknown | Not Veg | 2015-07-10 | N | 70.5434 | N | 3 | N | N | 1.1101 | 39.4971 | 25517.7753
[7 empty] | 10470 | 1619 | 1288396 | 2015-07-10 20:40 | 2015-07-10 22:25 | 105 | 11kV | 2625 | 25 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 152626 ## P0295. No protection operations. Section isolated to retie pin GW-90032. | July | 2015 | 2016Q1 | 2016 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Not Veg | 2015-07-10 | N | 105 | N | 3 | N | N | 1.1101 | 39.4971 | 1918.2726
[7 empty] | 11309 | 11024 | 1288535 | 2015-07-11 18:03 | 2015-07-11 19:40 | 97 | 11kV | 135064.7167 | 1528 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ZN 10999 Kogarah - Pnl 32 - Trip/reclose/trip, Earth fault, Earth fault Check, EFI, Lockout, Field EFIs. HV bond blown off on UGOH to S 10469. S 10469 restored via LV//. ME: 1289692. Rest Step: 1289693. GIS: 1288539, 41, 42. Withdrawn: 1288535, 45. | July | 2015 | 2016Q1 | 2016 | ZN10999:PA32 | ZN10999:PA32 | ZN10999/000032 | BAYSIDE | OH | Not Veg | 2015-07-11 | N | 88.3931 | N | 5 | N | N | 1.1101 | 39.4971 | 98701.3112
[7 empty] | 11224 | 10107 | 1288548 | 2015-07-11 19:06 | 2015-07-11 20:10 | 64 | 11kV | 48047 | 770 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2635 Epping Panel 50 Tripped on C phase OC EF and EFI Cause: UF fault between S7707 SW/B and S63381 SW/A See OMS 1290171 1290173 1288548 | July | 2015 | 2016Q1 | 2016 | ZN2635:PA50 | ZN2635:PA50 | ZN02635/000050 | RYDE | UG | Not Veg | 2015-07-11 | N | 62.3987 | N | 5 | N | N | 1.1101 | 39.4971 | 35111.3305
[7 empty] | 10971 | 7300 | 1288570 | 2015-07-11 23:35 | 2015-07-12 05:10 | 335 | 11kV | 24700 | 108 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap Rd" RE44602 Ourimbah Ck Rd opened on overcurrent Tree rbanch brought down 1 phase of 11kv near AB42559 See 1289396,9,401 exclude 1288570 | July | 2015 | 2016Q1 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2015-07-11 | N | 228.7037 | N | 5 | N | N | 1.1101 | 39.4971 | 18050.0315
[7 empty] | 11494 | 12683 | 1288581 | 2015-07-12 06:05 | 2015-07-12 07:00 | 55 | 11kV | 5225 | 95 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152633 C phase DOLF : 31Amp | July | 2015 | 2016Q1 | 2016 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Veg | 2015-07-12 | N | 55 | N | 5 | N | N | 1.1101 | 39.4971 | 3818.2759
[7 empty] | 10482 | 1763 | 1288533 | 2015-07-11 17:49 | 2015-07-12 10:35 | 1006 | 11kV | 11063 | 159 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 152631 U/G cable fault to sub 51068 | July | 2015 | 2016Q1 | 2016 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | UG | Not Veg | 2015-07-11 | N | 69.5786 | N | 5 | N | N | 1.1101 | 39.4971 | 8084.5141
[7 empty] | 10979 | 7410 | 1288596 | 2015-07-12 07:53 | 2015-07-12 12:15 | 262 | 11kV | 343063 | 3019 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2310 Punchbowl Panel 34 Slyvester King Georges Feeder tripped on: A phase O/C, EFI Field EFIs: down to S2198 & S2187 S3831 p40 Abnormal: sw/B closed S2187 Sw/A open S7745, S274 closed Sw/B, Sw/A open Remarks: UG fault. See defective OOS for S3529 Panel 40 from 21/04/2015. Therefore 1 centre cannot be fed LV// required plus extension for Haz S3712, S3105, S2510 were in LV// for disc 362341 | July | 2015 | 2016Q1 | 2016 | ZN2310:PA34 | ZN2310:PA14 | ZN02310/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-07-12 | N | 113.6346 | N | 5 | N | N | 1.1101 | 39.4971 | 250700.3218
[7 empty] | 11582 | 13510 | 1288567 | 2015-07-11 23:26 | 2015-07-12 17:45 | 1099 | 11kV | 280343 | 493 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 152632 Mains down DV-34620 Wollombi | July | 2015 | 2016Q1 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2015-07-11 | N | 568.6471 | N | 5 | N | N | 1.1101 | 39.4971 | 204866.3957
[7 empty] | 10434 | 1023 | 1288795 | 2015-07-12 18:43 | 2015-07-12 19:13 | 30.4333 | 11kV | 38650.3333 | 1270 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152639 tree branch at No 6 Carrington st Excluded oms 1288795 | July | 2015 | 2016Q1 | 2016 | 216:10728 | 216:10728 | ZN00216/010728 | LAKE MACQUARIE | OH | Veg | 2015-07-12 | N | 30.4333 | N | 5 | N | N | 1.1101 | 39.4971 | 28244.5236
[7 empty] | 11551 | 13117 | 1288801 | 2015-07-12 19:04 | 2015-07-12 19:24 | 20 | 11kV | 36372 | 3352 | HV | Overload Operational | Utility Process Issue | Circuit Breaker | Unplanned | No Weather Impact | N | Zn3672 Maroubra Pnl.46 tripped on overload Abnormal: Sw A @ S1946 Flower St OPEN - Sw C @ S542 Boomerang Malabar CLOSED (Defective) Overload due to abnormal switching see 1288800 1288946 CC1: 22-"Refer to SOp" | July | 2015 | 2016Q1 | 2016 | ZN3672:PA46 | ZN3672:PA46 | ZN03672/000046 | RANDWICK | Unknown | Not Veg | 2015-07-12 | N | 10.8508 | N | 5 | N | N | 1.1101 | 39.4971 | 26579.5848
[7 empty] | 11434 | 12150 | 1288827 | 2015-07-12 22:15 | 2015-07-13 01:10 | 175 | 11kV | 31325 | 179 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152640 si P0296 Emergency interruption for removal of tree above ABS 42779. Excluded oms 1288843 | July | 2015 | 2016Q1 | 2016 | 217:33612 | 217:33605 | ZN00217/033605 | LAKE MACQUARIE | OH | Veg | 2015-07-12 | N | 175 | N | 5 | N | N | 1.1101 | 39.4971 | 22891.3861
[7 empty] | 10628 | 3665 | 1289292 | 2015-07-13 17:06 | 2015-07-13 17:50 | 44.4667 | 11kV | 1245.0667 | 28 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 152645 11kV Fdr isolated to remove tree from OHM between poles IQ-21641 & IQ-21642. | July | 2015 | 2016Q1 | 2016 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2015-07-13 | N | 44.4667 | N | 1 | N | N | 1.1101 | 39.4971 | 909.858
[7 empty] | 10895 | 6554 | 1289561 | 2015-07-14 08:12 | 2015-07-14 14:30 | 378 | 11kV | 41202 | 109 | HV | Overload LV Parallel | Utility Process Issue | O/H Link | Unplanned | No Weather Impact | N | At PT912 Kuppa Kulgoa 400A fuse blown on A B C distributor Cause: LV parallel during feeder trip. see separate interruption report on 92G suspect disttributor 1 and were in parallel hence rolled up to hv fuse See OMS1289595 1289571 1289561 CC1: 22-"Refer to SOp" | July | 2015 | 2016Q1 | 2016 | ZN4545:PA24 | ZN35500:PA16 | ZN35500/000016 | RYDE | OH | Not Veg | 2015-07-14 | N | 378 | N | 1 | N | N | 1.1101 | 39.4971 | 30109.2063
[7 empty] | 11088 | 8633 | 1290376 | 2015-07-15 14:28 | 2015-07-15 21:40 | 432 | 11kV | 432 | 1 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 152671 Feeder isolated to repair broken insulators & crossarm at pole IV-90728. SI No. p0299 Excluded OMS No. 1290376 | July | 2015 | 2016Q1 | 2016 | 206:34432 | 206:34432 | ZN00206/034432 | LAKE MACQUARIE | OH | Not Veg | 2015-07-15 | N | 432 | N | 2 | N | N | 1.1101 | 39.4971 | 315.6929
[7 empty] | 11165 | 9562 | 1290515 | 2015-07-15 23:08 | 2015-07-16 01:45 | 157 | 11kV | 2826 | 18 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S 10376 Turrella NCR - 11kV B phase fuse switch. Transformer failure. 11kV fuse switch was found to have B phase 11kV fuse blown; however, Tx had no volts. Supply restored via LV//. ME: 1290561. Withdrawn: 1290515. | July | 2015 | 2016Q1 | 2016 | ZN10990:PA8 | ZN10998:PA10 | ZN10998/000010 | BAYSIDE | UG | Not Veg | 2015-07-15 | N | 157 | N | 2 | N | N | 1.1101 | 39.4971 | 2065.1574
[7 empty] | 10798 | 5473 | 1290523 | 2015-07-16 03:37 | 2015-07-16 06:04 | 147 | 11kV | 107979 | 833 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Pa14 Fdr tripped Relays: C phase timed overcurrent, EFI Signals: 11kv trip EFI's Nil Cause not ascertained. Feeder patrolled by DOp See 1292020,1 exclude 1290523 | July | 2015 | 2016Q1 | 2016 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Veg | 2015-07-16 | N | 129.6267 | N | 1 | N | N | 1.1101 | 39.4971 | 78907.8684
[7 empty] | 11149 | 9389 | 1291087 | 2015-07-17 08:36 | 2015-07-17 10:00 | 84 | 11kV | 4620 | 55 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 152687 B phase DOLF : 20 Amp, Incorrect operation of fuses Excluded OMS 1291087 | July | 2015 | 2016Q1 | 2016 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | OH | Not Veg | 2015-07-17 | N | 84 | N | 6 | N | N | 1.1101 | 39.4971 | 3376.1597
[7 empty] | 11616 | 13937 | 1291248 | 2015-07-17 11:55 | 2015-07-17 13:30 | 95 | 11kV | 950 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | LID 152689 C phase DOLF : 40 Amp - Incorrect operation of fuses Excluded OMS 1291248 & 1291269 | July | 2015 | 2016Q1 | 2016 | 265:81649 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Not Veg | 2015-07-17 | N | 95 | N | 6 | N | N | 1.1101 | 39.4971 | 694.232
[7 empty] | 11566 | 13320 | 1291286 | 2015-07-17 13:13 | 2015-07-17 14:30 | 77.1 | 11kV | 693.9 | 9 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 152690 Patrol found pole with damaged head. Temporary repairs made. Pole DN-40062 | July | 2015 | 2016Q1 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2015-07-17 | N | 77.1 | N | 6 | N | N | 1.1101 | 39.4971 | 507.0817
[7 empty] | 11836 | 16423 | 1291395 | 2015-07-17 16:07 | 2015-07-17 16:55 | 48 | 11kV | 48 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152691 Single phase DOLF : 10 Amp Excluded OMS 1291395 | July | 2015 | 2016Q1 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-07-17 | N | 48 | N | 6 | N | N | 1.1101 | 39.4971 | 35.077
[7 empty] | 11633 | 14052 | 1291412 | 2015-07-17 17:00 | 2015-07-17 18:36 | 96 | 11kV | 49944 | 709 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | At ZN1068 Lidcombe - Panel 16 "Stanley Water" tripped on: Relays: A & C phase OC, EFI Signals: 11kv trip, Zone earth, Tx3 Group Earth EFI's: S1985, S35258 Remarks: UG fault. 11kv UG fault between S35268 Water Clarence Sw/B and S.6036 New St Sw/A | July | 2015 | 2016Q1 | 2016 | ZN1068:PA16 | ZN1068:PA16 | ZN01068/000016 | CUMBERLAND | UG | Not Veg | 2015-07-17 | N | 70.4429 | N | 6 | N | N | 1.1101 | 39.4971 | 36497.6021
[7 empty] | 11638 | 14114 | 1291091 | 2015-07-17 08:37 | 2015-07-17 19:15 | 638 | 11kV | 154120 | 1682 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn15002 Narrabeen Pa6 tripped Relays: C phase timed, EFi, Frame Leakage Signals: 11kv trip, Zone Earth, Under Voltage Protection EFI's: nil Abnormal: USL 22437 opned for DR364007 @Zn15002 narrabeen SEL/REC non auto Pa6 Truck clipped distributor wire outside No16 Boondah Rd Warriewood HV mains into LV mains & broken HV Cross arm II required LV Services Access permit issued to lineworker @1200 See 1292150,1 exclude 1291091,112,5,99 | July | 2015 | 2016Q1 | 2016 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | OH | Not Veg | 2015-07-17 | N | 91.629 | N | 6 | N | N | 1.1101 | 39.4971 | 112626.3502
[7 empty] | 10936 | 6986 | 1291518 | 2015-07-18 09:32 | 2015-07-18 11:10 | 97.9333 | 11kV | 293.8 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152695 Singe phase DOLF : 10 Amp Please Investigate. Please Patrol. Apparently this is the 3rd or 4th time this has blown in recent times. Also on 21/05/15, 13/06/15, 26/06/15. | July | 2015 | 2016Q1 | 2016 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-07-18 | N | 97.9333 | N | 3 | N | N | 1.1101 | 39.4971 | 214.7004
[7 empty] | 11797 | 15943 | 1291659 | 2015-07-18 19:47 | 2015-07-18 21:04 | 76.65 | 11kV | 3602.55 | 47 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152700 No Protection Operation. Service brought down at sub 52166 AND LARGE BRANCH ON dw IN FRONT OF PREMISES 14 RICHMOND VALE RD MULBRING nmi 41022727470 Excluded OMS 1291645. | July | 2015 | 2016Q1 | 2016 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2015-07-18 | N | 76.65 | N | 3 | N | N | 1.1101 | 39.4971 | 2632.6373
[7 empty] | 11236 | 10237 | 1291666 | 2015-07-18 20:42 | 2015-07-18 22:10 | 88 | 11kV | 147616 | 1930 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | Zn15004 Newport Pa9 "Avaln" fdr tripped Relays - ABC IOC, EFI, fault check Signals: 11kv trip, Tx2 Group Earth EFI's: S16880 S16526 Cause not ascertained. Fdr fault S16526 to S16840 to S17157 See 1292177,8,9 exclude 1291666 | July | 2015 | 2016Q1 | 2016 | ZN15004:PA9 | ZN15004:PA9 | ZN15004/000009 | NORTHERN BEACHES | UG | Not Veg | 2015-07-18 | N | 76.485 | N | 3 | N | N | 1.1101 | 39.4971 | 107873.4189
[7 empty] | 11684 | 14607 | 1291682 | 2015-07-19 04:48 | 2015-07-19 07:48 | 180 | 11kV | 9360 | 52 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12570 section of Pa34 PT12826 Lake Shoer Easter A phase 31.5 HDO operated HV drop out fuse blown on PT12826 causing low volts. A-N 80v, B-N 240v, C-N 165v also refer to OMS 1291682 | July | 2015 | 2016Q1 | 2016 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2015-07-19 | N | 180 | N | 2 | N | N | 1.1101 | 39.4971 | 6840.0119
[7 empty] | 12123 | 19164 | 1291741 | 2015-07-19 11:35 | 2015-07-19 17:50 | 375 | 11kV | 1125 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 152706 A phase LV fuse Replaced LV fuse assembly Excluded OMS 1291741 | July | 2015 | 2016Q1 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2015-07-19 | N | 375 | N | 2 | N | N | 1.1101 | 39.4971 | 822.1168
[7 empty] | 10424 | 829 | 1292345 | 2015-07-21 07:02 | 2015-07-21 08:50 | 108 | 11kV | 864 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152714 C phase DOLF : 10 Amp Excluded OMS 1292345 | July | 2015 | 2016Q1 | 2016 | 243:80080 | 243:80080 | ZN00243/080080 | LAKE MACQUARIE | OH | Veg | 2015-07-21 | N | 108 | N | 2 | N | N | 1.1101 | 39.4971 | 631.3857
[7 empty] | 11724 | 15146 | 1292769 | 2015-07-21 23:09 | 2015-07-22 02:30 | 201 | 11kV | 59496 | 296 | HV | 3rd Party Action | 3rd Party Impact | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 152729 No protection operations. Section isolated on request from Jemena following gas leak beneath sub 752. | July | 2015 | 2016Q1 | 2016 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | Unknown | Not Veg | 2015-07-21 | N | 201 | N | 2 | N | N | 1.1101 | 39.4971 | 43477.922
[7 empty] | 10663 | 4010 | 1292952 | 2015-07-22 11:17 | 2015-07-22 13:20 | 123 | 11kV | 137475 | 1295 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S187 Crows Nest Panel 4 Opened on Earth Fault EFI and Fault Check Signals: 11kV trip, No 4 Group Eartth and Zone Earth Cause: UG cable fault See OMS 1293467 1293470 1293469 1292952 | July | 2015 | 2016Q1 | 2016 | ZN187:PA4 | ZN187:PA4 | ZN00187/000004 | NORTH SYDNEY | UG | Not Veg | 2015-07-22 | N | 106.1583 | N | 3 | N | N | 1.1101 | 39.4971 | 100462.6752
[7 empty] | 10864 | 6247 | 1293200 | 2015-07-22 23:24 | 2015-07-23 02:00 | 156 | 11kV | 21528 | 138 | HV | Animal Other | Animal | DC Transformer | Unplanned | No Weather Impact | N | S15193 Stuart St 53 - Red phase HV TX tail blown clear Rat on TV HV | July | 2015 | 2016Q1 | 2016 | ZN15009:PA5 | ZN15009:PA5 | ZN15009/000005 | NORTHERN BEACHES | OH | Not Veg | 2015-07-22 | N | 156 | N | 3 | N | N | 1.1101 | 39.4971 | 15732.0274
[7 empty] | 10653 | 3912 | 1293174 | 2015-07-22 17:23 | 2015-07-23 10:05 | 1002 | 11kV | 1002 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 152746 Spur fuses 2 x DOLF : 20 Amp | July | 2015 | 2016Q1 | 2016 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Veg | 2015-07-22 | N | 1002 | N | 3 | N | N | 1.1101 | 39.4971 | 732.232
[7 empty] | 12143 | 19283 | 1293325 | 2015-07-23 09:33 | 2015-07-23 18:40 | 547 | 33kV Distribution | 5889 | 36 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | LID 152752 and LID 152754 Bird blew up UGOH at pole JT-67029, 33kV OHM down at pole KT-71011, Blown tapping at UGOH pole KT-70522 80500 A prot - AB&Cph O/C E/F multitrip B prot - O/C & E/F Timed O/C Aph, multitrip 90706 prot - A & Cph DIR O/C 80500 A prot - Bph O/C E/F, multitrip B prot - timed O/C A & Cph Excluded OMS 1293320/25/27/29/35/38/41/44 | July | 2015 | 2016Q1 | 2016 |  |  |  | NEWCASTLE | OH | Not Veg | 2015-07-23 | N | 163.5833 | N | 2 | N | N | 1.1101 | 39.4971 | 4303.5075
[7 empty] | 11874 | 16758 | 1293590 | 2015-07-23 20:23 | 2015-07-24 02:20 | 357 | 11kV | 46812 | 137 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 152761 Mains twisted together pole 8H-20038 caused by fallen tree. Excluded OMS REPORT NO 1293590. | July | 2015 | 2016Q1 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-07-23 | N | 341.6934 | N | 2 | N | N | 1.1101 | 39.4971 | 34208.8289
[7 empty] | 11115 | 8867 | 1293607 | 2015-07-24 06:52 | 2015-07-24 10:15 | 203 | 11kV | 1624 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT18875 Hensons Hoipos 0.5 centre phase HDO failed Fuse fatigue. Failed at Crimp See 1294363 exclude 1293607 | July | 2015 | 2016Q1 | 2016 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2015-07-24 | N | 203 | N | 2 | N | N | 1.1101 | 39.4971 | 1186.7713
[7 empty] | 12071 | 18645 | 1293959 | 2015-07-24 17:59 | 2015-07-24 19:30 | 90.9 | 11kV | 1999.8 | 22 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152774 A Phase HV Cartridge fuse : 80 Amp leads faulty between switchfuse & trans CC1: 22-"Refer to SOp" | July | 2015 | 2016Q1 | 2016 | 213:33777 | 213:33777 | ZN00213/033777 | LAKE MACQUARIE | OH | Not Veg | 2015-07-24 | N | 90.9 | N | 2 | N | N | 1.1101 | 39.4971 | 1461.3949
[7 empty] | 12220 | 20099 | 1293987 | 2015-07-25 02:24 | 2015-07-25 03:49 | 85 | 11kV | 31186 | 554 | HV | Arcing | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | Zn195 Pymble Pa25 fdr has tripped on: Signals: 11kv trip, Tx4 Group Earth, Zone Earth Relays: Earth Fault, EFI, Fault Check EFI: All EFI's above PT1425 operated ABNORMAL: S4639:B Open S4651:B closed @PT1425 Cultowa Rd DOp found HV insulators have flashed over need inspection/replacement. PT1425 open on 11kv HDO's/415V fuses & in LV// See 1294636,7 exclude 1293987 | July | 2015 | 2016Q1 | 2016 | ZN195:PA25 | ZN195:PA25 | ZN00195/000025 | KU-RING-GAI | OH | Not Veg | 2015-07-25 | N | 56.2924 | N | 3 | N | N | 1.1101 | 39.4971 | 22789.809
[7 empty] | 10998 | 7574 | 1294022 | 2015-07-25 10:21 | 2015-07-25 12:00 | 99 | 11kV | 62007 | 903 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | ZN 10994 Mortdale - Pnl 19 - Trip/reclose/trip, A phase IOC, Earth Fault, Field EFIs. 11kV UGOH failed in service. Compount filled cast iron UGOH box appears to have scorch marks and requires replacement. ME: 1296138. Rest Steps: 1296140, 2. Withdrawn: 1294022, 24, 39, 98. | July | 2015 | 2016Q1 | 2016 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | Unknown | Unknown | 2015-07-25 | N | 68.6678 | N | 3 | N | N | 1.1101 | 39.4971 | 45312.8867
[7 empty] | 11589 | 13604 | 1294424 | 2015-07-25 15:31 | 2015-07-25 16:10 | 39 | 11kV | 95 | 57 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap rd" @RE44604 Dog Trap rd tripped and reclosed on IOC trip and OC trip Cutaway defective lightning arrestors at PT13702 region to follow up See 1294424,5 | July | 2015 | 2016Q1 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2015-07-25 | N | 1.6667 | N | 3 | N | N | 1.1101 | 39.4971 | 69.4232
[7 empty] | 10760 | 5075 | 1294188 | 2015-07-26 15:25 | 2015-07-26 16:55 | 90 | 11kV | 5220 | 58 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa25 @PT12843 Hillcrest Bellbird 11kv centre phase 31.5Amp Dropout fuse operated. Tree branch across Tx bushing See 1294194 exclude 1294188,95,8,9,200,1,4 CC1: 22-"Refer to SOp" | July | 2015 | 2016Q1 | 2016 | ZN12570:PA25 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | OH | Veg | 2015-07-26 | N | 90 | N | 2 | N | N | 1.1101 | 39.4971 | 3814.622
[7 empty] | 11450 | 12243 | 1294179 | 2015-07-26 15:02 | 2015-07-26 17:00 | 118 | 11kV | 2124 | 18 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 152781 C phase DOLF : 31 Amp Fuse Fatigue excluded OMS 1294179 | July | 2015 | 2016Q1 | 2016 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Not Veg | 2015-07-26 | N | 118 | N | 2 | N | N | 1.1101 | 39.4971 | 1552.1566
[7 empty] | 11722 | 15131 | 1294273 | 2015-07-27 07:39 | 2015-07-27 08:35 | 56 | 11kV | 62888 | 1123 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12580 Erina section of Pa4 @RE49613 Marna Tulip tripped and locked out on SEF trip, OC trip Cause not ascertained. feeder to be patrolled See 1295538 exclude 1294273,8 | July | 2015 | 2016Q1 | 2016 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2015-07-27 | N | 56 | N | 5 | N | N | 1.1101 | 39.4971 | 45956.6955
[7 empty] | 11524 | 12888 | 1294513 | 2015-07-27 12:43 | 2015-07-27 14:55 | 132 | 11kV | 7788 | 59 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | PT13650 centre phase HDO operated. suspect developing transformer fault exclude 1294513 1294530 | July | 2015 | 2016Q1 | 2016 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Not Veg | 2015-07-27 | N | 132 | N | 5 | N | N | 1.1101 | 39.4971 | 5691.2407
[7 empty] | 11588 | 13595 | 1294509 | 2015-07-27 12:36 | 2015-07-27 18:50 | 374 | 11kV | 134542 | 930 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa13 @RE62730 Manns Narara Creek tripped reclosed lockout on oc trip suspect UG fault from S63690 to UGOH or S18009 to UGOH See 1295541,2,3,4 exclude 1294509 | July | 2015 | 2016Q1 | 2016 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | UG | Not Veg | 2015-07-27 | N | 144.6688 | N | 5 | N | N | 1.1101 | 39.4971 | 98319.3253
[7 empty] | 11235 | 10206 | 1294712 | 2015-07-27 19:50 | 2015-07-27 20:52 | 62.2 | 11kV | 43166.8 | 694 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Cold <10C | N | At Zn965 Pennant Hills, 11kv Pnl 21 "Sub 8212 Pennant Beecroft" tripped on: Relays: C phase IOC, Earth fault, EFI Signals: 11kv trip Field EFI's: Sub 8212, Sub 4967 Remarks: Animals/Birds. Possum found clear of overheard at PT1887 Chapman Cardinal | July | 2015 | 2016Q1 | 2016 | ZN965:PA21 | ZN965:PA21 | ZN00965/000021 | HORNSBY | OH | Not Veg | 2015-07-27 | N | 62.2 | N | 5 | N | N | 1.1101 | 39.4971 | 31545.0242
[7 empty] | 11234 | 10187 | 1294711 | 2015-07-27 19:43 | 2015-07-27 21:29 | 106 | 11kV | 100666 | 1085 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | At Zn129 Hunters Hill: 11kv Pnl 9 "Sub 8345 Pittwater Gannet" feeder C/B tripped, reclosed and locked out on: Relays: A phase IOC & timed, earth leakage, reclose, lockout, fault check, EFI, No1 tx Frame leakage check. Signals: 11kv trip Field EFI's: Nil Remarks: UG fault. 11kv U/G cable fault from ZN 129 Hunters Hill Pnl 9 to sub 8345 Pittwater Gannet sw/A | July | 2015 | 2016Q1 | 2016 | ZN129:PA9 | ZN129:PA41 | ZN00129/000041 | LANE COVE | UG | Not Veg | 2015-07-27 | N | 92.7797 | N | 5 | N | N | 1.1101 | 39.4971 | 73563.7437
[7 empty] | 11991 | 17982 | 1294836 | 2015-07-28 09:41 | 2015-07-28 10:36 | 55.2833 | 11kV | 45055.9167 | 815 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN874 Concord, 11kv Panel 3 'S.2031 Llewellyn St, etc" feeder tripped Relays: E/F, efi Signals: 11kv trip, ZE, Tx4 GE Field efi's: S.35569, S5826, S.7107, S.49526, S49525 Remarks: UG fault, 11kv feeder fault at/from S.49525 Gauthorpe Marquet No.3 to S.7485 Leeds Cavell No.1 | July | 2015 | 2016Q1 | 2016 | ZN874:PA3 | ZN874:PA3 | ZN00874/000003 | CANADA BAY | UG | Not Veg | 2015-07-28 | N | 55.2833 | N | 2 | N | N | 1.1101 | 39.4971 | 32925.535
[7 empty] | 10563 | 2757 | 1295158 | 2015-07-28 18:36 | 2015-07-28 21:15 | 159 | 11kV | 41363 | 364 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | EX ZN 9252 Jannali - Pnl 21 - OC phase. Suspect open circuit HV bond at ABS 35179. Some LV distributors were in LV// at the time. ME: 1295993. Withdrawn: 1295158, 59, 65, 66. | July | 2015 | 2016Q1 | 2016 | ZN9252:PA21 | ZN9252:PA21 | ZN09252/000021 | SUTHERLAND | OH | Not Veg | 2015-07-28 | N | 113.6346 | N | 2 | N | N | 1.1101 | 39.4971 | 30226.8604
[7 empty] | 12172 | 19654 | 1295191 | 2015-07-29 01:23 | 2015-07-29 02:16 | 53 | 11kV | 4240 | 80 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 152818 Section opened by S.O. mva pole LS-67008 Nelson Bay Rd. wires reported down by ambos | July | 2015 | 2016Q1 | 2016 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2015-07-29 | N | 53 | N | 6 | N | N | 1.1101 | 39.4971 | 3098.4669
[7 empty] | 11206 | 9984 | 1295196 | 2015-07-29 05:34 | 2015-07-29 06:46 | 72 | 11kV | 35980 | 500 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 931 Darlinghurst 11kV Panel 13 Feeder " Liverpool West No.2" tripped Relays: EF, EFI Signals: 11kV trip, group 3 Earth, Zone Earth EFIs: S35244 UG Fault Ex Panel 13 Darlinghurst - 11kV cable fault between S35244 Liverpool West No.2 SwB, S8948 Bethel Lane SwA, S3302 Spring Shad SwA See 1297300 and 1297301 | July | 2015 | 2016Q1 | 2016 | ZN931:PA13 | ZN931:PA13 | ZN00931/000013 | WOOLLAHRA | UG | Not Veg | 2015-07-29 | N | 71.96 | N | 6 | N | N | 1.1101 | 39.4971 | 26293.1228
[7 empty] | 10562 | 2739 | 1297503 | 2015-07-29 12:40 | 2015-07-29 12:45 | 5 | 11kV | 7225 | 1445 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Primary Equip | Unplanned | No Weather Impact | N | ZN 9035 Caringbah - Pnl 6 (A bus section switch) - Opened with no protection. "A" bus section opened 1 minute after charging while closed. No command was given. | July | 2015 | 2016Q1 | 2016 | ZN9035:PA2 | ZN9035:PA2 | ZN09035/000002 | SUTHERLAND | Exclude | Not Veg | 2015-07-29 | N | 5 | N | 6 | N | N | 1.1101 | 39.4971 | 5279.8169
[7 empty] | 10385 | 229 | 1295362 | 2015-07-29 11:01 | 2015-07-29 13:10 | 129.1167 | 11kV | 387.35 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 152827 Single phase RH Fuse carrier fell out. Fuse did not operate. | July | 2015 | 2016Q1 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2015-07-29 | N | 129.1167 | N | 6 | N | N | 1.1101 | 39.4971 | 283.064
[7 empty] | 11325 | 11173 | 1295513 | 2015-07-29 15:37 | 2015-07-29 16:47 | 69.6 | 11kV | 5359.2 | 77 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 152828 Isolated for safety and to allow repairs no protection operated, wire spotted of pin by helicopter patrol. Location given to control room was pin off insulator on main trunk of feeder between subs50201/53022 and sub 6705. | July | 2015 | 2016Q1 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-07-29 | N | 69.6 | N | 6 | N | N | 1.1101 | 39.4971 | 3916.3453
[7 empty] | 10438 | 1105 | 1295617 | 2015-07-29 19:59 | 2015-07-30 01:15 | 315.8333 | 11kV | 14212.5 | 45 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 152830 Isolated for safety reasons to conduct repairs MVA pole LS-67008 | July | 2015 | 2016Q1 | 2016 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2015-07-29 | N | 315.8333 | N | 6 | N | N | 1.1101 | 39.4971 | 10386.0758
[7 empty] | 10837 | 5895 | 1295626 | 2015-07-30 04:25 | 2015-07-30 06:10 | 105 | 11kV | 56880 | 630 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Sub 35800 bankstown Zn Panel #19 labelled british paints etc tripped on Earth fault, EFI, 11kv trip Remarks: UG fault, section of 11kv feeder from Sub 6413 Carlton Blenheim Sw/B to Sub 872 Bramhall Av SW A Note Sub 872 is a Haz | July | 2015 | 2016Q1 | 2016 | ZN35800:PA19 | ZN35800:PA19 | ZN35800/000019 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-07-30 | N | 90.2857 | N | 1 | N | N | 1.1101 | 39.4971 | 41566.2263
[7 empty] | 11095 | 8677 | 1296379 | 2015-07-31 17:27 | 2015-07-31 17:57 | 30 | 11kV | 810 | 27 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 152851 Broken strands on 11kV OHM near pole ET-25538 Customer reports 11 kv mains struck by lightning. Please check and repair. Between sub 46097 and 5825. Excluded OMS 1296379 & 1292222 | July | 2015 | 2016Q1 | 2016 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2015-07-31 | N | 30 | N | 2 | N | N | 1.1101 | 39.4971 | 591.9241
[7 empty] | 10417 | 756 | 1296369 | 2015-07-31 16:37 | 2015-07-31 18:23 | 106 | 11kV | 43778 | 413 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | 11kv Bond to AB76 (S1100 side) Ex Sefton Panel 29 "Joanne court" burned off Remarks: 11kv bond to AB76 (S1100 side) ex Sefton Panel 29 "Joanne cour" burned off | July | 2015 | 2016Q1 | 2016 | ZN3472:PA29 | ZN3472:PA29 | ZN03472/000029 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-07-31 | N | 106 | N | 2 | N | N | 1.1101 | 39.4971 | 31991.6712
[7 empty] | 11598 | 13707 | 1296413 | 2015-08-01 02:22 | 2015-08-01 03:13 | 50.5833 | 11kV | 51190.3333 | 1012 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Panel 11L at Mona Vale - Recloser 20397 Pitwater Cabbage Tree tripped and locked out Cause not Ascertained | August | 2015 | 2016Q1 | 2016 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2015-08-01 | N | 50.5833 | N | 3 | N | N | 1.1101 | 39.4971 | 37408.3857
[7 empty] | 11911 | 17033 | 1296686 | 2015-08-01 07:39 | 2015-08-01 07:43 | 4 | 11kV | 1668 | 417 | HV | Staff Other | Utility Process Issue | Air Break Switch | Unplanned | No Weather Impact | N | LID 152853 1 fault operation single phase Overcurrent During SI 7469 Sw 43321 tripped (50A pickup) on Over load. Also blew A phase LVF sub 17452 causing low volts (180V) as was in parallel with sub 25485 & 25487, ABS 84 was open being feed from Fdr 80075. also see report 152854 and OMS 1296687 | August | 2015 | 2016Q1 | 2016 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2015-08-01 | N | 4 | N | 3 | N | N | 1.1101 | 39.4971 | 1218.9252
[7 empty] | 11006 | 7660 | 1296465 | 2015-08-01 12:17 | 2015-08-01 13:39 | 81.7333 | 11kV | 19074.3833 | 234 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN.7900 Campbell St - 11kV Panel 3 " Sub 35022 Campbell Samuel" feeder tripped Relays: A phase timed O/C, Earth Fault, EFI, Fault check relay Signals: 11kV trip, No.1 Tx Group Earth Field EFIs: S35002 UG Fault - 11kV UG fault from ZN7900 campbell St to Sub 35022 Campbell Samuel | August | 2015 | 2016Q1 | 2016 | ZN7900:PA3 | ZN7900:PA3 | ZN07900/000003 | SYDNEY | UG | Not Veg | 2015-08-01 | N | 81.5145 | N | 3 | N | N | 1.1101 | 39.4971 | 13938.9967
[7 empty] | 11668 | 14462 | 1296567 | 2015-08-02 08:46 | 2015-08-02 08:53 | 7 | 11kV | 10325 | 1475 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Secondary Equip | Unplanned | No Weather Impact | N | ZN.15011 Beacon Hill 11kV Panel 10 tripped Relays - Panel 10L: EFI, SEL Panel 10R: SEL Tx#2 Protection Panel: B-phase/fault check relay Signals- 11kV trip, Zone Earth Protection Malfunction- When restoring protection after defective works repaired & completed, Panel#10 @ ZN.15011 Beacon Hill tripped when making SEL auto on Panel#10L | August | 2015 | 2016Q1 | 2016 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | Exclude | Not Veg | 2015-08-02 | N | 7 | N | 1 | N | N | 1.1101 | 39.4971 | 7545.2055
[7 empty] | 11076 | 8425 | 1296754 | 2015-08-03 09:59 | 2015-08-03 11:45 | 106 | 11kV | 48760 | 460 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ZN 3154 St Ives Ex Panel 16 there was a Burnt Bond between LB 3238 and LB 62189 | August | 2015 | 2016Q1 | 2016 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Not Veg | 2015-08-03 | N | 106 | N | 4 | N | N | 1.1101 | 39.4971 | 35632.3698
[7 empty] | 11618 | 13947 | 1296743 | 2015-08-03 09:35 | 2015-08-03 14:55 | 320 | 11kV | 7162 | 59 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Panel 1 "Grants Rd" feeder - 11kV Rec.46763 Grants Keighly 0.3 Tripped, reclosed, tripped and locked out Tree/ branch brought down OH 11kV mains brought down adjacent AB.42606 by tree see 1297469,1297486 and 1297488 | August | 2015 | 2016Q1 | 2016 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2015-08-03 | N | 121.3898 | N | 4 | N | N | 1.1101 | 39.4971 | 5233.7784
[7 empty] | 10853 | 6102 | 1296666 | 2015-08-03 07:47 | 2015-08-03 16:30 | 523 | 11kV | 42266 | 82 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 152864 11kV was found to be touching the x arm at sub 27058. At 11kV link 8365 load side B phase tapping had blown open.also refer to T&R events 1297191 and 1297193 Excluded OMS 1296666, 1296665 and 1296667. | August | 2015 | 2016Q1 | 2016 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Not Veg | 2015-08-03 | N | 515.439 | N | 4 | N | N | 1.1101 | 39.4971 | 30886.7462
[7 empty] | 12085 | 18776 | 1296783 | 2015-08-03 10:25 | 2015-08-03 19:05 | 520 | 11kV | 55640 | 107 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | : FOUND 11KV DROP OUT FUSE OPERATION, ROAD SIDE PHASE AT PT 1062, DIST/VOLTS A-245V, B-250V, C-236V, AB-435V, AC-413V, BC-415V. DOP REQUIRED. PT OUTSIDE 40 HIGGINBOTHAM RD. See OMS 1297493 1296783 | August | 2015 | 2016Q1 | 2016 | ZN129:PA19 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Not Veg | 2015-08-03 | N | 520 | N | 4 | N | N | 1.1101 | 39.4971 | 40660.0709
[7 empty] | 11706 | 14870 | 1297150 | 2015-08-04 03:25 | 2015-08-04 05:05 | 100 | 11kV | 31230 | 390 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1285 Greenacre Park Panel No.35 "Heath St" feeder tripped on Signals: 11kv trip, Zone earth, Tx4 Group Earth Relays: @ Zn1285 Greenacre Park (Pnl 35): translay, I/T receive and fault check. (Pnl 32): fault check @S2420 Bankstown Square No.1: I/T send, Translay EFI's: Zn1285 (Pnl32), S5760 Remarks: UG fault. Suspect cable fault between S4315 Heath St, S5760 The Mall jacobs and S35076 mall Appian | August | 2015 | 2016Q1 | 2016 | ZN1285:PA35 | ZN1285:PA35 | ZN01285/000035 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-08-04 | N | 80.0769 | N | 5 | N | N | 1.1101 | 39.4971 | 22821.9629
[7 empty] | 10654 | 3920 | 1297151 | 2015-08-04 05:24 | 2015-08-04 13:45 | 501 | 11kV | 56112 | 112 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 152871 11kV mains on the ground load side of ABS 40244. Also damaged steel 11kV OH tee to sub 50992. | August | 2015 | 2016Q1 | 2016 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2015-08-04 | N | 501 | N | 5 | N | N | 1.1101 | 39.4971 | 41004.9946
[7 empty] | 10455 | 1349 | 1297415 | 2015-08-04 12:57 | 2015-08-04 14:20 | 83 | 11kV | 32167 | 1781 | HV | Wind Blown Debris | Adverse Weather/Environment | UGOH | Unplanned | No Weather Impact | N | LID 152883 Piece of wire on UGOH pole KR-70458 | August | 2015 | 2016Q1 | 2016 | 264:81236 | 264:81236 | ZN00264/081236 | PORT STEPHENS | OH | Veg | 2015-08-04 | N | 18.0612 | N | 5 | N | N | 1.1101 | 39.4971 | 23506.6948
[7 empty] | 12137 | 19250 | 1297573 | 2015-08-04 17:15 | 2015-08-04 19:15 | 119.9667 | 11kV | 3599 | 30 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 152889 Lidar reportd broken x-arm at pole 5O-80121, Adjacent to PT.72490. Repaired by K Garland. | August | 2015 | 2016Q1 | 2016 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2015-08-04 | N | 119.9667 | N | 5 | N | N | 1.1101 | 39.4971 | 2630.043
[7 empty] | 11121 | 8933 | 1297593 | 2015-08-04 18:32 | 2015-08-04 19:21 | 49 | 11kV | 131271 | 2679 | HV | Staff Other | Utility Process Issue | U/G Cable | Unplanned | No Weather Impact | N | @Zn2310 Punchbowl Panel 34 'Sylvester King George' tripped on: Relays - A phase timed O/C EFI Signals: Zone earth, Tx 5 Group earth & 11kv trip Field EFI's: Nil Abnormal: N/O SwB Close @ Sub 2187 Phillip Hill Remarks: other - details provided. Section of feeder being returned to service out of Campsie Zone DMA. See DAROS #364516A. Dop Keen was in the process of restoring repaired feeder when switching at Sub 274 Wilson Ave Closing Sw/A and opening Sw/B N/O the feeder was across the 2 zones. Punchbowl P#34 and Campsie P#18 | August | 2015 | 2016Q1 | 2016 | ZN2310:PA34 | ZN2310:PA14 | ZN02310/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-08-04 | N | 49 | N | 5 | N | N | 1.1101 | 39.4971 | 95928.975
[7 empty] | 11354 | 11518 | 1297797 | 2015-08-05 10:29 | 2015-08-05 11:02 | 33 | 11kV | 38757 | 1413 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ZN 10991 Blakehurst - Pnl 12 - Trip/reclose, A & C phase IOC and Timed OC, Timing, Lockout, EFI, Field EFI. Centre phase bond burnt off at 11kV UGOH above S 10077. Section of feeder isolated. ME: 1298181. Rest Step: 1298182. Withdrawn: 1297797, 816. | August | 2015 | 2016Q1 | 2016 | ZN10991:PA12 | ZN10991:PA12 | ZN10991/000012 | GEORGES RIVER | OH | Not Veg | 2015-08-05 | N | 27.4289 | N | 4 | N | N | 1.1101 | 39.4971 | 28322.4725
[7 empty] | 11779 | 15712 | 1297715 | 2015-08-05 08:51 | 2015-08-05 11:49 | 178 | 11kV | 5992 | 64 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 152902 Overcurrent; Earth fault Excavator contacted mains near pole EQ-80288. Excluded oms 1297745 and 1297795. | August | 2015 | 2016Q1 | 2016 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2015-08-05 | N | 93.625 | N | 4 | N | N | 1.1101 | 39.4971 | 4378.7769
[7 empty] | 10669 | 4093 | 1298088 | 2015-08-05 20:43 | 2015-08-05 21:30 | 47 | 11kV | 29473 | 721 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S80 Chatswood Panel 21 Tripped on Relays: C phase EF, EFI and Fault Check Signals: 11kV trip Zone Earth and TX11 Group Earth Cause: UG cable Fault from S80 Chatswood to S2471 to S6610 to S7848 See OMS 1298465 1298468 1298467 1298088 | August | 2015 | 2016Q1 | 2016 | ZN80:PA21 | ZN80:PA21 | ZN00080/000021 | LANE COVE | UG | Not Veg | 2015-08-05 | N | 40.8779 | N | 4 | N | N | 1.1101 | 39.4971 | 21537.9991
[7 empty] | 12119 | 19089 | 1298089 | 2015-08-05 20:50 | 2015-08-05 22:00 | 70 | 11kV | 248022 | 7475 | HV | Overload Operational | Utility Process Issue | U/G Cable | Unplanned | Cold <10C | N | ZN15001 Brookvale Panel 2 "Delmar Pittwater" feeder tripped Abnormal - S16703 Griffin Pacific Sw/A Closed & S16863 Oaks Pittwater Temporary Sw/A Open S16794 Howard Av 28 Sw/A open & S16190 Dee Why PDE 25 Sw/D Closed Signals: 11kV Trip Relays: 150TN (EFI), 51C O/C Overload - Circulating current as well as high load caused feeder to trip during load relief switching ZN15006 Panel 9 Circuit Breaker would not close see 1298242,243 1298089, 094,091,092,101,109 | August | 2015 | 2016Q1 | 2016 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | UG | Not Veg | 2015-08-05 | N | 33.1802 | N | 4 | N | N | 1.1101 | 39.4971 | 181247.1622
[7 empty] | 11855 | 16572 | 1298854 | 2015-08-06 14:20 | 2015-08-06 15:30 | 70 | 11kV | 39095 | 629 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN7900 Campbell street 11kV Panel 15 "S.6833 & S.64388" tripped on: Relays: Overcurrent & Earth fault, Earth fault Timed, EFI Flag, Tx#2 Earth Fault Pick-up Signals: Tx#2 Group Earth Field EFI's -Nil UG Fault- @ ZN7900 Campbell street front line feeder fault from Panel 15 to S/W A @ S.64388 Palmer Burton No.1 to S/W A @ S.6833 Belmore Mary See 1298864,1298397,1298432,1298403,1298864,1298856,1298854 | August | 2015 | 2016Q1 | 2016 | ZN7900:PA15 | ZN7900:PA15 | ZN07900/000015 | SYDNEY | UG | Not Veg | 2015-08-06 | N | 62.1542 | N | 2 | N | N | 1.1101 | 39.4971 | 28569.4729
[7 empty] | 11959 | 17617 | 1298534 | 2015-08-06 20:34 | 2015-08-07 00:05 | 211 | 11kV | 85641 | 1301 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | Sub 36300 Balgowlah North Panel 5 "Hope Sydney" opened on Relays: 51N, EFI, FC Signals: Tx1 Group Earth, prtection trip Field EFI operated @ subs: S17148,16758,16759,16505,16506,16517 Fire at S16507 Grandview Aden | August | 2015 | 2016Q1 | 2016 | ZN36300:PA5 | ZN36300:PA5 | ZN36300/000005 | NORTHERN BEACHES | UG | Not Veg | 2015-08-06 | N | 65.8271 | N | 2 | N | N | 1.1101 | 39.4971 | 62583.9168
[7 empty] | 12030 | 18316 | 1298549 | 2015-08-07 02:17 | 2015-08-07 04:50 | 153 | 11kV | 20196 | 132 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | No 1 TX RMCB at S6876 Christie Oxley ex Gore Hill Panel 23 Tripped on Low Gas and No2 TX RMCB Tripped via Parallel Tripping Cause: DOp reports No1 Tx RMCB at S6876 Tripped due to low Gas See OMS 1303109 1298549 1298550 | August | 2015 | 2016Q1 | 2016 | ZN5868:PA23 | ZN187:PA23 | ZN00187/000023 | LANE COVE | Unknown | Not Veg | 2015-08-07 | N | 153 | N | 3 | N | N | 1.1101 | 39.4971 | 14758.6411
[7 empty] | 11867 | 16663 | 1298932 | 2015-08-07 17:40 | 2015-08-07 18:40 | 60 | 11kV | 720 | 12 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 152926 A phase Aph LV tapping from sub fuse burnt off at LV OHM Replaced LV tapping & repaired LV OHM | August | 2015 | 2016Q1 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-08-07 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 11458 | 12334 | 1299558 | 2015-08-07 17:38 | 2015-08-07 19:08 | 90 | 11kV | 90 | 1 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | S4065 Flemington Markets Interrupted as a result of faulty circuit breaker indication. Remarks: while changing over supplies from ex Panel 33 to Sw/B as part of programmed maintenance, supply was interrupted after the Sw/B Cb at S4065 indicated closed but was in fact open. Supply resotred within customers network via customers third supply from S772 | August | 2015 | 2016Q1 | 2016 | ZN2466:PA43 | ZN36000:PA10 | ZN36000/000010 | STRATHFIELD | Unknown | Not Veg | 2015-08-07 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 11116 | 8868 | 1298971 | 2015-08-08 02:51 | 2015-08-08 03:38 | 47 | 11kV | 4465 | 95 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152927 B Phase DOLF : 40 Amp Possum at base of sub pole. Excluded OMS1298971 | August | 2015 | 2016Q1 | 2016 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2015-08-08 | N | 47 | N | 4 | N | N | 1.1101 | 39.4971 | 3262.8903
[7 empty] | 10683 | 4305 | 1298974 | 2015-08-08 06:02 | 2015-08-08 12:30 | 388 | 11kV | 162076 | 452 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At S547 Rockwell Ces - Bz trip on No.2 11kV/415V transformer, Note: //Tripping installed operating HV and LV C/Bs on No.1 and No.2 Transformers Section of 11kV feeder Ex Panel 18 " County Ave etc" ZN 342 Paddington Bucholz trip- Apparent oil leaks on the No.2 transformer @ S 547 Rockwell Cres that allowed Tx to go low oil and operate protection. Refer sub to organize repair and monitor oil leak rate until repaired see 1299910, 1299912,1299913 | August | 2015 | 2016Q1 | 2016 | ZN342:PA18 | ZN342:PA18 | ZN00342/000018 | SYDNEY | UG | Not Veg | 2015-08-08 | N | 358.5752 | N | 4 | N | N | 1.1101 | 39.4971 | 118440.3604
[7 empty] | 12177 | 19677 | 1298992 | 2015-08-08 09:01 | 2015-08-08 13:25 | 264 | 11kV | 9768 | 37 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152930 interrupt to remove tree off ohm | August | 2015 | 2016Q1 | 2016 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2015-08-08 | N | 264 | N | 4 | N | N | 1.1101 | 39.4971 | 7138.1663
[7 empty] | 10923 | 6861 | 1298963 | 2015-08-08 00:24 | 2015-08-08 14:20 | 836 | 11kV | 289284 | 513 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Cold <10C | N | ZN12620 Noraville Panel 2 "Budgewoi" feeder trippped, reclosed, tripped and locked out Relays: C phase Overcurrent and IOC, Relcoser, Lockout Signals: 11kV trip Police report Vechilce Hit pole corner of Budgewoi Rd and Gomul St. Pole snapped and 11kV still in the air with no pole under it but LV ABC on the ground. See 1299313 and 1299317 | August | 2015 | 2016Q1 | 2016 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Not Veg | 2015-08-08 | N | 563.9064 | N | 4 | N | N | 1.1101 | 39.4971 | 211400.2148
[7 empty] | 11001 | 7612 | 1299128 | 2015-08-09 06:47 | 2015-08-09 09:10 | 143 | 11kV | 143 | 1 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152941 A & B Phase DOLF : 20 Amp Possum Excluded oms 1299128 | August | 2015 | 2016Q1 | 2016 |  |  |  |  | OH | Not Veg | 2015-08-09 | N | 143 | N | 2 | N | N | 1.1101 | 39.4971 | 104.5002
[7 empty] | 11225 | 10110 | 1299187 | 2015-08-09 12:02 | 2015-08-09 13:37 | 95 | 11kV | 23655 | 249 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | S15002 Narrabeen Ex Panel 2 "Rickard Anana" feeder Beyond Rec 20112 Kalang Rd Tripped & Reclosed on O/C Ex Panel 2 "Rickard Anana" Feeder beyond USL 20424 Bond Off Cause not Ascertained during trip of the Recloser 20112, Bond Off USL 20424 during the fault on the recloser 20112 See Jobs 1299024, 1299191, 1299187, 1299476 | August | 2015 | 2016Q1 | 2016 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2015-08-09 | N | 95 | N | 2 | N | N | 1.1101 | 39.4971 | 17286.3763
[7 empty] | 11956 | 17611 | 1299352 | 2015-08-10 09:08 | 2015-08-10 11:02 | 114 | 11kV | 264796 | 2394 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S3922 Drummoyne the 11kv Panel 5 "Byrnes Manning, etc" feeder tripped on; Relays: A phase timed, EFI, FC Signals: 11kv trip, Tx1 Group Earth, Zone Earth Field EFI's: Nil Remarks: UG Fault. 11kv UG fault between S.3922 Drummoyne Panel 5, S36165 Byrnes Manning SwA, S2401 Sibbick Eden SwB to S1528 MWS & DB Martin St No1 SwB Ex S3922 Drummoyne Panel 5 "Byrnes Manning, etc" | August | 2015 | 2016Q1 | 2016 | ZN3922:PA5 | ZN3922:PA5 | ZN03922/000005 | INNER WEST | UG | Not Veg | 2015-08-10 | N | 110.6082 | N | 6 | N | N | 1.1101 | 39.4971 | 193505.1066
[7 empty] | 11750 | 15380 | 1300080 | 2015-08-10 16:02 | 2015-08-10 16:09 | 7 | 11kV | 10640 | 1520 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S15004 Newport 11kV Panel 5 " Mitalia Fdr etc" feeder Tripped Relays: E/F, EFI, Fault check Signals: Zone Earth, 11kV trip Field EFIs: CP25772,S16564,S161519,S16521,S15858,S16222,S15109,S16624,S15743,S15994,S16128 Subs Required to follow up: At S47698 suspect EFI operated no access into sub, S16523 failed to operate check EFI operation Abnoram Switching - Closed S/W5960 @ S16040, Opened S/W5963 @ S16038, S16128 in LV // at time of failure reconnecting Daros No 365105 Panel 5 @ S15004 - Failed on energising to RMI (Note all HV switches Open) @ S16128 Paradise Riverview suspect cable or S/W B endbox failure | August | 2015 | 2016Q1 | 2016 | ZN15004:PA5 | ZN15004:PA5 | ZN15004/000005 | NORTHERN BEACHES | UG | Not Veg | 2015-08-10 | N | 7 | N | 6 | N | N | 1.1101 | 39.4971 | 7775.3982
[7 empty] | 10502 | 1992 | 1299869 | 2015-08-10 15:08 | 2015-08-10 18:25 | 197 | 11kV | 294561 | 1749 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | S12570 Avoca Panel 24 "Woodfield Waldron Feeder" Tripped on SEL Lighting/ Surge Arrestor failure at PT12780 Wyuna Branga See 1300245, 1300247, 1300248 | August | 2015 | 2016Q1 | 2016 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2015-08-10 | N | 168.4168 | N | 6 | N | N | 1.1101 | 39.4971 | 215256.4907
[7 empty] | 10513 | 2154 | 1300024 | 2015-08-10 20:00 | 2015-08-10 21:00 | 60 | 11kV | 9060 | 151 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 152951 pin off 11kV OHM job #p0326 | August | 2015 | 2016Q1 | 2016 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2015-08-10 | N | 60 | N | 6 | N | N | 1.1101 | 39.4971 | 6620.7808
[7 empty] | 10746 | 4953 | 1300026 | 2015-08-10 20:50 | 2015-08-11 00:23 | 213.45 | 11kV | 8111.1 | 38 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 152952 tapping burnt off ohm adj rec 74466 CC1: 22-"Refer to SOp" | August | 2015 | 2016Q1 | 2016 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2015-08-10 | N | 213.45 | N | 6 | N | N | 1.1101 | 39.4971 | 5927.3526
[7 empty] | 11948 | 17458 | 1300033 | 2015-08-10 22:52 | 2015-08-11 00:30 | 98 | 11kV | 116823 | 1203 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S2196 Milperra Panel 2 "Bullecourt Horsley No.1" fdr tripped Relays: A phase O/C, EFI Signals: 11kv trip, Zone Earth, Tx3 Group Earth EFI's: S61792, S4534, S6612, S35688 Abnormal: AB290 closed, AB3077 Open, IS3265 Open Remarks: UG fault. Underground cable fault from S35688 Ganmain Treadgold Sw/B to S8702 Ingram Bullecourt Sw/A | August | 2015 | 2016Q1 | 2016 | ZN2196:PA2 | ZN2196:PA2 | ZN02196/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-08-10 | N | 97.1097 | N | 6 | N | N | 1.1101 | 39.4971 | 85370.8027
[7 empty] | 11433 | 12149 | 1300499 | 2015-08-12 08:10 | 2015-08-12 09:23 | 73 | 11kV | 28752 | 394 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN384 Camperdown 11kV Panel 22 "S.5385, S.142, S.7327" feeder tripped Relays: E/F, EFI Signals: 5kV trip, Tx2 GE Field EFI's: S.2358 UG Fault - 5kV feeder tripped from S.2358 Womens College to S.74440 Lander Raglan - Isolated and Earthed. See 1301019, 1301024 Withdrawn: 1300499, 1300506 | August | 2015 | 2016Q1 | 2016 | ZN384:PA22 | ZN384:PA22 | ZN00384/000022 | SYDNEY | UG | Not Veg | 2015-08-12 | N | 72.9746 | N | 6 | N | N | 1.1101 | 39.4971 | 21011.1136
[7 empty] | 11093 | 8671 | 1300813 | 2015-08-12 15:30 | 2015-08-12 18:05 | 155.05 | 11kV | 155.05 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 152985 Single phase DOLF : 10 Amp S/W repaired at POA | August | 2015 | 2016Q1 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2015-08-12 | N | 155.05 | N | 6 | N | N | 1.1101 | 39.4971 | 113.306
[7 empty] | 11351 | 11506 | 1300885 | 2015-08-12 17:57 | 2015-08-12 19:12 | 75 | 11kV | 88349 | 1579 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | ZN384 Camperdown 11kV Panel 43 " Hereford St" feeder tripped on A phase O/C Signals: Tx 1 group earth EFI Field EFI's : Sub 4538 and Sub 2753 UG Fault - Cable fault between Sub 2753 Charles Cross to sub 267 Ross Street to Sub 2783 Mt Vernon Street to Sub 1638 AAP Ross Street. Difficult access at Sub 1638 See 1301168, 1301165, 1300885 | August | 2015 | 2016Q1 | 2016 | ZN384:PA43 | ZN384:PA70 | ZN00384/000070 | SYDNEY | UG | Not Veg | 2015-08-12 | N | 55.9525 | N | 6 | N | N | 1.1101 | 39.4971 | 64562.8433
[7 empty] | 10444 | 1161 | 1300852 | 2015-08-12 16:38 | 2015-08-12 20:00 | 202 | 11kV | 202 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 152983 Single phase DOLF : 10 Amp excluded OMS 1300852 | August | 2015 | 2016Q1 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2015-08-12 | N | 202 | N | 6 | N | N | 1.1101 | 39.4971 | 147.6156
[7 empty] | 12228 | 20224 | 1300828 | 2015-08-12 15:58 | 2015-08-12 22:00 | 362 | 11kV | 6154 | 17 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 152986 A phase tapping burnt off pole 9L-70377 Excluded oms 1300828 | August | 2015 | 2016Q1 | 2016 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2015-08-12 | N | 362 | N | 6 | N | N | 1.1101 | 39.4971 | 4497.1617
[7 empty] | 11756 | 15454 | 1300737 | 2015-08-12 13:20 | 2015-08-12 22:25 | 545 | 11kV | 1635 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 152987 LLC off to sub Excluded OMS 1300737 | August | 2015 | 2016Q1 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2015-08-12 | N | 545 | N | 6 | N | N | 1.1101 | 39.4971 | 1194.8098
[7 empty] | 11710 | 14959 | 1301018 | 2015-08-13 09:16 | 2015-08-13 10:33 | 77 | 11kV | 2582 | 34 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN1788 Matraville 11kV Panel 21 "S.5180, S.7169, S.48354" feeder tripped Relays: E/F, EFI Signals: 11kV trip, Tx3 GE, ZE Field EFI's: S.5180 UG Fault - 11kV feeder at S.5180 Caltex Botany Rd to S.6721 Botany Foreshore Isloted & Earthed ME: 1301568, 1301564 Withdrawn: 1301018, 1301042,1301070,1301075 | August | 2015 | 2016Q1 | 2016 | ZN1788:PA21 | ZN35700:PA12 | ZN35700/000012 | BAYSIDE | UG | Not Veg | 2015-08-13 | N | 75.9412 | N | 2 | N | N | 1.1101 | 39.4971 | 1886.8494
[7 empty] | 10823 | 5715 | 1301317 | 2015-08-13 15:53 | 2015-08-13 17:25 | 92 | 11kV | 149188 | 1694 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN3472 Sefton 11kv VCB panel 33 "S-2771 feeder" tripped on: Relays - O/C + E/F, EFI, E/F check Field EFI's: S2771, 4295, 3921 Signals: Zn E, TX4 GE Remarks: UG fault. 11kv feeder fault from S3921 TILBA st Sw-B to S-1920 Mt Auburn rd Sw-A to S2663 Chestnut Rd Sw-B | August | 2015 | 2016Q1 | 2016 | ZN3472:PA33 | ZN3472:PA33 | ZN03472/000033 | CUMBERLAND | UG | Not Veg | 2015-08-13 | N | 88.0685 | N | 2 | N | N | 1.1101 | 39.4971 | 109022.1901
[7 empty] | 12174 | 19671 | 1301611 | 2015-08-14 10:11 | 2015-08-14 16:10 | 359 | 11kV | 1795 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | Y | EX ZN 9534 Kurnell South - Pnl 18 - Rec 35971 Trip and lock out. 132kV 916 Fdr overhead earth wire fell down into 11kV beyond REC 35971. There was also an interruption on the subtrans side. | August | 2015 | 2016Q1 | 2016 | ZN9534:PA18 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2015-08-14 | Y | 359 | N |  | N | Y | 1.1101 | 39.4971 | 1311.7331
[7 empty] | 11068 | 8281 | 1301875 | 2015-08-15 08:54 | 2015-08-15 13:10 | 256 | 11kV | 183478 | 1817 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | No Weather Impact | N | LID 153018 Feeder opened for safety after phone report from David Barr describing car impacted Kiosk 72234 Ironbark Ave. HV end mostly intact LV end board broken. | August | 2015 | 2016Q1 | 2016 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | Unknown | Not Veg | 2015-08-15 | N | 100.9785 | N | 2 | N | N | 1.1101 | 39.4971 | 134080.3107
[7 empty] | 11830 | 16363 | 1302006 | 2015-08-15 19:33 | 2015-08-15 20:18 | 45 | 11kV | 78255 | 1739 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor ABC | Unplanned | No Weather Impact | N | S15008 Harbord Ex Panel 7 "Curl Curl" tripped OH down - wires down on bridge across curl curl lagoon - no apparent cause, suspect fatigue ME: 1302696 Withdrawn: 1302010, 1302011, 1302009, 1302006 | August | 2015 | 2016Q1 | 2016 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2015-08-15 | N | 45 | N | 2 | N | N | 1.1101 | 39.4971 | 57186.4459
[7 empty] | 11893 | 16916 | 1302475 | 2015-08-17 15:33 | 2015-08-17 16:22 | 49 | 11kV | 53101 | 1092 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN12620 Noraville 11kV VCB panel 10 " Buff Point" feeder tripped on Relays - Bassler relay - trip LED, Targets - 1.2.1 & 5.2.1 Field EFI's - nil Signals - 11kV trip Cause not Ascertained ME: 1302673, 1302674 Withdrawn: 1302475, 1302481, 1302484 | August | 2015 | 2016Q1 | 2016 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Veg | 2015-08-17 | N | 48.6273 | N | 1 | N | N | 1.1101 | 39.4971 | 38804.6446
[7 empty] | 10871 | 6303 | 1302634 | 2015-08-18 08:32 | 2015-08-18 09:50 | 78 | 11kV | 19266 | 317 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S12690 Berkeley Vale - Panel 22L "Teamster Reliance" tripped on: Relays: A Phase IOC, EFI Signals: 11kV trip, Zone Earth, Tx 12 Group Earth EFI's: S.18333, S.18332, S.18372 UG Fault between S.18372 Reliance Fleet and S.14828 Reliance Wyong 0.3 See: 1303100, 1303106 Withdrawn: 1302634,1302686,1302687 | August | 2015 | 2016Q1 | 2016 | ZN12690:PA22 | ZN12690:PA22 | ZN12690/000022 | CENTRAL COAST | UG | Not Veg | 2015-08-18 | N | 60.776 | N | 2 | N | N | 1.1101 | 39.4971 | 14079.0245
[7 empty] | 11055 | 8088 | 1302964 | 2015-08-18 21:42 | 2015-08-18 22:15 | 33 | 11kV | 63723 | 1931 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | ZN9035 Caringbah 11kV Panel 11R "S9420, S9791 feeder tripped Relays: E/ F, EFI Signals: 11kV trip Field EFI's: S9420, S9836, S9357 Possum at PT9579 Kareena President - subs to do visual inspection of HDOs ME:1304039 Withdrawn: 1302964, 1302966 ,1302967 | August | 2015 | 2016Q1 | 2016 | ZN9035:PA11 | ZN9035:PA11 | ZN09035/000011 | SUTHERLAND | OH | Not Veg | 2015-08-18 | N | 33 | N | 2 | N | N | 1.1101 | 39.4971 | 46566.8889
[7 empty] | 11761 | 15496 | 1303364 | 2015-08-19 21:46 | 2015-08-19 23:17 | 91 | 11kV | 84539 | 929 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S342 Paddington Panel 35 " The Clement Waratah etc" feeder tripped on: Relays: EF, EFI Field EFI's: Nil UG Fault - cable failure section of 11kV feeder from S342 Paddington (Panel 35) to S4371 Clement Waratah(s/w A) to S1681 New South Rushcutters (s/w F) ME: 1303429 Secondary: 1303426 Withdrawn: 1303367, 1303364 | August | 2015 | 2016Q1 | 2016 | ZN342:PA35 | ZN342:PA35 | ZN00342/000035 | SYDNEY | UG | Not Veg | 2015-08-19 | N | 91 | N | 1 | N | N | 1.1101 | 39.4971 | 61778.6077
[7 empty] | 12181 | 19705 | 1303371 | 2015-08-20 03:16 | 2015-08-20 04:03 | 47 | 11kV | 94423 | 2009 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | At S36300 Balgowlah Panel 3 tripped on A B and C phase IOC Signals: No1 Group Earth and 11kV Trip Cause: Flashover by possum at ELB61276 O/S22 Waratah St Balgowlah. mains to inspect in daylight 1303371 1303372 | August | 2015 | 2016Q1 | 2016 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2015-08-20 | N | 47 | N | 3 | N | N | 1.1101 | 39.4971 | 69001.5434
[7 empty] | 10765 | 5107 | 1303452 | 2015-08-20 08:48 | 2015-08-20 12:00 | 191.6667 | 11kV | 1150 | 6 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 153051 interrupt to repair wire off pin at pole WB-81103 near sub 13227 | August | 2015 | 2016Q1 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2015-08-20 | N | 191.6667 | N | 3 | N | N | 1.1101 | 39.4971 | 840.3861
[7 empty] | 11889 | 16882 | 1303856 | 2015-08-20 15:41 | 2015-08-20 18:00 | 139 | 11kV | 556 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 153060 10 amp fuse Substation DOLF Operator suspects a fatigued fuse. exclude OMS # 1303856 | August | 2015 | 2016Q1 | 2016 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2015-08-20 | N | 139 | N | 3 | N | N | 1.1101 | 39.4971 | 406.3084
[7 empty] | 10732 | 4765 | 1303969 | 2015-08-21 08:01 | 2015-08-21 10:03 | 122 | 11kV | 130328 | 1231 | HV | 3rd Party Vehicle | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At ZN1610 Homebush Bay Panel No.11 "RAS Showring NOrth etc" feeders tripped on Signals: 11kv trip, Zone Earth, Tx1 Group Earth Relays: B phase OVercurret, Earth fault, EFI Remarks: UG cable damaged by contractor. Excavator hit 11kv underround cable outside 17 Burlington St, Homebush. Cable is between S3304 Burlingon Homebush and S61841 Burlington Rocestor. | August | 2015 | 2016Q1 | 2016 | ZN1610:PA11 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | UG | Not Veg | 2015-08-21 | N | 105.8716 | N | 2 | N | N | 1.1101 | 39.4971 | 95239.8584
[7 empty] | 12176 | 19674 | 1304289 | 2015-08-21 19:33 | 2015-08-21 22:58 | 205 | 11kV | 206065 | 1507 | HV | Animal Possum | Animal | Bond | Unplanned | No Weather Impact | N | LID 153076 6 fault operations Overcurrent; Sensitive Earth Fault ## possum at ELB 61643 caused tapping to open at pole OR-30278 ELB 61643 L/As blackened require replacing. Excluded oms # 1304289 | August | 2015 | 2016Q1 | 2016 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2015-08-21 | N | 136.7386 | N | 2 | N | N | 1.1101 | 39.4971 | 150586.2241
[7 empty] | 10997 | 7561 | 1304391 | 2015-08-22 14:58 | 2015-08-22 20:00 | 302 | 11kV | 78462 | 326 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 153078 2 fault operations 3 phase Overcurrent UGOH fault at pole JT-77031; OHM down at pole JT-71291 Excluded OMS 1304388 | August | 2015 | 2016Q1 | 2016 | 258:80776 | 258:80776 | ZN00258/080776 | NEWCASTLE | Unknown | Unknown | 2015-08-22 | N | 240.681 | N | 2 | N | N | 1.1101 | 39.4971 | 57337.7154
[7 empty] | 11557 | 13237 | 1304423 | 2015-08-22 19:24 | 2015-08-22 20:45 | 81 | 11kV | 21964 | 276 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | ZN12600 Lisarow Panel 12 "Sub 18264 etc" feeder tripped and reclosed Signals: 11kV trip Relays: Aph OC, E/F, EFI Field EFI's: S18264, S18250 UG fault between Sw/B @ sub 18250 Lisarow Shopping Centre No.1, Sw/B @ Sub 62282 Parsons Pacific and Sw/A @ Sub 18078 Pacific Parsons 0.5. Dop Parker and Montague have found a cable has been hit by digging equipment in the Lisarow Plaza shopping centre project construction site. Builder is Stevens Constructions, Site manager is Greg Williams - 0428153192 ME: 1304723, 1304725 Withdrawn: 1304423 | August | 2015 | 2016Q1 | 2016 | ZN12600:PA12 | ZN12600:PA12 | ZN12600/000012 | CENTRAL COAST | UG | Not Veg | 2015-08-22 | N | 79.5797 | N | 2 | N | N | 1.1101 | 39.4971 | 16050.6434
[7 empty] | 12166 | 19556 | 1304442 | 2015-08-23 05:17 | 2015-08-23 08:10 | 173 | 11kV | 140476 | 812 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | S12570 Avoca Zone Ex Panel 37 " The Pickets Scenic 0.7" - Open Bond on roadside at AB41429 ME: 1304626 WIthdrawn: 1304442 | August | 2015 | 2016Q1 | 2016 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2015-08-23 | N | 173 | N | 14 | N | N | 1.1101 | 39.4971 | 102655.7175
[7 empty] | 10635 | 3715 | 1304471 | 2015-08-23 08:44 | 2015-08-23 10:50 | 126 | 11kV | 126 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153095 Single phase DOLF : 10 Amp Excluded OMS 1304471 | August | 2015 | 2016Q1 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2015-08-23 | N | 126 | N | 14 | N | N | 1.1101 | 39.4971 | 92.0771
[7 empty] | 11775 | 15679 | 1304491 | 2015-08-23 10:22 | 2015-08-23 13:35 | 193 | 11kV | 772 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 153100 Single phase Broken LLC dropper Only | August | 2015 | 2016Q1 | 2016 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2015-08-23 | N | 193 | N | 14 | N | N | 1.1101 | 39.4971 | 564.1548
[7 empty] | 11439 | 12188 | 1304494 | 2015-08-23 10:26 | 2015-08-23 13:40 | 194 | 11kV | 5164 | 29 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 153099 3 fault operations Earth fault Mains Down near 8F-10009 | August | 2015 | 2016Q1 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2015-08-23 | N | 178.069 | N | 14 | N | N | 1.1101 | 39.4971 | 3773.6989
[7 empty] | 10530 | 2379 | 1304459 | 2015-08-23 07:41 | 2015-08-23 14:55 | 434 | 11kV | 868 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 153101 Single phase DOLF : 5 Amp | August | 2015 | 2016Q1 | 2016 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2015-08-23 | N | 434 | N | 14 | N | N | 1.1101 | 39.4971 | 634.3088
[7 empty] | 11935 | 17263 | 1304490 | 2015-08-23 10:21 | 2015-08-23 14:58 | 277 | 11kV | 1108 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Replaced blown HV fuse on Sub 51329 exclude OMS 1304490 | August | 2015 | 2016Q1 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-08-23 | N | 277 | N | 14 | N | N | 1.1101 | 39.4971 | 809.6937
[7 empty] | 12167 | 19581 | 1304525 | 2015-08-23 13:47 | 2015-08-23 15:25 | 98 | 11kV | 980 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153102 A & C phase DOLF : 16 Amp Staff patrolled as best as possible, please complete the line patrol when conditions permit. Outage time based on above oms number. Excluded OMS 1304536. | August | 2015 | 2016Q1 | 2016 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2015-08-23 | N | 98 | N | 14 | N | N | 1.1101 | 39.4971 | 716.1551
[7 empty] | 12202 | 19869 | 1304549 | 2015-08-23 15:45 | 2015-08-23 16:45 | 60 | 11kV | 60 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 153103 B phase DOLF : 10 Amp It appears a magpie building a nearby nest may have dropped a short section of wire causing a fault near the b phase arrestor. Excluded OMS # 1305459. | August | 2015 | 2016Q1 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-08-23 | N | 60 | N | 14 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 11751 | 15385 | 1304566 | 2015-08-23 17:04 | 2015-08-23 17:47 | 43 | 11kV | 18406 | 1438 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | ZN14891 Wyong 11kV Panel 5 "Wyong" tripped & reclosed: Relays: IOC B+C phase, Auto- Reclose Lockout Relay, Reclose timing Relay Signals: 11kV trip Field EFI's - RFI line side of USL44800 @ Rec40082 Jilliby tripped, reclosed & locked out Relays: Overcurrent & lockout Tree branch contact - Burnt tree branched removed adjacent to PT18460 Huse Jilliby ME: 1304662, 1304664 Withdrawn: 1304566 | August | 2015 | 2016Q1 | 2016 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2015-08-23 | N | 12.7997 | N | 14 | N | N | 1.1101 | 39.4971 | 13450.5619
[7 empty] | 11642 | 14138 | 1304524 | 2015-08-23 13:18 | 2015-08-23 19:40 | 382 | 11kV | 382 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 153107 Single phase DOLF Surge Diverters | August | 2015 | 2016Q1 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2015-08-23 | N | 382 | N | 14 | N | N | 1.1101 | 39.4971 | 279.1543
[7 empty] | 12247 | 20401 | 1304593 | 2015-08-23 19:57 | 2015-08-23 20:40 | 43 | 11kV | 344 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex. Panel 5 "Sommersby" at ZN 12630 Peats Ridge - At PT14862 Elwyns Linton 11kV HDO fuse 31.5 A roadside phase Tree branch resting on HV bushing @ PT14862 Shroud cover distingerated and non-existant Part of HV Bushing has broken away Region staff to inspect exclude OMS 1304593 | August | 2015 | 2016Q1 | 2016 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2015-08-23 | N | 43 | N | 14 | N | N | 1.1101 | 39.4971 | 251.3851
[7 empty] | 11729 | 15194 | 1304547 | 2015-08-23 15:39 | 2015-08-23 21:30 | 351 | 11kV | 1053 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 153108 Single phase DOLF : 10 Amp Excluded OMS 1304547 | August | 2015 | 2016Q1 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-08-23 | N | 351 | N | 14 | N | N | 1.1101 | 39.4971 | 769.5013
[7 empty] | 11888 | 16874 | 1304685 | 2015-08-24 09:25 | 2015-08-24 10:26 | 61 | 11kV | 87897 | 1461 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S2400 Berowra Panel 231 tripped reclosed tripped and locked out on Relays: A and B phase OC, EFI, Fault Check Note: Recloser CP3202 Pacific South Cowan Tripped aswell Cause; DOp removed branch from 11 KV OH near AB1061. See OMS 1305245 1305247 1304697 1304685 | August | 2015 | 2016Q1 | 2016 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Veg | 2015-08-24 | N | 60.1622 | N | 18 | N | N | 1.1101 | 39.4971 | 64232.5351
[7 empty] | 10778 | 5268 | 1304533 | 2015-08-23 13:47 | 2015-08-24 10:30 | 1242.55 | 11kV | 10880.8 | 16 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 153109 2 defective LA's at sub 70795 LF 74408 operated Mains down found beyond 74408 | August | 2015 | 2016Q1 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2015-08-23 | N | 680.05 | N | 14 | N | N | 1.1101 | 39.4971 | 7951.3677
[7 empty] | 11500 | 12711 | 1304563 | 2015-08-23 16:54 | 2015-08-24 12:35 | 1181 | 11kV | 1181 | 1 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 153105 A Regan confirmed the transformer had failed, possibly due to a lightning strike. A Regan said customer ok to leave out overnight and repalce the transformer tomorrow. Excluded OMS # 1304563. | August | 2015 | 2016Q1 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2015-08-23 | N | 1181 | N | 14 | N | N | 1.1101 | 39.4971 | 863.04
[7 empty] | 10631 | 3673 | 1304730 | 2015-08-24 10:07 | 2015-08-24 13:35 | 208 | 11kV | 1248 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153118 A & C phases : 5 Amp sub 46751 Cph DOLF 5A & LF 40762 Aph 5A DOLF Excluded OMS 1304730 | August | 2015 | 2016Q1 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2015-08-24 | N | 208 | N | 18 | N | N | 1.1101 | 39.4971 | 912.0016
[7 empty] | 12179 | 19695 | 1304923 | 2015-08-24 13:31 | 2015-08-24 14:51 | 79.8667 | 11kV | 8625.6 | 108 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 153123 Emergency repairs at pole KR-90069 | August | 2015 | 2016Q1 | 2016 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2015-08-24 | N | 79.8667 | N | 18 | N | N | 1.1101 | 39.4971 | 6303.3341
[7 empty] | 11798 | 15963 | 1304939 | 2015-08-24 13:30 | 2015-08-24 15:15 | 105 | 11kV | 5460 | 52 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 153119 Wire off pin at pole KS-40067. Cabbage tree RD Excluded OMS 1304939 | August | 2015 | 2016Q1 | 2016 | 229:34986 | 229:34986 | ZN00229/034986 | PORT STEPHENS | OH | Not Veg | 2015-08-24 | N | 105 | N | 18 | N | N | 1.1101 | 39.4971 | 3990.007
[7 empty] | 11120 | 8926 | 1304997 | 2015-08-24 14:50 | 2015-08-24 16:20 | 90 | 11kV | 1080 | 12 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Panel 12- Wyong ZN14891 @ PT18434 Chand 1.0 ,roadside and middle phase 16A HDO's opearted due to lightning exclude OMS 1305976 | August | 2015 | 2016Q1 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2015-08-24 | N | 90 | N | 18 | N | N | 1.1101 | 39.4971 | 789.2321
[7 empty] | 10801 | 5500 | 1305040 | 2015-08-24 15:23 | 2015-08-24 16:20 | 57 | 11kV | 4697 | 1561 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 153127 Trip & reclose 1 fault operation Basler Relay 51B OC/EF Blown LA at sub 5090 (faulty Tx) Excluded oms 1305042 | August | 2015 | 2016Q1 | 2016 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Not Veg | 2015-08-24 | N | 3.009 | N | 18 | N | N | 1.1101 | 39.4971 | 3432.4291
[7 empty] | 11502 | 12715 | 1304928 | 2015-08-24 13:36 | 2015-08-24 16:55 | 199 | 11kV | 73772 | 839 | HV | Vandalism | 3rd Party Impact | Pole | Unplanned | Electrical Storm | N | ZN14892 Charmhaven 11kV feeder Panel 14 " TAvern Pacific" fdr opened on Trip LED, 1.2.1 target, O/C and or E/F, with EFI, fault check relay EFI's down at Subs 18599, 18600, 14932, 14765, 14749, 49500 Vandalism - PT 12988 Thompson Vale Link 1.5 has been cut down by person unknown. PT pole cut with chainsaw 1 meter from ground and copper winding of the TX removed See: 1307611, 1307602, 1307614, 1307597, 1307605, 1307607, 1307613 | August | 2015 | 2016Q1 | 2016 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Not Veg | 2015-08-24 | N | 87.9285 | N | 18 | N | N | 1.1101 | 39.4971 | 53910.4017
[7 empty] | 11147 | 9367 | 1305055 | 2015-08-24 15:48 | 2015-08-24 17:00 | 72 | 11kV | 4824 | 67 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 153134 DOLF : 32 Amp Blown L/A Excluded OMS 1305055 | August | 2015 | 2016Q1 | 2016 | 205:12205 | 214:8669 | ZN00214/008669 | LAKE MACQUARIE | OH | Not Veg | 2015-08-24 | N | 72 | N | 18 | N | N | 1.1101 | 39.4971 | 3525.2369
[7 empty] | 12112 | 19031 | 1304919 | 2015-08-24 13:26 | 2015-08-24 17:15 | 229 | 11kV | 76911 | 424 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | Ex Panel 3 ZN15009 Manly @ S15297 James West Esplanade and S15376 Commonwealth Pde, LV// failed and MG tripped off UGOH fault short circuit - 415V UGOH on cnr of Gilbert and Heuston sts failed. see D&R 363222 See:1305387,1305400, 1305402, 1305403 1305391 Withdrawn:1304919, 1304920, 1304922, 1304932 | August | 2015 | 2016Q1 | 2016 | ZN15009:PA3 | ZN15009:PA3 | ZN15009/000003 | NORTHERN BEACHES | Unknown | Unknown | 2015-08-24 | N | 181.3939 | N | 18 | N | N | 1.1101 | 39.4971 | 56204.2903
[7 empty] | 11534 | 12983 | 1305117 | 2015-08-24 15:45 | 2015-08-24 19:25 | 220 | 11kV | 763 | 543 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153132 Trip & reclose 1 fault operation Overcurrent also on sub 61638:11kV B & C phase DOLF : 10 Amp replaced see OMS 1305117 | August | 2015 | 2016Q1 | 2016 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Veg | 2015-08-24 | N | 1.4052 | N | 18 | N | N | 1.1101 | 39.4971 | 557.5779
[7 empty] | 11260 | 10509 | 1305147 | 2015-08-24 18:48 | 2015-08-24 19:40 | 52 | 11kV | 1092 | 21 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 153141 JOB ISSUED FROM DEPOT (LIDAR REPORT). FAULTY CROSS-ARM POLE GU-12205. ISOLATED AT SW 19737. | August | 2015 | 2016Q1 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2015-08-24 | N | 52 | N | 18 | N | N | 1.1101 | 39.4971 | 798.0014
[7 empty] | 11594 | 13643 | 1305038 | 2015-08-24 15:31 | 2015-08-24 21:15 | 344 | 11kV | 1376 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 153143 A phase DOLF : 10 Amp Excluded OMS REPORT NO 1305038. | August | 2015 | 2016Q1 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2015-08-24 | N | 344 | N | 18 | N | N | 1.1101 | 39.4971 | 1005.5402
[7 empty] | 10651 | 3906 | 1305084 | 2015-08-24 16:29 | 2015-08-24 22:22 | 353 | 11kV | 706 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 153140 DOLF : 10 Amp REPLACE FAULTY TRANSFORMER . Excluded OMS REPORT NO 1305084. | August | 2015 | 2016Q1 | 2016 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2015-08-24 | N | 353 | N | 18 | N | N | 1.1101 | 39.4971 | 515.924
[7 empty] | 12140 | 19267 | 1305170 | 2015-08-24 21:07 | 2015-08-25 00:05 | 178 | 11kV | 356 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 153146 Single Phase DOLF : 3 Amp Replaced 2 x 3A DOLF Excluded OMS 1305170, 1305185 | August | 2015 | 2016Q1 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2015-08-24 | N | 178 | N | 18 | N | N | 1.1101 | 39.4971 | 260.1543
[7 empty] | 11081 | 8472 | 1305088 | 2015-08-24 16:30 | 2015-08-25 01:15 | 525 | 11kV | 1050 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Panel 12- Wyong ZN14891 @ PT12021 Yarramalong Kiddman 3.8 blown HDO's centre and road side phase 15A due to lightning exclude OMS 1305431,1305088,1305116 | August | 2015 | 2016Q1 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2015-08-24 | N | 525 | N | 18 | N | N | 1.1101 | 39.4971 | 767.309
[7 empty] | 11727 | 15163 | 1305352 | 2015-08-24 15:38 | 2015-08-25 02:00 | 622 | 11kV | 1190 | 56 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 153131 1 fault operation T/R Intellirupter; Overcurrent Related sustained outage due to Defective transformer Sub 43130 | August | 2015 | 2016Q1 | 2016 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2015-08-24 | N | 21.25 | N | 18 | N | N | 1.1101 | 39.4971 | 869.6169
[7 empty] | 11163 | 9545 | 1305089 | 2015-08-24 16:33 | 2015-08-25 09:30 | 1017 | 11kV | 2034 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | Replaced A phase 3amp Boric Acid HV fuse on sub HP53429 Note - delayed restoration due to No access due to flood waters. Please attend Tuesday Customer reports that part of the pole had broken off at the top exclude OMS 1305089 | August | 2015 | 2016Q1 | 2016 | 520:48172 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2015-08-24 | N | 1017 | N | 18 | N | N | 1.1101 | 39.4971 | 1486.3872
[7 empty] | 11664 | 14388 | 1305467 | 2015-08-24 17:51 | 2015-08-25 09:50 | 959 | 11kV | 959 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153150 Single phase DOLF : 10 Amp Replaced blown 10amp HV fuse on sub HP07612 Restored 0950 25/08/2015 Note: first call made by customer was 24/08/15 17:51 - no eta was available to give to customer as there was water reported on the roads, delayed restoration due to access issues (water on roads) calls 1 and 2 by customer are attached to momentary record 1305133 | August | 2015 | 2016Q1 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-08-24 | N | 959 | N | 18 | N | N | 1.1101 | 39.4971 | 700.8089
[7 empty] | 11601 | 13715 | 1305413 | 2015-08-25 10:50 | 2015-08-25 11:45 | 55 | 11kV | 110 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 153155 A phase DOLF : 10 Amp Excluded OMS 1305413 | August | 2015 | 2016Q1 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2015-08-25 | N | 55 | N | 5 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 10449 | 1261 | 1305284 | 2015-08-25 08:23 | 2015-08-25 12:05 | 222 | 11kV | 222 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 153156 broken llc dropper Excluded oms 1305284 | August | 2015 | 2016Q1 | 2016 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2015-08-25 | N | 222 | N | 5 | N | N | 1.1101 | 39.4971 | 162.2311
[7 empty] | 10759 | 5063 | 1305303 | 2015-08-25 11:38 | 2015-08-25 12:40 | 62.0667 | 11kV | 993.0667 | 16 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN12630 Peats Ridge Ex Panel 4 " Kulnura" from LB40985 Interrupted for safety reasons - tree branch on OH in Euloo Rd, Peats Ridge near LB40985 | August | 2015 | 2016Q1 | 2016 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2015-08-25 | N | 62.0667 | N | 5 | N | N | 1.1101 | 39.4971 | 725.7038
[7 empty] | 11462 | 12384 | 1305421 | 2015-08-25 10:56 | 2015-08-25 13:17 | 140.75 | 11kV | 13652.75 | 97 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN14144 Wamberal Ex Panel 10L "Waberal Aux No.2" feeder from CP44607 Matcham North Interrupted for safety reasons - Tree on OH Matcham Rd near AB40248 | August | 2015 | 2016Q1 | 2016 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2015-08-25 | N | 140.75 | N | 5 | N | N | 1.1101 | 39.4971 | 9977.027
[7 empty] | 12251 | 20426 | 1305246 | 2015-08-25 07:21 | 2015-08-25 15:05 | 464 | 11kV | 1856 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 153162 A phase DOLF : 10 Amp REPLACED FAULTY ARRESTOR. Excluded OMS REPORT NO 1305246. | August | 2015 | 2016Q1 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-08-25 | N | 464 | N | 5 | N | N | 1.1101 | 39.4971 | 1356.3101
[7 empty] | 10660 | 3968 | 1305734 | 2015-08-26 07:17 | 2015-08-26 09:25 | 128 | 11kV | 128 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 153168 Single phase DOLF : 10 Amp FAILED LA'S REPLACED UNDER PERMIT (0850-0920) Excluded OMS 1305733 | August | 2015 | 2016Q1 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2015-08-26 | N | 128 | N | 7 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 12107 | 19007 | 1305950 | 2015-08-26 13:09 | 2015-08-26 14:30 | 81 | 11kV | 81 | 1 | HV | Overload | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 153176 B & C phase DOLF : 10 Amp DOp found 3A elements in all DOLFs. Replaced with 10A. Volts = 243. | August | 2015 | 2016Q1 | 2016 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2015-08-26 | N | 81 | N | 7 | N | N | 1.1101 | 39.4971 | 59.1924
[7 empty] | 11964 | 17655 | 1306069 | 2015-08-26 17:40 | 2015-08-26 19:24 | 104 | 11kV | 267150 | 2596 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn 262 Marrickville Panel 15 "Harrison Enfield" tripped on Relays: B phase (Earth fault), EFI Signals: Tx 4 and zone earth, 11kv trip Field EFI's: S3058, S2064, S2712 Remarks: UG fault. UG feeder fault between sub 2712 Darley Marrick and sub 8163 St Maroun's School. Dop left switching tag at Sub 2712 | August | 2015 | 2016Q1 | 2016 | ZN262:PA15 | ZN262:PA15 | ZN00262/000015 | INNER WEST | UG | Not Veg | 2015-08-26 | N | 102.9083 | N | 7 | N | N | 1.1101 | 39.4971 | 195225.3404
[7 empty] | 11226 | 10117 | 1306119 | 2015-08-26 19:55 | 2015-08-26 20:35 | 40 | 11kV | 80360 | 2009 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN36300 Balgowlah North 11kV VCB panel 3 " S.17119" feeder tripped on: Relays: O/C + EF, 50 T ABC, INST ABC, Target 1.2.1, UF & FC / EFI Field EFI's: nil Signals: 11kV trip Animals/ Bird Possum at base of pole of LB61276. covers have blown off LB61276. Feeder is back in service. Region to orgainse Inspection/ repairs and replacement of covers. ME:1307562 Withdrawn:1306119, 1306120 | August | 2015 | 2016Q1 | 2016 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2015-08-26 | N | 40 | N | 7 | N | N | 1.1101 | 39.4971 | 58724.7178
[7 empty] | 10756 | 5035 | 1306072 | 2015-08-26 20:39 | 2015-08-26 23:50 | 191 | 11kV | 955 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 153179 Broken 11kV crossarm at pole 8L-90191 | August | 2015 | 2016Q1 | 2016 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2015-08-26 | N | 191 | N | 7 | N | N | 1.1101 | 39.4971 | 697.8858
[7 empty] | 11925 | 17164 | 1306131 | 2015-08-26 23:37 | 2015-08-27 00:45 | 67.6333 | 11kV | 56406.2 | 834 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | ZN 9550 Gwawley Bay - Pnl 1 - Earth Leakage, EFI, Field EFIs. Possum on PT 9636. ME: 1306131. Withdrawn: 1306132. | August | 2015 | 2016Q1 | 2016 | ZN9550:PA1 | ZN9550:PA1 | ZN09550/000001 | SUTHERLAND | OH | Not Veg | 2015-08-26 | N | 67.6333 | N | 7 | N | N | 1.1101 | 39.4971 | 41219.9873
[7 empty] | 11320 | 11141 | 1306133 | 2015-08-26 23:54 | 2015-08-27 05:51 | 357.65 | 11kV | 25035.5 | 70 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153182 No protection operation, 11kV main on ground at pole GQ-14618. Protection malgrade ? | August | 2015 | 2016Q1 | 2016 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2015-08-26 | N | 357.65 | N | 7 | N | N | 1.1101 | 39.4971 | 18295.205
[7 empty] | 11574 | 13414 | 1306494 | 2015-08-27 18:51 | 2015-08-27 21:00 | 129 | 11kV | 129 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 153196 dislocated live line clamp was reconnected Excluded oms 1306494 | August | 2015 | 2016Q1 | 2016 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2015-08-27 | N | 129 | N | 1 | N | N | 1.1101 | 39.4971 | 94.2694
[7 empty] | 11629 | 14038 | 1306523 | 2015-08-28 08:15 | 2015-08-28 11:25 | 190 | 11kV | 570 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 153203 A & C phases DOLF : 10 Amp Aph HV Lead broken away from sub DOLF. Excluded OMS No. 1306523 | August | 2015 | 2016Q1 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2015-08-28 | N | 190 | N | 2 | N | N | 1.1101 | 39.4971 | 416.5392
[7 empty] | 11745 | 15328 | 1306855 | 2015-08-28 22:41 | 2015-08-29 00:20 | 99 | 11kV | 198 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 153206 Repair broken Live Line Clamp Excluded OMD 1306855 | August | 2015 | 2016Q1 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2015-08-28 | N | 99 | N | 2 | N | N | 1.1101 | 39.4971 | 144.6926
[7 empty] | 11996 | 18054 | 1306859 | 2015-08-29 00:41 | 2015-08-29 13:15 | 754 | 11kV | 68893 | 130 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153207 5 fault operationsC phase Earth Fault Sw 47812 trip L/O 0047hrs but did not indicate open on DNMS till 0139hrs OHM down at pole JP-86520 Excluded OMS 1306859 | August | 2015 | 2016Q1 | 2016 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2015-08-29 | N | 529.9462 | N | 3 | N | N | 1.1101 | 39.4971 | 50344.9724
[7 empty] | 11045 | 7982 | 1306965 | 2015-08-29 22:41 | 2015-08-29 23:29 | 48 | 11kV | 13032 | 280 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN188 Zetland Panel 25 "S3457 Allen George" tripped on Relays: EF Timed, EFI, FC Signals: 11kV Trip, ZE, No.2 Group Earth Field EFI's: subs 3457, 6702 UG Fault - The 11kV UG feeder from S6702 Botany Mandible to S1639 Dunning Cre to S123 Johnson Queen has a suspect cable fault- testers required See 1307469, 1307470 Withdrawn: 130965 | August | 2015 | 2016Q1 | 2016 | ZN188:PA25 | ZN188:PA13 | ZN00188/000013 | SYDNEY | UG | Not Veg | 2015-08-29 | N | 46.5429 | N | 3 | N | N | 1.1101 | 39.4971 | 9523.4012
[7 empty] | 10842 | 5962 | 1307111 | 2015-08-30 09:30 | 2015-08-30 10:30 | 60 | 11kV | 180 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 153213 No protection operation , open tapping pole JU-35704 Denison St. | August | 2015 | 2016Q1 | 2016 | 203:8090 | 204:82701 | ZN00204/082701 | NEWCASTLE | OH | Not Veg | 2015-08-30 | N | 60 | N | 2 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 11825 | 16300 | 1306959 | 2015-08-29 22:05 | 2015-08-30 15:20 | 1035 | 11kV | 1035 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 153214 Single phase DOLF : 10 Amp Incompleted by mistake in OMS. Reissued as OMS 1307018. excluded OMS 1306959. | August | 2015 | 2016Q1 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2015-08-29 | N | 1035 | N | 3 | N | N | 1.1101 | 39.4971 | 756.3475
[7 empty] | 10677 | 4239 | 1307064 | 2015-08-30 19:48 | 2015-08-30 22:10 | 141.9833 | 11kV | 425.95 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 153216 B & C phase DOLF : 10 Amp Replaced burnt up DOLF carrier Bph. Please patrol fdr CC1: 11-"Despatch to re-issue" | August | 2015 | 2016Q1 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-08-30 | N | 141.9833 | N | 2 | N | N | 1.1101 | 39.4971 | 311.2717
[7 empty] | 10902 | 6683 | 1307078 | 2015-08-31 02:47 | 2015-08-31 04:54 | 127 | 11kV | 85254 | 678 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1193 Lindfield Panel 27 tripped reclosed tripped and locked out on Signals: 11kV Trip, Tx4 Group Earth Relays: 50TC C phase IOC and LockoutUG cable fault - Suspect cable fault in front line section of cable See OMS1307971 1307974 1307078 | August | 2015 | 2016Q1 | 2016 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | UG | Not Veg | 2015-08-31 | N | 125.7434 | N | 2 | N | N | 1.1101 | 39.4971 | 62301.1086
[7 empty] | 12134 | 19218 | 1307156 | 2015-08-31 12:10 | 2015-08-31 14:35 | 145 | 11kV | 2465 | 17 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153221 A phase 11kV main fallen pole jq-55829. Excluded OMS REPORT NO 1307273. | August | 2015 | 2016Q1 | 2016 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2015-08-31 | N | 145 | N | 2 | N | N | 1.1101 | 39.4971 | 1801.3493
[7 empty] | 11302 | 10970 | 1308009 | 2015-09-02 12:25 | 2015-09-02 17:20 | 295 | 11kV | 1475 | 5 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 153242 car hit pole ks-90068 Lavis Lane Williamtown. section isolated for repairs POLICE RADIO - MICK - MVA - CAR INTO POLE - PERSON TRAPPED IN THE CAR - CAD NO # 999044 . | September | 2015 | 2016Q1 | 2016 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2015-09-02 | N | 295 | N | 1 | N | N | 1.1101 | 39.4971 | 1077.8865
[7 empty] | 10520 | 2282 | 1308245 | 2015-09-03 04:25 | 2015-09-03 14:05 | 580 | 11kV | 143303 | 1569 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 153249 3 fault operations Earth Fault Include OMS 1315570 Exclude OMS 1308245/250/257, 13096264/266/267 | September | 2015 | 2016Q1 | 2016 | 233:82815 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2015-09-03 | N | 91.334 | N | 4 | N | N | 1.1101 | 39.4971 | 104721.6057
[7 empty] | 11290 | 10834 | 1308549 | 2015-09-03 16:17 | 2015-09-03 17:31 | 74 | 11kV | 59334 | 821 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 398 Dulwich Hill - Pnl 29 - B phase OC and Earth Fault, EFI, Field EFIs. 11kV underground fault between S 4307 and S 3314. ME: 1310461. Rest Step: 1310463. Withdrawn: 1308549. | September | 2015 | 2016Q1 | 2016 | ZN398:PA29 | ZN398:PA29 | ZN00398/000029 | INNER WEST | UG | Not Veg | 2015-09-03 | N | 72.2704 | N | 4 | N | N | 1.1101 | 39.4971 | 43359.5371
[7 empty] | 10752 | 5006 | 1308581 | 2015-09-03 19:43 | 2015-09-03 20:19 | 35.9667 | 11kV | 24025.7333 | 668 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN14144 Wamberal 11kV VCB panel 10L "S.18824" feeder tripped re-closed tripped and locked out on: Relays: Inst O/C A+ B phase, feeder reclose relay. Field EFI's : nil Siganls: 11kV trip Tree branch on O/H mains adjcent to PT.13671 Brush old Gosford. | September | 2015 | 2016Q1 | 2016 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2015-09-03 | N | 35.9667 | N | 4 | N | N | 1.1101 | 39.4971 | 17557.2973
[7 empty] | 12046 | 18469 | 1308600 | 2015-09-03 23:57 | 2015-09-04 02:41 | 164 | 11kV | 95760 | 870 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 9252 Jannali - Pnl 25 - Trip/reclose/trip, Earth Fault, EFI, Lockout, Field EFIs. Cause not ascertained. Suspected underground cable. ME: 1310471. Rest Steps: 1310475, 6, 8. Withdrawn: 1308600. | September | 2015 | 2016Q1 | 2016 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | UG | Not Veg | 2015-09-03 | N | 110.069 | N | 4 | N | N | 1.1101 | 39.4971 | 69978.5836
[7 empty] | 10471 | 1632 | 1308619 | 2015-09-04 07:30 | 2015-09-04 08:50 | 80 | 11kV | 160 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 153266 10 amp fuse Substation DOLF Exclude OMS 1308619 | September | 2015 | 2016Q1 | 2016 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-09-04 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 11562 | 13287 | 1308669 | 2015-09-04 09:32 | 2015-09-04 10:36 | 64 | 11kV | 39946 | 1597 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | ZN12570 Avoca 11kV Panel 22 "Sub 62297 Davies Wilma" feeder tripped & reclosed Relays: A + B phase timed O/C Signals: 11kV trip Field EFI's Nil At same time Recloser 46529 Davistown Mundoora tripped & locked out on timed O/C Tree/ branch on 11kV mains near AB.40392 See: 1309160, 1309163, 1309165 Withdrawn: 1308669,1308682 | September | 2015 | 2016Q1 | 2016 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2015-09-04 | N | 25.0131 | N | 3 | N | N | 1.1101 | 39.4971 | 29191.3586
[7 empty] | 11661 | 14373 | 1309189 | 2015-09-04 11:50 | 2015-09-04 11:55 | 5 | 11kV | 185 | 37 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN12620 Noraville 11kV feeder Ex panel 2 " Budgewoi" feeder tripped from LK.41777 to LB.40214 by Dop to restore feeder to normal Interrupted to change BSP Note: life support customers notified | September | 2015 | 2016Q1 | 2016 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Not Veg | 2015-09-04 | N | 5 | N | 3 | N | N | 1.1101 | 39.4971 | 135.1925
[7 empty] | 11122 | 8938 | 1309429 | 2015-09-05 12:02 | 2015-09-05 12:06 | 4 | 11kV | 20 | 5 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn384 Camperdown (11kV) Pnl.66 tripped on: O/C, EF and EFI Field EFIs down at S46773, S5834, S2497 Abormal: Abormal switching due to 5kV to 11kV migration (SAO 360965) UG cable fault from S2497 (SwA) to S48306 (SwB) to S2472 (SWD) - failed on energising to 11kV. See 1309429 1309431 1309432 | September | 2015 | 2016Q1 | 2016 | ZN384:PA36 | ZN384:PA66 | ZN00384/000066 | SYDNEY | UG | Not Veg | 2015-09-05 | N | 4 | N | 3 | N | N | 1.1101 | 39.4971 | 14.6154
[7 empty] | 10890 | 6510 | 1308903 | 2015-09-05 00:17 | 2015-09-05 17:00 | 1003 | 11kV | 67466 | 341 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | No Weather Impact | N | ZN12630 Peats Ridge Ex Panel 1 "Grants Road" feeder - 11 kV IR.63734 George Downes Blood 2.45 tripped on SEF O/ H Down - span of CCT found on the ground beyond LB.48444. Protection malgrading as recloser upstream did not trip. Also Enclosed LB.44577 did not indicate SEF detection. See: 1309222, 228, 227, 226, 231, 239, 241, 240, 237 Withdrawn: 1308904, 903, 946 | September | 2015 | 2016Q1 | 2016 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2015-09-05 | N | 197.8475 | N | 3 | N | N | 1.1101 | 39.4971 | 49302.1629
[7 empty] | 12189 | 19735 | 1309005 | 2015-09-05 20:34 | 2015-09-06 09:00 | 745.7833 | 11kV | 48475.9167 | 65 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 153277 Overhead Mains Insulator - Repairs made at pole WB-53944 also refer to previous failuer 7 mins earlier - OMS 1309210 | September | 2015 | 2016Q1 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2015-09-05 | N | 745.7833 | N | 3 | N | N | 1.1101 | 39.4971 | 35424.7701
[7 empty] | 10507 | 2051 | 1309057 | 2015-09-06 10:39 | 2015-09-06 11:50 | 71 | 11kV | 36843 | 525 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2473 North Sydney Panel 11 Tripped on Relays: Earth Fault With EFI Cause: UG cable fault from S2473 to CP3337 to S6063 See OMS 1310087 1310089 1309057 | September | 2015 | 2016Q1 | 2016 | ZN2473:PA11 | ZN35400:PA68 | ZN35400/000068 | NORTH SYDNEY | UG | Not Veg | 2015-09-06 | N | 70.1771 | N | 2 | N | N | 1.1101 | 39.4971 | 26923.7777
[7 empty] | 10604 | 3271 | 1309131 | 2015-09-07 05:53 | 2015-09-07 09:00 | 187 | 11kV | 1309 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | PT 9424 New Illawarra Rd - HDO B phase (31.5A). Cause not ascertained. Withdrawn: 1309131, 158, 1310169 | September | 2015 | 2016Q1 | 2016 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | OH | Veg | 2015-09-07 | N | 187 | N | 5 | N | N | 1.1101 | 39.4971 | 956.5786
[7 empty] | 10877 | 6368 | 1309310 | 2015-09-07 11:53 | 2015-09-07 13:34 | 100.5667 | 11kV | 37109.1 | 369 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35370 Galston feeder tripped reclosed tripped and locked out on Relays: A and C phase Timed Overcurrent, reclose and lockout Signals: 11kV trip Cause: Tree branch removed off 11kV OH adjacent to PT808 see OMS 1309310 1309358 | September | 2015 | 2016Q1 | 2016 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2015-09-07 | N | 100.5667 | N | 5 | N | N | 1.1101 | 39.4971 | 27118.2357
[7 empty] | 10865 | 6248 | 1309369 | 2015-09-07 13:21 | 2015-09-07 15:15 | 114 | 11kV | 83128 | 1486 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn 72 Five Dock - 11kv Panel No.26 "Sub 46567 Parramatta Davids etc" feeder tripped Relays: Earth fault Signals: 11kv trip, Zone Earth, No.1 & No.3 Group Earths Field EFI's: Remarks: UG fault. Front line fault. Section of 11kv feeder from Sub 72 Five Dock Pnl #26 to Sub 46567 Parramatta Davids tee to Sub 5972 Parramatta Croydon. | September | 2015 | 2016Q1 | 2016 | ZN72:PA26 | ZN35555:PA13 | ZN35555/000013 | INNER WEST | UG | Not Veg | 2015-09-07 | N | 55.9408 | N | 5 | N | N | 1.1101 | 39.4971 | 60747.4905
[7 empty] | 11796 | 15936 | 1309444 | 2015-09-07 15:11 | 2015-09-07 16:40 | 89 | 11kV | 59823 | 778 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | ZN12600 Lisarow Panel 2 " The Chamberlain Taylor 0.1 fdr tripped reclosed and locked out on B phase timed OC and EFI EFI's: S.63243, S.14337, S.14495, S.14494 Lighting / Surge Arrestor on ugoh to S.18040 O'Donnell Woodview 0.9 failed See 1309558, 1309560, 1309559, 1309558 Withdrawn:1309444 | September | 2015 | 2016Q1 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2015-09-07 | N | 76.8933 | N | 5 | N | N | 1.1101 | 39.4971 | 43716.8839
[7 empty] | 11292 | 10863 | 1309118 | 2015-09-06 20:37 | 2015-09-08 05:38 | 1981 | 11kV | 72871 | 1026 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S35500 Top Ryde Panel 27 Tripped Reclosed Tripped and Locked out on Relays: Earth Fault, EFI and Lockout Signals: TX3 Group Earth, 11kV trip Cause: 11kV Feederfault from S7905 Macquarie Hospital to LK2127 Tee S8544 See OMS 1310082 1310084 1310085 1310086 1309118 | September | 2015 | 2016Q1 | 2016 | ZN35500:PA27 | ZN35500:PA27 | ZN35500/000027 | RYDE | UG | Not Veg | 2015-09-06 | N | 71.0244 | N | 2 | N | N | 1.1101 | 39.4971 | 53251.9775
[7 empty] | 12122 | 19127 | 1309574 | 2015-09-08 07:38 | 2015-09-08 09:03 | 85 | 11kV | 154124 | 1996 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN2835 Burwood, 11kv Panel 23L 'S3007, S6676, etc" feeder tripped Relays: 'A' & 'C' phase IOC, E/F, EFI Signals: 11kv trip, Tx2 GE, ZE Field efi s: S3007, S48182, S64517, S64518, S136, S46336, S2812 Remarks: UG fault. 11kv feeder Isolated & Earthed from S2812 Duff Burwood to S2410 Appian Bur to S241 Iceton St | September | 2015 | 2016Q1 | 2016 | ZN2835:PA23 | ZN4853:PA15 | ZN04853/000015 | BURWOOD | UG | Not Veg | 2015-09-08 | N | 77.2164 | N | 2 | N | N | 1.1101 | 39.4971 | 112629.2733
[7 empty] | 10815 | 5642 | 1309521 | 2015-09-07 17:35 | 2015-09-08 14:50 | 1275 | 11kV | 4520 | 5 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn384 Camperdown Pnl.66 (11kV) tripped on: Earth Fault with EFI Abnormal: Defective UG cable from S2497 (Sw A) to S2472 to S48306 UG fault from Pnl 66 to S46773 See 1310059 1310060 1310061 | September | 2015 | 2016Q1 | 2016 | ZN384:PA36 | ZN384:PA66 | ZN00384/000066 | SYDNEY | UG | Not Veg | 2015-09-07 | N | 904 | N | 5 | N | N | 1.1101 | 39.4971 | 3303.0827
[7 empty] | 10564 | 2758 | 1310116 | 2015-09-08 13:56 | 2015-09-08 16:40 | 164 | 11kV | 164 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153300 A phase Aph LL Clamp lead broken away from sub DOLF. Excluded OMS 1309815 | September | 2015 | 2016Q1 | 2016 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2015-09-08 | N | 164 | N | 2 | N | N | 1.1101 | 39.4971 | 119.8464
[7 empty] | 11590 | 13613 | 1310023 | 2015-09-09 04:39 | 2015-09-09 06:30 | 111 | 11kV | 166133 | 1988 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1285 Greenacre Park Panel 31 "ANZAC Dominon etc" feeder has tripped, reclosed, tripped and locked out on: Relays: LHS Earth fault, EFI, Timing relay Signals: 11kv trip, Zone Earth, Tx 4 Group Earth Field EFI's: Nil Remarks: UG fault. UG feeder fault Zn 1285 Greenacre Park Panel 31 to Sub 5729 ANZAC Dominon to Sub 4862 Wangee Water tee to PT 1576 Bromley Av | September | 2015 | 2016Q1 | 2016 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-09-09 | N | 83.5679 | N | 3 | N | N | 1.1101 | 39.4971 | 121405.0963
[7 empty] | 11850 | 16537 | 1310318 | 2015-09-09 17:06 | 2015-09-09 19:45 | 159 | 11kV | 18921 | 119 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 153312 A phase DOLF : 30 Amp Defective Lightning Arrestor Excluded OMS 1310321 | September | 2015 | 2016Q1 | 2016 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2015-09-09 | N | 159 | N | 3 | N | N | 1.1101 | 39.4971 | 13826.9087
[7 empty] | 11639 | 14116 | 1310065 | 2015-09-09 18:43 | 2015-09-09 20:05 | 82 | 11kV | 60423 | 1039 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | At S1673 Turramurra Panel 7tripped on C phase IOC with EFI At PT1561 Footpath Phase HDO fuse Operated cause:Possum committed Hari Kari at PT1561 Daly Derwent. See OMS 1310465 1310467 1310337 1310341 | September | 2015 | 2016Q1 | 2016 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Not Veg | 2015-09-09 | N | 58.155 | N | 3 | N | N | 1.1101 | 39.4971 | 44155.3462
[7 empty] | 12060 | 18582 | 1310699 | 2015-09-10 18:06 | 2015-09-10 19:13 | 67 | 11kV | 33013 | 499 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | Y | At S2635 Epping Panel 46 tripped on SEL Signals: 11kV Trip Cause: Bonds burnt CP351 and CP1124 during restoration of 92J Feeder (refer to event 1310619) See OMS 1310845 | September | 2015 | 2016Q1 | 2016 | ZN2635:PA46 | ZN2635:PA46 | ZN02635/000046 | RYDE | OH | Not Veg | 2015-09-10 | Y | 66.1583 | N |  | N | Y | 1.1101 | 39.4971 | 24124.9267
[7 empty] | 10909 | 6761 | 1310702 | 2015-09-10 18:29 | 2015-09-11 09:40 | 911 | 11kV | 215246 | 1885 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | At Zn262 Marrickville 11kv Pnl 16 "Victoria Sydenham" feeder tripped on: Relays: Earth fault Signals: 11kv trip, Zone and Tx 4 group earth with efi Field efi's: Sub 7843 Abnormal: Tx isolated and in lv parallel at Sub 6973 Remarks: UG fault. No access to Sub 6973 shepherd Chap #1 at the time of feeder failure, but was previously in lv parallel due to Tx fault. See DMA report on Tx @ Sub 6973. Tony Gale contacted to follow up. UG cable fault located between Sub 7843 Victoria Sydenham to Sub 6973 Shephard Chap No.1 | September | 2015 | 2016Q1 | 2016 | ZN262:PA16 | ZN262:PA16 | ZN00262/000016 | INNER WEST | UG | Not Veg | 2015-09-10 | Y | 114.1889 | N |  | N | Y | 1.1101 | 39.4971 | 157295.4281
[7 empty] | 11923 | 17157 | 1310905 | 2015-09-11 11:30 | 2015-09-11 13:25 | 115 | 11kV | 805 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153341 A phase DOLF : 16 Amp Excluded OMS 1310905 | September | 2015 | 2016Q1 | 2016 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2015-09-11 | N | 115 | N | 1 | N | N | 1.1101 | 39.4971 | 588.2703
[7 empty] | 11298 | 10934 | 1311155 | 2015-09-12 14:01 | 2015-09-12 21:02 | 421 | 11kV | 67674 | 668 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN14144 Wamberal 11kV Panel 10 "S.18824 Wamberal Auxillary No.2" tripped: Relays: EFI, SEF Signals: 11kV trip Field EFI's: S.18824, S18802, S48880, S18825 Tree/ branch brought down OH - HV mains down at Matcham Rd, near PT.48782 Matcham Elaine See 1312466, 1312467 Withdrawn: 1311155, 1311157, 1311158, 1311160, 1311167 | September | 2015 | 2016Q1 | 2016 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2015-09-12 | N | 101.3084 | N | 1 | N | N | 1.1101 | 39.4971 | 49454.1632
[7 empty] | 12022 | 18245 | 1311212 | 2015-09-13 01:35 | 2015-09-13 02:25 | 50 | 11kV | 4900 | 98 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | ZN15010 Ex Panel 1 - PT.15443 Dolphin Cr 61 - 11kV 31.5A footpath side drop out fuse operated @ ZN15010 Careel Bay Relays - On Panel No.1 " Sub 16432 & Sub 16428" feeder EFI operated Signals - ZN Earth Possum across Tx bushings. No damage to Tx ME:1312046 Withdrawn:1311212 | September | 2015 | 2016Q1 | 2016 | ZN15010:PA1 | ZN15010:PA24 | ZN15010/000024 | NORTHERN BEACHES | OH | Not Veg | 2015-09-13 | N | 50 | N | 3 | N | N | 1.1101 | 39.4971 | 3580.7755
[7 empty] | 10624 | 3629 | 1311213 | 2015-09-13 03:00 | 2015-09-13 04:14 | 74 | 11kV | 54218 | 740 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S5868 Gore HIll Panel 5 feeder tripped on Relays: Timed earth fault, fault check and EFI Signals: 11kV Trip, No3 Group Earth Zn Earth Cause: 11kV UG cable fault from S8474 Clarendon Dickson to S8156 Hotham Pde 18 to S2379 See OMS 1311351 1311352 1311213 | September | 2015 | 2016Q1 | 2016 | ZN5868:PA5 | ZN5868:PA5 | ZN05868/000005 | WILLOUGHBY | UG | Not Veg | 2015-09-13 | N | 73.2676 | N | 3 | N | N | 1.1101 | 39.4971 | 39620.9152
[7 empty] | 10641 | 3772 | 1311292 | 2015-09-13 21:48 | 2015-09-13 22:33 | 45 | 11kV | 1440 | 32 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153351 A phase DOLF 16 Amp excluded OMS 1311292 | September | 2015 | 2016Q1 | 2016 | 221:11898 | 220:8687 | ZN00220/008687 | LAKE MACQUARIE | OH | Veg | 2015-09-13 | N | 45 | N | 3 | N | N | 1.1101 | 39.4971 | 1052.3095
[7 empty] | 10540 | 2475 | 1311968 | 2015-09-14 18:35 | 2015-09-14 20:00 | 85 | 11kV | 1920 | 24 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn8000 Macquarie Park Panel 4 Tripped reclosed tripped and locked out on Relays: Earth Fault, EFI, Fault Check, Timing and Lockout Cause: Zn80000 Macquarie Park Front Line Feeder fault See OMS 1312007 1311968 | September | 2015 | 2016Q1 | 2016 | ZN8000:PA4 | ZN8000:PA4 | ZN08000/000004 | RYDE | UG | Not Veg | 2015-09-14 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 1403.0794
[7 empty] | 11718 | 15089 | 1311849 | 2015-09-14 14:28 | 2015-09-14 21:20 | 412 | 11kV | 41882 | 524 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | ZN14891 Wyong 11kV Panel 20 " Warnervale West Railway" tripped on Relays: SEF with fault check Signals: 11kV trip, Tx 2 group earth with EFI Field EFI's: sub 18534 and sub 18246 Vehicle Hit the pole at LK43338 cnr Jack Grants Rd and Sparkes Rd in Warnervale. Dop and lineworker isolated, repaired and restored supply. Wires reported down by the RFS starting a grass fire, fire brigade in attendance See 1312074, 1312075 Withdrawn: 1311867, 1311851, 1311849 | September | 2015 | 2016Q1 | 2016 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2015-09-14 | N | 79.9275 | N | 3 | N | N | 1.1101 | 39.4971 | 30606.1303
[7 empty] | 10637 | 3736 | 1311988 | 2015-09-14 23:57 | 2015-09-15 00:40 | 43 | 11kV | 1978 | 46 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | PT 9188 Cowan Scylla - Footpath side HDO (31.5A). Possum on PT transformer. ME: 1312032. Withdrawn: 1311988. | September | 2015 | 2016Q1 | 2016 | ZN9252:PA27 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | OH | Not Veg | 2015-09-14 | N | 43 | N | 3 | N | N | 1.1101 | 39.4971 | 1445.4641
[7 empty] | 11135 | 9218 | 1312026 | 2015-09-15 07:49 | 2015-09-15 08:50 | 61 | 11kV | 488 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 1533355 B phase DOLF : 40 Amp Fuse Fatigue Excluded OMS 1312026 | September | 2015 | 2016Q1 | 2016 | 257:81999 | 257:81999 | ZN00257/081999 | NEWCASTLE | OH | Not Veg | 2015-09-15 | N | 61 | N | 2 | N | N | 1.1101 | 39.4971 | 356.616
[7 empty] | 11142 | 9339 | 1312419 | 2015-09-15 22:54 | 2015-09-16 00:42 | 108 | 11kV | 68624 | 708 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN 10995 Riverwood - Pnl 8 - Trip/reclose/trip, A & C pahse IOC, C phase timed OC, EFI, Field EFIs. DOp patrolled feeder and no cause was found. ME: 1315015. Rest Step: 1315016. Withdrawn: 1312419. | September | 2015 | 2016Q1 | 2016 | ZN10995:PA8 | ZN10995:PA8 | ZN10995/000008 | GEORGES RIVER | OH | Veg | 2015-09-15 | N | 96.9266 | N | 2 | N | N | 1.1101 | 39.4971 | 50148.3951
[7 empty] | 10941 | 7011 | 1312430 | 2015-09-16 06:36 | 2015-09-16 11:25 | 289 | 11kV | 11271 | 39 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | ZN12600 EX Panel 3 "Lisarow High Taylor" 11kV feeder @ PT.12334 Berrys Head Gregory road phase 31.5A HDO blown Fuse Fatigue - fuse failed at crimp ME: 1312856 Withdrawn: 1312430 | September | 2015 | 2016Q1 | 2016 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2015-09-16 | N | 289 | N | 5 | N | N | 1.1101 | 39.4971 | 8236.5144
[7 empty] | 11125 | 9016 | 1312549 | 2015-09-16 10:25 | 2015-09-16 11:52 | 87 | 11kV | 107349 | 1239 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN15001 Brookvale - Panel 6L "Winbourne Rd" tripped on: Relays: B & C phase IOC relay Signals: 11kV trip EFI's: S.16892, 15189, 16948 See: 1312847, 1312848 Withdrawn: 1312549 | September | 2015 | 2016Q1 | 2016 | ZN15001:PA6 | ZN15001:PA6 | ZN15001/000006 | NORTHERN BEACHES | OH | Veg | 2015-09-16 | N | 86.6416 | N | 5 | N | N | 1.1101 | 39.4971 | 78447.4829
[7 empty] | 11871 | 16708 | 1312819 | 2015-09-16 22:03 | 2015-09-16 22:39 | 36 | 11kV | 3204 | 89 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN8100 Green Square 11kV VCB panel 17R "S.35631" feeder tripped on Relays: Panel 17R O/C, EFI Field EFI's: S.35361, S.4355, S.6725 Signals: 11kV trip 11kV U/G fault between S.6725 Bourke Bowden No.1 Sw/ B to S.8193 McEvoey fountain Sw/B to S.7635 Bowden McEvoey Sw/ B | September | 2015 | 2016Q1 | 2016 | ZN8100:PA17 | ZN8100:PA17 | ZN08100/000017 | SYDNEY | UG | Not Veg | 2015-09-16 | N | 36 | N | 5 | N | N | 1.1101 | 39.4971 | 2341.3887
[7 empty] | 11730 | 15195 | 1312815 | 2015-09-16 20:47 | 2015-09-16 22:45 | 118 | 11kV | 9794 | 83 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S2635 Epping Panel 46 tripped, reclosed tripped and locked out on Relays: A and C phase IOC and EFI Signals: Reclose Relay, Trip Cause: Optus cable hit by passing truck caused HV feeder to twist together. Lionsman found damage to OH conductor which has been repaired. Abnormal switching: AB351 Defective and Open. LB 3159 Closed See OMS 1314099 1312815 1312816 | September | 2015 | 2016Q1 | 2016 | ZN2635:PA46 | ZN2635:PA46 | ZN02635/000046 | RYDE | OH | Not Veg | 2015-09-16 | N | 118 | N | 5 | N | N | 1.1101 | 39.4971 | 7157.1663
[7 empty] | 10780 | 5281 | 1312820 | 2015-09-16 22:36 | 2015-09-17 00:29 | 113 | 11kV | 116779 | 1291 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 690 Campsie - Pnl 36 - Earth Leakage, C phase IOC, EFI, Fault Check, Field EFIs. 11kV UG feeder fault between S 3339 to S 3557 to S 3380 to S 2380. ME: 1315018. Rest Steps: 1315019, 20. Withdrawn: 1312820. | September | 2015 | 2016Q1 | 2016 | ZN690:PA36 | ZN690:PA36 | ZN00690/000036 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-09-16 | N | 90.4562 | N | 5 | N | N | 1.1101 | 39.4971 | 85338.6488
[7 empty] | 12212 | 20039 | 1313388 | 2015-09-17 09:00 | 2015-09-17 12:00 | 180 | 11kV | 360 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153397 interrupt to repair stranded wire | September | 2015 | 2016Q1 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-09-17 | N | 180 | N | 11 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 11287 | 10793 | 1313032 | 2015-09-17 11:33 | 2015-09-17 13:22 | 109 | 11kV | 137449 | 1261 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | ZN12610 Long Jetty 11kV Panel 24 " Hammond Park" Tripped, Reclosed & locked out on: Relays: A phase IOC, A & B phase timed OC, EFI, Fault check Signals: 11kV trip, Zone earth, No.3 Group Earth EFI's: LB.44646 Lightning hit Ab.42629 tripping Pnl's 24 & 5. No damage found Me: 1313614 Withdrawn: 1313032, 1313040 | September | 2015 | 2016Q1 | 2016 | ZN12610:PA24 | ZN12610:PA24 | ZN12610/000024 | CENTRAL COAST | OH | Not Veg | 2015-09-17 | N | 109 | N | 11 | N | N | 1.1101 | 39.4971 | 100443.6751
[7 empty] | 10673 | 4130 | 1313036 | 2015-09-17 11:40 | 2015-09-17 14:25 | 165 | 11kV | 330 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153407 5 amp fuse Substation DOLF exclude OMS 1313036 | September | 2015 | 2016Q1 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2015-09-17 | N | 165 | N | 11 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 11924 | 17161 | 1313161 | 2015-09-17 14:07 | 2015-09-17 14:45 | 38 | 11kV | 38 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153408 10 amp fuse exclude OMS 1313161 | September | 2015 | 2016Q1 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2015-09-17 | N | 38 | N | 11 | N | N | 1.1101 | 39.4971 | 27.7693
[7 empty] | 11739 | 15234 | 1313055 | 2015-09-17 11:52 | 2015-09-17 16:05 | 253.15 | 11kV | 4303.55 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153412 20 amp fuse Line DOLF | September | 2015 | 2016Q1 | 2016 | 507:80914 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Veg | 2015-09-17 | N | 253.15 | N | 11 | N | N | 1.1101 | 39.4971 | 3144.9074
[7 empty] | 10579 | 2946 | 1313262 | 2015-09-17 16:28 | 2015-09-17 17:35 | 67 | 11kV | 134 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153414 10 amp fuse Substation DOLF exclude OMS 1313262 | September | 2015 | 2016Q1 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2015-09-17 | N | 67 | N | 11 | N | N | 1.1101 | 39.4971 | 97.9232
[7 empty] | 12109 | 19013 | 1313291 | 2015-09-17 17:19 | 2015-09-17 18:25 | 66 | 11kV | 264 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 153415 10 amp fuse Substation DOLF exclude OMS 1313291 | September | 2015 | 2016Q1 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2015-09-17 | N | 66 | N | 11 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 10715 | 4554 | 1313288 | 2015-09-17 17:13 | 2015-09-17 19:15 | 122 | 11kV | 610 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 153416 10 amp fuse Substation DOLF exclude OMS 1313288 | September | 2015 | 2016Q1 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2015-09-17 | N | 122 | N | 11 | N | N | 1.1101 | 39.4971 | 445.77
[7 empty] | 11185 | 9740 | 1313298 | 2015-09-17 17:52 | 2015-09-17 20:50 | 178 | 11kV | 356 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 153419 10 amp fuse exclude OMS 1313298 | September | 2015 | 2016Q1 | 2016 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2015-09-17 | N | 178 | N | 11 | N | N | 1.1101 | 39.4971 | 260.1543
[7 empty] | 11186 | 9795 | 1313286 | 2015-09-17 17:11 | 2015-09-17 21:50 | 279 | 11kV | 837 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153418 10 amp fuse Substation DOLF exclude OMS 1313286 | September | 2015 | 2016Q1 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2015-09-17 | N | 279 | N | 11 | N | N | 1.1101 | 39.4971 | 611.6549
[7 empty] | 11133 | 9164 | 1313355 | 2015-09-18 03:04 | 2015-09-18 04:33 | 89 | 11kV | 111999 | 1544 | HV | Arcing | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn1287 Revesby 11kv Pnl 3 "Mars Virginius, etc" feeder tripped on Relays: Earth fault, lockout, reclose and fault check Signals: 11kv trip, Tx #1 group earth with efi Field efi's: S5046 Remarks: flashover/arcing. Flashover at ugoh cnr Chamberlain and Courtney roads between AB1783, AB562 and Sub 5049 | September | 2015 | 2016Q1 | 2016 | ZN1287:PA3 | ZN1287:PA3 | ZN01287/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-09-18 | N | 72.5382 | N | 3 | N | N | 1.1101 | 39.4971 | 81845.5658
[7 empty] | 11879 | 16799 | 1313392 | 2015-09-18 08:01 | 2015-09-18 09:43 | 102 | 11kV | 306 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 153422 interrupt to repair broken Live Line Clamp Excluded OMS 13213392 | September | 2015 | 2016Q1 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2015-09-18 | N | 102 | N | 3 | N | N | 1.1101 | 39.4971 | 223.6158
[7 empty] | 11317 | 11092 | 1313301 | 2015-09-17 17:53 | 2015-09-18 09:50 | 957 | 11kV | 6699 | 7 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Snow / Hail Storm | N | ZN14144 Wamberal Ex panel 4L at PT .11694 Collingwood Matcham, foothpath phase HDO operated Lightning/ Surge Arrestor Me:1314025 Withdrawn:1313831 | September | 2015 | 2016Q1 | 2016 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2015-09-17 | N | 957 | N | 11 | N | N | 1.1101 | 39.4971 | 4895.4316
[7 empty] | 10422 | 814 | 1313622 | 2015-09-18 13:18 | 2015-09-18 14:57 | 99 | 11kV | 38898 | 466 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 153427 2 fault operations B phase Instantaneous Earth Fault; Earth Fault Cable fault between Sw 34261 & Sw 34249 Excluded OMS 1313622 | September | 2015 | 2016Q1 | 2016 | 202:34261 | 202:34261 | ZN00202/034261 | NEWCASTLE | UG | Not Veg | 2015-09-18 | N | 83.4721 | N | 3 | N | N | 1.1101 | 39.4971 | 28425.5111
[7 empty] | 12056 | 18550 | 1313829 | 2015-09-19 06:52 | 2015-09-19 09:16 | 144 | 11kV | 3017.8833 | 21 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Light | N | S 10117 Commercial Vanessa - RMI No 2 and RMI No 3 (Both 80A). No 3 Transformer at S 10117 failed in service. LV Bus section was found closed which cuased the fuse on Tx 2 to operate as well. ME: 1315190. Rest Ste: 1315191. GIS: 1313829, 52. Withdrawn: 1313835, 6. | September | 2015 | 2016Q1 | 2016 | ZN10993:PA33 | ZN10993:PA33 | ZN10993/000033 | GEORGES RIVER | UG | Not Veg | 2015-09-19 | N | 143.7087 | N | 2 | N | N | 1.1101 | 39.4971 | 2205.3801
[7 empty] | 11004 | 7630 | 1313830 | 2015-09-19 07:02 | 2015-09-19 16:10 | 548 | 11kV | 108963 | 535 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN12630 Peats Ridge Ex Panel 2 "Gunderman" 11kV feeder at Recloser 45189 Cooks Peats Ridge 0.5 tripped and lock-out Abnormal -Recloser 44945 Lower Mangrove defective with by-pass ABS closed OH down 100 metres of 11kV fdr at PT.12514 Oystershell Wise 8.2 See:1314032, 1314033, 1314034 Withdrawn:1313830, 1313837 | September | 2015 | 2016Q1 | 2016 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2015-09-19 | N | 203.6692 | N | 2 | N | N | 1.1101 | 39.4971 | 79626.9465
[7 empty] | 10776 | 5242 | 1313971 | 2015-09-20 12:32 | 2015-09-20 14:01 | 89 | 11kV | 114547 | 1323 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN1287 Revesby Panel 17 'Hinemoa St' tripped Relays - E/F, Fault check, reclose time, lokcout, efi Singals: 11kv trip, ZE, Tx1 GE Abnormal: S8484 Lucas Henry Sw B closed and AB 14 Open and defective Remarks: UG fault. 11kv ug cable fault from S35325 Lambeth tower to S5035 Sherlock Av | September | 2015 | 2016Q1 | 2016 | ZN1287:PA17 | ZN1287:PA17 | ZN01287/000017 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-09-20 | N | 86.5813 | N | 2 | N | N | 1.1101 | 39.4971 | 83707.569
[7 empty] | 11475 | 12562 | 1313997 | 2015-09-20 18:31 | 2015-09-20 21:35 | 184 | 11kV | 304607 | 2129 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ZN12570 Avoca Zone panel 37L "Avoca Beach" tripped on: SEL 11kV tripped Bond - 11kV roadside bond off at AB.44536, note bond resting on Xarm zoned side. Section of feeder isolated from AB.43413 to AB.44563 tee to PT.11926 Alt Laird placed in LV// links 20952 and 20982 See: 1314042, 1314044, 1314047, 1314045 Withdrawn: 1313997, 1314004 | September | 2015 | 2016Q1 | 2016 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2015-09-20 | N | 143.0752 | N | 2 | N | N | 1.1101 | 39.4971 | 222597.8112
[7 empty] | 10678 | 4256 | 1314151 | 2015-09-21 10:13 | 2015-09-21 11:40 | 87 | 11kV | 29171 | 422 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | ZN3154 St Ives 11kV feeder Panel 14 "Carbeen Killeaton" tripped on: Relays: B phase IOC Signals: 11kV trip, Tx1 group earth and EFI Field EFI's: S.4264 and S.4910 UG cable damaged by contractor between S.4910 Banool Mudies to S.4917 Toolang Warrimoo tee to PT.1417 marlborough Warrimoo at cnr of Warrimoo and Carbeen Rd see:1314408,1314409, 1314411 Withdrawn: 1314151, 1314197 | September | 2015 | 2016Q1 | 2016 | ZN3154:PA14 | ZN3154:PA14 | ZN03154/000014 | KU-RING-GAI | UG | Not Veg | 2015-09-21 | N | 69.1256 | N | 3 | N | N | 1.1101 | 39.4971 | 21317.3064
[7 empty] | 11231 | 10174 | 1314225 | 2015-09-21 12:20 | 2015-09-21 13:40 | 80 | 11kV | 23440 | 293 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 153439 SUB ISOLATED TO REPAIR HV TRACKING AT SW 35144 AVENTINE SUB. Excluded OMS REPORT NO 1314225. | September | 2015 | 2016Q1 | 2016 | 202:34261 | 202:34261 | ZN00202/034261 | NEWCASTLE | UG | Not Veg | 2015-09-21 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 17129.2606
[7 empty] | 11941 | 17320 | 1314053 | 2015-09-21 08:09 | 2015-09-21 17:10 | 541 | 11kV | 703 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | ZN14143 Somersby 11kV feeder Ex Panel 6 " Pinnacle Trennium " at S.14278 Pacific Applied Plastics 11kV/415V LV Tx A phase bushing H/R. T/ Con replaced Tx Include OMS 1315263 Exclude OMS 1314433/34 | September | 2015 | 2016Q1 | 2016 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | OH | Not Veg | 2015-09-21 | N | 234.3333 | N | 3 | N | N | 1.1101 | 39.4971 | 513.7317
[7 empty] | 11559 | 13264 | 1314427 | 2015-09-22 07:40 | 2015-09-22 13:55 | 375 | 33kV Distribution | 927 | 10 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 153449 2 fault operations A & C phase Overcurrent; Earth fault CAR HIT POLE JT-90039. SW 90706 DIR E/FAULT; SW 80507 A PROT = A&C O/C E/F; B PROT E/F Excluded OMS REPORT NO 1314427 & 1314436. | September | 2015 | 2016Q1 | 2016 |  |  |  | NEWCASTLE | OH | Not Veg | 2015-09-22 | N | 92.7 | N | 2 | N | N | 1.1101 | 39.4971 | 677.4243
[7 empty] | 11702 | 14840 | 1314998 | 2015-09-22 09:50 | 2015-09-22 20:20 | 630 | 33kV Distribution | 3405 | 6 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 153455 SUB 59108 ISOLATED TO REPAIR LV BOARD , DAMAGED FROM HV INTO LV EARLIER TODAY. SEE U/P OUTAGE 153449. Excluded OMS REPORT NO 1314809. | September | 2015 | 2016Q1 | 2016 |  |  |  | NEWCASTLE | OH | Not Veg | 2015-09-22 | N | 567.5 | N | 2 | N | N | 1.1101 | 39.4971 | 2488.2736
[7 empty] | 10814 | 5635 | 1315025 | 2015-09-23 10:30 | 2015-09-23 12:55 | 145 | 11kV | 17337 | 237 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | IR64824 Deepwater Holy Tripped and Locked Out Relays: Overcurrent, Lockout Cause: 11kV has come of pin and resting on crossarm between LB62056 to LB62055 tee S3346 Neerim Daymar 11kV Has come into contact with LV - II requested See OMS 1316715 1316717 1315025 1315040 1315068 | September | 2015 | 2016Q1 | 2016 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | OH | Not Veg | 2015-09-23 | N | 73.1519 | N | 5 | N | N | 1.1101 | 39.4971 | 12669.3682
[7 empty] | 10643 | 3786 | 1315160 | 2015-09-23 13:13 | 2015-09-23 13:48 | 35 | 11kV | 45710 | 1306 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 153465 1 fault operation B & C phase Overcurrent This doesn't appear to have reclosed. Please check relay for events and repair as required | September | 2015 | 2016Q1 | 2016 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | OH | Veg | 2015-09-23 | N | 35 | N | 5 | N | N | 1.1101 | 39.4971 | 33403.5198
[7 empty] | 11992 | 17993 | 1315065 | 2015-09-23 11:27 | 2015-09-23 16:45 | 318 | 11kV | 26784 | 233 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153461 3 fault operations C phase Earth Fault; Overcurrent Repaired 11kV main on ground near sub 25064. Excluded OMS 1315065, 1315077 | September | 2015 | 2016Q1 | 2016 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2015-09-23 | N | 114.9528 | N | 5 | N | N | 1.1101 | 39.4971 | 19572.9572
[7 empty] | 10946 | 7079 | 1315283 | 2015-09-23 17:30 | 2015-09-23 17:36 | 6 | 11kV | 6816 | 1136 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153474 After mulitable T & R S.O. opened Fdr 82128 for Dop to remove tree branch from 11kV main at pole SW-10251. | September | 2015 | 2016Q1 | 2016 | 239:82128 | 239:82136 | ZN00239/082136 | LAKE MACQUARIE | OH | Veg | 2015-09-23 | N | 6 | N | 5 | N | N | 1.1101 | 39.4971 | 4980.9318
[7 empty] | 11525 | 12890 | 1315381 | 2015-09-23 20:43 | 2015-09-24 02:00 | 317 | 11kV | 162932 | 1227 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153476 2 fault operation 3 Phase Earth Fault; Overcurrent A prot = E/F trip, BG trip; B Prot = E/F trip ABCph Bph main down at pole IV-71082 HV into LV checked OK by D Myers Excluded OMS 1315381 | September | 2015 | 2016Q1 | 2016 | 239:82132 | 239:82132 | ZN00239/082132 | LAKE MACQUARIE | OH | Veg | 2015-09-23 | N | 132.7889 | N | 5 | N | N | 1.1101 | 39.4971 | 119065.8999
[7 empty] | 12027 | 18298 | 1315554 | 2015-09-24 10:52 | 2015-09-24 11:10 | 18 | 11kV | 29664 | 1648 | HV | Staff Operation | Utility Process Issue | Air Break Switch | Unplanned | No Weather Impact | N | ZN12570 Avoca Ex panel 37L and 24 section of 11kV mains from AB44010 to LB42288 to AB44536 to S.61891 WWPS Ficus Ave No.2 de-energised due to operating error. Abnormal Switching: AB43413 to AB4536 Iso and defective, LB40439 & AB44523 closed, LB42288 open PT12977 in LV// Staff error - Switching listed LB40439 as N/O but LB was closed due to defective mains from AB43413 to AB44536. On de-energising from AB44010, part of panel 37L was de-energised Me: 1315943 Withdrawn:131554, 1315571, 1315563, 1315564 | September | 2015 | 2016Q1 | 2016 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2015-09-24 | N | 18 | N | 6 | N | N | 1.1101 | 39.4971 | 21677.5763
[7 empty] | 11859 | 16617 | 1315492 | 2015-09-24 09:39 | 2015-09-24 12:01 | 142 | 11kV | 568 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Unselected | N | ZN15012 Killarnery 11kV feeder Ex Panel 6L "Killarney West" at Rec.26228 Valley Rd tripped & reclosed Relays: O/C, IOC, L/O Tree branch on OH mains at Roseville Bridge National Park Note: Previous T&R | September | 2015 | 2016Q1 | 2016 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2015-09-24 | N | 142 | N | 6 | N | N | 1.1101 | 39.4971 | 415.0776
[7 empty] | 11188 | 9835 | 1315817 | 2015-09-24 20:30 | 2015-09-24 21:38 | 68 | 11kV | 142677 | 2512 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | At S2635 Epping New 11kV Panel 58 Tripped on Relays: SEL Cause: Open bond on AB1213. 1316588 1316589 1316659 1316663 1315817 1315831 1315833 1315834 | September | 2015 | 2016Q1 | 2016 | ZN2635:PA58 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | OH | Not Veg | 2015-09-24 | N | 56.7982 | N | 6 | N | N | 1.1101 | 39.4971 | 104264.1433
[7 empty] | 11507 | 12762 | 1315810 | 2015-09-24 19:50 | 2015-09-24 22:40 | 170 | 11kV | 2720 | 16 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Wind Storm | N | ZN12630 Peats Ridge section of 11kV feeder Ex Panel 3 " Mangrove Mountain at PT12148 Waratah Wise Ferry footpath HDO operated 20Amp LAS Cause not Ascertained- supply restored ME:1316035 Withdrawn: 1315810, 1315829, 1315841 | September | 2015 | 2016Q1 | 2016 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2015-09-24 | N | 170 | N | 6 | N | N | 1.1101 | 39.4971 | 1987.6958
[7 empty] | 10630 | 3671 | 1315749 | 2015-09-24 19:40 | 2015-09-24 23:50 | 250 | 11kV | 18500 | 74 | HV | Animal Insect | Animal | Pole | Unplanned | No Weather Impact | N | LID 153494 Emergency pole replacement. Pole reported by customer to be eaten away by termites P: HR-61860 Park St, Telarah. Excluded OMS 1315749, 1315811, 1315807, 1315806 | September | 2015 | 2016Q1 | 2016 | 502:48010 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2015-09-24 | N | 250 | N | 6 | N | N | 1.1101 | 39.4971 | 13519.2543
[7 empty] | 11641 | 14133 | 1315851 | 2015-09-24 23:45 | 2015-09-25 14:05 | 860 | 11kV | 345360 | 735 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Rain Heavy | N | At S2835 Burwood 11kv feeder Panel 23 "Wentworth Hornsley" tripped Relays: A phase O/C, and E/F Field EFi's: S3007, S48182 ( after first attempt, due to EFI's as found mislead indication of failure) Note: Delays in locating subs within building sites and mislead with EFI indication Abnormal: DMA feeder 08/09/2015 11kv feeder from S2812 to S2410 to S241, Closed @ S294 and S5784 Remarks: UG fault. 11kv feeder in section from S48182 Oxford Norwood (Sw/B) to S2764 Wynne Ave (SwB) to S64517 Wynne Ave No2 (SwA) by excavator borer O/S 28 Belmore POLICE RADIO CALL PER OMS 1315853 | September | 2015 | 2016Q1 | 2016 | ZN2835:PA23 | ZN4853:PA15 | ZN04853/000015 | BURWOOD | UG | Not Veg | 2015-09-24 | N | 469.8776 | N | 6 | N | N | 1.1101 | 39.4971 | 252378.9016
[7 empty] | 10709 | 4501 | 1316445 | 2015-09-27 10:09 | 2015-09-27 11:50 | 101 | 11kV | 101 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153508 Single phase fuse : 10 Amp Sub supplies cattle shed only. Excluded OMS No. 1316445 | September | 2015 | 2016Q1 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-09-27 | N | 101 | N | 4 | N | N | 1.1101 | 39.4971 | 73.8078
[7 empty] | 10731 | 4731 | 1316638 | 2015-09-27 12:55 | 2015-09-27 14:23 | 88 | 11kV | 880 | 10 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 153510 3 phase cust interupted to make emergency repair to 11kV crossarm | September | 2015 | 2016Q1 | 2016 | 203:8089 | 204:82703 | ZN00204/082703 | NEWCASTLE | OH | Not Veg | 2015-09-27 | N | 88 | N | 4 | N | N | 1.1101 | 39.4971 | 643.078
[7 empty] | 12080 | 18748 | 1316473 | 2015-09-27 14:15 | 2015-09-27 15:15 | 60 | 11kV | 240 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN15012 Kilarney Ex Panel 6L " S.16651 etc" 11kV feeder at Rec.26228 Valley Rd tripped: Relays: O/C , IOC, Lockout Signals: 33kV Tx 2 thermal alarm, CP.26228 Position open, CP.26288 Lockout Field EFI's: Nil Cause not Ascertained - to be reported to DeeWhy O/H Monday Business hours | September | 2015 | 2016Q1 | 2016 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2015-09-27 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 10735 | 4796 | 1316514 | 2015-09-27 22:58 | 2015-09-28 01:35 | 157 | 11kV | 628 | 4 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 153512 Single Phase Repaired broken 11kV conductor to LL Clamp. Excluded OMS 1316514, 1316515 | September | 2015 | 2016Q1 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2015-09-27 | N | 157 | N | 4 | N | N | 1.1101 | 39.4971 | 458.9239
[7 empty] | 10658 | 3938 | 1316519 | 2015-09-28 05:19 | 2015-09-28 06:00 | 41 | 11kV | 123 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 153515 B phase DOLF : 63 Amp DOLF carrier burnt in half, replaced. Excluded OMS 1316519 | September | 2015 | 2016Q1 | 2016 | 214:8671 | 214:8671 | ZN00214/008671 | LAKE MACQUARIE | OH | Not Veg | 2015-09-28 | N | 41 | N | 3 | N | N | 1.1101 | 39.4971 | 89.8848
[7 empty] | 12041 | 18425 | 1316718 | 2015-09-28 12:31 | 2015-09-28 13:09 | 38 | 11kV | 9648 | 261 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN12620 Noraville Ex Panel 11 " Norah Head" 11kV feeder at RE.45050 Magenta tripped and locked out on IOC & OC Cause not Ascertained - Dop patrolled clear See 1317299, 1317301 | September | 2015 | 2016Q1 | 2016 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Veg | 2015-09-28 | N | 36.9655 | N | 3 | N | N | 1.1101 | 39.4971 | 7050.4738
[7 empty] | 11857 | 16604 | 1316880 | 2015-09-28 18:53 | 2015-09-28 20:15 | 82 | 11kV | 820 | 10 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ZN12580 Erina Ex 16R " Robina Kurrajong" 11kV feeder at PT 14420 Lingi Wanani Center phase connection on HDO burnt off. Bond - restored via LV// links 19943, 18690, 16981 Me: 1317289 Withdrawn:1316880, 1316881 | September | 2015 | 2016Q1 | 2016 | ZN12580:PA16 | ZN12580:PA8 | ZN12580/000008 | CENTRAL COAST | OH | Not Veg | 2015-09-28 | N | 82 | N | 3 | N | N | 1.1101 | 39.4971 | 599.2318
[7 empty] | 11053 | 8082 | 1317042 | 2015-09-29 11:17 | 2015-09-29 12:09 | 52 | 11kV | 13728 | 264 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN12620 Noraville Ex Panel 11 " Norah Head" 11kV feeder at RE.45050 Magenta tripped and locked out on IOC & OC Cause not Ascertained - Dop patrolled clear, tripped yesterday, possible faulty recloser, to be checked by region staff | September | 2015 | 2016Q1 | 2016 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Veg | 2015-09-29 | N | 52 | N | 2 | N | N | 1.1101 | 39.4971 | 10032.0175
[7 empty] | 10891 | 6518 | 1317251 | 2015-09-29 19:41 | 2015-09-30 07:35 | 714 | 11kV | 67901 | 1184 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 153540 car hit pole, high into low, pole snapped, sub on ground, section isolated for repair, fdr restored, targets 51BC Excluded oms 1317251, 1317252, 1317253 POLICE RADIO CALLS - SEE OMS 1317251/252 | September | 2015 | 2016Q1 | 2016 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2015-09-29 | N | 57.3488 | N | 2 | N | N | 1.1101 | 39.4971 | 49620.0481
[7 empty] | 11051 | 8043 | 1317263 | 2015-09-30 00:25 | 2015-09-30 10:14 | 588.8667 | 11kV | 1766.6 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ZN12620 Ex Panel 11 " Norah Head" OMS report of arching pole top. Dop found 11kV UG/OH adjacent S.14654 Wilfred Barrett -broken bonds Interrupted for safety Reasons - Section of 11kV isolated from S.14654 Wilfred Barrett Wyuna to open bonds @ UGOH near PT18414 ME:1317266 Withdrawn:1317263 | September | 2015 | 2016Q1 | 2016 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2015-09-30 | N | 588.8667 | N | 2 | N | N | 1.1101 | 39.4971 | 1290.9792
[7 empty] | 11161 | 9501 | 1317607 | 2015-10-01 00:19 | 2015-10-01 06:55 | 396 | 11kV | 222374 | 1581 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Pa24 Feeder tripped and locked out on Relays C phase overcurrent Signals: 11kV Trip. Zone Earth Tx3 Group Earth. Fault beyond AB1988 Caused a bond to fail at AB1988. 1318768 1318769 1318770 1318773 1317607 1317609 | October | 2015 | 2016Q2 | 2016 | ZN129:PA24 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Not Veg | 2015-10-01 | N | 140.654 | N | 1 | N | N | 1.1101 | 39.4971 | 162504.3603
[7 empty] | 11467 | 12438 | 1317572 | 2015-09-30 17:23 | 2015-10-01 12:45 | 1162 | 11kV | 30389 | 101 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153557 22kV mains on ground at pole 8W-20014. Repairs required, left isolated at Links 40764. Excluded oms 1317572, 1317605 | September | 2015 | 2016Q1 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-09-30 | N | 300.8812 | N | 2 | N | N | 1.1101 | 39.4971 | 22207.3849
[7 empty] | 11517 | 12827 | 1318050 | 2015-10-02 09:18 | 2015-10-02 10:55 | 97 | 11kV | 97 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153578 B Phase DOLF : 10 Amp Excluded OMS 1318050 | October | 2015 | 2016Q2 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2015-10-02 | N | 97 | N | 5 | N | N | 1.1101 | 39.4971 | 70.8847
[7 empty] | 11315 | 11068 | 1318013 | 2015-10-02 08:22 | 2015-10-02 11:40 | 198 | 11kV | 28017 | 264 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | ZN12620 Noraville 11kV feeder Ex Panel 11"Norah Head" at Rec.45050 Magenta tripped & locked out: Relays: OC trip, IOC trip, Lockout Signals: 11kV CP.45050 open, CP.45050 lockout Interrupted REC.45050 Magenta @ 0945 A-phase load side links @ REC.45050 Magenta caught on fire Field EFI's: Nil See: 1318831, 1318834, 1318835, 1318836 Withdrawn: 1318013 | October | 2015 | 2016Q2 | 2016 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2015-10-02 | N | 106.125 | N | 5 | N | N | 1.1101 | 39.4971 | 20473.9972
[7 empty] | 12141 | 19276 | 1318162 | 2015-10-02 13:51 | 2015-10-02 15:26 | 95 | 11kV | 52941 | 1149 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn.901 Surry Hills - Pnl.14 tripped on: B Phase O/C and EF, EFI Field EFIs: NIL UG cable fault on frontline section from Pnl.14 to S1226 Bourke Crescent No.2 (Sw A) Also caused LV parallel to fail from S2539 Dist #1 to S5531 Dist #2 See 1318750 LV :1318752 1318169 | October | 2015 | 2016Q2 | 2016 | ZN901:PA14 | ZN901:PA32 | ZN00901/000032 | SYDNEY | UG | Not Veg | 2015-10-02 | N | 46.0757 | N | 5 | N | N | 1.1101 | 39.4971 | 38687.7213
[7 empty] | 11973 | 17695 | 1318214 | 2015-10-02 17:57 | 2015-10-02 18:03 | 6 | 11kV | 1410 | 235 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153586 BAT ON 33KV CAUSED POLE FIRE POLE IP-82890. 11KV ISOLATED FOR FIRE BRIGADE. PLEASE CHECK IF POLE CAP NEEDS REPLACING. Excluded OMS REPORT NO 1318264 & 1318214 | October | 2015 | 2016Q2 | 2016 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2015-10-02 | N | 6 | N | 5 | N | N | 1.1101 | 39.4971 | 1030.3864
[7 empty] | 10475 | 1686 | 1318237 | 2015-10-02 16:52 | 2015-10-03 02:00 | 548 | 11kV | 115598 | 1351 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 153585 SEE ALSO 153584. Car hit pole IS-62320. Replaced 3 x blown 315A fuses LVF 14492. Excluded OMS 1318230 | October | 2015 | 2016Q2 | 2016 | 235:2123 | 235:2123 | ZN00235/002123 | NEWCASTLE | OH | Not Veg | 2015-10-02 | N | 85.5648 | N | 5 | N | N | 1.1101 | 39.4971 | 84475.6088
[7 empty] | 10432 | 1004 | 1318297 | 2015-10-03 07:14 | 2015-10-03 07:45 | 31 | 11kV | 31 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153591 Single Phase DOLF : 10 Amp Excluded OMS 1318297 | October | 2015 | 2016Q2 | 2016 | 238:34137 | 238:34137 | ZN00238/034137 | MAITLAND | OH | Veg | 2015-10-03 | N | 31 | N | 2 | N | N | 1.1101 | 39.4971 | 22.6539
[7 empty] | 11656 | 14305 | 1318388 | 2015-10-03 21:57 | 2015-10-04 00:53 | 176 | 11kV | 1232 | 7 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | ZN12600 Lisarow Ex Panel 2 from AB.44323 to Rec.44605 Ridgeway Rd tee PT.13306 The Ridgeway Awabakil and PT.12757 Awabakil The Ridgeway Interrupted for Safety Reasons to put conductors back on pins ME: 1318741 Withdrawn:1318388 | October | 2015 | 2016Q2 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2015-10-03 | N | 176 | N | 2 | N | N | 1.1101 | 39.4971 | 900.3093
[7 empty] | 11352 | 11508 | 1318450 | 2015-10-04 12:28 | 2015-10-04 13:56 | 88 | 11kV | 171938 | 2044 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn262 Marrickville Panel 42 'Schwebel St" feeder has tripped Signals: 11kv trip, No.1 Tx GE, ZE Relays: EF, EFI, FC Field EFI's: S2063 Remarks: UG fault. UG Fault between Sw/B @ S2063 Schwebel St, Sw/A @ Sub 6291 View Harnett, Sw/A @ S5289 Schwebel Illawarra and Sw/D @ Sub 283 Henson St | October | 2015 | 2016Q2 | 2016 | ZN262:PA42 | ZN262:PA42 | ZN00262/000042 | INNER WEST | UG | Not Veg | 2015-10-04 | N | 84.1184 | N | 2 | N | N | 1.1101 | 39.4971 | 125647.2191
[7 empty] | 10929 | 6907 | 1318477 | 2015-10-04 15:44 | 2015-10-04 21:20 | 336 | 11kV | 149793.3833 | 446 | HV | Fire (Non Ausgrid) | UNKNOWN | 3rd Party Asset | Unplanned | No Weather Impact | N | S1681 New South Rushcutters - TX 1, 2 & 3 tripped on summated O/C with multi trip relay Fire on customers switchboard at 100 Baywater Rd Rushcutters Bay See 1318478 GIS: 1318477 | October | 2015 | 2016Q2 | 2016 | ZN342:PA28 | ZN342:PA28 | ZN00342/000028 | SYDNEY | Unknown | Not Veg | 2015-10-04 | N | 335.8596 | N | 2 | N | N | 1.1101 | 39.4971 | 109464.5864
[7 empty] | 12074 | 18696 | 1318534 | 2015-10-05 00:22 | 2015-10-05 01:55 | 93 | 11kV | 113023 | 1221 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn262 Marrickville 11kv OCB panel 33 "S-4394" feeder tripped on: Relays: Fault check relay, Alstrom O/C, E/F fault relay - IOC, EFI Field EFI's - S4394 Signals - 11kv trip Abnormal: Sw/B closed @ S-1975, Sw-A open @ S-5289 Remarks: UG fault. 11kv feeder fault between Sw/B S4394 Meeks Marrick and Sw-A S36026 Meeks Rd. Dop has left sw tag at S4394. No access to S36026 Meeks Rd behind locked gate had to jump fence to isolate. Region to organise | October | 2015 | 2016Q2 | 2016 | ZN262:PA42 | ZN262:PA42 | ZN00262/000042 | INNER WEST | UG | Not Veg | 2015-10-05 | N | 92.5659 | N | 8 | N | N | 1.1101 | 39.4971 | 82593.8748
[7 empty] | 11326 | 11193 | 1318550 | 2015-10-05 07:44 | 2015-10-05 08:44 | 60 | 11kV | 29874 | 696 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn901 Surry Hills Pnl.8 tripped on: Earth Fault with EFI (P8R) UG cable fault from Pnl.8 to S8825 (swA) to S6423 (Sw A) to CP2917 | October | 2015 | 2016Q2 | 2016 | ZN901:PA8 | ZN7900:PA12 | ZN07900/000012 | SYDNEY | UG | Not Veg | 2015-10-05 | N | 42.9224 | N | 8 | N | N | 1.1101 | 39.4971 | 21831.0381
[7 empty] | 11029 | 7843 | 1318566 | 2015-10-05 10:42 | 2015-10-05 11:26 | 44 | 11kV | 65384 | 1486 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | ZN12600 Lisarow 11kV Panel 9 "Wyoming South" tripped Earth Fault EFI C phase O/C IOC UGOH fault short circuit found on second UGOH out from zone | October | 2015 | 2016Q2 | 2016 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | Unknown | Unknown | 2015-10-05 | N | 44 | N | 8 | N | N | 1.1101 | 39.4971 | 47780.6987
[7 empty] | 10772 | 5191 | 1318590 | 2015-10-05 13:06 | 2015-10-05 14:31 | 85 | 11kV | 149949 | 2090 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | ZN12600 Lisarow 33/11kV Tx2 tripped: Tx2 group bus & Panel 5 Relays: Tx 2 panel: O/C proc relay & multi trip. 11kV group 2 BBP: ABC trip & multi trip Panel 5: E/F & EFI Signals: see DNMS log At Panel 5 " Pacific Parsons" feeder tripped: EF & EFI Interruption on panel 5 sametime prot operation times as BBP group 2 and Tx2 UG fault 11kV UGOH failure on section of 11kV feeder from S.18221 Pacific Parsons 0.1 (SW/B) to AB.40322 See: 1318772, 1318774, 1318776, 1318777, 1318778 Withdrawn: 1318590,1318592, 1318591, 1318594 | October | 2015 | 2016Q2 | 2016 | ZN12600:PA11 | ZN12600:PA11 | ZN12600/000011 | CENTRAL COAST | UG | Not Veg | 2015-10-05 | N | 71.7459 | N | 8 | N | N | 1.1101 | 39.4971 | 109578.3065
[7 empty] | 11723 | 15145 | 1318611 | 2015-10-05 15:13 | 2015-10-05 16:30 | 77 | 11kV | 154 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S7391 Macquarie University No 6 HV Fuse tripped on B phase Cause not ascertained for outage See OMS 1318993 131861 1318612 | October | 2015 | 2016Q2 | 2016 | ZN2635:PA65 | ZN2635:PA65 | ZN02635/000065 | RYDE | OH | Veg | 2015-10-05 | N | 77 | N | 8 | N | N | 1.1101 | 39.4971 | 112.5387
[7 empty] | 11560 | 13266 | 1318600 | 2015-10-05 14:16 | 2015-10-05 17:33 | 197 | 11kV | 137177 | 845 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Ex ZN 10994 Mortdale - IR 6226 Connells Terry - OC. 11kV UGOH fault at S 10728. DOp and Lineworker cut away UGOH and restored supply. ME: 1318785. Rest Steps: 1318786, 7. Withdrawn: 1318600, 2. | October | 2015 | 2016Q2 | 2016 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | Unknown | Unknown | 2015-10-05 | N | 162.3396 | N | 8 | N | N | 1.1101 | 39.4971 | 100244.9056
[7 empty] | 10741 | 4869 | 1318626 | 2015-10-05 16:19 | 2015-10-06 01:52 | 573 | 11kV | 12695 | 39 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | ZN14143 Somersby Ex Panel 17 "Wise ferry Somersby 2.0" 11kV tripped at Rec.45037 UGOH fault short circuit failure in Dawson St, staff called out to carry repairs 2 PT's interrupted ME:1318861, 1318863 Withdrawn: 1318626 | October | 2015 | 2016Q2 | 2016 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | Unknown | Unknown | 2015-10-05 | N | 325.5128 | N | 8 | N | N | 1.1101 | 39.4971 | 9277.1316
[7 empty] | 11365 | 11597 | 1318671 | 2015-10-06 | 2015-10-06 02:00 | 120 | 11kV | 104992 | 911 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 pennant Hills Panel 26 Tripped reclosed tripped and locke dout on Relays: Earth Fault, Timing , Lockout and EFI Field EFIs: NIL Signals: 11kV Trip Cause: 11kV UG fault between S6153 - S2896 - S4988 - S4491 See OMS 1318712 1318715 1318671 | October | 2015 | 2016Q2 | 2016 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | UG | Not Veg | 2015-10-06 | N | 115.2492 | N | 9 | N | N | 1.1101 | 39.4971 | 76725.0569
[7 empty] | 11938 | 17271 | 1322428 | 2015-10-06 01:50 | 2015-10-06 03:51 | 121 | 11kV | 121 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | At S4219 MWS and DB Ryde Pump. Tripped off with no relay operations Restoration time assumed | October | 2015 | 2016Q2 | 2016 |  |  |  | RYDE | UG | Not Veg | 2015-10-06 | N | 121 | N | 9 | N | N | 1.1101 | 39.4971 | 88.4232
[7 empty] | 11167 | 9579 | 1318820 | 2015-10-06 10:24 | 2015-10-06 12:02 | 98 | 11kV | 55400 | 592 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 37 Tripped on A and C phase OC Cause: UG cable Fault Truynk section see related 1327456/1327458 1327459 1327461 1327462 1318819/820/823/827/833/865 | October | 2015 | 2016Q2 | 2016 | ZN965:PA37 | ZN965:PA37 | ZN00965/000037 | HORNSBY | UG | Not Veg | 2015-10-06 | N | 93.5811 | N | 9 | N | N | 1.1101 | 39.4971 | 40484.686
[7 empty] | 12232 | 20254 | 1318912 | 2015-10-06 12:14 | 2015-10-06 16:59 | 285 | 11kV | 14545 | 61 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 153612 Car hit pole HU90047. section isolated and repaired under AP Excluded OMS No. 1318862 + 1318912 | October | 2015 | 2016Q2 | 2016 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2015-10-06 | N | 238.4426 | N | 9 | N | N | 1.1101 | 39.4971 | 10629.057
[7 empty] | 11192 | 9872 | 1319092 | 2015-10-06 15:54 | 2015-10-06 18:30 | 156.3667 | 11kV | 312.7333 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At S7391 Macquarie University High voltage fuse blown cause not ascertained for failure | October | 2015 | 2016Q2 | 2016 | ZN2635:PA65 | ZN2635:PA65 | ZN02635/000065 | RYDE | OH | Not Veg | 2015-10-06 | N | 156.3667 | N | 9 | N | N | 1.1101 | 39.4971 | 228.5363
[7 empty] | 11896 | 16923 | 1319068 | 2015-10-06 15:37 | 2015-10-06 20:40 | 303 | 11kV | 303 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | AT Sub 61188 Boorea Nyrang #3 11kv RMCB tripped on A phase diff (fuse relay) Remarks: other - details provided. Suspect transformer fault (1500kva). Dop and T/Con assisted and restored supply | October | 2015 | 2016Q2 | 2016 | ZN1068:PA11 | ZN1068:PA19 | ZN01068/000019 | CUMBERLAND | UG | Not Veg | 2015-10-06 | N | 303 | N | 9 | N | N | 1.1101 | 39.4971 | 221.4235
[7 empty] | 12005 | 18101 | 1319183 | 2015-10-06 20:45 | 2015-10-06 23:09 | 144 | 11kV | 11376 | 79 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 153615 No Protection operation. Section isolated to repair Crossarm on pole IS-82084 Excluded OMS 1319183 | October | 2015 | 2016Q2 | 2016 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2015-10-06 | N | 144 | N | 9 | N | N | 1.1101 | 39.4971 | 8313.2453
[7 empty] | 11695 | 14766 | 1319192 | 2015-10-07 00:06 | 2015-10-07 01:06 | 60 | 11kV | 68640 | 1144 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN 10991 Blakehurst - Pnl 13 - Trip/reclose/trip, C phase IOC and timed OC, lockout, EFI. Possum found under OH during feeder patrol. ME: 1319192. Withdrawn: 1319193. | October | 2015 | 2016Q2 | 2016 | ZN10991:PA13 | ZN10991:PA13 | ZN10991/000013 | GEORGES RIVER | OH | Not Veg | 2015-10-07 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 50160.0875
[7 empty] | 10662 | 4009 | 1318931 | 2015-10-06 12:24 | 2015-10-07 03:00 | 876 | 11kV | 2148 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | ZN14143 Somersby 11kV Ex Panel 6 "Pinnacle Triennium" feeder @ Sub14278 Pacific Applied Plastic tripped - HV fuse operated Tx Failure - Dop advised connection box where Tx Bushing are connected to conductor was open. On attempting to restore 11kV/415V Tx @ S.14278 Pacific Applied Plastics, Dop unable to close Tx switch, 11kV RMI @ S.14278 taken OOS for TCon to investigate Include OMS 1321193 Exclude OMS 1320095/96 | October | 2015 | 2016Q2 | 2016 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | UG | Not Veg | 2015-10-06 | N | 716 | N | 9 | N | N | 1.1101 | 39.4971 | 1569.695
[7 empty] | 12145 | 19327 | 1319195 | 2015-10-06 19:37 | 2015-10-07 05:40 | 603 | 11kV | 8653 | 32 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153616 C phase DOLF : 20 Amp wires down at LF 6903 section opened off to make repairs Excluded oms # 1319168 + 1319174 | October | 2015 | 2016Q2 | 2016 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2015-10-06 | N | 270.4062 | N | 9 | N | N | 1.1101 | 39.4971 | 6323.3572
[7 empty] | 10819 | 5693 | 1318642 | 2015-10-05 18:18 | 2015-10-07 17:20 | 2822 | 11kV | 15067 | 156 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 153600 2 fault operations Earth fault faulty UGOH feeding sub 27332 Barnum E fault level = 680A Excluded oms 1318642 | October | 2015 | 2016Q2 | 2016 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | Unknown | Unknown | 2015-10-05 | N | 96.5833 | N | 8 | N | N | 1.1101 | 39.4971 | 11010.5192
[7 empty] | 11486 | 12627 | 1319554 | 2015-10-07 15:52 | 2015-10-07 18:12 | 140 | 11kV | 112601 | 1002 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | ZN 10999 Kogarah - Pnl 7 - Trip/reclose/trip, B & C phase OC, Earth fault check. DOp patrolled and found nothing. AB 30077 fell apart whilst breaking up feeder on restoration. ME: 1319661. Rest Step: 1319662. WIthdrawn: 1319554, 57, 60. | October | 2015 | 2016Q2 | 2016 | ZN10999:PA7 | ZN10999:PA7 | ZN10999/000007 | BAYSIDE | OH | Veg | 2015-10-07 | N | 112.3762 | N | 3 | N | N | 1.1101 | 39.4971 | 82285.4896
[7 empty] | 10872 | 6306 | 1319618 | 2015-10-07 20:46 | 2015-10-07 23:14 | 148 | 11kV | 92170 | 841 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN14892 Charmhaven - Panel 14" Tavern Pacific" 11kV feeder tripped on: 51 ABC O/C EFI Fault check - Tx 2 Prot B EF check Signals: 11kV trip Cause not Ascertained - patrol in daylight See: 1320108, 1320109, 1320110, 1320111 Withdrawn: 1319618 | October | 2015 | 2016Q2 | 2016 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Veg | 2015-10-07 | N | 109.5957 | N | 3 | N | N | 1.1101 | 39.4971 | 67355.1174
[7 empty] | 11715 | 15060 | 1319855 | 2015-10-08 12:18 | 2015-10-08 14:25 | 127 | 11kV | 59372 | 874 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 153644/02 1 fault operation A & B phases Overcurrent; Earth Fault Sw 8676 New Lambton sub = A & B O/C & E/F Sw 8676 Reclose Function on Non Auto for SI 9157. | October | 2015 | 2016Q2 | 2016 | 210:8676 | 210:83474 | ZN00210/083474 | NEWCASTLE | OH | Not Veg | 2015-10-08 | N | 67.9314 | N | 2 | N | N | 1.1101 | 39.4971 | 43387.3064
[7 empty] | 10748 | 4985 | 1319994 | 2015-10-08 18:41 | 2015-10-08 19:30 | 49 | 11kV | 30232 | 700 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 10993 Hurstville North - Pnl 33 - Trip/reclose/trip, Earth fault, Timing, lockout, EFI, Field EFIs. Underground cable fault from S 10275 to S 10944. ME: 1322588. Rest Step: 1322589. Withdrawn: 1319994. | October | 2015 | 2016Q2 | 2016 | ZN10993:PA33 | ZN10993:PA33 | ZN10993/000033 | GEORGES RIVER | UG | Not Veg | 2015-10-08 | N | 43.1886 | N | 2 | N | N | 1.1101 | 39.4971 | 22092.6539
[7 empty] | 11733 | 15203 | 1320295 | 2015-10-09 17:11 | 2015-10-09 18:00 | 49 | 11kV | 245 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153661 sub isolated to replace LV service Excluded oms 1320226 | October | 2015 | 2016Q2 | 2016 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2015-10-09 | N | 49 | N | 1 | N | N | 1.1101 | 39.4971 | 179.0388
[7 empty] | 10742 | 4876 | 1320427 | 2015-10-10 06:01 | 2015-10-10 07:05 | 64 | 11kV | 3968 | 62 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153663 A phase DOLF : 40 Amp possum on Transformer Excluded OMS 1320427 | October | 2015 | 2016Q2 | 2016 | 227:13016 | 227:13016 | ZN00227/013016 | LAKE MACQUARIE | OH | Not Veg | 2015-10-10 | N | 64 | N | 4 | N | N | 1.1101 | 39.4971 | 2899.6974
[7 empty] | 10784 | 5324 | 1320454 | 2015-10-10 10:00 | 2015-10-10 13:00 | 180 | 11kV | 360 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153669 B Phase DOLF : 16 Amp Burnt up DOLF DOLF carrier contacts loose/burnt. Excluded OMS No. 1320454 | October | 2015 | 2016Q2 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2015-10-10 | N | 180 | N | 4 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 11312 | 11056 | 1320495 | 2015-10-10 13:16 | 2015-10-10 15:32 | 136 | 11kV | 64942 | 492 | HV | Bushfire | Adverse Weather/Environment | Lightning Arrestor | Unplanned | No Weather Impact | N | ZN14143 Somersby Ex pnl 17 "Somersby Falls" 11kV feeder at Recloser 45202 Pacific Ashbrooke 2.0 tripped on O/C Signals: Tx2 group earth and EFI on Pnl 17 @ Somersby Bushfire - Back buring near Rec 44961 Morgan Pacific 0.4 caused flashover on Bypass AB @ Rec 44961 as confirmed by firefighters on site. Surge Arrestors require replacement in section of 11kV between AB 40581 and Rec 44981 as fdr failed on restoration. See:1321739,, 1321741, 1321742, 1321746 Withdrawn: 1320495, 1320498 | October | 2015 | 2016Q2 | 2016 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2015-10-10 | N | 131.9959 | N | 4 | N | N | 1.1101 | 39.4971 | 47457.6981
[7 empty] | 10835 | 5880 | 1320527 | 2015-10-10 17:30 | 2015-10-10 18:56 | 86 | 11kV | 100350 | 1250 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 9900 Menai - Pnl 8 - Trip/reclose/trip, Earth fault, Lockout, EFI, Field EFIs. Underground fault in 11kV feeder from S 9513 to S 9045. ME: 1322577. Rest Step: 1322578. Withdrawn: 1320527. | October | 2015 | 2016Q2 | 2016 | ZN9900:PA8 | ZN9900:PA8 | ZN09900/000008 | SUTHERLAND | UG | Not Veg | 2015-10-10 | N | 80.28 | N | 4 | N | N | 1.1101 | 39.4971 | 73332.8202
[7 empty] | 11096 | 8683 | 1320594 | 2015-10-11 06:28 | 2015-10-11 08:33 | 125 | 11kV | 99297 | 870 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN 9252 Jannali - Pnl 25 - Trip/reclose/trip, EFI, Lockout, Field EFIs. DOp patrolled and found nothing. ME: 1322620. Rest Steps: 1322621, 2. Withdrawn: 1320594. | October | 2015 | 2016Q2 | 2016 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | OH | Veg | 2015-10-11 | N | 114.1345 | N | 16 | N | N | 1.1101 | 39.4971 | 72563.3188
[7 empty] | 12002 | 18077 | 1320669 | 2015-10-11 10:01 | 2015-10-11 12:00 | 119 | 11kV | 46234 | 486 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | No Weather Impact | N | ZN 9550 Gwawley Bay - Pnl 33 - Instantaneous Earth Fault, All phases Timed OC, EFI, Field EFIs. Vehicle hit S 64822 Kiosk. Direct distributor not restored. Customer advised to get their own generator as per Peter Shori. ME: 1322600. Rest Steps: 1322602, 3. Withdrawn: 1320669, 77, 79. | October | 2015 | 2016Q2 | 2016 | ZN9550:PA33 | ZN9550:PA33 | ZN09550/000033 | SUTHERLAND | Unknown | Not Veg | 2015-10-11 | N | 95.1317 | N | 16 | N | N | 1.1101 | 39.4971 | 33786.4435
[7 empty] | 11736 | 15222 | 1320686 | 2015-10-11 10:46 | 2015-10-11 13:38 | 172 | 11kV | 93524 | 728 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 9252 Jannali - Pnl 25 - Trip/reclose/trip, A & C phase OC, EFI. Underground fault between S 48498 to S 9987. ME: 1324900. Rest Step: 1324901. Withdrawn: 1320686. | October | 2015 | 2016Q2 | 2016 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | UG | Not Veg | 2015-10-11 | N | 128.467 | N | 16 | N | N | 1.1101 | 39.4971 | 68344.5807
[7 empty] | 11457 | 12326 | 1320743 | 2015-10-11 16:08 | 2015-10-11 17:49 | 101 | 11kV | 29492 | 292 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN14892 Charmhaven 11kV Pnl 5 " Sub 14804 Arazona Borg" feeder tripped (Note: CB charged but did not close) Relays: B + C phase timed O/C, EFI Signals: 11kV trip Lightning - feeder to be patrolled by Dop Me:1322067 Withdrawn:1320746 | October | 2015 | 2016Q2 | 2016 | ZN14892:PA5 | ZN14892:PA5 | ZN14892/000005 | CENTRAL COAST | OH | Not Veg | 2015-10-11 | N | 101 | N | 16 | N | N | 1.1101 | 39.4971 | 21551.8837
[7 empty] | 11979 | 17812 | 1320758 | 2015-10-11 16:18 | 2015-10-11 18:05 | 107 | 11kV | 235091 | 2233 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN14892 Charmhaven 11kV Pnl 16 " Charmhaven Ran Remo" feeder tripped, reclosed & locked out Relays: A+ B phase O/C, EFI, reclose, timing & lockout relays Signals: 11kV trip Lightning - feeder to be patrolled by Dop See: 1322071, 1322072 Withdrawn: 1320765, 1320758 | October | 2015 | 2016Q2 | 2016 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Not Veg | 2015-10-11 | N | 105.2803 | N | 16 | N | N | 1.1101 | 39.4971 | 171797.5688
[7 empty] | 10611 | 3403 | 1320744 | 2015-10-11 16:09 | 2015-10-11 18:17 | 128 | 11kV | 107648 | 841 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN14892 Charmhaven 11kV Pnl 14 " Sub 118599 Tavern Pacific" feeder tripped Relays:A+ B + C phase timed O/C, EFI Signals: 11kV trip Lightning - feeder to be patrolled by Dop | October | 2015 | 2016Q2 | 2016 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Not Veg | 2015-10-11 | N | 128 | N | 16 | N | N | 1.1101 | 39.4971 | 78665.9833
[7 empty] | 11014 | 7708 | 1320831 | 2015-10-11 18:09 | 2015-10-11 18:39 | 30 | 11kV | 9450 | 315 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | UGOH | Unplanned | Electrical Storm | N | LID 153692 3 fault operations B Phase Earth Fault Defective UGOH | October | 2015 | 2016Q2 | 2016 | 235:2857 | 235:2857 | ZN00235/002857 | MAITLAND | OH | Not Veg | 2015-10-11 | N | 30 | N | 16 | N | N | 1.1101 | 39.4971 | 6905.7813
[7 empty] | 11443 | 12208 | 1320914 | 2015-10-11 19:12 | 2015-10-11 20:53 | 101 | 11kV | 129670 | 1438 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153693 No Cause found Overcurrent Excluded OMS 1320914 | October | 2015 | 2016Q2 | 2016 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2015-10-11 | N | 90.1739 | N | 16 | N | N | 1.1101 | 39.4971 | 94759.0114
[7 empty] | 11978 | 17782 | 1320757 | 2015-10-11 16:19 | 2015-10-11 21:30 | 311 | 11kV | 367850 | 1247 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN12620 Noraville Panel 8 " Manoa Ave" 11kV tripped, reclosed and locked out on: Relays: E/F & EFI Signals: 11kV trip Lightning hit 11kV O/H adjacent to PT12755 See: 1322659, 1322660, 1322663, 1322664 Withdrawn: 1320768, 769, 766,1320757 | October | 2015 | 2016Q2 | 2016 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2015-10-11 | N | 294.988 | N | 16 | N | N | 1.1101 | 39.4971 | 268813.9303
[7 empty] | 10994 | 7537 | 1320981 | 2015-10-11 21:24 | 2015-10-11 22:10 | 46 | 11kV | 46 | 1 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Lightning | N | ZN14892 Charmhaven 11kV Ex pnl 5 at S14019 Freeway Toohey the S/w "6033" tripped on OC and earth fault End box fault on customers HV equiptment Me:1322075 Withdrawn: 1320981 | October | 2015 | 2016Q2 | 2016 |  |  |  | CENTRAL COAST | UG | Not Veg | 2015-10-11 | N | 46 | N | 16 | N | N | 1.1101 | 39.4971 | 33.6154
[7 empty] | 11337 | 11367 | 1320814 | 2015-10-11 22:00 | 2015-10-11 22:40 | 40 | 11kV | 4640 | 116 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 153691 burnt 11kV tapping at pole Excluded oms 1320823,1320814, | October | 2015 | 2016Q2 | 2016 | 507:80923 | 507:80923 | ZN00507/080923 | CESSNOCK | OH | Not Veg | 2015-10-11 | N | 40 | N | 16 | N | N | 1.1101 | 39.4971 | 3390.7751
[7 empty] | 10722 | 4633 | 1320776 | 2015-10-11 16:48 | 2015-10-11 23:10 | 382 | 11kV | 4202 | 11 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | ZN14891 Wyong Ex Panel 20 " Warnervale" 11kV fdr at PT11792 Sandra Hue Hue the footpath phase 20A HDO operated. Lightining arrestor blown clear exclude OMS 1320776 | October | 2015 | 2016Q2 | 2016 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2015-10-11 | N | 382 | N | 16 | N | N | 1.1101 | 39.4971 | 3070.6977
[7 empty] | 11400 | 11827 | 1321050 | 2015-10-12 04:15 | 2015-10-12 05:25 | 70 | 11kV | 7250 | 833 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S1193 Lindfield Panel 21 Tripped and reclosed on Relays: Basler Relay , Earth Fault, EFI and 11kV trip Field EFI's NIL Cause: PT1148 Longford St Flashover caused by Possum, removed and supply restored See OMS 1322445 1322446 1321050 | October | 2015 | 2016Q2 | 2016 | ZN1193:PA21 | ZN1193:PA21 | ZN01193/000021 | KU-RING-GAI | OH | Not Veg | 2015-10-12 | N | 8.7035 | N | 6 | N | N | 1.1101 | 39.4971 | 5298.0862
[7 empty] | 11607 | 13809 | 1321063 | 2015-10-12 06:34 | 2015-10-12 08:50 | 136 | 11kV | 272 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Previous Storm | N | ZN14892 Charmhaven Ex pnl 14 at PT.13948 Thompson Vale Link 0.2 - single phase HDO operation Cause not Ascertained ME:1322182 Withdrawn:1321063 | October | 2015 | 2016Q2 | 2016 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Not Veg | 2015-10-12 | N | 136 | N | 6 | N | N | 1.1101 | 39.4971 | 198.7696
[7 empty] | 11372 | 11635 | 1320784 | 2015-10-11 17:05 | 2015-10-12 09:47 | 1002 | 11kV | 10020 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Electrical Storm | N | ZN14891 Wyong Ex Panel 5 "wyong " 11kV fdr at PT12625 Buangi Hills Mandalong single PT phase HDO blown Cause not Ascertained Me:1321767 Withdrawn:1320784 | October | 2015 | 2016Q2 | 2016 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2015-10-11 | N | 1002 | N | 16 | N | N | 1.1101 | 39.4971 | 7322.3205
[7 empty] | 12096 | 18897 | 1321091 | 2015-10-12 07:21 | 2015-10-12 10:35 | 194 | 11kV | 582 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | PT 13135 Wise Ferry Parukala 0.2 - footpath 11kV HDO opearted Cause not Ascertained exclude OMS 1322081 | October | 2015 | 2016Q2 | 2016 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2015-10-12 | N | 194 | N | 6 | N | N | 1.1101 | 39.4971 | 425.3084
[7 empty] | 10684 | 4307 | 1320794 | 2015-10-11 18:24 | 2015-10-12 11:50 | 1046 | 11kV | 187225 | 2030 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Lightning | N | ZN12630 Peats Ridge - Panel 4" Kulnura" 11kV feeder tripped & reclosed (prior @15.33 see separate interruption report) - 33kV & 11kV No.1 Tx CB's tripped - 33kV & 11kV No.2 Tx CB's tripped Relays: On panel 4 - A phase timed O/C & BU/OC On Back up Panel - Multi trip Tx1 Panel - Multi trip Tx2 Panel - Multi trip 11kV found sitting on cross arm at PT.13129 Kilpa Peats Ridge Fault on panel 4 cleared by BU/OV protection interrupting zone. See 1323096 1323097 1323098 1323099 1323101 | October | 2015 | 2016Q2 | 2016 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2015-10-11 | N | 92.2291 | N | 16 | N | N | 1.1101 | 39.4971 | 136818.5078
[7 empty] | 12204 | 19919 | 1320861 | 2015-10-11 17:45 | 2015-10-12 12:35 | 1130 | 11kV | 3351 | 108 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Electrical Storm | N | LID 153710 10 amp fuse Substation DOLF replaced 3 x fuses volts 232 load 6, 14, 1 amps Exclude OMS 1320861 | October | 2015 | 2016Q2 | 2016 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2015-10-11 | N | 31.0278 | N | 16 | N | N | 1.1101 | 39.4971 | 2448.812
[7 empty] | 11101 | 8731 | 1321226 | 2015-10-12 10:00 | 2015-10-12 12:40 | 160 | 11kV | 1600 | 10 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Lightning | N | PT 13883 Peats Ridge Karee 0.4 - footpath 11kV HDO opearted Lightning - Customers reports lightening hit PT exclude OMS 1322089 | October | 2015 | 2016Q2 | 2016 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2015-10-12 | N | 160 | N | 6 | N | N | 1.1101 | 39.4971 | 1169.2328
[7 empty] | 11748 | 15354 | 1321146 | 2015-10-12 08:37 | 2015-10-12 15:00 | 383 | 11kV | 3064 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 153711 11VkV DROPPER CABLES HAD SHORTED. Replaced LA & 11kV dropper lead at sub 16701. Excluded OMS # 1321146. | October | 2015 | 2016Q2 | 2016 | 229:34992 | 229:34992 | ZN00229/034992 | PORT STEPHENS | OH | Not Veg | 2015-10-12 | N | 383 | N | 6 | N | N | 1.1101 | 39.4971 | 2239.0808
[7 empty] | 12233 | 20266 | 1320883 | 2015-10-11 18:48 | 2015-10-12 15:45 | 1257 | 11kV | 1257 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 153713 Service burned up. Replaced. | October | 2015 | 2016Q2 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2015-10-11 | N | 1257 | N | 16 | N | N | 1.1101 | 39.4971 | 918.5785
[7 empty] | 12081 | 18755 | 1321669 | 2015-10-12 18:50 | 2015-10-13 09:25 | 875 | 11kV | 875 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153723 A phase DOLF : 10 Amp Excluded OMS 1321669 & 1321722 | October | 2015 | 2016Q2 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2015-10-12 | N | 875 | N | 6 | N | N | 1.1101 | 39.4971 | 639.4242
[7 empty] | 11030 | 7868 | 1322123 | 2015-10-13 00:33 | 2015-10-13 11:15 | 642 | 11kV | 1926 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153733 Single Phase DOLF : 10 Amp REPLACED 2 X HV FUSES Excluded OMS 1321657 | October | 2015 | 2016Q2 | 2016 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2015-10-13 | N | 642 | N | 1 | N | N | 1.1101 | 39.4971 | 1407.464
[7 empty] | 11953 | 17545 | 1322063 | 2015-10-14 06:04 | 2015-10-14 08:15 | 131 | 11kV | 393 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 153744 C Phase DOLF : 10 Amp Excluded OMS 1322063 | October | 2015 | 2016Q2 | 2016 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2015-10-14 | N | 131 | N | 5 | N | N | 1.1101 | 39.4971 | 287.1928
[7 empty] | 10652 | 3907 | 1322374 | 2015-10-14 15:22 | 2015-10-14 17:10 | 108 | 11kV | 324 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153760 A Phase Dolf Bird Excluded OMS1322374 | October | 2015 | 2016Q2 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-10-14 | N | 108 | N | 5 | N | N | 1.1101 | 39.4971 | 236.7696
[7 empty] | 11396 | 11815 | 1322048 | 2015-10-14 21:00 | 2015-10-14 23:30 | 150 | 11kV | 1650 | 11 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT 641 11kV HV fuse operated. Cause fuse fatigue See OMS 1327531 1323055 1322051 01322048 | October | 2015 | 2016Q2 | 2016 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2015-10-14 | N | 150 | N | 5 | N | N | 1.1101 | 39.4971 | 1205.7713
[7 empty] | 12121 | 19108 | 1322451 | 2015-10-14 17:49 | 2015-10-15 05:50 | 721 | 11kV | 380031 | 982 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | No Weather Impact | N | S1287 Revesby Panel 4 "Tower Condon" fdr tripped Relays - SEF Signals - 11kv Trip EFI's - Nil REmarks: OH down. 11kv CCT down on the road NR tee to PT2249 Binga Gambier | October | 2015 | 2016Q2 | 2016 | ZN1287:PA4 | ZN1287:PA4 | ZN01287/000004 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-10-14 | N | 386.9969 | N | 5 | N | N | 1.1101 | 39.4971 | 277715.4458
[7 empty] | 11221 | 10085 | 1322514 | 2015-10-15 07:55 | 2015-10-15 08:40 | 45 | 11kV | 1440 | 32 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153762 B phase DOLF : 16 Amp Excluded OMS 1322514 | October | 2015 | 2016Q2 | 2016 | 221:11898 | 220:8687 | ZN00220/008687 | LAKE MACQUARIE | OH | Veg | 2015-10-15 | N | 45 | N | 2 | N | N | 1.1101 | 39.4971 | 1052.3095
[7 empty] | 11050 | 8041 | 1322492 | 2015-10-15 06:35 | 2015-10-15 10:15 | 220 | 11kV | 2200 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | ZN12690 Berkeley Vale Ex Panel 12 "Craftsman Ave" 11kV feeder at PT12289 Golding Lewis- B phase HDO 16A Fuse fatigue ME:1322889 Withdrawn: 1322492, 1322568 | October | 2015 | 2016Q2 | 2016 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2015-10-15 | N | 220 | N | 2 | N | N | 1.1101 | 39.4971 | 1607.6951
[7 empty] | 12013 | 18204 | 1322882 | 2015-10-16 03:36 | 2015-10-16 05:38 | 122 | 11kV | 123029 | 1145 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN 10991 Blakehurst - Pnl 13 - Trip/reclose/trip, A & C pahse IOC, A phase Timed, Timing and Lockout, EFI, Field EFIs. Cause not ascertained. Linesmen to patrol in daylight hours. ME: 1324880. Rest Step: 1324882, 3. Withdrawn: 1322882. | October | 2015 | 2016Q2 | 2016 | ZN10991:PA13 | ZN10991:PA13 | ZN10991/000013 | GEORGES RIVER | OH | Veg | 2015-10-16 | N | 107.4489 | N | 3 | N | N | 1.1101 | 39.4971 | 89905.9645
[7 empty] | 11254 | 10445 | 1323083 | 2015-10-16 10:38 | 2015-10-16 14:08 | 210 | 11kV | 8190 | 39 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | ZN12600 Lisarow Ex panel 3 "Lisarow High Taylor" 11kV fdr at PT 12334 Berrys Head Gregory 31.5A centre phase HDO operated Fuse Fatigue ME:1323461 Withdrawn:1323083 | October | 2015 | 2016Q2 | 2016 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2015-10-16 | N | 210 | N | 3 | N | N | 1.1101 | 39.4971 | 5985.0104
[7 empty] | 10790 | 5372 | 1323119 | 2015-10-16 14:33 | 2015-10-16 16:45 | 132 | 11kV | 264 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153783 A & B Phase DEOLF : 3 Amp Operator found 2 x 3.15A dolfs blown. Remaining fuse was 16A. Replaced all with 31.5 for 200kVA sub. Excluded OMS 1323119 | October | 2015 | 2016Q2 | 2016 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2015-10-16 | N | 132 | N | 3 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 12114 | 19061 | 1322288 | 2015-10-14 12:41 | 2015-10-16 19:00 | 3259 | 11kV | 312012 | 2233 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn3922 Drummoyne Panel 2 "Edenholme St" tripped on: Relays: earth fault and overcurretn, fault check and EFI. Signals: Zone and TX1 earths and 11kv trip Field EFI's: S1212, S1521, S1460, S48988, Remarks: UG fault. Underground feeder fault from S48988 Little Arthur to S1546 Laggan Ave to S1513 Spectacle Island. Jointers contacted this morning and have advised this morning and have advised SCR cables are wet and will need to excuvate further to find dry bit to joint onto. | October | 2015 | 2016Q2 | 2016 | ZN3922:PA2 | ZN3922:PA2 | ZN03922/000002 | INNER WEST | UG | Not Veg | 2015-10-14 | N | 139.7277 | N | 5 | N | N | 1.1101 | 39.4971 | 228009.1668
[7 empty] | 12086 | 18795 | 1323216 | 2015-10-17 00:59 | 2015-10-17 02:32 | 93 | 11kV | 38223 | 411 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153786 2 fault operations B & C Phase Overcurrent bat on OHM pole EO-90002 Bat on 11kV | October | 2015 | 2016Q2 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-10-17 | N | 93 | N | 2 | N | N | 1.1101 | 39.4971 | 27932.241
[7 empty] | 10626 | 3648 | 1323220 | 2015-10-17 05:00 | 2015-10-17 06:08 | 68 | 11kV | 136748 | 2011 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN36300 Balgowlah North 11kV Panel 3 "S.17119 etc" tripped on: Relays: IOC A+ B phase, EFI Signals: 11kV CB.3 open, Tx1 Group Earth No Field EFI's Cooked Flying Fox on the ground outside 29 Waratah St. OH lineworker to inspect 11kV UGOH above ME:132320 Withdrawn:1323221 | October | 2015 | 2016Q2 | 2016 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2015-10-17 | N | 68 | N | 2 | N | N | 1.1101 | 39.4971 | 99931.405
[7 empty] | 11795 | 15924 | 1323357 | 2015-10-18 08:00 | 2015-10-18 10:35 | 155 | 11kV | 465 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153792 C Phase DOLF : 10 Amp excluded OMS 1323357 | October | 2015 | 2016Q2 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2015-10-18 | N | 155 | N | 2 | N | N | 1.1101 | 39.4971 | 339.8083
[7 empty] | 10585 | 3030 | 1323372 | 2015-10-18 08:00 | 2015-10-18 11:35 | 215 | 11kV | 5375 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 153794 C Phase DOLF : 20 Amp Excluded oms 1323372,1323373,1323379 | October | 2015 | 2016Q2 | 2016 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2015-10-18 | N | 215 | N | 2 | N | N | 1.1101 | 39.4971 | 3927.8915
[7 empty] | 10566 | 2792 | 1323460 | 2015-10-19 15:20 | 2015-10-19 19:20 | 240 | 11kV | 26160 | 109 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 153815 Transformer found with low oil, oil leaking. Replaced & retro- fitted. Excluded OMS 1323680 | October | 2015 | 2016Q2 | 2016 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2015-10-19 | N | 240 | N | 1 | N | N | 1.1101 | 39.4971 | 19116.9564
[7 empty] | 10869 | 6273 | 1324196 | 2015-10-20 17:24 | 2015-10-20 20:07 | 163 | 11kV | 299268 | 1836 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN 10991 Blakehurst - Pnl 8 - Trip/reclose/trip, A phase IOC and Timed OC, C phase IOC and Earth Fault, timing, lockout, EFI. Lightning in the area. Linesmen to patrol. ME: 1324196. WIthdrawn: 1324211, 3, 7. | October | 2015 | 2016Q2 | 2016 | ZN10991:PA8 | ZN10991:PA8 | ZN10991/000008 | GEORGES RIVER | OH | Veg | 2015-10-20 | N | 163 | N | 9 | N | N | 1.1101 | 39.4971 | 218696.2275
[7 empty] | 10806 | 5524 | 1324139 | 2015-10-20 16:26 | 2015-10-20 20:30 | 244 | 11kV | 292855 | 1623 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Lightning | N | ZN 398 Dulwich Hill - Pnl 15 - Earth Leakage, EFI, Field EFIs. 11kV Underground cable fault between S 2583 to S 8972 tee S 5067. ME: 1324557. Rest Steps: 1324560, 1. GIS: 1324203. Withdrawn: 1324139. | October | 2015 | 2016Q2 | 2016 | ZN398:PA15 | ZN398:PA15 | ZN00398/000015 | INNER WEST | UG | Not Veg | 2015-10-20 | N | 180.4405 | N | 9 | N | N | 1.1101 | 39.4971 | 214009.7962
[7 empty] | 10511 | 2120 | 1324277 | 2015-10-20 21:12 | 2015-10-20 23:04 | 112 | 11kV | 99182 | 917 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN3922 Drummoyne, 11kv Panel 22 "S62472, S7804, S2076" feeder tripped Relays: EF, EFI Signals: 11kv trip, ZE, Tx1 GE Field EFI's: None operated Remarks: UG fault. Suspect UG fault. | October | 2015 | 2016Q2 | 2016 | ZN3922:PA22 | ZN3922:PA22 | ZN03922/000022 | CANADA BAY | UG | Not Veg | 2015-10-20 | N | 108.1592 | N | 9 | N | N | 1.1101 | 39.4971 | 72479.2802
[7 empty] | 10834 | 5847 | 1324419 | 2015-10-20 22:48 | 2015-10-20 23:30 | 42 | 11kV | 3948 | 94 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 153835 PFA reports pole PO-111 transformer on fire, fire brigade on site Isolated sub to cut clear C phase LV arrestor. Requires LV arrestor to be replaced. | October | 2015 | 2016Q2 | 2016 | 243:80084 | 243:80084 | ZN00243/080084 | LAKE MACQUARIE | OH | Not Veg | 2015-10-20 | N | 42 | N | 9 | N | N | 1.1101 | 39.4971 | 2885.082
[7 empty] | 11407 | 11909 | 1324258 | 2015-10-20 18:16 | 2015-10-20 23:41 | 325 | 11kV | 366077 | 1662 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | N | ZN 9037 Miranda - Pnl 8 - Trip/reclose/trip, Earth Fault, EFI, Timing, Lockout, Field EFIs. Tree branch made contact between HV and LV. EMSO checked customer installations before returning to supply at PT 61907. ME: 1324548. Rest Step: 1324549. Withdrawn: 1324258, 60. | October | 2015 | 2016Q2 | 2016 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Veg | 2015-10-20 | N | 220.2629 | N | 9 | N | N | 1.1101 | 39.4971 | 267518.2742
[7 empty] | 11230 | 10164 | 1324344 | 2015-10-20 23:05 | 2015-10-20 23:53 | 48 | 11kV | 44016 | 917 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | @ZN3922 Drummoyne, 11kv Panel 22 "S62472 The parade hampden etc" fdr tripped on Relays: A & C phase IOC, fault check Signals: 11kv trip NO field EFIs operated Remarks: UG fault. 11kv UG cable fault from S3922 Drummoyne (Panel 22) to S62472 the Parade Hampden to S2076 Gears Av to S7804 Point Av. | October | 2015 | 2016Q2 | 2016 | ZN3922:PA22 | ZN3922:PA22 | ZN03922/000022 | CANADA BAY | UG | Not Veg | 2015-10-20 | N | 48 | N | 9 | N | N | 1.1101 | 39.4971 | 32165.5945
[7 empty] | 11303 | 10983 | 1324210 | 2015-10-20 17:25 | 2015-10-21 01:32 | 487 | 11kV | 944166 | 3199 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | ZN 10999 Kogarah - Pnl 24 - A & B phase IOC and Earth fault check, EFI. Multiple lightning strikes at the time of failure. Region to follow up multiple LV// found in around S 10745, S 10690 and S 10966. ME: 1324941. Rest Step: 1324943, 4, 5. Withdrawn: 1324210, 42, 315. | October | 2015 | 2016Q2 | 2016 | ZN10999:PA24 | ZN10999:PA24 | ZN10999/000024 | BAYSIDE | OH | Not Veg | 2015-10-20 | N | 295.1441 | N | 9 | N | N | 1.1101 | 39.4971 | 689968.6646
[7 empty] | 11865 | 16641 | 1324123 | 2015-10-20 15:50 | 2015-10-21 01:50 | 600 | 11kV | 56670 | 320 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153831 3 fault operations B phase Overcurrent 11kV main brought down by Galah at pole GW-10025. Repairs completed. Also see report 153838. | October | 2015 | 2016Q2 | 2016 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2015-10-20 | N | 177.0938 | N | 9 | N | N | 1.1101 | 39.4971 | 41412.7645
[7 empty] | 12165 | 19550 | 1324144 | 2015-10-20 16:35 | 2015-10-21 02:00 | 565 | 11kV | 441781 | 1895 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Lightning | N | @ZN35900 Potts Hill, 11kv Panel 20L "S35889 Muir Dasea" feeder tripped Relays: 50T, 51AB Signals: ZE, Tx2 GE, 11kv trip Abnormal: AB1412 Closed, AB520 Open Remarks: lightning. 11kv UGOH damaged Arnold Av near Caldwell Pde Yagoona. 11kv feeder Isolated at/from S4475 Ashby Av to AB505 to AB1412 tee PT2408 Arnold Ashby. | October | 2015 | 2016Q2 | 2016 | ZN35900:PA20 | ZN35900:PA20 | ZN35900/000020 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-10-20 | N | 233.1298 | N | 9 | N | N | 1.1101 | 39.4971 | 322840.5245
[7 empty] | 10972 | 7305 | 1324421 | 2015-10-21 08:58 | 2015-10-21 10:00 | 62 | 11kV | 62 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | No Weather Impact | N | LID 153848 C Phase DOLF : 16 Amp load 107, 88, 90 240 volts Excluded oms 1324421 | October | 2015 | 2016Q2 | 2016 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | UG | Not Veg | 2015-10-21 | N | 62 | N | 4 | N | N | 1.1101 | 39.4971 | 45.3078
[7 empty] | 11342 | 11432 | 1324381 | 2015-10-21 09:45 | 2015-10-21 11:47 | 122 | 11kV | 36460 | 318 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 132851 Tree branch on mains adjacent to ABS 18855 Excluded OMS 1324381. | October | 2015 | 2016Q2 | 2016 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2015-10-21 | N | 114.6541 | N | 4 | N | N | 1.1101 | 39.4971 | 26643.8926
[7 empty] | 11788 | 15765 | 1324487 | 2015-10-21 08:10 | 2015-10-21 14:15 | 365 | 11kV | 730 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 153858 B Phase DOLF : 10 Amp HV arrestor changed under AP. Volts =243. Excluded OMS 1324487. | October | 2015 | 2016Q2 | 2016 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2015-10-21 | N | 365 | N | 4 | N | N | 1.1101 | 39.4971 | 533.4625
[7 empty] | 11927 | 17188 | 1324717 | 2015-10-21 17:13 | 2015-10-21 20:50 | 217 | 11kV | 1736 | 8 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 153865 burnt off tapping CQ-80025 | October | 2015 | 2016Q2 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-10-21 | N | 217 | N | 4 | N | N | 1.1101 | 39.4971 | 1268.6176
[7 empty] | 10412 | 649 | 1325005 | 2015-10-22 12:28 | 2015-10-22 13:15 | 47 | 11kV | 45650 | 1010 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At S2635 Epping Panel 38 opened on A and B phase overcurrent with lockout. Signals: 11kV Trip Cause: O/S 131Norfolk Rd Nr LB1308 See OMS 1327380 1327383 1325005 | October | 2015 | 2016Q2 | 2016 | ZN2635:PA38 | ZN2635:PA38 | ZN02635/000038 | HORNSBY | OH | Veg | 2015-10-22 | N | 45.198 | N | 9 | N | N | 1.1101 | 39.4971 | 33359.6736
[7 empty] | 12245 | 20360 | 1325076 | 2015-10-22 14:35 | 2015-10-22 14:45 | 10 | 11kV | 60 | 6 | HV | Equipment Failed in Service | Equipment Failure | Tap Changer | Unplanned | No Weather Impact | N | LID 153878 Isolation due to high volts. M. Brown lowered taps from 4 to 2 with a resultant voltage of 244. | October | 2015 | 2016Q2 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | Unknown | Not Veg | 2015-10-22 | N | 10 | N | 9 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 10620 | 3559 | 1325074 | 2015-10-22 15:30 | 2015-10-22 16:48 | 78 | 11kV | 234 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 153885 A & B phase DOLF : 10 Amp | October | 2015 | 2016Q2 | 2016 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2015-10-22 | N | 78 | N | 9 | N | N | 1.1101 | 39.4971 | 171.0003
[7 empty] | 12084 | 18763 | 1325101 | 2015-10-22 15:38 | 2015-10-22 17:36 | 118 | 11kV | 116661 | 1448 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153886 1 fault operation 3 phase Overcurrent; Earth Fault flags ABC; O/C & E/F | October | 2015 | 2016Q2 | 2016 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2015-10-22 | N | 80.567 | N | 9 | N | N | 1.1101 | 39.4971 | 85252.4179
[7 empty] | 11843 | 16491 | 1325162 | 2015-10-22 18:36 | 2015-10-22 20:09 | 93 | 11kV | 35343 | 813 | HV | Equipment Failed in Service | Equipment Failure | U/G Link | Unplanned | No Weather Impact | N | LID 153887 1 fault operation Overcurrent; Earth Fault Ventura Close sub Hazemyer burned. Possible cable damage also. Targets. Rutherford, A & B O/C and E/F Excluded OMS 1325162 | October | 2015 | 2016Q2 | 2016 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | UG | Not Veg | 2015-10-22 | N | 43.4723 | N | 9 | N | N | 1.1101 | 39.4971 | 25827.622
[7 empty] | 11107 | 8778 | 1325107 | 2015-10-22 15:50 | 2015-10-22 21:00 | 309.9167 | 11kV | 14417.9167 | 145 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 153888 1 fault operation 3 phase Overcurrent; Earth Fault 2 span of HV down near tee off to PT.52650 Font Hill. | October | 2015 | 2016Q2 | 2016 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2015-10-22 | N | 99.4339 | N | 9 | N | N | 1.1101 | 39.4971 | 10536.1882
[7 empty] | 10446 | 1192 | 1325177 | 2015-10-22 19:44 | 2015-10-22 21:30 | 106 | 11kV | 212 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 153890 A & B DOLF : 10 Amp LA's blown. Replaced AP from 2055-2120 | October | 2015 | 2016Q2 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2015-10-22 | N | 106 | N | 9 | N | N | 1.1101 | 39.4971 | 154.9233
[7 empty] | 11703 | 14854 | 1325216 | 2015-10-22 23:13 | 2015-10-23 01:01 | 108 | 11kV | 112860 | 1045 | HV | Animal Bird | Animal | UGOH | Unplanned | Rain Wind Storm | N | ZN 9037 Miranda - Pnl 2 - Trip/reclose/trip, C phase Timed OC, Lockout, Timing, EFI. DOp suspects bird on UGOH to S 9153. ME: 1325215. Withdrawn: 1325216, 20. | October | 2015 | 2016Q2 | 2016 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Not Veg | 2015-10-22 | N | 108 | N | 9 | N | N | 1.1101 | 39.4971 | 82474.7592
[7 empty] | 11164 | 9548 | 1325130 | 2015-10-22 16:41 | 2015-10-23 03:35 | 654 | 11kV | 1308 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 153889 Feeder tripped when PT DOLF 54692 was tried back Sub 54692 dolf blew again,de energised and dangar taged TX Feeder went back on 2 minutes later (refer to 1325402) . Emso left job to be given to CAW. Excluded OMS 1325130 | October | 2015 | 2016Q2 | 2016 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2015-10-22 | N | 654 | N | 9 | N | N | 1.1101 | 39.4971 | 955.8478
[7 empty] | 11346 | 11465 | 1325289 | 2015-10-23 08:52 | 2015-10-23 11:55 | 183 | 11kV | 1098 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 153904 C Phase DOLF : 20 Amp Excluded OMS 1325289 | October | 2015 | 2016Q2 | 2016 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2015-10-23 | N | 183 | N | 1 | N | N | 1.1101 | 39.4971 | 802.386
[7 empty] | 11232 | 10177 | 1325529 | 2015-10-24 00:30 | 2015-10-24 01:30 | 60 | 11kV | 240 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153909 Isolated section to remove tree branch. See emerg SI P0400. Excluded OMS 1325529 & 1325541 | October | 2015 | 2016Q2 | 2016 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Veg | 2015-10-24 | N | 60 | N | 2 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 11233 | 10186 | 1325542 | 2015-10-24 01:06 | 2015-10-24 02:11 | 65 | 11kV | 40495 | 623 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 12 feeder tripped Relays A and C phase Timed OC Signals: 11kV Trip Field EFI's Nil Cause not ascertained for outage | October | 2015 | 2016Q2 | 2016 | ZN965:PA12 | ZN965:PA13 | ZN00965/000013 | HORNSBY | OH | Veg | 2015-10-24 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 29592.5516
[7 empty] | 10447 | 1239 | 1325650 | 2015-10-25 07:18 | 2015-10-25 08:40 | 82 | 11kV | 82 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 132911 C phase DOLF : 10 Amp Bird on Arrestor | October | 2015 | 2016Q2 | 2016 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2015-10-25 | N | 82 | N | 2 | N | N | 1.1101 | 39.4971 | 59.9232
[7 empty] | 12018 | 18229 | 1325730 | 2015-10-25 17:32 | 2015-10-25 23:00 | 328 | 11kV | 41480 | 140 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 153918 3 fault operation A Phase Earth Fault 11kV OHM down at sub 59069. Excluded OMS No. 1325730 + 1325742 + 1325751 | October | 2015 | 2016Q2 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-10-25 | N | 296.2857 | N | 2 | N | N | 1.1101 | 39.4971 | 30312.3605
[7 empty] | 11520 | 12848 | 1325758 | 2015-10-26 06:00 | 2015-10-26 08:55 | 175 | 11kV | 350 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 153923 C Phase DOLF : 32 Amp LA blown. Replaced under permit 0800-0845 | October | 2015 | 2016Q2 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2015-10-26 | N | 175 | N | 21 | Y | Y | 1.1101 | 39.4971 | 255.7697
[7 empty] | 10911 | 6768 | 1326008 | 2015-10-26 14:40 | 2015-10-26 15:31 | 50.6667 | 11kV | 50.6667 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153938 10 amp fuse Substation DOLF Replaced blown high voltage fuse. | October | 2015 | 2016Q2 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2015-10-26 | N | 50.6667 | N | 21 | Y | Y | 1.1101 | 39.4971 | 37.0257
[7 empty] | 10499 | 1981 | 1326025 | 2015-10-26 14:46 | 2015-10-26 16:03 | 77 | 11kV | 31878 | 414 | HV | Lightning Strike | Adverse Weather/Environment | Bond | Unplanned | Rain Wind Storm | N | Zn14891 Wyong Pa17 "Louisiana Mareen" tripped on, Relays: Overcurrent, Earth Fault, Lock out, Reclose timing and fault check Signals: 11kv trip and EFI EFI's: nil 11kV bond burnt at corner Louisiana and Warner Vale road due to Lightning | October | 2015 | 2016Q2 | 2016 | ZN14891:PA17 | ZN14891:PA17 | ZN14891/000017 | CENTRAL COAST | OH | Not Veg | 2015-10-26 | N | 77 | N | 21 | Y | Y | 1.1101 | 39.4971 | 23295.5022
[7 empty] | 12151 | 19402 | 1326036 | 2015-10-26 14:59 | 2015-10-26 16:27 | 88 | 11kV | 8624 | 98 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153940 2 fault operations Pole mounted RAGCB | October | 2015 | 2016Q2 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2015-10-26 | N | 88 | N | 21 | Y | Y | 1.1101 | 39.4971 | 6302.1648
[7 empty] | 10693 | 4382 | 1326009 | 2015-10-26 14:38 | 2015-10-26 17:25 | 167 | 11kV | 1249 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap Rd" RE45010 Palm Grove tripped on SEF Tree Branch brought down OH. DOp and lineworker repaired mains and restored supply See 1326382,3 Exclude 1326009 | October | 2015 | 2016Q2 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2015-10-26 | N | 73.4706 | N | 21 | Y | Y | 1.1101 | 39.4971 | 912.7324
[7 empty] | 11052 | 8079 | 1326072 | 2015-10-26 15:23 | 2015-10-26 17:55 | 152 | 11kV | 1064 | 7 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 153954 16 amp fuse Substation DOLF Cut L/A away exclude OMS 1326072 | October | 2015 | 2016Q2 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2015-10-26 | N | 152 | N | 21 | Y | Y | 1.1101 | 39.4971 | 777.5398
[7 empty] | 10969 | 7295 | 1326058 | 2015-10-26 15:12 | 2015-10-26 18:15 | 183 | 11kV | 6212 | 44 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 153946 2 fault operations Pole mounted RAGCB, Overcurrent Include OMS 1326523 Exclude OMS 1326058/86 | October | 2015 | 2016Q2 | 2016 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2015-10-26 | N | 141.1818 | N | 21 | Y | Y | 1.1101 | 39.4971 | 4539.5464
[7 empty] | 11655 | 14300 | 1326061 | 2015-10-26 17:10 | 2015-10-26 18:30 | 80 | 11kV | 160 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 153949 Live Line Clamp come lose OMS 1326061 | October | 2015 | 2016Q2 | 2016 | 512:48048 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Not Veg | 2015-10-26 | N | 80 | N | 21 | Y | Y | 1.1101 | 39.4971 | 116.9233
[7 empty] | 11041 | 7960 | 1326133 | 2015-10-26 16:14 | 2015-10-26 18:40 | 146 | 11kV | 292 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 153952 A & B phase DOLF : 10 Amp Exclided OMS 1326133 | October | 2015 | 2016Q2 | 2016 | 243:80080 | 243:80075 | ZN00243/080075 | CENTRAL COAST | OH | Veg | 2015-10-26 | N | 146 | N | 21 | Y | Y | 1.1101 | 39.4971 | 213.385
[7 empty] | 10443 | 1156 | 1324078 | 2015-10-26 16:11 | 2015-10-26 18:45 | 154 | 11kV | 182490 | 1185 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 153939 UGOH hit by lightning pole IV-97076. | October | 2015 | 2016Q2 | 2016 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2015-10-26 | N | 154 | N | 21 | Y | Y | 1.1101 | 39.4971 | 133358.3095
[7 empty] | 11481 | 12591 | 1326161 | 2015-10-26 16:46 | 2015-10-26 19:15 | 149 | 11kV | 447 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153953 10 amp fuse Substation DOLF exclude OMS 1326161 | October | 2015 | 2016Q2 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-10-26 | N | 149 | N | 21 | Y | Y | 1.1101 | 39.4971 | 326.6544
[7 empty] | 10468 | 1611 | 1326100 | 2015-10-26 16:09 | 2015-10-26 20:15 | 246 | 11kV | 4920 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 153943 A & B Phase DOLF : 10 Amp Fallen Tree at pole DD-98002 | October | 2015 | 2016Q2 | 2016 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2015-10-26 | N | 246 | N | 21 | Y | Y | 1.1101 | 39.4971 | 3595.3909
[7 empty] | 11417 | 11996 | 1326217 | 2015-10-26 20:07 | 2015-10-26 21:00 | 53 | 11kV | 106 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153960 A & B Phase DOLF : 10 Amp Excluded OMS 1326217 | October | 2015 | 2016Q2 | 2016 | 243:80080 | 243:80075 | ZN00243/080075 | CENTRAL COAST | OH | Veg | 2015-10-26 | N | 53 | N | 21 | Y | Y | 1.1101 | 39.4971 | 77.4617
[7 empty] | 11905 | 16989 | 1326103 | 2015-10-26 15:52 | 2015-10-26 21:10 | 318.3667 | 11kV | 10824.4667 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 153957 16 amp fuse Line DOLF Partly patrolled | October | 2015 | 2016Q2 | 2016 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-10-26 | N | 318.3667 | N | 21 | Y | Y | 1.1101 | 39.4971 | 7910.201
[7 empty] | 11615 | 13923 | 1326230 | 2015-10-26 20:18 | 2015-10-26 21:15 | 57 | 11kV | 40717 | 1045 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | Zn9037 Miranda Pnl.2 tripped on: A & C phase timing relay and Earth Fault, Lockout OH resting on cross arm outside #2 The Esplanade. See 1327352 1327353 | October | 2015 | 2016Q2 | 2016 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Not Veg | 2015-10-26 | N | 38.9636 | N | 21 | Y | Y | 1.1101 | 39.4971 | 29754.7827
[7 empty] | 10529 | 2373 | 1326391 | 2015-10-26 14:48 | 2015-10-26 21:25 | 397 | 11kV | 27929 | 100 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 153945 1 fault operation Sensitive Earth Fault wires down at sub 48941 Replaced fuses at LF 40460 | October | 2015 | 2016Q2 | 2016 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2015-10-26 | N | 279.29 | N | 21 | Y | Y | 1.1101 | 39.4971 | 20409.6894
[7 empty] | 10901 | 6624 | 1326014 | 2015-10-26 16:42 | 2015-10-26 22:44 | 362 | 11kV | 10606 | 47 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 153961 2 fault operations Pole mounted RAGCB Sw 74275 tripped @ 1642hrs. Restored at 2010hrs. Isolations at 62785 & s 71140 completed after this time. Include OMS 1326438/439 Exclude OMS 1326014 | October | 2015 | 2016Q2 | 2016 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Not Veg | 2015-10-26 | N | 225.6596 | N | 21 | Y | Y | 1.1101 | 39.4971 | 7750.552
[7 empty] | 11334 | 11349 | 1326015 | 2015-10-26 14:43 | 2015-10-26 23:10 | 507 | 11kV | 37037 | 146 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 153958 3 fault operations A & C phase Overcurrent Wires down across train line at pole 9L40063. Wires down past Sw 74712. at pole 9L-40296 Note: had to use 1326573 as the master job as 1326570 has nil customers attached to record | October | 2015 | 2016Q2 | 2016 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2015-10-26 | N | 253.6781 | N | 21 | Y | Y | 1.1101 | 39.4971 | 27065.5472
[7 empty] | 11838 | 16432 | 1326063 | 2015-10-26 15:15 | 2015-10-27 00:15 | 540 | 11kV | 419594 | 1169 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 153959 2 fault operations A & B phase Earth fault Wires down at pole FT-33378. HV into LV Excluded OMS 1326063; 1326094; 1326092 & 1326072 | October | 2015 | 2016Q2 | 2016 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2015-10-26 | N | 358.9341 | N | 21 | Y | Y | 1.1101 | 39.4971 | 306626.9193
[7 empty] | 10734 | 4795 | 1326111 | 2015-10-26 20:57 | 2015-10-27 00:19 | 202 | 11kV | 6642 | 36 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | Electrical Storm | N | LID 153955 No Protection Operation. broken crossarm pole FR-92065 Include OMS 1326413/414 Exclude OMS 1326111/242 | October | 2015 | 2016Q2 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2015-10-26 | N | 184.5 | N | 21 | Y | Y | 1.1101 | 39.4971 | 4853.7777
[7 empty] | 11652 | 14259 | 1329336 | 2015-10-27 01:30 | 2015-10-27 02:15 | 45 | 11kV | 1485 | 33 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 153962 Sub 7498 B phase DOLF dropper burnt off Section isolated for repairs Excluded OMS 1326219 | October | 2015 | 2016Q2 | 2016 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2015-10-27 | N | 45 | N | 7 | N | N | 1.1101 | 39.4971 | 1085.1942
[7 empty] | 11024 | 7789 | 1326219 | 2015-10-26 19:29 | 2015-10-27 02:15 | 406 | 11kV | 2030 | 5 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 153962 Sub 7498 B phase DOLF dropper burnt off Section isolated for repairs Excluded OMS 1326219 | October | 2015 | 2016Q2 | 2016 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2015-10-26 | N | 406 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1483.4641
[7 empty] | 12178 | 19691 | 1326260 | 2015-10-27 02:24 | 2015-10-27 04:50 | 146 | 11kV | 86366 | 991 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn35900 Potts Hill (Panel 20 "Muir Dasea") tripped, reclosed & tripped on: A+B phase OC, EFI, fault check, lockout Signals: 11kv trip Remarks: Oh resting on cross arm, at Pole RP06434(adjacent PT2408 Arnold Ashby) all three phases of 11kv OH had come off their insulators and were found to be resting on the crossarm. | October | 2015 | 2016Q2 | 2016 | ZN35900:PA20 | ZN35900:PA20 | ZN35900/000020 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-10-27 | N | 87.1504 | N | 7 | N | N | 1.1101 | 39.4971 | 63113.7254
[7 empty] | 11869 | 16696 | 1326292 | 2015-10-27 07:09 | 2015-10-27 08:57 | 108 | 11kV | 62481 | 597 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 153965 2 fault operations C phase Overcurrent Excluded OMS 1326292 | October | 2015 | 2016Q2 | 2016 | 227:13018 | 227:13018 | ZN00227/013018 | LAKE MACQUARIE | OH | Veg | 2015-10-27 | N | 104.6583 | N | 7 | N | N | 1.1101 | 39.4971 | 45659.2719
[7 empty] | 10419 | 796 | 1326561 | 2015-10-27 13:15 | 2015-10-27 14:45 | 90 | 11kV | 1350 | 15 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 153976 isolate to repair insulators at pole LS-30310 | October | 2015 | 2016Q2 | 2016 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2015-10-27 | N | 90 | N | 7 | N | N | 1.1101 | 39.4971 | 986.5402
[7 empty] | 12124 | 19173 | 1326676 | 2015-10-27 17:23 | 2015-10-27 18:45 | 82 | 11kV | 328 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 153979 A Phase DOLF : 10 Amp exclude OMS 1326676 | October | 2015 | 2016Q2 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2015-10-27 | N | 82 | N | 7 | N | N | 1.1101 | 39.4971 | 239.6927
[7 empty] | 10963 | 7208 | 1326733 | 2015-10-27 21:45 | 2015-10-27 22:22 | 37 | 11kV | 38480 | 1040 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S1673 Turramurra Panel 7 Tripped on B phase IOC and fault check All field EFI's down to S4711 Cause: Possum on PT1561 See OMS 1326731 1326732 1326733 | October | 2015 | 2016Q2 | 2016 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Not Veg | 2015-10-27 | N | 37 | N | 7 | N | N | 1.1101 | 39.4971 | 28120.049
[7 empty] | 11550 | 13106 | 1326737 | 2015-10-27 23:42 | 2015-10-28 01:15 | 93 | 11kV | 7905 | 85 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 153980 B Phase DOLF : 31 Amp Excluded OMS 1326737 & 1326740 | October | 2015 | 2016Q2 | 2016 | 258:80779 | 258:80779 | ZN00258/080779 | NEWCASTLE | OH | Veg | 2015-10-27 | N | 93 | N | 7 | N | N | 1.1101 | 39.4971 | 5776.7408
[7 empty] | 11409 | 11943 | 1326743 | 2015-10-28 05:03 | 2015-10-28 06:18 | 75 | 11kV | 99776 | 1593 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington Pnl.18 tripped on: 18L O/C & E/F, EFI Field EFIs @ S935 UG cable fault from S935 (Sw B) to S6816 (Sw A) to A7468 (Sw A) to S3692 (Sw A) see 1327312 1327314 1327315 | October | 2015 | 2016Q2 | 2016 | ZN342:PA18 | ZN342:PA18 | ZN00342/000018 | SYDNEY | UG | Not Veg | 2015-10-28 | N | 62.634 | N | 4 | N | N | 1.1101 | 39.4971 | 72913.3579
[7 empty] | 12052 | 18495 | 1326830 | 2015-10-28 09:51 | 2015-10-28 13:44 | 233 | 11kV | 19533 | 403 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | Zn711 Blackwattle Bay - Pnl.11 interrupted due to suspected Transformer fault @ S7511 ADA Pyrmont Bridge. Fault found while performing in service trip checks. Tx 2 found to be faulty after T-Con winding test. see 1327319 1327321 | October | 2015 | 2016Q2 | 2016 | ZN711:PA11 | ZN7481:PA17 | ZN07481/000017 | SYDNEY | UG | Not Veg | 2015-10-28 | N | 48.469 | N | 4 | N | N | 1.1101 | 39.4971 | 14274.1403
[7 empty] | 10712 | 4524 | 1326930 | 2015-10-28 13:38 | 2015-10-28 14:45 | 67 | 11kV | 67 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 153994 3 Phase DOLF : 31 Amp Installed 3 off 31.5 Amp fuses. on arrival there was 1 off 10 Amp & 2 off 20 Amp fuses Excluded OMS 1326930 | October | 2015 | 2016Q2 | 2016 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-10-28 | N | 67 | N | 4 | N | N | 1.1101 | 39.4971 | 48.9616
[7 empty] | 11336 | 11360 | 1327256 | 2015-10-28 22:21 | 2015-10-29 | 99 | 11kV | 140562 | 2372 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | @ZN10999 Kogarah 11kv Panel No.36 'S10669 Buchanan Hampton' feeder tripped Relays: SEL trip Signals: 11kv trip Remarks: cause not ascertained. Feeder patrolled, no cause found | October | 2015 | 2016Q2 | 2016 | ZN10999:PA36 | ZN10991:PA2 | ZN10991/000002 | GEORGES RIVER | OH | Veg | 2015-10-28 | N | 59.2589 | N | 4 | N | N | 1.1101 | 39.4971 | 102718.5637
[7 empty] | 10621 | 3561 | 1327284 | 2015-10-29 07:47 | 2015-10-29 08:50 | 63 | 11kV | 252 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 154002 16 amp fuse Substation DOLF replaced DOLFfatigued Exclude OMS 1327284/285 | October | 2015 | 2016Q2 | 2016 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Not Veg | 2015-10-29 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 10822 | 5704 | 1327372 | 2015-10-29 09:45 | 2015-10-29 16:42 | 417 | 11kV | 834 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At S7391 Macquarie University No 6 B phase HV fuse operated Cause: Transformer failure See OMS 1328286 1327387 1327381 1327372 | October | 2015 | 2016Q2 | 2016 | ZN2635:PA65 | ZN2635:PA65 | ZN02635/000065 | RYDE | UG | Not Veg | 2015-10-29 | N | 417 | N | 5 | N | N | 1.1101 | 39.4971 | 609.4626
[7 empty] | 10588 | 3086 | 1327576 | 2015-10-29 17:35 | 2015-10-29 20:00 | 145 | 11kV | 290 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 154024 40855 Line fuse not yet in model A phase | October | 2015 | 2016Q2 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2015-10-29 | N | 145 | N | 5 | N | N | 1.1101 | 39.4971 | 211.9234
[7 empty] | 11098 | 8690 | 1327609 | 2015-10-29 21:26 | 2015-10-29 22:55 | 89 | 11kV | 178 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 154025 No protection operations. Broken tapping from LLC replaced under AP. Exclude OMS 1327609 | October | 2015 | 2016Q2 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2015-10-29 | N | 89 | N | 5 | N | N | 1.1101 | 39.4971 | 130.0771
[7 empty] | 11468 | 12458 | 1327596 | 2015-10-29 20:47 | 2015-10-29 23:33 | 166 | 11kV | 312824 | 2372 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.36L tripped on SEL Field EFIs: NIL Cause not ascertained Lineworker to patrol. Panel 36L switched abnormally to open AB31027 for future fault ID. See 1328369 1328370 1328372 1328373 1328374 1328377 | October | 2015 | 2016Q2 | 2016 | ZN10999:PA36 | ZN10991:PA2 | ZN10991/000002 | GEORGES RIVER | UG | Not Veg | 2015-10-29 | N | 131.882 | N | 5 | N | N | 1.1101 | 39.4971 | 228602.5525
[7 empty] | 11576 | 13424 | 1327622 | 2015-10-30 07:18 | 2015-10-30 15:15 | 477 | 11kV | 1431 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 154031 A Phase DOLF : 10 Amp | October | 2015 | 2016Q2 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2015-10-30 | N | 477 | N | 1 | N | N | 1.1101 | 39.4971 | 1045.7326
[7 empty] | 11172 | 9633 | 1327917 | 2015-10-31 08:51 | 2015-10-31 09:50 | 59 | 11kV | 10500 | 1974 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn12640 Empire Bay Pa2 tripped on A & B Phase IOC @PT11374 Ocean Beach Pioneer Road & centre phase 50K HDO HV fuses failed due to animals/birds. See 1328416,7 exclude 1327917,8,9,20,1,2,3 | October | 2015 | 2016Q2 | 2016 | ZN12640:PA2 | ZN12640:PA2 | ZN12640/000002 | CENTRAL COAST | OH | Not Veg | 2015-10-31 | N | 5.3191 | N | 1 | N | N | 1.1101 | 39.4971 | 7673.0903
[7 empty] | 10774 | 5208 | 1328005 | 2015-11-01 01:31 | 2015-11-01 03:40 | 129 | 11kV | 9373 | 669 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC 63272 Georges Wattle tripped and Reclosed. Relays: NIL @ PT9010 Second Georges - Centre and footpath phase HDOs blown Two dead possums outside 3 Second Ave. PT9010 restored via LV //'s 560 & 558. See 1328387 1328388 | November | 2015 | 2016Q2 | 2016 | ZN9252:PA31 | ZN9252:PA31 | ZN09252/000031 | SUTHERLAND | OH | Not Veg | 2015-11-01 | N | 14.0105 | N | 9 | N | N | 1.1101 | 39.4971 | 6849.5119
[7 empty] | 11189 | 9845 | 1328010 | 2015-11-01 04:57 | 2015-11-01 06:14 | 77 | 11kV | 41426 | 538 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Panel 9, Rec63182 Riverview College has tripped Relays: OC trip. Abnormal Switching: CP3030 Closed, Ab1988 Open Causwe: Bat found outside 60 Tarranya Rd See OMS 1328306 1328010 | November | 2015 | 2016Q2 | 2016 | ZN129:PA9 | ZN129:PA41 | ZN00129/000041 | LANE COVE | OH | Not Veg | 2015-11-01 | N | 77 | N | 9 | N | N | 1.1101 | 39.4971 | 30272.8989
[7 empty] | 10495 | 1931 | 1328099 | 2015-11-01 17:18 | 2015-11-01 18:41 | 83 | 11kV | 60781 | 740 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At S5868 Gore Hill Panel 5 Tripped Cause: UG cable fault between S2379 - S2601 - S7856 See OMS 1328406 1328413 1328099 | November | 2015 | 2016Q2 | 2016 | ZN5868:PA5 | ZN5868:PA5 | ZN05868/000005 | WILLOUGHBY | UG | Not Veg | 2015-11-01 | N | 82.1365 | N | 9 | N | N | 1.1101 | 39.4971 | 44416.9621
[7 empty] | 11540 | 13015 | 1328078 | 2015-11-01 19:10 | 2015-11-01 20:45 | 95 | 11kV | 1330 | 14 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154036 No protection operation, staff on site advised of the need to isolate and clear the tree before the tree fell onto the 11kV lines and created a hazardous situation and damaged the 11kV mains. Sub 50447 within isolation area was paralleled due to medical customers. | November | 2015 | 2016Q2 | 2016 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2015-11-01 | N | 95 | N | 9 | N | N | 1.1101 | 39.4971 | 971.9248
[7 empty] | 12211 | 20003 | 1328181 | 2015-11-01 21:14 | 2015-11-01 22:15 | 61 | 11kV | 37210 | 610 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | Zn12660 Woy WOy 11kv Pa13 "Koolewong" fdr: tripped , reclosed & locked out Relays: A phase IOC Singals: 11kv trip EFI's: Nil Tree branch on 11kv Mains outside 38 Payton st. See 1328181 exclude 1328188 | November | 2015 | 2016Q2 | 2016 | ZN12660:PA13 | ZN12660:PA13 | ZN12660/000013 | CENTRAL COAST | OH | Veg | 2015-11-01 | N | 61 | N | 9 | N | N | 1.1101 | 39.4971 | 27191.9705
[7 empty] | 11737 | 15227 | 1328176 | 2015-11-01 21:17 | 2015-11-01 22:44 | 87 | 11kV | 75081 | 863 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | ex Zn10991 Blakehurst Pnl.1 - HV Bond open from either USL 30777 or UGOH below S10137 | November | 2015 | 2016Q2 | 2016 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2015-11-01 | N | 87 | N | 9 | N | N | 1.1101 | 39.4971 | 54866.9803
[7 empty] | 11010 | 7678 | 1328190 | 2015-11-01 21:40 | 2015-11-02 00:55 | 195 | 11kV | 308827 | 1665 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Zn12640 Umina 11kv Pa10 fdr tripped: Relays: A+B phase IOC Signals: 11kv trip EFI's: Nil Cause not ascertained. Fdr patroled by DOp See 1329205,6 exclude 1328190,7 | November | 2015 | 2016Q2 | 2016 | ZN12640:PA10 | ZN12640:PA10 | ZN12640/000010 | CENTRAL COAST | OH | Veg | 2015-11-01 | N | 185.4817 | N | 9 | N | N | 1.1101 | 39.4971 | 225681.6627
[7 empty] | 11791 | 15856 | 1328187 | 2015-11-01 21:27 | 2015-11-02 01:10 | 223 | 11kV | 232271 | 1543 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Electrical Storm | N | Zn12650 West Gosford 11kv Pa20 fdr tripped Relays: A+C phase timed overcurrent Singals: 11kv trip EFI's: Nil 11kv UGOH damaged by lightning below S11142 York Masons See 1329196,8,9,200 exclude 1328187 | November | 2015 | 2016Q2 | 2016 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | OH | Not Veg | 2015-11-01 | N | 150.5321 | N | 9 | N | N | 1.1101 | 39.4971 | 169736.796
[7 empty] | 11271 | 10619 | 1328212 | 2015-11-02 02:42 | 2015-11-02 03:29 | 47 | 11kV | 33088 | 704 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S8000 Macquarie Park Panel 6 tripped on Relays: Timed Overcurrent, Earth Fault and Fault Check 11kV Fault from S8000 Macquarie Park Panel 6 to S8150 Lane Cover LTalavera | November | 2015 | 2016Q2 | 2016 | ZN8000:PA6 | ZN8000:PA6 | ZN08000/000006 | KU-RING-GAI | UG | Not Veg | 2015-11-02 | N | 47 | N | 10 | N | N | 1.1101 | 39.4971 | 24179.7345
[7 empty] | 10988 | 7476 | 1328196 | 2015-11-01 22:11 | 2015-11-02 03:30 | 319 | 11kV | 54053 | 187 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | Zn14891 Wyong Pa19 fdr tripped and reclosed & locked out Relays: 51N, fault check , timing, reclosed, EFI Signals: Tx2 Group Earth EFI's: Nil Suspect UG fault from S14346 to CP49497 tee PT11866 See 1329231,2,3 exclude 1328196 | November | 2015 | 2016Q2 | 2016 | ZN14891:PA19 | ZN14891:PA19 | ZN14891/000019 | CENTRAL COAST | UG | Not Veg | 2015-11-01 | N | 289.0535 | N | 9 | N | N | 1.1101 | 39.4971 | 39500.3381
[7 empty] | 11515 | 12808 | 1330651 | 2015-11-02 04:10 | 2015-11-02 07:06 | 176 | 11kV | 125937 | 1075 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S80 Chatswood Panel 25 Murry Ralston Tripped reclosed tripped and locked out on Relays: O/C, Timing, Lockout and EFI Cause: Tree branch contact Branch found near PT1537 See OMS 1330651 1330660 1330664 1330665 1328217 | November | 2015 | 2016Q2 | 2016 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Veg | 2015-11-02 | N | 117.1507 | N | 10 | N | N | 1.1101 | 39.4971 | 92031.0451
[7 empty] | 11674 | 14509 | 1328221 | 2015-11-02 04:53 | 2015-11-02 07:15 | 142 | 11kV | 4544 | 32 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154038 DOLF : 16 Amp Dead possum at base of pole Excluded oms 1328221 | November | 2015 | 2016Q2 | 2016 | 221:11898 | 220:8687 | ZN00220/008687 | LAKE MACQUARIE | OH | Not Veg | 2015-11-02 | N | 142 | N | 10 | N | N | 1.1101 | 39.4971 | 3320.6212
[7 empty] | 12144 | 19295 | 1328262 | 2015-11-02 08:07 | 2015-11-02 12:15 | 248 | 11kV | 1240 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of Pa6 "Pinnacle Triennium" fdr PT18018 Quarry Girrakool centre phase 16Amp HDO blown cause not ascertained See 1329276 exclude 1328262 | November | 2015 | 2016Q2 | 2016 | ZN14143:PA6 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | OH | Veg | 2015-11-02 | N | 248 | N | 10 | N | N | 1.1101 | 39.4971 | 906.1554
[7 empty] | 11793 | 15860 | 1328603 | 2015-11-02 17:03 | 2015-11-02 17:55 | 52 | 11kV | 47480 | 920 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154048 SEF Trip Patrolled with nothing found | November | 2015 | 2016Q2 | 2016 | 221:11894 | 221:11894 | ZN00221/011894 | LAKE MACQUARIE | OH | Veg | 2015-11-02 | N | 51.6087 | N | 10 | N | N | 1.1101 | 39.4971 | 34696.9836
[7 empty] | 10919 | 6835 | 1328605 | 2015-11-02 17:09 | 2015-11-02 18:00 | 51 | 11kV | 1712 | 762 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 154049 Feeder Tripped and Reclosed ABS 27884 burnt off bonds Sub 26248 Blown Arrestors | November | 2015 | 2016Q2 | 2016 | 216:10726 | 216:10726 | ZN00216/010726 | LAKE MACQUARIE | OH | Not Veg | 2015-11-02 | N | 2.2467 | N | 10 | N | N | 1.1101 | 39.4971 | 1251.0791
[7 empty] | 12216 | 20061 | 1328610 | 2015-11-02 17:24 | 2015-11-02 18:20 | 56 | 11kV | 111160 | 1985 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Electrical Storm | N | LID 154051 1 fault operation A & B Phase Overcurrent Report of lightning strike at ABS 62204, Mereweather St. Possibly related to # 154050. | November | 2015 | 2016Q2 | 2016 | 202:34254 | 202:34254 | ZN00202/034254 | NEWCASTLE | OH | Not Veg | 2015-11-02 | N | 56 | N | 10 | N | N | 1.1101 | 39.4971 | 81232.4493
[7 empty] | 10601 | 3243 | 1328660 | 2015-11-02 22:13 | 2015-11-02 23:29 | 76.4667 | 11kV | 4485.2333 | 79 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 154057 A Phase DOLF : 40 Amp | November | 2015 | 2016Q2 | 2016 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Veg | 2015-11-02 | N | 56.7751 | N | 10 | N | N | 1.1101 | 39.4971 | 3277.6762
[7 empty] | 11169 | 9586 | 1328615 | 2015-11-02 17:53 | 2015-11-03 01:03 | 430 | 11kV | 17270 | 53 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 154053 3 phase DOLF : 20 Amp 11kV overhead mains on ground all 3 phase line fuses blown Excluded oms 1328615,1328623,1328629 | November | 2015 | 2016Q2 | 2016 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2015-11-02 | N | 325.8491 | N | 10 | N | N | 1.1101 | 39.4971 | 12620.4066
[7 empty] | 10888 | 6461 | 1328669 | 2015-11-03 02:22 | 2015-11-03 03:59 | 97 | 11kV | 61013 | 629 | HV | Equipment Failed in Service | Equipment Failure | Pillar | Unplanned | No Weather Impact | N | LID 154060 2 fault operations 3 phase Overcurrent Anzac Pde Sw cubical fire. Excluded oms 1328669 | November | 2015 | 2016Q2 | 2016 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | UG | Not Veg | 2015-11-03 | N | 97 | N | 4 | N | N | 1.1101 | 39.4971 | 44586.5008
[7 empty] | 10672 | 4116 | 1328655 | 2015-11-02 20:55 | 2015-11-03 04:55 | 480 | 11kV | 28460 | 284 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Electrical Storm | N | LID 154058 Phases B & C Excluded OMS 1326855, 1328665 | November | 2015 | 2016Q2 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2015-11-02 | N | 100.2113 | N | 10 | N | N | 1.1101 | 39.4971 | 20797.7286
[7 empty] | 10536 | 2433 | 1329136 | 2015-11-03 08:44 | 2015-11-03 13:00 | 256 | 11kV | 1792 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 154069 B & C phase DOLF : 20 Amp | November | 2015 | 2016Q2 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2015-11-03 | N | 256 | N | 4 | N | N | 1.1101 | 39.4971 | 1309.5407
[7 empty] | 10847 | 6046 | 1329035 | 2015-11-03 19:05 | 2015-11-03 20:00 | 55 | 11kV | 43010 | 782 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca 11kv Pa334 "Terrigal" fdr tripped, reclosed & locked out Relays: A+B phase IOC, TIming & Lockout Relays Signals: 11kv trip EFI's: Nil Tree branch on 11kv mains outside 34 Francis Rd | November | 2015 | 2016Q2 | 2016 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2015-11-03 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 31430.4394
[7 empty] | 11126 | 9041 | 1328981 | 2015-11-03 16:56 | 2015-11-03 23:40 | 404 | 11kV | 72325 | 1199 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 154071/01 & 02 2 fault operation Earth fault High into low. Isoate RH/LH LVF 26037 for emso checks. Excluded OMS 1328981,1328983, 1328985, 1328987, 1328988, 1328993 & 1329020 | November | 2015 | 2016Q2 | 2016 | 225:33676 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Not Veg | 2015-11-03 | N | 60.3211 | N | 4 | N | N | 1.1101 | 39.4971 | 52852.9768
[7 empty] | 11374 | 11651 | 1329062 | 2015-11-04 06:26 | 2015-11-04 07:15 | 49 | 11kV | 65758 | 1342 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 15 Tripped on A and B phase IOC Signals 11kV Trip Cause: Tree branch on 11kV Mains O/S 19 Page St | November | 2015 | 2016Q2 | 2016 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | OH | Veg | 2015-11-04 | N | 49 | N | 8 | N | N | 1.1101 | 39.4971 | 48054.0069
[7 empty] | 12130 | 19203 | 1329064 | 2015-11-04 06:32 | 2015-11-04 08:30 | 118 | 11kV | 1534 | 13 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 PT13268 Jilliby Durren 4.1 16amp HDO operated Tree branch across HV TX bushings See 1329622 exclude 1329064,7,8 | November | 2015 | 2016Q2 | 2016 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2015-11-04 | N | 118 | N | 8 | N | N | 1.1101 | 39.4971 | 1121.002
[7 empty] | 12242 | 20340 | 1329090 | 2015-11-04 08:01 | 2015-11-04 11:15 | 194 | 11kV | 194 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 154079 A Phase DOLF : 10 Amp | November | 2015 | 2016Q2 | 2016 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-11-04 | N | 194 | N | 8 | N | N | 1.1101 | 39.4971 | 141.7695
[7 empty] | 11764 | 15523 | 1329403 | 2015-11-04 16:34 | 2015-11-04 17:07 | 33 | 11kV | 29997 | 909 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Ex Zn12650 West Gosford section of Pa17 "Fagans Bay" Intelliruptor 63069 tripped on overcurrent tree branch on mains See 1329403,7,9,14 | November | 2015 | 2016Q2 | 2016 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | OH | Veg | 2015-11-04 | N | 33 | N | 8 | N | N | 1.1101 | 39.4971 | 21920.9228
[7 empty] | 11430 | 12122 | 1329394 | 2015-11-04 16:22 | 2015-11-04 18:10 | 108 | 11kV | 84600 | 825 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn9037 Miranda Zone - Pnl.9 tripped on: E/F, IOC C phase, EFI and timing & lockout relay UGOH fault short circuit on UGOH to PT9593 The Promenade Moray AB35472 also open and defective with 2 switch blades stuck in EFI @ CP35943 Garnet Amaroo defect see 1329748 1329749 1329750 | November | 2015 | 2016Q2 | 2016 | ZN9037:PA9 | ZN9037:PA9 | ZN09037/000009 | SUTHERLAND | Unknown | Unknown | 2015-11-04 | N | 102.5455 | N | 8 | N | N | 1.1101 | 39.4971 | 61823.1847
[7 empty] | 11036 | 7931 | 1329490 | 2015-11-04 21:44 | 2015-11-04 22:38 | 54 | 11kV | 14437 | 348 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3672 Maroubra Pnl.42 tripped on: B phase EF, EFI & Fault Check Field EFI @ S35869 UG cable fault from S49063 (Sw B) to S6742 (Sw B). Note EFI defective at S49063 resulting in P34 (Maroubra Zn) tripping when attempting restoration. See 1329783 1329784 | November | 2015 | 2016Q2 | 2016 | ZN3672:PA42 | ZN3672:PA42 | ZN03672/000042 | BAYSIDE | UG | Not Veg | 2015-11-04 | N | 41.4856 | N | 8 | N | N | 1.1101 | 39.4971 | 10550.1338
[7 empty] | 10796 | 5466 | 1329481 | 2015-11-04 21:19 | 2015-11-04 22:40 | 81.1667 | 11kV | 4220.6667 | 52 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Light | N | Ex Zn14891 Wyong section of Pa16 PT14042 Tuggerwong Myrna centre phase HDO Tree branch on PT. PT on fire Damage to poly droppers see 1329486 exclude 1329481 | November | 2015 | 2016Q2 | 2016 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Veg | 2015-11-04 | N | 81.1667 | N | 8 | N | N | 1.1101 | 39.4971 | 3084.3387
[7 empty] | 12050 | 18485 | 1329464 | 2015-11-04 19:07 | 2015-11-04 23:10 | 243 | 11kV | 972 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 154084 B & C Phase DOLF : 10 Amp Readings as left at sub 52034 = 232V per phase. Excluded OMS 1329464, 1329468 | November | 2015 | 2016Q2 | 2016 | 503:48017 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Veg | 2015-11-04 | N | 243 | N | 8 | N | N | 1.1101 | 39.4971 | 710.3089
[7 empty] | 11305 | 10986 | 1329645 | 2015-11-05 10:24 | 2015-11-05 12:35 | 131 | 11kV | 8112 | 112 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 154085 2 fault operation 3 phase Earth fault Tree fell on mains at pole MG-20237. Excluded OMS 1329645 & 1329681 | November | 2015 | 2016Q2 | 2016 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2015-11-05 | N | 72.4286 | N | 3 | N | N | 1.1101 | 39.4971 | 5928.0103
[7 empty] | 11536 | 12987 | 1329715 | 2015-11-05 12:19 | 2015-11-05 20:40 | 501 | 11kV | 70714 | 498 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | ex Zn15002 Narrabeen P2L - REC 20112 Kalang Rd tripped and locked out on: OC trip, lockout Abnormal: LB20234 CLOSED - AB26206 OPEN & DEFECTIVE Tree branch brought down HV mains in Addison Rd. See 1330688 1330690 1330691 | November | 2015 | 2016Q2 | 2016 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2015-11-05 | N | 141.996 | N | 3 | N | N | 1.1101 | 39.4971 | 51675.7055
[7 empty] | 11931 | 17226 | 1329924 | 2015-11-06 02:11 | 2015-11-06 04:52 | 161 | 11kV | 7728 | 48 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 154094 B Phase Faulty DOLF carrier | November | 2015 | 2016Q2 | 2016 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2015-11-06 | N | 161 | N | 15 | N | N | 1.1101 | 39.4971 | 5647.3945
[7 empty] | 11834 | 16406 | 1329970 | 2015-11-06 08:00 | 2015-11-06 09:10 | 70 | 11kV | 70 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 154096 A Phase DOLF : 10 Amp Excluded OMS 1329970 | November | 2015 | 2016Q2 | 2016 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Veg | 2015-11-06 | N | 70 | N | 15 | N | N | 1.1101 | 39.4971 | 51.1539
[7 empty] | 10710 | 4505 | 1329979 | 2015-11-06 07:00 | 2015-11-06 09:20 | 140 | 11kV | 560 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 154098 B Phase DOLF : 10 Amp customer called straight through to depot Replaced 10 amp HV fuse on Sub 51091. exclude OMS 1329979 | November | 2015 | 2016Q2 | 2016 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2015-11-06 | N | 140 | N | 15 | N | N | 1.1101 | 39.4971 | 409.2315
[7 empty] | 11987 | 17943 | 1329888 | 2015-11-05 19:24 | 2015-11-06 12:55 | 1051 | 11kV | 241915 | 320 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14891 Wyong Pa21 "40823 fdr" tripped on A & C phase overucrrent fault check EFI, Reclose time delay, lockout EFI's: Nil Large tree on mains near PT13392 See 1331214,6,7,8 exclude 1329888,92,981 | November | 2015 | 2016Q2 | 2016 | ZN14891:PA21 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Veg | 2015-11-05 | N | 755.9844 | N | 3 | N | N | 1.1101 | 39.4971 | 176784.3467
[7 empty] | 10824 | 5738 | 1330080 | 2015-11-06 11:53 | 2015-11-06 14:40 | 167 | 11kV | 334 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 154115 A Phase DOLF : 10 Amp Excluded OMS 1330080 | November | 2015 | 2016Q2 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2015-11-06 | N | 167 | N | 15 | N | N | 1.1101 | 39.4971 | 244.0773
[7 empty] | 12195 | 19798 | 1330164 | 2015-11-06 14:50 | 2015-11-06 15:20 | 30 | 11kV | 300 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 154118 B & C Phase DOLF : 10 Amp | November | 2015 | 2016Q2 | 2016 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2015-11-06 | N | 30 | N | 15 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 10451 | 1292 | 1330197 | 2015-11-06 14:50 | 2015-11-06 15:20 | 30 | 11kV | 180 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 154117 B Phase DOLF : 16 Amp | November | 2015 | 2016Q2 | 2016 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2015-11-06 | N | 30 | N | 15 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 10944 | 7063 | 1330177 | 2015-11-06 14:40 | 2015-11-06 16:04 | 84 | 11kV | 250351 | 4339 | HV | Animal Bird | Animal | Air Break Switch | Unplanned | Lightning | N | Zn36300 Balgowlah North - Panel 11 tripped and locked out on: 11R A & B phase O/C, Fautl Check, EFI Field EFIs down at: S16980 S17011 S16708 S46413 S17100 S16610 Zn36300 Balgowlah North - Pnl.19 tripped and reclosed on: ABC phase O/C, Fault Check and EFI Field EFIs down at: S16827 S16064 S49927 S16928 Bird was building a nest on AB22777 (N/O). P19 supplying other side. See other interruption DOp has removed piece of wire. See 1330177 1330702 | November | 2015 | 2016Q2 | 2016 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | OH | Not Veg | 2015-11-06 | N | 57.6979 | N | 15 | N | N | 1.1101 | 39.4971 | 182949.1267
[7 empty] | 10405 | 537 | 1330203 | 2015-11-06 15:18 | 2015-11-06 16:15 | 57 | 11kV | 114 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 154119 A phase DOLF : 10 Amp Excluded OMS 1330203 | November | 2015 | 2016Q2 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2015-11-06 | N | 57 | N | 15 | N | N | 1.1101 | 39.4971 | 83.3078
[7 empty] | 10675 | 4185 | 1330218 | 2015-11-06 15:40 | 2015-11-06 17:30 | 110 | 11kV | 143800 | 1665 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Rain Wind Storm | N | Zn12640 Umina Pa10 "McEvoy Bapaume" tripped and locked out Relays: A&C phase timed overcurrent and IOC and EFI Signals: 11kv trip PT13703 Glen Ryans hit by lightning isolated HV and LV and now in LV//. Links closed See 1331233,4 exclude 1330218,65,7,70 | November | 2015 | 2016Q2 | 2016 | ZN12640:PA10 | ZN12640:PA10 | ZN12640/000010 | CENTRAL COAST | OH | Not Veg | 2015-11-06 | N | 86.3664 | N | 15 | N | N | 1.1101 | 39.4971 | 105084.7986
[7 empty] | 11109 | 8797 | 1330216 | 2015-11-06 15:39 | 2015-11-06 18:18 | 159 | 11kV | 235161 | 1479 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap Rd" fdr RE44936 Bentley RD OC trip and lock out Weather related. Patrolled aznd found tree branch on mains near CP47645 See 1330216 exclude 1330262,79 | November | 2015 | 2016Q2 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2015-11-06 | N | 159 | N | 15 | N | N | 1.1101 | 39.4971 | 171848.7227
[7 empty] | 11331 | 11331 | 1330107 | 2015-11-06 12:34 | 2015-11-06 18:40 | 366 | 11kV | 87578 | 792 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Rain Wind Storm | N | Zn12640 Umina Pa16 fdr opened on C phase overcurrent @PT13148 Transformer hit by lightning PT13148 Perth Adelaide in LV// links closed See 1331227,9,30 exclude 1330107,54 | November | 2015 | 2016Q2 | 2016 | ZN12640:PA16 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Not Veg | 2015-11-06 | N | 110.5783 | N | 15 | N | N | 1.1101 | 39.4971 | 63999.4193
[7 empty] | 11340 | 11422 | 1330236 | 2015-11-06 16:10 | 2015-11-06 19:20 | 190 | 11kV | 18620 | 98 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | PT13967 McLaurin Kahibah HDO operated 31.5kA fuse replaced Weather related See 1331256 exclude 1330236,88 | November | 2015 | 2016Q2 | 2016 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Veg | 2015-11-06 | N | 190 | N | 15 | N | N | 1.1101 | 39.4971 | 13606.9468
[7 empty] | 11573 | 13409 | 1330303 | 2015-11-06 18:53 | 2015-11-06 21:50 | 177 | 11kV | 1593 | 9 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Wind Storm | N | PT11510 Howes Burns 0.4 Insulator Failed on HDO at PT exclude OMS 1330303 | November | 2015 | 2016Q2 | 2016 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2015-11-06 | N | 177 | N | 15 | N | N | 1.1101 | 39.4971 | 1164.1174
[7 empty] | 10485 | 1790 | 1330333 | 2015-11-06 21:18 | 2015-11-06 22:40 | 82 | 11kV | 164 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 154122 Single phase DOLF : 10 Amp excluded OMS 1330333 | November | 2015 | 2016Q2 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2015-11-06 | N | 82 | N | 15 | N | N | 1.1101 | 39.4971 | 119.8464
[7 empty] | 11571 | 13382 | 1330289 | 2015-11-06 17:48 | 2015-11-07 00:01 | 373 | 11kV | 64608 | 321 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn12630 Peat Ridge pa4 AOp manoukian opened fdr CB for safety 11kv OH mains down beyond USL 43383 to PT11131 George Downes hall 0.5 Intterupted for safety reasons See 1331288,9 exclude 1330289 | November | 2015 | 2016Q2 | 2016 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2015-11-06 | N | 201.271 | N | 15 | N | N | 1.1101 | 39.4971 | 47213.6208
[7 empty] | 11501 | 12714 | 1330429 | 2015-11-07 13:23 | 2015-11-07 16:00 | 157 | 11kV | 137532 | 876 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Pa8 "O'Hart Pacific" fdr tripped, reclosed, tripped and locked out on: Signals: 11kv trip, Group Earth Relays: Earth Fault (51N), fault check, timing, reclose lockout, EFI See 1330429 GIS 1330445 | November | 2015 | 2016Q2 | 2016 | ZN14892:PA8 | ZN14892:PA8 | ZN14892/000008 | CENTRAL COAST | UG | Not Veg | 2015-11-07 | N | 157 | N | 2 | N | N | 1.1101 | 39.4971 | 100504.3291
[7 empty] | 11310 | 11040 | 1330764 | 2015-11-07 20:25 | 2015-11-07 21:20 | 55 | 11kV | 660 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154124 B Phase DOLF : 10 Amp Excluded OMS 1330483 & 1330484 | November | 2015 | 2016Q2 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2015-11-07 | N | 55 | N | 2 | N | N | 1.1101 | 39.4971 | 482.3085
[7 empty] | 10505 | 2016 | 1330494 | 2015-11-08 02:34 | 2015-11-08 08:25 | 351 | 11kV | 702 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154125 A Phase DOLF : 10 Amp Exclided OMS 1330494 | November | 2015 | 2016Q2 | 2016 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2015-11-08 | N | 351 | N | 2 | N | N | 1.1101 | 39.4971 | 513.0009
[7 empty] | 11118 | 8903 | 1330596 | 2015-11-08 22:07 | 2015-11-09 13:35 | 928 | 11kV | 15925 | 163 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale 11kv Pa17 fdr tripped, reclosed and locked out Relays: Earth Fault, EFI, Auto Close & lockout relays Signals: 11kv trip, TX 13 Group Earth EFI's: S14827 S14003. Suspect 11kv UG fault from S14003 Formfit to S14034 WSC Sewer IBIS to LB40026 tee PT13930 Canntree Wyong See 1331321,2,3 exclude 1330596,7 | November | 2015 | 2016Q2 | 2016 | ZN12690:PA17 | ZN12690:PA17 | ZN12690/000017 | CENTRAL COAST | UG | Not Veg | 2015-11-08 | N | 97.6994 | N | 2 | N | N | 1.1101 | 39.4971 | 11637.5203
[7 empty] | 11579 | 13454 | 1330962 | 2015-11-09 17:06 | 2015-11-09 17:45 | 39 | 11kV | 78 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154160 A Phase DOLF : 10 Amp excluded OMS 1330962 | November | 2015 | 2016Q2 | 2016 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2015-11-09 | N | 39 | N | 1 | N | N | 1.1101 | 39.4971 | 57.0001
[7 empty] | 12093 | 18859 | 1331049 | 2015-11-10 01:05 | 2015-11-10 03:20 | 135 | 11kV | 18238 | 1868 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 154161 2 fault operations A Phase Overcurrent Removed bamboo from pole OR-80237. Excluded OMS 1330998 | November | 2015 | 2016Q2 | 2016 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Veg | 2015-11-10 | N | 9.7634 | N | 3 | N | N | 1.1101 | 39.4971 | 13327.7925
[7 empty] | 12191 | 19758 | 1331171 | 2015-11-10 12:15 | 2015-11-10 12:35 | 20 | 11kV | 3520 | 176 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | At S2975 Cliff Lavender NO2 SWA HV CB HR Due to commissioning Changes at North Sydney Panel 15 S2975 Tx1 no longer has I/T protection as the LV pilot wire has been cut. Substation door has been danger tagged Abnormal Switching: 6568 SW/Closed S6402 SW/A Open S6726 SW/A Closed S5475 SW/A Open Note: Supply restored via S35047 | November | 2015 | 2016Q2 | 2016 | ZN2473:PA15 | ZN35400:PA61 | ZN35400/000061 | NORTH SYDNEY | Unknown | Not Veg | 2015-11-10 | N | 20 | N | 3 | N | N | 1.1101 | 39.4971 | 2572.3122
[7 empty] | 10781 | 5295 | 1331269 | 2015-11-10 14:53 | 2015-11-10 15:50 | 57 | 11kV | 513 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 154183 B phase DOLF : 20 Amp Excluded OMS 1331263 CC1: 06-"Urgent - O.H Mains - No others" | November | 2015 | 2016Q2 | 2016 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2015-11-10 | N | 57 | N | 3 | N | N | 1.1101 | 39.4971 | 374.8853
[7 empty] | 11401 | 11828 | 1331751 | 2015-11-11 14:09 | 2015-11-11 15:55 | 106 | 11kV | 212 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154203 C Phase DOLF : 16 Amp Excluded OMS 1331550 | November | 2015 | 2016Q2 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-11-11 | N | 106 | N | 2 | N | N | 1.1101 | 39.4971 | 154.9233
[7 empty] | 12069 | 18641 | 1331651 | 2015-11-11 18:14 | 2015-11-11 21:45 | 211 | 11kV | 4544 | 24 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 154205 A phase DOLF : 20 Amp Conductor on ground at sub 51893. A phase fuse blown at LF 40613. Excluded OMS 1331651 | November | 2015 | 2016Q2 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-11-11 | N | 189.3333 | N | 2 | N | N | 1.1101 | 39.4971 | 3320.6212
[7 empty] | 11572 | 13400 | 1331727 | 2015-11-12 08:18 | 2015-11-12 09:28 | 70.5833 | 11kV | 50820 | 720 | HV | Vegetation Grow In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | LID 154223 3 fault operations Overcurrent branch on ohm removed no further action required. dq exclude OMS 1331732 | November | 2015 | 2016Q2 | 2016 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Veg | 2015-11-12 | N | 70.5833 | N | 6 | N | N | 1.1101 | 39.4971 | 37137.7571
[7 empty] | 12205 | 19922 | 1331854 | 2015-11-12 10:15 | 2015-11-12 11:30 | 75 | 11kV | 75 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 154217 B Phase No protection operation, a contractor called the depot directly to report the burnt contact on the b phase DOLF. No fuses operated. Operator said no OMS job generated. | November | 2015 | 2016Q2 | 2016 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Not Veg | 2015-11-12 | N | 75 | N | 6 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 11841 | 16470 | 1332029 | 2015-11-12 17:58 | 2015-11-12 19:15 | 77 | 11kV | 539 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154233 5 amp fuse Line DOLF exclude OMS 1332029 | November | 2015 | 2016Q2 | 2016 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2015-11-12 | N | 77 | N | 6 | N | N | 1.1101 | 39.4971 | 393.8853
[7 empty] | 11306 | 10987 | 1332002 | 2015-11-12 16:20 | 2015-11-12 22:00 | 340 | 11kV | 47465 | 140 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | LID 154237 5 fault operations Earth fault ARRESTOR REPLACED AT POLE BS-10018 include OMS 1332256 exclude OMS 1332002 | November | 2015 | 2016Q2 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-11-12 | N | 339.0357 | N | 6 | N | N | 1.1101 | 39.4971 | 34686.022
[7 empty] | 10634 | 3699 | 1332063 | 2015-11-12 18:21 | 2015-11-12 23:35 | 314 | 11kV | 3729 | 286 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 154236 20 amp fuse Substation DOLF JOB 1332073 REPORTED ELECTRIC SHOCK-HAPPENED AT TIME OF LIGHTNING STRIKE. ALSO SEE U/PLANNED REPORT 154232. A PH ARRESTOR BLOWN. exclude OMS 1332065,1332071,1332073,1332063 | November | 2015 | 2016Q2 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-11-12 | N | 13.0385 | N | 6 | N | N | 1.1101 | 39.4971 | 2725.0432
[7 empty] | 11966 | 17662 | 1332030 | 2015-11-12 17:57 | 2015-11-13 03:25 | 568 | 11kV | 2874 | 89 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | N | Ex Zn14891 Wyong section of Pa14R @RE45181 McPherson Rd tripped & reclosed on overcurrent @PT12261 McPherson Freeway Nth 11kv HD0 10Amp operated @PT12596 McPherson Freeway 11kv HDO 10Amp 10 amp operated DOp found 11kv bond off at Pole WY3135 between USL41641 & USL42294. Repaired by lineworkers. See 1332319,21,22 Exclude 1332030,1 | November | 2015 | 2016Q2 | 2016 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | OH | Not Veg | 2015-11-12 | N | 32.2921 | N | 6 | N | N | 1.1101 | 39.4971 | 2100.2344
[7 empty] | 10519 | 2278 | 1332098 | 2015-11-13 05:25 | 2015-11-13 06:00 | 35 | 11kV | 385 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 154238 DOLF : 20 Amp Excluded OMS 1332101 | November | 2015 | 2016Q2 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2015-11-13 | N | 35 | N | 20 | Y | Y | 1.1101 | 39.4971 | 281.3466
[7 empty] | 10504 | 2008 | 1332365 | 2015-11-13 15:57 | 2015-11-13 17:36 | 99 | 11kV | 7029 | 71 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Ex Zn12570 Avoca section of Pa33 "McMasters Beach" IR44797 Bouddi tripped & Locked out on B & C Phase Overcurrent DOp patrolled fdr, all clear Storm | November | 2015 | 2016Q2 | 2016 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2015-11-13 | N | 99 | N | 20 | Y | Y | 1.1101 | 39.4971 | 5136.5859
[7 empty] | 11452 | 12274 | 1332345 | 2015-11-13 14:44 | 2015-11-13 17:50 | 186 | 11kV | 155422 | 1296 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Lightning | N | S1290 Leightonfield Panel 4 "Miller Sir Thomas" fdr tripped, reclosed, tripped and locked out. Relays: C phase overcurrent, reclose timer, lockout Singals: 11kv trip Abnormal: LB407 Closed, AB169 Remarks: tree/branch on OH mains. Tree branch on HV at PT63837 Hynes St. Removed by Dop | November | 2015 | 2016Q2 | 2016 | ZN1290:PA4 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | OH | Veg | 2015-11-13 | N | 119.9244 | N | 20 | Y | Y | 1.1101 | 39.4971 | 113577.8134
[7 empty] | 11831 | 16368 | 1332459 | 2015-11-13 17:27 | 2015-11-13 18:30 | 63 | 11kV | 55539 | 1947 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 154261 DOLF : 20 Amp OMS 1332459 Lightning damaqe at sub 42494 caused feeder outage.SUB Interrconnected. REPLACED TX ON 15/11/15. | November | 2015 | 2016Q2 | 2016 | 532:83293 | 532:83314 | ZN00532/083314 | MAITLAND | OH | Not Veg | 2015-11-13 | N | 28.5254 | N | 20 | Y | Y | 1.1101 | 39.4971 | 40586.2631
[7 empty] | 11198 | 9915 | 1332400 | 2015-11-13 16:30 | 2015-11-13 18:35 | 125 | 11kV | 625 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 154259 A Phase DOLF : 10 Amp Excluded OMS 1332400 | November | 2015 | 2016Q2 | 2016 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2015-11-13 | N | 125 | N | 20 | Y | Y | 1.1101 | 39.4971 | 456.7316
[7 empty] | 10797 | 5472 | 1332412 | 2015-11-13 16:42 | 2015-11-13 19:20 | 158 | 11kV | 107397 | 704 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | Zn14892 Charmhaven Pa9 fdr tripped & locked out on Relays: O/C & EF, Reclose timing, fault check, lockout, EFI Signals: 11kv trip, tx1 Group Earth 11kv UG fault from LB40124 to S16288 Wallarah Pacific to S14678 Heritage Eden See 1333312,3,4 Exclude 1332412 | November | 2015 | 2016Q2 | 2016 | ZN14892:PA9 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | UG | Not Veg | 2015-11-13 | N | 152.5526 | N | 20 | Y | Y | 1.1101 | 39.4971 | 78482.5599
[7 empty] | 11419 | 12022 | 1332360 | 2015-11-13 15:50 | 2015-11-13 21:05 | 315 | 11kV | 110181 | 648 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | Ex Zn12570 Avoca section of Pa33 "McMasters Beach" IR50407 The scenic bounty tripped, reclosed, tripped & locked out on A & B phase overcurrent 1 Bay of 1kv OH mains down into LV near PT48464 McMasters Scenic See 1333283,4 Exclude 1332360,505,385 | November | 2015 | 2016Q2 | 2016 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2015-11-13 | N | 170.0324 | N | 20 | Y | Y | 1.1101 | 39.4971 | 80517.025
[7 empty] | 11477 | 12571 | 1332451 | 2015-11-13 17:26 | 2015-11-13 21:40 | 254 | 11kV | 695768 | 3572 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154280 1 fault operatuion Earth fault System abnormal at time of fault, Sw 66253 closed Excluded OMS 1332450, 1332455 | November | 2015 | 2016Q2 | 2016 | 503:48011 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Veg | 2015-11-13 | N | 194.7839 | N | 20 | Y | Y | 1.1101 | 39.4971 | 508446.7327
[7 empty] | 11035 | 7899 | 1332540 | 2015-11-13 20:00 | 2015-11-13 22:20 | 140 | 11kV | 239932 | 1988 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Lightning | N | S35800 Bankstown Panel 14 "Hoskins Cottam" fdr tripped Remarks: lightning hit AB3069 destroyed | November | 2015 | 2016Q2 | 2016 | ZN35800:PA14 | ZN35800:PA14 | ZN35800/000014 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-11-13 | N | 120.6901 | N | 20 | Y | Y | 1.1101 | 39.4971 | 175335.2288
[7 empty] | 11339 | 11403 | 1332574 | 2015-11-13 21:30 | 2015-11-13 23:15 | 105 | 11kV | 149100 | 1420 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 154278 2 fault operations A & B phases Overcurrent Tree branch removed by DOps outside the Wangi Workers Club | November | 2015 | 2016Q2 | 2016 | 239:82129 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Veg | 2015-11-13 | N | 105 | N | 20 | Y | Y | 1.1101 | 39.4971 | 108957.8823
[7 empty] | 11013 | 7701 | 1332568 | 2015-11-13 21:23 | 2015-11-13 23:36 | 133 | 11kV | 214529 | 1613 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At S10999 Kogarah Panel 36 tripped on SEL Abnormal Switching: CP30048 Closed, CP31027 Open Cause not ascertained for outage sere OMS 1333311 1332568 | November | 2015 | 2016Q2 | 2016 | ZN10999:PA36 | ZN10999:PA36 | ZN10999/000036 | GEORGES RIVER | OH | Veg | 2015-11-13 | N | 133 | N | 20 | Y | Y | 1.1101 | 39.4971 | 156771.4657
[7 empty] | 11949 | 17472 | 1332352 | 2015-11-13 15:40 | 2015-11-14 02:00 | 620 | 11kV | 333057 | 1326 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Electrical Storm | N | Zn36200 Empire Bay Pa8 tripped and locked out on Relays: SEF Signals: 11kv trip IR63104 Wards Hill stewart 0.4 tripped , reclosed, tripeed & locked out on B&C phase O/C 1. 11kv OH down between LB48657 & LB48645 tee PT13952 & PT13455 2. 11kv OH down beyond AB42221 tee S18839 & PT13402 Cause: Storm See 1333264,7,8,9,70 Exclude 1332352,6,99,415,21,48,9,92,503,4,9,16,54,5,8 | November | 2015 | 2016Q2 | 2016 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2015-11-13 | N | 251.1742 | N | 20 | Y | Y | 1.1101 | 39.4971 | 243388.2321
[7 empty] | 10633 | 3693 | 1332594 | 2015-11-13 23:25 | 2015-11-14 09:20 | 595 | 11kV | 8925 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154286 A Phase DOLF : 20 Amp Excluded OMS 1332594 | November | 2015 | 2016Q2 | 2016 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2015-11-13 | N | 595 | N | 20 | Y | Y | 1.1101 | 39.4971 | 6522.1268
[7 empty] | 11620 | 13965 | 1332539 | 2015-11-13 23:37 | 2015-11-14 10:00 | 623 | 11kV | 1869 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 154289 B Phase DOLF : 10 Amp Excluded OMS 1332597 & 1332539 | November | 2015 | 2016Q2 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-11-13 | N | 623 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1365.8101
[7 empty] | 10512 | 2128 | 1332425 | 2015-11-13 17:02 | 2015-11-14 11:26 | 1104 | 11kV | 173475 | 257 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 154262 11kV mains down between pole FR-61901 and Fr-64705, Wilderness Rd. Excluded 1332348 | November | 2015 | 2016Q2 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2015-11-13 | N | 675 | N | 20 | Y | Y | 1.1101 | 39.4971 | 126770.4134
[7 empty] | 11665 | 14402 | 1332545 | 2015-11-13 20:08 | 2015-11-14 11:38 | 930 | 11kV | 84372 | 422 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 154272 3 fault operation 3 phase Overcurrent OHM dowm at pole HQ-61509 Excluded OMS 1332545 | November | 2015 | 2016Q2 | 2016 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2015-11-13 | N | 199.9336 | N | 20 | Y | Y | 1.1101 | 39.4971 | 61656.569
[7 empty] | 11772 | 15615 | 1332609 | 2015-11-14 03:29 | 2015-11-14 12:40 | 551 | 11kV | 2204 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | Ex Zn12600 Lisarow section of Pa13 "Brush rd" PT18804 Tuggerah McDonalds centre phase HV Drop out fuse replaced. 20K Fuse Batch 1005 See 1333369 exclude 1332609 | November | 2015 | 2016Q2 | 2016 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2015-11-14 | N | 551 | N | 8 | N | N | 1.1101 | 39.4971 | 1610.6182
[7 empty] | 11826 | 16302 | 1332613 | 2015-11-14 06:19 | 2015-11-14 14:10 | 471 | 11kV | 4239 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 154293 3 Phase DOLF : 31 Amp Excluded OMS 1332639 | November | 2015 | 2016Q2 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2015-11-14 | N | 471 | N | 8 | N | N | 1.1101 | 39.4971 | 3097.7362
[7 empty] | 10607 | 3305 | 1332715 | 2015-11-14 12:33 | 2015-11-14 14:45 | 132 | 11kV | 660 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 154292 A phase DOLF : 16 Amp Excluded OMS 1332715 | November | 2015 | 2016Q2 | 2016 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2015-11-14 | N | 132 | N | 8 | N | N | 1.1101 | 39.4971 | 482.3085
[7 empty] | 10535 | 2425 | 1332532 | 2015-11-13 19:41 | 2015-11-14 15:00 | 1159 | 11kV | 51642 | 55 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 154285 Tree on mains near sub 53180 Excluded OMS 1332532, 1332685, 1332634. ## | November | 2015 | 2016Q2 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2015-11-13 | N | 938.9455 | N | 20 | Y | Y | 1.1101 | 39.4971 | 37738.4504
[7 empty] | 11997 | 18057 | 1333741 | 2015-11-14 14:10 | 2015-11-14 16:00 | 110 | 11kV | 1650 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 154294 Mains down to sub 51505. Taps broken to sub to restore supply Excluded OMS 1332732, 1332686. | November | 2015 | 2016Q2 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2015-11-14 | N | 110 | N | 8 | N | N | 1.1101 | 39.4971 | 1205.7713
[7 empty] | 12206 | 19926 | 1332551 | 2015-11-13 20:23 | 2015-11-14 20:06 | 1422.6833 | 11kV | 1422.6833 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | No information from control room, no LID Customer reports "heard explosion then power went off", assume that DOLF blew during the storm, the job was referred to Singleton ERC. Note: This job closed off around 1am, then customer called again at 14/11/2015 11:28:36 and JOB was then ASSIGNED TO SINGLETON DEPOT - refer to job 1332696 | November | 2015 | 2016Q2 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2015-11-13 | N | 1422.6833 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1039.655
[7 empty] | 10526 | 2358 | 1332526 | 2015-11-13 19:24 | 2015-11-14 21:00 | 1536 | 11kV | 12264 | 41 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 154284 A & C phase Overcurrent HV Reportwed down Excluded OMS 1332526 & 1332543 | November | 2015 | 2016Q2 | 2016 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Veg | 2015-11-13 | N | 299.122 | N | 20 | Y | Y | 1.1101 | 39.4971 | 8962.1695
[7 empty] | 12128 | 19198 | 1332685 | 2015-11-13 20:23 | 2015-11-14 21:40 | 1517 | 11kV | 4551 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 154295 Burnt off tapping P: FP-80347 tee off to sub 51641 Excluded OMS 1332551, 1332696, 1332768. | November | 2015 | 2016Q2 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2015-11-13 | N | 1517 | N | 20 | Y | Y | 1.1101 | 39.4971 | 3325.7366
[7 empty] | 12171 | 19652 | 1332783 | 2015-11-14 21:49 | 2015-11-14 22:45 | 56 | 11kV | 36288 | 648 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12570 Avoca seciotn of Pa33 "McMasters Beach" RE50407 THe Scenic Bountry tripped, reclosed and locked out Tree on mains adjacent to USL41821 | November | 2015 | 2016Q2 | 2016 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2015-11-14 | N | 56 | N | 8 | N | N | 1.1101 | 39.4971 | 26518.2001
[7 empty] | 11416 | 11985 | 1332566 | 2015-11-14 21:15 | 2015-11-14 22:50 | 95 | 11kV | 1710 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154282 DOLF : 16 Amp Excluded OMS 1332566 | November | 2015 | 2016Q2 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2015-11-14 | N | 95 | N | 8 | N | N | 1.1101 | 39.4971 | 1249.6176
[7 empty] | 11805 | 16026 | 1332784 | 2015-11-14 21:25 | 2015-11-15 01:54 | 269 | 11kV | 122116 | 492 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn14143 Somersby section of Pa17 "Somersby Falls" fdr @RE45202 Pacific Ashbrook tripped, reclosed and locked tree branch on OH between USL65168 to LB45060 (defective and unable to open) to LB47495 See 1333378,80,1 exclude 1332773,80,4 | November | 2015 | 2016Q2 | 2016 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2015-11-14 | N | 248.2033 | N | 8 | N | N | 1.1101 | 39.4971 | 89238.771
[7 empty] | 11383 | 11752 | 1332790 | 2015-11-15 02:28 | 2015-11-15 04:14 | 106.1 | 11kV | 169547.8 | 1598 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | At S15001 Beacon Hill Panel 2 Tripped Reclosed Tripped and locked out on A and C phase O/C Cause: Adjacent to LB20328 Removed By DOp 13327920 1332792 1332791 | November | 2015 | 2016Q2 | 2016 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Veg | 2015-11-15 | N | 106.1 | N | 9 | N | N | 1.1101 | 39.4971 | 123900.5314
[7 empty] | 11353 | 11510 | 1333000 | 2015-11-15 09:40 | 2015-11-15 10:31 | 51 | 11kV | 65428 | 1574 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1788 Matraville Panel 17 tripped on B phase overcurrent and efi Signals: 11kV Trip, Tx4 Group Earth and Zone Earth Cause: 11kV UG feeder fault from S2306 to S2307 See OMS 1333498 1333499 1333000 | November | 2015 | 2016Q2 | 2016 | ZN1788:PA17 | ZN1788:PA17 | ZN01788/000017 | BAYSIDE | UG | Not Veg | 2015-11-15 | N | 41.568 | N | 9 | N | N | 1.1101 | 39.4971 | 47812.8526
[7 empty] | 10567 | 2807 | 1332612 | 2015-11-14 05:45 | 2015-11-15 15:00 | 1995 | 11kV | 1995 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 154298 Single phase DOLF : 5 Amp OMS REPORT NO 1332612.REPLACED ARRESTORS , TX FAULTY 14/11/15 REPLACED TX 15/11/15. | November | 2015 | 2016Q2 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-11-14 | N | 1995 | N | 8 | N | N | 1.1101 | 39.4971 | 1457.8872
[7 empty] | 11321 | 11142 | 1333415 | 2015-11-15 20:11 | 2015-11-15 20:15 | 4 | 11kV | 192 | 48 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 154299 1 fault operation A phase Earth Fault Reclose function was NA at the time Ragcb tripped when trying back sub 54366 which had a blown L/A refer OMS 1333066, see report 154301 | November | 2015 | 2016Q2 | 2016 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2015-11-15 | N | 4 | N | 9 | N | N | 1.1101 | 39.4971 | 140.3079
[7 empty] | 10708 | 4495 | 1333066 | 2015-11-15 18:01 | 2015-11-15 22:10 | 249 | 11kV | 249 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 154301 Single phase DOLF : 10 Amp Replaced L/A's | November | 2015 | 2016Q2 | 2016 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2015-11-15 | N | 249 | N | 9 | N | N | 1.1101 | 39.4971 | 181.9619
[7 empty] | 11546 | 13086 | 1333069 | 2015-11-15 18:08 | 2015-11-15 22:10 | 242 | 11kV | 145214 | 1207 | HV | Equipment Failed in Service | Equipment Failure | Busbar | Unplanned | Rain Heavy | N | At S3155 Double Bay Panel 20 tripped on C phase overcurrent, Earth Fault and Fault Check. Cause: Busbar fault at S1718 See OMS 1333407 1333409 1333069 | November | 2015 | 2016Q2 | 2016 | ZN3155:PA20 | ZN3155:PA20 | ZN03155/000020 | WOOLLAHRA | Unknown | Not Veg | 2015-11-15 | N | 120.3099 | N | 9 | N | N | 1.1101 | 39.4971 | 106118.1081
[7 empty] | 10400 | 489 | 1333078 | 2015-11-15 21:10 | 2015-11-15 23:05 | 114.7833 | 11kV | 2240.5667 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 154300 3 phase line DOLF Line fuses open to fix welded dolfs at sub 71355 Excluded refer oms 1333078 | November | 2015 | 2016Q2 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2015-11-15 | N | 89.6227 | N | 9 | N | N | 1.1101 | 39.4971 | 1637.34
[7 empty] | 12136 | 19235 | 1333061 | 2015-11-15 17:43 | 2015-11-15 23:05 | 322 | 11kV | 26324 | 379 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyon section of Pa20 @IR50560 Hue Hue Sandra tripped, reclosed, tripped and locked out Large tree fell and rested against 11kv mains bringing two phases together near 17 Holloway Drive See 1333399,400,1,2 exclude 1333061,3 | November | 2015 | 2016Q2 | 2016 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2015-11-15 | N | 69.4565 | N | 9 | N | N | 1.1101 | 39.4971 | 19236.8028
[7 empty] | 10720 | 4607 | 1333102 | 2015-11-15 21:35 | 2015-11-16 01:00 | 205.4333 | 11kV | 2054.3333 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 154302 Single phase DOLF : 5 Amp Replaced blown LF 41571 Please patrol Fdr | November | 2015 | 2016Q2 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2015-11-15 | N | 205.4333 | N | 9 | N | N | 1.1101 | 39.4971 | 1501.2462
[7 empty] | 11864 | 16640 | 1333121 | 2015-11-16 04:21 | 2015-11-16 10:04 | 343 | 11kV | 71277 | 777 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 154304 2 fault operation Earth fault Sw 82812 trip L/O, Sw 19722 trip/reclose Sw 19722 prot- E/F Sw 82812 prot 51N E/F 1.2.1 ohm down at pole KR-30679. Hi into Low checked OK. | November | 2015 | 2016Q2 | 2016 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2015-11-16 | N | 91.7336 | N | 2 | N | N | 1.1101 | 39.4971 | 52087.1293
[7 empty] | 10839 | 5937 | 1333120 | 2015-11-16 02:43 | 2015-11-16 10:40 | 477 | 11kV | 53424 | 112 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 154303 3 fault operations A & B phases Overcurrent Prot trip I - U=1075A, V=1082A, W=185A tree into ohm at pole MG-20104 | November | 2015 | 2016Q2 | 2016 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2015-11-16 | N | 477 | N | 2 | N | N | 1.1101 | 39.4971 | 39040.6835
[7 empty] | 11526 | 12896 | 1333089 | 2015-11-15 19:43 | 2015-11-16 17:00 | 1277 | 11kV | 102348 | 194 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of Pa2 "Gunderman" RE45013 Gunderman tripped and locked out Tree borught down 11kv OH adj AB42503. section of 11kv fdr from LK40442 via AB42503 to LK43530 tee PT etc. Note: section of fdr is part of planned interruption form 08:00-17:00 hrs on Mon 16th See 1333878,9,80,1 | November | 2015 | 2016Q2 | 2016 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2015-11-15 | N | 527.567 | N | 9 | N | N | 1.1101 | 39.4971 | 74792.8996
[7 empty] | 11898 | 16945 | 1334126 | 2015-11-18 11:36 | 2015-11-18 12:50 | 74 | 11kV | 13144 | 1026 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn9245 Engadine - Pnl.45 tripped and reclosed on: C phase timed O/C, Lockout Bond burnt off footpath phase on zone side of AB35963. Possible tree contact. See 1337738 1337737 | November | 2015 | 2016Q2 | 2016 | ZN9245:PA45 | ZN9245:PA10 | ZN09245/000010 | SUTHERLAND | OH | Not Veg | 2015-11-18 | N | 12.8109 | N | 6 | N | N | 1.1101 | 39.4971 | 9605.2475
[7 empty] | 10874 | 6325 | 1334140 | 2015-11-18 12:26 | 2015-11-18 13:24 | 58 | 11kV | 6902 | 119 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At CP2749 Delhi Rd ex S1193 Lindfield Panel 28L Tripped reclosed and locked out Relays: OC Trip Signals: 11kV Trip Cause: Cause not ascertained for outage mains to patrol. See OMS 1334552 1334140 | November | 2015 | 2016Q2 | 2016 | ZN1193:PA28 | ZN1193:PA28 | ZN01193/000028 | RYDE | OH | Veg | 2015-11-18 | N | 58 | N | 6 | N | N | 1.1101 | 39.4971 | 5043.778
[7 empty] | 11074 | 8367 | 1334266 | 2015-11-18 17:30 | 2015-11-18 19:20 | 110 | 11kV | 110712 | 1278 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Greenacre Zone 1285, 11kv panel 20 "Sub 4409" feeder C/B tripped on; Relays: Timed O/C, EFI, Timing Relay, Lockout, Fault Check Signals: 11kv trip Field EFi's: Sub 4409 Islington Cres Remarks: UG fault. 11kv UG fault from Sw/B @ Sub 4409 Islington to Sw/A @ Sub 3965 Chiswick Water tee to PT1203 Nobe Cres | November | 2015 | 2016Q2 | 2016 | ZN1285:PA20 | ZN1285:PA20 | ZN01285/000020 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-11-18 | N | 86.6291 | N | 6 | N | N | 1.1101 | 39.4971 | 80905.0641
[7 empty] | 11288 | 10798 | 1334135 | 2015-11-18 12:26 | 2015-11-18 20:30 | 484 | 11kV | 38883 | 378 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | At S35500 Top Ryde Panel 23 Tripped on Timed Earth Fault EFI Signals 11kV trip, Tx2 Group Earth Cause:T/Con and jointers found defective endbox at S5835 Epping Rydegate SW/B to S4048 Epping Lane Cove See OMS 1334564 1334565 1334135 | November | 2015 | 2016Q2 | 2016 | ZN35500:PA23 | ZN35500:PA23 | ZN35500/000023 | RYDE | UG | Not Veg | 2015-11-18 | N | 102.8651 | N | 6 | N | N | 1.1101 | 39.4971 | 28414.5495
[7 empty] | 12170 | 19612 | 1334311 | 2015-11-18 20:57 | 2015-11-18 23:37 | 160 | 11kV | 221826 | 2012 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.12 - tripped on: A phase Inst O/C, Fault Check, EFI Field EFIs: S266 & S8108 UG cable fault between S8108 (Sw B) and S35958 (Sw A) See 1337742 1337743 others: 1334316 1334313 | November | 2015 | 2016Q2 | 2016 | ZN690:PA12 | ZN690:PA12 | ZN00690/000012 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-11-18 | N | 110.2515 | N | 6 | N | N | 1.1101 | 39.4971 | 162103.898
[7 empty] | 10393 | 358 | 1334207 | 2015-11-18 15:32 | 2015-11-19 01:48 | 616 | 11kV | 27334 | 434 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 154343 2 fault operation Phases A & C Overcurrent Faulty UGOHs at poles GW-30285 & GV-97005 Excluded OMS 1334213, 1334207, 1334320 | November | 2015 | 2016Q2 | 2016 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | Unknown | Unknown | 2015-11-18 | N | 62.9816 | N | 6 | N | N | 1.1101 | 39.4971 | 19974.881
[7 empty] | 11281 | 10683 | 1334576 | 2015-11-19 13:20 | 2015-11-19 14:15 | 55 | 11kV | 385 | 7 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 154358 B Phase DOLF : 10 Amp dead bird on ground | November | 2015 | 2016Q2 | 2016 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2015-11-19 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 281.3466
[7 empty] | 11778 | 15708 | 1334482 | 2015-11-19 11:30 | 2015-11-19 16:15 | 285 | 11kV | 5700 | 20 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 154354 isolated to make repairs at MG-30446 | November | 2015 | 2016Q2 | 2016 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2015-11-19 | N | 285 | N | 3 | N | N | 1.1101 | 39.4971 | 4165.3919
[7 empty] | 11852 | 16549 | 1334674 | 2015-11-19 16:58 | 2015-11-19 19:46 | 168 | 11kV | 203984 | 2922 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Hot >35C | N | At Zn2635 Epping Panel 58 Tripped on Signals: 11kV Trip Relays: O/C, Timed earth fault and lockout Cause: Fire at S5675 Willow Ray (Normally Open POint between Panel 55 and Panel 58) See OMS 1334795 1334798 1334800 1334824 1334827 1334828 | November | 2015 | 2016Q2 | 2016 | ZN2635:PA58 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | UG | Not Veg | 2015-11-19 | N | 69.8097 | N | 3 | N | N | 1.1101 | 39.4971 | 149065.4907
[7 empty] | 12147 | 19353 | 1334783 | 2015-11-20 07:39 | 2015-11-20 09:00 | 81 | 11kV | 121728 | 1742 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn12600 Lisarow Pa3 "Lisarow High Talor" tripped an dlocked out on Earth Fault, EFI, 11kv trip EFI's S12399 - S14623 - S14247 UGOH fault on section of fde between S14262:A to LB44819 to LB45174 tee PT11702 See 1335888,90,2,4 exclude 1334783,5 | November | 2015 | 2016Q2 | 2016 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | Unknown | Unknown | 2015-11-20 | N | 69.8783 | N | 17 | N | N | 1.1101 | 39.4971 | 88955.232
[7 empty] | 11294 | 10876 | 1335004 | 2015-11-20 14:23 | 2015-11-20 15:31 | 68 | 11kV | 4760 | 70 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 154411 B phase fault in underground cable | November | 2015 | 2016Q2 | 2016 | 224:80344 | 224:80344 | ZN00224/080344 | LAKE MACQUARIE | UG | Not Veg | 2015-11-20 | N | 68 | N | 17 | N | N | 1.1101 | 39.4971 | 3478.4676
[7 empty] | 11348 | 11493 | 1335047 | 2015-11-20 15:20 | 2015-11-20 16:32 | 72 | 11kV | 17720 | 255 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn12660 Woy Woy 11kv Pa16 "St Huberts" tripped Relays Earth Fault, EFI Signals: 11kv trip, CB16 open EFI: S18242 Suspectwed defective 11kv UGOH leading to S18156 SwA Pole WW3341 | November | 2015 | 2016Q2 | 2016 | ZN12660:PA16 | ZN12660:PA16 | ZN12660/000016 | CENTRAL COAST | Unknown | Unknown | 2015-11-20 | N | 69.4902 | N | 17 | N | N | 1.1101 | 39.4971 | 12949.2533
[7 empty] | 10480 | 1733 | 1335020 | 2015-11-20 14:47 | 2015-11-20 17:10 | 143 | 11kV | 4290 | 30 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | PT11027 Tumbi Eastern 0.4 B phase HDO was found to be broken exclude 1335020/023 GIS 1335090 | November | 2015 | 2016Q2 | 2016 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Not Veg | 2015-11-20 | N | 143 | N | 17 | N | N | 1.1101 | 39.4971 | 3135.0055
[7 empty] | 10649 | 3870 | 1335070 | 2015-11-20 15:35 | 2015-11-20 17:43 | 128 | 11kV | 52292 | 439 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn14891 Wyong Pa14 tripped Relays: Basler Relay 150TN, 51N, EFI, Fault check Signals: Tx2 Group Earth, Cb14 open EFI's: S14799 S14630 UGOH fault short circuit seciont of 11kv fdr S14630:B tp LB41853 to S11553:A on pole WY1539. Please also check UGOH on Pole WE1432 See 1335928,9,30 exclude 1335070,6,7,8,145,51,2,8,60 | November | 2015 | 2016Q2 | 2016 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | Unknown | Unknown | 2015-11-20 | N | 119.1162 | N | 17 | N | N | 1.1101 | 39.4971 | 38213.4512
[7 empty] | 10739 | 4866 | 1335189 | 2015-11-20 18:14 | 2015-11-20 19:00 | 46 | 11kV | 2944 | 64 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | Ex Zn12650 West Gosford section of Pa6 PT12116 Jerret Adnamira A phase HDO fuse was found open. ABB 40 AMp batch 0632 See 1336007 exclude 1335189 | November | 2015 | 2016Q2 | 2016 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Not Veg | 2015-11-20 | N | 46 | N | 17 | N | N | 1.1101 | 39.4971 | 2151.3884
[7 empty] | 10574 | 2870 | 1334956 | 2015-11-20 13:10 | 2015-11-20 19:05 | 355 | 11kV | 1775 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 154374 HV lead burnt off at bottom of DOLF Excluded OMS 1334956 | November | 2015 | 2016Q2 | 2016 | 228:7490 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Not Veg | 2015-11-20 | N | 355 | N | 17 | N | N | 1.1101 | 39.4971 | 1297.1176
[7 empty] | 11033 | 7889 | 1335008 | 2015-11-20 17:40 | 2015-11-20 19:10 | 90 | 11kV | 90 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Hot >35C | N | LID 154375 LL Clamp burned up at 7L-90377. Temporarily tightened by Ken but needs new loops installed asap. Interrupted for safety. | November | 2015 | 2016Q2 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2015-11-20 | N | 90 | N | 17 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 11952 | 17512 | 1335119 | 2015-11-20 16:50 | 2015-11-20 19:25 | 155 | 11kV | 298053 | 2359 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Zn10995 Riverwood - Pnl.2 - tripped and Reclosed on: A Phase IOC, O/C, lock out and timing. Bond burnt off on AB31172 on one phase. See 1335944 1335945 | November | 2015 | 2016Q2 | 2016 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | OH | Not Veg | 2015-11-20 | N | 126.3472 | N | 17 | N | N | 1.1101 | 39.4971 | 217808.3413
[7 empty] | 12199 | 19834 | 1335192 | 2015-11-20 18:15 | 2015-11-20 19:36 | 81 | 11kV | 93079 | 1363 | HV | Overload Operational | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | Ex Zn15005 Belrose Pnl.6 - REC 24831 Lockwood Peacock tripped on: OC trip Abnormal: Sw A @ S63681 CLOSED - REC 21818 OPEN - REC 21802 CLOSED - Sw B @ S16249 OPEN & DEFECTIVE Overload - high loads due to abnormal switching and heat See 1337808 1337809 | November | 2015 | 2016Q2 | 2016 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | Unknown | Not Veg | 2015-11-20 | N | 68.2898 | N | 17 | N | N | 1.1101 | 39.4971 | 68019.3878
[7 empty] | 11531 | 12965 | 1335208 | 2015-11-20 18:44 | 2015-11-20 19:40 | 56 | 11kV | 27925 | 1466 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | LID 154373 follows on from T/R see report 154372/OMS 1335660. Sw 80644 opened for safety. UGOH fault at pole JU-50890 Kings Rd. Excluded OMS 1335208 / 11 / 12 / 21. | November | 2015 | 2016Q2 | 2016 | 256:80644 | 256:80644 | ZN00256/080644 | NEWCASTLE | Unknown | Unknown | 2015-11-20 | N | 19.0484 | N | 17 | N | N | 1.1101 | 39.4971 | 20406.7664
[7 empty] | 11465 | 12400 | 1335112 | 2015-11-20 17:01 | 2015-11-20 21:00 | 239 | 11kV | 144207 | 2098 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Hot >35C | N | Zn690 Campsie - Pnl.14 tripped on: IOC C phase, timed O/C & EFI Substation fire at S35327 Lewins Clarke. Dist #2 @ S35327 restored via LV //. Dist #3 (Direct feed to customer - Coles) restored via customer generator. See 1336574 1336575 | November | 2015 | 2016Q2 | 2016 | ZN690:PA14 | ZN690:PA14 | ZN00690/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-11-20 | N | 68.7355 | N | 17 | N | N | 1.1101 | 39.4971 | 105382.2222
[7 empty] | 10413 | 650 | 1335159 | 2015-11-20 17:34 | 2015-11-20 21:00 | 206 | 11kV | 422203 | 2057 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn.10995 Riverwood - Pnl.1 - tripped on: C phase IOC, lock out and timing UGOH fault short circuit between AB31318, S10758 and AB31319. See1335972 1335974 | November | 2015 | 2016Q2 | 2016 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | Unknown | Unknown | 2015-11-20 | N | 205.2518 | N | 17 | N | N | 1.1101 | 39.4971 | 308533.4995
[7 empty] | 11970 | 17685 | 1335093 | 2015-11-20 20:10 | 2015-11-20 22:30 | 140 | 11kV | 1120 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | PT11568 interrupted by DOp due to tree branch on OH mains See 1336011 exclude 1335093 | November | 2015 | 2016Q2 | 2016 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2015-11-20 | N | 140 | N | 17 | N | N | 1.1101 | 39.4971 | 818.463
[7 empty] | 10478 | 1721 | 1335308 | 2015-11-20 22:12 | 2015-11-21 00:06 | 114 | 11kV | 107046 | 939 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | At Zn965 Pennant Hills Panel 35 tripped on A and B phase OC Cause not asceratined See OMS 1335308 1335309 1335310 | November | 2015 | 2016Q2 | 2016 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | HORNSBY | OH | Veg | 2015-11-20 | N | 114 | N | 17 | N | N | 1.1101 | 39.4971 | 78226.0595
[7 empty] | 11182 | 9720 | 1335356 | 2015-11-21 07:35 | 2015-11-21 09:10 | 95 | 11kV | 4465 | 47 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley vale Pa12 "Craftsmen Ave" PT14509 Ace North Gavenlock roadside 31.5Amp HDO operated Cause not ascertained. Fuse operated after day of heatwave See 1336047 exclude 1335356 | November | 2015 | 2016Q2 | 2016 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2015-11-21 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 3262.8903
[7 empty] | 10845 | 6033 | 1335149 | 2015-11-20 17:29 | 2015-11-21 11:10 | 1061 | 11kV | 200085 | 2130 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn12570 Avoca 11kv Pa37L labelled "Avoca Beach" tripped on Relays: Basley Relays 50TA, EFI Signals: CB37 open EFI's: S18438 S49066 section of 11kv fdr between S49066:B to S18135:A to AB44670 tee PT18112 suspected defective UGOH leading to S18135:A Pole AV2930 opposite bowling club @ avoca beach See 1335990,12,3 exclude 1335149 | November | 2015 | 2016Q2 | 2016 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | Unknown | Unknown | 2015-11-20 | N | 93.9366 | N | 17 | N | N | 1.1101 | 39.4971 | 146216.2165
[7 empty] | 12049 | 18482 | 1335315 | 2015-11-20 22:54 | 2015-11-21 11:30 | 756 | 11kV | 26460 | 35 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | At S7767 Beaumont Warrinda TC Defective on C phase. Open circuit to Earth See OMS 1335344 1335315 CC1: 22-"Refer to SOp" FRC1: 322-"No Supply at Point of Attachment - Other Services affected - District Operator required" | November | 2015 | 2016Q2 | 2016 | ZN2400:PA23 | ZN2400:PA23 | ZN02400/000023 | HORNSBY | OH | Not Veg | 2015-11-20 | N | 756 | N | 17 | N | N | 1.1101 | 39.4971 | 19336.1876
[7 empty] | 12217 | 20082 | 1335349 | 2015-11-21 07:40 | 2015-11-21 16:37 | 537 | 11kV | 1611 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 154379 B & C phase DOLF : 10 Amp FAULTY TRANSFORMER Excluded OMS 1335349 | November | 2015 | 2016Q2 | 2016 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2015-11-21 | N | 537 | N | 4 | N | N | 1.1101 | 39.4971 | 1177.2713
[7 empty] | 11159 | 9474 | 1335430 | 2015-11-21 14:17 | 2015-11-21 18:00 | 223 | 11kV | 1115 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby pa17 "somersby falls" PT11371 Pacific AShbrook 0.7 A phase HVDO 10Amp NGK operated See 1336048 exclude 1335430 | November | 2015 | 2016Q2 | 2016 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2015-11-21 | N | 223 | N | 4 | N | N | 1.1101 | 39.4971 | 814.8091
[7 empty] | 12045 | 18463 | 1335521 | 2015-11-22 03:47 | 2015-11-22 10:30 | 403 | 11kV | 191467 | 1217 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.25 tripped on: A & B phase timed Overcurrent One Span of HV and LV brought down by tree branch. LV span cut away in vicinity of LK31790. HV span cut away between S10762, S10865, S10320 tee to S10517. See 1336605 1336606 1336607 GIS: 1335521 | November | 2015 | 2016Q2 | 2016 | ZN10999:PA25 | ZN10999:PA25 | ZN10999/000025 | BAYSIDE | OH | Veg | 2015-11-22 | N | 157.327 | N | 5 | N | N | 1.1101 | 39.4971 | 139918.4363
[7 empty] | 11075 | 8404 | 1335516 | 2015-11-22 02:55 | 2015-11-22 12:40 | 585 | 11kV | 55382 | 288 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | U/G Cable | Unplanned | No Weather Impact | N | LID 154382 3 phase Overcurrent; Earth Fault possible cable fault at sw 57290 Liverpool st sub Excluded OMS oms 1335516 | November | 2015 | 2016Q2 | 2016 | 813:89059 | 813:89059 | ZN00813/089059 | UPPER HUNTER | UG | Not Veg | 2015-11-22 | N | 192.2986 | N | 5 | N | N | 1.1101 | 39.4971 | 40471.5321
[7 empty] | 10996 | 7547 | 1335569 | 2015-11-22 11:41 | 2015-11-22 13:00 | 79 | 11kV | 3239 | 41 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 154383 50 amp fuse Substation DOLF exclude OMS 1335569 | November | 2015 | 2016Q2 | 2016 | 513:48051 | 513:83493 | ZN00513/083493 | SINGLETON | OH | Veg | 2015-11-22 | N | 79 | N | 5 | N | N | 1.1101 | 39.4971 | 2366.9657
[7 empty] | 12059 | 18569 | 1335590 | 2015-11-22 13:52 | 2015-11-22 14:26 | 34 | 11kV | 170 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 154384 No protection operation. Fdr isolated to remake taps following outage to repair UGOH. Excluded OMS 1335590. | November | 2015 | 2016Q2 | 2016 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Not Veg | 2015-11-22 | N | 34 | N | 5 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 11148 | 9375 | 1335868 | 2015-11-22 19:50 | 2015-11-22 20:58 | 68 | 11kV | 6256 | 92 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 154387 Isolated section 11kV mains to remove tree branch at pole KR-60361. Excluded OMS 1335616. | November | 2015 | 2016Q2 | 2016 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2015-11-22 | N | 68 | N | 5 | N | N | 1.1101 | 39.4971 | 4571.7003
[7 empty] | 11783 | 15723 | 1335645 | 2015-11-23 05:54 | 2015-11-23 07:10 | 76 | 11kV | 22876 | 301 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Abnormal: AB76 was open and defective with AB1867 closed Remarks: Bond. HV bond burnt off at AB1510. Ex Panel 29 | November | 2015 | 2016Q2 | 2016 | ZN3472:PA29 | ZN3472:PA29 | ZN03472/000029 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-11-23 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 16717.1061
[7 empty] | 11965 | 17661 | 1335649 | 2015-11-23 06:01 | 2015-11-23 08:45 | 164 | 11kV | 328 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 154389 B Phase DOLF : 10 Amp Excluded OMS 1335649 | November | 2015 | 2016Q2 | 2016 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2015-11-23 | N | 164 | N | 3 | N | N | 1.1101 | 39.4971 | 239.6927
[7 empty] | 10671 | 4109 | 1336072 | 2015-11-23 19:42 | 2015-11-23 20:46 | 64 | 11kV | 47748 | 867 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S5868 Gore Hill Panel 6 tripped Relays: Earth Fault, Fault Check and EFI Cause: 11kV UG fault from S8112 to S3417 See OMS 1337144 1337147 | November | 2015 | 2016Q2 | 2016 | ZN5868:PA6 | ZN5868:PA6 | ZN05868/000006 | WILLOUGHBY | UG | Not Veg | 2015-11-23 | N | 55.0727 | N | 3 | N | N | 1.1101 | 39.4971 | 34892.8301
[7 empty] | 11183 | 9724 | 1336168 | 2015-11-24 10:00 | 2015-11-24 12:35 | 155 | 11kV | 155 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154403 A phase live lince clamp broken on A Phase Excluded oms 1336168 | November | 2015 | 2016Q2 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2015-11-24 | N | 155 | N | 5 | N | N | 1.1101 | 39.4971 | 113.2694
[7 empty] | 11364 | 11595 | 1336330 | 2015-11-24 14:18 | 2015-11-24 14:55 | 37 | 11kV | 3367 | 91 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN8100 Green Square - Pnl.17 tripped on: 17R EFI, OC & EF FIeld EFIs down at S35631, S4355 & S6725 UG cable fault from S6725 (Sw A) to S8193 (Sw B) to S7636 (Sw B) See 1336330 1336432 1336345 CC1: 22-"Refer to SOp" | November | 2015 | 2016Q2 | 2016 | ZN8100:PA17 | ZN8100:PA17 | ZN08100/000017 | SYDNEY | UG | Not Veg | 2015-11-24 | N | 37 | N | 5 | N | N | 1.1101 | 39.4971 | 2460.5043
[7 empty] | 12055 | 18526 | 1335444 | 2015-11-21 14:48 | 2015-11-24 15:15 | 4347 | 11kV | 13281 | 12 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At S35252 Leichhardt Oval, A phase 80A HV transformer fuse blown Remarks: tx failure. Leichhardt oval interrupted, and street supply restored via LV parallel | November | 2015 | 2016Q2 | 2016 | ZN116:PA44 | ZN116:PA12 | ZN00116/000012 | INNER WEST | UG | Not Veg | 2015-11-21 | N | 1106.75 | N | 4 | N | N | 1.1101 | 39.4971 | 9705.3631
[7 empty] | 10740 | 4868 | 1336281 | 2015-11-24 12:24 | 2015-11-24 18:57 | 393 | 11kV | 89289 | 1246 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn12660 Woy Woy 11kv Fdr Pa14 VCB "south woy woy" tripped reclosed tripped and locked out Relays: Earth Fault, EFI, REC, Lockout EFI's: Nil Signals: 11kv trip RE48036 Rawson Woy Woy tripped on IOC, OC DOp patrolled beyond nothing found Excavator Hit 11kv underground cable near S12858 Nagari Shoalhaven No.2 HV UGOH broken away. See 1336617,23,4,5,6,7 exclude 1336279,81,311 | November | 2015 | 2016Q2 | 2016 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | UG | Not Veg | 2015-11-24 | N | 71.6605 | N | 5 | N | N | 1.1101 | 39.4971 | 65249.7676
[7 empty] | 11082 | 8480 | 1336122 | 2015-11-24 08:08 | 2015-11-24 19:37 | 689 | 11kV | 3445 | 5 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Lightning strike brought down 11 kV OHM and wire picked up by passing train. New OHM run and supply restored. esxclude OMS 1336122 | November | 2015 | 2016Q2 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2015-11-24 | N | 689 | N | 5 | N | N | 1.1101 | 39.4971 | 2517.5044
[7 empty] | 11920 | 17138 | 1336446 | 2015-11-24 19:03 | 2015-11-24 21:35 | 152.2 | 11kV | 1369.8 | 9 | HV | Vandalism | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 154409 Repair stolen earths at poles HQ-47438 & HQ-47443. | November | 2015 | 2016Q2 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2015-11-24 | N | 152.2 | N | 5 | N | N | 1.1101 | 39.4971 | 1001.0094
[7 empty] | 11649 | 14201 | 1336513 | 2015-11-25 08:09 | 2015-11-25 09:25 | 76 | 11kV | 1976 | 26 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Electrical Storm | N | Ex Zn12660 Woy Woy section of Pa14 PT18577 Woy Woy Pier 0.4 HDO operated 31.5 Amp roadside. Fuse failure See 1337296 GIS 1336541 exclude 1336513 | November | 2015 | 2016Q2 | 2016 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2015-11-25 | N | 76 | N | 4 | N | N | 1.1101 | 39.4971 | 1444.0025
[7 empty] | 11319 | 11116 | 1336810 | 2015-11-25 18:42 | 2015-11-25 20:10 | 88 | 11kV | 88 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 154421 10 amp fuse Substation DOLF Tx Volts 242V exclude OMS 1336810 | November | 2015 | 2016Q2 | 2016 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2015-11-25 | N | 88 | N | 4 | N | N | 1.1101 | 39.4971 | 64.3078
[7 empty] | 11394 | 11807 | 1336824 | 2015-11-25 20:44 | 2015-11-25 22:11 | 87 | 11kV | 163519 | 2011 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn10991 Blakehurst - Pnl.13 tripped & reclosed on: C phase timed, reclose timing, lockout Abnormal: AB 31023 CLOSED - Sw B @ S10137 OPEN After trip and reclose, bond found burnt off at AB30121. DOp isolating feeder for lineworker to repair airbreak later at night due to load. See 1336975 1336977 | November | 2015 | 2016Q2 | 2016 | ZN10991:PA13 | ZN10991:PA13 | ZN10991/000013 | GEORGES RIVER | OH | Not Veg | 2015-11-25 | N | 81.3123 | N | 4 | N | N | 1.1101 | 39.4971 | 119494.8622
[7 empty] | 11453 | 12299 | 1336847 | 2015-11-25 21:09 | 2015-11-25 22:22 | 73 | 11kV | 98339 | 1494 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington - Pnl.17 tripped (no relays given) Field EFIs down at: S4194, S50187, S671 Abnormal: S2246 (Sw B) OPEN - S5853 (Sw B) CLOSED (defective pilot between S5227 and S2246) UG cable fault between S671 (Sw B), S36251 (Sw B) and S160 (Sw D). Underground pit lid was found blown off on Cnr Queen St & Oxford St Wollahra See 1337021 1337022 | November | 2015 | 2016Q2 | 2016 | ZN342:PA17 | ZN342:PA17 | ZN00342/000017 | WOOLLAHRA | UG | Not Veg | 2015-11-25 | N | 65.8226 | N | 4 | N | N | 1.1101 | 39.4971 | 71863.2407
[7 empty] | 10453 | 1338 | 1336860 | 2015-11-26 01:35 | 2015-11-26 03:50 | 135 | 11kV | 43875 | 325 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 154423 Section isolated for clearance to replace insulator on 33kV pole OR-20620 TM9. see report 154422 Excluded OMS 1336860 | November | 2015 | 2016Q2 | 2016 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2015-11-26 | N | 135 | N | 24 | Y | Y | 1.1101 | 39.4971 | 32062.5559
[7 empty] | 12066 | 18626 | 1336918 | 2015-11-26 08:25 | 2015-11-26 09:38 | 73 | 11kV | 26937 | 369 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn35370 Galston - Pnl.2 - tripped on: A & C phase O/C Pnl.2 recloser made Non/Auto for total fire ban Tree branch on OH mains outside 10 Taylors Rd | November | 2015 | 2016Q2 | 2016 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2015-11-26 | N | 73 | N | 24 | Y | Y | 1.1101 | 39.4971 | 19684.7651
[7 empty] | 11895 | 16922 | 1336997 | 2015-11-26 09:38 | 2015-11-26 12:24 | 166 | 11kV | 155268 | 1062 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | At S35900 Potts Hill Panel 4 "Dasea Rook" fdr opened, closed and opened on: Relays: A and B phase O/C, EFI, reclose, lockout Signals: 11kv trip EFIs down at subs: 4379, 62691, 4412, 4415 and 50039 Remarks: Tree/branch on OH mains. Banks L/M reported tree branch down into HV and LV O/S #273 Cooper Rd, Yagoona | November | 2015 | 2016Q2 | 2016 | ZN35900:PA4 | ZN35900:PA4 | ZN35900/000004 | CANTERBURY-BANKSTOWN | OH | Veg | 2015-11-26 | N | 146.2034 | N | 24 | Y | Y | 1.1101 | 39.4971 | 113465.2748
[7 empty] | 11539 | 12998 | 1336993 | 2015-11-26 09:42 | 2015-11-26 14:00 | 258 | 11kV | 16076 | 118 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | Ex Peats Ridge Zn Pnl.5 - REC 46803 Wise Ferry Dog Trap 0.1 tripped on: IOC and OC OH mains down on ground beyond CP46831 Konda Wise Ferry 0.1 See 1337861 1337862 1337863 1337864 | November | 2015 | 2016Q2 | 2016 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2015-11-26 | N | 136.2373 | N | 24 | Y | Y | 1.1101 | 39.4971 | 11747.8666
[7 empty] | 12001 | 18073 | 1337867 | 2015-11-26 14:05 | 2015-11-26 14:39 | 34 | 11kV | 42330 | 1245 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Link | Unplanned | Hot >35C | N | @Zn12570 Avoca panel 39 'North Avoca' Ext rec 44855 Lake Tramway HR link on load side of Rec Abnormal: Sw 2721 @ Sub 12181 GCC Pump Tramway Closed AB42799 Open Remarks: Underslung Links - details below. Rec 44855 Lake Tramway HR link on load side of Rec | November | 2015 | 2016Q2 | 2016 | ZN12570:PA39 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2015-11-26 | N | 34 | N | 24 | Y | Y | 1.1101 | 39.4971 | 30933.5155
[7 empty] | 11431 | 12126 | 1337107 | 2015-11-26 12:16 | 2015-11-26 15:10 | 174 | 11kV | 80400 | 920 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Hot >35C | N | Zn36200 Empire Bay - Pnl.4 tripped on: E/F and EFI Field EFIs: S18061, S18062, S12492 S14999 S18290 Sewer contractor dug through 11kV UG cable between S18290 and S49880 tee to PT64990. CODMAH sewer contractor for Gosford City Council using directional borer (Joe Vaughn 0406579185) See 1337837 1337838 1337839 | November | 2015 | 2016Q2 | 2016 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | UG | Not Veg | 2015-11-26 | N | 87.3913 | N | 24 | Y | Y | 1.1101 | 39.4971 | 58753.9486
[7 empty] | 11677 | 14555 | 1337117 | 2015-11-26 13:12 | 2015-11-26 15:45 | 153 | 11kV | 289455 | 2671 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor ABC | Unplanned | Hot >35C | N | @ZN12570 Avoca Panel 24 'Woodfield' tripped on: Relays: A&C phase O/C Abnormal: LB40439 Closed and AB41333 Open and Sw/A @ Sub 14564 Gill Round Open, S18135 Sw/A open, Sw/B closed @ S18698, Sw/B closed @ S61891 Remarks: weather related | November | 2015 | 2016Q2 | 2016 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2015-11-26 | N | 108.3695 | N | 24 | Y | Y | 1.1101 | 39.4971 | 211525.1765
[7 empty] | 10375 | 106 | 1337295 | 2015-11-26 15:06 | 2015-11-26 15:50 | 44 | 11kV | 40480 | 920 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 154434 2 fault operations Overcurrent Treee branch on pole JV-11750. | November | 2015 | 2016Q2 | 2016 | 221:11894 | 221:11894 | ZN00221/011894 | LAKE MACQUARIE | OH | Veg | 2015-11-26 | N | 44 | N | 24 | Y | Y | 1.1101 | 39.4971 | 29581.59
[7 empty] | 10516 | 2235 | 1337202 | 2015-11-26 14:32 | 2015-11-26 16:00 | 88 | 11kV | 88 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 154439 Broken Live Line Dropper Excluded OMS 1337202 | November | 2015 | 2016Q2 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-11-26 | N | 88 | N | 24 | Y | Y | 1.1101 | 39.4971 | 64.3078
[7 empty] | 10681 | 4287 | 1337218 | 2015-11-26 13:33 | 2015-11-26 16:22 | 169 | 11kV | 108427 | 738 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | At Zn14143 Somersby 11kv Pnl 17 "Somersby Falls" feeder tripped on A and B phase overcurrent Signals: 11kv trip Field EFi's: nil Remarks: tree branch contact - other. Bark at PT13021 Wise Ferry Ulinga | November | 2015 | 2016Q2 | 2016 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2015-11-26 | N | 146.9201 | N | 24 | Y | Y | 1.1101 | 39.4971 | 79235.2535
[7 empty] | 11919 | 17114 | 1337359 | 2015-11-26 16:07 | 2015-11-26 16:46 | 39 | 11kV | 84942 | 2178 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 154440 1 fault operation Earth fault Total Fire Ban Fdr. (Reclose non-auto) Branch broke off tree into mains near pole JV-11471. exsclude OMS 1337366 | November | 2015 | 2016Q2 | 2016 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Veg | 2015-11-26 | N | 39 | N | 24 | Y | Y | 1.1101 | 39.4971 | 62073.1082
[7 empty] | 11357 | 11551 | 1337470 | 2015-11-26 18:17 | 2015-11-26 19:14 | 57.0167 | 11kV | 106165.0333 | 1862 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 154446 2 fault operations Overcurrent Removed tree branch pole IV-51015 exclude OMS 1337483, 1337489 | November | 2015 | 2016Q2 | 2016 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | OH | Veg | 2015-11-26 | N | 57.0167 | N | 24 | Y | Y | 1.1101 | 39.4971 | 77582.275
[7 empty] | 11897 | 16944 | 1337442 | 2015-11-26 18:01 | 2015-11-26 20:10 | 129 | 11kV | 138266 | 1080 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn9245 Engadine - Pnl. 44 - tripped / reclosed / tripped and locked out on: A Phase IOC, Earth Fault, Lockout Field EFIs: S9287, S9642, UGOH Princess Hwy near Boronia Av Tree branch has falled and clashed HV mains o/s 6 Jerrara St Engadine. See 1337698 1337699 GIS: 1337669 | November | 2015 | 2016Q2 | 2016 | ZN9245:PA44 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Veg | 2015-11-26 | N | 128.0241 | N | 24 | Y | Y | 1.1101 | 39.4971 | 101040.7146
[7 empty] | 10699 | 4427 | 1337165 | 2015-11-26 13:14 | 2015-11-26 20:25 | 431 | 11kV | 117457 | 536 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn12630 Peats Ridge - Pnl.2 - REC 45189 Cooks Peats Ridge 0.5 tripped on: SEF Tree branch brought down OH mains on Wisemans Ferry Road. See 1337870 1337872 | November | 2015 | 2016Q2 | 2016 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2015-11-26 | N | 219.1362 | N | 24 | Y | Y | 1.1101 | 39.4971 | 85834.1112
[7 empty] | 11293 | 10867 | 1337169 | 2015-11-26 13:09 | 2015-11-26 20:25 | 436 | 11kV | 19127 | 322 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn12630 Peats Ridge - Pnl.4 - tripped on: A Phase Overcurrent Tree branch brought down OH mains. See 1337865 1337866 | November | 2015 | 2016Q2 | 2016 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2015-11-26 | N | 59.4006 | N | 24 | Y | Y | 1.1101 | 39.4971 | 13977.4474
[7 empty] | 12241 | 20337 | 1337512 | 2015-11-26 19:25 | 2015-11-26 20:35 | 70 | 11kV | 7280 | 104 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 154449 16 amp fuse Substatoin DOLF exclude oms 1337512/16/28/30/34/35 | November | 2015 | 2016Q2 | 2016 | 502:48008 | 502:48008 | ZN00502/048008 | MAITLAND | OH | Veg | 2015-11-26 | N | 70 | N | 24 | Y | Y | 1.1101 | 39.4971 | 5320.0093
[7 empty] | 10462 | 1446 | 1337491 | 2015-11-26 18:27 | 2015-11-26 21:25 | 178 | 11kV | 106656 | 1173 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex San Souci Zn - Pnl.12 - AB30364 bond burnt off on PT10539 side with HV resting on cross arm. AB30299 opened for safety to repair. See 1337707 1337708 | November | 2015 | 2016Q2 | 2016 | ZN10997:PA12 | ZN10997:PA12 | ZN10997/000012 | BAYSIDE | OH | Not Veg | 2015-11-26 | N | 90.9258 | N | 24 | Y | Y | 1.1101 | 39.4971 | 77941.059
[7 empty] | 11644 | 14149 | 1337325 | 2015-11-26 15:33 | 2015-11-26 22:00 | 387 | 11kV | 3483 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 154443 3 fault operations Earth fault exclude OMS 1337325 | November | 2015 | 2016Q2 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2015-11-26 | N | 387 | N | 24 | Y | Y | 1.1101 | 39.4971 | 2545.2737
[7 empty] | 11890 | 16887 | 1337192 | 2015-11-26 13:19 | 2015-11-26 22:20 | 541 | 11kV | 19111 | 101 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn12630 Peats Ridge - Pnl.1 - REC 44995 Kulnura tripped on: SEF Tree branch brought down wires on George Downs and Collins Rd See 1337875 1337876 | November | 2015 | 2016Q2 | 2016 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2015-11-26 | N | 189.2178 | N | 24 | Y | Y | 1.1101 | 39.4971 | 13965.7551
[7 empty] | 12236 | 20297 | 1337589 | 2015-11-26 22:20 | 2015-11-26 23:35 | 75 | 11kV | 41850 | 558 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S35900 Potts Hill Panel 25 "S8773 Botanica Cedar" fdr tripped on Relays: 1.2.1 Targets, 50TN, 51N Signals: 11kv trip, tx2 GE All field EFI's operated Remarks: UG fault. 11kv UG fault from S35085 Betty Grevillea to Panel 7 @ S3472 Sefton | November | 2015 | 2016Q2 | 2016 | ZN35900:PA25 | ZN3472:PA7 | ZN03472/000007 | CUMBERLAND | UG | Not Veg | 2015-11-26 | N | 75 | N | 24 | Y | Y | 1.1101 | 39.4971 | 30582.7456
[7 empty] | 11237 | 10247 | 1337561 | 2015-11-26 21:22 | 2015-11-27 00:25 | 183 | 11kV | 43679 | 293 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Ex Zn14891 Wyong - Pnl.12 - REC 48813 Yarramalong Boyds 3.7 tripped. (No relays RTU failed) Cause not ascertained possibly wind See 1337844 1337845 | November | 2015 | 2016Q2 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2015-11-26 | N | 149.0751 | N | 24 | Y | Y | 1.1101 | 39.4971 | 31919.3249
[7 empty] | 11329 | 11237 | 1337135 | 2015-11-26 12:47 | 2015-11-27 00:44 | 717 | 11kV | 18626 | 42 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 154442 3 fault operations single phase Repaired and Erected new mains Excluded OMS 1337503 | November | 2015 | 2016Q2 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2015-11-26 | N | 443.4762 | N | 24 | Y | Y | 1.1101 | 39.4971 | 13611.3314
[7 empty] | 10867 | 6263 | 1337471 | 2015-11-26 17:55 | 2015-11-27 03:05 | 550 | 11kV | 97220 | 200 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | Ex Zn12600 Lisarow Pnl.2 - AB41934 opened Abnormal: Recloser 40239 CLOSED - LK 42880 OPEN 11kV Cross arm broken between AB41934 and AB45095 and AB41771. Also AB45094 Defective. See 1337853 & SE: 1337855 (DOp later found REC41020 open) | November | 2015 | 2016Q2 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2015-11-26 | N | 486.1 | N | 24 | Y | Y | 1.1101 | 39.4971 | 71045.5085
[7 empty] | 11667 | 14432 | 1337519 | 2015-11-26 18:47 | 2015-11-27 06:00 | 673 | 11kV | 78412 | 320 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 154447 1 fault operation Earth fault 1 trip due to reclose off for total fire ban. Tree brought down mains at pole GW-10029 Repairs completed include OMS 1337658 exclude OMS 1337502/519 | November | 2015 | 2016Q2 | 2016 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2015-11-26 | N | 245.0375 | N | 24 | Y | Y | 1.1101 | 39.4971 | 57301.1768
[7 empty] | 11375 | 11658 | 1337609 | 2015-11-27 06:24 | 2015-11-27 08:10 | 106 | 11kV | 83145 | 862 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill - Pnl.25 tripped on: Zone Earth, Timed EF, EFI Field EFIs: S7551 S65790 S4028 S2016 S4359 UG cable fault between S4359 (Sw B) and S1097 (Sw A) and S35350 (Sw A) See 1338421 1338422 | November | 2015 | 2016Q2 | 2016 | ZN398:PA25 | ZN398:PA25 | ZN00398/000025 | INNER WEST | UG | Not Veg | 2015-11-27 | N | 96.4559 | N | 2 | N | N | 1.1101 | 39.4971 | 60759.9136
[7 empty] | 10581 | 2972 | 1337924 | 2015-11-27 16:55 | 2015-11-27 18:10 | 75 | 11kV | 300 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 154462 CCT Mains off pin at sub 52679 | November | 2015 | 2016Q2 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2015-11-27 | N | 75 | N | 2 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 11387 | 11771 | 1337994 | 2015-11-28 08:08 | 2015-11-28 10:09 | 121 | 11kV | 73629 | 709 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S3425 Castle Cove Panel 22 tripped on Relays: Timed Earth Fault, Fault Check EFI Signals: 11kV trip, Zone Earth, No4 Group Earth Cause: 11kV UG fault between S48401 Nicholoson Blakesley and S3521 See OMS 1338335 1338337 1337994 | November | 2015 | 2016Q2 | 2016 | ZN3425:PA22 | ZN3425:PA22 | ZN03425/000022 | WILLOUGHBY | UG | Not Veg | 2015-11-28 | N | 103.8491 | N | 5 | N | N | 1.1101 | 39.4971 | 53805.9015
[7 empty] | 10508 | 2058 | 1338019 | 2015-11-28 09:49 | 2015-11-28 12:01 | 132 | 11kV | 396 | 3 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | The 11kV IR50285 Sirius Orion Tripped on OC. Cause HV fault between S64397, S7075 and S750 See OMS 1338344 1338346 1338019 | November | 2015 | 2016Q2 | 2016 | ZN129:PA27 | ZN129:PA51 | ZN00129/000051 | LANE COVE | UG | Not Veg | 2015-11-28 | N | 132 | N | 5 | N | N | 1.1101 | 39.4971 | 289.3851
[7 empty] | 11861 | 16622 | 1338001 | 2015-11-28 08:47 | 2015-11-28 12:50 | 243 | 11kV | 1458 | 6 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 154466 A phase DOLF : 10 Amp blown surge arrestor replaced.dq Excluded oms 1338001 | November | 2015 | 2016Q2 | 2016 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2015-11-28 | N | 243 | N | 5 | N | N | 1.1101 | 39.4971 | 1065.4634
[7 empty] | 11600 | 13711 | 1338136 | 2015-11-28 23:03 | 2015-11-28 23:45 | 42.4833 | 11kV | 3398.6667 | 80 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | LID 154468 40 amp fuse Sectionaliser exclude OMS 1338139/140/142 | November | 2015 | 2016Q2 | 2016 | 221:11900 | 221:11900 | ZN00221/011900 | LAKE MACQUARIE | OH | Not Veg | 2015-11-28 | N | 42.4833 | N | 5 | N | N | 1.1101 | 39.4971 | 2483.6454
[7 empty] | 11632 | 14051 | 1338107 | 2015-11-28 21:10 | 2015-11-29 00:50 | 220 | 11kV | 489060 | 2808 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.1 tripped on: Panel 1 Left : ABC phase O/C fault (51ABC), EFI, O/L & Leakage, frame leakage, Fault Check UG cable fault from Panel 1 tp S2184 to S4207 tee S2370 See 1338410 1338412 GIS 1338138 | November | 2015 | 2016Q2 | 2016 | ZN35600:PA1 | ZN35600:PA1 | ZN35600/000001 | RANDWICK | UG | Not Veg | 2015-11-28 | N | 174.1667 | N | 5 | N | N | 1.1101 | 39.4971 | 357390.6232
[7 empty] | 10416 | 677 | 1338239 | 2015-11-29 16:57 | 2015-11-29 17:55 | 58 | 11kV | 1380 | 25 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2196 Milperra Panel 22 tripped on Relays: Earth Fault, EFI Signals 11kV Trip, No2 Group Earth Zone Earth ause: Fault in section of 11kV feeder from S8137 Fitzpatrick to S2444 Fitz Patrick St See OMS 138521 1338522 1338329 | November | 2015 | 2016Q2 | 2016 | ZN2196:PA22 | ZN2196:PA22 | ZN02196/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-11-29 | N | 55.2 | N | 4 | N | N | 1.1101 | 39.4971 | 1008.4633
[7 empty] | 12024 | 18290 | 1338236 | 2015-11-29 16:30 | 2015-11-29 18:21 | 111 | 11kV | 5113 | 50 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S14143 Somersby Panel 6 tripped on Earth fault with EFI down and No1 Tx Group Earth and earth fault check. Cause: UG Cable Fault See OM 1338382 1338385 1338387 1338236 | November | 2015 | 2016Q2 | 2016 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | UG | Not Veg | 2015-11-29 | N | 102.26 | N | 4 | N | N | 1.1101 | 39.4971 | 3736.4296
[7 empty] | 11809 | 16101 | 1338406 | 2015-11-29 20:31 | 2015-11-29 23:25 | 174 | 11kV | 1740 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 154482 C phase DOLF : 10 Amp Branch fell on mains near sub 72276. Excluded OMS 1338266. | November | 2015 | 2016Q2 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2015-11-29 | N | 174 | N | 4 | N | N | 1.1101 | 39.4971 | 1271.5407
[7 empty] | 11940 | 17318 | 1338273 | 2015-11-29 21:30 | 2015-11-29 23:58 | 148 | 11kV | 107168 | 857 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Lightning | N | At Zn12600 Lisarow Panel 13 Tripped, reclosed tripped and locked out on 51ABC, Recloser Timing and lockout Signals: 11kV trip Cause: Suspect Lightning Strike See OMS 1338281 1338273 OMS1338273 1338281 | November | 2015 | 2016Q2 | 2016 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2015-11-29 | N | 125.0502 | N | 4 | N | N | 1.1101 | 39.4971 | 78315.2135
[7 empty] | 11777 | 15706 | 1338553 | 2015-11-30 14:21 | 2015-11-30 15:40 | 79 | 11kV | 158 | 2 | HV | Customer Installation Fault | Customer Installation | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At Zn167 Auburn Ex Panel 17 at S 8103Durbey Suttor No3 11kV RMCB has tripped Customer overloading supply See OMS 1338819 1338553 | November | 2015 | 2016Q2 | 2016 | ZN167:PA17 | ZN167:PA17 | ZN00167/000017 | PARRAMATTA | Unknown | Unknown | 2015-11-30 | N | 79 | N | 6 | N | N | 1.1101 | 39.4971 | 115.4617
[7 empty] | 11643 | 14141 | 1338519 | 2015-11-30 13:12 | 2015-11-30 15:45 | 153 | 11kV | 1530 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 154493 DOLF : 5 Amp Excluded OMS 1338506 & 1338519. | November | 2015 | 2016Q2 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2015-11-30 | N | 153 | N | 6 | N | N | 1.1101 | 39.4971 | 1118.0789
[7 empty] | 11160 | 9493 | 1338488 | 2015-11-30 12:56 | 2015-11-30 16:12 | 196 | 11kV | 55138 | 293 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Recloser 48813 Yarramalong Boys 3.7 Found Open With Hot Line Tag on See OMS 1338809/810/811/812 1338488 1338500 | November | 2015 | 2016Q2 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2015-11-30 | N | 188.1843 | N | 6 | N | N | 1.1101 | 39.4971 | 40293.2241
[7 empty] | 10926 | 6880 | 1338666 | 2015-11-30 16:20 | 2015-11-30 17:30 | 70 | 11kV | 2940 | 42 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LB 40564 was interrupted to remove tree branch from mains near PT13707 Forest Bumble Hill 0.7 See previous trip & reclose of REC49506 #1338820 | November | 2015 | 2016Q2 | 2016 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2015-11-30 | N | 70 | N | 6 | N | N | 1.1101 | 39.4971 | 2148.4653
[7 empty] | 11815 | 16200 | 1338689 | 2015-11-30 17:36 | 2015-11-30 18:46 | 70 | 11kV | 37163 | 568 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 154496 1 fault operation C phase Overcurrent; Earth Fault 11kV Cable fault inside kiosk sub between Sw 41126 and Sw 40896. A few earth fault indicators along this feeder would significantly speed up most future fault locations in this area. Excluded OMS 1338689, 1338694, 1338695 & 1338692. | November | 2015 | 2016Q2 | 2016 | 523:33507 | 523:33507 | ZN00523/033507 | SINGLETON | UG | Not Veg | 2015-11-30 | N | 65.4278 | N | 6 | N | N | 1.1101 | 39.4971 | 27157.6243
[7 empty] | 12182 | 19708 | 1338709 | 2015-11-30 18:59 | 2015-12-01 00:30 | 331 | 11kV | 331 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At Zn1068 Lidcombe ex Panel 11. At S61188 Boorea Nyrang No3 RMCB has tripped on differential. At S61188 Boorea Nyrang No3 RMCB Has Tripped on Diff Suspected TX Failure See OMS 1341054 1338709 | November | 2015 | 2016Q2 | 2016 | ZN1068:PA11 | ZN1068:PA19 | ZN01068/000019 | CUMBERLAND | UG | Not Veg | 2015-11-30 | N | 331 | N | 6 | N | N | 1.1101 | 39.4971 | 241.885
[7 empty] | 11699 | 14813 | 1338825 | 2015-12-01 00:59 | 2015-12-01 01:57 | 58 | 11kV | 1821 | 35 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1290 Leightonfield Panel 10 Tripped on Relays: Earth Fault and EFI Cause: 11kV UG fault between S5539 and S8425 See OMS 1338825 1338829 1338730 | December | 2015 | 2016Q2 | 2016 | ZN1290:PA10 | ZN1290:PA10 | ZN01290/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-12-01 | N | 52.0286 | N | 6 | N | N | 1.1101 | 39.4971 | 1330.7331
[7 empty] | 11091 | 8652 | 1338736 | 2015-12-01 04:19 | 2015-12-01 08:05 | 226 | 11kV | 2260 | 10 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 154501 Single phase DOLF : 5 Amp Excluded OMS 1338736 | December | 2015 | 2016Q2 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2015-12-01 | N | 226 | N | 6 | N | N | 1.1101 | 39.4971 | 1651.5413
[7 empty] | 10937 | 6995 | 1339020 | 2015-12-01 16:14 | 2015-12-01 18:30 | 136 | 11kV | 17090 | 127 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | At PT846 Cressy melba 11kV Centre phase 31.5 Dropout Fuse Operated. At S47709 Cressy Twin 400A fuse blown on C phase of distributor 1 Note: Customers experienced Low Volts Cause; Fuse Fatigue 1339188 1339022 1339022 1338980 | December | 2015 | 2016Q2 | 2016 | ZN35500:PA34 | ZN35500:PA36 | ZN35500/000036 | RYDE | OH | Not Veg | 2015-12-01 | N | 134.5669 | N | 6 | N | N | 1.1101 | 39.4971 | 12488.8679
[7 empty] | 11333 | 11343 | 1339066 | 2015-12-01 17:54 | 2015-12-01 20:10 | 136 | 11kV | 55771 | 811 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 154513 2 fault operations A phase Overcurrent Excluded OMS 1339066 & 1339086 | December | 2015 | 2016Q2 | 2016 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | Unknown | Unknown | 2015-12-01 | N | 68.7682 | N | 6 | N | N | 1.1101 | 39.4971 | 40755.8018
[7 empty] | 11266 | 10586 | 1339096 | 2015-12-01 20:22 | 2015-12-01 23:30 | 188 | 11kV | 14664 | 78 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC 527 Catherine Paul - tripped and reclosed on IOC & Earth Fault. Cause not ascertained. Also around the same time: PT12570 Cassandra Avenue - 31.5 Amp drop out fuse operated. Cause not ascertained. See 1339215 1339216 | December | 2015 | 2016Q2 | 2016 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Veg | 2015-12-01 | N | 188 | N | 6 | N | N | 1.1101 | 39.4971 | 10716.0187
[7 empty] | 12034 | 18380 | 1339006 | 2015-12-01 15:19 | 2015-12-02 07:20 | 961 | 11kV | 12221 | 44 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 154514 2 fault operations A & C phase Overcurrent Truck hit Alfabs pole sub No 853 and caused extensive damage. EMSO G Wuolane did a check of the customers LV board and requested the customer be advised he left the main switch off and his staff or elecrtrician should carry out their own inspection before closing their switch. The customers name is Jason Torrence his mobile is 0412 074 079 and he has already made arrangements with the Maitland ERC to have staff on site before closing his main switches. Their on site number at the factory os 4937 5079. | December | 2015 | 2016Q2 | 2016 | 507:80926 | 507:80926 | ZN00507/080926 | CESSNOCK | OH | Not Veg | 2015-12-01 | N | 277.75 | N | 6 | N | N | 1.1101 | 39.4971 | 8930.7463
[7 empty] | 11782 | 15719 | 1339178 | 2015-12-02 08:25 | 2015-12-02 12:40 | 255 | 11kV | 510 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154530 A & C phase DOLF : 10 Amp Excluded OMS 1339178 | December | 2015 | 2016Q2 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-12-02 | N | 255 | N | 3 | N | N | 1.1101 | 39.4971 | 372.693
[7 empty] | 10576 | 2931 | 1339476 | 2015-12-02 18:31 | 2015-12-02 22:30 | 239 | 11kV | 78792 | 948 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 154536 1 fault operation Protection details required pole fire at SW-31798 Excluded OMS 1339460 - see also T&R 1339537 (LID 154538) | December | 2015 | 2016Q2 | 2016 | 222:33602 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | OH | Not Veg | 2015-12-02 | N | 83.1139 | N | 3 | N | N | 1.1101 | 39.4971 | 57578.8696
[7 empty] | 11752 | 15417 | 1339381 | 2015-12-02 15:42 | 2015-12-02 23:00 | 438 | 11kV | 677158 | 3231 | HV | Animal Bird | Animal | UGOH | Unplanned | Wind Strong | N | Zn35800 Bankstown - Pnl.15L tripped, reclosed, tripped & locked out on: EF, Reclose relay & Lockout Field EFIs: UGOH Cnr Victoria and Owens St Abnormal: S5153 Sw B CLOSED - AB2035 OPEN (Load relief switching) Bird found dead beneath UGOH between AB748 and AB747 tee S1230. UGOH tails also damaged. Second fault - road side Surge arrestor found blown at PT47706. Also multiple LV//'s failed with wires down. See 1339976 1339982 1339983 SE: LV // Failures: 1339984 1339985 1339986 1339987 1339988 | December | 2015 | 2016Q2 | 2016 | ZN35800:PA15 | ZN2310:PA23 | ZN02310/000023 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-12-02 | N | 209.5816 | N | 3 | N | N | 1.1101 | 39.4971 | 494847.0936
[7 empty] | 12158 | 19492 | 1339550 | 2015-12-03 02:19 | 2015-12-03 08:55 | 396 | 11kV | 2772 | 7 | HV | Animal Possum | Animal | Fuse | Unplanned | No Weather Impact | N | PT14302 Wattle tree Knox 11kv Footpath HDO operated Possum on Transformer. 10Amp (10k) HDO fuse operated See 1340702 exclude 1339550 | December | 2015 | 2016Q2 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2015-12-03 | N | 396 | N | 2 | N | N | 1.1101 | 39.4971 | 2025.6958
[7 empty] | 11679 | 14576 | 1339796 | 2015-12-03 15:35 | 2015-12-03 16:29 | 54 | 11kV | 39834 | 794 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10993 Hurstville North - Pnl.39L - tripped, reclosed, tripped & locked out on: Earth Fault, reclose timer, lockout UG cable fault between S47506 Patrick Elizabeth (Sw B) and S10543 The Avenue Bristol (Sw A) See 1340799 1340800 | December | 2015 | 2016Q2 | 2016 | ZN10993:PA39 | ZN10993:PA39 | ZN10993/000039 | GEORGES RIVER | UG | Not Veg | 2015-12-03 | N | 50.1688 | N | 2 | N | N | 1.1101 | 39.4971 | 29109.5123
[7 empty] | 11608 | 13825 | 1339888 | 2015-12-04 07:58 | 2015-12-04 09:05 | 67 | 11kV | 603 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 154560 B Phase DOLF : 20 Amp This Fuse has blown several times in the last 2 years. Possible overload issue. Excluded OMS 1339888 | December | 2015 | 2016Q2 | 2016 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2015-12-04 | N | 67 | N | 3 | N | N | 1.1101 | 39.4971 | 440.6546
[7 empty] | 11440 | 12195 | 1340009 | 2015-12-04 12:18 | 2015-12-04 14:01 | 103 | 11kV | 174373 | 1741 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | @Zn3922 Drummoyne 11kv Panel 14 "S4672 The parade Gipps, etc" feeder tripped Relays: earth leakage, EFI Signals: ZE, Tx1GE Field efi's: S4672, S46991, S35812, S3024, S2116 Remarks: UG fault. Civil works 179 Victoria Remedial Civ access via renwick st. Salem 0404008835. (contruction site)steel bar has hit u/g service | December | 2015 | 2016Q2 | 2016 | ZN3922:PA14 | ZN3922:PA14 | ZN03922/000014 | CANADA BAY | UG | Not Veg | 2015-12-04 | N | 100.1568 | N | 3 | N | N | 1.1101 | 39.4971 | 127426.6453
[7 empty] | 12249 | 20411 | 1340138 | 2015-12-04 18:20 | 2015-12-04 20:30 | 130 | 11kV | 910 | 7 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 154570 OMS Pole FQ50131 moved in ground causing Optical Fibre to be pulled very tight. NOTE: Stay was not installed as originally requested. Optical fibre was loosened off to reduce tension. No Protection. | December | 2015 | 2016Q2 | 2016 | 512:48048 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Not Veg | 2015-12-04 | N | 130 | N | 3 | N | N | 1.1101 | 39.4971 | 665.0012
[7 empty] | 10749 | 4993 | 1340148 | 2015-12-05 02:37 | 2015-12-05 03:20 | 43 | 11kV | 3999 | 93 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow Zone section of Pa3 PT11072 Morven Kent Roadside & Centre phase HDO fuses operated Possum across HDO fuses damaging lightning arrestor See 1340679 exclude 1340148 | December | 2015 | 2016Q2 | 2016 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2015-12-05 | N | 43 | N | 4 | N | N | 1.1101 | 39.4971 | 2922.3512
[7 empty] | 11917 | 17102 | 1340149 | 2015-12-05 03:09 | 2015-12-05 04:50 | 101 | 11kV | 77366 | 766 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn36300 Balgowlah Nth section of Pa1L Bond burnt off AB25105 See 1343193 exclude 1340149 | December | 2015 | 2016Q2 | 2016 | ZN36300:PA1 | ZN36300:PA1 | ZN36300/000001 | NORTHERN BEACHES | OH | Not Veg | 2015-12-05 | N | 101 | N | 4 | N | N | 1.1101 | 39.4971 | 56536.7909
[7 empty] | 10664 | 4024 | 1340159 | 2015-12-05 06:53 | 2015-12-05 09:50 | 177 | 11kV | 177 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 154573 B phase DOLF : 10 Amp Replaced blown Bph LAs. Excluded OMS No. 1340159 | December | 2015 | 2016Q2 | 2016 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2015-12-05 | N | 177 | N | 4 | N | N | 1.1101 | 39.4971 | 129.3464
[7 empty] | 12190 | 19744 | 1340244 | 2015-12-05 17:22 | 2015-12-05 18:30 | 68 | 11kV | 1292 | 19 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn35370 Galston Pa4L At PT329 Cobar Henstock 11kV HDO centre phase blown Cause: tree branch opn OH Mains See OMS 1340245 1340249 1340244 CC1: 22-"Refer to SOp" | December | 2015 | 2016Q2 | 2016 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2015-12-05 | N | 68 | N | 4 | N | N | 1.1101 | 39.4971 | 944.1555
[7 empty] | 11368 | 11605 | 1340280 | 2015-12-06 04:32 | 2015-12-06 05:34 | 62 | 11kV | 17050 | 275 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn2466 Flemington Panel 7 "Carnarvon Day" fdr tripped on Relays: 3 phase O/C EFI and fault check relay Signals: 11kv trip, Tx4 and group earth Field EFI's: Nil Remarks: UG fault. Front line feeder fault from Zn2466 Flemington Panel 7 'Carnarvon Day' to Sub 8376 | December | 2015 | 2016Q2 | 2016 | ZN2466:PA7 | ZN2466:PA7 | ZN02466/000007 | PARRAMATTA | UG | Not Veg | 2015-12-06 | N | 62 | N | 5 | N | N | 1.1101 | 39.4971 | 12459.6371
[7 empty] | 11037 | 7934 | 1340376 | 2015-12-06 16:41 | 2015-12-06 16:49 | 8 | 11kV | 16520 | 2065 | HV | Staff Other | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | @Sub 10991 Blakehurst Zn Panel #12 tripped on: SEL 11kv trip Abnormal: sub 10133 Sw/B closed, IR 62226 open Remarks: Staff error - details below Aop switching error | December | 2015 | 2016Q2 | 2016 | ZN10991:PA12 | ZN10991:PA12 | ZN10991/000012 | GEORGES RIVER | Unknown | Not Veg | 2015-12-06 | N | 8 | N | 5 | N | N | 1.1101 | 39.4971 | 12072.3287
[7 empty] | 11350 | 11505 | 1340427 | 2015-12-06 21:00 | 2015-12-07 05:38 | 518.3333 | 11kV | 30783.3333 | 190 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12660 Woy WOy Pa5 "Empire Bay" fdr tripped on Relays: C Phase Timed Overcurrent Signals: 11kv Trip 11kv OH down between LB62072 & PT13414 Plumber Fishermans See 1340427 exclude 1340439 | December | 2015 | 2016Q2 | 2016 | ZN12660:PA5 | ZN12660:PA5 | ZN12660/000005 | CENTRAL COAST | OH | Not Veg | 2015-12-06 | N | 162.0175 | N | 5 | N | N | 1.1101 | 39.4971 | 22495.552
[7 empty] | 10698 | 4426 | 1340489 | 2015-12-07 09:07 | 2015-12-07 10:50 | 103 | 11kV | 22887 | 223 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12640 Umiona section of Pa7 @PT11150 Springwood Clifford 31.5 Amp footpath phase HDO blown due to fuse fatigue See 1340489 LV// 1340508 exclude 1340494 | December | 2015 | 2016Q2 | 2016 | ZN12640:PA7 | ZN12640:PA7 | ZN12640/000007 | CENTRAL COAST | OH | Not Veg | 2015-12-07 | N | 102.6323 | N | 4 | N | N | 1.1101 | 39.4971 | 16725.1445
[7 empty] | 10934 | 6947 | 1340425 | 2015-12-06 20:57 | 2015-12-07 11:30 | 873 | 11kV | 313930 | 2015 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Zn10990 Arncliffe Zn - pnl.11 - Tripped on: A phase timed O/C, A Phase IOC, Earth Fault, Lockout, Timing, EFI Field EFIs: S10957 & S10126 ELBS indications CP62101: Earth fault, ABC phase OC Pole KO14076 has fallen down. Pole is a stay pole and had stay wire attached for #767 feeder. South OH OC and Transmission OC called in for urgent repairs and replacement of pole. See 1340805 1340806 1340807 | December | 2015 | 2016Q2 | 2016 | ZN10990:PA11 | ZN10998:PA17 | ZN10998/000017 | BAYSIDE | OH | Not Veg | 2015-12-06 | N | 155.7965 | N | 5 | N | N | 1.1101 | 39.4971 | 229410.7846
[7 empty] | 11153 | 9431 | 1340445 | 2015-12-07 04:23 | 2015-12-07 11:32 | 429 | 11kV | 106353 | 421 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 154582 1 fault operation Sensitive Earth Fault 1 phase open cct at ABS 40373. Excluded OMS No. 1340445 | December | 2015 | 2016Q2 | 2016 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2015-12-07 | N | 252.62 | N | 4 | N | N | 1.1101 | 39.4971 | 77719.6355
[7 empty] | 11720 | 15120 | 1340809 | 2015-12-07 10:36 | 2015-12-07 11:40 | 64 | 11kV | 64 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154587 A Phase DOLF : 63 Amp Excluded OMS 1340542 | December | 2015 | 2016Q2 | 2016 |  |  |  | UPPER HUNTER | OH | Veg | 2015-12-07 | N | 64 | N | 4 | N | N | 1.1101 | 39.4971 | 46.7693
[7 empty] | 10995 | 7544 | 1340387 | 2015-12-06 16:47 | 2015-12-07 20:15 | 1648 | 11kV | 19863 | 162 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 154579 UG fault beyond Sw 35221 Mahogany Ridge No.1 sub. Maitland ERC advised to arrange staff. Excluded OMS 1340387 & 1340412 | December | 2015 | 2016Q2 | 2016 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | UG | Not Veg | 2015-12-06 | N | 122.6111 | N | 5 | N | N | 1.1101 | 39.4971 | 14515.2945
[7 empty] | 11631 | 14046 | 1340801 | 2015-12-07 21:15 | 2015-12-07 21:53 | 38 | 11kV | 27398 | 721 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC 63641 Manchester View - tripped and reclosed on Overcurrnet Ex Kirawee ZN P23. Cause not ascertained. Mains to patrol | December | 2015 | 2016Q2 | 2016 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | OH | Veg | 2015-12-07 | N | 38 | N | 4 | N | N | 1.1101 | 39.4971 | 20021.6503
[7 empty] | 10407 | 602 | 1340788 | 2015-12-08 06:27 | 2015-12-08 12:56 | 389 | 11kV | 63331 | 257 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 154595 11kV OHM down at pole FR-62004. Excluded OMS No. 1340788, 1340792 & 1340822. | December | 2015 | 2016Q2 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2015-12-08 | N | 246.4241 | N | 2 | N | N | 1.1101 | 39.4971 | 46280.4269
[7 empty] | 11496 | 12687 | 1341191 | 2015-12-08 20:50 | 2015-12-08 21:55 | 65 | 11kV | 2535 | 39 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154611 B Phase DOLF : 16 Amp Possum on B phase L/A Excluded OMS 1341191 CC1: 22-"Refer to SOp" | December | 2015 | 2016Q2 | 2016 | 217:33612 | 221:11893 | ZN00221/011893 | LAKE MACQUARIE | OH | Not Veg | 2015-12-08 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 1852.5032
[7 empty] | 10935 | 6969 | 1342621 | 2015-12-09 00:15 | 2015-12-09 01:16 | 61 | 11kV | 14457 | 237 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | Section of Panel 33 ex Zn3425 Castle Cove 11kV recloser CP64824 Deepwater Holly Tripped and reclosed on overcurrent Cause: Mains to patrol | December | 2015 | 2016Q2 | 2016 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | OH | Veg | 2015-12-09 | N | 61 | N | 6 | N | N | 1.1101 | 39.4971 | 10564.7492
[7 empty] | 11393 | 11806 | 1341377 | 2015-12-09 07:53 | 2015-12-09 08:05 | 12 | 11kV | 12 | 1 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Rain Light | Y | LID 154615 Branch arcing on tx bushings. exclude OMS 1341377 | December | 2015 | 2016Q2 | 2016 | 239:82132 | 239:82132 | ZN00239/082132 | LAKE MACQUARIE | OH | Veg | 2015-12-09 | Y | 12 | N | 6 | N | Y | 1.1101 | 39.4971 | 8.7692
[7 empty] | 11418 | 12018 | 1341571 | 2015-12-09 11:32 | 2015-12-09 13:37 | 125 | 11kV | 189355 | 1541 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | At S2635 Epping Panel 55 Epping Aus tripped on Relays - earth fault and efi Signals: 11kV trip Abnormal Switching SW/B Closed, SW/A open S2985 SW/B Closed, AB1213 Open Cause: UG cable fault See OMS 1345585 1345589 1341812/597/580/577 | December | 2015 | 2016Q2 | 2016 | ZN2635:PA58 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | UG | Not Veg | 2015-12-09 | Y | 122.878 | N | 6 | N | Y | 1.1101 | 39.4971 | 138375.049
[7 empty] | 10705 | 4456 | 1341667 | 2015-12-09 13:46 | 2015-12-09 16:15 | 149 | 11kV | 149 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | Y | LID 154626 HV DOLF broke causing grass fire - 3 x fuses replaced | December | 2015 | 2016Q2 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2015-12-09 | N | 149 | N | 6 | N | N | 1.1101 | 39.4971 | 108.8848
[7 empty] | 10466 | 1545 | 1341740 | 2015-12-09 15:55 | 2015-12-09 17:30 | 95 | 11kV | 285 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | Y | LID 154628 C Phase 16 A Fuse Operated | December | 2015 | 2016Q2 | 2016 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2015-12-09 | N | 95 | N | 6 | N | N | 1.1101 | 39.4971 | 208.2696
[7 empty] | 11441 | 12198 | 1341797 | 2015-12-09 18:11 | 2015-12-09 20:00 | 109 | 11kV | 42183 | 387 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Lightning | Y | @Zn167 Auburn 11kv Panel 20L "S2951 Station Park etc" feeder tripped Relays: Earth Fault, O/C, E/F, efi Signals: 11kv trip Field EFI's: S2951 Remarks: UG fault. Front line feeder fault. 11kv feeder from Zn167 Auburn Panel 20 to S2951 Station Par to S35622 Auburn Aux No.2 tee S1338 Adderley Station. Note: Dop could not access S1338 Adderley Station. Sw tag @ Auburn Zn | December | 2015 | 2016Q2 | 2016 | ZN167:PA20 | ZN167:PA20 | ZN00167/000020 | PARRAMATTA | UG | Not Veg | 2015-12-09 | Y | 109 | N | 6 | N | Y | 1.1101 | 39.4971 | 30826.0922
[7 empty] | 12004 | 18083 | 1341847 | 2015-12-09 19:56 | 2015-12-09 20:44 | 48 | 11kV | 83616 | 1742 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Zn12600 Lisarow Pa3 "Lisarow High taylor" tripped, reclosed, tripped and locked out on Relays: C phase timed overcurrent, efi, lockout Signals: 11kv trip Lightning. Branch removed by DOp from PT11618 See 1341847 exclude 1341850,2 | December | 2015 | 2016Q2 | 2016 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2015-12-09 | Y | 48 | N | 6 | N | Y | 1.1101 | 39.4971 | 61104.1065
[7 empty] | 11800 | 15969 | 1341821 | 2015-12-09 19:33 | 2015-12-09 20:45 | 72 | 11kV | 5688 | 79 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Secondary Equip | Unplanned | Rain Light | Y | Zn630 Mascot - Pnl.40 tripped on: Earth Fault, A & C phase timed O/C Field EFIs: S5377 Dop Found 11kV/415V Tx No.2 @ S1629 Burrows Rd tripped off. Suspected protection malfunction - relay race. | December | 2015 | 2016Q2 | 2016 | ZN630:PA40 | ZN630:PA40 | ZN00630/000040 | SYDNEY | Exclude | Not Veg | 2015-12-09 | N | 72 | N | 6 | N | N | 1.1101 | 39.4971 | 4156.6226
[7 empty] | 10962 | 7187 | 1341484 | 2015-12-09 19:40 | 2015-12-09 21:20 | 100 | 11kV | 200 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor ABC | Unplanned | No Weather Impact | Y | LID 154630 sub isolated to repair lv bundle box Excluded oms 1341484 | December | 2015 | 2016Q2 | 2016 | 264:81240 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Not Veg | 2015-12-09 | N | 100 | N | 6 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 11040 | 7945 | 1341882 | 2015-12-09 20:33 | 2015-12-09 21:55 | 82 | 11kV | 113819 | 1512 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 154642 2 fault operations Sensitive Earth Fault, Overcurrent no faukt found Include OMS 1342104 exclude OMS 1341882 | December | 2015 | 2016Q2 | 2016 | 223:14394 | 223:14394 | ZN00223/014394 | LAKE MACQUARIE | OH | Veg | 2015-12-09 | Y | 75.2771 | N | 6 | N | Y | 1.1101 | 39.4971 | 83175.5681
[7 empty] | 11933 | 17239 | 1341857 | 2015-12-09 20:07 | 2015-12-09 22:20 | 133 | 11kV | 126616 | 952 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor ABC | Unplanned | Lightning | Y | @Zn2196 Milperra, 11kv Panel 18 "S.4859 Lachlan Cant" feeder tripped Relays: O/C trip, Fault check, efi Signals: ZE, Tx2 GE, 11kv trip Field EFi's: S4859, S4860 Remarks: Lightning, dop patrolled, no damage found. Mains to patrol. Note: Panel 1 @ Btown Zn tripped at the same time. N/O AB608 is common between the two feeders | December | 2015 | 2016Q2 | 2016 | ZN2196:PA18 | ZN2196:PA18 | ZN02196/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-12-09 | Y | 133 | N | 6 | N | Y | 1.1101 | 39.4971 | 92527.2383
[7 empty] | 11079 | 8457 | 1341828 | 2015-12-09 19:40 | 2015-12-09 23:07 | 207 | 11kV | 116352 | 618 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Zn12600 Lisarow Pa1 "Dog Trap Guly" tripped, reclosed and locked out on: Relays: 50TBC, timing, lockout Signals: 11kv trip Remarks: Tree branch on HV mains adjacent to UGOH below S14833 Cambourn Exelsior SwB See 1342533,4,5 exclude 1341828 | December | 2015 | 2016Q2 | 2016 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Veg | 2015-12-09 | Y | 188.2718 | N | 6 | N | Y | 1.1101 | 39.4971 | 85026.6098
[7 empty] | 10599 | 3227 | 1341930 | 2015-12-09 21:06 | 2015-12-09 23:10 | 124 | 11kV | 2604 | 21 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 154643 B Phase DOLF : 16 Amp Suspect faulty Tx Excluded OMS 1341930 | December | 2015 | 2016Q2 | 2016 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2015-12-09 | Y | 124 | N | 6 | N | Y | 1.1101 | 39.4971 | 1902.9264
[7 empty] | 10860 | 6197 | 1341947 | 2015-12-09 21:02 | 2015-12-09 23:11 | 129 | 11kV | 14190 | 110 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Ex Zn15013 section of Pa4 Re21350 Booralie Kalgoa tripped and locked out Relays: overcurrent & lockout Abnormal closed LB25194 Open AB26217 Cause not ascertained. Feeder patrolled no obvious damage, suspect lightning See 1343286 exclude 1341947 | December | 2015 | 2016Q2 | 2016 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2015-12-09 | Y | 129 | N | 6 | N | Y | 1.1101 | 39.4971 | 10369.6335
[7 empty] | 11614 | 13921 | 1341858 | 2015-12-09 20:11 | 2015-12-09 23:13 | 182 | 11kV | 180364 | 1566 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor ABC | Unplanned | Lightning | Y | @Zn1287 Revesby 11kv Panel 21 "S4871 Vega mars" feeder tripped, reclosed, tripped Relays: A phase O/C, L/O, timing relay Signals: 11kv trip Field EFI's: Nil Remarks: lightning. 11kv feeder from LB 1516 to LB 593 to AB 2997 tee PT2161 Steele Sandakan Isolated. Sw/tag left at AB 593. Tree on 11kv o/s 25 Sandakan Rd. PT2161 in LV//: usl's 14631, 13699. See seperated DMA on LB 1516 | December | 2015 | 2016Q2 | 2016 | ZN1287:PA21 | ZN1287:PA21 | ZN01287/000021 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-12-09 | Y | 115.175 | N | 6 | N | Y | 1.1101 | 39.4971 | 131804.6914
[7 empty] | 11848 | 16523 | 1341860 | 2015-12-09 20:07 | 2015-12-09 23:19 | 192 | 11kV | 242682 | 1266 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor ABC | Unplanned | Lightning | Y | @Zn35800 Bankstown 11kv Panel #1 labelled "S.35208 Gow Gibson" tripped: Relays: O/C trip, efi Signals: 11kv trip CB#1 Open, Tx#11 Group Earth Field EFI's: S35208, S7287 Remarks: lightning. See related outage Panel #18 Milperra. EFI on 11kv pole at Irvine St nr Northam Av defective. Mains to patrol | December | 2015 | 2016Q2 | 2016 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-12-09 | Y | 191.6919 | N | 6 | N | Y | 1.1101 | 39.4971 | 177344.8477
[7 empty] | 10591 | 3138 | 1341933 | 2015-12-09 21:08 | 2015-12-09 23:21 | 133 | 11kV | 92381 | 1438 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 154644 2 fault operations C Phase Overcurrent | December | 2015 | 2016Q2 | 2016 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Veg | 2015-12-09 | Y | 64.2427 | N | 6 | N | Y | 1.1101 | 39.4971 | 67509.31
[7 empty] | 11519 | 12837 | 1341868 | 2015-12-09 20:21 | 2015-12-10 00:10 | 229 | 11kV | 142534 | 1420 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | Electrical Storm | Y | LID 154645 2 fault operations B & C phase overcurrent suspected defective HV CCT Excluded 1341868 | December | 2015 | 2016Q2 | 2016 | 239:82129 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2015-12-09 | Y | 100.3761 | N | 6 | N | Y | 1.1101 | 39.4971 | 104159.6432
[7 empty] | 11511 | 12780 | 1341942 | 2015-12-09 21:09 | 2015-12-10 00:20 | 191 | 11kV | 38831 | 237 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15013 Terrey Hills 11kV Panel 6 Relays: A 7 C phase overcurrent + IOC, Reclose Lockout, Reclose Timing Signals: 11kv trip ABNORMAL: Closed LB25194, Open AB26217 11kv isolated between USL24937 to USL24466 tee to PT15377. Tree branch on 11kV OH See 1344148,50,51 exclude 1341942 | December | 2015 | 2016Q2 | 2016 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2015-12-09 | Y | 163.8439 | N | 6 | N | Y | 1.1101 | 39.4971 | 28376.5495
[7 empty] | 12240 | 20323 | 1342077 | 2015-12-09 23:38 | 2015-12-10 01:21 | 103 | 11kV | 33681 | 327 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | Ex Zn15014 Mona Vale section of Pa14 has tripped RE22381 lane Cove Walter Relays: Overcurrent trip, IOC, Lockout Cause not ascertained. Suspect Lightning | December | 2015 | 2016Q2 | 2016 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2015-12-09 | Y | 103 | N | 6 | N | Y | 1.1101 | 39.4971 | 24613.0814
[7 empty] | 11827 | 16315 | 1341887 | 2015-12-09 20:38 | 2015-12-10 01:52 | 314 | 11kV | 8384 | 71 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 154650 C phase OMS No. 1341887 Blown C ph tapping in main line at pole GQ-14620 Excluded OMS 1341887 | December | 2015 | 2016Q2 | 2016 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2015-12-09 | N | 118.0845 | N | 6 | N | N | 1.1101 | 39.4971 | 6126.7799
[7 empty] | 11754 | 15423 | 1342096 | 2015-12-10 01:36 | 2015-12-10 02:32 | 56 | 11kV | 24634 | 1339 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn2635 Epping Panel 52 Interrupted for safety Cause; Possum found on UGOH beneath. Through fault caused HV wires to come down. Panel 52 interrupted for safety 11kV OH down and on fire between AB2162 to SW/A at S8770 tee PT2382. Dop requested interruption for safety | December | 2015 | 2016Q2 | 2016 | ZN2635:PA52 | ZN2635:PA52 | ZN02635/000052 | HORNSBY | OH | Not Veg | 2015-12-10 | N | 18.3973 | N | 39 | Y | Y | 1.1101 | 39.4971 | 18001.8006
[7 empty] | 10509 | 2075 | 1341855 | 2015-12-09 20:14 | 2015-12-10 03:08 | 414 | 11kV | 285579 | 842 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Zn14892 Charmahven Pa14 "Submarine cable" fdr tripped & locked out on Relays: EFI, B+C overcurrent, fault check Signals: 11kv trip Cause not ascertained Suspected lightning strike See 1342624,6,7,8 exclude 1341855 | December | 2015 | 2016Q2 | 2016 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Not Veg | 2015-12-09 | Y | 339.1675 | N | 6 | N | Y | 1.1101 | 39.4971 | 208692.71
[7 empty] | 11803 | 15997 | 1341854 | 2015-12-09 20:12 | 2015-12-10 03:30 | 438 | 11kV | 703695 | 2235 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | Y | Zn14892 Charmhaven Pa16 "Chamrheaven San Remo" fdr tripped & locked out on Relays: A+B phase overcurrent, fault cehck relay, SEL, recloser & timing relay, Lockout Relay, EFI Signals: 11kv trip EFI's: S12884 S46911 Surge Arrestors hit by lightning @ PT13576 Goorama McCrae Footpath phase HDO blown See 1342554,7,8,9,60,1 exclude 1341854 | December | 2015 | 2016Q2 | 2016 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Not Veg | 2015-12-09 | Y | 314.8523 | N | 6 | N | Y | 1.1101 | 39.4971 | 514239.5505
[7 empty] | 12012 | 18177 | 1341937 | 2015-12-09 21:00 | 2015-12-10 04:02 | 422 | 11kV | 407982 | 1673 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 154670 2 fault operations blown l/a at ugoh ju-45243 cut away include OMS 1342471 exclude OMS 1341937 | December | 2015 | 2016Q2 | 2016 | 205:12205 | 205:12205 | ZN00205/012205 | LAKE MACQUARIE | OH | Not Veg | 2015-12-09 | Y | 243.8625 | N | 6 | N | Y | 1.1101 | 39.4971 | 298141.2122
[7 empty] | 11821 | 16245 | 1341910 | 2015-12-09 20:50 | 2015-12-10 04:53 | 483 | 11kV | 240535 | 846 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | Y | LID 154673 2 Fault Operations A Phase Overcurrent Wires down & ugoh blown @ JV-12362. Excluded OMS 1341910. | December | 2015 | 2016Q2 | 2016 | 221:11897 | 221:11897 | ZN00221/011897 | LAKE MACQUARIE | Unknown | Unknown | 2015-12-09 | Y | 284.3203 | N | 6 | N | Y | 1.1101 | 39.4971 | 175775.8834
[7 empty] | 11345 | 11459 | 1342121 | 2015-12-10 03:03 | 2015-12-10 05:45 | 162 | 11kV | 187801 | 1674 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 154674 3 fault operations Overcurrent, Earth Fault BLown arrestor at sub 860 Woodward Street. Prot. 51N Excluded oms1342121 | December | 2015 | 2016Q2 | 2016 | 256:80646 | 256:80646 | ZN00256/080646 | NEWCASTLE | OH | Not Veg | 2015-12-10 | N | 112.187 | N | 39 | Y | Y | 1.1101 | 39.4971 | 137239.4316
[7 empty] | 10572 | 2855 | 1342110 | 2015-12-10 02:20 | 2015-12-10 05:56 | 216 | 11kV | 42378 | 223 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154668 2 fault operations 11kV OHM down at pole | December | 2015 | 2016Q2 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2015-12-10 | N | 190.0359 | N | 39 | Y | Y | 1.1101 | 39.4971 | 30968.5925
[7 empty] | 10786 | 5335 | 1342119 | 2015-12-10 02:59 | 2015-12-10 06:20 | 201 | 11kV | 230349 | 2089 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 154676 1 Fault operation - possible L/A breakdown at Sub 10080 also refer to 1344096 and 1342119 | December | 2015 | 2016Q2 | 2016 | 202:34254 | 202:34254 | ZN00202/034254 | NEWCASTLE | OH | Not Veg | 2015-12-10 | N | 110.2676 | N | 39 | Y | Y | 1.1101 | 39.4971 | 168332.2551
[7 empty] | 11373 | 11647 | 1341914 | 2015-12-09 20:53 | 2015-12-10 07:50 | 657 | 11kV | 351055 | 1591 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | Y | LID 154646 11kV pole 0n ground IU 80268 Possible High inot Low Despatch requested to have EMSO check. Excluded OMS 1341914 | December | 2015 | 2016Q2 | 2016 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2015-12-09 | Y | 220.6505 | N | 6 | N | Y | 1.1101 | 39.4971 | 256540.6396
[7 empty] | 11508 | 12769 | 1344000 | 2015-12-10 05:19 | 2015-12-10 08:30 | 191 | 11kV | 174648 | 1083 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 154679 1 fault operation possible faulty tx 27402 - customers held in LV// Excluded OMS 1342134 | December | 2015 | 2016Q2 | 2016 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2015-12-10 | N | 161.2632 | N | 39 | Y | Y | 1.1101 | 39.4971 | 127627.6072
[7 empty] | 10892 | 6520 | 1342032 | 2015-12-09 19:33 | 2015-12-10 08:44 | 790.7 | 11kV | 300466 | 380 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Ex Zn14891 Wyong section Pa12 "Yarramalong" fdr IR50630 Tarramalong chandlers 0.1 tripped & locked out on overcurrent Tree branch on OH mains See 1341827 exclude 1342032ne | December | 2015 | 2016Q2 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2015-12-09 | Y | 790.7 | N | 6 | N | Y | 1.1101 | 39.4971 | 219571.6906
[7 empty] | 12099 | 18905 | 1342340 | 2015-12-10 02:26 | 2015-12-10 08:55 | 389 | 11kV | 229573 | 597 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154699 2 fault operations B & C phase Overcurrent | December | 2015 | 2016Q2 | 2016 | 227:13018 | 227:13018 | ZN00227/013018 | LAKE MACQUARIE | OH | Veg | 2015-12-10 | N | 384.5444 | N | 39 | Y | Y | 1.1101 | 39.4971 | 167765.1771
[7 empty] | 12183 | 19718 | 1341966 | 2015-12-10 05:55 | 2015-12-10 08:55 | 180 | 11kV | 15840 | 88 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 154693 Substation DOLF Arrestors changed under AP exclude OMS 1341966 | December | 2015 | 2016Q2 | 2016 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2015-12-10 | N | 180 | N | 39 | Y | Y | 1.1101 | 39.4971 | 11575.4048
[7 empty] | 11367 | 11603 | 1342040 | 2015-12-09 22:40 | 2015-12-10 09:50 | 670.4333 | 11kV | 10056.5 | 15 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Electrical Storm | Y | Ex Zn14891 Wyong section of Pa21 PT13920 Bruce Dakara 0.7 Footpath HDO 20amp fuse replaced Lightning See 1342040 exclude 1342189 | December | 2015 | 2016Q2 | 2016 | ZN14891:PA21 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Not Veg | 2015-12-09 | Y | 670.4333 | N | 6 | N | Y | 1.1101 | 39.4971 | 7348.9936
[7 empty] | 10497 | 1978 | 1342125 | 2015-12-10 03:16 | 2015-12-10 10:05 | 409 | 11kV | 409 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 154696 DOLF : 10 Amp Excluded OMS 1342125 | December | 2015 | 2016Q2 | 2016 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2015-12-10 | N | 409 | N | 39 | Y | Y | 1.1101 | 39.4971 | 298.8851
[7 empty] | 10433 | 1016 | 1342115 | 2015-12-10 02:44 | 2015-12-10 10:50 | 486 | 11kV | 295696.4167 | 776 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 154678 2 fault operations Blown arrestor at UGOH pole HS-20087 | December | 2015 | 2016Q2 | 2016 | 507:80923 | 507:80923 | ZN00507/080923 | CESSNOCK | OH | Not Veg | 2015-12-10 | N | 381.0521 | N | 39 | Y | Y | 1.1101 | 39.4971 | 216086.2197
[7 empty] | 11786 | 15745 | 1341822 | 2015-12-09 19:35 | 2015-12-10 11:00 | 925 | 11kV | 22636 | 186 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Electrical Storm | Y | Zn14891 Wyong Pa19 fdr tripped, reclosed & locked out on Relays: C phase timed overcurrent, Earth Fault, EFi, Lockout, Timing Signals: 11k vtrip 2x 11kV UGOHs hit by lightning near AB40001 & S14737 UGOH fault short circuit See1344337,9,40,1 exclude 1341822,2038,653 | December | 2015 | 2016Q2 | 2016 | ZN14891:PA19 | ZN14891:PA19 | ZN14891/000019 | CENTRAL COAST | OH | Not Veg | 2015-12-09 | Y | 121.6989 | N | 6 | N | Y | 1.1101 | 39.4971 | 16541.7212
[7 empty] | 11358 | 11563 | 1342112 | 2015-12-10 02:27 | 2015-12-10 11:14 | 527 | 11kV | 120655 | 257 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 154677 2 fault operations Lightning Arrestors failed on outgoing/load side of Recloser 42067 Excluded OMS 1342112 | December | 2015 | 2016Q2 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2015-12-10 | N | 469.4747 | N | 39 | Y | Y | 1.1101 | 39.4971 | 88171.1153
[7 empty] | 11876 | 16772 | 1342018 | 2015-12-09 22:12 | 2015-12-10 11:32 | 800 | 11kV | 50400 | 63 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | Y | LID 154700 A Phase DOLF : 40 Amp Faulty HV arrestor cut away. Amps as left = 100, 80, 30 Excluded 30OMS 1342018. | December | 2015 | 2016Q2 | 2016 | 261:81876 | 261:81876 | ZN00261/081876 | NEWCASTLE | OH | Not Veg | 2015-12-09 | Y | 800 | N | 6 | N | Y | 1.1101 | 39.4971 | 36830.8335
[7 empty] | 10726 | 4700 | 1342184 | 2015-12-10 07:17 | 2015-12-10 11:35 | 258 | 11kV | 1548 | 6 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 154704 10 amp fuse Substation DOLF exclude OMS 1342184 Removed possum and replaced fuses. | December | 2015 | 2016Q2 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-12-10 | N | 258 | N | 39 | Y | Y | 1.1101 | 39.4971 | 1131.2327
[7 empty] | 10425 | 832 | 1342248 | 2015-12-10 08:12 | 2015-12-10 11:55 | 223 | 11kV | 2007 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154706 16 amp fuse Substation DOLF exclude OMS 1342248 | December | 2015 | 2016Q2 | 2016 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2015-12-10 | N | 223 | N | 39 | Y | Y | 1.1101 | 39.4971 | 1466.6564
[7 empty] | 11768 | 15576 | 1342436 | 2015-12-10 11:11 | 2015-12-10 12:59 | 108 | 11kV | 207169 | 1941 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.18 tripped on: Timed O/C "C" Phase, Earth Fault, Fault Check Field EFIs: S1346, S1688, S8056, S5608, S2947, S35039 UG cable hit by contractor between S35039 Clearly Lakemba (Sw/A) and S35562 Lakemba St Clair (Sw/B) See 1344084 1344085 Other: 1342459 | December | 2015 | 2016Q2 | 2016 | ZN690:PA18 | ZN690:PA18 | ZN00690/000018 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-12-10 | N | 106.7331 | N | 39 | Y | Y | 1.1101 | 39.4971 | 151392.9947
[7 empty] | 10943 | 7043 | 1342216 | 2015-12-10 07:40 | 2015-12-10 13:00 | 320 | 11kV | 1280 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 154709 10 amp fuse Substation DOLF exclude OMS 1342216/2384 | December | 2015 | 2016Q2 | 2016 | 227:13014 | 227:13014 | ZN00227/013014 | LAKE MACQUARIE | OH | Veg | 2015-12-10 | N | 320 | N | 39 | Y | Y | 1.1101 | 39.4971 | 935.3862
[7 empty] | 10515 | 2209 | 1341996 | 2015-12-09 20:44 | 2015-12-10 13:35 | 1011 | 11kV | 1211178 | 1198 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 154869 B Phase tapping on UGOH Jv-12460 | December | 2015 | 2016Q2 | 2016 | 221:11900 | 221:11900 | ZN00221/011900 | LAKE MACQUARIE | OH | Not Veg | 2015-12-09 | Y | 1011 | N | 6 | N | Y | 1.1101 | 39.4971 | 885093.1587
[7 empty] | 10554 | 2645 | 1342247 | 2015-12-10 08:10 | 2015-12-10 14:00 | 349.85 | 11kV | 15393.4 | 44 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 154717 Arestors blown sub left in lv // | December | 2015 | 2016Q2 | 2016 | 224:80329 | 224:80329 | ZN00224/080329 | LAKE MACQUARIE | OH | Not Veg | 2015-12-10 | N | 349.85 | N | 39 | Y | Y | 1.1101 | 39.4971 | 11249.0427
[7 empty] | 11872 | 16713 | 1341960 | 2015-12-09 20:57 | 2015-12-10 14:45 | 1068 | 11kV | 96714 | 423 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Ex Zn12690 Berkeley Vale section of Panel 24L "Berkeley Vale Rd" fdr IR44289 Berkeley Enterprise 0.3 tripped & locked out on overcurrent Tree Branch on Overhaed mains. adjacent to PT11426 Curringa Southfork See 1343122,4,5,6 exclude 1341952,60,2013,91 | December | 2015 | 2016Q2 | 2016 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2015-12-09 | Y | 228.6383 | N | 6 | N | Y | 1.1101 | 39.4971 | 70675.7386
[7 empty] | 11544 | 13050 | 1341866 | 2015-12-09 20:22 | 2015-12-10 16:00 | 1178 | 11kV | 462802 | 1076 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | Y | LID 154665 3 fault operations Sensitive Earth Fault Excluded OMS 1341866 | December | 2015 | 2016Q2 | 2016 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Not Veg | 2015-12-09 | Y | 430.1134 | N | 6 | N | Y | 1.1101 | 39.4971 | 338202.0513
[7 empty] | 11449 | 12223 | 1342572 | 2015-12-10 14:11 | 2015-12-10 16:00 | 109 | 11kV | 11881 | 109 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 154731 Pole fire at Pole IS-68504 Sub restored via LV parallel Excluded OMS 1342572 & 1342496 | December | 2015 | 2016Q2 | 2016 | 235:8685 | 235:8685 | ZN00235/008685 | NEWCASTLE | OH | Not Veg | 2015-12-10 | N | 109 | N | 39 | Y | Y | 1.1101 | 39.4971 | 8682.2844
[7 empty] | 12197 | 19819 | 1342098 | 2015-12-10 01:08 | 2015-12-10 17:00 | 952 | 11kV | 298096 | 1063 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 154671 2 fault operations A & C phase Overcurrent, Earth Fault wires down & high into low Excluded oms1342098 | December | 2015 | 2016Q2 | 2016 | 223:14393 | 223:14393 | ZN00223/014393 | LAKE MACQUARIE | OH | Not Veg | 2015-12-10 | N | 280.429 | N | 39 | Y | Y | 1.1101 | 39.4971 | 217839.7645
[7 empty] | 11634 | 14054 | 1342179 | 2015-12-10 07:13 | 2015-12-10 18:06 | 652.7833 | 11kV | 54833.8 | 84 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 154712 No protection operations. Tapping off at ABS 64395. Repaired by LL crew. | December | 2015 | 2016Q2 | 2016 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2015-12-10 | N | 652.7833 | N | 39 | Y | Y | 1.1101 | 39.4971 | 40070.9237
[7 empty] | 10617 | 3489 | 1342795 | 2015-12-10 17:46 | 2015-12-10 18:20 | 33.5167 | 11kV | 22858.3667 | 682 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Ex Zn12640 Umina section of Pa19 "Ettalong" fdr 11kV AB40672 middle phase bond burnt off CC1: 22-"Refer to SOp" | December | 2015 | 2016Q2 | 2016 | ZN12640:PA19 | ZN12640:PA14 | ZN12640/000014 | CENTRAL COAST | OH | Not Veg | 2015-12-10 | N | 33.5167 | N | 39 | Y | Y | 1.1101 | 39.4971 | 16704.2202
[7 empty] | 10928 | 6892 | 1342174 | 2015-12-10 16:25 | 2015-12-10 18:25 | 120 | 11kV | 5520 | 46 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | No Lid report - switching sheet saved with LIDS Drop Out fuse reported to be out, not stated which phase, customers reporting low volts all day refer to OMS 1342707 and 1342174 | December | 2015 | 2016Q2 | 2016 | 256:80644 | 256:80644 | ZN00256/080644 | NEWCASTLE | OH | Veg | 2015-12-10 | N | 120 | N | 39 | Y | Y | 1.1101 | 39.4971 | 4033.8532
[7 empty] | 10816 | 5644 | 1342581 | 2015-12-10 14:25 | 2015-12-10 18:35 | 250 | 11kV | 293336 | 1194 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154770 2 fault operations A & C phase Overcurrent 1 FAULT DETECTOR AT SW 62045 OPERATED. LINE FUSE 47070 FOUND DOWN C PHASE. RESTORED FDR. Note during this restoration A Phase DOLF : 16 Amp sub 50024:11kV was identified blown at 10/12/2015 14:46:00 and replaced at 10/12/2015 17:20:00 (see LID 154718) Excluded OMS REPORT 134258 | December | 2015 | 2016Q2 | 2016 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2015-12-10 | N | 245.675 | N | 39 | Y | Y | 1.1101 | 39.4971 | 214361.2969
[7 empty] | 11605 | 13794 | 1342658 | 2015-12-10 15:30 | 2015-12-10 18:52 | 202 | 11kV | 136421 | 884 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154780 Reclose off for TOBAN Reclose function nonauto for bush fire season Excluded OMS OMS 1342658 | December | 2015 | 2016Q2 | 2016 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2015-12-10 | N | 154.3224 | N | 39 | Y | Y | 1.1101 | 39.4971 | 99692.4431
[7 empty] | 11157 | 9458 | 1342699 | 2015-12-10 16:03 | 2015-12-10 19:37 | 214.3333 | 11kV | 24648.3333 | 115 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 154777 A & B phase Overcurrent Tree branch on OHM at pole FO-10180. The flashover had caused some arc damage and stranding of the ACSR conductor (Raisin) which required repair and Below the mains they also found a small burnt patch in the grass of about 1m diameter.The weather was a very hot 42 deg with strong westerly winds | December | 2015 | 2016Q2 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2015-12-10 | N | 214.3333 | N | 39 | Y | Y | 1.1101 | 39.4971 | 18012.275
[7 empty] | 10524 | 2335 | 1342709 | 2015-12-10 16:11 | 2015-12-10 20:00 | 228.5833 | 11kV | 6171.75 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154747 20 amp fuse Line DOLF | December | 2015 | 2016Q2 | 2016 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2015-12-10 | N | 228.5833 | N | 39 | Y | Y | 1.1101 | 39.4971 | 4510.1329
[7 empty] | 11807 | 16069 | 1342733 | 2015-12-10 16:28 | 2015-12-10 20:15 | 227 | 11kV | 227 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of Pa1 "Grants Rd" fdr PT11991 Radio Twr Kyola 1.3. two 11kV 16Amp HDO fuses found blown Cause not ascertained See 1343176 exclude 1342733 | December | 2015 | 2016Q2 | 2016 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2015-12-10 | N | 227 | N | 39 | Y | Y | 1.1101 | 39.4971 | 165.8849
[7 empty] | 10904 | 6726 | 1342531 | 2015-12-10 13:32 | 2015-12-10 20:40 | 428 | 11kV | 90047 | 1271 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 154721 SECTION ISOLATED FOR POLE REPAIR | December | 2015 | 2016Q2 | 2016 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Not Veg | 2015-12-10 | N | 70.8474 | N | 39 | Y | Y | 1.1101 | 39.4971 | 65803.6917
[7 empty] | 10458 | 1412 | 1342696 | 2015-12-10 16:00 | 2015-12-10 21:20 | 320 | 11kV | 92244 | 672 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154782 Broken pole FT-32824. Low volts beyond this pole on Fdr 48028 until 1914. Excluded oms 1342696 | December | 2015 | 2016Q2 | 2016 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Veg | 2015-12-10 | N | 137.2679 | N | 39 | Y | Y | 1.1101 | 39.4971 | 67409.1945
[7 empty] | 11521 | 12851 | 1342841 | 2015-12-10 19:23 | 2015-12-10 21:55 | 152 | 11kV | 760 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154741 20 amp fuse Substation DOLF exclude OMS 1342841/864 | December | 2015 | 2016Q2 | 2016 | 524:33578 | 524:33578 | ZN00524/033578 | CESSNOCK | OH | Veg | 2015-12-10 | N | 152 | N | 39 | Y | Y | 1.1101 | 39.4971 | 555.3856
[7 empty] | 10644 | 3803 | 1342803 | 2015-12-10 17:52 | 2015-12-10 22:00 | 248 | 11kV | 496 | 2 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 154743 10 amp fuse Substation DOLF exclude OMS 1342803 | December | 2015 | 2016Q2 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2015-12-10 | N | 248 | N | 39 | Y | Y | 1.1101 | 39.4971 | 362.4622
[7 empty] | 11489 | 12645 | 1342757 | 2015-12-10 16:51 | 2015-12-10 22:45 | 354 | 11kV | 131956 | 1358 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 1344327 SECTION ISOLATED TO REPAIR MAINS UGOH POLE JR50830 TO BE REPAIRED 11.12.15 | December | 2015 | 2016Q2 | 2016 | 238:34140 | 532:83298 | ZN00532/083298 | MAITLAND | Unknown | Unknown | 2015-12-10 | N | 97.1694 | N | 39 | Y | Y | 1.1101 | 39.4971 | 96429.5528
[7 empty] | 10959 | 7161 | 1342766 | 2015-12-10 17:10 | 2015-12-10 22:50 | 340 | 11kV | 1700 | 5 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 154720 16 amp fuse Substation DOLF exclude OMSA 1342766/815 NEIGHBOUR SAW POLE HIT BY LIGTENING POLE NO JR72431 | December | 2015 | 2016Q2 | 2016 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2015-12-10 | N | 340 | N | 39 | Y | Y | 1.1101 | 39.4971 | 1242.3099
[7 empty] | 11585 | 13548 | 1341926 | 2015-12-09 21:02 | 2015-12-10 23:20 | 1578 | 11kV | 444602 | 2267 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | Y | Zn15001 Brookvale Pa18 tripped Relays: Tax1 Earth Fault Check pa18:Lockout, Timing, 18L Fault Check, A phase IOC, Earth Fault, EFI Signals: 11kv trip EFI's S16312 S46338 Suspect lightning hit HV UGOH to S16532 See 1343257,8,9 exclude 1341926,2003,53 | December | 2015 | 2016Q2 | 2016 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | Unknown | Unknown | 2015-12-09 | Y | 196.1191 | N | 6 | N | Y | 1.1101 | 39.4971 | 324902.0281
[7 empty] | 11276 | 10634 | 1342838 | 2015-12-10 19:17 | 2015-12-11 00:30 | 313 | 11kV | 9703 | 31 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 154776 REPLACED 3 11KV ARRESTORS also refer to 1342838 and 13428695 | December | 2015 | 2016Q2 | 2016 | 528:83019 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Not Veg | 2015-12-10 | N | 313 | N | 39 | Y | Y | 1.1101 | 39.4971 | 7090.6662
[7 empty] | 11635 | 14070 | 1342390 | 2015-12-10 10:47 | 2015-12-11 02:25 | 938 | 11kV | 938 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 154730 SECTION ISOLATED FOR REPLACE TX SUB 35714 exclude OMS 1342390 | December | 2015 | 2016Q2 | 2016 | 224:80331 | 224:80331 | ZN00224/080331 | LAKE MACQUARIE | UG | Not Veg | 2015-12-10 | N | 938 | N | 39 | Y | Y | 1.1101 | 39.4971 | 685.4627
[7 empty] | 11806 | 16058 | 1342721 | 2015-12-10 16:21 | 2015-12-11 02:30 | 609.15 | 11kV | 9137.25 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID's 154729 + 154732 20 amp fuse Line DOLF | December | 2015 | 2016Q2 | 2016 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2015-12-10 | N | 609.15 | Y | 39 | N | Y | 1.1101 | 39.4971 | 6677.2328
[7 empty] | 11884 | 16851 | 1342822 | 2015-12-10 18:27 | 2015-12-11 02:55 | 508 | 11kV | 9144 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154733 Single phase DOLF : 10 Amp | December | 2015 | 2016Q2 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | SINGLETON | OH | Veg | 2015-12-10 | N | 508 | N | 39 | Y | Y | 1.1101 | 39.4971 | 6682.1655
[7 empty] | 10577 | 2935 | 1342483 | 2015-12-10 12:15 | 2015-12-11 03:10 | 895 | 11kV | 1790 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154735 10 amp fuse Substation DOLF exclude OMS 1342483 | December | 2015 | 2016Q2 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2015-12-10 | N | 895 | N | 39 | Y | Y | 1.1101 | 39.4971 | 1308.0792
[7 empty] | 11218 | 10052 | 1342870 | 2015-12-10 20:21 | 2015-12-11 03:45 | 444 | 11kV | 444 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | REPLACED DOLF RESTORED AT 0345 - NO FURTHER INFORMATION SUPPLIED, NO lid REPORT | December | 2015 | 2016Q2 | 2016 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2015-12-10 | N | 444 | N | 39 | Y | Y | 1.1101 | 39.4971 | 324.4621
[7 empty] | 10817 | 5658 | 1342920 | 2015-12-11 06:17 | 2015-12-11 07:13 | 56 | 11kV | 41744 | 775 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2634 Epping panel 11 tripped on Relays: IOC, C phase OC, EFI and EF UG cable fault between S7707 and S63381 ex S2634 Epping Pa50 See OMS 1344045 1344051 1342920 | December | 2015 | 2016Q2 | 2016 | ZN2635:PA50 | ZN2635:PA50 | ZN02635/000050 | RYDE | UG | Not Veg | 2015-12-11 | N | 53.8632 | N | 17 | N | N | 1.1101 | 39.4971 | 30505.284
[7 empty] | 10852 | 6099 | 1342990 | 2015-12-11 07:00 | 2015-12-11 08:25 | 85 | 11kV | 170 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154759 10 AMP FUSE Substation DOLF No OMS number due to first job being incorrectly removed from system. re-issued OMS 1342990. Not sure of initial outage time. exclude OMS 1342990 | December | 2015 | 2016Q2 | 2016 | 264:81240 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Veg | 2015-12-11 | N | 85 | N | 17 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 10829 | 5803 | 1342924 | 2015-12-11 06:55 | 2015-12-11 08:35 | 100 | 11kV | 300 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 154757 10 amp fuse Substation DOLF exclude OMS 1342924 | December | 2015 | 2016Q2 | 2016 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2015-12-11 | N | 100 | N | 17 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 12213 | 20048 | 1342836 | 2015-12-10 19:05 | 2015-12-11 08:40 | 815 | 11kV | 815 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 154764 10 amp fuse Substation DOLF exclude OMS 1342836 | December | 2015 | 2016Q2 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2015-12-10 | N | 815 | Y | 39 | N | Y | 1.1101 | 39.4971 | 595.578
[7 empty] | 11145 | 9353 | 1342919 | 2015-12-11 06:13 | 2015-12-11 09:09 | 176.4667 | 11kV | 2999.9333 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 154763 Replaced blown 20 amp C phase HV line fuse CC1: 06-"Urgent - O.H Mains - No others" | December | 2015 | 2016Q2 | 2016 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2015-12-11 | N | 176.4667 | N | 17 | N | N | 1.1101 | 39.4971 | 2192.2628
[7 empty] | 11851 | 16547 | 1342839 | 2015-12-10 19:21 | 2015-12-11 10:10 | 889 | 11kV | 2667 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 154771 10 amp fuse Substation DOLF exclude OMS 1342839 | December | 2015 | 2016Q2 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2015-12-10 | N | 889 | N | 39 | Y | Y | 1.1101 | 39.4971 | 1948.9649
[7 empty] | 11090 | 8643 | 1342714 | 2015-12-10 16:13 | 2015-12-11 10:20 | 1087 | 11kV | 2174 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 154772 Single phase DOLF : 10 Amp Excluded OMS 1342714 | December | 2015 | 2016Q2 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2015-12-10 | N | 1087 | Y | 39 | N | Y | 1.1101 | 39.4971 | 1588.6951
[7 empty] | 10670 | 4096 | 1342785 | 2015-12-10 17:34 | 2015-12-11 10:45 | 1031 | 11kV | 2062 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 154774 DOLF : 10 Amp | December | 2015 | 2016Q2 | 2016 | 511:29877 | 511:29877 | ZN00511/029877 | CESSNOCK | OH | Veg | 2015-12-10 | N | 1031 | N | 39 | Y | Y | 1.1101 | 39.4971 | 1506.8488
[7 empty] | 10398 | 406 | 1342955 | 2015-12-11 08:01 | 2015-12-11 12:10 | 249 | 11kV | 2490 | 10 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 154766 c phase LLC let go and hanging. exclude OMS 1342955 | December | 2015 | 2016Q2 | 2016 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2015-12-11 | N | 249 | N | 17 | N | N | 1.1101 | 39.4971 | 1819.6186
[7 empty] | 11384 | 11760 | 1343119 | 2015-12-11 12:59 | 2015-12-11 13:58 | 59 | 11kV | 85427 | 1888 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 154781 1 fault operation Overcurrent Tree on mains IV-30439. Cleared by DOps. Include OMS 1343770 exclude OMS 1343119 | December | 2015 | 2016Q2 | 2016 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Veg | 2015-12-11 | N | 45.2474 | N | 17 | N | N | 1.1101 | 39.4971 | 62427.5319
[7 empty] | 10459 | 1421 | 1343096 | 2015-12-11 12:18 | 2015-12-11 16:20 | 242 | 11kV | 484 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 154784 10 amp fuse Substation DOLF exclude OMS 1343096 | December | 2015 | 2016Q2 | 2016 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2015-12-11 | N | 242 | N | 17 | N | N | 1.1101 | 39.4971 | 353.6929
[7 empty] | 10629 | 3670 | 1344458 | 2015-12-11 14:48 | 2015-12-11 17:25 | 157 | 11kV | 108577 | 2086 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | LID 154785 2 fault operations UGOH pole JU-22025 failed | December | 2015 | 2016Q2 | 2016 | 257:81987 | 257:81987 | ZN00257/081987 | NEWCASTLE | Unknown | Unknown | 2015-12-11 | N | 52.0503 | N | 17 | N | N | 1.1101 | 39.4971 | 79344.8691
[7 empty] | 11422 | 12057 | 1343178 | 2015-12-11 14:18 | 2015-12-11 17:49 | 211 | 11kV | 139740 | 718 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn35370 Galston Panel; 4 Tripped reclosed tripped and locked out on Overcurrent Cause: DOp Cleared tree branch from 11kV OH near PT329 Cobah Henstock See OMS 1347626 1347627 1347628 See OMS 13443178/180/194/282 | December | 2015 | 2016Q2 | 2016 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2015-12-11 | N | 194.624 | N | 17 | N | N | 1.1101 | 39.4971 | 102117.8704
[7 empty] | 11137 | 9256 | 1342771 | 2015-12-10 17:18 | 2015-12-11 17:50 | 1472 | 11kV | 4416 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 154793 TX 291 isolated HV / LV and dangar tagged,tank black TX Faulty | December | 2015 | 2016Q2 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2015-12-10 | N | 1472 | N | 39 | Y | Y | 1.1101 | 39.4971 | 3227.0826
[7 empty] | 11128 | 9056 | 1343314 | 2015-12-11 15:59 | 2015-12-11 19:45 | 226 | 11kV | 18532 | 82 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At PT247 Kethel Malton HVDO operated Tree branch fell on PT247 | December | 2015 | 2016Q2 | 2016 | ZN965:PA11 | ZN965:PA17 | ZN00965/000017 | HORNSBY | OH | Not Veg | 2015-12-11 | N | 226 | N | 17 | N | N | 1.1101 | 39.4971 | 13542.639
[7 empty] | 11327 | 11195 | 1343730 | 2015-12-11 19:45 | 2015-12-11 20:40 | 55 | 11kV | 13695 | 249 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 154721 SECTION ISOLATED FOR POLE REPAIR | December | 2015 | 2016Q2 | 2016 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Not Veg | 2015-12-11 | N | 55 | N | 17 | N | N | 1.1101 | 39.4971 | 10007.9021
[7 empty] | 10467 | 1569 | 1343271 | 2015-12-11 15:57 | 2015-12-11 20:44 | 286.6833 | 11kV | 9747.2333 | 34 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | lid 154797 16 AMP FUSE Line DOLF TREES IN MAINS BETWEEN POLES EF-90104 & EF-90105, PLEASE ARRANGE FDR MAINTENANCE. | December | 2015 | 2016Q2 | 2016 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-12-11 | N | 286.6833 | N | 17 | N | N | 1.1101 | 39.4971 | 7122.9906
[7 empty] | 10862 | 6210 | 1344432 | 2015-12-11 17:50 | 2015-12-11 21:35 | 225 | 11kV | 960 | 16 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 154792 Bush Fire Section opened for fire near pole IU-77046 | December | 2015 | 2016Q2 | 2016 | 224:80329 | 224:80329 | ZN00224/080329 | LAKE MACQUARIE | OH | Veg | 2015-12-11 | N | 60 | N | 17 | N | N | 1.1101 | 39.4971 | 701.5397
[7 empty] | 10561 | 2737 | 1343407 | 2015-12-11 21:28 | 2015-12-11 23:10 | 102.4 | 11kV | 1024 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 154800 TREE IN 11KV MAINS REPORTED BY D.MYORS MSO. AT POLE CV-53676 UPPER YANGO. | December | 2015 | 2016Q2 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2015-12-11 | N | 102.4 | N | 17 | N | N | 1.1101 | 39.4971 | 748.309
[7 empty] | 12047 | 18471 | 1343416 | 2015-12-11 23:20 | 2015-12-12 00:45 | 85 | 11kV | 59249 | 749 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 154804 3 fault operations Earth fault, Overcurrent Include OMS 1344254/255 exclude OMS 1343416 cable fault Broadmeadow | December | 2015 | 2016Q2 | 2016 | 257:81994 | 257:81994 | ZN00257/081994 | NEWCASTLE | UG | Not Veg | 2015-12-11 | N | 79.1041 | N | 17 | N | N | 1.1101 | 39.4971 | 43297.4217
[7 empty] | 10401 | 492 | 1343430 | 2015-12-12 06:19 | 2015-12-12 07:20 | 61 | 11kV | 305 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 154809 10 amp fuse Substation DOLF exclude OMS 1343430 | December | 2015 | 2016Q2 | 2016 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2015-12-12 | N | 61 | N | 9 | N | N | 1.1101 | 39.4971 | 222.885
[7 empty] | 10680 | 4278 | 1343422 | 2015-12-12 02:57 | 2015-12-12 07:55 | 298 | 11kV | 29576 | 114 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge Pa5 "Somersby" fdr tripped on Relays - SEF Signals: 11kV trip IR61082 Brieses Peats Ridge 0.3 tripped on Relays: overcurrent, SEF, Lockout ABNORMAL: LB62765 closed, AB44636 open & defective Feeder patrolled. No cause found See 1343911,17 2nd Event 1343918,20,1,2,3 Exclude 1343419,22 | December | 2015 | 2016Q2 | 2016 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2015-12-12 | N | 259.4386 | N | 9 | N | N | 1.1101 | 39.4971 | 21613.2685
[7 empty] | 10687 | 4333 | 1343419 | 2015-12-11 23:44 | 2015-12-12 08:15 | 511 | 11kV | 20656 | 286 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa5 "Somersby" IR61082 Brieses Peats Ridge 0.3 tripped, reclosed, tripped, reclosed, tripped & locked out on overcurrent ABNORMAL: LB62765 closed, AB44636 open & defective Tree brought down 11kV OH Down near PT14029 See 1343911,17 2nd Event 1343918,20,1,2,3 Exclude 1343419,22 | December | 2015 | 2016Q2 | 2016 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2015-12-11 | N | 72.2238 | N | 17 | N | N | 1.1101 | 39.4971 | 15094.7956
[7 empty] | 11994 | 18004 | 1342660 | 2015-12-10 15:31 | 2015-12-12 09:15 | 2503.7667 | 11kV | 45067.8 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 154812 2 amp fuse Line DOLF exclude OMS 1343453 Apparently a shorting service wire blew the 2amp line fuse 40470. NOTE CREW DID NOT HAVE A 2 AMP REPLACEMENT FUSE SO USED A 3.15 AMP FUSE. THE CONTROL ROOM WAS NOT MADE AWARE OF THE LARGER FUSE WAS INSTALLED UNTIL AFTER THE FUSES WERE INSTALLED. DEPOT STAFF WILL HAVE TO FOLLOW THIS UP AS THE CORRECT SIZE FUSES WERE NOT INSTALLED. | December | 2015 | 2016Q2 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | SINGLETON | OH | Not Veg | 2015-12-10 | N | 2503.7667 | Y | 39 | N | Y | 1.1101 | 39.4971 | 32934.219
[7 empty] | 11680 | 14580 | 1343294 | 2015-12-11 16:25 | 2015-12-12 12:15 | 1190 | 11kV | 1190 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 154806 40 amp fuse Substation DOLF defective tx replaced dq exclude OMS 1343294 | December | 2015 | 2016Q2 | 2016 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2015-12-11 | N | 1190 | N | 17 | N | N | 1.1101 | 39.4971 | 869.6169
[7 empty] | 10469 | 1612 | 1343470 | 2015-12-12 11:40 | 2015-12-12 12:55 | 75 | 11kV | 150 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 154814 16 amp fuse Substation DOLF exclude OMS 1343470 No cause found | December | 2015 | 2016Q2 | 2016 | 532:83309 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Veg | 2015-12-12 | N | 75 | N | 9 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 10605 | 3277 | 1343478 | 2015-12-12 12:35 | 2015-12-12 13:35 | 60 | 11kV | 960 | 16 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 154813 Broken 11kV insulator conductor on X-arm pole 8L-90252 exclude OMS 1343478 | December | 2015 | 2016Q2 | 2016 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2015-12-12 | N | 60 | N | 9 | N | N | 1.1101 | 39.4971 | 701.5397
[7 empty] | 10846 | 6042 | 1343481 | 2015-12-12 12:42 | 2015-12-12 13:45 | 63 | 11kV | 6501 | 107 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 154815 interupted to make emergency repairs to 33kV fdr above. DQ include OMS 1343804 exclude oms 1343481/482 | December | 2015 | 2016Q2 | 2016 | 222:33602 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | OH | Not Veg | 2015-12-12 | N | 60.757 | N | 9 | N | N | 1.1101 | 39.4971 | 4750.7391
[7 empty] | 10569 | 2828 | 1343412 | 2015-12-12 00:01 | 2015-12-12 17:00 | 1019 | 11kV | 9709 | 12 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 154805 no protection operation Faulty insulators at ABS 20776 Fdr isolated include OMS 1344238 exclude OMS 1343412/415 | December | 2015 | 2016Q2 | 2016 | 224:80329 | 224:80329 | ZN00224/080329 | LAKE MACQUARIE | OH | Not Veg | 2015-12-12 | N | 809.0833 | N | 9 | N | N | 1.1101 | 39.4971 | 7095.0508
[7 empty] | 11347 | 11470 | 1343496 | 2015-12-12 15:03 | 2015-12-12 17:48 | 165 | 11kV | 44715 | 271 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | Related to LID 154778 No Protection operation Isolated to repair 33kV OHM | December | 2015 | 2016Q2 | 2016 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Not Veg | 2015-12-12 | N | 165 | N | 9 | N | N | 1.1101 | 39.4971 | 32676.4031
[7 empty] | 11272 | 10620 | 1343525 | 2015-12-12 18:34 | 2015-12-12 19:34 | 60 | 11kV | 5880 | 98 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 154838 no protection operation section of 11kV fdr isolated to make repairs on 33kV Fdr 3239. exclude oms 1343525 1343526 1343527 | December | 2015 | 2016Q2 | 2016 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Not Veg | 2015-12-12 | N | 60 | N | 9 | N | N | 1.1101 | 39.4971 | 4296.9306
[7 empty] | 11746 | 15348 | 1343520 | 2015-12-12 18:34 | 2015-12-12 19:34 | 60 | 11kV | 1800 | 30 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 154839 no protection operation 11kV Fdr isolated to make repairs on 33kV Fdr 3239 exclude oms 1343520 | December | 2015 | 2016Q2 | 2016 | 206:34437 | 206:34437 | ZN00206/034437 | LAKE MACQUARIE | OH | Not Veg | 2015-12-12 | N | 60 | N | 9 | N | N | 1.1101 | 39.4971 | 1315.3869
[7 empty] | 11637 | 14085 | 1343567 | 2015-12-13 08:13 | 2015-12-13 10:50 | 157 | 11kV | 1413 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge 11kV Pa1 "Grants Rd" fdr PT14542 Finns Greta B phase 10Amp HVDO operated Cause not ascertained. Fuse Fatigue See 1343948 exclude 1343567 | December | 2015 | 2016Q2 | 2016 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2015-12-13 | N | 157 | N | 5 | N | N | 1.1101 | 39.4971 | 1032.5787
[7 empty] | 11960 | 17633 | 1347631 | 2015-12-13 13:22 | 2015-12-13 13:27 | 5 | 11kV | 5585 | 1117 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At S1673 Turramurra Panel 13 tripped on Relays: Earth Fault, Fault CHeck, Under frequency and EFI Signals: Group Earth, Earth Fault trip Cause: PT1609 Failed on energising | December | 2015 | 2016Q2 | 2016 | ZN1673:PA13 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | UG | Not Veg | 2015-12-13 | N | 5 | N | 5 | N | N | 1.1101 | 39.4971 | 4081.3533
[7 empty] | 11250 | 10411 | 1343624 | 2015-12-13 14:28 | 2015-12-13 16:26 | 118 | 11kV | 118 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 154852 10 amp fuse Substation DOLF exclude OMS 1343620/21 | December | 2015 | 2016Q2 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2015-12-13 | N | 118 | N | 5 | N | N | 1.1101 | 39.4971 | 86.2309
[7 empty] | 11405 | 11881 | 1343646 | 2015-12-13 16:27 | 2015-12-13 18:53 | 146 | 11kV | 11357 | 97 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14144 Wamberal section of Pa10 tripped, reclosed and tripped on overcurrent, Earth Fault Trip OH was down outside 319 Matcham rd, matcham See 1343952,3 exclude 1343643,7 | December | 2015 | 2016Q2 | 2016 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2015-12-13 | N | 117.0825 | N | 5 | N | N | 1.1101 | 39.4971 | 8299.3606
[7 empty] | 11299 | 10946 | 1343688 | 2015-12-14 01:15 | 2015-12-14 01:35 | 20.2333 | 11kV | 3985.9667 | 197 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn2400 Berowra Panel 18 CP349 Opened for Safety Cause: Tree on mains Kirk Patrick way near Berowra Waters Rd. - | December | 2015 | 2016Q2 | 2016 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2015-12-14 | N | 20.2333 | N | 4 | N | N | 1.1101 | 39.4971 | 2912.8269
[7 empty] | 10560 | 2735 | 1343691 | 2015-12-14 01:47 | 2015-12-14 02:31 | 44 | 11kV | 45804 | 1041 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn9245 Engadine - Pnl.41 tripped on: Earth Fault and EFI. Field EFIs: S9971, S9965, S9057 Possum at PT9360 Parklands Mimosa | December | 2015 | 2016Q2 | 2016 | ZN9245:PA41 | ZN9245:PA4 | ZN09245/000004 | SUTHERLAND | OH | Not Veg | 2015-12-14 | N | 44 | N | 4 | N | N | 1.1101 | 39.4971 | 33472.2122
[7 empty] | 10590 | 3129 | 1343711 | 2015-12-14 07:46 | 2015-12-14 09:10 | 84 | 11kV | 202679 | 2853 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington - Pnl.26 tripped on: 26R Over Current, Earth Fault and EFI No Field EFi's Operated UG cable fault from P26 to S8252 to S6899 to S778 (Front Line) | December | 2015 | 2016Q2 | 2016 | ZN342:PA26 | ZN342:PA26 | ZN00342/000026 | SYDNEY | UG | Not Veg | 2015-12-14 | N | 71.0407 | N | 4 | N | N | 1.1101 | 39.4971 | 148111.8352
[7 empty] | 10991 | 7530 | 1343686 | 2015-12-13 23:24 | 2015-12-14 11:10 | 706 | 11kV | 3530 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa3 PT13362 Iron bark Kirks 1.7 11kv Paddock side 10amp dropout fuse operated Lightning Surge Arrestor failed See 1344345 exclude 1343686,702 | December | 2015 | 2016Q2 | 2016 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2015-12-13 | N | 706 | N | 5 | N | N | 1.1101 | 39.4971 | 2579.6199
[7 empty] | 10556 | 2689 | 1344082 | 2015-12-14 15:21 | 2015-12-14 18:19 | 178 | 11kV | 1050 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154874 A Phase DOLF : 10 Amp tripped Sw 74365 on DOLF try back B Gowing sub 73105 | December | 2015 | 2016Q2 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2015-12-14 | N | 116.6667 | N | 4 | N | N | 1.1101 | 39.4971 | 767.309
[7 empty] | 11242 | 10265 | 1344191 | 2015-12-15 05:15 | 2015-12-15 06:45 | 90 | 11kV | 93355 | 1372 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1193 Lindfield Panel 26 Tripped on Signals: 11kV trip, Tx4 Group Earth Relays: B phase IOC and EFI Cause: UG cable fault See OMS 1345051 1305053 1344191 | December | 2015 | 2016Q2 | 2016 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | UG | Not Veg | 2015-12-15 | N | 68.043 | N | 10 | N | N | 1.1101 | 39.4971 | 68221.0805
[7 empty] | 11097 | 8687 | 1344627 | 2015-12-15 20:03 | 2015-12-15 20:39 | 36 | 11kV | 36 | 1 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.19 tripped on: B Phase E/F, F/C, EFI Field EFI: S134 UG cable fault between S134 to S88 to S1087 See 1344801 1344800 | December | 2015 | 2016Q2 | 2016 | ZN2602:PA19 | ZN2602:PA36 | ZN02602/000036 | RANDWICK | UG | Not Veg | 2015-12-15 | N | 36 | N | 10 | N | N | 1.1101 | 39.4971 | 26.3077
[7 empty] | 10442 | 1152 | 1344668 | 2015-12-15 22:07 | 2015-12-15 23:30 | 83 | 11kV | 166 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 154904 Single phase DOLF : 3 Amp replaced 2 x 3.15A DOLF's | December | 2015 | 2016Q2 | 2016 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2015-12-15 | N | 83 | N | 10 | N | N | 1.1101 | 39.4971 | 121.3079
[7 empty] | 12000 | 18072 | 1344661 | 2015-12-15 22:35 | 2015-12-15 23:30 | 55 | 11kV | 4235 | 77 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Wind Storm | N | Ex Zn12570 Avoca section of Pa24 PT13766 Vista Del Monte isolated by DOp after fire on 11kv cross arm See 1345317 GIS 1344677 exclude 1344661,6,71,76,9 | December | 2015 | 2016Q2 | 2016 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2015-12-15 | N | 55 | N | 10 | N | N | 1.1101 | 39.4971 | 3094.8131
[7 empty] | 10795 | 5452 | 1344681 | 2015-12-15 23:03 | 2015-12-16 01:50 | 167 | 11kV | 2505 | 15 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 154908 Opened for clearance Interrupted sub 25874 as part of 11kV outage to replace 33kV pin insulator pole IV-60035. see report 154892. | December | 2015 | 2016Q2 | 2016 | 206:34437 | 206:34437 | ZN00206/034437 | LAKE MACQUARIE | OH | Not Veg | 2015-12-15 | N | 167 | N | 10 | N | N | 1.1101 | 39.4971 | 1830.5801
[7 empty] | 12215 | 20059 | 1344659 | 2015-12-15 21:42 | 2015-12-16 03:00 | 317.8167 | 11kV | 4449.4333 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154910 B phase DOLF : 5 Amp | December | 2015 | 2016Q2 | 2016 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2015-12-15 | N | 317.8167 | N | 10 | N | N | 1.1101 | 39.4971 | 3251.5146
[7 empty] | 10665 | 4039 | 1344663 | 2015-12-15 21:52 | 2015-12-16 03:30 | 338.5 | 11kV | 12186 | 36 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 154912 Repaired blown tapping at ABS 43794. | December | 2015 | 2016Q2 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2015-12-15 | N | 338.5 | N | 10 | N | N | 1.1101 | 39.4971 | 8905.1694
[7 empty] | 11910 | 17022 | 1344698 | 2015-12-16 05:08 | 2015-12-16 06:08 | 60 | 11kV | 34746 | 580 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN10999 Kogarah panel 28L "Post Office Derby" fdr tripped Relays: earth fault, efi Signals: 11kv trip Efi's: S10223 Remarks: UG fault from S10223 Post office Derby Sw/B to S10801 Post Office Belgrave Sw/A | December | 2015 | 2016Q2 | 2016 | ZN10999:PA28 | ZN10999:PA28 | ZN10999/000028 | GEORGES RIVER | UG | Not Veg | 2015-12-16 | N | 59.9069 | N | 45 | Y | Y | 1.1101 | 39.4971 | 25391.352
[7 empty] | 11060 | 8180 | 1344694 | 2015-12-16 04:00 | 2015-12-16 06:45 | 164.95 | 11kV | 3628.9 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154913 Single phase DOLF : 20 Amp | December | 2015 | 2016Q2 | 2016 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2015-12-16 | N | 164.95 | N | 45 | Y | Y | 1.1101 | 39.4971 | 2651.8931
[7 empty] | 11875 | 16771 | 1344711 | 2015-12-16 06:31 | 2015-12-16 07:10 | 39 | 11kV | 156 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 154915 Single phase DOLF : 16 Amp | December | 2015 | 2016Q2 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2015-12-16 | N | 39 | N | 45 | Y | Y | 1.1101 | 39.4971 | 114.0002
[7 empty] | 10391 | 348 | 1344727 | 2015-12-16 07:19 | 2015-12-16 07:35 | 16 | 11kV | 48 | 3 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154916 C Phase DOLF : 10 Amp Dead possum found at sub. Excluded OMS NO. 1344727 | December | 2015 | 2016Q2 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2015-12-16 | N | 16 | N | 45 | Y | Y | 1.1101 | 39.4971 | 35.077
[7 empty] | 11707 | 14928 | 1344740 | 2015-12-16 07:38 | 2015-12-16 08:23 | 45 | 11kV | 58711 | 1347 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | REC 20285 Alfred Parr tripped on: EF trip Abnormal: Sw B Closed @ S17070 Victor Redman and USL 23776 open. After Dop opened USL23776 for a job, recloser 20285 tripped on earth fault. No obvious cause was found. DOp measured 130 Amps circulating current after closing Sw B @ S17070. Suspect Protection malfunction See 1345548 1345552 | December | 2015 | 2016Q2 | 2016 | ZN15006:PA8 | ZN15006:PA8 | ZN15006/000008 | NORTHERN BEACHES | OH | Veg | 2015-12-16 | N | 43.5865 | N | 45 | Y | Y | 1.1101 | 39.4971 | 42904.2671
[7 empty] | 12133 | 19215 | 1344705 | 2015-12-16 06:10 | 2015-12-16 09:20 | 190 | 11kV | 950 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 154923 B Phase DOLF : 31 Amp Replaced B phase 31.5 amp spur fuse 64734 Excluded OMS 1344705 | December | 2015 | 2016Q2 | 2016 | 514:18141 | 514:18141 | ZN00514/018141 | SINGLETON | OH | Veg | 2015-12-16 | N | 190 | N | 45 | Y | Y | 1.1101 | 39.4971 | 694.232
[7 empty] | 11887 | 16872 | 1344653 | 2015-12-15 22:20 | 2015-12-16 10:00 | 700 | 11kV | 1400 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 154907 Single phase DOLF : 20 Amp Replaced A phase LF 41057 and DOLFs at sub 53391. Excluded OMS No. 1344715 | December | 2015 | 2016Q2 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-12-15 | N | 700 | N | 10 | N | N | 1.1101 | 39.4971 | 1023.0787
[7 empty] | 10975 | 7351 | 1344787 | 2015-12-16 08:46 | 2015-12-16 10:15 | 89.2333 | 11kV | 3480.1 | 39 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 154936 B Phase DOLF Faulty arrestor replaced under AP. Excluded OMS 1344793 & 1344806 | December | 2015 | 2016Q2 | 2016 | 217:33612 | 221:11893 | ZN00221/011893 | LAKE MACQUARIE | OH | Not Veg | 2015-12-16 | N | 89.2333 | N | 45 | Y | Y | 1.1101 | 39.4971 | 2543.1544
[7 empty] | 11673 | 14508 | 1345507 | 2015-12-16 10:13 | 2015-12-16 10:17 | 4 | 11kV | 2916 | 729 | HV | Staff Other | Utility Process Issue | ZS STS Secondary Equip | Unplanned | No Weather Impact | N | Zn8100 Green Square - Pnl.4 tripped on: Under frequency trip Staff error: Protection fitter (Brett Smith) was working on Panel 4 closing UFLS links nad believe he inadvertently shorted the UF links causing a trip | December | 2015 | 2016Q2 | 2016 | ZN8100:PA4 | ZN8100:PA4 | ZN08100/000004 | SYDNEY | Exclude | Not Veg | 2015-12-16 | N | 4 | N | 45 | Y | Y | 1.1101 | 39.4971 | 2130.9268
[7 empty] | 11328 | 11211 | 1344737 | 2015-12-16 07:39 | 2015-12-16 10:30 | 171 | 11kV | 171 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154938 B Phase DOLF : 10 Amp Excluided OMS 1344737 | December | 2015 | 2016Q2 | 2016 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2015-12-16 | N | 171 | N | 45 | Y | Y | 1.1101 | 39.4971 | 124.9618
[7 empty] | 12131 | 19211 | 1344794 | 2015-12-16 09:55 | 2015-12-16 10:49 | 54 | 11kV | 96174 | 1781 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154934 1 fault operation Reclose function on FDR 83309 was turned off for L/Line work on SI-10295 at time off outage. FDR patrolled to Morpeth. Excluded OMS REPORT NO 1344794. | December | 2015 | 2016Q2 | 2016 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Veg | 2015-12-16 | N | 54 | N | 45 | Y | Y | 1.1101 | 39.4971 | 70281.1225
[7 empty] | 11989 | 17952 | 1345025 | 2015-12-16 12:28 | 2015-12-16 14:04 | 96 | 11kV | 8256 | 86 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154979 no fault found - tech services advised AR didn't work. | December | 2015 | 2016Q2 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2015-12-16 | N | 96 | N | 45 | Y | Y | 1.1101 | 39.4971 | 6033.2413
[7 empty] | 11084 | 8531 | 1345111 | 2015-12-16 13:41 | 2015-12-16 14:15 | 34 | 11kV | 9810 | 660 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Electrical Storm | N | LID 154997 interrupt fdr 74181 to switch around burnt out ABS 74375. | December | 2015 | 2016Q2 | 2016 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2015-12-16 | N | 14.8636 | N | 45 | Y | Y | 1.1101 | 39.4971 | 7168.8587
[7 empty] | 10406 | 564 | 1345796 | 2015-12-16 12:28 | 2015-12-16 14:20 | 112 | 11kV | 784 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154982 C phase DOLF : 10 Amp | December | 2015 | 2016Q2 | 2016 | 513:48056 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2015-12-16 | N | 112 | N | 45 | Y | Y | 1.1101 | 39.4971 | 572.9241
[7 empty] | 12115 | 19062 | 1345048 | 2015-12-16 12:40 | 2015-12-16 14:30 | 110 | 11kV | 17590 | 164 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zone 9035 Caringbah: 11kv Pnl 8 "S9017 Kirimbla Kareena" feeder tripped: "IO" light?, with EFI Signals: 11kv trip, No2 Group earth, Zone earth Remarks: UG fault | December | 2015 | 2016Q2 | 2016 | ZN9035:PA8 | ZN9035:PA8 | ZN09035/000008 | SUTHERLAND | UG | Not Veg | 2015-12-16 | N | 107.2561 | N | 45 | Y | Y | 1.1101 | 39.4971 | 12854.2532
[7 empty] | 11425 | 12074 | 1345094 | 2015-12-16 12:30 | 2015-12-16 14:30 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 154983 C Phase DOLF : 10 Amp | December | 2015 | 2016Q2 | 2016 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2015-12-16 | N | 120 | N | 45 | Y | Y | 1.1101 | 39.4971 | 87.6925
[7 empty] | 11512 | 12796 | 1345108 | 2015-12-16 13:28 | 2015-12-16 14:30 | 62 | 11kV | 124 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154981 10 amp fuse Substation DOLF | December | 2015 | 2016Q2 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2015-12-16 | N | 62 | N | 45 | Y | Y | 1.1101 | 39.4971 | 90.6155
[7 empty] | 11503 | 12730 | 1345183 | 2015-12-16 14:00 | 2015-12-16 14:43 | 43 | 11kV | 2279 | 53 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 154971 interrupt to remove fallen tree at pole BL-10204 | December | 2015 | 2016Q2 | 2016 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2015-12-16 | N | 43 | N | 45 | Y | Y | 1.1101 | 39.4971 | 1665.426
[7 empty] | 11824 | 16291 | 1345020 | 2015-12-16 12:30 | 2015-12-16 15:10 | 160 | 11kV | 1120 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154986 A Phase DOLF : 10 Amp also replaced DOLF sub 64461 | December | 2015 | 2016Q2 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-12-16 | N | 160 | N | 45 | Y | Y | 1.1101 | 39.4971 | 818.463
[7 empty] | 11516 | 12818 | 1345191 | 2015-12-16 14:15 | 2015-12-16 15:10 | 55 | 11kV | 110 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154984 Replace 10 amp HV fuse on sub 53450 exclude OMS 1345191 | December | 2015 | 2016Q2 | 2016 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2015-12-16 | N | 55 | N | 45 | Y | Y | 1.1101 | 39.4971 | 80.3848
[7 empty] | 10985 | 7459 | 1344771 | 2015-12-16 12:58 | 2015-12-16 15:52 | 174 | 11kV | 33273 | 198 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154977 2 fault operations Pole mounted RAGCB, Overcurrent Include OMS 1345554/55/56 exclude OMS 1345074 | December | 2015 | 2016Q2 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-12-16 | N | 168.0455 | N | 45 | Y | Y | 1.1101 | 39.4971 | 24314.927
[7 empty] | 11207 | 9995 | 1345628 | 2015-12-16 12:28 | 2015-12-16 15:55 | 207 | 11kV | 1035 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154987 10 amp fuse Substation DOLF | December | 2015 | 2016Q2 | 2016 | 513:48056 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2015-12-16 | N | 207 | N | 45 | Y | Y | 1.1101 | 39.4971 | 756.3475
[7 empty] | 11774 | 15671 | 1345262 | 2015-12-16 14:00 | 2015-12-16 16:00 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154988 10 amp fuse Substation DOLF Note: customers were also a part of wider area feeder T/R at 16/12/2015 14:09:00 refer to OMS 1345674 and LID 154970 | December | 2015 | 2016Q2 | 2016 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2015-12-16 | N | 120 | N | 45 | Y | Y | 1.1101 | 39.4971 | 87.6925
[7 empty] | 11731 | 15197 | 1345150 | 2015-12-16 12:30 | 2015-12-16 16:15 | 225 | 11kV | 225 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 154978 DOLF : 10 Amp also replace arrestor Excluded oms 1345150 | December | 2015 | 2016Q2 | 2016 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2015-12-16 | N | 225 | N | 45 | Y | Y | 1.1101 | 39.4971 | 164.4234
[7 empty] | 10583 | 3003 | 1345275 | 2015-12-16 14:10 | 2015-12-16 16:20 | 130 | 11kV | 4834 | 1351 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Rain Wind Storm | N | Zn36200 Empire Bay Pa1 tripped and reclosed on Signals: 11k vtrip Relays: Left Leg overcurrent relay 51IOC, EFI NO field EFI's At PT12286 Awinya Empire Bay footpath side 20k HDO operated Mains to Patrol . Suspect lightning See 1345510,1 exclude 1345275 | December | 2015 | 2016Q2 | 2016 | ZN36200:PA1 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2015-12-16 | N | 3.5781 | N | 45 | Y | Y | 1.1101 | 39.4971 | 3532.5446
[7 empty] | 11916 | 17073 | 1344675 | 2015-12-15 22:47 | 2015-12-16 16:29 | 1062 | 11kV | 22979 | 126 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 154902 5 fault operations 3 phase Overcurrent Excluded OMS 1344675 | December | 2015 | 2016Q2 | 2016 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | Unknown | Unknown | 2015-12-15 | N | 182.373 | N | 10 | N | N | 1.1101 | 39.4971 | 16792.3754
[7 empty] | 12237 | 20300 | 1345273 | 2015-12-16 14:00 | 2015-12-16 16:30 | 150 | 11kV | 3450 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154989 20 amp fuse DOLF exclude OMS 1345635 | December | 2015 | 2016Q2 | 2016 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2015-12-16 | N | 150 | N | 45 | Y | Y | 1.1101 | 39.4971 | 2521.1582
[7 empty] | 10500 | 1982 | 1345027 | 2015-12-16 12:31 | 2015-12-16 16:46 | 255 | 11kV | 27145 | 1241 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 154954 2 fault operations 3 phase Earth Fault wires down at pole 5I-40054 Excluded OMS 1345027 | December | 2015 | 2016Q2 | 2016 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2015-12-16 | N | 21.8735 | N | 45 | Y | Y | 1.1101 | 39.4971 | 19836.7654
[7 empty] | 11564 | 13311 | 1344613 | 2015-12-15 19:24 | 2015-12-16 17:05 | 1301 | 11kV | 45261 | 242 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser 3202 Pacific South Cowan tripped reclosed tripped and locked out on O/C and Earth Fault PT1585 South Pacific Cowan Interrupted By Dops for safety - LV distributors Tangled with downed 11kV Cause: 11kV Mains down one span below CP3202 Pacific South Cowan See OMS 1347634 1347635 n1347637 1347636 1347639 1344613 | December | 2015 | 2016Q2 | 2016 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Not Veg | 2015-12-15 | N | 187.0289 | N | 10 | N | N | 1.1101 | 39.4971 | 33075.4038
[7 empty] | 11181 | 9718 | 1345619 | 2015-12-16 14:00 | 2015-12-16 17:10 | 190 | 11kV | 380 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154980 3 amp fuse Substation DOLF exclude OMS 1345619 | December | 2015 | 2016Q2 | 2016 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2015-12-16 | N | 190 | N | 45 | Y | Y | 1.1101 | 39.4971 | 277.6928
[7 empty] | 12180 | 19703 | 1345210 | 2015-12-16 14:12 | 2015-12-16 17:14 | 182 | 11kV | 48860 | 464 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154973 Overcurrent Include OMS 1345680 exclude OMS 1345210/235 10A DOLF replaced sub 11715 | December | 2015 | 2016Q2 | 2016 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Veg | 2015-12-16 | N | 105.3017 | N | 45 | Y | Y | 1.1101 | 39.4971 | 35705.4469
[7 empty] | 11958 | 17614 | 1345344 | 2015-12-16 14:00 | 2015-12-16 17:15 | 195 | 11kV | 2730 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154990 10 amp fused Line DOLF Replaced blown spur fuses CC1: 06-"Urgent - O.H Mains - No others" | December | 2015 | 2016Q2 | 2016 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2015-12-16 | N | 195 | N | 45 | Y | Y | 1.1101 | 39.4971 | 1995.0035
[7 empty] | 11599 | 13709 | 1345304 | 2015-12-16 15:54 | 2015-12-16 17:40 | 106 | 11kV | 9752 | 92 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Electrical Storm | N | LID 154985 B Phase DOLF : 40 Amp Dolf carrier found burnt in 1/2. | December | 2015 | 2016Q2 | 2016 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2015-12-16 | N | 106 | N | 45 | Y | Y | 1.1101 | 39.4971 | 7126.474
[7 empty] | 11456 | 12322 | 1345281 | 2015-12-16 15:27 | 2015-12-16 18:05 | 158 | 11kV | 1738 | 11 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | Ex Zn14891 Wyong Pa20 PT11792 Sandra Hue Hue was found with a 20K footpath side dropout fuse operated Surge arrestor broken and appears to have been struck by lightning. Has been cut away and made safe See 1346782 exclude 1345281,342 | December | 2015 | 2016Q2 | 2016 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2015-12-16 | N | 158 | N | 45 | Y | Y | 1.1101 | 39.4971 | 1270.0791
[7 empty] | 11124 | 8977 | 1344837 | 2015-12-16 09:50 | 2015-12-16 18:10 | 500.4833 | 11kV | 7507.25 | 15 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At PT1308 Silverwater Estate 16A HVDO fuse blown Cause: Resident reported a lightning strike prior to interruption Please see OMS 11344837 1345060 CC1: 06-"Urgent - O.H Mains - No others" | December | 2015 | 2016Q2 | 2016 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2015-12-16 | N | 500.4833 | N | 45 | Y | Y | 1.1101 | 39.4971 | 5486.0769
[7 empty] | 10484 | 1781 | 1345694 | 2015-12-16 14:30 | 2015-12-16 18:12 | 222 | 11kV | 1554 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154991 10 amp fuse Substation DOLF SWER tx | December | 2015 | 2016Q2 | 2016 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-12-16 | N | 222 | N | 45 | Y | Y | 1.1101 | 39.4971 | 1135.6174
[7 empty] | 10370 | 18 | 1345297 | 2015-12-16 15:00 | 2015-12-16 18:13 | 193 | 11kV | 193 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154992 10 amp fuse Substation DOLF | December | 2015 | 2016Q2 | 2016 |  |  |  |  | OH | Veg | 2015-12-16 | N | 193 | N | 45 | Y | Y | 1.1101 | 39.4971 | 141.0387
[7 empty] | 10825 | 5744 | 1345358 | 2015-12-16 16:53 | 2015-12-16 18:20 | 87 | 11kV | 4089 | 47 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Ex Zn14891 Wyong section of Pa21 PT1431 Ninian De Lisle was found to have the centre and roadside 31K HDO fuses operated Cause not ascertained See 1345359 exclude 1345358 | December | 2015 | 2016Q2 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2015-12-16 | N | 87 | N | 45 | Y | Y | 1.1101 | 39.4971 | 2988.1206
[7 empty] | 11275 | 10633 | 1344874 | 2015-12-16 10:30 | 2015-12-16 18:25 | 475 | 11kV | 4080 | 24 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At sub 9534 Kurnell Sth, panel 18 "Kurnell Aux No 1" fdr opened, closed and opened on O/C, with auto reclose lockout and EFI. Feeder down between Sub 48890 Kurnell Aux No 1 to Sub 9535 Catptain Sir Joseph also refer to OMS 1348111 | December | 2015 | 2016Q2 | 2016 | ZN9534:PA18 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2015-12-16 | N | 170 | N | 45 | Y | Y | 1.1101 | 39.4971 | 2981.5437
[7 empty] | 10812 | 5605 | 1345084 | 2015-12-16 13:06 | 2015-12-16 18:27 | 321 | 11kV | 23678 | 134 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154993 2 fault operations Earth fault include OMS 1345577/78/80/81/82/83 esxclude OMS 1345084/376 | December | 2015 | 2016Q2 | 2016 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-12-16 | N | 176.7015 | N | 45 | Y | Y | 1.1101 | 39.4971 | 17303.184
[7 empty] | 11801 | 15976 | 1344832 | 2015-12-16 09:38 | 2015-12-16 18:40 | 542 | 11kV | 8746 | 54 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | N | Cp3281 Bay Copper ex Zn2400 Berowra Panel 18 Tripped reclosed tripped and locked out on Ovhercurrent and earth fault Cause; Flames seen shooting out of lightning arrestor at PT2066 See OMS 1347603 1347605 1347604 1344832 1345060 | December | 2015 | 2016Q2 | 2016 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2015-12-16 | N | 161.963 | N | 45 | Y | Y | 1.1101 | 39.4971 | 6391.3188
[7 empty] | 11000 | 7610 | 1345284 | 2015-12-16 15:31 | 2015-12-16 20:40 | 309 | 11kV | 309 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 155001 Single fuse DOLF : 10 Amp replace tx - SAO to come Excluded OMS 1345284 | December | 2015 | 2016Q2 | 2016 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | UG | Not Veg | 2015-12-16 | N | 309 | N | 45 | Y | Y | 1.1101 | 39.4971 | 225.8081
[7 empty] | 11129 | 9096 | 1345420 | 2015-12-16 18:40 | 2015-12-16 20:50 | 130 | 11kV | 650 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 155004 31 amp fuse Substation DOLF exclude OMS 1345420 | December | 2015 | 2016Q2 | 2016 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2015-12-16 | N | 130 | N | 45 | Y | Y | 1.1101 | 39.4971 | 475.0008
[7 empty] | 10707 | 4489 | 1345417 | 2015-12-16 18:07 | 2015-12-16 21:25 | 198 | 11kV | 198 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 155006 10 amp fuse Substation DOLF exclude OMS 1345417 | December | 2015 | 2016Q2 | 2016 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2015-12-16 | N | 198 | N | 45 | Y | Y | 1.1101 | 39.4971 | 144.6926
[7 empty] | 11256 | 10453 | 1345449 | 2015-12-16 20:18 | 2015-12-16 21:40 | 82 | 11kV | 41292 | 664 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 155000 3 fault operations sub 17148 faulty - restored via LV parallel | December | 2015 | 2016Q2 | 2016 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2015-12-16 | N | 62.1867 | N | 45 | Y | Y | 1.1101 | 39.4971 | 30174.9757
[7 empty] | 10873 | 6313 | 1345338 | 2015-12-16 16:31 | 2015-12-17 00:05 | 454 | 11kV | 2270 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 155003 A Phase DOLF : 10 Amp replace L/A's Sub 43968 (3 phase) Excluded OMS 1345338 | December | 2015 | 2016Q2 | 2016 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2015-12-16 | N | 454 | N | 45 | Y | Y | 1.1101 | 39.4971 | 1658.849
[7 empty] | 11258 | 10492 | 1345547 | 2015-12-17 08:23 | 2015-12-17 09:45 | 82 | 11kV | 164 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Previous Storm | N | Ex Zn12630 Peats Ridge Zone section of Pa4 PT14537 Peats Ridge 11kv Centre Phase HDO found blown Possibly form previous storm. Volts taken at a customer switchboard to prove healthy after HDO replaced. 244V 245V 246V See 1346842 exclude 1345547 | December | 2015 | 2016Q2 | 2016 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2015-12-17 | N | 82 | N | 4 | N | N | 1.1101 | 39.4971 | 119.8464
[7 empty] | 11323 | 11163 | 1345418 | 2015-12-16 18:16 | 2015-12-17 11:55 | 1059 | 11kV | 3177 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 155013 10 amp fuse Substation DOLF Blown LAs | December | 2015 | 2016Q2 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-12-16 | N | 1059 | N | 45 | Y | Y | 1.1101 | 39.4971 | 2321.6579
[7 empty] | 11483 | 12608 | 1345446 | 2015-12-16 20:01 | 2015-12-17 12:20 | 979 | 11kV | 10769 | 11 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Previous Storm | N | Ex Zn14891 Wyong Zn section of Pa20 "THe Warnervale" fdr PT11792 Sandra Hue Hue footpath 20Amp HDO fuse blown Fuse Failure See 1345448 exclude 1345446 CC1: 22-"Refer to SOp" | December | 2015 | 2016Q2 | 2016 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2015-12-16 | N | 979 | N | 45 | Y | Y | 1.1101 | 39.4971 | 7869.6676
[7 empty] | 10380 | 197 | 1345748 | 2015-12-17 11:48 | 2015-12-17 14:00 | 132 | 11kV | 132 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 155023 A Phase 16A DOLF operated during storm | December | 2015 | 2016Q2 | 2016 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Veg | 2015-12-17 | N | 132 | N | 4 | N | N | 1.1101 | 39.4971 | 96.4617
[7 empty] | 10810 | 5567 | 1371702 | 2015-12-17 07:32 | 2015-12-17 16:30 | 538 | 11kV | 47344 | 88 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | D/R#373083A/1 | December | 2015 | 2016Q2 | 2016 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | Unknown | Unknown | 2015-12-17 | N | 538 | N | 4 | N | N | 1.1101 | 39.4971 | 34597.5988
[7 empty] | 10538 | 2460 | 1345957 | 2015-12-17 18:44 | 2015-12-17 21:55 | 191 | 11kV | 191 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 155025 B Phase 10A DOLF Operated | December | 2015 | 2016Q2 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2015-12-17 | N | 191 | N | 4 | N | N | 1.1101 | 39.4971 | 139.5772
[7 empty] | 11268 | 10610 | 1346082 | 2015-12-18 10:15 | 2015-12-18 10:40 | 25 | 11kV | 125 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 155031 Feeder isolated to repair low 11kV OHM from pole SM-20003 to sub 71969. Include OMS 1346789 exclude OMS No. 1346082/087 | December | 2015 | 2016Q2 | 2016 | 813:89062 | 813:89058 | ZN00813/089058 | UPPER HUNTER | OH | Not Veg | 2015-12-18 | N | 25 | N | 5 | N | N | 1.1101 | 39.4971 | 91.3463
[7 empty] | 11017 | 7726 | 1346130 | 2015-12-18 11:11 | 2015-12-18 11:28 | 17 | 11kV | 36584 | 2152 | HV | Staff Operation | Utility Process Issue | Circuit Breaker | Unplanned | No Weather Impact | N | LID 155033 1 fault operation Local backup Include OMS 1347481/82/83 exclude OMS 1346130/853 S Groves working on CB 34140 under AP see SI 10745 initiated a back up protection trip to the 11kV section 2 bus tripping CB's 34146, 34145, 34144, 34143, 34141, 34139. All feeders restored at 1128hrs. Note feeder 34140 was supplied from feeder 34136 (no customers interupted.) | December | 2015 | 2016Q2 | 2016 | 238:34143 | 238:34143 | ZN00238/034143 | MAITLAND | Unknown | Not Veg | 2015-12-18 | N | 17 | N | 5 | N | N | 1.1101 | 39.4971 | 26734.5082
[7 empty] | 10448 | 1258 | 1346075 | 2015-12-18 10:15 | 2015-12-18 12:30 | 135 | 11kV | 540 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 155032 Repair 2 broken insulators at pole FL-90087. | December | 2015 | 2016Q2 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2015-12-18 | N | 135 | N | 5 | N | N | 1.1101 | 39.4971 | 394.6161
[7 empty] | 11957 | 17613 | 1346203 | 2015-12-18 12:00 | 2015-12-18 13:40 | 100 | 11kV | 1000 | 10 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 155035 exclude OMS No. 1346203 Replace condemned pole 8L-70082 | December | 2015 | 2016Q2 | 2016 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2015-12-18 | N | 100 | N | 5 | N | N | 1.1101 | 39.4971 | 730.7705
[7 empty] | 11447 | 12216 | 1346342 | 2015-12-19 08:36 | 2015-12-19 09:50 | 74 | 11kV | 74 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 155047 10 amp fuse Substation DOLF exclude OMS 1346342 | December | 2015 | 2016Q2 | 2016 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2015-12-19 | N | 74 | N | 9 | N | N | 1.1101 | 39.4971 | 54.077
[7 empty] | 11577 | 13430 | 1346348 | 2015-12-19 09:02 | 2015-12-19 11:05 | 123 | 11kV | 123 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 155048 10 amp fuse Substation DOLF exclude OMS 1346348 | December | 2015 | 2016Q2 | 2016 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2015-12-19 | N | 123 | N | 9 | N | N | 1.1101 | 39.4971 | 89.8848
[7 empty] | 10723 | 4638 | 1346360 | 2015-12-19 10:36 | 2015-12-19 12:00 | 84 | 11kV | 3612 | 43 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT49602 Kulgoa Bristol - Footpath phase 63A HDO operated Fuse Fatigue | December | 2015 | 2016Q2 | 2016 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | OH | Not Veg | 2015-12-19 | N | 84 | N | 9 | N | N | 1.1101 | 39.4971 | 2639.5431
[7 empty] | 12051 | 18492 | 1346336 | 2015-12-18 23:22 | 2015-12-19 14:33 | 911.4333 | 11kV | 80206.1333 | 88 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn2400 Berowra seciton of pa18 "berowra waters" fdr RE3227 Berowra Creek tripped, reclosed, tripped and locked out Tree/branch brought OH down. beyond AB540 See 1346315 exclude 1346336,8 | December | 2015 | 2016Q2 | 2016 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2015-12-18 | N | 911.4333 | N | 5 | N | N | 1.1101 | 39.4971 | 58612.2766
[7 empty] | 10743 | 4910 | 1346415 | 2015-12-19 13:51 | 2015-12-19 15:30 | 99 | 11kV | 198 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 155051 100 amp fuse burnt up fuse assembly exclude OMS 1346405/415 | December | 2015 | 2016Q2 | 2016 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2015-12-19 | N | 99 | N | 9 | N | N | 1.1101 | 39.4971 | 144.6926
[7 empty] | 12208 | 19943 | 1346431 | 2015-12-19 15:21 | 2015-12-19 17:00 | 99.4667 | 11kV | 3381.8667 | 34 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 155052 burnt b phase llc | December | 2015 | 2016Q2 | 2016 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2015-12-19 | N | 99.4667 | N | 9 | N | N | 1.1101 | 39.4971 | 2471.3684
[7 empty] | 11792 | 15859 | 1346445 | 2015-12-19 16:21 | 2015-12-19 17:30 | 69 | 11kV | 138 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 155054 10 amp fuse Substation DOLF FUSE HAS DROPPED OUT ON POLE TX IN PADDOCK. 1 PHASE DOWN exclude OMS 1346445 | December | 2015 | 2016Q2 | 2016 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-12-19 | N | 69 | N | 9 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 11065 | 8256 | 1348060 | 2015-12-19 16:40 | 2015-12-19 18:10 | 90 | 11kV | 3510 | 39 | HV | Bushfire | Adverse Weather/Environment | Pole | Unplanned | Hot >35C | N | LID 1550536 Isolated section of 11kV mains to complete repairs after pole replacement from bush fire see earlier LIDs 155039 and 155040 (OMS 1346279) | December | 2015 | 2016Q2 | 2016 | 229:34983 | 233:82818 | ZN00233/082818 | PORT STEPHENS | OH | Veg | 2015-12-19 | N | 90 | N | 9 | N | N | 1.1101 | 39.4971 | 2565.0045
[7 empty] | 11563 | 13307 | 1346486 | 2015-12-19 20:13 | 2015-12-19 21:37 | 84 | 11kV | 15120 | 180 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 155056 isolated for repair broken dead end at abs 74412 exclude OMS 1346486 | December | 2015 | 2016Q2 | 2016 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2015-12-19 | N | 84 | N | 9 | N | N | 1.1101 | 39.4971 | 11049.25
[7 empty] | 11058 | 8125 | 1346465 | 2015-12-19 18:33 | 2015-12-20 01:00 | 387 | 11kV | 143255 | 2130 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca Pa37L fdr tripped on Signals: 11kv Trip Relays: A+B Phase IOC No field EFI's Large tree branch on 11kv OH outside 148 hillside Rd, Avoca beach. Feeder Isoalted & Earthed from AB40431 to S14561:A tee PT13570 & PT13921. Lineworker required to clear See 1346903,4,5,6,7 exclude 1346465,470,92 | December | 2015 | 2016Q2 | 2016 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2015-12-19 | N | 67.2559 | N | 9 | N | N | 1.1101 | 39.4971 | 104686.5287
[7 empty] | 12148 | 19356 | 1346517 | 2015-12-20 03:35 | 2015-12-20 09:25 | 350 | 11kV | 36750 | 105 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 155058 PFA CALL - Car hit pole GW-60017, LV OHM down, 11kV ties broken No LVF blown. Sub 13029 isolated Exclude OMS 1346517/520 | December | 2015 | 2016Q2 | 2016 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2015-12-20 | N | 350 | N | 8 | N | N | 1.1101 | 39.4971 | 26855.8161
[7 empty] | 10881 | 6416 | 1346524 | 2015-12-20 06:30 | 2015-12-20 09:25 | 175 | 11kV | 20125 | 115 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 155059 Isolate 11kV mains for repairs after MVA pole GW-60017. exclude OMS 1346524 | December | 2015 | 2016Q2 | 2016 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2015-12-20 | N | 175 | N | 8 | N | N | 1.1101 | 39.4971 | 14706.7564
[7 empty] | 10606 | 3281 | 1346533 | 2015-12-20 08:17 | 2015-12-20 09:53 | 96 | 11kV | 768 | 8 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 155060 SECTION ISOLATED TO BREAK TAPS AT FAULTY ABS 13885 OFF WOLLOMBI RD FOR SI 10163 TO BE COMPLETED exclude OMS 1346533/534 | December | 2015 | 2016Q2 | 2016 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2015-12-20 | N | 96 | N | 8 | N | N | 1.1101 | 39.4971 | 561.2317
[7 empty] | 11199 | 9916 | 1346558 | 2015-12-20 10:41 | 2015-12-20 18:41 | 480 | 11kV | 1920 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | No LID Report found - no further information available SMITH, GRAHAM WAYNE LOW VOLTS ON 1 PHASE. HIGH VOLTAGE FUSE HAS DROPPED OUT FROM POLE TX. REPORTED E/C ERROL ELLIOTT. | December | 2015 | 2016Q2 | 2016 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2015-12-20 | N | 480 | N | 8 | N | N | 1.1101 | 39.4971 | 1403.0794
[7 empty] | 10582 | 2973 | 1346637 | 2015-12-20 18:18 | 2015-12-20 19:43 | 85 | 11kV | 200570 | 2419 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn3299 Drummoyne - Pnl.5 tripped on: A phase timed O/C, EFI and Fault Check No Field EFIs Front line feeder from Panel 5 to S36165 tee S2401 and S1528 | December | 2015 | 2016Q2 | 2016 | ZN3922:PA5 | ZN3922:PA5 | ZN03922/000005 | INNER WEST | UG | Not Veg | 2015-12-20 | N | 82.9144 | N | 8 | N | N | 1.1101 | 39.4971 | 146570.6402
[7 empty] | 10831 | 5816 | 1346650 | 2015-12-20 19:11 | 2015-12-20 20:25 | 74 | 11kV | 130864 | 1769 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Primary Equip | Unplanned | Wind Strong | N | Zn12650 West Gosford Pa13 "Hanlan St" fdr tripped Relays: Nil Signals: Nil EFI's: Nil Protection Malfunction. Only indication from fault was an in display on screen. No flags or local alarms. No cause was found and no credible reports were received. TPE to investigate See 1346924,6 exclude 1346650 | December | 2015 | 2016Q2 | 2016 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | Exclude | Not Veg | 2015-12-20 | N | 73.9763 | N | 8 | N | N | 1.1101 | 39.4971 | 95631.5514
[7 empty] | 10803 | 5504 | 1346675 | 2015-12-20 23:00 | 2015-12-21 01:11 | 131 | 11kV | 189450 | 1646 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn15014 Mona Vale - Pnl.5L tripped on: Overcurrent B & C phase phase, T1 on SEF relay Field EFIs: S15186 & S16847 Cause not ascertained See 1346779 1346780 1346781 | December | 2015 | 2016Q2 | 2016 | ZN15014:PA5 | ZN15014:PA5 | ZN15014/000005 | NORTHERN BEACHES | OH | Veg | 2015-12-20 | N | 115.0972 | N | 8 | N | N | 1.1101 | 39.4971 | 138444.4722
[7 empty] | 11504 | 12744 | 1347226 | 2015-12-20 14:25 | 2015-12-21 12:30 | 1325 | 11kV | 18243 | 141 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 155068 AND 155069 1 fault operation Pole mounted RAGCB Wire on ground police reported bushfire started from fallen ohm Include OMS 1347228 exclude OMS 1346588 | December | 2015 | 2016Q2 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2015-12-20 | N | 129.383 | N | 8 | N | N | 1.1101 | 39.4971 | 13331.4463
[7 empty] | 12035 | 18389 | 1346811 | 2015-12-21 11:31 | 2015-12-21 12:42 | 71 | 11kV | 79699 | 1307 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15012 Kilarney - Pnl.2 tripped on: Earth Fault, Fault Check and EFI Field EFIs: S16552 S15797 S16553 S15569 S14140 S16555 S16632 UG cable fault between S16632 Starky Westmeath (Sw B) and S15418 Starky O'Connell (Sw A) See 1347319 1347321 1347322 | December | 2015 | 2016Q2 | 2016 | ZN15012:PA2 | ZN15012:PA2 | ZN15012/000002 | NORTHERN BEACHES | UG | Not Veg | 2015-12-21 | N | 60.9786 | N | 8 | N | N | 1.1101 | 39.4971 | 58241.6785
[7 empty] | 10916 | 6809 | 1347004 | 2015-12-21 16:38 | 2015-12-21 17:30 | 51.9333 | 11kV | 363.5333 | 7 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | Ex Zn14891 Wyong seciton of Pa5 "Wyong" fdr DOp opened 11kV LB42066 for safety. 11kv Cross arm broken at PT11875 Dunks Watagan 0.8 | December | 2015 | 2016Q2 | 2016 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2015-12-21 | N | 51.9333 | N | 8 | N | N | 1.1101 | 39.4971 | 265.6594
[7 empty] | 11344 | 11452 | 1347053 | 2015-12-21 17:50 | 2015-12-21 18:25 | 35 | 11kV | 490 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 155083 10 amp fuse Line DOLF exclude OMS 1347053/58 | December | 2015 | 2016Q2 | 2016 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2015-12-21 | N | 35 | N | 8 | N | N | 1.1101 | 39.4971 | 358.0775
[7 empty] | 10692 | 4381 | 1347024 | 2015-12-21 17:16 | 2015-12-21 19:15 | 119 | 11kV | 321929 | 4191 | HV | Animal Bird | Animal | Air Break Switch | Unplanned | Rain Heavy | N | Ex Zn4545 Meadowbank section of Pa36 RE46118 Dalton Blaxland has tripped Relays: IOC trip, OC trip and LO Bird @ AB448. See outage at Top Ryde at same time. See 1347287,8 2nd 1347295,8,300 Exclude 1347024,5,6,35,44,6,7,8,9 | December | 2015 | 2016Q2 | 2016 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2015-12-21 | N | 76.8144 | N | 8 | N | N | 1.1101 | 39.4971 | 235256.2179
[7 empty] | 10498 | 1979 | 1347087 | 2015-12-21 18:24 | 2015-12-21 19:40 | 76 | 11kV | 3268 | 43 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Heavy | N | Ex Zn965 Pennant Hills section of Pa33 PT1726 Duneba Apanie footpath side HDO has blown 50AMP Tree branch at PT1726 See 1347323 exclude 1347087,9,95,7 | December | 2015 | 2016Q2 | 2016 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Veg | 2015-12-21 | N | 76 | N | 8 | N | N | 1.1101 | 39.4971 | 2388.158
[7 empty] | 10403 | 528 | 1347096 | 2015-12-21 18:58 | 2015-12-21 21:24 | 146 | 11kV | 8737 | 62 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Rain Heavy | N | Ex Zn14891 Wyong section of Pa5 "Wyong" fdr 11kV Re45083 DUrren tripped on overcurrent Defective link 41028 See 1347250,1 exclude 1347096,105 | December | 2015 | 2016Q2 | 2016 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2015-12-21 | N | 140.9194 | N | 8 | N | N | 1.1101 | 39.4971 | 6384.7419
[7 empty] | 11108 | 8780 | 1347130 | 2015-12-21 20:38 | 2015-12-21 22:00 | 82 | 11kV | 164 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 155186 10 amp fuse Substation DOLF CALLER REPORTS A LIGHNING STRIKE ON A POLE SHARED WITH NEIGHBOURS FOLLOWED BY A LOSS OF ALL PWR exclude OMS 1347130 | December | 2015 | 2016Q2 | 2016 | 511:29877 | 511:29877 | ZN00511/029877 | CESSNOCK | OH | Not Veg | 2015-12-21 | N | 82 | N | 8 | N | N | 1.1101 | 39.4971 | 119.8464
[7 empty] | 11279 | 10652 | 1347154 | 2015-12-21 22:13 | 2015-12-21 23:30 | 77 | 11kV | 10963 | 159 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 155087 3 fault operations Earth fault Blown L/A at JS-60030 include OMS 1347252/54/55 exclude OMS 1347154 | December | 2015 | 2016Q2 | 2016 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2015-12-21 | N | 68.9497 | N | 8 | N | N | 1.1101 | 39.4971 | 8011.437
[7 empty] | 10925 | 6871 | 1347257 | 2015-12-22 00:39 | 2015-12-22 03:50 | 191 | 11kV | 3959 | 159 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 155087 3 fault operations Earth fault Blown L/A at JS-60030 include OMS 1347258 | December | 2015 | 2016Q2 | 2016 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2015-12-22 | N | 24.8994 | N | 12 | N | N | 1.1101 | 39.4971 | 2893.1204
[7 empty] | 11490 | 12647 | 1347170 | 2015-12-22 02:58 | 2015-12-22 06:02 | 184 | 11kV | 256969 | 2691 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | Zn12620 Noraville Zone Pa 1 Left tripped on C phase overcurrent EFI HV UGOH fault between S14068 & Re41873 See 1347263,7,8,9 Exclude 1347170 | December | 2015 | 2016Q2 | 2016 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | Unknown | Unknown | 2015-12-22 | N | 95.492 | N | 12 | N | N | 1.1101 | 39.4971 | 187785.3659
[7 empty] | 11270 | 10617 | 1347280 | 2015-12-22 09:17 | 2015-12-22 09:49 | 32 | 11kV | 55616 | 1738 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Heavy | N | Zn2196 Milperra - Pnl.25 tripped on: B & C phase timed O/C Field EFIs: S4684 S4276 S8790 S5371 IS 35 failed which is Normally open between Revesby P23 and Milperra P25. Failed on the Revesby side but caused Milperra P25 to trip. See #1247280 See 1347753 1347280 | December | 2015 | 2016Q2 | 2016 | ZN2196:PA25 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-12-22 | N | 32 | N | 12 | N | N | 1.1101 | 39.4971 | 40642.5324
[7 empty] | 11842 | 16482 | 1347293 | 2015-12-22 09:27 | 2015-12-22 12:38 | 191 | 11kV | 50977 | 555 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Heavy | N | LID 155090 Overcurrent section isolated for repairs include OMS 1347874 exclude OMS 1347293/412 | December | 2015 | 2016Q2 | 2016 | 513:48052 | 513:83503 | ZN00513/083503 | SINGLETON | OH | Not Veg | 2015-12-22 | N | 91.8505 | N | 12 | N | N | 1.1101 | 39.4971 | 37252.488
[7 empty] | 11072 | 8317 | 1347271 | 2015-12-22 09:08 | 2015-12-22 16:10 | 422 | 11kV | 3014 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12650 West Gosford section of Pa1 "Dog trap rd" fdr 11kv Re45010 Palm Grove tripped , reclosed, tripped Relays: OC trip LO Signals: trip 11kv mains down 11kv fdr isoalted form LK43412 to PT12537 to PT12553 AP to LW issued at LK43412 See 1347813,4 exclude 1347271 | December | 2015 | 2016Q2 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2015-12-22 | N | 177.2941 | N | 12 | N | N | 1.1101 | 39.4971 | 2202.5423
[7 empty] | 12227 | 20206 | 1348159 | 2015-12-22 18:44 | 2015-12-22 18:52 | 8 | 11kV | 2168 | 271 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Rain Light | N | LID 155094 Incomming A phase link at Bridgeman recloser has fallen out and will not remain closed. Recloser was bypassed to restore network to normal. | December | 2015 | 2016Q2 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-12-22 | N | 8 | N | 12 | N | N | 1.1101 | 39.4971 | 1584.3105
[7 empty] | 11397 | 11819 | 1347664 | 2015-12-22 20:04 | 2015-12-22 20:30 | 26 | 11kV | 45994 | 1769 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Primary Equip | Unplanned | Rain Heavy | N | Zn12650 West Gosford 11kv Pa13 "Hanlan st" fdr tripped on no indication. Protection Malfunction. Repeat trip on no indication. TPE to investigate | December | 2015 | 2016Q2 | 2016 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | Exclude | Not Veg | 2015-12-22 | N | 26 | N | 12 | N | N | 1.1101 | 39.4971 | 33611.0586
[7 empty] | 10514 | 2176 | 1347689 | 2015-12-22 20:53 | 2015-12-22 22:15 | 82 | 11kV | 4836 | 66 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn14143 Somersby Pa14 "Ace Aust Conveyor Enf" fdr tripped on Relays: E/F, EFI Signals: Tx2 Group Earth, 11kv trip EFI's S14458 S18149 S18268 S18670 S18516 S14856 S14957 S18103 UG fault See 1347840,1 exclude 1347689 | December | 2015 | 2016Q2 | 2016 | ZN14143:PA14 | ZN14143:PA14 | ZN14143/000014 | CENTRAL COAST | UG | Not Veg | 2015-12-22 | N | 73.2727 | N | 12 | N | N | 1.1101 | 39.4971 | 3534.0062
[7 empty] | 10716 | 4556 | 1347651 | 2015-12-22 19:18 | 2015-12-22 22:50 | 212 | 11kV | 14020 | 283 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Zn12600 Lisarow section of Pa2 "Holgate" fdr 11kv RE41845 North Erina tripped on overcurrent Wires down outside 17 manor hill close. Tree branch brought down OH See 1347824,6,7 exclude 1347651,5,9,88 | December | 2015 | 2016Q2 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2015-12-22 | N | 49.5406 | N | 12 | N | N | 1.1101 | 39.4971 | 10245.4025
[7 empty] | 10614 | 3458 | 1347687 | 2015-12-22 20:51 | 2015-12-22 23:10 | 139 | 11kV | 834 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 155096 10 amp fuse Substation DOLF exclude OMS 1347687 | December | 2015 | 2016Q2 | 2016 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-12-22 | N | 139 | N | 12 | N | N | 1.1101 | 39.4971 | 609.4626
[7 empty] | 10826 | 5755 | 1347698 | 2015-12-22 21:38 | 2015-12-22 23:15 | 97 | 11kV | 7275 | 75 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | PT9514 Caravan Farrar - Road side phase HDO 50A fuse operated Possible tree branch found near PT | December | 2015 | 2016Q2 | 2016 | ZN9252:PA28 | ZN9252:PA28 | ZN09252/000028 | SUTHERLAND | OH | Veg | 2015-12-22 | N | 97 | N | 12 | N | N | 1.1101 | 39.4971 | 5316.3554
[7 empty] | 10868 | 6269 | 1347709 | 2015-12-22 22:31 | 2015-12-23 00:20 | 109 | 11kV | 327 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 155097 Phase C Fuse Size: 10 Amp No cause found not storm conditions | December | 2015 | 2016Q2 | 2016 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2015-12-22 | N | 109 | N | 12 | N | N | 1.1101 | 39.4971 | 238.962
[7 empty] | 11740 | 15235 | 1347879 | 2015-12-23 11:20 | 2015-12-23 12:45 | 85 | 11kV | 85 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 155100 16 amp fuse Sectionaliser exclude OMS 1347879 | December | 2015 | 2016Q2 | 2016 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2015-12-23 | N | 85 | N | 4 | N | N | 1.1101 | 39.4971 | 62.1155
[7 empty] | 10714 | 4549 | 1348003 | 2015-12-23 16:40 | 2015-12-23 17:45 | 65 | 11kV | 195 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 155103 Blown disk insulator found on pole AL-10126. Isolated for safety to repair. exclude OMS 1348003/4 | December | 2015 | 2016Q2 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2015-12-23 | N | 65 | N | 4 | N | N | 1.1101 | 39.4971 | 142.5002
[7 empty] | 11934 | 17249 | 1347893 | 2015-12-23 11:59 | 2015-12-23 20:00 | 481 | 11kV | 19240 | 40 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | No Weather Impact | N | Ex Zn12690 Berkelev Vale section of Pa24 S18726 BURNS PACIFIC hit by kiosk See 1348953 exclude 1347893 | December | 2015 | 2016Q2 | 2016 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | Unknown | Not Veg | 2015-12-23 | N | 481 | N | 4 | N | N | 1.1101 | 39.4971 | 14060.0245
[7 empty] | 11545 | 13063 | 1347858 | 2015-12-23 10:40 | 2015-12-23 20:45 | 605 | 11kV | 55724 | 283 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 155102 Earth fault Fault at sub 54144. LV x-arm & links broken. NOTE. Recloser was found with a Work tag applied. This meant the reclose function was diabled and only instantaious element operational. This meeant a far larger outage was experienced that was necessary include OMS 1348135 exclude OMS 1347858/897/942 | December | 2015 | 2016Q2 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2015-12-23 | N | 196.9046 | N | 4 | N | N | 1.1101 | 39.4971 | 40721.4556
[7 empty] | 11682 | 14599 | 1348046 | 2015-12-24 00:18 | 2015-12-24 08:35 | 497 | 11kV | 9567 | 21 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 155105 Crossarm broken at pole 3H-80067 | December | 2015 | 2016Q2 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2015-12-24 | N | 455.5714 | N | 2 | N | N | 1.1101 | 39.4971 | 6991.2814
[7 empty] | 11647 | 14191 | 1348322 | 2015-12-24 23:45 | 2015-12-25 00:50 | 65 | 11kV | 4030 | 62 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty section of Pa25 EFI down with fault check relay EFI:'s S18095 @PT11560 Lynwood Lakeside roadside HDO 31.5 Amp fuse operated. Lightning Surge Arrestor appears damaged See 1348941 exclude 1348322,3,5 | December | 2015 | 2016Q2 | 2016 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2015-12-24 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 2945.0051
[7 empty] | 11210 | 10014 | 1348356 | 2015-12-25 10:49 | 2015-12-25 13:07 | 138 | 11kV | 74717 | 1283 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | S12650 West Gosford Panel 6 "SCC Racecourse" fdr tripped, reclosed, tripped and locked out. Relays: A phase IOC, reclose timer, lockout Signals: 11kv trip Remarks: tree/branch on OH mains. Large tree branch feel on 11kv mains outside No.7 Jirrang Rd causing 11kv to sag into the low. EMSO checked services and gave clearnace to re-energise | December | 2015 | 2016Q2 | 2016 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Veg | 2015-12-25 | N | 58.2362 | N | 3 | N | N | 1.1101 | 39.4971 | 54600.9798
[7 empty] | 10770 | 5165 | 1348377 | 2015-12-25 15:37 | 2015-12-26 01:55 | 618 | 11kV | 140793 | 236 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby Pa17 "Somersby Falls" Fdr Signals: Tx2 Group Earth Panel 17 EFI EFI's: S18569 S18639 IR61922 Pacifric Bar Point founr tripped. (Note: Trip not inidcated in control room & can't interrogate what tripped on as intelliruptor not cpommunicating properly. Tree rbought down 11kv & 415V Overhead outside 4 cheero point road. (no indication of HV contacting LV). 11kV isoalted & Earthed AB42508 to AB43257 tee PT113520, PT11368. See 1349864,7,8 exclude 1348377 | December | 2015 | 2016Q2 | 2016 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2015-12-25 | N | 596.5805 | N | 3 | N | N | 1.1101 | 39.4971 | 102887.3717
[7 empty] | 11044 | 7976 | 1349456 | 2015-12-26 01:38 | 2015-12-26 02:50 | 72 | 11kV | 36739 | 623 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn965 Pennant Hills Pa12 fdr CB tripped on Signals: 11kv trip, Zone Earth, Group Eartrh Relays: A+C phase timed EFI EFI's: S7444 S7248 Possum shorted across & damaged HV UGOH to S7248 See 1349456,7,8 exclude 1348422,4 | December | 2015 | 2016Q2 | 2016 | ZN965:PA12 | ZN965:PA13 | ZN00965/000013 | HORNSBY | OH | Not Veg | 2015-12-26 | N | 58.9711 | N | 3 | N | N | 1.1101 | 39.4971 | 26847.7776
[7 empty] | 10702 | 4448 | 1348446 | 2015-12-26 08:48 | 2015-12-26 09:45 | 57 | 11kV | 114 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 155108 A Phase 10A DOLF Operated | December | 2015 | 2016Q2 | 2016 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-12-26 | N | 57 | N | 3 | N | N | 1.1101 | 39.4971 | 83.3078
[7 empty] | 10371 | 40 | 1348508 | 2015-12-26 14:06 | 2015-12-26 15:16 | 70 | 11kV | 77310 | 1229 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | No Weather Impact | N | Zn9900 Menai 11kv fdr pa1 tripped Relays: Right side EFI timer, lockout overcurrent Signals: 11kv trip zone earth, Group Earth Lightning struck UGOH connection on S998/3 side fo river crossing See 1349477,8 exclude 1348508 | December | 2015 | 2016Q2 | 2016 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | OH | Not Veg | 2015-12-26 | N | 62.9048 | N | 3 | N | N | 1.1101 | 39.4971 | 56495.8677
[7 empty] | 11388 | 11786 | 1348413 | 2015-12-25 23:13 | 2015-12-26 21:00 | 1307 | 11kV | 160675 | 266 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn12620 Noraville section of Pa1L RE47817 Buff point Elouera Tripped on overcurrent Car hit pole in Buff point rd (Corner Karanagal Cres) Buff Point. See 1349426,7 exclude 1348413,5,53 | December | 2015 | 2016Q2 | 2016 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2015-12-25 | N | 604.0414 | N | 3 | N | N | 1.1101 | 39.4971 | 117416.5509
[7 empty] | 11228 | 10157 | 1348617 | 2015-12-27 08:07 | 2015-12-27 08:51 | 43.7833 | 11kV | 77978.1167 | 1781 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 155111 Tree on OHM near sub 14446 Northumberland St No. 2 Tree cleared, no damage to OHM A Prot A & B O/C B Prot A & B O/C Aph = 1.131kA, Bph=1.039kA, Cph=159A | December | 2015 | 2016Q2 | 2016 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Veg | 2015-12-27 | N | 43.7833 | N | 4 | N | N | 1.1101 | 39.4971 | 56984.1077
[7 empty] | 11758 | 15456 | 1348609 | 2015-12-27 07:33 | 2015-12-27 10:00 | 147 | 11kV | 735 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 155112 A Phase 10A DOLF Operated | December | 2015 | 2016Q2 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2015-12-27 | N | 147 | N | 4 | N | N | 1.1101 | 39.4971 | 537.1163
[7 empty] | 11530 | 12953 | 1348585 | 2015-12-27 03:47 | 2015-12-27 11:30 | 463 | 11kV | 41058 | 362 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 "Wyong" RE45101 Jilliby Danks tripped on overcurrent & IOC Large branch on CCT near LB45103 See 1349433,4,5,6 exclude 1348585,91 | December | 2015 | 2016Q2 | 2016 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2015-12-27 | N | 113.4199 | N | 4 | N | N | 1.1101 | 39.4971 | 30003.9754
[7 empty] | 10636 | 3728 | 1348689 | 2015-12-27 16:55 | 2015-12-27 20:20 | 205 | 11kV | 61529 | 1045 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn9037 Miranda Pa2 tripped Relays AC phase timed overcurrent, EFI, Lockout , TIming SIgnals: 11kv trip, Zone Earth broken HV crossarm See 1349482,3,4,5 exclude 1348689,715 | December | 2015 | 2016Q2 | 2016 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Not Veg | 2015-12-27 | N | 58.8794 | N | 4 | N | N | 1.1101 | 39.4971 | 44963.5784
[7 empty] | 11928 | 17210 | 1348860 | 2015-12-28 21:08 | 2015-12-28 22:15 | 67 | 11kV | 9319 | 2257 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9700 Kirawee Zone Pa17 "Hotham Badteo" tripped and reclosed Relays: Aphse leakage, timing lockout, EFI, FC, relay Signals: F/C Tx3 EFI's: S9048 S9587 S9838 S9807 LB49932 Dead possum found at UGOH between PT9721 & S9112. Suspected bond off UGOH. See 1349487,8 exclude 1348860,4 | December | 2015 | 2016Q2 | 2016 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Not Veg | 2015-12-28 | N | 4.1289 | N | 1 | N | N | 1.1101 | 39.4971 | 6810.0503
[7 empty] | 11480 | 12588 | 1348881 | 2015-12-29 07:37 | 2015-12-29 09:01 | 84 | 11kV | 94718 | 1170 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 155121 Bang reported from Houston Sub 50874 - nothing found 1 Fault operation, overcurrent, no cause found, not storm condition, also see OMS 1348881 Note: AR was Non auto for Fire season | December | 2015 | 2016Q2 | 2016 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2015-12-29 | N | 80.9556 | N | 3 | N | N | 1.1101 | 39.4971 | 69217.1207
[7 empty] | 12193 | 19777 | 1348909 | 2015-12-29 08:53 | 2015-12-29 09:40 | 47 | 11kV | 23429 | 621 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn340 Botany Pa2 "Edgehill Ave" fdr opened on Earth fault S6340 Bay McFall endbox failed See 1349491,2,3 exclude 1348909,13 | December | 2015 | 2016Q2 | 2016 | ZN340:PA2 | ZN340:PA45 | ZN00340/000045 | BAYSIDE | UG | Not Veg | 2015-12-29 | N | 37.7279 | N | 3 | N | N | 1.1101 | 39.4971 | 17121.2222
[7 empty] | 10844 | 6017 | 1349036 | 2015-12-29 14:25 | 2015-12-29 15:40 | 75 | 11kV | 225 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 155123 16 Amp fuse, no cause found not storm conditions see 1349036 | December | 2015 | 2016Q2 | 2016 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Veg | 2015-12-29 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 164.4234
[7 empty] | 11019 | 7732 | 1349105 | 2015-12-30 05:59 | 2015-12-30 06:54 | 55 | 11kV | 77880 | 1416 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 155127 2 Fault operations, Earth Fault | December | 2015 | 2016Q2 | 2016 | 504:48034 | 522:83129 | ZN00522/083129 | CESSNOCK | OH | Veg | 2015-12-30 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 56912.4069
[7 empty] | 10414 | 656 | 1349113 | 2015-12-30 08:00 | 2015-12-30 10:45 | 165 | 11kV | 8250 | 50 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 155124 Blown tapping at Link Fuse 40438 CC1: 22-"Refer to SOp" | December | 2015 | 2016Q2 | 2016 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Not Veg | 2015-12-30 | N | 165 | N | 4 | N | N | 1.1101 | 39.4971 | 6028.8567
[7 empty] | 11158 | 9468 | 1349257 | 2015-12-30 16:24 | 2015-12-30 18:30 | 126 | 11kV | 378 | 3 | HV | Burnt Contacts | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 155129 Broken live line dropper also see 1349257 | December | 2015 | 2016Q2 | 2016 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2015-12-30 | N | 126 | N | 4 | N | N | 1.1101 | 39.4971 | 276.2313
[7 empty] | 11046 | 8013 | 1349283 | 2015-12-30 23:57 | 2015-12-31 01:20 | 83 | 11kV | 19920 | 240 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa5 "Somserby fdr" USL 41866 centre phase HV Link open circuit See 1349440 exclude 1349283 | December | 2015 | 2016Q2 | 2016 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2015-12-30 | N | 83 | N | 4 | N | N | 1.1101 | 39.4971 | 14556.9485
[7 empty] | 11482 | 12601 | 1349287 | 2015-12-31 00:42 | 2015-12-31 02:45 | 123 | 11kV | 100259 | 1212 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15002 Narrabaeen Pa2 tripped on A&C phase lockout, reclose, time delay, frame leakage Tree on 11kV outside 36 Allawah rd See 1349450,1,2 exclude 1349287,9,95 | December | 2015 | 2016Q2 | 2016 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2015-12-31 | N | 82.7219 | N | 3 | N | N | 1.1101 | 39.4971 | 73266.3201
[7 empty] | 11099 | 8726 | 1349385 | 2015-12-31 11:43 | 2015-12-31 13:00 | 77 | 11kV | 231 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 155131 Wire about to come off pin at AK-40011 Excluded OMS 1349385/6/7. | December | 2015 | 2016Q2 | 2016 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2015-12-31 | N | 77 | N | 3 | N | N | 1.1101 | 39.4971 | 168.808
[7 empty] | 11204 | 9951 | 1349399 | 2015-12-31 13:10 | 2015-12-31 13:22 | 12 | 11kV | 42000 | 3500 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Primary Equip | Unplanned | No Weather Impact | N | Zn3155 Double Bay 11kv 4A Group Bar (Panels 27,28,30,31,32,34_ was de-energised when switching Tx2 Back on load. It appears when the 11kv 4B Circuit breaker was opened at the same time. The 11kV 4A CB was in the de-acitvated state at teh time and therefore did not show any change of state. See 1350068 exclude 1349399,400,14 | December | 2015 | 2016Q2 | 2016 | ZN3155:PA32 | ZN3155:PA32 | ZN03155/000032 | WOOLLAHRA | Exclude | Not Veg | 2015-12-31 | N | 12 | N | 3 | N | N | 1.1101 | 39.4971 | 30692.3612
[7 empty] | 12044 | 18461 | 1349560 | 2016-01-01 15:35 | 2016-01-01 19:30 | 235 | 11kV | 44445 | 253 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12620 Noraville section of Pa13 "Wallarah Point" @ 11kv USL42034 bond off centre phase @S14497 Bann Beachomber Sw/B interrupted for safety/repair @18:45 See 1349903 2nd 1349904 Exclude 1349560 | January | 2016 | 2016Q3 | 2016 | ZN12620:PA13 | ZN12620:PA13 | ZN12620/000013 | CENTRAL COAST | OH | Not Veg | 2016-01-01 | N | 175.6719 | N | 2 | N | N | 1.1101 | 39.4971 | 32479.0951
[7 empty] | 10747 | 4984 | 1349577 | 2016-01-01 17:42 | 2016-01-01 19:50 | 128 | 11kV | 384 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn35370 Galston section of Pa8 @PT706 Peebles rd, roadside phase found blown Ultra fuse S1 Patch 517 Fuse Fatigue See 1350017 exclude 1349577 | January | 2016 | 2016Q3 | 2016 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2016-01-01 | N | 128 | N | 2 | N | N | 1.1101 | 39.4971 | 280.6159
[7 empty] | 11823 | 16259 | 1349604 | 2016-01-02 05:59 | 2016-01-02 07:26 | 87 | 11kV | 133579 | 1547 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3472 Sefton Pa33 "Wrights York" fdr tripped on Relays: Earth Fault with Fault check Signals: 11kv trip, EFUI and Zone Earth EFI's: S2771 UG Fault between S2771 to S4295 to S35181 See 1350062,3 exclude 1349604 | January | 2016 | 2016Q3 | 2016 | ZN3472:PA33 | ZN3472:PA33 | ZN03472/000033 | CUMBERLAND | UG | Not Veg | 2016-01-02 | N | 86.3471 | N | 3 | N | N | 1.1101 | 39.4971 | 97615.5933
[7 empty] | 10861 | 6209 | 1349848 | 2016-01-02 17:09 | 2016-01-02 19:33 | 144 | 11kV | 122935 | 1194 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 165134 3 fault operations A & B phase Overcurrent, Earth Fault Faulty UGM between Sw 58234 & ABS 41358. Excluded OMS No. 1349670 + 1349680 | January | 2016 | 2016Q3 | 2016 | 502:48004 | 502:48004 | ZN00502/048004 | MAITLAND | UG | Not Veg | 2016-01-02 | N | 102.9606 | N | 3 | N | N | 1.1101 | 39.4971 | 89837.272
[7 empty] | 12155 | 19433 | 1349675 | 2016-01-02 18:08 | 2016-01-02 22:35 | 267 | 11kV | 13988 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 165135 2 fault operations Earth Fault Excluded OMS 1349675 | January | 2016 | 2016Q3 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-01-02 | N | 259.037 | N | 3 | N | N | 1.1101 | 39.4971 | 10222.0178
[7 empty] | 11950 | 17473 | 1349701 | 2016-01-03 01:11 | 2016-01-03 04:30 | 199 | 11kV | 357598 | 2476 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10990 Arncliffe Pa2 fdr tripped, reclosed, tripped and locked out Relays: 2L Earth Fault, EFI Signals: 11kv trip, Zone Earth, Tx1 Group Earth Abnormal: AB31125 closed LB31015 open, LB30241 open Underground Feeder Fault in section of mains beyond link to pot end via S10640 The Glen Shepherd See 1350050,2,3,4,5,6 exclude 1349701,2 | January | 2016 | 2016Q3 | 2016 | ZN10990:PA2 | ZN10998:PA29 | ZN10998/000029 | BAYSIDE | UG | Not Veg | 2016-01-03 | N | 144.4257 | N | 2 | N | N | 1.1101 | 39.4971 | 261322.071
[7 empty] | 11558 | 13241 | 1349761 | 2016-01-03 15:09 | 2016-01-03 17:00 | 111 | 11kV | 62826 | 566 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn384 Camperdown Pa43 "herefod st" fdr tripped on Relays: C phase overcurrent EFI Signals: Tx1 Group Earth 5kV trip Abnormal: Please Contaqct Loads and Ratings for the full Interruption report Fronline feeder fault from Pa43 to S4538 See 1350074 exclude 1349761 | January | 2016 | 2016Q3 | 2016 | ZN384:PA43 | ZN384:PA70 | ZN00384/000070 | SYDNEY | UG | Not Veg | 2016-01-03 | N | 111 | N | 2 | N | N | 1.1101 | 39.4971 | 45911.3877
[7 empty] | 11247 | 10394 | 1349819 | 2016-01-04 00:26 | 2016-01-04 01:30 | 64 | 11kV | 71424 | 1116 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn1673 TUrramurra 11kV VCB Pa13 tripped Relays: Cphase Earth Fault, EFI EFI's: S4705 Signals: 11kv trip ABNORMAL: S4721 S/B closed, S4711 Sw/A opened Possum found at base of UGOH near PT1750. No apparent damage caused See 1350027 exclude 1349819 | January | 2016 | 2016Q3 | 2016 | ZN1673:PA13 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | OH | Not Veg | 2016-01-04 | N | 64 | N | 5 | N | N | 1.1101 | 39.4971 | 52194.5525
[7 empty] | 10947 | 7083 | 1350085 | 2016-01-04 17:33 | 2016-01-04 18:55 | 82 | 11kV | 7178 | 98 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | @ZN2196 Milperra Panel 17 'Armour Ladbroke' fdr tripped on Relays: A & C phase timed O/C and EFI Signals: Tx 2 Group earth and zone earth and 11kv trip Field EFI's: S6979, S4354, S7504, S8563, S7544, S8887, S7103, S49766, S3325 Remarks: UG fault. UG cable fault from Sub 3325 Horsley Amour to Sub 35595 Works Place No.5 | January | 2016 | 2016Q3 | 2016 | ZN2196:PA17 | ZN2196:PA17 | ZN02196/000017 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-01-04 | N | 73.2449 | N | 5 | N | N | 1.1101 | 39.4971 | 5245.4707
[7 empty] | 12184 | 19726 | 1350065 | 2016-01-04 16:23 | 2016-01-04 21:40 | 317 | 11kV | 834 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | LID 165143 A Phase tapping burnt off to Lilleys Rd sub 46360 Excluded oms 1350065. | January | 2016 | 2016Q3 | 2016 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2016-01-04 | N | 139 | N | 5 | N | N | 1.1101 | 39.4971 | 609.4626
[7 empty] | 11648 | 14194 | 1350130 | 2016-01-04 23:00 | 2016-01-05 00:32 | 92 | 11kV | 4968 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Recloser Cp3281 Bay Cooper Tripped and Locked out on Earth Fault Cause: DOp Patrolled and Cause not ascertained for outage | January | 2016 | 2016Q3 | 2016 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2016-01-04 | N | 92 | N | 5 | N | N | 1.1101 | 39.4971 | 3630.4679
[7 empty] | 11424 | 12060 | 1350131 | 2016-01-04 23:10 | 2016-01-05 01:50 | 160 | 11kV | 800 | 5 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | Section of 11 KV Mains Isolated from LB44745 to LB 44503 tee PT14319 and PT12541 Cause: vehicle Hit PT12451 Bush Ourimbah 3.0 Mains to Inspect for Damage See OMS 1350131/128 | January | 2016 | 2016Q3 | 2016 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2016-01-04 | N | 160 | N | 5 | N | N | 1.1101 | 39.4971 | 584.6164
[7 empty] | 11784 | 15738 | 1350148 | 2016-01-05 06:05 | 2016-01-05 14:15 | 490 | 11kV | 15009 | 95 | HV | Vegetation Blow/Fall In | Vegetation | Recloser / Sectionaliser | Unplanned | Rain Heavy | N | The 11kv Rec.61364 Bressies Peats 0.4 (ex S12630 Peats Ridge Panel 1 "Grants Rd") tripped and locked out on SEF and OC Remarks: Tree/branch brought down OH tree on 11kv mains in vitasalo rd (Ex. S12630 Peats Ridge Panel 1 "Grants Rd") | January | 2016 | 2016Q3 | 2016 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2016-01-05 | N | 157.9895 | N | 8 | N | N | 1.1101 | 39.4971 | 10968.1345
[7 empty] | 10794 | 5419 | 1350406 | 2016-01-05 16:12 | 2016-01-05 17:59 | 107 | 11kV | 198835 | 2284 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 165146 2 fault operations A & B phase Overcurrent No fault found Fdr returned to service. Detailed patrol required. Excluded OMS 1350406 | January | 2016 | 2016Q3 | 2016 | 240:34849 | 240:34849 | ZN00240/034849 | NEWCASTLE | OH | Veg | 2016-01-05 | N | 87.0556 | N | 8 | N | N | 1.1101 | 39.4971 | 145302.7534
[7 empty] | 11595 | 13660 | 1350464 | 2016-01-05 18:40 | 2016-01-05 19:56 | 76 | 11kV | 103431 | 2284 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 165148 1 fault operation 3 phase Earth Fault prot: 50 TN FDR LEFT REARRANGED TO LIMIT OUTAGE FOR FURTHER FAULTS. SECOND FAULT TODAY WITHOUT LOCATING PROBLEM. SEE REPORT 165146; Excluded OMS 1350464 | January | 2016 | 2016Q3 | 2016 | 240:34849 | 240:34849 | ZN00240/034849 | NEWCASTLE | OH | Veg | 2016-01-05 | N | 45.285 | N | 8 | N | N | 1.1101 | 39.4971 | 75584.3241
[7 empty] | 10657 | 3937 | 1350333 | 2016-01-05 15:25 | 2016-01-05 20:30 | 305 | 11kV | 2135 | 7 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | LID 165145 No protection operation. MVA at pole MG-20014, 11kV main off pin insulator & pole fire. Isolated 11kV mains for pole replacement. Excluded OMS 1350333 | January | 2016 | 2016Q3 | 2016 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2016-01-05 | N | 305 | N | 8 | N | N | 1.1101 | 39.4971 | 1560.195
[7 empty] | 11472 | 12513 | 1350226 | 2016-01-05 10:00 | 2016-01-05 21:40 | 700 | 11kV | 16796 | 82 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15005 Belrose Section of Panel 10 from Recloser CP24722 Tripped, Reclosed Tripped and Locked out on Overcurrent. Cause: Tree branch on OH Mains. See OMS 1351319 1351321 1350226 | January | 2016 | 2016Q3 | 2016 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Veg | 2016-01-05 | N | 204.8293 | N | 8 | N | N | 1.1101 | 39.4971 | 12274.0214
[7 empty] | 11316 | 11088 | 1350491 | 2016-01-05 22:56 | 2016-01-05 23:59 | 63 | 11kV | 13718 | 259 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | LID 165149 3 phase Overcurrent, Earth Fault prot 50TN Cable fault at ugoh pole JT-82205 Tourle St Mayfield. Section isolated for repairs ASAP. 3rd fault see reports 154146 & 165148 fdr was rearranged after previous faults so only 3 subs interrupted(10300, 44011 & 68740) Excluded oms 1350491, 1350519 | January | 2016 | 2016Q3 | 2016 | 240:34849 | 240:34849 | ZN00240/034849 | NEWCASTLE | UG | Not Veg | 2016-01-05 | N | 52.9653 | N | 8 | N | N | 1.1101 | 39.4971 | 10024.7098
[7 empty] | 10849 | 6068 | 1350499 | 2016-01-05 21:51 | 2016-01-06 00:15 | 144 | 11kV | 11088 | 77 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | 11kv LB47306 (Ex S14891 Wyong Panel 20 "Warnervale West Railway") has a burned off footpath phase bond Remarks: bond. 11kv LB 47306 (Ex S14891 Wyong Panel 20 "Warnervale West Railway") has burned off footpath phase bond) | January | 2016 | 2016Q3 | 2016 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2016-01-05 | N | 144 | N | 8 | N | N | 1.1101 | 39.4971 | 8102.7834
[7 empty] | 10695 | 4393 | 1350515 | 2016-01-05 22:55 | 2016-01-06 01:46 | 171 | 11kV | 11862 | 82 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Heavy | N | The 11kV Recloser 24722 Forest Crozier tripped reclosed tripped and locked out Cause: Recloser tripped earlier due to tree branch. Dop patrolled feeder and found no further damage. Feeder went back ok See OMS 1350652 1350656 1350515 | January | 2016 | 2016Q3 | 2016 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Veg | 2016-01-05 | N | 144.6585 | N | 8 | N | N | 1.1101 | 39.4971 | 8668.3997
[7 empty] | 11814 | 16153 | 1350619 | 2016-01-06 08:55 | 2016-01-06 09:50 | 55 | 11kV | 110 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | Rain Light | N | LID 165154 interrupt to repair LV conductor in contact with tx tank Excluded oms 1350619 | January | 2016 | 2016Q3 | 2016 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2016-01-06 | N | 55 | N | 14 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 10411 | 648 | 1350781 | 2016-01-06 08:43 | 2016-01-06 10:55 | 132 | 11kV | 19416 | 1250 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 165163 Tree on Fdr at IU-92248 Fdr opened by so section isolated for repairs Excluded 1350813 etc. | January | 2016 | 2016Q3 | 2016 | 261:81882 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | OH | Veg | 2016-01-06 | N | 15.5328 | N | 14 | N | N | 1.1101 | 39.4971 | 14188.6401
[7 empty] | 10376 | 124 | 1350563 | 2016-01-06 05:25 | 2016-01-06 12:00 | 395 | 11kV | 188325 | 686 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 165153 1 fault operation 3 phase Excluded OMS 1350563 | January | 2016 | 2016Q3 | 2016 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2016-01-06 | N | 274.5262 | N | 14 | N | N | 1.1101 | 39.4971 | 137622.3554
[7 empty] | 11660 | 14367 | 1350909 | 2016-01-06 11:45 | 2016-01-06 12:50 | 65 | 11kV | 49985 | 769 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 165177 2 fault operation | January | 2016 | 2016Q3 | 2016 | 243:80084 | 243:80084 | ZN00243/080084 | LAKE MACQUARIE | OH | Veg | 2016-01-06 | N | 65 | N | 14 | N | N | 1.1101 | 39.4971 | 36527.5637
[7 empty] | 11463 | 12388 | 1350887 | 2016-01-06 11:34 | 2016-01-06 13:15 | 101 | 11kV | 10998 | 138 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn1193 Lindfield Panel 21 Tripped on B and C Overcurrent Signals: 11kV Trip Cause: A tree branch was sitting on the 11kV OH outside 36 Strickland Ave Lindfield. DOP Driver was ub the process of isolating section of feeder when panel 21 tripped See OMS 1352415 1352416 1350881 | January | 2016 | 2016Q3 | 2016 | ZN1193:PA21 | ZN1193:PA21 | ZN01193/000021 | KU-RING-GAI | OH | Veg | 2016-01-06 | N | 79.6957 | N | 14 | N | N | 1.1101 | 39.4971 | 8037.014
[7 empty] | 10976 | 7392 | 1350643 | 2016-01-06 08:14 | 2016-01-06 14:26 | 372 | 11kV | 4464 | 12 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 165168 broken dropper lead to dolf Excluded OMS 1350643, 1350814 | January | 2016 | 2016Q3 | 2016 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2016-01-06 | N | 372 | N | 14 | N | N | 1.1101 | 39.4971 | 3262.1595
[7 empty] | 11543 | 13044 | 1351022 | 2016-01-06 14:04 | 2016-01-06 15:35 | 91 | 11kV | 62277 | 702 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | At Zn9900 Menai 11kv Pnl19 "Menai Exchange" tripped on Relays: B phase IOC with timing and lock out Signals: 11kv trip, efi, zone and Tx2 group earth Field efi's: Pnl 19 to Sub 9426 Remarks: other - details provided. Suspect UGOH or cable fault between Sub 9426 Menai Goorgool and Sub 9698 Menai Sewerage pump. | January | 2016 | 2016Q3 | 2016 | ZN9900:PA19 | ZN9900:PA19 | ZN09900/000019 | SUTHERLAND | Unknown | Unknown | 2016-01-06 | N | 88.7137 | N | 14 | N | N | 1.1101 | 39.4971 | 45510.1947
[7 empty] | 11862 | 16633 | 1350610 | 2016-01-06 07:38 | 2016-01-06 16:30 | 532 | 11kV | 173970 | 874 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 165162 3 fault operations 3 phase Overcurrent, Earth Fault Tree brought down OHM adj sub 3696 Excluded OMS 1350610, 1350985. | January | 2016 | 2016Q3 | 2016 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2016-01-06 | N | 199.0503 | N | 14 | N | N | 1.1101 | 39.4971 | 127132.1448
[7 empty] | 11042 | 7965 | 1351147 | 2016-01-06 16:39 | 2016-01-06 17:05 | 26 | 11kV | 2782 | 107 | HV | Vegetation Blow/Fall In | Vegetation | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | N | 11kv recloser 45026 Foutaindale tripped Relays: OC trip, L/O Section of 11kv Panel No.16 'S.14716 Catamara Sailcraft, etc' fdr, Zn 12690 Berkeley Vale Remarks: tree branch contact - other. Tree fell down and made contact with HV o/s 6 Berry ln | January | 2016 | 2016Q3 | 2016 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2016-01-06 | N | 26 | N | 14 | N | N | 1.1101 | 39.4971 | 2033.0035
[7 empty] | 10886 | 6452 | 1351083 | 2016-01-06 15:17 | 2016-01-06 18:10 | 173 | 11kV | 4757 | 49 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Wind Storm | N | 11kv Recloser 44603 Footest Rd tripped Relays: OC trip, EF trip, L/O Section of 11kv Panel No.1 "Dog Trap Rd" fdr, Zn 12650 W Gosford Remarks: Tree/branch brought down OH. Near PT13644 Footes Frederick 1.0, Tree brought down OH, HV into LV | January | 2016 | 2016Q3 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2016-01-06 | N | 97.0816 | N | 14 | N | N | 1.1101 | 39.4971 | 3476.2753
[7 empty] | 11653 | 14272 | 1350845 | 2016-01-06 10:48 | 2016-01-06 18:18 | 450 | 11kV | 52664 | 683 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | AtS3472 Sefton Panel 29 Joanne Court feeder tripped on: Earth fault, EFI, fault check, lockout, reclose time delay Remarks: vehicle hit pole. Car hit pole at ABS 2736 in Hector St HV & LV down | January | 2016 | 2016Q3 | 2016 | ZN3472:PA29 | ZN3472:PA29 | ZN03472/000029 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-01-06 | N | 77.1069 | N | 14 | N | N | 1.1101 | 39.4971 | 38485.2979
[7 empty] | 11690 | 14717 | 1351015 | 2016-01-06 14:01 | 2016-01-06 20:45 | 404.4833 | 11kV | 5662.7667 | 14 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Rain Wind Storm | N | @PT11481 Fern Glen 0.8, 11kv road side HDO 16k found blown Section of 11kv Panel No.1 "Dog Trap Rd" fdr, Zn 12650 W Gosford Remarks: Transformer failure, PT11481 Fern Glen 0.8 Defective. PT11481 Isolate on HV & LV. MG installed CC1: 22-"Refer to SOp" CC2: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" FRC2: 329-"High Voltage Fuse - Requires replacement" | January | 2016 | 2016Q3 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2016-01-06 | N | 404.4833 | N | 14 | N | N | 1.1101 | 39.4971 | 4138.1829
[7 empty] | 10528 | 2371 | 1351207 | 2016-01-06 18:25 | 2016-01-07 01:00 | 394.6167 | 11kV | 1973.0833 | 5 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | @PT12182 Ourimbah CK Footes 0.3 C phase 16A HDO Fuse operated Ex Panel 1 "Dog Trap Rd" frd from S12650 West Gosford Remarks: tree/branch on OH Mains. Removed by Dop | January | 2016 | 2016Q3 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2016-01-06 | N | 394.6167 | N | 14 | N | N | 1.1101 | 39.4971 | 1441.8711
[7 empty] | 10859 | 6189 | 1351007 | 2016-01-06 13:23 | 2016-01-07 03:15 | 832 | 11kV | 47424 | 57 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Heavy | N | LID 165169 1 fault operation A phase Overcurrent; Earth Fault pole OS-20180 leaning over, held up by mains Excluded OMS 1350952, 1350981 | January | 2016 | 2016Q3 | 2016 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2016-01-06 | N | 832 | N | 14 | N | N | 1.1101 | 39.4971 | 34656.0604
[7 empty] | 11972 | 17693 | 1351279 | 2016-01-07 01:10 | 2016-01-07 07:10 | 360 | 11kV | 46080 | 128 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165172 A Phase DOLF : 40 Amp Excluded OMS 1351279 | January | 2016 | 2016Q3 | 2016 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Veg | 2016-01-07 | N | 360 | N | 5 | N | N | 1.1101 | 39.4971 | 33673.9049
[7 empty] | 12038 | 18406 | 1351407 | 2016-01-07 09:49 | 2016-01-07 10:39 | 50 | 11kV | 6500 | 130 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Rain Heavy | N | At Zn675/ Castle Cove Panel 19 Tripped on Signals 11kV Trip, Tx4 Eartth Fault The 11kV RMI No1 Endbox at S6602 Railway Help No 2 Explosed | January | 2016 | 2016Q3 | 2016 | ZN3425:PA19 | ZN3425:PA19 | ZN03425/000019 | WILLOUGHBY | UG | Not Veg | 2016-01-07 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 4750.0083
[7 empty] | 11005 | 7633 | 1351385 | 2016-01-07 09:14 | 2016-01-07 11:00 | 106 | 11kV | 1696 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 165176 C phase DOLF : 20 Amp Excluded OMS 1351385 | January | 2016 | 2016Q3 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2016-01-07 | N | 106 | N | 5 | N | N | 1.1101 | 39.4971 | 1239.3868
[7 empty] | 10595 | 3180 | 1351691 | 2016-01-07 17:04 | 2016-01-07 17:45 | 40.7333 | 11kV | 1792.2667 | 44 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 165181 lead off at dolf repairs complete no protection operation Excluded oms 1351698 | January | 2016 | 2016Q3 | 2016 | 258:80775 | 258:80775 | ZN00258/080775 | NEWCASTLE | OH | Not Veg | 2016-01-07 | N | 40.7333 | N | 5 | N | N | 1.1101 | 39.4971 | 1309.7356
[7 empty] | 11246 | 10379 | 1351885 | 2016-01-07 18:57 | 2016-01-07 20:00 | 63 | 11kV | 3390 | 54 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S1610 Homebush Bay Panel 26 "Fariola Wetherill" fdr trippd Relays: Earth fault, EFI Signals: Tx2 Group Earth, 11kv trip EFI's: S63496 Remarks: UG fault. Underground feeder fault from S63496 Farila Wetherill Sw/B to S8931 Wetheril Fairola No.3 Sw/A | January | 2016 | 2016Q3 | 2016 | ZN1610:PA26 | ZN1610:PA26 | ZN01610/000026 | PARRAMATTA | UG | Not Veg | 2016-01-07 | N | 62.7778 | N | 5 | N | N | 1.1101 | 39.4971 | 2477.312
[7 empty] | 11686 | 14623 | 1351762 | 2016-01-08 08:05 | 2016-01-08 09:00 | 55 | 11kV | 110 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165183 C phase DOLF : 16 Amp Excluded OMS 1351762 | January | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-01-08 | N | 55 | N | 5 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 11474 | 12561 | 1351858 | 2016-01-08 11:25 | 2016-01-08 13:20 | 115 | 11kV | 74695 | 1051 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S12570 Avoca Panel 35 Kincumber feeder opened on Overcurrent and Earth Fault relays - With EFI and auto closing lockoutr Signals: 11kV Trip, Zone Earth and TX12 Group Earth Relays: C phase Overcurrent, Earth Fault, EFI, Timing and Lockout Cause: NBN contractor hit cable outside 1 Julian St Avoca See OMS 1353236 1353237 1353239 1353240 1351858 1351860 | January | 2016 | 2016Q3 | 2016 | ZN12570:PA35 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | UG | Not Veg | 2016-01-08 | N | 71.0704 | N | 5 | N | N | 1.1101 | 39.4971 | 54584.9029
[7 empty] | 10917 | 6815 | 1351918 | 2016-01-08 13:41 | 2016-01-08 15:52 | 131 | 11kV | 20960 | 160 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S5289 Schwebel illawarra appears to have an internal HR developing on B phase ex Panel 42 Schwebel st fdr Remarks: transformer failure. Volts at Tx links (as close to the Tx as the Dop can check) measured 245, 190, 245. Dop placed 2 LV//'s 13404 and 22286 to boost volts to 230 on B phase. tx left in service as MDI was K240 1.7 | January | 2016 | 2016Q3 | 2016 | ZN262:PA42 | ZN262:PA42 | ZN00262/000042 | INNER WEST | UG | Not Veg | 2016-01-08 | N | 131 | N | 5 | N | N | 1.1101 | 39.4971 | 15316.9498
[7 empty] | 11034 | 7894 | 1351890 | 2016-01-08 12:42 | 2016-01-08 17:00 | 258 | 11kV | 2322 | 9 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT14540 Buangi Hills Mand 0.1 the roadside HDO was found blown Cause: Fuse fatigue See OMS 1353253 1351890 | January | 2016 | 2016Q3 | 2016 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2016-01-08 | N | 258 | N | 5 | N | N | 1.1101 | 39.4971 | 1696.8491
[7 empty] | 11335 | 11353 | 1352010 | 2016-01-08 21:27 | 2016-01-08 22:25 | 57.8833 | 11kV | 3241.4667 | 56 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165197 A Phase DOLF : 31 Amp Possum | January | 2016 | 2016Q3 | 2016 | 225:33679 | 270:83586 | ZN00270/083586 | LAKE MACQUARIE | OH | Not Veg | 2016-01-08 | N | 57.8833 | N | 5 | N | N | 1.1101 | 39.4971 | 2368.7682
[7 empty] | 11205 | 9956 | 1353259 | 2016-01-09 05:04 | 2016-01-09 06:29 | 85 | 11kV | 58690 | 705 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 21 tripped on Relays: Earth Fault and EFI Signals - 11kV Trip, TX2 Group Earth and Zone Earth Cause: 11kV UG feeder fault from S4677 to S5233 to S8291 See OMS 1353259 1353261 1352025 | January | 2016 | 2016Q3 | 2016 | ZN129:PA21 | ZN129:PA63 | ZN00129/000063 | LANE COVE | UG | Not Veg | 2016-01-09 | N | 83.2482 | N | 5 | N | N | 1.1101 | 39.4971 | 42888.9209
[7 empty] | 11026 | 7805 | 1352026 | 2016-01-09 05:36 | 2016-01-09 07:39 | 123 | 11kV | 55787 | 456 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 165200 2 fault operations B & C phase Overcurrent Excluded OMS 1352026 | January | 2016 | 2016Q3 | 2016 | 238:34148 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2016-01-09 | N | 122.3399 | N | 5 | N | N | 1.1101 | 39.4971 | 40767.4942
[7 empty] | 12221 | 20100 | 1352075 | 2016-01-09 12:06 | 2016-01-09 13:30 | 84 | 11kV | 7224 | 86 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At S3093 Smith Rhodes 11kv HV fuse operated A and B phase Type: SRLDO 63 amp Section of 11kv Panel No.35 'S2662 Holden Taylor' fdr, Zn 3672 Maroubra Relays: EFi, fault check Field EFI's: S2652, S1802, S62943, S833 Remarks: transfomer failure. Suspected defective transformer 11kv/415v @ S3093 Smith Rhodges usl's 1180, 1178, supply restored via LV//s | January | 2016 | 2016Q3 | 2016 | ZN3672:PA35 | ZN3672:PA35 | ZN03672/000035 | BAYSIDE | UG | Not Veg | 2016-01-09 | N | 84 | N | 5 | N | N | 1.1101 | 39.4971 | 5279.0861
[7 empty] | 10977 | 7406 | 1352082 | 2016-01-09 12:30 | 2016-01-09 15:30 | 180 | 11kV | 130157 | 942 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At ZN965 Pennant Hills Panel 35 Tripped on Relays: Earth and EFI Signals: 11kV Trip, Group Earth and Zone Earth Cause: UGOH Fault short circuit @ PT612 See OMS 1353269 1353271 1353272 1352082 | January | 2016 | 2016Q3 | 2016 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | HORNSBY | Unknown | Unknown | 2016-01-09 | N | 138.1709 | N | 5 | N | N | 1.1101 | 39.4971 | 95114.8966
[7 empty] | 12214 | 20051 | 1360599 | 2016-01-09 18:11 | 2016-01-09 20:10 | 119 | 11kV | 42223 | 387 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Lightning | N | Zn167 Auburn 11kv Pa20L fdr tripped Relays: Earth Fault, Overcurrent, Earth Fault, EFI Signals: 11kv trip EFI's: S2951 Cause: UG Fault | January | 2016 | 2016Q3 | 2016 | ZN167:PA20 | ZN167:PA20 | ZN00167/000020 | PARRAMATTA | UG | Not Veg | 2016-01-09 | N | 109.1034 | N | 5 | N | N | 1.1101 | 39.4971 | 30855.323
[7 empty] | 10912 | 6779 | 1352138 | 2016-01-10 08:15 | 2016-01-10 08:19 | 4 | 11kV | 812 | 203 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kV feeder Pa27 Lindfield From AB457 to S48976 to AB1584 to S6186 Interrupted to remove tree branch from OH Cause: Tree branch on 11kV Mains vicinity S6186 and LV parallel not suitable for load. | January | 2016 | 2016Q3 | 2016 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Veg | 2016-01-10 | N | 4 | N | 3 | N | N | 1.1101 | 39.4971 | 593.3857
[7 empty] | 10840 | 5945 | 1352218 | 2016-01-10 13:20 | 2016-01-10 19:30 | 370 | 11kV | 55711 | 321 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 165210 3 fault operations Earth Fault Tree down OHM down near sub 8398 DOp reported tree trimming required on this Fdr Excluded OMS 1352218 | January | 2016 | 2016Q3 | 2016 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2016-01-10 | N | 173.5545 | N | 3 | N | N | 1.1101 | 39.4971 | 40711.9556
[7 empty] | 11220 | 10066 | 1352284 | 2016-01-10 20:12 | 2016-01-10 21:37 | 85 | 11kV | 64695 | 813 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2466 Flemington - 11kv Panel No.40 :Telopea Courallie" tripped on: Relays: B phase instant, EFI, Fault Check Signals: 11kv trip, Zone Earth, Group Earth EFI's: S4133, S8029, CP48, S3137, S6687, S6981 Remarks: 11kv UG fault between S6981 Arthur Richmond No.2 and S8260 Arthur Richmond No.6 | January | 2016 | 2016Q3 | 2016 | ZN2466:PA40 | ZN36000:PA4 | ZN36000/000004 | STRATHFIELD | UG | Not Veg | 2016-01-10 | N | 79.5756 | N | 3 | N | N | 1.1101 | 39.4971 | 47277.1978
[7 empty] | 10782 | 5303 | 1352324 | 2016-01-11 09:10 | 2016-01-11 10:25 | 75 | 11kV | 75 | 1 | HV | Animal Bird | Animal | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | LID 165217 C Phase Sectionaliser Bird on UGOH Excluded OMS 1352324 | January | 2016 | 2016Q3 | 2016 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2016-01-11 | N | 75 | N | 20 | Y | Y | 1.1101 | 39.4971 | 54.8078
[7 empty] | 11408 | 11912 | 1352574 | 2016-01-11 15:04 | 2016-01-11 15:41 | 37 | 11kV | 22948 | 664 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 165228 Pothead blown up in substation Fdr 33679. Cable box blown up in sub pole HV-60031 Flags required. excluded OMS 1352574 | January | 2016 | 2016Q3 | 2016 | 225:33679 | 270:83594 | ZN00270/083594 | LAKE MACQUARIE | UG | Not Veg | 2016-01-11 | N | 34.5602 | N | 20 | Y | Y | 1.1101 | 39.4971 | 16769.7215
[7 empty] | 11003 | 7628 | 1352561 | 2016-01-11 14:43 | 2016-01-11 16:00 | 77 | 11kV | 77 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID165230 B Phase DOLF : 10 Amp Excluded OMS 1352561 | January | 2016 | 2016Q3 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2016-01-11 | N | 77 | N | 20 | Y | Y | 1.1101 | 39.4971 | 56.2693
[7 empty] | 11002 | 7624 | 1352604 | 2016-01-11 16:29 | 2016-01-11 20:07 | 218 | 11kV | 436 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | At PT12420 Kidman Yarra North 0.7 lost supply Cause: Ligntning | January | 2016 | 2016Q3 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2016-01-11 | N | 218 | N | 20 | Y | Y | 1.1101 | 39.4971 | 318.6159
[7 empty] | 10479 | 1727 | 1352644 | 2016-01-11 18:10 | 2016-01-11 20:30 | 139.8167 | 11kV | 4334.3167 | 31 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 165241 A phase DOLF LV L/A Blown. Excluded OMS 1352657. | January | 2016 | 2016Q3 | 2016 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Not Veg | 2016-01-11 | N | 139.8167 | N | 20 | Y | Y | 1.1101 | 39.4971 | 3167.3908
[7 empty] | 11296 | 10909 | 1352639 | 2016-01-11 20:35 | 2016-01-11 21:00 | 24.7 | 11kV | 395.2 | 16 | HV | Vegetation Blow/Fall In | Vegetation | Air Break Switch | Unplanned | Lightning | N | Section of Panel 1 Umina - LB41494 - Supply Manually Interrupted Cause: Supply interrupted to allow removal of Large Tree off AB45136 See OMS 1352692 1352639 | January | 2016 | 2016Q3 | 2016 | ZN12640:PA1 | ZN12640:PA1 | ZN12640/000001 | CENTRAL COAST | OH | Veg | 2016-01-11 | N | 24.7 | N | 20 | Y | Y | 1.1101 | 39.4971 | 288.8005
[7 empty] | 10639 | 3764 | 1352708 | 2016-01-11 21:05 | 2016-01-11 21:14 | 9 | 11kV | 2007 | 223 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165244 1 fault operation Overcurrent | January | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-01-11 | N | 9 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1466.6564
[7 empty] | 10539 | 2462 | 1352688 | 2016-01-11 20:33 | 2016-01-11 21:40 | 66.6 | 11kV | 1398.6 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165256 A phase DOLF : 16 Amp | January | 2016 | 2016Q3 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-01-11 | N | 66.6 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1022.0556
[7 empty] | 11988 | 17949 | 1352691 | 2016-01-11 20:31 | 2016-01-11 22:09 | 98 | 11kV | 31458 | 321 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165252 2 fault operations Single phase | January | 2016 | 2016Q3 | 2016 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2016-01-11 | N | 98 | N | 20 | Y | Y | 1.1101 | 39.4971 | 22988.5785
[7 empty] | 11527 | 12913 | 1352679 | 2016-01-11 20:35 | 2016-01-11 22:20 | 105 | 11kV | 105 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 165250 Blown Lightning Arrestor Excluded 1352690 & 1352679 | January | 2016 | 2016Q3 | 2016 | 512:48049 | 264:81231 | ZN00264/081231 | SINGLETON | OH | Not Veg | 2016-01-11 | N | 105 | N | 20 | Y | Y | 1.1101 | 39.4971 | 76.7309
[7 empty] | 11435 | 12153 | 1352707 | 2016-01-11 21:47 | 2016-01-12 00:40 | 173 | 11kV | 1038 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165261 3 phase DOLF : 10 Amp Excluded OMS 1352707 | January | 2016 | 2016Q3 | 2016 | 528:83014 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Veg | 2016-01-11 | N | 173 | N | 20 | Y | Y | 1.1101 | 39.4971 | 758.5398
[7 empty] | 11932 | 17232 | 1352972 | 2016-01-11 21:07 | 2016-01-12 01:30 | 263 | 11kV | 8422 | 64 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165245 1 fault operation 3 phase DOLF : 10 Amp Sectionaliser Replaced 1 x 10 Amp DOLF at sub 51650 | January | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-01-11 | N | 131.5938 | N | 20 | Y | Y | 1.1101 | 39.4971 | 6154.5492
[7 empty] | 11056 | 8093 | 1352713 | 2016-01-11 22:56 | 2016-01-12 02:35 | 219 | 11kV | 10074 | 46 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165263 A & C phase DOLF : 40 Amp also related see 1352860 | January | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-01-11 | N | 219 | N | 20 | Y | Y | 1.1101 | 39.4971 | 7361.7821
[7 empty] | 10382 | 212 | 1352686 | 2016-01-11 20:26 | 2016-01-12 02:42 | 376 | 11kV | 1880 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 165265 B & C Phase DOLF : 10 Amp Excluded OMS 1352694 & 1352686 | January | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-01-11 | N | 376 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1373.8485
[7 empty] | 11341 | 11430 | 1352710 | 2016-01-11 22:19 | 2016-01-12 04:43 | 384 | 11kV | 384 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 165267 LLC burnt off top of DOLF Excluded OMS 1352710 | January | 2016 | 2016Q3 | 2016 | 532:83307 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Not Veg | 2016-01-11 | N | 384 | N | 20 | Y | Y | 1.1101 | 39.4971 | 280.6159
[7 empty] | 11144 | 9350 | 1352611 | 2016-01-11 16:22 | 2016-01-12 04:45 | 743 | 11kV | 37303 | 77 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 165262 2 fault operations 2 span down between subs 17135, 54031 & 25823 Excluded OMS 1352611, 1352667, 1352670 | January | 2016 | 2016Q3 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2016-01-11 | N | 484.4545 | N | 20 | Y | Y | 1.1101 | 39.4971 | 27259.9321
[7 empty] | 10903 | 6706 | 1352733 | 2016-01-12 04:02 | 2016-01-12 04:55 | 53 | 11kV | 23638 | 446 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN3155 Double Bay 11kv OCB panel 18 "S35856" feeder tripped on: Relays: Earth fault, EFI, fault check Field EFI's: nil Signals: 11kv trip Remarks: UG fault. 11kv U/G fault from Zn 3155 Double Bay (Panel 18) to S35856 Manning Pine Sw/A to S36083 Wallaroy Rd Sw/B | January | 2016 | 2016Q3 | 2016 | ZN3155:PA18 | ZN3155:PA18 | ZN03155/000018 | WOOLLAHRA | UG | Not Veg | 2016-01-12 | N | 53 | N | 8 | N | N | 1.1101 | 39.4971 | 17273.9532
[7 empty] | 11421 | 12027 | 1352703 | 2016-01-11 21:18 | 2016-01-12 11:55 | 877 | 11kV | 1754 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165279 Single Phase DOLF : 10 Amp Tx volts: 243V Excluded OMS No. 1352703 | January | 2016 | 2016Q3 | 2016 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2016-01-11 | N | 877 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1281.7715
[7 empty] | 12149 | 19360 | 1352760 | 2016-01-12 07:23 | 2016-01-12 12:20 | 297 | 11kV | 891 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165280 A Phase DOLF : 10 Amp Excluded OMS 1352760 | January | 2016 | 2016Q3 | 2016 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2016-01-12 | N | 297 | N | 8 | N | N | 1.1101 | 39.4971 | 651.1165
[7 empty] | 12244 | 20356 | 1352681 | 2016-01-11 19:58 | 2016-01-12 13:29 | 1051 | 11kV | 46321 | 91 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Lightning | N | Recloser CP45016 Dickson Tripped on Overcurrent and IOC Trip UG/OH Fault adjacent to LB42008 Abnormal Switching: USL41028 Open and Defective LB44532 Closed See OMS 1353405 1353407 1352867 1352740 1352682 1352681 | January | 2016 | 2016Q3 | 2016 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | Unknown | Unknown | 2016-01-11 | N | 509.022 | N | 20 | Y | Y | 1.1101 | 39.4971 | 33850.0206
[7 empty] | 12210 | 19991 | 1352958 | 2016-01-12 11:54 | 2016-01-12 13:40 | 106 | 11kV | 530 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165300 substation DOLF Excluded OMS 1352958 | January | 2016 | 2016Q3 | 2016 | 239:82131 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Veg | 2016-01-12 | N | 106 | N | 8 | N | N | 1.1101 | 39.4971 | 387.3084
[7 empty] | 11891 | 16888 | 1353413 | 2016-01-11 19:38 | 2016-01-12 14:55 | 1157 | 11kV | 11404 | 69 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Lightning | N | Recloser 44994 Mangrove Creek Trippen and Locked out on O/C and IOC Cause: 11kV Dcown between LB44211 to PT14121 See OMS 1353413 1353414 1353415 1353416 1352724 1352719 1352677 | January | 2016 | 2016Q3 | 2016 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2016-01-11 | N | 165.2754 | N | 20 | Y | Y | 1.1101 | 39.4971 | 8333.7068
[7 empty] | 11581 | 13495 | 1352742 | 2016-01-12 07:04 | 2016-01-12 15:00 | 476 | 11kV | 1428 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 165289 Single phase DOLF : 10 Amp isolated sub to replace 2 x la's Excluded OMS No. 1352754 | January | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-01-12 | N | 476 | N | 8 | N | N | 1.1101 | 39.4971 | 1043.5403
[7 empty] | 10476 | 1689 | 1352939 | 2016-01-12 11:24 | 2016-01-12 15:35 | 250.6 | 11kV | 31558.8 | 223 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 165813 A & C phase Overcurrent; Earth fault | January | 2016 | 2016Q3 | 2016 | 232:11460 | 232:11460 | ZN00232/011460 | PORT STEPHENS | OH | Not Veg | 2016-01-12 | N | 141.5193 | N | 8 | N | N | 1.1101 | 39.4971 | 23062.2402
[7 empty] | 12116 | 19063 | 1353080 | 2016-01-12 15:39 | 2016-01-12 17:01 | 82 | 11kV | 167608 | 2044 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn9035 Caringbah - 11kv Panel No.11 "Sub 9791, Sub 9420" feeder tripped Relays: Earth fault, EFI Signals: 11kv trip, No.2 Group earth, Zone earth Field EFi's: S9420, S9836, S9357, S9532 Remarks: 11kv UG fault from S9532 Taren Binalong to Sub 9314 Caringbah Taren Note: S9017 Karimbla Kareema was isolated in LV// from Panel No.11 at time of interruption | January | 2016 | 2016Q3 | 2016 | ZN9035:PA11 | ZN9035:PA11 | ZN09035/000011 | SUTHERLAND | UG | Not Veg | 2016-01-12 | N | 82 | N | 8 | N | N | 1.1101 | 39.4971 | 122482.9828
[7 empty] | 11592 | 13637 | 1353010 | 2016-01-12 13:44 | 2016-01-12 17:35 | 231 | 11kV | 1155 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 165294 Single phase DOLF : 10 Amp sub isolated to replace arrestor Excluded OMS 1353010 | January | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2016-01-12 | N | 231 | N | 8 | N | N | 1.1101 | 39.4971 | 844.0399
[7 empty] | 11027 | 7811 | 1353132 | 2016-01-12 16:58 | 2016-01-12 19:00 | 122 | 11kV | 366 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165299 A phase DOLF : 10 Amp load 22, 10, 17amps 244 volts Excluded OMS 1353132 | January | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-01-12 | N | 122 | N | 8 | N | N | 1.1101 | 39.4971 | 267.462
[7 empty] | 11537 | 12988 | 1353333 | 2016-01-13 10:44 | 2016-01-13 12:15 | 91 | 11kV | 1001 | 11 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 165310 C Phase DOLF : 40 Amp Dolf carrier caught fire. Excluded OMS 1353333, 1353335, 1353337 & 1353344 | January | 2016 | 2016Q3 | 2016 | 511:29874 | 511:29874 | ZN00511/029874 | MAITLAND | OH | Not Veg | 2016-01-13 | N | 91 | N | 6 | N | N | 1.1101 | 39.4971 | 731.5013
[7 empty] | 11575 | 13419 | 1353435 | 2016-01-13 14:52 | 2016-01-13 16:00 | 68 | 11kV | 136 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165318 Single Phase DOLF : 10 Amp Excluded OMS 1353435 | January | 2016 | 2016Q3 | 2016 | 526:34635 | 526:34635 | ZN00526/034635 | CESSNOCK | OH | Veg | 2016-01-13 | N | 68 | N | 6 | N | N | 1.1101 | 39.4971 | 99.3848
[7 empty] | 10437 | 1094 | 1353490 | 2016-01-13 16:50 | 2016-01-13 18:30 | 100 | 11kV | 3000 | 30 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 165321 Isolated to repair unravelling main near sub 10856 | January | 2016 | 2016Q3 | 2016 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2016-01-13 | N | 100 | N | 6 | N | N | 1.1101 | 39.4971 | 2192.3115
[7 empty] | 10989 | 7498 | 1353496 | 2016-01-13 16:58 | 2016-01-13 19:25 | 147 | 11kV | 294 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165320 A & B phase DOLF : 10 Amp Excluded OMS 1353496 | January | 2016 | 2016Q3 | 2016 | 526:34635 | 526:34635 | ZN00526/034635 | CESSNOCK | OH | Veg | 2016-01-13 | N | 147 | N | 6 | N | N | 1.1101 | 39.4971 | 214.8465
[7 empty] | 10700 | 4431 | 1353440 | 2016-01-13 15:00 | 2016-01-13 23:10 | 490 | 11kV | 1470 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 165322 Single phase DOLF : 10 Amp Replaced faulty transformer Excluded OMS 1353440 | January | 2016 | 2016Q3 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2016-01-13 | N | 490 | N | 6 | N | N | 1.1101 | 39.4971 | 1074.2326
[7 empty] | 10850 | 6084 | 1353549 | 2016-01-13 23:14 | 2016-01-14 00:39 | 85 | 11kV | 255 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 165323 Replaced DOLF & Carrier Excluded OMS 1353549 | January | 2016 | 2016Q3 | 2016 | 532:83309 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2016-01-13 | N | 85 | N | 6 | N | N | 1.1101 | 39.4971 | 186.3465
[7 empty] | 12062 | 18596 | 1353628 | 2016-01-14 02:31 | 2016-01-14 02:39 | 8 | 11kV | 1648 | 206 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | LID 165324 Staff opened 11kV links 3992 at Leconfield RAGCB by mistake. Should have opened links 42741 at Dalwood Rd RAGCB See report 165325/ OMS1353627 | January | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2016-01-14 | N | 8 | N | 4 | N | N | 1.1101 | 39.4971 | 1204.3098
[7 empty] | 11591 | 13622 | 1353523 | 2016-01-13 18:46 | 2016-01-14 05:40 | 654 | 11kV | 10464 | 16 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 165325 OHM down from Links 41609, section isolated to repair see emerg SI Q0006 Excluded OMS 1353523, | January | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2016-01-13 | N | 654 | Y | 6 | N | Y | 1.1101 | 39.4971 | 7646.7826
[7 empty] | 11404 | 11875 | 1353571 | 2016-01-14 07:16 | 2016-01-14 11:35 | 259 | 11kV | 777 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | Y | LID 165335 B Phase DOLF : 10Amp Excluded OMS 1353571 | January | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-01-14 | Y | 259 | N | 4 | N | Y | 1.1101 | 39.4971 | 567.8087
[7 empty] | 10887 | 6454 | 1353806 | 2016-01-14 15:04 | 2016-01-14 16:23 | 79 | 11kV | 99856 | 1264 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor ABC | Unplanned | Lightning | Y | @Zn35800 Bankstown 11kv Pnl 1 "S35208" feeder tripped on: Relays - Bassler 50TBC, EFI Field EFi's - Nil Signals - 11kv trip Remarks: lightning. DEOP patrolled nothing found | January | 2016 | 2016Q3 | 2016 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-01-14 | Y | 79 | N | 4 | N | Y | 1.1101 | 39.4971 | 72971.8195
[7 empty] | 11322 | 11150 | 1353847 | 2016-01-14 15:18 | 2016-01-14 16:57 | 98.5333 | 11kV | 146814.6667 | 1490 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | Y | Ex Zn1850 Bass Hill 11kv Panel 12 S-4344 feeder REC50006 marion Wilkons tripped and reclosed tripped and locked out on O/C Remarks: lightning. Dop patrolled nothing found | January | 2016 | 2016Q3 | 2016 | ZN1850:PA12 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-01-14 | Y | 98.5333 | N | 4 | N | Y | 1.1101 | 39.4971 | 107287.8281
[7 empty] | 10421 | 804 | 1353828 | 2016-01-14 15:12 | 2016-01-14 16:59 | 107 | 11kV | 102827 | 961 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | Y | Ex Zn3472 Seftib 11kv Panel 28 "S35463" feeder tripped re closed tripped and locked out on Relays: B and C phase IOC, reclose, lockout, Field EFI's: nil Signals: 11kv trip Remarks: tree/branch on OH mains. Tree branch removed by Dop ADJ to LB2714 | January | 2016 | 2016Q3 | 2016 | ZN3472:PA28 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-01-14 | Y | 107 | N | 4 | N | Y | 1.1101 | 39.4971 | 75142.9387
[7 empty] | 11765 | 15528 | 1353821 | 2016-01-14 15:09 | 2016-01-14 17:02 | 113 | 11kV | 144979 | 1283 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZN10095 Riverwood Panel 12 Tripped and reclosed tripped and locked out on Relays: A phase IOC and Timed O/C Cause: Tree branch on 11kV mains on cnr of Belmore and Henry Lawson Dr | January | 2016 | 2016Q3 | 2016 | ZN10995:PA12 | ZN10995:PA12 | ZN10995/000012 | GEORGES RIVER | OH | Veg | 2016-01-14 | Y | 113 | N | 4 | N | Y | 1.1101 | 39.4971 | 105946.377
[7 empty] | 12218 | 20094 | 1352697 | 2016-01-11 20:47 | 2016-01-14 17:15 | 4108 | 11kV | 69661 | 316 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 165254 2 fault operations A phase Earth fault UGOH HV-20210 to sub 1356 faulty Excluded oms 1352697 | January | 2016 | 2016Q3 | 2016 | 239:82131 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | Unknown | Unknown | 2016-01-11 | N | 220.4462 | N | 20 | Y | Y | 1.1101 | 39.4971 | 50906.2041
[7 empty] | 11744 | 15325 | 1354368 | 2016-01-14 16:42 | 2016-01-14 17:30 | 48 | 11kV | 46628 | 1014 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | ZN15014 Mona Vale Ex Panel 11L "S16231, S16490" - Rec 20397 has Tripped/ Reclosed/Tripped & Lock Out Relays: IOC Trip, OC Trip Tree/ Branch on HV Feeder o/s #38 Rednal St, Mona Vale. This is on the 11kV tee to PT15500 Rednal St Me:1358861, 1358866 Withdrawn:1354368 | January | 2016 | 2016Q3 | 2016 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2016-01-14 | N | 45.9842 | N | 4 | N | N | 1.1101 | 39.4971 | 34074.3671
[7 empty] | 11020 | 7746 | 1354076 | 2016-01-14 15:39 | 2016-01-14 17:43 | 124 | 11kV | 59148 | 477 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | Y | Zn12630 Peats Ridge Pa4 "Kulnura" fdr tripped and reclosed and locked out Abnormal: LB62765 closed with HV link 41886 open and defective Weather related See 1357048 exclude 1354049,6119 | January | 2016 | 2016Q3 | 2016 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2016-01-14 | Y | 124 | N | 4 | N | Y | 1.1101 | 39.4971 | 43223.6138
[7 empty] | 11197 | 9904 | 1353792 | 2016-01-14 14:52 | 2016-01-14 17:46 | 174 | 11kV | 205842 | 1183 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZN9245 Engadine Panel 38 tripped on A phase Timed Overcurrent, Timing and lockout relays Tree on OH mains adjacent to AB35462. | January | 2016 | 2016Q3 | 2016 | ZN9245:PA38 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | OH | Veg | 2016-01-14 | Y | 174 | N | 4 | N | Y | 1.1101 | 39.4971 | 150423.2623
[7 empty] | 12152 | 19414 | 1353820 | 2016-01-14 15:11 | 2016-01-14 17:56 | 165 | 11kV | 207570 | 1258 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Wind Storm | Y | @Zn10995 Riverwood - 11kv Panel No.6 "Pearce Ave" feeder tripped, reclosed and locked out Relays: A phase IOC & timed O/C, timing/lockout relay Signals: 11kv trip Field EFI's: Nil Remarks: tree/branch on OH mains. Tree on 11kv mains adjacent LB 46333 | January | 2016 | 2016Q3 | 2016 | ZN10995:PA6 | ZN10995:PA6 | ZN10995/000006 | GEORGES RIVER | OH | Veg | 2016-01-14 | Y | 165 | N | 4 | N | Y | 1.1101 | 39.4971 | 151686.0337
[7 empty] | 10836 | 5883 | 1353912 | 2016-01-14 15:26 | 2016-01-14 18:05 | 159 | 11kV | 379610 | 2410 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | Y | @ZN 3472 Sefton 11kv OCB panel 30 "S4411" feeder tripped reclosed tripped and locked out on Relays: O/C B & C phase EFI reclose, lockout, fault check Field EFI's: nil Signals: 11kv trip Remarks: lightning damaged 11kv feeder @ IS2360 also 11kv come away from insulator on the cnr of Marion and Dutton STS. 11kv feeder isolated between IS2360 to LB2984 to S36196 Highland Marion Sw/B | January | 2016 | 2016Q3 | 2016 | ZN3472:PA30 | ZN3472:PA30 | ZN03472/000030 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-01-14 | Y | 157.5145 | N | 4 | N | Y | 1.1101 | 39.4971 | 277407.7914
[7 empty] | 12229 | 20236 | 1353829 | 2016-01-14 15:12 | 2016-01-14 18:18 | 186 | 11kV | 221898 | 1193 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn10994 Mortdale Panel 9 Tripped reclosed tripped and locked out on Relays: A and B phase IOC, E/F, EFI, Reclose/Lockout Cause: Rain wind storm | January | 2016 | 2016Q3 | 2016 | ZN10994:PA9 | ZN10994:PA9 | ZN10994/000009 | GEORGES RIVER | OH | Not Veg | 2016-01-14 | Y | 186 | N | 4 | N | Y | 1.1101 | 39.4971 | 162156.5135
[7 empty] | 11760 | 15471 | 1353888 | 2016-01-14 15:16 | 2016-01-14 19:04 | 228 | 11kV | 238260 | 1045 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S9037 Miranda panel 2 tripped, reclosed tripped and locked out on Relays: C phase Timed Overcurrenrt, Earthfault and EFI Cause: Tree on OHG mains O/S 98 Holt Rd | January | 2016 | 2016Q3 | 2016 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Veg | 2016-01-14 | Y | 228 | N | 4 | N | Y | 1.1101 | 39.4971 | 174113.3805
[7 empty] | 11117 | 8882 | 1353848 | 2016-01-14 15:15 | 2016-01-14 19:37 | 262 | 11kV | 75983 | 726 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | Y | Ex Zn1788 Matraville section of Panel 36 11kV Fdr Fault from S35216:S to S8906:B LV Pilot fault from S929:B to S3519: "Tx1 fdr" See 1360972,4,5,6,9,83,5,6 Exclude 1353848 | January | 2016 | 2016Q3 | 2016 | ZN1788:PA36 | ZN1788:PA69 | ZN01788/000069 | RANDWICK | UG | Not Veg | 2016-01-14 | Y | 104.6598 | N | 4 | N | Y | 1.1101 | 39.4971 | 55526.1353
[7 empty] | 11039 | 7942 | 1360983 | 2016-01-14 17:30 | 2016-01-14 19:38 | 128 | 11kV | 5738 | 188 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | Y | Ex Zn1788 Matraville section of Panel 36 11kV Fdr Fault from S35216:S to S8906:B LV Pilot fault from S929:B to S3519: "Tx1 fdr" See 1360972,4,5,6,9,83,5,6 Exclude 1353848 | January | 2016 | 2016Q3 | 2016 | ZN1788:PA36 | ZN1788:PA69 | ZN01788/000069 | RANDWICK | UG | Not Veg | 2016-01-14 | Y | 30.5213 | N | 4 | N | Y | 1.1101 | 39.4971 | 4193.1612
[7 empty] | 12104 | 18956 | 1353823 | 2016-01-14 15:12 | 2016-01-14 19:40 | 268 | 11kV | 1023406 | 4177 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S10994 Mortdale Panel 4 Broughton St tripped, reclosed, tripped and locked out on Relays: C phase IOC , E/F efi, reclose/timing relay Cause not ascertained for outage feeder patrolled by DOp See OMS 1357039 1357042 1353823 | January | 2016 | 2016Q3 | 2016 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | OH | Not Veg | 2016-01-14 | Y | 245.0098 | N | 4 | N | Y | 1.1101 | 39.4971 | 747874.9194
[7 empty] | 11243 | 10278 | 1353818 | 2016-01-14 15:06 | 2016-01-14 19:55 | 289 | 11kV | 596207 | 2063 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn10995 Riverwood Panel 1 tripped RelaysL C phase IOC and Timed OC with EFI Cause: Rain wind storm | January | 2016 | 2016Q3 | 2016 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | OH | Not Veg | 2016-01-14 | Y | 289 | N | 4 | N | Y | 1.1101 | 39.4971 | 435690.4905
[7 empty] | 11868 | 16678 | 1353997 | 2016-01-14 15:44 | 2016-01-14 20:09 | 265 | 11kV | 461100 | 1740 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | Y | @Zn2196 Milperra 11kv VCB panel 25 "S4684" feeder tripped on Relays: OC trip Field EFI's: Nil Signals: 11kv trip Remarks: lightning. Dop patrolled nothing found | January | 2016 | 2016Q3 | 2016 | ZN2196:PA25 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-01-14 | Y | 265 | N | 4 | N | Y | 1.1101 | 39.4971 | 336958.2799
[7 empty] | 10771 | 5171 | 1354659 | 2016-01-14 11:58 | 2016-01-14 20:10 | 492 | 11kV | 83244 | 182 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 165345 overcurrent; Earth Fault mains down pole AI-80090 section isolated for repairs fdr restored to links 74996 & sw 74582 Excluded oms 1354659 | January | 2016 | 2016Q3 | 2016 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2016-01-14 | Y | 457.3846 | N | 4 | N | Y | 1.1101 | 39.4971 | 60832.2599
[7 empty] | 11873 | 16751 | 1354068 | 2016-01-14 15:50 | 2016-01-14 20:35 | 285 | 11kV | 129864 | 618 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | Y | Zn12600 Panel 1 "The Dog Trap Gully" fdr tripped, reclosed and locked out on A phase timed OC, EFI, reclose timing and lockout relays EFI: S14727 Cause: Storm See 1357587,8,9 exclude 1354068 | January | 2016 | 2016Q3 | 2016 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Veg | 2016-01-14 | Y | 210.1359 | N | 4 | N | Y | 1.1101 | 39.4971 | 94900.7809
[7 empty] | 11031 | 7872 | 1353995 | 2016-01-14 15:44 | 2016-01-14 20:36 | 292 | 11kV | 198268 | 679 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | Y | @Zn2196 Milperra 11kv VCB panel 2 "S61792" feeder tripped on: Relays - C phase O/C trip, EFI Field EFI's: S61792, S4534, S6612, S35688 Signals- 11kv trip Abnormal: AB2735 Open AB290 Closed Remarks: lightning dop patrolled nothing found | January | 2016 | 2016Q3 | 2016 | ZN2196:PA2 | ZN2196:PA2 | ZN02196/000002 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-01-14 | Y | 292 | N | 4 | N | Y | 1.1101 | 39.4971 | 144888.4065
[7 empty] | 12067 | 18628 | 1353898 | 2016-01-14 15:15 | 2016-01-14 20:54 | 339 | 11kV | 279675 | 825 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | At Zn9037 Miranda 11kv Panel 9 Tripped, reclosed tripped and locked out on Relays: Earth Fault with efi Cause: Storm, feeder patrolled by Dop | January | 2016 | 2016Q3 | 2016 | ZN9037:PA9 | ZN9037:PA9 | ZN09037/000009 | SUTHERLAND | OH | Not Veg | 2016-01-14 | Y | 339 | N | 4 | N | Y | 1.1101 | 39.4971 | 204378.241
[7 empty] | 12252 | 20441 | 1353994 | 2016-01-14 15:38 | 2016-01-14 21:00 | 322 | 11kV | 138205 | 608 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn35370 Galston Panel 4 tripped Abnormal Switching: CP555 Arcadia Park Open due to previous fault. Cause: Tree branch on 11kV OH adjacent to LB1166.. See OMS 1360522 1362523 1360524 1360526 1360528 1353994 | January | 2016 | 2016Q3 | 2016 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2016-01-14 | Y | 227.3109 | N | 4 | N | Y | 1.1101 | 39.4971 | 100996.1376
[7 empty] | 11379 | 11718 | 1353846 | 2016-01-14 15:17 | 2016-01-14 21:20 | 363 | 11kV | 364089 | 1003 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S10999 Kogarah Panel 36 tripped on Relays: A and C phase IOC, EFI, Earth Fault Abnormal Switching: SW/A Open at S47631 with AB30048 Closed Cause: Rain wind storm See OMS 1357602 1353846 | January | 2016 | 2016Q3 | 2016 | ZN10999:PA36 | ZN10999:PA36 | ZN10999/000036 | GEORGES RIVER | OH | Not Veg | 2016-01-14 | Y | 363 | N | 4 | N | Y | 1.1101 | 39.4971 | 266065.5024
[7 empty] | 11853 | 16558 | 1353785 | 2016-01-14 14:32 | 2016-01-14 22:00 | 448 | 11kV | 448 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Hot >35C | Y | LID 165340 B phase DOLF : 10 Amp excluded omd 1353785 | January | 2016 | 2016Q3 | 2016 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2016-01-14 | Y | 448 | N | 4 | N | Y | 1.1101 | 39.4971 | 327.3852
[7 empty] | 12029 | 18308 | 1353927 | 2016-01-14 15:06 | 2016-01-14 22:03 | 417 | 11kV | 548355 | 1315 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor ABC | Unplanned | Lightning | Y | @Zn1287 Revesby 11kv VCB panel 11 "S4452" feeder tripped and reclosed tripped and locked out onL Relays: AC phase IOC, timmed O/C, reclose, timming, lockout Field EFI's: Nil Signals: 11kv trip Remarks: lightning, Dop patrolled nothing found | January | 2016 | 2016Q3 | 2016 | ZN1287:PA11 | ZN1287:PA11 | ZN01287/000011 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-01-14 | Y | 417 | N | 4 | N | Y | 1.1101 | 39.4971 | 400721.6603
[7 empty] | 11847 | 16518 | 1354045 | 2016-01-14 15:37 | 2016-01-14 22:25 | 408 | 11kV | 463776 | 1265 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | At Zn1287 Revesby Panel 17 tripped, reclosed tripped and locked out on Relays: B phase Earth Fault, Overcurrent, EFI, E/F Check, Reclose, Timing and Lockout Signals: 11kV Trip, Group Earth and Zone Earth Cause: Weather related Lightning in area. Kiosk on fire reported by the public See OMS 1361116 1353954 1354406 13504045 | January | 2016 | 2016Q3 | 2016 | ZN1287:PA17 | ZN1287:PA17 | ZN01287/000017 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-01-14 | Y | 366.6213 | N | 4 | N | Y | 1.1101 | 39.4971 | 338913.8217
[7 empty] | 11894 | 16920 | 1354067 | 2016-01-14 15:56 | 2016-01-14 22:46 | 410 | 11kV | 652009 | 1742 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12600 Lisarow Panel 3 "Lisarow High Talor" tripped and locked out on C phase, timed overcurrent, lockout and timing relay large branch near PT11618 See 1357596,7 exclude 1354067 | January | 2016 | 2016Q3 | 2016 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2016-01-14 | Y | 374.2876 | N | 4 | N | Y | 1.1101 | 39.4971 | 476468.9462
[7 empty] | 11410 | 11947 | 1353830 | 2016-01-14 15:06 | 2016-01-15 00:02 | 535.95 | 11kV | 263687.4 | 492 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S10994 Mortdale Panel 14 Tripped reclosed tripped and locked out on Relays: A B and C phase IOC, Earth Fault, reclose, Timing and EFI Signals: 11kV Trip Field EFI's Cause: DOp Patrolled ok. Suspect Lightning strike | January | 2016 | 2016Q3 | 2016 | ZN10994:PA14 | ZN10994:PA14 | ZN10994/000014 | GEORGES RIVER | OH | Not Veg | 2016-01-14 | Y | 535.95 | N | 4 | N | Y | 1.1101 | 39.4971 | 192694.9745
[7 empty] | 10800 | 5498 | 1353840 | 2016-01-14 15:15 | 2016-01-15 00:05 | 530 | 11kV | 807190 | 1523 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | Y | At S109999 Kogarah Panel 17 tripped reclosed tripped and locked out on A + B phase timed overcurrent, earth fault, reclose timing, E/F check Cause: 11kV Bond off at UGOH. 11kV feeder isolated from PA417 to Link 30790 | January | 2016 | 2016Q3 | 2016 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | OH | Not Veg | 2016-01-14 | Y | 530 | N | 4 | N | Y | 1.1101 | 39.4971 | 589870.6439
[7 empty] | 11846 | 16516 | 1355163 | 2016-01-14 21:11 | 2016-01-15 00:35 | 204 | 11kV | 168171 | 1224 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | At S129 Hunters Hill Panel 8 tripped on Signals: 11kV Trip Relays: B phase O/C and EF , EFI and Fault Check Cause not ascertained for outage See OMS 1360503 1360504 1360505 1355163 | January | 2016 | 2016Q3 | 2016 | ZN129:PA8 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Veg | 2016-01-14 | N | 137.3946 | N | 4 | N | N | 1.1101 | 39.4971 | 122894.4066
[7 empty] | 10952 | 7101 | 1354616 | 2016-01-14 16:38 | 2016-01-15 01:00 | 502 | 11kV | 737720 | 1718 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Rain Wind Storm | Y | Zn12610 Long Jetty Pa6 "Rhodin Drive" tripped on Sensitive Earth EFI PT12775 Boomerang Eloora Possible Lightning strike restored via LV// See trip on Panel 22 during restoration See 1358352,3,4,5,6,7,8 exclude 1354616 | January | 2016 | 2016Q3 | 2016 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Not Veg | 2016-01-14 | Y | 429.4063 | N | 4 | N | Y | 1.1101 | 39.4971 | 539104.0169
[7 empty] | 11954 | 17562 | 1354710 | 2016-01-14 17:45 | 2016-01-15 01:06 | 441 | 11kV | 5330 | 14 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 165350 4 fault operations Feeder off pin near ELB 46133. Targets please. Excluded OMS 1354710 | January | 2016 | 2016Q3 | 2016 | 813:89058 | 813:89058 | ZN00813/089058 | UPPER HUNTER | OH | Not Veg | 2016-01-14 | Y | 380.7143 | N | 4 | N | Y | 1.1101 | 39.4971 | 3895.0068
[7 empty] | 10762 | 5100 | 1353730 | 2016-01-14 13:13 | 2016-01-15 01:10 | 717 | 11kV | 133794 | 193 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | Y | Recloser CP555 Arcadia tripped on Overcurrent Abnormal Switching: LB61258 Closed With CP3281 Bay Cooper Open Cause: Cause not ascertained DOp found HV close to within minimum clearances - adjacent to LB 2874. See OMS 1360490 1360494 1353730 1353994 1355173 | January | 2016 | 2016Q3 | 2016 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2016-01-14 | Y | 693.2332 | N | 4 | N | Y | 1.1101 | 39.4971 | 97772.7089
[7 empty] | 12098 | 18900 | 1354943 | 2016-01-14 19:33 | 2016-01-15 01:37 | 364 | 11kV | 178634 | 527 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 165355 2 fault operations Earth Fault | January | 2016 | 2016Q3 | 2016 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2016-01-14 | Y | 338.9639 | N | 4 | N | Y | 1.1101 | 39.4971 | 130540.4584
[7 empty] | 11709 | 14957 | 1355318 | 2016-01-14 23:44 | 2016-01-15 01:50 | 126 | 11kV | 25762 | 847 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Cross arm | Unplanned | No Weather Impact | Y | LID 165443 1 fault operation C phase Overcurrent Replaced Xarm pole JV-12809, will require pole replacement from D Linich. Excluded OMS 1355318 | January | 2016 | 2016Q3 | 2016 | 221:11897 | 221:11897 | ZN00221/011897 | LAKE MACQUARIE | OH | Veg | 2016-01-14 | Y | 30.4156 | N | 4 | N | Y | 1.1101 | 39.4971 | 18826.1097
[7 empty] | 10667 | 4078 | 1354250 | 2016-01-14 16:26 | 2016-01-15 02:00 | 574 | 11kV | 282408 | 492 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | Y | ex Panel 4 from S109999 Kogarah 11kV UGOH bond blown off anf clear. Bond Between AB31104 and AB31001 See OMS 1357595 1354250 | January | 2016 | 2016Q3 | 2016 | ZN10999:PA4 | ZN10997:PA6 | ZN10997/000006 | GEORGES RIVER | OH | Not Veg | 2016-01-14 | Y | 574 | N | 4 | N | Y | 1.1101 | 39.4971 | 206375.4368
[7 empty] | 11947 | 17444 | 1355063 | 2016-01-14 20:05 | 2016-01-15 03:34 | 449.4 | 11kV | 635901 | 1415 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 165378 2 fault operations B phase Overcurrent | January | 2016 | 2016Q3 | 2016 | 258:80793 | 258:80793 | ZN00258/080793 | NEWCASTLE | OH | Veg | 2016-01-14 | N | 449.4 | N | 4 | N | N | 1.1101 | 39.4971 | 464697.6949
[7 empty] | 11138 | 9266 | 1353979 | 2016-01-14 13:53 | 2016-01-15 03:45 | 832 | 11kV | 456768 | 549 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | Y | eX pANEL 2 s48648 rIVERWOOD aUX nO2 HV Bond Burnt off HV UGOH (Between SW/A S10987 to UGOH) See OMS 1357969 13539479 Note customers also impacted by event OMS 1357039 and 1357042 that began 14/01/2016 15:12 and finished 14/01/2016 19:07 | January | 2016 | 2016Q3 | 2016 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | Unknown | Unknown | 2016-01-14 | Y | 832 | N | 4 | N | Y | 1.1101 | 39.4971 | 333792.582
[7 empty] | 11506 | 12761 | 1353935 | 2016-01-14 15:34 | 2016-01-15 04:30 | 776 | 11kV | 535990 | 1221 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn10991 Blakehurst Panel 12 feeder Tripped Reclosed Tripped on Signals: 11kV Trip. Cause:Tree branch brought down 11kV OH mains . Feeder was isolated and earthed. See OMS 1357995 1357998 135779987 1355259 135369135 | January | 2016 | 2016Q3 | 2016 | ZN10991:PA12 | ZN10991:PA12 | ZN10991/000012 | GEORGES RIVER | OH | Veg | 2016-01-14 | Y | 438.9762 | N | 4 | N | Y | 1.1101 | 39.4971 | 391685.683
[7 empty] | 11858 | 16605 | 1354811 | 2016-01-14 18:40 | 2016-01-15 04:52 | 612 | 11kV | 645184 | 1061 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor CCT | Unplanned | Rain Wind Storm | Y | Zn12690 Berkeley Vale 11kV Panel 12 tripped on AB phase overcurrent, EFI, SEF, timing and lockout 4 bays of 11kv CCT down in section of HV fdr bewteen LB43167 to LB43329 to LB40019 See 1358018,9,20 exclude 1354811 | January | 2016 | 2016Q3 | 2016 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2016-01-14 | Y | 608.0905 | N | 4 | N | Y | 1.1101 | 39.4971 | 471481.4375
[7 empty] | 11650 | 14217 | 1355120 | 2016-01-14 20:02 | 2016-01-15 05:00 | 538 | 11kV | 271248 | 762 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 165369 2 fault operations A & C phase Overcurrent 11kV mains down at ABS 25516 | January | 2016 | 2016Q3 | 2016 | 216:10726 | 216:10726 | ZN00216/010726 | LAKE MACQUARIE | OH | Not Veg | 2016-01-14 | Y | 355.9685 | N | 4 | N | Y | 1.1101 | 39.4971 | 198220.0379
[7 empty] | 12003 | 18078 | 1354954 | 2016-01-14 19:35 | 2016-01-15 05:05 | 570 | 11kV | 488490 | 857 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12600 Lisarow Panel 13 "Brush rd" tripped and locked out on BC phase overcurrent Reclose and lockout timing 11kv trip Branch on mains near PT11064 | January | 2016 | 2016Q3 | 2016 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2016-01-14 | Y | 570 | N | 4 | N | Y | 1.1101 | 39.4971 | 356974.084
[7 empty] | 11386 | 11765 | 1354782 | 2016-01-14 16:20 | 2016-01-15 06:15 | 835 | 11kV | 554737 | 961 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | Y | Zn12690 Berkeley Vale Panel 6 "Krone Enterprise" fdr tripped, reclosed, tripped and locked out Relays - B&C phase IOC, Reclose Timer, Lockout , EFI Signals: 11kv Trip, Zone Earth, Group EFI':s S18124 HV Bond off LB41187 See 1358037,8 Exclude 1354782,5108,83,342 | January | 2016 | 2016Q3 | 2016 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2016-01-14 | Y | 577.2497 | N | 4 | N | Y | 1.1101 | 39.4971 | 405385.4376
[7 empty] | 12117 | 19083 | 1354958 | 2016-01-14 19:36 | 2016-01-15 06:47 | 671 | 11kV | 625372 | 932 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 165398 A & B phase Overcurrent | January | 2016 | 2016Q3 | 2016 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Veg | 2016-01-14 | Y | 671 | N | 4 | N | Y | 1.1101 | 39.4971 | 457003.4122
[7 empty] | 10685 | 4326 | 1355319 | 2016-01-14 23:49 | 2016-01-15 08:45 | 536 | 11kV | 52528 | 98 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 165403 B Phase DOLF : 31 Amp Excluded OMS 1355319 | January | 2016 | 2016Q3 | 2016 | 221:11894 | 221:11894 | ZN00221/011894 | LAKE MACQUARIE | OH | Veg | 2016-01-14 | Y | 536 | N | 4 | N | Y | 1.1101 | 39.4971 | 38385.9131
[7 empty] | 11361 | 11578 | 1354991 | 2016-01-14 19:50 | 2016-01-15 09:15 | 805 | 11kV | 44855 | 56 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 165348 4 fault operations Excluded OMS 1354991 | January | 2016 | 2016Q3 | 2016 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2016-01-14 | Y | 800.9821 | N | 4 | N | Y | 1.1101 | 39.4971 | 32778.711
[7 empty] | 11763 | 15520 | 1355475 | 2016-01-15 07:08 | 2016-01-15 09:20 | 132 | 11kV | 264 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165400 A phase DOLF : 10 Amp Transformer volts 246V excluded OMS 1355475 | January | 2016 | 2016Q3 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | MUSWELLBROOK | OH | Veg | 2016-01-15 | N | 132 | N | 19 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 11602 | 13731 | 1354906 | 2016-01-14 19:17 | 2016-01-15 09:25 | 848 | 11kV | 9328 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 165406 C Phase DOLF : 16 Amp Excluded OMS 1354906 | January | 2016 | 2016Q3 | 2016 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2016-01-14 | Y | 848 | N | 4 | N | Y | 1.1101 | 39.4971 | 6816.6273
[7 empty] | 10857 | 6182 | 1355394 | 2016-01-15 04:50 | 2016-01-15 09:30 | 280 | 11kV | 268320 | 1415 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | LID 165396 Sensitive Earth Fault suspect transformer at sub 14042 | January | 2016 | 2016Q3 | 2016 | 258:80793 | 258:80793 | ZN00258/080793 | NEWCASTLE | UG | Not Veg | 2016-01-15 | N | 189.6254 | N | 19 | N | N | 1.1101 | 39.4971 | 196080.3419
[7 empty] | 11304 | 10985 | 1355477 | 2016-01-15 07:09 | 2016-01-15 09:45 | 156 | 11kV | 11388 | 73 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 135407 B phase striker fuse excluded OMS 1355477 | January | 2016 | 2016Q3 | 2016 | 221:11894 | 221:11894 | ZN00221/011894 | LAKE MACQUARIE | OH | Veg | 2016-01-15 | N | 156 | N | 19 | N | N | 1.1101 | 39.4971 | 8322.0145
[7 empty] | 11047 | 8014 | 1358004 | 2016-01-14 16:52 | 2016-01-15 10:14 | 1042 | 11kV | 752664 | 725 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 165402 1 fault operation Earth Fault Excluded OMS 1355377 | January | 2016 | 2016Q3 | 2016 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Veg | 2016-01-14 | Y | 1038.1572 | N | 4 | N | Y | 1.1101 | 39.4971 | 550024.6514
[7 empty] | 12156 | 19473 | 1358412 | 2016-01-15 09:46 | 2016-01-15 10:14 | 28 | 11kV | 48300 | 1725 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 165405 2 fault operations B Phase Earth fault Bird flashed over at pole JU-45209 | January | 2016 | 2016Q3 | 2016 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2016-01-15 | N | 28 | N | 19 | N | N | 1.1101 | 39.4971 | 35296.2154
[7 empty] | 12068 | 18638 | 1353560 | 2016-01-14 04:30 | 2016-01-15 10:30 | 1800 | 11kV | 5400 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | Y | LID 165331 A Phase DOLF : 10 Amp Excluded OMS 1353560 | January | 2016 | 2016Q3 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2016-01-14 | Y | 1800 | N | 4 | N | Y | 1.1101 | 39.4971 | 3946.1607
[7 empty] | 11630 | 14041 | 1354107 | 2016-01-14 16:10 | 2016-01-15 10:32 | 1101.5333 | 11kV | 1101.5333 | 1 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | Y | Subpole 59040 9T90040 blown over in severe storm caused this section of fdr to trip out. same as job 1354143 CC1: 22-"Refer to SOp" | January | 2016 | 2016Q3 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2016-01-14 | Y | 1101.5333 | N | 4 | N | Y | 1.1101 | 39.4971 | 804.9681
[7 empty] | 11200 | 9918 | 1355260 | 2016-01-14 22:22 | 2016-01-15 10:35 | 733 | 11kV | 1466 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | Y | LID 165401 A phase DOLF : 10 Amp Replaced Lightning Arrestors Excluded OMS 1355260 | January | 2016 | 2016Q3 | 2016 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2016-01-14 | Y | 733 | N | 4 | N | Y | 1.1101 | 39.4971 | 1071.3096
[7 empty] | 11977 | 17777 | 1353863 | 2016-01-14 15:18 | 2016-01-15 10:45 | 1167 | 11kV | 257423 | 631 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn9550 Gwawley Bay Panel 9 feeder tripped Relays: Earth Fault, EFI Signals: 11kV Trip Cause: Tree on PT9745 Shirley Gwawley No Access to S9899 or S9395 See OMS 1357520 1357524 1357523 1357522 1353863 1355374 | January | 2016 | 2016Q3 | 2016 | ZN9550:PA9 | ZN9550:PA9 | ZN09550/000009 | SUTHERLAND | OH | Veg | 2016-01-14 | Y | 407.9604 | N | 4 | N | Y | 1.1101 | 39.4971 | 188117.1357
[7 empty] | 12163 | 19512 | 1355085 | 2016-01-14 20:25 | 2016-01-15 11:00 | 875 | 11kV | 707900 | 1145 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Transformer | Unplanned | Electrical Storm | Y | LID 165362 1 fault operation Sensitive Earth Fault defective transformer 11105 | January | 2016 | 2016Q3 | 2016 | 214:8667 | 224:80326 | ZN00224/080326 | LAKE MACQUARIE | OH | Not Veg | 2016-01-14 | Y | 618.2533 | N | 4 | N | Y | 1.1101 | 39.4971 | 517312.4405
[7 empty] | 12072 | 18661 | 1363847 | 2016-01-14 17:53 | 2016-01-15 11:40 | 1067 | 11kV | 23474 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | LID 165414 B Phase DOLF : 16 Amp Excluded OMS 1354854 | January | 2016 | 2016Q3 | 2016 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2016-01-14 | Y | 1067 | N | 4 | N | Y | 1.1101 | 39.4971 | 17154.1068
[7 empty] | 11570 | 13379 | 1357184 | 2016-01-14 16:00 | 2016-01-15 12:10 | 1210 | 11kV | 94380 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At Zn1287 Revesby ex Panel 21 there is a burnt bond at AB2989 Abnormal: AB2997 Closed, LB1516 open and defective Remarks: storm, tree branch on OH in Sandaka. Burnt bond at AB2989 | January | 2016 | 2016Q3 | 2016 | ZN1287:PA21 | ZN1287:PA21 | ZN01287/000021 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-01-14 | Y | 1210 | N | 4 | N | Y | 1.1101 | 39.4971 | 68970.1203
[7 empty] | 11624 | 14011 | 1354281 | 2016-01-14 18:06 | 2016-01-15 12:15 | 1089 | 11kV | 17424 | 16 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | Y | At Sub 2585 Gipps Loftus all three 11kv Tx fuses have blown Remarks: tx failure. 11kv/415v tx has failed @ Sub 2585 Gipps Loftus. left switched only. See outage @ S450 at similar time due to LV//8908 being closed at time of fault. | January | 2016 | 2016Q3 | 2016 | ZN2835:PA24 | ZN2835:PA19 | ZN02835/000019 | BURWOOD | UG | Not Veg | 2016-01-14 | Y | 1089 | N | 4 | N | Y | 1.1101 | 39.4971 | 12732.9453
[7 empty] | 10642 | 3777 | 1355051 | 2016-01-15 00:17 | 2016-01-15 12:20 | 723 | 11kV | 29643 | 41 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 165409 Sub isolated for safety LV mains down at pole JU-42044 excluded OMS 1355051, 1355823, 1355513 | January | 2016 | 2016Q3 | 2016 | 261:81870 | 261:81870 | ZN00261/081870 | NEWCASTLE | OH | Not Veg | 2016-01-15 | N | 723 | Y | 19 | N | Y | 1.1101 | 39.4971 | 21662.2301
[7 empty] | 11089 | 8638 | 1355861 | 2016-01-15 10:46 | 2016-01-15 13:00 | 134 | 11kV | 670 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165417 A phase DOLF : 10 Amp Excluded OMS 1355861 | January | 2016 | 2016Q3 | 2016 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2016-01-15 | N | 134 | N | 19 | N | N | 1.1101 | 39.4971 | 489.6162
[7 empty] | 12007 | 18129 | 1355829 | 2016-01-15 10:28 | 2016-01-15 13:05 | 157 | 11kV | 2041 | 13 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 165412 Fedder isolated to repair broken 11kV tappings at pole AI-80063. Excluded OMS No. 1355829 | January | 2016 | 2016Q3 | 2016 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2016-01-15 | N | 157 | N | 19 | N | N | 1.1101 | 39.4971 | 1491.5026
[7 empty] | 11217 | 10051 | 1356073 | 2016-01-15 00:01 | 2016-01-15 13:35 | 814 | 11kV | 136752 | 168 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 165423 Burnt off tapping on pole HR-80470 Excluded OMS 1355324, 1356073,1356096. | January | 2016 | 2016Q3 | 2016 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2016-01-15 | N | 814 | N | 19 | N | N | 1.1101 | 39.4971 | 99934.3281
[7 empty] | 11162 | 9541 | 1355401 | 2016-01-15 05:10 | 2016-01-15 13:35 | 505 | 11kV | 14140 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165419 A phase DOLF : 16 Amp | January | 2016 | 2016Q3 | 2016 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2016-01-15 | N | 505 | N | 19 | N | N | 1.1101 | 39.4971 | 10333.0949
[7 empty] | 10578 | 2945 | 1356114 | 2016-01-15 13:29 | 2016-01-15 14:00 | 31 | 11kV | 26195 | 845 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 165421 B phase ABS 17680 open circuit one phase Excluded OMS 1356114 | January | 2016 | 2016Q3 | 2016 | 221:11894 | 221:11894 | ZN00221/011894 | LAKE MACQUARIE | OH | Not Veg | 2016-01-15 | N | 31 | N | 19 | N | N | 1.1101 | 39.4971 | 19142.5334
[7 empty] | 11370 | 11630 | 1355507 | 2016-01-15 07:31 | 2016-01-15 14:22 | 410.6 | 11kV | 43934.2 | 107 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex Zn12690 Berkeley Vale section of Pa16 "Catamaran Sailcraft" fdr Recloser 45026 Fountaindale tripped OH down between Isolating links 43843 to links 40384 | January | 2016 | 2016Q3 | 2016 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Not Veg | 2016-01-15 | N | 410.6 | N | 19 | N | N | 1.1101 | 39.4971 | 32105.8175
[7 empty] | 10848 | 6048 | 1355469 | 2016-01-15 06:00 | 2016-01-15 15:13 | 553 | 11kV | 40922 | 74 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong Zone section of Pa8 CP48425 Kangy Angy tripped on IOC trip Tree branch brought down OH near AB44575 | January | 2016 | 2016Q3 | 2016 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2016-01-15 | N | 553 | N | 19 | N | N | 1.1101 | 39.4971 | 29904.5906
[7 empty] | 10532 | 2405 | 1353868 | 2016-01-14 19:12 | 2016-01-15 16:30 | 1277.7833 | 11kV | 102222.6667 | 80 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Large tree branch on wires O/S 46 Baxter Road, Bass Hill. Wires also reported down | January | 2016 | 2016Q3 | 2016 | ZN1290:PA4 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-01-14 | Y | 1277.7833 | N | 4 | N | Y | 1.1101 | 39.4971 | 74701.3097
[7 empty] | 11658 | 14340 | 1355589 | 2016-01-15 08:32 | 2016-01-15 17:00 | 508 | 11kV | 2540 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165431 C phase DOLF : 10 Amp 248V Load 11; 11; 1 amp Excluded OMS 1355589 | January | 2016 | 2016Q3 | 2016 | 528:83014 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Veg | 2016-01-15 | N | 508 | N | 19 | N | N | 1.1101 | 39.4971 | 1856.1571
[7 empty] | 10931 | 6921 | 1355565 | 2016-01-15 08:16 | 2016-01-15 17:45 | 569 | 11kV | 3983 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 1357536 B Phase DOLF : 16 Amp excluded OMS 1355565 | January | 2016 | 2016Q3 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2016-01-15 | N | 569 | N | 19 | N | N | 1.1101 | 39.4971 | 2910.6589
[7 empty] | 10763 | 5102 | 1356037 | 2016-01-15 12:38 | 2016-01-15 17:50 | 312 | 11kV | 624 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165436 C Phase DOLF : 16 Amp Excluded OMS 1356037 | January | 2016 | 2016Q3 | 2016 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2016-01-15 | N | 312 | N | 19 | N | N | 1.1101 | 39.4971 | 456.0008
[7 empty] | 11392 | 11801 | 1354266 | 2016-01-14 15:41 | 2016-01-15 18:15 | 1594 | 11kV | 1065415 | 670 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Panel 11 Berowra CP1772 Seymours Creek tripped on overcurrent Cause: Tree branch brought down 11kV OH adjacent to CP1238 Milsons Passage Tree branch also brought down 11kV OH adjacent to PT643 Wharf Rd Brooklyn See OMS 1360336 1360337 1360350 1354266 | January | 2016 | 2016Q3 | 2016 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2016-01-14 | Y | 1590.1716 | N | 4 | N | Y | 1.1101 | 39.4971 | 778573.8576
[7 empty] | 11789 | 15827 | 1353800 | 2016-01-14 15:08 | 2016-01-15 19:05 | 1677 | 11kV | 1437049 | 1623 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | Y | @ZN2196 Milperra: 11kv Panel 5 "S8696 Marigold Amour No.4" tripped/reclosed/tripped: Relays: C phase timed OC, timing, lockout Signals: 11kv trip Abnormal: AB290 closed, AB2735 Defective and open Remarks: lightning, feeder damaged in multiple locations, broken X arm below AB2800, Burnt off bond on load side of LB133, Tree on 11kv O/H below Sub6358 Cook Park between UGOH's. | January | 2016 | 2016Q3 | 2016 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-01-14 | Y | 885.4276 | N | 4 | N | Y | 1.1101 | 39.4971 | 1050153.0234
[7 empty] | 10724 | 4679 | 1355369 | 2016-01-15 07:45 | 2016-01-15 19:05 | 680 | 11kV | 27200 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | At PT9489 Kangaroo Point rd North HDO operated Cause:weather related see OMS 1357104 1356045 1355529 | January | 2016 | 2016Q3 | 2016 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Veg | 2016-01-15 | N | 680 | N | 19 | N | N | 1.1101 | 39.4971 | 19876.9577
[7 empty] | 11127 | 9050 | 1357362 | 2016-01-15 07:42 | 2016-01-15 19:10 | 688 | 11kV | 688 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 165442 A phase DOLF : 16 Amp sub isolated to replace transformer | January | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | OH | Not Veg | 2016-01-15 | N | 688 | Y | 19 | N | Y | 1.1101 | 39.4971 | 502.7701
[7 empty] | 10885 | 6451 | 1354530 | 2016-01-14 16:19 | 2016-01-15 19:55 | 1656 | 11kV | 62928 | 38 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14891 Wyong Zone section of Panel 12 CP46228 Ravensdale recloser tripped and locked out No Flags Tree/Branch brought down OH | January | 2016 | 2016Q3 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2016-01-14 | Y | 1656 | N | 4 | N | Y | 1.1101 | 39.4971 | 45985.9263
[7 empty] | 11262 | 10524 | 1354727 | 2016-01-14 16:20 | 2016-01-15 21:45 | 1765 | 11kV | 627451 | 812 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn12610 Long Jetty section of Pa1 IR61580 Yimbala Cornish tripped and locke dout on overcurrent Tree branch on seciton of 11kV near PT11377 isoalted from AB42091 AB42071 AB42098 AB42072 tee PT11377 See 1358338,9,40,41,2 exclude 1354727,5868,6116 | January | 2016 | 2016Q3 | 2016 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Veg | 2016-01-14 | Y | 772.7229 | N | 4 | N | Y | 1.1101 | 39.4971 | 458522.6841
[7 empty] | 11820 | 16218 | 1357432 | 2016-01-15 21:25 | 2016-01-15 23:50 | 145 | 11kV | 7250 | 50 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 165447 No Protection operation 11kV mains dwon pole GS-62101 | January | 2016 | 2016Q3 | 2016 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2016-01-15 | N | 145 | N | 19 | N | N | 1.1101 | 39.4971 | 5298.0862
[7 empty] | 10388 | 298 | 1355362 | 2016-01-15 02:31 | 2016-01-15 23:59 | 1288 | 11kV | 170016 | 132 | HV | Lightning Strike | Adverse Weather/Environment | Fuse Assembly | Unplanned | Previous Storm | N | At PT10893 Calendonia Park A and B phase HDO operated Cause: B PHase HDO assembly damaged +Lightning See OMS 1355365 1355362 | January | 2016 | 2016Q3 | 2016 | ZN10995:PA13 | ZN10995:PA13 | ZN10995/000013 | GEORGES RIVER | OH | Not Veg | 2016-01-15 | N | 1288 | N | 19 | N | N | 1.1101 | 39.4971 | 124242.6782
[7 empty] | 11645 | 14150 | 1353856 | 2016-01-14 15:17 | 2016-01-16 08:00 | 2443 | 11kV | 1007076 | 1509 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Rain Wind Storm | Y | At S109999 Kogarah Panel 15 tripped reclosed tripped and locked out on A and B phase IOC, Timing, Earth Fault. 11kV UGOH Defective after lightning. See OMS 1357565 1357567 1353856 1355288 1355901 1357567 | January | 2016 | 2016Q3 | 2016 | ZN10999:PA15 | ZN10999:PA15 | ZN10999/000015 | BAYSIDE | OH | Not Veg | 2016-01-14 | Y | 667.3797 | N | 4 | N | Y | 1.1101 | 39.4971 | 735941.4371
[7 empty] | 10423 | 818 | 1354740 | 2016-01-14 16:25 | 2016-01-16 11:35 | 2590 | 11kV | 706776 | 2100 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | Y | Zn12610 Long Jetty Pa13 "The Blue Bay" fdr tripped on timed overcurrent and EFI 11kV Link 40385 to AB40376 tee PT11003 footpath phase bond off See 1358347,8 exclude 1354740 | January | 2016 | 2016Q3 | 2016 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2016-01-14 | Y | 336.56 | N | 4 | N | Y | 1.1101 | 39.4971 | 516491.0544
[7 empty] | 10377 | 171 | 1356460 | 2016-01-16 07:09 | 2016-01-16 12:28 | 319.9667 | 33kV Distribution | 319.9667 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N |  | January | 2016 | 2016Q3 | 2016 |  |  |  | NEWCASTLE | Unknown | Not Veg | 2016-01-16 | N | 319.9667 | N | 10 | N | N | 1.1101 | 39.4971 | 233.8222
[7 empty] | 12006 | 18115 | 1354603 | 2016-01-14 16:19 | 2016-01-16 12:54 | 2675 | 11kV | 149800 | 56 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn14891 Wyong section of Panel 12 REc45015 Bursh Creek tripped, reclosed & locked out on Relays: IOC Signals: 11kv trip Tree/Branch brought down Overhead CC1: 22-"Refer to SOp" | January | 2016 | 2016Q3 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2016-01-14 | Y | 2675 | N | 4 | N | Y | 1.1101 | 39.4971 | 109469.4216
[7 empty] | 10882 | 6421 | 1355777 | 2016-01-16 10:04 | 2016-01-16 13:30 | 206 | 11kV | 1442 | 7 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Previous Storm | N | PT14507 Arundal Milina 11kv A phase HDO operated Cause: Lightning/Surge Arrestor | January | 2016 | 2016Q3 | 2016 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2016-01-16 | N | 206 | N | 10 | N | N | 1.1101 | 39.4971 | 1053.7711
[7 empty] | 10549 | 2597 | 1356487 | 2016-01-16 08:33 | 2016-01-16 14:30 | 357 | 11kV | 1071 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165452 Single phase DOLF : 10 Amp dead bird found at sub Excluded OMS 1356487 | January | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-01-16 | N | 357 | N | 10 | N | N | 1.1101 | 39.4971 | 782.6552
[7 empty] | 11627 | 14030 | 1353822 | 2016-01-14 15:12 | 2016-01-16 16:15 | 2943 | 11kV | 687549 | 1020 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S10994 Mortdale Panle 1 Seaforth Ave tripped reclosed tripped and locked out on Relays: A and B phase IOC, Earth Fault, Timing, Lockout and EFI Signals: 11kV Trip Cause: Tree brought down 11kV OH. HV into LV. Lineworkers have cutaway and made safe See OMS 1357861 1357863 1357864 1355372 1355392 1355835 | January | 2016 | 2016Q3 | 2016 | ZN10994:PA1 | ZN10994:PA1 | ZN10994/000001 | GEORGES RIVER | OH | Veg | 2016-01-14 | Y | 674.0676 | N | 4 | N | Y | 1.1101 | 39.4971 | 502440.5299
[7 empty] | 10522 | 2301 | 1354232 | 2016-01-14 16:19 | 2016-01-16 16:28 | 2889 | 11kV | 1160461 | 1168 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12690 Berkeley Vale Panel 19 tripped on IOC RH Leg Weather related See 1357886,8,9,90,1,2,3,4,5,6,7,8 Exclude 1354232,5976,7,9,80,1,2,3,4 | January | 2016 | 2016Q3 | 2016 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2016-01-14 | Y | 993.5454 | N | 4 | N | Y | 1.1101 | 39.4971 | 848030.671
[7 empty] | 11937 | 17270 | 1354799 | 2016-01-14 18:28 | 2016-01-16 16:32 | 2764 | 11kV | 1211689 | 2121 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12580 Erina Panel 4 tripped, closed, tripped on A phase instantaneous & timed overcurrent, EFI HV Down & into LV in section of fdr AB43779to LB42564 to AB40759 tee PT14204 7 PT12799 See 1358374,5,6,7,8 exclude 1354799,864,6107,11 | January | 2016 | 2016Q3 | 2016 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Not Veg | 2016-01-14 | Y | 571.2819 | N | 4 | N | Y | 1.1101 | 39.4971 | 885466.5824
[7 empty] | 12063 | 18611 | 1356662 | 2016-01-16 15:47 | 2016-01-16 16:45 | 58 | 11kV | 5306 | 112 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 165453 3 fault operations C phase Overcurrent tree fell on 11kV ohm os 195 Browns Rd. Reports it was from a customer using a chainsaw but denied onsite. no further repair action required. DQ Excluded oms1356662## | January | 2016 | 2016Q3 | 2016 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2016-01-16 | N | 47.375 | N | 10 | N | N | 1.1101 | 39.4971 | 3877.4683
[7 empty] | 11900 | 16948 | 1354140 | 2016-01-14 15:48 | 2016-01-16 17:15 | 2967 | 11kV | 117463 | 87 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | Ex Zn12630 Peats Ridge section of Panel 5 CP61082 Breises Peats tripped and locked out on ovvercurrent and SEF ABNORMAL: HV link 41886 open and defective LB62765 closed from Panel 4 OH DOwn between USL41638 to LB44805 See 1357052,3,4 Exclude 1354049,6119 | January | 2016 | 2016Q3 | 2016 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2016-01-14 | Y | 1350.1494 | N | 4 | N | Y | 1.1101 | 39.4971 | 85838.4958
[7 empty] | 11448 | 12218 | 1356676 | 2016-01-16 16:19 | 2016-01-16 17:20 | 61 | 11kV | 122 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165454 A Phase DOLF : 10 Amp Excluded OMS 1356676 | January | 2016 | 2016Q3 | 2016 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2016-01-16 | N | 61 | N | 10 | N | N | 1.1101 | 39.4971 | 89.154
[7 empty] | 12185 | 19727 | 1356385 | 2016-01-15 19:48 | 2016-01-16 17:32 | 1304 | 11kV | 10432 | 8 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 165455 LLC off OHM to DOLF at sub 5517 Repairs completed Excluded OMS 1356385 | January | 2016 | 2016Q3 | 2016 | 264:81232 | 264:81232 | ZN00264/081232 | MAITLAND | OH | Not Veg | 2016-01-15 | N | 1304 | N | 19 | N | N | 1.1101 | 39.4971 | 7623.3979
[7 empty] | 11415 | 11966 | 1355033 | 2016-01-14 20:15 | 2016-01-16 18:00 | 2745 | 11kV | 21960 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn12630 Peats Ridge section of Panel 1 RE61340 George Bloodtree 0.2 Relays: SEF Signals: 11kv trip Cause: Tree/Branch brought down OH adjacent PT13500 See 1357574,5 exclude 1355033 | January | 2016 | 2016Q3 | 2016 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2016-01-14 | Y | 2745 | N | 4 | N | Y | 1.1101 | 39.4971 | 16047.7203
[7 empty] | 10993 | 7533 | 1356402 | 2016-01-16 12:10 | 2016-01-16 18:45 | 395 | 11kV | 5530 | 14 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Previous Storm | N | Ex Zn12630 Peats Ridge section of Pa3 PT13226 Kirks Ironbark 0.4 HDO assembly failure See 1356001 exclude 1356402,583 CC1: 22-"Refer to SOp" | January | 2016 | 2016Q3 | 2016 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2016-01-16 | N | 395 | N | 10 | N | N | 1.1101 | 39.4971 | 4041.1609
[7 empty] | 10527 | 2363 | 1356685 | 2016-01-16 17:16 | 2016-01-16 19:30 | 134 | 11kV | 3752 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165456 A phase DOLF : 16 Amp No cause found Same fuse blew on 15/01/16. Excluded OMS 1356695, 1356685 | January | 2016 | 2016Q3 | 2016 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2016-01-16 | N | 134 | N | 10 | N | N | 1.1101 | 39.4971 | 2741.8509
[7 empty] | 10596 | 3199 | 1356723 | 2016-01-16 20:08 | 2016-01-16 21:12 | 64 | 11kV | 88474 | 1888 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 165458 2 fault operations 3 phase Earth Fault ; Overcurrent | January | 2016 | 2016Q3 | 2016 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | Unknown | Unknown | 2016-01-16 | N | 46.8612 | N | 10 | N | N | 1.1101 | 39.4971 | 64654.1897
[7 empty] | 11432 | 12132 | 1356709 | 2016-01-16 19:42 | 2016-01-16 23:29 | 227 | 11kV | 598842 | 2766 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn10990 Arncliffe Panel 6 Tripped on Relays: A phase IOC, A phase timed O/C, E/F, reclose, timing and lockout Abnormal Switching: SW/B closed at S47163 AB30032 Opened Cause: UG fault on section of 11kV feeder from SW/B at S10437 to SW/B at S47163. See OMS 13580255 1358026 1358027 1356711 1356709 | January | 2016 | 2016Q3 | 2016 | ZN10990:PA8 | ZN10998:PA10 | ZN10998/000010 | BAYSIDE | UG | Not Veg | 2016-01-16 | N | 216.5011 | N | 10 | N | N | 1.1101 | 39.4971 | 437616.0708
[7 empty] | 10974 | 7335 | 1356768 | 2016-01-17 08:39 | 2016-01-17 09:15 | 36 | 11kV | 2232 | 62 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | Ex Zn12610 Long Jetty section of Pa25 PT11560 Lynwood Lakseide 11kv roadside HDO operated. Surge arrestor defective See 1356769 exclude 1356768,71 CC1: 22-"Refer to SOp" | January | 2016 | 2016Q3 | 2016 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2016-01-17 | N | 36 | N | 2 | N | N | 1.1101 | 39.4971 | 1631.0798
[7 empty] | 11840 | 16459 | 1354137 | 2016-01-14 15:48 | 2016-01-17 14:45 | 4257 | 11kV | 105120 | 35 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn12630 Peats Ridge section of Panel 1 "Grants Rd" RE46763 Grants Keighly 0.3 fdr tripped and locked out on Relays: OC, EF Signals: 11kv trip EFI's: Nil 11kv mains down beyond AB47842 plus tree on 11kv mains beyond AB40514 See 1357548,9,50 exclude 1355830 | January | 2016 | 2016Q3 | 2016 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2016-01-14 | Y | 3003.4286 | N | 4 | N | Y | 1.1101 | 39.4971 | 76818.5955
[7 empty] | 11881 | 16820 | 1356817 | 2016-01-17 12:48 | 2016-01-17 16:37 | 229 | 11kV | 458 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165469 C phase DOLF : 10 Amp excluded OMS 1356817 | January | 2016 | 2016Q3 | 2016 | 264:81240 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Veg | 2016-01-17 | N | 229 | N | 2 | N | N | 1.1101 | 39.4971 | 334.6929
[7 empty] | 11245 | 10301 | 1354084 | 2016-01-14 15:55 | 2016-01-17 19:15 | 4520 | 11kV | 2240376 | 1710 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12650 West Gosford Panel "Dog Trap Rd" fdr tripped reclosed and locked out on AB phase timed Overcurrent, Earthfault, lockout and timing relay, efi CP44936 Bentley Rd Recloser tripped on SEF Multiple OH Down btw AB44060 to LB44051 btw AB40343 to LB40624 to USL42939 near PT12952 See 1357636,9,40,1,3,4,5,6,7,8,9,50,1,2 Exclude 1354084,120,200,938,5224,6083,4,5,185,406,7,706,7 | January | 2016 | 2016Q3 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2016-01-14 | Y | 1310.1614 | N | 4 | N | Y | 1.1101 | 39.4971 | 1637200.7009
[7 empty] | 10395 | 364 | 1356736 | 2016-01-16 23:14 | 2016-01-17 23:25 | 1451 | 11kV | 92864 | 64 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Previous Storm | N | Ex Zn12690 Berkeley Vale section of Pa24 Between LB42219 to USL 42212 tee PT11881,12121,13334,12516 interrutped for safety Tree Branch on HV ABC cable in Anderson Rd See 1358956 exclude 1356736,7,8,9 | January | 2016 | 2016Q3 | 2016 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2016-01-16 | N | 1451 | N | 10 | N | N | 1.1101 | 39.4971 | 67862.2722
[7 empty] | 12089 | 18807 | 1357316 | 2016-01-18 18:57 | 2016-01-18 20:20 | 83 | 11kV | 166 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165484 DOLF : 10 Amp Excluded OMS 1357316 | January | 2016 | 2016Q3 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2016-01-18 | N | 83 | N | 1 | N | N | 1.1101 | 39.4971 | 121.3079
[7 empty] | 10966 | 7254 | 1356431 | 2016-01-15 22:36 | 2016-01-19 02:10 | 4534 | 11kV | 108995 | 1186 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 165449 REPLACED FAULTY A PHASE L/A POLE HR-22489. excluded oms 1356431, 1356441 | January | 2016 | 2016Q3 | 2016 | 528:83013 | 528:83013 | ZN00528/083013 | MAITLAND | OH | Not Veg | 2016-01-15 | N | 91.9013 | N | 19 | N | N | 1.1101 | 39.4971 | 79650.3312
[7 empty] | 10474 | 1673 | 1357410 | 2016-01-19 09:41 | 2016-01-19 10:55 | 74 | 11kV | 4736 | 64 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165494 B Phase DOLF : 31 Amp Excluded OMS 1357428 | January | 2016 | 2016Q3 | 2016 | 221:11897 | 221:11897 | ZN00221/011897 | LAKE MACQUARIE | OH | Veg | 2016-01-19 | N | 74 | N | 4 | N | N | 1.1101 | 39.4971 | 3460.9291
[7 empty] | 10820 | 5694 | 1357398 | 2016-01-19 09:16 | 2016-01-19 13:54 | 278 | 11kV | 4170 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 165490 No Cause Found | January | 2016 | 2016Q3 | 2016 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2016-01-19 | N | 278 | N | 4 | N | N | 1.1101 | 39.4971 | 3047.313
[7 empty] | 10573 | 2862 | 1357502 | 2016-01-19 12:25 | 2016-01-19 17:40 | 315 | 11kV | 315 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 165505 B & C phase DOLF blown arrestors excluded OMS 1357502 | January | 2016 | 2016Q3 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2016-01-19 | N | 315 | N | 4 | N | N | 1.1101 | 39.4971 | 230.1927
[7 empty] | 10983 | 7452 | 1357661 | 2016-01-19 16:16 | 2016-01-19 18:26 | 130 | 11kV | 111304 | 1078 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn10994 Mortdale Panel 21L "Balmore Barr" fdr tripped, reclosed, treipped and locked out Relays: AB phase IOC, Earth Fault, EFI Signals: 11kv trip EFI's: nil Tree branch on mains found burnt on ground near tree off to S10699 Brittany Place See 1359874,6 exclude 1357661 | January | 2016 | 2016Q3 | 2016 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Veg | 2016-01-19 | N | 103.2505 | N | 4 | N | N | 1.1101 | 39.4971 | 81337.6803
[7 empty] | 11241 | 10255 | 1357760 | 2016-01-20 07:38 | 2016-01-20 09:06 | 88 | 11kV | 263335 | 3184 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN35600 Kingsford Panel 9 R & L tripped on: E/F F/L EFI Panel left No field EFI's UG fault - front line of feeder fault ME: 1360769 Withdrawn: 1357764, 1357760 | January | 2016 | 2016Q3 | 2016 | ZN35600:PA9 | ZN35600:PA9 | ZN35600/000009 | RANDWICK | UG | Not Veg | 2016-01-20 | N | 82.7057 | N | 8 | N | N | 1.1101 | 39.4971 | 192437.4509
[7 empty] | 11136 | 9235 | 1357987 | 2016-01-20 14:27 | 2016-01-20 15:12 | 45 | 11kV | 26978 | 707 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35400 North Sydney New 11kV Panel 95 Feeder Tripped on Relays: A phase overcurrent and earth fault on A and B protection 11kV cable fault betwen S726 Paul Northcliff units to S7734 Northcliff Paul. See OMS 1359775 1359776 1357987 1357992 | January | 2016 | 2016Q3 | 2016 | ZN35400:PA95 | ZN35400:PA95 | ZN35400/000095 | NORTH SYDNEY | UG | Not Veg | 2016-01-20 | N | 38.1584 | N | 8 | N | N | 1.1101 | 39.4971 | 19714.7267
[7 empty] | 10918 | 6825 | 1357927 | 2016-01-20 12:11 | 2016-01-20 15:35 | 204 | 11kV | 816 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 "Wyong" Autolink 48568 Private Dickson centre phase fuse had operated See 1358977 Exclude 1357916,27,8082 Suspect customer from PT18650 called to inform about neighbours no supply | January | 2016 | 2016Q3 | 2016 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2016-01-20 | N | 204 | N | 8 | N | N | 1.1101 | 39.4971 | 596.3087
[7 empty] | 10613 | 3433 | 1358053 | 2016-01-20 16:10 | 2016-01-20 19:24 | 194.1667 | 11kV | 5523.45 | 35 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165524 A phase DOLF : 31 Amp Excluded OMS 1358116 | January | 2016 | 2016Q3 | 2016 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Veg | 2016-01-20 | N | 157.8129 | N | 8 | N | N | 1.1101 | 39.4971 | 4036.3743
[7 empty] | 11951 | 17474 | 1358086 | 2016-01-20 17:22 | 2016-01-20 19:48 | 146 | 11kV | 335760 | 2813 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Zn10993 Hurstville North Zone Panel 23 Relays: SEL Signals: 11kv trip ABNORMAL: Sw/A closed @ S48119 Shaw West, LB31271 Open Bond Burnt at AB31126 Load Relief AB31213 Open S49272 SwB Closed, SwA S48119 Open, SwB S10815 Closed, SwB S10183 Closed See 1359880,2,3,4 exclude 1358088 | January | 2016 | 2016Q3 | 2016 | ZN10993:PA23 | ZN10993:PA23 | ZN10993/000023 | BAYSIDE | OH | Not Veg | 2016-01-20 | N | 119.3601 | N | 8 | N | N | 1.1101 | 39.4971 | 245363.5048
[7 empty] | 12186 | 19728 | 1358111 | 2016-01-20 17:49 | 2016-01-20 20:00 | 131 | 11kV | 131 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165523 B Phase DOLF : 16 Amp Excluded OMS 1358111 | January | 2016 | 2016Q3 | 2016 |  |  |  |  | OH | Veg | 2016-01-20 | N | 131 | N | 8 | N | N | 1.1101 | 39.4971 | 95.7309
[7 empty] | 12008 | 18131 | 1357916 | 2016-01-20 19:28 | 2016-01-20 21:00 | 92 | 11kV | 2484 | 27 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Air Break Switch | Unplanned | No Weather Impact | N | EX Zn14891 Wyong Zone section of Pa5 "Wyong" fdr LK44052 center phase was not fully closed See 1358984 exclude 1358134 | January | 2016 | 2016Q3 | 2016 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2016-01-20 | N | 92 | N | 8 | N | N | 1.1101 | 39.4971 | 1815.2339
[7 empty] | 10744 | 4929 | 1358157 | 2016-01-20 20:03 | 2016-01-20 22:15 | 132 | 11kV | 119088 | 1301 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn10995 Riverwood Panel 13" Hedley St" fdr tripped, reclosed, tripped and locked out Relays: EFI ACphase IOC and timed, relcose timing relay, Lockout Signals: 11kV protection. No2 Hollow Volts, No2 Tx GE EFI's: S10174 11kV UGOH between AB31153 and S10937 failed explosively See 1359917,8,9 exclude 1358157,72 | January | 2016 | 2016Q3 | 2016 | ZN10995:PA13 | ZN10995:PA13 | ZN10995/000013 | GEORGES RIVER | Unknown | Unknown | 2016-01-20 | N | 91.5357 | N | 8 | N | N | 1.1101 | 39.4971 | 87025.9979
[7 empty] | 11215 | 10031 | 1358221 | 2016-01-21 08:25 | 2016-01-21 09:50 | 85 | 11kV | 9520 | 112 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165531 B Phase DOLF : 40 Amp Cockatoo A = 243V 187A B = 233V 366A C = 239V 241A Excluded 1358221 | January | 2016 | 2016Q3 | 2016 | 222:33600 | 222:33600 | ZN00222/033600 | LAKE MACQUARIE | OH | Not Veg | 2016-01-21 | N | 85 | N | 18 | N | N | 1.1101 | 39.4971 | 6956.9352
[7 empty] | 11492 | 12664 | 1358298 | 2016-01-21 10:57 | 2016-01-21 11:50 | 53 | 11kV | 45898 | 866 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 165545 Following reconnect SI 11334, tapping burnt off ABS 999. Burnt off flag on ABS 999. ABS needs replacing. Excluded OMS 1358298 & 1359711 | January | 2016 | 2016Q3 | 2016 | 225:33676 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Not Veg | 2016-01-21 | N | 53 | N | 18 | N | N | 1.1101 | 39.4971 | 33540.9046
[7 empty] | 10646 | 3836 | 1358206 | 2016-01-21 10:00 | 2016-01-21 12:15 | 135 | 11kV | 270 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165543 A Phase DOLF : 10 Amp excluded OMS 1358206 | January | 2016 | 2016Q3 | 2016 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2016-01-21 | N | 135 | N | 18 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 11484 | 12618 | 1358223 | 2016-01-21 08:40 | 2016-01-21 12:45 | 245 | 11kV | 7350 | 30 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 165527 Emerg isolation to repair/replace OHM from pole MG-20236 to MG-20237 | January | 2016 | 2016Q3 | 2016 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2016-01-21 | N | 245 | N | 18 | N | N | 1.1101 | 39.4971 | 5371.1632
[7 empty] | 11469 | 12475 | 1358520 | 2016-01-21 16:09 | 2016-01-21 17:40 | 91 | 11kV | 19905 | 288 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 165552 4 fault operations A phase Earth Fault; Overcurrent faulty UGM off Sw 57290 liverpool st sub Excluded oms 1358520 | January | 2016 | 2016Q3 | 2016 | 813:89059 | 813:89059 | ZN00813/089059 | UPPER HUNTER | UG | Not Veg | 2016-01-21 | N | 69.1146 | N | 18 | N | N | 1.1101 | 39.4971 | 14545.9869
[7 empty] | 11906 | 17002 | 1358567 | 2016-01-21 18:14 | 2016-01-21 19:29 | 75 | 11kV | 8374 | 234 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | ZN15013 Terry Hills , Ex."Aumuna Mona" Panel 4, Rec 21350 Booralie Kulgoa has tripped Relays: OC trip and LO ZN15013 Terry Hills, Ex "Cooyong Rd" Panel 6, Rec 20828 Cooyong Rd has tripped Relays: IOC trip, OC trip and LO Abnormal switching: AB25194 closed defective, AB26217 open Lightning has hit AB64842, only appears to be a mark on metal work, Lineworker to inspect ME:1359718, 1359721 Withdrawn:1358567 | January | 2016 | 2016Q3 | 2016 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Not Veg | 2016-01-21 | N | 35.7863 | N | 18 | N | N | 1.1101 | 39.4971 | 6119.4722
[7 empty] | 11518 | 12830 | 1358582 | 2016-01-21 18:24 | 2016-01-21 19:44 | 80 | 11kV | 58750 | 799 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Zn12600 Lisarow Panel 1 "The Lisarow" fdr tripped and locked out on BC phase timed overcurrent, reclose timer and reclose lockout CP44937 Allan st tripped reclosed and locked out on BC phase overcurrent ABNORMAL: AB44473 (West Gosford Panel 1) open defective, AB44606 closed (Lisarow Panel 1) Lightning near CP44937 See 1359062,4,6 exclude 1358582,4,92 | January | 2016 | 2016Q3 | 2016 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Not Veg | 2016-01-21 | N | 73.5294 | N | 18 | N | N | 1.1101 | 39.4971 | 42932.7672
[7 empty] | 12057 | 18552 | 1358205 | 2016-01-21 07:29 | 2016-01-21 21:10 | 821 | 11kV | 1642 | 2 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Rain Heavy | N | LID 165556 Customer LV Board fault. Aph 10A sub DOLF & LV Cph 200A LVF blown. Excluded OMS 1358205 | January | 2016 | 2016Q3 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | Unknown | Not Veg | 2016-01-21 | N | 821 | N | 18 | N | N | 1.1101 | 39.4971 | 1199.9252
[7 empty] | 12164 | 19515 | 1358647 | 2016-01-21 18:34 | 2016-01-21 21:10 | 156 | 11kV | 18896 | 1536 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | N | Zn9252 Jannali Panel 22 tripped and reclosed Relays: overcurrent AC phase Signals: 11kv trip Cause: weather relateed Mains to patrol. Suspect lightning strike at LB35800 bond burnt off at AB35689 | January | 2016 | 2016Q3 | 2016 | ZN9252:PA22 | ZN9252:PA22 | ZN09252/000022 | SUTHERLAND | OH | Not Veg | 2016-01-21 | N | 12.3021 | N | 18 | N | N | 1.1101 | 39.4971 | 13808.6395
[7 empty] | 10420 | 801 | 1358669 | 2016-01-21 19:52 | 2016-01-21 21:13 | 81 | 11kV | 91929 | 1224 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At S129 Hunters Hill Panel 8 Tripped on earth fault with fault check Cause: Cable fault from S7579 to S4078 See OMS 1359911 1359914 1358669 | January | 2016 | 2016Q3 | 2016 | ZN129:PA8 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | UG | Not Veg | 2016-01-21 | N | 75.1054 | N | 18 | N | N | 1.1101 | 39.4971 | 67179.0018
[7 empty] | 11612 | 13878 | 1358495 | 2016-01-21 14:51 | 2016-01-21 21:18 | 387 | 11kV | 2322 | 6 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 165554 broken tie wire found by ausgrid staff at pole HD-70006. interrupt to repair | January | 2016 | 2016Q3 | 2016 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2016-01-21 | N | 387 | N | 18 | N | N | 1.1101 | 39.4971 | 1696.8491
[7 empty] | 11253 | 10429 | 1358673 | 2016-01-21 19:59 | 2016-01-21 21:35 | 96 | 11kV | 1536 | 16 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Lightning | N | Ex Zn14143 Somersby section of Panel 17 "Somersby Falls" PT14340 Reeves Dawson footpath 16Amp HDO Cause: Lightning See 1358760 exclude 1358673,6,89 | January | 2016 | 2016Q3 | 2016 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2016-01-21 | N | 96 | N | 18 | N | N | 1.1101 | 39.4971 | 1122.4635
[7 empty] | 11717 | 15086 | 1358566 | 2016-01-21 17:54 | 2016-01-21 22:00 | 246 | 11kV | 232237 | 1026 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Rain Heavy | N | Zn9245 Engadine 11kv pa45 fdr tripped Relays: IOC C Phase, Lockout, EFI Signals: 11kv trip EFI's S9089 S9069 S48595 Weather related Panel 45 will not close. Solenoid fuses blowing See 1360357,9,60 exclude 1358558 | January | 2016 | 2016Q3 | 2016 | ZN9245:PA45 | ZN9245:PA10 | ZN09245/000010 | SUTHERLAND | Unknown | Not Veg | 2016-01-21 | N | 226.3519 | N | 18 | N | N | 1.1101 | 39.4971 | 169711.9498
[7 empty] | 10721 | 4608 | 1358711 | 2016-01-21 20:46 | 2016-01-21 22:25 | 99 | 11kV | 396 | 4 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Lightning | N | Ex Zn14891 Wyong section of Pa12 PT18829 Ravensdale Brush 2.7 11kv roadside & centre phase 10AMp dropout fuses operated Tree branch across Transformer See 1359084 exclude 1358711 | January | 2016 | 2016Q3 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2016-01-21 | N | 99 | N | 18 | N | N | 1.1101 | 39.4971 | 289.3851
[7 empty] | 10719 | 4598 | 1358677 | 2016-01-21 20:01 | 2016-01-21 22:34 | 153 | 11kV | 11896 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 165557 1 fault operation Sensitive Earth Fault Large Tree Limb coming into contact with low 11kV conductor between poles SF-10137 & SF-10138. Excluded OMS No. 1358677 | January | 2016 | 2016Q3 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2016-01-21 | N | 121.3878 | N | 18 | N | N | 1.1101 | 39.4971 | 8693.2459
[7 empty] | 11613 | 13903 | 1358720 | 2016-01-21 21:12 | 2016-01-21 23:18 | 126 | 11kV | 107873 | 1277 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At Zn195 Pymble Panel 11 Tripped on A and C phase IOC with timing, Lockout and fault check Cause: Cable fault between S4144 Pymble Park to S2772 Telegraph Pacific tee to S5629. See OMS 1359921 1359925 1359923 1359924 See OMS 1358720 | January | 2016 | 2016Q3 | 2016 | ZN195:PA11 | ZN195:PA11 | ZN00195/000011 | KU-RING-GAI | UG | Not Veg | 2016-01-21 | N | 84.4738 | N | 18 | N | N | 1.1101 | 39.4971 | 78830.4067
[7 empty] | 12100 | 18916 | 1358773 | 2016-01-22 02:01 | 2016-01-22 03:30 | 89 | 11kV | 7420 | 86 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | @Zn 2466 Flemington - 11kv Panel No.27 "Sub 2566 Carter King" feeder tripped Relays: Earth fault, EFI, fault check Signals: 11kv trip, No.3 Group Earth, Zone Earth Field EFI's: Sub 2566, S35475 | January | 2016 | 2016Q3 | 2016 | ZN2466:PA27 | ZN2466:PA1 | ZN02466/000001 | CUMBERLAND | UG | Not Veg | 2016-01-22 | N | 86.2791 | N | 30 | Y | Y | 1.1101 | 39.4971 | 5422.3171
[7 empty] | 11063 | 8236 | 1358768 | 2016-01-22 01:48 | 2016-01-22 03:35 | 107 | 11kV | 81962 | 766 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 165562 Blown tapping ABS 20855 Excluded OMS 1358768, 1358769, 1358770, 1358771, 1358772 | January | 2016 | 2016Q3 | 2016 | 239:82129 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2016-01-22 | N | 107 | N | 30 | Y | Y | 1.1101 | 39.4971 | 59895.4121
[7 empty] | 11833 | 16402 | 1358980 | 2016-01-22 12:06 | 2016-01-22 13:00 | 54 | 11kV | 1944 | 36 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | Ex Zn14143 Somersby section of Pa12 "Phillips Gindurra" PT47217 Woy Woy Dandaloo 11kv 63Amp B phase HDO Fuse Failure See 1360442 exclude 1358980,96 | January | 2016 | 2016Q3 | 2016 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Not Veg | 2016-01-22 | N | 54 | N | 30 | Y | Y | 1.1101 | 39.4971 | 1420.6179
[7 empty] | 11837 | 16431 | 1358690 | 2016-01-21 20:14 | 2016-01-22 13:36 | 1042 | 11kV | 1042 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | LID 165560 3 phase DOLF : 10 Amp Faulty Transformer Excluded OMS 1358690 | January | 2016 | 2016Q3 | 2016 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2016-01-21 | N | 1042 | N | 18 | N | N | 1.1101 | 39.4971 | 761.4629
[7 empty] | 11538 | 12989 | 1358995 | 2016-01-22 12:34 | 2016-01-22 14:45 | 131 | 11kV | 7336 | 56 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Hot >35C | N | Ex Zn12640 Umina section of Panel 8 PT12588 Albert Mulhall has blown centre phase HDO Tree branch on PT See 1360444 exclude 1358995 | January | 2016 | 2016Q3 | 2016 | ZN12640:PA8 | ZN12640:PA8 | ZN12640/000008 | CENTRAL COAST | OH | Veg | 2016-01-22 | N | 131 | N | 30 | Y | Y | 1.1101 | 39.4971 | 5360.9324
[7 empty] | 11426 | 12093 | 1358666 | 2016-01-21 19:12 | 2016-01-22 15:45 | 1233 | 11kV | 4251 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | Ex Zn12650 West Gosford section of Panel 1 "Dog Trap Rd" CP45010 Palm Grove tripped reclosed and locked out on timed overcurrent 11kv LK43168 to PT12434 and PT12433 radial See 1360427,8 exclude 1358666 | January | 2016 | 2016Q3 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2016-01-21 | N | 250.0588 | N | 18 | N | N | 1.1101 | 39.4971 | 3106.5054
[7 empty] | 10463 | 1485 | 1359144 | 2016-01-22 16:57 | 2016-01-22 18:25 | 88.4333 | 11kV | 88.4333 | 1 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | CC1: 06-"Urgent - O.H Mains - No others" | January | 2016 | 2016Q3 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2016-01-22 | N | 88.4333 | N | 30 | Y | Y | 1.1101 | 39.4971 | 64.6245
[7 empty] | 10938 | 7001 | 1359161 | 2016-01-22 17:08 | 2016-01-22 18:57 | 109 | 11kV | 10791 | 99 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At Zn35370 Galston Panel 8 Recloser CP559 Cobah Rd tripped, reclosed, tripped and lockout Cause: Storm - Cause not ascertained | January | 2016 | 2016Q3 | 2016 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2016-01-22 | N | 109 | N | 30 | Y | Y | 1.1101 | 39.4971 | 7885.7445
[7 empty] | 11565 | 13313 | 1359157 | 2016-01-22 17:07 | 2016-01-22 19:15 | 128 | 11kV | 256 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 165601 Single phase DOLF : 10 Amp Excluded OMS 1359157 | January | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2016-01-22 | N | 128 | N | 30 | Y | Y | 1.1101 | 39.4971 | 187.0772
[7 empty] | 10615 | 3459 | 1359188 | 2016-01-22 18:07 | 2016-01-22 19:35 | 88 | 11kV | 792 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165604 B & C Phase DOLF : 20 Amp | January | 2016 | 2016Q3 | 2016 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2016-01-22 | N | 88 | N | 30 | Y | Y | 1.1101 | 39.4971 | 578.7702
[7 empty] | 10426 | 842 | 1359155 | 2016-01-22 17:04 | 2016-01-22 20:45 | 221.25 | 11kV | 4867.5 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165612 C phase DOLF : 16 Amp replaced toff fuse | January | 2016 | 2016Q3 | 2016 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2016-01-22 | N | 221.25 | N | 30 | Y | Y | 1.1101 | 39.4971 | 3557.0254
[7 empty] | 10948 | 7088 | 1359176 | 2016-01-22 17:33 | 2016-01-22 20:50 | 197 | 11kV | 394 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 165613 Single phase DOLF : 10 Amp Excluded OMS 1359176 | January | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2016-01-22 | N | 197 | N | 30 | Y | Y | 1.1101 | 39.4971 | 287.9236
[7 empty] | 11064 | 8239 | 1360673 | 2016-01-22 16:00 | 2016-01-22 21:20 | 320 | 11kV | 1280 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165616 3 phase DOLF : 16 Amp | January | 2016 | 2016Q3 | 2016 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2016-01-22 | N | 320 | N | 30 | Y | Y | 1.1101 | 39.4971 | 935.3862
[7 empty] | 11103 | 8743 | 1359199 | 2016-01-22 18:22 | 2016-01-22 21:20 | 178 | 11kV | 712 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 165615 Trip & Reclose single phase DOLF : 16 Amp Excluded OMS 1359199 | January | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2016-01-22 | N | 178 | N | 30 | Y | Y | 1.1101 | 39.4971 | 520.3086
[7 empty] | 11866 | 16659 | 1359226 | 2016-01-22 19:12 | 2016-01-22 21:36 | 144 | 11kV | 11330 | 99 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | At Zn35370 Galston Panel 8 Recloser 559 Cobah Rd Tripped, Reclosed Tripped and locked out Cause not ascertained - Storm See OMS 1363147 1363148 1363149 1359226 | January | 2016 | 2016Q3 | 2016 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2016-01-22 | N | 114.4444 | N | 30 | Y | Y | 1.1101 | 39.4971 | 8279.6298
[7 empty] | 12111 | 19024 | 1359150 | 2016-01-22 16:58 | 2016-01-22 21:40 | 282 | 11kV | 564 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 165610 A phase Repair burnt off Aph tapping at pole 8N-30413. Excluded OMS No. 1359150 | January | 2016 | 2016Q3 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2016-01-22 | N | 282 | N | 30 | Y | Y | 1.1101 | 39.4971 | 412.1546
[7 empty] | 11844 | 16503 | 1359266 | 2016-01-22 20:43 | 2016-01-22 23:05 | 142 | 11kV | 284 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 165624 C phase DOLF : 10 Amp Excluded OMS 1359266 | January | 2016 | 2016Q3 | 2016 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Veg | 2016-01-22 | N | 142 | N | 30 | Y | Y | 1.1101 | 39.4971 | 207.5388
[7 empty] | 10483 | 1764 | 1360910 | 2016-01-22 16:14 | 2016-01-22 23:22 | 428 | 11kV | 39542 | 96 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165626 2 fault operations Instantenious Overcurrent No Fauly Found | January | 2016 | 2016Q3 | 2016 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2016-01-22 | N | 411.8958 | N | 30 | Y | Y | 1.1101 | 39.4971 | 28896.1273
[7 empty] | 11728 | 15176 | 1359252 | 2016-01-22 20:03 | 2016-01-23 00:25 | 262 | 11kV | 1048 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 165631 A & B phase DOLF : 20 Amp DOp found HV earth at sub 50278 broken. Bridged to LV earth at this sub. Please repair. Excluded 1359252 & 1359259 | January | 2016 | 2016Q3 | 2016 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2016-01-22 | N | 262 | N | 30 | Y | Y | 1.1101 | 39.4971 | 765.8475
[7 empty] | 12126 | 19185 | 1359112 | 2016-01-22 16:08 | 2016-01-23 01:03 | 535 | 11kV | 6863 | 40 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 165603 2 fault operations B & C phase Overcurrent OHM off insulators at pole 9N-20173. Excluded OMS No. 1359112 | January | 2016 | 2016Q3 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2016-01-22 | N | 171.575 | N | 30 | Y | Y | 1.1101 | 39.4971 | 5015.278
[7 empty] | 12083 | 18759 | 1359219 | 2016-01-22 18:59 | 2016-01-23 01:45 | 406 | 11kV | 51646 | 1021 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 165625 Trip & Reclose 1 fault operation 3 phase Overcurrent C ph tapping at pole IR-71213 blown after T/R. Repaired under AP. Excluded OMS 1359219. etc. | January | 2016 | 2016Q3 | 2016 | 532:83301 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Not Veg | 2016-01-22 | N | 50.5837 | N | 30 | Y | Y | 1.1101 | 39.4971 | 37741.3735
[7 empty] | 10956 | 7140 | 1359306 | 2016-01-23 01:35 | 2016-01-23 03:20 | 105 | 11kV | 308888 | 3275 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn72 Five Dock Zn Panel 10 "Parramatta Page" tripped on A phase OC B phase EF EFI EFI's: S7651 S3714 S2255 S3388 S3853 S49715 ABNORMAL: Pa26 OOS from Five dock to S46567:B S4256:A S1913 UG Fault. Section of 11kv feeder from S49715:B to S1906:A to S2201:A See 1360535,8,9 exclude 1359306,7 | January | 2016 | 2016Q3 | 2016 | ZN72:PA10 | ZN35555:PA9 | ZN35555/000009 | INNER WEST | UG | Not Veg | 2016-01-23 | N | 94.3169 | N | 17 | N | N | 1.1101 | 39.4971 | 225726.2397
[7 empty] | 12150 | 19382 | 1359339 | 2016-01-23 06:43 | 2016-01-23 11:10 | 266.5333 | 11kV | 1066.1333 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165635 C Phase DOLF : 20 Amp | January | 2016 | 2016Q3 | 2016 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2016-01-23 | N | 266.5333 | N | 17 | N | N | 1.1101 | 39.4971 | 779.0988
[7 empty] | 10510 | 2080 | 1359275 | 2016-01-22 21:18 | 2016-01-23 12:55 | 937 | 11kV | 6559 | 7 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 165649 3 Phase DOLF : 16 Amp Arrestors already cut away. Please replace arrestors. Excluded oms 1359275. | January | 2016 | 2016Q3 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2016-01-22 | N | 937 | N | 30 | Y | Y | 1.1101 | 39.4971 | 4793.1237
[7 empty] | 11263 | 10526 | 1359395 | 2016-01-23 12:21 | 2016-01-23 13:24 | 63 | 11kV | 252 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa1 IR63115 George Blood Tree 1.0 tripped on overcurrent, lockout Cause not ascertained. No Interruption report produced. Based on DNMS and IONS | January | 2016 | 2016Q3 | 2016 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2016-01-23 | N | 63 | N | 17 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 11330 | 11328 | 1361240 | 2016-01-23 06:00 | 2016-01-23 13:30 | 450 | 11kV | 6300 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 165645 3 Phase DOLF : 10 Amp | January | 2016 | 2016Q3 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2016-01-23 | N | 450 | N | 17 | N | N | 1.1101 | 39.4971 | 4603.8542
[7 empty] | 11712 | 15002 | 1361171 | 2016-01-23 08:03 | 2016-01-23 14:03 | 360 | 11kV | 93741 | 271 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165639 1 fault operation Sensitive Earth Fault | January | 2016 | 2016Q3 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-01-23 | N | 345.9077 | N | 17 | N | N | 1.1101 | 39.4971 | 68503.1579
[7 empty] | 11324 | 11172 | 1359102 | 2016-01-22 15:42 | 2016-01-23 16:45 | 1503 | 11kV | 15437 | 57 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 165609 2 fault operation OHM down beyond 11kV links 75290 Excluded OMS 1359102 & 1359265 | January | 2016 | 2016Q3 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2016-01-22 | N | 270.8246 | N | 30 | Y | Y | 1.1101 | 39.4971 | 11280.9043
[7 empty] | 10843 | 5973 | 1359439 | 2016-01-23 14:54 | 2016-01-23 17:31 | 157 | 11kV | 471 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 165656 A phase DOLF : 10 Amp Excluded OMS 1359439 | January | 2016 | 2016Q3 | 2016 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2016-01-23 | N | 157 | N | 17 | N | N | 1.1101 | 39.4971 | 344.1929
[7 empty] | 10768 | 5132 | 1359438 | 2016-01-23 14:53 | 2016-01-23 17:44 | 171 | 11kV | 171 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 165657 A phase DOLF : 10 Amp address wrong in oms next door neighbour affected at sub 50978. dq Excluded oms 1359438 | January | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-01-23 | N | 171 | N | 17 | N | N | 1.1101 | 39.4971 | 124.9618
[7 empty] | 11697 | 14794 | 1359484 | 2016-01-23 17:18 | 2016-01-23 18:45 | 87 | 11kV | 117219 | 1421 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1673 Turramurra 11kV panel 1 feeder tripped on c phase IOC and earth fault Signals: Tx 2 Earth Fault and EFI Cause: Cable fault between S49983 to S35425 See OMS 1363368 1363372 1363373 1359484 | January | 2016 | 2016Q3 | 2016 | ZN1673:PA1 | ZN1673:PA1 | ZN01673/000001 | KU-RING-GAI | UG | Not Veg | 2016-01-23 | N | 82.4905 | N | 17 | N | N | 1.1101 | 39.4971 | 85660.1878
[7 empty] | 10968 | 7277 | 1359404 | 2016-01-23 13:11 | 2016-01-23 18:50 | 339 | 11kV | 339 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165662 Single phase DOLF : 10 Amp Burnt DOLF. Volts as left = 241. excluded OMS 1359404. | January | 2016 | 2016Q3 | 2016 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2016-01-23 | N | 339 | N | 17 | N | N | 1.1101 | 39.4971 | 247.7312
[7 empty] | 10555 | 2649 | 1359445 | 2016-01-23 15:08 | 2016-01-23 19:26 | 257.8167 | 11kV | 515.6333 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Blown DOLF replaced KRAJEVSKI, HENRY HV FUSE HAS DROPPED OUT FROM SUB 52736. 1 PHASE DOWN | January | 2016 | 2016Q3 | 2016 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2016-01-23 | N | 257.8167 | N | 17 | N | N | 1.1101 | 39.4971 | 376.8096
[7 empty] | 11356 | 11536 | 1359189 | 2016-01-22 18:06 | 2016-01-23 20:36 | 1590 | 11kV | 182736 | 249 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 165673 A & B phase Overcurrent; Earth Fault; Sensitive Earth Fault mutliple device operations on restoration attempts Broken Insulator pole LI-81310 & LI-81313 Pole fire DN -20328 beyond thomas lane RAGCB Excluded oms 1359189 1359331 | January | 2016 | 2016Q3 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2016-01-22 | N | 733.8795 | N | 30 | Y | Y | 1.1101 | 39.4971 | 133538.079
[7 empty] | 11799 | 15964 | 1359107 | 2016-01-22 15:58 | 2016-01-23 21:00 | 1742 | 11kV | 11080 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 165618 2 fault operations Overcurrent Excluded OMS 1359107 & 1359304 | January | 2016 | 2016Q3 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2016-01-22 | N | 738.6667 | N | 30 | Y | Y | 1.1101 | 39.4971 | 8096.9372
[7 empty] | 10415 | 657 | 1359512 | 2016-01-23 19:08 | 2016-01-23 21:00 | 112 | 11kV | 224 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165671 3 phase DOLF : 10 Amp Excluded OMS 1359512 | January | 2016 | 2016Q3 | 2016 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2016-01-23 | N | 112 | N | 17 | N | N | 1.1101 | 39.4971 | 163.6926
[7 empty] | 10603 | 3261 | 1359515 | 2016-01-23 20:00 | 2016-01-23 21:45 | 105 | 11kV | 105 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165672 DOLF : 10 Amp Excluded OMS 1359515 | January | 2016 | 2016Q3 | 2016 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2016-01-23 | N | 105 | N | 17 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 10402 | 499 | 1359209 | 2016-01-22 18:43 | 2016-01-23 22:36 | 1673 | 11kV | 75026 | 112 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 165611 1 fault operation Sensitive Earth Fault excluded OMS 1359209 & 1359303 | January | 2016 | 2016Q3 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-01-22 | N | 669.875 | N | 30 | Y | Y | 1.1101 | 39.4971 | 54826.7879
[7 empty] | 11523 | 12878 | 1359372 | 2016-01-23 10:31 | 2016-01-24 01:10 | 879 | 11kV | 1758 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 165678 A & C phase DOLF : 10 Amp Transformer replaced under AP Volts 243V Excluded OMS 1359372 | January | 2016 | 2016Q3 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2016-01-23 | N | 879 | N | 17 | N | N | 1.1101 | 39.4971 | 1284.6945
[7 empty] | 11166 | 9568 | 1361294 | 2016-01-23 15:45 | 2016-01-24 01:20 | 575 | 11kV | 2248 | 185 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165677 C Phase DOLF : 40 Amp Arrestor replaced under AP. Note Sw 42002 opened auto 0024 hrs when closing DOLF at sub 53460. Sw 42002 closed at 0030hrs. | January | 2016 | 2016Q3 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2016-01-23 | N | 12.1514 | N | 17 | N | N | 1.1101 | 39.4971 | 1642.7721
[7 empty] | 10465 | 1527 | 1359589 | 2016-01-24 12:21 | 2016-01-24 13:30 | 69 | 11kV | 82779 | 1674 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 165687 2 fault operation 3 phase Earth fault blown surge arrestor on UGOH JU45242 replaced by linecrew. DQ Excluded oms 1359593 | January | 2016 | 2016Q3 | 2016 | 205:12205 | 205:12205 | ZN00205/012205 | LAKE MACQUARIE | OH | Not Veg | 2016-01-24 | N | 49.4498 | N | 9 | N | N | 1.1101 | 39.4971 | 60492.4516
[7 empty] | 11691 | 14727 | 1363413 | 2016-01-22 16:14 | 2016-01-24 14:15 | 2761 | 11kV | 2761 | 1 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 165680 sub isolated open LVF - Trees on OHM Excluded OMS 1359526 | January | 2016 | 2016Q3 | 2016 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Veg | 2016-01-22 | N | 2761 | N | 30 | Y | Y | 1.1101 | 39.4971 | 2017.6574
[7 empty] | 11604 | 13784 | 1359406 | 2016-01-23 13:14 | 2016-01-24 16:02 | 1608 | 11kV | 19168 | 21 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 165679 pole fire 3H-50051 Excluded oms 1359539 | January | 2016 | 2016Q3 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2016-01-23 | N | 912.7619 | N | 17 | N | N | 1.1101 | 39.4971 | 14007.409
[7 empty] | 10598 | 3207 | 1361428 | 2016-01-24 15:15 | 2016-01-24 16:55 | 100 | 11kV | 1200 | 12 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 165685 interrupt to reapir wire of pin at pole AN-10027 | January | 2016 | 2016Q3 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2016-01-24 | N | 100 | N | 9 | N | N | 1.1101 | 39.4971 | 876.9246
[7 empty] | 11255 | 10450 | 1359267 | 2016-01-22 16:14 | 2016-01-24 17:41 | 2967 | 11kV | 349015 | 257 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165710 Sensitive Earth Fault Excluded OMS 1359526 & 1359543 | January | 2016 | 2016Q3 | 2016 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2016-01-22 | N | 1358.035 | N | 30 | Y | Y | 1.1101 | 39.4971 | 255049.8678
[7 empty] | 10452 | 1300 | 1359105 | 2016-01-22 15:57 | 2016-01-24 17:41 | 2984 | 11kV | 153595 | 68 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165709 Sensitive Earth Fault Excluded OMS 1359526 & 1359543 | January | 2016 | 2016Q3 | 2016 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2016-01-22 | N | 2258.75 | N | 30 | Y | Y | 1.1101 | 39.4971 | 112242.6957
[7 empty] | 11692 | 14747 | 1359217 | 2016-01-22 19:06 | 2016-01-24 18:00 | 2814 | 11kV | 44544 | 215 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 165688 3 fault operations Earth Fault; Sensitive Earth Fault Faulty Transformer 7661 Cox sub Excluded oms 1359217 1359287 1359331 | January | 2016 | 2016Q3 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2016-01-22 | N | 207.1814 | N | 30 | Y | Y | 1.1101 | 39.4971 | 32551.4414
[7 empty] | 10450 | 1266 | 1359638 | 2016-01-24 15:57 | 2016-01-24 18:00 | 123.0833 | 11kV | 369.25 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165690 A Phase DOLF : 10 Amp | January | 2016 | 2016Q3 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2016-01-24 | N | 123.0833 | N | 9 | N | N | 1.1101 | 39.4971 | 269.837
[7 empty] | 11936 | 17265 | 1359670 | 2016-01-24 19:00 | 2016-01-24 19:40 | 40 | 11kV | 80 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165691 A Phase DOLF : 10 Amp Bird Excluded 1359670 | January | 2016 | 2016Q3 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2016-01-24 | N | 40 | N | 9 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 10706 | 4462 | 1359117 | 2016-01-22 16:13 | 2016-01-24 19:45 | 3092 | 11kV | 120687 | 77 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 165706 2 fsault operation A phase Instantaneous Overcurrent problems at multiple sites after severe storms Excluded oms report no 1359117. | January | 2016 | 2016Q3 | 2016 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Veg | 2016-01-22 | N | 1567.3636 | N | 30 | Y | Y | 1.1101 | 39.4971 | 88194.4999
[7 empty] | 10531 | 2382 | 1359609 | 2016-01-24 13:58 | 2016-01-24 21:00 | 422 | 11kV | 844 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 165696 Replace defective Transformer Excluded OMS 1359609 | January | 2016 | 2016Q3 | 2016 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2016-01-24 | N | 422 | N | 9 | N | N | 1.1101 | 39.4971 | 616.7703
[7 empty] | 11943 | 17362 | 1359499 | 2016-01-23 18:20 | 2016-01-24 22:00 | 1660 | 11kV | 6640 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165698 A & B phase DOLF : 10 Amp Excluded OMS 1359499 | January | 2016 | 2016Q3 | 2016 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2016-01-23 | N | 1660 | N | 17 | N | N | 1.1101 | 39.4971 | 4852.3162
[7 empty] | 12076 | 18733 | 1359660 | 2016-01-24 17:35 | 2016-01-24 23:52 | 377 | 11kV | 1508 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 165699 A phase DOLF : 10 Amp Faulty arrestors replaced under AP Excluded OMS 1359660 | January | 2016 | 2016Q3 | 2016 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2016-01-24 | N | 377 | N | 9 | N | N | 1.1101 | 39.4971 | 1102.0019
[7 empty] | 10736 | 4840 | 1359612 | 2016-01-24 14:04 | 2016-01-25 00:56 | 652 | 11kV | 256549 | 1746 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn129 Hunters Hills Panel 19 tripped, reclosed, tripped and locked out on Relays: C phase IOC, E/F, L/O EFI Signals: 11kV Trip Cause: Tree brought down 11kV OH o/s 270 Pittwater Rd North Ryde LV OH down aswell due to LV Parallel during feeder fault Defective feeder from LB1766 to LB1277 to LB1409 to PT47437 See OMS 1363398 1363399 1363403 1363406 1359612 1359616 1359618 1359649 1359650 1359652 1359663 | January | 2016 | 2016Q3 | 2016 | ZN129:PA19 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Veg | 2016-01-24 | N | 146.9353 | N | 9 | N | N | 1.1101 | 39.4971 | 187478.4423
[7 empty] | 10550 | 2608 | 1359697 | 2016-01-25 04:54 | 2016-01-25 07:20 | 146 | 11kV | 11775.3333 | 81 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT61803 Banksia Anzac 11kV Roadside HDO fuse operated. Cause: Fuse fatigue See OMS 1359697 1359700 | January | 2016 | 2016Q3 | 2016 | ZN9245:PA43 | ZN9245:PA21 | ZN09245/000021 | SUTHERLAND | OH | Not Veg | 2016-01-25 | N | 145.3745 | N | 4 | N | N | 1.1101 | 39.4971 | 8605.0663
[7 empty] | 11227 | 10148 | 1359565 | 2016-01-24 09:19 | 2016-01-25 08:30 | 1391 | 11kV | 9737 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165701 C phase DOLF : 16 Amp Excluded OMS 1359565 | January | 2016 | 2016Q3 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2016-01-24 | N | 1391 | N | 9 | N | N | 1.1101 | 39.4971 | 7115.5124
[7 empty] | 11184 | 9725 | 1359558 | 2016-01-22 18:48 | 2016-01-25 13:50 | 4022 | 11kV | 12066 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 165707 Replaced faulty sub Excluded OMS 1359558 | January | 2016 | 2016Q3 | 2016 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2016-01-22 | N | 4022 | N | 30 | Y | Y | 1.1101 | 39.4971 | 8817.4769
[7 empty] | 10553 | 2643 | 1359600 | 2016-01-24 13:04 | 2016-01-25 14:35 | 1531 | 11kV | 6124 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 165708 Replace faulty Transformer Excluded OMS 1359600 | January | 2016 | 2016Q3 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2016-01-24 | N | 1531 | N | 9 | N | N | 1.1101 | 39.4971 | 4475.2386
[7 empty] | 11669 | 14476 | 1359819 | 2016-01-25 11:11 | 2016-01-25 14:40 | 209.2333 | 11kV | 11717.0667 | 56 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Previous Storm | N |  | January | 2016 | 2016Q3 | 2016 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2016-01-25 | N | 209.2333 | N | 4 | N | N | 1.1101 | 39.4971 | 8562.4867
[7 empty] | 10543 | 2509 | 1360002 | 2016-01-25 16:56 | 2016-01-25 18:22 | 86 | 11kV | 6450 | 75 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | ZN15005 Belrose Ex Panel 10 "S.16807" feeder tripped 11kV bond burnt off at at AB.20467 Footpath side. Me:1360408 Withdrawn:1360002 | January | 2016 | 2016Q3 | 2016 | ZN15005:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Not Veg | 2016-01-25 | N | 86 | N | 4 | N | N | 1.1101 | 39.4971 | 4713.4698
[7 empty] | 10397 | 403 | 1359881 | 2016-01-25 12:52 | 2016-01-25 18:50 | 358 | 11kV | 1074 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165711 B Phase DOLF : 10 Amp Excluded OMS 1359881 | January | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-01-25 | N | 358 | N | 4 | N | N | 1.1101 | 39.4971 | 784.8475
[7 empty] | 11780 | 15717 | 1362921 | 2016-01-23 12:00 | 2016-01-26 13:50 | 4430 | 11kV | 1919 | 86 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 165716 A Phase DOLF : 10 Amp Blew line fuse 14793 when energising replacement Tx 72219. Faulty arrestor still in | January | 2016 | 2016Q3 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-01-23 | N | 22.314 | N | 17 | N | N | 1.1101 | 39.4971 | 1402.3486
[7 empty] | 12073 | 18672 | 1360170 | 2016-01-26 18:10 | 2016-01-26 22:00 | 230 | 11kV | 6307 | 82 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 1657182 fault operations A phase Sensitive Earth Fault; Earth Fault Sw 43954 tripped on SEF, found damaged links 3101 at Ben Ean RAGCB. When restoring Fdr Sw 43954 tripped on EF after closing Sw 28400. Sectioned fdr & restored, no fault found. Excluded OMS OMS 1360170 ## | January | 2016 | 2016Q3 | 2016 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2016-01-26 | N | 76.9146 | N | 1 | N | N | 1.1101 | 39.4971 | 4608.9696
[7 empty] | 10392 | 357 | 1360209 | 2016-01-27 02:13 | 2016-01-27 03:35 | 82 | 11kV | 86012 | 2121 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12580 Erina Pa4R fdr tripped and locked out on Relays: Instantaneous overucrretn, EFI EFI's: S18397 Sgnals: 11kv trip UG fault from S18397 to LB40351 via S180000 and PT13437 See 1360491,2,3 exclude 1360209 | January | 2016 | 2016Q3 | 2016 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | UG | Not Veg | 2016-01-27 | N | 40.5526 | N | 4 | N | N | 1.1101 | 39.4971 | 62855.0327
[7 empty] | 11769 | 15595 | 1363013 | 2016-01-27 20:02 | 2016-01-27 22:05 | 123 | 11kV | 17097 | 139 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 165733 1 Fault operation Sensitive Earth Fault Fdr Abnormal ABS 40293 closed, Sw 43029 Open Excluded OMS 1360642 & 1360344 | January | 2016 | 2016Q3 | 2016 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2016-01-27 | N | 123 | N | 4 | N | N | 1.1101 | 39.4971 | 12493.9833
[7 empty] | 10930 | 6914 | 1360642 | 2016-01-27 20:02 | 2016-01-27 22:31 | 149 | 11kV | 155494 | 1471 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 165732 1 Fault operation Sensitive Earth Fault Fdr Abnormal ABS 40293 closed, Sw 43029 Open Excluded OMS 1360642 & 1360344 | January | 2016 | 2016Q3 | 2016 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2016-01-27 | N | 105.7063 | N | 4 | N | N | 1.1101 | 39.4971 | 113630.4289
[7 empty] | 10896 | 6557 | 1360184 | 2016-01-27 20:03 | 2016-01-27 23:50 | 227 | 11kV | 227 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Dust Storm | N | LID 165720 A phase DOLF : 10 Amp Excluded OMS 1360184 | January | 2016 | 2016Q3 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-01-27 | N | 227 | N | 4 | N | N | 1.1101 | 39.4971 | 165.8849
[7 empty] | 10460 | 1429 | 1360728 | 2016-01-28 09:10 | 2016-01-28 11:04 | 114 | 11kV | 73140 | 685 | HV | Arcing | Equipment Failure | O/H Conductor Insulated | Unplanned | No Weather Impact | N | Zn15001 Brookvale Pa8 "Harbord Rd" tripped on Relays: IOC BC phase, Relay Code (50TBC) Signals: 11kv trip Floshover/arcing OH Mains shorted together on tee off near USL22550 to 2x UGOH's See 1363596,7 exclude 1360728 | January | 2016 | 2016Q3 | 2016 | ZN15001:PA8 | ZN15001:PA8 | ZN15001/000008 | NORTHERN BEACHES | OH | Not Veg | 2016-01-28 | N | 106.7737 | N | 4 | N | N | 1.1101 | 39.4971 | 53448.5547
[7 empty] | 10542 | 2506 | 1360779 | 2016-01-28 11:11 | 2016-01-28 13:00 | 109.0167 | 11kV | 2398.3667 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 165737 B Phase DOLF : 16 Amp T off fuse | January | 2016 | 2016Q3 | 2016 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2016-01-28 | N | 109.0167 | N | 4 | N | N | 1.1101 | 39.4971 | 1752.6556
[7 empty] | 10645 | 3823 | 1360784 | 2016-01-28 11:25 | 2016-01-28 13:42 | 137 | 11kV | 137 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 165740 Sub isolated to repair burnt off dropper lead | January | 2016 | 2016Q3 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2016-01-28 | N | 137 | N | 4 | N | N | 1.1101 | 39.4971 | 100.1156
[7 empty] | 12139 | 19266 | 1360813 | 2016-01-28 11:52 | 2016-01-28 14:30 | 158 | 11kV | 158 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 165741 3 phase Found open. No cause. Possibly left open from previous planned job. Excluded OMS 1360813. | January | 2016 | 2016Q3 | 2016 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2016-01-28 | N | 158 | N | 4 | N | N | 1.1101 | 39.4971 | 115.4617
[7 empty] | 12009 | 18133 | 1361086 | 2016-01-29 01:49 | 2016-01-29 03:10 | 81 | 11kV | 60588 | 748 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | Y | Ex Zn12690 Berkeley Vale section of Panel 12 "Craftsman Av" fdr 11kv Link 43333, middle phase bond burnt off Zone side See 1361588 exclude 1361086 | January | 2016 | 2016Q3 | 2016 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2016-01-29 | N | 81 | N | 7 | N | N | 1.1101 | 39.4971 | 44275.9234
[7 empty] | 11403 | 11869 | 1361084 | 2016-01-29 01:55 | 2016-01-29 07:40 | 345 | 11kV | 2070 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | Y | LID 165746 A phase DOLF : 10 Amp Excluded OMS 1361084 | January | 2016 | 2016Q3 | 2016 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2016-01-29 | N | 345 | N | 7 | N | N | 1.1101 | 39.4971 | 1512.6949
[7 empty] | 12031 | 18322 | 1361314 | 2016-01-29 13:09 | 2016-01-29 14:42 | 93 | 11kV | 127224 | 1368 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | S35900 Potts Hill Panel 24 "Potts Hill Aux No.2" fdr tripped Relays - A and B phase overcurrent Signals - 11kv trip Remarks: OH down. 11kv down, resting on streetlight in Joseph St | January | 2016 | 2016Q3 | 2016 | ZN35900:PA24 | ZN35900:PA24 | ZN35900/000024 | CUMBERLAND | OH | Not Veg | 2016-01-29 | N | 93 | N | 7 | N | N | 1.1101 | 39.4971 | 92971.5467
[7 empty] | 11908 | 17009 | 1361342 | 2016-01-29 13:11 | 2016-01-29 15:40 | 149 | 11kV | 161069 | 1288 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Electrical Storm | Y | At Zn965 Pennant Hills Panel 33 tripped, reclosed tripped and locked out inb RelaysL Earth Fault, EFi, Reclose timing and lockout relays Signals: 11kV Trip, Zone Earth, No1 Group Earth PT1693 Schofield Lawerence Hit by lightning. PT isolated and in LV parallel See OMS 1363751 1363755 1363756 1361342 | January | 2016 | 2016Q3 | 2016 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Not Veg | 2016-01-29 | Y | 125.0536 | N | 7 | N | Y | 1.1101 | 39.4971 | 117704.4745
[7 empty] | 12037 | 18403 | 1361336 | 2016-01-29 13:04 | 2016-01-29 15:55 | 171 | 11kV | 247266 | 1446 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At Zn847 Hornsby Panel 39 tripped, reclosed tripped and lockout on Earth Fault, Timing/Lockout, Fault Check and EFI Cause: Storm, Suspect Lightning | January | 2016 | 2016Q3 | 2016 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Not Veg | 2016-01-29 | Y | 171 | N | 7 | N | Y | 1.1101 | 39.4971 | 180694.6997
[7 empty] | 12138 | 19261 | 1361443 | 2016-01-29 13:40 | 2016-01-29 17:12 | 212 | 11kV | 337603 | 1632 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | Y | Zn9245 Engadine - Pnl.34 tripped on: A phase timed O/C, EFI, SEL Lightning caused bond to burn off near LB35051 | January | 2016 | 2016Q3 | 2016 | ZN9245:PA34 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | OH | Not Veg | 2016-01-29 | N | 206.8646 | N | 7 | N | N | 1.1101 | 39.4971 | 246710.3148
[7 empty] | 11173 | 9636 | 1361339 | 2016-01-29 13:11 | 2016-01-29 17:20 | 249 | 11kV | 79864 | 862 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | Y | Zn3154 St Ives 11kV Panel 11 "Ellalong Keats" tripped Relays: C Phase IOC & Timed, EFI Signals: 11kV trip EFI's:Nil Tree on 11kV mains in Miowera st See 1363138,40,41 exclude 1361339,659 | January | 2016 | 2016Q3 | 2016 | ZN3154:PA11 | ZN3154:PA11 | ZN03154/000011 | KU-RING-GAI | OH | Veg | 2016-01-29 | N | 92.6497 | N | 7 | N | N | 1.1101 | 39.4971 | 58362.2556
[7 empty] | 11606 | 13799 | 1361448 | 2016-01-29 13:45 | 2016-01-29 18:01 | 256 | 11kV | 417084 | 1785 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | Y | Zn9245 Engadine Pnl.40 tripped on: A & C phase timed and Instantaneous, E/F, Lockout Field EFIs: S9668, 9007, 9792 9263 Lightning arrestor on footpath side damaged by lightning. See 1363460 1343461 | January | 2016 | 2016Q3 | 2016 | ZN9245:PA40 | ZN9245:PA13 | ZN09245/000013 | SUTHERLAND | OH | Not Veg | 2016-01-29 | N | 233.6605 | N | 7 | N | N | 1.1101 | 39.4971 | 304792.6853
[7 empty] | 11497 | 12691 | 1361388 | 2016-01-29 13:19 | 2016-01-29 18:13 | 294 | 11kV | 260778 | 887 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Recloser / Sectionaliser | Unplanned | Electrical Storm | Y | Recloser 49253 Rex McClean tripped ex Panel 3 "Carnarvon Heron" fdr Remarks: Cause not ascertained. No cause found | January | 2016 | 2016Q3 | 2016 | ZN1850:PA3 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-01-29 | Y | 294 | N | 7 | N | Y | 1.1101 | 39.4971 | 190568.8708
[7 empty] | 11048 | 8024 | 1361300 | 2016-01-29 12:58 | 2016-01-29 19:25 | 387 | 11kV | 233755 | 714 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At Zn35370 Galston Panel 8 tripped, reclosed, tripped and locked out on Relays: A, B and C phase IOC, lockout and EFI Signals 11kV Trip Field EFI's NIL Cause: Tree into 11kV Mains adjacent to PT2112 Hansen Johnson See OMS 1363913 1363914 1363916 13631431 1361300 1361814 | January | 2016 | 2016Q3 | 2016 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2016-01-29 | Y | 327.388 | N | 7 | N | Y | 1.1101 | 39.4971 | 170821.2594
[7 empty] | 10960 | 7163 | 1361344 | 2016-01-29 13:23 | 2016-01-29 19:35 | 372 | 11kV | 470208 | 1264 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | S35800 Bankstown Panel 1 "Gow Gibson" fdr tripped Relays: A, B, C Phase IOC, EFI, Earth Fault Check Signals: 11kv trip Remarks: cause not ascertained. Patrolled by Praneel Singh | January | 2016 | 2016Q3 | 2016 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-01-29 | Y | 372 | N | 7 | N | Y | 1.1101 | 39.4971 | 343614.1376
[7 empty] | 10813 | 5619 | 1361315 | 2016-01-29 13:03 | 2016-01-29 19:36 | 393 | 11kV | 129108 | 370 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At S35370 Galston Pnale 2 tripped, reclosed, tripped and locked out on Relays: B and C phase overcurrent, Timing and lockout with efi Signals: 11kV trip Cause: Tree branch on OH mains o/s 19 Muraban See OMS 1363873 1363874 1361381 1361315 | January | 2016 | 2016Q3 | 2016 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2016-01-29 | Y | 348.9405 | N | 7 | N | Y | 1.1101 | 39.4971 | 94348.3184
[7 empty] | 10730 | 4728 | 1361482 | 2016-01-29 14:10 | 2016-01-29 20:25 | 375 | 11kV | 13875 | 37 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | Y | At PT1994 Altona Ventura 11kV footpath HDO operated Cause: transformer defective and requires replacement See OMS 1361482 1361780 | January | 2016 | 2016Q3 | 2016 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Not Veg | 2016-01-29 | Y | 375 | N | 7 | N | Y | 1.1101 | 39.4971 | 10139.4408
[7 empty] | 12010 | 18149 | 1361647 | 2016-01-29 15:57 | 2016-01-29 20:59 | 302 | 11kV | 289316 | 958 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Section of 11kV panel 40 Recloser CP1437 Shaftsbury Morvan tripped reclosed tripped and locked out At Zn4545 Meadowbank Panel 40 tripped when re energising feeder from S1437. Relays: SEF, fault check and EFI Signals: 11kV trip, No3 Group earth and Zone Earth Cause: Tree on 11kV OH and Bond Failed adjacent to CP1965. See OMS 1363740 1363741 1361647 1361662 1362076 1361673 | January | 2016 | 2016Q3 | 2016 | ZN4545:PA40 | ZN4545:PA40 | ZN04545/000040 | RYDE | OH | Veg | 2016-01-29 | N | 302 | N | 7 | N | N | 1.1101 | 39.4971 | 211423.5994
[7 empty] | 11491 | 12658 | 1361384 | 2016-01-29 13:33 | 2016-01-29 21:15 | 462 | 11kV | 571586 | 1266 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | S1287 Revesby Panel 17 "Hinemoa St" fdr tripped, reclosed, tripped and locked out Relays - A phase Inst & timed O/C, SEL, EFI, F/C, Timer & L/O Signals - 11kv trip, Zone Earth, Tx1 Group Earth Remarks: lightning. 2 x blown HV fuses @ PT1581 Eddie Ave on condemned pole | January | 2016 | 2016Q3 | 2016 | ZN1287:PA17 | ZN1287:PA17 | ZN01287/000017 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-01-29 | Y | 451.4897 | N | 7 | N | Y | 1.1101 | 39.4971 | 417698.1899
[7 empty] | 11239 | 10250 | 1361350 | 2016-01-29 13:23 | 2016-01-29 22:11 | 528 | 11kV | 1050720 | 1990 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | S35800 Bankstown Panel 14 "Hoskins Cottam" fdr tripped Relays - A, B and C Phase IOC, Earth fault, EFI, Earth fault check Signals - 11kv trip Abnormal: see DMA AB 422 closed. Sw/B closed at S5762 and Sub AB315 Sub 5895 in LV// Remarks: cause not ascertained. Mains to patrol | January | 2016 | 2016Q3 | 2016 | ZN35800:PA14 | ZN35800:PA14 | ZN35800/000014 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-01-29 | Y | 528 | N | 7 | N | Y | 1.1101 | 39.4971 | 767835.185
[7 empty] | 11285 | 10731 | 1363221 | 2016-01-29 13:16 | 2016-01-30 00:30 | 674 | 11kV | 250843 | 961 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | S3472 Sefton Panel 28 "Baird Buist" feeder tripped, relcosed. tripped and locked out Relays - A, B and C Phase overcurrent, B Phase IOC, Earth fault, EFI, Reclose Timer, Lockout Signals: 11kv trip, Zone Earth, Tx4 Group Earth Remarks: UG fault. Underground feeder fault from S7382 Johnston Manuka Sw/B to S5963 Bass Hill Shopping Ctr Sw/A to LB2714 tee PT64952 Handle Carey | January | 2016 | 2016Q3 | 2016 | ZN3472:PA28 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-01-29 | Y | 261.0229 | N | 7 | N | Y | 1.1101 | 39.4971 | 183308.6658
[7 empty] | 10718 | 4576 | 1361357 | 2016-01-29 13:19 | 2016-01-30 01:35 | 736 | 11kV | 927360 | 1260 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | At Zn1290 Leightonfield Panel 4 'S5013 Miller Sir Thomas" feeder has tripped/reclosed/tripped on: Signals: 11kv trip, Tx1 Group Earth, Zone Earth Relays: A + C Phase IOC, A+C timed, reclose timing, lockout, efi Field EFI's: S5013, S4284 Remarks: Lightning, Storm, feeder patrolled, suspect lightning | January | 2016 | 2016Q3 | 2016 | ZN1290:PA4 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-01-29 | Y | 736 | Y | 7 | N | Y | 1.1101 | 39.4971 | 677687.3355
[7 empty] | 10876 | 6348 | 1361892 | 2016-01-30 00:57 | 2016-01-30 02:00 | 63 | 11kV | 91098 | 1446 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | At S547 Hornsby Panel 39 tripped, reclosed, tripped and locked out on Earth fault, lockout, timing, fault check and efi Cause: First UGOH on feeder has black marks and needs inspected | January | 2016 | 2016Q3 | 2016 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Not Veg | 2016-01-30 | Y | 63 | N | 8 | N | Y | 1.1101 | 39.4971 | 66571.7315
[7 empty] | 11080 | 8458 | 1361532 | 2016-01-29 13:02 | 2016-01-30 05:20 | 978 | 11kV | 139111 | 489 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At S847 11kV panel 45 tripped tripped Relays: A and C phase IOC and EFI Signals: 11kv trip, No3 Group Earth, Zone Earth Cause: Tree branch brought down Near PT740 Galston Rd See OMS 1364081 1364083 1364085 1361333 1361857 | January | 2016 | 2016Q3 | 2016 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2016-01-29 | Y | 284.4806 | N | 7 | N | Y | 1.1101 | 39.4971 | 101658.2157
[7 empty] | 11399 | 11825 | 1361710 | 2016-01-29 16:54 | 2016-01-30 11:20 | 1105.9 | 11kV | 8847.2 | 8 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Previous Storm | Y | At PT2335 McCallum Chilcott 31.5A footpath phase dropout fuse operated Cause: Lightning struck surge arrestor See OMS 1361710 1361945 1361950 | January | 2016 | 2016Q3 | 2016 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2016-01-29 | Y | 1105.9 | N | 7 | N | Y | 1.1101 | 39.4971 | 6465.2728
[7 empty] | 11380 | 11741 | 1362059 | 2016-01-30 14:51 | 2016-01-30 16:18 | 87 | 11kV | 4522 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | LID 165763 1 fault operation Sensitive Earth Fault nothing found - Note - SEF set at 5A for 1s, see DARTS for more info. Excluded oms 1362059 | January | 2016 | 2016Q3 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-01-30 | N | 83.7407 | N | 8 | N | N | 1.1101 | 39.4971 | 3304.5442
[7 empty] | 10440 | 1126 | 1362074 | 2016-01-30 16:24 | 2016-01-30 17:20 | 56 | 11kV | 1624 | 29 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | Y | LID 165764 A Phase DOLF : 16 Amp Excluded OMS 1362074 | January | 2016 | 2016Q3 | 2016 | 264:81236 | 264:81236 | ZN00264/081236 | PORT STEPHENS | OH | Veg | 2016-01-30 | N | 56 | N | 8 | N | N | 1.1101 | 39.4971 | 1186.7713
[7 empty] | 10650 | 3874 | 1362078 | 2016-01-30 16:41 | 2016-01-30 18:09 | 88 | 11kV | 127248 | 1446 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At S847 Hornsby Panel 39 Tripped tripped and locked out Cause: Likely Lightning | January | 2016 | 2016Q3 | 2016 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Not Veg | 2016-01-30 | Y | 88 | N | 8 | N | Y | 1.1101 | 39.4971 | 92989.0852
[7 empty] | 11390 | 11796 | 1362164 | 2016-01-30 17:24 | 2016-01-30 20:00 | 156 | 11kV | 170206 | 1117 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | On Panel 18 Berowra Waters beyond CP1047 had low Volts Cause: B phase burnt off on the corner of Kita Rd and Cambewarra Cres. See OMS 1364023 1362164 136228 | January | 2016 | 2016Q3 | 2016 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2016-01-30 | Y | 152.3778 | N | 8 | N | Y | 1.1101 | 39.4971 | 124381.5246
[7 empty] | 10957 | 7148 | 1362148 | 2016-01-30 17:03 | 2016-01-30 20:15 | 192 | 11kV | 280512 | 1682 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Wind Storm | Y | At Zn35800 Bankstown Panel 16 "Canterbury Fair" tripped on: Signals: 11kv Trip, minor alarm Relays: A & B phase IOC, Earth fault, EFI Abnormal: Sw/B closed at S5153 Seddon St, AB2035 open Remarks: Tx failure. PT421 Hoskins Ave was found with a blown HDO. Suspect hit by lightning | January | 2016 | 2016Q3 | 2016 | ZN35800:PA15 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-01-30 | N | 166.7729 | N | 8 | N | N | 1.1101 | 39.4971 | 204989.8959
[7 empty] | 12097 | 18898 | 1362010 | 2016-01-30 19:25 | 2016-01-30 20:15 | 50 | 11kV | 50 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | LID 165766 LL Lead Broken | January | 2016 | 2016Q3 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2016-01-30 | N | 50 | N | 8 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 11252 | 10421 | 1362292 | 2016-01-30 18:26 | 2016-01-30 20:55 | 149 | 11kV | 298 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 165765 A Phase DOLF : 16 Amp Excluded OMS 1362292 | January | 2016 | 2016Q3 | 2016 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-01-30 | N | 149 | N | 8 | N | N | 1.1101 | 39.4971 | 217.7696
[7 empty] | 11016 | 7720 | 1362397 | 2016-01-30 19:55 | 2016-01-30 21:10 | 75 | 11kV | 99591 | 1379 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | Zn36300 Balgowlah North Panel 19L on SEL At LB49832 SEL fault thrower Footpath phase bond off on HV UGOH above LB49832 (pole #FF38865) See 1363178,80 exclude 1362397 | January | 2016 | 2016Q3 | 2016 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2016-01-30 | N | 72.2197 | N | 8 | N | N | 1.1101 | 39.4971 | 72778.1654
[7 empty] | 11547 | 13088 | 1363722 | 2016-01-30 18:37 | 2016-01-30 21:34 | 177 | 11kV | 255942 | 1446 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | At S847 Hornsby Panel 39 tripped on Timed earth lakage and fault check. Cause: HV bond fefect on first UGOH out of zone. | January | 2016 | 2016Q3 | 2016 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Not Veg | 2016-01-30 | Y | 177 | N | 8 | N | Y | 1.1101 | 39.4971 | 187034.8646
[7 empty] | 10594 | 3169 | 1362381 | 2016-01-30 19:44 | 2016-01-30 23:10 | 206 | 11kV | 16007 | 1452 | HV | Lightning Strike | Adverse Weather/Environment | Bond | Unplanned | Previous Storm | Y | Zn15005 Belrose Panel 12L "Belrose" tripped and reclosed on Overcurrent, Earth fault relay - Lmax L1 L2 l3 EFI timing & lockout relays Lightning. Bond off n tee off to PT15863 andove st. Place in LV// to restore volts See 1363162,6 exclude 1362381 | January | 2016 | 2016Q3 | 2016 | ZN15005:PA12 | ZN15005:PA12 | ZN15005/000012 | NORTHERN BEACHES | OH | Not Veg | 2016-01-30 | N | 11.0241 | N | 8 | N | N | 1.1101 | 39.4971 | 11697.4435
[7 empty] | 11455 | 12319 | 1362079 | 2016-01-30 16:41 | 2016-01-30 23:33 | 412 | 11kV | 7416 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | on Panel 8 ex Galston Zone - Recloser 560 Peebles Nollands tripped on O/C Cause: Tree on HV near 20 peebles Rd | January | 2016 | 2016Q3 | 2016 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2016-01-30 | Y | 412 | N | 8 | N | Y | 1.1101 | 39.4971 | 5419.3941
[7 empty] | 10799 | 5477 | 1362527 | 2016-01-30 21:51 | 2016-01-31 00:03 | 132 | 11kV | 39600 | 300 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At S35370 Galston Panel 2 tripped reclosed tripped and locked out on B phase O/C and EFI and Lockout Abnormal Switching: AB3340 Open Cause: Brid contactedHV on PT651 Carters Galston Removed By Dop See OMS 1364061 1363744 1362527 1362537 | January | 2016 | 2016Q3 | 2016 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2016-01-30 | Y | 132 | N | 8 | N | Y | 1.1101 | 39.4971 | 28938.512
[7 empty] | 11201 | 9928 | 1362186 | 2016-01-30 17:39 | 2016-01-31 00:05 | 386.8333 | 11kV | 386.8333 | 1 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | HV pins cam loose, LV on the floor, all restored and power restored CC1: 22-"Refer to SOp" | January | 2016 | 2016Q3 | 2016 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2016-01-30 | Y | 386.8333 | N | 8 | N | Y | 1.1101 | 39.4971 | 282.6864
[7 empty] | 11355 | 11525 | 1362013 | 2016-01-30 15:59 | 2016-01-31 04:20 | 741 | 11kV | 22548 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Electrical Storm | Y | On Panel 2 ex Galston Recloser Cp3280 Hunt ave Tripped, reclosed tripped and locked out on Overcurrent Cause: Tree hit HV and damaged cct conductror in Cotsworld PT2353 Had a broken LV fuse assembly See OMS 1364056 1364057 1364059 1364060 1362069 | January | 2016 | 2016Q3 | 2016 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2016-01-30 | Y | 289.0769 | N | 8 | N | Y | 1.1101 | 39.4971 | 16477.4133
[7 empty] | 11464 | 12393 | 1362395 | 2016-01-30 17:11 | 2016-01-31 07:50 | 879 | 11kV | 326047 | 728 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn10996 Rockdale - Pnl.11 tripped and locked out on: A & B phase IOC, A phase timed O/C, EFI, lockout Reports of lightning strikes. Feeder patrolled and returned to service LV parallel failure at the same time affecting 3 DCs. 11kV Feeder outage # 1363682 SE LV parallel failures # 1363684 1363686 1363685 GIS Error: 1363687 | January | 2016 | 2016Q3 | 2016 | ZN10996:PA11 | ZN10998:PA16 | ZN10998/000016 | BAYSIDE | OH | Not Veg | 2016-01-30 | Y | 447.8668 | N | 8 | N | Y | 1.1101 | 39.4971 | 238265.5308
[7 empty] | 11811 | 16128 | 1361869 | 2016-01-30 22:23 | 2016-01-31 08:10 | 587 | 11kV | 2935 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | Y | LID 165761 DOLF : 10 Amp Excluded OMS 1361869 | January | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-01-30 | N | 587 | N | 8 | N | N | 1.1101 | 39.4971 | 2144.8114
[7 empty] | 11790 | 15849 | 1362559 | 2016-01-30 22:51 | 2016-01-31 13:30 | 879 | 11kV | 96084 | 649 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | Ex Zn12570 Avoca section of Pa33 "Scraybrood Waldron" fdr RE50407 THe scenic Bounty tripped and locked out Large tree on 11kV OH outside 486 The Scenic Rd, Macmaster Beach See 1363078,80,1 exclude 1362550,9,92 | January | 2016 | 2016Q3 | 2016 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2016-01-30 | Y | 148.0493 | N | 8 | N | Y | 1.1101 | 39.4971 | 70215.3532
[7 empty] | 11725 | 15148 | 1362713 | 2016-01-31 11:34 | 2016-01-31 23:50 | 736 | 11kV | 5888 | 8 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Kurnell South Zone - Pnl.18 - AB 35183 was found to have the roadside phase bond burnt off | January | 2016 | 2016Q3 | 2016 | ZN9534:PA18 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2016-01-31 | N | 736 | Y | 1 | N | Y | 1.1101 | 39.4971 | 4302.7767
[7 empty] | 12187 | 19730 | 1363133 | 2016-01-31 15:00 | 2016-01-31 23:59 | 539 | 33kV Distribution | 539 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165770 sub found with all dolfs blown AP left on site. head of pole KT-70897 also found damaged. | January | 2016 | 2016Q3 | 2016 |  |  |  | NEWCASTLE | OH | Veg | 2016-01-31 | N | 539 | N | 1 | N | N | 1.1101 | 39.4971 | 393.8853
[7 empty] | 10805 | 5521 | 1362143 | 2016-01-30 17:11 | 2016-02-01 01:50 | 1959 | 11kV | 714650 | 3754 | HV | Lightning Strike | Adverse Weather/Environment | DC Not Transformer | Unplanned | Lightning | Y | Zn10999 Kogarah - Pnl.10 tripped, reclosed and locked out on: ABC phase timed O/C, EFI, Earth Fault Check Field EFIs: LB62011, S10158, UGOH, S10183, S10422 Abnormal: S10183 Sw/B CLOSED - LB31271 OPEN (Arncliffe 1/B5) Lightning strike caused S10737 to ignite and cause significant damage, resulting in an extended restoration time. The fault check then burnt off a HV bond near tee off to S10608. See 1363704 1363707 1363712 SE: 1363705 (Arncliffe P11 interrupted for safety) | January | 2016 | 2016Q3 | 2016 | ZN10999:PA10 | ZN10999:PA10 | ZN10999/000010 | BAYSIDE | UG | Not Veg | 2016-01-30 | Y | 190.3703 | N | 8 | N | Y | 1.1101 | 39.4971 | 522245.1414
[7 empty] | 10501 | 1983 | 1362856 | 2016-02-01 05:48 | 2016-02-01 08:15 | 147 | 11kV | 147 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At Sub 7284 Australia Carter B Phase HV fuse operated section of Panel Mo.18 "Australia Carter" feeder ex Sub 2466 Flemington Remarks: Transformer Failure. See DMA | February | 2016 | 2016Q3 | 2016 | ZN2466:PA18 | ZN36000:PA17 | ZN36000/000017 | PARRAMATTA | UG | Not Veg | 2016-02-01 | N | 147 | N | 3 | N | N | 1.1101 | 39.4971 | 107.4233
[7 empty] | 12039 | 18417 | 1362741 | 2016-01-30 17:03 | 2016-02-01 11:30 | 2547 | 11kV | 34204 | 52 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn3472 Sefton Panel 18 "Royal Well etc" tripped, reclosed & tripped on: Signals: 11kv trip, zone earth, Tx3 group earth Relays: C phase IOC, C phase timed OC, EFI, Fault Check, Reclose timing, Lockout Remarks: Tree/branch on OH mains. Tree branch on 11kv mains on cnr of Mary St and Bellona Ave Regents park S1211 Bellona Ave left isolated as appears LV board has flashed over. T/Con to inspect before energising S1211 Bellona Avenue Dist No.1, Dist No.2, Dist No.3 and Dist No.4v"No 15 Bellona Ave" restored at 01/02/16 11:30 Phase: ABC Fuse: 400A Remarks: weather related. | January | 2016 | 2016Q3 | 2016 | ZN3472:PA18 | ZN3472:PA18 | ZN03472/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-01-30 | Y | 657.7692 | N | 8 | N | Y | 1.1101 | 39.4971 | 24995.2744
[7 empty] | 11914 | 17047 | 1365554 | 2016-02-01 12:07 | 2016-02-01 12:20 | 13 | 11kV | 65 | 5 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kV feeder from CP3343 to CP555 interrupted by DOp Cause: Removal of Large Tree from 11kV OH See OMS 1365554 1363089 | February | 2016 | 2016Q3 | 2016 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2016-02-01 | N | 13 | N | 3 | N | N | 1.1101 | 39.4971 | 47.5001
[7 empty] | 10430 | 954 | 1363086 | 2016-02-01 10:00 | 2016-02-01 13:40 | 220 | 11kV | 220 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165777 B phase DOLF : 10 Amp Excluded OMS 1363085 | February | 2016 | 2016Q3 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2016-02-01 | N | 220 | N | 3 | N | N | 1.1101 | 39.4971 | 160.7695
[7 empty] | 10992 | 7531 | 1363348 | 2016-02-02 03:33 | 2016-02-02 05:00 | 87 | 11kV | 39043 | 521 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | At S35370 Galston Panel 10 Tripped and locke dout on 50TBC B and C phase OC Lockout and Timing 11kV Trip Cause: Large Tree branch on 11kV See OMS 1365426 1365427 1365425 1363348 | February | 2016 | 2016Q3 | 2016 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2016-02-02 | N | 74.9386 | N | 5 | N | N | 1.1101 | 39.4971 | 28531.4728
[7 empty] | 11974 | 17724 | 1363571 | 2016-01-14 16:10 | 2016-02-02 11:20 | 27070 | 11kV | 93452 | 101 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 165544 6 Fault operations H.V. Reported down sub pole 59040 on ground section left isolated at 11kV Links 5345 Excluded oms # 1354143 & 1354151 | January | 2016 | 2016Q3 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2016-01-14 | Y | 925.2673 | N | 4 | N | Y | 1.1101 | 39.4971 | 68291.9652
[7 empty] | 11021 | 7767 | 1363499 | 2016-02-02 09:51 | 2016-02-02 11:23 | 92 | 11kV | 68965 | 769 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2835 Burwood 11kv "Mosely Cooper" feeder panel 36 tripped on: Relays - B phase E/F, EFI, fault check Signals: Zone E, Group 1 Earth, 11kv trip Remarks: UG fault. 11kv feeder from S3835 Burwood to S3108 Mosley Cooper is defective | February | 2016 | 2016Q3 | 2016 | ZN2835:PA36 | ZN2835:PA36 | ZN02835/000036 | STRATHFIELD | UG | Not Veg | 2016-02-02 | N | 89.6814 | N | 5 | N | N | 1.1101 | 39.4971 | 50397.5879
[7 empty] | 10381 | 199 | 1363561 | 2016-02-02 11:09 | 2016-02-02 12:34 | 85.35 | 11kV | 1792.35 | 21 | HV | Animal Bird | Animal | Fuse | Unplanned | No Weather Impact | N | Blown HV spur fuse 63353. Caused by bird at sub 27632. | February | 2016 | 2016Q3 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Not Veg | 2016-02-02 | N | 85.35 | N | 5 | N | N | 1.1101 | 39.4971 | 1309.7965
[7 empty] | 12090 | 18824 | 1363744 | 2016-02-02 15:00 | 2016-02-02 17:40 | 159.5 | 11kV | 5742 | 36 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Auto Link CP443 Found Operated on one phase only Section of 11kV feeder No2 Cause: Suspected defective auto link CP443 Bypass AB closed to restore supply | February | 2016 | 2016Q3 | 2016 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2016-02-02 | N | 159.5 | N | 5 | N | N | 1.1101 | 39.4971 | 4196.0842
[7 empty] | 12162 | 19510 | 1363821 | 2016-02-02 21:15 | 2016-02-02 22:02 | 47 | 11kV | 15463 | 329 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN8000 Macquarie Park Panel 6 tripped on Relays: B and C phase OC and Earth Fault, Fault Check, EFI, No1 Group Earth Signals: No1 Group Earth, 11kV trip Abnormal Switching: DMA feeder O/O/S from S48819 to S4647 tee PT1188. Cause: 11kV feeder fault from S8000 Macquarie Park Pa6 to S8150 See OMS 1365675 1363821 | February | 2016 | 2016Q3 | 2016 | ZN8000:PA6 | ZN8000:PA6 | ZN08000/000006 | KU-RING-GAI | UG | Not Veg | 2016-02-02 | N | 47 | N | 5 | N | N | 1.1101 | 39.4971 | 11299.9043
[7 empty] | 12198 | 19822 | 1363835 | 2016-02-03 05:23 | 2016-02-03 07:05 | 102 | 11kV | 15300 | 150 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12640 Umina section of Pa19 PT18515 Booker Bay Hood centre phase 50A HVDO batch no.0218 blown due to possible fuse fatigue See 1364839 exclude 1363835 | February | 2016 | 2016Q3 | 2016 | ZN12640:PA19 | ZN12640:PA14 | ZN12640/000014 | CENTRAL COAST | OH | Not Veg | 2016-02-03 | N | 102 | N | 2 | N | N | 1.1101 | 39.4971 | 11180.7887
[7 empty] | 11657 | 14327 | 1363852 | 2016-02-03 07:35 | 2016-02-03 11:00 | 205.6333 | 11kV | 10898.5667 | 53 | HV | Animal Bird | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty section of panel 16 PT11555 Gladstan Tuggerah 11kv Road & centre phase 31Amp Dropout fuses operated Pigeon on Tranformer bushings See 1363857 exclude 1363852,78 | February | 2016 | 2016Q3 | 2016 | ZN12610:PA16 | ZN12610:PA16 | ZN12610/000016 | CENTRAL COAST | OH | Not Veg | 2016-02-03 | N | 205.6333 | N | 2 | N | N | 1.1101 | 39.4971 | 7964.3511
[7 empty] | 10396 | 378 | 1364219 | 2016-02-04 03:05 | 2016-02-04 04:36 | 91 | 11kV | 8933 | 99 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | 11kV Recloser 559 Cobah tripped and reclosed Dop Patrolled, Cause not ascertained for outage See OMS 1365396 1365397 1364219 | February | 2016 | 2016Q3 | 2016 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2016-02-04 | N | 90.2323 | N | 8 | N | N | 1.1101 | 39.4971 | 6527.9729
[7 empty] | 11773 | 15637 | 1364226 | 2016-02-04 05:27 | 2016-02-04 08:33 | 186 | 11kV | 14082 | 99 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | 11kV Recloser CP559 Tripped and reclosed to lockout Relays: O/C Trip Cause: DOp to patrol feeder and found main ok. Mains to patrol from LB62108 to find faulty section. See OMS 1365747 1365749 1364226 | February | 2016 | 2016Q3 | 2016 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2016-02-04 | N | 142.2424 | N | 8 | N | N | 1.1101 | 39.4971 | 10290.7103
[7 empty] | 10939 | 7002 | 1364305 | 2016-02-04 08:58 | 2016-02-04 10:45 | 107 | 11kV | 2209 | 99 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | At Zn35370 Galston Panel 8 - Recloser CP559 Cobah Rd Tripped on Overcurrent Cause: DOp/Linesman found insulator damaged on AB3342 on load side to PT63876 | February | 2016 | 2016Q3 | 2016 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2016-02-04 | N | 22.3131 | N | 8 | N | N | 1.1101 | 39.4971 | 1614.272
[7 empty] | 10783 | 5321 | 1364229 | 2016-02-04 03:27 | 2016-02-04 13:20 | 593 | 33kV Distribution | 2372 | 4 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 165812 1 fault operation A phase Earth Fault 33kV crossarm burnt through at KT70974 High into low sub 19207 C phase RH LVF blown 315A | February | 2016 | 2016Q3 | 2016 |  |  |  | NEWCASTLE | OH | Not Veg | 2016-02-04 | N | 593 | N | 8 | N | N | 1.1101 | 39.4971 | 1733.3876
[7 empty] | 11580 | 13490 | 1364428 | 2016-02-04 14:00 | 2016-02-04 14:40 | 40 | 11kV | 120 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 165838 A Phase DOLF : 10 Amp Excluded OMS 1364428 | February | 2016 | 2016Q3 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2016-02-04 | N | 40 | N | 8 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 10924 | 6870 | 1364224 | 2016-02-04 04:51 | 2016-02-04 16:10 | 679 | 11kV | 116272 | 537 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Ex Zn12630 Peats Ridge section of panel 2 RE45189 Cooks Peats Ridge 0.5 tripped and reclosed to lockout X Relays: SEF trip, Overcurrent trip Tree branch has brought 11kv mains down adjacent PT13482 Wise Ferry Oyster 0.9 See 1364855,7,8,9,60 exclude 1364224,373,84 | February | 2016 | 2016Q3 | 2016 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2016-02-04 | N | 216.5214 | N | 8 | N | N | 1.1101 | 39.4971 | 84968.1482
[7 empty] | 10883 | 6422 | 1364572 | 2016-02-04 15:54 | 2016-02-04 20:45 | 291 | 11kV | 77214 | 670 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn14144 Wamberal Panel 10 fdr tripped, reclosed, tripped and locked out Signals: 11kv trip, Tx2 GE Relays: A phase OC, EFI, Timing, Lockout EFI: S18824 S18802 S18826 S48880 S18825 RE44607 Matcham North (Defective) tripped/reclosed/tripped but did not clear fault Relays: First Go - OC, IOC trip. Second Go - EF Trip, IOC Trip Tree brought down 11kv OH Fdr btwn PT14718 & PT11815. High into Low Voltage See 1364866,7,8,9,70,1,2 exclude 1364572,8,80,638,59 | February | 2016 | 2016Q3 | 2016 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2016-02-04 | N | 115.2448 | N | 8 | N | N | 1.1101 | 39.4971 | 56425.7138
[7 empty] | 10856 | 6153 | 1364687 | 2016-02-04 19:53 | 2016-02-04 23:05 | 192 | 11kV | 39682 | 241 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | At Zn35900 Potts Hill Panel 16 "Ballad St No2" tripped, reclosed & locked out on: Signals: 11kv trip, Group Earth Tx 2 Relays: Basler Relay - 50TN & 51N, Reclose lockout, EFI Remarks: suspected UG fault between S4396 Ballad St No 1 Sw/A to S4473 Sutherland Brunker Sw/B to S1254 Metal Coatings Sw/B. Dop also found a burnt off bond at the ugoh above LB881 | February | 2016 | 2016Q3 | 2016 | ZN35900:PA16 | ZN35900:PA16 | ZN35900/000016 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-02-04 | N | 164.6556 | N | 8 | N | N | 1.1101 | 39.4971 | 28998.4352
[7 empty] | 10880 | 6409 | 1366123 | 2016-02-05 04:11 | 2016-02-05 05:13 | 62 | 11kV | 39804 | 642 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S1673 Turramurra Panel 7 Tripped and reclosed on IOC with Earth Fault and EFI Cause: Possum on 11kV at PT1753 Hampden Eric Abnormal Switching SW/B at S4710 and S4711 SW/A Open and S1721 Closed See OMS 1366123 1364714 | February | 2016 | 2016Q3 | 2016 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Not Veg | 2016-02-05 | N | 62 | N | 4 | N | N | 1.1101 | 39.4971 | 29087.5892
[7 empty] | 11025 | 7798 | 1364730 | 2016-02-05 07:29 | 2016-02-05 11:16 | 227 | 11kV | 111201 | 529 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Zn14891 Wyong Panel 20 "Warnervale West Railway" fdr tripped, reclosed & locked out Relays: B & C phase timed overcurrent, Efi, Reclose/Lockout relay. Earth Fault check relay Signals: 11kv trip EFI's S18535 S18246 @ sametime Recloser 45203 Butt Gas Generator tripped & locked out Suspect flashover @ LK42001 causing centre phase bond to fail See 1365436,9,40,2,3,4 Exclude 1364730,94 | February | 2016 | 2016Q3 | 2016 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2016-02-05 | N | 210.2098 | N | 4 | N | N | 1.1101 | 39.4971 | 81262.4109
[7 empty] | 11499 | 12709 | 1364828 | 2016-02-05 10:20 | 2016-02-05 13:45 | 205 | 11kV | 410 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165869 A Phase DOLF : 10 Amp Excluded OMS 1364828 | February | 2016 | 2016Q3 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-02-05 | N | 205 | N | 4 | N | N | 1.1101 | 39.4971 | 299.6159
[7 empty] | 11596 | 13666 | 1365072 | 2016-02-05 21:41 | 2016-02-05 22:39 | 58 | 11kV | 91640 | 1580 | HV | Arcing | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North Panel 8 "Innes Condamine" fdr tripped & reclosed on Relays: B phase overcurrent, BC phase IOC EFI Signals: 11kv trip, No1 Group Earth EFI's: S50695 S16960 S16243 S16275 Flashover at UGOH to S16275. Overhead to inspect in daylight hours Refer TPE basler relay at Zone had reset button jammed in and failed to flag. DOp released button to allow future operations. If spring release could be checked on that panel and others at zone with same relay as DOp found others jammed in See 1365072 GIS 1365076 exclude 1365075 | February | 2016 | 2016Q3 | 2016 | ZN36300:PA8 | ZN36300:PA8 | ZN36300/000008 | NORTHERN BEACHES | OH | Not Veg | 2016-02-05 | N | 58 | N | 4 | N | N | 1.1101 | 39.4971 | 66967.8091
[7 empty] | 11378 | 11704 | 1365113 | 2016-02-06 06:58 | 2016-02-06 08:21 | 83 | 11kV | 64821 | 1071 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn15002 Narrabeen 11kv Pa8 tripped on Relays: AC phase timed overcurrent Signals: 11kv trip @PT15224 Irrawong rd - middle phase HDO blown Tree branch and large piece of bark fell onto poly droppers and HDO damaging the HDO HV fuse. See 1365465,7,8 exclude 1365112,3,5 | February | 2016 | 2016Q3 | 2016 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | OH | Veg | 2016-02-06 | N | 60.5238 | N | 4 | N | N | 1.1101 | 39.4971 | 47369.2749
[7 empty] | 10668 | 4079 | 1365101 | 2016-02-06 07:35 | 2016-02-06 08:55 | 80 | 11kV | 7110 | 130 | HV | 3rd Party Action | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 165872 Car hit LV pole CH-50130 11kV isolated to replace pole. Excluded OMS 1365101 & 1365120 | February | 2016 | 2016Q3 | 2016 | 223:14395 | 223:14395 | ZN00223/014395 | LAKE MACQUARIE | OH | Not Veg | 2016-02-06 | N | 54.6923 | N | 4 | N | N | 1.1101 | 39.4971 | 5195.7783
[7 empty] | 11131 | 9122 | 1365153 | 2016-02-06 10:18 | 2016-02-06 12:10 | 112 | 11kV | 448 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165876 C Phase DOLF : 10 Amp Excluded OMS 1365153 | February | 2016 | 2016Q3 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2016-02-06 | N | 112 | N | 4 | N | N | 1.1101 | 39.4971 | 327.3852
[7 empty] | 11146 | 9354 | 1365142 | 2016-02-06 09:19 | 2016-02-06 14:50 | 331 | 11kV | 331 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165875 C Phase DOLF : 10 Amp Could not access sub pole - bushes & lantana growing around sub pole. Mait O/C required to clear access. Replaced Blown L/A Excluded OMS 1365142 | February | 2016 | 2016Q3 | 2016 | 265:81648 | 265:81648 | ZN00265/081648 | PORT STEPHENS | OH | Veg | 2016-02-06 | N | 331 | N | 4 | N | N | 1.1101 | 39.4971 | 241.885
[7 empty] | 11583 | 13518 | 1365235 | 2016-02-07 09:00 | 2016-02-07 10:05 | 65 | 11kV | 650 | 10 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 165881 Sect isolated to replace 33kV insulator at pole LS-20021 Excluded OMS 1365235 & LID report 165880 | February | 2016 | 2016Q3 | 2016 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2016-02-07 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 475.0008
[7 empty] | 12234 | 20268 | 1365248 | 2016-02-07 08:08 | 2016-02-07 10:50 | 162 | 11kV | 162 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 165882 C Phase DOLF : 10 Amp Blown Lightning Arrestor replaced Excluded OMS 1365248 | February | 2016 | 2016Q3 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-02-07 | N | 162 | N | 5 | N | N | 1.1101 | 39.4971 | 118.3848
[7 empty] | 11267 | 10588 | 1365283 | 2016-02-07 12:32 | 2016-02-07 13:35 | 63 | 11kV | 189 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165883 A phase DOLF J Frazer reports sub is single phase, on system diagram it is three phase. Excluded OMS 1365283 | February | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-02-07 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 138.1156
[7 empty] | 11832 | 16373 | 1365306 | 2016-02-07 16:16 | 2016-02-07 17:20 | 64 | 11kV | 7872 | 123 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty section of Pa13 PT13068 Boondilla Warrigal road phase arrestor blown Lightning arrestor roadside phase blown See 1365311 exclude 1365306,7,13 CC1: 22-"Refer to SOp" | February | 2016 | 2016Q3 | 2016 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2016-02-07 | N | 64 | N | 5 | N | N | 1.1101 | 39.4971 | 5752.6254
[7 empty] | 11178 | 9687 | 1365329 | 2016-02-07 19:57 | 2016-02-08 12:15 | 978 | 11kV | 978 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 165887 Sub Isolated 3 phase 100 Amp Distribution fuses Customer private pole failed, LV mains Shorted, 1 LV fuse only blown. Transformer now faulty, needs replacement. Only feeds Irrigation pump. Excluded OMS 1365329 | February | 2016 | 2016Q3 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2016-02-07 | N | 978 | N | 5 | N | N | 1.1101 | 39.4971 | 714.6936
[7 empty] | 11663 | 14380 | 1365654 | 2016-02-08 15:00 | 2016-02-08 16:00 | 60 | 11kV | 180 | 3 | HV | Vegetation Grow In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 165899 No protection operation, line isolated to allow tree to be removed safely from CCT. | February | 2016 | 2016Q3 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-02-08 | N | 60 | N | 6 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 12135 | 19224 | 1365572 | 2016-02-08 17:30 | 2016-02-08 18:30 | 60 | 11kV | 120 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165901 No protection operation. A tractor driver was burnt following an explosion. Ausgrid were called in case the cause of the fault was contact with an unidentifed cable. John Frazer advises the cause was determined to be an old acetylene bottle left in the grass and whilst the tractor was operating not far from a pole it DID NOT come into contact with any electrical cables or equipment . This sub supplies a house and also had a service going to an abondoned workshop. The Switchboard was already isolated at the workshop switchboard and the service going to it was low, | February | 2016 | 2016Q3 | 2016 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2016-02-08 | N | 60 | N | 6 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 11264 | 10536 | 1365559 | 2016-02-08 16:00 | 2016-02-08 19:00 | 180 | 11kV | 360 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165902 DOLF : 3 Amp Bird contacting 11kV caused DOLF to blow. Excluded OMS # 1365559. | February | 2016 | 2016Q3 | 2016 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2016-02-08 | N | 180 | N | 6 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 11877 | 16790 | 1365584 | 2016-02-08 18:59 | 2016-02-08 20:41 | 102 | 11kV | 85884 | 842 | HV | Vegetation Blow/Fall In | Vegetation | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | @ZN10994 Mortdale Exiting Panel #7 labelled "S.10200 Letitia Frederick" Rec62226 Connells Terry tripped: Relays: OC trip, lockout, Signals: 11kv CB.62226 Open, 33kv sub Batt Charger Defect Remarks: tree branch contact. 1 span beyond PT10312 Queens Rose | February | 2016 | 2016Q3 | 2016 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Veg | 2016-02-08 | N | 102 | N | 6 | N | N | 1.1101 | 39.4971 | 62761.4941
[7 empty] | 10779 | 5270 | 1365609 | 2016-02-08 20:35 | 2016-02-08 21:34 | 59 | 11kV | 24957 | 423 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn3154 St Ives 11kV Panel 14 tripped on Relays: B phase IOC, EFI Signals: 11kv trio EFI: S4264 Possum at PT1258 Benaroon Avenue, removed by DOp See 1365609 exclude 1365613 | February | 2016 | 2016Q3 | 2016 | ZN3154:PA14 | ZN3154:PA14 | ZN03154/000014 | KU-RING-GAI | OH | Not Veg | 2016-02-08 | N | 59 | N | 6 | N | N | 1.1101 | 39.4971 | 18237.8395
[7 empty] | 11505 | 12760 | 1365614 | 2016-02-08 20:55 | 2016-02-08 22:15 | 80 | 11kV | 102802 | 1659 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Zn12640 Umina 11kv Pa7 "Berth West" tripped on Signals: 11kV trip Relays: OC, EFI, Earth Fault, SEF EFI's:S18126 S18128 S18136 Footpath side surge arrestor at PT11577 Palm Barrenjoey has failed due to possum which also appears to have casued the 11kv HDO to flash over See 1365726,7,8 Exclude 1365614,5,6 | February | 2016 | 2016Q3 | 2016 | ZN12640:PA7 | ZN12640:PA7 | ZN12640/000007 | CENTRAL COAST | OH | Not Veg | 2016-02-08 | N | 61.9662 | N | 6 | N | N | 1.1101 | 39.4971 | 75124.6695
[7 empty] | 11808 | 16071 | 1365683 | 2016-02-09 02:13 | 2016-02-09 03:40 | 87 | 11kV | 77082 | 1179 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 165907 1 fault Operation B & C phase overcurrent Faulty UGOH pole JU-61523. Sw 34245 Targets = Inst B & C O/C Excluded OMS 1365636 | February | 2016 | 2016Q3 | 2016 | 202:34245 | 202:34245 | ZN00202/034245 | NEWCASTLE | Unknown | Unknown | 2016-02-09 | N | 65.3791 | N | 5 | N | N | 1.1101 | 39.4971 | 56329.2521
[7 empty] | 11975 | 17767 | 1365633 | 2016-02-09 02:17 | 2016-02-09 08:45 | 388 | 11kV | 42263 | 470 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | Zn7900 Campbell St - Pnl.15 tripped on: C phase timed O/C , EFI, Fault Check Field EFIs: S6833 & S2701 11kV RMI @ S3277 Commonwealth Fov appears to have failed as the operator reported a burning smell upon entering the substation and visible carbon marks on the RMI. Customers called in from 1:03am out of S3722 reporting fluctating supply. Feeder tripped at 2:17am See 1365984 1365985 1365986 | February | 2016 | 2016Q3 | 2016 | ZN7900:PA15 | ZN7900:PA15 | ZN07900/000015 | SYDNEY | Unknown | Not Veg | 2016-02-09 | N | 89.9213 | N | 5 | N | N | 1.1101 | 39.4971 | 30884.5539
[7 empty] | 10725 | 4683 | 1366075 | 2016-02-09 11:25 | 2016-02-09 11:35 | 10 | 11kV | 240 | 24 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Tree resting on HV mains O/S 71 Quarry Rd Dural. Interruption for safety to carry out repairs on site Supply interrupted on PT2062, PT1752, PT1121 and PT2175 | February | 2016 | 2016Q3 | 2016 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2016-02-09 | N | 10 | N | 5 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 11510 | 12775 | 1365742 | 2016-02-09 11:17 | 2016-02-09 13:06 | 109 | 11kV | 18919 | 211 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S4545 Meadowbanks Panel 40 tripped on Relays: Timed OC, E/F,Fault Check and EFI Signals: 11kV Trip, Group Earth and No3 Zone Earth Abnormal Switching: AB1965 Open, SW/B at S8740 Closed Cause: UG cable fault in section from S64687 Betts Chatham SW/B to AB1965 to S5086 See OMS 1366003 1366004 1365742 NOTE: No customers are connected on either S47010 or S64687 - Appear to be new Subs | February | 2016 | 2016Q3 | 2016 | ZN4545:PA35 | ZN4545:PA40 | ZN04545/000040 | RYDE | UG | Not Veg | 2016-02-09 | N | 89.6635 | N | 5 | N | N | 1.1101 | 39.4971 | 13825.4472
[7 empty] | 10858 | 6187 | 1365890 | 2016-02-09 17:44 | 2016-02-09 18:55 | 71 | 11kV | 89531 | 1261 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Panel 24 Hammond Park fdr tripped, reclosed and locked out on C phase IOC, EFI, Earth Fault check, reclose lockout, reclose timer Underground fault. between Panel 24 and AB44646. | February | 2016 | 2016Q3 | 2016 | ZN12610:PA24 | ZN12610:PA24 | ZN12610/000024 | CENTRAL COAST | UG | Not Veg | 2016-02-09 | N | 71 | N | 5 | N | N | 1.1101 | 39.4971 | 65426.6141
[7 empty] | 11880 | 16800 | 1365923 | 2016-02-10 00:17 | 2016-02-10 01:50 | 93 | 11kV | 2604 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165919 B Phase DOLF : 16 Amp READINGS AS LEFT = 141A, 14A, 20A @ 249V. Excluded OMS 1365923 | February | 2016 | 2016Q3 | 2016 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2016-02-10 | N | 93 | N | 4 | N | N | 1.1101 | 39.4971 | 1902.9264
[7 empty] | 11211 | 10021 | 1366173 | 2016-02-10 16:34 | 2016-02-10 17:06 | 32 | 11kV | 56672 | 1771 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12650 West Gosford Panel 13 "THe Hanlan St" fdr tripped on BC phase IOC tree branch on OH mains. near AB44565 manns rd gosford Recloser did not operate. TPE to investigate | February | 2016 | 2016Q3 | 2016 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2016-02-10 | N | 32 | N | 4 | N | N | 1.1101 | 39.4971 | 41414.2261
[7 empty] | 10811 | 5600 | 1366192 | 2016-02-10 16:54 | 2016-02-10 18:09 | 75 | 11kV | 159225 | 2123 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca Pa37 "The Avoca Beach" fdr tripped reclosed out on AB phase IOC, reclos etimer, relcose lockout Tree branch on OH Mains near AB43305 round st Avoca See 1366183 exclude 1366192 | February | 2016 | 2016Q3 | 2016 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2016-02-10 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 116356.9337
[7 empty] | 11554 | 13137 | 1366282 | 2016-02-10 21:12 | 2016-02-10 23:31 | 139 | 11kV | 168254 | 1509 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 165935 1 fault operation Sensitive Earth Fault Feeder abnormally switched IE ABS 40293 closed and ABS 9101 open. No fault found detailed daylight patrol required. Excluded OMS 1366236, 1366234 | February | 2016 | 2016Q3 | 2016 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2016-02-10 | N | 111.5003 | N | 4 | N | N | 1.1101 | 39.4971 | 122955.0605
[7 empty] | 10593 | 3161 | 1366411 | 2016-02-11 13:00 | 2016-02-11 13:30 | 30 | 11kV | 240 | 8 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165949 C Phase DOLF : 16 Amp | February | 2016 | 2016Q3 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2016-02-11 | N | 30 | N | 5 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 10587 | 3052 | 1366502 | 2016-02-11 15:34 | 2016-02-11 17:05 | 91 | 11kV | 32760 | 360 | HV | Burnt Contacts | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | At Zn1850 Bass Hill ex panel 15 'Wren St", At LB 2212 road side arm has been burnt off Remarks: air break switch - details below. LB2212 road side arm has been burnt off | February | 2016 | 2016Q3 | 2016 | ZN1850:PA15 | ZN3472:PA30 | ZN03472/000030 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-02-11 | N | 91 | N | 5 | N | N | 1.1101 | 39.4971 | 23940.0417
[7 empty] | 10728 | 4712 | 1366549 | 2016-02-11 17:17 | 2016-02-11 18:51 | 94 | 11kV | 102914 | 1131 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn35800 bankstown Panel 16 "Canterbury Fair" feeder has tripped Signals: 11kv trip Relays: 51 T AB IOC A and B, EFI Field EFI's: nil Abnormal: close sw/b @ S5153, open AB439 Remarks: tree/branch on OH mains. Branch OS 60 Hoskins. PT 1237 in LV parallel at time of fault with PT1804. See outage at PT1248 at similar time | February | 2016 | 2016Q3 | 2016 | ZN35800:PA15 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-02-11 | N | 90.9938 | N | 5 | N | N | 1.1101 | 39.4971 | 75206.5158
[7 empty] | 11813 | 16144 | 1366609 | 2016-02-11 23:34 | 2016-02-12 00:55 | 81 | 11kV | 8056 | 122 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN1068 Lidcombe 11kv Panel 29 tripped on: Relays: B phase E/F, EFI Signals - 11kv Trip, Zone Earth, Group Earth No.1 TX Remarks: UG fault. 11kv feeder fault from Zn1068 Lidcombe to S8209 Percy Boorea No2 tee to S2151 Cockthorpe RD | February | 2016 | 2016Q3 | 2016 | ZN1068:PA29 | ZN1068:PA28 | ZN01068/000028 | CUMBERLAND | UG | Not Veg | 2016-02-11 | N | 66.0328 | N | 5 | N | N | 1.1101 | 39.4971 | 5887.0872
[7 empty] | 12101 | 18948 | 1366616 | 2016-02-12 06:23 | 2016-02-12 07:30 | 67 | 11kV | 201 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166151 B Phase DOLF : 16 Amp Excluded oms 1366617,1366616 | February | 2016 | 2016Q3 | 2016 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2016-02-12 | N | 67 | N | 5 | N | N | 1.1101 | 39.4971 | 146.8849
[7 empty] | 11442 | 12204 | 1366594 | 2016-02-11 18:36 | 2016-02-12 11:15 | 999 | 11kV | 8088 | 104 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Panel 1 RE44995 Kulnura tripped and reclosed X1 Relays IOC, O/C trip Tree branch brough down OH outside Yorky Waters Rd, Kulnura tree brougth down HV into LV See 1367245,6 exclude 1366594 | February | 2016 | 2016Q3 | 2016 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2016-02-11 | N | 77.7692 | N | 5 | N | N | 1.1101 | 39.4971 | 5910.4718
[7 empty] | 12095 | 18892 | 1366702 | 2016-02-12 11:00 | 2016-02-12 14:30 | 210 | 11kV | 161907 | 2087 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 165968 30 Fault operations 3 phase Earth Fault ug cable fault between Sw 38056 & Sw 13514 Targets Sw 34254 Newcastle CBD: E/F Excluded oms 1366702 | February | 2016 | 2016Q3 | 2016 | 202:34254 | 202:34254 | ZN00202/034254 | NEWCASTLE | UG | Not Veg | 2016-02-12 | N | 77.5788 | N | 5 | N | N | 1.1101 | 39.4971 | 118316.8602
[7 empty] | 10922 | 6858 | 1366788 | 2016-02-12 15:32 | 2016-02-12 18:28 | 176 | 11kV | 10912 | 62 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Section of Panel 30 ex Pymble At PT62782 Centre Phase 63k fuse blown. Cause: Fuse fatigue See OMS 1366788 1366784 | February | 2016 | 2016Q3 | 2016 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Not Veg | 2016-02-12 | N | 176 | N | 5 | N | N | 1.1101 | 39.4971 | 7974.1678
[7 empty] | 10789 | 5364 | 1367278 | 2016-02-12 08:40 | 2016-02-12 18:50 | 610 | 11kV | 610 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165969 A Phase DOLF : 3 Amp Excluded OMS 1366640 | February | 2016 | 2016Q3 | 2016 | 509:33444 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-02-12 | N | 610 | N | 5 | N | N | 1.1101 | 39.4971 | 445.77
[7 empty] | 11685 | 14614 | 1366852 | 2016-02-12 17:56 | 2016-02-12 19:35 | 99 | 11kV | 105696 | 1174 | HV | Overload | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Section of Pnl 3 "Rex Rd" feeder at Zn1850 Bass Hill 11kv Recloser 49253 Rex McClean tripped on overcurrent Abnormal: AB2947 closed and sw/A at Sub 5963 opened, also LB 2713 closed and LB 2714 opened Remarks: overload. suspect overload due to cable fault on Pnl28 at Sefton | February | 2016 | 2016Q3 | 2016 | ZN1850:PA3 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-02-12 | N | 90.0307 | N | 5 | N | N | 1.1101 | 39.4971 | 77239.5193
[7 empty] | 11828 | 16320 | 1366891 | 2016-02-13 01:08 | 2016-02-13 02:06 | 58 | 11kV | 24168 | 684 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | @Zn3472 Sefton - 11kv Panel No.29 "Sub 4410 Joanne Court" feeder tripped and reclosed Relays: A + B phase IOC, EFI, Fault Check, timing/reclose relay Signals: 11kv trip, Zone Earth, No 4 Group Earth Remarks: bond. 11kv bond failed and flashed over on UGOH below AB76 | February | 2016 | 2016Q3 | 2016 | ZN3472:PA29 | ZN3472:PA29 | ZN03472/000029 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-02-13 | N | 35.3333 | N | 5 | N | N | 1.1101 | 39.4971 | 17661.2616
[7 empty] | 11701 | 14829 | 1366901 | 2016-02-13 08:11 | 2016-02-13 12:15 | 244 | 11kV | 244 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165980 Single phase DOLF : 10 Amp excluded OMS 1366901 Damaged DOLF replaced. Tx Volts: 247V Tx Load: 23A | February | 2016 | 2016Q3 | 2016 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2016-02-13 | N | 244 | N | 5 | N | N | 1.1101 | 39.4971 | 178.308
[7 empty] | 10894 | 6552 | 1366918 | 2016-02-13 12:50 | 2016-02-13 16:15 | 205 | 11kV | 6765 | 33 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa2 between AB44993 to AB42920 to LB43440 isoalted interrupting PT11410 PT13059 PT11409 Vehicle hit pole. See 1367255 exclude 1366918,20,30,51 | February | 2016 | 2016Q3 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2016-02-13 | N | 205 | N | 5 | N | N | 1.1101 | 39.4971 | 4943.6625
[7 empty] | 11308 | 11014 | 1366981 | 2016-02-13 17:30 | 2016-02-13 18:13 | 43 | 11kV | 86 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 165983 A phase DOLF : 10 Amp Starlings Excluded OMS 1366981 | February | 2016 | 2016Q3 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2016-02-13 | N | 43 | N | 5 | N | N | 1.1101 | 39.4971 | 62.8463
[7 empty] | 10473 | 1663 | 1367021 | 2016-02-13 22:15 | 2016-02-14 01:23 | 188 | 11kV | 13912 | 74 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 165985 Burnt off tapping at ABS 5274 Aph source side. Opened 42023 at 0120hrs for safety, open 5274, closed 42023 & 4104. Excluded OMS 1367021. | February | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-02-13 | N | 188 | N | 5 | N | N | 1.1101 | 39.4971 | 10166.4793
[7 empty] | 10713 | 4545 | 1367037 | 2016-02-14 08:50 | 2016-02-14 10:30 | 100 | 11kV | 700 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 165987 Single phase DOLF : 5 Amp excluded OMS 1367037 & 1367039 | February | 2016 | 2016Q3 | 2016 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2016-02-14 | N | 100 | N | 7 | N | N | 1.1101 | 39.4971 | 511.5394
[7 empty] | 11675 | 14522 | 1367083 | 2016-02-14 14:47 | 2016-02-14 17:06 | 139 | 11kV | 22543 | 171 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn12580 Erina Panel 7 "North Gosford" fdr has tripped Signals: 11kv trip Relays: 51N (EF) EFI, FC, reclose timer? (No reclose on panel), LO EFI's: S18072 (S18675 failed to operate) UG fault between S18072 Sw/B & S18751 Sw/A See 1367261,3,4 exclude 1367083 | February | 2016 | 2016Q3 | 2016 | ZN12580:PA7 | ZN12580:PA7 | ZN12580/000007 | CENTRAL COAST | UG | Not Veg | 2016-02-14 | N | 131.8304 | N | 7 | N | N | 1.1101 | 39.4971 | 16473.7595
[7 empty] | 11155 | 9443 | 1367095 | 2016-02-14 15:46 | 2016-02-14 17:35 | 109 | 11kV | 13843 | 127 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 165991 2 fault operations Overcurrent UGOH Faulty leading to sub 3737 HMR Pump. NOTE ABS 4104 was closed due to a previous fault on ABS 5274. Excluded OMS 1367095 & 1367096 | February | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | Unknown | Unknown | 2016-02-14 | N | 109 | N | 7 | N | N | 1.1101 | 39.4971 | 10116.0561
[7 empty] | 12196 | 19810 | 1367031 | 2016-02-14 03:50 | 2016-02-14 18:00 | 850 | 11kV | 30746 | 65 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 165986 3 fault operations Single phase Earth fault 11kV OHM down between poles DT-73964 & DT-73965. C. Jones also found leaking TX at PT 54395. This Tx was replaced after restoring the rest of the feeer. excluded OMS 1367031 | February | 2016 | 2016Q3 | 2016 | 509:33444 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2016-02-14 | N | 473.0154 | N | 7 | N | N | 1.1101 | 39.4971 | 22468.2699
[7 empty] | 10689 | 4369 | 1367143 | 2016-02-14 19:38 | 2016-02-14 20:39 | 61 | 11kV | 61 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Ex Zn12630 Peats Ridge section of Pa1 "Grants Rd" fdr RE44994 Mangrove Creek has tripped Relays: Overcurrent trip and Lockout @LB44211 overcurrent detection AB phase Tree branch across two phases near PT14121 Boomerang Creek Portal See 367267,8 exclude 1367143 | February | 2016 | 2016Q3 | 2016 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2016-02-14 | N | 61 | N | 7 | N | N | 1.1101 | 39.4971 | 44.577
[7 empty] | 11278 | 10645 | 1367123 | 2016-02-14 18:01 | 2016-02-15 01:09 | 428 | 11kV | 13743 | 118 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 165990 3 fault operations A phase Overcurrent Faulty UGOH at pole GW-30299, Isolated & TA/P left. Excluded OMS 1367123 | February | 2016 | 2016Q3 | 2016 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | Unknown | Unknown | 2016-02-14 | N | 116.4661 | N | 7 | N | N | 1.1101 | 39.4971 | 10042.9791
[7 empty] | 11999 | 18070 | 1367167 | 2016-02-14 22:02 | 2016-02-15 12:15 | 853 | 11kV | 1706 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166002 C phase DOLF : 10 Amp Transformer volts = 244V Excluded OMS 1367167 | February | 2016 | 2016Q3 | 2016 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2016-02-14 | N | 853 | N | 7 | N | N | 1.1101 | 39.4971 | 1246.6945
[7 empty] | 10908 | 6754 | 1367274 | 2016-02-15 10:50 | 2016-02-15 13:20 | 150 | 11kV | 3300 | 22 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | Ex Zn847 Hornsby Pa45 11kV Roadside HDO replaced at PT654 Knights Chadd Cause: Fuse Fatigue See OMS 137601 1367343 1367274 | February | 2016 | 2016Q3 | 2016 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2016-02-15 | N | 150 | N | 5 | N | N | 1.1101 | 39.4971 | 2411.5427
[7 empty] | 10464 | 1507 | 1367282 | 2016-02-15 11:10 | 2016-02-15 14:03 | 173 | 11kV | 46369 | 801 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166001 2 fault operations Overcurrent; Earth Fault Truck hit OHM Excluded OMS 1367282 | February | 2016 | 2016Q3 | 2016 | 258:80791 | 258:80791 | ZN00258/080791 | NEWCASTLE | OH | Not Veg | 2016-02-15 | N | 57.8889 | N | 5 | N | N | 1.1101 | 39.4971 | 33885.0975
[7 empty] | 10855 | 6147 | 1367486 | 2016-02-15 17:38 | 2016-02-15 18:10 | 31.7 | 11kV | 2567.7 | 81 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 166013 A phase Top of DOLF burning carrier replaced | February | 2016 | 2016Q3 | 2016 | 205:12206 | 205:12206 | ZN00205/012206 | NEWCASTLE | OH | Not Veg | 2016-02-15 | N | 31.7 | N | 5 | N | N | 1.1101 | 39.4971 | 1876.3994
[7 empty] | 10727 | 4706 | 1367512 | 2016-02-15 18:49 | 2016-02-15 19:40 | 51 | 11kV | 153 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 166009 B Phase DOLF : 10 Amp 243 Volts Excluded OMS 1367512 | February | 2016 | 2016Q3 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2016-02-15 | N | 51 | N | 5 | N | N | 1.1101 | 39.4971 | 111.8079
[7 empty] | 11556 | 13221 | 1367545 | 2016-02-15 22:45 | 2016-02-16 01:58 | 193 | 11kV | 95342 | 494 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | At ZN3472 Sefton Section of 11kv feeder Ex panel 22 from S47490 Weenala Virgil sw/A to S7342 Waldron Campbell Hill Sw/B to IS2105 to S1100 Esme Hector Sw/A Abnormal: AB1867 closed, Sw/A open at S1100 Esme Hector open. Defective section of feeder from AB76 to S1100 Remarks: air break switch - details below. 11kv AB3272 was arcing, section of feeder from S47490 Weenala Virgil to S7342 Waldron Campbell Hill to IS2105 to AB1867 was interrupted for repairs to be carried out by lineworker | February | 2016 | 2016Q3 | 2016 | ZN3472:PA29 | ZN3472:PA29 | ZN03472/000029 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-02-15 | N | 193 | N | 5 | N | N | 1.1101 | 39.4971 | 69673.1215
[7 empty] | 11567 | 13339 | 1367592 | 2016-02-16 07:34 | 2016-02-16 09:17 | 103 | 11kV | 206 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 166022 A phase DOLF : 10 Amp DOLF carrier burnt up. Excluded OMS No. 1367592 | February | 2016 | 2016Q3 | 2016 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2016-02-16 | N | 103 | N | 9 | N | N | 1.1101 | 39.4971 | 150.5387
[7 empty] | 10647 | 3860 | 1367594 | 2016-02-16 07:37 | 2016-02-16 10:02 | 145 | 11kV | 342018 | 2423 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN3922 Drummoyne - 11kv Panel No.5 "Sub 36165, Sub 2401, Sub 1528 "feeder tripped" Relays: A phase timed O/C, EFI, Fault check relay Signals: 11kv trip, Zone Earth, No.2 Group Earth Field EFI's: Nil Remarks: UG fault. See possibly related outage on Pa.34 Leichhardt. Excavation near S2926 Apia Frazer | February | 2016 | 2016Q3 | 2016 | ZN3922:PA5 | ZN3922:PA5 | ZN03922/000005 | INNER WEST | UG | Not Veg | 2016-02-16 | N | 141.1548 | N | 9 | N | N | 1.1101 | 39.4971 | 249936.6666
[7 empty] | 11054 | 8083 | 1367612 | 2016-02-16 08:22 | 2016-02-16 10:05 | 103 | 11kV | 56576 | 596 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | @ZN35800 Bankstown - 11kv Panel No.6 "Sub 46101 Bankstown Aux No.1" feeder tripped Relays: Earth fault, EFI Signals: 11kv Trip, Tx 11 Group Earth Remarks: UG fault. 11kv ug feeder fault from S6110 Fairford Bryant to S7104 Arab Davies No.1 to S6674 Stuart Fairford | February | 2016 | 2016Q3 | 2016 | ZN35800:PA6 | ZN35800:PA6 | ZN35800/000006 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-02-16 | N | 94.9262 | N | 9 | N | N | 1.1101 | 39.4971 | 41344.0721
[7 empty] | 11023 | 7784 | 1367595 | 2016-02-16 07:40 | 2016-02-16 10:18 | 158 | 11kV | 275441 | 2050 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn116 leichhardt Panel No.34 "Balmain Derby" feeder tripped on Signals: 11kv Trip, Zone Earth, Tx2 Group Earth Relays: Pa334 Earth fault, EFI, B phase O/C, EFI Remarks: UG fault. See possibly related outage on Pa 5 Drummoyne. Excavation near S2926 | February | 2016 | 2016Q3 | 2016 | ZN116:PA34 | ZN116:PA12 | ZN00116/000012 | INNER WEST | UG | Not Veg | 2016-02-16 | N | 134.3615 | N | 9 | N | N | 1.1101 | 39.4971 | 201284.1587
[7 empty] | 11742 | 15296 | 1367926 | 2016-02-16 10:53 | 2016-02-16 11:31 | 38 | 11kV | 12084 | 318 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 166030 2 fault operations A phase Overcurrent termination failed on return of planned switching SI11013 Excluded OMS 1367694 | February | 2016 | 2016Q3 | 2016 | 235:2857 | 235:2857 | ZN00235/002857 | MAITLAND | Unknown | Unknown | 2016-02-16 | N | 38 | N | 9 | N | N | 1.1101 | 39.4971 | 8830.6308
[7 empty] | 10913 | 6782 | 1367730 | 2016-02-16 12:23 | 2016-02-16 13:10 | 47 | 11kV | 1504 | 32 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166031 C phase DOLF : 50 Amp Tx Volts ; 248V excluded OMS 1367730 | February | 2016 | 2016Q3 | 2016 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2016-02-16 | N | 47 | N | 9 | N | N | 1.1101 | 39.4971 | 1099.0788
[7 empty] | 10697 | 4401 | 1367777 | 2016-02-16 14:31 | 2016-02-16 15:15 | 44 | 11kV | 17952 | 408 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mountain" tripped on overcurrent and IOC Tree Down outside 200 ironbark See 1368162 exclude 1367777,8,96 | February | 2016 | 2016Q3 | 2016 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2016-02-16 | N | 44 | N | 9 | N | N | 1.1101 | 39.4971 | 13118.7921
[7 empty] | 11313 | 11065 | 1367830 | 2016-02-16 16:17 | 2016-02-16 17:56 | 99 | 11kV | 155348 | 2157 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | AT Sub 2835 Burwood, Panel 23 "Wentworth Hornsey" fdr opened on Earth fault with EFI and E/F check relays. Signals: 11kv trip, Zone earth and #1 and #2 Tx Group earth Remarks: UG fault. Fault between Sub49738 Shaftesbury Clarence and S5560 Clifton Shaftesbury No2 | February | 2016 | 2016Q3 | 2016 | ZN2835:PA23 | ZN4853:PA15 | ZN04853/000015 | BURWOOD | UG | Not Veg | 2016-02-16 | N | 72.0204 | N | 9 | N | N | 1.1101 | 39.4971 | 113523.7364
[7 empty] | 11878 | 16796 | 1367928 | 2016-02-16 16:58 | 2016-02-16 18:00 | 62 | 11kV | 682 | 11 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 166033 B Phase Jonathon Smith called the Control Room and said they had spotted the centre phase conductor broken away from its insulator and sitting on the x arm at pole FR-61517. No protection operated, interruption required to make safe. Excluded OMS 1367824 | February | 2016 | 2016Q3 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2016-02-16 | N | 62 | N | 9 | N | N | 1.1101 | 39.4971 | 498.3855
[7 empty] | 10399 | 409 | 1367889 | 2016-02-17 02:38 | 2016-02-17 04:43 | 125 | 11kV | 2000 | 16 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S2635 Epping Panel 33 tripped on Earth Fault, EFI, 11kV Trip Cause: UG cable fault in section of 11kVV feeder from S6151 SW/F to S7716 to S7488. | February | 2016 | 2016Q3 | 2016 | ZN2635:PA33 | ZN2635:PA33 | ZN02635/000033 | RYDE | UG | Not Veg | 2016-02-17 | N | 125 | N | 2 | N | N | 1.1101 | 39.4971 | 1461.541
[7 empty] | 11213 | 10026 | 1368015 | 2016-02-17 13:09 | 2016-02-17 20:05 | 416 | 11kV | 416 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166053 Single phase DOLF : 10 Amp 243 volts 6 amps Excluded oms 1368015 | February | 2016 | 2016Q3 | 2016 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2016-02-17 | N | 416 | N | 2 | N | N | 1.1101 | 39.4971 | 304.0005
[7 empty] | 10525 | 2352 | 1368122 | 2016-02-18 03:45 | 2016-02-18 05:05 | 80 | 11kV | 80 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166054 1 fault operation 3 phase Earth Fault | February | 2016 | 2016Q3 | 2016 |  |  |  | SINGLETON | OH | Veg | 2016-02-18 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 10951 | 7096 | 1369120 | 2016-02-18 08:10 | 2016-02-18 08:45 | 35 | 11kV | 35 | 1 | HV | Animal Flying Fox | Animal | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 166062 Earth Fault sw 43764 L/O E/FAULT. I.Obrien from liddell coal reported bat on liddell coal equipment. I.Obrien to investigate liddell coal protection equipment. | February | 2016 | 2016Q3 | 2016 |  |  |  | SINGLETON | OH | Not Veg | 2016-02-18 | N | 35 | N | 5 | N | N | 1.1101 | 39.4971 | 25.577
[7 empty] | 10775 | 5234 | 1368176 | 2016-02-18 11:41 | 2016-02-18 13:10 | 89 | 11kV | 41617 | 1169 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | @ZN1290 Leightonfield 11kv Panel #4 labelled "S3374 MacKenzie Vic" tripped: Relays: C phase IOC & timed, A phase timed O/C & IOC, Rec timed & lockout, EFI Signals: 11kv trip, Zone earth, Tx1 Group earth, Tx3 Group earth, 11kv CB4 open field EFI's Remarks: vehicle hit pole. Wires down outside 11 Mundamatta Street Villawood | February | 2016 | 2016Q3 | 2016 | ZN1290:PA4 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-02-18 | N | 35.6005 | N | 5 | N | N | 1.1101 | 39.4971 | 30412.4761
[7 empty] | 11549 | 13098 | 1368198 | 2016-02-18 11:14 | 2016-02-18 15:14 | 240 | 11kV | 29031 | 167 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 166069 3 fault operations A & C phase Overcurrent; Earth Fault 11KV MAINS DOWN AT POLE 8K-60326.HIT BY TRUCK.MAINS TO SUB 72729 LEFT ISOLATED.SUB NOT REQUIRED.(MINE SITE) | February | 2016 | 2016Q3 | 2016 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2016-02-18 | N | 173.8383 | N | 5 | N | N | 1.1101 | 39.4971 | 21214.9985
[7 empty] | 12246 | 20377 | 1368426 | 2016-02-18 20:50 | 2016-02-19 00:35 | 225 | 11kV | 61650 | 274 | HV | Staff Operation | Utility Process Issue | U/G Link | Unplanned | No Weather Impact | N | Section of Panel 24 ex Mosman Zone. From S4930 Kameruka The outpost to S49722 Minnamurra Courallie, section of feeder was left energised via LV // after works. Customers experienced voltage issues. | February | 2016 | 2016Q3 | 2016 | ZN180:PA24 | ZN180:PA24 | ZN00180/000024 | WILLOUGHBY | UG | Not Veg | 2016-02-18 | N | 225 | N | 5 | N | N | 1.1101 | 39.4971 | 45052.0016
[7 empty] | 11726 | 15149 | 1368443 | 2016-02-19 08:00 | 2016-02-19 09:15 | 75 | 11kV | 75 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | PT9764 Captain Cook Amatek was interrupted to carry out urgent repairs to AB35183 (burnt bond), to be able to restore supply to section of interrupted feeder. Sections of 11kv Panel 18 "S48890 Kurnell Aux No.1" feeder @ Zn9534 Kurnell Sth See seperate 11kv interruption Cronulla Diagram Ref 1F6. Defective 11kv fdr from S9601 to S9820 to S65467 to S9775 tee S9629 Remarks: other - details provided. Urgent repairs to restore supply | February | 2016 | 2016Q3 | 2016 | ZN9534:PA18 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2016-02-19 | N | 75 | N | 6 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 12223 | 20147 | 1368434 | 2016-02-19 04:29 | 2016-02-19 09:25 | 296 | 11kV | 247154 | 1906 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9118 Cronulla - Pnl.15 tripped, reclosed and tripped on: B Phase O/C, E/F, EFI, Lockout & Timing. Field EFIs: S9386 S9290 S9771 S9770 S9601 Abnormal: IS35910 Closed - AB35183 OPEN (Kurnell Sht 1 C/7) First restore attempt failed - tripped again on: Earth leakge, EFI UG cable fault from S9601 to S9820 to S65467 to S9775 tee to S9629. (S9629 restored via LV //'s 1512, 147, 67) See 1369276 1369277 1369278 1369279 | February | 2016 | 2016Q3 | 2016 | ZN9118:PA15 | ZN9118:PA15 | ZN09118/000015 | SUTHERLAND | UG | Not Veg | 2016-02-19 | N | 129.6716 | N | 6 | N | N | 1.1101 | 39.4971 | 180612.8534
[7 empty] | 10369 | 16 | 1368521 | 2016-02-19 12:30 | 2016-02-19 14:52 | 142 | 11kV | 994 | 7 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 166083 Repair conductor on crossarm at pole 7k-70012 | February | 2016 | 2016Q3 | 2016 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2016-02-19 | N | 142 | N | 6 | N | N | 1.1101 | 39.4971 | 726.3859
[7 empty] | 12118 | 19084 | 1368549 | 2016-02-19 14:31 | 2016-02-19 15:49 | 78 | 11kV | 72774 | 933 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 166087 A phase Overcurrent abs 10848 burnt up contacts flashed over Excluded oms 1368549 | February | 2016 | 2016Q3 | 2016 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Not Veg | 2016-02-19 | N | 78 | N | 6 | N | N | 1.1101 | 39.4971 | 53181.0927
[7 empty] | 11735 | 15213 | 1368581 | 2016-02-19 15:35 | 2016-02-19 17:30 | 115 | 11kV | 460 | 4 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 166085 section isolated to repair crossarm at pole BM-20092 | February | 2016 | 2016Q3 | 2016 | 514:18146 | 514:18156 | ZN00514/018156 | MUSWELLBROOK | OH | Not Veg | 2016-02-19 | N | 115 | N | 6 | N | N | 1.1101 | 39.4971 | 336.1544
[7 empty] | 11174 | 9641 | 1368556 | 2016-02-19 14:51 | 2016-02-19 17:54 | 183 | 11kV | 247151 | 1402 | HV | Burnt Contacts | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | At Zn10997 Sans Souci Panel 12 "LK 30382" tripped, reclosed and locked out on: Signals: 11kv trip Relays: IOC, EFI, Reclose timing, Reclose lockout Remarks: US. The centre phase of the 11kv LK 30385 was found to have a cracked and burnt insulator | February | 2016 | 2016Q3 | 2016 | ZN10997:PA12 | ZN10997:PA12 | ZN10997/000012 | BAYSIDE | OH | Not Veg | 2016-02-19 | N | 176.2846 | N | 6 | N | N | 1.1101 | 39.4971 | 180610.6611
[7 empty] | 10955 | 7133 | 1368745 | 2016-02-20 15:12 | 2016-02-20 16:50 | 98 | 11kV | 196 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166091 Single phase DOLF 10 Amp Transformer volts = 245V | February | 2016 | 2016Q3 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2016-02-20 | N | 98 | N | 5 | N | N | 1.1101 | 39.4971 | 143.231
[7 empty] | 10733 | 4792 | 1368741 | 2016-02-20 14:48 | 2016-02-20 17:40 | 172 | 11kV | 516 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 166092 REPAIR BROKEN LIVE LINE LEAD TO DOLF. Excluded OMS REPORT NO 1368741. | February | 2016 | 2016Q3 | 2016 | 512:48048 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2016-02-20 | N | 172 | N | 5 | N | N | 1.1101 | 39.4971 | 377.0776
[7 empty] | 11176 | 9669 | 1368758 | 2016-02-20 16:42 | 2016-02-20 17:50 | 68 | 11kV | 68 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166093 B Phase DOLF : 3 Amp STARLING AT B PH ARRESTOR Excluded OMS REPORT NO 1368758. | February | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-02-20 | N | 68 | N | 5 | N | N | 1.1101 | 39.4971 | 49.6924
[7 empty] | 10898 | 6567 | 1369148 | 2016-02-20 16:02 | 2016-02-20 19:50 | 228 | 11kV | 3735 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 166095 Overcurrent LINE PATROLLED NO FAULT FOUND. | February | 2016 | 2016Q3 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2016-02-20 | N | 177.8571 | N | 5 | N | N | 1.1101 | 39.4971 | 2729.4278
[7 empty] | 11714 | 15053 | 1368784 | 2016-02-20 19:40 | 2016-02-20 21:15 | 95 | 11kV | 95 | 1 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166096 C phase DOLF : 10 Amp Cleared palm tree from hitting L/A. Reolaced 10A for 10A. Readings as left = 241V, 242V, 241V @ 0A Excluded OMS 1368784 | February | 2016 | 2016Q3 | 2016 | 238:34150 | 238:34150 | ZN00238/034150 | NEWCASTLE | OH | Veg | 2016-02-20 | N | 95 | N | 5 | N | N | 1.1101 | 39.4971 | 69.4232
[7 empty] | 12230 | 20243 | 1368818 | 2016-02-21 03:01 | 2016-02-21 04:10 | 69 | 11kV | 99498 | 1442 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Zn10995 Riverwood - Pnl.5 - tripped, reclosed, tripped and locked out on: A Phase itmed O/C, A Phase IOC, EFI No cause found. Possibly weather related | February | 2016 | 2016Q3 | 2016 | ZN10995:PA5 | ZN10995:PA5 | ZN10995/000005 | GEORGES RIVER | OH | Veg | 2016-02-21 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 72710.2037
[7 empty] | 11767 | 15572 | 1368965 | 2016-02-21 15:10 | 2016-02-21 17:30 | 140 | 11kV | 560 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 166101 B phase DOLF : 16 Amp Excluded OMS 1368965 | February | 2016 | 2016Q3 | 2016 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2016-02-21 | N | 140 | N | 3 | N | N | 1.1101 | 39.4971 | 409.2315
[7 empty] | 10854 | 6138 | 1368953 | 2016-02-21 14:00 | 2016-02-21 22:55 | 535 | 11kV | 34021 | 187 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166100 1 fault operation Sensitive Earth Fault tree on mains at pole 8M-82202 Burrulong Valley. , supply restored & Blown tapping found, Isolated to make repairs. Excluded OMS OMS 1369021; 1368953,1368967& 1368989. | February | 2016 | 2016Q3 | 2016 | 509:33444 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-02-21 | N | 181.9305 | N | 3 | N | N | 1.1101 | 39.4971 | 24861.5434
[7 empty] | 10827 | 5778 | 1369031 | 2016-02-22 03:48 | 2016-02-22 08:40 | 292 | 11kV | 9953 | 52 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166103 3 fault operations A & B phase Overcurrent Excluded OMS 1369031 | February | 2016 | 2016Q3 | 2016 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Veg | 2016-02-22 | N | 191.4038 | N | 2 | N | N | 1.1101 | 39.4971 | 7273.3588
[7 empty] | 10755 | 5023 | 1369283 | 2016-02-22 15:39 | 2016-02-22 16:53 | 74 | 11kV | 63192 | 930 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2435 Castle Cove Panel 17 tripped on relays: timed earth fault. EFI and Fault Check Cause: UG cable fault from S2435 to S35061 to S35214 See OMS 1370574 1369283 | February | 2016 | 2016Q3 | 2016 | ZN3425:PA17 | ZN3425:PA17 | ZN03425/000017 | WILLOUGHBY | UG | Not Veg | 2016-02-22 | N | 67.9484 | N | 2 | N | N | 1.1101 | 39.4971 | 46178.8498
[7 empty] | 11969 | 17677 | 1369508 | 2016-02-23 12:58 | 2016-02-23 14:30 | 92 | 11kV | 4082 | 50 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14143 Somersby Panel 6 "Pinnacle Triennium' tripped Relays: EF, TX1 EF check flag, EFI Signals: Tx1 Group Earth, EFI, 11kv trip UG Fdr fault from S18454 to S18253. Due to SCADA issues at Somersby Zone DOp had to drive to and from Zone several times to switch feeder back on as protection was required to be set up. See 1369742,3,4 exclude 1369508 | February | 2016 | 2016Q3 | 2016 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | UG | Not Veg | 2016-02-23 | N | 81.64 | N | 2 | N | N | 1.1101 | 39.4971 | 2983.0052
[7 empty] | 12078 | 18741 | 1369556 | 2016-02-23 15:28 | 2016-02-23 16:50 | 82.1 | 11kV | 5993.3 | 73 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT48828 Ulooloo Aldinga centre phase HDO open cct 63Amp Fuse fatigue See 1369556 exclude 1369561,79 | February | 2016 | 2016Q3 | 2016 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Not Veg | 2016-02-23 | N | 82.1 | N | 2 | N | N | 1.1101 | 39.4971 | 4379.7269
[7 empty] | 12169 | 19593 | 1369678 | 2016-02-24 07:49 | 2016-02-24 11:25 | 216 | 11kV | 216 | 1 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166150 Dead possum found at sub Replaced 5 Amp HV DOLF at tx 7113 . Possum cause of blown fuse | February | 2016 | 2016Q3 | 2016 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2016-02-24 | N | 216 | N | 5 | N | N | 1.1101 | 39.4971 | 157.8464
[7 empty] | 11854 | 16561 | 1369785 | 2016-02-24 12:30 | 2016-02-24 14:25 | 115 | 11kV | 115 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Replaced 10 Amp HV fuse on C phase . Birds cause of blown fuse Customer reports fuse has dropped out on pole AI20011, 71990. irrigation pump | February | 2016 | 2016Q3 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-02-24 | N | 115 | N | 5 | N | N | 1.1101 | 39.4971 | 84.0386
[7 empty] | 11395 | 11814 | 1369864 | 2016-02-24 14:53 | 2016-02-24 16:48 | 115 | 11kV | 4968 | 538 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 166156 2 fault operations Instantaneous Overcurrent; Instantaneous Earth Fault UGOH pole DP-70265 Excluded OMS 1369864 | February | 2016 | 2016Q3 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | Unknown | Unknown | 2016-02-24 | N | 9.2342 | N | 5 | N | N | 1.1101 | 39.4971 | 3630.4679
[7 empty] | 11175 | 9661 | 1369990 | 2016-02-24 20:19 | 2016-02-24 21:15 | 56 | 11kV | 280 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 166158 Phase C - Fuse Size 20 Amp, Substation DOLF, Fuses Incorrect Operation, DOLF Faulty - burnt out carrier Customer Reports - TRANSFORMER ON FIRE - FIRE BRIGADE ON SIGHT ADVISED BY FIRE BRIGADE GRAHAEM | February | 2016 | 2016Q3 | 2016 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2016-02-24 | N | 56 | N | 5 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 11369 | 11627 | 1369907 | 2016-02-24 20:35 | 2016-02-24 21:25 | 50 | 11kV | 100 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166157 interrupt to repair tapping pole FO-20196 fluctuating supply. Excluded oms 1369907 | February | 2016 | 2016Q3 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2016-02-24 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 11248 | 10398 | 1370016 | 2016-02-25 03:23 | 2016-02-25 04:15 | 52 | 11kV | 106548 | 2049 | HV | Animal Flying Fox | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill - Pnl.3 - Tripped on: Earth leakage Field EFIs: S3149 & S3034 Flash over caused by Bat at Q type PT1156 Eltham Vic. No apparent damage. | February | 2016 | 2016Q3 | 2016 | ZN398:PA3 | ZN398:PA3 | ZN00398/000003 | INNER WEST | OH | Not Veg | 2016-02-25 | N | 52 | N | 4 | N | N | 1.1101 | 39.4971 | 77862.1358
[7 empty] | 11603 | 13759 | 1370019 | 2016-02-25 04:23 | 2016-02-25 05:27 | 64 | 11kV | 31348 | 723 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ex 11kV Panel 28 Castle Cove AB3229 roadside bond blown off See OMS 1370562 1370563 1370019 | February | 2016 | 2016Q3 | 2016 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | OH | Not Veg | 2016-02-25 | N | 43.3582 | N | 4 | N | N | 1.1101 | 39.4971 | 22908.1938
[7 empty] | 10481 | 1743 | 1370176 | 2016-02-25 14:47 | 2016-02-25 16:20 | 93 | 11kV | 112473 | 1225 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn690 Campsie - Pnl.10 - tripped on: Earth Leakage, fault check and EFI EFI @ CP571 UG cable fault from CP571 to S6622 tee S6160 See 1370329 1370505 CC1: 23-"Mains Required" FRC1: 325-"No Supply at Service Fuse -POA Inaccessible-No Other Services affected -Linesman required" | February | 2016 | 2016Q3 | 2016 | ZN690:PA10 | ZN690:PA10 | ZN00690/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-02-25 | N | 91.8147 | N | 4 | N | N | 1.1101 | 39.4971 | 82191.951
[7 empty] | 11584 | 13539 | 1370242 | 2016-02-25 16:11 | 2016-02-25 17:00 | 49 | 11kV | 49 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 166170 A phase DOLF : 10 Amp | February | 2016 | 2016Q3 | 2016 | 509:33444 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-02-25 | N | 49 | N | 4 | N | N | 1.1101 | 39.4971 | 35.8078
[7 empty] | 10404 | 533 | 1370390 | 2016-02-26 06:16 | 2016-02-26 09:15 | 179 | 11kV | 2864 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166181 B Phase DOLF : 16 Amp | February | 2016 | 2016Q3 | 2016 | 217:33612 | 217:33605 | ZN00217/033605 | LAKE MACQUARIE | OH | Veg | 2016-02-26 | N | 179 | N | 5 | N | N | 1.1101 | 39.4971 | 2092.9267
[7 empty] | 10472 | 1637 | 1370388 | 2016-02-26 06:00 | 2016-02-26 11:15 | 315 | 11kV | 945 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 166176 Single phase Broken LL Clamp lead. Excluded OMS No. 1370388 | February | 2016 | 2016Q3 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2016-02-26 | N | 315 | N | 5 | N | N | 1.1101 | 39.4971 | 690.5781
[7 empty] | 11498 | 12697 | 1370451 | 2016-02-26 09:13 | 2016-02-26 13:40 | 267 | 11kV | 171900 | 1666 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Insulated | Unplanned | No Weather Impact | N | At S12640 Umina Panel 10 has tripped on Relays: 11kV protection tirp, C phase timed OC, IOC earthf ault, Times earth fault, Lockout Cause: tree has fallen into mains near AB43662. See OMS 1371074 1371075 1371077 13710476 1370451 | February | 2016 | 2016Q3 | 2016 | ZN12640:PA10 | ZN12640:PA10 | ZN12640/000010 | CENTRAL COAST | OH | Veg | 2016-02-26 | N | 103.1813 | N | 5 | N | N | 1.1101 | 39.4971 | 125619.4498
[7 empty] | 12192 | 19768 | 1370662 | 2016-02-26 21:37 | 2016-02-26 22:23 | 46 | 11kV | 55936 | 1216 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | Snow / Hail Storm | N | At Zn12690 Berkeley Vale Panel 19 Tripped on Relays: IOC and EFI Signals: 11kV trip, IOC trip and EFI. TX12 Group Earth and Under Voltage Alarm. Cause: Possum on 11kV UGOH below PT18115. | February | 2016 | 2016Q3 | 2016 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Not Veg | 2016-02-26 | N | 46 | N | 5 | N | N | 1.1101 | 39.4971 | 40876.379
[7 empty] | 11382 | 11751 | 1370661 | 2016-02-26 21:31 | 2016-02-26 22:58 | 87 | 11kV | 282802 | 3848 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | Zn15006 Dee Why West - Pnl.9 tripped on: B Phase O/C, Fault Check, EFI Field EFIs: All down to S16745 Abnormal: S16676 Sw/B closed with S16592 Sw/A open End box failure at S15403 Dee Why RSL See 1370978 1370980 | February | 2016 | 2016Q3 | 2016 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | Unknown | Not Veg | 2016-02-26 | N | 73.4932 | N | 5 | N | N | 1.1101 | 39.4971 | 206663.3604
[7 empty] | 10907 | 6739 | 1370689 | 2016-02-27 05:59 | 2016-02-27 08:07 | 128 | 11kV | 113551 | 905 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn10994 Mortdale Panel 19 Tripped Reclosed Tripped on IOC, IOC E/F, EFI, Reclose Note: Panel 19 Tripped a further 2 more times upon restoration. Cause: Suspected UGOH fault below SW/B at S10954 See OMS 1371184 1371185 1370689 1370699 | February | 2016 | 2016Q3 | 2016 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | Unknown | Unknown | 2016-02-27 | N | 125.4707 | N | 3 | N | N | 1.1101 | 39.4971 | 82979.7216
[7 empty] | 11067 | 8269 | 1370748 | 2016-02-27 14:29 | 2016-02-27 15:57 | 88 | 11kV | 230910 | 2658 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | At S4545 Meadowbank 11kV panel 42 tripped on Relays: Sensitive Earth Signals: 11kV Trip Cause: Interrupter Switch No180 has failed. SW/B closed at S8740 AB1965 Open See OMS 1371673 1371672 1370749 1370748 | February | 2016 | 2016Q3 | 2016 | ZN4545:PA40 | ZN4545:PA40 | ZN04545/000040 | RYDE | OH | Not Veg | 2016-02-27 | N | 86.8736 | N | 3 | N | N | 1.1101 | 39.4971 | 168742.2173
[7 empty] | 11985 | 17932 | 1371023 | 2016-02-27 20:45 | 2016-02-27 23:00 | 135 | 11kV | 1350 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166198 C Phase DOLF : 16 Amp | February | 2016 | 2016Q3 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-02-27 | N | 135 | N | 3 | N | N | 1.1101 | 39.4971 | 986.5402
[7 empty] | 10439 | 1115 | 1370810 | 2016-02-28 00:55 | 2016-02-28 02:43 | 108 | 11kV | 4862 | 52 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S3472 Seefton Panel 18 "Chisolm Marjorie" feeder tripped on: C phase IOC EFI Reclose time delay lockout Field EFI: down to S1256 Remarks: tree branch contact. Removed by Dop | February | 2016 | 2016Q3 | 2016 | ZN3472:PA18 | ZN3472:PA18 | ZN03472/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-02-28 | N | 93.5 | N | 3 | N | N | 1.1101 | 39.4971 | 3553.0062
[7 empty] | 10490 | 1876 | 1370957 | 2016-02-28 08:17 | 2016-02-28 09:30 | 73 | 11kV | 146 | 2 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166199 C phase DOLF : 10 Amp Bird | February | 2016 | 2016Q3 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2016-02-28 | N | 73 | N | 3 | N | N | 1.1101 | 39.4971 | 106.6925
[7 empty] | 11092 | 8653 | 1370820 | 2016-02-28 07:37 | 2016-02-28 11:20 | 223 | 11kV | 223 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT13206 Brush Creek Yarramalong 11kV Centre Phase 16A Drop Out fiuses operated. Cause: Fuse Fatigue see OMS 1371189 1370820 | February | 2016 | 2016Q3 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2016-02-28 | N | 223 | N | 3 | N | N | 1.1101 | 39.4971 | 162.9618
[7 empty] | 10978 | 7407 | 1371200 | 2016-02-29 16:06 | 2016-02-29 16:55 | 49 | 11kV | 147 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166213 Single phase DOLF : 10 Amp Dead starling found at sub. Excluded OMS No. 1371200 | February | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-02-29 | N | 49 | N | 2 | N | N | 1.1101 | 39.4971 | 107.4233
[7 empty] | 11968 | 17669 | 1371283 | 2016-02-29 19:35 | 2016-02-29 19:42 | 7 | 11kV | 539 | 77 | HV | Equipment Failed in Service | Equipment Failure | Tap Changer | Unplanned | No Weather Impact | N | LID 166214 Fdr interrupted to bypass Burralong reg which is stuck on tap +16. Customers beyond had high volts beyond emergency limit (262V). | February | 2016 | 2016Q3 | 2016 | 509:33444 | 509:33395 | ZN00509/033395 | CESSNOCK | Unknown | Not Veg | 2016-02-29 | N | 7 | N | 2 | N | N | 1.1101 | 39.4971 | 393.8853
[7 empty] | 11747 | 15350 | 1371270 | 2016-03-01 03:50 | 2016-03-01 05:05 | 75 | 11kV | 90630 | 1237 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn847 Hornsby panel 23 tripped reclosed tripped and locked out on Relays: A phase overcurrent, Earth fault, reclose timer, lockout, Fault check Signals; TX2 Group Earth, Zone Earth, 11kV Trip Cause: UG feeder fault from S7795SW/F to S6978 Hunter Florence NO2 SW/A See OMS 1371700 1371701 1371270 | March | 2016 | 2016Q3 | 2016 | ZN847:PA23 | ZN847:PA23 | ZN00847/000023 | HORNSBY | UG | Not Veg | 2016-03-01 | N | 73.266 | N | 2 | N | N | 1.1101 | 39.4971 | 66229.7309
[7 empty] | 11385 | 11763 | 1371415 | 2016-03-01 13:30 | 2016-03-01 15:30 | 120 | 11kV | 6840 | 57 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 166227 3 phase Section isolated to repair UGOH pole OS-20183. Excluded OMS 1371308 & 1371415. | March | 2016 | 2016Q3 | 2016 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | Unknown | Unknown | 2016-03-01 | N | 120 | N | 2 | N | N | 1.1101 | 39.4971 | 4998.4703
[7 empty] | 11219 | 10058 | 1371533 | 2016-03-02 02:22 | 2016-03-02 04:36 | 134 | 11kV | 288502 | 2153 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | Zn12620 Noraville Zone Panel 7 "Fravent st" tripped on: 51 B & C phase overcurrent 415 change over SW 11kv trip Dead Possum at 11kv USL 43751. Note: DOp could not close panel & TPE were required See 1373556 exclude 1371533,6 | March | 2016 | 2016Q3 | 2016 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | OH | Not Veg | 2016-03-02 | N | 134 | N | 5 | N | N | 1.1101 | 39.4971 | 210828.7522
[7 empty] | 10568 | 2821 | 1371543 | 2016-03-02 06:32 | 2016-03-02 08:09 | 97 | 11kV | 69549 | 717 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn15001 Brookevale - Pnl.18L - LK21622 footpath side bond burnt off. Start time taken from load trend | March | 2016 | 2016Q3 | 2016 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | OH | Not Veg | 2016-03-02 | N | 97 | N | 5 | N | N | 1.1101 | 39.4971 | 50824.3579
[7 empty] | 11445 | 12214 | 1371532 | 2016-03-02 02:26 | 2016-03-02 09:45 | 439.1167 | 11kV | 38642.2667 | 88 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At CP3227 Berowra Creek tripped and locked out Cause: OH mains to remove vine off pole behind No42 beriwra Creek | March | 2016 | 2016Q3 | 2016 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2016-03-02 | N | 439.1167 | N | 5 | N | N | 1.1101 | 39.4971 | 28238.6287
[7 empty] | 11569 | 13362 | 1371794 | 2016-03-02 19:53 | 2016-03-02 21:40 | 107 | 11kV | 428 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166246 B Phase DOLF : 10 Amp LV Damaged at sub 53571 | March | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-03-02 | N | 107 | N | 5 | N | N | 1.1101 | 39.4971 | 312.7698
[7 empty] | 12168 | 19583 | 1371798 | 2016-03-02 21:15 | 2016-03-03 01:00 | 225 | 11kV | 75673 | 1035 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 166248 Sw 33600 opened by S.O. Faulty xarm at pole SW-50429.Found 11kv cross arm spapped and on fire. Excluded OMS 1371809 | March | 2016 | 2016Q3 | 2016 | 222:33600 | 222:33600 | ZN00222/033600 | LAKE MACQUARIE | OH | Not Veg | 2016-03-02 | N | 73.114 | N | 5 | N | N | 1.1101 | 39.4971 | 55299.5964
[7 empty] | 10764 | 5105 | 1371841 | 2016-03-03 08:04 | 2016-03-03 11:35 | 211 | 11kV | 211 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa12 "Yarramalong" PT13206 Bursh creek Yarramalong 3.9 11kv HDO roadside fuse fell out of fuse carrier See 1373540 exclude 1371841 | March | 2016 | 2016Q3 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2016-03-03 | N | 211 | N | 2 | N | N | 1.1101 | 39.4971 | 154.1926
[7 empty] | 11885 | 16852 | 1372112 | 2016-03-03 22:40 | 2016-03-03 23:55 | 75.1833 | 11kV | 3683.9833 | 49 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT39 Waterhouse Torrens - 11kV footpath phase HDO 31.5A fuse blown Fuse fatigue See 1372112 GIS: 1372113 | March | 2016 | 2016Q3 | 2016 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Not Veg | 2016-03-03 | N | 75.1833 | N | 2 | N | N | 1.1101 | 39.4971 | 2692.1464
[7 empty] | 10958 | 7155 | 1372336 | 2016-03-04 19:23 | 2016-03-04 20:50 | 87 | 11kV | 36627 | 481 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | No Weather Impact | N | At S1673 Turramurra ZOne Panel 9 tripped on Relays: INST O/C and EFI Field EFI's - NIL Cause: Tree branch contact burnt branch found at PT 30 - Damage to PT See OMS 1373342 1373345 1372316 | March | 2016 | 2016Q3 | 2016 | ZN1673:PA9 | ZN1673:PA9 | ZN01673/000009 | KU-RING-GAI | OH | Veg | 2016-03-04 | N | 76.1476 | N | 1 | N | N | 1.1101 | 39.4971 | 26765.9313
[7 empty] | 11929 | 17211 | 1372498 | 2016-03-05 20:26 | 2016-03-05 21:43 | 77 | 11kV | 375790 | 8174 | HV | Animal Possum | Animal | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S9700 Kirrawee Zn Tx3A 11kv CB tripped on A protection EF check relay P 23 the talara kingsway fdr relay indication EFI flag on the OC and EF relay Abnormal: P18 open (oos) Sw/B closed at S9544, P21 open (oos) sw/B closed at S49934 Sw/A open at S9458 with Sw/B closed at S9811 Remarks: Protection malfunction. Possum on ugoh to S9505 Manchester Nyinya (sw/B), P23 CB "Talara Kingsway fdr" | March | 2016 | 2016Q3 | 2016 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Not Veg | 2016-03-05 | N | 45.9738 | N | 2 | N | N | 1.1101 | 39.4971 | 274616.2481
[7 empty] | 12108 | 19012 | 1372503 | 2016-03-05 20:48 | 2016-03-05 22:13 | 85 | 11kV | 510 | 6 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT14302 Wattle Tree Knox - 11kV HDO blown on footpath phase (10Amp) Possum at PT14302. | March | 2016 | 2016Q3 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2016-03-05 | N | 85 | N | 2 | N | N | 1.1101 | 39.4971 | 372.693
[7 empty] | 11759 | 15459 | 1372521 | 2016-03-06 00:03 | 2016-03-07 10:03 | 2039.55 | 11kV | 271076 | 1159 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166276 Possum. High into low at pole JU-65040. Note: LVL 45358 where found closed which was back feeding into 11kV fdr 34250. Excluded oms1372521/22. | March | 2016 | 2016Q3 | 2016 | 202:34250 | 202:34250 | ZN00202/034250 | NEWCASTLE | OH | Not Veg | 2016-03-06 | N | 233.8878 | N | 1 | N | N | 1.1101 | 39.4971 | 198094.3454
[7 empty] | 11479 | 12585 | 1372891 | 2016-03-07 18:38 | 2016-03-07 23:10 | 272 | 11kV | 544 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166300 Single phase broken LLC dropper Excluded OMS 1372891 | March | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2016-03-07 | N | 272 | N | 1 | N | N | 1.1101 | 39.4971 | 397.5392
[7 empty] | 10612 | 3404 | 1372952 | 2016-03-08 05:52 | 2016-03-08 08:04 | 132 | 11kV | 2586 | 1293 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166314 2 fault operations A & C phase Overcurrent Bat removed from OHM at pole FS-92874 Excluded OMS 1372952, 1372960 | March | 2016 | 2016Q3 | 2016 |  |  |  | CESSNOCK | OH | Not Veg | 2016-03-08 | N | 2 | N | 4 | N | N | 1.1101 | 39.4971 | 1889.7725
[7 empty] | 11113 | 8827 | 1373015 | 2016-03-08 10:28 | 2016-03-08 11:15 | 47 | 11kV | 47 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166315 C phase DOLF : 10 Amp Dead owl found on site Replaced HV fuse Excluded OMS 1373015 | March | 2016 | 2016Q3 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2016-03-08 | N | 47 | N | 4 | N | N | 1.1101 | 39.4971 | 34.3462
[7 empty] | 11070 | 8309 | 1373249 | 2016-03-08 10:35 | 2016-03-08 16:33 | 358 | 11kV | 358 | 1 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S7972 Hume Tennyson, Dop Mote found switch "C" open, #3 TX ACB open, with translay relay operation IT send and EFI. At S7215 Muir Hume, Dop found switch "A" open with #1 Tx ACB still closed and battery with "0" volts. At S7850 Hume Shellcote No3, still alive via LV at S7215. Load 700A per LV phase, volts 234, 236, 235 Remarks: Ug fault. UG cable fault between S7850 and S7215, failure of LV ACB to trip at S7215 | March | 2016 | 2016Q3 | 2016 | ZN1285:PA34 | ZN1285:PA34 | ZN01285/000034 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-03-08 | N | 358 | N | 4 | N | N | 1.1101 | 39.4971 | 261.6158
[7 empty] | 11282 | 10692 | 1373160 | 2016-03-08 22:53 | 2016-03-09 00:45 | 112 | 11kV | 109557 | 1226 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 Matraville Pnl.37 tripped on: Earth Fault Abnormal: S2672 9Sw/B) closed with S892 (Sw/A) Open. For Fuse switch replacement at S2208 UG cable fault from Panel 37 to S35450 (Sw/A) to S2672 (Sw/B) See 1373219 GIS: 1373167 | March | 2016 | 2016Q3 | 2016 | ZN1788:PA37 | ZN1788:PA70 | ZN01788/000070 | RANDWICK | UG | Not Veg | 2016-03-08 | N | 89.3613 | N | 4 | N | N | 1.1101 | 39.4971 | 80061.0242
[7 empty] | 10627 | 3657 | 1373201 | 2016-03-09 08:00 | 2016-03-09 11:50 | 230 | 11kV | 195671 | 1429 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn9245 Engadine - Pnl.33 tripped on: SEL & Lockout Abnormal: AB35873 Closed with AB35951 Open Bond on footpath phase failed beyond AB35873 See 1373537 1373538 1373539 | March | 2016 | 2016Q3 | 2016 | ZN9245:PA33 | ZN9245:PA15 | ZN09245/000015 | SUTHERLAND | OH | Not Veg | 2016-03-09 | N | 136.9286 | N | 5 | N | N | 1.1101 | 39.4971 | 142990.5955
[7 empty] | 11654 | 14297 | 1373292 | 2016-03-09 11:22 | 2016-03-09 13:40 | 137.75 | 11kV | 13912.75 | 101 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 166331 A phase Earth Fault tree branch fallen on mains pole 9T-90047 REMOVED FDR RESTORED Tree fell into mains causing fire to start under mains. Tree removed with insulated height stick and feeder restored. | March | 2016 | 2016Q3 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2016-03-09 | N | 137.75 | N | 5 | N | N | 1.1101 | 39.4971 | 10167.0273
[7 empty] | 10580 | 2959 | 1373397 | 2016-03-09 15:54 | 2016-03-09 17:34 | 100 | 11kV | 32616 | 329 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 12 the Sirius Lane Cove Fdr Tripped on Earth Fault, Fault Check and EFI Abnormal switching: Pa21 OOS, SW/B closed at S8023, SW/A open At S35155, SW/B closed at S2944, SW/D Open At S5233, SW/A closed at S8291. Cause: UG cable fault. S7684 to S35155 to S7878. See OMS 1376663 1376665 1376666 1373397 1373401 | March | 2016 | 2016Q3 | 2016 | ZN129:PA12 | ZN129:PA56 | ZN00129/000056 | LANE COVE | UG | Not Veg | 2016-03-09 | N | 99.1368 | N | 5 | N | N | 1.1101 | 39.4971 | 23834.8108
[7 empty] | 12250 | 20415 | 1373364 | 2016-03-09 14:44 | 2016-03-09 17:39 | 175 | 11kV | 239762 | 1930 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1285 Greenacre Park 11kv {anel 31 "Anzac Dominion etc" fdr tripped on earth fault with reclose timing and lock out Signals: 11kv trip with EFI EFI's: Nil Cable fault from Zn1285 Greenacre Park to S5729 to S4862 tee to PT1576 Panel 31 relays not labelled correctly to indicate left or right panels See 1373571,2,3,4 exclude 1373364,86,410,19,23 | March | 2016 | 2016Q3 | 2016 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-03-09 | N | 124.229 | N | 5 | N | N | 1.1101 | 39.4971 | 175210.9978
[7 empty] | 10980 | 7423 | 1373491 | 2016-03-10 04:06 | 2016-03-10 07:45 | 219 | 11kV | 3723 | 17 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166335 Vehicle brought down service wire, damaged LVF assembly, sub isolated for repair Excluded OMS 1373491 | March | 2016 | 2016Q3 | 2016 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Not Veg | 2016-03-10 | N | 219 | N | 3 | N | N | 1.1101 | 39.4971 | 2720.6586
[7 empty] | 11753 | 15420 | 1373517 | 2016-03-10 08:18 | 2016-03-10 09:58 | 100 | 11kV | 95350 | 1009 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.8 tripped on: C phase O/C, EFI Field EFI down @ S8812 UG cable fault between S8812 (Sw/B) to S6834 (Sw/A) to S4198 (Sw/A) to S2861 (Sw/A) See 1374602 1374605 | March | 2016 | 2016Q3 | 2016 | ZN2602:PA8 | ZN2602:PA46 | ZN02602/000046 | WAVERLEY | UG | Not Veg | 2016-03-10 | N | 94.4995 | N | 3 | N | N | 1.1101 | 39.4971 | 69678.9677
[7 empty] | 11032 | 7874 | 1373482 | 2016-03-09 21:47 | 2016-03-10 12:20 | 873 | 11kV | 469233 | 576 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S3425 Castle Cove Panel 18 Tripped on Earth Fault and EFI with 11kV Trip Cause: Section of 11kV Feeder from S1854 to S4102 to S4742 is defective. See OMS 1376699 1376900 1373482 | March | 2016 | 2016Q3 | 2016 | ZN3425:PA18 | ZN3425:PA18 | ZN03425/000018 | WILLOUGHBY | UG | Not Veg | 2016-03-09 | N | 814.6406 | N | 5 | N | N | 1.1101 | 39.4971 | 342901.6364
[7 empty] | 11488 | 12642 | 1373774 | 2016-03-10 14:50 | 2016-03-10 19:20 | 270 | 11kV | 270 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Hot >35C | N | LID 166356 Replace leaking Tx. Caused small grassfire. Excluded OMS No. 1373623 | March | 2016 | 2016Q3 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2016-03-10 | N | 270 | N | 3 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 11781 | 15718 | 1373763 | 2016-03-11 06:43 | 2016-03-11 11:45 | 302 | 11kV | 10881 | 136 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166360 1 fault operation A Phase Sensitive Earth Fault wires down at pole AG-10010 to sub 70062 Excluded oms 1373763 | March | 2016 | 2016Q3 | 2016 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2016-03-11 | N | 80.0074 | N | 1 | N | N | 1.1101 | 39.4971 | 7951.5139
[7 empty] | 11528 | 12934 | 1374179 | 2016-03-13 13:50 | 2016-03-13 14:19 | 29 | 11kV | 8178 | 282 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | EX Zn12600 Lisarow section of Pa2 RE41845 North Erina tripped on overcurrent, lockout Tree branch was across 3 phases of HV near the corner of Wattle Tree Rd and Paroo rd. Removed by DOp See 1374179,80 | March | 2016 | 2016Q3 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2016-03-13 | N | 29 | N | 3 | N | N | 1.1101 | 39.4971 | 5976.2412
[7 empty] | 10949 | 7094 | 1374178 | 2016-03-13 13:49 | 2016-03-13 17:40 | 231 | 11kV | 184798 | 1227 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S847 Hornsby Pa 15 tripped on Earth fault on OC and E/F relay, fault check and EFi Cause: UG cable fault from S35194 to S5230 tee 36238 See OMS 1376711 1376715 1376716 1376717 1374206 1374178 | March | 2016 | 2016Q3 | 2016 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | UG | Not Veg | 2016-03-13 | N | 150.6096 | N | 3 | N | N | 1.1101 | 39.4971 | 135044.9278
[7 empty] | 11623 | 13993 | 1374225 | 2016-03-13 19:43 | 2016-03-13 22:55 | 191.7167 | 11kV | 1150.3 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166388 B & C Phase DOLF : 20 Amp Possibly birds please patrol Excluded OMS 1374225 | March | 2016 | 2016Q3 | 2016 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2016-03-13 | N | 191.7167 | N | 3 | N | N | 1.1101 | 39.4971 | 840.6053
[7 empty] | 11343 | 11447 | 1374249 | 2016-03-14 02:22 | 2016-03-14 04:00 | 98 | 11kV | 6272 | 64 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa17L PT11592 Campbell Dwyer 11kv HDO fuse holder was found broken in half See 1374336 exclude 1374249 | March | 2016 | 2016Q3 | 2016 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | OH | Not Veg | 2016-03-14 | N | 98 | N | 13 | N | N | 1.1101 | 39.4971 | 4583.3926
[7 empty] | 11203 | 9940 | 1374345 | 2016-03-14 10:59 | 2016-03-14 12:30 | 91 | 11kV | 91 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166397 B & C phase DOLF : 16 Amp Volts 243 Excluded OMS 1374345 | March | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2016-03-14 | N | 91 | N | 13 | N | N | 1.1101 | 39.4971 | 66.5001
[7 empty] | 11732 | 15199 | 1374458 | 2016-03-14 17:15 | 2016-03-14 18:30 | 75.4333 | 11kV | 528.0333 | 7 | HV | Staff Other | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 166409 C Phase DOLF : 31 Amp Incorrect Fuse elements previouslt installed. Replaced 3 x 31.55 A | March | 2016 | 2016Q3 | 2016 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2016-03-14 | N | 75.4333 | N | 13 | N | N | 1.1101 | 39.4971 | 385.8712
[7 empty] | 10711 | 4510 | 1374446 | 2016-03-14 16:38 | 2016-03-14 18:37 | 119 | 11kV | 357 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 166408 Single phase DOLF : 10 Amp Meter Damaged on customers board Excluded oms 1374446 | March | 2016 | 2016Q3 | 2016 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2016-03-14 | N | 119 | N | 13 | N | N | 1.1101 | 39.4971 | 260.8851
[7 empty] | 11666 | 14406 | 1374475 | 2016-03-14 18:17 | 2016-03-14 20:55 | 158 | 11kV | 33812 | 214 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 166412 1 fault operation Earth Fault; Overcurrent Excluded OMS 1374475 | March | 2016 | 2016Q3 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-03-14 | N | 158 | N | 13 | N | N | 1.1101 | 39.4971 | 24708.8123
[7 empty] | 11522 | 12868 | 1374441 | 2016-03-14 16:20 | 2016-03-14 21:30 | 310 | 11kV | 310 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 166424 Single phse DOLF : 3 Amp Excluded OMS 1374441 | March | 2016 | 2016Q3 | 2016 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2016-03-14 | N | 310 | N | 13 | N | N | 1.1101 | 39.4971 | 226.5389
[7 empty] | 10436 | 1050 | 1374481 | 2016-03-14 19:05 | 2016-03-14 21:42 | 157 | 33kV Distribution | 157 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 166426 2 fault operations Overcurrent PAtrolled Ausgrid 33kV Feeder . OK Contacted Newpac B4 closing 32126. | March | 2016 | 2016Q3 | 2016 |  |  |  | SINGLETON | OH | Veg | 2016-03-14 | N | 157 | N | 13 | N | N | 1.1101 | 39.4971 | 114.731
[7 empty] | 10753 | 5010 | 1374504 | 2016-03-14 20:04 | 2016-03-14 22:09 | 125 | 11kV | 298286 | 2710 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35500 Top Ryde Panel 24 Tripped Relays A and B phase IOC and EFI Cause: Possum on 11kV UGOH below S4599 signals: 11kV Trip See OMS 1374504 1375550 1375550 | March | 2016 | 2016Q3 | 2016 | ZN35500:PA24 | ZN35500:PA24 | ZN35500/000024 | RYDE | OH | Not Veg | 2016-03-14 | N | 110.0686 | N | 13 | N | N | 1.1101 | 39.4971 | 217978.6109
[7 empty] | 12194 | 19786 | 1374471 | 2016-03-14 18:03 | 2016-03-15 00:15 | 372 | 11kV | 1116 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 166425 DOLF : 10 Amp Broken DOLF Dropper Lead Excluded oms 1374471 | March | 2016 | 2016Q3 | 2016 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2016-03-14 | N | 372 | N | 13 | N | N | 1.1101 | 39.4971 | 815.5399
[7 empty] | 12129 | 19199 | 1374499 | 2016-03-14 19:53 | 2016-03-15 03:35 | 462 | 11kV | 20598 | 87 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 166447 A Phase bond apping burnt off at pole Al-10372 repaired by A Regan.oms 1374499 ## dq | March | 2016 | 2016Q3 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2016-03-14 | N | 236.7586 | N | 13 | N | N | 1.1101 | 39.4971 | 15052.4109
[7 empty] | 11291 | 10840 | 1374609 | 2016-03-15 07:38 | 2016-03-15 08:13 | 35 | 11kV | 27405 | 783 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca 11kv Pa34 "Terrigal" tripped, reclosed and locked out on: Relays: A & B phase IOC, reclose timer Signals: 11kV trip EFI's: Nil Cause: Tree branch on OH Mains. near 36 Surf Rider Ave See 1374609 exclude 1374616,7,23 | March | 2016 | 2016Q3 | 2016 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2016-03-15 | N | 35 | N | 10 | N | N | 1.1101 | 39.4971 | 20026.7657
[7 empty] | 11371 | 11632 | 1374509 | 2016-03-14 20:19 | 2016-03-15 08:25 | 726 | 11kV | 8712 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 166448 A & B phase DOLF : 10 Amp Excluded OMS 1374509 | March | 2016 | 2016Q3 | 2016 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2016-03-14 | N | 726 | N | 13 | N | N | 1.1101 | 39.4971 | 6366.4726
[7 empty] | 12219 | 20097 | 1374564 | 2016-03-15 05:46 | 2016-03-15 08:35 | 169 | 11kV | 507 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 166449 A Phase DOLF : 10 Amp Excluded OMD 1374570 | March | 2016 | 2016Q3 | 2016 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2016-03-15 | N | 169 | N | 10 | N | N | 1.1101 | 39.4971 | 370.5006
[7 empty] | 11057 | 8120 | 1374631 | 2016-03-15 08:03 | 2016-03-15 08:52 | 49 | 11kV | 6321 | 129 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12600 Lisarow section of Pa2 CP41020 Wattle Tree Rd North tripped, reclosed and locked out Relays: TImed OC Signals: 11kv trip Tree/Branch on OH Mains Adjacent to LB45186 | March | 2016 | 2016Q3 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2016-03-15 | N | 49 | N | 10 | N | N | 1.1101 | 39.4971 | 4619.2004
[7 empty] | 11716 | 15078 | 1374486 | 2016-03-14 19:14 | 2016-03-15 09:25 | 851 | 11kV | 288173 | 2427 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S2635 Epping Panel 58 Tripped, reclosed tripped and locked out on Relays: C phase overcurrent, Earth Fault and EFI. Signals: 11kV Trip, Zone Earth Cause: Tree branch brought high into low outside 3 Hepburn Ave Carlingford. See OMS 1375253 1375255 1375257 1374486 1374492 1374530 1374559 | March | 2016 | 2016Q3 | 2016 | ZN2635:PA58 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | OH | Veg | 2016-03-14 | N | 118.7363 | N | 13 | N | N | 1.1101 | 39.4971 | 210588.3287
[7 empty] | 11111 | 8813 | 1374611 | 2016-03-15 07:43 | 2016-03-15 10:30 | 167 | 11kV | 334 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 166457 B Phase DOLF : 10 Amp Excluded OMS 1374611 | March | 2016 | 2016Q3 | 2016 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2016-03-15 | N | 167 | N | 10 | N | N | 1.1101 | 39.4971 | 244.0773
[7 empty] | 11983 | 17870 | 1374614 | 2016-03-15 07:42 | 2016-03-15 12:05 | 263 | 11kV | 206204 | 2158 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman - Pnl.21 tripped on: B Phase timed O/C, EFI, Fault Check Field EFIs: NIL UG cable fault from Pnl.21 at Mosman to S325 (Sw/A) to S2989 (Sw/A) See 1375229 SE(LV // failure): 1375233 1375231 1375233 1374861 1374645 | March | 2016 | 2016Q3 | 2016 | ZN180:PA21 | ZN180:PA21 | ZN00180/000021 | MOSMAN | UG | Not Veg | 2016-03-15 | N | 95.5533 | N | 10 | N | N | 1.1101 | 39.4971 | 150687.8012
[7 empty] | 12075 | 18710 | 1374587 | 2016-03-15 07:06 | 2016-03-15 12:35 | 329 | 11kV | 329 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 166461 C Phase DOLF : 10 Amp Excluded OMS 1374587 | March | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-03-15 | N | 329 | N | 10 | N | N | 1.1101 | 39.4971 | 240.4235
[7 empty] | 10441 | 1131 | 1374823 | 2016-03-15 12:59 | 2016-03-15 14:27 | 88 | 11kV | 176 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 166468 B & C Phase DOLF : 10 Amp Excluded OMS 1374823 | March | 2016 | 2016Q3 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2016-03-15 | N | 88 | N | 10 | N | N | 1.1101 | 39.4971 | 128.6156
[7 empty] | 10373 | 47 | 1374834 | 2016-03-15 13:11 | 2016-03-15 14:35 | 84 | 11kV | 84 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 166469 B Phase DOLF : 10 Amp Excluded OMS 1374834 | March | 2016 | 2016Q3 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2016-03-15 | N | 84 | N | 10 | N | N | 1.1101 | 39.4971 | 61.3847
[7 empty] | 10386 | 257 | 1374899 | 2016-03-15 15:10 | 2016-03-15 15:25 | 15 | 11kV | 975 | 65 | HV | Staff Other | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166465 HV Mains close to LV mains. Short outage to repair. Excluded OMS 1374899 | March | 2016 | 2016Q3 | 2016 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Not Veg | 2016-03-15 | N | 15 | N | 10 | N | N | 1.1101 | 39.4971 | 712.5012
[7 empty] | 10616 | 3462 | 1374571 | 2016-03-14 19:54 | 2016-03-15 16:54 | 1260 | 11kV | 28392 | 249 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 166446 Burnt off tapping at ABS 43794 Excluded OMS 1374501 | March | 2016 | 2016Q3 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2016-03-14 | N | 114.0241 | N | 13 | N | N | 1.1101 | 39.4971 | 20748.0362
[7 empty] | 12020 | 18236 | 1374983 | 2016-03-15 23:36 | 2016-03-16 03:17 | 221 | 11kV | 205236 | 1085 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn10996 Rockdale - Pnl.12 tripped, reclosed and locked out on: A phase IOC, EFI & Lockout Field EFIs: NIL Cause not ascertained. Feeder has tripped 4 times in 24 hours. Opposite 113 Bestic Rd is low trees possbly causing outage. To be inspected by Linesman in daylight. See 1375241 1375242 1375243 | March | 2016 | 2016Q3 | 2016 | ZN10996:PA12 | ZN10998:PA32 | ZN10998/000032 | BAYSIDE | OH | Veg | 2016-03-15 | N | 189.1576 | N | 10 | N | N | 1.1101 | 39.4971 | 149980.4154
[7 empty] | 11555 | 13208 | 1374993 | 2016-03-16 02:53 | 2016-03-16 05:00 | 127 | 11kV | 470408 | 3704 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North - Pnl.11 tripped on: B & C phase O/C Abormal: Sw A Closed @ S16511 with LB49832 Open Possum caused minor damage to OH mains 1 span from PT15227 Woolgoola Eileen. | March | 2016 | 2016Q3 | 2016 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | OH | Not Veg | 2016-03-16 | N | 127 | N | 11 | N | N | 1.1101 | 39.4971 | 343760.2917
[7 empty] | 11366 | 11600 | 1375040 | 2016-03-16 08:04 | 2016-03-16 11:00 | 176 | 11kV | 56757.5833 | 1195 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn187 Crows Nest Panel 21 tripped on Signals: 11kV Trip, Tx3 Group Earth Relays: Panel 21 IOC and Earthh Fault See OMS 1375040 1376252 1375088 1376253 1375052 1375057 1375048 Cause: UG cable fault between S36023 Miller Shirley and S2921 Telopea Milray Note: Base on Customer Calls: Suspect S4945#3 and S2757#3 Were in LV Parallel during feeder trip. | March | 2016 | 2016Q3 | 2016 | ZN187:PA21 | ZN187:PA21 | ZN00187/000021 | NORTH SYDNEY | UG | Not Veg | 2016-03-16 | N | 47.4959 | N | 11 | N | N | 1.1101 | 39.4971 | 41476.7678
[7 empty] | 10492 | 1895 | 1375078 | 2016-03-16 09:14 | 2016-03-16 11:00 | 106 | 11kV | 100445 | 1055 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S187 Crows Nest Panel 21 tripped Signals 11kV trip TX3 Group Earth Relays: IOC Earth Fault. UG fault between S4848 Shirley Belmount and S36023 Miller Shirley See OMS 1377059 1377060 1375088 1375078 | March | 2016 | 2016Q3 | 2016 | ZN187:PA21 | ZN187:PA21 | ZN00187/000021 | NORTH SYDNEY | UG | Not Veg | 2016-03-16 | N | 95.2085 | N | 11 | N | N | 1.1101 | 39.4971 | 73402.2434
[7 empty] | 10897 | 6566 | 1375010 | 2016-03-16 06:08 | 2016-03-16 12:15 | 367 | 11kV | 63061 | 1405 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 166471/02 11kV Fdr 7490 Stockton sub isolated to repair burning crossarm on pole KT-70078. Excluded OMS No. 1375010 + 1375018 | March | 2016 | 2016Q3 | 2016 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2016-03-16 | N | 44.8833 | N | 11 | N | N | 1.1101 | 39.4971 | 46083.1188
[7 empty] | 11100 | 8729 | 1375118 | 2016-03-16 08:36 | 2016-03-16 12:45 | 249 | 11kV | 23157 | 93 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Insulated | Unplanned | Rain Heavy | N | Zn12660 Woy WOy section of Pa10 "The Woy WOy Leagues Black" fdr Link 41577 to S14713 tee PT11514 interrutped for safe removal of tree on OH Mains near 79 Glenbrooke Pde Koolewong See 1375817 exclude 1375118,25 | March | 2016 | 2016Q3 | 2016 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | OH | Veg | 2016-03-16 | N | 249 | N | 11 | N | N | 1.1101 | 39.4971 | 16922.4526
[7 empty] | 11297 | 10922 | 1375772 | 2016-03-16 13:30 | 2016-03-16 13:35 | 5 | 11kV | 27565 | 6300 | HV | Staff Other | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At ZN35800 Bankstown the following Panels tripped: Signals: 11kv trip Panel 2, Panel 3, Panel 7, Pa9, Pa10 Frame leakage prohibition relay Remarks: staff error. Protection Technician Stephen Burgo was working at Zn35800 Bankstown on Panel 1 when he accidentally knocked the underfrequency load shedding relay which caused a simultaneous trip of Panels 2,3,7,9 & 10 | March | 2016 | 2016Q3 | 2016 | ZN35800:PA10 | ZN35800:PA10 | ZN35800/000010 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2016-03-16 | N | 4.3754 | N | 11 | N | N | 1.1101 | 39.4971 | 20143.689
[7 empty] | 10409 | 607 | 1375245 | 2016-03-16 14:46 | 2016-03-16 16:50 | 124 | 11kV | 225994 | 2109 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill - Pnl.3 tripped on Earth fault with EFI Field EFIs: S3149, 3034, 5660, 3525, 1938, 64092, 5748 UG cable fault between S.5748 and S.63643 See 1375464 1375465 1375466 | March | 2016 | 2016Q3 | 2016 | ZN398:PA3 | ZN398:PA3 | ZN00398/000003 | INNER WEST | UG | Not Veg | 2016-03-16 | N | 107.1569 | N | 11 | N | N | 1.1101 | 39.4971 | 165149.7495
[7 empty] | 10792 | 5383 | 1375335 | 2016-03-16 21:51 | 2016-03-16 22:01 | 10 | 11kV | 5140 | 514 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Heavy | N | Zn9245 Engadine - Pnl.43 tripped on: SEF Abnormal: LB35729 closed with AB35585 open Flicker blade was still closed on recently opened AB35585 | March | 2016 | 2016Q3 | 2016 | ZN9245:PA43 | ZN9245:PA21 | ZN09245/000021 | SUTHERLAND | OH | Not Veg | 2016-03-16 | N | 10 | N | 11 | N | N | 1.1101 | 39.4971 | 3756.1604
[7 empty] | 11743 | 15301 | 1375309 | 2016-03-16 18:34 | 2016-03-16 23:59 | 325 | 11kV | 325 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166489 Single phase Lead to dolf burned off. Replaced by Maitland CAW under AP by A Mills. Excluded OMS 1375309 | March | 2016 | 2016Q3 | 2016 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2016-03-16 | N | 325 | N | 11 | N | N | 1.1101 | 39.4971 | 237.5004
[7 empty] | 11349 | 11499 | 1375343 | 2016-03-16 22:35 | 2016-03-17 00:15 | 100 | 11kV | 117796 | 1393 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | Zn10996 Rockdale - Pnl.9 tripped/ reclosed and locked out on: A phase timed O/C and IOC, EFI and lockout Abnormal: S1014 Sw/B closed with S10716 Sw/A open. LB30097 closed with AB31263 open. Lightning arrested failed at PT10909. Panel previously tripped and reclosed, fault stuck this time. See further interruption for unknown cause. See 1375556 1375557 | March | 2016 | 2016Q3 | 2016 | ZN10996:PA12 | ZN10998:PA32 | ZN10998/000032 | BAYSIDE | OH | Not Veg | 2016-03-16 | N | 84.5628 | N | 11 | N | N | 1.1101 | 39.4971 | 86081.8424
[7 empty] | 12065 | 18625 | 1375351 | 2016-03-16 23:26 | 2016-03-17 00:30 | 64 | 11kV | 40208 | 629 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S8000 Macquarie Park Panel 38 tripped and locked out on Relays: Earth Fault See OMS 1376400 1376401 1375351 11KV UG fault betweent from S8180 Lane Cove to S5934 Waterloo North See OMS 1376400 1376401 1375351 | March | 2016 | 2016Q3 | 2016 | ZN8000:PA38 | ZN8000:PA38 | ZN08000/000038 | RYDE | UG | Not Veg | 2016-03-16 | N | 63.9237 | N | 11 | N | N | 1.1101 | 39.4971 | 29382.8205
[7 empty] | 11818 | 16210 | 1375358 | 2016-03-17 01:35 | 2016-03-17 03:06 | 91 | 11kV | 99425 | 1393 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Zn10996 Rockdale - Pnl.9 tripped, reclosed and locked out on: A phase timed O/C and IOC, EFI and lockout Abnormal: S10104 Sw/B closed with S10716 Sw/A open. LB30097 closed with AB31263 open. Cause not ascertained. Lineworker to patrol feeder again. See 1375668 1375669 | March | 2016 | 2016Q3 | 2016 | ZN10996:PA12 | ZN10998:PA32 | ZN10998/000032 | BAYSIDE | OH | Veg | 2016-03-17 | N | 71.3747 | N | 10 | N | N | 1.1101 | 39.4971 | 72656.8575
[7 empty] | 10818 | 5672 | 1375363 | 2016-03-17 02:55 | 2016-03-17 04:10 | 75 | 11kV | 4630 | 66 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn14143 Somersby 11kV Pa14 "Ace Aust Conveyor Eng" tripped on: Relays: Earth Fault Signals: 11kv trip Group Earth EFI's: S14458 S18149 S18268 S8670 S18516 S14856 S14957 S18103 11kV UG Fault from S18103 Sw/A to S49664 Sw/A See 1375827,8 exclude 1375363 | March | 2016 | 2016Q3 | 2016 | ZN14143:PA14 | ZN14143:PA14 | ZN14143/000014 | CENTRAL COAST | UG | Not Veg | 2016-03-17 | N | 70.1515 | N | 10 | N | N | 1.1101 | 39.4971 | 3383.4674
[7 empty] | 11485 | 12623 | 1375360 | 2016-03-17 01:41 | 2016-03-17 04:34 | 173 | 11kV | 105376 | 825 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166491 2 fault operations A phase Instantaneous Earth Fault; Instantaneous Overcurrent Nothing found. Excluded OMS 1375360 | March | 2016 | 2016Q3 | 2016 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Veg | 2016-03-17 | N | 127.7285 | N | 10 | N | N | 1.1101 | 39.4971 | 77005.6727
[7 empty] | 11860 | 16620 | 1375366 | 2016-03-17 04:50 | 2016-03-17 05:40 | 50 | 11kV | 12200 | 244 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | CP49996 Churchill Fairbard (ex Lindfield Panel 12) Tripped on Relays O/C Trip Cause not ascertaine- mains to patrol | March | 2016 | 2016Q3 | 2016 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Veg | 2016-03-17 | N | 50 | N | 10 | N | N | 1.1101 | 39.4971 | 8915.4002
[7 empty] | 11939 | 17303 | 1376502 | 2016-03-17 11:13 | 2016-03-17 11:29 | 16 | 11kV | 16672 | 1042 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn10996 Rockdale, 11kv Panel 9 '30804' fdr C/B opened. Relays: Nil Signals: Nil Abnormal: Sw/A @ S10716 Rockdale Princes 1 opened, Sw/B @ S10104 Bestic Cameron Closed, AB30097 closed Remarks:: other - details provided. Dop closed Panel 9 feeder C/B at zone and indicated closed. C/B opened prior to opening AB30097. T/Pe to investigate. Dop noticed power out while completing switching. No alarms or signals received | March | 2016 | 2016Q3 | 2016 | ZN10996:PA9 | ZN10998:PA8 | ZN10998/000008 | BAYSIDE | OH | Veg | 2016-03-17 | N | 16 | N | 10 | N | N | 1.1101 | 39.4971 | 12183.4059
[7 empty] | 11693 | 14755 | 1375480 | 2016-03-17 11:10 | 2016-03-17 12:23 | 73 | 11kV | 35435 | 903 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Rain Heavy | N | Zn188 Zetland - Pnl.4 tripped on: B Phase earth Fault, Fault Check and EFI Field EFI: S65408 Contractor excavator hit HV cable between S65408, S48559 and S64007. See 1376287 GIS: 1375488 1375487 | March | 2016 | 2016Q3 | 2016 | ZN188:PA4 | ZN188:PA10 | ZN00188/000010 | SYDNEY | UG | Not Veg | 2016-03-17 | N | 39.2414 | N | 10 | N | N | 1.1101 | 39.4971 | 25894.8528
[7 empty] | 10804 | 5515 | 1375460 | 2016-03-17 10:31 | 2016-03-17 12:50 | 139 | 11kV | 6950 | 50 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | @ZN35800 Bankstown Exiting Panel #16 labelled "S.5149 Canterbury Fair" PT421 Hoskins Ave A+ C phase 11kv HDO fuses blown (16 amp) Remarks: Suspected transformer fault @ PT421 Hoskins Ave. Outage previous month from suspected lightning strike. Restored via LV// USL.16667+3719. N/O Dist#2 @ S.64012 Hoskins Cottam. Switching Tag ONLY. Region (Renee Ison) to organise cut-out for test/repair | March | 2016 | 2016Q3 | 2016 | ZN35800:PA16 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-03-17 | N | 139 | N | 10 | N | N | 1.1101 | 39.4971 | 5078.855
[7 empty] | 11123 | 8956 | 1375537 | 2016-03-17 13:43 | 2016-03-17 15:15 | 92 | 11kV | 76636 | 859 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12600 Lisarow Pa13 "Brush Rd" fdr opened, closed and opened onA & C overcurrent with timing and lock out relays Signals: 11kv trip Tree Branch on OH Mains in brush rd 50m below tee off to S14735, adjacent to Uni Campus. Tree need trimming. See 1375832,3 exclude 1375537 | March | 2016 | 2016Q3 | 2016 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2016-03-17 | N | 89.2154 | N | 10 | N | N | 1.1101 | 39.4971 | 56003.3284
[7 empty] | 10961 | 7165 | 1375659 | 2016-03-17 23:57 | 2016-03-18 02:12 | 135 | 11kV | 145530 | 1078 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn10994 Mortdale 11kv feeder Panel No.21 "Balmoral Barrs" feeder tripped to lockout x1 on: Relays: B and C phase IOC Signals: 11kv trip Field EFIs: Nil Remarks: cause not ascertained. Next available L/men to patrol extent of feeder. Note: limited access to section beyond AB31154 | March | 2016 | 2016Q3 | 2016 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Veg | 2016-03-17 | N | 135 | N | 10 | N | N | 1.1101 | 39.4971 | 106349.0316
[7 empty] | 11209 | 10013 | 1375670 | 2016-03-18 07:01 | 2016-03-18 08:35 | 94 | 11kV | 37302 | 825 | HV | Equipment Failed in Service | Equipment Failure | U/G Link | Unplanned | No Weather Impact | N | LID 166513 2 fault operations A & C phase Instantaneous Overcurrent failed hezemeyer link cable termination Excluded oms 1375670 | March | 2016 | 2016Q3 | 2016 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | UG | Not Veg | 2016-03-18 | N | 45.2145 | N | 15 | N | N | 1.1101 | 39.4971 | 27259.2014
[7 empty] | 12064 | 18618 | 1375643 | 2016-03-17 21:45 | 2016-03-18 11:30 | 825 | 11kV | 270149 | 1759 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca Pa24 "Woodfield Waldron" fdr opened and closed on Relays: B and C phase overcurrent lockout timing Cause: Overhead down. Fault 1: Outside 166 Del mar Dr Copacaabanna 11kv OH mains failure making contact with LV entwork neutral conductor Fault 2: 11kv bond open circuit on pole AV863 adjacent LB 42015 Note:TPE to investigate SEL failure to operate See 1376274,7,8,9 exclude 1375643,4,5,51,8 | March | 2016 | 2016Q3 | 2016 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2016-03-17 | N | 153.581 | N | 10 | N | N | 1.1101 | 39.4971 | 197416.9212
[7 empty] | 11194 | 9880 | 1375717 | 2016-03-18 10:20 | 2016-03-18 13:50 | 210 | 11kV | 420 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166516 B & C Phase DOLF : 16 Amp No cause found, site not staffed so fuse may have blown a few days ago. excluded OMS # 1375717. | March | 2016 | 2016Q3 | 2016 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2016-03-18 | N | 210 | N | 15 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 12019 | 18235 | 1375740 | 2016-03-18 11:54 | 2016-03-18 15:15 | 201 | 11kV | 32948 | 464 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | Zn10996 Rockdale - Pnl.12 tripped on: A & B phase IOC, Earth Fault and EFI Abnormal switching: AB30559 Open with S10402 (Sw/B) closed. AB31095 open with S64835 (Sw/B) closed. S10612 (Sw/A) open with AB31283 closed. Abnormal switching in place to assist in fault location ID. This panel has had multiple interruptions when it has been raining. Found defective surge arrestor on tee off UGOH to S10796 West Botany Barton. Note: S10612 Pantallon West Botany remained alive via LV // See 1376330 1376331 1376332 | March | 2016 | 2016Q3 | 2016 | ZN10996:PA12 | ZN10998:PA32 | ZN10998/000032 | BAYSIDE | OH | Not Veg | 2016-03-18 | N | 71.0086 | N | 15 | N | N | 1.1101 | 39.4971 | 24077.4266
[7 empty] | 11907 | 17008 | 1375724 | 2016-03-18 11:11 | 2016-03-18 16:45 | 334 | 11kV | 158141 | 1287 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 33 tripped, reclosed tripped and locked out on Relays: O/C trip, Earth fault, EFI, Recloser and lockout Cause: 11kV feeder down between S3245 to AB2830 to PT2005. See OMS 1376740 1376741 1375724 | March | 2016 | 2016Q3 | 2016 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Not Veg | 2016-03-18 | N | 122.8757 | N | 15 | N | N | 1.1101 | 39.4971 | 115564.7784
[7 empty] | 10558 | 2732 | 1375841 | 2016-03-18 16:50 | 2016-03-18 17:40 | 50 | 11kV | 1600 | 32 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At S965 ex Panel 6 Pennant Hills S6740 Pennant Hillmont Suspect Faulty Transfomer See OMS 1376743 1375840 | March | 2016 | 2016Q3 | 2016 | ZN965:PA6 | ZN965:PA6 | ZN00965/000006 | HORNSBY | UG | Not Veg | 2016-03-18 | N | 50 | N | 15 | N | N | 1.1101 | 39.4971 | 1169.2328
[7 empty] | 11816 | 16208 | 1375847 | 2016-03-18 16:50 | 2016-03-18 18:40 | 110 | 11kV | 1895 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 166521 1 fault operation Overcurrent Excluded OMS 1375847 | March | 2016 | 2016Q3 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2016-03-18 | N | 90.2381 | N | 15 | N | N | 1.1101 | 39.4971 | 1384.8101
[7 empty] | 11578 | 13432 | 1375874 | 2016-03-18 18:23 | 2016-03-18 20:40 | 137 | 11kV | 274 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LIS 166524 A Phase DOLF : 10 Amp Excluded OMS 1375874 | March | 2016 | 2016Q3 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2016-03-18 | N | 137 | N | 15 | N | N | 1.1101 | 39.4971 | 200.2311
[7 empty] | 11105 | 8767 | 1375837 | 2016-03-18 17:40 | 2016-03-18 21:20 | 220 | 11kV | 24640 | 112 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Insulated | Unplanned | Rain Light | N | @Zn1287 Revesby exiting Panel #4 labelled "S46609 Tower Condon" Section of feeder beyond LB1626 interrupted for safety/repair Remarks: tree/branch on OH mains. Tree on OH mains two bays beyond LB1626. Interrupted for safety/repair @ 1740 | March | 2016 | 2016Q3 | 2016 | ZN1287:PA4 | ZN1287:PA4 | ZN01287/000004 | SUTHERLAND | OH | Veg | 2016-03-18 | N | 220 | N | 15 | N | N | 1.1101 | 39.4971 | 18006.1852
[7 empty] | 11338 | 11384 | 1375866 | 2016-03-18 17:39 | 2016-03-18 21:39 | 240 | 11kV | 13278 | 65 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Electrical Storm | N | LID 166519 2 fault operations A & C phases Overcurrent Car hit pole 7L-10011. Broken x arm and insulator needed replacement. Excluded OMS 1375866 | March | 2016 | 2016Q3 | 2016 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2016-03-18 | N | 204.2769 | N | 15 | N | N | 1.1101 | 39.4971 | 9703.1708
[7 empty] | 11617 | 13940 | 1375899 | 2016-03-18 20:45 | 2016-03-18 22:20 | 95 | 11kV | 190 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 166526 A phase DOLF : 10 Amp Excluded OMS 1375899 | March | 2016 | 2016Q3 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2016-03-18 | N | 95 | N | 15 | N | N | 1.1101 | 39.4971 | 138.8464
[7 empty] | 11945 | 17401 | 1375879 | 2016-03-18 18:55 | 2016-03-18 22:45 | 230.3 | 11kV | 37538.9 | 163 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S1595 Morrice River West 400A fuse blown on A and C phase of distributor 2. At S1595 Morrice Rive HV fuses failed to grade with LV fuses. Cause: Falled tree branch O/S 4 Wangalla Rd Lane Cove See OMS 1375879 1375890 | March | 2016 | 2016Q3 | 2016 | ZN80:PA40 | ZN80:PA40 | ZN00080/000040 | LANE COVE | OH | Veg | 2016-03-18 | N | 230.3 | N | 15 | N | N | 1.1101 | 39.4971 | 27432.3209
[7 empty] | 11423 | 12058 | 1375902 | 2016-03-18 21:21 | 2016-03-18 23:10 | 109 | 11kV | 120881 | 1109 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Previous Storm | N | Zn13000 Lake Munmorah AZone section of Pa11 "The Lake Munmorah Aux No2" fdr from IR45092 Mannering Park recloser tripped and locked out on B and C phase overcurrent Pole Defective in rutley rd pole BP399 head of pole failure | March | 2016 | 2016Q3 | 2016 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2016-03-18 | N | 109 | N | 15 | N | N | 1.1101 | 39.4971 | 88336.2694
[7 empty] | 12146 | 19331 | 1375901 | 2016-03-18 21:26 | 2016-03-19 00:50 | 204 | 11kV | 816 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 166527 A phase DOLF : 10 Amp Excluded OMS 1375901 | March | 2016 | 2016Q3 | 2016 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2016-03-18 | N | 204 | N | 15 | N | N | 1.1101 | 39.4971 | 596.3087
[7 empty] | 10830 | 5811 | 1375851 | 2016-03-18 17:04 | 2016-03-19 03:00 | 596 | 11kV | 271519 | 2379 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Lightning | N | Zn9245 Engadine - Pnl.40 tripped on A & B phase IOC and EFI Pnl.43 tripped on: B phase IOC and EFI plus sealing contactor Field EFIs: (P40) S9007, S9792. (P43) S48146, S9199 Abnormal switching: AB3554 open with LB35729 closed and AB35585 welded closed (defective) Lightning struck pole with normall open AB35254 on it. Top of pole snapped. Bonds broke away on P40 side of AB35254 See 1376361 1376362 1376363 1376364 | March | 2016 | 2016Q3 | 2016 | ZN9245:PA40 | ZN9245:PA13 | ZN09245/000013 | SUTHERLAND | OH | Not Veg | 2016-03-18 | N | 114.1316 | N | 15 | N | N | 1.1101 | 39.4971 | 198418.0767
[7 empty] | 11265 | 10576 | 1375891 | 2016-03-18 19:41 | 2016-03-19 08:30 | 769 | 11kV | 17540 | 131 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 166523 2 fault operations Overcurrent | March | 2016 | 2016Q3 | 2016 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2016-03-18 | N | 133.8931 | N | 15 | N | N | 1.1101 | 39.4971 | 12817.7147
[7 empty] | 10851 | 6085 | 1376035 | 2016-03-19 18:45 | 2016-03-19 20:45 | 120 | 11kV | 360 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 166530 A Phase line DOLF Excluded OMS 1376035 | March | 2016 | 2016Q3 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2016-03-19 | N | 120 | N | 1 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 11513 | 12798 | 1376052 | 2016-03-20 01:21 | 2016-03-20 04:30 | 189 | 11kV | 23230 | 2174 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn15006 Dee Why West section of Pa8 CP20285 Alfred Par Relays IOC trip OC trip PT15350 centre phase hdo operated. Size 40A Abnormal: DMA AB21622 with S50262:B closed. DMA 11kv fdr S16402 to AB20903 to S46338:B with S17070:B See 1376313,4 exclude 1376052 | March | 2016 | 2016Q3 | 2016 | ZN15006:PA8 | ZN15006:PA8 | ZN15006/000008 | NORTHERN BEACHES | OH | Not Veg | 2016-03-20 | N | 10.6854 | N | 7 | N | N | 1.1101 | 39.4971 | 16975.7988
[7 empty] | 11269 | 10613 | 1376056 | 2016-03-20 05:26 | 2016-03-20 06:55 | 88.5667 | 11kV | 619.9667 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166532 A phase DOLF : 10 Amp | March | 2016 | 2016Q3 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-03-20 | N | 88.5667 | N | 7 | N | N | 1.1101 | 39.4971 | 453.0534
[7 empty] | 12110 | 19018 | 1376058 | 2016-03-20 06:48 | 2016-03-20 07:37 | 49 | 11kV | 62083 | 1267 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166533 Switching error during SI 12012 ABS 40177 opened instead of ABS 40117 Excluded oms 1376058 | March | 2016 | 2016Q3 | 2016 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Not Veg | 2016-03-20 | N | 49 | N | 7 | N | N | 1.1101 | 39.4971 | 45368.4253
[7 empty] | 10893 | 6531 | 1376070 | 2016-03-20 07:45 | 2016-03-20 08:35 | 50 | 11kV | 50 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | No Weather Impact | N | LID 166536 A phase DOLF : 31 Amp No cause found | March | 2016 | 2016Q3 | 2016 | 206:34441 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | UG | Not Veg | 2016-03-20 | N | 50 | N | 7 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 10410 | 621 | 1376080 | 2016-03-20 08:32 | 2016-03-20 12:45 | 253 | 11kV | 253 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166537 Single phase Broken LLC Dropper Excluded OMS 1376080 | March | 2016 | 2016Q3 | 2016 | 509:33444 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2016-03-20 | N | 253 | N | 7 | N | N | 1.1101 | 39.4971 | 184.8849
[7 empty] | 11261 | 10516 | 1376103 | 2016-03-20 10:45 | 2016-03-20 13:00 | 135 | 11kV | 540 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 166538 C phase DOLF : 10 Amp Burnt up DOLF carrier Excluded OMS 1376103 | March | 2016 | 2016Q3 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2016-03-20 | N | 135 | N | 7 | N | N | 1.1101 | 39.4971 | 394.6161
[7 empty] | 10879 | 6408 | 1376200 | 2016-03-20 22:37 | 2016-03-20 23:26 | 49 | 11kV | 39592 | 808 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Zn1673 11kv fdr Pa2 "Forbes Ray" fdr tripped Relays: A & B Phase IOC EFI Signals: 11kv trip, Group Earth EFI's: S8202 S4699 S4700 Tree branch removed by DOp adjacent PT1542 refer region to follow up tree trimming in area required | March | 2016 | 2016Q3 | 2016 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | OH | Veg | 2016-03-20 | N | 49 | N | 7 | N | N | 1.1101 | 39.4971 | 28932.6658
[7 empty] | 12094 | 18878 | 1376214 | 2016-03-21 04:30 | 2016-03-21 06:29 | 119 | 11kV | 2760 | 24 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At Zn2466 Flemington 11kv feeder Panel No.6 "Aquatic temp" feeder tripped Relays: earth fault, EFI, fault check Signals: No2 grp earth, 11kv trip, Zone earth Remarks: UG fault. 11kv UG fault from S6327 Olympic Hotel sw/D to S4800 Olympic Stadium NE Sw/A | March | 2016 | 2016Q3 | 2016 | ZN2466:PA6 | ZN36000:PA8 | ZN36000/000008 | PARRAMATTA | UG | Not Veg | 2016-03-21 | N | 115 | N | 5 | N | N | 1.1101 | 39.4971 | 2016.9266
[7 empty] | 11414 | 11965 | 1376215 | 2016-03-21 04:57 | 2016-03-21 06:45 | 108 | 11kV | 324 | 3 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166543 Single phase DOLF : 10 Amp Possum Excluded OMS 1376215 | March | 2016 | 2016Q3 | 2016 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2016-03-21 | N | 108 | N | 5 | N | N | 1.1101 | 39.4971 | 236.7696
[7 empty] | 10866 | 6260 | 1376217 | 2016-03-21 10:50 | 2016-03-21 14:40 | 230 | 11kV | 5290 | 23 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT16023 Gilwinga Dr Dist 2 "Gilwinga Dr East" interrupted for safety. Large tree down on LV mains outside 18 Gilwinga Dr Bayview See 1376384 exclude 1376217 | March | 2016 | 2016Q3 | 2016 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2016-03-21 | N | 230 | N | 5 | N | N | 1.1101 | 39.4971 | 3865.776
[7 empty] | 11802 | 15986 | 1376491 | 2016-03-21 14:31 | 2016-03-21 16:00 | 89 | 11kV | 712 | 8 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166555 B Phase DOLF : 63 Amp Bird made contact blowing DOLF. Excluded OMS # 1376491. | March | 2016 | 2016Q3 | 2016 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2016-03-21 | N | 89 | N | 5 | N | N | 1.1101 | 39.4971 | 520.3086
[7 empty] | 10777 | 5251 | 1376304 | 2016-03-21 09:39 | 2016-03-21 16:30 | 411 | 11kV | 37149 | 262 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Recloser CP1126 Mona Vale Rd Locked out on O/C and Earth Fault and EFI Cause: HV feeder down O/S No 5 Addison Rd Ingleside. appears Crimp Gave Away See OMS 1377313 1377314 1377315 1377316 1376304 Note: Restoration time for last switching step has been assumed. | March | 2016 | 2016Q3 | 2016 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2016-03-21 | N | 141.7901 | N | 5 | N | N | 1.1101 | 39.4971 | 27147.3935
[7 empty] | 10990 | 7519 | 1376828 | 2016-03-22 17:30 | 2016-03-22 18:15 | 45 | 11kV | 405 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166572 B Phase DOLF : 20 Amp only incorrect CASS number given to identify job Number given 193679 which was at Concord west correct number was 193677 or OMS 1376828 which is what should have been quoted in first place | March | 2016 | 2016Q3 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-03-22 | N | 45 | N | 2 | N | N | 1.1101 | 39.4971 | 295.9621
[7 empty] | 10570 | 2834 | 1376833 | 2016-03-22 18:10 | 2016-03-22 18:40 | 30 | 11kV | 210 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166573 A Phase DOLF : 16 Amp Excluded OMS 1376833 | March | 2016 | 2016Q3 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-03-22 | N | 30 | N | 2 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 11177 | 9670 | 1376919 | 2016-03-23 09:05 | 2016-03-23 09:22 | 17 | 11kV | 24616 | 1560 | HV | Staff Operation | Utility Process Issue | U/G Cable | Unplanned | No Weather Impact | N | At Zn15001 Brookvale Panel 18 Tripped on Relays: Fault Check, EFI and 50T and 150TN Cause: Dop Closed onto earthed feeder after presuming feeder was isolated and not earthed See OMS 1377305 1377306 1376919 1376926 | March | 2016 | 2016Q3 | 2016 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | UG | Not Veg | 2016-03-23 | N | 15.7795 | N | 4 | N | N | 1.1101 | 39.4971 | 17988.6468
[7 empty] | 11698 | 14803 | 1377046 | 2016-03-23 14:14 | 2016-03-23 16:25 | 131 | 11kV | 1834 | 14 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S4642 Kendall Phillip 400A fuse blown on A and B phase of distributor 2. Cause: Truck hit optus catinary wire on the corner of Kendall and Binnalong St causing contact with LV distributor wires. See OMS 1377273 1377046 1377076 | March | 2016 | 2016Q3 | 2016 | ZN195:PA29 | ZN195:PA29 | ZN00195/000029 | KU-RING-GAI | OH | Not Veg | 2016-03-23 | N | 131 | N | 4 | N | N | 1.1101 | 39.4971 | 1340.2331
[7 empty] | 11134 | 9181 | 1377123 | 2016-03-23 19:10 | 2016-03-23 22:05 | 175 | 11kV | 175 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 166587 A Phase Sub isolated to replace LV fuse assembly excluded OMS 1377123 | March | 2016 | 2016Q3 | 2016 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2016-03-23 | N | 175 | N | 4 | N | N | 1.1101 | 39.4971 | 127.8848
[7 empty] | 10487 | 1810 | 1377061 | 2016-03-23 15:12 | 2016-03-24 03:05 | 713 | 11kV | 713 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 166585 A Phase DOLF : 10 Amp Blown Lightning Arrestor Excluded OMS 1377061 | March | 2016 | 2016Q3 | 2016 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2016-03-23 | N | 713 | N | 4 | N | N | 1.1101 | 39.4971 | 521.0394
[7 empty] | 10648 | 3866 | 1377213 | 2016-03-24 10:07 | 2016-03-24 11:10 | 63 | 11kV | 34083 | 785 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Pa7 'S14805' fdr has tripped Signals: 11kv trip Relays: EFOC, EFI EFI's: S14935 11kV UGOH located in section of feeder between S14935/SwA, AB43777, LB40025 and PT11468 has failed See 1377867,8 Exclude 1377213,6 | March | 2016 | 2016Q3 | 2016 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | UG | Not Veg | 2016-03-24 | N | 43.4178 | N | 5 | N | N | 1.1101 | 39.4971 | 24906.8511
[7 empty] | 11671 | 14486 | 1377153 | 2016-03-24 07:49 | 2016-03-24 11:56 | 247 | 11kV | 85462 | 346 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | At S10999 Kogarah section of Panel 4 Fronm CP31028 to CP31104 to CP30626 lost supply Cause: Air break switch CP30626 failure See OMS 1377837 1377159 1377180 1377185 1377189 | March | 2016 | 2016Q3 | 2016 | ZN10999:PA4 | ZN10999:PA4 | ZN10999/000004 | GEORGES RIVER | OH | Not Veg | 2016-03-24 | N | 247 | N | 5 | N | N | 1.1101 | 39.4971 | 62453.1089
[7 empty] | 10429 | 889 | 1377247 | 2016-03-24 11:50 | 2016-03-24 12:35 | 45 | 11kV | 90 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166597 DOLF : 16 Amp Excluded OMS 1377247 | March | 2016 | 2016Q3 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2016-03-24 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 11986 | 17941 | 1377365 | 2016-03-24 22:48 | 2016-03-24 23:40 | 52 | 11kV | 2652 | 51 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 166605 C Phase ABS 74212 burning C phase open circuit Excluded 1377365 1377366 1377367 | March | 2016 | 2016Q3 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-03-24 | N | 52 | N | 5 | N | N | 1.1101 | 39.4971 | 1938.0034
[7 empty] | 11190 | 9849 | 1377362 | 2016-03-24 12:40 | 2016-03-25 01:15 | 755 | 11kV | 7550 | 10 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166606 Section isolated to remove tree Excluded OMS 1377362 | March | 2016 | 2016Q3 | 2016 | 509:33444 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-03-24 | N | 755 | N | 5 | N | N | 1.1101 | 39.4971 | 5517.3173
[7 empty] | 11008 | 7665 | 1377371 | 2016-03-25 06:07 | 2016-03-25 08:00 | 113 | 11kV | 21783 | 193 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.45 tripped on: Earth Fault, Fault Check and EFI UG cable fault from Pnl.45 to S4176 (Sw/B) to S6283 (Sw/B ) to S35862 (Sw/B) | March | 2016 | 2016Q3 | 2016 | ZN188:PA45 | ZN188:PA45 | ZN00188/000045 | SYDNEY | UG | Not Veg | 2016-03-25 | N | 112.8653 | N | 3 | N | N | 1.1101 | 39.4971 | 15918.3739
[7 empty] | 11437 | 12180 | 1377374 | 2016-03-25 07:34 | 2016-03-25 08:55 | 81 | 11kV | 19916 | 276 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.43 tripped on: A & C phase overcurrent, Fault Check, EFI Field EFIs: S35508, S8246, S7379 UG cable fault between S8246 (Sw/B) and S7379 (Sw/A) Pit lid damaged outside Ibis Hotel between poles LE31369 and LE31370 See 1377848 1377849 | March | 2016 | 2016Q3 | 2016 | ZN2568:PA43 | ZN2568:PA43 | ZN02568/000043 | INNER WEST | UG | Not Veg | 2016-03-25 | N | 72.1594 | N | 3 | N | N | 1.1101 | 39.4971 | 14554.0254
[7 empty] | 10906 | 6732 | 1377482 | 2016-03-25 21:51 | 2016-03-26 10:20 | 749 | 11kV | 1498 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 166608 A phase DOLF : 10 Amp Defective transformer replaced excluded OMS 1377458 | March | 2016 | 2016Q3 | 2016 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2016-03-25 | N | 749 | N | 3 | N | N | 1.1101 | 39.4971 | 1094.6942
[7 empty] | 10592 | 3146 | 1377562 | 2016-03-26 19:38 | 2016-03-26 22:51 | 193 | 11kV | 69104 | 1085 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166611 2 fault operation C phase Earth Fault bat found on pole iu-50248 Excluded oms 1377562 | March | 2016 | 2016Q3 | 2016 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2016-03-26 | N | 63.6903 | N | 1 | N | N | 1.1101 | 39.4971 | 50499.165
[7 empty] | 11711 | 14963 | 1377575 | 2016-03-27 06:41 | 2016-03-27 11:04 | 263 | 11kV | 292019 | 1482 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166613 1 fault operation Sensitive Earth Fault This is the 3rd SEF Fault in 2 months. No cause found. Feeder fully patrolled. Other LID reports # 165732 & 165935. There have been 6 trips on this feeder in the last 5 months. Excluded OMS 1377575 | March | 2016 | 2016Q3 | 2016 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2016-03-27 | N | 197.0439 | N | 3 | N | N | 1.1101 | 39.4971 | 213398.8721
[7 empty] | 11944 | 17388 | 1377595 | 2016-03-27 10:30 | 2016-03-27 12:20 | 110 | 11kV | 110 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166614 Single phase DOLF : 10 Amp Replaced both 3.15 trial fuses with 10 Amp Excluded OMS 1377595 | March | 2016 | 2016Q3 | 2016 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2016-03-27 | N | 110 | N | 3 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 10610 | 3364 | 1377636 | 2016-03-27 16:20 | 2016-03-27 18:21 | 121 | 11kV | 17753 | 162 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166618 2 fault operatioon B phase Overcurrent flying fox at pole FR-75206 Excluded oms 1377636 | March | 2016 | 2016Q3 | 2016 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2016-03-27 | N | 109.5864 | N | 3 | N | N | 1.1101 | 39.4971 | 12973.3688
[7 empty] | 12173 | 19659 | 1377676 | 2016-03-28 07:19 | 2016-03-28 08:34 | 75 | 11kV | 14250 | 190 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166622 3 fault operations Overcurrent Scott Carson did a patrol in area advised by customer who saw arcing on a pole at Louth Park Rd x Dagworth Rd. Found nothing. | March | 2016 | 2016Q3 | 2016 | 532:83307 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Veg | 2016-03-28 | N | 75 | N | 2 | N | N | 1.1101 | 39.4971 | 10413.4797
[7 empty] | 11770 | 15596 | 1377698 | 2016-03-28 09:49 | 2016-03-28 11:32 | 103 | 11kV | 2266 | 22 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZN12570 Avoca section of Pa33 PT62041 Cullens Melville 11kV 31.5K footpath Phase HDO Operated. Fuse failed mechanically on crimp Restoration time taken from OMS time incompleted. CR report does not have restoration time. See 1377870 exclude 1377698,9 | March | 2016 | 2016Q3 | 2016 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2016-03-28 | N | 103 | N | 2 | N | N | 1.1101 | 39.4971 | 1655.926
[7 empty] | 11028 | 7816 | 1377801 | 2016-03-29 03:58 | 2016-03-29 05:04 | 66 | 11kV | 67496 | 1123 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman Panel 23 "Brady Ourimbah, Harbour Mosman" fdr tripped Relays - A phase Overcurrent and IOC, FI, Fault CHeck Signals: 11kv trip, Zone Earth, Tx1 Group Earth EFI's S6694 S48858 S2781 S569 S48855 S7919 UG feeder fault from S7919/SwB to S36124/SwA See 1377893,919 exclude 1377801 | March | 2016 | 2016Q3 | 2016 | ZN180:PA23 | ZN180:PA23 | ZN00180/000023 | MOSMAN | UG | Not Veg | 2016-03-29 | N | 60.1033 | N | 6 | N | N | 1.1101 | 39.4971 | 49324.086
[7 empty] | 11845 | 16514 | 1377839 | 2016-03-29 08:32 | 2016-03-29 10:00 | 88 | 11kV | 88 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166626 C phase DOLF : 16 Amp Excluded OMS 1377839 | March | 2016 | 2016Q3 | 2016 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2016-03-29 | N | 88 | N | 6 | N | N | 1.1101 | 39.4971 | 64.3078
[7 empty] | 12102 | 18950 | 1378049 | 2016-03-29 17:15 | 2016-03-29 18:15 | 60 | 11kV | 1860 | 31 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166641 Phases A & B 11Kv wrap unravelled at pole GU24364 | March | 2016 | 2016Q3 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2016-03-29 | N | 60 | N | 6 | N | N | 1.1101 | 39.4971 | 1359.2331
[7 empty] | 11882 | 16828 | 1377796 | 2016-03-29 00:29 | 2016-03-29 19:50 | 1161 | 11kV | 21413 | 153 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mountain" RE45071 Central Mangrove tripped, reclosed, tripped and locked out Truck hot pole near LK43991 and snapped it at the base. DOp and lineworker repaired and restored See 1378506,7 Exclude 1377796 | March | 2016 | 2016Q3 | 2016 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2016-03-29 | N | 139.9542 | N | 6 | N | N | 1.1101 | 39.4971 | 15647.9888
[7 empty] | 10676 | 4214 | 1378086 | 2016-03-29 22:24 | 2016-03-30 00:05 | 101 | 11kV | 101 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 166645 DOLF : 10 Amp Possible fuse fatigue Excluded OMS 1378086 | March | 2016 | 2016Q3 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2016-03-29 | N | 101 | N | 6 | N | N | 1.1101 | 39.4971 | 73.8078
[7 empty] | 11963 | 17646 | 1378097 | 2016-03-30 06:07 | 2016-03-30 07:00 | 53 | 11kV | 3816 | 72 | HV | Vegetation Blow/Fall In | Vegetation | Air Break Switch | Unplanned | Rain Light | N | Ex Zn12630 Peats Ridge section of Pa3 IR49206 Mangrove Mountain West triped amd tripped Relays OC Trip, Lockout Small branch across phases at LK42143 removed by DOp | March | 2016 | 2016Q3 | 2016 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2016-03-30 | N | 53 | N | 3 | N | N | 1.1101 | 39.4971 | 2788.6202
[7 empty] | 11610 | 13843 | 1378152 | 2016-03-30 09:10 | 2016-03-30 10:35 | 85 | 11kV | 425 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166658 Single phase DOLF : 10 Amp Excluded OMS 1378152 | March | 2016 | 2016Q3 | 2016 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2016-03-30 | N | 85 | N | 3 | N | N | 1.1101 | 39.4971 | 310.5775
[7 empty] | 11705 | 14858 | 1378093 | 2016-03-29 04:38 | 2016-03-30 11:25 | 1846.7833 | 11kV | 389253 | 2367 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 166646 B & C phase Overcurrent targets sw 11458 C phase OC sw 33409 B-C OC Faulty UGOH at pole OR-30086 SECTION ISOLATED FOR REPAIRS Excluded oms 1378093, 1378103, 1378095, 1378096 | March | 2016 | 2016Q3 | 2016 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | Unknown | Unknown | 2016-03-29 | N | 164.4499 | N | 6 | N | N | 1.1101 | 39.4971 | 284454.6114
[7 empty] | 11762 | 15513 | 1378449 | 2016-03-31 10:16 | 2016-03-31 11:32 | 76 | 11kV | 80992 | 1090 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Panel 6 "SCC Racecourse" RE50531 Showground Maliwa 0.35 tripped on Field Relay operations on recloser: OC, SEF and lockout 11kv bond on AB44599 open cct line side See 1378692,3 exclude 1378449 | March | 2016 | 2016Q3 | 2016 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Not Veg | 2016-03-31 | N | 74.3046 | N | 5 | N | N | 1.1101 | 39.4971 | 59186.5647
[7 empty] | 11141 | 9316 | 1378350 | 2016-03-30 20:25 | 2016-03-31 13:30 | 1025 | 11kV | 61168 | 183 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Circuit Breaker | Unplanned | No Weather Impact | N | At S220 Burwood rd the Tx1 feeder (Sw/B) tripped on: Relays: Earth fault, intertrip send, EFI At Zone 2835 Burwood Panel 29 "Parramatta Esther" - Relays: intertrip receive (Intertrip link open) Remarks: flooding. S4246 Railway Burleigh was found to have about 1 metre of water in it. After pumping the water out Dop reports that the 11kv RMI endbox on Sw/A at S4246 is warped. Dist 2 at S4246 was left de-energised as the LV board is full of mud. | March | 2016 | 2016Q3 | 2016 | ZN2835:PA9 | ZN2835:PA29 | ZN02835/000029 | BURWOOD | Unknown | Unknown | 2016-03-30 | N | 334.2514 | N | 3 | N | N | 1.1101 | 39.4971 | 44699.7702
[7 empty] | 12222 | 20144 | 1378545 | 2016-03-31 15:03 | 2016-03-31 16:10 | 67 | 11kV | 201 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166678 A Phase - Fuse 10 Amp Details of bird strike not provided refer to 1378562 | March | 2016 | 2016Q3 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-03-31 | N | 67 | N | 5 | N | N | 1.1101 | 39.4971 | 146.8849
[7 empty] | 11398 | 11822 | 1378569 | 2016-03-31 16:25 | 2016-03-31 17:19 | 54 | 11kV | 94230 | 1745 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166680 2 Fault operations, C Phase, Overcurrent Trees Growing into Mins, with branch on feeder near sub 3219 | March | 2016 | 2016Q3 | 2016 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2016-03-31 | N | 54 | N | 5 | N | N | 1.1101 | 39.4971 | 68860.5047
[7 empty] | 11238 | 10248 | 1378583 | 2016-03-31 17:01 | 2016-03-31 18:01 | 60 | 11kV | 9060 | 151 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Panel 12 RE44753 Bunning Creek rec one shot for bushfire unable to be made auto due to RTU problems Tree on 11kv near LB46564 | March | 2016 | 2016Q3 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2016-03-31 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 6620.7808
[7 empty] | 11541 | 13039 | 1378624 | 2016-04-01 05:13 | 2016-04-01 06:45 | 92.3333 | 11kV | 92.3333 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166685 Single phase DOLF : 10 Amp Excluded OMS 1378625 | April | 2016 | 2016Q4 | 2016 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2016-04-01 | N | 92.3333 | N | 3 | N | N | 1.1101 | 39.4971 | 67.4745
[7 empty] | 12016 | 18223 | 1378522 | 2016-03-31 13:19 | 2016-04-01 08:30 | 1151.25 | 11kV | 1151.25 | 1 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Flooding | March | 2016 | 2016Q3 | 2016 | ZN2835:PA9 | ZN2835:PA9 | ZN02835/000009 | BURWOOD | Unknown | Not Veg | 2016-03-31 | N | 1151.25 | N | 5 | N | N | 1.1101 | 39.4971 | 841.2995
[7 empty] | 12161 | 19506 | 1378646 | 2016-04-01 08:45 | 2016-04-01 11:41 | 176 | 11kV | 173091 | 992 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn35900 Potts Hill 11kv Panel #20 labelled "S35889 Muir Dasea" tripped & reclosed & tripped: relays: Timed Earth fault, B phase overcurrent, EFI, lockout relay Signals: Tx2 Group Earth, CB20 open, CB20 closed Tx2 group earth, Cb20 open Field EFI's Nil Remarks: UG fault. 11kv underground feeder fault from : "Sw.A" @ S35889 Muir Dasea to "Sw/A" @ S4314 Claremont Res Tester/Jointer Permit issued @ 1130 Sw/A @ S35889 Muir Dasea. Note: EFI @ S35889 Muir Dasea did not operate on multiple occassions and is FAULTY Region please replace | April | 2016 | 2016Q4 | 2016 | ZN35900:PA20 | ZN35900:PA20 | ZN35900/000020 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-04-01 | N | 174.4869 | N | 3 | N | N | 1.1101 | 39.4971 | 126489.7975
[7 empty] | 11899 | 16946 | 1379004 | 2016-04-01 11:19 | 2016-04-01 11:45 | 26 | 11kV | 2002 | 77 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn9245 Engadine - Section of Pnl.38 from AB35718 experienced low volts due to burnt off centre phase bond. Abnormal: LB35535 and AB35463 tee PT6044 isoalted for job #377729 | April | 2016 | 2016Q4 | 2016 | ZN9245:PA38 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | OH | Not Veg | 2016-04-01 | N | 26 | N | 3 | N | N | 1.1101 | 39.4971 | 1463.0026
[7 empty] | 11214 | 10027 | 1378847 | 2016-04-02 05:53 | 2016-04-02 12:05 | 372 | 11kV | 5952 | 16 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166703 Single phase DOLF 11kv mains down between poles GR-47460 & GR-47461 off Majors Lane Keinbah. mains are rusted steel please investigate if mains need replacing. | April | 2016 | 2016Q4 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2016-04-02 | N | 372 | N | 3 | N | N | 1.1101 | 39.4971 | 4349.546
[7 empty] | 11180 | 9710 | 1378901 | 2016-04-02 17:00 | 2016-04-02 18:48 | 108 | 11kV | 9072 | 84 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | No Weather Impact | N | At PT1508 Rabaul Road 50amp footpath phase hdo blown Remarks: cause not ascertained. | April | 2016 | 2016Q4 | 2016 | ZN1850:PA10 | ZN1850:PA40 | ZN01850/000040 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-04-02 | N | 108 | N | 3 | N | N | 1.1101 | 39.4971 | 6629.55
[7 empty] | 10932 | 6929 | 1378894 | 2016-04-02 14:43 | 2016-04-02 19:00 | 257 | 11kV | 3325 | 30 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12570 Avoca Pa37 "Avoca Beach" fdr tripped, reclosed, tripped and locked out on Relays: Earth Fault, C Phase IOC, EFI and lockout Signals: 11kv Pa37 trip EFI's: S18439 S49066 ABNORMAL: AB40431 open SwB 61891 Closed 11kv fdr fault from UGOH (Avoca dr nr Townsend Av) to SwA S18135 See 1379361,2,3 exclude 1378894,905,9329,31 | April | 2016 | 2016Q4 | 2016 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | UG | Not Veg | 2016-04-02 | N | 110.8333 | N | 3 | N | N | 1.1101 | 39.4971 | 2429.8119
[7 empty] | 11114 | 8847 | 1378926 | 2016-04-03 03:35 | 2016-04-03 04:44 | 69.1167 | 11kV | 31517.2 | 456 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12660 Woy Woy ex Pa10R RE49684 Brisban water Lara has tripped on OC trip Tree branch on OH mains, Near LB48312 | April | 2016 | 2016Q4 | 2016 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | OH | Veg | 2016-04-03 | N | 69.1167 | N | 3 | N | N | 1.1101 | 39.4971 | 23031.8402
[7 empty] | 10565 | 2763 | 1378964 | 2016-04-03 12:19 | 2016-04-03 12:55 | 36 | 11kV | 252 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Snow / Hail Storm | N | LID 166709 B phase DOLF : 10 Amp Excluded OMS 1378964 | April | 2016 | 2016Q4 | 2016 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2016-04-03 | N | 36 | N | 3 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 11193 | 9875 | 1378967 | 2016-04-03 12:35 | 2016-04-03 16:15 | 220 | 11kV | 1320 | 6 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | S8167 Tech College Thomas - Tx No.1 & No.2 tripped on summated O/C Fault on customers main switchboard which did not grade. | April | 2016 | 2016Q4 | 2016 | ZN901:PA2 | ZN901:PA2 | ZN00901/000002 | SYDNEY | Unknown | Not Veg | 2016-04-03 | N | 220 | N | 3 | N | N | 1.1101 | 39.4971 | 964.6171
[7 empty] | 10878 | 6397 | 1379005 | 2016-04-04 02:12 | 2016-04-04 04:06 | 114 | 11kV | 101403 | 1093 | HV | Animal Possum | Animal | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn12620 Noraville Pa10 "uff Point" tripped and locked out on OC and EF 11kv trip Cause not ascertained. Possibly Possum Possibly related to outage at PT18578 1379330 See 1379338,9 exclude 1379005,14 | April | 2016 | 2016Q4 | 2016 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Not Veg | 2016-04-04 | N | 92.7749 | N | 4 | N | N | 1.1101 | 39.4971 | 74102.3215
[7 empty] | 11280 | 10682 | 1379136 | 2016-04-04 11:37 | 2016-04-04 14:30 | 173 | 11kV | 1384 | 8 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166719 A Phase DOLF : 10 Amp Excluded OMS 1379136 | April | 2016 | 2016Q4 | 2016 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2016-04-04 | N | 173 | N | 4 | N | N | 1.1101 | 39.4971 | 1011.3864
[7 empty] | 10597 | 3206 | 1379235 | 2016-04-04 16:50 | 2016-04-04 17:48 | 58 | 11kV | 116 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166724 A Phase DOLF : 10 Amp Excluded OMS 1379235 | April | 2016 | 2016Q4 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2016-04-04 | N | 58 | N | 4 | N | N | 1.1101 | 39.4971 | 84.7694
[7 empty] | 10390 | 341 | 1379272 | 2016-04-04 19:55 | 2016-04-05 12:30 | 995 | 11kV | 212394 | 1066 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At S1193 Lindfield Panel 27 Tripped on Relays: A and C phase IOC and EFI, Lockout, Reclose Signals: Group Earth Vehicle Hit Pole and Wires down. See OMS 1379598 1379600 1379601 1379272 1379274 | April | 2016 | 2016Q4 | 2016 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Not Veg | 2016-04-04 | N | 199.2439 | N | 4 | N | N | 1.1101 | 39.4971 | 155211.2706
[7 empty] | 10537 | 2442 | 1379419 | 2016-04-05 12:43 | 2016-04-05 13:15 | 32 | 11kV | 544 | 17 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 166743 A phase DOLF : 40 Amp Excluded oms 1379419 | April | 2016 | 2016Q4 | 2016 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Not Veg | 2016-04-05 | N | 32 | N | 3 | N | N | 1.1101 | 39.4971 | 397.5392
[7 empty] | 12032 | 18331 | 1379476 | 2016-04-05 15:09 | 2016-04-05 16:30 | 81 | 11kV | 19464 | 248 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S5868 Gore Hill Panel 17 tripped on Relays: Earth Fault with Fault Check. Signals: 11kV Trip, Zone Earth and TX3 Group Earth. Cause: Cable Fault between S3266 and S7770 See OMS 1379661 1379476 1379662 | April | 2016 | 2016Q4 | 2016 | ZN5868:PA17 | ZN5868:PA17 | ZN05868/000017 | LANE COVE | UG | Not Veg | 2016-04-05 | N | 78.4839 | N | 3 | N | N | 1.1101 | 39.4971 | 14223.7171
[7 empty] | 11535 | 12986 | 1379558 | 2016-04-05 20:21 | 2016-04-05 22:30 | 129 | 11kV | 129 | 1 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT12419 Bumble CK Ourimbah 0.9 11kv HDO fuse fell out of fuse carrier. Tree branh on mains adjacent PT12419 See 1379642 exclude 1379558 | April | 2016 | 2016Q4 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2016-04-05 | N | 129 | N | 3 | N | N | 1.1101 | 39.4971 | 94.2694
[7 empty] | 10493 | 1900 | 1379567 | 2016-04-06 03:43 | 2016-04-06 09:30 | 347 | 11kV | 694 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa1 "Grants Rd" fdr PT14997 Forest Bumble Hill 3.2 Footpath 10Amp HDO blew due to Fuse Fatigue See 1379960 exclude 1379567 | April | 2016 | 2016Q4 | 2016 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2016-04-06 | N | 347 | N | 3 | N | N | 1.1101 | 39.4971 | 507.1547
[7 empty] | 10602 | 3248 | 1379855 | 2016-04-06 09:53 | 2016-04-06 10:31 | 38 | 11kV | 1292 | 34 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | ex Galston Pa8. Supply manually interrupted between CP62108 to CP2871 Insulators Cracked and Failed When Operating CP2871 for DAROS 3768991 Feeder De energised for staff safety | April | 2016 | 2016Q4 | 2016 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2016-04-06 | N | 38 | N | 3 | N | N | 1.1101 | 39.4971 | 944.1555
[7 empty] | 11078 | 8455 | 1379819 | 2016-04-06 20:23 | 2016-04-07 10:20 | 837 | 11kV | 14907 | 81 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 166760 6 fault operations Sensitive Earth Fault Tx at S-51270 Faulty needs replacement. Excluded OMS 1379819 ## | April | 2016 | 2016Q4 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2016-04-06 | N | 184.037 | N | 3 | N | N | 1.1101 | 39.4971 | 10893.5959
[7 empty] | 10456 | 1389 | 1380043 | 2016-04-07 17:00 | 2016-04-07 19:30 | 150 | 11kV | 37950 | 253 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 1380043 Fdr isolated to repair broken 11kV termination crossarm at sub 6523. | April | 2016 | 2016Q4 | 2016 | 509:33444 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2016-04-07 | N | 150 | N | 2 | N | N | 1.1101 | 39.4971 | 27732.7407
[7 empty] | 10546 | 2524 | 1380075 | 2016-04-07 20:44 | 2016-04-07 23:55 | 191 | 11kV | 955 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 166774 L/FUSE 74921 OPENED TO ISOLATE HOT JOINT ON 11KV MAINS. | April | 2016 | 2016Q4 | 2016 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2016-04-07 | N | 191 | N | 2 | N | N | 1.1101 | 39.4971 | 697.8858
[7 empty] | 11168 | 9582 | 1380083 | 2016-04-08 04:35 | 2016-04-08 06:03 | 88 | 11kV | 79589 | 1337 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 16 Tripped and Locked out on C phase OC DOp Patrolled OH section and cause not ascertained See OMS 1380507 1380510 1380511 1380083 | April | 2016 | 2016Q4 | 2016 | ZN129:PA16 | ZN129:PA46 | ZN00129/000046 | RYDE | OH | Veg | 2016-04-08 | N | 59.528 | N | 1 | N | N | 1.1101 | 39.4971 | 58161.2937
[7 empty] | 12105 | 18993 | 1380325 | 2016-04-09 12:04 | 2016-04-09 15:00 | 176 | 11kV | 3344 | 19 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | S10269 Vanessa The Crescent No.2 - Tx No.1 HV fuse blown. Fuse failure - defective tee off switch in No.1 RMI. Failed to operate trip bar. | April | 2016 | 2016Q4 | 2016 | ZN10993:PA33 | ZN10993:PA33 | ZN10993/000033 | GEORGES RIVER | OH | Not Veg | 2016-04-09 | N | 176 | N | 4 | N | N | 1.1101 | 39.4971 | 2443.6966
[7 empty] | 11981 | 17828 | 1380351 | 2016-04-09 16:11 | 2016-04-09 17:30 | 79 | 11kV | 59855 | 2033 | HV | Animal Bird | Animal | Bond | Unplanned | No Weather Impact | N | Zn12640 Umina Pa13 "Patonga" feeder tripped and reclosed Signals: 11kv trip Relays: A ph overcurrent, EFI, SEF (after switching) EFI's: nil Bird strike at PT18022 caused 11kv burnt bond at 12 Kabhibah Rd, Umina (near LB45147) See 1380635,7,9 exclude 1380351,2,3,65 | April | 2016 | 2016Q4 | 2016 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2016-04-09 | N | 29.4417 | N | 4 | N | N | 1.1101 | 39.4971 | 43740.2686
[7 empty] | 11626 | 14022 | 1380369 | 2016-04-09 17:56 | 2016-04-09 19:20 | 84 | 11kV | 10984 | 132 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT10117 Carrington Pearl - roadside phase HDO failed. Fuse failure See 1380370 GIS: 1380377 1380369 CC1: 22-"Refer to SOp" | April | 2016 | 2016Q4 | 2016 | ZN10993:PA27 | ZN10993:PA27 | ZN10993/000027 | GEORGES RIVER | OH | Not Veg | 2016-04-09 | N | 83.2121 | N | 4 | N | N | 1.1101 | 39.4971 | 8026.7832
[7 empty] | 11734 | 15204 | 1380380 | 2016-04-09 22:03 | 2016-04-10 01:40 | 217 | 11kV | 217 | 1 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | No Weather Impact | N | Sub 7827 Weeroona Rail No.1 interrupted to carry out repairs on broken x arm following car hit pole, section of Panel No.6 "Lewis St" feeder ex sub 35900 Potts Hill. Remarks: vehicle hit pole. 1 bay west of AB3290 | April | 2016 | 2016Q4 | 2016 |  |  |  | CUMBERLAND | OH | Not Veg | 2016-04-09 | N | 217 | N | 4 | N | N | 1.1101 | 39.4971 | 158.5772
[7 empty] | 11921 | 17152 | 1380446 | 2016-04-10 14:42 | 2016-04-10 20:55 | 373 | 11kV | 34292 | 404 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166795 Tree branch on mains opposite sub 1573. Crew retensioned mains & replaced insulators under AP. Excluded OMS 1380446 & 1380455 | April | 2016 | 2016Q4 | 2016 | 224:80329 | 224:80329 | ZN00224/080329 | LAKE MACQUARIE | OH | Veg | 2016-04-10 | N | 84.8812 | N | 2 | N | N | 1.1101 | 39.4971 | 25059.5822
[7 empty] | 11086 | 8608 | 1380467 | 2016-04-10 23:31 | 2016-04-11 01:35 | 124 | 11kV | 52094 | 484 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN262 Marrickville: 11kv feeder Panel No: 27 "Marrickville aux No1" feeder tripped Relays: B phase E/F, EFI, fault check Signals: No1 Grp Earth, Zone Earth, 11kv trip Field EFI's: S49749 Remarks: UG fault in pit O/S 243 Sydenham Rd in: section of 11kv feeder from S49749 Marrickville Aux No1 (Sw/B) to HAZ RMI @ S5259 Coronation Park (Sw/A) to S2062 Yabsley Ave (Sw/A) tee S5132 Centennial St Nth. Note: Due Haz LV// req to extend isolation | April | 2016 | 2016Q4 | 2016 | ZN262:PA27 | ZN262:PA27 | ZN00262/000027 | INNER WEST | UG | Not Veg | 2016-04-10 | N | 107.6322 | N | 2 | N | N | 1.1101 | 39.4971 | 38068.7587
[7 empty] | 12159 | 19494 | 1380482 | 2016-04-11 05:33 | 2016-04-11 08:00 | 147.4333 | 11kV | 2064.0667 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166796 A & B Phase DOLF : 20 Amp | April | 2016 | 2016Q4 | 2016 | 512:48048 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2016-04-11 | N | 147.4333 | N | 3 | N | N | 1.1101 | 39.4971 | 1508.359
[7 empty] | 12175 | 19672 | 1380663 | 2016-04-11 13:50 | 2016-04-11 15:30 | 100 | 11kV | 1000 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 166807 A Phase DOLF : 16 Amp 4 small dead birds found at sub. Tx volts: 244V TX Load: Aph - 14A, Bph - 4A, Cph - 4A Excluded OMS No. 1380663 | April | 2016 | 2016Q4 | 2016 | 528:83014 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Veg | 2016-04-11 | N | 100 | N | 3 | N | N | 1.1101 | 39.4971 | 730.7705
[7 empty] | 11402 | 11857 | 1380720 | 2016-04-11 17:17 | 2016-04-11 17:35 | 18 | 11kV | 9486 | 527 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa2 "Gunderman" fdr RE44961 Morgans Pacific 0.4 tripped and locked out on overcurrent during switching. Overload See 1380720 GIS 1380734 | April | 2016 | 2016Q4 | 2016 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | Unknown | Not Veg | 2016-04-11 | N | 18 | N | 3 | N | N | 1.1101 | 39.4971 | 6932.089
[7 empty] | 11259 | 10506 | 1380878 | 2016-04-12 10:38 | 2016-04-12 11:19 | 41 | 11kV | 4592 | 112 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 166816 Earth Fault Sw 3609 A/R was non Auto for SI 12810 E/F 84A | April | 2016 | 2016Q4 | 2016 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2016-04-12 | N | 41 | N | 4 | N | N | 1.1101 | 39.4971 | 3355.6982
[7 empty] | 10838 | 5909 | 1380868 | 2016-04-12 10:03 | 2016-04-12 12:05 | 122 | 11kV | 56014 | 892 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Panel 24R LB49513 fdr tripped on Relays: EFI, O/C, C phase to Earth EFI's: S18726 S11984 Signals: 11kv trip C phase UGOH fault between S11984:SwA to AB42214 See 1381073,4,5,6,7 exclude 1380868 | April | 2016 | 2016Q4 | 2016 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | Unknown | Unknown | 2016-04-12 | N | 62.796 | N | 4 | N | N | 1.1101 | 39.4971 | 40933.3791
[7 empty] | 11360 | 11577 | 1380908 | 2016-04-12 12:08 | 2016-04-12 17:08 | 300 | 11kV | 16094 | 124 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 166820 2 Fault Operations A & B phase Overcurrent, Earth Fault Sw 3609 A/R was non Auto for SI 12810 E/F 84A | April | 2016 | 2016Q4 | 2016 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2016-04-12 | N | 129.7903 | N | 4 | N | N | 1.1101 | 39.4971 | 11761.0205
[7 empty] | 11683 | 14604 | 1380984 | 2016-04-12 18:28 | 2016-04-12 21:50 | 202 | 11kV | 202 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 166823 Single phase LL Clamp lead broken at Roeth sub 52061. Excluded OMS No. 1380984 | April | 2016 | 2016Q4 | 2016 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2016-04-12 | N | 202 | N | 4 | N | N | 1.1101 | 39.4971 | 147.6156
[7 empty] | 11011 | 7689 | 1381015 | 2016-04-13 07:43 | 2016-04-13 09:10 | 87 | 11kV | 41915 | 493 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S35500 Top Ryde Panel; 34 tripped on A and B phase OC, Fault Check and EFI Abnormal Switching: LB1590 Closed and SW/B open at S35738 Cause: At First arrival all efi'S Down. Feeder tried back and failed. UGOH near S7615 faulty See OMS 1381486 1381487 See OMS 1381486 1381487 1381015 | April | 2016 | 2016Q4 | 2016 | ZN35500:PA34 | ZN4545:PA4 | ZN04545/000004 | RYDE | Unknown | Unknown | 2016-04-13 | N | 85.0203 | N | 4 | N | N | 1.1101 | 39.4971 | 30630.2457
[7 empty] | 12014 | 18211 | 1381060 | 2016-04-13 09:11 | 2016-04-13 09:53 | 42 | 11kV | 49371 | 1678 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 166824 1 fault operation B & C phase Overcurrent Tree on main cleared by Dop at Pole JU-63261 Edward St Merewether. Excluded OMS 1381060 | April | 2016 | 2016Q4 | 2016 | 256:80646 | 256:80646 | ZN00256/080646 | NEWCASTLE | OH | Veg | 2016-04-13 | N | 29.4225 | N | 4 | N | N | 1.1101 | 39.4971 | 36078.8706
[7 empty] | 10534 | 2407 | 1381158 | 2016-04-13 14:55 | 2016-04-13 16:05 | 70 | 11kV | 420 | 6 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 166838 Single phase Wire off pin | April | 2016 | 2016Q4 | 2016 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2016-04-13 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 11552 | 13120 | 1381138 | 2016-04-13 13:41 | 2016-04-13 22:30 | 529 | 11kV | 12923 | 249 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166839 2 fault operations 3 phase Overcurrent Excavator brought down mains at P. LI-81308. During restoration the handle on ABS 3551 Broke. Then we had a blown tapping. Excluded OMS 1381138 | April | 2016 | 2016Q4 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2016-04-13 | N | 51.8996 | N | 4 | N | N | 1.1101 | 39.4971 | 9443.7472
[7 empty] | 12248 | 20409 | 1381465 | 2016-04-14 23:22 | 2016-04-15 00:45 | 83 | 11kV | 58764 | 708 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3154 St Ives Pa12 "Killeaton Warrimo" tripped on Relays: C phase IOC, timed overcurrent, lock out and timing relay and EFI Signals: 11kv trip, Tx1 Group Earth and Zone Earth EFI's: Nil Possum found on UGOH to PT83 Bannockburn McRae & Frontline feeder fault | April | 2016 | 2016Q4 | 2016 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | UG | Not Veg | 2016-04-14 | N | 83 | N | 1 | N | N | 1.1101 | 39.4971 | 42942.998
[7 empty] | 10754 | 5015 | 1381469 | 2016-04-15 01:47 | 2016-04-15 03:08 | 81 | 11kV | 134009 | 1680 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn4545 Meadowbank Panel 29 tripped on Relays: Fault check and EFI Signals: 11kV Trip, Zone Earth and Tx2 Group Earth. Underground feeder fault from S46659 to S48870 to S48871. See OMS 1381513 1381514 1381515 1381469 | April | 2016 | 2016Q4 | 2016 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | UG | Not Veg | 2016-04-15 | N | 79.7673 | N | 3 | N | N | 1.1101 | 39.4971 | 97929.8246
[7 empty] | 12079 | 18743 | 1381609 | 2016-04-15 16:00 | 2016-04-15 17:30 | 90 | 11kV | 93330 | 1037 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 166867 2 fault operation A & C phase Overcurrent UGM near UGOH SW-60985 damaged by contractor working at air port PAUL MOLLISON SAID WORKER CLEARING CONCRETE, HAS HIT 11KV CABLE IN THE GROUND. APPROX 25 METERS NORTH OF AIRPORT. PERSON ON SITE IS LANCE PALMER 0413490601. POLE NUMBER SW6 -985 Excluded OMS 1381617 | April | 2016 | 2016Q4 | 2016 | 222:33600 | 222:33600 | ZN00222/033600 | LAKE MACQUARIE | UG | Not Veg | 2016-04-15 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 68202.8112
[7 empty] | 11930 | 17219 | 1381629 | 2016-04-15 13:06 | 2016-04-15 22:55 | 589 | 11kV | 2945 | 5 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 166868 C phase Earth Fault repaired UGOH cable fault pole LI-40046. | April | 2016 | 2016Q4 | 2016 | 514:18146 | 514:18156 | ZN00514/018156 | MUSWELLBROOK | Unknown | Unknown | 2016-04-15 | N | 589 | N | 3 | N | N | 1.1101 | 39.4971 | 2152.1191
[7 empty] | 10950 | 7095 | 1381742 | 2016-04-16 18:30 | 2016-04-16 21:02 | 152 | 11kV | 152 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166872 Overcurrent | April | 2016 | 2016Q4 | 2016 |  |  |  | SINGLETON | OH | Veg | 2016-04-16 | N | 152 | N | 2 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 11179 | 9701 | 1381755 | 2016-04-16 22:05 | 2016-04-16 23:50 | 105 | 11kV | 1995 | 19 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 166874 LLC burnt through bail clamp. LV interconnected. New bail clamp required. Excluded OMS 1381752,1381754,1381756. | April | 2016 | 2016Q4 | 2016 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2016-04-16 | N | 105 | N | 2 | N | N | 1.1101 | 39.4971 | 1457.8872
[7 empty] | 12042 | 18426 | 1381807 | 2016-04-17 10:36 | 2016-04-17 12:23 | 107 | 11kV | 268035 | 2505 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn 35800 Bankstown the 11kv Panel 1 & the 132kv/11kv Tx 11 tripped on: Tx Panel 82: multitrip 3A - PR3A, multitrip 4A - PR4A Tx11A1 protection Panel: Back up OC trip indicator - PI21A Backup OC Panel: 11kv fdr group 1 BUOC - PR multitrip Panel 1: 50 TBC - inst OC B & C phase, BUOC - OC B & C phase Remarks: tree/branch on OH mains. A tree branch was found on the 11kv OH outside 34 Oxford Ave, Bankstown, also refer previous event on panels 5 and 8 - OMS 1381786 | April | 2016 | 2016Q4 | 2016 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-04-17 | N | 107 | N | 10 | N | N | 1.1101 | 39.4971 | 195872.0723
[7 empty] | 11819 | 16214 | 1381821 | 2016-04-17 12:14 | 2016-04-17 13:42 | 88 | 11kV | 98208 | 1116 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1673 Turramurra Panel 13 feeder tripped on Relays: C phase IOC, Earth Fault, Fault Check, UF and EFI Signals: 11kV Trip, Tx3 Group Earth and Zone Earth. Abnromal Switching: S4711 SW/A open, S4721 Cliff Boundary SW/B Closed Cause: Front Line Feeder fault from Zn1673 Turramurra Panel 13 to S4705 King Eastern See OMS 1382244 1381821 1381823 | April | 2016 | 2016Q4 | 2016 | ZN1673:PA13 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | UG | Not Veg | 2016-04-17 | N | 88 | N | 10 | N | N | 1.1101 | 39.4971 | 71767.5098
[7 empty] | 10523 | 2321 | 1381845 | 2016-04-17 14:13 | 2016-04-17 15:00 | 47 | 11kV | 47 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 166893 A phase DOLF : 10 Amp Excluded OMS 1381845 | April | 2016 | 2016Q4 | 2016 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2016-04-17 | N | 47 | N | 10 | N | N | 1.1101 | 39.4971 | 34.3462
[7 empty] | 10870 | 6286 | 1381848 | 2016-04-17 14:30 | 2016-04-17 15:10 | 40 | 11kV | 80 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 166894 C phase DOLF : 20 Amp Fatigue Excluded OMS 1381848 & 1381849 | April | 2016 | 2016Q4 | 2016 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2016-04-17 | N | 40 | N | 10 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 12231 | 20251 | 1381854 | 2016-04-17 14:57 | 2016-04-17 15:20 | 23 | 11kV | 46 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 166896 Single phase DOLF : 10 Amp Excluded OMS 1381854 | April | 2016 | 2016Q4 | 2016 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2016-04-17 | N | 23 | N | 10 | N | N | 1.1101 | 39.4971 | 33.6154
[7 empty] | 11132 | 9123 | 1381843 | 2016-04-17 13:59 | 2016-04-17 17:00 | 181 | 11kV | 724 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 166897 C Phase DOLF : 10 Amp Failure of DOLF Carrier Excluded OMS 1381843 | April | 2016 | 2016Q4 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2016-04-17 | N | 181 | N | 10 | N | N | 1.1101 | 39.4971 | 529.0778
[7 empty] | 11863 | 16637 | 1381862 | 2016-04-17 15:50 | 2016-04-17 17:43 | 113 | 11kV | 324061 | 3363 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166898 1 fault operation Local Back up Branch on fdr 80074 near ABS 19159 failed to clear due to faulty protection relay back up protection tripped 11kv bus section no 1 Excluded OMS 1381862 & 1381864 | April | 2016 | 2016Q4 | 2016 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Veg | 2016-04-17 | N | 96.3607 | N | 10 | N | N | 1.1101 | 39.4971 | 236814.2206
[7 empty] | 10807 | 5526 | 1381890 | 2016-04-17 18:31 | 2016-04-17 23:20 | 289 | 11kV | 11271 | 39 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 166902 Defective transformer Low volts on arrival A 241V, 32A - B 236V, 88A - C 213V, 31A placed in LV // then volts = 240-238-228 Tx faulty to be replaced Excluded oms1381890 & 1381903 | April | 2016 | 2016Q4 | 2016 | 258:80784 | 258:80784 | ZN00258/080784 | NEWCASTLE | OH | Not Veg | 2016-04-17 | N | 289 | N | 10 | N | N | 1.1101 | 39.4971 | 8236.5144
[7 empty] | 10900 | 6602 | 1381910 | 2016-04-17 21:55 | 2016-04-17 23:20 | 85 | 11kV | 7905 | 93 | HV | Vegetation Blow/Fall In | Vegetation | OTHER - REFER COMMENTS | Unplanned | Rain Light | N | Ex Zn12600 Lisarow section of Pa2 "Holgate" fdr Recloser 41066 McDonalds Rd tripped, reclosed and locked out on timed overcurrent Tree branch contact other See 1381991 exclude 1381910,2 | April | 2016 | 2016Q4 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2016-04-17 | N | 85 | N | 10 | N | N | 1.1101 | 39.4971 | 5776.7408
[7 empty] | 11009 | 7668 | 1381913 | 2016-04-17 23:16 | 2016-04-17 23:49 | 33.4667 | 11kV | 59436.8 | 1776 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn9700 Kirrawee Panel 20 tripped reclosed tripped and locked out on Relays: OC and IOC - Timing and lockout Signals: 11kV trip Cause: Tree caused 11kV to clash and brought down LV streetlight between pole SU04748 and Pole 04749 | April | 2016 | 2016Q4 | 2016 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Veg | 2016-04-17 | N | 33.4667 | N | 10 | N | N | 1.1101 | 39.4971 | 43434.6604
[7 empty] | 12238 | 20301 | 1382024 | 2016-04-18 10:37 | 2016-04-18 12:55 | 138 | 11kV | 153356 | 1146 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 15 Tripped reclosed tripped and locked out on Relays: A and Cphase IOC and Timed, Timing, Lockout Cause: Dop Patrolled feeder and found no cause for outage See OMS 1382253 1382254 1382255 1382024 | April | 2016 | 2016Q4 | 2016 | ZN965:PA15 | ZN965:PA15 | ZN00965/000015 | HORNSBY | OH | Veg | 2016-04-18 | N | 133.8185 | N | 3 | N | N | 1.1101 | 39.4971 | 112068.0416
[7 empty] | 11856 | 16601 | 1382076 | 2016-04-18 12:04 | 2016-04-18 17:30 | 326 | 11kV | 1131 | 118 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 166912 2 fault operations Overcurrent At the time the feeder tripped Feeder abnormal ELB 63469 closed and ABS 44305 OPEN. Cause was a pole fire at pole fire at pole AM-10034. | April | 2016 | 2016Q4 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2016-04-18 | N | 9.5847 | N | 3 | N | N | 1.1101 | 39.4971 | 826.5014
[7 empty] | 10933 | 6942 | 1382080 | 2016-04-18 13:40 | 2016-04-18 21:30 | 470 | 11kV | 6580 | 14 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 166909 Fdr isolated to remove truck from pole JS-90318. See LID Trip & Reclose report #166908. Excluded OMS 1382080 & 1382135 | April | 2016 | 2016Q4 | 2016 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2016-04-18 | N | 470 | N | 3 | N | N | 1.1101 | 39.4971 | 4808.4699
[7 empty] | 11196 | 9903 | 1382218 | 2016-04-19 01:07 | 2016-04-19 01:30 | 23 | 11kV | 2277 | 99 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166915 1 Fault operation A & C phase Overcurrent Closed OK | April | 2016 | 2016Q4 | 2016 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2016-04-19 | N | 23 | N | 5 | N | N | 1.1101 | 39.4971 | 1663.9644
[7 empty] | 12200 | 19844 | 1382220 | 2016-04-19 03:42 | 2016-04-19 04:40 | 58 | 11kV | 1624 | 28 | HV | Animal Possum | Animal | Pole | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty section of Pa18 PT12882 Alistair North Scenic Middle phase 40Amp HDO blown Dead Possum found at the base of pole See 1383691 exclude 1382220 | April | 2016 | 2016Q4 | 2016 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2016-04-19 | N | 58 | N | 5 | N | N | 1.1101 | 39.4971 | 1186.7713
[7 empty] | 10703 | 4449 | 1382466 | 2016-04-19 12:40 | 2016-04-19 14:25 | 105 | 11kV | 105 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 166931 DOLF : 10 Amp Operator suspected damage was occured a previous storm. Excluded OMS 1382348 | April | 2016 | 2016Q4 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2016-04-19 | N | 105 | N | 5 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 11314 | 11066 | 1382368 | 2016-04-19 14:03 | 2016-04-19 15:48 | 105 | 11kV | 210 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 167217 A Phase DOLF : 20 Amp Aph DOLF horns loose. Fuse carrierdropped out. Excluded OMS No. 1382368 | April | 2016 | 2016Q4 | 2016 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2016-04-19 | N | 105 | N | 5 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 11154 | 9433 | 1382452 | 2016-04-19 20:55 | 2016-04-19 21:13 | 18 | 11kV | 18 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166933 1 fault operation Overcurrent Ian O'Brien from Lidell Coal advised that there was an overcurrent operation on like this on Saturday. | April | 2016 | 2016Q4 | 2016 |  |  |  | SINGLETON | OH | Veg | 2016-04-19 | N | 18 | N | 5 | N | N | 1.1101 | 39.4971 | 13.1539
[7 empty] | 11427 | 12111 | 1382485 | 2016-04-20 08:15 | 2016-04-20 10:55 | 160 | 11kV | 320 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166943 A & B phase DOLF : 20 Amp Excluded OMS 1382485 | April | 2016 | 2016Q4 | 2016 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Veg | 2016-04-20 | N | 160 | N | 2 | N | N | 1.1101 | 39.4971 | 233.8466
[7 empty] | 11223 | 10104 | 1382651 | 2016-04-20 23:02 | 2016-04-21 03:08 | 246.4833 | 11kV | 23415.9167 | 95 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 166951 3 fault operations 3 phase Earth Fault not fully patrolled no cause found. | April | 2016 | 2016Q4 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-04-20 | N | 246.4833 | N | 2 | N | N | 1.1101 | 39.4971 | 17111.6612
[7 empty] | 11672 | 14506 | 1382656 | 2016-04-21 03:18 | 2016-04-21 04:15 | 57 | 11kV | 91998 | 1614 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15009 manly - Pnl.5 - tripped on: B & C phase O/C Possum found below pole on corner of Stuart & Cove Sts | April | 2016 | 2016Q4 | 2016 | ZN15009:PA5 | ZN15009:PA5 | ZN15009/000005 | NORTHERN BEACHES | OH | Not Veg | 2016-04-21 | N | 57 | N | 4 | N | N | 1.1101 | 39.4971 | 67229.4249
[7 empty] | 12036 | 18392 | 1382657 | 2016-04-21 04:38 | 2016-04-21 07:21 | 162.65 | 11kV | 101168.3 | 622 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn15009 manly - Section of feeder beyond S15095 (Sw/B) - Bond burnt on corner Cove and Stuart Sts at UGOH. Low volts expereinced beyond S15095. Suspect failed after previous panel 5 outage where a possum was found at the base of the same pole.See #1382656 | April | 2016 | 2016Q4 | 2016 | ZN15009:PA5 | ZN15009:PA5 | ZN15009/000005 | NORTHERN BEACHES | OH | Not Veg | 2016-04-21 | N | 162.65 | N | 4 | N | N | 1.1101 | 39.4971 | 73930.8097
[7 empty] | 11286 | 10786 | 1382689 | 2016-04-21 09:02 | 2016-04-21 11:50 | 168 | 11kV | 840 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 138959 A Phase DOLF : 10 Amp Dolf carrier could not be found. Replaced carrier and fuse element. Excluded OMS 1382689 | April | 2016 | 2016Q4 | 2016 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2016-04-21 | N | 168 | N | 4 | N | N | 1.1101 | 39.4971 | 613.8472
[7 empty] | 11766 | 15570 | 1382807 | 2016-04-21 15:47 | 2016-04-21 17:51 | 124 | 11kV | 124 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 166971 A Phase Broken LL Dropper Excluded OMS 1382807 | April | 2016 | 2016Q4 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-04-21 | N | 124 | N | 4 | N | N | 1.1101 | 39.4971 | 90.6155
[7 empty] | 11883 | 16843 | 1382968 | 2016-04-22 12:03 | 2016-04-22 13:15 | 72 | 11kV | 6480 | 90 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 166984 outage to backfeed moonan sub to fix 33kV pins | April | 2016 | 2016Q4 | 2016 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2016-04-22 | N | 72 | N | 21 | Y | Y | 1.1101 | 39.4971 | 4735.3929
[7 empty] | 10841 | 5951 | 1383022 | 2016-04-22 14:44 | 2016-04-22 16:10 | 86 | 11kV | 24248 | 286 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 167030 Excluded OMS 1383022 | April | 2016 | 2016Q4 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2016-04-22 | N | 84.7832 | N | 21 | Y | Y | 1.1101 | 39.4971 | 17719.7232
[7 empty] | 11946 | 17431 | 1383010 | 2016-04-22 13:36 | 2016-04-22 16:20 | 164 | 11kV | 164 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZN9900 Menai 11kv panel 6 "S9295" feeder @ S9262 Thomas WPS.173 Mitchell - A phase 50A OQFRN operated Remarks: fuse fatigue. Possible fuse fatigue. | April | 2016 | 2016Q4 | 2016 |  |  |  | SUTHERLAND | OH | Not Veg | 2016-04-22 | N | 164 | N | 21 | Y | Y | 1.1101 | 39.4971 | 119.8464
[7 empty] | 11073 | 8335 | 1383001 | 2016-04-22 15:53 | 2016-04-22 17:09 | 76 | 11kV | 99332 | 1307 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At Zn10995 Riverwood Panel 13 'Hedley St' feeder CB has tripped. Relays: IOC and timed A phase, Recloser relay, LO. Signals: 11kv trip Remarks: tree branch contact - other. Tree branch touching/laying on HV @ 4 Belmore Rd Peakhurst from earlier trip lineworker inspected and found a very small branch on one phase. Dop not available earlier due to a lack thereof. See earlier outage in conjuction. | April | 2016 | 2016Q4 | 2016 | ZN10995:PA13 | ZN10995:PA13 | ZN10995/000013 | GEORGES RIVER | OH | Veg | 2016-04-22 | N | 76 | N | 21 | Y | Y | 1.1101 | 39.4971 | 72588.8958
[7 empty] | 10970 | 7296 | 1383910 | 2016-04-22 15:11 | 2016-04-22 17:29 | 138 | 11kV | 552 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 167024 A Phase DOLF : 16 Amp Excluded OMS 1383028 & 1383036 | April | 2016 | 2016Q4 | 2016 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2016-04-22 | N | 138 | N | 21 | Y | Y | 1.1101 | 39.4971 | 403.3853
[7 empty] | 10454 | 1348 | 1383043 | 2016-04-22 15:43 | 2016-04-22 17:38 | 115 | 11kV | 345 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 167028 B Phase DOLF : 10 Amp Excluded OMS 1383043 | April | 2016 | 2016Q4 | 2016 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2016-04-22 | N | 115 | N | 21 | Y | Y | 1.1101 | 39.4971 | 252.1158
[7 empty] | 10618 | 3490 | 1383038 | 2016-04-22 15:29 | 2016-04-22 18:31 | 181.5833 | 11kV | 8171.25 | 45 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 167025 A phase DOLF : 16 Amp | April | 2016 | 2016Q4 | 2016 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2016-04-22 | N | 181.5833 | N | 21 | Y | Y | 1.1101 | 39.4971 | 5971.3085
[7 empty] | 12091 | 18843 | 1383111 | 2016-04-22 17:38 | 2016-04-22 18:40 | 62 | 11kV | 124 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 167027 A Phase DOLF : 10 Amp Excluded OMS 1383111 | April | 2016 | 2016Q4 | 2016 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2016-04-22 | N | 62 | N | 21 | Y | Y | 1.1101 | 39.4971 | 90.6155
[7 empty] | 10418 | 759 | 1383071 | 2016-04-22 16:04 | 2016-04-22 18:45 | 161 | 11kV | 1127 | 7 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 167026 DOLF : 40 Amp Replaced Tx. SAO Required Excluded OMS # 1383071. | April | 2016 | 2016Q4 | 2016 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2016-04-22 | N | 161 | N | 21 | Y | Y | 1.1101 | 39.4971 | 823.5784
[7 empty] | 10551 | 2628 | 1383118 | 2016-04-22 16:42 | 2016-04-22 20:50 | 248 | 11kV | 248 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 167031 Re-Attach LL Clamp Excluded OMS 1383118 | April | 2016 | 2016Q4 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-04-22 | N | 248 | N | 21 | Y | Y | 1.1101 | 39.4971 | 181.2311
[7 empty] | 11476 | 12565 | 1383097 | 2016-04-22 16:35 | 2016-04-22 21:59 | 324 | 11kV | 972 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 167033 A Phase DOLF : 10 Amp Excluded OMS 1383097 | April | 2016 | 2016Q4 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-04-22 | N | 324 | N | 21 | Y | Y | 1.1101 | 39.4971 | 710.3089
[7 empty] | 12061 | 18585 | 1383081 | 2016-04-22 16:11 | 2016-04-22 22:12 | 361 | 11kV | 1083 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 167036 Single Phase DOLF : 10 Amp Replaced L/A Excluded OMS 1383081 | April | 2016 | 2016Q4 | 2016 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2016-04-22 | N | 361 | N | 21 | Y | Y | 1.1101 | 39.4971 | 791.4245
[7 empty] | 12026 | 18297 | 1383100 | 2016-04-22 16:31 | 2016-04-22 23:05 | 393.9333 | 11kV | 23636 | 60 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 167034 C Phase DOLF : 31 Amp Excluded OMS 1383100 | April | 2016 | 2016Q4 | 2016 | 512:48046 | 512:83741 | ZN00512/083741 | CESSNOCK | OH | Veg | 2016-04-22 | N | 393.9333 | N | 21 | Y | Y | 1.1101 | 39.4971 | 17272.4917
[7 empty] | 11926 | 17169 | 1383154 | 2016-04-22 17:51 | 2016-04-22 23:45 | 354 | 11kV | 708 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 167040 3 phase DOLF : 10 Amp Excluded OMS 1383154 | April | 2016 | 2016Q4 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2016-04-22 | N | 354 | N | 21 | Y | Y | 1.1101 | 39.4971 | 517.3855
[7 empty] | 10967 | 7256 | 1383213 | 2016-04-23 07:35 | 2016-04-23 08:20 | 45 | 11kV | 33840 | 752 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 167052 1 fault operation C Phase Earth fault Maitland Z/S supplied from Beresfield 132kV sub at time of fault. Reclose Function was switched off due to previous fault on Fdr 83011. Also Fdr 83011 supplying abnormal telarah Fdr 48010. No fault found please patrol feeder. Excluded OMS No. 1383213, 1383215, 1383223, 1383221 | April | 2016 | 2016Q4 | 2016 | 528:83024 | 528:83024 | ZN00528/083024 | MAITLAND | OH | Veg | 2016-04-23 | N | 45 | N | 7 | N | N | 1.1101 | 39.4971 | 24729.2739
[7 empty] | 11077 | 8454 | 1383141 | 2016-04-22 17:29 | 2016-04-23 08:50 | 921 | 11kV | 14736 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 167053 B Phase DOLF : 20 Amp Excluded OMS 1383141 | April | 2016 | 2016Q4 | 2016 | 512:48048 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Veg | 2016-04-22 | N | 921 | N | 21 | Y | Y | 1.1101 | 39.4971 | 10768.6342
[7 empty] | 12209 | 19977 | 1383230 | 2016-04-23 08:49 | 2016-04-23 10:00 | 71 | 11kV | 284 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 167054 A phase DOLF : 10 Amp Excluded OMS 1383230 | April | 2016 | 2016Q4 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2016-04-23 | N | 71 | N | 7 | N | N | 1.1101 | 39.4971 | 207.5388
[7 empty] | 11140 | 9294 | 1383252 | 2016-04-23 10:19 | 2016-04-23 10:25 | 6 | 11kV | 7218 | 1203 | HV | Excavation Ausgrid Staff | Utility Process Issue | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 167056 11kV Fdr isolated to repair broken 33kV Fdr KU4 OHEW into 11kV OHM at pole HR-60408. 33kV Fdr KU4 was already isolated due to previous fault and 11kV Fdr 83024 was abnormal with Fdr 83011 and Telarah Fdr 48010. Excluded OMS 13832521, 1383253 See LID 167023 | April | 2016 | 2016Q4 | 2016 | 528:83024 | 528:83024 | ZN00528/083024 | MAITLAND | UG | Not Veg | 2016-04-23 | N | 6 | N | 7 | N | N | 1.1101 | 39.4971 | 5274.7015
[7 empty] | 10889 | 6492 | 1383144 | 2016-04-22 17:31 | 2016-04-23 10:35 | 1024 | 11kV | 42242 | 417 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 167037 3 phase DOLF : 10 Amp Started as a tx fault. Feeder tripped while trying to close DOLFS at Tx 51597. Fdr tripped on SEF. Patrolled but found no problem. Possible issue with SEF relay on Fdr 48056 Excluded OMS 1383189 & 1383144. | April | 2016 | 2016Q4 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2016-04-22 | N | 101.2998 | N | 21 | Y | Y | 1.1101 | 39.4971 | 30869.2077
[7 empty] | 11451 | 12250 | 1383181 | 2016-04-22 19:22 | 2016-04-23 11:30 | 968 | 11kV | 3872 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 167058 C Phase DOLF : 20 Amp Maitland Z/S/ supplied from Beresfield 132kV sub at time of fault. Excluded OMS No. 1383181, 1383238, 1383245 | April | 2016 | 2016Q4 | 2016 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2016-04-22 | N | 968 | N | 21 | Y | Y | 1.1101 | 39.4971 | 2829.5434
[7 empty] | 11085 | 8601 | 1383243 | 2016-04-23 09:47 | 2016-04-23 12:15 | 148 | 11kV | 444 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 167057 C Phase DOLF : 10 Amp Repair earth wire to sub tank Excluded OMS 1383243 | April | 2016 | 2016Q4 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2016-04-23 | N | 148 | N | 7 | N | N | 1.1101 | 39.4971 | 324.4621
[7 empty] | 12243 | 20341 | 1383262 | 2016-04-23 10:45 | 2016-04-23 12:40 | 115 | 11kV | 230 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 167060 Single phase DOLF : 10 Amp Excluded OMS 1383262 | April | 2016 | 2016Q4 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2016-04-23 | N | 115 | N | 7 | N | N | 1.1101 | 39.4971 | 168.0772
[7 empty] | 11143 | 9341 | 1383274 | 2016-04-23 11:45 | 2016-04-23 13:10 | 85 | 11kV | 170 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 167061 A Phase DOLF : 16 Amp Excluded OMS 1383274 | April | 2016 | 2016Q4 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-04-23 | N | 85 | N | 7 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 10717 | 4560 | 1383163 | 2016-04-22 16:35 | 2016-04-23 13:50 | 1275 | 11kV | 3825 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 167039 A phase DOLF : 10 Amp Blown L/A Replaced Excluded OMS 1383108 | April | 2016 | 2016Q4 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2016-04-22 | N | 1275 | N | 21 | Y | Y | 1.1101 | 39.4971 | 2795.1972
[7 empty] | 10638 | 3743 | 1383166 | 2016-04-22 18:26 | 2016-04-23 14:50 | 1224 | 11kV | 2448 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 167062 A & C phase DOLF : 16 Amp Excluded OMS 1383166 | April | 2016 | 2016Q4 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-04-22 | N | 1224 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1788.9262
[7 empty] | 10394 | 362 | 1383190 | 2016-04-22 17:19 | 2016-04-23 17:05 | 1426 | 11kV | 1426 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 167042 A Phase | April | 2016 | 2016Q4 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-04-22 | N | 1426 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1042.0787
[7 empty] | 11487 | 12633 | 1383321 | 2016-04-23 16:30 | 2016-04-23 18:00 | 90 | 11kV | 180 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 167063 Single phase DOLF : 3 Amp Excluded OMS 1383321 | April | 2016 | 2016Q4 | 2016 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2016-04-23 | N | 90 | N | 7 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 11719 | 15103 | 1383117 | 2016-04-22 16:38 | 2016-04-23 18:47 | 1569 | 11kV | 94588 | 455 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 167023 2 fault operations Overcurrent; Earth Fault 33kV Earth wire into 33kv and 11kV at pole HR-60416. 11kV permit area was increased as per LID 167056 to repair second OHEW failure. Sw 83011 A Prot (Timed OC) B Prot (OC and EF on b and C phases) Excluded OMS 1383117, 1389193 & 1383194 See also LID 167056 | April | 2016 | 2016Q4 | 2016 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2016-04-22 | N | 207.8857 | N | 21 | Y | Y | 1.1101 | 39.4971 | 69122.1205
[7 empty] | 11038 | 7941 | 1384086 | 2016-04-24 00:29 | 2016-04-24 01:13 | 44 | 11kV | 10428 | 237 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP64824 Deepwater Holly Tripped and Reclosed Relays: O/C Trip Cause: Branch removed by DOp in deepwater rd near S1720 | April | 2016 | 2016Q4 | 2016 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | OH | Not Veg | 2016-04-24 | N | 44 | N | 7 | N | N | 1.1101 | 39.4971 | 7620.4748
[7 empty] | 11295 | 10904 | 1383350 | 2016-04-24 00:36 | 2016-04-24 05:54 | 318 | 11kV | 101462 | 696 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 167066 1 fault operation A & C phase Overcurrent broken crossarm near sub 14988 Excluded OMS 1383350 | April | 2016 | 2016Q4 | 2016 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2016-04-24 | N | 145.7787 | N | 7 | N | N | 1.1101 | 39.4971 | 74145.437
[7 empty] | 10981 | 7434 | 1383375 | 2016-04-24 08:40 | 2016-04-24 10:05 | 85 | 11kV | 85 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167067 Single phase DOLF : 10 Amp Dead galah found at sub. Excluded OMS No. 1383375 | April | 2016 | 2016Q4 | 2016 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2016-04-24 | N | 85 | N | 7 | N | N | 1.1101 | 39.4971 | 62.1155
[7 empty] | 10586 | 3049 | 1383412 | 2016-04-24 11:54 | 2016-04-24 13:42 | 108 | 11kV | 108 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167068 A phase DOLF : 10 Amp excluded OMS 1383412 | April | 2016 | 2016Q4 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2016-04-24 | N | 108 | N | 7 | N | N | 1.1101 | 39.4971 | 78.9232
[7 empty] | 11912 | 17035 | 1383444 | 2016-04-24 17:51 | 2016-04-24 19:10 | 79.1 | 11kV | 1423.8 | 18 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Electrical Storm | N | LID 167069 A Phase Dolf Replace 11kV Fuse Carrier LV in parallel at 1950hrs to restore customers CC1: 22-"Refer to SOp" | April | 2016 | 2016Q4 | 2016 | 512:48048 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Not Veg | 2016-04-24 | N | 79.1 | N | 7 | N | N | 1.1101 | 39.4971 | 1040.471
[7 empty] | 12070 | 18642 | 1383450 | 2016-04-24 20:55 | 2016-04-24 21:13 | 18.4333 | 11kV | 110.6 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 167071 PG Clamp at LF 40742 glowing. replaced by LL crew | April | 2016 | 2016Q4 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2016-04-24 | N | 18.4333 | N | 7 | N | N | 1.1101 | 39.4971 | 80.8232
[7 empty] | 11909 | 17019 | 1383453 | 2016-04-24 19:10 | 2016-04-24 21:24 | 134 | 11kV | 299830 | 2357 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn10999 Kogarah Zn P11 the gladestone princess fdr tripped on sel Remarks: bond on ugoh adj S10076. LV// found in with S10960 and S10032 | April | 2016 | 2016Q4 | 2016 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | OH | Not Veg | 2016-04-24 | N | 127.2083 | N | 7 | N | N | 1.1101 | 39.4971 | 219106.9205
[7 empty] | 11087 | 8632 | 1383503 | 2016-04-25 09:56 | 2016-04-25 10:40 | 44 | 11kV | 5970 | 145 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Signals: Tx12 GE @ Hurstville Nth @ 0939 (Ex Panel 39L S10993 Hurstville North) 11kv Roadside HDO assembly failure/partial Blow fuse @ PT10888 Binder Donald Remarks: fuse equipment - details below. 11kv Roadside HDO assembly failure after HDO possibly failed to clear @ PT10888 Binder Donald. (Indicating possibly Tx fault) | April | 2016 | 2016Q4 | 2016 | ZN10993:PA39 | ZN10993:PA39 | ZN10993/000039 | GEORGES RIVER | OH | Not Veg | 2016-04-25 | N | 41.1724 | N | 2 | N | N | 1.1101 | 39.4971 | 4362.6999
[7 empty] | 11187 | 9831 | 1383992 | 2016-04-25 17:48 | 2016-04-25 22:00 | 252 | 11kV | 5292 | 21 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 167076 Single phase 11kV Link 6L732 Shattered AP issued to replace links isolated from 11 kv links 6L790 | April | 2016 | 2016Q4 | 2016 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2016-04-25 | N | 252 | N | 2 | N | N | 1.1101 | 39.4971 | 3867.2375
[7 empty] | 10541 | 2476 | 1383585 | 2016-04-26 01:35 | 2016-04-26 02:42 | 67 | 11kV | 66330 | 990 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 5 tripped Relays: Earth Fault, Fault Check Possum found at the base of UGOH to PT2431 Lisgar Rd | April | 2016 | 2016Q4 | 2016 | ZN847:PA5 | ZN847:PA5 | ZN00847/000005 | HORNSBY | OH | Not Veg | 2016-04-26 | N | 67 | N | 6 | N | N | 1.1101 | 39.4971 | 48472.0076
[7 empty] | 12053 | 18501 | 1383692 | 2016-04-26 10:23 | 2016-04-26 10:50 | 27 | 11kV | 81 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 167088 Single phase DOLF : 10 Amp Tx volts = 240V Excluded OMS 1383692 | April | 2016 | 2016Q4 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-04-26 | N | 27 | N | 6 | N | N | 1.1101 | 39.4971 | 59.1924
[7 empty] | 10486 | 1796 | 1383690 | 2016-04-26 10:12 | 2016-04-26 11:21 | 69 | 11kV | 9951 | 146 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167087 2 fault operation B & C phases Overcurrent | April | 2016 | 2016Q4 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2016-04-26 | N | 68.1575 | N | 6 | N | N | 1.1101 | 39.4971 | 7271.8973
[7 empty] | 10729 | 4717 | 1383735 | 2016-04-26 12:02 | 2016-04-26 12:55 | 53 | 11kV | 159 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167090 C Phase DOLF : 10 Amp Excluded OMS 1383735 | April | 2016 | 2016Q4 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2016-04-26 | N | 53 | N | 6 | N | N | 1.1101 | 39.4971 | 116.1925
[7 empty] | 10461 | 1445 | 1383702 | 2016-04-26 10:46 | 2016-04-26 13:20 | 154 | 11kV | 462 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 167092 A & B phase DOLF : 10 Amp Tx volts = 238V Excluded OMS 1383702 | April | 2016 | 2016Q4 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2016-04-26 | N | 154 | N | 6 | N | N | 1.1101 | 39.4971 | 337.616
[7 empty] | 12224 | 20157 | 1383768 | 2016-04-26 13:21 | 2016-04-26 17:59 | 277.65 | 11kV | 6663.6 | 24 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 167094 C phase DOLF C ph DOLF dropped out when pole sounded by inspector. EMSO found DOLF carrier burnt up. | April | 2016 | 2016Q4 | 2016 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2016-04-26 | N | 277.65 | N | 6 | N | N | 1.1101 | 39.4971 | 4869.5623
[7 empty] | 11429 | 12116 | 1383898 | 2016-04-27 08:06 | 2016-04-27 11:00 | 174 | 11kV | 352140 | 2505 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35800 Bankstown Panel 1 "Gow Gibson" fdr locked out on C phase O/C and Earth Fault, (51C and 51N) with EFI, reclose and lockout relays, also earth check relay B. Signals, 11kv trip, Zone earth and Tx11 group earth EFIs down at Subs Remarks: animals/bird. Bird on 11kv UG/OH in Irvine St nr Hortham Bankstown | April | 2016 | 2016Q4 | 2016 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-04-27 | N | 140.5749 | N | 2 | N | N | 1.1101 | 39.4971 | 257333.5256
[7 empty] | 11062 | 8212 | 1385086 | 2016-04-28 02:22 | 2016-04-28 04:41 | 139 | 11kV | 102977 | 1222 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S15005 Belrose Panel 4 Tripped on OVercurrent EFI and Lockout Recloser 21801 Sorlie Merrilee Tripped on O/C Suspected UG fault in 11kV feeder from S16208 SW/B to S16247 SW/A See OMS 1385086 1385088 1385089 1384157 | April | 2016 | 2016Q4 | 2016 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | UG | Not Veg | 2016-04-28 | N | 84.2692 | N | 3 | N | N | 1.1101 | 39.4971 | 75252.5543
[7 empty] | 11829 | 16351 | 1384072 | 2016-04-27 14:59 | 2016-04-28 07:57 | 1018.35 | 11kV | 76566 | 813 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | LID 167106 2 fault operations A phase Earth Fault, Overcurrent Prot 1st trip = Aph O/C & E/F, fault current Aph = 500A Reclose trip = A,B&Cph O/C E/F, fault currents Aph = 7122A, Bph = 8873A, Cph = 7831A, E/F = 2720A | April | 2016 | 2016Q4 | 2016 | 225:33670 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Not Veg | 2016-04-27 | N | 94.1771 | N | 2 | N | N | 1.1101 | 39.4971 | 55952.1745
[7 empty] | 11678 | 14563 | 1384157 | 2016-04-28 05:10 | 2016-04-28 08:38 | 208 | 11kV | 118768 | 571 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn15005 Belrose ex Pnl.4 - OH bond burnt off between Panel 4 and AB21076 to LB25618 Abnormal: REC 21802 Closed with S16208 (Sw/B) and S16247 (Sw/A) open for a defective UG cable. | April | 2016 | 2016Q4 | 2016 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Not Veg | 2016-04-28 | N | 208 | N | 3 | N | N | 1.1101 | 39.4971 | 86792.1513
[7 empty] | 10521 | 2290 | 1390908 | 2016-04-28 07:00 | 2016-04-28 14:25 | 445 | 11kV | 17800 | 40 | HV | Overload Operational | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Planned LID 167125 SINO 13107 | April | 2016 | 2016Q4 | 2016 | ZN12570:PA41 | ZN12570:PA41 | ZN12570/000041 | CENTRAL COAST | OH | Not Veg | 2016-04-28 | N | 445 | N | 3 | N | N | 1.1101 | 39.4971 | 13007.715
[7 empty] | 11470 | 12479 | 1384387 | 2016-04-29 05:29 | 2016-04-29 07:01 | 92 | 11kV | 8028 | 146 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167131 2 fault operations No targets. Faulty relay. See LID# 167142/OMS 1384407 Excluded OMS No. 1384387 | April | 2016 | 2016Q4 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2016-04-29 | N | 54.9863 | N | 5 | N | N | 1.1101 | 39.4971 | 5866.6256
[7 empty] | 11244 | 10297 | 1384459 | 2016-04-29 11:30 | 2016-04-29 12:53 | 83 | 11kV | 103545 | 1410 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn2835 Burwood - 11kv panel No.16 "Sub 2035, Sub 3390, Sub 3183" feeder tripped Relays: earth fault, EFI, fault check Signals: 11kv trip, Zone earth, No.2 Group Earth Field EFI's: Nil Remarks: UG fault. 11kv UG fault from Zn2835 Burwood Panel No.16 to Sub 2035 Vernon Redmyre to Sub 3183 Raw Albert to Sub 3390 Albert Elva. | April | 2016 | 2016Q4 | 2016 | ZN2835:PA16 | ZN2835:PA16 | ZN02835/000016 | STRATHFIELD | UG | Not Veg | 2016-04-29 | N | 73.4362 | N | 5 | N | N | 1.1101 | 39.4971 | 75667.6319
[7 empty] | 11532 | 12977 | 1384407 | 2016-04-29 08:38 | 2016-04-29 16:35 | 477 | 11kV | 31572 | 146 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167142 1 fault operation Faulty prot. relay. Internal relay fault. No targets. Fdr patrolled OK. Exvcluded OMS No. 1384407 | April | 2016 | 2016Q4 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2016-04-29 | N | 216.2466 | N | 5 | N | N | 1.1101 | 39.4971 | 23071.8864
[7 empty] | 11971 | 17686 | 1384424 | 2016-04-29 09:19 | 2016-04-29 17:40 | 501 | 11kV | 1002 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 167141 B Phase DOLF : 16 Amp 11kV Bph tapping burnt off at pole FR-75206 Bph sub DOLF blown. Excluded OMS No. 1384424 | April | 2016 | 2016Q4 | 2016 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2016-04-29 | N | 501 | N | 5 | N | N | 1.1101 | 39.4971 | 732.232
[7 empty] | 11150 | 9406 | 1384545 | 2016-04-29 19:06 | 2016-04-29 21:00 | 114.05 | 11kV | 2965.3 | 26 | HV | Animal Other | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167143 B Phase DOLF : 10 Amp STAFF FOUND A BURNT RAT BELOW SUB 52204 WITH A BLOWN DOLF. 10A STAFF ALSO FOUND A BLOWN L/FUSE AT 41291 10A. SAME PHASE. Excluded OMS REPORT 1384545. | April | 2016 | 2016Q4 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2016-04-29 | N | 114.05 | N | 5 | N | N | 1.1101 | 39.4971 | 2166.9538
[7 empty] | 10378 | 177 | 1384647 | 2016-04-30 15:13 | 2016-04-30 18:15 | 182 | 11kV | 910 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 167150 C Phase 11KV LEAD AT TOP OF DOLF BROKEN. Excluded OMS REPORT NO 1384647. | April | 2016 | 2016Q4 | 2016 | 532:83309 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2016-04-30 | N | 182 | N | 2 | N | N | 1.1101 | 39.4971 | 665.0012
[7 empty] | 12132 | 19213 | 1384657 | 2016-04-30 17:23 | 2016-04-30 19:00 | 96.9167 | 11kV | 5136.5833 | 53 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 167151 A phase HV LEAD BURNT OFF SUB INTERCONNECTED TO REPAIR HV LEAD. Excluded OMS REPORT NO 1384665. | April | 2016 | 2016Q4 | 2016 | 532:83293 | 532:83314 | ZN00532/083314 | MAITLAND | OH | Not Veg | 2016-04-30 | N | 96.9167 | N | 2 | N | N | 1.1101 | 39.4971 | 3753.6636
[7 empty] | 10701 | 4436 | 1384715 | 2016-05-01 08:55 | 2016-05-01 11:45 | 170 | 11kV | 1190 | 7 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex N12600 Lisarow section of Pa2 "The Holgate" fdr PT13305 The Ridgeway Cutrock. Footpath 16Amp HDO operated Lightning See 1384983 exclude 1384715 | May | 2016 | 2016Q4 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2016-05-01 | N | 170 | N | 2 | N | N | 1.1101 | 39.4971 | 869.6169
[7 empty] | 10793 | 5403 | 1384797 | 2016-05-01 19:33 | 2016-05-01 20:20 | 47 | 11kV | 3901 | 83 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa11 PT13856 Malison Maple, HDO operated on footpath and middle phases Possum removed from PT See 1384800 exclude 1384797,8,9 | May | 2016 | 2016Q4 | 2016 | ZN12600:PA11 | ZN12600:PA11 | ZN12600/000011 | CENTRAL COAST | OH | Not Veg | 2016-05-01 | N | 47 | N | 2 | N | N | 1.1101 | 39.4971 | 2850.7357
[7 empty] | 11106 | 8771 | 1385005 | 2016-05-02 15:23 | 2016-05-02 16:05 | 42 | 11kV | 126 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167172 A Phase DOLF : 10 Amp excluded OMS 1385005 | May | 2016 | 2016Q4 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2016-05-02 | N | 42 | N | 2 | N | N | 1.1101 | 39.4971 | 92.0771
[7 empty] | 12154 | 19430 | 1385097 | 2016-05-02 23:13 | 2016-05-03 02:33 | 200 | 11kV | 14200 | 71 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167176 2 fault operations 3 phase Overcurrent Main trunk patrolled. No fault found. Please patrol. | May | 2016 | 2016Q4 | 2016 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2016-05-02 | N | 200 | N | 2 | N | N | 1.1101 | 39.4971 | 10376.9412
[7 empty] | 10545 | 2521 | 1385066 | 2016-05-03 05:05 | 2016-05-03 11:47 | 402 | 11kV | 39798 | 99 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 167181 No Protection Ops Burnt off tapping HQ-81465 Excluded OMS 1385066 & 1385129 | May | 2016 | 2016Q4 | 2016 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2016-05-03 | N | 402 | N | 5 | N | N | 1.1101 | 39.4971 | 29083.2046
[7 empty] | 10571 | 2848 | 1385256 | 2016-05-03 15:11 | 2016-05-03 16:06 | 55 | 11kV | 9405 | 171 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167190 2 fault operations Overcurrent tree branch fell on ohm near sub 1357 | May | 2016 | 2016Q4 | 2016 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2016-05-03 | N | 55 | N | 5 | N | N | 1.1101 | 39.4971 | 6872.8966
[7 empty] | 10833 | 5846 | 1385225 | 2016-05-03 15:30 | 2016-05-03 16:20 | 50 | 11kV | 200 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167191 A Phase DOLF : 10 Amp | May | 2016 | 2016Q4 | 2016 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2016-05-03 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 10738 | 4860 | 1385329 | 2016-05-03 20:39 | 2016-05-03 22:10 | 90.5667 | 11kV | 1720.7667 | 19 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167193 interrupt to fix 11kV OHM clearance to new pole GS-40020 | May | 2016 | 2016Q4 | 2016 | 507:80925 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2016-05-03 | N | 90.5667 | N | 5 | N | N | 1.1101 | 39.4971 | 1257.4855
[7 empty] | 11810 | 16111 | 1385504 | 2016-05-04 03:02 | 2016-05-04 05:20 | 138 | 11kV | 154292 | 1525 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn847 Hornsby Panel 2 tripped on Relays: C phase overcurrent, Fault check and EFI Signals: 11kV Trip, Zone Earth and No1 Group Earth Cause: Fault in section of 11kV Feeder from CP382 to S8314 tee PT749 Pleasant Pennant See OMS 1386044 1386046 1386047 1385504 | May | 2016 | 2016Q4 | 2016 | ZN847:PA2 | ZN847:PA2 | ZN00847/000002 | HORNSBY | UG | Not Veg | 2016-05-04 | N | 101.1751 | N | 2 | N | N | 1.1101 | 39.4971 | 112752.0428
[7 empty] | 11277 | 10637 | 1385743 | 2016-05-04 12:19 | 2016-05-04 14:00 | 101 | 11kV | 808 | 8 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 167204 3 phase section of fdr 82579 brandy hill interrupted due to failure on essential energy network. SI 12871 required abs 40262 to be opened and backfed to that point via abs 27959 from EE. | May | 2016 | 2016Q4 | 2016 | 508:82579 | 508:82579 | ZN00508/082579 | DUNGOG | OH | Not Veg | 2016-05-04 | N | 101 | N | 2 | N | N | 1.1101 | 39.4971 | 590.4626
[7 empty] | 10704 | 4452 | 1385171 | 2016-05-03 12:37 | 2016-05-04 14:00 | 1523.3333 | 11kV | 47177 | 845 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167186 A & B phase Overcurrent TREE ON MAINS REMOVED UNDER AP Excluded OMS 1385171 | May | 2016 | 2016Q4 | 2016 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2016-05-03 | N | 55.8308 | N | 5 | N | N | 1.1101 | 39.4971 | 34475.5601
[7 empty] | 10623 | 3624 | 1385931 | 2016-05-06 07:13 | 2016-05-06 08:30 | 77 | 11kV | 29463 | 491 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | zn711 Blackwattle Bay - Pnl.15 tripped on: Earth leakage and EFI Front line UG cable fault from Panel 15 to S7026 (Sw/F) to S7527 (Sw/A) | May | 2016 | 2016Q4 | 2016 | ZN711:PA15 | ZN7481:PA13 | ZN07481/000013 | SYDNEY | UG | Not Veg | 2016-05-06 | N | 60.0061 | N | 2 | N | N | 1.1101 | 39.4971 | 21530.6914
[7 empty] | 10488 | 1841 | 1386026 | 2016-05-06 15:38 | 2016-05-06 17:20 | 102 | 11kV | 408 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 167239 Single phase lv terminal on tx replaced | May | 2016 | 2016Q4 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2016-05-06 | N | 102 | N | 2 | N | N | 1.1101 | 39.4971 | 298.1544
[7 empty] | 12017 | 18224 | 1386113 | 2016-05-07 03:56 | 2016-05-07 04:35 | 39 | 11kV | 73827 | 1893 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167243 2 fault operations B & C phase Overcurrent 2 dead possums near sub 10976 | May | 2016 | 2016Q4 | 2016 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Not Veg | 2016-05-07 | N | 39 | N | 1 | N | N | 1.1101 | 39.4971 | 53950.5941
[7 empty] | 11993 | 18001 | 1386251 | 2016-05-08 07:48 | 2016-05-08 09:05 | 77 | 11kV | 1232 | 16 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167249 Single phase DOLF : 20 Amp magpie on mains pole GS-31339 | May | 2016 | 2016Q4 | 2016 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2016-05-08 | N | 77 | N | 1 | N | N | 1.1101 | 39.4971 | 900.3093
[7 empty] | 10600 | 3231 | 1386366 | 2016-05-09 08:11 | 2016-05-09 09:15 | 64 | 11kV | 128 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167252 C Phase DOLF : 16 Amp Excluded OMS 1386366 | May | 2016 | 2016Q4 | 2016 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2016-05-09 | N | 64 | N | 4 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 10584 | 3017 | 1386554 | 2016-05-09 15:35 | 2016-05-09 16:35 | 60 | 11kV | 300 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 167262 isolated to repair LIDAR defect. Pole 6N-90092. conductor on x-arm. | May | 2016 | 2016Q4 | 2016 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Not Veg | 2016-05-09 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 12103 | 18952 | 1386463 | 2016-05-09 13:25 | 2016-05-09 16:40 | 195 | 11kV | 1170 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 167260 burnt off tapping pole 9N-20145 SECTION ISOLATED TO CARRY OUT REPAIRS Excluded oms 1386463 | May | 2016 | 2016Q4 | 2016 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2016-05-09 | N | 195 | N | 4 | N | N | 1.1101 | 39.4971 | 855.0015
[7 empty] | 11998 | 18068 | 1386563 | 2016-05-09 16:35 | 2016-05-09 16:50 | 15 | 11kV | 547 | 57 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 167263 interrupt to open damaged ABS 13587 during RSI 13220 Excluded oms 1386563 | May | 2016 | 2016Q4 | 2016 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Not Veg | 2016-05-09 | N | 9.5965 | N | 4 | N | N | 1.1101 | 39.4971 | 399.7315
[7 empty] | 11903 | 16958 | 1387140 | 2016-05-10 00:04 | 2016-05-10 07:12 | 428 | 11kV | 19598 | 280 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S9700 Kirrawee Panel 22 tripped and locked out on earth leakage C phase IOC Lockout timing relay EFI and Fault check Cause: UG fault from S9533 to S9124 to . No Access to S9533 during business hours whhich delayed its restoration see OMS 1387140 1387142 1387143 S1386619 1386623 | May | 2016 | 2016Q4 | 2016 | ZN9700:PA22 | ZN9700:PA22 | ZN09700/000022 | SUTHERLAND | UG | Not Veg | 2016-05-10 | N | 69.9929 | N | 8 | N | N | 1.1101 | 39.4971 | 14321.6404
[7 empty] | 10408 | 606 | 1386673 | 2016-05-10 09:12 | 2016-05-10 10:12 | 60 | 11kV | 48480 | 808 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | At S1673 Turramurra Panel 2 tripped on Relays: B and C phase IOC Cause not ascertained for outage | May | 2016 | 2016Q4 | 2016 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | OH | Veg | 2016-05-10 | N | 60 | N | 8 | N | N | 1.1101 | 39.4971 | 35427.7541
[7 empty] | 11980 | 17815 | 1386699 | 2016-05-10 10:06 | 2016-05-10 11:31 | 85 | 11kV | 31450 | 370 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | At S35370 Galston Panel 2 tripped on Relays: B phase IOC, A and C phase Overcurrent Cause not ascertained for | May | 2016 | 2016Q4 | 2016 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2016-05-10 | N | 85 | N | 8 | N | N | 1.1101 | 39.4971 | 22982.7324
[7 empty] | 11413 | 11954 | 1386710 | 2016-05-10 10:18 | 2016-05-10 11:51 | 93 | 11kV | 62389 | 677 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S9035 Caringbah panel 2 tripped, reclosed, tripped and locked out on A phase IOC and Timed O/C, Lockout and Timed with EFI Signals:11kV Trip, Zone Earth, Group Earth. Cause: Dop paqtrolled feeder and found several sticks on ground which may have caused fault See OMS 1387091 1387093 1386710 | May | 2016 | 2016Q4 | 2016 | ZN9035:PA2 | ZN9035:PA2 | ZN09035/000002 | SUTHERLAND | OH | Veg | 2016-05-10 | N | 92.1551 | N | 8 | N | N | 1.1101 | 39.4971 | 45592.041
[7 empty] | 11112 | 8817 | 1386932 | 2016-05-10 15:16 | 2016-05-10 19:23 | 247 | 11kV | 7657 | 31 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | PT1753 Hayle Woodbury Dist 1 "Hayle Street" BC phase fuse blown due to strong winds tree brought down outside 6 Hayle st. Affected other DC's due to unknown LV//'s found in. Repairs carried out and LV//'s removed See 1387137 exclude 1386932 | May | 2016 | 2016Q4 | 2016 | ZN3154:PA25 | ZN3154:PA25 | ZN03154/000025 | KU-RING-GAI | OH | Veg | 2016-05-10 | N | 247 | N | 8 | N | N | 1.1101 | 39.4971 | 5595.5098
[7 empty] | 11102 | 8738 | 1387009 | 2016-05-10 19:30 | 2016-05-10 21:03 | 93 | 11kV | 1767 | 19 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 167286 Feeder found stuck on pole step of new pole not tied in. Paul Lee issued AP and tied in feeder. | May | 2016 | 2016Q4 | 2016 | 507:80925 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2016-05-10 | N | 93 | N | 8 | N | N | 1.1101 | 39.4971 | 1291.2715
[7 empty] | 10608 | 3314 | 1387015 | 2016-05-10 20:00 | 2016-05-10 21:55 | 114.8667 | 11kV | 689.2 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167287 Single phase DOLF : 10 Amp | May | 2016 | 2016Q4 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2016-05-10 | N | 114.8667 | N | 8 | N | N | 1.1101 | 39.4971 | 503.647
[7 empty] | 10383 | 221 | 1386888 | 2016-05-10 15:15 | 2016-05-11 01:35 | 620 | 11kV | 79520 | 545 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167281 2 fault operations Wires down pole MW-90223 | May | 2016 | 2016Q4 | 2016 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Not Veg | 2016-05-10 | N | 145.9083 | N | 8 | N | N | 1.1101 | 39.4971 | 58110.8706
[7 empty] | 10914 | 6795 | 1387038 | 2016-05-11 05:10 | 2016-05-11 07:03 | 113 | 11kV | 121758 | 1573 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn36300 Balgowlah North Panel 8 Tripped and Locked out on Relays: SEL and EFI Signals 11kV Trip Field EFIS Cause: Possum on Normally open LB61274 NOTE: DOp suspects 11kV UGOH was down and alive from earlier trip and reclose. See OMS 1387401 1387402 1387038 | May | 2016 | 2016Q4 | 2016 | ZN36300:PA8 | ZN36300:PA8 | ZN36300/000008 | NORTHERN BEACHES | OH | Not Veg | 2016-05-11 | N | 77.405 | N | 6 | N | N | 1.1101 | 39.4971 | 88977.1551
[7 empty] | 10787 | 5336 | 1387066 | 2016-05-11 08:22 | 2016-05-11 11:04 | 162 | 11kV | 30178 | 272 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 167297 1 fault operation A phase Earth Fault underground cable fault Excluded oms 1387066 | May | 2016 | 2016Q4 | 2016 | 240:34843 | 240:34843 | ZN00240/034843 | NEWCASTLE | UG | Not Veg | 2016-05-11 | N | 110.9485 | N | 6 | N | N | 1.1101 | 39.4971 | 22053.1923
[7 empty] | 10761 | 5079 | 1387119 | 2016-05-11 10:00 | 2016-05-11 11:59 | 119 | 11kV | 66411 | 811 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167295 B & C phase Instantaneous Overcurrent tree on mains near abs 9290 11kV OHM off pin at pole JS-30978 | May | 2016 | 2016Q4 | 2016 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Veg | 2016-05-11 | N | 81.8878 | N | 6 | N | N | 1.1101 | 39.4971 | 48531.2
[7 empty] | 12157 | 19476 | 1387277 | 2016-05-11 17:28 | 2016-05-11 17:50 | 21.9667 | 11kV | 13004.2667 | 592 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S9252 Jannali IR 63274 Soldiers Washington Tripped Cause: Dop Patrolled and cause not ascertained. CP63274 is in scan fail | May | 2016 | 2016Q4 | 2016 | ZN9252:PA31 | ZN9252:PA31 | ZN09252/000031 | SUTHERLAND | OH | Veg | 2016-05-11 | N | 21.9667 | N | 6 | N | N | 1.1101 | 39.4971 | 9503.1345
[7 empty] | 10999 | 7602 | 1387239 | 2016-05-11 15:30 | 2016-05-11 20:09 | 279 | 11kV | 837 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 167305 A phase Dropper from LLC to dolf failed. A Pople replaced undere AP. Excluded OMS 1387239 | May | 2016 | 2016Q4 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2016-05-11 | N | 279 | N | 6 | N | N | 1.1101 | 39.4971 | 611.6549
[7 empty] | 11083 | 8518 | 1387302 | 2016-05-11 21:57 | 2016-05-12 00:35 | 158 | 11kV | 70803 | 621 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12660 Woy Woy seciton of Pa14 RE48036 Rawson Woy Woy tripped and locked out on overcurrent Cause: Tree/branch on OH Mains See 1388064,6,8 exclude 1387302,7,8,11 | May | 2016 | 2016Q4 | 2016 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Veg | 2016-05-11 | N | 114.0145 | N | 6 | N | N | 1.1101 | 39.4971 | 51740.7441
[7 empty] | 11059 | 8152 | 1387315 | 2016-05-12 01:53 | 2016-05-12 06:55 | 302 | 11kV | 4832 | 16 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT13671 Brush ol Gosford 11kv road and centre phase HV fuse blown 31.5Amp Possum found at base of pole See 1388071 exclude 1387315,21 | May | 2016 | 2016Q4 | 2016 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2016-05-12 | N | 302 | N | 4 | N | N | 1.1101 | 39.4971 | 3531.0831
[7 empty] | 12082 | 18758 | 1387389 | 2016-05-12 10:15 | 2016-05-12 12:30 | 135 | 11kV | 9720 | 72 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 167316 live line lead broken off at dolf sub interrconnected for repairs also refer to OMS 1387389 | May | 2016 | 2016Q4 | 2016 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Not Veg | 2016-05-12 | N | 135 | N | 4 | N | N | 1.1101 | 39.4971 | 7103.0893
[7 empty] | 11420 | 12026 | 1387449 | 2016-05-12 13:00 | 2016-05-12 15:45 | 165.2667 | 11kV | 3258.7 | 22 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167318 Section isolated at request of Tim Musgrove requested emergency job due to high winds - because mains contacting newly installed poles, which have not had mains tied in | May | 2016 | 2016Q4 | 2016 | 507:80925 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2016-05-12 | N | 148.1227 | N | 4 | N | N | 1.1101 | 39.4971 | 2381.3618
[7 empty] | 11640 | 14118 | 1387538 | 2016-05-12 18:37 | 2016-05-12 22:10 | 213 | 11kV | 26584.1833 | 125 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | S10844 Jubilee Park - B phase 11kV fuse (OQFRN 75 Amp) blown Transformer tail defective. Also Dist #2 was in LV parallel with PT63295 Prince Edward Jubilee. LV parallel failed when load from football stadium lights came on. See 1388046 - Secondary Event 1387538 - GIS:1387544 | May | 2016 | 2016Q4 | 2016 | ZN10999:PA4 | ZN10999:PA4 | ZN10999/000004 | GEORGES RIVER | UG | Not Veg | 2016-05-12 | N | 212.6735 | N | 4 | N | N | 1.1101 | 39.4971 | 19426.9371
[7 empty] | 11311 | 11053 | 1387694 | 2016-05-13 16:00 | 2016-05-13 16:35 | 35 | 11kV | 3121 | 185 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa2 "Ghamberlain Taylor 0.1" 11kV Reclsoer 41845 North Erina tripped on earth fault Abnormal: AB42920 opened and LB43440 closed Cause: not ascertained. Patrolled mains and okay See 1388074,5exclude 1387694 | May | 2016 | 2016Q4 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2016-05-13 | N | 16.8703 | N | 4 | N | N | 1.1101 | 39.4971 | 2280.7347
[7 empty] | 11561 | 13283 | 1387594 | 2016-05-13 08:49 | 2016-05-13 19:35 | 646 | 11kV | 16183 | 73 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 167329 Phases A & B Overcurrent Truck hit pole HR-10118 Kyle St sub Excluded OMS 1387594 ## | May | 2016 | 2016Q4 | 2016 | 511:29872 | 511:29872 | ZN00511/029872 | MAITLAND | OH | Not Veg | 2016-05-13 | N | 221.6849 | N | 4 | N | N | 1.1101 | 39.4971 | 11826.0591
[7 empty] | 11459 | 12364 | 1387729 | 2016-05-13 19:03 | 2016-05-13 21:15 | 132 | 11kV | 34455 | 292 | HV | Animal Possum | Animal | O/H Link | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa12 "Yarramalong" fdr 11kv recloser 48813 yarramalong Boyds 3.7 tripped on overcurrent Cause: Possum at autolink 47340 No SCADA control at Re48813 and RE44753 See 1388078,9 exclude 1387729,41 | May | 2016 | 2016Q4 | 2016 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2016-05-13 | N | 117.9966 | N | 4 | N | N | 1.1101 | 39.4971 | 25178.6977
[7 empty] | 10751 | 5004 | 1387755 | 2016-05-13 21:17 | 2016-05-14 00:25 | 188 | 11kV | 183315 | 1222 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S2400 Berowra Panel 15 tripped reclosed tripped and locked out on Cause not ascertained for outage. See OMS 1388024 1388025 1388026 1387755 | May | 2016 | 2016Q4 | 2016 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Veg | 2016-05-13 | N | 150.0123 | N | 4 | N | N | 1.1101 | 39.4971 | 133961.1951
[7 empty] | 10661 | 3994 | 1387880 | 2016-05-15 03:00 | 2016-05-15 04:05 | 65 | 11kV | 41559 | 932 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12610 Long Jetty 11kV Panel 20 "Matcham St" tripped, reclosed & locked out on: Relays: A phase IOC, EFI, REcloser, Lockout, Earth fault check Signals: 11kv trip, Zone EArth, Group Earth EFI's:Nil 11kV UG Fault from Zn12610 Long Jetty Panel 20 to LB41498 tee to PT 64154 See 1388111,2 exclude 1387880 | May | 2016 | 2016Q4 | 2016 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | UG | Not Veg | 2016-05-15 | N | 44.5912 | N | 3 | N | N | 1.1101 | 39.4971 | 30370.0914
[7 empty] | 10679 | 4266 | 1387878 | 2016-05-15 00:18 | 2016-05-15 07:28 | 430 | 11kV | 51971 | 322 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 167337 2 fault operations Earth Fault Targets V -279A, W-189A, E-179A Main down pole GW-10025. Excluded OMS 1387878. | May | 2016 | 2016Q4 | 2016 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2016-05-15 | N | 161.4006 | N | 3 | N | N | 1.1101 | 39.4971 | 37978.8739
[7 empty] | 10987 | 7475 | 1387896 | 2016-05-15 09:20 | 2016-05-15 17:45 | 505 | 11kV | 8960 | 18 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | UGOH | Unplanned | No Weather Impact | N | LID 167339 interrupt from sw 37772 to reconnect UGOH to new pole HR-10118 | May | 2016 | 2016Q4 | 2016 | 511:29872 | 511:29872 | ZN00511/029872 | MAITLAND | OH | Not Veg | 2016-05-15 | N | 497.7778 | N | 3 | N | N | 1.1101 | 39.4971 | 6547.7037
[7 empty] | 10927 | 6890 | 1388223 | 2016-05-16 23:43 | 2016-05-17 01:55 | 132 | 11kV | 28427 | 1572 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At S36300 Balgowlah North Panel 8 tripped and reclosed on A phase O/C, EFI, Timing, Lockout Signals: 11kV Trip, No1 Group Earth, Zone Earth. Cause: Possum on UGOH to S16275 Cres 25. Bond Burnt Off 1388244 1388245 1388223 | May | 2016 | 2016Q4 | 2016 | ZN36300:PA8 | ZN36300:PA8 | ZN36300/000008 | NORTHERN BEACHES | OH | Not Veg | 2016-05-16 | N | 18.0833 | N | 1 | N | N | 1.1101 | 39.4971 | 20773.6131
[7 empty] | 11191 | 9865 | 1388265 | 2016-05-17 09:45 | 2016-05-17 18:00 | 495 | 11kV | 495 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 167365 Live Line Lead burnt off A phase DOLF on sub52629. Address is 44 Jenkins Rd Oakhampton. Line Crew or Subs Crew req'd. also refer to 1388265 | May | 2016 | 2016Q4 | 2016 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2016-05-17 | N | 495 | N | 1 | N | N | 1.1101 | 39.4971 | 361.7314
[7 empty] | 11659 | 14353 | 1388525 | 2016-05-18 13:45 | 2016-05-18 18:08 | 263 | 11kV | 21413 | 83 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa14 S18032 Singleton Manooka 50A OQFRN centre phase HV fuse blown due to transformer failure See 1388750,1 exclude 1388525 | May | 2016 | 2016Q4 | 2016 | ZN12650:PA14 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | UG | Not Veg | 2016-05-18 | N | 257.988 | N | 2 | N | N | 1.1101 | 39.4971 | 15647.9888
[7 empty] | 10659 | 3956 | 1388563 | 2016-05-18 16:24 | 2016-05-18 19:04 | 160 | 11kV | 2488 | 16 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | IR50285 Sirius Orion tripped, reclosed tripped and locked out on O/C Trip Suspect UG fault between S64397 and S750 and S7075 1388663 1388665 1388666 1388563 | May | 2016 | 2016Q4 | 2016 | ZN129:PA27 | ZN80:PA31 | ZN00080/000031 | LANE COVE | UG | Not Veg | 2016-05-18 | N | 155.5 | N | 2 | N | N | 1.1101 | 39.4971 | 1818.157
[7 empty] | 11904 | 16959 | 1388605 | 2016-05-19 03:01 | 2016-05-19 03:46 | 45 | 11kV | 29700 | 660 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At S195 Pymble 11kV panel 22 tripped and reclosed Relays: Earth Fault, A phase timed O/C, EFI and Fault Check Relays. Tx4 Fault Check Signals: 11kV trip, Zone Earth, No4 Group Earth Cause: Possum on 11kV UGOH adjacent to PT1140 Pearson Ave | May | 2016 | 2016Q4 | 2016 | ZN195:PA22 | ZN195:PA10 | ZN00195/000010 | KU-RING-GAI | OH | Not Veg | 2016-05-19 | N | 45 | N | 7 | N | N | 1.1101 | 39.4971 | 21703.884
[7 empty] | 11240 | 10252 | 1388637 | 2016-05-19 09:24 | 2016-05-19 10:05 | 41 | 11kV | 81344 | 1984 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12640 Umina Pa2 opened, reclosed & opened on Trip Alarm, IOC A to B & Lockout relay. 11kv trip Bird hit 11kv at PT11374 OCean Beach Pioneer. Removed by DOp See 1388637,47,55 | May | 2016 | 2016Q4 | 2016 | ZN12640:PA2 | ZN12640:PA2 | ZN12640/000002 | CENTRAL COAST | OH | Not Veg | 2016-05-19 | N | 41 | N | 7 | N | N | 1.1101 | 39.4971 | 59443.796
[7 empty] | 11007 | 7661 | 1388608 | 2016-05-19 06:24 | 2016-05-19 14:45 | 501 | 11kV | 73632 | 257 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 167388 2 fault operations A & B phase Overcurrent 11kV OHM down between sub 54002 and pole FR-62004. Excluded oms 1388608 + 1388609 | May | 2016 | 2016Q4 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2016-05-19 | N | 286.5058 | N | 7 | N | N | 1.1101 | 39.4971 | 53808.0938
[7 empty] | 10547 | 2549 | 1388694 | 2016-05-19 11:30 | 2016-05-19 15:15 | 225 | 11kV | 900 | 4 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167394 Urgent repairs to broken dead end at pole LS-20320 | May | 2016 | 2016Q4 | 2016 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2016-05-19 | N | 225 | N | 7 | N | N | 1.1101 | 39.4971 | 657.6935
[7 empty] | 11318 | 11100 | 1391008 | 2016-05-19 23:03 | 2016-05-19 23:25 | 22 | 11kV | 16302 | 741 | HV | Staff Operation | Utility Process Issue | O/H Link | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty 11kV Panel 6 "Rohdin Drive" fdr RE62166 Watking Thompson Aux Supply Fail Incorrect switching. LB40825 opened instead of AB40285 | May | 2016 | 2016Q4 | 2016 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Not Veg | 2016-05-19 | N | 22 | N | 7 | N | N | 1.1101 | 39.4971 | 11913.0208
[7 empty] | 10757 | 5053 | 1388842 | 2016-05-19 23:10 | 2016-05-20 00:02 | 52 | 11kV | 66872 | 1286 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn9550 Gwawley bay Panel 3 tripped on B and C phase OC E/E and EFI Signals: 11kV Trip Protection trip Cause: Possum found at the base of UGOH adjacent to S9086 No apparent damage | May | 2016 | 2016Q4 | 2016 | ZN9550:PA3 | ZN9550:PA3 | ZN09550/000003 | SUTHERLAND | Unknown | Unknown | 2016-05-19 | N | 52 | N | 7 | N | N | 1.1101 | 39.4971 | 48868.0852
[7 empty] | 11071 | 8312 | 1388859 | 2016-05-20 07:34 | 2016-05-20 08:50 | 76 | 11kV | 97736 | 1286 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12640 Umina Pa10 Open Bond, Roadside Phase at AB43812 11kv Bond opened on roadside phase at AB43812 See 1391011 exclude 1388859 | May | 2016 | 2016Q4 | 2016 | ZN12640:PA10 | ZN12640:PA10 | ZN12640/000010 | CENTRAL COAST | OH | Not Veg | 2016-05-20 | N | 76 | N | 2 | N | N | 1.1101 | 39.4971 | 71422.5861
[7 empty] | 10384 | 222 | 1388904 | 2016-05-20 09:25 | 2016-05-20 10:25 | 60 | 11kV | 47625 | 1179 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 167410 3 fault operations A phase Instantaneous Overcurrent; Earth Fault | May | 2016 | 2016Q4 | 2016 | 202:34245 | 202:34245 | ZN00202/034245 | NEWCASTLE | UG | Not Veg | 2016-05-20 | N | 40.3944 | N | 2 | N | N | 1.1101 | 39.4971 | 34802.9453
[7 empty] | 11681 | 14588 | 1388807 | 2016-05-19 19:19 | 2016-05-20 13:05 | 1066 | 11kV | 120030 | 1368 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 21 tripped and locked out Relays: SEL Singals: 11kV Trip. UGOH to S4487 Old Berowra Ethel Midle Phase lightning arrestor blown. Previosuly tripped and reclosed. See OMS 1389371 1389372 1388199 1388818 1388810 1388807 | May | 2016 | 2016Q4 | 2016 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Not Veg | 2016-05-19 | N | 87.7412 | N | 7 | N | N | 1.1101 | 39.4971 | 87714.3837
[7 empty] | 12225 | 20181 | 1389107 | 2016-05-21 03:24 | 2016-05-21 06:25 | 181 | 11kV | 9584 | 404 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa12 @ recloser 46929 Jarrett Kirkness tripped and reclose on: Relays OC, IOC. Signals: 11kv trip @PT11573 Marangani Yuroka centre phase 31.5 Amp HDO blown Stick at HDO on PT11573. Made safe and restored supply See 1391182,4 exclude 1389107 | May | 2016 | 2016Q4 | 2016 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Veg | 2016-05-21 | N | 23.7228 | N | 3 | N | N | 1.1101 | 39.4971 | 7003.7045
[7 empty] | 11609 | 13842 | 1389110 | 2016-05-21 04:14 | 2016-05-21 09:50 | 336 | 11kV | 358682 | 1744 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12600 Lisarow Panel 3 "Lisarow High Taylor" fdr tripped on Relays: Inst O/C, timed O/C, EFI Signals: 11kv trip EFI's: S12399 S18173 S14623 S14247 Cable fault from S14378 Pierce Northview Sw6364 to open UGOH NB: Sw6365 at S14378 is WDNO and AB41007 is open defective See 1391197,8,9,200 exclude 1389110 | May | 2016 | 2016Q4 | 2016 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | UG | Not Veg | 2016-05-21 | N | 205.6663 | N | 3 | N | N | 1.1101 | 39.4971 | 262114.2263
[7 empty] | 10374 | 56 | 1389195 | 2016-05-21 22:15 | 2016-05-22 04:49 | 394 | 11kV | 7541 | 39 | HV | 3rd Party Vehicle | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167416 car hit abs 7717 pole opening one phase. ABS bridged out (fatality). dq | May | 2016 | 2016Q4 | 2016 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Not Veg | 2016-05-21 | N | 193.359 | N | 3 | N | N | 1.1101 | 39.4971 | 5510.7404
[7 empty] | 11568 | 13357 | 1389497 | 2016-05-23 19:27 | 2016-05-23 19:55 | 27.65 | 11kV | 2654.4 | 96 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167434 DOLF : 63 Amp Excluded OMS 1389497 & 1389524 | May | 2016 | 2016Q4 | 2016 | 524:33578 | 524:33578 | ZN00524/033578 | CESSNOCK | OH | Veg | 2016-05-23 | N | 27.65 | N | 1 | N | N | 1.1101 | 39.4971 | 1939.7572
[7 empty] | 10435 | 1047 | 1389542 | 2016-05-24 01:26 | 2016-05-24 02:11 | 45 | 11kV | 133875 | 2975 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 31 tripped on Relays: B phase overcurrent, Earth Fault, fault Check and EFI. Signals: 11kV trip, Zone Earth, TX3 Group Earth Cause: Possum came einto contact with 11kV UGOH to Recloser 48117 - Broken Surge Arrestor | May | 2016 | 2016Q4 | 2016 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Not Veg | 2016-05-24 | N | 45 | N | 1 | N | N | 1.1101 | 39.4971 | 97831.9014
[7 empty] | 12106 | 19001 | 1389911 | 2016-05-25 18:42 | 2016-05-25 19:19 | 37.4333 | 11kV | 3219.2667 | 86 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 167465 A phase DOLF : 31 Amp Possible fuse fatigue Excluded OMS 1389911 | May | 2016 | 2016Q4 | 2016 | 242:81538 | 242:81538 | ZN00242/081538 | PORT STEPHENS | OH | Not Veg | 2016-05-25 | N | 37.4333 | N | 3 | N | N | 1.1101 | 39.4971 | 2352.5451
[7 empty] | 10457 | 1399 | 1389919 | 2016-05-25 20:53 | 2016-05-25 21:25 | 32.2 | 11kV | 2543.8 | 79 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167467 C Phase DOLF : 31 Amp Dead possum 245V, loads 70A, 105A, 95A excluded OMS 1389922 | May | 2016 | 2016Q4 | 2016 | 214:8665 | 214:8665 | ZN00214/008665 | LAKE MACQUARIE | OH | Not Veg | 2016-05-25 | N | 32.2 | N | 3 | N | N | 1.1101 | 39.4971 | 1858.934
[7 empty] | 11284 | 10730 | 1389937 | 2016-05-26 01:36 | 2016-05-26 03:41 | 125 | 11kV | 178899 | 1852 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN3472 Sefton 11kv Panel 27 'S4003 Gascoine Rodd' feeder tripped Relays: E/F, F/C, EFI Signals: 11kv trip, Tx2 GE, ZE Field Efi's: no access to S4003, S8762, Dop unable to interpret electronic efi's at S47550, S47549, S47546 & S35161 Remarks: UG fault. Feeder isolated, Sw/tag left at S8762. 11kv feeder fault from S8762 Woods Batt to S47550 Batt Allawah to S47551 Wallace Rodd | May | 2016 | 2016Q4 | 2016 | ZN3472:PA27 | ZN3472:PA27 | ZN03472/000027 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-05-26 | N | 96.5977 | N | 4 | N | N | 1.1101 | 39.4971 | 130734.1126
[7 empty] | 11621 | 13975 | 1389932 | 2016-05-25 23:33 | 2016-05-26 07:00 | 447 | 11kV | 15229 | 95 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa21 "Grants Rd" fdr 11kv IR61364 Brieses Peats 0.4 tripped Relays: OC trip, SEF trip, Lockout Tree/branch brough down HV OH outside 52 Viitasalo Rd Region please investigate why RE46763 did not trip for HV wires down at PT61544. DOp issued permits at LK42028 See 1391222,3,4 exclude 1389932,8 | May | 2016 | 2016Q4 | 2016 | ZN12630:PA21 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2016-05-25 | N | 160.3053 | N | 3 | N | N | 1.1101 | 39.4971 | 11128.904
[7 empty] | 11249 | 10400 | 1389942 | 2016-05-26 06:08 | 2016-05-26 08:45 | 156.9667 | 11kV | 470.9 | 3 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167474 Single phase DOLF : 16 Amp Possum excluded OMS 1389953 | May | 2016 | 2016Q4 | 2016 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2016-05-26 | N | 156.9667 | N | 4 | N | N | 1.1101 | 39.4971 | 344.1198
[7 empty] | 10982 | 7439 | 1390003 | 2016-05-26 08:32 | 2016-05-26 11:30 | 178 | 11kV | 356 | 2 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Panel 20 "Warnervale feeder" PT11981 Footpath phase 10k HDO Tree branch on PT11981 removed by DOp | May | 2016 | 2016Q4 | 2016 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2016-05-26 | N | 178 | N | 4 | N | N | 1.1101 | 39.4971 | 260.1543
[7 empty] | 11776 | 15699 | 1390070 | 2016-05-26 13:05 | 2016-05-26 15:40 | 154.5 | 11kV | 4789.5 | 31 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167481 Single phase Suspect no protection operated. Job was initially given to EMSO D Meyers for a single customer at a single sub. Dave advised the outage was more widespread. Fuse Saver 44033 was found open when DOP's first arrived on the site. DOPs patrolled the feeder and found no fault then successfully closed Fuse Saver 44033. | May | 2016 | 2016Q4 | 2016 | 511:29877 | 511:29877 | ZN00511/029877 | CESSNOCK | OH | Veg | 2016-05-26 | N | 154.5 | N | 4 | N | N | 1.1101 | 39.4971 | 3500.0253
[7 empty] | 12120 | 19104 | 1390792 | 2016-05-27 13:00 | 2016-05-27 13:50 | 50 | 11kV | 250 | 5 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 167493 Broken tie wire No protection operated, line isolated for LL technique with feeder de-energised to repair broken tie wire. | May | 2016 | 2016Q4 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2016-05-27 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 12235 | 20292 | 1386484 | 2016-05-27 10:10 | 2016-05-27 14:10 | 240 | 11kV | 36519 | 364 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Suring switching at S15013 11kV panel 10 tripped on SEL and Lockout Signals 11kV Trip Cause: bond burnt off between S16910 and Link 24212. Abnormal Switching: CP20234 Closed, CP1126 Open See OMS1390862 1390865 1390866 1390272 1390241 1386484 | May | 2016 | 2016Q4 | 2016 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2016-05-27 | N | 100.3269 | N | 4 | N | N | 1.1101 | 39.4971 | 26687.0081
[7 empty] | 11587 | 13557 | 1390314 | 2016-05-27 13:59 | 2016-05-27 15:51 | 112 | 11kV | 23866 | 239 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa25 Intellirupter CP61082 Brieses Peats 0.3 tripped on overcurrent, lockout Cause not ascertained See 1391279,80,1,3 exclude 1390314 | May | 2016 | 2016Q4 | 2016 | ZN12630:PA25 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2016-05-27 | N | 99.8577 | N | 4 | N | N | 1.1101 | 39.4971 | 17440.5689
[7 empty] | 11495 | 12685 | 1390377 | 2016-05-27 22:40 | 2016-05-28 00:30 | 110 | 11kV | 21560 | 196 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 167495 B Phase No protection operated. Interruption required to carry out repairs. B phase Line DOLF 41526 arcing, also surge arrestor damaged and tail swinging in the air. | May | 2016 | 2016Q4 | 2016 | 502:48004 | 502:48004 | ZN00502/048004 | MAITLAND | OH | Not Veg | 2016-05-27 | N | 110 | N | 4 | N | N | 1.1101 | 39.4971 | 15755.4121
[7 empty] | 12048 | 18472 | 1390455 | 2016-05-28 10:08 | 2016-05-28 14:30 | 262 | 11kV | 1792 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167497 Single phase broken llc dropper lead. Excluded oms 1390455 | May | 2016 | 2016Q4 | 2016 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2016-05-28 | N | 99.5556 | N | 1 | N | N | 1.1101 | 39.4971 | 1309.5407
[7 empty] | 10785 | 5328 | 1390578 | 2016-05-29 03:22 | 2016-05-29 09:45 | 383 | 11kV | 6128 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 167498 Single phase DOLF : 10 Amp wire down to sub 25777 Excluded oms 1390578 | May | 2016 | 2016Q4 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2016-05-29 | N | 383 | N | 5 | N | N | 1.1101 | 39.4971 | 4478.1617
[7 empty] | 11222 | 10087 | 1390605 | 2016-05-29 09:49 | 2016-05-29 10:25 | 36 | 11kV | 3636 | 101 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167500 A Phase DOLF : 40 Amp Dead possum at base of pole 247V, loads 400A, 350A, 250A Excluded OMS 1390605 | May | 2016 | 2016Q4 | 2016 | 258:80790 | 258:80790 | ZN00258/080790 | NEWCASTLE | OH | Not Veg | 2016-05-29 | N | 36 | N | 5 | N | N | 1.1101 | 39.4971 | 2657.0816
[7 empty] | 11406 | 11901 | 1390677 | 2016-05-29 19:01 | 2016-05-29 20:25 | 84 | 11kV | 128436 | 1529 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 35 tripped Abnormal Switching: CP61231 Closed, SW/B Opened At S48870 Birdwood Blaxland Possums found at the base of pole LB61231. Possible damage to surge arrestors. See OMS 1390677 1390678 1390682 1390814 | May | 2016 | 2016Q4 | 2016 | ZN4545:PA35 | ZN4545:PA35 | ZN04545/000035 | RYDE | OH | Not Veg | 2016-05-29 | N | 84 | N | 5 | N | N | 1.1101 | 39.4971 | 93857.2406
[7 empty] | 11069 | 8302 | 1391314 | 2016-05-29 21:19 | 2016-05-29 21:28 | 9 | 11kV | 13338 | 1482 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn13000 Lake Mummorah Panel 4 "pacific Hwy Nth tripped and reclosed Relays: C phase timed overcurrent & EFI Signals: 11kv trip EFI's: Nil Abnormal:AB43825 is open with LB40172 closede Cause not ascetained | May | 2016 | 2016Q4 | 2016 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Veg | 2016-05-29 | N | 9 | N | 5 | N | N | 1.1101 | 39.4971 | 9747.017
[7 empty] | 11216 | 10035 | 1390690 | 2016-05-29 20:38 | 2016-05-30 08:20 | 702 | 11kV | 407854.6833 | 3966 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn10990 Arncliffe 11kv Panel No 2 tripped on: Relays - SEL left Signals: 11kv trip Abnormal: LB31125 closed, Sw/A open @ S10126 Shepherd Bardwell Remarks: cause not ascertained. Span of 11kv down beyond LK30826. Lman have repaired | May | 2016 | 2016Q4 | 2016 | ZN10990:PA2 | ZN10998:PA29 | ZN10998/000029 | BAYSIDE | OH | Not Veg | 2016-05-29 | N | 102.8378 | N | 5 | N | N | 1.1101 | 39.4971 | 298048.1729
[7 empty] | 10625 | 3632 | 1390732 | 2016-05-30 11:00 | 2016-05-30 15:00 | 240 | 11kV | 1440 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 167513 Broken Bph dropper 11kV links 46855 Excluded oms 1390732 | May | 2016 | 2016Q4 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2016-05-30 | N | 240 | N | 5 | N | N | 1.1101 | 39.4971 | 1052.3095
[7 empty] | 11529 | 12952 | 1390967 | 2016-05-30 15:20 | 2016-05-30 15:49 | 29 | 11kV | 12731 | 439 | HV | Staff Operation | Utility Process Issue | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Ex Zn14144 Wamberal section of panel 2 Gleneagles Fairqway feeder beyond RE44946 Kulnurra rd Abnormal: Lisarow Zn 42920 open KB43440 closed USL 40857 open AB41247 closed AOp set up RE44936 not 44946 for D&R 382417 See 1391325 exclude 1390967,8,78,9,81,2,90 | May | 2016 | 2016Q4 | 2016 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2016-05-30 | N | 29 | N | 5 | N | N | 1.1101 | 39.4971 | 9303.4393
[7 empty] | 10496 | 1944 | 1391041 | 2016-05-30 19:02 | 2016-05-30 20:48 | 106 | 11kV | 74890 | 741 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn10990 Arncliffe - 11kV Pnl.12 - Tripped on: Timed IOC A & C phase, Reclose timing, lockout, EFI Vehicle hit pole between S10718 (Sw/B) and S10147 (Sw/B) and S65351 (Sw/A) See 1391156 1399157 | May | 2016 | 2016Q4 | 2016 | ZN10990:PA12 | ZN10998:PA9 | ZN10998/000009 | BAYSIDE | OH | Not Veg | 2016-05-30 | N | 101.0661 | N | 5 | N | N | 1.1101 | 39.4971 | 54727.4031
[7 empty] | 10954 | 7131 | 1391066 | 2016-05-30 21:09 | 2016-05-30 22:50 | 101 | 11kV | 202 | 2 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167517 A phase DOLF : 10 Amp POSSUM FOUND AT BASE OF SUB POLE REPLACED 10A DOLF FOR 10A. Excluded OMS 1391066 | May | 2016 | 2016Q4 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2016-05-30 | N | 101 | N | 5 | N | N | 1.1101 | 39.4971 | 147.6156
[7 empty] | 11156 | 9451 | 1391042 | 2016-05-30 20:12 | 2016-05-31 02:00 | 348 | 11kV | 696 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 167516 No protection operation, transformer spitting oil. Transformer changed. Excluded OMS 1391042 | May | 2016 | 2016Q4 | 2016 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2016-05-30 | N | 348 | N | 5 | N | N | 1.1101 | 39.4971 | 508.6163
[7 empty] | 11902 | 16953 | 1391076 | 2016-05-31 01:30 | 2016-05-31 02:30 | 60 | 11kV | 16135 | 287 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S1850 Bass Hill Zone - The 11kv Panel 11 "Georgina St" feeder tripped on: Signals: 11kv trip Relays: SEL Remarks: Bond. 11kv Bond off on Roadside phase of AB 8 | May | 2016 | 2016Q4 | 2016 | ZN1850:PA11 | ZN1850:PA42 | ZN01850/000042 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-05-31 | N | 56.2195 | N | 5 | N | N | 1.1101 | 39.4971 | 11790.9821
[7 empty] | 11597 | 13680 | 1391085 | 2016-05-31 06:56 | 2016-05-31 13:51 | 415 | 11kV | 27632 | 80 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Cold <10C | N | LID 167520 Single phase DOLF : 10 Amp mains down near sub 25777 Excluded oms 1341104 & 1391085 | May | 2016 | 2016Q4 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2016-05-31 | N | 345.4 | N | 5 | N | N | 1.1101 | 39.4971 | 20192.6506
[7 empty] | 11915 | 17060 | 1391129 | 2016-05-31 09:30 | 2016-05-31 16:45 | 435 | 11kV | 30571 | 101 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167535 Overcurrent; Earth Fault Excluded OMS 1391129 | May | 2016 | 2016Q4 | 2016 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2016-05-31 | N | 302.6832 | N | 5 | N | N | 1.1101 | 39.4971 | 22340.3851
[7 empty] | 10758 | 5062 | 1391368 | 2016-05-31 17:49 | 2016-05-31 18:50 | 61 | 11kV | 4472 | 512 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Heavy | N | Ex Zn12690 Berkeley Vale section of Pa8 REC41115 Lake Edge Audie tripped & reclosed @PT12481 Waroon Chetwyn 31.5k centre phase blown. Tree branch at PT12481 See 1391490,1 exclude 1391368 | May | 2016 | 2016Q4 | 2016 | ZN12690:PA8 | ZN12690:PA8 | ZN12690/000008 | CENTRAL COAST | OH | Veg | 2016-05-31 | N | 8.7344 | N | 5 | N | N | 1.1101 | 39.4971 | 3268.0057
[7 empty] | 11990 | 17974 | 1391439 | 2016-05-31 23:37 | 2016-06-01 01:23 | 106 | 11kV | 70399 | 845 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Planned LID 167536 2 fault operations C phase Overcurrent; Earth Fault Blown L/A UGOH pole GW-80140 . Excluded OMS 1391412 | May | 2016 | 2016Q4 | 2016 | 223:14398 | 223:14398 | ZN00223/014398 | LAKE MACQUARIE | OH | Not Veg | 2016-05-31 | N | 83.3124 | N | 5 | N | N | 1.1101 | 39.4971 | 51445.5128
[7 empty] | 12033 | 18354 | 1391416 | 2016-06-01 03:45 | 2016-06-01 05:01 | 76 | 11kV | 152 | 2 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Light | N | Ex Zn13000 Lakemunmorah section of Pa2 PT14113 Tall Timbers STW 31.5K centre phase & road fuses blown due to branch across 11kv bushings See 1391502 exclude 1391416 | June | 2016 | 2016Q4 | 2016 | ZN13000:PA2 | ZN13000:PA2 | ZN13000/000002 | CENTRAL COAST | OH | Veg | 2016-06-01 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 11955 | 17566 | 1391539 | 2016-06-01 11:18 | 2016-06-01 16:05 | 287 | 11kV | 106706 | 825 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN2835 Burwood 11kv Panel 36 'S3108 Mosley Cooper' feeder tripped Relays: 'A' phase O/C, F/C, efi Signals: Tx 3 GE, ZE, 11kv trip Field efi's: S3108 @S3770 Weeroona Centenary No.1 A/C Relay Panel: L/O Remarks: UG fault. 11kv feeder fault from S3108 Mosely Cooper to S331 Oxford Homebush to S1904 Strathfield Sq to S7956 The Crescent Homebush No.2 tee S68 Albert Homebush | June | 2016 | 2016Q4 | 2016 | ZN2835:PA36 | ZN2835:PA36 | ZN02835/000036 | STRATHFIELD | UG | Not Veg | 2016-06-01 | N | 129.3406 | N | 3 | N | N | 1.1101 | 39.4971 | 77977.5975
[7 empty] | 11625 | 14015 | 1391421 | 2016-06-01 06:24 | 2016-06-01 21:30 | 906 | 11kV | 22792 | 204 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167541 1 fault operation 3 phase Intellirupter Txf 26746 found faulty. Note Sw 43392 did not trip. Excluded OMS 1391421 | June | 2016 | 2016Q4 | 2016 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2016-06-01 | N | 111.7255 | N | 3 | N | N | 1.1101 | 39.4971 | 16655.7213
[7 empty] | 11687 | 14645 | 1391829 | 2016-06-02 11:27 | 2016-06-02 14:40 | 193 | 11kV | 47147 | 1251 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Zn847 Hornsby - Panel 15 tripped on: B & C phase IOC, EFI Field EFIs: S4722, S4413 & S4465 Lightning arrestor failed at PT2046. Could not restore via LV // See 1392064 1392065 | June | 2016 | 2016Q4 | 2016 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | OH | Not Veg | 2016-06-02 | N | 37.6875 | N | 3 | N | N | 1.1101 | 39.4971 | 34453.637
[7 empty] | 11982 | 17847 | 1391962 | 2016-06-02 17:04 | 2016-06-02 17:31 | 27 | 11kV | 30105 | 1115 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | REC 20285 Alfred Parr - tripped on: Earth Fault Abnormal: S50262 (Sw/A) Closed with LK21622 Open. S16549 (Sw/A) Closed with S17099 (Sw/A) Open. Protection malfunction - Recloser has been tripping on earth fault when switching is taking place on the feeder. Recloser has now been by-passed. | June | 2016 | 2016Q4 | 2016 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | OH | Not Veg | 2016-06-02 | N | 27 | N | 3 | N | N | 1.1101 | 39.4971 | 21999.8461
[7 empty] | 11307 | 11008 | 1392019 | 2016-06-02 22:04 | 2016-06-02 23:45 | 101 | 11kV | 30381 | 396 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167568 2 fault operation A & B phase Overcurrent Protection AB O/C 3.3kA; Fdr trunk patroled no cause found Excluded OMS 1392019 | June | 2016 | 2016Q4 | 2016 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2016-06-02 | N | 76.7197 | N | 3 | N | N | 1.1101 | 39.4971 | 22201.5387
[7 empty] | 11704 | 14857 | 1392254 | 2016-06-03 17:14 | 2016-06-03 19:25 | 131 | 11kV | 213915 | 2399 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.36L - tripped onl: Sensitive Earth Fault Cause not ascertained. Suspected fault between S47631 (Sw/B) to S10662 (Sw/A) tee AB30048 tee AB30226 tee PT61469. DOp unable to located cause of SEF trip in this area. See 1394756 1394757 1394759 | June | 2016 | 2016Q4 | 2016 | ZN10999:PA36 | ZN10991:PA2 | ZN10991/000002 | GEORGES RIVER | OH | Veg | 2016-06-03 | N | 89.1684 | N | 1 | N | N | 1.1101 | 39.4971 | 156322.7726
[7 empty] | 10940 | 7010 | 1392301 | 2016-06-04 00:49 | 2016-06-04 02:18 | 89 | 11kV | 21626 | 274 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | Y | Zn3472 Sefton - Pnl.29 tripped, reclosed, tripped and lockout out on: EF, EFI, Fault Check Abormal: S6819 (Sw/B) closed with (Sw/A) Open. AB1867 Closed with S1100 (Sw/A) Open UG cable fault between S8974 (Sw/B) to S4235 (Sw/A) to S6819 (Sw/B) See 1396055 1396056 | June | 2016 | 2016Q4 | 2016 | ZN3472:PA29 | ZN3472:PA29 | ZN03472/000029 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-06-04 | N | 78.927 | N | 8 | N | N | 1.1101 | 39.4971 | 15803.6429
[7 empty] | 11428 | 12114 | 1394684 | 2016-06-04 02:50 | 2016-06-04 03:51 | 61 | 11kV | 14884 | 244 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | EX Zn1193 Lindfield Zn section of Pa12 CP49996 Churchill Fairbairn tripped, reclosed & locked out on Relays:OC Signals: 11kv trip EFI's Nil Cause not ascertained Lineworker to Patrol | June | 2016 | 2016Q4 | 2016 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Veg | 2016-06-04 | N | 61 | N | 8 | N | N | 1.1101 | 39.4971 | 10876.7882
[7 empty] | 10656 | 3935 | 1392442 | 2016-06-04 12:06 | 2016-06-04 13:26 | 80 | 11kV | 103840 | 1298 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn36300 Balgowlah North - Pnl.13 tripped, reclosed, tripped and locked out on: Earth Fault, IOC C phase Tree branch on mains in Quirk Rd near Balgowlah Zone Sub (1 Span Out) | June | 2016 | 2016Q4 | 2016 | ZN36300:PA13 | ZN36300:PA13 | ZN36300/000013 | NORTHERN BEACHES | OH | Veg | 2016-06-04 | Y | 80 | N | 8 | N | Y | 1.1101 | 39.4971 | 75883.2092
[7 empty] | 11628 | 14032 | 1392420 | 2016-06-04 11:24 | 2016-06-04 13:30 | 126 | 11kV | 252 | 2 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | Y | LID 167581 Single phase DOLF : 3 Amp tree branch on lv mains Excluded oms 1392420 | June | 2016 | 2016Q4 | 2016 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-06-04 | N | 126 | N | 8 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 10372 | 44 | 1392486 | 2016-06-04 12:53 | 2016-06-04 14:36 | 103 | 11kV | 6180 | 60 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15011 Beacon Hill - Pnl.4 tripped on: C phase O/C, C phase IOC Tree branch on mains outside of Zone Substation, removed by DOp | June | 2016 | 2016Q4 | 2016 | ZN15011:PA4 | ZN15011:PA6 | ZN15011/000006 | NORTHERN BEACHES | OH | Veg | 2016-06-04 | Y | 103 | N | 8 | N | Y | 1.1101 | 39.4971 | 4516.1617
[7 empty] | 10828 | 5796 | 1392559 | 2016-06-04 13:42 | 2016-06-04 14:44 | 62 | 11kV | 103168 | 1664 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn10993 Hurstville North - Pnl.35 tripped on: Earth Leakage, IOC, Lockout, EFI Abnormal: S10876 (Sw/B) Closed with S10987 (Sw/A) Open Tree brench on OH mains. | June | 2016 | 2016Q4 | 2016 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | OH | Veg | 2016-06-04 | N | 62 | N | 8 | N | N | 1.1101 | 39.4971 | 75392.1315
[7 empty] | 11817 | 16209 | 1392767 | 2016-06-04 15:13 | 2016-06-04 15:50 | 37 | 11kV | 40700 | 1100 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | Zn847 Hornsby Panel 18 "Carrington Pacific" fdr tripped and reclsoed and tripped on Signals: 11kv trip, Prot UV Relays: C phase IOC, Cph O/C, Timing, Lockout EFI's: Nil Branch on OH wires outside 225 Galston Rd, Hornsby Heights See 1392767 exclude 1392782,5,8 | June | 2016 | 2016Q4 | 2016 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Veg | 2016-06-04 | Y | 37 | N | 8 | N | Y | 1.1101 | 39.4971 | 29742.3596
[7 empty] | 11738 | 15229 | 1392501 | 2016-06-04 13:05 | 2016-06-04 16:58 | 233 | 11kV | 233 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | Y | Ex Zn12690 Berkeley Vale section of Pa26 @PT14761 Pacific Old Tuggerah centre phase 16Amp HDO blown due to Fatigue See 1395603 exclude 1392501 | June | 2016 | 2016Q4 | 2016 | ZN12690:PA26 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Not Veg | 2016-06-04 | Y | 233 | N | 8 | N | Y | 1.1101 | 39.4971 | 170.2695
[7 empty] | 11274 | 10632 | 1392449 | 2016-06-04 12:17 | 2016-06-04 17:35 | 318 | 11kV | 36528 | 652 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | iR50407 The Scenic Bounty - tripped and lockout out on: OC Trip, Lockout Field Fault indicators operated at: The Scenic Rd nr Bounty Hill Rd (Roadside and Middle phase), The Scenic Dr near Warri Cres (Roadside and Middle phase) HV & LV mains down in Dajani Dr cnr Mamatjira McMasters beach See 1395732 1395735 | June | 2016 | 2016Q4 | 2016 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2016-06-04 | Y | 56.0245 | N | 8 | N | Y | 1.1101 | 39.4971 | 26693.585
[7 empty] | 11771 | 15613 | 1392790 | 2016-06-04 15:23 | 2016-06-04 17:40 | 137 | 11kV | 6850 | 50 | HV | Vegetation Blow/Fall In | Vegetation | Bond | Unplanned | Rain Wind Storm | Y | Ex Zn847 Hornsby section of Pa39 PT2237 Bundarra Brentford 11kv roadside 31.5K HDO operated Tree branch hit 11kv Droppers See 1392860 exclude 1392790.830.968.79 | June | 2016 | 2016Q4 | 2016 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Veg | 2016-06-04 | Y | 137 | N | 8 | N | Y | 1.1101 | 39.4971 | 5005.778
[7 empty] | 11332 | 11332 | 1392872 | 2016-06-04 16:20 | 2016-06-04 18:25 | 125 | 11kV | 7375 | 59 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Wind Storm | Y | Ex Zn12640 Umina section of Pa18 @PT12883 Mt Ettalong Calypta Blown HDO footpath side 31.5Amps See 1395624 exclude 1392872 | June | 2016 | 2016Q4 | 2016 | ZN12640:PA18 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Not Veg | 2016-06-04 | Y | 125 | N | 8 | N | Y | 1.1101 | 39.4971 | 5389.4325
[7 empty] | 11533 | 12980 | 1392997 | 2016-06-04 17:15 | 2016-06-04 18:30 | 75 | 11kV | 4275 | 57 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | Y | PT11421 Bayview Carrol 0.5 - Brown out due to Centre phase HV bond failed at pole GO05437 PT restored via LV // links 11516 and 30037 | June | 2016 | 2016Q4 | 2016 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Not Veg | 2016-06-04 | Y | 75 | N | 8 | N | Y | 1.1101 | 39.4971 | 3124.0439
[7 empty] | 11942 | 17340 | 1393201 | 2016-06-04 19:29 | 2016-06-04 22:15 | 166 | 11kV | 21401 | 425 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | Y | Ex Zn12690 Berkeely Vale section of Pa24L "Berkeley Rd" IR44289 Berkeley Enterprise 0.3 tripped and locked out on OC Breakdown' staff confirmed that this was a high resistance joint with discolouration consistent with a higher than normal operating temperature. They confirmed that whilst there was evidence of over heating at this bond, there was no evidence of flame or fire. See 1397981,6 exclude 1393201 | June | 2016 | 2016Q4 | 2016 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2016-06-04 | Y | 50.3553 | N | 8 | N | Y | 1.1101 | 39.4971 | 15639.2196
[7 empty] | 10494 | 1924 | 1393277 | 2016-06-04 21:56 | 2016-06-04 22:40 | 44 | 11kV | 7304 | 166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | REC44946 Kunarra Rd - tripped and locked out on: O/C Tree branch on mains | June | 2016 | 2016Q4 | 2016 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2016-06-04 | Y | 44 | N | 8 | N | Y | 1.1101 | 39.4971 | 5337.5478
[7 empty] | 11195 | 9894 | 1392500 | 2016-06-04 13:05 | 2016-06-05 00:10 | 665 | 11kV | 95760 | 144 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | S16802 The Crescent Carew - Roadside (C Phase) 40Amp (11kV) fuse blown Tree branch brough down OH wires outside 16-20 The Crescent Way, Dee Why. LV fuses failed to blow | June | 2016 | 2016Q4 | 2016 | ZN15001:PA2 | ZN15001:PA2 | ZN15001/000002 | NORTHERN BEACHES | OH | Veg | 2016-06-04 | Y | 665 | N | 8 | N | Y | 1.1101 | 39.4971 | 69978.5836
[7 empty] | 10809 | 5555 | 1393232 | 2016-06-04 20:13 | 2016-06-05 00:50 | 277 | 11kV | 14063 | 74 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Rain Heavy | Y | LID 167582 Three phase DOLF's : 16 Amp LV mains down pole NB-40475 to NB-40440 Blew 3 DOLFs & B&Cph LVF 250A Removed LV OHM between above poles, to be replaced. Excluded OMS OMS 1393232 | June | 2016 | 2016Q4 | 2016 | 242:81535 | 242:81535 | ZN00242/081535 | PORT STEPHENS | OH | Not Veg | 2016-06-04 | N | 190.0405 | N | 8 | N | N | 1.1101 | 39.4971 | 10276.8256
[7 empty] | 10477 | 1697 | 1393328 | 2016-06-04 23:39 | 2016-06-05 01:55 | 136 | 11kV | 137230 | 1834 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | LID 167585 2 fault operations A & B phase Overcurrent tree branch on OHM at IV-10948 removed by DOp Excluded OMS 1393328 | June | 2016 | 2016Q4 | 2016 | 224:80332 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | OH | Veg | 2016-06-04 | N | 74.8255 | N | 8 | N | N | 1.1101 | 39.4971 | 100283.6364
[7 empty] | 10690 | 4370 | 1393327 | 2016-06-04 23:39 | 2016-06-05 01:59 | 140 | 11kV | 74001 | 641 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn3425 Castle Cove section of Pa28 Easter Valley Smith" RE49995 Holly Kendall tripped on overcurrent Tree branch on mains at 54 Willowie Rd. Dist 2 isolated at S5367 also HV mains isolated between LB62052 LB62054 & S35369 See 1399518,9,20 exclude 1393327 | June | 2016 | 2016Q4 | 2016 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | OH | Veg | 2016-06-04 | N | 115.4462 | N | 8 | N | N | 1.1101 | 39.4971 | 54077.7481
[7 empty] | 12040 | 18422 | 1393351 | 2016-06-05 00:03 | 2016-06-05 02:28 | 145 | 11kV | 220255 | 1519 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | Y | LID 167587 2 fault operation B phase Overcurrent Branch on mains pole IV-90913 Pacific HWY and Floraville Rd. Flags 50TB Excluded OMS 1393351 | June | 2016 | 2016Q4 | 2016 | 220:8687 | 220:8687 | ZN00220/008687 | LAKE MACQUARIE | OH | Veg | 2016-06-05 | N | 145 | N | 9 | N | N | 1.1101 | 39.4971 | 160955.8576
[7 empty] | 11870 | 16707 | 1393400 | 2016-06-05 01:06 | 2016-06-05 03:20 | 134 | 11kV | 105165 | 1887 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | Zn965 Pennant Hills - Pnl.20 tripped on: C phase IOC Field EFIs: Pnl 20 through to S5429 UG cable fault between S5429 and S5388. Note: Panel 38 also tripped when attempting to restore supply via S5942. See 1396004 1396006 1396007 | June | 2016 | 2016Q4 | 2016 | ZN965:PA20 | ZN965:PA20 | ZN00965/000020 | HORNSBY | UG | Not Veg | 2016-06-05 | Y | 55.7313 | N | 9 | N | Y | 1.1101 | 39.4971 | 76851.4802
[7 empty] | 11466 | 12409 | 1393417 | 2016-06-05 01:54 | 2016-06-05 03:24 | 90 | 11kV | 127875 | 1463 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | @Sub 72 Five Dock Panel #10 labelled parramatta page tripped on Earth fault, EFI, 11kv trip, ZE and GE, field EFis Abnormal: S49715 open Sw/B, S2201 open sw/A, Sw B closed at S1527 Remarks: UG fault. UG fault section of 11kv feeder from S35570 Henry Richmond Sw/B to S3660 Bland Julia Sw/A | June | 2016 | 2016Q4 | 2016 | ZN72:PA10 | ZN35555:PA5 | ZN35555/000005 | INNER WEST | UG | Not Veg | 2016-06-05 | Y | 87.406 | N | 9 | N | Y | 1.1101 | 39.4971 | 93447.2783
[7 empty] | 10622 | 3563 | 1393422 | 2016-06-05 02:04 | 2016-06-05 03:48 | 104 | 11kV | 25168 | 242 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | Y | LID 167589 3 fault operations 3 phase Overcurrent tree branch on OHM adjacent sub 26967 | June | 2016 | 2016Q4 | 2016 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2016-06-05 | N | 104 | N | 9 | N | N | 1.1101 | 39.4971 | 18392.0321
[7 empty] | 10491 | 1889 | 1393427 | 2016-06-05 02:38 | 2016-06-05 04:34 | 116 | 11kV | 9744 | 84 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | Zn398 Dulwich Hill - Pnl.22 tripped on: Earth Fault Front line feeder fault from Panel 22 to S35901 and S48137 | June | 2016 | 2016Q4 | 2016 | ZN398:PA22 | ZN398:PA22 | ZN00398/000022 | INNER WEST | UG | Not Veg | 2016-06-05 | Y | 116 | N | 9 | N | Y | 1.1101 | 39.4971 | 7120.6278
[7 empty] | 10953 | 7117 | 1393316 | 2016-06-04 22:57 | 2016-06-05 06:10 | 433 | 11kV | 78847 | 1675 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | LID 167583 2 fault operations Eath Fault Prot = 50TN, Faut detector op at ELBS 61353 A&Cph O/C E/F tree on OHM NB-10217, mains off pin ins NB- 10253 Excluded OMS 1393316, 1393493 | June | 2016 | 2016Q4 | 2016 | 242:81541 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Veg | 2016-06-04 | N | 47.0728 | N | 8 | N | N | 1.1101 | 39.4971 | 57619.062
[7 empty] | 11436 | 12178 | 1393475 | 2016-06-05 05:48 | 2016-06-05 07:33 | 105 | 11kV | 42650 | 410 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | Zn262 Marrickville 11kv Panel 34 tripped on Relays: Earth Fault, Fault check, EFI Signals: 11kv trip, Group Earth, Zone Earth UG fault from S7168:B to S2789:A See 1395460,7 exclude 1393475 | June | 2016 | 2016Q4 | 2016 | ZN262:PA34 | ZN262:PA34 | ZN00262/000034 | INNER WEST | UG | Not Veg | 2016-06-05 | Y | 104.0244 | N | 9 | N | Y | 1.1101 | 39.4971 | 31167.362
[7 empty] | 11022 | 7782 | 1393379 | 2016-06-05 00:27 | 2016-06-05 07:45 | 438 | 11kV | 42098 | 100 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | Ex Zn12690 Berkeley Vale section of feeder Panel 7 "Wyong Mingara etc" fdr No visible signs of fault. However recloser continually triped with PT11912 in service. T/Con to assess. See 1397201,2 exclude 1393379 | June | 2016 | 2016Q4 | 2016 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Veg | 2016-06-05 | Y | 420.98 | N | 9 | N | Y | 1.1101 | 39.4971 | 30763.9767
[7 empty] | 10518 | 2248 | 1393408 | 2016-06-05 01:35 | 2016-06-05 08:04 | 389 | 11kV | 310033 | 797 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | REC35756 Bundeena tripped, reclosed and tripped on: Overcurrent, lockout Cause not ascertained | June | 2016 | 2016Q4 | 2016 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Veg | 2016-06-05 | Y | 389 | N | 9 | N | Y | 1.1101 | 39.4971 | 226562.972
[7 empty] | 11849 | 16530 | 1393721 | 2016-06-05 08:01 | 2016-06-05 08:53 | 52 | 11kV | 85528 | 1921 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12610 Long Jetty - Pnl.10 tripped, reclosed, tripped and lockout out on: A & B phase IOC, Reclose timer, Lockout Tree branch on Mains beyond LB61730 See 1395705 1395706 | June | 2016 | 2016Q4 | 2016 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Veg | 2016-06-05 | Y | 44.5226 | N | 9 | N | Y | 1.1101 | 39.4971 | 62501.3398
[7 empty] | 10389 | 319 | 1393480 | 2016-06-05 05:58 | 2016-06-05 09:06 | 188 | 11kV | 752 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC26228 Valley Rd - tripped and locked out on: OC and IOC trip Tree branch on OH adjacent to PT16261 Davison Park S | June | 2016 | 2016Q4 | 2016 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2016-06-05 | Y | 188 | N | 9 | N | Y | 1.1101 | 39.4971 | 549.5394
[7 empty] | 10503 | 1998 | 1393612 | 2016-06-05 07:30 | 2016-06-05 09:12 | 102 | 11kV | 107712 | 1056 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn4545 Meadowbank Panel 41 "Lovell holliss etc' fdr tripped on Signals: 11k trip Relays: Overcurrent ABC phase EFI: nil Palm Frong at 41 Denman st hit HV OH Mains | June | 2016 | 2016Q4 | 2016 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | OH | Veg | 2016-06-05 | Y | 102 | N | 9 | N | Y | 1.1101 | 39.4971 | 78712.7526
[7 empty] | 11651 | 14226 | 1393502 | 2016-06-05 07:03 | 2016-06-05 09:22 | 139 | 11kV | 17931 | 129 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn12600 Lisarow section of Pa2 "Holgate" fdr REclsoer 41020 Wattle Tree Rd North tripped and locked out Branch removed from mains near PT13773 The Ridgeway Tumbi 1.6 See 1395675 exclude 1393502 | June | 2016 | 2016Q4 | 2016 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2016-06-05 | Y | 139 | N | 9 | N | Y | 1.1101 | 39.4971 | 13103.4459
[7 empty] | 10682 | 4290 | 1393757 | 2016-06-05 08:23 | 2016-06-05 09:37 | 74 | 11kV | 71336 | 964 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | Ex Zn4545 Meadowbank section of Pa40 RE1437 Shftsbury Morvan tripped and reclosed and triped on Relays: OV trip, Lockout Branch brought down OH OV mains adjacent to PT1406 Morvan Moira. HV hiit LV mains. PT1406 to remain isolated until further notice. | June | 2016 | 2016Q4 | 2016 | ZN4545:PA40 | ZN4545:PA40 | ZN04545/000040 | RYDE | OH | Veg | 2016-06-05 | Y | 74 | N | 9 | N | Y | 1.1101 | 39.4971 | 52130.2447
[7 empty] | 10557 | 2731 | 1393745 | 2016-06-05 08:03 | 2016-06-05 10:40 | 157 | 11kV | 56909 | 389 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | REC50247 Blackett Faunce tripped and lockout on Large tree branch on mains near PT14612 See 1395825 1395827 | June | 2016 | 2016Q4 | 2016 | ZN12650:PA2 | ZN12650:PA2 | ZN12650/000002 | CENTRAL COAST | OH | Veg | 2016-06-05 | Y | 146.2956 | N | 9 | N | Y | 1.1101 | 39.4971 | 41587.4187
[7 empty] | 10788 | 5343 | 1393079 | 2016-06-04 18:03 | 2016-06-05 10:45 | 1002 | 11kV | 749816 | 1776 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn9700 Kirrawee - Pnl.20 tripped on: A & B phase timed O/C, IOC, Lockout, Timing OH mains down between S9764 and AB35151 See 1394982 1394983 1394988 1394995 1394998 1394992 1395003 | June | 2016 | 2016Q4 | 2016 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2016-06-04 | Y | 422.1937 | N | 8 | N | Y | 1.1101 | 39.4971 | 547943.417
[7 empty] | 10986 | 7469 | 1393636 | 2016-06-05 07:38 | 2016-06-05 11:45 | 247 | 11kV | 273742 | 1513 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Wind Storm | Y | At Zn1285 Greenacre Park 11kv feeder Panel 24 tripped on: Relays: A & B phase IOC, EFI, Lockout, Timing relay Signals: Group Earth, Zone Earth, 11kv trip Remarks: cause not ascertained. AB2803 requires replacing, phase to phase fault | June | 2016 | 2016Q4 | 2016 | ZN1285:PA24 | ZN37100:PA11 | ZN37100/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-06-05 | Y | 180.9266 | N | 9 | N | Y | 1.1101 | 39.4971 | 200042.5796
[7 empty] | 11755 | 15439 | 1393674 | 2016-06-05 07:55 | 2016-06-05 12:20 | 265 | 11kV | 309520 | 1168 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn35800 Bankstown 11kv fdr Panel 7 tripped, reclosed and tripped on Relays: B&C phase IOC Signals: 11kv trip EFI's: S2703 S2327 S49915 S3579 S7432 Big branches found on ground below OH mains near end of feeder | June | 2016 | 2016Q4 | 2016 | ZN35800:PA7 | ZN35800:PA7 | ZN35800/000007 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-06-05 | Y | 265 | N | 9 | N | Y | 1.1101 | 39.4971 | 226188.0867
[7 empty] | 12239 | 20319 | 1393640 | 2016-06-05 07:41 | 2016-06-05 12:35 | 294 | 11kV | 68985 | 270 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC20112 Kalang Rd - tripped and locked out on: OC Trip Tree branch found on mains between LB65798 and LB65780 and LB20518 tee PT15544 Ouside 247 Powder Works Rd. See 1395401 1395403 | June | 2016 | 2016Q4 | 2016 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2016-06-05 | Y | 255.5 | N | 9 | N | Y | 1.1101 | 39.4971 | 50412.2033
[7 empty] | 11152 | 9424 | 1393859 | 2016-06-05 08:43 | 2016-06-05 12:55 | 252 | 11kV | 209320 | 911 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn965 Pennant Hills - Pnl.26 tripped, reclosed and tripped on: C phase IOC, C phase OC, Timing lockout Field EFIs: S6153, S4988, S7942, S4494 (No Access to S1389) Tree brought down OH mains outside 16 Larool Cres Thornleigh See 1395979 1395985 1395982 1395984 | June | 2016 | 2016Q4 | 2016 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Veg | 2016-06-05 | Y | 229.7695 | N | 9 | N | Y | 1.1101 | 39.4971 | 152964.8821
[7 empty] | 11804 | 16024 | 1393378 | 2016-06-05 00:21 | 2016-06-05 13:00 | 759 | 11kV | 441879 | 2157 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12620 Noraville Panel 7 "Fravent St" fdr tripped and locked out on Relays: Overcurrent and Earth Fault, EFI Signals: 11kv trip EFI's: S14590 S14589 1 Span of 11kv down from UGOH to next pole outside 2 Pandora Pde Noraville. Isoalted from S14590:B to S14589:A tee PT11188 & PT12649 See 1398126,7,8,9,30 exclude 1393378,83,435,6 | June | 2016 | 2016Q4 | 2016 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | OH | Not Veg | 2016-06-05 | Y | 204.8581 | N | 9 | N | Y | 1.1101 | 39.4971 | 322912.14
[7 empty] | 10589 | 3108 | 1394054 | 2016-06-05 09:26 | 2016-06-05 13:50 | 264 | 11kV | 331233 | 1400 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn3472 Sefton 11kv Panel 28 "35463" tripped, reclosed and tripped on: Relays: A & B phase O/C, A & C phase IOC, E/F, timed A & C I, E/F, Timing and lockout Remarks: tree branch contact - other. Near LB2714 tree resting on mains. Mains cut away branch with Dop | June | 2016 | 2016Q4 | 2016 | ZN3472:PA28 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-06-05 | Y | 236.595 | N | 9 | N | Y | 1.1101 | 39.4971 | 242055.3067
[7 empty] | 11586 | 13556 | 1393744 | 2016-06-05 08:09 | 2016-06-05 13:51 | 342 | 11kV | 5472 | 16 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC44938 "Somersby" tripped Tree branch on mains outside 155 Kilkenny Rd, Somersby | June | 2016 | 2016Q4 | 2016 | ZN12630:PA25 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2016-06-05 | Y | 342 | N | 9 | N | Y | 1.1101 | 39.4971 | 3998.7762
[7 empty] | 11273 | 10627 | 1394975 | 2016-06-05 13:02 | 2016-06-05 14:00 | 58 | 11kV | 2262 | 39 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | Y | LID 167596 A Phase DOLF : 16 Amp Fatigued fuse excluded OMS 1394975 | June | 2016 | 2016Q4 | 2016 | 256:80632 | 256:80632 | ZN00256/080632 | NEWCASTLE | OH | Not Veg | 2016-06-05 | N | 58 | N | 9 | N | N | 1.1101 | 39.4971 | 1653.0029
[7 empty] | 11694 | 14756 | 1394834 | 2016-06-05 12:26 | 2016-06-05 14:12 | 106 | 11kV | 143311 | 1540 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | Zn188 Zetland - 11kV Pnl.44 - tripped on: A & C phase OC, Earth Fault, EFI Field EFIs: S8332, S50240, S2718, S2683, S8510, S47445, S3757, S61768, S6739 UG cable fault between S6739 Danks Young to S46893 George McEvoy See 1395476 1395480 | June | 2016 | 2016Q4 | 2016 | ZN188:PA44 | ZN188:PA44 | ZN00188/000044 | SYDNEY | UG | Not Veg | 2016-06-05 | N | 93.0591 | N | 9 | N | N | 1.1101 | 39.4971 | 104727.4518
[7 empty] | 12125 | 19180 | 1394618 | 2016-06-04 21:59 | 2016-06-05 15:00 | 1021 | 11kV | 346119 | 339 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | Y | Ex Zn847 Hornsby section of Pa18 "Carrington Pacific" AB2679 Defective bond open on one phase. Not closing al 3 phases. See 1395860 exclude 1393278,924 | June | 2016 | 2016Q4 | 2016 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Not Veg | 2016-06-04 | Y | 1021 | N | 8 | N | Y | 1.1101 | 39.4971 | 252933.5564
[7 empty] | 11066 | 8261 | 1393712 | 2016-06-05 08:00 | 2016-06-05 15:30 | 450 | 11kV | 19935 | 94 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC44937 Alan St tripped, reclosed and lockout out Tree branch brought down OH mains into LV in Fern Rd. See 1396119 1396122 | June | 2016 | 2016Q4 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2016-06-05 | Y | 212.0745 | N | 9 | N | Y | 1.1101 | 39.4971 | 14567.91
[7 empty] | 11822 | 16256 | 1395132 | 2016-06-05 13:54 | 2016-06-05 15:56 | 122 | 11kV | 229777 | 2116 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | Y | Zn15008 Harbord Panel 5 "Queenscliff" fdr tripped and locked out on Relays: SEF, IOC AC phase EFI Signals: 11kv trip EFI's: S16800 11kv B Phase burnt off pole #4456128 outside #1 HIghview Ave Section of 11kv fdr between S16197:B to S16950:A to LB23499 isoalted and Tag left at S16917 See 1398273,5 exclude 1385132 | June | 2016 | 2016Q4 | 2016 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | OH | Not Veg | 2016-06-05 | Y | 108.5903 | N | 9 | N | Y | 1.1101 | 39.4971 | 167914.2543
[7 empty] | 10965 | 7224 | 1393908 | 2016-06-05 08:42 | 2016-06-05 16:40 | 478 | 11kV | 312134 | 653 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Ex Zn2400 Berowra section of Pa21 Recloser 3228 Berowra Pump has tripped, reclosed and tripped again Relays: IOC trip, OC trip, Lockout Weather related | June | 2016 | 2016Q4 | 2016 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Veg | 2016-06-05 | Y | 478 | N | 9 | N | Y | 1.1101 | 39.4971 | 228098.3208
[7 empty] | 10552 | 2640 | 1395242 | 2016-06-05 14:31 | 2016-06-05 16:40 | 129 | 11kV | 645 | 5 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12630 Peats Ridge seciont of Pa23 "Mangrove Mountain" fdr PT11046 Wise Ferry Lillicrapps roadside HDO operated. Tree branch on OH Mains. Removed by DOp See 1395944 exclude 1395242 | June | 2016 | 2016Q4 | 2016 | ZN12630:PA23 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2016-06-05 | Y | 129 | N | 9 | N | Y | 1.1101 | 39.4971 | 471.347
[7 empty] | 11636 | 14075 | 1394425 | 2016-06-05 14:23 | 2016-06-05 18:21 | 238 | 11kV | 129234 | 543 | HV | Vegetation Blow/Fall In | Vegetation | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | Y | IR63157 Mooney Mowbray ex Chatswood Zn80 Pa32L tripped, reclosed, tripped again on: OC trip, Lockout Abnormal: S7075 Sw/A opem S7075 Sw/B closed REmarks: tree branch contact - other | June | 2016 | 2016Q4 | 2016 | ZN80:PA32 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Veg | 2016-06-05 | N | 238 | N | 9 | N | N | 1.1101 | 39.4971 | 94440.3954
[7 empty] | 11251 | 10416 | 1394194 | 2016-06-05 11:01 | 2016-06-05 18:22 | 441 | 11kV | 507591 | 1151 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn3154 St Ives - Pnl.5 tripped, reclosed, tripped and locked out on: A pahse timed O/C, lockout, timing Tree brnach on mains Adj AB2514 Note: S5902 Curagul Bobbin Head Dist 3 "Curagul Rd East" B phase fuse blown LV found in parallel Fuses have been installed | June | 2016 | 2016Q4 | 2016 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | OH | Veg | 2016-06-05 | N | 441 | N | 9 | N | N | 1.1101 | 39.4971 | 370932.5314
[7 empty] | 12188 | 19733 | 1393265 | 2016-06-05 18:17 | 2016-06-05 18:24 | 7 | 11kV | 5813 | 2429 | HV | Staff Operation | Utility Process Issue | Air Break Switch | Unplanned | Rain Wind Storm | Y | At Zn35800 Bankstown ZN: 11kv Panel 15L interrupted to safely open defective AB 75 Abnormal: AB802 Open. AB2481 was closed. Note: was isolated between AB802, AB148 (defective) & PT61219 Dumped Remarks: interrupted for safety reasons. AB75 was HR/Heating up/melting on middle phase, Panel 15L @ Bankstown Zone interrupted for safety | June | 2016 | 2016Q4 | 2016 | ZN35800:PA15 | ZN2310:PA23 | ZN02310/000023 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-06-05 | Y | 2.3932 | N | 9 | N | Y | 1.1101 | 39.4971 | 4247.9689
[7 empty] | 11473 | 12514 | 1394406 | 2016-06-05 10:28 | 2016-06-05 18:30 | 482 | 11kV | 293914 | 797 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC35756 Bundeena tripped, reclosed and tripped on: Overcurrent & lockout Large tree on HV betwen S47481, S9090 tee PT9061 See 1394406 1395857 | June | 2016 | 2016Q4 | 2016 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Veg | 2016-06-05 | Y | 368.7754 | N | 9 | N | Y | 1.1101 | 39.4971 | 214783.6822
[7 empty] | 11389 | 11789 | 1394110 | 2016-06-05 08:24 | 2016-06-05 18:45 | 621 | 11kV | 42852 | 95 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC20852 McCarrs Creek Rd tripped and reclosed on: OC Trip & IOC trip CP49122 tripped and lockout out on OC at the same time Tree branch on mains @ Cottage Point See 1397145 1397149 1397151 | June | 2016 | 2016Q4 | 2016 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2016-06-05 | Y | 451.0737 | N | 9 | N | Y | 1.1101 | 39.4971 | 31314.9777
[7 empty] | 11300 | 10964 | 1393458 | 2016-06-05 07:01 | 2016-06-05 19:15 | 734 | 11kV | 72051 | 425 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn12690 Berkeley Vale section of Panel 24L "Berkeley Rd" fdr Tree Brought down 11kv mains into contact with LV mains near PT11881 Glenning Anderson See 1398104,6,7,8 exclude 1393509,55 | June | 2016 | 2016Q4 | 2016 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2016-06-05 | Y | 169.5318 | N | 9 | N | Y | 1.1101 | 39.4971 | 52652.7457
[7 empty] | 10973 | 7306 | 1394497 | 2016-06-05 10:58 | 2016-06-05 20:00 | 542 | 11kV | 573029 | 1646 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Wind Storm | Y | At Zn2400 Berowra Panel No.22 'S4776 Glenview Pacific' feeder tripped and reclosed and tripped on Signals: 11kv trip Relays: O/C, Lockout EFI: nil Remarks: weather related. AB964 Open and defective. Weather related. Gull crossing not patrolled between LB134 and AB1337 | June | 2016 | 2016Q4 | 2016 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Not Veg | 2016-06-05 | Y | 348.1343 | N | 9 | N | Y | 1.1101 | 39.4971 | 418752.6917
[7 empty] | 11708 | 14931 | 1395598 | 2016-06-05 15:50 | 2016-06-05 21:15 | 325 | 11kV | 83593 | 1483 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn12650 West Gosford section of Pa1 "The Dog Trap Rd" fdr from CP44936 Bentley Rd Recloser tripped on overcurrent Tree/Branch brought down OH outside 33 Allan St Narara. See 1397416,8,9 exclude 1395604,888,9 | June | 2016 | 2016Q4 | 2016 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2016-06-05 | Y | 56.3675 | N | 9 | N | Y | 1.1101 | 39.4971 | 61087.2988
[7 empty] | 10875 | 6333 | 1393512 | 2016-06-05 06:39 | 2016-06-05 21:30 | 891 | 11kV | 16143 | 130 | HV | Equipment Failed in Service | Equipment Failure | U/G Link | Unplanned | Rain Heavy | Y | LID 167591 & 167599 4 fault operations Overcurrent; Earth Fault UG cable fault at Pole HR-10714. Sub 76778 is only 3 weeks old. Excluded OMS 1393512 & 1394241 | June | 2016 | 2016Q4 | 2016 | 511:29874 | 511:29874 | ZN00511/029874 | MAITLAND | UG | Not Veg | 2016-06-05 | Y | 124.1769 | N | 9 | N | Y | 1.1101 | 39.4971 | 11796.8283
[7 empty] | 11886 | 16861 | 1396120 | 2016-06-05 19:28 | 2016-06-05 21:40 | 132 | 11kV | 126034 | 1078 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | Zn965 Pennant Hills Panel 46 "Hull Verney" tripped on Relays: Earth Fault, EFI Signals: 11kv trip Zone and Group Earth UG Fault between S5848 Hull Verney & S35195 Cherrybrook New Farm tee PT704 Verney Chelsea See 1397874,5,6 exclude 1396120 | June | 2016 | 2016Q4 | 2016 | ZN965:PA46 | ZN965:PA46 | ZN00965/000046 | HORNSBY | UG | Not Veg | 2016-06-05 | Y | 116.9147 | N | 9 | N | Y | 1.1101 | 39.4971 | 92101.9298
[7 empty] | 11509 | 12770 | 1395789 | 2016-06-05 16:53 | 2016-06-05 23:23 | 390 | 11kV | 32324 | 114 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | Y | LID 167597 2 fault operations Earth Fault Car hit pole HV reported down | June | 2016 | 2016Q4 | 2016 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2016-06-05 | N | 283.5439 | N | 9 | N | N | 1.1101 | 39.4971 | 23621.4258
[7 empty] | 10905 | 6729 | 1396121 | 2016-06-05 19:30 | 2016-06-06 00:05 | 275 | 11kV | 104725 | 766 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | Y | LID 167598 2 fault operations A phase Earth Fault faulty xarm at pole KU-13044 repaired Excluded OMS 1396121 | June | 2016 | 2016Q4 | 2016 | 228:7491 | 228:85415 | ZN00228/085415 | NEWCASTLE | OH | Not Veg | 2016-06-05 | N | 136.7167 | N | 9 | N | N | 1.1101 | 39.4971 | 76529.9411
[7 empty] | 10821 | 5696 | 1394568 | 2016-06-05 09:33 | 2016-06-06 00:35 | 901.5667 | 11kV | 141545.9667 | 157 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Wind Storm | Y | Ex Zn2635 Epping Zone section of Pa38 S4566 York Chester 11kV A phase HDO operated Weather related | June | 2016 | 2016Q4 | 2016 | ZN2635:PA38 | ZN2635:PA38 | ZN02635/000038 | PARRAMATTA | OH | Not Veg | 2016-06-05 | Y | 901.5667 | N | 9 | N | Y | 1.1101 | 39.4971 | 103437.6175
[7 empty] | 11794 | 15898 | 1395919 | 2016-06-05 17:47 | 2016-06-06 00:41 | 414 | 11kV | 98118 | 237 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15013 Terry Hills - Pnl.6 tripped on: SEF Abnormal: LB25194 Closed with AB26217 Open and defective Tree branch no mains near PT16705 | June | 2016 | 2016Q4 | 2016 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2016-06-05 | Y | 414 | N | 9 | N | Y | 1.1101 | 39.4971 | 71701.7404
[7 empty] | 11967 | 17665 | 1396381 | 2016-06-05 23:22 | 2016-06-06 01:47 | 145 | 11kV | 173875 | 1475 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Wind Storm | Y | Ex Zn12570 Avoce section of Pa39 "North Avoca" fdr from Recloser 40425 Kurrawyba Cadell has tripped Relays: OC trip, IOC trip @0020 relays were EF, OC @PT13232 Footpath Phase HDO 63Amp fuse blown. Abnormal: Re40425 closed, Re44855 open & defective, Sw2721 closed @S12181, AB43138 open & defective Possum @ PT13232. Unable to ascertained cause of Earth Fault on 0020 restoration fail. See 1397464,5,6,7,70 exclude 1396381,2,6 | June | 2016 | 2016Q4 | 2016 | ZN12570:PA39 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2016-06-05 | Y | 117.8814 | N | 9 | N | Y | 1.1101 | 39.4971 | 127062.7216
[7 empty] | 11478 | 12575 | 1396406 | 2016-06-06 00:12 | 2016-06-06 02:21 | 129 | 11kV | 20124 | 156 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Rain Wind Storm | N | S1323 Domain Parking Station - 11kV CB tripped Sub flooded due to heavy rain. No load on S1323 being replaced by S49444 | June | 2016 | 2016Q4 | 2016 | ZN931:PA24 | ZN931:PA24 | ZN00931/000024 | SYDNEY | UG | Not Veg | 2016-06-06 | N | 129 | N | 11 | N | N | 1.1101 | 39.4971 | 14706.0256
[7 empty] | 12011 | 18166 | 1396329 | 2016-06-05 22:14 | 2016-06-06 02:58 | 284 | 11kV | 17061 | 125 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | Y | LID 167601 3 fault operations xarm at pole AL-10017 faulty Excluded oms # 1396329 | June | 2016 | 2016Q4 | 2016 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2016-06-05 | N | 136.488 | N | 9 | N | N | 1.1101 | 39.4971 | 12467.6756
[7 empty] | 10445 | 1181 | 1396412 | 2016-06-06 00:54 | 2016-06-06 03:33 | 159 | 11kV | 3607 | 41 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 167602 3 fault operations | June | 2016 | 2016Q4 | 2016 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2016-06-06 | N | 87.9756 | N | 11 | N | N | 1.1101 | 39.4971 | 2635.8892
[7 empty] | 11171 | 9619 | 1392920 | 2016-06-04 16:33 | 2016-06-06 03:40 | 2107 | 11kV | 750720 | 2922 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZN35800 Bankstown 11kv Panel No.15 tripped on: Relays - Instantaneous IOC A & B phase, B & C phase Earth fault, EFI, Lockout. Signals: 11kv trip Remarks: tree/branch on OH mains. Large tree on HV mains near PT61219 Acacia Chaseling | June | 2016 | 2016Q4 | 2016 | ZN35800:PA15 | ZN2310:PA23 | ZN02310/000023 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-06-04 | Y | 256.9199 | N | 8 | N | Y | 1.1101 | 39.4971 | 548604.0335
[7 empty] | 11139 | 9284 | 1396630 | 2016-06-06 08:07 | 2016-06-06 08:55 | 47.6 | 11kV | 4855.2 | 102 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | No Weather Impact | N | LID 167604 DOLF : 40 Amp | June | 2016 | 2016Q4 | 2016 | 532:83293 | 532:83293 | ZN00532/083293 | MAITLAND | UG | Not Veg | 2016-06-06 | N | 47.6 | N | 11 | N | N | 1.1101 | 39.4971 | 3548.037
[7 empty] | 11049 | 8026 | 1394131 | 2016-06-05 08:57 | 2016-06-06 09:03 | 1446 | 11kV | 600090 | 415 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | IR50015 Quarry Old Northern Tripped and Locked out on overcurrent Ex Zn35370 Galston Panel 2 "GGalston Aux No2" Abnormal: AB782 Open and Defective. LB62157 Closed Remarks: weather related. See related interruptions at 05/06/16 08:57 (ex Galston Pa2) and Galston 06/06/16 06:34 (burnt bond) | June | 2016 | 2016Q4 | 2016 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2016-06-05 | Y | 1446 | N | 9 | N | Y | 1.1101 | 39.4971 | 438528.0723
[7 empty] | 11835 | 16422 | 1398144 | 2016-06-05 08:57 | 2016-06-06 09:58 | 1501 | 11kV | 339226 | 226 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | IR50015 Quarry Old Northern Tripped and Locked out on overcurrent Ex Zn35370 Galston Panel 2 "CP2831 alston Hight School tee PT63541 Galston Recreation Reserve" Abnormal: AB782 Open and Defective. LB62157 Closed Remarks: weather related. See related interruptions at 05/06/16 08:57 (ex Galston Pa10) and Galston 06/06/16 06:34 (burnt bond) | June | 2016 | 2016Q4 | 2016 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2016-06-05 | Y | 1501 | N | 9 | N | Y | 1.1101 | 39.4971 | 247896.3553
[7 empty] | 11493 | 12681 | 1396654 | 2016-06-06 09:28 | 2016-06-06 12:00 | 152 | 11kV | 168957 | 1745 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Cable End Box | Unplanned | No Weather Impact | N | At Zn2196 Milperra Panel 25 "Turvey river feeder" tripped on ABC IOC 50T efi fault check, efis down to S8790 Remarks: end box fault. end box flooded S5371 T/Con required to check endboxes etc (jointers) of RMI L/W required to earth area to arrange | June | 2016 | 2016Q4 | 2016 | ZN2196:PA25 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-06-06 | N | 96.8235 | N | 11 | N | N | 1.1101 | 39.4971 | 123468.7922
[7 empty] | 10899 | 6574 | 1394571 | 2016-06-05 13:58 | 2016-06-06 13:00 | 1382 | 11kV | 373586 | 287 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Rain Wind Storm | Y | At ZN15006 Dee Why West 11kv feeder Panel No.16 "grow fisher etc" feeder switched away and interrupted section of 11kv feeder from ZN15006 PA16 to SWA @ S16715 Grover Fisher to SWB @ SWB @ S16623 Deviit Park Interrupting supply to S16762 MWS and DB and S17041 Mactier Walker flooded subs. Remarks: flooding. S16762 MWS and DB and S17041 Mactier Walker flooded interrupted 11kv to enable isolation to allow for follow up inspection and repairs | June | 2016 | 2016Q4 | 2016 | ZN15006:PA16 | ZN15006:PA16 | ZN15006/000016 | NORTHERN BEACHES | UG | Not Veg | 2016-06-05 | Y | 1301.6934 | N | 9 | N | Y | 1.1101 | 39.4971 | 273005.6299
[7 empty] | 11696 | 14771 | 1396276 | 2016-06-05 21:28 | 2016-06-06 13:20 | 952 | 11kV | 118458 | 672 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14144 Wamberal Panel 10L fdr tripped Signals: 11kv trip Relays: 50T ABC, EFI EFI's: Nil Cause: Tree down with 11kV across rd corner brush and Milina Rd. Lineworker required ASAP. Section of Dist 2 out of S18826. Isolated from LV link on Pole WL3997 as low voltage is also down See 1397931,2,3 exclude 1396276,431,278 | June | 2016 | 2016Q4 | 2016 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2016-06-05 | Y | 176.2768 | N | 9 | N | Y | 1.1101 | 39.4971 | 86565.6125
[7 empty] | 11688 | 14687 | 1396629 | 2016-06-06 08:06 | 2016-06-06 13:57 | 351 | 11kV | 1053 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 167612 A phase excluded OMS 1396629 | June | 2016 | 2016Q4 | 2016 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-06-06 | N | 351 | N | 11 | N | N | 1.1101 | 39.4971 | 769.5013
[7 empty] | 10533 | 2406 | 1397316 | 2016-06-06 13:55 | 2016-06-06 16:40 | 165 | 11kV | 1320 | 8 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Wind Storm | N | S5716 Conrail Park McPerson - 11kV HV A & B phase fuses blown (KEMXO 90Amp) Faulty Transformer No.2 | June | 2016 | 2016Q4 | 2016 | ZN340:PA19 | ZN340:PA32 | ZN00340/000032 | BAYSIDE | UG | Not Veg | 2016-06-06 | N | 165 | N | 11 | N | N | 1.1101 | 39.4971 | 964.6171
[7 empty] | 11454 | 12316 | 1396133 | 2016-06-05 19:36 | 2016-06-06 16:50 | 1274 | 11kV | 7125 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn14891 Wyong section of Pa20 "Warnervale West Railway" fdr REC47302 Hue Hue Sparks 0.1 has tripped Signals: 11kv trip Relays: EF Trip Tree Brought down 11kV between USL 41170 & PT14257 Hue Hue Mountain 0.5. Left Isolated only by DOp as no line crew available. Linecrew to attend AM See 1397899,900 exclude 1396133,355 | June | 2016 | 2016Q4 | 2016 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2016-06-05 | Y | 712.5 | N | 9 | N | Y | 1.1101 | 39.4971 | 5206.7398
[7 empty] | 11713 | 15043 | 1392713 | 2016-06-04 14:41 | 2016-06-06 17:29 | 3048 | 11kV | 3048 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Ex Zn3154 St Ives section of Pa12 IR62283 Bobbin Head Leura tripped on Relays Overcurrent Trip, Lockout Cause not ascertained. DOp Lasheras patrolled HV feeder from IR62283. All Ok. Private section of feeder was patrolled by National Parks Level 1A HV switcher John. Phone 0403 186 097. He gave OK to energise | June | 2016 | 2016Q4 | 2016 |  |  |  | KU-RING-GAI | OH | Veg | 2016-06-04 | Y | 3048 | Y | 8 | N | Y | 1.1101 | 39.4971 | 2227.3885
[7 empty] | 11839 | 16457 | 1393919 | 2016-06-05 08:32 | 2016-06-06 17:45 | 1993 | 11kV | 447825 | 240 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn3154 St Ives Panel 23 "Yarrabung Killeaton" fdr Recloser 527 Catherine Paul tripped, relcoed, tripped and locked out on OC and IOC Tree Branch removed outside No5 Cassandra ave St Ives See 1398180,4,5 exclude 1393919,4449 | June | 2016 | 2016Q4 | 2016 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Veg | 2016-06-05 | Y | 1865.9375 | Y | 9 | N | Y | 1.1101 | 39.4971 | 327257.3014
[7 empty] | 11812 | 16142 | 1397372 | 2016-06-06 14:39 | 2016-06-06 17:48 | 189 | 11kV | 74450 | 824 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Previous Storm | N | Zn9118 Cronulla - Pnl.3 tripped on: Earth fault with A phase timed O/C and lock out Field EFIs: S9876 and S9848 UG cable fault between Pnl.3 and S9250 and S9876 tee S9850 | June | 2016 | 2016Q4 | 2016 | ZN9118:PA3 | ZN9118:PA3 | ZN09118/000003 | SUTHERLAND | UG | Not Veg | 2016-06-06 | N | 90.3519 | N | 11 | N | N | 1.1101 | 39.4971 | 54405.8641
[7 empty] | 11446 | 12215 | 1397396 | 2016-06-06 15:03 | 2016-06-06 17:55 | 172 | 11kV | 337166 | 2013 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North Panel 3 "Jackson White" tripped and locked out Relays: EFI Fault check (51N) Signals: #1 Group Earth, 11kv trip EFI's: S17119 S16912 S5433 S7092 UGOH fault between 11kv fdr from Zn36300 Balgowlah North Pa3 to S17119 to LB61276 See 1399244,6 exclude 1393796,415,28 | June | 2016 | 2016Q4 | 2016 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | UG | Not Veg | 2016-06-06 | N | 167.4943 | N | 11 | N | N | 1.1101 | 39.4971 | 246390.9681
[7 empty] | 10737 | 4847 | 1397272 | 2016-06-06 13:25 | 2016-06-06 18:30 | 305 | 11kV | 610 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | PT18261 Kyola Williams 0.6 Dist 1 "Rural Property c phase fuse blown due to Weather related See 1397941 exclude 1397272 | June | 2016 | 2016Q4 | 2016 | ZN12630:PA21 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2016-06-06 | N | 305 | N | 11 | N | N | 1.1101 | 39.4971 | 445.77
[7 empty] | 11381 | 11745 | 1396164 | 2016-06-05 19:50 | 2016-06-06 19:00 | 1390 | 11kV | 60601 | 347 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12690 Berkeley Vale section of Pa24 "LB49474 etc" fdr RE44289 Berkeley Enterprise 0.5 tripped on OC and SEF trip Abnormal: LK42212 open LB42205 closed CP45117 Open LB44503 closed Tree brought down 11kV OH Mains between LB63855 & PT12516 Linecrew to attend ASAP See 1397917,9,20 exclude 1396164,433 | June | 2016 | 2016Q4 | 2016 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2016-06-05 | Y | 174.6427 | N | 9 | N | Y | 1.1101 | 39.4971 | 44285.4234
[7 empty] | 11787 | 15757 | 1393325 | 2016-06-04 23:37 | 2016-06-06 20:00 | 2663 | 11kV | 251491 | 1032 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn15008 Harbord section of Pa9 "Soldiers Av" Recloser 62774 Kentwell Pittwater trippe on overcurrent Abnormal: LB21857 open with AB22843 closed Tree on overhead mains vicinity PT15781 Alenby Park Parade See 1398156,60,1 exclude 1393325 | June | 2016 | 2016Q4 | 2016 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Veg | 2016-06-04 | Y | 243.6928 | N | 8 | N | Y | 1.1101 | 39.4971 | 183782.2051
[7 empty] | 10964 | 7221 | 1393797 | 2016-06-05 08:32 | 2016-06-06 21:28 | 2216 | 11kV | 908341 | 1343 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn2400 Berowra Panel 18 "Berowra Waters" Fdrs tripped on Signals: 11kv trip Relays: SEF, Fault check EFI: S4368 S62786 Weather related See 1399579,80,1,2,3,4,6 exclude 139797,6155 | June | 2016 | 2016Q4 | 2016 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2016-06-05 | Y | 676.3522 | N | 9 | N | Y | 1.1101 | 39.4971 | 663788.8113
[7 empty] | 10609 | 3339 | 1396015 | 2016-06-05 10:19 | 2016-06-07 00:30 | 2291 | 11kV | 267939.6667 | 117 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | PT1406 Morcan Moira - HV mains into LV Adj to PT Restored via LV network once I.I completed checks See 1394302 GIS: 1398205 | June | 2016 | 2016Q4 | 2016 | ZN4545:PA40 | ZN4545:PA40 | ZN04545/000040 | RYDE | OH | Not Veg | 2016-06-05 | Y | 2290.0826 | N | 9 | N | Y | 1.1101 | 39.4971 | 195802.4055
[7 empty] | 11622 | 13989 | 1394473 | 2016-06-05 11:11 | 2016-06-07 01:00 | 2269.4 | 11kV | 257442.3333 | 175 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S1937 Hubert St - 11kv B phase OC10M 40A Fuse was found blown Remarks: tree/branch brought down OH. Large tree down on dist 32, appears there was a protection malgrade as HV fuses have blown. Multiple sets of wires down on dist #2, & LV UGOH burnt up. Restored via fuses & LV// | June | 2016 | 2016Q4 | 2016 | ZN116:PA47 | ZN116:PA19 | ZN00116/000019 | INNER WEST | OH | Veg | 2016-06-05 | Y | 1471.099 | N | 9 | N | Y | 1.1101 | 39.4971 | 188131.2639
[7 empty] | 12054 | 18515 | 1394026 | 2016-06-06 13:28 | 2016-06-07 01:00 | 691.6167 | 11kV | 691.6167 | 1 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | HC STRAIGH THROUGH CROSSARM BROKEN LIGHTING ARRESTORS ON X-ARM. OTHER POLES REQUIRED CCT TO BE TIED IN. 3 CUSTOMERS WITHOUT SUPPLY - 62, 62a AND 62b. ASP REQUIRED. TREE ON MAINS Ap earths on EP75852 and EP75843 TC required CC1: 06-"Urgent - O.H Mains - No others" | June | 2016 | 2016Q4 | 2016 | ZN965:PA15 | ZN965:PA15 | ZN00965/000015 | HORNSBY | OH | Veg | 2016-06-06 | N | 691.6167 | N | 11 | N | N | 1.1101 | 39.4971 | 505.4131
[7 empty] | 10773 | 5206 | 1393707 | 2016-06-05 08:07 | 2016-06-07 12:32 | 3145 | 11kV | 745944 | 1815 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Wind Storm | Y | Zn15011 Beacon Hill Panel 2 "Allambie Rd 252" tripped on Signals: 11kv trip 33kV Zone Earth Relays: Earth Fault Abnomral: LB62775 closed, LB64922 open AB22843 closed LK21857 open & defective 11kV pole was found snapped on the corner of Coolalie Pl & Souther Cross Way. Electrically this is between AB22843 & LK21858 tee S16223 See 1398587,8,9,93 exclude 1393707,6106,8073 | June | 2016 | 2016Q4 | 2016 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Not Veg | 2016-06-05 | Y | 410.9884 | N | 9 | N | Y | 1.1101 | 39.4971 | 545113.8736
[7 empty] | 10920 | 6845 | 1394896 | 2016-06-05 12:42 | 2016-06-07 12:41 | 2879 | 11kV | 267747 | 93 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | Y | S9670 Merton Street - Reports of Low Volts due to defective transformer | June | 2016 | 2016Q4 | 2016 | ZN9700:PA12 | ZN9700:PA12 | ZN09700/000012 | SUTHERLAND | UG | Not Veg | 2016-06-05 | Y | 2879 | Y | 9 | N | Y | 1.1101 | 39.4971 | 195661.6104
[7 empty] | 12021 | 18238 | 1395116 | 2016-06-05 13:04 | 2016-06-07 13:30 | 2906 | 11kV | 178358 | 103 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Rain Wind Storm | Y | Ex Zn15002 Narrabeen section of Pa6 S16443 Warraba Powderworks & S16444 The Crescent Warraba have been interrupted on all three distributors due to flooding See 1396420,1 GIS 1396422 | June | 2016 | 2016Q4 | 2016 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | Unknown | Unknown | 2016-06-05 | Y | 1731.6311 | N | 9 | N | Y | 1.1101 | 39.4971 | 130338.7657
[7 empty] | 10791 | 5374 | 1398078 | 2016-06-07 12:27 | 2016-06-07 13:50 | 83 | 11kV | 249 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 167624 No protection operation cable fell of insulator and had to be isolated at 11kv links 43792 as it was burning through the cross arm at pole LI31174 and need immediate repairs. | June | 2016 | 2016Q4 | 2016 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2016-06-07 | N | 83 | N | 3 | N | N | 1.1101 | 39.4971 | 181.9619
[7 empty] | 12088 | 18804 | 1398036 | 2016-06-07 12:10 | 2016-06-07 17:00 | 290 | 11kV | 1370 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167632 A Phase DOLF : 20 Amp excluded OMS 1398036 | June | 2016 | 2016Q4 | 2016 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2016-06-07 | N | 195.7143 | N | 3 | N | N | 1.1101 | 39.4971 | 1001.1556
[7 empty] | 12043 | 18449 | 1396660 | 2016-06-05 13:28 | 2016-06-07 19:00 | 3211.7333 | 11kV | 584535.4667 | 182 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | Y | 11kv Bond off after Rec 48460 Wakehurst Wimbledon on tee to PT15857 and PT15139 Ex "collaroy" fdr panel No.4 at S15002 Narrabeen Remarks: bond. Bond off on corner of wimbledon and wakehurst | June | 2016 | 2016Q4 | 2016 | ZN15002:PA4 | ZN15002:PA4 | ZN15002/000004 | NORTHERN BEACHES | OH | Not Veg | 2016-06-05 | Y | 3211.7333 | N | 9 | N | Y | 1.1101 | 39.4971 | 427161.2782
[7 empty] | 11391 | 11800 | 1393373 | 2016-06-05 00:16 | 2016-06-08 00:08 | 4312 | 11kV | 873673 | 695 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn2400 Berowra Section of Pa11 RE3282 Relays IOC trip, OC trip, Lockout Tree Brought down 11kV OH on Pacific Hwy Cowan near PT641. 3 Bays down between AB204 & AB1093 See 1399543,6,7,8,9,50,2,3,4 exclude 1393373,7612,3 | June | 2016 | 2016Q4 | 2016 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2016-06-05 | Y | 1257.0835 | N | 9 | N | Y | 1.1101 | 39.4971 | 638454.4594
[7 empty] | 12087 | 18800 | 1398410 | 2016-06-07 23:43 | 2016-06-08 01:26 | 103 | 11kV | 21048 | 226 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167634 2 fault operations B & C phase Overcurrent nothing found Aph = 74A, Bph = 1157A, Cph = 1125A | June | 2016 | 2016Q4 | 2016 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2016-06-07 | N | 93.1327 | N | 3 | N | N | 1.1101 | 39.4971 | 15381.2576
[7 empty] | 11202 | 9938 | 1398451 | 2016-06-08 07:49 | 2016-06-08 10:05 | 135.8167 | 11kV | 6655.0167 | 49 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167637 A phase DOLF : 32 Amp | June | 2016 | 2016Q4 | 2016 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Veg | 2016-06-08 | N | 135.8167 | N | 4 | N | N | 1.1101 | 39.4971 | 4863.2899
[7 empty] | 12160 | 19495 | 1398439 | 2016-06-08 07:27 | 2016-06-08 11:15 | 227.8833 | 11kV | 29530.6667 | 282 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 167643 A phase tapping burnt off at ugoh pole OR-70074 repaired by LW. dq OMS 1398439 test by system operator which became entangled with this job | June | 2016 | 2016Q4 | 2016 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2016-06-08 | N | 104.7187 | N | 4 | N | N | 1.1101 | 39.4971 | 21580.1402
[7 empty] | 10688 | 4335 | 1393749 | 2016-06-05 08:23 | 2016-06-08 11:50 | 4527 | 11kV | 233073 | 123 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN15013 Terry Hills 11kv Panel 4 "S16440" feeder - CP21350 Booralie Kulgoa tripped on O/C Abnormal: AB26217 defective and open Remarks: tree/branch on OH mains. Tree on PT16215 has caused extensive damage and pole leaning 2 poles sth of Pt16215. Also 11kv wires down between AB26217 and LB25194 - sw tag @ AB26217 | June | 2016 | 2016Q4 | 2016 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2016-06-05 | Y | 1894.9024 | N | 9 | N | Y | 1.1101 | 39.4971 | 170322.8739
[7 empty] | 12015 | 18214 | 1398307 | 2016-06-08 12:50 | 2016-06-08 15:00 | 130 | 11kV | 6760 | 52 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | PT1809 Billyard Young - Interrupted for safety Lineworker removed branch from 11kV OH | June | 2016 | 2016Q4 | 2016 | ZN1673:PA19 | ZN1673:PA19 | ZN01673/000019 | KU-RING-GAI | OH | Veg | 2016-06-08 | N | 130 | N | 4 | N | N | 1.1101 | 39.4971 | 4940.0086
[7 empty] | 12153 | 19417 | 1398863 | 2016-06-08 17:45 | 2016-06-08 18:45 | 60 | 11kV | 2940 | 49 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 167648 A phase blown tapping near sub 53407 | June | 2016 | 2016Q4 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2016-06-08 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 2148.4653
[7 empty] | 10863 | 6240 | 1400275 | 2016-06-09 09:12 | 2016-06-09 09:39 | 27 | 11kV | 58617 | 2171 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167652 Magpie flew into mains at cnr of Ivy and Lyndhurst St Dudley. Dropped clear of mains. Fdr 11895 & 11899 were paralleled at Sw 24563 for NAR 13388. AR was off at the time. | June | 2016 | 2016Q4 | 2016 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Not Veg | 2016-06-09 | N | 27 | N | 4 | N | N | 1.1101 | 39.4971 | 42835.5747
[7 empty] | 11461 | 12382 | 1399087 | 2016-06-09 10:59 | 2016-06-09 11:34 | 35 | 11kV | 19810 | 566 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12580 Erina section of Pa16 RE46673 Terrgial Penrose tripped and reclosed on timed overcurrent Tree Branch on OH Mains. Branch removed by DOp See 1399087 exclude 1399090,2 | June | 2016 | 2016Q4 | 2016 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2016-06-09 | N | 35 | N | 4 | N | N | 1.1101 | 39.4971 | 14476.5637
[7 empty] | 11918 | 17105 | 1399120 | 2016-06-09 11:55 | 2016-06-09 12:00 | 5 | 11kV | 1095 | 219 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1193 Lindfield Section Panel 16 "S36136" from Sw/B @ S49259 has been interrupted to remove a tree branch Remarks: tree/branch on OH mains. Branch OS 37 Craner Ave Lindfield | June | 2016 | 2016Q4 | 2016 | ZN1193:PA16 | ZN1193:PA16 | ZN01193/000016 | KU-RING-GAI | OH | Veg | 2016-06-09 | N | 5 | N | 4 | N | N | 1.1101 | 39.4971 | 800.1937
[7 empty] | 10942 | 7040 | 1399266 | 2016-06-09 19:22 | 2016-06-09 22:55 | 213 | 11kV | 166774 | 1574 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn4545 Meadowbank Pa29fdr tripped on Relays: Signals: 11kv trip, Zone Earth, Tx2 Group Earth Possum committed Hari Kiri @ PT1194 North Woorang See 1399592,3,4,5 Exclude 1399298,303,4,29 | June | 2016 | 2016Q4 | 2016 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Not Veg | 2016-06-09 | N | 105.9555 | N | 4 | N | N | 1.1101 | 39.4971 | 121873.5202
[7 empty] | 12201 | 19862 | 1399563 | 2016-06-10 15:34 | 2016-06-10 17:10 | 96 | 11kV | 2304 | 24 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 167671 interrupt to repair HV tapping at pole AH-72298 CC1: 06-"Urgent - O.H Mains - No others" | June | 2016 | 2016Q4 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-06-10 | N | 96 | N | 2 | N | N | 1.1101 | 39.4971 | 1683.6952
[7 empty] | 11438 | 12182 | 1399734 | 2016-06-10 22:36 | 2016-06-11 00:15 | 99 | 11kV | 90358 | 1136 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN1788 Matraville 11kv OCB panel 8 "S-1170" feeder tripped on - Relays: Earth fault, EFI Field EFI's: S1170, 7934, 50054 Signals: 11kv trip, Zn E, No.5 Tx group earth Remarks: 11kv feeder fault between S50054 Raglan Victoria No.2 Sw/B to S35502 Raglan McGowan Sw/A tee to S1813 Victoria Nap | June | 2016 | 2016Q4 | 2016 | ZN1788:PA8 | ZN1788:PA61 | ZN01788/000061 | RANDWICK | UG | Not Veg | 2016-06-10 | N | 79.5405 | N | 2 | N | N | 1.1101 | 39.4971 | 66030.9613
[7 empty] | 11018 | 7731 | 1399745 | 2016-06-11 02:13 | 2016-06-11 10:40 | 507 | 11kV | 13352 | 203 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 167674 1 fault operation A phase Overcurrent car hit pole DP-20224 Fdr tripped and reclosed at 0134 Excluded oms 1399745,1399750 | June | 2016 | 2016Q4 | 2016 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2016-06-11 | N | 65.7734 | N | 2 | N | N | 1.1101 | 39.4971 | 9757.2478
[7 empty] | 11208 | 9997 | 1399901 | 2016-06-11 22:38 | 2016-06-12 00:40 | 122 | 11kV | 16348 | 134 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12690 Berkely Vale section of Pa12 "Craftsman Ave" 11kv centre Phase burnt bond between LK42304 & PT12046 See 1400404 exclude 1399901.4.7 | June | 2016 | 2016Q4 | 2016 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2016-06-11 | N | 122 | N | 2 | N | N | 1.1101 | 39.4971 | 11946.6362
[7 empty] | 11749 | 15371 | 1399989 | 2016-06-12 16:30 | 2016-06-12 20:53 | 263 | 11kV | 14075 | 213 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Panel 5 "Bateau Bay"fdr interrutped for safety Broken Crossarm. 11kv Hanging in danger of contacting LV as per EMSO See 1400410,1,2 Exclude 1399989,400011 | June | 2016 | 2016Q4 | 2016 | ZN12610:PA5 | ZN12610:PA5 | ZN12610/000005 | CENTRAL COAST | OH | Not Veg | 2016-06-12 | N | 66.0798 | N | 2 | N | N | 1.1101 | 39.4971 | 10285.5949
[7 empty] | 11553 | 13122 | 1400062 | 2016-06-12 23:52 | 2016-06-13 01:00 | 68 | 11kV | 45584 | 962 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Panel 6 "Krone Enterprises" tripped and reclose Sensitive Earth, Overcurrent, Lockout Burnt off bond road side on Pole BV758 outside 45 Chittaway Rd See 1400828,9 Exclude 1400062 | June | 2016 | 2016Q4 | 2016 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2016-06-12 | N | 47.3846 | N | 2 | N | N | 1.1101 | 39.4971 | 33311.4427
[7 empty] | 12058 | 18553 | 1400075 | 2016-06-13 05:41 | 2016-06-13 07:11 | 90 | 11kV | 11700 | 130 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167678 2 fault operations A phase Overcurrent fdr patrolled no cause found - sub 52785 DOLF FOUND BLOWN WHEN PATROLLING FDR OUTAGE | June | 2016 | 2016Q4 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-06-13 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 8550.0149
[7 empty] | 11119 | 8924 | 1400185 | 2016-06-13 16:45 | 2016-06-13 20:30 | 225 | 11kV | 8100 | 36 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 167681 B phase Broken live line clamp Excluded OMS 1400185 | June | 2016 | 2016Q4 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2016-06-13 | N | 225 | N | 3 | N | N | 1.1101 | 39.4971 | 5919.2411
[7 empty] | 11061 | 8195 | 1400242 | 2016-06-14 01:12 | 2016-06-14 02:46 | 94 | 11kV | 160802 | 1742 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | @Sub9118 Cronulla Zn panel #12 tripped and locked out on B phase timed EFI #2 Tx GE 11kv trip Abnormal: Sw B closed at S9684, rec 35260 open, S9876 Sw/B open Remarks: cause not ascertained. mains to patrol | June | 2016 | 2016Q4 | 2016 | ZN9118:PA12 | ZN9118:PA12 | ZN09118/000012 | SUTHERLAND | OH | Veg | 2016-06-14 | N | 92.3088 | N | 3 | N | N | 1.1101 | 39.4971 | 117509.3587
[7 empty] | 11212 | 10022 | 1400246 | 2016-06-14 05:33 | 2016-06-14 06:50 | 77 | 11kV | 693 | 9 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn384 Camperdown - Pnl.66 (11kV) tripped on: B Phase E/F, EFI UG cable fault from Pnl.66 to S35316 barff City to S46773 Parra Syd Uni | June | 2016 | 2016Q4 | 2016 | ZN384:PA66 | ZN384:PA66 | ZN00384/000066 | SYDNEY | UG | Not Veg | 2016-06-14 | N | 77 | N | 3 | N | N | 1.1101 | 39.4971 | 506.424
[7 empty] | 11913 | 17036 | 1400233 | 2016-06-13 22:43 | 2016-06-14 09:00 | 616.9667 | 11kV | 30231.3667 | 49 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 167682 A Phase DOLF : 31 Amp B phase 11kV mains down pole FS-31909. Repaired under AP. supply restored and found low volts, burnt off tapping at pole FS-31908.section isolated again. | June | 2016 | 2016Q4 | 2016 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Not Veg | 2016-06-13 | N | 616.9667 | N | 3 | N | N | 1.1101 | 39.4971 | 22092.1911
[7 empty] | 12207 | 19933 | 1400588 | 2016-06-14 16:48 | 2016-06-14 22:40 | 352 | 11kV | 1408 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167696 Replaced DOLF assembly. Excluded OMS 1400588 | June | 2016 | 2016Q4 | 2016 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2016-06-14 | N | 352 | N | 3 | N | N | 1.1101 | 39.4971 | 1028.9249
[7 empty] | 10767 | 5113 | 1400656 | 2016-06-15 07:22 | 2016-06-15 09:34 | 131.9667 | 11kV | 7654.0667 | 58 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167697 B & C phase DOLF : 20 Amp 16Amp fuses installed instead of 20A. Please go back and install 20A fuses. CC1: 22-"Refer to SOp" | June | 2016 | 2016Q4 | 2016 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2016-06-15 | N | 131.9667 | N | 4 | N | N | 1.1101 | 39.4971 | 5593.3662
[7 empty] | 11984 | 17905 | 1400792 | 2016-06-15 13:26 | 2016-06-15 13:34 | 8 | 11kV | 5106 | 828 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn14143 Somersby Zone Panel 14 fdr CB tripped on Relays: SEF Signals: 11kv trip Staff Error. AOp reset protection on incorrect job See 1400987,97 2nd 1400792 | June | 2016 | 2016Q4 | 2016 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | Unknown | Not Veg | 2016-06-15 | N | 6.1667 | N | 4 | N | N | 1.1101 | 39.4971 | 3731.3142
[7 empty] | 11229 | 10163 | 1400900 | 2016-06-15 19:46 | 2016-06-15 20:55 | 69 | 11kV | 23811 | 416 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3922 Drummoyne Panel 30 fdr tripped Relays: Earth Fault, EFI, Fault CHeck Relay Signals: 11kv trip, No2 Group Earth, Zone Earth EFI's: Nil 11kV Underground fault from S2857 to S3717 See 1401002,3 exclude 1400900 | June | 2016 | 2016Q4 | 2016 | ZN3922:PA30 | ZN3922:PA27 | ZN03922/000027 | CANADA BAY | UG | Not Veg | 2016-06-15 | N | 57.238 | N | 4 | N | N | 1.1101 | 39.4971 | 17400.3765
[7 empty] | 10691 | 4378 | 1400886 | 2016-06-15 19:22 | 2016-06-15 21:33 | 131 | 11kV | 67787 | 803 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | On Panel 33 Pennant Hills (Supplying most of panel 10 Galston) IR2691 Duneba Drive Tripped on O/C and SEF. Report of Low Volts Beyond AB2839 on Panel 33 Pennant Hills Abnormal Switching: AB2270 Open and Recloser CP2691 Closed. Cause: Roadside bond burnt off at AB2839. Also Recloser 2691 Tripped on SEF and Overcurrent. tree branch on OH near LB1478 See OMS 1402454 1402458 1400886/890 | June | 2016 | 2016Q4 | 2016 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2016-06-15 | N | 84.4172 | N | 4 | N | N | 1.1101 | 39.4971 | 49536.7402
[7 empty] | 10431 | 1000 | 1396453 | 2016-06-06 04:36 | 2016-06-16 13:25 | 14929 | 11kV | 20161 | 40 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 167600 wire down beyond 11kV Links 40583 Excluded oms # 1396453 | June | 2016 | 2016Q4 | 2016 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2016-06-06 | N | 504.025 | N | 11 | N | N | 1.1101 | 39.4971 | 14733.0642
[7 empty] | 11548 | 13093 | 1401180 | 2016-06-17 04:46 | 2016-06-17 05:53 | 67 | 11kV | 102963 | 1687 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | At Zn262 Marrickville 11kv Pnl 17 "Marrickville Aux #2" tripped on earth fault with fault check. Signals: 11kv trip and efi Field efi's: Pnl17 to S169 Remarks: UG fault. cable fault between S169 Wardell George to S2842 Wardell Frazer to S1795 Yule St | June | 2016 | 2016Q4 | 2016 | ZN262:PA17 | ZN262:PA17 | ZN00262/000017 | INNER WEST | UG | Not Veg | 2016-06-17 | N | 61.0332 | N | 3 | N | N | 1.1101 | 39.4971 | 75242.3235
[7 empty] | 10575 | 2925 | 1401189 | 2016-06-17 07:38 | 2016-06-17 10:25 | 167 | 11kV | 1002 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 167743 C Phase DOLF : 16 Amp Fuse Fatigue excluded OMS 1401198 | June | 2016 | 2016Q4 | 2016 | 509:33397 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2016-06-17 | N | 167 | N | 3 | N | N | 1.1101 | 39.4971 | 732.232
[7 empty] | 11741 | 15256 | 1401220 | 2016-06-17 09:26 | 2016-06-17 11:40 | 134 | 11kV | 134 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167744 DOLF : 10 Amp Excluded OMS 1401220 | June | 2016 | 2016Q4 | 2016 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2016-06-17 | N | 134 | N | 3 | N | N | 1.1101 | 39.4971 | 97.9232
[7 empty] | 11015 | 7710 | 1401565 | 2016-06-19 07:51 | 2016-06-19 07:57 | 6 | 11kV | 840 | 140 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn7481 Darling Harbour - Pnl.19 tripped on: Earth Fault & EFI Field EFIs: S6421, S3044, S3092 Staff error - DOp mistakenly closed earth switch on Sw/A at S3092 Darling Harbour Markets | June | 2016 | 2016Q4 | 2016 | ZN7481:PA19 | ZN7481:PA19 | ZN07481/000019 | SYDNEY | Unknown | Not Veg | 2016-06-19 | N | 6 | N | 3 | N | N | 1.1101 | 39.4971 | 613.8472
[7 empty] | 11757 | 15455 | 1401627 | 2016-06-19 14:41 | 2016-06-19 15:55 | 74 | 11kV | 74 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167756 A phase DOLF : 10 Amp Excluded OMS 1401627 | June | 2016 | 2016Q4 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-06-19 | N | 74 | N | 3 | N | N | 1.1101 | 39.4971 | 54.077
[7 empty] | 11411 | 11949 | 1401654 | 2016-06-19 17:16 | 2016-06-19 23:20 | 364 | 11kV | 9271 | 64 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 167759 2 fault operations Overcurrent Tree into OHM at pole ER-33113 Excluded OMS 1401654 | June | 2016 | 2016Q4 | 2016 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2016-06-19 | N | 144.8594 | N | 3 | N | N | 1.1101 | 39.4971 | 6774.9734
[7 empty] | 10696 | 4400 | 1402179 | 2016-06-20 09:34 | 2016-06-20 13:50 | 256 | 11kV | 1536 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167767 A & B phase DOLF : 20 Amp Tree on mains. Wires down near PT 27153. Excluded OMS 1401824 | June | 2016 | 2016Q4 | 2016 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2016-06-20 | N | 256 | N | 9 | N | N | 1.1101 | 39.4971 | 1122.4635
[7 empty] | 10674 | 4132 | 1402201 | 2016-06-20 18:51 | 2016-06-20 18:58 | 7 | 11kV | 1708 | 244 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 167770 Feeder de-energised for safety | June | 2016 | 2016Q4 | 2016 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2016-06-20 | N | 7 | N | 9 | N | N | 1.1101 | 39.4971 | 1248.156
[7 empty] | 11670 | 14485 | 1402067 | 2016-06-20 18:47 | 2016-06-20 19:42 | 55 | 11kV | 16826 | 314 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167771 1 fault operation 3 phase Overcurrent Tree on mains near PT 2623 Scott St. 4 Scott St Seaham. Excluded OMS 1402067.1402073,1402071. | June | 2016 | 2016Q4 | 2016 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2016-06-20 | N | 53.586 | N | 9 | N | N | 1.1101 | 39.4971 | 12295.9445
[7 empty] | 10428 | 878 | 1402024 | 2016-06-20 16:33 | 2016-06-20 21:10 | 277.2 | 11kV | 2494.8 | 9 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167776 A & C phase LLC lead burned off from main to DOLF 2 phases. Excluded OMS 1402051 | June | 2016 | 2016Q4 | 2016 | 238:34140 | 532:83298 | ZN00532/083298 | MAITLAND | OH | Not Veg | 2016-06-20 | N | 277.2 | N | 9 | N | N | 1.1101 | 39.4971 | 1823.1263
[7 empty] | 11359 | 11568 | 1402102 | 2016-06-20 20:36 | 2016-06-20 23:43 | 187 | 11kV | 28974 | 282 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167775 Tree down on 11kV near sub 61982 Excluded oms 1402103 | June | 2016 | 2016Q4 | 2016 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2016-06-20 | N | 102.7447 | N | 9 | N | N | 1.1101 | 39.4971 | 21173.3446
[7 empty] | 11362 | 11580 | 1402077 | 2016-06-20 18:59 | 2016-06-21 04:30 | 571 | 11kV | 9223 | 425 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of Pa24 "Berkeley Rd" IR44289 Berkeley Enterprise 0.3 interrupted for safety Car hit Pole. Pole snapped and Lineworker on site requested feeder to be interrupted for safety See 1402694 2nd 1402691,2,3 exclude 1402077 | June | 2016 | 2016Q4 | 2016 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2016-06-20 | N | 21.7012 | N | 9 | N | N | 1.1101 | 39.4971 | 6739.8964
[7 empty] | 12028 | 18299 | 1402406 | 2016-06-20 22:36 | 2016-06-21 10:30 | 713.5667 | 11kV | 19979.8667 | 28 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167789 1 fault operation Sectionaliser | June | 2016 | 2016Q4 | 2016 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2016-06-20 | N | 713.5667 | N | 9 | N | N | 1.1101 | 39.4971 | 14600.6973
[7 empty] | 11619 | 13952 | 1402210 | 2016-06-21 08:31 | 2016-06-21 13:14 | 283.5167 | 11kV | 1134.0667 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167790 No protection operation. A phase dropper out of DOLF. Isolated for repair | June | 2016 | 2016Q4 | 2016 | 216:10727 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Not Veg | 2016-06-21 | N | 283.5167 | N | 7 | N | N | 1.1101 | 39.4971 | 828.7425
[7 empty] | 10632 | 3675 | 1402132 | 2016-06-20 22:31 | 2016-06-21 13:45 | 914 | 11kV | 97877 | 2012 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167778 Trip & Reclose 1 fault operation Earth Fault Tree branch at pole IU-20944 fell onto LV OHM at sub 10799. See outage 167779 - OMS 1402716 | June | 2016 | 2016Q4 | 2016 | 216:10727 | 216:10727 | ZN00216/010727 | LAKE MACQUARIE | OH | Veg | 2016-06-20 | N | 48.6466 | N | 9 | N | N | 1.1101 | 39.4971 | 71525.6247
[7 empty] | 11363 | 11594 | 1402390 | 2016-06-21 14:11 | 2016-06-21 16:49 | 158 | 11kV | 304538 | 3192 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167796 2 fault operation Overcurrent; Earth Fault Tree onto mains at sub 1817. Relay failed at Sw 34141 tripping Tx2 & bus section 2 at Thornton. Fdr mgmt relay B phase OC. A phase 2.9k amps, B 2.8k amps, C 66.25 amps. Back up, O/C E/F ABC trip Excluded OMS 1402393, 1402469, 1402397, 1402393, 1402501 ,1402499 | June | 2016 | 2016Q4 | 2016 | 238:34143 | 238:34143 | ZN00238/034143 | MAITLAND | OH | Veg | 2016-06-21 | N | 95.4066 | N | 7 | N | N | 1.1101 | 39.4971 | 222547.388
[7 empty] | 11257 | 10460 | 1402095 | 2016-06-20 20:36 | 2016-06-21 17:15 | 1239 | 11kV | 215827 | 461 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID167802 2 fault operations A & C phase Overcurrent Tree in mains pole JP-82411 | June | 2016 | 2016Q4 | 2016 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2016-06-20 | N | 468.1714 | N | 9 | N | N | 1.1101 | 39.4971 | 157720.0058
[7 empty] | 10766 | 5108 | 1402704 | 2016-06-21 16:30 | 2016-06-21 17:15 | 45 | 11kV | 225 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167798 A phase HV LEAD TO TOP OF DOLF BROKEN. Excluded OMS REPORT NO 1402091. | June | 2016 | 2016Q4 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2016-06-21 | N | 45 | N | 7 | N | N | 1.1101 | 39.4971 | 164.4234
[7 empty] | 10686 | 4327 | 1402370 | 2016-06-21 13:38 | 2016-06-21 17:38 | 240 | 11kV | 15167 | 145 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167799 3 fault operation A & B phase Overcurrent TREE ON MAINS AT POLE HR-40011 FARLEY. Excluded OMS REPORT NO 1402370. tree on 33kV and 11kV mains also see OMS 1402639 | June | 2016 | 2016Q4 | 2016 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2016-06-21 | N | 104.6 | N | 7 | N | N | 1.1101 | 39.4971 | 11083.5962
[7 empty] | 12113 | 19042 | 1402312 | 2016-06-21 11:56 | 2016-06-21 20:10 | 493.8333 | 11kV | 17778 | 36 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167804 Mains down poles FR-92057 & FR-92041 Section isolated for repairs | June | 2016 | 2016Q4 | 2016 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2016-06-21 | N | 493.8333 | N | 7 | N | N | 1.1101 | 39.4971 | 12991.638
[7 empty] | 10832 | 5829 | 1402402 | 2016-06-21 11:04 | 2016-06-21 22:25 | 681 | 11kV | 9581 | 61 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn14891 Wyong Ex Panel 5 recloser CP45083 Durren tripped and reclosed on Relays: IOC and OC Signals: Nil 11kV Auto Link opened by Staff due tomains on the ground Cause: After trip and reclose on RE45083 Durren Line Workers patrolled feeder to find wires doen beyond CP44788. See OMS 1403097 1403098 1402402 | June | 2016 | 2016Q4 | 2016 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2016-06-21 | N | 157.0656 | N | 7 | N | N | 1.1101 | 39.4971 | 7001.5122
[7 empty] | 10884 | 6442 | 1402562 | 2016-06-21 19:59 | 2016-06-22 02:30 | 391 | 11kV | 152886 | 1506 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 167803 UGOH tapping blown at pole JV-40609 Excluded OMS 1402562 | June | 2016 | 2016Q4 | 2016 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2016-06-21 | N | 101.5179 | N | 7 | N | N | 1.1101 | 39.4971 | 111724.5794
[7 empty] | 10506 | 2046 | 1402594 | 2016-06-22 07:08 | 2016-06-22 09:00 | 112 | 11kV | 11200 | 100 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 167806 BURNT OFF LINE SIDE TAPPING ON A PHASE AT ABS 74547.BACK FED FROM ABS 75153. Replaced PG connector at ABS 74547 | June | 2016 | 2016Q4 | 2016 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-06-22 | N | 112 | N | 5 | N | N | 1.1101 | 39.4971 | 8184.6297
[7 empty] | 11110 | 8810 | 1402616 | 2016-06-22 08:08 | 2016-06-22 11:40 | 212 | 11kV | 46004 | 217 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT10828 Melvin Edgbaston - Roadside 40A HDO operated Fuse Fatigue | June | 2016 | 2016Q4 | 2016 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | OH | Not Veg | 2016-06-22 | N | 212 | N | 5 | N | N | 1.1101 | 39.4971 | 33618.3663
[7 empty] | 11962 | 17641 | 1402797 | 2016-06-22 14:49 | 2016-06-22 16:44 | 115 | 11kV | 45286 | 420 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2466 Flemington Panel 12 and Panel 21 tripped on Relays: Panel 12L E/F, FC and EFI Relays: Panel 21 E/F, F/C and EFIO Signals: 11kV Trip, ZE and TX4 Group Earth At S3620 Tooheys Lidcombe 11kV CB tripped on UV At S986 Egg Board - 11kV SW/B tripped on Short Translay UG feeder fault from S4137 Frances Grace to S4025 Frances Edith is locked with SW/Tag. See OMS 1403086 1403088 1402797 1402838 1043089 NOTE: Final Step time taken from DNMS. Blue outage form did not have a feasible time | June | 2016 | 2016Q4 | 2016 | ZN2466:PA12 | ZN2466:PA12 | ZN02466/000012 | CUMBERLAND | UG | Not Veg | 2016-06-22 | N | 107.8238 | N | 5 | N | N | 1.1101 | 39.4971 | 33093.6731
[7 empty] | 12127 | 19192 | 1402917 | 2016-06-22 10:07 | 2016-06-22 16:47 | 400 | 11kV | 800 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167809 Single phase BROKEN HV LEAD TO DOLF 54539. excluded OMS 1402674. | June | 2016 | 2016Q4 | 2016 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2016-06-22 | N | 400 | N | 5 | N | N | 1.1101 | 39.4971 | 584.6164
[7 empty] | 11593 | 13640 | 1402925 | 2016-06-22 14:38 | 2016-06-22 17:45 | 187 | 11kV | 374 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167814 3 phase 11kV dropper broken away from top of DOLF Excluded OMS 1402789 | June | 2016 | 2016Q4 | 2016 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2016-06-22 | N | 187 | N | 5 | N | N | 1.1101 | 39.4971 | 273.3082
[7 empty] | 11785 | 15741 | 1404065 | 2016-06-23 12:30 | 2016-06-23 14:00 | 90 | 11kV | 90 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 167825 A phase DOLF : 10 Amp Excluded OMS 1403018 | June | 2016 | 2016Q4 | 2016 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2016-06-23 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 11721 | 15129 | 1403103 | 2016-06-23 16:40 | 2016-06-23 18:10 | 90 | 11kV | 32042 | 993 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 167828 B phase Bph tapping broken off load side of ABS 41431 Excluded OMS 1403103 & 5 | June | 2016 | 2016Q4 | 2016 | 532:83314 | 532:83314 | ZN00532/083314 | MAITLAND | OH | Not Veg | 2016-06-23 | N | 32.2679 | N | 3 | N | N | 1.1101 | 39.4971 | 23415.3485
[7 empty] | 10427 | 858 | 1403199 | 2016-06-24 08:54 | 2016-06-24 11:00 | 126 | 11kV | 35431 | 286 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.25 tripped on: B Phase O/C, EFI and Fault Check Field EFIs: S3457 & S6702 UG cable fault between S6702 (Sw/B) and S1639 (Sw/A) tee S123 (Sw/A) See 1404022 1404023 1404024 | June | 2016 | 2016Q4 | 2016 | ZN188:PA25 | ZN188:PA13 | ZN00188/000013 | SYDNEY | UG | Not Veg | 2016-06-24 | N | 123.8846 | N | 11 | N | N | 1.1101 | 39.4971 | 25891.9298
[7 empty] | 11471 | 12509 | 1403902 | 2016-06-24 13:19 | 2016-06-24 13:55 | 36 | 11kV | 2736 | 76 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 167840 Isolated for safety Insulator broken pole GV-90321, Freemans Dr. | June | 2016 | 2016Q4 | 2016 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Not Veg | 2016-06-24 | N | 36 | N | 11 | N | N | 1.1101 | 39.4971 | 1999.3881
[7 empty] | 11289 | 10827 | 1403283 | 2016-06-24 12:47 | 2016-06-24 14:20 | 93 | 11kV | 111966 | 1239 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35370 Galston Panel 4 tripped reclosed tripped and locked out on C phase IOC Signals: 11kV Trip Abnormal Swicthing: LB64 Open aned Defective, LB 62159 Closed. Cause Not ascertained for outage 1404165 1404167 1404168 1403281 1403279 1403283 | June | 2016 | 2016Q4 | 2016 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2016-06-24 | N | 90.368 | N | 11 | N | N | 1.1101 | 39.4971 | 81821.4504
[7 empty] | 11444 | 12213 | 1402928 | 2016-06-23 08:39 | 2016-06-24 16:30 | 1911 | 11kV | 157653 | 672 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser 1772 Seymours Creek opened on Overcurrent Section of Panel 11 Cause: Large Tree brought down 3 Phases of 11kV OH. OH mains to replace poles See OMS 1404348 1404350 1402928 1402981 | June | 2016 | 2016Q4 | 2016 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2016-06-23 | N | 234.6027 | N | 3 | N | N | 1.1101 | 39.4971 | 115208.1624
[7 empty] | 10559 | 2733 | 1403386 | 2016-06-24 16:31 | 2016-06-24 19:05 | 154 | 11kV | 1078 | 7 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 167850 B & C Phase DOLF : 20 Amp tree on mains pole 8M-50069 | June | 2016 | 2016Q4 | 2016 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-06-24 | N | 154 | N | 11 | N | N | 1.1101 | 39.4971 | 787.7706
[7 empty] | 10945 | 7072 | 1403393 | 2016-06-24 16:53 | 2016-06-24 20:10 | 197.0833 | 11kV | 6700.8333 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 167852 Single phase DOLF : 16 Amp | June | 2016 | 2016Q4 | 2016 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2016-06-24 | N | 197.0833 | N | 11 | N | N | 1.1101 | 39.4971 | 4896.7714
[7 empty] | 10984 | 7458 | 1403379 | 2016-06-24 16:18 | 2016-06-24 21:20 | 302 | 11kV | 13976 | 88 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167848 2 fault operations Earth Fault TREE BROUGHT DOWN MAINS AT POLE EI30074 | June | 2016 | 2016Q4 | 2016 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2016-06-24 | N | 158.8182 | N | 11 | N | N | 1.1101 | 39.4971 | 10213.2486
[7 empty] | 11151 | 9407 | 1403412 | 2016-06-24 17:03 | 2016-06-24 22:53 | 350 | 11kV | 14632 | 56 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 167846 Overcurrent Tree on mains Cook Dve Swan Bay Excluded OMS 1403412 | June | 2016 | 2016Q4 | 2016 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2016-06-24 | N | 261.2857 | N | 11 | N | N | 1.1101 | 39.4971 | 10692.634
[7 empty] | 11460 | 12381 | 1403473 | 2016-06-25 01:44 | 2016-06-25 03:54 | 130 | 11kV | 127846 | 1074 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Panel 21 fdr tripped on Relays: EF, EFI Signals: 11kv trip, Tx2 Group Earth 11kV UG Cable fault from S14461 Keswick Bensley to Zn141810 Alisa Holly See 1404436,7 exclude 1403473 | June | 2016 | 2016Q4 | 2016 | ZN14892:PA21 | ZN14892:PA21 | ZN14892/000021 | CENTRAL COAST | UG | Not Veg | 2016-06-25 | N | 119.0372 | N | 5 | N | N | 1.1101 | 39.4971 | 93426.086
[7 empty] | 10489 | 1854 | 1403468 | 2016-06-24 23:08 | 2016-06-25 07:45 | 517 | 11kV | 1551 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 167855 C phase Tapping burnt off to DOLF Excluded OMS 1403468 | June | 2016 | 2016Q4 | 2016 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2016-06-24 | N | 517 | N | 11 | N | N | 1.1101 | 39.4971 | 1133.4251
[7 empty] | 10379 | 191 | 1403367 | 2016-06-24 15:56 | 2016-06-25 10:30 | 1114 | 11kV | 232423 | 493 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 167853 & 167857 1 fault operation Sensitive Earth Fault Broken crossarm near sub 54407 Excluded OMS 1403367 | June | 2016 | 2016Q4 | 2016 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2016-06-24 | N | 471.4462 | N | 11 | N | N | 1.1101 | 39.4971 | 169847.8731
[7 empty] | 10769 | 5137 | 1403418 | 2016-06-24 17:27 | 2016-06-25 11:18 | 1070.5333 | 11kV | 13916.9333 | 13 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167854 4 operations Earth Fault HV reported down between poles DI-80035 & DI-70034 | June | 2016 | 2016Q4 | 2016 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2016-06-24 | N | 1070.5333 | N | 11 | N | N | 1.1101 | 39.4971 | 10170.0844
[7 empty] | 11662 | 14379 | 1403524 | 2016-06-25 10:46 | 2016-06-25 12:45 | 119 | 11kV | 9996 | 84 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | Ex Zn9252 Jannali section of Pa27 11kv centre phase HV dropout fuse blown, but is damaged and could not be removed Footpath phase fuse carrier is blown and support is cracked, burnt and needs to be replaced. Restored via LV// USL250 USL1050 & USL1051 See 1404505 exclude 1403524 | June | 2016 | 2016Q4 | 2016 | ZN9252:PA27 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | OH | Not Veg | 2016-06-25 | N | 119 | N | 5 | N | N | 1.1101 | 39.4971 | 7304.782
[7 empty] | 11901 | 16952 | 1403383 | 2016-06-24 16:24 | 2016-06-25 18:10 | 1546 | 11kV | 3092 | 2 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 167851 OHM stolen between JT-17004 & Jt-17002. To be repaired Sat 25/6/16. Excluded OMS 1403383 | June | 2016 | 2016Q4 | 2016 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2016-06-24 | N | 1546 | N | 11 | N | N | 1.1101 | 39.4971 | 2259.5424
[7 empty] | 11961 | 17639 | 1403627 | 2016-06-25 18:38 | 2016-06-25 21:59 | 201 | 11kV | 370351 | 3303 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S80 Chatswood Panel 22 tripped on Relays: Overcurrent, Earth fault and fault check Signals: 11kV trip Abnromal Switching: SW/B S46610 Currawong Eloora Closed, SW/A at S5233 Mars Woodcock Open, SW/B at S2944 Burns Gentle Closed, SW/A at S47769 Open Cause: Cable fault between S35000 to S3911 to S2504 to S46610 to S3027 to S3026 See OMS 1405457 1405460 1405461 14054631403627 1403648 1403629 1403628 | June | 2016 | 2016Q4 | 2016 | ZN80:PA22 | ZN80:PA22 | ZN00080/000022 | LANE COVE | UG | Not Veg | 2016-06-25 | N | 112.1256 | N | 5 | N | N | 1.1101 | 39.4971 | 270641.5873
[7 empty] | 11646 | 14174 | 1403666 | 2016-06-25 21:21 | 2016-06-25 22:40 | 79 | 11kV | 9717 | 123 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167862 A phase DOLF : 40 Amp Excluded oms 1403666/7/9/72 | June | 2016 | 2016Q4 | 2016 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2016-06-25 | N | 79 | N | 5 | N | N | 1.1101 | 39.4971 | 7100.897
[7 empty] | 11104 | 8766 | 1403670 | 2016-06-25 22:03 | 2016-06-25 23:38 | 95 | 11kV | 80275 | 845 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Middle Phase 11kv Bond off @ AB36 Ex panel 5 'S8696 Marigold Amour No.4" from S2196 Milperra Remarks: bond @ 36 | June | 2016 | 2016Q4 | 2016 | ZN2196:PA5 | ZN2196:PA3 | ZN02196/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-06-25 | N | 95 | N | 5 | N | N | 1.1101 | 39.4971 | 58662.6023
[7 empty] | 11700 | 14820 | 1403747 | 2016-06-26 13:07 | 2016-06-26 15:10 | 123 | 11kV | 984 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167871 B Phase DOLF : 10 Amp Excluded OMS 1403747 | June | 2016 | 2016Q4 | 2016 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2016-06-26 | N | 123 | N | 4 | N | N | 1.1101 | 39.4971 | 719.0782
[7 empty] | 10921 | 6847 | 1403769 | 2016-06-26 15:03 | 2016-06-26 16:36 | 93 | 11kV | 126666 | 1362 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale sectin of Panel 10 "Chittaway" 11kv Bond found off @ USL40030 (roadside phase) Abnormal: Closed LB63384 Open LB41187 Cause: 11kv Bond burnt off @ USL 40030 (roadside phase) See 1404451 GIS 1403790 exclude 1403769,70 | June | 2016 | 2016Q4 | 2016 | ZN12690:PA10 | ZN12690:PA10 | ZN12690/000010 | CENTRAL COAST | OH | Not Veg | 2016-06-26 | N | 93 | N | 4 | N | N | 1.1101 | 39.4971 | 92563.7768
[7 empty] | 10517 | 2241 | 1403801 | 2016-06-26 16:20 | 2016-06-26 19:00 | 160 | 11kV | 1920 | 12 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | Wind Strong | N | LID 167872 main hanging low, tree broke x arm p DI-80035 excluded oms 1403746 | June | 2016 | 2016Q4 | 2016 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2016-06-26 | N | 160 | N | 4 | N | N | 1.1101 | 39.4971 | 1403.0794
[7 empty] | 10745 | 4946 | 1403754 | 2016-06-26 14:10 | 2016-06-26 22:04 | 474 | 11kV | 775551 | 3809 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At S1285 Greenacre Park, Panel 27 "Sub 4861, Sub 6424, Sub 7025" feeder locked out on B phase E/F, with timing and lockout relays, also EFI. EFIs down at all subs on 27L. Signals: 11kv trip, #4 tx group earth, and zone earth Abnormal: section of 11kv O/O/S between sub 3220 to LB 3270 (2A3) with AB1875 (2C9) ckised, Also defective ABs 75 & 148 open (Banks 3EF) with AB73 closed (2C7) Remarks: vehicle hit pole. cnr wattle st and waterloo rd punchbowl | June | 2016 | 2016Q4 | 2016 | ZN1285:PA24 | ZN37100:PA11 | ZN37100/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-06-26 | N | 203.6101 | N | 4 | N | N | 1.1101 | 39.4971 | 566749.7959
[7 empty] | 11130 | 9102 | 1404232 | 2016-06-27 18:09 | 2016-06-27 19:25 | 76 | 11kV | 95876 | 1305 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14891 Wyong Panel 1 "Minnesota" tripped, reclosed & tripped Relays: 51N, Earth Fault, Lockout out, timing, fault check, Tx1 Fault check, EFI Signals: Tx1 Group Earth, CB1 open, CB1 Closed, CB1 Open, CB1 A/R Lockout CP49433 Aux supply fail, CP41441 Aux Supply Fail EFI's: Nil Frontline UG Feeder fault Between Panel 1 to S18527:A See 1404385,6 exclude 1404232 | June | 2016 | 2016Q4 | 2016 | ZN14891:PA1 | ZN14891:PA1 | ZN14891/000001 | CENTRAL COAST | UG | Not Veg | 2016-06-27 | N | 73.4682 | N | 1 | N | N | 1.1101 | 39.4971 | 70063.3529
[7 empty] | 11094 | 8672 | 1404318 | 2016-06-28 07:36 | 2016-06-28 11:31 | 235 | 11kV | 219441 | 2482 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Cold <10C | N | Zn36300 Balgowlah 11kv Panel 9 "Orchard Bently" fdr tripped to lock out 2 times Relays: timed OC & EF, SEL trip, EFI, Lockout, Timing Tx No-1 Panel 1:11kv fault check Signals: 11kv trip EFI's:S47615 S17143 S17107 S17130 S17131 S46416 S16717 ABNORMAL: Defective Pa3 to S17119 tee LB61276, S17132:B closed, S17119:A opened, S16453:A closed 11kv roadside bond failure to UGOH located between LK22338 to PT15573 & S17132 outside 15 Bareena DR Balgowlah Heights See 1405105,6,7 exclude 1404318,25 | June | 2016 | 2016Q4 | 2016 | ZN36300:PA9 | ZN36300:PA9 | ZN36300/000009 | NORTHERN BEACHES | OH | Not Veg | 2016-06-28 | N | 88.413 | N | 3 | N | N | 1.1101 | 39.4971 | 160361.0104
[7 empty] | 12142 | 19281 | 1404553 | 2016-06-28 15:35 | 2016-06-28 17:41 | 126 | 11kV | 72292 | 1128 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn3155 Double Bay - Pnl.17 tripped on: Fault Check, EFI, IOC Field EFIs: S35410, S517, S6230 End box failure - S6230 Victoria Rose bay (Sw/B) end box failed explosively. See 1404952 1404953 | June | 2016 | 2016Q4 | 2016 | ZN3155:PA17 | ZN3155:PA17 | ZN03155/000017 | WOOLLAHRA | UG | Not Veg | 2016-06-28 | N | 64.0887 | N | 3 | N | N | 1.1101 | 39.4971 | 52828.8613
[7 empty] | 11170 | 9600 | 1404604 | 2016-06-28 18:08 | 2016-06-28 20:30 | 142 | 11kV | 195493 | 1929 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn15004 Newport Panel 9 "Avalon" fdr tripped on Relays: OC EF relay Bassler, trip LED Minor alarm LED. 50T ABC IOC, fram leakage fault check flag. EFI's: S16880 S16526 S17157 Signals: 11kv trio UGOH failed adj PT15467 Hillside rd 22. Section of fdr from AB21783 to S16868:A to S16681:A tee PT15467 See 1405121,4,5 exclude 1404604,15,24,42 | June | 2016 | 2016Q4 | 2016 | ZN15004:PA9 | ZN15004:PA9 | ZN15004/000009 | NORTHERN BEACHES | Unknown | Unknown | 2016-06-28 | N | 101.3442 | N | 3 | N | N | 1.1101 | 39.4971 | 142860.5183
[7 empty] | 12092 | 18858 | 1404660 | 2016-06-29 04:02 | 2016-06-29 05:30 | 88 | 11kV | 123632 | 1539 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn931 Darlinghurst - Pnl.9 tripped on: B phase O/C, IOC, EFI Field EFIs: S35007 & S35008 UG cable fault between S35008 East Sydney Tech No.3 (Sw/B) and S8249 Early Victoria (Sw/A) | June | 2016 | 2016Q4 | 2016 | ZN931:PA9 | ZN931:PA9 | ZN00931/000009 | SYDNEY | UG | Not Veg | 2016-06-29 | N | 80.3327 | N | 5 | N | N | 1.1101 | 39.4971 | 90346.6191
[7 empty] | 11892 | 16893 | 1404670 | 2016-06-29 05:23 | 2016-06-29 09:20 | 237 | 11kV | 11139 | 47 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167907 A phase DOLF : 20 Amp Possum on TX bushing. Note it has burnt through shroud. Please investigate/replace as required. Excluded OMS 1404670 | June | 2016 | 2016Q4 | 2016 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2016-06-29 | N | 237 | N | 5 | N | N | 1.1101 | 39.4971 | 8140.0527
[7 empty] | 10619 | 3552 | 1404760 | 2016-06-29 10:40 | 2016-06-29 12:54 | 134 | 11kV | 134 | 1 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 167913 Vegetation on 11kv mains Excluded OMS 1404760 | June | 2016 | 2016Q4 | 2016 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2016-06-29 | N | 134 | N | 5 | N | N | 1.1101 | 39.4971 | 97.9232
[7 empty] | 10915 | 6801 | 1404818 | 2016-06-29 12:00 | 2016-06-29 14:00 | 120 | 11kV | 960 | 8 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167915 C Phase DOLF : 10 Amp Animals or Birds excluded OMS 1404818 | June | 2016 | 2016Q4 | 2016 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2016-06-29 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 701.5397
[7 empty] | 11689 | 14694 | 1404905 | 2016-06-29 19:10 | 2016-06-29 20:55 | 105 | 11kV | 1050 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167916 B phase DOLF : 16 Amp VOLTS=A -242 B -239 C -242 Excluded OMS REPORT NO 1404905. | June | 2016 | 2016Q4 | 2016 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2016-06-29 | N | 105 | N | 5 | N | N | 1.1101 | 39.4971 | 767.309
[7 empty] | 11514 | 12803 | 1405058 | 2016-06-30 11:08 | 2016-06-30 12:38 | 90 | 11kV | 50976 | 613 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC1622 Eastern Arterial - tripped, reclosed and locked out on: O/C B & C phase, IOC Cause not ascertained. See 1405386 1405387 | June | 2016 | 2016Q4 | 2016 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Veg | 2016-06-30 | N | 83.1582 | N | 3 | N | N | 1.1101 | 39.4971 | 37251.7573
[7 empty] | 10910 | 6767 | 1405163 | 2016-06-30 15:50 | 2016-06-30 16:35 | 45 | 11kV | 135 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 167933 A & B phases - DOLF : 10 Amp Fuse Fatigue Excluded OMS 1405163 | June | 2016 | 2016Q4 | 2016 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2016-06-30 | N | 45 | N | 3 | N | N | 1.1101 | 39.4971 | 98.654
[7 empty] | 10548 | 2573 | 1405239 | 2016-06-30 21:44 | 2016-06-30 22:20 | 36.25 | 11kV | 1595 | 44 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167934 A Phase DOLF : 16 Amp | June | 2016 | 2016Q4 | 2016 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2016-06-30 | N | 36.25 | N | 3 | N | N | 1.1101 | 39.4971 | 1165.579
[7 empty] | 10192 | 18433 | 1405469 | 2016-07-01 14:45 | 2016-07-01 16:15 | 90 | 11kV | 137430 | 1527 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | UGOH | Unplanned | No Weather Impact | N | At ZN10991 Blakehurst ZN Panel 1 tripped reclosed and locked out on ef, rclose lockout, reclose time delay, efi Efi's at S10137, S10860 Remarks: UGOH fault short circuit. UGOH in tee off to S10851 mt vernon centre (found in lv//) CC1: 22-"Refer to SOp" | July | 2016 | 2017Q1 | 2017 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2016-07-01 | N | 90 | N | 2 | N | N | 1.1101 | 39.4971 | 100429.7905
[7 empty] | 10294 | 19517 | 1405368 | 2016-07-01 11:40 | 2016-07-01 20:10 | 510 | 11kV | 237795 | 1261 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | At Zn9118 Cronulla the 11kv panel 12 "Searl Holland" tripped on: Signals: 132kv zone earth, 132kv Tx 2 Group earth, 11kv Relays: C phase timed o/c and e/fault Field EFI's: Nil Remarks: the 11kv rmi at S9135 Searl Holland has failed explosivel | July | 2016 | 2017Q1 | 2017 | ZN9118:PA12 | ZN9118:PA12 | ZN09118/000012 | SUTHERLAND | UG | Not Veg | 2016-07-01 | N | 188.5765 | N | 2 | N | N | 1.1101 | 39.4971 | 173773.5722
[7 empty] | 9250 | 6992 | 1405632 | 2016-07-02 16:16 | 2016-07-02 21:10 | 294 | 11kV | 126073 | 1176 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 167946 2 Fault operations A phase Overcurrent 11kV feeder down on the road from pole HS-73436 and HS-72458. Excludeed OMS 1405632/ 1405635 | July | 2016 | 2017Q1 | 2017 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2016-07-02 | N | 107.2049 | N | 1 | N | N | 1.1101 | 39.4971 | 92130.4299
[7 empty] | 9242 | 6934 | 1405676 | 2016-07-03 02:00 | 2016-07-03 10:35 | 515 | 11kV | 81445 | 159 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 167947 2 fault operations Earth Fault pole 9G-50146 broken and on the ground. Excluded OMS 1405676 | July | 2016 | 2017Q1 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-07-03 | N | 512.2327 | N | 3 | N | N | 1.1101 | 39.4971 | 59517.6038
[7 empty] | 10095 | 17202 | 1405769 | 2016-07-03 19:48 | 2016-07-03 20:30 | 42 | 11kV | 13944 | 332 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT2080 Meadow Cres - Foot path phase HDO (ABB 50K ) operated HV fuse fatigue. S5721 Dist #1 - multiple no supply calls suspect LV //'s in place. See 1405896 1405895 | July | 2016 | 2017Q1 | 2017 | ZN4545:PA28 | ZN4545:PA28 | ZN04545/000028 | RYDE | OH | Not Veg | 2016-07-03 | N | 42 | N | 3 | N | N | 1.1101 | 39.4971 | 10189.8639
[7 empty] | 9140 | 5886 | 1405978 | 2016-07-04 14:30 | 2016-07-04 14:36 | 6 | 11kV | 264 | 44 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Panel 1 CP44853 Ourimbah Bumble opened for safety 11kv OH resting on Crossarm adjacent PT14120 Ourimbah Ck Bumble 0.5 | July | 2016 | 2017Q1 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2016-07-04 | N | 6 | N | 2 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 9211 | 6637 | 1405783 | 2016-07-03 22:40 | 2016-07-04 14:49 | 969 | 11kV | 19380 | 20 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 167982 section isolated to replace pole JS-60028 see report # 167952 & 167953 | July | 2016 | 2017Q1 | 2017 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2016-07-03 | N | 969 | N | 3 | N | N | 1.1101 | 39.4971 | 14162.3324
[7 empty] | 9751 | 13103 | 1406118 | 2016-07-04 20:46 | 2016-07-04 22:17 | 91 | 11kV | 64801 | 842 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 167962 fdr interupted by Sop Quail due to 11kV link 64217Y Wyee Reg roadside phase burning up. (note 3G device outage prevented remote operation on Wyee IR) excluded oms##1406118 | July | 2016 | 2017Q1 | 2017 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2016-07-04 | N | 76.9608 | N | 2 | N | N | 1.1101 | 39.4971 | 47354.6595
[7 empty] | 10063 | 16695 | 1406141 | 2016-07-05 01:02 | 2016-07-05 02:24 | 82 | 11kV | 89954 | 1097 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn12620 Noraville Panel 10 "Buff Point" fdr tripped on Relays: B&C timmed overcurrent Signals: 11kv trip Cause: Tree/Branch on OH Mains See 1406141,3 | July | 2016 | 2017Q1 | 2017 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Veg | 2016-07-05 | N | 82 | N | 5 | N | N | 1.1101 | 39.4971 | 65735.73
[7 empty] | 9210 | 6601 | 1406145 | 2016-07-05 02:47 | 2016-07-05 06:52 | 245 | 11kV | 21738 | 156 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | LID 167965 2 fault operations 3 phase Overcurrent; Earth Fault truck hit pole White truck, Rego BR19GC. Excluded oms 1406145 | July | 2016 | 2017Q1 | 2017 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2016-07-05 | N | 139.3462 | N | 5 | N | N | 1.1101 | 39.4971 | 15885.4892
[7 empty] | 8818 | 1682 | 1406181 | 2016-07-05 08:32 | 2016-07-05 15:05 | 393 | 11kV | 20341 | 157 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 167969 no protection operation section isolated after vehicle accident | July | 2016 | 2017Q1 | 2017 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2016-07-05 | N | 129.5605 | N | 5 | N | N | 1.1101 | 39.4971 | 14864.6028
[7 empty] | 10353 | 20278 | 1406155 | 2016-07-05 06:30 | 2016-07-05 20:35 | 845 | 11kV | 59572 | 322 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 167967 1 fault operation Tx was damaged at sub 21848. Excluded oms # 1406155 | July | 2016 | 2017Q1 | 2017 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2016-07-05 | N | 185.0062 | N | 5 | N | N | 1.1101 | 39.4971 | 43533.4605
[7 empty] | 8990 | 3879 | 1406492 | 2016-07-05 21:59 | 2016-07-05 23:03 | 64 | 11kV | 90911 | 1519 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 167981 1 fault operation 3 phase Sensitive Earth Fault Excluded OMS 1406492 | July | 2016 | 2017Q1 | 2017 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2016-07-05 | N | 59.8492 | N | 5 | N | N | 1.1101 | 39.4971 | 66435.0774
[7 empty] | 9341 | 7946 | 1406501 | 2016-07-06 05:07 | 2016-07-06 07:05 | 118 | 11kV | 143861 | 1338 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 43 tripped on Earth Fault with EFI Cause: UG cable fault Abnromal Switching CP2839 Open and CP2664 Closed See OMS 1406901 1406902 1406903 1406501 1406502 1406503 | July | 2016 | 2017Q1 | 2017 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | UG | Not Veg | 2016-07-06 | N | 107.5194 | N | 7 | N | N | 1.1101 | 39.4971 | 105129.3756
[7 empty] | 8940 | 3173 | 1406594 | 2016-07-06 10:19 | 2016-07-06 10:38 | 19 | 11kV | 12292 | 673 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S3425 castle Cove panel 39 tripped on Earth leakage Cause: UG cable fault See OMS 1406928 1406929 1406594 | July | 2016 | 2017Q1 | 2017 | ZN3425:PA39 | ZN3425:PA39 | ZN03425/000039 | WILLOUGHBY | UG | Not Veg | 2016-07-06 | N | 18.2645 | N | 7 | N | N | 1.1101 | 39.4971 | 8982.631
[7 empty] | 9963 | 15440 | 1406648 | 2016-07-06 11:52 | 2016-07-06 12:33 | 41 | 11kV | 16187 | 1027 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | LID 167996 Bird into UGOH at pole AH-20820, trip & reclose on Sw 89063. Burnt off tapping on B phase, interrupted downstream customers to de-energise. sw 89063 prot 51 AB 51N Excluded OMS 1406652, 1406651, 1406648. | July | 2016 | 2017Q1 | 2017 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Not Veg | 2016-07-06 | N | 15.7614 | N | 7 | N | N | 1.1101 | 39.4971 | 11828.9822
[7 empty] | 8851 | 2055 | 1406702 | 2016-07-06 12:10 | 2016-07-06 15:04 | 174 | 11kV | 60419 | 741 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 167998 No protection operated, taps burnt off at UGOH pole SW-80995. | July | 2016 | 2017Q1 | 2017 | 223:14398 | 223:14398 | ZN00223/014398 | LAKE MACQUARIE | OH | Not Veg | 2016-07-06 | N | 81.5371 | N | 7 | N | N | 1.1101 | 39.4971 | 44152.4231
[7 empty] | 9552 | 10689 | 1406769 | 2016-07-06 15:10 | 2016-07-06 17:10 | 120 | 11kV | 12767 | 125 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn630 Mascot Panel 40 tripped on Signals: 11kV trip, Zone Earth, TX6 group Earth Relays: B phase IOC and EFI Abnormal Switching: S2821 Burrows SW/B closed, S7006 Canal Princes SW/A open, S66098 to Panel 33 Closed and in a ring for switching At S2568 St.Peters Panel 33 Tripped on B phase Overcurrent with fault check Cause: Underground cable fault bwtween ZN630 Pa40 and S5377. Feeder tripped when closed to Pa33 St Peters See OMS 1407071 1407099 1406769 1406768 1406808 | July | 2016 | 2017Q1 | 2017 | ZN630:PA40 | ZN630:PA40 | ZN00630/000040 | SYDNEY | UG | Not Veg | 2016-07-06 | N | 102.136 | N | 7 | N | N | 1.1101 | 39.4971 | 9329.747
[7 empty] | 9532 | 10396 | 1406875 | 2016-07-07 01:21 | 2016-07-07 03:21 | 120 | 11kV | 63300 | 546 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At S711 Blackwattle Bay the 5kV Panel 22 tripped on Earth Fault and EFI Signals: 5kV trip, TX3 Group Earth and Zone Earth 5kV UG cable fault between S6509 and S753 See OMS 1407120 1407121 1406875 | July | 2016 | 2017Q1 | 2017 | ZN711:PA22 | ZN7481:PA12 | ZN07481/000012 | SYDNEY | UG | Not Veg | 2016-07-07 | N | 115.9341 | N | 4 | N | N | 1.1101 | 39.4971 | 46257.773
[7 empty] | 9677 | 12135 | 1406871 | 2016-07-06 23:28 | 2016-07-07 04:25 | 297 | 11kV | 220801 | 1761 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Air Break Switch | Unplanned | Rain Heavy | N | Zn12570 AVoca Zone Panel 24 "Kincumber" tripped and reclsoed on Overcurrent A & B phase Timing Relay Lockout 11kv trip LB42015 not closed properly flashed over See 1407336,7 exclude 1406873,8 | July | 2016 | 2017Q1 | 2017 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2016-07-06 | N | 125.3839 | N | 7 | N | N | 1.1101 | 39.4971 | 161354.8583
[7 empty] | 10258 | 19070 | 1407038 | 2016-07-06 21:56 | 2016-07-07 12:00 | 844 | 11kV | 844 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168003 No protection operation 11kV main broken at sub 94159, Isolated for repairs on Thursday 7/7/16. Excluded OMS 1406861 | July | 2016 | 2017Q1 | 2017 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2016-07-06 | N | 844 | N | 7 | N | N | 1.1101 | 39.4971 | 616.7703
[7 empty] | 9240 | 6932 | 1407108 | 2016-07-07 14:22 | 2016-07-07 17:00 | 158 | 11kV | 315283 | 2493 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn2635 Epping Panel 58 tripped Relays: B phase timed, Earth fault, lockout and efi Signals: 11kV Trip 11kV feeder fault from S5145 Kent Fernhill to S5822 Dawson Elgatta tee PT58 Possum also found on centre phase at pole EP76887. See OMS 1407869 1407871 1407872 1406909 1407108 1407137 | July | 2016 | 2017Q1 | 2017 | ZN2635:PA58 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | UG | Not Veg | 2016-07-07 | N | 126.4673 | N | 4 | N | N | 1.1101 | 39.4971 | 230399.5171
[7 empty] | 9385 | 8619 | 1407168 | 2016-07-07 20:29 | 2016-07-08 01:30 | 301 | 11kV | 268886 | 1640 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Zn15015 Nth Head "Manly Hospital No1" fdr locked out on timed overcurrent and EFI with 11k vtrip and LED alarm. Signals: 11kv trip and Zone Earth EFI down at S16721 only. 11kv fdr down outside 35 Marshall St See 1407356,60,1 exclude 1407168,78 | July | 2016 | 2017Q1 | 2017 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | OH | Veg | 2016-07-07 | N | 163.9549 | N | 4 | N | N | 1.1101 | 39.4971 | 196493.958
[7 empty] | 8825 | 1739 | 1407045 | 2016-07-07 13:30 | 2016-07-08 09:45 | 1215 | 11kV | 1215 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 168020 A Phase DOLF : 10 Amp Excluded OMS 1407045 | July | 2016 | 2017Q1 | 2017 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2016-07-07 | N | 1215 | N | 4 | N | N | 1.1101 | 39.4971 | 887.8862
[7 empty] | 9179 | 6284 | 1407198 | 2016-07-08 06:49 | 2016-07-08 14:15 | 446 | 11kV | 68067 | 558 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | N | Ex 11kv panel No.18 "Forresters Beach" feeder from Zn12610 Long Jetty. Recloser 50249 Kipling Shakespeare tripped, reclose and locked out Remarks: OH down. Broken 11kv crossarm adjacent LB43226 | July | 2016 | 2017Q1 | 2017 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2016-07-08 | N | 121.9839 | N | 7 | N | N | 1.1101 | 39.4971 | 49741.356
[7 empty] | 9420 | 9073 | 1407350 | 2016-07-08 15:04 | 2016-07-08 17:18 | 134 | 11kV | 112499 | 1256 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S12650 West Gosford Zn P3 the south gosford fdr tripped reclosed and locked out on b/c phase ioc, efi, rclose timing relay, reclose l/o relay EFI's at S18075, S14168, S18198, S14823, S14503 Remarks: UG fault. S14503 Henry Parry Donnison to S18561 Donnison Henry Parry | July | 2016 | 2017Q1 | 2017 | ZN12650:PA3 | ZN12650:PA3 | ZN12650/000003 | CENTRAL COAST | UG | Not Veg | 2016-07-08 | N | 89.5693 | N | 7 | N | N | 1.1101 | 39.4971 | 82210.951
[7 empty] | 9107 | 5425 | 1407286 | 2016-07-08 13:00 | 2016-07-08 17:20 | 260 | 11kV | 4680 | 18 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 168021 SECTION ISOLATED FOR REPAIR AFTER REPORTS OF LEAKAGE VOLTS AT POLE CS-83910. INSULATORS CHANGED ON 4 POLES. Excluded OMS 1407286 | July | 2016 | 2017Q1 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | SINGLETON | OH | Not Veg | 2016-07-08 | N | 260 | N | 7 | N | N | 1.1101 | 39.4971 | 3420.006
[7 empty] | 9260 | 7086 | 1407345 | 2016-07-08 17:15 | 2016-07-08 19:15 | 120 | 11kV | 4440 | 37 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 168024 BROKEN HV CROSSARM AT POLE WS-90012 MITCHELLS FLAT. Excluded OMS REPORT NO 1407403 & 1407345. | July | 2016 | 2017Q1 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2016-07-08 | N | 120 | N | 7 | N | N | 1.1101 | 39.4971 | 3244.621
[7 empty] | 9477 | 9769 | 1407401 | 2016-07-08 17:02 | 2016-07-08 21:25 | 263 | 11kV | 26563 | 1876 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | At ZN1287 Revesby Panel No.15 'Ashmead Av' Feeder tripped and reclosed on Signals: 11kv trip Relays: A & C phase IOC and A & C phase timed O/C, lockout, timing, Efi: nil Remarks: insulator failed at AB147 and bond burnt off | July | 2016 | 2017Q1 | 2017 | ZN1287:PA15 | ZN1287:PA15 | ZN01287/000015 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-07-08 | N | 14.1594 | N | 7 | N | N | 1.1101 | 39.4971 | 19411.4569
[7 empty] | 8876 | 2490 | 1407185 | 2016-07-08 04:23 | 2016-07-08 21:35 | 1032 | 11kV | 37498 | 69 | HV | Vegetation Blow/Fall In | Vegetation | Recloser / Sectionaliser | Unplanned | Rain Heavy | N | At Zn12570 Ex Panel 33, "Macmasters Beach" feeder from Rec 44797 Bouddi has tripped on OC and SEL Remarks: tree/branch brought down OH. Tree down @ LB44320 | July | 2016 | 2017Q1 | 2017 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2016-07-08 | N | 543.4493 | N | 7 | N | N | 1.1101 | 39.4971 | 27402.4324
[7 empty] | 8996 | 3934 | 1407432 | 2016-07-08 20:49 | 2016-07-08 23:30 | 161 | 11kV | 405117 | 3703 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S36300 Balgowlah North Panel 11 tripped 11R Leg: O/C and E/F with EFI Signals: 11kV Trip, Zone Earth Abnromal Switching: SW/A closed at S16511, LB49832 Open Cause: UG cable fault in section of feeder from S16980 to S17102 to S17011. Note: EFI defective at S16980 See OMS 1409964 1409963 1407432 1407435 | July | 2016 | 2017Q1 | 2017 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | UG | Not Veg | 2016-07-08 | N | 109.4024 | N | 7 | N | N | 1.1101 | 39.4971 | 296047.5547
[7 empty] | 10035 | 16433 | 1407618 | 2016-07-10 10:18 | 2016-07-10 13:30 | 192 | 11kV | 1536 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168033 DOLF : 10 Amp Excluded OMS 1407618 & 1407619 | July | 2016 | 2017Q1 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2016-07-10 | N | 192 | N | 3 | N | N | 1.1101 | 39.4971 | 1122.4635
[7 empty] | 9206 | 6572 | 1407637 | 2016-07-10 13:55 | 2016-07-10 17:40 | 225 | 11kV | 7650 | 34 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12570 Avoca Zn Section of P33 the mcmaster beach fdr from lb50212 to hvl41826 Remarks: OH down. Interrupted by dop to repair fallen cct cable os 89 damien cres mcmasters beach | July | 2016 | 2017Q1 | 2017 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2016-07-10 | N | 225 | N | 3 | N | N | 1.1101 | 39.4971 | 5590.3944
[7 empty] | 10350 | 20223 | 1407647 | 2016-07-10 14:10 | 2016-07-10 18:30 | 260 | 11kV | 202604 | 1014 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S3154 St Ives Panel 9 feeder tripped on Relays: Earth fault and EFI Signals: 11kV Trip, Zone Earth and TX3 Group Earth Cause: 11kV Feeder from S7419 to LB1831 tee PT1127 Isolated 11kV UGOH on CNR of Rosedale and Vista is defective See OMS 1409890 1409891 1409892 1407647 1407649 1407650 1407665 1407668 | July | 2016 | 2017Q1 | 2017 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | Unknown | Unknown | 2016-07-10 | N | 199.8067 | N | 3 | N | N | 1.1101 | 39.4971 | 148057.0274
[7 empty] | 9818 | 13824 | 1407950 | 2016-07-11 19:45 | 2016-07-11 21:35 | 110 | 11kV | 440 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168046 B Phase DOLF : 10 Amp | July | 2016 | 2017Q1 | 2017 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2016-07-11 | N | 110 | N | 1 | N | N | 1.1101 | 39.4971 | 321.539
[7 empty] | 8804 | 1515 | 1407977 | 2016-07-12 07:03 | 2016-07-12 09:30 | 147 | 11kV | 4557 | 31 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168056 A phase DOLF : 16 Amp Excluded OMS 1407977 | July | 2016 | 2017Q1 | 2017 | 528:83019 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Veg | 2016-07-12 | N | 147 | N | 8 | N | N | 1.1101 | 39.4971 | 3330.1212
[7 empty] | 8938 | 3164 | 1408007 | 2016-07-12 08:49 | 2016-07-12 11:10 | 141 | 11kV | 141 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168063 Single phase DOLF : 10 Amp excluded OMS 1408007 | July | 2016 | 2017Q1 | 2017 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2016-07-12 | N | 141 | N | 8 | N | N | 1.1101 | 39.4971 | 103.0386
[7 empty] | 8970 | 3660 | 1408120 | 2016-07-12 13:35 | 2016-07-12 15:00 | 85 | 11kV | 28751 | 377 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S35500 Top Ryde Panel 23 tripped on Earth Fault and EFI Signals: TX2 Group Earth Cause: Contractor stump grinding hit cable. Concept Landscaping. See OMS 1409688 14081201408142 | July | 2016 | 2017Q1 | 2017 | ZN35500:PA23 | ZN35500:PA23 | ZN35500/000023 | RYDE | UG | Not Veg | 2016-07-12 | N | 76.2626 | N | 8 | N | N | 1.1101 | 39.4971 | 21010.3828
[7 empty] | 9482 | 9803 | 1408209 | 2016-07-12 16:31 | 2016-07-12 18:42 | 131 | 11kV | 54096 | 530 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN690 Campsie 11kv Panel #5 labelled "S61717 Wade St etc" tripped: Relays: B phase overcurrent & leakage, EFI, Fault Check, Signals: Zone Earth, Tx 1 Group Earth, 11kv trip, CB 5 open Field EFI's: S61717, S2894, S8356 Remarks: UG fault. 11kv underground feeder fault from "Sw/A" @ S6309 Forrester Sheffield to "Sw A" @ S2093 Holder Stroud to "Sw B" @ S1797 Sheffield St | July | 2016 | 2017Q1 | 2017 | ZN690:PA5 | ZN690:PA5 | ZN00690/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-07-12 | N | 102.0679 | N | 8 | N | N | 1.1101 | 39.4971 | 39531.7612
[7 empty] | 9839 | 14055 | 1408248 | 2016-07-12 18:19 | 2016-07-12 21:15 | 176 | 11kV | 528 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168078 A Phase DOLF Excluded OMS 1408248 | July | 2016 | 2017Q1 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-07-12 | N | 176 | N | 8 | N | N | 1.1101 | 39.4971 | 385.8468
[7 empty] | 8758 | 761 | 1408131 | 2016-07-12 16:52 | 2016-07-12 21:35 | 283 | 11kV | 7531 | 109 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 168077 Interrupt to repair fallen OHM near sub 50457 excluded oms 1408131 | July | 2016 | 2017Q1 | 2017 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2016-07-12 | N | 69.0917 | N | 8 | N | N | 1.1101 | 39.4971 | 5503.4327
[7 empty] | 9793 | 13561 | 1408252 | 2016-07-12 18:36 | 2016-07-12 22:30 | 234 | 11kV | 1170 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Name Comment At PT18018 Quarry Girrakool HV fuse blown. Cause: Fuse Fatigue CROWTHER, BETTY low volts reported by Anne Robards See 1409708 exclude 1408252 | July | 2016 | 2017Q1 | 2017 | ZN14143:PA6 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | OH | Not Veg | 2016-07-12 | N | 234 | N | 8 | N | N | 1.1101 | 39.4971 | 855.0015
[7 empty] | 10073 | 16837 | 1408278 | 2016-07-12 23:54 | 2016-07-13 01:53 | 119 | 11kV | 53173 | 461 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 168079 2 fault operations A & C phases Overcurrent Excluded OMS 1408278 | July | 2016 | 2017Q1 | 2017 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2016-07-12 | N | 115.3427 | N | 8 | N | N | 1.1101 | 39.4971 | 38857.2601
[7 empty] | 9932 | 15135 | 1408726 | 2016-07-13 11:25 | 2016-07-13 13:38 | 133 | 11kV | 133 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind Strong | N | LID 168093 A phase DOLF : 63 Amp possible fuse fatigue. 244V Excluded OMS 1408455 | July | 2016 | 2017Q1 | 2017 | 242:81541 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Not Veg | 2016-07-13 | N | 133 | N | 5 | N | N | 1.1101 | 39.4971 | 97.1925
[7 empty] | 9832 | 13973 | 1408105 | 2016-07-13 08:55 | 2016-07-13 14:28 | 333 | 11kV | 4995 | 15 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S6807 Belmont Military No2 Dist No.1 "357-359 Military Rd" Remarks: Suspect Tx fault A-N 240v, B-N 200V, C-N 240V, A-B 371V, A-C 415V, B-C 400V. T/Con required to test Tx. Supply restored by closing 2 x LV// links. | July | 2016 | 2017Q1 | 2017 | ZN180:PA22 | ZN180:PA22 | ZN00180/000022 | MOSMAN | UG | Not Veg | 2016-07-13 | N | 333 | N | 5 | N | N | 1.1101 | 39.4971 | 3650.1987
[7 empty] | 9381 | 8560 | 1408402 | 2016-07-13 10:30 | 2016-07-13 14:30 | 240 | 11kV | 163772 | 951 | HV | Vegetation Blow/Fall In | Vegetation | UGOH | Unplanned | Wind Strong | N | At S965 Pennant Hills Panel 24 tripped on Relays: 51N EFOC, EFI Signals: Zone Earth, Tx1 Group Earth Cause: branch fell on 11kV UGOH to PT1296 NO apparent damage See OMS 1409671 1409672 1408597 1408470 1408498 1408409 1408408 1408402 | July | 2016 | 2017Q1 | 2017 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | HORNSBY | OH | Veg | 2016-07-13 | N | 172.2103 | N | 5 | N | N | 1.1101 | 39.4971 | 119679.7471
[7 empty] | 9878 | 14510 | 1408679 | 2016-07-13 17:36 | 2016-07-13 19:08 | 92 | 11kV | 5152 | 56 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168095 B phase DOLF : 31 Amp excluded OMS 1408679 | July | 2016 | 2017Q1 | 2017 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2016-07-13 | N | 92 | N | 5 | N | N | 1.1101 | 39.4971 | 3764.9296
[7 empty] | 8898 | 2744 | 1408625 | 2016-07-13 15:16 | 2016-07-13 22:20 | 424 | 11kV | 1272 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 168096 interrupt to repair LL lead Excluded oms 1408625 | July | 2016 | 2017Q1 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2016-07-13 | N | 424 | N | 5 | N | N | 1.1101 | 39.4971 | 929.5401
[7 empty] | 9814 | 13783 | 1408966 | 2016-07-15 08:15 | 2016-07-15 10:00 | 105 | 11kV | 2415 | 23 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Cold <10C | N | LID 168111 Car hit pole, pole snapped and broken tie on 11kV OHM reported by Police Radio - MVA into pole. distributor dislodge and hanging low over roadway. Nr 1143 RAYMOND TERRACE RD MILLERS FOREST excluded OMS 1408948 | July | 2016 | 2017Q1 | 2017 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2016-07-15 | N | 105 | N | 3 | N | N | 1.1101 | 39.4971 | 1764.8108
[7 empty] | 9092 | 5282 | 1409052 | 2016-07-15 11:29 | 2016-07-15 13:05 | 96 | 11kV | 70752 | 961 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9037 Miranda Zone - Pnl.7 tripped on: A phase IOC, EFI ABNORMAL: AB35498 (Closed) with LB35849 (Open) - Jannali P27 due to PT9538 Defective UG cable fault from Pnl.7 @ Miranda Zn to S9938 to AB39346 tee PT9467 See - M.E 1409738 1409739 (11kv trip) S.E 1409743 | July | 2016 | 2017Q1 | 2017 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | UG | Not Veg | 2016-07-15 | N | 73.6233 | N | 3 | N | N | 1.1101 | 39.4971 | 51703.4748
[7 empty] | 9117 | 5564 | 1409178 | 2016-07-15 19:26 | 2016-07-15 23:59 | 273 | 11kV | 58422 | 214 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 168121 section of 11kV fdr from ABS 63978 interupted to make repairs to damaged pole IV-70561 MVA into pole. Excluded oms 1409198 | July | 2016 | 2017Q1 | 2017 | 239:82132 | 239:82132 | ZN00239/082132 | LAKE MACQUARIE | OH | Not Veg | 2016-07-15 | N | 273 | N | 3 | N | N | 1.1101 | 39.4971 | 42693.0744
[7 empty] | 9612 | 11397 | 1409259 | 2016-07-16 09:20 | 2016-07-16 10:35 | 75.3833 | 11kV | 2713.8 | 36 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168123 A Phase DOLF : 31 Amp CC1: 22-"Refer to SOp" | July | 2016 | 2017Q1 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2016-07-16 | N | 75.3833 | N | 2 | N | N | 1.1101 | 39.4971 | 1983.165
[7 empty] | 10018 | 16257 | 1409382 | 2016-07-16 22:41 | 2016-07-17 00:10 | 89 | 11kV | 100582 | 1133 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN15008 Harbord 11kv Panel 5 "Queenscliff" feeder tripped Relays: IOC & EFI Signals: 11kv trip, Zone earth Field EFI's: S16800 Abnormal: Sw/B @ Sub 16917 Undercliff Charles open with sw B closed @ S17118 Queenscliff Dally closed (defective section) Remarks: UG fault. 11kv fault from S16800 Albert Moore to Sub 17052 Murray Moore to AB22787 | July | 2016 | 2017Q1 | 2017 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | UG | Not Veg | 2016-07-16 | N | 88.7749 | N | 2 | N | N | 1.1101 | 39.4971 | 73502.3589
[7 empty] | 8883 | 2552 | 1409406 | 2016-07-17 07:25 | 2016-07-17 08:25 | 60 | 11kV | 180 | 3 | HV | Animal Flying Fox | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168126 C Phase DOLF : 10 Amp Bat on Arrestor Excluded OMS 1409406 | July | 2016 | 2017Q1 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-07-17 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 9374 | 8445 | 1409396 | 2016-07-17 03:45 | 2016-07-17 10:00 | 375 | 11kV | 10900 | 129 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Panel 2 "Holgate" fdr Reclsoer 41020 Wattle Tree rd Nth tripped on timed overcurrent & SEL 11kv OH down near PT12703. Repaired by Linesman | July | 2016 | 2017Q1 | 2017 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2016-07-17 | N | 84.4961 | N | 3 | N | N | 1.1101 | 39.4971 | 7965.3985
[7 empty] | 8903 | 2783 | 1409494 | 2016-07-17 17:49 | 2016-07-17 19:01 | 72 | 11kV | 136042 | 2025 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill -Pnl.24 tripped on: Earth leakage with EFI Field EFIs: S1458 & S35032 UG Cable fault from S35032 (Sw/B) and S2263 (Sw/A) See 1409757 1409758 | July | 2016 | 2017Q1 | 2017 | ZN398:PA24 | ZN398:PA24 | ZN00398/000024 | INNER WEST | UG | Not Veg | 2016-07-17 | N | 67.1812 | N | 3 | N | N | 1.1101 | 39.4971 | 99415.481
[7 empty] | 9392 | 8712 | 1409813 | 2016-07-18 19:25 | 2016-07-18 21:45 | 140 | 11kV | 426313 | 3201 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde Panel 28L tripped on Relays: Lockout and C phase IOC and EFI Signals: 11kV Trip, EFI on panels 26L and 31R and TX3 Hroup Earth Cause: UG Cable fault, LV distributor wires found down due to LV parallel See OMS 1409977 1409820 1409813 1409816 1409817 1409818 1409819 | July | 2016 | 2017Q1 | 2017 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | UG | Not Veg | 2016-07-18 | N | 133.1812 | N | 2 | N | N | 1.1101 | 39.4971 | 311536.9663
[7 empty] | 9602 | 11280 | 1409911 | 2016-07-19 10:14 | 2016-07-19 11:39 | 85 | 11kV | 58587 | 701 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S10993 Hustville North Panel 33 tripped reclosed tripped and locked out on Relays: A and B phase OC, EFI and Lockout Signals: 11kV trip Cause not ascertained. Dops patrolled feeder. cause not ascertained for outage 1410128 1410130 1409928 1409911 1409933 | July | 2016 | 2017Q1 | 2017 | ZN10993:PA33 | ZN10993:PA33 | ZN10993/000033 | GEORGES RIVER | OH | Veg | 2016-07-19 | N | 83.5763 | N | 4 | N | N | 1.1101 | 39.4971 | 42813.6516
[7 empty] | 9607 | 11335 | 1409920 | 2016-07-19 10:45 | 2016-07-19 11:52 | 66.8667 | 11kV | 12637.8 | 189 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168140 B phase DOLF : 31 Amp Excluded OMS 1409935 | July | 2016 | 2017Q1 | 2017 | 223:14394 | 223:14394 | ZN00223/014394 | LAKE MACQUARIE | OH | Veg | 2016-07-19 | N | 66.8667 | N | 4 | N | N | 1.1101 | 39.4971 | 9235.3315
[7 empty] | 10134 | 17600 | 1409937 | 2016-07-19 11:26 | 2016-07-19 13:50 | 144 | 11kV | 94590 | 1044 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At S9037 Miranda panel 2 tripped reclosed tripped and locked out on Relays: B phase earth leakage Cause: Lightning/surge arrestor failed. Footpath side See OMS 1410697 1409950 1409937 1410698 | July | 2016 | 2017Q1 | 2017 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Not Veg | 2016-07-19 | N | 90.6034 | N | 4 | N | N | 1.1101 | 39.4971 | 69123.5821
[7 empty] | 9792 | 13560 | 1409938 | 2016-07-19 11:30 | 2016-07-19 14:21 | 171 | 11kV | 72504 | 424 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12630 Pest Ridge section Pa23 "USL44918" fdr @Ab44889 11kv Bond Burnt off Abnormal: Ab44077 clsoed Ab44079 open and defective See 1410170 exclude 1409938 | July | 2016 | 2017Q1 | 2017 | ZN12630:PA23 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2016-07-19 | N | 171 | N | 4 | N | N | 1.1101 | 39.4971 | 52983.7847
[7 empty] | 9569 | 10883 | 1409838 | 2016-07-18 23:27 | 2016-07-19 17:33 | 1086 | 11kV | 173580 | 160 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn931 Darlinghurst - Pnl.24 tripped on: Earth Fault & EFI Abnormal Switching: S49444 (Sw/B) Open with S1393 (Sw/A) Closed due to defective UG cable at S1323 Domain Parking Station. UG cable fault. 4 Centres could not be supplied until cable was repaired due to out of service cable at S1323. See 1410115 1410116 1410117 | July | 2016 | 2017Q1 | 2017 | ZN931:PA24 | ZN931:PA24 | ZN00931/000024 | SYDNEY | UG | Not Veg | 2016-07-18 | N | 1084.875 | N | 2 | N | N | 1.1101 | 39.4971 | 126847.1443
[7 empty] | 9226 | 6794 | 1410094 | 2016-07-20 02:54 | 2016-07-20 07:20 | 266 | 11kV | 3990 | 15 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168145 A & B phase DOLF : 20 Amp Removed tree branch from OHM. Excluded OMS 1410100, 1410106, 1410094 | July | 2016 | 2017Q1 | 2017 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2016-07-20 | N | 266 | N | 6 | N | N | 1.1101 | 39.4971 | 2915.7743
[7 empty] | 8762 | 890 | 1410168 | 2016-07-20 09:51 | 2016-07-20 12:00 | 129 | 11kV | 774 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 168147 B Phase DOLF : 16 Amp | July | 2016 | 2017Q1 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2016-07-20 | N | 129 | N | 6 | N | N | 1.1101 | 39.4971 | 565.6164
[7 empty] | 9522 | 10246 | 1410096 | 2016-07-20 05:15 | 2016-07-20 12:10 | 415 | 11kV | 141187 | 887 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn11963 Lindfield Panel 16 tripped, reclosed, tripped and locked out on Relays: B and C phase overcurrent and lockout Cause: 11kV OH down in Crana Ave East Lindfield See OMS 1411964 1411965 1411966 1410096 1410097 1410112 1410113 1410131 | July | 2016 | 2017Q1 | 2017 | ZN1193:PA16 | ZN1193:PA16 | ZN01193/000016 | KU-RING-GAI | OH | Not Veg | 2016-07-20 | N | 159.1736 | N | 6 | N | N | 1.1101 | 39.4971 | 103175.2953
[7 empty] | 10343 | 20188 | 1410226 | 2016-07-20 13:13 | 2016-07-20 14:20 | 67 | 11kV | 1474 | 22 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | LID 168148 B Phase DOLF Fatigued Fuse | July | 2016 | 2017Q1 | 2017 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | OH | Not Veg | 2016-07-20 | N | 67 | N | 6 | N | N | 1.1101 | 39.4971 | 1077.1557
[7 empty] | 8941 | 3213 | 1410192 | 2016-07-20 15:35 | 2016-07-20 17:20 | 105 | 11kV | 1680 | 16 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Rain Heavy | N | Zn12600 Lisarow sectin of 11kv Panel 2 "Holgate" fdr was interrutped between USL41935 and AB41934 to remove tree Tree on CCT Between USL41935 and AB41934 See 1410273,8 Exclude 1410192 | July | 2016 | 2017Q1 | 2017 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2016-07-20 | N | 105 | N | 6 | N | N | 1.1101 | 39.4971 | 1227.6944
[7 empty] | 10065 | 16704 | 1410299 | 2016-07-20 18:03 | 2016-07-21 01:50 | 467 | 11kV | 7939 | 17 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 168150 B phase burnt off tapping adj sub 3097 Excluded OMS 141209##dq | July | 2016 | 2017Q1 | 2017 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2016-07-20 | N | 467 | N | 6 | N | N | 1.1101 | 39.4971 | 5801.587
[7 empty] | 9106 | 5416 | 1410373 | 2016-07-21 09:20 | 2016-07-21 11:20 | 120 | 11kV | 600 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | ExZn12630 Peats Ridge section of Pa23 "Calga" fdr PT18733 WiseFerry Okara 0.2 footpath 20K HDO operated Fuse Fatigue See 1410623 exclude 1410373 | July | 2016 | 2017Q1 | 2017 | ZN12630:PA23 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2016-07-21 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 10128 | 17563 | 1410481 | 2016-07-21 15:46 | 2016-07-21 18:05 | 139 | 11kV | 101565 | 1622 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | LID 168162 Earth Fault Faulty section of UG from sw 37162 Diggers Dr. Successful FDIR operation Excluded OMS 1410481 | July | 2016 | 2017Q1 | 2017 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | UG | Not Veg | 2016-07-21 | N | 62.6171 | N | 4 | N | N | 1.1101 | 39.4971 | 74220.7063
[7 empty] | 10325 | 19883 | 1410530 | 2016-07-21 21:44 | 2016-07-21 23:25 | 101 | 11kV | 59691 | 591 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S8000 Macquarie Park Panel 1 tripped on Relays: E/F, Fault Check and EFI Signals: 11kv Trip, ZN Earth, No1 Group Earth Cause: UG cable fault S1887 to S7128 | July | 2016 | 2017Q1 | 2017 | ZN8000:PA1 | ZN8000:PA2 | ZN08000/000002 | RYDE | UG | Not Veg | 2016-07-21 | N | 101 | N | 4 | N | N | 1.1101 | 39.4971 | 43620.4222
[7 empty] | 9456 | 9447 | 1410520 | 2016-07-21 19:14 | 2016-07-22 12:00 | 1006 | 11kV | 1437 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 168163 A phase DOLF : 2 Amp Faulty transformer 54310 Excluded OMS 1410520 | July | 2016 | 2017Q1 | 2017 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2016-07-21 | N | 718.5 | N | 4 | N | N | 1.1101 | 39.4971 | 1050.1172
[7 empty] | 8788 | 1330 | 1410706 | 2016-07-22 14:18 | 2016-07-22 15:15 | 57 | 11kV | 29241 | 513 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 168174 2 fault operations C phase Instantaneous Earth Fault; Instantaneous Overcurrent Excluded OMS 1410706 | July | 2016 | 2017Q1 | 2017 | 532:83300 | 532:83300 | ZN00532/083300 | MAITLAND | UG | Not Veg | 2016-07-22 | N | 57 | N | 6 | N | N | 1.1101 | 39.4971 | 21368.4603
[7 empty] | 8813 | 1605 | 1410755 | 2016-07-22 19:43 | 2016-07-22 21:20 | 97 | 11kV | 102238 | 1054 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S4545 Meadowbank panel 41 tripped on relays A and C phase OC Cause not ascertained for outage | July | 2016 | 2017Q1 | 2017 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | OH | Veg | 2016-07-22 | N | 97 | N | 6 | N | N | 1.1101 | 39.4971 | 74712.5149
[7 empty] | 8973 | 3683 | 1410762 | 2016-07-22 20:26 | 2016-07-22 22:05 | 99 | 11kV | 23450 | 372 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | LID 168176 1 fault operation Earth Fault Cable fault at hazermeyer RMU sub 53168. Fdr abnormal due to earlier fault. Excluded OMS 1410762, 1410763 ## | July | 2016 | 2017Q1 | 2017 | 523:33507 | 523:33507 | ZN00523/033507 | SINGLETON | UG | Not Veg | 2016-07-22 | N | 63.0376 | N | 6 | N | N | 1.1101 | 39.4971 | 17136.5683
[7 empty] | 10247 | 18999 | 1410756 | 2016-07-22 19:47 | 2016-07-23 00:20 | 273 | 11kV | 6649 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168178 2 faulty operations excluded OMS 1410756 | July | 2016 | 2017Q1 | 2017 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2016-07-22 | N | 237.4643 | N | 6 | N | N | 1.1101 | 39.4971 | 4858.8931
[7 empty] | 9239 | 6925 | 1410760 | 2016-07-22 20:01 | 2016-07-23 01:05 | 304 | 11kV | 6110 | 29 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 168179 tapping off at ABS 74356 fdr isolated from sw 74500 to make repairs. Excluded OMS 1410760 | July | 2016 | 2017Q1 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-07-22 | N | 210.6897 | N | 6 | N | N | 1.1101 | 39.4971 | 4465.0078
[7 empty] | 10177 | 18132 | 1410770 | 2016-07-23 00:30 | 2016-07-23 04:35 | 245 | 11kV | 3675 | 15 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | Ex Zn12600 LIsarow section of Panel 2 "Holgate" fdr LK41373 interrupted for safety after vehicle hit pole. Live 11kV Mains were resting on LV cross arm and tracking. Mains Repaired. See 1411374 exclude 1410770 | July | 2016 | 2017Q1 | 2017 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2016-07-23 | N | 245 | N | 15 | N | N | 1.1101 | 39.4971 | 2685.5816
[7 empty] | 9418 | 9033 | 1410780 | 2016-07-23 02:26 | 2016-07-23 07:50 | 324 | 11kV | 4255 | 56 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn14891 Wyong section of Panel 12 "Cedar Northcott" fdr RE45015 Bursh Creek tripped and reclosed Autolink 44776 Brush Creek operated Tree/branch on OH Mains adjacent to PT13354 removed by DOps See 1411390,1 exclude 1410780,97 | July | 2016 | 2017Q1 | 2017 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2016-07-23 | N | 75.9821 | N | 15 | N | N | 1.1101 | 39.4971 | 3109.4285
[7 empty] | 10117 | 17446 | 1410782 | 2016-07-23 03:34 | 2016-07-23 08:05 | 271 | 11kV | 107051 | 1406 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 168184 2 fault operations C phase Instantaneous Overcurrent; Earth Fault system abnormal abs 43204 closed & Sw 74118 open. wires down at pole AK-60053 Excluded oms 141082 & 1410784. | July | 2016 | 2017Q1 | 2017 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Not Veg | 2016-07-23 | N | 76.1387 | N | 15 | N | N | 1.1101 | 39.4971 | 78229.7133
[7 empty] | 9478 | 9770 | 1410807 | 2016-07-23 07:19 | 2016-07-23 08:37 | 78 | 11kV | 67984 | 910 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | ZN9700 Kirrawee Panel 19 'Hotham Jowyn' tripped reclosed and locked out Relays: EFI, B phase O/C, Timing/lockout relay and fault check Signals: Zone earth, Tx 3 Group earth and 11kv trip Remarks: UG fault. UG cable from S9410 Yalgar bath No3 to Sub 9023 Boulevarde Mokera No2 | July | 2016 | 2017Q1 | 2017 | ZN9700:PA19 | ZN9700:PA19 | ZN09700/000019 | SUTHERLAND | UG | Not Veg | 2016-07-23 | N | 74.7077 | N | 15 | N | N | 1.1101 | 39.4971 | 49680.702
[7 empty] | 9616 | 11438 | 1410791 | 2016-07-22 23:15 | 2016-07-23 08:50 | 575 | 11kV | 8625 | 15 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168190 A & B Phase DOLF : 16 Amp Fallen tree had hit OHM near pole NG-30586 | July | 2016 | 2017Q1 | 2017 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2016-07-22 | N | 575 | N | 6 | N | N | 1.1101 | 39.4971 | 6302.8956
[7 empty] | 9162 | 6150 | 1410800 | 2016-07-23 07:01 | 2016-07-23 09:15 | 134 | 11kV | 102180 | 892 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168191 2 fault operations A phase Overcurrent; Earth Fault Excluded OMS 1410800 | July | 2016 | 2017Q1 | 2017 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2016-07-23 | N | 114.5516 | N | 15 | N | N | 1.1101 | 39.4971 | 74670.1302
[7 empty] | 9310 | 7546 | 1410776 | 2016-07-23 01:50 | 2016-07-23 12:30 | 640 | 11kV | 96788 | 821 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168177 2 fault operations Earth Fault tree branch on OHM at pole DP-30210 HV into LV. LV at sub 51501 isolated Excluded oms 1410776 | July | 2016 | 2017Q1 | 2017 | 513:48051 | 513:83493 | ZN00513/083493 | SINGLETON | OH | Veg | 2016-07-23 | N | 117.8904 | N | 15 | N | N | 1.1101 | 39.4971 | 70729.8156
[7 empty] | 9973 | 15579 | 1410823 | 2016-07-23 08:28 | 2016-07-23 12:50 | 262 | 11kV | 1834 | 7 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 168196 interrupt to repair broken LL lead Excluded oms 1410823 | July | 2016 | 2017Q1 | 2017 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2016-07-23 | N | 262 | N | 15 | N | N | 1.1101 | 39.4971 | 1340.2331
[7 empty] | 9221 | 6751 | 1410826 | 2016-07-23 08:35 | 2016-07-23 14:12 | 337 | 11kV | 72373 | 925 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn36200 Empire Bay Panel 4 "Palmers Lane" fdr opened and locked out on, B & C phase overcurrent, Signals, 11kV trip Large tree on HV mains outside 35 Huntley Rd Bensville See 1411454,7,8,9 exclude 1410826,912,843 | July | 2016 | 2017Q1 | 2017 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2016-07-23 | N | 78.2411 | N | 15 | N | N | 1.1101 | 39.4971 | 52888.0538
[7 empty] | 9504 | 10005 | 1410941 | 2016-07-23 13:24 | 2016-07-23 14:35 | 71 | 11kV | 46789 | 659 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168202 3 fault operations C phase Overcurrent tree branch on OHM near sub 11937 | July | 2016 | 2017Q1 | 2017 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2016-07-23 | N | 71 | N | 15 | N | N | 1.1101 | 39.4971 | 34192.0212
[7 empty] | 10323 | 19867 | 1410949 | 2016-07-23 13:41 | 2016-07-23 16:10 | 149 | 11kV | 298 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 168201 Single phase Live Line Clamp off DOLF Excluded OMS 1410949 | July | 2016 | 2017Q1 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2016-07-23 | N | 149 | N | 15 | N | N | 1.1101 | 39.4971 | 217.7696
[7 empty] | 9907 | 14891 | 1410998 | 2016-07-23 16:01 | 2016-07-23 16:56 | 55 | 11kV | 55000 | 1000 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn3154 St Ives - Pnl.24 tripped on: A Phase IOC and timed Tree branch on OH mains outside 8 Acron St. No apparent damage. | July | 2016 | 2017Q1 | 2017 | ZN3154:PA24 | ZN3154:PA24 | ZN03154/000024 | KU-RING-GAI | OH | Veg | 2016-07-23 | N | 55 | N | 15 | N | N | 1.1101 | 39.4971 | 40192.3778
[7 empty] | 10143 | 17746 | 1411010 | 2016-07-23 16:28 | 2016-07-23 17:58 | 90 | 11kV | 23040 | 256 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | Ex 11kv Panel No.1 "S9755, S9665" feeder from ZN9118 Cronulla @Recloser 35756 Bundeena - 111kv load side, Nth side phase link HR and arcing Remarks: Underslung links-details below. @ Recloser 35756 Bundeena - 11kv load side, Nth side phase link HR and arcing | July | 2016 | 2017Q1 | 2017 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2016-07-23 | N | 90 | N | 15 | N | N | 1.1101 | 39.4971 | 16836.9524
[7 empty] | 9791 | 13558 | 1411013 | 2016-07-23 16:37 | 2016-07-23 19:40 | 183 | 11kV | 915 | 5 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Insulated | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa23 PT11046 Wise Ferry Lillicrapps 11kv 10amp roadside HVDO operated Tree Branch hit 11kv Conductors See 1411845 exclude 1411013 1411039 | July | 2016 | 2017Q1 | 2017 | ZN12630:PA23 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2016-07-23 | N | 183 | N | 15 | N | N | 1.1101 | 39.4971 | 668.655
[7 empty] | 8792 | 1406 | 1411016 | 2016-07-23 16:44 | 2016-07-23 20:00 | 196 | 11kV | 196 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 168203 Single phase LLC off DOLF Excluded OMS 1411016 | July | 2016 | 2017Q1 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2016-07-23 | N | 196 | N | 15 | N | N | 1.1101 | 39.4971 | 143.231
[7 empty] | 10254 | 19047 | 1410789 | 2016-07-23 04:48 | 2016-07-23 20:40 | 952 | 11kV | 9520 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 168208 Single phase 11kV MAins down. LA faulty at sub 6158 & Cut away. Excluded OMS 1410789 | July | 2016 | 2017Q1 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-07-23 | N | 952 | N | 15 | N | N | 1.1101 | 39.4971 | 6956.9352
[7 empty] | 9083 | 5226 | 1411181 | 2016-07-24 18:15 | 2016-07-24 20:40 | 145 | 11kV | 182100 | 1794 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn12650 West Gosford Panel 13 "Racecoruse Faunce etc" fdr tripped and reclosed and tripped on Signals: 11kv trip B, No.13 Group Earth Relays: SEF, IOC, UF2, Timing Relays, Lockout EFI's Pa13 S14116 IR62731 Narara Creek Manns (also tripped) Relays: OC trip, SEF trip, Lockout Bond Burnt off at UGOH on POle GO9637 near LB41071. Feeder patrolled not other cause found. Fire Brigade reports Grass fire in location of burnt bond See 1411856,7,8,9 exclude 1411181,91,9,205 | July | 2016 | 2017Q1 | 2017 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2016-07-24 | N | 101.505 | N | 2 | N | N | 1.1101 | 39.4971 | 133073.309
[7 empty] | 8867 | 2331 | 1411146 | 2016-07-24 14:08 | 2016-07-24 21:30 | 442 | 11kV | 29718 | 281 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | The 11kV CP554 Arcadia Ross Common ex S2420 Galston Panel 8 tripped. Note: Protection details not available - Recloser out of SCAN Cause: Tree branch on OH mains O/S Sunny Ridge Rd See OMS 1412696 1412699 1412698 1412700 1411147 1411146 | July | 2016 | 2017Q1 | 2017 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2016-07-24 | N | 105.758 | N | 2 | N | N | 1.1101 | 39.4971 | 21717.0379
[7 empty] | 9375 | 8449 | 1411519 | 2016-07-25 17:17 | 2016-07-25 19:37 | 140 | 11kV | 2660 | 19 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 168219 STRANDING MAINS NEAR POLE EU-61501 & LOW MAINS NEAR POLE EU-61530. SECTION ISOLATED BY OPERATOR. | July | 2016 | 2017Q1 | 2017 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2016-07-25 | N | 140 | N | 2 | N | N | 1.1101 | 39.4971 | 1943.8495
[7 empty] | 9282 | 7250 | 1411753 | 2016-07-25 23:40 | 2016-07-26 01:43 | 123 | 11kV | 159432 | 1442 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN9118 Cronulla 11kv Panel #22 labelled "S9786 Franklin King" tripped, reclosed & tripped: Relays: Earth fault, EFI, A phase timed O/C, Lockout relay Signals: Zone earth, Tx1 Group earth, 11kv trip, CB 22 open, CB 22 closed, CB 22 open Field EFI's: S9786, S9787, S9437 Remarks: UG fault. 11kv feeder fault from "SW/B" @ S9180 Denman Harnleigh to "SW/A" @ S9305 Gannons Denman | July | 2016 | 2017Q1 | 2017 | ZN9118:PA22 | ZN9118:PA22 | ZN09118/000022 | SUTHERLAND | UG | Not Veg | 2016-07-25 | N | 110.5631 | N | 2 | N | N | 1.1101 | 39.4971 | 116508.2032
[7 empty] | 9225 | 6792 | 1411767 | 2016-07-26 07:15 | 2016-07-26 08:35 | 80 | 11kV | 240 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168223 C Phase DOLF : 10 Amp 243V | July | 2016 | 2017Q1 | 2017 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2016-07-26 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 9361 | 8215 | 1411764 | 2016-07-26 06:06 | 2016-07-26 09:00 | 174 | 11kV | 1354 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At CP24720 Cromer Fitness A + C phase OQFRN 71A fuse blown Section of panel 12L "South Creek Rd Penrith" feeder @ ZN15006 Dee Why West Remarks: tree/branch on OH mains. On section of OH between S16970 Sports Academy No1 Sw/B and S17023 Sports Academy No2 Sw/A | July | 2016 | 2017Q1 | 2017 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Veg | 2016-07-26 | N | 169.25 | N | 4 | N | N | 1.1101 | 39.4971 | 989.4633
[7 empty] | 9666 | 11982 | 1411754 | 2016-07-26 00:57 | 2016-07-26 12:30 | 693 | 11kV | 92955 | 1286 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor ABC | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 33 tripped and locked out on Relays: electronic Basler 50TBC -(B and C phase Timed overcurrent) Lockout Relays:, Timing Relay and EFI Cause: 11kV and 415 OH down adjacent to PT722 Vaughn Laurence/ See OMS 1412737 1412740 1412741 1412742 1411754 1411756 | July | 2016 | 2017Q1 | 2017 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Not Veg | 2016-07-26 | N | 72.2823 | N | 4 | N | N | 1.1101 | 39.4971 | 67928.7723
[7 empty] | 9479 | 9771 | 1411982 | 2016-07-26 16:20 | 2016-07-26 18:50 | 150 | 11kV | 560 | 262 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Recloser 1126 Mona Vale Rd tripped and reclosed ex Panel 10 "Mona Vale Aumuna" fdr Remarks: cause not ascertained. 50 a SIBA HV fuse blown at S16127 Ingleside 30. No apparent cause. Dop reports that he has been here several times over the past year for this same reason. | July | 2016 | 2017Q1 | 2017 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2016-07-26 | N | 2.1374 | N | 4 | N | N | 1.1101 | 39.4971 | 409.2315
[7 empty] | 9075 | 5089 | 1412021 | 2016-07-27 06:45 | 2016-07-27 12:10 | 324.5667 | 11kV | 8763.3 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168247 fdr patrolled nothing found fdr restored | July | 2016 | 2017Q1 | 2017 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2016-07-27 | N | 324.5667 | N | 2 | N | N | 1.1101 | 39.4971 | 6403.9612
[7 empty] | 9360 | 8209 | 1412299 | 2016-07-27 22:31 | 2016-07-27 23:25 | 54 | 11kV | 2376 | 44 | HV | Arcing | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa1 "Bentley Rd etc" Cause: Bond RE44853 Ourmibah Bumble opened by AOp, Linesman reported arcing HV mains outside ourimbah creek rd, Ourimbah | July | 2016 | 2017Q1 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2016-07-27 | N | 54 | N | 2 | N | N | 1.1101 | 39.4971 | 1736.3107
[7 empty] | 9819 | 13840 | 1412527 | 2016-07-28 14:00 | 2016-07-28 14:45 | 45 | 11kV | 5755 | 292 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn9035 Caringbah Zone - Pnl.2 tripped & reclosed on: A & C phase IOC Field EFIs: S9796, S9070, S9149, S9117, S9543, S9342 DOp interrupted feeder from S9342 Sw/B due to end box failure at S9574 Captain Woodfield @ 1400 See 1412680 1412681 | July | 2016 | 2017Q1 | 2017 | ZN9035:PA2 | ZN9035:PA2 | ZN09035/000002 | SUTHERLAND | UG | Not Veg | 2016-07-28 | N | 19.7089 | N | 4 | N | N | 1.1101 | 39.4971 | 4205.5843
[7 empty] | 8796 | 1448 | 1412521 | 2016-07-28 12:23 | 2016-07-28 16:04 | 221 | 11kV | 221 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168262 A Phase DOLF : 10 Amp Excluded OMS 1412521 | July | 2016 | 2017Q1 | 2017 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2016-07-28 | N | 221 | N | 4 | N | N | 1.1101 | 39.4971 | 161.5003
[7 empty] | 9667 | 11987 | 1412449 | 2016-07-28 11:39 | 2016-07-28 19:28 | 469 | 11kV | 1215 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 168263 B Phase Found Bph dolf mount broken sub 15829, Aph also broke when operating, Section isolated at 11kV links 12799 at1315hrs for repairs. Excluded OMS 1412449 | July | 2016 | 2017Q1 | 2017 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2016-07-28 | N | 405 | N | 4 | N | N | 1.1101 | 39.4971 | 887.8862
[7 empty] | 9356 | 8145 | 1412612 | 2016-07-28 19:01 | 2016-07-28 21:19 | 138 | 11kV | 370738 | 3041 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Zn10996 Rockdale Pnl.19 tripped and reclosed on C phase inst O/C and timed O/C Abnormal: S10166 Chapel Aboukir (Sw/A) closed with S10076 Harrow Victor open bond UGOH Sw/A side. Flashover/arcing at LB31200 See 1412727 1412729 1412731 | July | 2016 | 2017Q1 | 2017 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | OH | Not Veg | 2016-07-28 | N | 121.9132 | N | 4 | N | N | 1.1101 | 39.4971 | 270924.3955
[7 empty] | 9402 | 8811 | 1412958 | 2016-07-30 15:56 | 2016-07-30 16:55 | 59 | 11kV | 1460 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn14144 Wamberal sedction of Pa10L "Wamberal Aux No.2" PT11282 Coachwood Matcham centre phase 50k HDO operated PT12011 Dist 2 was in LV Parallel with LV link 16997 closed and Dist fuses blown as well. Cause not ascertained See 1412958,1421668 exclude 1412959 | July | 2016 | 2017Q1 | 2017 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2016-07-30 | N | 58.4 | N | 1 | N | N | 1.1101 | 39.4971 | 1066.9249
[7 empty] | 10058 | 16658 | 1412996 | 2016-07-31 01:50 | 2016-07-31 09:25 | 455 | 11kV | 52325 | 115 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa22 "Gunderman" RE61097 Wise Ferry Lavender 10.2 tripped on overcurrent & locked out RE61097 is non operational and defective. SCAD telecontrol defect Requires urgent Repairs or replacement | July | 2016 | 2017Q1 | 2017 | ZN12630:PA22 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | Unknown | Not Veg | 2016-07-31 | N | 455 | N | 2 | N | N | 1.1101 | 39.4971 | 38237.5667
[7 empty] | 9622 | 11492 | 1413044 | 2016-07-31 11:26 | 2016-07-31 12:25 | 59 | 11kV | 3540 | 60 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZnAvoca section of Pa25 "Hillcrest st" PT14181 Riviera South Parry footpath phase 31.5 HDO (batch 443) operated Fus Fatigue See 1413278 exclude 1413044,55 | July | 2016 | 2017Q1 | 2017 | ZN12570:PA25 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | OH | Not Veg | 2016-07-31 | N | 59 | N | 2 | N | N | 1.1101 | 39.4971 | 2586.9276
[7 empty] | 9568 | 10869 | 1413225 | 2016-08-01 11:10 | 2016-08-01 11:58 | 48 | 11kV | 17952 | 374 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 168285 1 fault operation 3 phase Earth Fault, Overcurrent Contractor cut cable cnr Watt & King St Newcastle. Excluded OMS 1413225, 1413230 | August | 2016 | 2017Q1 | 2017 | 202:34259 | 202:34259 | ZN00202/034259 | NEWCASTLE | UG | Not Veg | 2016-08-01 | N | 48 | N | 2 | N | N | 1.1101 | 39.4971 | 13118.7921
[7 empty] | 9024 | 4271 | 1413311 | 2016-08-01 15:57 | 2016-08-01 17:01 | 64 | 11kV | 85632 | 1338 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Panel 1 'Woids Ave' fdr from S10991 Blakehurst Remarks: Bond. Centre Phase HV Bond off @ AB31134 | August | 2016 | 2017Q1 | 2017 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2016-08-01 | N | 64 | N | 2 | N | N | 1.1101 | 39.4971 | 62577.3399
[7 empty] | 9252 | 7004 | 1413512 | 2016-08-02 00:11 | 2016-08-02 02:41 | 150 | 11kV | 152198 | 1172 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn12610 Long Jetty Zone Panel 18 "Forresters Beach" tripped and locked out on C phase IOC, EFI, Earth F/C, Rec L/O timing, #3 Tx F/C, ZE EFi's: S12806 S18070 S11788 UG fault in section of 11kv fdr from S12806:B to S18070:A to S18402 See 1413580,1,2,3,4 exclude 1413512 | August | 2016 | 2017Q1 | 2017 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | UG | Not Veg | 2016-08-02 | N | 129.8618 | N | 4 | N | N | 1.1101 | 39.4971 | 111221.8093
[7 empty] | 9285 | 7268 | 1413520 | 2016-08-02 03:18 | 2016-08-02 05:20 | 122 | 11kV | 220811 | 2146 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | Zn12650 West Gosford 11kv Panel 17 Right "Fagans Bay" tripped on Aphase O/C, SEF, EFI & TX13 E/F Check Abnormal: LB48906 open & defective, LB50063 closed Transformer Failure at PT14098. See 1413601,3,4,5,6 exclude 1413520 | August | 2016 | 2017Q1 | 2017 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | OH | Not Veg | 2016-08-02 | N | 102.8942 | N | 4 | N | N | 1.1101 | 39.4971 | 161362.166
[7 empty] | 9378 | 8527 | 1413650 | 2016-08-02 12:53 | 2016-08-02 13:19 | 26 | 11kV | 494 | 19 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168295 Isolated to remove tree from mains near PT 52887 Sahm. NOTE. Planned interruption (SI 14592) beyond LF 40418 for full duration of this interruption. Excluded OMS 1413650 | August | 2016 | 2017Q1 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-08-02 | N | 26 | N | 4 | N | N | 1.1101 | 39.4971 | 361.0006
[7 empty] | 10032 | 16388 | 1413771 | 2016-08-02 21:24 | 2016-08-03 11:10 | 826 | 11kV | 157435 | 1311 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | LID 168300 2 fault operations A phase Earth Fault SW 64158 failed and needs replacing | August | 2016 | 2017Q1 | 2017 | 532:83307 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Not Veg | 2016-08-02 | N | 120.0877 | N | 4 | N | N | 1.1101 | 39.4971 | 115048.8545
[7 empty] | 9632 | 11561 | 1414107 | 2016-08-04 02:07 | 2016-08-04 04:18 | 131 | 11kV | 235720 | 1818 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | @S10991 Blakehurst Zn panel #8 labelled Tavistock Rd tripped reclosed and locked out on C phase timed OC and C phase INST EFI Remarks: UG fault. First UGOH out bitumen on ground | August | 2016 | 2017Q1 | 2017 | ZN10991:PA8 | ZN10991:PA8 | ZN10991/000008 | GEORGES RIVER | UG | Not Veg | 2016-08-04 | N | 129.659 | N | 3 | N | N | 1.1101 | 39.4971 | 172257.2234
[7 empty] | 9512 | 10074 | 1413991 | 2016-08-03 15:03 | 2016-08-04 17:05 | 1562 | 11kV | 9372 | 6 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn12660 Woy Woy section of Pa14 Reclsoer 45093 Wondabyne opened on Overcurrent OH cables twiested together near PT18603 See 1414606,7 exclude 1413991 | August | 2016 | 2017Q1 | 2017 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2016-08-03 | N | 1562 | N | 1 | N | N | 1.1101 | 39.4971 | 6848.7812
[7 empty] | 9809 | 13719 | 1414937 | 2016-08-04 15:39 | 2016-08-04 18:15 | 156 | 11kV | 156 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 168312 LL Lead from mains to sub broke away and had to be repaired.. Excluded OMS 1414353 | August | 2016 | 2017Q1 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2016-08-04 | N | 156 | N | 3 | N | N | 1.1101 | 39.4971 | 114.0002
[7 empty] | 9617 | 11448 | 1414301 | 2016-08-04 23:30 | 2016-08-04 23:40 | 10 | 11kV | 710 | 71 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Rain Light | N | PT11801 Moramba Bradys Gully the HDO fuses were opened for safety Possum wrapped around bushings of PT See 1414609 exclude 1414301 | August | 2016 | 2017Q1 | 2017 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Not Veg | 2016-08-04 | N | 10 | N | 3 | N | N | 1.1101 | 39.4971 | 518.8471
[7 empty] | 10174 | 18071 | 1414665 | 2016-08-06 08:26 | 2016-08-06 09:55 | 89 | 11kV | 10591 | 119 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa24 11kv roadside phase bond burnt off at AB44437 ABnormal: section of feeder isoalted from LB42015 to LB42022 tee PT12189, PT11831. S14667:B closed See 1414991 exclude 1414665,74 | August | 2016 | 2017Q1 | 2017 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2016-08-06 | N | 89 | N | 1 | N | N | 1.1101 | 39.4971 | 7739.5904
[7 empty] | 9688 | 12212 | 1414797 | 2016-08-07 08:32 | 2016-08-07 09:25 | 53 | 11kV | 35616 | 672 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | EX Zn2400 Berowra Panel 11. Cause: CP14772 Seymours Creek tripped on IOC annd O/C Cause Not ascertained for outage See OMS 1414797 1414806 | August | 2016 | 2017Q1 | 2017 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2016-08-07 | N | 53 | N | 1 | N | N | 1.1101 | 39.4971 | 26027.1223
[7 empty] | 10153 | 17813 | 1414916 | 2016-08-08 01:28 | 2016-08-08 02:37 | 69 | 11kV | 70035 | 1015 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn15014 Mona Vale 11kV Panel 11L Recloser CP20397 Pittwater Cabbage Tripped and locked out on OC and IOC Cause: Fruit Bat found near PT15500 No Damage Caused | August | 2016 | 2017Q1 | 2017 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Not Veg | 2016-08-08 | N | 69 | N | 5 | N | N | 1.1101 | 39.4971 | 51179.5123
[7 empty] | 9384 | 8605 | 1415057 | 2016-08-08 12:05 | 2016-08-08 12:41 | 36 | 11kV | 214 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa25 CP46831 Tree Branch on OH Mains outside 24 konda St See 1415623,4 exclude 1415057 | August | 2016 | 2017Q1 | 2017 | ZN12630:PA25 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2016-08-08 | N | 35.6667 | N | 5 | N | N | 1.1101 | 39.4971 | 156.3849
[7 empty] | 10180 | 18175 | 1415197 | 2016-08-08 18:29 | 2016-08-08 20:00 | 91 | 11kV | 125475 | 1915 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 168336 3 fault operatioons C phase Overcurrent Excluded OMS 1415197 | August | 2016 | 2017Q1 | 2017 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | UG | Not Veg | 2016-08-08 | N | 65.5222 | N | 5 | N | N | 1.1101 | 39.4971 | 91693.4291
[7 empty] | 10305 | 19626 | 1415236 | 2016-08-09 06:55 | 2016-08-09 10:10 | 195 | 11kV | 19890 | 102 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 168346 tapping burnt away to top of UGOH Excluded OMS 1415236 | August | 2016 | 2017Q1 | 2017 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Not Veg | 2016-08-09 | N | 195 | N | 2 | N | N | 1.1101 | 39.4971 | 14535.0253
[7 empty] | 9214 | 6664 | 1415221 | 2016-08-08 23:48 | 2016-08-09 10:40 | 652 | 11kV | 234565 | 1680 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S4545 Meadowbank 11kV Panel 29 tripped on Relays: EFI, Fault Check, A and B phase time O/C and Earth Fault Field EFI's S46658n S48870. Signals: 11kV Trip, Zone Earth Cause: Possum cause damage at LB61231 and 11kV OH mains came down into contact with LV distributor ex48870. Permits left for linesman to repair fallen 11kV feeder In addition to the above suspect Parallel failed at S36078#3 See OMS 1415515 1415516 1415517 1415224 1413130 1413133 1414569 1415221 | August | 2016 | 2017Q1 | 2017 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Not Veg | 2016-08-08 | N | 139.622 | N | 5 | N | N | 1.1101 | 39.4971 | 171413.1835
[7 empty] | 9182 | 6312 | 1415315 | 2016-08-09 11:17 | 2016-08-09 12:50 | 93 | 11kV | 186 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168343 C Phase DOLF : 3 Amp Excluded OMS 1415315 | August | 2016 | 2017Q1 | 2017 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2016-08-09 | N | 93 | N | 2 | N | N | 1.1101 | 39.4971 | 135.9233
[7 empty] | 9899 | 14819 | 1415219 | 2016-08-08 22:19 | 2016-08-09 13:30 | 911 | 11kV | 131460 | 376 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 168388 4 fault operations Earth Fault OHM down betweemn IQ-40013 and IQ-42201. High into low sub 26791. Excluded oms1415219, 1415232, 1415233 & 1415246 | August | 2016 | 2017Q1 | 2017 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2016-08-08 | N | 349.6277 | N | 5 | N | N | 1.1101 | 39.4971 | 96067.0906
[7 empty] | 10089 | 17137 | 1415663 | 2016-08-10 16:55 | 2016-08-10 18:15 | 80 | 11kV | 2080 | 26 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 168358 SECTION ISOLATED TO REPAIR MAIN OFF PIN AT POLE GC-10195. | August | 2016 | 2017Q1 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2016-08-10 | N | 80 | N | 1 | N | N | 1.1101 | 39.4971 | 1520.0027
[7 empty] | 9820 | 13849 | 1415749 | 2016-08-11 08:49 | 2016-08-11 11:05 | 136 | 11kV | 136 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168363 B phase DOLF : 10 Amp Service connector burned up. Also fixed. blown b phase dolf | August | 2016 | 2017Q1 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2016-08-11 | N | 136 | N | 2 | N | N | 1.1101 | 39.4971 | 99.3848
[7 empty] | 8793 | 1411 | 1415805 | 2016-08-11 11:45 | 2016-08-11 14:06 | 141 | 11kV | 173135 | 1305 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9700 Kirrawee - Pnl.18 tripped, reclosed and locked out on: Timed leakage, Lockout, Timer, EFI, Fault Check Suspect UG cable fault from AB35959 to S9361 to AB35949 See 1415975 1415976 | August | 2016 | 2017Q1 | 2017 | ZN9700:PA18 | ZN9700:PA18 | ZN09700/000018 | SUTHERLAND | UG | Not Veg | 2016-08-11 | N | 132.6705 | N | 2 | N | N | 1.1101 | 39.4971 | 126521.9514
[7 empty] | 9543 | 10508 | 1416328 | 2016-08-12 11:59 | 2016-08-12 12:12 | 13 | 11kV | 3406 | 262 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168380 Low volts due to Mitchels flat Zone TX running to lowest tap (IE to tap 27) during outage. When the parallel was made on the 11kV CB 48172 The CB 42016 tripped on OL. further investigation revealed zone volts at approx 9kV. CB 48172 was opened to restore full volts from CB 42016 for a 30 second interruption. Please investigate VR. | August | 2016 | 2017Q1 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2016-08-12 | N | 13 | N | 1 | N | N | 1.1101 | 39.4971 | 2489.0043
[7 empty] | 8783 | 1251 | 1416172 | 2016-08-13 16:35 | 2016-08-13 18:10 | 95 | 11kV | 8138 | 130 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168386 1 fault operation 3 phase Overcurrent ERxcluded OMS 1416172 | August | 2016 | 2017Q1 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-08-13 | N | 62.6 | N | 2 | N | N | 1.1101 | 39.4971 | 5947.0104
[7 empty] | 9605 | 11315 | 1416201 | 2016-08-13 22:40 | 2016-08-13 23:24 | 44 | 11kV | 4796 | 109 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168387 A Phase DOLF : 31 Amp Excluded OMS 1416201 | August | 2016 | 2017Q1 | 2017 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Veg | 2016-08-13 | N | 44 | N | 2 | N | N | 1.1101 | 39.4971 | 3504.7753
[7 empty] | 10087 | 17106 | 1416781 | 2016-08-16 07:25 | 2016-08-16 11:50 | 265 | 33kV Distribution | 1525 | 13 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | LID 168399 1 fault operation 3 phase Overcurrent Duck in UGOH JT-67029. Section isolated for repair under AP. Targets: 80507 A prot A-E 6070amps; B prot 51N. 90706 E/F Excluded OMS 1416781. | August | 2016 | 2017Q1 | 2017 |  |  |  | NEWCASTLE | OH | Not Veg | 2016-08-16 | N | 117.3077 | N | 1 | N | N | 1.1101 | 39.4971 | 1114.425
[7 empty] | 10292 | 19468 | 1417126 | 2016-08-17 14:59 | 2016-08-17 18:30 | 211 | 11kV | 194791 | 1935 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn10994 Mortdale Pnl.2 - tripped, reclosed, tripped and locked out on: A & C phase Overcurrent, Reclose timing & lockout, Fault Check & EFI Field EFIs :S10169 UGOH failed adjacent AB30351 Secondary Events: S10683 Laycock Hillcrest - DIst #1 - A & B phase fuses blown - LV parallel Failure during feeder trip PT10216 Cronin King Georges - Dist #2 - A phase fuse blown - LV parallel failure during feeder trip See 1417248 1417249 SE (LV//) 1417138 1417135 | August | 2016 | 2017Q1 | 2017 | ZN10994:PA2 | ZN10994:PA2 | ZN10994/000002 | GEORGES RIVER | Unknown | Unknown | 2016-08-17 | N | 100.6672 | N | 2 | N | N | 1.1101 | 39.4971 | 142347.5174
[7 empty] | 9675 | 12087 | 1417195 | 2016-08-17 21:05 | 2016-08-17 22:00 | 55 | 11kV | 76890 | 1398 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Ex Zn13000 Lake Munmorah section of Pa7 REC45061 Chain Valley Mulloway tripped and locked out on overcurrent Possum on 11kv UGOH between PT12231 Government Omega and S18412 Government Gnganaup. Lineworker to inspect during day See 141795 exclude 1417199 | August | 2016 | 2017Q1 | 2017 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2016-08-17 | N | 55 | N | 2 | N | N | 1.1101 | 39.4971 | 56188.9441
[7 empty] | 8785 | 1263 | 1417440 | 2016-08-19 12:30 | 2016-08-19 14:15 | 105 | 11kV | 1785 | 17 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 168432 crossarm broken Adj sub 71706 | August | 2016 | 2017Q1 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2016-08-19 | N | 105 | N | 3 | N | N | 1.1101 | 39.4971 | 1304.4254
[7 empty] | 9674 | 12079 | 1417394 | 2016-08-19 13:30 | 2016-08-19 19:40 | 370 | 11kV | 16940 | 102 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | EX ZN35270 Galston Panel 10L Section of HV Feeder isolated for safety between S8612 to S8613 tee PT65525 and S7872 Cause: HV and LV hit and damaged by excavator near S7872. DOp interrupted section of HV feeder at 1330 for safety Note: TRADES WORKING ON SITE HAVE DUG UP A CABLE - NO INJURIES REPORTED - CONTACT PERSON VICTOR FAHD - HE ADVISED WAS USING DIAL BEFORE DIG MAPS CABLE NOT LISTED ON MAPPING - LOCATION BLDG 4 See OOMS 14178636 1417868 1417439 1417394 1417414 | August | 2016 | 2017Q1 | 2017 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | UG | Not Veg | 2016-08-19 | N | 166.0784 | N | 3 | N | N | 1.1101 | 39.4971 | 12379.2524
[7 empty] | 8989 | 3872 | 1417514 | 2016-08-19 19:22 | 2016-08-19 20:39 | 77 | 11kV | 143231 | 2167 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3155 Double Bay - Pnl.19 tripped on: A phase IOC, Fault Check and EFI Field EFIs: S35003, S357, S731, S5350 Abnormal: Sw/B closed @ S2689 with Pnl.20 at Double Bay Zone Open. UG cable fault from S731 to S47924 to S2689 See 1417765 1417766 | August | 2016 | 2017Q1 | 2017 | ZN3155:PA20 | ZN3155:PA20 | ZN03155/000020 | WOOLLAHRA | UG | Not Veg | 2016-08-19 | N | 66.0964 | N | 3 | N | N | 1.1101 | 39.4971 | 104668.9902
[7 empty] | 9098 | 5339 | 1417660 | 2016-08-21 07:39 | 2016-08-21 09:40 | 121 | 11kV | 44631 | 530 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S690 Campsie Panel 5 "Wade St" fdr tripped Relays: earth fault, EFI, fault check Signals: 11kv trip, zone earth Tx2 Group earth EFIs: S61717, S2894, S6309 Remarks: UG fault. Underground cable fault between S6309 Forrester Sheffield Sw/A to S2093 Holder Stroud Sw/A to S1797 Sheffield St Sw/B | August | 2016 | 2017Q1 | 2017 | ZN690:PA5 | ZN690:PA5 | ZN00690/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-08-21 | N | 84.2094 | N | 1 | N | N | 1.1101 | 39.4971 | 32615.0184
[7 empty] | 9005 | 4000 | 1417711 | 2016-08-22 11:22 | 2016-08-22 12:15 | 53 | 11kV | 59572 | 1124 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Interrupted to carry out repairs on faulty AB44674. See SOp arrange D&R389148 | August | 2016 | 2017Q1 | 2017 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Not Veg | 2016-08-22 | N | 53 | N | 4 | N | N | 1.1101 | 39.4971 | 43533.4605
[7 empty] | 8906 | 2802 | 1417761 | 2016-08-22 09:11 | 2016-08-22 12:55 | 224 | 11kV | 448 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168447 A Phase DOLF : 10 Amp Excluded OMS 1417761 | August | 2016 | 2017Q1 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-08-22 | N | 224 | N | 4 | N | N | 1.1101 | 39.4971 | 327.3852
[7 empty] | 10166 | 17973 | 1417880 | 2016-08-22 14:59 | 2016-08-22 16:08 | 69 | 11kV | 12627 | 183 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Panel 11 tripped on Relays: A phase Tiimed and Inst OC Signals: 11kV Trip. Cause: UG cable fault from Panel 11 to S62360 Etham Monash | August | 2016 | 2017Q1 | 2017 | ZN129:PA11 | ZN129:PA55 | ZN00129/000055 | RYDE | OH | Veg | 2016-08-22 | N | 69 | N | 4 | N | N | 1.1101 | 39.4971 | 9227.4392
[7 empty] | 9324 | 7817 | 1417923 | 2016-08-22 19:30 | 2016-08-22 19:43 | 13 | 11kV | 40349 | 3263 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At Zn180 Mosman Panel 23 tripped on C phase timed overcurrent At Zn180 Mosman Panel 34 tripped on A phase timed overcurrent. Abnormal Switching: SW/B Closed at S2415 Killarney Mitchell, SW/A Open at S36190, SW/A Open at S507, SW/B Closed at S4929, SW/A Closed at S5659. Cause: During Switching Panel 23 and 34 Tripped due to high circulating current. See OMS 1418027 1418025 1417930 1417929 1417926 1417921 1417923 | August | 2016 | 2017Q1 | 2017 | ZN180:PA23 | ZN180:PA23 | ZN00180/000023 | MOSMAN | Unknown | Unknown | 2016-08-22 | N | 12.3656 | N | 4 | N | N | 1.1101 | 39.4971 | 29485.8591
[7 empty] | 8965 | 3608 | 1418126 | 2016-08-23 17:16 | 2016-08-23 19:30 | 134.25 | 11kV | 5101.5 | 38 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168460 Single phase | August | 2016 | 2017Q1 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-08-23 | N | 134.25 | N | 1 | N | N | 1.1101 | 39.4971 | 3728.0257
[7 empty] | 9955 | 15352 | 1418437 | 2016-08-25 04:42 | 2016-08-25 06:13 | 91 | 11kV | 67264 | 757 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Zone STS Transformer | Unplanned | Rain Heavy | N | At Zn1068 Lidcombe the Panel 27 "Queen Marion" tripped on: Signals: 11kv trip, Tx 1 Group earth, Zone Earth Relays: B phase leakage, EFI Field EFI's: S1544 Queen Marion Abnormal: Sw/C at S524 Beatrice St open. Sw/B at S8461 Sheffield Rhyl No2 closed | August | 2016 | 2017Q1 | 2017 | ZN1068:PA27 | ZN1068:PA27 | ZN01068/000027 | CUMBERLAND | Exclude | Not Veg | 2016-08-25 | N | 88.856 | N | 4 | N | N | 1.1101 | 39.4971 | 49154.5472
[7 empty] | 9294 | 7409 | 1418405 | 2016-08-24 20:45 | 2016-08-25 11:18 | 873 | 11kV | 142349 | 1308 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn690 Campsie Panel 30 Tripped on overcurrent with efi. Signals: 11kV trip, Zone Earth and TX4 group earth UG cable fault between S4261 Coney Rd to CP 1561 Hocking Ave to S4049 Homer bayview to S2040 Homer St North to S 2350 See OMS 1418639 1418640 1418641 1418405 1418456 | August | 2016 | 2017Q1 | 2017 | ZN690:PA30 | ZN690:PA30 | ZN00690/000030 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-08-24 | N | 108.8295 | N | 1 | N | N | 1.1101 | 39.4971 | 104024.4506
[7 empty] | 10298 | 19527 | 1418614 | 2016-08-25 12:50 | 2016-08-25 14:05 | 75 | 11kV | 1875 | 25 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168477 B Phase DOLF : 16 Amp Excluded OMS 1418614 | August | 2016 | 2017Q1 | 2017 | 801:74120 | 801:74120 | ZN00801/074120 | MUSWELLBROOK | OH | Not Veg | 2016-08-25 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 1370.1947
[7 empty] | 8859 | 2218 | 1418649 | 2016-08-25 14:34 | 2016-08-25 14:45 | 11 | 11kV | 275 | 25 | HV | Animal Other | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | BLOWN DOLF - Note: No LID report | August | 2016 | 2017Q1 | 2017 | 801:74120 | 801:74120 | ZN00801/074120 | MUSWELLBROOK | OH | Not Veg | 2016-08-25 | N | 11 | N | 4 | N | N | 1.1101 | 39.4971 | 200.9619
[7 empty] | 10088 | 17119 | 1418496 | 2016-08-25 08:42 | 2016-08-25 20:20 | 698 | 11kV | 177129 | 1112 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn180 Mosman - Pnl.20 tripped on Earth Fault Field EFIs: NIL UG cable fault between S63994 and S4282. S63994 was in LV parallel. Multiple calls from around the area. See1419341 1419342 1419343 1419344 - SE: 1418715 | August | 2016 | 2017Q1 | 2017 | ZN180:PA20 | ZN180:PA20 | ZN00180/000020 | NORTH SYDNEY | UG | Not Veg | 2016-08-25 | N | 159.2887 | N | 4 | N | N | 1.1101 | 39.4971 | 129440.6488
[7 empty] | 10182 | 18241 | 1418755 | 2016-08-26 | 2016-08-26 00:40 | 40 | 11kV | 2040 | 51 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong Zone section of Pa16 "Wadallba" PT13099 Palmer Wolsley 31.5Amp footpath side pahse HDO blew (batch 1007) Animals Possum exclude 1418755 1418757 | August | 2016 | 2017Q1 | 2017 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2016-08-26 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 1490.7718
[7 empty] | 10129 | 17564 | 1418858 | 2016-08-26 14:21 | 2016-08-26 15:10 | 49 | 11kV | 30164 | 836 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 168492 2 fault operations 3 phase Overcurrent 50 T ABC Cable fault on UGOH at pole JT-87122 section isolated for repairs. Excluded OMS 1418858 | August | 2016 | 2017Q1 | 2017 | 240:34846 | 240:34846 | ZN00240/034846 | NEWCASTLE | Unknown | Unknown | 2016-08-26 | N | 36.0813 | N | 4 | N | N | 1.1101 | 39.4971 | 22042.9615
[7 empty] | 9660 | 11878 | 1418909 | 2016-08-26 18:21 | 2016-08-26 20:52 | 151 | 11kV | 453 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 168495 C Phase DOLF : 10 Amp fuse fatigue excluded OMS 1418909 | August | 2016 | 2017Q1 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2016-08-26 | N | 151 | N | 4 | N | N | 1.1101 | 39.4971 | 331.039
[7 empty] | 10328 | 19945 | 1418917 | 2016-08-26 20:39 | 2016-08-26 21:58 | 79 | 11kV | 102284 | 1324 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn195 Pymble Panel 9 tripped reclosed tripped and locked out on Signals: 11kV Trip, TX1 Group Earth and Zone Earth Relays: Timed earth fault See OMS 1420194 1418917 | August | 2016 | 2017Q1 | 2017 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | UG | Not Veg | 2016-08-26 | N | 77.2538 | N | 4 | N | N | 1.1101 | 39.4971 | 74746.1303
[7 empty] | 9964 | 15446 | 1419056 | 2016-08-28 04:03 | 2016-08-28 05:42 | 99 | 11kV | 33759 | 341 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 168497 3 fault operations 3 phase Overcurrent, Earth Fault UGOH fault. between 3913/29775. Pole FS-93201 Excluded OMS 1419056 | August | 2016 | 2017Q1 | 2017 | 504:48032 | 522:83121 | ZN00522/083121 | CESSNOCK | UG | Not Veg | 2016-08-28 | N | 99 | N | 3 | N | N | 1.1101 | 39.4971 | 24670.0815
[7 empty] | 10044 | 16524 | 1419081 | 2016-08-28 08:49 | 2016-08-28 10:56 | 127 | 11kV | 241062 | 1936 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15004 Newport - Pnl.9 tripped on: C phase timed O/C, EFI, Frame leakage, Fault Check. Field EFIs: S16880 Bishop Bardo UG cable fault from S16880 (Sw/B) to S16689 (Sw/A) to S16526 (Sw/A) See 1419479 1419481 | August | 2016 | 2017Q1 | 2017 | ZN15004:PA9 | ZN15004:PA9 | ZN15004/000009 | NORTHERN BEACHES | UG | Not Veg | 2016-08-28 | N | 124.5155 | N | 3 | N | N | 1.1101 | 39.4971 | 176160.9995
[7 empty] | 9388 | 8684 | 1419128 | 2016-08-28 16:37 | 2016-08-29 03:15 | 638 | 11kV | 105820 | 1121 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa9 tripped on: Relays: OC, SEF Signals: 11kv trip 11kv into 415v mains o tee off to PT46364 Dalton East Maizens Tree Branch brought down OH See 1419251,3,4 exclude 1419128,55 | August | 2016 | 2017Q1 | 2017 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2016-08-28 | N | 94.3979 | N | 3 | N | N | 1.1101 | 39.4971 | 77330.1348
[7 empty] | 10131 | 17575 | 1419204 | 2016-08-29 08:35 | 2016-08-29 10:00 | 85 | 11kV | 75605 | 905 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At Zn195 Pymble 11kV feeder panel 28 tripped on Relays: (E/F 951N) Fault Check Signals: 11kV trip No4 Group Earth and Zone Earth. Cause: Contractor adjacted to S4459 Merriwa Vale on excavator appears to have damaged a section of 11kV feeder from S8728 Craiglands Vale to S4933 Browns Pennant to S4459 Merriwa Vale See OMS 1419958 141960 1419204 | August | 2016 | 2017Q1 | 2017 | ZN195:PA28 | ZN195:PA28 | ZN00195/000028 | KU-RING-GAI | UG | Not Veg | 2016-08-29 | N | 83.5414 | N | 3 | N | N | 1.1101 | 39.4971 | 55249.904
[7 empty] | 9533 | 10399 | 1419189 | 2016-08-29 08:00 | 2016-08-29 12:16 | 256 | 11kV | 3840 | 15 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 168505 1 fault operation Overcurrent feeder tripped and reclosed at 0558 report of dozer into pole HD 50016 and low mains feeder opened for safety 0800 Excluded oms 1419193,1419189 | August | 2016 | 2017Q1 | 2017 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2016-08-29 | N | 256 | N | 3 | N | N | 1.1101 | 39.4971 | 2806.1587
[7 empty] | 10083 | 16973 | 1419391 | 2016-08-29 09:15 | 2016-08-29 21:30 | 735 | 11kV | 735 | 1 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 168508 Repaired Aph 11kV OHM off insulator at pole AI-10054. Restored supply at 2130hrs. Excluded OMS 1419391 | August | 2016 | 2017Q1 | 2017 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2016-08-29 | N | 735 | N | 3 | N | N | 1.1101 | 39.4971 | 537.1163
[7 empty] | 10312 | 19766 | 1419528 | 2016-08-30 10:14 | 2016-08-30 11:09 | 55 | 11kV | 151244 | 2838 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 paddington - Pnl.26 tripped on: Left side E/F, O/C and EFI Field EFIs: S8252 S3568 S48371 S8803 UG cable fault from S8803 Pennys Bayswater (Sw/B) to S35520 St Lukes Potts Point (Sw/A) See 1419779 1414780 | August | 2016 | 2017Q1 | 2017 | ZN342:PA26 | ZN342:PA26 | ZN00342/000026 | SYDNEY | UG | Not Veg | 2016-08-30 | N | 53.2925 | N | 5 | N | N | 1.1101 | 39.4971 | 110524.6543
[7 empty] | 9398 | 8781 | 1419434 | 2016-08-30 06:52 | 2016-08-30 11:15 | 263 | 11kV | 526 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT2247 Nollands End Roadside 10A HDO Blown. Supply restored and checked out ok See OMS 1420232 1419434 | August | 2016 | 2017Q1 | 2017 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2016-08-30 | N | 263 | N | 5 | N | N | 1.1101 | 39.4971 | 384.3853
[7 empty] | 9333 | 7863 | 1419573 | 2016-08-30 11:45 | 2016-08-30 12:45 | 60 | 11kV | 72642 | 1537 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.3 tripped on: IOC, Fault Check and EFI Field EFIs: S3682, S36179, S2275, S48581 UG cable fault from S3364 Dolphin Mount to S2548 Mount Carr. Note: S3364 EFI is defective which resulted in closing onto the fault from Kingsford P22 (See OMS # 1419786) See 1419783 1414784 1419785 1419786 | August | 2016 | 2017Q1 | 2017 | ZN2602:PA3 | ZN2602:PA29 | ZN02602/000029 | RANDWICK | UG | Not Veg | 2016-08-30 | N | 47.2622 | N | 5 | N | N | 1.1101 | 39.4971 | 53084.631
[7 empty] | 10196 | 18493 | 1419552 | 2016-08-30 10:58 | 2016-08-30 15:27 | 268.6333 | 11kV | 23639.7333 | 88 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP3227 Berowra Creek tripped reclosed tripped and locked out on B and Cphase O/C Cause: Vine Growing into HV mains at Pole BB89646 Near PT1502. CC1: 22-"Refer to SOp" | August | 2016 | 2017Q1 | 2017 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2016-08-30 | N | 268.6333 | N | 5 | N | N | 1.1101 | 39.4971 | 17275.2199
[7 empty] | 9042 | 4624 | 1419662 | 2016-08-30 14:52 | 2016-08-30 16:25 | 93 | 11kV | 465 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168522 C Phase DOLF : 10 Amp Tx Volts: Aph - 244V, Bph - 242V, Cph - 243V Tx Load: Aph - 15A, Bph - 12A, Cph - 18A Excluded OMS No. 1419662 | August | 2016 | 2017Q1 | 2017 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2016-08-30 | N | 93 | N | 5 | N | N | 1.1101 | 39.4971 | 339.8083
[7 empty] | 9633 | 11584 | 1419755 | 2016-08-31 02:40 | 2016-08-31 04:43 | 123 | 11kV | 10825 | 140 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 168526 5 fault operations 3 phase Earth Fault suspect ug cable fault between Mitchell Line zone and Ea depot sub. M Brook tech service to required to check if fault maint required on CB 19065. Excluded oms 1419755 | August | 2016 | 2017Q1 | 2017 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | UG | Not Veg | 2016-08-31 | N | 77.3214 | N | 3 | N | N | 1.1101 | 39.4971 | 7910.5907
[7 empty] | 8839 | 1883 | 1419801 | 2016-08-31 09:00 | 2016-08-31 10:20 | 80 | 11kV | 36880 | 461 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 168529 A Phase Burnt off tapping at ABS 74953.Closed sw 11244 & opened ABS 74953.(Note system abnormal) oms report no 1419811. | August | 2016 | 2017Q1 | 2017 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2016-08-31 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 26950.8162
[7 empty] | 9724 | 12648 | 1420068 | 2016-09-01 02:50 | 2016-09-01 04:24 | 94 | 11kV | 206008 | 2692 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | Zn12620 Noraville Pa1L "Woolana Woodlands" tripped on Relays-Left Leg A phase Earth trip and EFI signals: See DNMS (Zone Aux is off 1L) Panel 1R no relay operations RE41873 Woolana Woodland operated on IOC and earth fault trip Found possum on RE41873 on VT surge arrestor. Mains to inspect in daylight hours. See 1420144,5 exclude 1420068,9 | September | 2016 | 2017Q1 | 2017 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2016-09-01 | N | 76.526 | N | 4 | N | N | 1.1101 | 39.4971 | 150544.5702
[7 empty] | 9284 | 7257 | 1420036 | 2016-08-31 18:19 | 2016-09-01 09:30 | 911 | 11kV | 84429 | 958 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1610 Homebush Bay - Pnl.2 tripped on: Earth Leakage Field EFIs: S5696 (Sw/B) UG cable fault from S1397 (Sw/B) and S65706 (Sw/A). No access after hours to S35706 to isolate or check EFI. See 1420301 1420302 1420303 1420304 | August | 2016 | 2017Q1 | 2017 | ZN1610:PA2 | ZN1610:PA2 | ZN01610/000002 | PARRAMATTA | UG | Not Veg | 2016-08-31 | N | 88.1305 | N | 3 | N | N | 1.1101 | 39.4971 | 61698.223
[7 empty] | 8789 | 1334 | 1420094 | 2016-09-01 10:50 | 2016-09-01 12:20 | 90 | 11kV | 450 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 168546 11kv links 43155 opened to isolate broken x-arm on pole FO-60246. | September | 2016 | 2017Q1 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2016-09-01 | N | 90 | N | 4 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 9269 | 7178 | 1420279 | 2016-09-01 22:07 | 2016-09-01 23:20 | 73 | 11kV | 140396 | 2050 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15006 Dee Why West - Pnl.15 tripped on: earth Fault & EFI Field EFIs: S16890, S16619, S16620 CP21177, S16785, S16878 UG cable fault from S16878 (Sw/A) to S16626 (Sw/A) to S17069 (Sw/B) See 1420305 1420306 | September | 2016 | 2017Q1 | 2017 | ZN15006:PA15 | ZN15006:PA15 | ZN15006/000015 | NORTHERN BEACHES | UG | Not Veg | 2016-09-01 | N | 68.4859 | N | 4 | N | N | 1.1101 | 39.4971 | 102597.2558
[7 empty] | 9037 | 4503 | 1420283 | 2016-09-02 04:30 | 2016-09-02 10:45 | 375 | 11kV | 11385 | 57 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 168554 3 fault operations Earth FAult Note: Geoff Blyth advised that the fault on sub 70876 was a HV lead shorting on to a cross arm. They replaced the lead, but apart from this there was no other damage to the installation. They also advised that there was no fire in relation to this fault, apart from the arc flash. HV DROPPER ON CROSSARM AT SUB 70876 SUB ISOLATED. FDR RESTORED 830. SUB 70876 RETORED AT 1045. Excluded OMS 1420283. | September | 2016 | 2017Q1 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2016-09-02 | N | 199.7368 | N | 3 | N | N | 1.1101 | 39.4971 | 8319.8222
[7 empty] | 9246 | 6968 | 1420408 | 2016-09-02 13:10 | 2016-09-02 13:30 | 20 | 11kV | 2581 | 135 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | LID 168556 Trip & Reclose 1 fault operation C phase Earth Fault, Instantaneous Overcurrent UG fault between Sw 75060 Hill St Switching Cubicle and Sw 6L824 Hill St sub. Flags Sw 74122 C phase and E/F instantaneous. Excluded OMS 1420387 | September | 2016 | 2017Q1 | 2017 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | UG | Not Veg | 2016-09-02 | N | 19.1185 | N | 3 | N | N | 1.1101 | 39.4971 | 1886.1187
[7 empty] | 9998 | 15934 | 1420260 | 2016-09-01 18:21 | 2016-09-03 05:50 | 2129 | 11kV | 290305.25 | 474 | HV | Overload | Utility Process Issue | DC Transformer | Unplanned | No Weather Impact | N | S135 William New - 11kV "A" phase HV fuse blown (100Amps) S1718 New South Head Rd - Dist #3 - All phase fuses blown Suspected overload at S135 (1500Amp MDI) and in LV parallel with S1718 Dist #3 at the time. LV// removed and supply restored. Link box 1119 opened and suspected defective. After investigation cable fault was the issue. Unit block left off until 3/9/16 approx5:50am. See 1420260 1421143 1421145 1420262 | September | 2016 | 2017Q1 | 2017 | ZN3155:PA34 | ZN3155:PA34 | ZN03155/000034 | WOOLLAHRA | UG | Not Veg | 2016-09-01 | N | 612.4583 | N | 4 | N | N | 1.1101 | 39.4971 | 212146.5141
[7 empty] | 9447 | 9328 | 1421603 | 2016-09-03 09:10 | 2016-09-03 09:40 | 30 | 11kV | 90 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa22 "GUnderman" fdr beyond 44952 Morgans Rd auto links Tree/Branch brought down OH. CCT hanging 1 meter from the ground reported by Staff | September | 2016 | 2017Q1 | 2017 | ZN12630:PA22 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2016-09-03 | N | 30 | N | 13 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 8766 | 945 | 1420648 | 2016-09-03 11:43 | 2016-09-03 12:55 | 72 | 11kV | 43992 | 611 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn3154 St Ives Pa12 "Killeaton Warrimoo etc" fdr tripped on A phase IOC and timed Tree brnach on mains vicinity LB64868 See 1421759 exclude 1420648,53 | September | 2016 | 2017Q1 | 2017 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Veg | 2016-09-03 | N | 72 | N | 13 | N | N | 1.1101 | 39.4971 | 32148.0561
[7 empty] | 9236 | 6895 | 1420669 | 2016-09-03 12:05 | 2016-09-03 13:20 | 75 | 11kV | 13350 | 178 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 168567 2 fault operations Branch on mains near ABS 41342. Removed by DOP | September | 2016 | 2017Q1 | 2017 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2016-09-03 | N | 75 | N | 13 | N | N | 1.1101 | 39.4971 | 9755.7862
[7 empty] | 8786 | 1274 | 1420602 | 2016-09-03 10:07 | 2016-09-03 13:48 | 221 | 11kV | 18746 | 100 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 168577 2 fault operations Earth fault Tree on mains at pole 9T-90024 | September | 2016 | 2017Q1 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2016-09-03 | N | 187.46 | N | 13 | N | N | 1.1101 | 39.4971 | 13699.0239
[7 empty] | 9143 | 5901 | 1420645 | 2016-09-03 11:43 | 2016-09-03 14:23 | 160.3667 | 11kV | 8178.7 | 51 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 168581 Section isolated for bond repair Broken tapping at pole 9L-40296 | September | 2016 | 2017Q1 | 2017 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2016-09-03 | N | 160.3667 | N | 13 | N | N | 1.1101 | 39.4971 | 5976.7527
[7 empty] | 8900 | 2759 | 1420644 | 2016-09-03 11:41 | 2016-09-03 15:00 | 199 | 11kV | 597 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 168576 High winds Excluded OMS 1420644 | September | 2016 | 2017Q1 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2016-09-03 | N | 199 | N | 13 | N | N | 1.1101 | 39.4971 | 436.27
[7 empty] | 10124 | 17521 | 1420676 | 2016-09-03 12:57 | 2016-09-03 15:25 | 148 | 11kV | 12044 | 92 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 168571 3 fault operation A & B phase Overcurrent no fault found please patrol. | September | 2016 | 2017Q1 | 2017 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2016-09-03 | N | 130.913 | N | 13 | N | N | 1.1101 | 39.4971 | 8801.4
[7 empty] | 9901 | 14838 | 1420668 | 2016-09-03 12:17 | 2016-09-03 15:50 | 213 | 11kV | 1491 | 7 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168575 LL Dropper lead failed in the wind Excluded OMS 1420668 | September | 2016 | 2017Q1 | 2017 | 512:48048 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2016-09-03 | N | 213 | N | 13 | N | N | 1.1101 | 39.4971 | 1089.5788
[7 empty] | 9124 | 5701 | 1421073 | 2016-09-03 12:29 | 2016-09-03 16:05 | 216 | 11kV | 15797 | 79 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 168569 3 fault operations B & C phase Overcurrent No fault found | September | 2016 | 2017Q1 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-09-03 | N | 199.962 | N | 13 | N | N | 1.1101 | 39.4971 | 11543.9817
[7 empty] | 9259 | 7058 | 1420690 | 2016-09-03 13:05 | 2016-09-03 18:30 | 324.9333 | 11kV | 27294.4 | 84 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 168570 3 fault operation Overcurrent Dop reports that there were no targets registed at recloser 46031 Six Mile Crk (targets from scada only). The fault current displayed only. Tech services to investigate. dq | September | 2016 | 2017Q1 | 2017 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Veg | 2016-09-03 | N | 324.9333 | N | 13 | N | N | 1.1101 | 39.4971 | 19945.9425
[7 empty] | 9255 | 7017 | 1420630 | 2016-09-03 10:59 | 2016-09-03 19:30 | 511 | 11kV | 35216 | 366 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 "Wyong" fdr RE45101 tripped on IOC and lockout Tree brought down wires down 57 little Jilliby Rd beyond autolinks 44782 See 142646,7,8 exclude 1420630,5,731 | September | 2016 | 2017Q1 | 2017 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2016-09-03 | N | 96.2186 | N | 13 | N | N | 1.1101 | 39.4971 | 25734.8141
[7 empty] | 8978 | 3746 | 1420704 | 2016-09-03 13:24 | 2016-09-03 20:20 | 416 | 11kV | 33470 | 262 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168579 Trees blown into mains Mains down massive tree into 11kV Excluded OMS 1420704 | September | 2016 | 2017Q1 | 2017 | 532:83298 | 532:83298 | ZN00532/083298 | MAITLAND | OH | Veg | 2016-09-03 | N | 127.7481 | N | 13 | N | N | 1.1101 | 39.4971 | 24458.8888
[7 empty] | 8921 | 2918 | 1420861 | 2016-09-04 08:28 | 2016-09-04 09:35 | 67 | 11kV | 201 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168584 C phase DOLF : 31 Amp Excluded OMS 1420861 | September | 2016 | 2017Q1 | 2017 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | OH | Not Veg | 2016-09-04 | N | 67 | N | 4 | N | N | 1.1101 | 39.4971 | 146.8849
[7 empty] | 9396 | 8750 | 1420882 | 2016-09-04 10:29 | 2016-09-04 12:00 | 91 | 11kV | 1365 | 15 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 168588 A phase interrupt to repair broken LLC Excluded OMS 1420882 | September | 2016 | 2017Q1 | 2017 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Not Veg | 2016-09-04 | N | 91 | N | 4 | N | N | 1.1101 | 39.4971 | 997.5017
[7 empty] | 9851 | 14196 | 1420670 | 2016-09-03 09:24 | 2016-09-04 13:00 | 1656 | 11kV | 190753 | 672 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Panel 11 Brooklyn EX Zn 2400 Berowra Recloser CP1772 Seymours Creek Tripped on SEF Cause: Tree brought down OH near PT645 Milsons Passage See OMS 1421939 1421940 1421941 1421942 | September | 2016 | 2017Q1 | 2017 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2016-09-03 | N | 283.8586 | N | 13 | N | N | 1.1101 | 39.4971 | 139396.6661
[7 empty] | 9921 | 15012 | 1421095 | 2016-09-04 11:35 | 2016-09-04 13:10 | 95 | 11kV | 475 | 5 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Previous Storm | N | LID 168585 3 phase ABS 42264 found to be damaged accross 3 phases. Outage to bridge out the switch, to be repaired later. | September | 2016 | 2017Q1 | 2017 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2016-09-04 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 347.116
[7 empty] | 8935 | 3114 | 1420878 | 2016-09-04 09:56 | 2016-09-04 13:30 | 214 | 11kV | 856 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168586 B phase DOLF : 16 Amp Excluded OMS 1420878 | September | 2016 | 2017Q1 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-09-04 | N | 214 | N | 4 | N | N | 1.1101 | 39.4971 | 625.5396
[7 empty] | 10057 | 16657 | 1420310 | 2016-09-02 09:31 | 2016-09-05 14:00 | 4589 | 11kV | 35136 | 255 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of Pa23 46992 Goolara Holy Cross tripped on: Relays: Overcurrent, Earth Fault, Lockout Large Tree brnach down HV and LV Mains between LK42664 and PT12154 Note: RE46992 did not appear to operate correctly, it was showing closed up untill 0959, but the down stream, reclosers had lost volts and aux supplies. PT12154 to restored 1500 Monday 5/9/16 See 1421592,3,4,5 Exclude 1420310,1420376 | September | 2016 | 2017Q1 | 2017 | ZN12630:PA23 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2016-09-02 | N | 137.7882 | N | 3 | N | N | 1.1101 | 39.4971 | 25676.3525
[7 empty] | 10332 | 20025 | 1421212 | 2016-09-06 02:50 | 2016-09-06 05:00 | 130 | 11kV | 5330 | 41 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa17 PT11294 Wendy Coolarn, 2xBlown HDO 31Amp centre and footpath phases Cause not ascertained See 1421608 exclude 1421212,4 | September | 2016 | 2017Q1 | 2017 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | OH | Veg | 2016-09-06 | N | 130 | N | 2 | N | N | 1.1101 | 39.4971 | 3895.0068
[7 empty] | 9230 | 6830 | 1421460 | 2016-09-06 18:58 | 2016-09-06 23:00 | 242 | 11kV | 120993 | 1493 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn901 Surry Hills - Pnl.18 tripped on: A phase Overcurrent and EFI Field EFIs: S1424, S63966, S3565, S2719, S36057, S5240 UG cable fault from S1016 PMG Redferen St (Tx 1) to S112 Renwick St See 1421514 1421515 GIS: 1421465 | September | 2016 | 2017Q1 | 2017 | ZN901:PA18 | ZN901:PA38 | ZN00901/000038 | SYDNEY | UG | Not Veg | 2016-09-06 | N | 81.0402 | N | 2 | N | N | 1.1101 | 39.4971 | 88418.1157
[7 empty] | 8896 | 2738 | 1421703 | 2016-09-07 23:41 | 2016-09-08 01:05 | 84 | 11kV | 211680 | 2520 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S10999 Kogarah Panel 24 tripped on IOC, EFI Cause: Bat on OH | September | 2016 | 2017Q1 | 2017 | ZN10999:PA24 | ZN10999:PA24 | ZN10999/000024 | GEORGES RIVER | OH | Not Veg | 2016-09-07 | N | 84 | N | 1 | N | N | 1.1101 | 39.4971 | 154689.5005
[7 empty] | 9116 | 5542 | 1421706 | 2016-09-08 01:51 | 2016-09-08 09:00 | 429 | 11kV | 57506 | 748 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn630 Mascot Pnl.24 tripped on: Earth Fault & EFI Field EFIs: S8459, S49580, S7766, S64258, S7937, S635 UG cable fault from S635 Morley Ave to S8224 Morley Botany Incorrect labelling at S635 Sw/A & Sw/B transposed. Also no access to S635 at night resulting in delay in restoration. See 1421935 1421936 1421937 | September | 2016 | 2017Q1 | 2017 | ZN630:PA24 | ZN630:PA24 | ZN00630/000024 | SYDNEY | UG | Not Veg | 2016-09-08 | N | 76.8797 | N | 6 | N | N | 1.1101 | 39.4971 | 42023.6887
[7 empty] | 10012 | 16206 | 1421714 | 2016-09-08 07:09 | 2016-09-08 09:15 | 126.4667 | 11kV | 9105.6 | 72 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 168622 C Phase DOLF : 31 Amp DOLF fuse carrier replaced burnt up. Excluded OMS 1421719 | September | 2016 | 2017Q1 | 2017 | 242:81538 | 242:81538 | ZN00242/081538 | PORT STEPHENS | OH | Not Veg | 2016-09-08 | N | 126.4667 | N | 6 | N | N | 1.1101 | 39.4971 | 6654.1039
[7 empty] | 9628 | 11542 | 1421826 | 2016-09-08 13:45 | 2016-09-08 14:07 | 22 | 11kV | 44 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 168633 FULL ISOLATION REQUIRED TO FIX TAPPING LIVE LINE. Custoemrs already had low volts due to burnt off tapping at 11kV link 41256.. | September | 2016 | 2017Q1 | 2017 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2016-09-08 | N | 22 | N | 6 | N | N | 1.1101 | 39.4971 | 32.1539
[7 empty] | 9710 | 12394 | 1421824 | 2016-09-08 13:39 | 2016-09-08 14:55 | 76.0167 | 11kV | 1520.3333 | 20 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168635 Isolated for safety to remove overhanging tree at pole HU-90065. | September | 2016 | 2017Q1 | 2017 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2016-09-08 | N | 76.0167 | N | 6 | N | N | 1.1101 | 39.4971 | 1111.0148
[7 empty] | 9109 | 5468 | 1421872 | 2016-09-08 17:00 | 2016-09-08 18:45 | 105 | 11kV | 210 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168636 C Phase DOLF : 10 Amp Excluded OMS 1421872 | September | 2016 | 2017Q1 | 2017 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2016-09-08 | N | 105 | N | 6 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 9896 | 14792 | 1421906 | 2016-09-08 21:27 | 2016-09-08 23:15 | 107.5667 | 11kV | 6238.8667 | 58 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168637 A Phase DOLF : 20 Amp | September | 2016 | 2017Q1 | 2017 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2016-09-08 | N | 107.5667 | N | 6 | N | N | 1.1101 | 39.4971 | 4559.1797
[7 empty] | 9948 | 15281 | 1422037 | 2016-09-09 16:12 | 2016-09-09 21:00 | 288 | 11kV | 23912 | 108 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Panel 1 RE44602 Ourimbah Ck Rd opened and locked out on overcurrent and earth fault Tree Branch brought down OH. Outside 296 Ourimbah Creek Rd See 1422402,3 exclude 1422037,8,40,61 | September | 2016 | 2017Q1 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2016-09-09 | N | 221.4074 | N | 1 | N | N | 1.1101 | 39.4971 | 17474.1843
[7 empty] | 10230 | 18861 | 1422137 | 2016-09-10 11:15 | 2016-09-10 13:15 | 120 | 11kV | 63120 | 526 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn931 Darlinghurst - pnl.22 tripped on: B phase Earth Fault, EFI UG cable fault from pnl.22 at Darlinghurst Zone to S606 Cathederal St. | September | 2016 | 2017Q1 | 2017 | ZN931:PA22 | ZN931:PA22 | ZN00931/000022 | SYDNEY | UG | Not Veg | 2016-09-10 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 46126.2343
[7 empty] | 9927 | 15075 | 1422086 | 2016-09-10 07:37 | 2016-09-10 15:20 | 463 | 11kV | 29403 | 237 | HV | Vegetation Blow/Fall In | Vegetation | O/H Link | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of pa25 Reclsoer 61082 Birieses Peats Ridge 0.3 opend and locked out on overcurrent and SEF Tree/Branch brought down OH Either side of USL44100 See 1422406,7,8,9 exclude 1422086,101 | September | 2016 | 2017Q1 | 2017 | ZN12630:PA25 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2016-09-10 | N | 124.0633 | N | 4 | N | N | 1.1101 | 39.4971 | 21486.8452
[7 empty] | 9313 | 7603 | 1422146 | 2016-09-10 12:52 | 2016-09-10 16:00 | 188 | 11kV | 564 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 168647 C Phase HV lead pulled out of top off DOLF. Excluded OMS 1422153 | September | 2016 | 2017Q1 | 2017 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2016-09-10 | N | 188 | N | 4 | N | N | 1.1101 | 39.4971 | 412.1546
[7 empty] | 9572 | 10902 | 1422192 | 2016-09-10 16:59 | 2016-09-10 18:20 | 81 | 11kV | 49566 | 706 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | At ZN10997 Sans Souci Panel 11 'Russel Av' feeder has tripped Signals: 11kv trip, No.1 GE Relays: Aph IOC, EF, FC, REC timer, LO, EFI Field EFI's: S10454, S10290, S10103 Remarks: Suspected UG Fault between Sw/B @ S10103 Plimsoll Nelson and Sw/A @ Sub 10154 Wellington Plimsoll | September | 2016 | 2017Q1 | 2017 | ZN10997:PA11 | ZN10997:PA11 | ZN10997/000011 | GEORGES RIVER | UG | Not Veg | 2016-09-10 | N | 70.2068 | N | 4 | N | N | 1.1101 | 39.4971 | 36221.3709
[7 empty] | 9424 | 9115 | 1422227 | 2016-09-11 09:07 | 2016-09-11 11:20 | 133 | 11kV | 133 | 1 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 168650 Ground stay wire broken to pole BN-70090. Excluded OMS No. 1422227 | September | 2016 | 2017Q1 | 2017 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2016-09-11 | N | 133 | N | 4 | N | N | 1.1101 | 39.4971 | 97.1925
[7 empty] | 10246 | 18991 | 1422215 | 2016-09-11 02:27 | 2016-09-11 12:50 | 623 | 11kV | 79093 | 716 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn10993 Hurstville North - Pnl.33 tripped on: 51ABC (Overcurrent), Lockout, EFI Field EFIs: S10664, S10072 Ex Pnl.35 - S10636 Vanessa The Crescent 1 - Dist #3 - All phase fuses blown Car hit pole on corner of Vanessa St and The Crescent (Adjacent LK30416) snapping pole and HV wires. HV wires came into contact with LV mains at S10636 Dist 3 See 1422549 1422550 | September | 2016 | 2017Q1 | 2017 | ZN10993:PA33 | ZN10993:PA33 | ZN10993/000033 | GEORGES RIVER | OH | Not Veg | 2016-09-11 | N | 110.4651 | N | 4 | N | N | 1.1101 | 39.4971 | 57798.8316
[7 empty] | 9232 | 6848 | 1422253 | 2016-09-11 16:03 | 2016-09-11 17:50 | 107 | 11kV | 228671 | 2476 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill - Pnl.16 tripped on: Earth Fault and EFI Field EFIs: S3464, S3141, S2023, S1823, S4259, S1900 UG cable fault between S1900 Greenhills St (Sw/B) and S482 Dickinson St (Sw/B) tee S1551 Highbury St (Sw/A) See 1422558 1422559 GIS: 1422254 | September | 2016 | 2017Q1 | 2017 | ZN398:PA16 | ZN398:PA16 | ZN00398/000016 | INNER WEST | UG | Not Veg | 2016-09-11 | N | 92.355 | N | 4 | N | N | 1.1101 | 39.4971 | 167106.0221
[7 empty] | 8747 | 633 | 1422269 | 2016-09-11 19:01 | 2016-09-11 22:28 | 207 | 11kV | 207 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 168652 Single phase LL Lead pulled out of DOLF Excluded OMS 1422269 | September | 2016 | 2017Q1 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2016-09-11 | N | 207 | N | 4 | N | N | 1.1101 | 39.4971 | 151.2695
[7 empty] | 9555 | 10728 | 1422410 | 2016-09-12 12:29 | 2016-09-12 13:45 | 76 | 11kV | 106213 | 1411 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn80 Chatswood Panel 25 Murray Ralston tripped on Relays: Earth Fault and EFI, Fault Check, Timing and Lockout, TX11 Fault Check Relay Signals: TX11 Grioup Earth, Zone Earth and 11kV Trip Cause: Crane Hit at worksite hit 11kV OH mains in Gordon Crescent See OMS 1422707 1422708 | September | 2016 | 2017Q1 | 2017 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Not Veg | 2016-09-12 | N | 75.275 | N | 3 | N | N | 1.1101 | 39.4971 | 77617.3276
[7 empty] | 9248 | 6972 | 1422365 | 2016-09-12 11:06 | 2016-09-12 17:55 | 409 | 11kV | 1227 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 168661 single phase Replaced 11kV to top of DOLF. While on site found 11kV OHM stranding near sub See report 168662 Excluded OMS 1422365 | September | 2016 | 2017Q1 | 2017 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2016-09-12 | N | 409 | N | 3 | N | N | 1.1101 | 39.4971 | 896.6554
[7 empty] | 9825 | 13876 | 1422538 | 2016-09-12 16:05 | 2016-09-12 17:55 | 110 | 11kV | 1980 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 168662 Section isolated to repair stranding on OHM near sub 1324. See report 168661. Excluded OMS 1422365 | September | 2016 | 2017Q1 | 2017 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2016-09-12 | N | 110 | N | 3 | N | N | 1.1101 | 39.4971 | 1446.9256
[7 empty] | 10009 | 16177 | 1422537 | 2016-09-13 08:18 | 2016-09-13 10:00 | 102 | 11kV | 102 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168667 Single phase DOLF : 10 Amp Excluded OMS 1422537 | September | 2016 | 2017Q1 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2016-09-13 | N | 102 | N | 2 | N | N | 1.1101 | 39.4971 | 74.5386
[7 empty] | 10105 | 17287 | 1422755 | 2016-09-13 20:01 | 2016-09-13 21:03 | 62 | 11kV | 3949 | 77 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 matraville Pnl.7 tripped on: B phase earth fault, EFI Field EFIs: S63510, S65311, S35094, S4678 UG cable fault between S4678 Brighton Stephen (Sw/A) and S2874 McPherson Ex (Sw/B) See 1422790 1422792 | September | 2016 | 2017Q1 | 2017 | ZN1788:PA7 | ZN1788:PA67 | ZN01788/000067 | BAYSIDE | UG | Not Veg | 2016-09-13 | N | 51.2857 | N | 2 | N | N | 1.1101 | 39.4971 | 2885.8127
[7 empty] | 10093 | 17186 | 1423027 | 2016-09-15 10:03 | 2016-09-15 12:15 | 132 | 11kV | 76090 | 758 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S1068 Lidcombe Panel 27 "Queen Marion" fdr tripped Relays - Earth fault, EFI Signals - 11kv trip, Tx1 Group Earth, Zone Earth EFI's - S1544 Abnormal: S524 Beatrice St Sw/C open and defective. S8641 Sw/B closed Remarks: UG fault. Appears to be 2 ug faults. Front line panel 27 and the previously repaired section of 11kv fdr from S1544 to S8466 to S524 both failed independantly on energising. | September | 2016 | 2017Q1 | 2017 | ZN1068:PA27 | ZN1068:PA27 | ZN01068/000027 | CUMBERLAND | UG | Not Veg | 2016-09-15 | N | 100.3826 | N | 5 | N | N | 1.1101 | 39.4971 | 55604.3277
[7 empty] | 8968 | 3646 | 1423066 | 2016-09-15 11:33 | 2016-09-15 12:15 | 42 | 11kV | 17472 | 416 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 168687 1 fault operation C phase Earth Fault faulty section 81991/15910 isolated & AP left | September | 2016 | 2017Q1 | 2017 | 257:81991 | 257:81991 | ZN00257/081991 | NEWCASTLE | OH | Veg | 2016-09-15 | N | 42 | N | 5 | N | N | 1.1101 | 39.4971 | 12768.0223
[7 empty] | 8995 | 3924 | 1423097 | 2016-09-15 13:02 | 2016-09-15 15:12 | 130 | 11kV | 30810 | 237 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn2400 Berowra section of Pa21 "Yallambee Pacific" Recloser 3202 Pacific Sth Cowan tripped on overcurrent Cause not asertained. Patrolled by DOp | September | 2016 | 2017Q1 | 2017 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Veg | 2016-09-15 | N | 130 | N | 5 | N | N | 1.1101 | 39.4971 | 22515.0393
[7 empty] | 9120 | 5606 | 1423092 | 2016-09-15 12:42 | 2016-09-15 15:35 | 173 | 11kV | 9233 | 89 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168691 3 fault operations B & C phase Overcurrent TREE ON 11KV MAINS AT POLE GR-40001. Excluded OMS 1423092 & 1423103 | September | 2016 | 2017Q1 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | OH | Veg | 2016-09-15 | N | 103.7416 | N | 5 | N | N | 1.1101 | 39.4971 | 6747.2041
[7 empty] | 10049 | 16546 | 1423166 | 2016-09-15 16:38 | 2016-09-15 20:35 | 237 | 11kV | 948 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168696 B phase LIVE LINE LEAD TO TOP OF DOLF BROKEN. Excluded OMS 1423166 | September | 2016 | 2017Q1 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2016-09-15 | N | 237 | N | 5 | N | N | 1.1101 | 39.4971 | 692.7704
[7 empty] | 9944 | 15269 | 1423202 | 2016-09-16 04:42 | 2016-09-16 05:28 | 46 | 11kV | 31556 | 686 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15001 Brookvale Panel 8 tripped on Relays: A and C phase Overcurrent Signals: 11kV Trip with EFI Cause: Possum found at the base of pole O/S 196 AHeadland Rd See OMS 1423202 1423204 | September | 2016 | 2017Q1 | 2017 | ZN15001:PA8 | ZN15001:PA8 | ZN15001/000008 | NORTHERN BEACHES | OH | Not Veg | 2016-09-16 | N | 46 | N | 1 | N | N | 1.1101 | 39.4971 | 23060.1941
[7 empty] | 9830 | 13936 | 1423488 | 2016-09-18 08:10 | 2016-09-18 11:05 | 175 | 11kV | 1020 | 6 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168717/01 B & C phase DOLF : 10 Amp Outage caused by bird contacting mains blowing both line and sub fuses. | September | 2016 | 2017Q1 | 2017 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Not Veg | 2016-09-18 | N | 170 | N | 3 | N | N | 1.1101 | 39.4971 | 745.3859
[7 empty] | 8814 | 1615 | 1423481 | 2016-09-18 04:10 | 2016-09-18 15:10 | 660 | 11kV | 10560 | 16 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 168714 car into pole JR-25091, no protection operation, fdr isolated to make repairs. | September | 2016 | 2017Q1 | 2017 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Not Veg | 2016-09-18 | N | 660 | N | 3 | N | N | 1.1101 | 39.4971 | 7716.9365
[7 empty] | 10238 | 18922 | 1423543 | 2016-09-18 17:11 | 2016-09-18 18:27 | 76 | 11kV | 97586 | 1355 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | LID 168719 2 fault operations B & C phase Overcurrent FAULTY UGOH AT POLE HQ-83704. TARGETS SW 29876 50TBC. NOTE. ABS 25959 CANNOT BE USED FOR AN ISOLATION POINT.(NOT OPENING FAR ENOUGH) | September | 2016 | 2017Q1 | 2017 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | Unknown | Unknown | 2016-09-18 | N | 72.0192 | N | 3 | N | N | 1.1101 | 39.4971 | 71312.9705
[7 empty] | 10007 | 16130 | 1423573 | 2016-09-19 00:10 | 2016-09-19 02:21 | 131 | 11kV | 63152 | 614 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 168720 3 fault operations A & B phase Overcurrent fdr sectionalised no fault found Excluded oms 1423573 | September | 2016 | 2017Q1 | 2017 | 801:74120 | 801:74120 | ZN00801/074120 | MUSWELLBROOK | OH | Veg | 2016-09-19 | N | 102.8534 | N | 2 | N | N | 1.1101 | 39.4971 | 46149.6189
[7 empty] | 9934 | 15158 | 1423589 | 2016-09-19 06:54 | 2016-09-19 12:20 | 326 | 11kV | 41538 | 428 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa25 "Somersby" IR61084 Bushells Peats 0.2 tripped & locked out Relays: OC trip, SEF, Lockout SEF detection @ LB61085 (supervisory control) Abnormal: Closed AB40570 to Panel 23 labelled "Mangrove Mountain" Open AB44889 Eagle on 11kv Mains between LB42326 & AB43090 tee PT13225 See 1423967,70,1,2 Exclude 1423589,94,657 | September | 2016 | 2017Q1 | 2017 | ZN12630:PA23 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2016-09-19 | N | 97.0514 | N | 2 | N | N | 1.1101 | 39.4971 | 30354.7452
[7 empty] | 9272 | 7202 | 1423884 | 2016-09-20 04:31 | 2016-09-20 06:11 | 100 | 11kV | 310400 | 3104 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Panel 16 AB phase dipped below low volts threshold down to 56 volts Zn12610 Long Jetty Panel 6 AB phase dipped below low volts threshold down to 56 volts Fire Brigade Report Pole on fire BV4653 See 1423884,4276 Exclude 1423887,8,9,90,1,2,3,4 CC1: 22-"Refer to SOp" | September | 2016 | 2017Q1 | 2017 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Not Veg | 2016-09-20 | N | 100 | N | 2 | N | N | 1.1101 | 39.4971 | 226831.1647
[7 empty] | 9138 | 5869 | 1424265 | 2016-09-20 06:11 | 2016-09-20 06:25 | 14 | 11kV | 19245 | 4104 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Panel 6 "Rohdin Drive" tripped on Relays: SEL trip alarm, OC EF EFI Signals: 11kv trip Zn12610 Long Jetty Panel 22 "Shelly Beach" tripped on Relays: SEL trip alarm, OC EF Check & EFI Signals: 11kv trip Abnormal: AB40909 Open and AB40824 Closed 11kV UGOH Fault Open/Short circuit front line of Panel 6 See 1424265,6,7 | September | 2016 | 2017Q1 | 2017 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | Unknown | Unknown | 2016-09-20 | N | 4.6893 | N | 2 | N | N | 1.1101 | 39.4971 | 14063.6784
[7 empty] | 9898 | 14812 | 1424120 | 2016-09-21 03:53 | 2016-09-21 07:35 | 222 | 11kV | 138896 | 1144 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn3472 Sefton 11kv OCB panel 8 "PT1943" tripped on - Relays - fault check, EFI, earth fault Field EFI's: S6200, 7035, 1921, 2907 Signals: 11kv trip Remarks: UG fault. 11kv feeder fault between S2907 Sw/B cornwell rd and S1969 Sw/B richmond rd. Sw tag left only at S1969. HAZ sw at S2907 feeder requires extension regions to organise | September | 2016 | 2017Q1 | 2017 | ZN3472:PA8 | ZN3472:PA8 | ZN03472/000008 | CUMBERLAND | UG | Not Veg | 2016-09-21 | N | 121.4126 | N | 4 | N | N | 1.1101 | 39.4971 | 101501.1001
[7 empty] | 9102 | 5363 | 1424219 | 2016-09-21 12:58 | 2016-09-21 15:00 | 122 | 11kV | 244 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168737 A Phase DOLF : 10 Amp Excluded OMS 1424219 | September | 2016 | 2017Q1 | 2017 | 509:33397 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Veg | 2016-09-21 | N | 122 | N | 4 | N | N | 1.1101 | 39.4971 | 178.308
[7 empty] | 8810 | 1579 | 1424236 | 2016-09-21 14:12 | 2016-09-21 15:41 | 89 | 11kV | 43467 | 530 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2835 Burwood 11kv Pnl33 "Franklyn Parramatta" feeder tripped on earth fault with fault check Signals: 11kv trip, Tx 3 Group and Zone earth Field EFI's: Pnl 9 to Sub 8494 Remarks: UG Fault. Cable fault between S8494 George Allen #1 to Sub 1485 Arnott to Sub 1531 George Beronga | September | 2016 | 2017Q1 | 2017 | ZN2835:PA33 | ZN2835:PA33 | ZN02835/000033 | STRATHFIELD | UG | Not Veg | 2016-09-21 | N | 82.0132 | N | 4 | N | N | 1.1101 | 39.4971 | 31764.4015
[7 empty] | 10022 | 16283 | 1424242 | 2016-09-21 18:50 | 2016-09-21 22:35 | 225 | 11kV | 450 | 2 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of Pa6 between RE44948 Myoora Somersby 0.1 to LB62393 tee PT12677 & PT49999 interrutped to allow linesman to replace broken LV cross arm at PT49999 LV service was struck by excavator snapping LV Cross Arm at PT49999. Arm was within clearances of 11kv | September | 2016 | 2017Q1 | 2017 | ZN14143:PA6 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | OH | Not Veg | 2016-09-21 | N | 225 | N | 4 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 9399 | 8782 | 1424527 | 2016-09-22 08:30 | 2016-09-22 16:10 | 460 | 11kV | 5600 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Planned LID 168743 SINO 15968 | September | 2016 | 2017Q1 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2016-09-22 | N | 400 | N | 2 | N | N | 1.1101 | 39.4971 | 4092.3148
[7 empty] | 10000 | 15971 | 1424487 | 2016-09-22 17:55 | 2016-09-22 19:07 | 72 | 11kV | 50688 | 704 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 paddington - Pnl.35 tripped on: Earth Fault & EFI on 35L Field EFIs: NIL UG cable fault from Pnl.35 to S4371 Clement Waratah to S1681 new South Rushcutters. | September | 2016 | 2017Q1 | 2017 | ZN342:PA35 | ZN342:PA35 | ZN00342/000035 | SYDNEY | UG | Not Veg | 2016-09-22 | N | 72 | N | 2 | N | N | 1.1101 | 39.4971 | 37041.2954
[7 empty] | 9560 | 10801 | 1424605 | 2016-09-23 14:13 | 2016-09-23 15:22 | 69 | 11kV | 19113 | 277 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S14144 Wamberal Panel 5 tripped reclosed tripped and locked out on Relays: 51BC, Reclose Lockout. Cause: Feeder patrolled and both hazard reports investigated. Cuase not ascertained. See OMS 1424605 1424606 1424609 | September | 2016 | 2017Q1 | 2017 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2016-09-23 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 13967.2167
[7 empty] | 9802 | 13651 | 1424611 | 2016-09-23 14:42 | 2016-09-23 16:25 | 103 | 11kV | 5253 | 51 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT11738 Bundilla Wyong Panel 19 Centre phase HDO blew due to fatigue. Cause: Fuse fatigue See OMS 1425519 1424628 1424611 | September | 2016 | 2017Q1 | 2017 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Not Veg | 2016-09-23 | N | 103 | N | 3 | N | N | 1.1101 | 39.4971 | 3838.7375
[7 empty] | 9905 | 14849 | 1424668 | 2016-09-23 19:31 | 2016-09-23 21:00 | 89 | 11kV | 8811 | 99 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15013 Terrey Hills Panel 8 "Mona Vale Myoora" tripped and reclosed and locked out on Relays: IOC, Timed Overcurrent C phase, Reclose Timer, Fault Check, Fault Check, Fault CHeck Tx2 and EFI Signals: 11kv trip and Zone Earth EFI's S16961 S15264 UG Cable Fault. 11kv fdr fault from S15264 National Panasonic Sw D to S16814 Narabang Way 13 SwA N/O to S16597 Narabang Way 7 Sw B N/O | September | 2016 | 2017Q1 | 2017 | ZN15013:PA8 | ZN15013:PA8 | ZN15013/000008 | NORTHERN BEACHES | UG | Not Veg | 2016-09-23 | N | 89 | N | 3 | N | N | 1.1101 | 39.4971 | 6438.8189
[7 empty] | 9508 | 10040 | 1424760 | 2016-09-24 23:16 | 2016-09-25 00:44 | 88 | 11kV | 102376 | 1165 | HV | Arcing | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn1287 Revesby 11kv feeder Panel No.24 "S61162" feeder tripped Relays: A phase timed O/C Signals: 11kv trip Field EFIs: Nil Remarks: flashover/arcing. Flashover at UGOH to PT1553 English St by fuit bat, removed clear by DOp | September | 2016 | 2017Q1 | 2017 | ZN1287:PA24 | ZN1287:PA24 | ZN01287/000024 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-09-24 | N | 87.8764 | N | 1 | N | N | 1.1101 | 39.4971 | 74813.3612
[7 empty] | 9988 | 15835 | 1424770 | 2016-09-25 05:15 | 2016-09-25 18:45 | 810 | 11kV | 32860 | 1309 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn10996 Rockdale - Pnl.12 tripped and reclosed on: Overcurrent and Earth fault. Field EFIs: S10401 and S10402 PT10779 Tancred General Holmes - Dist #2 - All phases off as per EMSO comments. No information provided from Control Room in regards to Distributor outage. Cause: Vehicle hit pole and was broken between LB31116 and S10402 See 1424971 1424972 | September | 2016 | 2017Q1 | 2017 | ZN10996:PA10 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Not Veg | 2016-09-25 | N | 25.1031 | N | 1 | N | N | 1.1101 | 39.4971 | 24013.1188
[7 empty] | 8962 | 3568 | 1424941 | 2016-09-26 10:58 | 2016-09-26 15:07 | 249 | 11kV | 11703 | 47 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 168768 1 fault operation 3 phase Overcurrent broken xarm sub 70829 section isolated for repairs | September | 2016 | 2017Q1 | 2017 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2016-09-26 | N | 249 | N | 1 | N | N | 1.1101 | 39.4971 | 8552.2072
[7 empty] | 9000 | 3958 | 1425302 | 2016-09-27 12:15 | 2016-09-27 13:45 | 90 | 11kV | 180 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 168776 No protection operated broken earth wire at pole JT-62048 required an isolation and interruption to allow repairs. | September | 2016 | 2017Q1 | 2017 |  |  |  | NEWCASTLE | OH | Not Veg | 2016-09-27 | N | 90 | N | 5 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 8866 | 2318 | 1425181 | 2016-09-27 15:02 | 2016-09-27 16:55 | 113 | 11kV | 565 | 5 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 168786 A Phase LLC broken away in wind. | September | 2016 | 2017Q1 | 2017 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2016-09-27 | N | 113 | N | 5 | N | N | 1.1101 | 39.4971 | 412.8853
[7 empty] | 9983 | 15762 | 1425238 | 2016-09-27 17:41 | 2016-09-27 21:55 | 254 | 11kV | 1016 | 4 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 168790 A Phase LLC broken in wind | September | 2016 | 2017Q1 | 2017 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2016-09-27 | N | 254 | N | 5 | N | N | 1.1101 | 39.4971 | 742.4628
[7 empty] | 10272 | 19236 | 1425117 | 2016-09-27 11:56 | 2016-09-27 22:15 | 619 | 11kV | 62018 | 692 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | No Weather Impact | N | Zn14891 Wyong Pa12 "Yarramalong" fdr tripped, reclosed, tripped & locked out on relays: Bassler 51BC EFI, EF Check, SE, reclose timing /lockout Signals: Tx2 GE ABNORMAL: USL44828 Open for DAROS 3960545 (carded interruptions) Tree fell down braking X-arms @ 138 Yarramalong rd wyong creek causing large fire in paddocks See 1425795,7,8 Exclude 1425117,21,4,47,68 | September | 2016 | 2017Q1 | 2017 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2016-09-27 | N | 89.6214 | N | 5 | N | N | 1.1101 | 39.4971 | 45320.9252
[7 empty] | 10296 | 19524 | 1425243 | 2016-09-27 17:52 | 2016-09-28 01:00 | 428 | 11kV | 856 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168792 Single phase DOLF : 3 Amp | September | 2016 | 2017Q1 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-09-27 | N | 428 | N | 5 | N | N | 1.1101 | 39.4971 | 625.5396
[7 empty] | 10268 | 19206 | 1425598 | 2016-09-29 14:32 | 2016-09-29 14:54 | 22 | 11kV | 1731 | 93 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 168813 Overcurrent excluded OMS 1425598 | September | 2016 | 2017Q1 | 2017 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2016-09-29 | N | 18.6129 | N | 2 | N | N | 1.1101 | 39.4971 | 1264.9637
[7 empty] | 9645 | 11721 | 1425600 | 2016-09-29 14:31 | 2016-09-29 16:24 | 113 | 11kV | 172801 | 1812 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn931 Darlinghurst the 11kv Panel 10 "Tewkesbury Darlinghurst" CB tripped on: Signals: 11kv trip, zone earth, Tx4 group earth Relays: B phase Earth fault, fault check relay, Earth fault indicator Field EFi's: S48459 Tewkesbury Darlinghurst, S7939 Kirketon Farrell, CP603 Kings Cross Tunnel Remarks: UG fault. There is an underground fault on the 11kv feeder fed from Zn931 Darlinghurst - Panel 10 between CP 603 Kings Cross Tunnel "Sw D" & S5224 St Peteres Bourke "Sw A" & S8599 William Craigend "SwB" | September | 2016 | 2017Q1 | 2017 | ZN931:PA10 | ZN931:PA10 | ZN00931/000010 | SYDNEY | UG | Not Veg | 2016-09-29 | N | 95.3648 | N | 2 | N | N | 1.1101 | 39.4971 | 126277.874
[7 empty] | 9829 | 13930 | 1425711 | 2016-09-30 04:25 | 2016-09-30 06:06 | 101 | 11kV | 9393 | 93 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168815 B phase DOLF : 20 Amp POSSUM FOUND AT SUB POLE. Excluded OMS 1425711, 1425714 | September | 2016 | 2017Q1 | 2017 | 205:12210 | 205:12210 | ZN00205/012210 | NEWCASTLE | OH | Not Veg | 2016-09-30 | N | 101 | N | 3 | N | N | 1.1101 | 39.4971 | 6864.1274
[7 empty] | 9021 | 4237 | 1425762 | 2016-09-30 09:42 | 2016-09-30 12:15 | 153 | 11kV | 765 | 5 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 168825 3 phase DOLF : 10 Amp Customer advises "no power after lighting strike (not sure where it was)" | September | 2016 | 2017Q1 | 2017 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2016-09-30 | N | 153 | N | 3 | N | N | 1.1101 | 39.4971 | 559.0394
[7 empty] | 8870 | 2396 | 1425809 | 2016-09-30 12:25 | 2016-09-30 13:20 | 55 | 11kV | 55 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 168830 A phase DOLF : 10 Amp | September | 2016 | 2017Q1 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2016-09-30 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 40.1924
[7 empty] | 9152 | 6023 | 1426074 | 2016-10-01 11:07 | 2016-10-01 12:44 | 97 | 11kV | 119601 | 1233 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S2635 Epping Panel 57 tripped reclosed tripped and locked out on Relays: A and B phase IOC and Lockout Signals: Substation protetcion trip, TX2 Cooling Fail Cause: Tree branch on OH mains See OMS 1426074 1426079 | October | 2016 | 2017Q2 | 2017 | ZN2635:PA57 | ZN2635:PA57 | ZN02635/000057 | PARRAMATTA | OH | Veg | 2016-10-01 | N | 97 | N | 3 | N | N | 1.1101 | 39.4971 | 87400.8832
[7 empty] | 9067 | 4973 | 1426156 | 2016-10-01 15:15 | 2016-10-01 15:21 | 6 | 11kV | 9726 | 1621 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | ZN12570 Avoca Ex.panel 24 "Woodfield Waldron", de-energised from LB.42288 to remove tree branch. LB.42288 opened momentarily to remove branch on OH mains. ME:1426954 Withdrawn:1426156 | October | 2016 | 2017Q2 | 2017 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2016-10-01 | N | 6 | N | 3 | N | N | 1.1101 | 39.4971 | 7107.4739
[7 empty] | 8958 | 3487 | 1426175 | 2016-10-01 16:33 | 2016-10-01 17:50 | 77 | 11kV | 77 | 1 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168841 Repair broken dropper lead to DOLF Excluded OMS 1426175 | October | 2016 | 2017Q2 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2016-10-01 | N | 77 | N | 3 | N | N | 1.1101 | 39.4971 | 56.2693
[7 empty] | 9546 | 10573 | 1426254 | 2016-10-02 17:30 | 2016-10-02 18:15 | 45 | 11kV | 4680 | 104 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 168846 No protection operation. 11kV main on xarm pole SW-40028 section isolated for repairs. Excluded OMS 1426254 | October | 2016 | 2017Q2 | 2017 | 239:82129 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2016-10-02 | N | 45 | N | 2 | N | N | 1.1101 | 39.4971 | 3420.006
[7 empty] | 9722 | 12615 | 1426281 | 2016-10-02 21:34 | 2016-10-02 23:40 | 126 | 11kV | 89920 | 904 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1287 Revesby the 11kv panel 12 'Tyalgum Av" feeder tripped on: Relays: Earth leakage, EFI, FC Signals: 11kv trip, Tx1 group earth, Zone earth Field EFIs: S4582, S50260, S5042, S5038, S8003 Remarks: UG fault. Suspect UG fault between S8003 Sw/B, S8587 Sw/A, S8172 SwB tee PT396 | October | 2016 | 2017Q2 | 2017 | ZN1287:PA12 | ZN1287:PA12 | ZN01287/000012 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-10-02 | N | 99.469 | N | 2 | N | N | 1.1101 | 39.4971 | 65710.8838
[7 empty] | 10041 | 16497 | 1426371 | 2016-10-03 16:44 | 2016-10-03 18:55 | 131 | 11kV | 98186 | 750 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn35370 Galston Panel 4 tripped, reclosed tripped and locked out on A and B phase IOC, Lockout, EFI Signals: 11kV Trip Cause: Feeder patrolled - No cause found See OMS 1426841 1426842 1426373 1426371 | October | 2016 | 2017Q2 | 2017 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2016-10-03 | N | 130.9147 | N | 3 | N | N | 1.1101 | 39.4971 | 71751.4328
[7 empty] | 9110 | 5488 | 1426418 | 2016-10-03 21:44 | 2016-10-03 22:28 | 44 | 11kV | 119856 | 2724 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN10999 Kograh 11kV panel 12 "Queen vic Washington,etc" feeder tripped, relcosed, tripped and locked out on: B & C phase IOC, reclose lockout Tree/ branch on OH mains - branch fell off, mains appear undamaged. ME:1426418 Withdrawn:1426422, 1426419 | October | 2016 | 2017Q2 | 2017 | ZN10999:PA12 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | OH | Veg | 2016-10-03 | N | 44 | N | 3 | N | N | 1.1101 | 39.4971 | 87587.2296
[7 empty] | 10060 | 16680 | 1426381 | 2016-10-03 17:12 | 2016-10-03 23:20 | 368 | 11kV | 240858 | 1580 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | At Zn2196 Milperra Panel 5 'Sub 8696' feeder has tripped Signals: 11kv trip, ZE Relays: B & C phase OC, EFI, FC, LO Remarks: UG fault. Possible fault between IS3265, AB2801, Sw/A @ Sub 8239, Sw/B @ S8990. Section of 11kv has two UGOH's unable to ascertain which on is defective due to no EFI | October | 2016 | 2017Q2 | 2017 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-10-03 | N | 152.4418 | N | 3 | N | N | 1.1101 | 39.4971 | 176011.9223
[7 empty] | 9604 | 11313 | 1426562 | 2016-10-04 11:07 | 2016-10-04 12:29 | 82 | 11kV | 126333 | 1594 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S2635 Epping Panel 31 Tripped on Relays: C phase Timed, Instant Earth Fault, EFI Cause: 11kV UG fault between S49276 to S4627 - Contractor (Arise Constructions) damaged cable - between 3 and 5 Cliff Rd Epping See OMS 1427787 1427789 1426646 1426562 | October | 2016 | 2017Q2 | 2017 | ZN2635:PA31 | ZN2635:PA31 | ZN02635/000031 | PARRAMATTA | UG | Not Veg | 2016-10-04 | N | 79.2553 | N | 8 | N | N | 1.1101 | 39.4971 | 92320.4302
[7 empty] | 9514 | 10149 | 1426610 | 2016-10-04 13:09 | 2016-10-04 13:50 | 41.4 | 11kV | 16808.4 | 406 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of Pa6 "Krone Enterprise" IR44444 Geoffrey Royle 0.1 tripped, reclosed and locked out on: OC trip A tree branch fell on the 11kv OH outside 81 Geoffrey Rd Chittaway Bay See 1426610 exclude 1426617,22 CC1: 22-"Refer to SOp" | October | 2016 | 2017Q2 | 2017 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Veg | 2016-10-04 | N | 41.4 | N | 8 | N | N | 1.1101 | 39.4971 | 12283.083
[7 empty] | 10208 | 18636 | 1426598 | 2016-10-04 12:42 | 2016-10-04 14:50 | 128 | 11kV | 128 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168866 B Phase Broken Bph LLC dropper Excluded oms 1426598 | October | 2016 | 2017Q2 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-10-04 | N | 128 | N | 8 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 9084 | 5228 | 1426716 | 2016-10-04 17:20 | 2016-10-04 17:55 | 35 | 11kV | 8400 | 240 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | section of 11kv feeder beyod AB31329. Ex panel 1 "Woids Ave" fdr Remarks: Bond. Roadside bond off at AB31329 | October | 2016 | 2017Q2 | 2017 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2016-10-04 | N | 35 | N | 8 | N | N | 1.1101 | 39.4971 | 6138.4722
[7 empty] | 9495 | 9896 | 1426730 | 2016-10-04 18:20 | 2016-10-04 20:05 | 105 | 11kV | 44310 | 422 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Section of 11kv feeder beyond S.10718 ex Panel 12 "Wickham St" feeder Remarks: Bond. Bond off 1st UGOH below S10718 Argyle Princes No.2 | October | 2016 | 2017Q2 | 2017 | ZN10990:PA12 | ZN10998:PA9 | ZN10998/000009 | BAYSIDE | OH | Not Veg | 2016-10-04 | N | 105 | N | 8 | N | N | 1.1101 | 39.4971 | 32380.4411
[7 empty] | 8756 | 712 | 1426728 | 2016-10-04 18:00 | 2016-10-04 20:55 | 175 | 11kV | 2800 | 16 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168867 Broken Live Line Dropper Excluded oms 1426725 | October | 2016 | 2017Q2 | 2017 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2016-10-04 | N | 175 | N | 8 | N | N | 1.1101 | 39.4971 | 2046.1574
[7 empty] | 10260 | 19094 | 1426784 | 2016-10-04 19:46 | 2016-10-05 02:40 | 414 | 11kV | 414 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 168870 Faulty ll lead Excluded OMS 1426784 | October | 2016 | 2017Q2 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2016-10-04 | N | 414 | N | 8 | N | N | 1.1101 | 39.4971 | 302.539
[7 empty] | 8928 | 2982 | 1426720 | 2016-10-04 17:33 | 2016-10-05 09:05 | 932 | 11kV | 3728 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 168874 Replaced blown 10 amp A and C phace HV fuses on sub. Tx Volts: 241V Refer to OMS No. 1426720 | October | 2016 | 2017Q2 | 2017 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2016-10-04 | N | 932 | N | 8 | N | N | 1.1101 | 39.4971 | 2724.3124
[7 empty] | 9941 | 15238 | 1426824 | 2016-10-05 08:09 | 2016-10-05 12:29 | 260 | 11kV | 91670 | 1565 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 168884 1 fault operation A phase Earth Fault, Overcurrent Blown Arrestor at ugoh pole OR-30109 | October | 2016 | 2017Q2 | 2017 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2016-10-05 | N | 58.5751 | N | 3 | N | N | 1.1101 | 39.4971 | 66989.7322
[7 empty] | 9038 | 4532 | 1427029 | 2016-10-05 19:05 | 2016-10-05 19:50 | 45 | 11kV | 45 | 1 | HV | 3rd Party Action | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | N | S6629 Mary Albion - HV switch found in the off postion by DOp HV end of the kiosk filled with rucksacks and other items that were being stored. Suspected one of the items has fallen onto HV switch and turned off the transformer. Items have been removed, kiosk locked and reported to Dave Hay to check security of the lock. | October | 2016 | 2017Q2 | 2017 | ZN7900:PA14 | ZN7900:PA14 | ZN07900/000014 | SYDNEY | OH | Not Veg | 2016-10-05 | N | 45 | N | 3 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 8820 | 1704 | 1427039 | 2016-10-05 21:05 | 2016-10-05 21:57 | 52 | 11kV | 15556 | 300 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn5868 Gore Hill Panel 2 tripped on Relays: 2L Side - Earth Fault Trip, Fault Check Relay, EFI Signals: 11kV trip, TX3 Hi/Low Volts Cause: 11kV UGOH fault between S3525 and S35668 See OMS 1427690 1427692 1427039 | October | 2016 | 2017Q2 | 2017 | ZN5868:PA2 | ZN5868:PA2 | ZN05868/000002 | WILLOUGHBY | UG | Not Veg | 2016-10-05 | N | 51.8533 | N | 3 | N | N | 1.1101 | 39.4971 | 11367.866
[7 empty] | 10356 | 20293 | 1427123 | 2016-10-06 11:47 | 2016-10-06 13:15 | 88 | 11kV | 63474 | 956 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.4 tripped on: no relay indication with fault check Field EFIs: S65408 and S48559 UG cable fault from S48559 Amelia St to S7645 lachlan Sth Downling tee S4563 Murray Amelia. See 1427263 1427264 1427266 | October | 2016 | 2017Q2 | 2017 | ZN188:PA4 | ZN188:PA10 | ZN00188/000010 | SYDNEY | UG | Not Veg | 2016-10-06 | N | 66.3954 | N | 3 | N | N | 1.1101 | 39.4971 | 46384.927
[7 empty] | 9737 | 12849 | 1427135 | 2016-10-06 12:29 | 2016-10-06 13:50 | 81 | 11kV | 81 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168901 B Phase DOLF : 10 Amp Excluded OMS 1427135 | October | 2016 | 2017Q2 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-10-06 | N | 81 | N | 3 | N | N | 1.1101 | 39.4971 | 59.1924
[7 empty] | 9056 | 4815 | 1427216 | 2016-10-06 21:07 | 2016-10-06 23:45 | 158 | 11kV | 474 | 3 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 168904 two phases of a section of 11kV OHM stolen between poles IU-30135 & IU-30136. No protection trip reported by passer by. No load loss as mains go to N/O point 4661. Interuption to make safe as dead side mains within reach. Please note that this is in bush off Newcastle link rd. There are 3 spans of OHM that are deenergised on 2 phases that could be stolen at any time. Please repair asap. dq | October | 2016 | 2017Q2 | 2017 | 216:10724 | 216:10724 | ZN00216/010724 | NEWCASTLE | OH | Not Veg | 2016-10-06 | N | 158 | N | 3 | N | N | 1.1101 | 39.4971 | 346.3852
[7 empty] | 10233 | 18885 | 1427232 | 2016-10-07 02:23 | 2016-10-07 03:36 | 73 | 11kV | 28324 | 388 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 14 tripped on Earth Fault / Fault Chek / EFI 11kV Trip / Zone Earth and Group Earth / TX1 EF check Cause: UG cable Fault from S8556 to CP1714 to S2046 See OMS 1427699 1427232 | October | 2016 | 2017Q2 | 2017 | ZN847:PA14 | ZN847:PA14 | ZN00847/000014 | HORNSBY | UG | Not Veg | 2016-10-07 | N | 73 | N | 3 | N | N | 1.1101 | 39.4971 | 20698.3438
[7 empty] | 9775 | 13349 | 1427316 | 2016-10-07 12:15 | 2016-10-07 16:20 | 245 | 11kV | 39125 | 958 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14892 Charmhaven section of Pa13 CP61133 Minnamurra Tosca opened by AOp Interrupted for safety reasons. Truck on OH on 40 Georgina Ave Gorokan See 1429346,7 Exclude 1427309,10,6,26 | October | 2016 | 2017Q2 | 2017 | ZN14892:PA13 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | OH | Not Veg | 2016-10-07 | N | 40.8403 | N | 3 | N | N | 1.1101 | 39.4971 | 28591.396
[7 empty] | 8770 | 1031 | 1427365 | 2016-10-07 15:00 | 2016-10-07 16:32 | 92 | 11kV | 277181 | 4213 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7481 Darling Harbour - Pnl.17 tripped on: Earth Fault 17L Field EFIs: S7642 & S5459 UG cable fault between S5459 Hudson Young and S1881 Johnson Rose (Compound End Box) See 1427842 1427843 1427845 1427846 | October | 2016 | 2017Q2 | 2017 | ZN7481:PA17 | ZN116:PA25 | ZN00116/000025 | SYDNEY | UG | Not Veg | 2016-10-07 | N | 65.7918 | N | 3 | N | N | 1.1101 | 39.4971 | 202555.6993
[7 empty] | 8798 | 1480 | 1427449 | 2016-10-08 03:53 | 2016-10-08 05:28 | 95 | 11kV | 138805 | 1547 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.17 tripped on: P17R Earth Fault, EFI UG cable fault between S4364 McPerson Al to S2138 Blandford Ave See 1427856 1427857 | October | 2016 | 2017Q2 | 2017 | ZN2602:PA17 | ZN2602:PA30 | ZN02602/000030 | RANDWICK | UG | Not Veg | 2016-10-08 | N | 89.7253 | N | 4 | N | N | 1.1101 | 39.4971 | 101434.5999
[7 empty] | 10222 | 18769 | 1427450 | 2016-10-08 04:24 | 2016-10-08 06:53 | 149 | 11kV | 298 | 2 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | Hot >35C | N | PT14537 Peats Ridge Lowe the road side 16Amp HDO has blown Possum on HV Arrestor @ PT14537 See 14294634 exclude 1427450 | October | 2016 | 2017Q2 | 2017 | ZN12630:PA24 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2016-10-08 | N | 149 | N | 4 | N | N | 1.1101 | 39.4971 | 217.7696
[7 empty] | 9679 | 12146 | 1427447 | 2016-10-08 03:39 | 2016-10-08 10:00 | 381 | 11kV | 210885 | 1505 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @ZN3472 Sefton Panel 28 'Baird Buist' tripped on Relays: reclose time, reclose lock out and O/C Signals: 11kv trip Field EFI's: Nil Remarks: Animals/Birds/ 11kv OH down cnr Denman and Ash. Bat found in mains tangled up. 11kv feeder isolated from AB1782 AB2594 tee PT61772 Caroline Denman and tee PT1678 Ash St via defective AB18. 11kv clipped LV mains. EMSO required to give clearance to re-energise LV from PT61772 and PT1678. PT1678 restored via LV//: Dist #1 usl 9001 @ 0750, Dist #2 usl 11610 @ 0745 PT61772, Dist #1 restored via LV// usl's 14929, 3640 @ 0805 | October | 2016 | 2017Q2 | 2017 | ZN3472:PA28 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-10-08 | N | 140.1229 | N | 4 | N | N | 1.1101 | 39.4971 | 154108.5379
[7 empty] | 9078 | 5175 | 1427480 | 2016-10-08 09:19 | 2016-10-08 11:22 | 123 | 11kV | 1353 | 11 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 168918 A Phase Broken Aph LL Clamp. Excluded OMS No. 1427480 | October | 2016 | 2017Q2 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-10-08 | N | 123 | N | 4 | N | N | 1.1101 | 39.4971 | 988.7325
[7 empty] | 9897 | 14810 | 1427632 | 2016-10-09 15:54 | 2016-10-09 17:15 | 81 | 11kV | 29970 | 386 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S15014 Mona Vale Panel 16 tripped on Relays: A phase IOC, EFI, NO1 TX Fault Check Signals: 11kV Trip Cause: UG cable Fault See OMS 1429307 1429308 1427632 | October | 2016 | 2017Q2 | 2017 | ZN15014:PA16 | ZN15014:PA16 | ZN15014/000016 | NORTHERN BEACHES | UG | Not Veg | 2016-10-09 | N | 77.6425 | N | 2 | N | N | 1.1101 | 39.4971 | 21901.192
[7 empty] | 9245 | 6955 | 1427696 | 2016-10-10 07:45 | 2016-10-10 08:30 | 45 | 11kV | 108249 | 2629 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10990 Arncliffe - Pnl.8 tripped on: Earth Fault with EFI. Field EFIs: S10001, S65562, Cnr Thompson and Booth, S10881, S10877, S10890, Bonar St near Thompson, S47415, S47416, S64912 Abnormal: S47163 (Sw/B) CLOSED with S10193 (Sw/A) OPEN. S6259 (Sw/B) Closed with (Sw/A) OPEN. S10810, S10494 and S10991 and all in LV // UG cable fault between S64912 Bonar Hirst No.3 (Sw/A) and S62059 Bonar Hirst No.4 (Sw/B) See 1428003 1428004 | October | 2016 | 2017Q2 | 2017 | ZN10990:PA8 | ZN10998:PA10 | ZN10998/000010 | BAYSIDE | UG | Not Veg | 2016-10-10 | N | 41.175 | N | 8 | N | N | 1.1101 | 39.4971 | 79105.1764
[7 empty] | 9670 | 12010 | 1427656 | 2016-10-09 21:16 | 2016-10-10 10:35 | 799.0667 | 11kV | 82155.1333 | 640 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn12640 Umina Pa1 fdr tripped, reclosed, tripped & locked out on Relays: B&C phase IOC, EF, EFI Signals: 11kv trip Vehicle Hit Pole See 1429455,7,8 Exclude 1427656,7,9,60,5 | October | 2016 | 2017Q2 | 2017 | ZN12640:PA1 | ZN12640:PA1 | ZN12640/000001 | CENTRAL COAST | OH | Not Veg | 2016-10-09 | N | 128.3674 | N | 2 | N | N | 1.1101 | 39.4971 | 60036.5483
[7 empty] | 9930 | 15108 | 1427762 | 2016-10-10 10:49 | 2016-10-10 11:20 | 31 | 11kV | 713 | 23 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap Rd" opened CP41467 tee PT111181 and PT11481 Tree Branch on mains at 20 Fern Rd | October | 2016 | 2017Q2 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2016-10-10 | N | 31 | N | 8 | N | N | 1.1101 | 39.4971 | 521.0394
[7 empty] | 9856 | 14249 | 1427834 | 2016-10-10 14:03 | 2016-10-10 15:45 | 102 | 11kV | 130303 | 1615 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn15009 Manly Panel 5 Tripped on Relays: Earth Leakage, Frame Leakage Fault Cgeck Cause: HV UGOH fault on pole MO46400 HV feeder isolated from s15095 sw/b TO s16911 TO s15965. See OMS 1429425 1427834 1429427 1429426 1427839 1427838 | October | 2016 | 2017Q2 | 2017 | ZN15009:PA5 | ZN15009:PA5 | ZN15009/000005 | NORTHERN BEACHES | Unknown | Unknown | 2016-10-10 | N | 80.683 | N | 8 | N | N | 1.1101 | 39.4971 | 95221.5891
[7 empty] | 9535 | 10407 | 1427933 | 2016-10-10 19:39 | 2016-10-10 21:54 | 135 | 11kV | 270 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 168929 HV Dropper to DOLF Failed. Excluded OMS 1427933 | October | 2016 | 2017Q2 | 2017 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2016-10-10 | N | 135 | N | 8 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 10347 | 20213 | 1427942 | 2016-10-10 21:13 | 2016-10-10 23:14 | 121 | 11kV | 3762 | 42 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 168930 Trip & Reclose Trip and reclose then report of blown Line Fuse 43997. Please inspect during daylight for possible lightening strike. 3 phase DOLF : 40 Amp | October | 2016 | 2017Q2 | 2017 | 229:34983 | 233:82818 | ZN00233/082818 | PORT STEPHENS | OH | Veg | 2016-10-10 | N | 89.5714 | N | 8 | N | N | 1.1101 | 39.4971 | 2749.1586
[7 empty] | 9149 | 5976 | 1427954 | 2016-10-10 23:00 | 2016-10-11 00:15 | 75 | 11kV | 55125 | 735 | HV | Vegetation Blow/Fall In | Vegetation | DC Not Transformer | Unplanned | No Weather Impact | N | @ S10618 Park Short 11 Kv switch Cap (Haz) was damaged after a tree came down on kiosk. Switch cap broken with exposed terminals and breaking the door of the kiosk on the HV end. S10618 isolated and in LV // | October | 2016 | 2017Q2 | 2017 | ZN10994:PA1 | ZN10994:PA1 | ZN10994/000001 | GEORGES RIVER | OH | Veg | 2016-10-10 | N | 75 | N | 8 | N | N | 1.1101 | 39.4971 | 40283.7241
[7 empty] | 9322 | 7777 | 1427952 | 2016-10-10 22:02 | 2016-10-11 04:30 | 388 | 11kV | 2364 | 510 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 168932 After trip and reclose customer report S-71141 blown DOLF caused by blown LA & faulty Tx Line Fuse 75319 A&B phase 20A blown | October | 2016 | 2017Q2 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2016-10-10 | N | 4.6353 | N | 8 | N | N | 1.1101 | 39.4971 | 1727.5415
[7 empty] | 9001 | 3962 | 1427865 | 2016-10-10 15:14 | 2016-10-11 13:49 | 1355 | 11kV | 417079 | 2619 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn15009 Manly Panel 7 Tripped reclosed tripped sand locked out on A and C phase IOC, Lockout, Timing Relay and Fault Check Signals: 11kV trip, EFI Abnormal Switching: SW/B Closed at S17080 SW/B open at S46401 Cause: Removalist truck hit pole, snapping pole and dropping mains to ground Report from customer - Pole fallen on house, live wires on house, house on fire and gas leak Note: miunor part of dist still interrupted after previous fault - bay of LV needs restringing (refer to 1429721) See OMS 1429480 1429485 1429486 1429487 142984 1427876/865/873/874/876 | October | 2016 | 2017Q2 | 2017 | ZN15009:PA7 | ZN15009:PA7 | ZN15009/000007 | NORTHERN BEACHES | OH | Not Veg | 2016-10-10 | N | 159.2512 | N | 8 | N | N | 1.1101 | 39.4971 | 304789.0315
[7 empty] | 9770 | 13295 | 1427971 | 2016-10-11 03:47 | 2016-10-11 14:20 | 633 | 11kV | 8877 | 22 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 168941 C Phase DOLF : 10 Amp new pole installed - not tied in. insufficent clearance to existing OHM. conductor was rubbing on crossarm and burnt through. Adjacent sub 77038 (old Maitland Albury sub 507/1 C9) Excluded OMS 1427971 & 1428139 | October | 2016 | 2017Q2 | 2017 | 507:80925 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2016-10-11 | N | 403.5 | N | 4 | N | N | 1.1101 | 39.4971 | 6487.0498
[7 empty] | 9421 | 9077 | 1428236 | 2016-10-11 15:38 | 2016-10-11 18:53 | 195 | 11kV | 780 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 168947 11kV burnt off tapping @ T off Pole MD-90696 Intitial Customer call at 1538hrs. | October | 2016 | 2017Q2 | 2017 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2016-10-11 | N | 195 | N | 4 | N | N | 1.1101 | 39.4971 | 570.001
[7 empty] | 10335 | 20102 | 1427984 | 2016-10-11 06:42 | 2016-10-11 19:45 | 783 | 11kV | 783 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 168949 Single phase DOLF : 10 Amp Put in MAitland Queue at 649hrs. I dont think it was attended too. Moved back to Control @ 2009hrs. Dave Myers attended. Replaced arcing DOLF carrier. Excluded OMS 1428295 & 1427984 | October | 2016 | 2017Q2 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2016-10-11 | N | 783 | N | 4 | N | N | 1.1101 | 39.4971 | 572.1933
[7 empty] | 9746 | 12972 | 1428289 | 2016-10-11 17:26 | 2016-10-11 20:25 | 179 | 11kV | 344860 | 1996 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn874 Concord Panel No.18 'Peninsula Rosewater' feeder tripped on Signals: 11kv trip, Zone earth, Tx1 Group Earth Relays: A & C ph IOC Remarks: UG fault. Underground feeder fault between Zn874 Concord Pa.18 warbrick Park Sw/A and S8361 Peninuslar Rosewater Sw/B. Secondary Cross- Country fault between S35719 Vineyard Village., S36240 Wiggins Brays and S7880 Fairwater drive | October | 2016 | 2017Q2 | 2017 | ZN874:PA18 | ZN874:PA18 | ZN00874/000018 | CANADA BAY | UG | Not Veg | 2016-10-11 | N | 172.7756 | N | 4 | N | N | 1.1101 | 39.4971 | 252013.5164
[7 empty] | 9135 | 5802 | 1428361 | 2016-10-12 07:00 | 2016-10-12 10:20 | 200 | 11kV | 400 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168955 10Amp Fuse No Cause Found - Not Storm conditions | October | 2016 | 2017Q2 | 2017 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2016-10-12 | N | 200 | N | 2 | N | N | 1.1101 | 39.4971 | 292.3082
[7 empty] | 10191 | 18430 | 1428481 | 2016-10-12 15:32 | 2016-10-12 16:59 | 87 | 11kV | 152598 | 1754 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN2196 Milperra Panel No.25 'Turvey River' feeder tripped on Signals: 11kv trip, Tx4 roup earth, Zone earth Relays: BASLER - trip EFI's: Nil Remarks: tree branch contact. Tree branch hit HV outside 13 Banks St | October | 2016 | 2017Q2 | 2017 | ZN2196:PA25 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-10-12 | N | 87 | N | 2 | N | N | 1.1101 | 39.4971 | 111514.1175
[7 empty] | 9163 | 6171 | 1428570 | 2016-10-13 08:30 | 2016-10-13 12:01 | 211 | 11kV | 1055 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 168967 20 Amp Fuse Line DOLF - no cause found, not storm conditions | October | 2016 | 2017Q2 | 2017 | 233:82819 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2016-10-13 | N | 211 | N | 4 | N | N | 1.1101 | 39.4971 | 770.9629
[7 empty] | 9131 | 5766 | 1428620 | 2016-10-13 11:11 | 2016-10-13 12:45 | 94 | 11kV | 51606 | 549 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | Ex Zn10990 Arncliffe Pnl.11 - USL 30538 roadside bond burnt off. Linesman to repair | October | 2016 | 2017Q2 | 2017 | ZN10990:PA11 | ZN10993:PA23 | ZN10993/000023 | BAYSIDE | OH | Not Veg | 2016-10-13 | N | 94 | N | 4 | N | N | 1.1101 | 39.4971 | 37712.1427
[7 empty] | 9278 | 7232 | 1428728 | 2016-10-13 17:23 | 2016-10-13 18:10 | 47 | 11kV | 47 | 1 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 168971 10 Amp fuse, substation DOLF Bird contacted the 11kV and caused A phase 10 amp dolf to blow power, on at 610pm. PD | October | 2016 | 2017Q2 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2016-10-13 | N | 47 | N | 4 | N | N | 1.1101 | 39.4971 | 34.3462
[7 empty] | 10225 | 18797 | 1428729 | 2016-10-13 20:15 | 2016-10-13 20:40 | 25 | 11kV | 25 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 168972 Surge arrestor found smoking, was cut away Power restored 2040 hours faulty surge arrestors cut away. also refer to 1428729 Lee Kelly confirmed that no fire event, the smoking insulator turned out to be a HV dolf that had failed to drop and the wasp nests inside it were tracking | October | 2016 | 2017Q2 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2016-10-13 | N | 25 | N | 4 | N | N | 1.1101 | 39.4971 | 18.2693
[7 empty] | 9086 | 5250 | 1428772 | 2016-10-14 04:56 | 2016-10-14 06:10 | 74 | 11kV | 32550 | 561 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 22 tripped on Earth Fault with EFI. Signals: 11kV trip, Zone Earth and TX3 Group Earth Cause: UG feeder fault from Pa22 to S5847 to PT1362 See OMS 1429207 1429209 1428772 1428774 | October | 2016 | 2017Q2 | 2017 | ZN965:PA22 | ZN965:PA22 | ZN00965/000022 | HORNSBY | UG | Not Veg | 2016-10-14 | N | 58.0214 | N | 3 | N | N | 1.1101 | 39.4971 | 23786.5799
[7 empty] | 9601 | 11278 | 1428768 | 2016-10-14 02:20 | 2016-10-14 09:15 | 415 | 11kV | 830 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 168975 LLC came undone. Excluded oms 1428768 | October | 2016 | 2017Q2 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2016-10-14 | N | 415 | N | 3 | N | N | 1.1101 | 39.4971 | 606.5395
[7 empty] | 9198 | 6425 | 1428949 | 2016-10-14 21:08 | 2016-10-14 22:55 | 107 | 11kV | 241139 | 2352 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S180 Mosman Panel 18 tripped on Overcurrent, Earth Fault, EFI and Fault Check Cause: 11kV cable fault between S4041 to S2460 See OMS 1429310 1429311 1428949 | October | 2016 | 2017Q2 | 2017 | ZN180:PA18 | ZN180:PA22 | ZN00180/000022 | NORTH SYDNEY | UG | Not Veg | 2016-10-14 | N | 102.5251 | N | 3 | N | N | 1.1101 | 39.4971 | 176217.2688
[7 empty] | 10125 | 17546 | 1428960 | 2016-10-15 06:09 | 2016-10-15 07:15 | 66 | 33kV Distribution | 132 | 2 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 168989 1 fault operation C phase Instantaneous Earth Fault, Instantaneous Overcurrent Customer problem. Their CB 91652 did not trip, did not grade with CB 91649 which did trip. Excluded oms 1428960 | October | 2016 | 2017Q2 | 2017 |  |  |  | NEWCASTLE | Unknown | Not Veg | 2016-10-15 | N | 66 | N | 4 | N | N | 1.1101 | 39.4971 | 96.4617
[7 empty] | 9317 | 7713 | 1428988 | 2016-10-15 12:55 | 2016-10-15 13:45 | 50 | 11kV | 100 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168991 Single phase DOLF : 10 Amp | October | 2016 | 2017Q2 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2016-10-15 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 10365 | 20400 | 1429020 | 2016-10-15 16:54 | 2016-10-15 18:05 | 71 | 11kV | 142 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 168992 C phase DOLF : 10 Amp Excluded OMS 1429020 | October | 2016 | 2017Q2 | 2017 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2016-10-15 | N | 71 | N | 4 | N | N | 1.1101 | 39.4971 | 103.7694
[7 empty] | 8988 | 3867 | 1429032 | 2016-10-15 19:48 | 2016-10-15 20:15 | 26.5667 | 11kV | 637.6 | 24 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of Pa7 PT14187 Palm Valley Victor centre phase HDO operated 31.5Amp batch 0220 Fuse Failure. Replaced HDO supply checked ok See 1429032 exclude 1429033 | October | 2016 | 2017Q2 | 2017 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Not Veg | 2016-10-15 | N | 26.5667 | N | 4 | N | N | 1.1101 | 39.4971 | 465.9393
[7 empty] | 8774 | 1057 | 1429137 | 2016-10-17 02:35 | 2016-10-17 03:18 | 43 | 11kV | 86387 | 2009 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169002 2 fault operations A & B phase Overcurrent Possum found at pole JU-12986 Excluded oms 1429138. | October | 2016 | 2017Q2 | 2017 | 258:80775 | 258:80775 | ZN00258/080775 | NEWCASTLE | OH | Not Veg | 2016-10-17 | N | 43 | N | 2 | N | N | 1.1101 | 39.4971 | 63129.0716
[7 empty] | 10301 | 19534 | 1429243 | 2016-10-17 12:21 | 2016-10-17 19:15 | 414 | 11kV | 1242 | 3 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 169013 Phase B & C DOLF TREE FELL ON TX. Excluded OMS REPORT NO 1429243. | October | 2016 | 2017Q2 | 2017 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2016-10-17 | N | 414 | N | 2 | N | N | 1.1101 | 39.4971 | 907.617
[7 empty] | 9203 | 6507 | 1429467 | 2016-10-18 08:15 | 2016-10-18 13:30 | 315 | 11kV | 25515 | 81 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12620 Noraville section of Pa2 "Budegwoi" fdr was interupted from L41777 After switching D&R391783 (DAROS 391783 DMA - PT12652[O] - OURRINGO OCEAN - HV OVERHAUL) a customer has informed us supply had not been restored. After investigation it was revealed that 4 bays of 11kv copper wire had been cut awaybetween LB40719 and the N/O LB40214 (Lake Munmorah SH2 F8) Upon restoringisolations for D&R 391783 LK417777 failed to stay closed on 2 phases requiring emergency repair See 1429870 exclude 1429467,8 | October | 2016 | 2017Q2 | 2017 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Not Veg | 2016-10-18 | N | 315 | N | 2 | N | N | 1.1101 | 39.4971 | 18645.6094
[7 empty] | 9126 | 5705 | 1429605 | 2016-10-18 20:23 | 2016-10-18 21:40 | 77 | 11kV | 308 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169026 B Phase DOLF : 63 Amp Excluded OMS 1429605 | October | 2016 | 2017Q2 | 2017 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Veg | 2016-10-18 | N | 77 | N | 2 | N | N | 1.1101 | 39.4971 | 225.0773
[7 empty] | 9957 | 15366 | 1429696 | 2016-10-19 12:01 | 2016-10-19 12:39 | 38 | 11kV | 6802 | 179 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn4990 City Central - 51/52 "K" feeder tripped on: Overcurrent & Earth Fault Left Abnormal: 51/52 "L" feeder out defective due to cable fault on 16/10/16 UG cable fault on 51K leg of feeder. At the same time, 11kV "L" section busbar tripped. Suspected due to fault current returning through the earthed defective 51/52L feeder. 57L feeder lost supply as it is not a city triplex feeder. See 1429790 1429789 1429788 1429696 | October | 2016 | 2017Q2 | 2017 | ZN4990:PA57L | ZN4990:PA57K | ZN04990/00057K | SYDNEY | UG | Not Veg | 2016-10-19 | N | 38 | N | 1 | N | N | 1.1101 | 39.4971 | 4970.701
[7 empty] | 9266 | 7153 | 1429779 | 2016-10-20 05:52 | 2016-10-20 08:42 | 170 | 11kV | 172435 | 1191 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S4545 Meadowbank 11kV panel 17 Tripped reclosed tripped and locked out on A and C phase IOC, A phase Timed, Timed Relay and Lockout Signals: TX2 group earth, 11kV Trip Cause not ascertained for outage - OH Patrolled - Nothing Found. See OMS 1430534 1430536 1430537 1429777 | October | 2016 | 2017Q2 | 2017 | ZN4545:PA17 | ZN129:PA36 | ZN00129/000036 | RYDE | OH | Veg | 2016-10-20 | N | 144.7817 | N | 4 | N | N | 1.1101 | 39.4971 | 126010.412
[7 empty] | 9959 | 15390 | 1430467 | 2016-10-20 11:10 | 2016-10-20 11:40 | 30 | 11kV | 1170 | 39 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN35370 Galston Section of 11kV from SW/A at S2831 to CP196 Supply Manually interrupted by DOp to remove tree See OMS 1430468 1430467 | October | 2016 | 2017Q2 | 2017 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2016-10-20 | N | 30 | N | 4 | N | N | 1.1101 | 39.4971 | 855.0015
[7 empty] | 9788 | 13536 | 1429897 | 2016-10-20 13:06 | 2016-10-20 18:45 | 339 | 11kV | 678 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169055 Single phase dropper lead replaced under ap Excluded oms 1429897 | October | 2016 | 2017Q2 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2016-10-20 | N | 339 | N | 4 | N | N | 1.1101 | 39.4971 | 495.4624
[7 empty] | 9646 | 11722 | 1429996 | 2016-10-20 21:13 | 2016-10-20 22:29 | 76 | 11kV | 58873 | 821 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Panel 7 "S14805 Wyong Mingara Etc" fdr tripped on Relays: B Phase overcurrent end Earth Fault EFI Signals: 11kv trip, Tx12 Group Earth EFI'S S14808 Cause not ascertained. Fdr Switch Back to Normal See 1430495,7 exclude 1429996,8 | October | 2016 | 2017Q2 | 2017 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Veg | 2016-10-20 | N | 71.7089 | N | 4 | N | N | 1.1101 | 39.4971 | 43022.6519
[7 empty] | 9787 | 13535 | 1430174 | 2016-10-21 17:24 | 2016-10-21 18:37 | 73 | 11kV | 2409 | 33 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169070 stranded mains repaired between poles ET-51634 & ET-51635 | October | 2016 | 2017Q2 | 2017 | 509:33397 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2016-10-21 | N | 73 | N | 4 | N | N | 1.1101 | 39.4971 | 1760.4261
[7 empty] | 8966 | 3616 | 1430200 | 2016-10-21 21:29 | 2016-10-22 02:55 | 326 | 11kV | 5216 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169071 A & B phase DOLF : 20 Amp | October | 2016 | 2017Q2 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-10-21 | N | 326 | N | 4 | N | N | 1.1101 | 39.4971 | 3811.699
[7 empty] | 9740 | 12922 | 1430214 | 2016-10-22 05:48 | 2016-10-22 07:06 | 78 | 11kV | 4446 | 57 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 WEst Gosford section of Pa1 "Resevoir Beckford 0.5 etc" RE44604 Dog Trap Road opened & locked out on IOC and overcurrent Tree Branch on OH Mains. Adajacent to LB44637 | October | 2016 | 2017Q2 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2016-10-22 | N | 78 | N | 4 | N | N | 1.1101 | 39.4971 | 3249.0057
[7 empty] | 9530 | 10360 | 1430235 | 2016-10-21 21:29 | 2016-10-22 09:05 | 696 | 11kV | 1392 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169074 Single phase DOLF : 10 Amp Relates to OMS 1430470 & unplanned outage 169071. Excluded OMS 1430235 & 1430465 | October | 2016 | 2017Q2 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-10-21 | N | 696 | N | 4 | N | N | 1.1101 | 39.4971 | 1017.2325
[7 empty] | 9216 | 6679 | 1430215 | 2016-10-21 21:29 | 2016-10-22 10:05 | 756 | 11kV | 756 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169075 Single phase DOLF : 10 Amp Relates to OMS 1430470 & unplanned outage 169071. Excluded OMS 1430215. | October | 2016 | 2017Q2 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-10-21 | N | 756 | N | 4 | N | N | 1.1101 | 39.4971 | 552.4625
[7 empty] | 9085 | 5238 | 1430230 | 2016-10-22 11:45 | 2016-10-22 12:40 | 55 | 11kV | 165 | 3 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 169076 3 phase No protection operations. Section isolated to remove tree under A/P at pole NR-91010. Excluded OMS 1430230 & 1430257. | October | 2016 | 2017Q2 | 2017 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2016-10-22 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 120.5771
[7 empty] | 10107 | 17307 | 1430221 | 2016-10-22 08:26 | 2016-10-22 17:10 | 524 | 11kV | 3668 | 7 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex14143 Somersby section of Pa17 "USL41994" fdr PT18651 Jones Peats Ridge HV Fuse operated Lightning/Surge Arrestor. Replaced surge arrestor, tested PT and okay See 1430502 exclude 1430221,1430271 | October | 2016 | 2017Q2 | 2017 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2016-10-22 | N | 524 | N | 4 | N | N | 1.1101 | 39.4971 | 2680.4662
[7 empty] | 9951 | 15303 | 1430325 | 2016-10-22 23:51 | 2016-10-23 00:45 | 54 | 11kV | 6480 | 120 | HV | Animal Possum | Animal | Fuse | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa16 PT13606 Tuggerawong Cadonia middle phase HDO blown 31.5Amp Possum on PT See 1430510 exclude 1430325 | October | 2016 | 2017Q2 | 2017 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2016-10-22 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 4735.3929
[7 empty] | 9823 | 13865 | 1430327 | 2016-10-23 04:54 | 2016-10-23 06:00 | 66 | 11kV | 53919 | 1034 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | Zn9118 Cronulla - Pnl.17 tripped on: Overcurrent, EFI, Zone Earth, Tx 2 Group Earth Field EFIs: NIL At PT9428 Yowie Waterview, middle phase HDO damaged from possum shorting across it. See 1430457 1430459 | October | 2016 | 2017Q2 | 2017 | ZN9118:PA17 | ZN9118:PA17 | ZN09118/000017 | SUTHERLAND | OH | Not Veg | 2016-10-23 | N | 52.146 | N | 2 | N | N | 1.1101 | 39.4971 | 39402.4149
[7 empty] | 9549 | 10618 | 1430371 | 2016-10-23 11:09 | 2016-10-23 11:53 | 44 | 11kV | 1100 | 25 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2196 Milperra the 11kv Panel 22 "Fitzpatrick car No.6 etc" feeder tripped on: Relays: Timed EF, EFI Signals: Zone Earth, Tx2 Group Earth, 11kv trip Field EFI's: Nil Remarks: UG fault. UG 11kv feeder fault between Milperra Panel 22, S7717 Fitzpatrick Car No.6 and S6481 Milperra Aux | October | 2016 | 2017Q2 | 2017 | ZN2196:PA22 | ZN2196:PA22 | ZN02196/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-10-23 | N | 44 | N | 2 | N | N | 1.1101 | 39.4971 | 803.8476
[7 empty] | 8809 | 1577 | 1430879 | 2016-10-25 23:42 | 2016-10-26 02:23 | 161 | 11kV | 228203 | 1579 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 39 tripped and locked out on sensitive earth lockout with 11kV trip Cause: AB1593 Roadside phase open circuit bond failed See OMS 1431937 1431939 1431940 1431941 1430879 | October | 2016 | 2017Q2 | 2017 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Not Veg | 2016-10-25 | N | 144.5237 | N | 1 | N | N | 1.1101 | 39.4971 | 166764.0216
[7 empty] | 9846 | 14143 | 1431247 | 2016-10-27 17:11 | 2016-10-27 18:10 | 59 | 11kV | 118 | 2 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169131 A Phase : 80 Amp Excluded OMS 1431247 | October | 2016 | 2017Q2 | 2017 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2016-10-27 | N | 59 | N | 6 | N | N | 1.1101 | 39.4971 | 86.2309
[7 empty] | 9876 | 14495 | 1431265 | 2016-10-27 18:44 | 2016-10-27 19:48 | 64 | 11kV | 5166 | 464 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169132 2 fault operations A & C phase Overcurrent | October | 2016 | 2017Q2 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2016-10-27 | N | 11.1336 | N | 6 | N | N | 1.1101 | 39.4971 | 3775.1604
[7 empty] | 9180 | 6291 | 1431267 | 2016-10-27 18:55 | 2016-10-27 20:35 | 100 | 11kV | 100 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169135 A phase DOLF : 10 Amp Excluded OMS 1431267 | October | 2016 | 2017Q2 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2016-10-27 | N | 100 | N | 6 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 9274 | 7219 | 1431282 | 2016-10-27 21:10 | 2016-10-27 22:54 | 104 | 11kV | 19344 | 186 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn35370 Galston panel 10 - CP50015 tripped on OC with lockout Signals: 11kV Trip See OMS 1431282 1431288 | October | 2016 | 2017Q2 | 2017 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2016-10-27 | N | 104 | N | 6 | N | N | 1.1101 | 39.4971 | 14136.0246
[7 empty] | 8755 | 710 | 1431244 | 2016-10-27 17:02 | 2016-10-27 23:23 | 381 | 11kV | 37295 | 835 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169133 black swan brought down ohm between pole HS-43365 & HS-43366, causing small fire tappings also blown at pole HS-43364, HS-43363 & HS-43344. Excluded oms 1431244 | October | 2016 | 2017Q2 | 2017 | 507:80923 | 507:80923 | ZN00507/080923 | CESSNOCK | OH | Not Veg | 2016-10-27 | N | 44.6647 | N | 6 | N | N | 1.1101 | 39.4971 | 27254.086
[7 empty] | 9500 | 9932 | 1431286 | 2016-10-27 21:14 | 2016-10-28 00:30 | 196 | 11kV | 73279 | 376 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169136 4 fault operations B & C phase Overcurrent Removed bat from OHM at pole IQ-42017. DOP advises trees at this location require trimming. Excluded oms 1431286 | October | 2016 | 2017Q2 | 2017 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2016-10-27 | N | 194.891 | N | 6 | N | N | 1.1101 | 39.4971 | 53550.1318
[7 empty] | 8769 | 1014 | 1432219 | 2016-10-28 01:55 | 2016-10-28 02:59 | 64 | 11kV | 3712 | 58 | HV | Animal Bird | Animal | UGOH | Unplanned | Rain Light | N | Ex Zn14891 Wyong section of Pa5 Recloser 45083 Durren opened and locked out on overcurrent Dead Possum found at UGOH adjacent to EFI sht 4 CD78 | October | 2016 | 2017Q2 | 2017 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2016-10-28 | N | 64 | N | 6 | N | N | 1.1101 | 39.4971 | 2712.6201
[7 empty] | 10113 | 17408 | 1431297 | 2016-10-28 03:09 | 2016-10-28 03:55 | 46 | 11kV | 2622 | 57 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 169138 A Phase DOLF : 20 Amp Dead possum at base of pole, Reading as left 245v @10A per phase. Excluded oms 1431297 & 1431298 | October | 2016 | 2017Q2 | 2017 | 221:11894 | 221:11894 | ZN00221/011894 | LAKE MACQUARIE | OH | Not Veg | 2016-10-28 | N | 46 | N | 6 | N | N | 1.1101 | 39.4971 | 1916.0803
[7 empty] | 8754 | 708 | 1431333 | 2016-10-28 09:24 | 2016-10-28 11:10 | 106 | 11kV | 212 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169142 A Phase DOLF : 16 Amp Excluded OMS 1431333 | October | 2016 | 2017Q2 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2016-10-28 | N | 106 | N | 6 | N | N | 1.1101 | 39.4971 | 154.9233
[7 empty] | 10015 | 16240 | 1431933 | 2016-10-28 14:00 | 2016-10-28 14:30 | 30 | 11kV | 540 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35370 Galston section of panel 4 from AB2894 to AB25 interrupted for safety Cause: Supply interrupted to remove tree from 19 smalls rd 1431934 1431933 | October | 2016 | 2017Q2 | 2017 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2016-10-28 | N | 30 | N | 6 | N | N | 1.1101 | 39.4971 | 394.6161
[7 empty] | 9747 | 12973 | 1431390 | 2016-10-28 14:32 | 2016-10-28 16:30 | 118 | 11kV | 334392 | 3529 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S874 Concord 11kv panel No4 tripped on: Relays: A + C phase IOC, EFI, fault check Signals: 11kv trip Abnormal: sw/b closed @ S8451 Peninsula Palms, Sw/B open @ S8361 Peninsula Rosewater, Sw/A open @ S35719 Village Vineyard. Sw/B closed @ S2507 Concord RSL, Sw/A open @ S5836 The drive Concord Remarks: UG cable damaged by Contractors. Contractor william knight mob 0428222114, hit cable with excavator between S6379 Hilly McDonald to S3883 Northcote Bennett to S2238 Bertram St | October | 2016 | 2017Q2 | 2017 | ZN874:PA4 | ZN874:PA4 | ZN00874/000004 | CANADA BAY | UG | Not Veg | 2016-10-28 | N | 94.7555 | N | 6 | N | N | 1.1101 | 39.4971 | 244363.8107
[7 empty] | 9164 | 6178 | 1431296 | 2016-10-28 03:04 | 2016-10-28 22:35 | 1171 | 11kV | 9328 | 8 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Cp24720 Cromer Fitness the 11kV Tee of tripped Fuse details: B phase B&S OQFRN 71A Cause: 11kV UG cable fault in Tee off from CP24720 Cromer Fitness. See OMS 1431766 1431768 1431769 1431296 | October | 2016 | 2017Q2 | 2017 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | UG | Not Veg | 2016-10-28 | N | 1166 | N | 6 | N | N | 1.1101 | 39.4971 | 6816.6273
[7 empty] | 10061 | 16685 | 1431813 | 2016-10-29 05:12 | 2016-10-29 05:32 | 20 | 11kV | 25000 | 1250 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn195 Pymble Panel 29 tripped on Relays: E/F, EFI Signals: 11kV trip, Zone earth and No4 Group Earth Panel 25 Opened By AOP at 0512 to allow safe removal of Possum at PT1846 See OMS 1431817 1431818 1431820 1431813 1431843/1431510/600/601/602/603/612 Cause: Fault in section of 11kV Feeder from S4641 to S4642 tee PT1141 Panel 25 Interrupted by AOP to remove possum | October | 2016 | 2017Q2 | 2017 | ZN195:PA25 | ZN195:PA25 | ZN00195/000025 | KU-RING-GAI | OH | Not Veg | 2016-10-29 | N | 20 | N | 4 | N | N | 1.1101 | 39.4971 | 18269.2626
[7 empty] | 9008 | 4029 | 1431483 | 2016-10-29 03:04 | 2016-10-29 05:55 | 171 | 11kV | 106677 | 1108 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn195 Pymble Panel 29 tripped on Relays: E/F, EFI Signals: 11kV trip, Zone earth and No4 Group Earth Panel 25 Opened By AOP at 0512 to allow safe removal of Possum at PT1846 See OMS 1431817 1431818 1431820 1431813 1431843/1431510/600/601/602/603/612 Cause: Fault in section of 11kV Feeder from S4641 to S4642 tee PT1141 Panel 25 Interrupted by AOP to remove possum | October | 2016 | 2017Q2 | 2017 | ZN195:PA29 | ZN195:PA29 | ZN00195/000029 | KU-RING-GAI | UG | Not Veg | 2016-10-29 | N | 96.2789 | N | 4 | N | N | 1.1101 | 39.4971 | 77956.4052
[7 empty] | 9882 | 14557 | 1431507 | 2016-10-29 09:13 | 2016-10-29 10:33 | 80 | 11kV | 85761 | 1170 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn80 Chatswood 11kV panel 30 tripped on IOC, Trip, Alarm, EFI, Fault Check Relay Signals: 11kV Trip, Zone Earth, TX11 Group Earth Cause: UG fault between SW/B @ S3038 and S4072 See OMS 1431944 1431946 1431507 | October | 2016 | 2017Q2 | 2017 | ZN80:PA30 | ZN80:PA30 | ZN00080/000030 | WILLOUGHBY | UG | Not Veg | 2016-10-29 | N | 73.3 | N | 4 | N | N | 1.1101 | 39.4971 | 62671.6093
[7 empty] | 10348 | 20221 | 1431566 | 2016-10-29 15:57 | 2016-10-29 18:15 | 138 | 11kV | 13809 | 931 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN3154 St Ives Panel 17 tripped reclosed tripped and locked out on B phase timed OC, Reclose Lockout, Reclose Timing Cause: Tree branch on OG mains at PT39 Waterhouse torrens removed by DOp See OMS 1431841 1431842 1431566 1431572 1431576 | October | 2016 | 2017Q2 | 2017 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Veg | 2016-10-29 | N | 14.8324 | N | 4 | N | N | 1.1101 | 39.4971 | 10091.2099
[7 empty] | 8971 | 3668 | 1431680 | 2016-10-30 17:25 | 2016-10-30 18:45 | 80.4333 | 11kV | 1447.8 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169153 A & B Phase DOLF : 20 Amp | October | 2016 | 2017Q2 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Veg | 2016-10-30 | N | 80.4333 | N | 7 | N | N | 1.1101 | 39.4971 | 1058.0095
[7 empty] | 10154 | 17818 | 1431677 | 2016-10-30 17:11 | 2016-10-30 20:45 | 214 | 11kV | 2996 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169155 B & C phase DOLF : 40 Amp Excluded OMS 1431677 | October | 2016 | 2017Q2 | 2017 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Veg | 2016-10-30 | N | 214 | N | 7 | N | N | 1.1101 | 39.4971 | 2189.3884
[7 empty] | 9254 | 7015 | 1431690 | 2016-10-30 18:04 | 2016-10-30 22:25 | 261 | 11kV | 13572 | 52 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 169156 interrupt to repair 2 x tappings at ABS 74218 Excluded OMS 1431690, 1431698 & 1431702 | October | 2016 | 2017Q2 | 2017 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Not Veg | 2016-10-30 | N | 261 | N | 7 | N | N | 1.1101 | 39.4971 | 9918.0173
[7 empty] | 8765 | 940 | 1431675 | 2016-10-30 16:36 | 2016-10-30 22:50 | 374 | 11kV | 99603 | 1672 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 169152 3 phase Car hit pole JU-42083 Fdr 12205 kotara interupted for safety by sop quail. dq Excluded oms 1431675## | October | 2016 | 2017Q2 | 2017 | 205:12205 | 205:12205 | ZN00205/012205 | LAKE MACQUARIE | OH | Not Veg | 2016-10-30 | N | 59.5712 | N | 7 | N | N | 1.1101 | 39.4971 | 72786.9346
[7 empty] | 8806 | 1558 | 1431725 | 2016-10-30 22:13 | 2016-10-31 00:01 | 108 | 11kV | 110784 | 1043 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn9550 Gwawley Bay Panel 43 ''S48722' feeder has tripped Signals: 11kv trip Relays: EF and EFI, 150tN, 51N Field EFI's: S49722, S49698. No operation at S9073 Remarks: cause not ascertained | October | 2016 | 2017Q2 | 2017 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Veg | 2016-10-30 | N | 106.2167 | N | 7 | N | N | 1.1101 | 39.4971 | 80957.6796
[7 empty] | 9844 | 14119 | 1431728 | 2016-10-30 23:01 | 2016-10-31 00:02 | 61 | 11kV | 39040 | 640 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN3425 Castle Cove Panel 28 Rec 49995 Holly Kendall Tripped Signals: 11kV trip Relays: OC trip EF Trip Possum Found Dead at base of LB62054 | October | 2016 | 2017Q2 | 2017 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | OH | Not Veg | 2016-10-30 | N | 61 | N | 7 | N | N | 1.1101 | 39.4971 | 28529.2805
[7 empty] | 9994 | 15918 | 1431731 | 2016-10-31 00:46 | 2016-10-31 02:36 | 110 | 11kV | 13640 | 124 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12640 Umina section of Pa15 PT18716 Australia Ocean Beach centre phase HDO was found blown 63Amps Cause not ascertained See 1432217 exclude 1431731,2 | October | 2016 | 2017Q2 | 2017 | ZN12640:PA15 | ZN12640:PA5 | ZN12640/000005 | CENTRAL COAST | OH | Veg | 2016-10-31 | N | 110 | N | 2 | N | N | 1.1101 | 39.4971 | 9967.7097
[7 empty] | 8727 | 127 | 1431715 | 2016-10-30 21:19 | 2016-10-31 03:10 | 351 | 11kV | 115435 | 1435 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | LID 169157 2 fault operations 3 phase Overcurrent UGOH failed at pole OS-20183. Excluded OMS 1431715 & 1431721. | October | 2016 | 2017Q2 | 2017 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | Unknown | Unknown | 2016-10-30 | N | 80.4425 | N | 7 | N | N | 1.1101 | 39.4971 | 84356.4932
[7 empty] | 10226 | 18803 | 1431733 | 2016-10-31 05:26 | 2016-10-31 10:25 | 299 | 11kV | 7297 | 79 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn15005 Belrose Panel 10 - Recloser 24722 Forest Crozier has tripped on OC trip and Lockout Cause: tree on OH mains Morgan Rd Oxford Falls See OMS 1432035 1432036 1431733 | October | 2016 | 2017Q2 | 2017 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Veg | 2016-10-31 | N | 92.3671 | N | 2 | N | N | 1.1101 | 39.4971 | 5332.4324
[7 empty] | 8835 | 1846 | 1431999 | 2016-11-01 03:25 | 2016-11-01 04:39 | 74 | 11kV | 36482 | 493 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169169 3 fault operation B & C phase Overcurrent | November | 2016 | 2017Q2 | 2017 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Veg | 2016-11-01 | N | 74 | N | 7 | N | N | 1.1101 | 39.4971 | 26659.9696
[7 empty] | 10200 | 18545 | 1432003 | 2016-11-01 04:48 | 2016-11-01 06:23 | 95 | 11kV | 5490 | 66 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S1648 Enfield Zn Panel #13 labelled Sub 35902 tripped on Relays: Translay, EFI Signals: 11kv trip, Group earth, Zone earth Field EFI's S35902 Remarks: UG fault. 11kv feeder from S35902 Telopea Hume Sw/B to Sub 7815 Braidwood Hume Sw/A. Switching Tag at Sub 35902 Telpoea Hume. | November | 2016 | 2017Q2 | 2017 | ZN1648:PA13 | ZN4853:PA22 | ZN04853/000022 | STRATHFIELD | UG | Not Veg | 2016-11-01 | N | 83.1818 | N | 7 | N | N | 1.1101 | 39.4971 | 4011.9301
[7 empty] | 9020 | 4235 | 1432002 | 2016-11-01 03:02 | 2016-11-01 12:28 | 566 | 11kV | 5647 | 10 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa20 "Warnervale West Railway" RE45203 Butt Gas Generator tripped due to low volt caused by 11kv Bond off just after tee off main feeder to reclosed 47302 Hue Hue Sparks 0.1 See 1434983,5 exclude 1432002,17 | November | 2016 | 2017Q2 | 2017 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2016-11-01 | N | 564.7 | N | 7 | N | N | 1.1101 | 39.4971 | 4126.661
[7 empty] | 9917 | 14976 | 1432094 | 2016-11-01 11:00 | 2016-11-01 12:45 | 105 | 11kV | 1995 | 19 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169175 Potential hazard reported by Adam Chapman. Mains may sag into newly installed pole GS-40014 in hot weather. | November | 2016 | 2017Q2 | 2017 | 507:80925 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2016-11-01 | N | 105 | N | 7 | N | N | 1.1101 | 39.4971 | 1457.8872
[7 empty] | 9054 | 4803 | 1432102 | 2016-11-01 11:35 | 2016-11-01 13:00 | 85 | 11kV | 2380 | 28 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Panel 37 PT12545 Willdeow Moores 11kv A phase 20amp Drop out fuse operated UG section of Dist 2 from PT12545 was hit by contractor. LV fuse did not grade. Jointer notified and isolated minor section of distributor which is still affected. See 1434986 GIS 1432127 exclude 1432102 | November | 2016 | 2017Q2 | 2017 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | UG | Not Veg | 2016-11-01 | N | 85 | N | 7 | N | N | 1.1101 | 39.4971 | 1739.2338
[7 empty] | 8932 | 3062 | 1432039 | 2016-11-01 09:02 | 2016-11-01 17:40 | 518 | 11kV | 518 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 169174 Single phase Live Line Clamp burnt off. | November | 2016 | 2017Q2 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2016-11-01 | N | 518 | N | 7 | N | N | 1.1101 | 39.4971 | 378.5391
[7 empty] | 9806 | 13694 | 1432177 | 2016-11-01 15:41 | 2016-11-01 21:35 | 354 | 11kV | 135753 | 1316 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 169176 1 fault operation B phase Earth fault Car into pole FS-93247 Excluded OMS 1432177 | November | 2016 | 2017Q2 | 2017 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2016-11-01 | N | 103.1558 | N | 7 | N | N | 1.1101 | 39.4971 | 99204.2884
[7 empty] | 9490 | 9864 | 1432256 | 2016-11-02 07:09 | 2016-11-02 11:17 | 248 | 11kV | 992 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169181 Live line lead aged - replaced (T O'Mahony) Found HV dropper lead burnt off at top of Dolf at Tx 52842. Opened and DT LV fuses at TX 52842 | November | 2016 | 2017Q2 | 2017 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2016-11-02 | N | 248 | N | 1 | N | N | 1.1101 | 39.4971 | 724.9243
[7 empty] | 10204 | 18605 | 1432458 | 2016-11-03 00:07 | 2016-11-03 02:42 | 155 | 11kV | 163695 | 1479 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn901 Surry Hills Pnl.18 tripped on: Earth leakage Field EFIs: All flagged down to S5240 Sw/B UG cable fault from S1016 to S112 (Sw /A) tee Tx #1 @ S1016 See 1432458 1432461 | November | 2016 | 2017Q2 | 2017 | ZN901:PA18 | ZN901:PA38 | ZN00901/000038 | SYDNEY | UG | Not Veg | 2016-11-03 | N | 110.6795 | N | 3 | N | N | 1.1101 | 39.4971 | 119623.4778
[7 empty] | 9962 | 15424 | 1432583 | 2016-11-03 15:42 | 2016-11-03 17:30 | 108 | 11kV | 68911 | 1042 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S2635 Epping Panel 52 tripped and locked out on Earth Fault with EFI reclose and lockout relays Abnormal Switching: SWB Closed at S8770 with AB790 Open and Defective Cause: Fault at the bottom of UGOH between LB916 to SW/A at S61095, AB3036 and LB1659. Fire looks to have started under the HV troughing and caught onto the area surrounding which was very dry See OMS 1433298 1433299 1433300 1432583 | November | 2016 | 2017Q2 | 2017 | ZN2635:PA52 | ZN2635:PA52 | ZN02635/000052 | HORNSBY | Unknown | Unknown | 2016-11-03 | N | 66.1334 | N | 3 | N | N | 1.1101 | 39.4971 | 50358.1263
[7 empty] | 9440 | 9279 | 1432592 | 2016-11-03 16:11 | 2016-11-03 19:11 | 180 | 11kV | 41040 | 228 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | Ex Panel 16 Marrickville Zone @ S.542 Macaulay Lane No.2 No protection Operations Remarks: Transformer failure. Low volts on B phase. Suspect defective/high resistance tx or tapchanger. Access given for T/con to test. Dop measure volts of A - 241V, B -192V, C - 241V with 200A/phase tx load. | November | 2016 | 2017Q2 | 2017 | ZN262:PA16 | ZN262:PA16 | ZN00262/000016 | INNER WEST | UG | Not Veg | 2016-11-03 | N | 180 | N | 3 | N | N | 1.1101 | 39.4971 | 29990.8215
[7 empty] | 10283 | 19361 | 1432652 | 2016-11-04 03:32 | 2016-11-04 04:10 | 38 | 11kV | 2470 | 65 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169215 A Phase DOLF : 31 Amp Excluded OMS 1432652 | November | 2016 | 2017Q2 | 2017 | 205:12203 | 205:12203 | ZN00205/012203 | NEWCASTLE | OH | Not Veg | 2016-11-04 | N | 38 | N | 2 | N | N | 1.1101 | 39.4971 | 1805.0031
[7 empty] | 9369 | 8338 | 1432809 | 2016-11-04 22:02 | 2016-11-04 22:36 | 34 | 11kV | 1326 | 39 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa13 PT14370 Kauri Shirley HDO centre phase 31.5Amp fuse had blown Dead possum at PT See 1435003 exclude 1432809,10 | November | 2016 | 2017Q2 | 2017 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2016-11-04 | N | 34 | N | 2 | N | N | 1.1101 | 39.4971 | 969.0017
[7 empty] | 9444 | 9319 | 1432817 | 2016-11-05 03:31 | 2016-11-05 04:54 | 83 | 11kV | 187912 | 2264 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At S2635 Epping panel 35 tripped on A and C phase IOC with Earth Fault Anbormal Switching: SW/B Closed at S5604 AB3036 and CP790 Open Cause: Possum found at the base of UGOH near Sub 5635 See OMS 1433190 1432817 | November | 2016 | 2017Q2 | 2017 | ZN2635:PA35 | ZN2635:PA35 | ZN02635/000035 | RYDE | OH | Not Veg | 2016-11-05 | N | 83 | N | 9 | N | N | 1.1101 | 39.4971 | 137320.5471
[7 empty] | 9153 | 6024 | 1432867 | 2016-11-05 12:06 | 2016-11-05 14:51 | 165 | 11kV | 197340 | 1196 | HV | 3rd Party Action | 3rd Party Impact | OTHER - REFER COMMENTS | Unplanned | Wind Strong | N | Zn9252 Jannali Pnl.27 - AB35647 was found open by DOp. Abnormal: LB35571 open with LB35517 Closed. Sw/A @ S9235 Open with LB 35626 Closed. Phantom Operator - DOp opened S9558 (Sw/B) @ 14:45 before closing AB35647 | November | 2016 | 2017Q2 | 2017 | ZN9252:PA27 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | Unknown | Not Veg | 2016-11-05 | N | 165 | N | 9 | N | N | 1.1101 | 39.4971 | 144210.2515
[7 empty] | 10078 | 16928 | 1432986 | 2016-11-05 18:53 | 2016-11-05 19:00 | 7 | 11kV | 3850 | 550 | HV | Bushfire | Adverse Weather/Environment | UGOH | Unplanned | Wind Strong | N | LID 169237 Sw opened to put fire out on UGOH pole FT-23112. -part of bushfire as per Guy Munro | November | 2016 | 2017Q2 | 2017 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2016-11-05 | N | 7 | N | 9 | N | N | 1.1101 | 39.4971 | 2813.4664
[7 empty] | 9257 | 7036 | 1432950 | 2016-11-05 15:09 | 2016-11-05 20:30 | 321 | 11kV | 6106 | 90 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 169238 2 fault operations Pole SF-10274 Feeder fell off pin after high wind broke tie. See previous T&R at 1502. | November | 2016 | 2017Q2 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2016-11-05 | N | 67.8444 | N | 9 | N | N | 1.1101 | 39.4971 | 4462.0847
[7 empty] | 9105 | 5415 | 1432912 | 2016-11-05 12:58 | 2016-11-05 20:50 | 471.9 | 11kV | 2831.4 | 6 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | Ex Zn12630 Peats Ridge section of Pa23 PT13299 Maroney Wise Ferry 0.7 interrupted by DOp to allow lineworker. Broken LV crossarm causing wires down. Minor Part of distributor affected at around 13:00 hours) before DOp's interruption. From customer calls first customer out was affected prior to DOps interruption. CC1: 23-"Mains Required" FRC1: 332-"Distributors Down - Cut away and made safe" | November | 2016 | 2017Q2 | 2017 | ZN12630:PA23 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2016-11-05 | N | 471.9 | N | 9 | N | N | 1.1101 | 39.4971 | 2069.1036
[7 empty] | 9172 | 6228 | 1433018 | 2016-11-05 22:36 | 2016-11-06 00:28 | 112 | 11kV | 96155 | 2031 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 4 tripped on Earth Fault, EFi and Fault Check Cause: 11kV Feeder fault between S8562 Frank College to S6300 College Laundries See OMS 1433206 1433209 1433210 1433200 1433018 | November | 2016 | 2017Q2 | 2017 | ZN4545:PA4 | ZN4545:PA4 | ZN04545/000004 | RYDE | UG | Not Veg | 2016-11-05 | N | 47.3437 | N | 9 | N | N | 1.1101 | 39.4971 | 70267.2379
[7 empty] | 9414 | 8957 | 1432998 | 2016-11-05 21:25 | 2016-11-06 01:10 | 225 | 11kV | 26407 | 292 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12640 Umina 11kv Panel 1 "LB478344" fdr tripped, reclosed and locked out Relays: Earth Fault, EFI, A Phase IOC, LO Signals: 11kv trip EFI's:Nil Possum brought down earth wire of 830 fdr into 66kV and 11kV feeders See 1435029 2nd 1435021,3,5,6 exclude 1432998,3000,2,4,7,29 | November | 2016 | 2017Q2 | 2017 | ZN12640:PA1 | ZN12640:PA1 | ZN12640/000001 | CENTRAL COAST | OH | Not Veg | 2016-11-05 | N | 90.4349 | N | 9 | N | N | 1.1101 | 39.4971 | 19297.4567
[7 empty] | 8775 | 1062 | 1433016 | 2016-11-05 22:28 | 2016-11-06 08:30 | 602 | 11kV | 3010 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169243 C Phase DOLF : 10 Amp Excluded OMS 1433016 | November | 2016 | 2017Q2 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-11-05 | N | 602 | N | 9 | N | N | 1.1101 | 39.4971 | 2199.6192
[7 empty] | 9766 | 13258 | 1432992 | 2016-11-05 19:51 | 2016-11-06 12:15 | 984 | 11kV | 40916 | 83 | HV | Fire (Non Ausgrid) | UNKNOWN | Pole | Unplanned | Wind Strong | N | LID 169241 3 fault operation 3 phase Earth Fault Excluded OMS 1432992 | November | 2016 | 2017Q2 | 2017 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Not Veg | 2016-11-05 | N | 492.9639 | N | 9 | N | N | 1.1101 | 39.4971 | 29900.206
[7 empty] | 9521 | 10239 | 1433079 | 2016-11-06 12:21 | 2016-11-06 12:48 | 27 | 11kV | 11077 | 476 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 169245 hot joint on ABS 74679, fdr dipped to open ABS Excluded oms 1433079,1433082,1433071 | November | 2016 | 2017Q2 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2016-11-06 | N | 23.271 | N | 3 | N | N | 1.1101 | 39.4971 | 8094.7449
[7 empty] | 10218 | 18745 | 1433049 | 2016-11-06 08:10 | 2016-11-06 14:24 | 374 | 11kV | 67531 | 559 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 169246 1 fault operation A & B phase Overcurrent Tree fell on mains from bushfire 11kV mains on the ground | November | 2016 | 2017Q2 | 2017 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2016-11-06 | N | 120.8068 | N | 3 | N | N | 1.1101 | 39.4971 | 49349.663
[7 empty] | 9903 | 14846 | 1433109 | 2016-11-06 15:58 | 2016-11-06 17:45 | 107 | 11kV | 68686 | 900 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35800 Panel 16 "S5149 Cantebury Fair" feeder tripped Signals: 11kv trip Relays: EFC (50TN), EF(51N), EFI Remarks: UG fault. 11kv UG feeder fault from S5946 Arkley Stacey (Sw/B) to S6417 Seddon St West (Sw/A) to S35925 Boxley Crescent (Sw/A) | November | 2016 | 2017Q2 | 2017 | ZN35800:PA16 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-11-06 | N | 76.3178 | N | 3 | N | N | 1.1101 | 39.4971 | 50193.7029
[7 empty] | 9249 | 6989 | 1433149 | 2016-11-07 01:10 | 2016-11-07 02:20 | 70 | 11kV | 21630 | 309 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn931 Darlinghurst - Pnl.24 - tripped on: B phase Earth Fault, EFI UG cable fault form panel 24 to S6101 Burrapore Corfu | November | 2016 | 2017Q2 | 2017 | ZN931:PA24 | ZN931:PA24 | ZN00931/000024 | SYDNEY | UG | Not Veg | 2016-11-07 | N | 70 | N | 3 | N | N | 1.1101 | 39.4971 | 15806.566
[7 empty] | 10228 | 18836 | 1433168 | 2016-11-07 08:03 | 2016-11-07 12:20 | 256.9333 | 11kV | 1284.6667 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169258 fdr opened at abs 74804 to repair ohm | November | 2016 | 2017Q2 | 2017 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Not Veg | 2016-11-07 | N | 256.9333 | N | 3 | N | N | 1.1101 | 39.4971 | 938.7965
[7 empty] | 9025 | 4279 | 1433400 | 2016-11-07 17:31 | 2016-11-08 03:23 | 592 | 11kV | 136568 | 278 | HV | Fire (Non Ausgrid) | UNKNOWN | Pole | Unplanned | No Weather Impact | N | LID 169261 Bushfire burnt pole FT-31548. Isolated to replace that pole and two other adjacent poles. Excluded OMS 1433400 | November | 2016 | 2017Q2 | 2017 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2016-11-07 | N | 491.2518 | N | 3 | N | N | 1.1101 | 39.4971 | 99799.8663
[7 empty] | 9630 | 11555 | 1433490 | 2016-11-08 10:05 | 2016-11-08 11:14 | 69 | 11kV | 1261 | 19 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2635 Epping Panel 33 tripped on Signals: 11kV trip Relays: Basele BE1 Combined O/C EF and EFI Relay - 50TA = A phase OC, Earth Fault Cause: there is an UG fault in the section of 11kV feeder between S7741 and S6151 See OMS 1433758 1433759 1433490 | November | 2016 | 2017Q2 | 2017 | ZN2635:PA33 | ZN2635:PA33 | ZN02635/000033 | RYDE | UG | Not Veg | 2016-11-08 | N | 66.3684 | N | 9 | N | N | 1.1101 | 39.4971 | 921.5016
[7 empty] | 8926 | 2963 | 1433433 | 2016-11-08 05:27 | 2016-11-08 16:15 | 648 | 11kV | 233169 | 1501 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At ZN3472 Sefton Panel No.28 "Baird Buist" feeder tripped and reclosed on Signals: 11kv trip, Zone earth, Tx2 Group Earth (Also Tx2 & Tx4 Thermal) Relays: E/F Check, Timing, Lockout, Remarks: vehicle hit pole. 167 Henry Lawson Drive | November | 2016 | 2017Q2 | 2017 | ZN3472:PA28 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-11-08 | N | 155.3424 | N | 9 | N | N | 1.1101 | 39.4971 | 170393.0279
[7 empty] | 9362 | 8217 | 1433582 | 2016-11-08 15:10 | 2016-11-08 17:55 | 165 | 11kV | 330 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169278 Single phase DOLF : 10 Amp Bird at base of sub pole. | November | 2016 | 2017Q2 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2016-11-08 | N | 165 | N | 9 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 10242 | 18947 | 1433574 | 2016-11-08 14:53 | 2016-11-08 18:00 | 187 | 11kV | 1683 | 9 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 169276 11kV Bridge at Pole AI-90379 broken. No Prot Op Excluded OMS 1433574 | November | 2016 | 2017Q2 | 2017 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2016-11-08 | N | 187 | N | 9 | N | N | 1.1101 | 39.4971 | 1229.8868
[7 empty] | 10367 | 20423 | 1433636 | 2016-11-08 18:42 | 2016-11-08 20:43 | 121 | 11kV | 184690 | 2012 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Lightning | N | Zn15012 Killarney Panel 4 "USL 23681" fdr opened on earth leakage, reclose timing & lockout relays, frame leakage fault check, EFI Fault Check No2 Tx Panel EFI's: S16795 S16846 S17136 Abnormal: USL 23330 Open & defective. N/O LB22077 closed Cause: Lihtning appears to have struck HV UGOH between S17136 S17150 S15775 See 1435094,5,6,7 exclude 1433636,9,41 | November | 2016 | 2017Q2 | 2017 | ZN15012:PA4 | ZN15012:PA4 | ZN15012/000004 | NORTHERN BEACHES | Unknown | Unknown | 2016-11-08 | N | 91.7942 | N | 9 | N | N | 1.1101 | 39.4971 | 134966.0046
[7 empty] | 9051 | 4779 | 1433651 | 2016-11-08 19:04 | 2016-11-08 22:05 | 181 | 11kV | 1267 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169283 B phase DOLF : 20 Amp Excluded OMS 1433651 & 1433676 | November | 2016 | 2017Q2 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2016-11-08 | N | 181 | N | 9 | N | N | 1.1101 | 39.4971 | 925.8862
[7 empty] | 10092 | 17177 | 1433691 | 2016-11-08 21:49 | 2016-11-08 22:50 | 61 | 11kV | 73384 | 1912 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169284 2 fault operations A & B phase Overcurrent possum at sub 4600, sub damaged left interconnected Excluded oms 1433692 | November | 2016 | 2017Q2 | 2017 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2016-11-08 | N | 38.3808 | N | 9 | N | N | 1.1101 | 39.4971 | 53626.8627
[7 empty] | 9036 | 4499 | 1433727 | 2016-11-09 06:40 | 2016-11-09 08:55 | 135 | 11kV | 270 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169291 A phase DOLF : 10 Amp Excluded OMS 1433727 | November | 2016 | 2017Q2 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2016-11-09 | N | 135 | N | 5 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 8986 | 3846 | 1433774 | 2016-11-09 10:00 | 2016-11-09 12:15 | 135 | 11kV | 405 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169297 B Phase DOLF : 10 Amp Excluded OMS 1433774 | November | 2016 | 2017Q2 | 2017 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2016-11-09 | N | 135 | N | 5 | N | N | 1.1101 | 39.4971 | 295.9621
[7 empty] | 10178 | 18173 | 1433752 | 2016-11-09 08:28 | 2016-11-09 14:23 | 355 | 11kV | 710 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169296 Single phase DOLF : 10 Amp Excluded OMS 1433752 | November | 2016 | 2017Q2 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2016-11-09 | N | 355 | N | 5 | N | N | 1.1101 | 39.4971 | 518.8471
[7 empty] | 8778 | 1093 | 1433653 | 2016-11-08 19:10 | 2016-11-09 15:35 | 1225 | 11kV | 128432 | 669 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | CP1772 Seymours Creek tipped on OC, SF6 Pressure, Lockout out AUX supply Cause: 11kV Mains down in Milson Island - Suspect lightning See OMS 1435069 1435070 1435071 | November | 2016 | 2017Q2 | 2017 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2016-11-08 | N | 191.9761 | N | 9 | N | N | 1.1101 | 39.4971 | 93854.3175
[7 empty] | 10091 | 17165 | 1433675 | 2016-11-08 19:49 | 2016-11-09 20:15 | 1466 | 11kV | 3967 | 3 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | Ex Zn9700 Kirrawee Pnl.20 - REC 35006 National Park tripped on Overcurrent Burnt cross arm near LK35543 See 1433977 1433979 1433980 | November | 2016 | 2017Q2 | 2017 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2016-11-08 | N | 1322.3333 | N | 9 | N | N | 1.1101 | 39.4971 | 2898.9666
[7 empty] | 9134 | 5801 | 1433921 | 2016-11-09 18:32 | 2016-11-09 20:30 | 118 | 11kV | 354 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Lightning | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap Rd" fdr PT13359 Dog Trap Kilkenny 4.4 11kV 16Amp footpath side HDO operated Lightning Strike. Weather related. See 1435036 exclude 1439321,2 | November | 2016 | 2017Q2 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2016-11-09 | N | 118 | N | 5 | N | N | 1.1101 | 39.4971 | 258.6928
[7 empty] | 9698 | 12304 | 1433936 | 2016-11-09 20:43 | 2016-11-09 22:44 | 121 | 11kV | 217146 | 2275 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn15014 Mona Vale 11kV Pa19 fdr tripped on Relays: A Phase IOC, EFI, Fault Check, TX1 Fault Check Signals: 11kV trip, Zone Earth EFI's: S15225 S16810 S46757 S16277 Zn15014 Mona Vale 11kV Pa16 tripped on Relays: A Phase IOC, EF, EFI, Fault CHeck, Tx 1 Fault CHeck Signals: 11kv trip EFI's S15221 Abnormal: S46757:B Closed S15221:A Open 11kv fdr fault from S15221 Pittwater Waratah Sw/B to S16277 Golf Barrenjoey Sw/A to S16825 Pittwater Centre No1 Sw/A See 1435110,1,2,3 Exclude 1433936,7,42,3,4,6 | November | 2016 | 2017Q2 | 2017 | ZN15014:PA19 | ZN15014:PA19 | ZN15014/000019 | NORTHERN BEACHES | UG | Not Veg | 2016-11-09 | N | 95.4488 | N | 5 | N | N | 1.1101 | 39.4971 | 158683.8921
[7 empty] | 9286 | 7303 | 1434082 | 2016-11-10 12:05 | 2016-11-10 12:49 | 44 | 11kV | 38588 | 877 | HV | Animal Other | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15011 Beacon Hill 11kv fdr Pa8 "Rodborough Warringah" fdr tripped Relay: A & C Phase IOC Signals: 11kv trip EFI's: S16265 S17140 S17141 S16691 S15180 S16907 S16228 S46676 S46675 Abnormal: DAROS 391294 Pa2 to S16011 OOS. Closed S46675:B, Opened AB20519 & LB64925 Flashover by animal on section of OH near tee to S15882 no damage to OH See 1435125 exclude 1434082,5 | November | 2016 | 2017Q2 | 2017 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Not Veg | 2016-11-10 | N | 44 | N | 4 | N | N | 1.1101 | 39.4971 | 28198.9722
[7 empty] | 9484 | 9830 | 1434117 | 2016-11-10 14:15 | 2016-11-10 14:30 | 15 | 11kV | 315 | 21 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 169313 Wire off pin at IT-41743 unable to repair live line section isolated for repairs | November | 2016 | 2017Q2 | 2017 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2016-11-10 | N | 15 | N | 4 | N | N | 1.1101 | 39.4971 | 230.1927
[7 empty] | 9493 | 9883 | 1433951 | 2016-11-10 03:15 | 2016-11-10 15:30 | 735 | 11kV | 2205 | 3 | HV | 3rd Party Vehicle | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169303 no protection operation, section isolated after MVA at pole MG-90405. Excluded oms # 1433951 & 1433953 | November | 2016 | 2017Q2 | 2017 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2016-11-10 | N | 735 | N | 4 | N | N | 1.1101 | 39.4971 | 1611.349
[7 empty] | 8874 | 2474 | 1434199 | 2016-11-10 18:40 | 2016-11-10 20:00 | 80 | 11kV | 26484 | 370 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S874 Concord Panel 9 "George Rothwell" fdr tripped Relays: EFI Signals: 11kv trip, Zone earth, Tx 3 Group Earth Remarks: UG fault. 11kv feeder fault from S2653 George Vic to Sw/A S.1450 Homebush Bay Drive No.2 | November | 2016 | 2017Q2 | 2017 | ZN874:PA9 | ZN874:PA9 | ZN00874/000009 | CANADA BAY | UG | Not Veg | 2016-11-10 | N | 71.5784 | N | 4 | N | N | 1.1101 | 39.4971 | 19353.7261
[7 empty] | 10080 | 16938 | 1434231 | 2016-11-11 08:44 | 2016-11-11 10:26 | 102 | 11kV | 102 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169327 C Phase DOLF : 10 Amp | November | 2016 | 2017Q2 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2016-11-11 | N | 102 | N | 5 | N | N | 1.1101 | 39.4971 | 74.5386
[7 empty] | 10257 | 19066 | 1434255 | 2016-11-11 10:27 | 2016-11-11 11:45 | 78 | 11kV | 312 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169330 A Phase DOLF : 16 Amp Excluded OMS 1434255 | November | 2016 | 2017Q2 | 2017 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2016-11-11 | N | 78 | N | 5 | N | N | 1.1101 | 39.4971 | 228.0004
[7 empty] | 8850 | 2036 | 1434244 | 2016-11-11 10:07 | 2016-11-11 13:41 | 214 | 11kV | 2782 | 13 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 169328 B Phase ABS 74460B B PHASE LEG FELL APART ON SI-17047.SEE EMERGENCY SWITCHING. | November | 2016 | 2017Q2 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2016-11-11 | N | 214 | N | 5 | N | N | 1.1101 | 39.4971 | 2033.0035
[7 empty] | 8838 | 1877 | 1434521 | 2016-11-11 21:02 | 2016-11-11 21:36 | 34 | 11kV | 15538 | 457 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay - Pnl.4 tripped on: Earth Fault, EFI Field EFIs: S9831, S9456 Possum on 11kV UGOH in Evelyn St Near Port Hacking Rd | November | 2016 | 2017Q2 | 2017 | ZN9550:PA4 | ZN9550:PA4 | ZN09550/000004 | SUTHERLAND | OH | Not Veg | 2016-11-11 | N | 34 | N | 5 | N | N | 1.1101 | 39.4971 | 11354.7121
[7 empty] | 9926 | 15074 | 1434511 | 2016-11-11 20:02 | 2016-11-12 01:50 | 348 | 11kV | 43390 | 185 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa22 "Gunderman" Re45013 'Gunderman' tripped, reclosed and tripped on: Relays: Overcurrent Abnormal: Re61097 Wise Ferry Lavender 10.3 and Regulator 61098 Wise Ferry Lavender 10.3 OOS defective with bypass LB61079Z closed Tree on Overhead mains near PT11793 Wise Ferry Laven 10.9 See 1435054,5,6 exclude 1434511,3,6 | November | 2016 | 2017Q2 | 2017 | ZN12630:PA22 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2016-11-11 | N | 234.5405 | N | 5 | N | N | 1.1101 | 39.4971 | 31708.1322
[7 empty] | 9583 | 11021 | 1434534 | 2016-11-12 04:12 | 2016-11-12 05:26 | 74 | 11kV | 53206 | 719 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S35370 Galston Panel 8 tripped reclosed tripped and locked out on relays: Basler BE1-51BC, B and C phase Overcurrent Field EFI's - NIL Cause: Tree branch on OH mains near PT1595 Arcadia Blacks - Removed By DOps - No Further action required | November | 2016 | 2017Q2 | 2017 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2016-11-12 | N | 74 | N | 17 | N | N | 1.1101 | 39.4971 | 38881.3755
[7 empty] | 9123 | 5623 | 1434533 | 2016-11-12 04:17 | 2016-11-12 07:15 | 177.9667 | 11kV | 3559.3333 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169351 DOLF : 20 Amp | November | 2016 | 2017Q2 | 2017 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2016-11-12 | N | 177.9667 | N | 17 | N | N | 1.1101 | 39.4971 | 2601.0558
[7 empty] | 8915 | 2877 | 1435471 | 2016-11-12 03:37 | 2016-11-12 07:33 | 236 | 11kV | 236 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169338 1 fault operation 3 phase Overcurrent | November | 2016 | 2017Q2 | 2017 |  |  |  | SINGLETON | OH | Veg | 2016-11-12 | N | 236 | N | 17 | N | N | 1.1101 | 39.4971 | 172.4618
[7 empty] | 8969 | 3655 | 1434549 | 2016-11-12 07:12 | 2016-11-12 07:43 | 31 | 11kV | 18745 | 1795 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 169348 2 Fault operations A & B phase Overcurrent Tree branch on OHM adjacent ABS 43563 Wamberal St. No.1 prot = AB O/C. No.2 prot = AB O/C start. Excluded OMS 1434549 | November | 2016 | 2017Q2 | 2017 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Veg | 2016-11-12 | N | 10.4429 | N | 17 | N | N | 1.1101 | 39.4971 | 13698.2931
[7 empty] | 9389 | 8693 | 1434535 | 2016-11-12 04:35 | 2016-11-12 08:45 | 250 | 11kV | 6750 | 27 | HV | Animal Possum | Animal | Fuse | Unplanned | No Weather Impact | N | PT14051 Pleasent Valley manns HDO 31Amp C phase fuse blown. Possum across HDO | November | 2016 | 2017Q2 | 2017 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Not Veg | 2016-11-12 | N | 250 | N | 17 | N | N | 1.1101 | 39.4971 | 4932.7009
[7 empty] | 9460 | 9565 | 1434552 | 2016-11-12 07:32 | 2016-11-12 08:50 | 78 | 11kV | 156 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169350 DOLF : 10 Amp Excluded OMS 1434552 | November | 2016 | 2017Q2 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2016-11-12 | N | 78 | N | 17 | N | N | 1.1101 | 39.4971 | 114.0002
[7 empty] | 10252 | 19040 | 1434537 | 2016-11-12 05:02 | 2016-11-12 09:30 | 268 | 11kV | 86658 | 705 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 169345 4 fault operationsw Earth Fault damaged insulator at pole 8M-30073 Excluded oms 1434537 | November | 2016 | 2017Q2 | 2017 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2016-11-12 | N | 122.9191 | N | 17 | N | N | 1.1101 | 39.4971 | 63327.1104
[7 empty] | 10068 | 16788 | 1434532 | 2016-11-12 03:56 | 2016-11-12 09:40 | 344 | 11kV | 37888 | 200 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 169340 4 fault operations A & C phase Overcurrent; Earth fault wires down at pole DP-30703 Excluded oms # 1434532 | November | 2016 | 2017Q2 | 2017 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2016-11-12 | N | 189.44 | N | 17 | N | N | 1.1101 | 39.4971 | 27687.4329
[7 empty] | 9734 | 12790 | 1434540 | 2016-11-12 06:14 | 2016-11-12 09:50 | 216 | 11kV | 3456 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169349 A & B phase DOLF : 20 Amp Replaced fuses at LF 74846 & LF 74388, DOLF at sub 71314 Excluded OMS 1434540, 1434571 | November | 2016 | 2017Q2 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2016-11-12 | N | 216 | N | 17 | N | N | 1.1101 | 39.4971 | 2525.5429
[7 empty] | 9343 | 7977 | 1434539 | 2016-11-12 06:00 | 2016-11-12 11:10 | 309.5833 | 11kV | 1547.9167 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 169355 DOLF : 10 Amp | November | 2016 | 2017Q2 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2016-11-12 | N | 309.5833 | N | 17 | N | N | 1.1101 | 39.4971 | 1131.1718
[7 empty] | 9557 | 10759 | 1434545 | 2016-11-12 06:58 | 2016-11-12 12:00 | 302 | 11kV | 604 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169356 A phase DOLF : 10 Amp Excluded OMS 1434566, 1434545 | November | 2016 | 2017Q2 | 2017 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2016-11-12 | N | 302 | N | 17 | N | N | 1.1101 | 39.4971 | 441.3854
[7 empty] | 9334 | 7867 | 1434572 | 2016-11-12 08:52 | 2016-11-12 12:30 | 218 | 11kV | 436 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 169359 Single phase DOLF : 10 Amp replaced arrestor Excluded OMS 1434572 | November | 2016 | 2017Q2 | 2017 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2016-11-12 | N | 218 | N | 17 | N | N | 1.1101 | 39.4971 | 318.6159
[7 empty] | 10038 | 16463 | 1434561 | 2016-11-12 08:01 | 2016-11-12 12:40 | 279 | 11kV | 279 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169360 C Phase DOLF : 10 Amp Excluded OMS 1434561 | November | 2016 | 2017Q2 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2016-11-12 | N | 279 | N | 17 | N | N | 1.1101 | 39.4971 | 203.885
[7 empty] | 9868 | 14395 | 1434612 | 2016-11-12 13:29 | 2016-11-12 15:00 | 91 | 11kV | 273 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169363 B Phase DOLF : 10 Amp Excluded OMS 1434612 | November | 2016 | 2017Q2 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2016-11-12 | N | 91 | N | 17 | N | N | 1.1101 | 39.4971 | 199.5003
[7 empty] | 8924 | 2932 | 1434573 | 2016-11-12 10:37 | 2016-11-12 16:12 | 335 | 11kV | 5025 | 15 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | LID 169357 MVA - car hit & broke pole JS-12432, Isolated for repairs. excluded OMS 1434573 & 1434599 | November | 2016 | 2017Q2 | 2017 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2016-11-12 | N | 335 | N | 17 | N | N | 1.1101 | 39.4971 | 3672.1218
[7 empty] | 9687 | 12206 | 1434654 | 2016-11-12 17:54 | 2016-11-12 20:08 | 134 | 11kV | 20122 | 152 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 169364 3 fault operations Overcurrent faulty UGOH pole DD-30184 Excluded OMS 1434654 | November | 2016 | 2017Q2 | 2017 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | Unknown | Unknown | 2016-11-12 | N | 132.3816 | N | 17 | N | N | 1.1101 | 39.4971 | 14704.5641
[7 empty] | 10351 | 20246 | 1434700 | 2016-11-12 22:37 | 2016-11-13 01:20 | 163 | 11kV | 3912 | 24 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S2540 Daisy Car no1 - 11kV RMI B phase fuse operated (OFME 75Amp) Transformer tails defective. | November | 2016 | 2017Q2 | 2017 | ZN2196:PA11 | ZN2196:PA11 | ZN02196/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-11-12 | N | 163 | N | 17 | N | N | 1.1101 | 39.4971 | 2858.7742
[7 empty] | 9386 | 8649 | 1434706 | 2016-11-13 01:54 | 2016-11-13 05:02 | 188 | 11kV | 208166 | 1184 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9245 Engadine - 11kV pnl.3 tripped & reclosed to lockout x 2 on: Earth Fault, Reclose, Lockout Field EFIs: S9279, S9445, S48684, S9246, S9225 - Delays in restoration due to defective EFIs @ S9346, S9586 & EFIs on UGOH (x2) beyond S9225. UG cable fault from S48684 Princes Wilson (Sw/B) to S90785 Copeland Dalley (Sw/B) Note: Cut out extended due to HAZ switchgear at S9075 for testing. See 1434979 1434980 1434981 1434982 | November | 2016 | 2017Q2 | 2017 | ZN9245:PA3 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | UG | Not Veg | 2016-11-13 | N | 175.8159 | N | 7 | N | N | 1.1101 | 39.4971 | 152121.5729
[7 empty] | 10187 | 18337 | 1434705 | 2016-11-13 01:50 | 2016-11-13 07:25 | 335 | 11kV | 3015 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169367 C Phase DOLF : 16 Amp Excluded OMS 1434705 | November | 2016 | 2017Q2 | 2017 | 528:83014 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Veg | 2016-11-13 | N | 335 | N | 7 | N | N | 1.1101 | 39.4971 | 2203.2731
[7 empty] | 9234 | 6885 | 1434729 | 2016-11-13 08:54 | 2016-11-13 10:00 | 66 | 11kV | 264 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169368 B Phase DOLF : 10 Amp Excluded OMS 1434729 | November | 2016 | 2017Q2 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-11-13 | N | 66 | N | 7 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 9582 | 11012 | 1434724 | 2016-11-13 08:38 | 2016-11-13 10:14 | 96 | 11kV | 79394 | 873 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Panel 14 "Taven Pacific" tripped on Relays: overcurrent, Earth Fault, EFI and Fault check relay Signals: 11kv trip, Tx2 Group Earth EFI's: S18599 S18600 S14932 See 1435858,61,3 exclude 1434724 See 1434739 for PT12929 Drysden Court Yuruga due to LV//'s being left in | November | 2016 | 2017Q2 | 2017 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | UG | Not Veg | 2016-11-13 | N | 90.9439 | N | 7 | N | N | 1.1101 | 39.4971 | 58018.7935
[7 empty] | 9316 | 7706 | 1434767 | 2016-11-13 13:48 | 2016-11-13 20:45 | 417 | 11kV | 36637 | 559 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 169375 1 fault operation B & C Phase Overcurrent burnt off tapping ugoh pole FS-80005 Excluded oms 1434768 | November | 2016 | 2017Q2 | 2017 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2016-11-13 | N | 65.5403 | N | 7 | N | N | 1.1101 | 39.4971 | 26773.239
[7 empty] | 8980 | 3751 | 1434753 | 2016-11-13 12:57 | 2016-11-13 22:40 | 583 | 11kV | 583 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 169376 Single phase broken ll dropper repaired under AP Excluded oms 1434753 | November | 2016 | 2017Q2 | 2017 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2016-11-13 | N | 583 | N | 7 | N | N | 1.1101 | 39.4971 | 426.0392
[7 empty] | 9276 | 7226 | 1434802 | 2016-11-13 15:50 | 2016-11-14 01:10 | 560 | 11kV | 117361 | 1067 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind Strong | N | LID 169373/02 Isolated for repairs no CB operation Excluded OMS 1434802 | November | 2016 | 2017Q2 | 2017 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Not Veg | 2016-11-13 | N | 109.9916 | N | 7 | N | N | 1.1101 | 39.4971 | 85763.9572
[7 empty] | 9443 | 9310 | 1434904 | 2016-11-14 05:31 | 2016-11-14 08:57 | 205.7833 | 11kV | 155572.2 | 756 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S547 Rockwall Cres - Tx 1 & 2 found tripped. Sub has 2 Tx's with LV links onto common bar with parallel trip coils) Low oil in transformer 2 - Buccholz relayed latched. | November | 2016 | 2017Q2 | 2017 | ZN342:PA18 | ZN342:PA18 | ZN00342/000018 | SYDNEY | UG | Not Veg | 2016-11-14 | N | 205.7833 | N | 7 | N | N | 1.1101 | 39.4971 | 113687.5752
[7 empty] | 9935 | 15169 | 1434966 | 2016-11-14 09:43 | 2016-11-14 11:30 | 107 | 11kV | 7811 | 73 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169385 Broken LL lead to DOLF | November | 2016 | 2017Q2 | 2017 | 528:83014 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Not Veg | 2016-11-14 | N | 107 | N | 7 | N | N | 1.1101 | 39.4971 | 5708.0484
[7 empty] | 9022 | 4238 | 1435075 | 2016-11-14 13:45 | 2016-11-14 17:10 | 205 | 11kV | 1435 | 7 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169387 Line DOLF :20 Amp C phase DOLF at sub 72880 : 10 Amp jobs were found in Muswellbrook queue. Dead bird found at base of sub 72880. Excluded OMS # 1435075 and 1435082 | November | 2016 | 2017Q2 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2016-11-14 | N | 205 | N | 7 | N | N | 1.1101 | 39.4971 | 1048.6557
[7 empty] | 8909 | 2826 | 1435136 | 2016-11-14 16:25 | 2016-11-14 17:20 | 55 | 11kV | 495 | 9 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 169389 Tree on Fdr at GW-40026 section isolated for removal Excluded OMS 1435136 | November | 2016 | 2017Q2 | 2017 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2016-11-14 | N | 55 | N | 7 | N | N | 1.1101 | 39.4971 | 361.7314
[7 empty] | 9340 | 7939 | 1435184 | 2016-11-14 18:32 | 2016-11-14 18:40 | 8 | 11kV | 5560 | 695 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn2400 Berowra Panel 11 recloser CP3282 Alberta Ave Opened Cause: Tree against 11kV Near Ab1093. See OMS 1435870 1435184/185/186/187/188/189/190 | November | 2016 | 2017Q2 | 2017 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2016-11-14 | N | 8 | N | 7 | N | N | 1.1101 | 39.4971 | 4063.084
[7 empty] | 9940 | 15236 | 1435182 | 2016-11-14 18:31 | 2016-11-14 20:40 | 129 | 11kV | 903 | 7 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169390 No protection operation open circuit at LL Clamp. Partial interruption at 1831hrs one phase down full interruption at 1940hrs to allow repairs. Excluded OMS 1435182 | November | 2016 | 2017Q2 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2016-11-14 | N | 129 | N | 7 | N | N | 1.1101 | 39.4971 | 659.8858
[7 empty] | 9727 | 12672 | 1435225 | 2016-11-15 03:50 | 2016-11-15 09:30 | 340 | 11kV | 16257 | 109 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 169392 4 fault operations Overcurrent Broken xarm pole GU-33131. Excluded OMS 1435226 | November | 2016 | 2017Q2 | 2017 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2016-11-15 | N | 149.1468 | N | 4 | N | N | 1.1101 | 39.4971 | 11880.1361
[7 empty] | 10056 | 16650 | 1435142 | 2016-11-14 16:32 | 2016-11-15 11:40 | 1148 | 11kV | 151178 | 726 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12650 Panel 14 Hargraves Holden" fdr tripped on 3 phase IOC, OC & Earth Fault, EFI, Reclose time delay, lockout Crane hit OH. 14-22 Kendall ave Gosford crane toppled over trapping driver PT13016 DIst 2 customers interrupted - work cover investigation Gosford OH working under own CTW Section of 415V Dist#2 @ PT.13761 Donnison St.George is still interrupted and under access for safety / repair by Gosford O.H. under own CTW issued See 1436021,2 Exclude 1435142,5,52,205,7,912,3,4,5 | November | 2016 | 2017Q2 | 2017 | ZN12650:PA14 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | OH | Not Veg | 2016-11-14 | N | 208.2342 | N | 7 | N | N | 1.1101 | 39.4971 | 110476.4234
[7 empty] | 9743 | 12947 | 1435278 | 2016-11-15 09:35 | 2016-11-15 13:55 | 260 | 11kV | 101921 | 1086 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169398 A & B phase Earth Fault tree on fdr near sub 18542 Excluded OMS 1435278 | November | 2016 | 2017Q2 | 2017 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2016-11-15 | N | 93.8499 | N | 4 | N | N | 1.1101 | 39.4971 | 74480.8606
[7 empty] | 9798 | 13614 | 1435383 | 2016-11-15 15:13 | 2016-11-15 17:10 | 117 | 11kV | 90746 | 824 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1285 Greenacre park - Pnl.10 tripped on: B Phase timed OC, Earth Fault, EFI, Fault Check UG cable fault from Panel 10 to S4109 East Terrace (Sw/A) to S8025 East Tce South (Sw/A) | November | 2016 | 2017Q2 | 2017 | ZN1285:PA10 | ZN1285:PA10 | ZN01285/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-11-15 | N | 110.1286 | N | 4 | N | N | 1.1101 | 39.4971 | 66314.5002
[7 empty] | 9016 | 4159 | 1435426 | 2016-11-15 19:15 | 2016-11-15 20:50 | 95 | 11kV | 1615 | 17 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 169400 Interrution was to allow repairs. Car hit pole DP-30546 knocking mains from tie's and causing some damage to the pole. Staff report the pole is now sound and ok for the short term but advise it will need longer term repairs within the next month. No protection operated the interruption was to allow repairs and ensure cables correctly re attached to the insulators. | November | 2016 | 2017Q2 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2016-11-15 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 1180.1944
[7 empty] | 8837 | 1875 | 1435442 | 2016-11-16 00:49 | 2016-11-16 01:28 | 39 | 11kV | 35061 | 899 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn3472 Sefton - Pnl.22 tripped, reclosed & tripped on: A Phase IOC Cause not ascertained. Mains to patrol in daylight. | November | 2016 | 2017Q2 | 2017 | ZN3472:PA22 | ZN3472:PA22 | ZN03472/000022 | CANTERBURY-BANKSTOWN | OH | Veg | 2016-11-16 | N | 39 | N | 4 | N | N | 1.1101 | 39.4971 | 25621.5447
[7 empty] | 8827 | 1754 | 1435560 | 2016-11-16 11:35 | 2016-11-16 12:40 | 65 | 11kV | 455 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 169409 A Phase fuse loose in carrier Excluded oms 1435560 | November | 2016 | 2017Q2 | 2017 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2016-11-16 | N | 65 | N | 4 | N | N | 1.1101 | 39.4971 | 332.5006
[7 empty] | 10075 | 16870 | 1435443 | 2016-11-16 03:04 | 2016-11-16 12:57 | 593 | 11kV | 160963 | 281 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | 11kV feeder from S35062 Meakin Virgil (Sw/A) to LB2733 tee PT1658 Kembla Waldron was interrupted for safety. While investigating LV parallel failures realted to previous Pnl.22 trip & reclose, DOp noticed HV dropper touching LV mains at PT1658. PT was unable to be paralleled due to ongoing LV problems in the area. Outage given from 3:04am as that was when customers started calling in with supply issues. See 1435779 1435781 1435534 1435508 | November | 2016 | 2017Q2 | 2017 | ZN3472:PA22 | ZN3472:PA22 | ZN03472/000022 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-11-16 | N | 572.8221 | N | 4 | N | N | 1.1101 | 39.4971 | 117627.0128
[7 empty] | 9544 | 10510 | 1435643 | 2016-11-16 19:26 | 2016-11-16 20:05 | 39 | 11kV | 975 | 25 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169413 Frayed conductor at pole GT-82244. No protection operations interruption to allow immediate repairs to conductor. Excluded OMS 1435643. | November | 2016 | 2017Q2 | 2017 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2016-11-16 | N | 39 | N | 4 | N | N | 1.1101 | 39.4971 | 712.5012
[7 empty] | 9336 | 7871 | 1435709 | 2016-11-17 02:31 | 2016-11-17 04:20 | 109 | 11kV | 279950 | 2728 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.1 tripped on: Earth leakage, Fault Check & EFI Field EFIs: S2184, S2182, S2368 (Note: S7256 did not operate) UG cable fault from S2368 Tucabia (Sw/B) to S36062 Asturias Macdili No.2 (Sw.A) See 1435787 1435788 | November | 2016 | 2017Q2 | 2017 | ZN35600:PA1 | ZN35600:PA1 | ZN35600/000001 | RANDWICK | UG | Not Veg | 2016-11-17 | N | 102.621 | N | 3 | N | N | 1.1101 | 39.4971 | 204579.2029
[7 empty] | 9744 | 12956 | 1435715 | 2016-11-17 06:39 | 2016-11-17 07:25 | 46 | 11kV | 230 | 5 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of Pa24 "Burns Rd" PT11301 Palmdale Pacific 1.4 centre phase 16Amp HDO fuse operated Possum committed suicide See 1436048 exclude 1435715 | November | 2016 | 2017Q2 | 2017 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2016-11-17 | N | 46 | N | 3 | N | N | 1.1101 | 39.4971 | 168.0772
[7 empty] | 9952 | 15326 | 1435941 | 2016-11-17 20:37 | 2016-11-17 22:48 | 131 | 11kV | 132834 | 1014 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn15014 Mona Vale section of Pa11 RE20397 Pittwater Cabbage tripped and reclosed to lockout Relays: IOC trip, OC trip EFI's: S16702 S16490 S47095 Cause not ascertained Cust reported explosion but no evidence found See 1435941 exclude 1435947 | November | 2016 | 2017Q2 | 2017 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2016-11-17 | N | 131 | N | 3 | N | N | 1.1101 | 39.4971 | 97071.1693
[7 empty] | 8895 | 2728 | 1436059 | 2016-11-18 11:45 | 2016-11-18 13:00 | 75 | 11kV | 1050 | 14 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa21 "Virginia Rd" PT13600 Bruce Sparks 1.1 interrupted Due to Car hit Pole. OH resting on Cross arm See 1436603 exclude 1436061 | November | 2016 | 2017Q2 | 2017 | ZN14891:PA21 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Not Veg | 2016-11-18 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 767.309
[7 empty] | 9640 | 11671 | 1436124 | 2016-11-18 15:47 | 2016-11-18 17:00 | 73 | 11kV | 72348 | 1212 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn15002 Narrabeen Panel 2 tripped and reclosed on B and C phase OC, Reclose time delay, Reclose lockout Signals: 11kV Trip Cause: There was a large tree on the 11kV OH outside 6 Kalang Rd. This caused a burnt off bond at the tee off below S16499 Rickard Anana See OMS 1437303 1437304 1436128 1436126 1436125 1436124 | November | 2016 | 2017Q2 | 2017 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2016-11-18 | N | 59.6931 | N | 3 | N | N | 1.1101 | 39.4971 | 52869.7845
[7 empty] | 9195 | 6390 | 1436190 | 2016-11-18 21:15 | 2016-11-18 22:31 | 76 | 11kV | 108376 | 1426 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn180 Mosman Panel 35 tripped on Signals: 11kV Trip, TX4 Group Earth, Zone Earth Relays: Earth Fault, Fault Check and EFI Cause: Feeder fault section from S180 Mosman Pa35 to S35148 Belrrave Cooper See OMS 1437311 1436190 | November | 2016 | 2017Q2 | 2017 | ZN180:PA35 | ZN180:PA35 | ZN00180/000035 | NORTH SYDNEY | UG | Not Veg | 2016-11-18 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 79197.9842
[7 empty] | 9202 | 6490 | 1436202 | 2016-11-19 01:02 | 2016-11-19 02:23 | 81 | 11kV | 67959 | 839 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1193 Lindfield Panel 21 tripped and locked out on B phase IOC Signals: 11kV trip Field EFIs - Nil Cause: Possum cause flash over on mains in Shirley Rd near PT116 - No further action required See OMS 1436202 1436203 | November | 2016 | 2017Q2 | 2017 | ZN1193:PA21 | ZN1193:PA21 | ZN01193/000021 | KU-RING-GAI | OH | Veg | 2016-11-19 | N | 81 | N | 3 | N | N | 1.1101 | 39.4971 | 49662.4327
[7 empty] | 10320 | 19814 | 1436232 | 2016-11-19 10:52 | 2016-11-19 21:15 | 623 | 11kV | 78077 | 1245 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn12660 Woy Woy panel 4 fdr tripped on Signals: 11kv trip Relays: A phase timed + instantaneous, EF. (Note: Autoreclosing was auto at time, fdr does not appear to have attempted to auto close - There was no flags up on SEF, Lockout or Autoclosing Relays) RE48036 Rawson Woy Woy tripped & reclosed on re-energisiing panel 14 Woy Woy. Relays: ABC phase OC trip, IOC Trip Vehilce hit & split pole. HV came off pin insulator, LV mains on ground on Woy Woy Rd, nr Shoalhaven Drive, Woy Woy. HV isolated from LB41785 to AB44221 tee PT11684 for repairs. Suspect inrush current See 1437182,4,5,6,7 exclude 1436232,3,7,69,70 | November | 2016 | 2017Q2 | 2017 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2016-11-19 | N | 62.7124 | N | 3 | N | N | 1.1101 | 39.4971 | 57056.3687
[7 empty] | 8948 | 3330 | 1436284 | 2016-11-19 18:09 | 2016-11-20 00:30 | 381 | 11kV | 381 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 169439 Single phase DOLF : 10 Amp Blown Tx. Trip & Reclose on # 169437 Excluded OMS 1436284 | November | 2016 | 2017Q2 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2016-11-19 | N | 381 | N | 3 | N | N | 1.1101 | 39.4971 | 278.4236
[7 empty] | 10243 | 18953 | 1436328 | 2016-11-20 07:51 | 2016-11-20 10:00 | 129 | 11kV | 2727 | 23 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington - Pnl.6 - tripped on: Timed O/C, Earth Fault, EFI Field EFIs: S7661 UG cable fault from S7661 Aquatic Temp (Sw.B) to S63435 Herb Elliott Showground No.2 (Sw/A) to S352262 Olympic Herb Elliot (Sw/A) See 1436496 1436497 | November | 2016 | 2017Q2 | 2017 | ZN2466:PA6 | ZN36000:PA8 | ZN36000/000008 | PARRAMATTA | UG | Not Veg | 2016-11-20 | N | 118.5652 | N | 5 | N | N | 1.1101 | 39.4971 | 1992.8112
[7 empty] | 9841 | 14060 | 1436354 | 2016-11-20 11:08 | 2016-11-20 11:35 | 27 | 11kV | 162 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 169444 A Phase DOLF : 20 Amp Fuse Fatigue Excluded OMS 1436364 | November | 2016 | 2017Q2 | 2017 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2016-11-20 | N | 27 | N | 5 | N | N | 1.1101 | 39.4971 | 118.3848
[7 empty] | 9867 | 14381 | 1436343 | 2016-11-20 09:37 | 2016-11-20 11:50 | 132.5333 | 11kV | 1325.3333 | 10 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 169443 Single phase Broken 11kV tappping on link 40971 | November | 2016 | 2017Q2 | 2017 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2016-11-20 | N | 132.5333 | N | 5 | N | N | 1.1101 | 39.4971 | 968.5145
[7 empty] | 9467 | 9655 | 1436352 | 2016-11-20 10:58 | 2016-11-20 19:00 | 482 | 11kV | 52810 | 315 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169445 2 fault opeations C Phase Directional Overcurrent Sw 90525 Baiada -- Dir C phase O/C Sw 2728 Tarro sub -- A phase O/C, SEF Magpie caused flash over at pole IS-62830 bringing down 2 phases of 11kV, possible hit neutral LV conductor sub 10620. Also see report 169446. Excluded OMS 1436352. | November | 2016 | 2017Q2 | 2017 | 235:2728 | 235:2728 | ZN00235/002728 | NEWCASTLE | OH | Not Veg | 2016-11-20 | N | 167.6508 | N | 5 | N | N | 1.1101 | 39.4971 | 38591.9904
[7 empty] | 9665 | 11957 | 1436353 | 2016-11-20 11:45 | 2016-11-20 19:00 | 435 | 11kV | 47415 | 109 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169446 No protection operation, Isolated for outage Fdr 2728 to erect fallen 11kV conductors, suspect hit neutral conductor. Also see report 169445. | November | 2016 | 2017Q2 | 2017 | 235:8685 | 235:8685 | ZN00235/008685 | NEWCASTLE | OH | Not Veg | 2016-11-20 | N | 435 | N | 5 | N | N | 1.1101 | 39.4971 | 34649.4835
[7 empty] | 9452 | 9400 | 1436413 | 2016-11-21 00:19 | 2016-11-21 01:25 | 66 | 11kV | 38214 | 579 | HV | Excavation Ausgrid Staff | Utility Process Issue | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington - Pnl.33 tripped on: O/C, E/F, EFI UG cable damaged by Ausgrid staff working at Moore Park Rd near Anzac Pde on out of service cables in vicinity of 11kV panel 33 feeder. | November | 2016 | 2017Q2 | 2017 | ZN342:PA33 | ZN342:PA33 | ZN00342/000033 | SYDNEY | UG | Not Veg | 2016-11-21 | N | 66 | N | 9 | N | N | 1.1101 | 39.4971 | 27925.6641
[7 empty] | 10116 | 17442 | 1436435 | 2016-11-21 08:16 | 2016-11-21 09:56 | 100 | 11kV | 18152 | 192 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.14L tripped on: A phase O/C, Earth Fault, Fault Check, EFI Field EFIs: S61947 A person unloading copper piping at a construction site has hit the 11kV open wire and has been injured. See 1436776 1436777 | November | 2016 | 2017Q2 | 2017 | ZN10999:PA14 | ZN10999:PA14 | ZN10999/000014 | GEORGES RIVER | OH | Not Veg | 2016-11-21 | N | 94.5417 | N | 9 | N | N | 1.1101 | 39.4971 | 13264.9462
[7 empty] | 9318 | 7745 | 1436743 | 2016-11-21 15:02 | 2016-11-21 16:10 | 68 | 11kV | 68 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169452 A Phase DOLF : 10 Amp Excluded OMS 1436611 | November | 2016 | 2017Q2 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2016-11-21 | N | 68 | N | 9 | N | N | 1.1101 | 39.4971 | 49.6924
[7 empty] | 8877 | 2491 | 1436635 | 2016-11-21 15:35 | 2016-11-21 16:38 | 63 | 11kV | 252 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169451 B Phase DOLF : 10 Amp excluded OMS 1436635 | November | 2016 | 2017Q2 | 2017 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2016-11-21 | N | 63 | N | 9 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 8944 | 3296 | 1436597 | 2016-11-21 14:49 | 2016-11-21 18:35 | 226 | 11kV | 678 | 3 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | REC35006 National Park opened for safety Arcing at AB35970 | November | 2016 | 2017Q2 | 2017 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2016-11-21 | N | 226 | N | 9 | N | N | 1.1101 | 39.4971 | 495.4624
[7 empty] | 9187 | 6347 | 1436416 | 2016-11-21 02:55 | 2016-11-21 19:15 | 980 | 11kV | 71033 | 118 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT2456 Sutherland Cobran supply lost on A B and C Phase of distributor1 At S62030 Cheltenham Station supply lost of A B and C phase of distributor 3 At PT2378 Day Robecq supply lost of A B and C phase of distributor 2 At S7701 supply Lost on A B and C phase Cause: Tree brought down OH mains - above sub in LV parallel See OMS 1437291 1437292 1437293 1436418 1436416 1436417 1436418 | November | 2016 | 2017Q2 | 2017 | ZN965:PA15 | ZN965:PA15 | ZN00965/000015 | HORNSBY | OH | Veg | 2016-11-21 | N | 601.9746 | N | 9 | N | N | 1.1101 | 39.4971 | 51908.8213
[7 empty] | 9268 | 7173 | 1436669 | 2016-11-21 17:42 | 2016-11-21 19:30 | 108 | 11kV | 32918 | 307 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2835 Burwood - Pnl.17 tripped on: Earth fault, EFI, Fault Check Field EFIs: S2931, S6321 UG cable fault from S2931 Burwood Wilga (Sw/B) to S7650 Victoria Burwood No.1 (Sw/A) See 1436762 1436763 | November | 2016 | 2017Q2 | 2017 | ZN2835:PA17 | ZN2835:PA17 | ZN02835/000017 | BURWOOD | UG | Not Veg | 2016-11-21 | N | 107.2248 | N | 9 | N | N | 1.1101 | 39.4971 | 24055.5035
[7 empty] | 10195 | 18486 | 1436699 | 2016-11-21 20:23 | 2016-11-21 22:15 | 112 | 11kV | 112 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | S4100 beresford Coventry - Centre phase 11kV fuse blown (OQFRN 80A) Cause not ascertained. | November | 2016 | 2017Q2 | 2017 | ZN2835:PA41 | ZN2835:PA41 | ZN02835/000041 | STRATHFIELD | OH | Veg | 2016-11-21 | N | 112 | N | 9 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 10255 | 19048 | 1436714 | 2016-11-21 22:42 | 2016-11-22 00:15 | 93 | 11kV | 93 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169455 A Phase DOLF : 10 Amp Excluded OMS 1436714 | November | 2016 | 2017Q2 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-11-21 | N | 93 | N | 9 | N | N | 1.1101 | 39.4971 | 67.9617
[7 empty] | 9129 | 5742 | 1436723 | 2016-11-22 02:00 | 2016-11-22 02:44 | 44 | 11kV | 111100 | 2525 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn15001 Brookvale Panel 2 "Delmar Pittwater etc" fdr tripped Relays: OC & EF Signals: 11kv trip EFI's: Nil Abnormal: DMA LK22550 with S16015:B Closed Flashover cause by possum on UGOH cnr Headland nr Quick, no apparent damage See 1437408 exclude 1436723 | November | 2016 | 2017Q2 | 2017 | ZN15001:PA2 | ZN15001:PA2 | ZN15001/000002 | NORTHERN BEACHES | OH | Not Veg | 2016-11-22 | N | 44 | N | 9 | N | N | 1.1101 | 39.4971 | 81188.6031
[7 empty] | 8724 | 41 | 1437035 | 2016-11-22 07:46 | 2016-11-22 07:50 | 4 | 11kV | 6356 | 1589 | HV | Staff Other | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn3472 Sefton - Pnl.29 tripped on: SEL Zn3472 Sefton - Pnl.22 tripped on: SEL Operator error, SEL not made non-auto prior to routine switching for D/R 393199 - AB1867 N/O was closed. See 1437036 1437035 | November | 2016 | 2017Q2 | 2017 | ZN3472:PA22 | ZN3472:PA22 | ZN03472/000022 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2016-11-22 | N | 4 | N | 9 | N | N | 1.1101 | 39.4971 | 4644.7773
[7 empty] | 8927 | 2975 | 1436729 | 2016-11-22 03:45 | 2016-11-22 09:20 | 335 | 11kV | 1005 | 3 | HV | Animal Other | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169462 Single phase DOLF : 10 Amp Dead rats found at sub. Excluded OMS No. 1436729 | November | 2016 | 2017Q2 | 2017 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2016-11-22 | N | 335 | N | 9 | N | N | 1.1101 | 39.4971 | 734.4244
[7 empty] | 9365 | 8284 | 1436754 | 2016-11-22 09:55 | 2016-11-22 10:03 | 8 | 11kV | 768 | 96 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow Panel 13 "Brush Rd" section of 11kv fdr from AB44456 tee PT14372 to PT12227 Interrupted for safety reasons. Dead Possum within clearances of in service mains. See 1437224 exclude 1436754,89 | November | 2016 | 2017Q2 | 2017 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2016-11-22 | N | 8 | N | 9 | N | N | 1.1101 | 39.4971 | 561.2317
[7 empty] | 9978 | 15634 | 1436829 | 2016-11-22 11:55 | 2016-11-22 13:55 | 120 | 11kV | 40399 | 548 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At Zn4545 Meadowbank Panel 19 tripped on Relays: B phase OC, C phase OC, Fault Check EFI Signals 11kV Trip Zone Earth Protection UV, TX2 High Low Volts and TX2 Group Earth At S5246 Payten Phillip on Fire - UGOH isolated and sub put in parallel See OMS 1437380 1437381 1437382 | November | 2016 | 2017Q2 | 2017 | ZN4545:PA19 | ZN4545:PA19 | ZN04545/000019 | RYDE | UG | Not Veg | 2016-11-22 | N | 73.7208 | N | 9 | N | N | 1.1101 | 39.4971 | 29522.3976
[7 empty] | 8946 | 3312 | 1436861 | 2016-11-22 13:48 | 2016-11-22 14:47 | 59 | 11kV | 27967 | 499 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn931 Darlinghurst - Pnl.3 tripped UG cable fault from S64501 (Sw/B) to S6903 (Sw/A) S1437032 1437033 | November | 2016 | 2017Q2 | 2017 | ZN931:PA3 | ZN931:PA3 | ZN00931/000003 | SYDNEY | UG | Not Veg | 2016-11-22 | N | 56.0461 | N | 9 | N | N | 1.1101 | 39.4971 | 20437.4587
[7 empty] | 10086 | 17054 | 1436899 | 2016-11-22 16:21 | 2016-11-22 17:37 | 76 | 11kV | 37392 | 492 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn12660 Woy Woy panel 6 "Davidstown" fdr tripped, reclosed, tripped and locked out on: Relays: C phase timed, reclose timer, lock out signals: 11kv trip EFI's: Nil Burned branch found on ground near AB42445 also near report of loud noise before interruption See 1436899 exclude 1436902 | November | 2016 | 2017Q2 | 2017 | ZN12660:PA6 | ZN12660:PA6 | ZN12660/000006 | CENTRAL COAST | OH | Not Veg | 2016-11-22 | N | 76 | N | 9 | N | N | 1.1101 | 39.4971 | 27324.9707
[7 empty] | 9461 | 9589 | 1436912 | 2016-11-22 16:52 | 2016-11-22 18:11 | 79 | 11kV | 114787 | 1453 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10995 Riverwood - Pnl.5 tripped, reclosed and tripped on: C phase IOC and Timed O/C, EFI UG cable fault from panel to S10986 Cairns Erskine (Sw/A) via section of 11kV OH. See 1436912 | November | 2016 | 2017Q2 | 2017 | ZN10995:PA5 | ZN10995:PA5 | ZN10995/000005 | GEORGES RIVER | UG | Not Veg | 2016-11-22 | N | 79 | N | 9 | N | N | 1.1101 | 39.4971 | 83882.954
[7 empty] | 9279 | 7233 | 1436955 | 2016-11-22 18:53 | 2016-11-22 20:15 | 82 | 11kV | 82 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169473 Single phase DOLF : 10 Amp Excluded OMS 1436955 | November | 2016 | 2017Q2 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-11-22 | N | 82 | N | 9 | N | N | 1.1101 | 39.4971 | 59.9232
[7 empty] | 9121 | 5616 | 1437051 | 2016-11-23 09:50 | 2016-11-23 10:22 | 32 | 11kV | 22400 | 700 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn14892 Charmhaven panel 9 "Advance Crowe" CB tripped, reclosed and locked out on: Signals: 11kv trip, TX1 Group Earth Relays: Earth Fault, Relcose Lockout, Reclose timing, Fault CHeck EFI's: S14513 S14237 S18288 S16833 S14638 S14724 S14755 S14786 Staff Error. During process of isolating a section of fdr between S14786:B to AB40923 to LB40879 tee to PT13992 via S14725, the DOp inadvertantly applied the earth at S14725:B before isolating at S14786 | November | 2016 | 2017Q2 | 2017 | ZN14892:PA9 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | Unknown | Not Veg | 2016-11-23 | N | 32 | N | 5 | N | N | 1.1101 | 39.4971 | 16369.2593
[7 empty] | 9576 | 10949 | 1437098 | 2016-11-23 12:03 | 2016-11-23 12:55 | 52 | 11kV | 16586 | 327 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn630 Mascot - Pnl.32 tripped on: Earth leakage with EFI Field EFI: All down to S2200 (Sw/A) UG cable fault from S2200 (Sw/A) to S 7926 See 1437342 1437343 | November | 2016 | 2017Q2 | 2017 | ZN630:PA32 | ZN630:PA18 | ZN00630/000018 | BAYSIDE | UG | Not Veg | 2016-11-23 | N | 50.7217 | N | 5 | N | N | 1.1101 | 39.4971 | 12120.5596
[7 empty] | 9592 | 11159 | 1437111 | 2016-11-23 12:52 | 2016-11-23 15:10 | 138 | 11kV | 69985 | 513 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | At Zn35370 Galston Panel 10 tripped on SEL Recloser CP50015 Quarry Old Northern tripped on on A and B overcurrent Cause: suspect flash over beyond Recloser 50015 and Bond Burnt between Pt2125 and Ab2270 at pole DU00056 Also - suspect Grass fire started due to burn bond See OMS 1438240 1438242 | November | 2016 | 2017Q2 | 2017 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2016-11-23 | N | 136.423 | N | 5 | N | N | 1.1101 | 39.4971 | 51142.9738
[7 empty] | 10366 | 20420 | 1437230 | 2016-11-23 17:36 | 2016-11-23 19:15 | 99.0667 | 11kV | 15058.1333 | 152 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 169488 B & C Phase DOLF : 31 Amp Damage appears to have been from a lightning strike. B and C phase HV lightning arrestors had blown and pole had some fire damage. DOPS requested Fire Brigade attend to put out pole fire. Excluded OMS 1437232, 1437236 and 1437249. | November | 2016 | 2017Q2 | 2017 | 240:34849 | 240:34849 | ZN00240/034849 | NEWCASTLE | OH | Not Veg | 2016-11-23 | N | 99.0667 | N | 5 | N | N | 1.1101 | 39.4971 | 11004.0397
[7 empty] | 10147 | 17770 | 1437277 | 2016-11-23 23:00 | 2016-11-24 00:16 | 75.5333 | 11kV | 67904.4667 | 899 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman Panel 33 tripped on: Relays: A+C phase instantaneous, A phase timed, Earth Fault, EFI, Fault CHeck Signals:11kv trip, Tx2 Group Earth, Tx2 & Tx4 thermal EFI's: S293 UG Fault from S293 Sw/A to S3839 Sw/B | November | 2016 | 2017Q2 | 2017 | ZN180:PA33 | ZN180:PA33 | ZN00180/000033 | NORTH SYDNEY | UG | Not Veg | 2016-11-23 | N | 75.5333 | N | 5 | N | N | 1.1101 | 39.4971 | 49622.5814
[7 empty] | 10024 | 16295 | 1437289 | 2016-11-24 06:55 | 2016-11-24 09:15 | 140 | 11kV | 212638 | 1787 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35900 Potts Hill - Pnl.17 tripped on: Earth Fault, B & C phase O/C Field EFIs: S1265, S8433, S62349, S8967 (Note: EFI not located on Ferrer Rd or Diffey Rd) Suspected UG cable fault between S1265 (Sw/B) and S8433 (Sw/A) tee PT531 See 1437527 1437528 1437529 1437530 | November | 2016 | 2017Q2 | 2017 | ZN35900:PA17 | ZN35900:PA17 | ZN35900/000017 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2016-11-24 | N | 118.9916 | N | 2 | N | N | 1.1101 | 39.4971 | 155389.5786
[7 empty] | 10308 | 19650 | 1437287 | 2016-11-24 06:31 | 2016-11-24 11:10 | 279 | 11kV | 279 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169497 Single phase broken LL dropper | November | 2016 | 2017Q2 | 2017 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2016-11-24 | N | 279 | N | 2 | N | N | 1.1101 | 39.4971 | 203.885
[7 empty] | 9627 | 11540 | 1437522 | 2016-11-25 04:22 | 2016-11-25 06:13 | 111 | 11kV | 164257 | 1759 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | 11kV IT62774 Kenwell Pittwater tripped and locked out on O/C Trip Abnormal Switching: DMA LB64925 Op[en With LB62775 Closed Cause not ascertained forn outage see OMS 1438290 1438291 1437521 1437523 1437522 | November | 2016 | 2017Q2 | 2017 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Veg | 2016-11-25 | N | 93.3809 | N | 3 | N | N | 1.1101 | 39.4971 | 120034.1708
[7 empty] | 9924 | 15062 | 1437559 | 2016-11-25 11:40 | 2016-11-25 13:00 | 80 | 11kV | 560 | 7 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169506 Single phase OHM stranding between subs 52081 & 54726 | November | 2016 | 2017Q2 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2016-11-25 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 409.2315
[7 empty] | 10361 | 20332 | 1437657 | 2016-11-25 18:50 | 2016-11-25 20:00 | 70 | 11kV | 70 | 1 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 169518 Emerg isolation to repair crossarm Excluded OMS 1437657 | November | 2016 | 2017Q2 | 2017 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2016-11-25 | N | 70 | N | 3 | N | N | 1.1101 | 39.4971 | 51.1539
[7 empty] | 10224 | 18794 | 1437748 | 2016-11-26 10:48 | 2016-11-26 12:05 | 77 | 11kV | 96966 | 1275 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169520 1 fault operation B & C phase Overcurrent Tree branch fell across mains outside 8 Kendall St, Bellbird near pole FT-10007. Excluded OMS 1437748 AND 1437750. | November | 2016 | 2017Q2 | 2017 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2016-11-26 | N | 76.0518 | N | 1 | N | N | 1.1101 | 39.4971 | 70859.8928
[7 empty] | 10011 | 16181 | 1437863 | 2016-11-27 14:01 | 2016-11-27 17:45 | 224 | 11kV | 8064 | 36 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | No Weather Impact | N | At Sub48087 Kerr Civic, Tx switch had tripped with all 3 phases still ok Remarks: Vehicle hit kiosk. Kerr Pde Auburn | November | 2016 | 2017Q2 | 2017 | ZN1068:PA18 | ZN1068:PA18 | ZN01068/000018 | CUMBERLAND | Unknown | Not Veg | 2016-11-27 | N | 224 | N | 1 | N | N | 1.1101 | 39.4971 | 5892.9334
[7 empty] | 8993 | 3914 | 1437958 | 2016-11-28 09:18 | 2016-11-28 11:00 | 102 | 11kV | 153192 | 1656 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN1068 Lidcombe: 11kv feeder Panel 17 'Sub 3367' C/B tripped on: Relays: O/C and Earth fault, EFI Signals: 11kv trip, Zone earth, Group Earth Abnormal: Closed Sw/B @ S8641 Sheffield Rhyl 2, Open Sw/C @ Sub 524 Beatrice St Remarks: UG fault. 11kv feeder fault from S6136 Harrow Bea 2 (sw/B) to Sub 35368 Harrow Mary 1 to Sub 5490 Park Mary, to 2663 Chestnut Rd (sw/A) to sub 5490 Park mary (Sw/A) | November | 2016 | 2017Q2 | 2017 | ZN1068:PA17 | ZN1068:PA17 | ZN01068/000017 | CUMBERLAND | UG | Not Veg | 2016-11-28 | N | 92.5072 | N | 2 | N | N | 1.1101 | 39.4971 | 111948.1952
[7 empty] | 9653 | 11798 | 1438100 | 2016-11-28 14:43 | 2016-11-28 19:17 | 274 | 11kV | 167962 | 613 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | The TCAT at CP77184 Brooklyn Causeway was emitting smoke from the centre phase 11kV Recloser @ CP77184 was opened interrupting alternate railway supply via DNMS Abnormal Switching: CP77184 Brooklyn Causeway Closed, CP1148 Oped D&R394268 Cause: Transformer Failure see OMS 1438230 1438164 1438100 | November | 2016 | 2017Q2 | 2017 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | UG | Not Veg | 2016-11-28 | N | 274 | N | 2 | N | N | 1.1101 | 39.4971 | 122741.6756
[7 empty] | 8816 | 1647 | 1438196 | 2016-11-29 03:17 | 2016-11-29 06:52 | 215 | 11kV | 95578 | 768 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn36300 Balgowlah North panel 17 tripped on Signals: 11kV Trip, TX1 Group Earth Relays: 50TBC (B and C phase IOC) Cause: Bond failure at Pole FF38936 in Kenneth Rd Horning Manly Vale See OMS 1438199 1438332 1438196 CC1: 22-"Refer to SOp" | November | 2016 | 2017Q2 | 2017 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Not Veg | 2016-11-29 | N | 124.4505 | N | 2 | N | N | 1.1101 | 39.4971 | 69845.5833
[7 empty] | 9837 | 14019 | 1438198 | 2016-11-29 05:34 | 2016-11-29 08:30 | 176 | 11kV | 704 | 4 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169552 Single phase DOLF : 16 Amp Possum found at base of the pole. Excluded OMS 1438198. | November | 2016 | 2017Q2 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2016-11-29 | N | 176 | N | 2 | N | N | 1.1101 | 39.4971 | 514.4624
[7 empty] | 9718 | 12515 | 1438432 | 2016-11-30 00:37 | 2016-11-30 02:55 | 138 | 11kV | 109572 | 794 | HV | Animal Possum | Animal | Pole | Unplanned | No Weather Impact | N | Ex ZN9118 Cronulla 11kv Panel 11 - REC 35756 tripped re-closed tripped reclosed triped and locked out on - O/C Remarks: Animals/birds. Possum found at base of pole in Reef st near Bournesmouth | November | 2016 | 2017Q2 | 2017 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2016-11-30 | N | 138 | N | 13 | N | N | 1.1101 | 39.4971 | 80071.9858
[7 empty] | 8912 | 2852 | 1438464 | 2016-11-30 08:04 | 2016-11-30 09:45 | 101 | 11kV | 202 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169574 Single phase Found LL Clamp off bail at pole 8J-80056. Excluded OMS No. 1438464 | November | 2016 | 2017Q2 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | UPPER HUNTER | OH | Veg | 2016-11-30 | N | 101 | N | 13 | N | N | 1.1101 | 39.4971 | 147.6156
[7 empty] | 9847 | 14148 | 1438534 | 2016-11-30 11:14 | 2016-11-30 14:06 | 172 | 11kV | 153336 | 1363 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14891 Wyong Pa8 "Betty Ann Green etc" fdr tripped on: Relays: Earth Fault Signals: 11kv trip, Tx1 Group Earth EFI's: Pa8 to S14841 UG Cable Fault between S14934 to S14993 Defective EFI's at S14842 S14992 See 1439589,90,1,2,3 exclude 1438534 | November | 2016 | 2017Q2 | 2017 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | UG | Not Veg | 2016-11-30 | N | 112.4989 | N | 13 | N | N | 1.1101 | 39.4971 | 112053.4262
[7 empty] | 8842 | 1906 | 1438623 | 2016-11-30 17:11 | 2016-11-30 19:41 | 150 | 11kV | 300 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169590 3 fault operations A & B phase Overcurrent; Earth Fault also damaged incoming and outgoing links on sw 18160. Excluded oms 1438623 | November | 2016 | 2017Q2 | 2017 | 514:18160 | 514:18160 | ZN00514/018160 | SINGLETON | OH | Veg | 2016-11-30 | N | 150 | N | 13 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 10319 | 19812 | 1438598 | 2016-11-30 16:33 | 2016-11-30 19:45 | 192 | 11kV | 40357 | 542 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 169591 2 fault operations A & C phase Overcurrent Faulty arrestor at UGOH 8N-30606 note - fdr abnormal ABS 74375 open, ABS 74953 closed - sys ab Excluded oms 1438598 | November | 2016 | 2017Q2 | 2017 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2016-11-30 | N | 74.4594 | N | 13 | N | N | 1.1101 | 39.4971 | 29491.7053
[7 empty] | 9826 | 13904 | 1438433 | 2016-11-30 00:51 | 2016-11-30 20:00 | 1149 | 11kV | 93069 | 81 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S4455 Pacific Bloomsbury 11kV HV fuse 40A blew. Cause: Did not grade with distributor 3 fault Distributor 3 restored via LV parallel See OMS 1438697 1438433 | November | 2016 | 2017Q2 | 2017 | ZN195:PA22 | ZN195:PA22 | ZN00195/000022 | KU-RING-GAI | UG | Not Veg | 2016-11-30 | N | 1149 | N | 13 | N | N | 1.1101 | 39.4971 | 68012.0801
[7 empty] | 9429 | 9204 | 1438591 | 2016-11-30 16:06 | 2016-11-30 20:15 | 249 | 11kV | 10362 | 44 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169592 2 fault operations 3 phase Overcurrent: Earth Fault Excluded OMS 1438591 CC1: 06-"Urgent - O.H Mains - No others" | November | 2016 | 2017Q2 | 2017 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2016-11-30 | N | 235.5 | N | 13 | N | N | 1.1101 | 39.4971 | 7572.244
[7 empty] | 9516 | 10181 | 1438631 | 2016-11-30 18:00 | 2016-11-30 20:35 | 155 | 11kV | 465 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169593 10 fault operations A Phase DOLF Excluded OMS 1438631 | November | 2016 | 2017Q2 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-11-30 | N | 155 | N | 13 | N | N | 1.1101 | 39.4971 | 339.8083
[7 empty] | 8844 | 1920 | 1438637 | 2016-11-30 18:07 | 2016-11-30 20:40 | 153 | 11kV | 1071 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169594 A & C Phases : 10 Amp Excluded OMS 1438637 | November | 2016 | 2017Q2 | 2017 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2016-11-30 | N | 153 | N | 13 | N | N | 1.1101 | 39.4971 | 782.6552
[7 empty] | 9779 | 13470 | 1438604 | 2016-11-30 16:38 | 2016-11-30 21:15 | 277 | 11kV | 277 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169596 C Phase DOLF : 3 Amp Excluded OMS 1438604 | November | 2016 | 2017Q2 | 2017 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2016-11-30 | N | 277 | N | 13 | N | N | 1.1101 | 39.4971 | 202.4234
[7 empty] | 9410 | 8883 | 1438646 | 2016-11-30 18:30 | 2016-11-30 21:20 | 170 | 11kV | 170 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169595 C Phase DOLF : 10 Amp Excluded OMS 1438646 | November | 2016 | 2017Q2 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-11-30 | N | 170 | N | 13 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 10278 | 19298 | 1438689 | 2016-12-01 07:05 | 2016-12-01 08:10 | 65 | 11kV | 130 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169605 Single Phase DOLF : 10 Amp Excluded OMS 1438689 | December | 2016 | 2017Q2 | 2017 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2016-12-01 | N | 65 | N | 10 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 8967 | 3642 | 1438680 | 2016-12-01 06:03 | 2016-12-01 08:43 | 160 | 11kV | 21709 | 149 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169610 2 fault operations Instantaneous Earth Fault Excluded OMS 1438680 | December | 2016 | 2017Q2 | 2017 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2016-12-01 | N | 145.698 | N | 10 | N | N | 1.1101 | 39.4971 | 15864.2969
[7 empty] | 9629 | 11554 | 1438664 | 2016-11-30 21:11 | 2016-12-01 08:45 | 694 | 11kV | 5552 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169606 B & C Phase DOLF : 20 Amp Excluded OMS 1438664 | November | 2016 | 2017Q2 | 2017 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2016-11-30 | N | 694 | N | 13 | N | N | 1.1101 | 39.4971 | 4057.2378
[7 empty] | 8863 | 2272 | 1438677 | 2016-12-01 06:01 | 2016-12-01 09:10 | 189 | 11kV | 378 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169604 Single phase DOLF : 10 Amp Tx Volts : 245V Excluded OMS 1438677 | December | 2016 | 2017Q2 | 2017 | 814:82285 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2016-12-01 | N | 189 | N | 10 | N | N | 1.1101 | 39.4971 | 276.2313
[7 empty] | 10360 | 20331 | 1438676 | 2016-12-01 05:55 | 2016-12-01 11:35 | 340 | 11kV | 340 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 169619 C Phase DOLF : 10 Amp Replaced blown sub LA's. Excluded OMS No. 1438676 | December | 2016 | 2017Q2 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2016-12-01 | N | 340 | N | 10 | N | N | 1.1101 | 39.4971 | 248.462
[7 empty] | 9307 | 7520 | 1438600 | 2016-11-30 16:33 | 2016-12-01 14:15 | 1302 | 11kV | 18641 | 127 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 169597 1 fault operation Sensitive Earth Fault faulty tx 72987 webster sub Excluded oms 1438600 | November | 2016 | 2017Q2 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2016-11-30 | N | 146.7795 | N | 13 | N | N | 1.1101 | 39.4971 | 13622.293
[7 empty] | 9763 | 13233 | 1438674 | 2016-12-01 09:00 | 2016-12-01 15:20 | 380 | 11kV | 380 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169628 Single phase DOLF : 10 Amp Excluded OMS 1438674 | December | 2016 | 2017Q2 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2016-12-01 | N | 380 | N | 10 | N | N | 1.1101 | 39.4971 | 277.6928
[7 empty] | 9040 | 4580 | 1438826 | 2016-12-01 14:38 | 2016-12-01 17:00 | 142 | 11kV | 40872 | 453 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 169624 2 fault operation A phase Overcurrent; Earth Fault targets 50T-A, 50T-N. Faulty arresters changes at pole JV-41137 live line. Excluded OMS 1438826. | December | 2016 | 2017Q2 | 2017 | 220:8688 | 220:8688 | ZN00220/008688 | LAKE MACQUARIE | OH | Not Veg | 2016-12-01 | N | 90.2252 | N | 10 | N | N | 1.1101 | 39.4971 | 29868.0521
[7 empty] | 10326 | 19911 | 1439471 | 2016-12-01 10:32 | 2016-12-01 18:05 | 453 | 11kV | 453 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 169629 A & C phase DOLF : 10 Amp Faulty Transformer Excluded OMS 1438753 | December | 2016 | 2017Q2 | 2017 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2016-12-01 | N | 453 | N | 10 | N | N | 1.1101 | 39.4971 | 331.039
[7 empty] | 10023 | 16292 | 1438857 | 2016-12-01 15:45 | 2016-12-01 22:13 | 388 | 11kV | 144970 | 376 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 169633 3 fault operations 3 phase Overcurrent, Earth Fault MAINS DOWN POLE IQ-42103 WOODVILLE. Excluded OMS REPORT NO 1438850 | December | 2016 | 2017Q2 | 2017 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2016-12-01 | N | 385.5585 | N | 10 | N | N | 1.1101 | 39.4971 | 105939.8001
[7 empty] | 9147 | 5949 | 1438918 | 2016-12-01 21:50 | 2016-12-01 23:05 | 75 | 11kV | 75 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 169641 A phase DOLF : 31 Amp suspect storm activity.dq Excluded oms 1438918 | December | 2016 | 2017Q2 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | UG | Not Veg | 2016-12-01 | N | 75 | N | 10 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 9804 | 13681 | 1438929 | 2016-12-02 01:55 | 2016-12-02 02:42 | 47 | 11kV | 2538 | 54 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169642 C Phase DOLF : 31 Amp possum found at base of pole Tx Excluded oms 1438928 | December | 2016 | 2017Q2 | 2017 | 214:8669 | 214:8669 | ZN00214/008669 | LAKE MACQUARIE | OH | Not Veg | 2016-12-02 | N | 47 | N | 8 | N | N | 1.1101 | 39.4971 | 1854.6955
[7 empty] | 9072 | 5055 | 1438930 | 2016-12-02 02:12 | 2016-12-02 03:15 | 63 | 11kV | 378 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169643 A Phase DOLF : 10 Amp Excluded OMS 1438930 | December | 2016 | 2017Q2 | 2017 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2016-12-02 | N | 63 | N | 8 | N | N | 1.1101 | 39.4971 | 276.2313
[7 empty] | 9950 | 15299 | 1438836 | 2016-12-01 15:21 | 2016-12-02 05:25 | 844 | 11kV | 220211 | 2072 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 169631 2 fault operations B Phase Earth Fault O/HEAD E/WIRE DOWN BETWEEN POLES HR-51011 & HR-51012. 33KV MAINS DOWN BETWEEN POLES HR-80555 & HR-50556. Targets fdr 80923 51N E/F Excluded OMS REPORT NO 1438836 & 1438839. | December | 2016 | 2017Q2 | 2017 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2016-12-01 | N | 106.2794 | N | 10 | N | N | 1.1101 | 39.4971 | 160923.7037
[7 empty] | 10114 | 17428 | 1438940 | 2016-12-02 06:10 | 2016-12-02 08:20 | 130 | 11kV | 390 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169645 Single phase DOLF : 10 Amp Transformwer volts 242V Excluded OMS 1438940 | December | 2016 | 2017Q2 | 2017 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2016-12-02 | N | 130 | N | 8 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 9499 | 9908 | 1438946 | 2016-12-02 07:00 | 2016-12-02 08:40 | 100 | 11kV | 200 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169653 A Phase DOLF : 16 Amp Excluded OMS 1438946 | December | 2016 | 2017Q2 | 2017 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2016-12-02 | N | 100 | N | 8 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 9411 | 8890 | 1438931 | 2016-12-02 02:38 | 2016-12-02 09:46 | 428 | 11kV | 143890 | 1559 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 169644 2 fault operation A Phase Overcurrent defective UGOH pole IV40332. possible HV into LV Excluded oms 1438931 | December | 2016 | 2017Q2 | 2017 | 225:13446 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | Unknown | Unknown | 2016-12-02 | N | 92.2963 | N | 8 | N | N | 1.1101 | 39.4971 | 105150.568
[7 empty] | 10030 | 16357 | 1439199 | 2016-12-02 21:10 | 2016-12-02 23:00 | 110 | 11kV | 81736 | 828 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale pa7 "Wyong Mingara etc" fdr tripped on: Relays: C phase timed voercurrent, Earth Fault, EFI Signals: No12 Group Earth, 11kv trip EFI's: S14805 S14821 S18429 S47532 S18179 Abnormal: section of fdr OOS S65075 to CP45055 with LB62464 closed Cause: UG Fault in section of 11kv fdr from S18179 to S14840 See 1439599,601 exclude 1439199,202 | December | 2016 | 2017Q2 | 2017 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | UG | Not Veg | 2016-12-02 | N | 98.715 | N | 8 | N | N | 1.1101 | 39.4971 | 59730.258
[7 empty] | 9803 | 13675 | 1439208 | 2016-12-02 23:30 | 2016-12-03 01:20 | 110.4333 | 11kV | 395768.0333 | 3587 | HV | Arcing | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At ZN10995 Riverwood 11kv feeder Panel No: 7 "Romilly St" feeder tripped and reclosed on: Relays: C phase O/C and C phase timed O/C, reclosing and timing relay Field EFIs: Nil Abnormal: DMA ZN10995 PA5 to S10986, CLosed Sw/B @ S10236 Remarks: flashover/arcing. Flashover caused by possum on UGOH on pole PE00261, no further action req | December | 2016 | 2017Q2 | 2017 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Not Veg | 2016-12-02 | N | 110.334 | N | 8 | N | N | 1.1101 | 39.4971 | 289215.6056
[7 empty] | 9624 | 11507 | 1439211 | 2016-12-03 00:25 | 2016-12-03 01:27 | 62 | 11kV | 65626 | 1091 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN262 Marrickville 11kv feeder Panel No: 27 "Marrickville Aux no1" feeder tripped Relays: B phase E/F, EFI, fault check Signals: Zone earth, No1 Grp Earth Remarks: UG fault. Fault in section of 11kv feeder from S5259 Coronation park (SwB) to S35139 Horton Amy (SwA) Note Haz RMI @ S5259 cut out extension req to be organised by region. | December | 2016 | 2017Q2 | 2017 | ZN262:PA27 | ZN262:PA27 | ZN00262/000027 | INNER WEST | UG | Not Veg | 2016-12-03 | N | 60.1522 | N | 3 | N | N | 1.1101 | 39.4971 | 47957.5452
[7 empty] | 9709 | 12392 | 1439210 | 2016-12-02 23:52 | 2016-12-03 07:19 | 447 | 11kV | 34764 | 390 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn8100 Green Square - Pnl.28 tripped on: O/C and E/F, EFI, Fault Check Field EFIs: S596, S6067, S7973 UG cable fault from S7973 (Sw/B) Joynton Hansard to S35286 (Sw/A) Mentmore Epsom No.2 Delays in restoring S6067 and S7973 due to No Access. See 1439488 1439489 1439214 | December | 2016 | 2017Q2 | 2017 | ZN8100:PA28 | ZN8100:PA28 | ZN08100/000028 | SYDNEY | UG | Not Veg | 2016-12-02 | N | 89.1385 | N | 8 | N | N | 1.1101 | 39.4971 | 25404.5058
[7 empty] | 9454 | 9420 | 1439232 | 2016-12-03 07:34 | 2016-12-03 11:15 | 221 | 11kV | 221 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169666 Single phase DOLF : 5 Amp excluded OMS 1439232 | December | 2016 | 2017Q2 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2016-12-03 | N | 221 | N | 3 | N | N | 1.1101 | 39.4971 | 161.5003
[7 empty] | 9890 | 14689 | 1439242 | 2016-12-03 09:02 | 2016-12-03 15:00 | 358 | 11kV | 716 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 169672 A Phase DOLF : 10 Amp Excluded OMS 1439242 | December | 2016 | 2017Q2 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-12-03 | N | 358 | N | 3 | N | N | 1.1101 | 39.4971 | 523.2317
[7 empty] | 10104 | 17286 | 1439327 | 2016-12-04 01:12 | 2016-12-04 02:51 | 99 | 11kV | 199751 | 2053 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn262 Marrickville the 11kv Panel 30 "New Canterbury Wardell" feeder CB tripped on: Signals: 11kv trip, Zone Earth, Tx 1 Group Earth Relays: B phase OC, EFI, Fault Check Remarks: UG fault. There is an UG fault in section of feeder between S3225 Stanmore Holt (Sw/B) and S4796 Holt Cavendish (Sw/A) | December | 2016 | 2017Q2 | 2017 | ZN262:PA30 | ZN262:PA30 | ZN00262/000030 | INNER WEST | UG | Not Veg | 2016-12-04 | N | 97.2971 | N | 2 | N | N | 1.1101 | 39.4971 | 145972.1391
[7 empty] | 10207 | 18620 | 1439434 | 2016-12-04 22:16 | 2016-12-04 23:41 | 85 | 11kV | 93340 | 1122 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Zn12570 Avoca Zn Pa26 labelled Woodfield Waldron tripped on ABC IOC, EFI, 11kv trip EFI's: All field EFI's down to RE40425 Possum found at Re40425 Kurrawyba Cadell See 1439624,7 exclude 1439434 | December | 2016 | 2017Q2 | 2017 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2016-12-04 | N | 83.1907 | N | 2 | N | N | 1.1101 | 39.4971 | 68210.1189
[7 empty] | 9805 | 13684 | 1439439 | 2016-12-05 01:45 | 2016-12-05 02:21 | 36 | 11kV | 26136 | 726 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | S542 Boomerang malabar - CB 'R' tripped on: Timed Earth Fault, EFI Field EFIs: All EFIs down from zone to S2650 UG cable fault from S2650 to S4155 | December | 2016 | 2017Q2 | 2017 | ZN3672:PA13 | ZN3672:PA13 | ZN03672/000013 | RANDWICK | UG | Not Veg | 2016-12-05 | N | 36 | N | 26 | Y | Y | 1.1101 | 39.4971 | 19099.4179
[7 empty] | 9881 | 14552 | 1439456 | 2016-12-05 06:29 | 2016-12-05 12:00 | 331 | 11kV | 118144 | 1479 | HV | Vegetation Blow/Fall In | Vegetation | DC Transformer | Unplanned | No Weather Impact | N | At S1193 Lindfield Panel 26 tripped on A and C phase O/C Cause: branch on PT2415 damage to lightning arrestor See OMS 1440229 1440231 1440232 1439454 1439456 1439547 | December | 2016 | 2017Q2 | 2017 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | OH | Veg | 2016-12-05 | N | 79.881 | N | 26 | Y | Y | 1.1101 | 39.4971 | 86336.1505
[7 empty] | 8951 | 3407 | 1439621 | 2016-12-05 12:44 | 2016-12-05 13:45 | 61 | 11kV | 115854 | 1944 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9035 Caringbah - Pnl.11 tripped on: Earth Fault with EFI Field EFIs: S9420 UG cable fault from S9420 banksia Mackay No.2 (Sw/B) to S9836 High president (Sw/A) to S9774 Willarong Venture Store See 1440131 1400132 | December | 2016 | 2017Q2 | 2017 | ZN9035:PA11 | ZN9035:PA11 | ZN09035/000011 | SUTHERLAND | UG | Not Veg | 2016-12-05 | N | 59.5957 | N | 26 | Y | Y | 1.1101 | 39.4971 | 84662.6861
[7 empty] | 9678 | 12143 | 1439633 | 2016-12-05 13:12 | 2016-12-05 14:41 | 89 | 11kV | 2101 | 24 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2466 Flemington 11kv Panel 19 tripped on: Panel 19 relays - earth fault, efi, fault check Panel 12 Relays - earth fault, fault check Panel 21 Relays - Earth fault, fault check 11kv "Toohey Lidcombe" fdr tripped at S986 Egg Board on Earth fault Signals: 11kv trip Field EFI's: S7306, S2898 Remarks: UG fault, front line feeder fault from Panel 19 to S7360 Carther Hill No.2 Sw/A | December | 2016 | 2017Q2 | 2017 | ZN2466:PA19 | ZN2466:PA19 | ZN02466/000019 | CUMBERLAND | UG | Not Veg | 2016-12-05 | N | 87.5417 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1535.3488
[7 empty] | 9472 | 9696 | 1439695 | 2016-12-05 15:00 | 2016-12-05 17:00 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169704 Single phase DOLF : 10 Amp Excluded OMS 1439695 | December | 2016 | 2017Q2 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-12-05 | N | 120 | N | 26 | Y | Y | 1.1101 | 39.4971 | 87.6925
[7 empty] | 10253 | 19043 | 1439692 | 2016-12-05 15:02 | 2016-12-05 17:30 | 147.85 | 11kV | 3844.1 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169702 A & C phase DOLF : 10 Amp lightning strike blown 2 dolfs, line patrol ok replaced - t brooks Excluded OMS 1439703 | December | 2016 | 2017Q2 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-12-05 | N | 147.85 | N | 26 | Y | Y | 1.1101 | 39.4971 | 2809.1549
[7 empty] | 9046 | 4673 | 1439774 | 2016-12-05 16:11 | 2016-12-05 18:00 | 109 | 11kV | 327 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169705 Single phase DOLF : 10 Amp Excluded OMS 1439774 | December | 2016 | 2017Q2 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-12-05 | N | 109 | N | 26 | Y | Y | 1.1101 | 39.4971 | 238.962
[7 empty] | 8752 | 694 | 1439720 | 2016-12-05 15:08 | 2016-12-05 18:30 | 202 | 11kV | 75260 | 520 | HV | Wind Blown Debris | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169708 2 fault operations Branch on mains at pole IR-42251. corrugated iron on feeder at PT 76850. Trampoline on LV at PT 44130. | December | 2016 | 2017Q2 | 2017 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2016-12-05 | N | 144.7308 | N | 26 | Y | Y | 1.1101 | 39.4971 | 54997.7882
[7 empty] | 10130 | 17572 | 1439813 | 2016-12-05 16:43 | 2016-12-05 18:44 | 121 | 11kV | 110352 | 912 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Lightning | N | At S15014 Mona Vale panel 20 tripped and locked out on B phase IOC, EFI, Fault Check and No1 TX fault check Cause: 11kV feeder between S24401 and CO20365 Flicked up into 33kV S42 | December | 2016 | 2017Q2 | 2017 | ZN15014:PA20 | ZN15014:PA20 | ZN15014/000020 | NORTHERN BEACHES | OH | Not Veg | 2016-12-05 | N | 121 | N | 26 | Y | Y | 1.1101 | 39.4971 | 80641.9868
[7 empty] | 9408 | 8855 | 1439790 | 2016-12-05 16:34 | 2016-12-05 18:58 | 144 | 11kV | 173048 | 1342 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At Zn2400 Berowra 11kV feeder Panel 18 tripped on Relays: IOC, Reclosing, Lockout, EFI, Relay Faulty Alarm Cause: Fault 1: Relay on Panel 18 @ Zn2400 Berowra Defective Fault 2: Lighting arrestor at UGOH on tee to PT16666 Kita Turner Failed - Cut away by lines man see OMS 1442116 1442118 1439790 1440290 1439859 | December | 2016 | 2017Q2 | 2017 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2016-12-05 | N | 128.9478 | N | 26 | Y | Y | 1.1101 | 39.4971 | 126458.3743
[7 empty] | 9827 | 13907 | 1439669 | 2016-12-05 14:16 | 2016-12-05 20:20 | 364 | 11kV | 1605 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169711 B & C phase Overcurrent Tie broken near tee off to PT 71193. repaired under permit. Excluded OMS 1439669 | December | 2016 | 2017Q2 | 2017 | 514:18146 | 514:18156 | ZN00514/018156 | MUSWELLBROOK | OH | Veg | 2016-12-05 | N | 321 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1172.8867
[7 empty] | 10072 | 16819 | 1439760 | 2016-12-05 15:59 | 2016-12-05 20:35 | 276 | 11kV | 191216 | 1731 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Lightning | N | At S35500 Top Ryde 11kV Feeder Pa27 tripped on Relays: EFI, Fault Check, E/F, U/F pickup Cause Fault 1: UG feeder fault trunk section Pa27 to S4341 SW/A Fault 2: HDO failure @ PT2407 supplied via LV parallel Fault 3: LV parallel faulure @ PT1324 See OMS 1440250 1440254 1440255 1440256 1439760 1439799 1439955 1439967 | December | 2016 | 2017Q2 | 2017 | ZN35500:PA27 | ZN35500:PA27 | ZN35500/000027 | RYDE | UG | Not Veg | 2016-12-05 | N | 110.4656 | N | 26 | Y | Y | 1.1101 | 39.4971 | 139735.0129
[7 empty] | 10138 | 17659 | 1439769 | 2016-12-05 16:06 | 2016-12-05 21:00 | 294 | 11kV | 294 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | replaced bphase hv fuse on sub 61067 - mgsmith Customer reported lightning strike on pole | December | 2016 | 2017Q2 | 2017 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2016-12-05 | N | 294 | N | 26 | Y | Y | 1.1101 | 39.4971 | 214.8465
[7 empty] | 9700 | 12317 | 1439824 | 2016-12-05 16:33 | 2016-12-05 22:15 | 342 | 11kV | 33516 | 98 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | N | 11kv Recloser CP559 Cobah Rd Tripped and Reclosed on Relays: O/L trip DMA - AB2907 centre phase bond burnt off | December | 2016 | 2017Q2 | 2017 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2016-12-05 | N | 342 | N | 26 | Y | Y | 1.1101 | 39.4971 | 24492.5042
[7 empty] | 9531 | 10375 | 1439702 | 2016-12-05 15:05 | 2016-12-05 22:30 | 445 | 11kV | 136538 | 705 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn14891 Wyong Pa21 "Yarramalong" tripped and locked out Relays: Lock Out, Reclose Timing Relay, Fault Check, B & C phase O/C EFI Signals: Minor Alarm Cause: Vehicle Hit Pole. Restoration delayed due to Tx2 @ Zn12630 Peats Ridge tripped and Tx1 under access See 1440682,4,5,6 exclude 1439702,17 | December | 2016 | 2017Q2 | 2017 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2016-12-05 | N | 193.6709 | N | 26 | Y | Y | 1.1101 | 39.4971 | 99777.9432
[7 empty] | 9776 | 13363 | 1439724 | 2016-12-05 15:32 | 2016-12-05 22:30 | 418 | 11kV | 418 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169716 A Phase DOLF : 10 Amp Excluded OMS 1439724 | December | 2016 | 2017Q2 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2016-12-05 | N | 418 | N | 26 | Y | Y | 1.1101 | 39.4971 | 305.4621
[7 empty] | 9987 | 15821 | 1439846 | 2016-12-05 17:35 | 2016-12-05 23:00 | 325 | 11kV | 133816 | 1013 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | Recloser CP20397 Pittwater Cabbage Tripped on O/C and IOC with Lockout Cause: 5 HV/LV bays down. cause by tree near 1666 Pitwater Rd Mona Vale (near supply point MV3236) See OMS 1440854 1439846 | December | 2016 | 2017Q2 | 2017 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2016-12-05 | N | 132.0987 | N | 26 | Y | Y | 1.1101 | 39.4971 | 97788.7859
[7 empty] | 9690 | 12229 | 1439926 | 2016-12-05 16:44 | 2016-12-05 23:20 | 396 | 11kV | 5041 | 696 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | At Zn2400 Berowra Panel 11 tripped and reclosed on Relays: B and C phase IOC, Fault Check and EFI Field EFI's - NIL Cause: Next available Linesman to patrol in daylight See OMS 1440341 1440342 1439926 | December | 2016 | 2017Q2 | 2017 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2016-12-05 | N | 7.2428 | N | 26 | Y | Y | 1.1101 | 39.4971 | 3683.8141
[7 empty] | 9558 | 10764 | 1439739 | 2016-12-05 15:35 | 2016-12-06 00:45 | 550 | 11kV | 1650 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 169721 Isolated section @ pole DG-50060 Live Line to repair HV & LV OHMs. | December | 2016 | 2017Q2 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2016-12-05 | N | 550 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1205.7713
[7 empty] | 9473 | 9709 | 1439708 | 2016-12-05 15:14 | 2016-12-06 02:10 | 656 | 11kV | 5248 | 8 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 169720 Replaced faulty Transformer Excluded OMS 1439708 | December | 2016 | 2017Q2 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2016-12-05 | N | 656 | N | 26 | Y | Y | 1.1101 | 39.4971 | 3835.0836
[7 empty] | 9315 | 7651 | 1440054 | 2016-12-05 22:21 | 2016-12-06 02:11 | 230 | 11kV | 637625 | 2991 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | At Zn4545 Meadowbank Panel 31 tripped on A and B phase OC trip, Fault check and EFI Signals: TX3 Group and Zone earth with 11kV Trip. Cause: See OMS 1440857 1440859 1440860 1440065 1440058 14400154 | December | 2016 | 2017Q2 | 2017 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Veg | 2016-12-05 | N | 213.1812 | N | 26 | Y | Y | 1.1101 | 39.4971 | 465957.5432
[7 empty] | 10045 | 16533 | 1439719 | 2016-12-05 15:41 | 2016-12-06 02:15 | 634.05 | 11kV | 9510.75 | 15 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 169719 Replace blown Transformer CC1: 22-"Refer to SOp" FRC1: 365-"Damaged/Defective Arrestor - Requires repair/replacement" | December | 2016 | 2017Q2 | 2017 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2016-12-05 | N | 634.05 | N | 26 | Y | Y | 1.1101 | 39.4971 | 6950.1756
[7 empty] | 9910 | 14922 | 1440017 | 2016-12-05 20:15 | 2016-12-06 04:45 | 510 | 11kV | 1905 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 169722 C Phase Repaired blown 11kV tapping pole GQ-55303. Replace blown B phase DOLF & LA sub 49635. Left sub 52390 Isolated from LL Clamps & LVF, Blown C phase DOLF & LA also has oil leaking, to be tested & checked working hours. Excluded OMS 1440017 1440020 1440021 1440076 | December | 2016 | 2017Q2 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2016-12-05 | N | 476.25 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1392.1178
[7 empty] | 10352 | 20277 | 1440089 | 2016-12-06 07:15 | 2016-12-06 08:30 | 75 | 11kV | 75 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169724 A Phase DOLF : 10 Amp start time as per customers call re OMS 1440089 Note customers also affected by T&R OMS 1440258 @ 19:24 | December | 2016 | 2017Q2 | 2017 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2016-12-06 | N | 75 | N | 20 | Y | Y | 1.1101 | 39.4971 | 54.8078
[7 empty] | 9715 | 12494 | 1440029 | 2016-12-05 20:35 | 2016-12-06 08:55 | 740 | 11kV | 1480 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169730 A phase DOLF : 10Amp Excluded OMS 1440029 | December | 2016 | 2017Q2 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-12-05 | N | 740 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1081.5403
[7 empty] | 10330 | 20013 | 1440149 | 2016-12-05 22:27 | 2016-12-06 09:25 | 658 | 11kV | 1974 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169725 B Phase DOLF : 10 Amp Excluded OMS 1440056 | December | 2016 | 2017Q2 | 2017 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2016-12-05 | N | 658 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1442.541
[7 empty] | 9376 | 8469 | 1440115 | 2016-12-06 08:28 | 2016-12-06 10:25 | 117 | 11kV | 89751 | 939 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 28 tripped on A and B phase OC and A phase IOC with EFI Cause: UG cable Fault S5268 to S859 See OMS 1441551 1441554 1441556 1440115 | December | 2016 | 2017Q2 | 2017 | ZN129:PA28 | ZN129:PA52 | ZN00129/000052 | LANE COVE | UG | Not Veg | 2016-12-06 | N | 95.5815 | N | 20 | Y | Y | 1.1101 | 39.4971 | 65587.3836
[7 empty] | 9598 | 11221 | 1440128 | 2016-12-06 08:50 | 2016-12-06 10:40 | 110 | 11kV | 130209 | 1204 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 169729 B Phase Instantaneous Earth Fault, Instantaneous Overcurrent prot A IOC & IEF B B-N OC & EF UGOH FAULTY POLE HR-61708 SECTION ISOLATED FOR REPAIRS | December | 2016 | 2017Q2 | 2017 | 528:83013 | 528:83013 | ZN00528/083013 | MAITLAND | Unknown | Unknown | 2016-12-06 | N | 108.147 | N | 20 | Y | Y | 1.1101 | 39.4971 | 95152.8967
[7 empty] | 9714 | 12469 | 1439815 | 2016-12-05 16:50 | 2016-12-06 11:30 | 1120 | 11kV | 3360 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Replased blown 3.15amp HV fuse on sub 51967. | December | 2016 | 2017Q2 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2016-12-05 | N | 1120 | N | 26 | Y | Y | 1.1101 | 39.4971 | 2455.3889
[7 empty] | 8794 | 1414 | 1440090 | 2016-12-06 07:22 | 2016-12-06 11:35 | 252.8167 | 11kV | 252.8167 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169738 B Phase DOLF : 10 Amp | December | 2016 | 2017Q2 | 2017 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2016-12-06 | N | 252.8167 | N | 20 | Y | Y | 1.1101 | 39.4971 | 184.751
[7 empty] | 9314 | 7636 | 1440192 | 2016-12-06 10:21 | 2016-12-06 12:20 | 119 | 11kV | 357 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169740 B Phase DOLF : 10 Amp Excluded OMS 1440192 | December | 2016 | 2017Q2 | 2017 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Veg | 2016-12-06 | N | 119 | N | 20 | Y | Y | 1.1101 | 39.4971 | 260.8851
[7 empty] | 9277 | 7228 | 1440168 | 2016-12-06 09:45 | 2016-12-06 12:25 | 160 | 11kV | 320 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169741 C Phase DOLF : 10 Amp sub isolated to replace c phase la Excluded oms1440168 | December | 2016 | 2017Q2 | 2017 |  |  |  |  | OH | Veg | 2016-12-06 | N | 160 | N | 20 | Y | Y | 1.1101 | 39.4971 | 233.8466
[7 empty] | 10223 | 18774 | 1440225 | 2016-12-06 11:12 | 2016-12-06 12:40 | 88 | 11kV | 440 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169739 Single phase DOLF : 10 Amp Excluded OMS 1440225 | December | 2016 | 2017Q2 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2016-12-06 | N | 88 | N | 20 | Y | Y | 1.1101 | 39.4971 | 321.539
[7 empty] | 8738 | 346 | 1440144 | 2016-12-06 13:10 | 2016-12-06 13:14 | 4 | 11kV | 596 | 149 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169742 2 fault operation 3 phase Overcurrent 2 trips over 2 two minutes. Fault curent 1300 amps. | December | 2016 | 2017Q2 | 2017 |  |  |  | MUSWELLBROOK | OH | Veg | 2016-12-06 | N | 4 | N | 20 | Y | Y | 1.1101 | 39.4971 | 435.5392
[7 empty] | 9264 | 7135 | 1440161 | 2016-12-06 09:30 | 2016-12-06 13:25 | 235 | 11kV | 235 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169745 3 Phase DOLF : 10 Amp replaced 3 x dolfs Excluded oms 1440161 | December | 2016 | 2017Q2 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-12-06 | N | 235 | N | 20 | Y | Y | 1.1101 | 39.4971 | 171.7311
[7 empty] | 8726 | 64 | 1439885 | 2016-12-06 12:00 | 2016-12-06 14:50 | 170 | 11kV | 14110 | 83 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | Section of 11kV feeder from CP24723 to S16633 isolated by DOp to allow removal of large tree on LV mains | December | 2016 | 2017Q2 | 2017 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | OH | Veg | 2016-12-06 | N | 170 | N | 20 | Y | Y | 1.1101 | 39.4971 | 10311.1718
[7 empty] | 9739 | 12914 | 1440265 | 2016-12-06 12:38 | 2016-12-06 14:58 | 140 | 11kV | 840 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169747 Single Phase DOLF : 5 Amp Excluded OMS 1440265 | December | 2016 | 2017Q2 | 2017 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2016-12-06 | N | 140 | N | 20 | Y | Y | 1.1101 | 39.4971 | 613.8472
[7 empty] | 9390 | 8698 | 1440260 | 2016-12-06 12:17 | 2016-12-06 15:15 | 178 | 11kV | 712 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169746 C Phase DOLF sub isolated for repair 3 x LA's replaced. Excluded OMS 1440260 | December | 2016 | 2017Q2 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2016-12-06 | N | 178 | N | 20 | Y | Y | 1.1101 | 39.4971 | 520.3086
[7 empty] | 9885 | 14583 | 1440286 | 2016-12-06 13:27 | 2016-12-06 15:20 | 113 | 11kV | 1720 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169751 Single phase DOLF : 20 Amp excluded OMS 1440286 | December | 2016 | 2017Q2 | 2017 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2016-12-06 | N | 86 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1256.9253
[7 empty] | 9865 | 14359 | 1440325 | 2016-12-06 14:42 | 2016-12-06 15:25 | 43 | 11kV | 129 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169748 C Phase DOLF : 10 Amp Excluded OMS 1440325 | December | 2016 | 2017Q2 | 2017 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2016-12-06 | N | 43 | N | 20 | Y | Y | 1.1101 | 39.4971 | 94.2694
[7 empty] | 9597 | 11210 | 1440317 | 2016-12-06 14:31 | 2016-12-06 17:05 | 154 | 11kV | 1386 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169755 B Phase DOLF : 20 Amp Excluded OMS 1440317 | December | 2016 | 2017Q2 | 2017 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2016-12-06 | N | 154 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1012.8479
[7 empty] | 8743 | 441 | 1440164 | 2016-12-06 09:38 | 2016-12-06 18:35 | 537 | 11kV | 23091 | 43 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 169735 Isolation to replace pole at sub 25495. Excluded OMS 1440164 | December | 2016 | 2017Q2 | 2017 | 233:82815 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Not Veg | 2016-12-06 | N | 537 | N | 20 | Y | Y | 1.1101 | 39.4971 | 16874.2217
[7 empty] | 9367 | 8293 | 1440373 | 2016-12-06 16:42 | 2016-12-06 19:13 | 151 | 11kV | 14215 | 2065 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S.10995 Riverwood - 11kv CB No.1 "Meadowland Rd" tripped and reclosed on: Relays: A Phase instant, recloser, Timer, Lockout, EFI Signals: 11kv trip, Tx1 Group Earth Abnormal: Sw/C at S10231 Junction Central is open & under access to S10554 Remarks: Animals/Birds. At PT10515 Olive Bonds | December | 2016 | 2017Q2 | 2017 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | OH | Not Veg | 2016-12-06 | N | 6.8838 | N | 20 | Y | Y | 1.1101 | 39.4971 | 10387.9027
[7 empty] | 9659 | 11871 | 1440393 | 2016-12-06 18:05 | 2016-12-06 20:00 | 115 | 11kV | 115 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169757 Single phase DOLF : 10 Amp Excluded OMS 1440393 | December | 2016 | 2017Q2 | 2017 | 814:82283 | 814:82283 | ZN00814/082283 | MUSWELLBROOK | OH | Veg | 2016-12-06 | N | 115 | N | 20 | Y | Y | 1.1101 | 39.4971 | 84.0386
[7 empty] | 10290 | 19455 | 1440396 | 2016-12-06 19:30 | 2016-12-06 20:27 | 57 | 11kV | 285 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 169758 B Phase DOLF : 10 Amp Excluded OMS 1440396 | December | 2016 | 2017Q2 | 2017 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2016-12-06 | N | 57 | N | 20 | Y | Y | 1.1101 | 39.4971 | 208.2696
[7 empty] | 10236 | 18913 | 1440403 | 2016-12-06 18:46 | 2016-12-06 22:50 | 244 | 11kV | 52286 | 628 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 169759 A & B Phases Overcurrent wires off pins at ir-52456 Excluded OMS 1440427 | December | 2016 | 2017Q2 | 2017 | 238:34148 | 238:34138 | ZN00238/034138 | MAITLAND | OH | Not Veg | 2016-12-06 | N | 83.258 | N | 20 | Y | Y | 1.1101 | 39.4971 | 38209.0666
[7 empty] | 9702 | 12324 | 1440444 | 2016-12-07 00:06 | 2016-12-07 01:03 | 57 | 11kV | 170373 | 2989 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn4545 Meadowbank Panel 31 tripped on Relays: A B and C phase O/C, Fault Check and EFI Signals: 11kV Trip, TX3 Group Earth and Zone Earth Cause: Possum on UGOH near AB4549 | December | 2016 | 2017Q2 | 2017 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Not Veg | 2016-12-07 | N | 57 | N | 7 | N | N | 1.1101 | 39.4971 | 124503.5632
[7 empty] | 8846 | 1946 | 1440448 | 2016-12-07 01:03 | 2016-12-07 01:54 | 51 | 11kV | 19737 | 387 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 14 Tripped on relays: C phase IOC, Fault Check and EFI Suspect UG feeder fault from S8556 to AB1714 tee TX2046 | December | 2016 | 2017Q2 | 2017 | ZN847:PA14 | ZN847:PA14 | ZN00847/000014 | HORNSBY | UG | Not Veg | 2016-12-07 | N | 51 | N | 7 | N | N | 1.1101 | 39.4971 | 14423.2175
[7 empty] | 9561 | 10803 | 1440445 | 2016-12-07 00:24 | 2016-12-07 03:45 | 201 | 11kV | 39918 | 668 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14144 Wamberal Panel 10 fdr tripped, reclosed, tripped & locked out on Relays - 51N (EF), EFI, trip, reclose Signals: Tx2 GE EFI's: S18824 S18802 S18826 OH wires down. Outside 30 Brush rd. Started Grassfire See 1441185,6 exclude 1440445,6,53 | December | 2016 | 2017Q2 | 2017 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2016-12-07 | N | 59.7575 | N | 7 | N | N | 1.1101 | 39.4971 | 29170.897
[7 empty] | 8852 | 2066 | 1440455 | 2016-12-07 03:07 | 2016-12-07 07:59 | 292 | 11kV | 28806 | 203 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 169760 1 fault operation B & C phase Earth Fault, Overcurrent Cause wire off pin at pole AL-10145. Excluded OMS 1440455. | December | 2016 | 2017Q2 | 2017 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2016-12-07 | N | 141.9015 | N | 7 | N | N | 1.1101 | 39.4971 | 21050.5752
[7 empty] | 9189 | 6360 | 1440486 | 2016-12-07 08:03 | 2016-12-07 10:10 | 127 | 11kV | 41275 | 325 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Reclose CP22381 (ex Panel 14) tripped reclosed tripped and locked out on Relays: IOC, OC and Lockout Cause: DOp removed Branch off mains near PT15894 | December | 2016 | 2017Q2 | 2017 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2016-12-07 | N | 127 | N | 7 | N | N | 1.1101 | 39.4971 | 30162.5526
[7 empty] | 10211 | 18671 | 1440666 | 2016-12-07 15:48 | 2016-12-07 17:30 | 102 | 11kV | 102 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169768 Single phase DOLF : 10 Amp | December | 2016 | 2017Q2 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-12-07 | N | 102 | N | 7 | N | N | 1.1101 | 39.4971 | 74.5386
[7 empty] | 8937 | 3134 | 1440680 | 2016-12-07 16:47 | 2016-12-07 18:00 | 73 | 11kV | 146 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169769 Single Phase DOLF : 10 Amp | December | 2016 | 2017Q2 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-12-07 | N | 73 | N | 7 | N | N | 1.1101 | 39.4971 | 106.6925
[7 empty] | 10198 | 18523 | 1440757 | 2016-12-08 02:56 | 2016-12-08 04:50 | 114 | 11kV | 25458 | 292 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Panel 7 fdr tripped to Relays: B Phase OC EFI EFI's: S14805 ABNORMAL: section of fdr OOS S65075 to CP45055 with LB62464 closed. DMA S18179 to S14840 with LB43317 closed Cause: UG fault: Possible fault developing See 1441191,3,4,5 exclude 1440757,9 | December | 2016 | 2017Q2 | 2017 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | UG | Not Veg | 2016-12-08 | N | 87.1849 | N | 3 | N | N | 1.1101 | 39.4971 | 18603.9555
[7 empty] | 10106 | 17301 | 1440884 | 2016-12-08 13:46 | 2016-12-08 15:50 | 124 | 11kV | 5084 | 41 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169783 A Phase Broken dropper lead at DOLF Excluded OMS 1440884 | December | 2016 | 2017Q2 | 2017 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2016-12-08 | N | 124 | N | 3 | N | N | 1.1101 | 39.4971 | 3715.2372
[7 empty] | 8854 | 2097 | 1441007 | 2016-12-08 23:29 | 2016-12-09 01:48 | 139 | 11kV | 8594 | 83 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169786 3 fault operations Excluded OMS 1441007 | December | 2016 | 2017Q2 | 2017 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Veg | 2016-12-08 | N | 103.5422 | N | 3 | N | N | 1.1101 | 39.4971 | 6280.2417
[7 empty] | 9229 | 6829 | 1441013 | 2016-12-09 02:51 | 2016-12-09 03:48 | 57 | 11kV | 1083 | 19 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2635 Epping Panel 33 "Herring Talavera #2" fdr tripped on Relays: C phase IOC Signals: 11kv trip with EFI EFI's: Nil Cable fault from Zn2635 Epping (Panel 33) to S7740 Herring Talavera #2 | December | 2016 | 2017Q2 | 2017 | ZN2635:PA33 | ZN2635:PA33 | ZN02635/000033 | RYDE | UG | Not Veg | 2016-12-09 | N | 57 | N | 7 | N | N | 1.1101 | 39.4971 | 791.4245
[7 empty] | 9459 | 9559 | 1441011 | 2016-12-09 01:09 | 2016-12-09 08:35 | 446 | 11kV | 16502 | 37 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZN12620 Noraville section of Pa1 PT12792 Karangal Sth Buff - Roadside 31.5Amp dropout fuse operated Fuse Fatigue See 1441634 exclude 1441011 | December | 2016 | 2017Q2 | 2017 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2016-12-09 | N | 446 | N | 7 | N | N | 1.1101 | 39.4971 | 12059.1749
[7 empty] | 9889 | 14688 | 1441603 | 2016-12-09 11:00 | 2016-12-09 12:20 | 80 | 11kV | 160 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169794 No protection operated, appears DOLF dropped out. NO OMS called to operator was to depot bypassing the OMS system. | December | 2016 | 2017Q2 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-12-09 | N | 80 | N | 7 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 9752 | 13123 | 1441133 | 2016-12-09 12:14 | 2016-12-09 13:04 | 50 | 11kV | 3110 | 66 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14143 Somersby Panel 14 fdr tripped Relays: Earth Fault & Fault CHeck on Tx No. 2 Signals: 11kv trip, Tx2 Group Earth EFI's:S14458 UG Fault from S14458 to S18149 See 1441635,6 Exclude 1441133 | December | 2016 | 2017Q2 | 2017 | ZN14143:PA14 | ZN14143:PA14 | ZN14143/000014 | CENTRAL COAST | UG | Not Veg | 2016-12-09 | N | 47.1212 | N | 7 | N | N | 1.1101 | 39.4971 | 2272.6963
[7 empty] | 9729 | 12695 | 1441072 | 2016-12-09 09:37 | 2016-12-09 13:46 | 249 | 11kV | 1743 | 7 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | Repaired broken live line lead at top of DOLF on sub 51746. Completed by live line crew | December | 2016 | 2017Q2 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-12-09 | N | 249 | N | 7 | N | N | 1.1101 | 39.4971 | 1273.733
[7 empty] | 9441 | 9290 | 1441218 | 2016-12-09 17:26 | 2016-12-09 19:00 | 94 | 11kV | 9024 | 96 | HV | 3rd Party Vehicle | 3rd Party Impact | Pillar | Unplanned | No Weather Impact | N | LID 169799 A Phase DOLF : 10 Amp Coincided with a vehicle hitting a private pillar at Mt Providence nursing home Excluded OMS 1441211 | December | 2016 | 2017Q2 | 2017 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | UG | Not Veg | 2016-12-09 | N | 94 | N | 7 | N | N | 1.1101 | 39.4971 | 6594.473
[7 empty] | 9160 | 6136 | 1441239 | 2016-12-09 18:25 | 2016-12-09 19:54 | 89 | 11kV | 9790 | 110 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | S1850 Bass Hill P9 USL2004 fdr from S8105 Allingham Townsend No.2 UGOH bond off Remarks: bond. S8105 Allingham Townsend No.2 UGOH bond off | December | 2016 | 2017Q2 | 2017 | ZN1850:PA9 | ZN1850:PA42 | ZN01850/000042 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-12-09 | N | 89 | N | 7 | N | N | 1.1101 | 39.4971 | 7154.2432
[7 empty] | 9468 | 9656 | 1441271 | 2016-12-10 02:12 | 2016-12-10 03:49 | 97 | 11kV | 145159 | 1675 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7481 Darling Harbour - Pnl.9 tripped on: Earth Fault Front ling UG cable fault from Pnl.9 to S4199 to S7825 to S5312 to S5023 | December | 2016 | 2017Q2 | 2017 | ZN7481:PA9 | ZN7481:PA9 | ZN07481/000009 | SYDNEY | UG | Not Veg | 2016-12-10 | N | 86.6621 | N | 2 | N | N | 1.1101 | 39.4971 | 106077.9157
[7 empty] | 9631 | 11558 | 1441292 | 2016-12-10 08:15 | 2016-12-10 13:00 | 285 | 11kV | 192046 | 1540 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1287 Revesby 11kv feeder panel No.3 "S5046 etc" feeder tripped to lockout Relays: C phase IOC, C phase timed OC, lockout, timing Signals: 11kv trip Field EFIs: Nil Remarks: tree trimming in area. At vacant block 3 doors up from cnr Dilke Rd and Henry Lawson Dr, cust advised, a tree pruner + Crane operator working on LGE liquid amber struck DWS | December | 2016 | 2017Q2 | 2017 | ZN1287:PA3 | ZN1287:PA3 | ZN01287/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-12-10 | N | 124.7052 | N | 2 | N | N | 1.1101 | 39.4971 | 140341.5524
[7 empty] | 9939 | 15231 | 1441484 | 2016-12-11 17:45 | 2016-12-11 19:20 | 95 | 11kV | 45695 | 481 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn36200 Empire Bay section of Pa8 "The Poole Belrose" fdr from LB48657 footpath bond failed See 1441638 exclude 1441484 | December | 2016 | 2017Q2 | 2017 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2016-12-11 | N | 95 | N | 2 | N | N | 1.1101 | 39.4971 | 33392.5582
[7 empty] | 9821 | 13852 | 1441501 | 2016-12-11 19:25 | 2016-12-12 11:35 | 970 | 11kV | 8834 | 45 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 169807 4 fault operations Sensitive Earth Fault Excluded OMS 1441501 | December | 2016 | 2017Q2 | 2017 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2016-12-11 | N | 196.3111 | N | 2 | N | N | 1.1101 | 39.4971 | 6455.6266
[7 empty] | 8777 | 1084 | 1441648 | 2016-12-12 12:49 | 2016-12-12 14:50 | 121 | 11kV | 121 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169816 A Phase DOLF : 10 Amp Excluded OMS 1441648 | December | 2016 | 2017Q2 | 2017 | 514:18141 | 514:18141 | ZN00514/018141 | SINGLETON | OH | Veg | 2016-12-12 | N | 121 | N | 4 | N | N | 1.1101 | 39.4971 | 88.4232
[7 empty] | 10344 | 20202 | 1441745 | 2016-12-12 14:30 | 2016-12-12 14:57 | 27.2 | 11kV | 27.2 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | No LID Report Customer advised AG system normal, recloser he mentioned is a private device. CC1: 22-"Refer to SOp" | December | 2016 | 2017Q2 | 2017 |  |  |  | SINGLETON | Unknown | Not Veg | 2016-12-12 | N | 27.2 | N | 4 | N | N | 1.1101 | 39.4971 | 19.877
[7 empty] | 9859 | 14299 | 1441767 | 2016-12-12 15:01 | 2016-12-12 16:35 | 94 | 11kV | 94 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169818 A Phase DOLF : 10 Amp Excluded OMS 1441767 | December | 2016 | 2017Q2 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-12-12 | N | 94 | N | 4 | N | N | 1.1101 | 39.4971 | 68.6924
[7 empty] | 10119 | 17469 | 1441859 | 2016-12-12 20:16 | 2016-12-12 23:15 | 179.0167 | 11kV | 358.0333 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169821 Single Phase No protection operations. Dropper to DOLF replaced under AP. Excluded OMS 14418566. | December | 2016 | 2017Q2 | 2017 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | OH | Not Veg | 2016-12-12 | N | 179.0167 | N | 4 | N | N | 1.1101 | 39.4971 | 261.6402
[7 empty] | 9767 | 13262 | 1441879 | 2016-12-13 04:49 | 2016-12-13 05:35 | 46 | 11kV | 37766 | 821 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S15006 Dee Why West Panel 12 tripped and locked out on O/C Cause: Loud Explosion heard in Greystone Ave Wheeler Heights - Mains to patrol in daylight CC1: 22-"Refer to SOp" | December | 2016 | 2017Q2 | 2017 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Veg | 2016-12-13 | N | 46 | N | 13 | N | N | 1.1101 | 39.4971 | 27598.2789
[7 empty] | 9094 | 5296 | 1441960 | 2016-12-13 10:24 | 2016-12-13 12:25 | 121 | 11kV | 242 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169828 B Phase DOLF : 10 Amp Excluded OMS 1441960 | December | 2016 | 2017Q2 | 2017 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2016-12-13 | N | 121 | N | 13 | N | N | 1.1101 | 39.4971 | 176.8465
[7 empty] | 9074 | 5078 | 1441983 | 2016-12-13 10:49 | 2016-12-13 12:47 | 118 | 11kV | 93063 | 832 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn901 Surry Hills - Pnl.20 tripped on: Overcurrent & E/F Field EFIs: S47954, S7237 Abnormal: S8947 (Sw/B) Open with S3624 (Sw/D) Closed UG cable fault from S7237 (Sw/B) to S3281 (Sw/B) to S8947 (Sw/B) See 1442811 1442812 | December | 2016 | 2017Q2 | 2017 | ZN901:PA20 | ZN901:PA29 | ZN00901/000029 | SYDNEY | UG | Not Veg | 2016-12-13 | N | 111.8546 | N | 13 | N | N | 1.1101 | 39.4971 | 68007.6955
[7 empty] | 9223 | 6775 | 1442050 | 2016-12-13 13:26 | 2016-12-13 14:34 | 68 | 11kV | 20094 | 306 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12580 Erina Pa8 "Entrance Salvation" fdr tripped on Signals: 11kv trip and EFI Relays: Earth Fault EFI's: S14427 S14631 Cause: UG Cable fault between S14631 to S14388 to S18654 See 1442515,6 exclude 1442050,6 | December | 2016 | 2017Q2 | 2017 | ZN12580:PA8 | ZN12580:PA8 | ZN12580/000008 | CENTRAL COAST | UG | Not Veg | 2016-12-13 | N | 65.6667 | N | 13 | N | N | 1.1101 | 39.4971 | 14684.1025
[7 empty] | 10098 | 17234 | 1442060 | 2016-12-13 13:45 | 2016-12-13 14:38 | 53 | 11kV | 78652 | 1484 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | At S80 Chatswood Panel 25 tripped and locked out on IOC Timing and Lockout with EFI and lockout 11kV trip, Zone Earth Group Earth and No11 TX fault Check Cause: Burnt stick found by dop. (Location Not provided) | December | 2016 | 2017Q2 | 2017 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Veg | 2016-12-13 | N | 53 | N | 13 | N | N | 1.1101 | 39.4971 | 57476.5618
[7 empty] | 9045 | 4650 | 1442079 | 2016-12-13 14:05 | 2016-12-13 15:15 | 70 | 11kV | 53096 | 1532 | HV | Arcing | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn12650 West Gosford Panel 20 "Central Moore" fdr tripped on Relays: EArth Fault Signals: 11kv trip EFI's: Paenl 20 to S18143 Cause: Flashover on UGOH vicinity S18143 (57 Albany Rd" Isolated 11kv UGOH from S18143 See 1442518,9 exclude 1442079 | December | 2016 | 2017Q2 | 2017 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | OH | Not Veg | 2016-12-13 | N | 34.658 | N | 13 | N | N | 1.1101 | 39.4971 | 38800.9907
[7 empty] | 10140 | 17700 | 1442056 | 2016-12-13 14:36 | 2016-12-13 15:17 | 41 | 11kV | 20623 | 503 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of Pa17 "Somersby Falls" Loss of supply at Recloser 45202 Pacific Ashbrook Recloser 44961 Morgan Pacific 0.4 tripped on undervoltage Abnormal: Recloser 44961 closed and LK43212 open (DAROS 394280) Low Volts due to abnormal swithcing. Restored and okay See 1442523 exclude 1442123,9,40,2 | December | 2016 | 2017Q2 | 2017 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | Unknown | Unknown | 2016-12-13 | N | 41 | N | 13 | N | N | 1.1101 | 39.4971 | 15070.6801
[7 empty] | 8897 | 2743 | 1442198 | 2016-12-13 16:00 | 2016-12-13 16:58 | 58 | 11kV | 26158 | 451 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN1610 Homebush Bay Zone Pnl 12 "S8703" feeder tripped on: Relays - FN,G1,BN Remarks: UG fault. 11kv UG fault between S8400 Underwood Bellona No.2 Sw/A to S8321 Underwood Bellona No.1 Sw/B | December | 2016 | 2017Q2 | 2017 | ZN1610:PA12 | ZN1610:PA14 | ZN01610/000014 | PARRAMATTA | UG | Not Veg | 2016-12-13 | N | 58 | N | 13 | N | N | 1.1101 | 39.4971 | 19115.4949
[7 empty] | 9048 | 4751 | 1442257 | 2016-12-13 17:33 | 2016-12-13 19:51 | 138 | 11kV | 303230 | 2505 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn12570 Avoca Panel 21 "LB49826" fdr tripped on Relays: Earth Fault Signals: 11kv trip and EFI EFI's: Paenl 21 to S14907 Abnormal: S18037:SwB closed and SwA Opened Cable Fault between S14907 Tallowood Avia to S14906 Karalta Riatta See 1442528,30,2,3,4, Exclude 1442257 | December | 2016 | 2017Q2 | 2017 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | UG | Not Veg | 2016-12-13 | N | 121.0499 | N | 13 | N | N | 1.1101 | 39.4971 | 221591.5402
[7 empty] | 8761 | 870 | 1442273 | 2016-12-13 18:03 | 2016-12-13 20:20 | 137 | 11kV | 2466 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 169835 B Phase DOLF : 3 Amp 3.15A fuses found, replaced with 31.5A Excluded OMS No. 1442273 + 1442324 | December | 2016 | 2017Q2 | 2017 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Veg | 2016-12-13 | N | 137 | N | 13 | N | N | 1.1101 | 39.4971 | 1802.0801
[7 empty] | 8847 | 1980 | 1442359 | 2016-12-13 20:44 | 2016-12-13 21:15 | 31 | 11kV | 558 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 169836 A Phase DOLF : 3 Amp Aph 3.15A Line Fuse replaced with 31.5A fuse. Excluded OMS No. 1442359 + 1442365 | December | 2016 | 2017Q2 | 2017 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Veg | 2016-12-13 | N | 31 | N | 13 | N | N | 1.1101 | 39.4971 | 407.7699
[7 empty] | 9371 | 8399 | 1442374 | 2016-12-13 22:22 | 2016-12-14 01:10 | 168 | 11kV | 387915 | 2430 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S3922 Drummoyne Panel 5 'S36165 Byrnes Manning Etc" fdr tripped on Signals: 11kv trip, ZE, Tx1 GE Remarks: UG fault. 11kv UG cable fault from S7583 Warayama Place to S7681 Warayama Yara | December | 2016 | 2017Q2 | 2017 | ZN3922:PA5 | ZN3922:PA5 | ZN03922/000005 | INNER WEST | UG | Not Veg | 2016-12-13 | N | 159.6358 | N | 13 | N | N | 1.1101 | 39.4971 | 283476.8404
[7 empty] | 10133 | 17587 | 1442167 | 2016-12-13 15:36 | 2016-12-14 01:50 | 614 | 11kV | 118039 | 1517 | HV | Bushfire | Adverse Weather/Environment | Pole | Unplanned | Hot >35C | N | LID 169834 2 fault operations B & C Phase Overcurrent Bushfire damaged pole GS-83344. Excluded OMS No. 1442217 + 1442167 + 1442193 | December | 2016 | 2017Q2 | 2017 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Veg | 2016-12-13 | N | 77.8108 | N | 13 | N | N | 1.1101 | 39.4971 | 86259.4196
[7 empty] | 9872 | 14455 | 1442536 | 2016-12-14 12:23 | 2016-12-14 12:45 | 21.7333 | 11kV | 1238.8 | 57 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 169847 A Phase Earth Fault fdr tripped after strands broke on ohm that live linesman were repairing causing ohm to come into contact with crane | December | 2016 | 2017Q2 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-12-14 | N | 21.7333 | N | 5 | N | N | 1.1101 | 39.4971 | 905.2785
[7 empty] | 8904 | 2787 | 1442677 | 2016-12-14 18:15 | 2016-12-14 19:44 | 89 | 11kV | 47882 | 538 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Ex Zn12620 Noraville section of Pa11 "Norah Head" fdr from CP45053 Norah Head Recloser tripped on overcurrent, IOC, Earth Fault, Lockout UGOH Fault Short Circuit. to S47832 Duson Baynton See 1442677 exclude 1442691 | December | 2016 | 2017Q2 | 2017 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | Unknown | Unknown | 2016-12-14 | N | 89 | N | 5 | N | N | 1.1101 | 39.4971 | 34990.7533
[7 empty] | 10316 | 19782 | 1442685 | 2016-12-14 19:02 | 2016-12-14 20:12 | 70 | 11kV | 3562 | 51 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | @Zn1610 Homebush Bay 11kv Panel No.10 tripped on; Relays: FN (EFI) G1, CN signals: 11kv trip, Tx1 group earth Remarks: UG 11kv cable fault S1610 Homebush bay panel 10 to S3889 SPS 1082 Sw/A to S7138 Slough Holker Sw/D | December | 2016 | 2017Q2 | 2017 | ZN1610:PA10 | ZN1610:PA10 | ZN01610/000010 | PARRAMATTA | UG | Not Veg | 2016-12-14 | N | 69.8431 | N | 5 | N | N | 1.1101 | 39.4971 | 2603.0045
[7 empty] | 9253 | 7014 | 1442542 | 2016-12-14 12:34 | 2016-12-15 01:30 | 776 | 11kV | 295656 | 381 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12640 Umina section of Pa13 "Patonga" 11kV Re47749 Palmtree Neera tripped Relays: OC trip, Lockout Signals: trip Cause: Fire. Beyond CP47749 Palmtree Neera. Open Circuit Bond near AB42017 Customer reports - large explosion and small grass fire, fire is out now | December | 2016 | 2017Q2 | 2017 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2016-12-14 | N | 776 | N | 5 | N | N | 1.1101 | 39.4971 | 216056.6844
[7 empty] | 9496 | 9901 | 1442723 | 2016-12-14 23:05 | 2016-12-15 01:50 | 164.95 | 11kV | 3958.8 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Zn12660 Woy Woy section of Panel 5 "Empire Bay" PT11014 Daley Empire Bay 11kv centre phase HDO fuse operated Weather related See 1442723 exclude 1442726 | December | 2016 | 2017Q2 | 2017 | ZN12660:PA5 | ZN12660:PA5 | ZN12660/000005 | CENTRAL COAST | OH | Veg | 2016-12-14 | N | 164.95 | N | 5 | N | N | 1.1101 | 39.4971 | 2892.9743
[7 empty] | 9087 | 5254 | 1442730 | 2016-12-15 00:58 | 2016-12-15 04:11 | 193 | 11kV | 210137 | 1213 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Zn36200 Empire Bay section of Panel 8 11kV IR63104 Wards Hill Stewart 0.4 tripped and reclosed and tripped Relays: OC trip, Lockout Signals: 11kv trip Weather related See 1444457,9,60,2 Exclude 1442730 | December | 2016 | 2017Q2 | 2017 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2016-12-15 | N | 173.2374 | N | 9 | N | N | 1.1101 | 39.4971 | 153561.9216
[7 empty] | 8983 | 3787 | 1442748 | 2016-12-15 04:30 | 2016-12-15 06:07 | 97 | 11kV | 38310 | 450 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At Zn1610 Homebush Bay panel 12 "S8703" feeder has tripped Signals: 11kv trip Relays: 11kv trip Remarks: UG fault between Sw/B @ S7643 Shirley Australia and Sw/A @ Sub 7854 Olympic Sarah | December | 2016 | 2017Q2 | 2017 | ZN1610:PA12 | ZN1610:PA14 | ZN01610/000014 | PARRAMATTA | UG | Not Veg | 2016-12-15 | N | 85.1333 | N | 9 | N | N | 1.1101 | 39.4971 | 27995.818
[7 empty] | 9526 | 10290 | 1442756 | 2016-12-15 06:35 | 2016-12-15 07:30 | 55.0833 | 11kV | 3139.75 | 57 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | Ex Zn12580 Erina Zone section of Panel 14 "East Gosford" PT11421 Bay View Carrol 0.5 11kV C phase 16Amp hDO fuse operated Fuse Fatigue See 1442763 exclude 1442756 | December | 2016 | 2017Q2 | 2017 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Not Veg | 2016-12-15 | N | 55.0833 | N | 9 | N | N | 1.1101 | 39.4971 | 2294.4367
[7 empty] | 8923 | 2929 | 1442755 | 2016-12-15 05:59 | 2016-12-15 07:40 | 101 | 11kV | 4343 | 43 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Heavy | N | PT21726 Duneba Apanie 50A HDO operated on footpath side Cause: Tree beanch on PT1726 - Contacted surge arrestor See OMS 1442757 1442755 CC1: 22-"Refer to SOp" | December | 2016 | 2017Q2 | 2017 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Veg | 2016-12-15 | N | 101 | N | 9 | N | N | 1.1101 | 39.4971 | 3173.7363
[7 empty] | 8822 | 1726 | 1442980 | 2016-12-15 15:35 | 2016-12-15 16:05 | 30 | 11kV | 540 | 18 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 169868 WIre coming off pin at HR-83424 | December | 2016 | 2017Q2 | 2017 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2016-12-15 | N | 30 | N | 9 | N | N | 1.1101 | 39.4971 | 394.6161
[7 empty] | 10205 | 18608 | 1442966 | 2016-12-15 14:33 | 2016-12-15 16:24 | 111 | 11kV | 444 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169869 Single phase DOLF : 10 Amp excluded OMS 1442966 & 1442970 | December | 2016 | 2017Q2 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2016-12-15 | N | 111 | N | 9 | N | N | 1.1101 | 39.4971 | 324.4621
[7 empty] | 9480 | 9788 | 1443038 | 2016-12-15 18:57 | 2016-12-15 19:33 | 36 | 11kV | 72 | 2 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Heavy | N | Ex Zn12600 Lisarow section of Pa2 PT14486 MacDonalds Tuggerah 1.5 middle and Roadside 16Amp HDO Fuse operated Tree Branch was removed from HV Bushings See 1444466 exclude 1443038 | December | 2016 | 2017Q2 | 2017 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2016-12-15 | N | 36 | N | 9 | N | N | 1.1101 | 39.4971 | 52.6155
[7 empty] | 9585 | 11069 | 1442972 | 2016-12-15 14:59 | 2016-12-15 21:02 | 363 | 11kV | 78605 | 1821 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | LID 169867 3 fault operations B Phase Earth Fault Excluded OMS 1442972 | December | 2016 | 2017Q2 | 2017 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | Unknown | Unknown | 2016-12-15 | N | 43.1658 | N | 9 | N | N | 1.1101 | 39.4971 | 57442.2155
[7 empty] | 9370 | 8390 | 1443070 | 2016-12-15 23:44 | 2016-12-16 14:10 | 866 | 11kV | 12049 | 141 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | LID 169871 4 fault operations 3 phase Overcurrent Blown UGON pole SF-80504 to sub 29673 Excluded OMS 1443070 | December | 2016 | 2017Q2 | 2017 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | Unknown | Unknown | 2016-12-15 | N | 85.4539 | N | 9 | N | N | 1.1101 | 39.4971 | 8805.0538
[7 empty] | 9742 | 12939 | 1443210 | 2016-12-16 13:30 | 2016-12-16 14:15 | 45 | 11kV | 45 | 1 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 169878 Switched out under emergency to retie pin insulator SI Q0266 | December | 2016 | 2017Q2 | 2017 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2016-12-16 | N | 45 | N | 1 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 9732 | 12753 | 1443335 | 2016-12-17 02:55 | 2016-12-17 03:55 | 60 | 11kV | 240 | 4 | HV | Animal Frog | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169883 A Phase DOLF : 10 Amp Frogs | December | 2016 | 2017Q2 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2016-12-17 | N | 60 | N | 8 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 9834 | 13995 | 1443349 | 2016-12-17 07:11 | 2016-12-17 08:01 | 50 | 11kV | 10862 | 445 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Sub 1610 Homebush Bay Panel No.12 "Bennelong Australia" feeder tripped on Earth Fault, EFI No.1 Tx Group earth, 11kV Trip Field EFI's operated Subs 8703, 64424, 64425, 65874, 65875, 5362, 63928 Remarks: UGOH to CP 2065 between Sub 63928 & Sub 6564 | December | 2016 | 2017Q2 | 2017 | ZN1610:PA12 | ZN1610:PA14 | ZN01610/000014 | PARRAMATTA | Unknown | Unknown | 2016-12-17 | N | 24.409 | N | 8 | N | N | 1.1101 | 39.4971 | 7937.6292
[7 empty] | 9912 | 14941 | 1443353 | 2016-12-17 07:36 | 2016-12-17 09:33 | 116.75 | 11kV | 10040.5 | 86 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT15422 Ambleside St 11kV Centre phase HDO was blown Cause: Fuse fatigue See OMS 1443353 1443358 | December | 2016 | 2017Q2 | 2017 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Not Veg | 2016-12-17 | N | 116.75 | N | 8 | N | N | 1.1101 | 39.4971 | 7337.3013
[7 empty] | 8964 | 3581 | 1443429 | 2016-12-17 13:29 | 2016-12-17 14:56 | 87 | 11kV | 42369 | 487 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP35078 Maianbar Open and Locked out on OC and Earth Fault Section of Panel 3 ex S9118 Cronulla Zone Cause: Catamaran hit wires and called advises all seems to be ok - Mains to inspect | December | 2016 | 2017Q2 | 2017 | ZN9118:PA3 | ZN9118:PA3 | ZN09118/000003 | SUTHERLAND | OH | Not Veg | 2016-12-17 | N | 87 | N | 8 | N | N | 1.1101 | 39.4971 | 30962.0155
[7 empty] | 10333 | 20058 | 1443531 | 2016-12-17 23:07 | 2016-12-18 00:10 | 63 | 11kV | 97725 | 1633 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | At S80 Chatswood 11kV panel 24 tripped on Earth Fault, EFI and Fault Check on Pa24R Cause: UG cable fault - Pa24 to S6968 to S49280 See OMS 1444170 1443531 | December | 2016 | 2017Q2 | 2017 | ZN80:PA24 | ZN80:PA24 | ZN00080/000024 | WILLOUGHBY | UG | Not Veg | 2016-12-17 | N | 59.8438 | N | 8 | N | N | 1.1101 | 39.4971 | 71414.5476
[7 empty] | 9880 | 14539 | 1443516 | 2016-12-17 22:33 | 2016-12-18 00:12 | 99 | 11kV | 98802 | 998 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Wind Strong | N | On Panel 45 ex S847 Hornsby. 11kV B phase bond burnt of UGOH above CP690 (Near Supply point MC5168) See OMS 1444174 1443529 1443516 | December | 2016 | 2017Q2 | 2017 | ZN847:PA46 | ZN847:PA46 | ZN00847/000046 | HORNSBY | Unknown | Unknown | 2016-12-17 | N | 99 | N | 8 | N | N | 1.1101 | 39.4971 | 72201.5874
[7 empty] | 10355 | 20290 | 1443538 | 2016-12-17 23:44 | 2016-12-18 00:45 | 61 | 11kV | 5490 | 90 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | At PT15854 Nillera Ave 11kV 31.5 Amp fuse blown Cause Possum on TX at S15854 See OMS 1443538 1443540 1443541 | December | 2016 | 2017Q2 | 2017 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Not Veg | 2016-12-17 | N | 61 | N | 8 | N | N | 1.1101 | 39.4971 | 4011.9301
[7 empty] | 9685 | 12201 | 1443551 | 2016-12-18 01:19 | 2016-12-18 02:30 | 71 | 11kV | 8449 | 119 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Wind Strong | N | At PT63637 Coonong Gymea 11kV centre and roadside dropout fuses operated Cause: Suspect transformer fault see OMS 1444448 1443551 1443554 | December | 2016 | 2017Q2 | 2017 | ZN9700:PA16 | ZN9700:PA16 | ZN09700/000016 | SUTHERLAND | OH | Not Veg | 2016-12-18 | N | 71 | N | 7 | N | N | 1.1101 | 39.4971 | 6174.28
[7 empty] | 9007 | 4020 | 1443556 | 2016-12-18 02:07 | 2016-12-18 03:54 | 107 | 11kV | 83512 | 1016 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn3922 Drummoyne - 11kv Panel No.17 "sub 35126 Jersey Barnstaple" feeder tripped Relays: C phase timed O/C, EFI Signals: 11kv trip, Zone earth, No.1 Group Earth Remarks: UG fault. Feeder fault from S49979 Longview Bayville to Sub 14487 National Napoleon. See separate interruption report for Panel No.84 @ Zn116 leichhardt (when trying back feeder from S1487) | December | 2016 | 2017Q2 | 2017 | ZN3922:PA17 | ZN3922:PA17 | ZN03922/000017 | INNER WEST | UG | Not Veg | 2016-12-18 | N | 82.1969 | N | 7 | N | N | 1.1101 | 39.4971 | 61028.1064
[7 empty] | 10241 | 18945 | 1443558 | 2016-12-18 02:33 | 2016-12-18 07:35 | 302 | 11kV | 1208 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169889 Single phase DOLF : 16 Amp Excluded OMS 1443558 | December | 2016 | 2017Q2 | 2017 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2016-12-18 | N | 302 | N | 7 | N | N | 1.1101 | 39.4971 | 882.7708
[7 empty] | 9842 | 14063 | 1443589 | 2016-12-18 07:48 | 2016-12-18 09:10 | 82 | 11kV | 328 | 4 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169890 A & B phase DOLF : 20 Amp bat on mains, removed by EMSO excluded OMS 1443607 | December | 2016 | 2017Q2 | 2017 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2016-12-18 | N | 82 | N | 7 | N | N | 1.1101 | 39.4971 | 239.6927
[7 empty] | 9781 | 13502 | 1443600 | 2016-12-18 08:20 | 2016-12-18 09:55 | 95 | 11kV | 285 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169891 C Phase DOLF : 10 Amp Correct sub 51203 not 53056. bird on tx. Excluded OMS 1443600 | December | 2016 | 2017Q2 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2016-12-18 | N | 95 | N | 7 | N | N | 1.1101 | 39.4971 | 208.2696
[7 empty] | 8861 | 2234 | 1443579 | 2016-12-18 07:28 | 2016-12-18 10:50 | 202 | 11kV | 1616 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 169894 Ap 0950-1030 to repair broken LLC lead. Excluded OMS 1443579 | December | 2016 | 2017Q2 | 2017 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2016-12-18 | N | 202 | N | 7 | N | N | 1.1101 | 39.4971 | 1180.9251
[7 empty] | 9923 | 15059 | 1443391 | 2016-12-17 10:07 | 2016-12-18 16:45 | 1838 | 11kV | 260661 | 1866 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35400 North Sydney Panel 110 tripped on B phase OC and E/F 11kV UG fault from S48019 to S2686 to S3198 tee S5645 Supply restored to distributor 2 @ 1645 on 18/12/2016 (Long Outage) Assumed Distributor 1 restored at 1300 on 17/12/2016 (This is when all the parallels started to fail) See OMS 1444708 1444709 1444711 1443391 1443420 | December | 2016 | 2017Q2 | 2017 | ZN35400:PA110 | ZN35400:PA110 | ZN35400/000110 | NORTH SYDNEY | UG | Not Veg | 2016-12-17 | N | 139.6897 | N | 8 | N | N | 1.1101 | 39.4971 | 190483.3706
[7 empty] | 9417 | 9009 | 1443722 | 2016-12-18 23:24 | 2016-12-19 00:15 | 51 | 11kV | 306 | 6 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Heavy | N | Ex Zn12690 Berkeley Vale section of Panel 24 PT12499 Brush Anderson 0.5 Blown HDO Footpath side 16 Amp Flashover caused by wet candle bark on PT Subs fitter to check PT in daylight See 1444470 exclude 1443722 | December | 2016 | 2017Q2 | 2017 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2016-12-18 | N | 51 | N | 7 | N | N | 1.1101 | 39.4971 | 223.6158
[7 empty] | 9204 | 6511 | 1443920 | 2016-12-19 17:57 | 2016-12-20 01:35 | 458 | 11kV | 45938 | 237 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Recloser CP64825 Deepwater Holly Tripped on O/C Cause: Car Hit Pole Causing 11kV to come down - LVF mains O/S 117 Neerim Rd See OMS 1444693 1444694 14443933 14443922 14443920 | December | 2016 | 2017Q2 | 2017 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | OH | Not Veg | 2016-12-19 | N | 193.8312 | N | 1 | N | N | 1.1101 | 39.4971 | 33570.1355
[7 empty] | 8856 | 2191 | 1443966 | 2016-12-20 00:23 | 2016-12-20 02:30 | 127 | 11kV | 5715 | 45 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn13000 Lake Munmorah section of Panel 7 PT12233 Kullaroo Cudgee 11KV B Phase HDO blown 10Amp. Fatigue Fuse See 1444478 exclude 1443966,8 | December | 2016 | 2017Q2 | 2017 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2016-12-20 | N | 127 | N | 4 | N | N | 1.1101 | 39.4971 | 4176.3534
[7 empty] | 10081 | 16939 | 1444012 | 2016-12-20 08:07 | 2016-12-20 10:00 | 113 | 11kV | 113 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 169901 C Phase DOLF: wrong sub in oms. Excluded OMS 1444012 | December | 2016 | 2017Q2 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2016-12-20 | N | 113 | N | 4 | N | N | 1.1101 | 39.4971 | 82.5771
[7 empty] | 8801 | 1492 | 1444156 | 2016-12-20 18:00 | 2016-12-20 19:10 | 70 | 11kV | 2590 | 37 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 169912 Also see # 169909/OMS 1444290 for initial T/R Isolate to repair leaning pole & Retie conductor.. Excluded OMS 1444156 & 1444216 | December | 2016 | 2017Q2 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-12-20 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 1892.6956
[7 empty] | 9705 | 12351 | 1444266 | 2016-12-21 02:37 | 2016-12-21 04:08 | 91 | 11kV | 76314 | 903 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | Zn10994 Mortdale Panel 19L "Roberts Fairway No.1" fdr tripped on Relays: O/C and E/F Signals: 11kv trip EFI's: S50482 S50483 S10040 S10954 S10898 S10605 Possum on UGOH bear S10082. Lineworkers to check in daylight Switching tag left at S10082 See 1444820,1 exclude 1444266 | December | 2016 | 2017Q2 | 2017 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2016-12-21 | N | 84.5116 | N | 4 | N | N | 1.1101 | 39.4971 | 55768.0203
[7 empty] | 10265 | 19165 | 1444257 | 2016-12-20 21:57 | 2016-12-21 10:10 | 733 | 11kV | 2199 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 169920 C phase DOLF : 3 Amp Replaced blown 3 amp Boric Acid HV fuse on sub. | December | 2016 | 2017Q2 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2016-12-20 | N | 733 | N | 4 | N | N | 1.1101 | 39.4971 | 1606.9643
[7 empty] | 10006 | 16093 | 1444378 | 2016-12-21 10:44 | 2016-12-21 15:30 | 286 | 11kV | 78135 | 1147 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S3154 St Ives 11kV panel 5 tripped, reclosed tripped and locke dout on Relays: B phase OC, Lockout, Timing and EFI Signals: 11kVTrip TX1Group Earth and Zone Earth Cause: tree branch brought down 11kV wires near PT1539 See OMS 1444701 1444702 1444703 1444378 1444383 1444384 1444428 | December | 2016 | 2017Q2 | 2017 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | OH | Veg | 2016-12-21 | N | 68.1212 | N | 4 | N | N | 1.1101 | 39.4971 | 57098.7534
[7 empty] | 9914 | 14964 | 1444472 | 2016-12-21 15:16 | 2016-12-21 17:20 | 124 | 11kV | 24576 | 200 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 169926 1 fault operation Sensitive Earth Fault One blade of OPEN Point ABS 40585 was closed causing out of balance currents between FDR 48050 & 48056. S.Apps. Possibly last operated in NAR 17636 15/12/2016. | December | 2016 | 2017Q2 | 2017 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2016-12-21 | N | 122.88 | N | 4 | N | N | 1.1101 | 39.4971 | 17959.4159
[7 empty] | 9238 | 6917 | 1444497 | 2016-12-21 16:43 | 2016-12-21 17:20 | 37 | 11kV | 12830 | 410 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 169927 1 fault operation A Phase Overcurrent One blade of OPEN Point ABS 40585 was closed causing out of balance currents between FDR 48050 & 48056. S.Apps. Possibly last operated in NAR 17636 15/12/2016. | December | 2016 | 2017Q2 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2016-12-21 | N | 31.2927 | N | 4 | N | N | 1.1101 | 39.4971 | 9375.7856
[7 empty] | 10043 | 16515 | 1443425 | 2016-12-22 01:46 | 2016-12-22 02:22 | 36 | 11kV | 24480 | 680 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill panel 10 tripped on Suignals: 11kV trip Relays: SEL SW/A Closed @ S6603 and SW/A open @ S5260 Cause: After switchingSEL was made N/A and feeder tripped. Feeder tripped, short OH section patrolled everything ok - No obvious cause - Possible faulty relay S1444698 1443425 1443427 | December | 2016 | 2017Q2 | 2017 | ZN35500:PA24 | ZN129:PA49 | ZN00129/000049 | RYDE | UG | Not Veg | 2016-12-22 | N | 36 | N | 3 | N | N | 1.1101 | 39.4971 | 17889.262
[7 empty] | 9218 | 6714 | 1444636 | 2016-12-22 12:21 | 2016-12-22 15:30 | 189 | 11kV | 189 | 1 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Electrical Storm | N | Ex Zn12640 Umina section of Panel 13 PT11051 Juno Point water side HDO blown and assembly destroyed 16Amp Lightning. Previous Storm See 1444848 exclude 1444636 | December | 2016 | 2017Q2 | 2017 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2016-12-22 | N | 189 | N | 3 | N | N | 1.1101 | 39.4971 | 138.1156
[7 empty] | 9759 | 13156 | 1444664 | 2016-12-22 15:27 | 2016-12-22 17:38 | 131 | 11kV | 271063 | 2092 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington Panel 23 "Renny Lane" opened on B phase overcurrent and earth fault No signals at zone Abnormal: Sw "D" closed at S47219 Victoria Elizabeth and Panel 17 open at Paddington UG Fault between S7839 Renny Lane and S49426 Renny Regent See 1444850,1 exclude 1444664,79 | December | 2016 | 2017Q2 | 2017 | ZN342:PA17 | ZN342:PA17 | ZN00342/000017 | WOOLLAHRA | UG | Not Veg | 2016-12-22 | N | 129.5712 | N | 3 | N | N | 1.1101 | 39.4971 | 198084.8454
[7 empty] | 10321 | 19828 | 1444941 | 2016-12-23 19:42 | 2016-12-23 20:50 | 68 | 11kV | 3876 | 57 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 169947 Phase A - fuse size 20 Amp Faulty arrestor A ph cut away by DOP. Please programme to replace arrestor | December | 2016 | 2017Q2 | 2017 | 221:11894 | 221:11894 | ZN00221/011894 | LAKE MACQUARIE | OH | Not Veg | 2016-12-23 | N | 68 | N | 3 | N | N | 1.1101 | 39.4971 | 2832.4665
[7 empty] | 8919 | 2914 | 1444955 | 2016-12-23 22:06 | 2016-12-23 23:45 | 99 | 11kV | 22956 | 457 | HV | Animal Possum | Animal | O/H Conductor Insulated | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay - Pnl.4 tripped on: C phase O/C, EFI @ PT9703 Melrose Av - Roadside & middle phase HDO fuses operated Possum found at base of pole @ PT9703 See 1445746 1445747 | December | 2016 | 2017Q2 | 2017 | ZN9550:PA4 | ZN9550:PA4 | ZN09550/000004 | SUTHERLAND | OH | Not Veg | 2016-12-23 | N | 50.2319 | N | 3 | N | N | 1.1101 | 39.4971 | 16775.5677
[7 empty] | 10368 | 20432 | 1444915 | 2016-12-23 17:53 | 2016-12-24 01:00 | 427 | 11kV | 101100 | 1744 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12600 Lisarow Pnl.3 tripped on: SEL with lockout tree brought down overhead near AB44819 - 769 Pacific Hwy See 1445790 1445791 1445793 | December | 2016 | 2017Q2 | 2017 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2016-12-23 | N | 57.9702 | N | 3 | N | N | 1.1101 | 39.4971 | 73880.8981
[7 empty] | 8872 | 2422 | 1444978 | 2016-12-24 08:39 | 2016-12-24 08:45 | 6 | 11kV | 630 | 105 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 169951 Phase A, Fuse no fuse blown, top of fuse carrier HR | December | 2016 | 2017Q2 | 2017 | 228:7491 | 228:85415 | ZN00228/085415 | NEWCASTLE | OH | Not Veg | 2016-12-24 | N | 6 | N | 21 | Y | Y | 1.1101 | 39.4971 | 460.3854
[7 empty] | 10164 | 17948 | 1445003 | 2016-12-24 09:57 | 2016-12-24 11:15 | 78 | 11kV | 78 | 1 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 169949 Phase B - Fuse 10 AMP Substation DOLF Animal - BIRD - no further information provided | December | 2016 | 2017Q2 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2016-12-24 | N | 78 | N | 21 | Y | Y | 1.1101 | 39.4971 | 57.0001
[7 empty] | 8942 | 3222 | 1445018 | 2016-12-24 11:03 | 2016-12-24 13:20 | 137 | 11kV | 822 | 6 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 169952 LLC came loose | December | 2016 | 2017Q2 | 2017 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2016-12-24 | N | 137 | N | 21 | Y | Y | 1.1101 | 39.4971 | 600.6934
[7 empty] | 8739 | 347 | 1445727 | 2016-12-24 16:44 | 2016-12-24 16:55 | 11 | 11kV | 1947 | 177 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169961 1 Fault operations, ABC Phase, targets required, patrol requested Thunderstorm at time of event | December | 2016 | 2017Q2 | 2017 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2016-12-24 | N | 11 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1422.8102
[7 empty] | 10288 | 19398 | 1445054 | 2016-12-24 16:13 | 2016-12-24 17:28 | 75 | 11kV | 19125 | 255 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169959 Earth Fault, Electrical storm at time | December | 2016 | 2017Q2 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2016-12-24 | N | 75 | N | 21 | Y | Y | 1.1101 | 39.4971 | 13975.9859
[7 empty] | 9869 | 14413 | 1445079 | 2016-12-24 17:57 | 2016-12-24 19:13 | 75.7 | 11kV | 4314.9 | 57 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169993 Phase B - 20 Amp Fuse, Line DOLF No obvious cause CC1: 22-"Refer to SOp" | December | 2016 | 2017Q2 | 2017 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2016-12-24 | N | 75.7 | N | 21 | Y | Y | 1.1101 | 39.4971 | 3153.2017
[7 empty] | 8957 | 3481 | 1445113 | 2016-12-24 18:54 | 2016-12-24 19:20 | 26 | 11kV | 52 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169991 Phase C, Fuse 16 AMP Substation DOLF Thunderstorm at time of event | December | 2016 | 2017Q2 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2016-12-24 | N | 26 | N | 21 | Y | Y | 1.1101 | 39.4971 | 38.0001
[7 empty] | 10008 | 16152 | 1445065 | 2016-12-24 17:01 | 2016-12-24 20:20 | 199 | 11kV | 199 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169992 Substation DOLF, Electrical storm at time of event Note: customer also affected by Trip and Reclose event 1445718 | December | 2016 | 2017Q2 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2016-12-24 | N | 199 | N | 21 | Y | Y | 1.1101 | 39.4971 | 145.4233
[7 empty] | 9096 | 5304 | 1445080 | 2016-12-24 18:00 | 2016-12-24 20:46 | 165.95 | 11kV | 62397.2 | 376 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 169997 - A Phase 10 AMP, Earth Fault - Electrical Storm at time LID 169995 - Phase A, 10 AMP Fuse, Substation DOLF - 13851 (OMS 144639) LID 169994 - Phase A - 10 AMP DOLF 25789, Electrical Storm at time (OMS 1445634) | December | 2016 | 2017Q2 | 2017 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2016-12-24 | N | 165.95 | N | 21 | Y | Y | 1.1101 | 39.4971 | 45598.0334
[7 empty] | 8759 | 775 | 1445058 | 2016-12-24 16:36 | 2016-12-24 21:15 | 279 | 11kV | 2790 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 160001 A & B Phases, 16 AMP, Line Dolf, thunderstorm time at time of event | December | 2016 | 2017Q2 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2016-12-24 | N | 279 | N | 21 | Y | Y | 1.1101 | 39.4971 | 2038.8497
[7 empty] | 8807 | 1559 | 1445145 | 2016-12-24 20:03 | 2016-12-24 21:45 | 102 | 11kV | 29478 | 289 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Zn1850 Bass Hill - Pnl.11 tripped on: A phase IOC & timed O/C Lighting arrestor failed in front line section of feeder. | December | 2016 | 2017Q2 | 2017 | ZN1850:PA11 | ZN1850:PA42 | ZN01850/000042 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-12-24 | N | 102 | N | 21 | Y | Y | 1.1101 | 39.4971 | 21541.6529
[7 empty] | 9068 | 5011 | 1445104 | 2016-12-24 20:46 | 2016-12-24 22:25 | 99 | 11kV | 198 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 169998 Phase A, 10 AMP DOLF replace blown Lightning arrestor Note: Customers also affected by OMS 1445080 event that started at 24/12/16 18:00 | December | 2016 | 2017Q2 | 2017 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2016-12-24 | N | 99 | N | 21 | Y | Y | 1.1101 | 39.4971 | 144.6926
[7 empty] | 9717 | 12504 | 1445119 | 2016-12-24 19:03 | 2016-12-24 22:55 | 232 | 11kV | 232 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 160009 Single Phase, fuse 10 AMP, substation DOLF Thunderstorm at time of event | December | 2016 | 2017Q2 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2016-12-24 | N | 232 | N | 21 | Y | Y | 1.1101 | 39.4971 | 169.5388
[7 empty] | 9100 | 5352 | 1445101 | 2016-12-24 19:29 | 2016-12-24 23:00 | 211 | 11kV | 1055 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 160005 Phase A, Fuse 10 Amp, Substation DOLF Thunderstorm at time of event | December | 2016 | 2017Q2 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2016-12-24 | N | 211 | N | 21 | Y | Y | 1.1101 | 39.4971 | 770.9629
[7 empty] | 9517 | 10208 | 1445077 | 2016-12-24 17:53 | 2016-12-24 23:53 | 360 | 11kV | 360 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | Replace C phase LA & replace HV fuse in Sub 62403 Chad Jones 26.12.2016 | December | 2016 | 2017Q2 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2016-12-24 | N | 360 | N | 21 | Y | Y | 1.1101 | 39.4971 | 263.0774
[7 empty] | 9893 | 14745 | 1445060 | 2016-12-24 16:42 | 2016-12-25 00:30 | 468 | 11kV | 468 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 160003 A Phases, 10 AMP, Substation Dolf, thunderstorm time at time of event | December | 2016 | 2017Q2 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2016-12-24 | N | 468 | N | 21 | Y | Y | 1.1101 | 39.4971 | 342.0006
[7 empty] | 8843 | 1909 | 1445062 | 2016-12-24 16:49 | 2016-12-25 01:50 | 541 | 11kV | 4328 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 160013 ABC Phases, Line DOLF - 16 AMP fuse thunderstorm at time of event | December | 2016 | 2017Q2 | 2017 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2016-12-24 | N | 541 | N | 21 | Y | Y | 1.1101 | 39.4971 | 3162.7747
[7 empty] | 10197 | 18508 | 1445059 | 2016-12-24 17:44 | 2016-12-25 01:52 | 487.5167 | 11kV | 56551.9333 | 116 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 160014 ABC Phases, Pole Mounted RAGCB 11kV mains beyond L 40610 restrung under AP LID 160016 Phase A, substation DOLF, 10 AMP - sub restored ( 25/12/16 01:20 ) | December | 2016 | 2017Q2 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2016-12-24 | N | 487.5167 | N | 21 | Y | Y | 1.1101 | 39.4971 | 41326.4849
[7 empty] | 10317 | 19800 | 1445103 | 2016-12-24 18:38 | 2016-12-25 02:00 | 441.65 | 11kV | 441.65 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 160004 Single Phase 10 AMP Fuse, DOLF replaced 2 arrestors under AP | December | 2016 | 2017Q2 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2016-12-24 | N | 441.65 | N | 21 | Y | Y | 1.1101 | 39.4971 | 322.7448
[7 empty] | 9151 | 6021 | 1445126 | 2016-12-25 01:52 | 2016-12-25 02:45 | 53 | 11kV | 159 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 160017 C phase Fuse 10 AMP, Substation DOLF Section isolated to replace arrestors Note: Customers affected also by OMS 1445073 - mains down that began at 24/12/16 17:44 | December | 2016 | 2017Q2 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2016-12-25 | N | 53 | N | 6 | N | N | 1.1101 | 39.4971 | 116.1925
[7 empty] | 9807 | 13697 | 1445075 | 2016-12-24 17:48 | 2016-12-25 08:25 | 877 | 11kV | 2631 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 160006 Phase A, Fuse 16 AMP, Substation DOLF blown arrestor cut away needs to be replaced | December | 2016 | 2017Q2 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2016-12-24 | N | 877 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1922.6572
[7 empty] | 8888 | 2635 | 1445160 | 2016-12-24 21:04 | 2016-12-25 09:30 | 746 | 11kV | 1492 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 160012 Phase A, 10 AMP Fuse, substation DOLF Electrical storm at time | December | 2016 | 2017Q2 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2016-12-24 | N | 746 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1090.3096
[7 empty] | 9241 | 6933 | 1445204 | 2016-12-25 07:35 | 2016-12-25 10:45 | 190 | 11kV | 4385 | 24 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 160023 4 fault operations C Phase Earth Fault excluded OMS 1445204 | December | 2016 | 2017Q2 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-12-25 | N | 182.7083 | N | 6 | N | N | 1.1101 | 39.4971 | 3204.4287
[7 empty] | 9997 | 15925 | 1445187 | 2016-12-25 00:01 | 2016-12-25 12:00 | 719 | 11kV | 2157 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 160021 Single Phase, Fuse 10 AMP Electrical storm at time of event | December | 2016 | 2017Q2 | 2017 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2016-12-25 | N | 719 | N | 6 | N | N | 1.1101 | 39.4971 | 1576.272
[7 empty] | 9097 | 5314 | 1445201 | 2016-12-25 06:38 | 2016-12-25 12:40 | 362 | 11kV | 724 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 160022 Phase B, Fuse 10 AMP, substation DOLF Previous Storm | December | 2016 | 2017Q2 | 2017 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2016-12-25 | N | 362 | N | 6 | N | N | 1.1101 | 39.4971 | 529.0778
[7 empty] | 8955 | 3461 | 1446893 | 2016-12-25 10:45 | 2016-12-25 14:35 | 230 | 11kV | 2055 | 24 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 160023 4 fault operations C Phase Earth Fault excluded OMS 1445204 | December | 2016 | 2017Q2 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2016-12-25 | N | 85.625 | N | 6 | N | N | 1.1101 | 39.4971 | 1501.7334
[7 empty] | 9657 | 11840 | 1445261 | 2016-12-25 14:39 | 2016-12-26 00:40 | 601 | 11kV | 31261 | 56 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | REC45015 Brush Creek tripped on: OC trip Tree branch down into 11kV and 415V near PT11492 - damaging 2 bays of mains and hardware on adjacent poles. Tree branch cleared repairs carried out and supply restored. Also Small grass fire started due to tree branch pulling down 11 KV and LV mains See 1445803 1445804 | December | 2016 | 2017Q2 | 2017 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2016-12-25 | N | 558.2321 | N | 6 | N | N | 1.1101 | 39.4971 | 22844.6168
[7 empty] | 9489 | 9863 | 1445332 | 2016-12-26 09:48 | 2016-12-26 11:45 | 116.9167 | 11kV | 818.4167 | 7 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 160031 Crossarm, broken @ DP-30845 | December | 2016 | 2017Q2 | 2017 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2016-12-26 | N | 116.9167 | N | 5 | N | N | 1.1101 | 39.4971 | 598.0748
[7 empty] | 9593 | 11171 | 1445324 | 2016-12-26 12:20 | 2016-12-26 13:30 | 70 | 11kV | 350 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 160032 Main off Pin at AK-52615 Note: customer reported part supply at 26/12/16 08:56 | December | 2016 | 2017Q2 | 2017 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2016-12-26 | N | 70 | N | 5 | N | N | 1.1101 | 39.4971 | 255.7697
[7 empty] | 9684 | 12193 | 1445394 | 2016-12-26 17:48 | 2016-12-26 19:12 | 84 | 11kV | 76944 | 916 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3922 Drummoyne - Pnl.22 tripped on: C phase O/C, E/F and EFI UG cable fault from Pnl.22 to S62472 to 2076 to S7804 | December | 2016 | 2017Q2 | 2017 | ZN3922:PA22 | ZN3922:PA22 | ZN03922/000022 | CANADA BAY | UG | Not Veg | 2016-12-26 | N | 84 | N | 5 | N | N | 1.1101 | 39.4971 | 56228.4057
[7 empty] | 9207 | 6584 | 1445429 | 2016-12-26 21:29 | 2016-12-26 22:24 | 55 | 11kV | 163856 | 3046 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Zn4242 Meadowbank - Pnl.31 tripped on: ABC phase O/C, EFI, F/C Field EFIs: S1829 ,S49273, S49274, S6579, S7356, S4360, S1572 DOp located dead possum on Recloser 46117 Balaclava Vimiera See 1445671 1445672 | December | 2016 | 2017Q2 | 2017 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Not Veg | 2016-12-26 | N | 53.7938 | N | 5 | N | N | 1.1101 | 39.4971 | 119741.1319
[7 empty] | 9462 | 9606 | 1445382 | 2016-12-26 17:02 | 2016-12-27 05:20 | 738 | 11kV | 86209 | 1744 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn12600 Lisarow - Pnl.3 tripped , relcosed, tripped & locked out on: A phase IOC, timed O/C, EFI Field EFis: S12399, S18173, S14247 Note: S14623 EFI did not operate Vehicle hit pole on corner of Newling Street & Pacific Hwy, Niagra Park 11kV & 415V mains and pole down. 11kV into 415V at PT47662 See 1445796 1445797 1445798 | December | 2016 | 2017Q2 | 2017 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2016-12-26 | N | 49.4318 | N | 5 | N | N | 1.1101 | 39.4971 | 62998.9945
[7 empty] | 9701 | 12323 | 1445446 | 2016-12-27 04:45 | 2016-12-27 05:43 | 58 | 11kV | 173362 | 2989 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn4545 Meadowbnka Pnl.31 tripped on: IOC ABC phase, EFI, F/C Field EFIs: S1829 S49273 S49274 S6579 S7356 S4360 S1572 S4669 S4549 Possum found at 1st UGOH below S4549 (Sw/B) | December | 2016 | 2017Q2 | 2017 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Not Veg | 2016-12-27 | N | 58 | N | 3 | N | N | 1.1101 | 39.4971 | 126687.8363
[7 empty] | 9637 | 11649 | 1445449 | 2016-12-27 10:30 | 2016-12-27 17:42 | 432.7333 | 11kV | 15578.4 | 36 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | No record from control room regarding this. Suspect AB2013 opened by DOp to remove tree branch or complete repairs CC1: 22-"Refer to SOp" | December | 2016 | 2017Q2 | 2017 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2016-12-27 | N | 432.7333 | N | 3 | N | N | 1.1101 | 39.4971 | 11384.2352
[7 empty] | 10263 | 19123 | 1445555 | 2016-12-27 19:17 | 2016-12-27 20:36 | 79 | 11kV | 36360 | 835 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn874 Concord - Pnl.2 tripped on: A phase O/C, EF, EFI Field EFIs: S2833 Note: S2034 EFI is faulty Abnormal: S7977 (Sw/F) Closed with S1450 (Sw/A) Open UG cable fault from S2034 to S6920 to S7977 See 1445735 1445736 1445737 | December | 2016 | 2017Q2 | 2017 | ZN874:PA9 | ZN874:PA9 | ZN00874/000009 | CANADA BAY | UG | Not Veg | 2016-12-27 | N | 43.5449 | N | 3 | N | N | 1.1101 | 39.4971 | 26570.8156
[7 empty] | 9510 | 10055 | 1445581 | 2016-12-28 03:40 | 2016-12-28 05:10 | 90 | 11kV | 118412 | 1598 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12580 Erina - Pnl.10 tripped on: C phase IOC, EFI Field EFIs: S13682, S12866 S14189 S14628 S14421 S12867 UG cable fault from S12867 9Sw/B) and S14719 (Sw/B) See 1445787 1445788 | December | 2016 | 2017Q2 | 2017 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | UG | Not Veg | 2016-12-28 | N | 74.1001 | N | 7 | N | N | 1.1101 | 39.4971 | 86531.997
[7 empty] | 8853 | 2087 | 1445617 | 2016-12-28 08:34 | 2016-12-28 10:00 | 85.75 | 11kV | 10204.25 | 119 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 160041 11kV tapping blown affecting sub 15513 | December | 2016 | 2017Q2 | 2017 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2016-12-28 | N | 85.75 | N | 7 | N | N | 1.1101 | 39.4971 | 7456.9649
[7 empty] | 9293 | 7400 | 1445725 | 2016-12-28 14:10 | 2016-12-28 14:50 | 40 | 11kV | 80 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 160044 Phase C CASS Job - 445725 Broken Live Line Lead | December | 2016 | 2017Q2 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2016-12-28 | N | 40 | N | 7 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 8956 | 3478 | 1445744 | 2016-12-28 12:03 | 2016-12-28 15:09 | 186 | 11kV | 372 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | replaced hv fuse | December | 2016 | 2017Q2 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2016-12-28 | N | 186 | N | 7 | N | N | 1.1101 | 39.4971 | 271.8466
[7 empty] | 9661 | 11894 | 1445842 | 2016-12-28 17:12 | 2016-12-28 18:43 | 91 | 11kV | 159341 | 1751 | HV | Vegetation Blow/Fall In | Vegetation | UGOH | Unplanned | Hot >35C | N | Zn15004 newport - Pnl.1 tripped on earth fault. Field EFIs: S15792, S16755, S48427 Tree branch on UGOH at 127 Crescent, near S16841 | December | 2016 | 2017Q2 | 2017 | ZN15004:PA1 | ZN15004:PA1 | ZN15004/000001 | NORTHERN BEACHES | OH | Veg | 2016-12-28 | N | 91 | N | 7 | N | N | 1.1101 | 39.4971 | 116441.703
[7 empty] | 8892 | 2658 | 1445835 | 2016-12-28 16:57 | 2016-12-28 20:00 | 183 | 11kV | 13725 | 75 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT2306 Norma North - 11kV HDO 'A' phase fuse fatigued. Replaced 50Amp fuse | December | 2016 | 2017Q2 | 2017 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Not Veg | 2016-12-28 | N | 183 | N | 7 | N | N | 1.1101 | 39.4971 | 10029.8252
[7 empty] | 9895 | 14783 | 1445875 | 2016-12-28 22:04 | 2016-12-28 22:36 | 32 | 11kV | 896 | 28 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn901 Surry Hills - Pnl.9 tripped on: B phase o/C and E/F Field EFIs: S7563, S6260 UG cable fault from S6260 (Sw/D) to S7898 (Sw/A) to S113 to S5514 (Sw/D) | December | 2016 | 2017Q2 | 2017 | ZN901:PA9 | ZN901:PA9 | ZN00901/000009 | SYDNEY | UG | Not Veg | 2016-12-28 | N | 32 | N | 7 | N | N | 1.1101 | 39.4971 | 654.7704
[7 empty] | 9352 | 8094 | 1445902 | 2016-12-29 08:33 | 2016-12-29 09:38 | 65 | 11kV | 124935 | 2031 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn342 paddington Pnl.17 tripped on: Earth Fault, Timed O/C, EFI Abnormal: S47219 Victoria elizabeth (Sw/D) Closed with S49426 Renny Regent (Sw/A) Open - due to UG cable fault. UG cable fault occured from Pnl.17 to S4194 Elizabeth Stewart. | December | 2016 | 2017Q2 | 2017 | ZN342:PA17 | ZN342:PA17 | ZN00342/000017 | WOOLLAHRA | UG | Not Veg | 2016-12-29 | N | 61.514 | N | 10 | N | N | 1.1101 | 39.4971 | 91298.813
[7 empty] | 8858 | 2206 | 1445910 | 2016-12-29 08:44 | 2016-12-29 13:38 | 294 | 11kV | 588 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 160047 Substation DOLF replaced c phase arrestor | December | 2016 | 2017Q2 | 2017 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2016-12-29 | N | 294 | N | 10 | N | N | 1.1101 | 39.4971 | 429.6931
[7 empty] | 9580 | 10978 | 1446065 | 2016-12-29 17:40 | 2016-12-29 18:34 | 54 | 11kV | 1890 | 35 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Hot >35C | N | Zn9037 Miranda Pnl.17 tripped on: E/F and EFI @ S9081 Westfield Miranda Fair No.5 - Tx 2 tripped on A & B phase differential Transformer No.3 @ S9081 failed. | December | 2016 | 2017Q2 | 2017 | ZN9037:PA17 | ZN9037:PA17 | ZN09037/000017 | SUTHERLAND | UG | Not Veg | 2016-12-29 | N | 54 | N | 10 | N | N | 1.1101 | 39.4971 | 1381.1563
[7 empty] | 10161 | 17916 | 1446052 | 2016-12-29 16:54 | 2016-12-29 19:00 | 126 | 11kV | 17007 | 289 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Zn1850 Bass Hill - Pnl.11 tripped on: SEL Bond burnt of AB 8 See 1446165 1446166 1446167 | December | 2016 | 2017Q2 | 2017 | ZN1850:PA11 | ZN1850:PA42 | ZN01850/000042 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2016-12-29 | N | 58.8478 | N | 10 | N | N | 1.1101 | 39.4971 | 12428.214
[7 empty] | 9680 | 12148 | 1446039 | 2016-12-29 16:30 | 2016-12-29 19:45 | 195 | 11kV | 91966 | 1555 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 160050 A & C phase Sensitive Earth Fault; Earth Fault; Overcurrent 11kV wire down pole KT-70089.dq Excluded OMS 1446039 | December | 2016 | 2017Q2 | 2017 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2016-12-29 | N | 59.1421 | N | 10 | N | N | 1.1101 | 39.4971 | 67206.0403
[7 empty] | 9128 | 5710 | 1446072 | 2016-12-29 18:20 | 2016-12-29 21:20 | 180 | 11kV | 82160 | 869 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 160052 2 fault operation A & B phase Overcurrent Branch on private OHM beyond 42786 Sw 42786 tripped EF 1820hrs Sw 82127 tripped A to B OC 1820hrs Damage from previous MVA repaired at HV-90076 Excluded OMS 1446106 | December | 2016 | 2017Q2 | 2017 | 239:82127 | 270:83583 | ZN00270/083583 | LAKE MACQUARIE | OH | Veg | 2016-12-29 | N | 94.5455 | N | 10 | N | N | 1.1101 | 39.4971 | 60040.1047
[7 empty] | 9497 | 9902 | 1446093 | 2016-12-29 19:08 | 2016-12-29 21:20 | 132 | 11kV | 130974 | 1048 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn2635 Epping Pnl.52 tripped, relcosed and tripped on: O/C & E/F, reclose, lockout Abnormal: LB790 was Open and Defective with S8770 (Sw/B) Closed UG cable fault from Pnl.52 to S48155 York Dorset Note: EFI at S48155 did not operate. | December | 2016 | 2017Q2 | 2017 | ZN2635:PA52 | ZN2635:PA52 | ZN02635/000052 | HORNSBY | UG | Not Veg | 2016-12-29 | N | 124.9752 | N | 10 | N | N | 1.1101 | 39.4971 | 95711.9361
[7 empty] | 8991 | 3902 | 1446061 | 2016-12-29 17:30 | 2016-12-29 21:25 | 235 | 11kV | 86483 | 832 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn12690 Berkeley Vale - Pnl.7 tripped on: Earth Fault, B Phase O/C and EFI Abnormal: LB62464 Closed with REC45055 Open for DAROS #395191. Lineworkers called in to removed AP earths and make ready for service. Has been ready since 13/12/16 per DOP. UG cable fault from Pnl.17 to S14864 (Sw/A) to S14805 (Sw/A) to S14935 (Sw/B) tee PT14407 See 1446177 1446179 | December | 2016 | 2017Q2 | 2017 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | UG | Not Veg | 2016-12-29 | N | 103.9459 | N | 10 | N | N | 1.1101 | 39.4971 | 63199.2256
[7 empty] | 9093 | 5291 | 1446096 | 2016-12-29 19:16 | 2016-12-29 22:55 | 219 | 11kV | 2193 | 29 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 160055 Blown tapping above dolf at sub 3910 isolated at 22950 for repairs Excluded OMS 1446096 | December | 2016 | 2017Q2 | 2017 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2016-12-29 | N | 75.6207 | N | 10 | N | N | 1.1101 | 39.4971 | 1602.5797
[7 empty] | 9590 | 11148 | 1446132 | 2016-12-30 02:40 | 2016-12-30 03:55 | 75 | 11kV | 92160 | 1358 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | REC41397 Karalta Rd tripped & locked out on: Earth fault (ex Pnl.21 Avoca) Field EFIs: S18017, S18038 UG cable fault from S14617 (Sw/B) to S18038 (Sw/A) to S18194 See 1446172 1446173 | December | 2016 | 2017Q2 | 2017 | ZN12570:PA21 | ZN12580:PA2 | ZN12580/000002 | CENTRAL COAST | UG | Not Veg | 2016-12-30 | N | 67.8645 | N | 9 | N | N | 1.1101 | 39.4971 | 67347.8097
[7 empty] | 9335 | 7870 | 1446139 | 2016-12-30 05:46 | 2016-12-30 07:35 | 109 | 11kV | 186389 | 1851 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn2466 Flemington - Pnl.30 tripped on: B Pahse Overcurrent, Earth Fault, EFI and Fault Check. Field EFIs: S4464, S61613, S3488, S47196 UG cable fault form S47196 (Sw/B) to S2080 (Sw/A) See 1446954 1446955 | December | 2016 | 2017Q2 | 2017 | ZN2466:PA30 | ZN36000:PA6 | ZN36000/000006 | STRATHFIELD | UG | Not Veg | 2016-12-30 | N | 100.6964 | N | 9 | N | N | 1.1101 | 39.4971 | 136207.5837
[7 empty] | 10184 | 18269 | 1446136 | 2016-12-30 05:40 | 2016-12-30 08:08 | 147.55 | 11kV | 14017.25 | 95 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 160056 2 Fault operations Overcurrent, no cause found NOT storm conditions Recorded at U to W 390 amps overcurrent Feeder patrolled, no cause found. Operation counter was reading 449 when power restored, this is 7 operations since 10/11/2016 | December | 2016 | 2017Q2 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2016-12-30 | N | 147.55 | N | 9 | N | N | 1.1101 | 39.4971 | 10243.3929
[7 empty] | 10118 | 17467 | 1446250 | 2016-12-30 13:29 | 2016-12-30 15:45 | 136 | 11kV | 544 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Hot >35C | N | LID 160058 Phase A DOLF - 10 AMP replaced fuse carrier and element | December | 2016 | 2017Q2 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2016-12-30 | N | 136 | N | 9 | N | N | 1.1101 | 39.4971 | 397.5392
[7 empty] | 9419 | 9040 | 1446070 | 2016-12-29 17:49 | 2016-12-30 16:05 | 1336 | 11kV | 1336 | 1 | HV | Equipment Failed in Service | Equipment Failure | 3rd Party Asset | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Panel 5 "Arizon Borg" Signals from Zone 1 TX Group Earth and EFI CP65573 Tooheys Motorway Link HVC customer Boral Roofing tripped on earth fault UGOH fault on customers installation See 1446913 exclude 1446070 | December | 2016 | 2017Q2 | 2017 |  |  |  | CENTRAL COAST | Unknown | Not Veg | 2016-12-29 | N | 1336 | N | 10 | N | N | 1.1101 | 39.4971 | 976.3094
[7 empty] | 9699 | 12314 | 1446245 | 2016-12-30 13:08 | 2016-12-30 16:30 | 202 | 11kV | 6812 | 35 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Hot >35C | N | Zn9037 Miranda - Pnl.17 tripped on: Earth fault with EFI Field EFIs: S9081 @ S9081 Westfield Miranda No.5 - 11kV /415V Tx No.2 failed on Differential. Transformer Fault on Tx No.2 See 1446855 1446856 | December | 2016 | 2017Q2 | 2017 | ZN9037:PA17 | ZN9037:PA17 | ZN09037/000017 | SUTHERLAND | UG | Not Veg | 2016-12-30 | N | 194.6286 | N | 9 | N | N | 1.1101 | 39.4971 | 4978.0087
[7 empty] | 9980 | 15677 | 1446300 | 2016-12-30 17:04 | 2016-12-30 17:50 | 46 | 11kV | 46 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 160059 Phase C, Fuse 10 Amp Substation DOLF | December | 2016 | 2017Q2 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2016-12-30 | N | 46 | N | 9 | N | N | 1.1101 | 39.4971 | 33.6154
[7 empty] | 10269 | 19222 | 1446336 | 2016-12-30 20:01 | 2016-12-30 20:45 | 44 | 11kV | 88 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 160062 Single Phase fuse 10 AMP. substation DOLF dead birds found at sub | December | 2016 | 2017Q2 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2016-12-30 | N | 44 | N | 9 | N | N | 1.1101 | 39.4971 | 64.3078
[7 empty] | 9708 | 12390 | 1446342 | 2016-12-30 12:02 | 2016-12-30 22:25 | 623 | 11kV | 40495 | 65 | HV | Staff Other | Utility Process Issue | Fuse | Unplanned | Hot >35C | N | LID 160063 Phase B, 3 Amp DOLF dop found 3.15A fuses installed in all 11kV dolfs, they have now been upgraded to 31.5 | December | 2016 | 2017Q2 | 2017 | 242:81541 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Not Veg | 2016-12-30 | N | 623 | N | 9 | N | N | 1.1101 | 39.4971 | 29592.5516
[7 empty] | 10054 | 16628 | 1446360 | 2016-12-30 23:30 | 2016-12-30 23:50 | 20 | 11kV | 1640 | 82 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 160065 3 phase interupted to de energise arcing surge arrestor. dq Excluded oms 1446348 | December | 2016 | 2017Q2 | 2017 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2016-12-30 | N | 20 | N | 9 | N | N | 1.1101 | 39.4971 | 1198.4636
[7 empty] | 8936 | 3121 | 1446365 | 2016-12-31 00:11 | 2016-12-31 01:25 | 74 | 11kV | 60754 | 821 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | REC 48234 South Creek Toronto tripped & lokced out on Overcurrent Lightning arrestor roadside phase to S16254 blown clear | December | 2016 | 2017Q2 | 2017 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Not Veg | 2016-12-31 | N | 74 | N | 4 | N | N | 1.1101 | 39.4971 | 44397.2313
[7 empty] | 9577 | 10951 | 1446369 | 2016-12-31 00:56 | 2016-12-31 02:49 | 113 | 11kV | 182535 | 1676 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Panel 6 "Doyalson" fdr tripped on A&C phase O/C lockout EFI reclose time delay fault check x2, no field EFI's centres out UG Fault. Front Line feeder See 1446916,8 exclude 1446369 | December | 2016 | 2017Q2 | 2017 | ZN14892:PA6 | ZN14892:PA6 | ZN14892/000006 | CENTRAL COAST | UG | Not Veg | 2016-12-31 | N | 108.9111 | N | 4 | N | N | 1.1101 | 39.4971 | 133391.1941
[7 empty] | 9928 | 15084 | 1446418 | 2016-12-31 11:49 | 2016-12-31 12:50 | 61 | 11kV | 19947 | 327 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | 11kV UGOH bond burnt off on Centre phase on main line from S17057 Telopea Veterans (Sw/B) | December | 2016 | 2017Q2 | 2017 | ZN15006:PA6 | ZN15006:PA6 | ZN15006/000006 | NORTHERN BEACHES | Unknown | Unknown | 2016-12-31 | N | 61 | N | 4 | N | N | 1.1101 | 39.4971 | 14576.6793
[7 empty] | 9311 | 7588 | 1446466 | 2016-12-31 17:56 | 2016-12-31 19:10 | 74 | 11kV | 148 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 160067 Single Phase Fuse 5 AMP, Line DOLF | December | 2016 | 2017Q2 | 2017 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Not Veg | 2016-12-31 | N | 74 | N | 4 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 9507 | 10039 | 1446495 | 2017-01-01 04:54 | 2017-01-01 06:17 | 83 | 11kV | 162680 | 1960 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn129 Hunters Hill Panel 24 "Eltham Pittwater" fdr tripped on C phase timed o/c x2 No field EFI, S Zn129 hunters Hill Panel 24 "Eltham Pittwater" fdr tripped on C Phase timed overcurrent x 2 Abnormal: SwD closed S3469 SwA Open S859 Cause: Cause not ascertained. Feeder Patrolled by DOp. OH Mains to Patrol in daylight See 1446949 exclude 1446495 | January | 2017 | 2017Q3 | 2017 | ZN129:PA24 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Veg | 2017-01-01 | N | 83 | N | 6 | N | N | 1.1101 | 39.4971 | 118881.7458
[7 empty] | 9888 | 14686 | 1446503 | 2017-01-01 07:19 | 2017-01-01 08:50 | 91 | 11kV | 364 | 4 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 170070 Phase B and C fuse size, 16 AMP LINE DOLF Birds across mains at 11kV LV 27387 | January | 2017 | 2017Q3 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2017-01-01 | N | 91 | N | 6 | N | N | 1.1101 | 39.4971 | 266.0005
[7 empty] | 8748 | 634 | 1446508 | 2017-01-01 08:17 | 2017-01-01 09:45 | 88 | 11kV | 352 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170071 Phase A, fuse 10 AMP Electrical Storm at time of event | January | 2017 | 2017Q3 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2017-01-01 | N | 88 | N | 6 | N | N | 1.1101 | 39.4971 | 257.2312
[7 empty] | 9300 | 7443 | 1446516 | 2017-01-01 09:09 | 2017-01-01 10:45 | 96 | 11kV | 96 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170072 Phase C, Fuse 10 AMO no cause found, not storm conditions | January | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2017-01-01 | N | 96 | N | 6 | N | N | 1.1101 | 39.4971 | 70.154
[7 empty] | 10159 | 17895 | 1446529 | 2017-01-01 10:22 | 2017-01-01 11:54 | 92 | 11kV | 25165 | 482 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn1673 Turramurra Panel 19 "Cherry Hastings" fdr opened on C phase IOC with EFI 11kv trip & No.3 Group Earth & Zone Earth Field EFI's S8372 S35802 CP2407 Large branch on UGOH @ PT1809 Billyard Young See 1446956,7,8 exclude 1446529 | January | 2017 | 2017Q3 | 2017 | ZN1673:PA19 | ZN1673:PA19 | ZN01673/000019 | KU-RING-GAI | OH | Veg | 2017-01-01 | N | 52.2095 | N | 6 | N | N | 1.1101 | 39.4971 | 18389.8398
[7 empty] | 10229 | 18847 | 1446627 | 2017-01-01 21:57 | 2017-01-01 23:10 | 73 | 11kV | 292 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 170075 Single Phase Fuse 10 AMP. substation DOLF no cause found | January | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-01-01 | N | 73 | N | 6 | N | N | 1.1101 | 39.4971 | 213.385
[7 empty] | 9227 | 6799 | 1446664 | 2017-01-02 06:56 | 2017-01-02 07:45 | 49 | 11kV | 245 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170080 Phase A Fuse Size 10 AMP substation DOLF electrical storm at time of event | January | 2017 | 2017Q3 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2017-01-02 | N | 49 | N | 2 | N | N | 1.1101 | 39.4971 | 179.0388
[7 empty] | 9817 | 13804 | 1446887 | 2017-01-02 10:53 | 2017-01-02 13:22 | 149 | 11kV | 149 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170084 1 Fault Operatrions No Cause Found, Not Storm Conditions Reported by Powercoal staff Peter Davidson direct to Control Room. Line patrol completed and supply restored. DOP unable to get protection details | January | 2017 | 2017Q3 | 2017 |  |  |  | LAKE MACQUARIE | OH | Veg | 2017-01-02 | N | 149 | N | 2 | N | N | 1.1101 | 39.4971 | 108.8848
[7 empty] | 10363 | 20338 | 1446833 | 2017-01-03 05:25 | 2017-01-03 06:45 | 80 | 11kV | 160 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170085 C Phase DOLF : 10 Amp Excluded OMS 1446833 | January | 2017 | 2017Q3 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2017-01-03 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 9457 | 9462 | 1447176 | 2017-01-03 10:07 | 2017-01-03 11:15 | 68 | 11kV | 68 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 170088 1 fault operation No supply reported direct to control room by mine staff Adam Jones. VCB 3474 tripped when customer starting pump, pump isolated & supply restored. DOP unable to read targets. Also see report 170084. | January | 2017 | 2017Q3 | 2017 |  |  |  | LAKE MACQUARIE | Unknown | Not Veg | 2017-01-03 | N | 68 | N | 3 | N | N | 1.1101 | 39.4971 | 49.6924
[7 empty] | 9853 | 14203 | 1447091 | 2017-01-03 19:32 | 2017-01-03 20:36 | 64 | 11kV | 39680 | 620 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn3154 St Ives - Pnl.13 tripped on: B & C phase timed Overcurrent Tree branch on mains outside 55 Kokoda Ave, Wahroonga | January | 2017 | 2017Q3 | 2017 | ZN3154:PA13 | ZN3154:PA13 | ZN03154/000013 | KU-RING-GAI | OH | Veg | 2017-01-03 | N | 64 | N | 3 | N | N | 1.1101 | 39.4971 | 28996.9736
[7 empty] | 9488 | 9862 | 1447258 | 2017-01-04 14:20 | 2017-01-04 15:10 | 49.6 | 11kV | 2380.8 | 48 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 170099 A phase broken strands at pole DM-30198 | January | 2017 | 2017Q3 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2017-01-04 | N | 49.6 | N | 4 | N | N | 1.1101 | 39.4971 | 1739.8184
[7 empty] | 9130 | 5761 | 1447232 | 2017-01-04 12:02 | 2017-01-04 16:34 | 272 | 11kV | 3808 | 14 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | 04/01/17 14:24 CASS: PT13348 found isolated and danger tagged. No crews seen in area. 04/01/17 14:28 t32381: emegency interruptions to replace defective 11 KV pole See 1447467 exclude 1447232 | January | 2017 | 2017Q3 | 2017 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2017-01-04 | N | 272 | N | 4 | N | N | 1.1101 | 39.4971 | 2782.7741
[7 empty] | 9251 | 7003 | 1447263 | 2017-01-04 14:46 | 2017-01-04 17:03 | 136.85 | 11kV | 13411.3 | 98 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn35370 Galston section of Pa8 "Galston" fdr beyond RE559 "Cobah Rd" tripped and locked out Cause not ascertained. Patrolled no cause obvious | January | 2017 | 2017Q3 | 2017 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2017-01-04 | N | 136.85 | N | 4 | N | N | 1.1101 | 39.4971 | 9800.5825
[7 empty] | 10051 | 16574 | 1447291 | 2017-01-04 16:42 | 2017-01-04 17:33 | 51 | 11kV | 16371 | 321 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170100 3 fault operations 3 phase Overcurrent BRANCH ON MAINS AT POLE GW-50250. 3 PHASE O/CURRENT AT SW 13793. PLEASE ARRANGE THERMO CAMERA FOR 11KV TAPPINGS AT POLE GW-60009.(SEE OMS 1447293) | January | 2017 | 2017Q3 | 2017 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2017-01-04 | N | 51 | N | 4 | N | N | 1.1101 | 39.4971 | 11963.4439
[7 empty] | 10345 | 20203 | 1447484 | 2017-01-05 12:11 | 2017-01-05 12:29 | 18 | 11kV | 17330 | 1290 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | Ex Pnl.16 at Miranda Zone - S9436 View Wandella (Sw/B) was opened by DOp for safety due to AB35860 damaged and carrying all load through flicker blades. Abnormal: LB35096 CLOSED with (Sw/A) at S9005 open. See 1448227 | January | 2017 | 2017Q3 | 2017 | ZN9037:PA10 | ZN9037:PA10 | ZN09037/000010 | SUTHERLAND | OH | Not Veg | 2017-01-05 | N | 13.4341 | N | 3 | N | N | 1.1101 | 39.4971 | 12664.2529
[7 empty] | 9433 | 9232 | 1447440 | 2017-01-05 11:40 | 2017-01-05 16:15 | 275 | 11kV | 825 | 3 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 170110 interrupt to replace crossarm at sub 70853. | January | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-01-05 | N | 275 | N | 3 | N | N | 1.1101 | 39.4971 | 602.8857
[7 empty] | 9026 | 4289 | 1447572 | 2017-01-05 20:14 | 2017-01-06 01:55 | 341 | 11kV | 39014 | 282 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa2 CP41845 North Erina tripped, reclosed and locked out on: Relays: Earth Fault Signals: 11kv trip EFI's: Nil Tree rbanch brought down OH 237 Wattle Tree Rd Holgate See 1447701,3 Exclude 1447572,92,3,608,9 | January | 2017 | 2017Q3 | 2017 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2017-01-05 | N | 138.3475 | N | 3 | N | N | 1.1101 | 39.4971 | 28510.2805
[7 empty] | 8910 | 2827 | 1447628 | 2017-01-06 07:14 | 2017-01-06 09:10 | 116 | 11kV | 812 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170113 C Phase DOLF : 20 Amp Excluded OMS 1447628 | January | 2017 | 2017Q3 | 2017 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2017-01-06 | N | 116 | N | 9 | N | N | 1.1101 | 39.4971 | 593.3857
[7 empty] | 9961 | 15407 | 1447664 | 2017-01-06 10:07 | 2017-01-06 11:50 | 103 | 11kV | 206 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170119 C Phase DOLF : 10 Amp Excluded OMS 1447664 | January | 2017 | 2017Q3 | 2017 |  |  |  |  | OH | Veg | 2017-01-06 | N | 103 | N | 9 | N | N | 1.1101 | 39.4971 | 150.5387
[7 empty] | 9879 | 14519 | 1447655 | 2017-01-06 11:08 | 2017-01-06 11:50 | 42 | 11kV | 26474 | 812 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 170118 A & B phase Sensitive Earth Fault; Line DOLF UGOH Fault AK-61411 L/F 6F902 A+B ph blown Excluded oms 1447685 | January | 2017 | 2017Q3 | 2017 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | Unknown | Unknown | 2017-01-06 | N | 32.6034 | N | 9 | N | N | 1.1101 | 39.4971 | 19346.4183
[7 empty] | 9586 | 11077 | 1447741 | 2017-01-06 13:54 | 2017-01-06 15:12 | 78 | 11kV | 20060 | 410 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170121 1 fault operation A phase Overcurrent Excluded OMS 1447741 | January | 2017 | 2017Q3 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2017-01-06 | N | 48.9268 | N | 9 | N | N | 1.1101 | 39.4971 | 14659.2563
[7 empty] | 8974 | 3686 | 1447710 | 2017-01-06 12:12 | 2017-01-06 15:30 | 198 | 11kV | 89892 | 690 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S720 Hannan Rd - Sw/A tripped on: Overcurrent & EFI Field EFIs: All dow to S720 (Sw/B) UG cable fault from S720 (Sw/A) to S2746 (Sw/A) tee S3068 See 1448224 1448225 | January | 2017 | 2017Q3 | 2017 | ZN2310:PA72 | ZN35800:PA22 | ZN35800/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-01-06 | N | 130.2783 | N | 9 | N | N | 1.1101 | 39.4971 | 65690.4222
[7 empty] | 8975 | 3714 | 1447726 | 2017-01-06 13:06 | 2017-01-06 15:45 | 159 | 11kV | 159 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | No Weather Impact | N | LID 170122 A Phase DOLF : 10 Amp Excluded OMS 1447726 | January | 2017 | 2017Q3 | 2017 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | UG | Not Veg | 2017-01-06 | N | 159 | N | 9 | N | N | 1.1101 | 39.4971 | 116.1925
[7 empty] | 9931 | 15110 | 1447782 | 2017-01-06 17:53 | 2017-01-06 20:45 | 172 | 11kV | 12556 | 73 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Panel 1 trap rd ect AB43847 bond off RE44937 Alan st tripped and reclosed on IOC and OC Abnormal: AB45434 open and defective, AB44606 closed Tree branch on 11kv mains removed See 1448167 excluded 1447782,3,92,807,8 | January | 2017 | 2017Q3 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2017-01-06 | N | 172 | N | 9 | N | N | 1.1101 | 39.4971 | 9175.5545
[7 empty] | 9070 | 5021 | 1447819 | 2017-01-06 23:38 | 2017-01-07 01:13 | 95 | 11kV | 62141 | 753 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 170126 5 fault operations cable faulty at hazemeyer switchgear at sub 22244. Excluded OMS 1447819 | January | 2017 | 2017Q3 | 2017 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | UG | Not Veg | 2017-01-06 | N | 82.5246 | N | 9 | N | N | 1.1101 | 39.4971 | 45410.81
[7 empty] | 10237 | 18919 | 1450948 | 2017-01-06 12:48 | 2017-01-07 02:45 | 837 | 11kV | 255947 | 1853 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | LID 170275 Overcurrent UGOH fault NB-40336 Excluded OMS 1451023, 1451068, 1451069, 1451024, 1451057, 1451135 | January | 2017 | 2017Q3 | 2017 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | Unknown | Unknown | 2017-01-06 | N | 138.1257 | N | 9 | N | N | 1.1101 | 39.4971 | 187038.5184
[7 empty] | 9713 | 12428 | 1447823 | 2017-01-07 02:13 | 2017-01-07 03:26 | 73 | 11kV | 4964 | 68 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 170124 C phase DOLF faulty dolf will not latch Excluded OMS 1447823 | January | 2017 | 2017Q3 | 2017 | 261:81882 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | OH | Not Veg | 2017-01-07 | N | 73 | N | 4 | N | N | 1.1101 | 39.4971 | 3627.5448
[7 empty] | 10280 | 19305 | 1447844 | 2017-01-07 08:53 | 2017-01-07 10:35 | 102 | 11kV | 204 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170128 C Phase DOLF : 10 Amp Excluded OMS 1447844 | January | 2017 | 2017Q3 | 2017 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2017-01-07 | N | 102 | N | 4 | N | N | 1.1101 | 39.4971 | 149.0772
[7 empty] | 9894 | 14749 | 1447950 | 2017-01-07 23:35 | 2017-01-08 00:54 | 79 | 11kV | 31133 | 510 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven 11kv panel 17 "plane tree apple gum etc" fdr tripped, reclosed tripped and locked out on Relays: EF, reclose timer, lockout Signals: Tx2 Group Earth, TX2 EF Check EFI's: S14750 S18241 S18096 S14836 UG Fault between S14836:A and S18155:B See 1448202,4,5 exclude 1447950 | January | 2017 | 2017Q3 | 2017 | ZN14892:PA17 | ZN14892:PA17 | ZN14892/000017 | CENTRAL COAST | UG | Not Veg | 2017-01-07 | N | 61.0451 | N | 4 | N | N | 1.1101 | 39.4971 | 22751.0781
[7 empty] | 9828 | 13910 | 1447940 | 2017-01-07 22:25 | 2017-01-08 02:28 | 243 | 11kV | 71345 | 821 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn15006 Deewhy sectino of Pa12L "South Creek Rd Penrith" IR48234 South Creek Toronto tripped and reclosed Bond burnt off See 1448184,5,7 exclude 1447940,1,2,3,4,5,6 | January | 2017 | 2017Q3 | 2017 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Not Veg | 2017-01-07 | N | 86.9001 | N | 4 | N | N | 1.1101 | 39.4971 | 52136.8217
[7 empty] | 10201 | 18584 | 1447968 | 2017-01-08 08:28 | 2017-01-08 09:45 | 77 | 11kV | 72471 | 997 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2635 Epping 11kv panel 44 "Karalee Yarwood" tripped on B phase IOC with earth fault Signals: 11kv trip with efi EFI's: pa44 to S65631 Cable fault between S65631 to S1796 See 1448214,5 exclude 1447968 | January | 2017 | 2017Q3 | 2017 | ZN2635:PA44 | ZN2635:PA44 | ZN02635/000044 | RYDE | UG | Not Veg | 2017-01-08 | N | 72.6891 | N | 2 | N | N | 1.1101 | 39.4971 | 52959.6693
[7 empty] | 8985 | 3832 | 1448032 | 2017-01-08 18:31 | 2017-01-08 19:29 | 58 | 11kV | 6936 | 126 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn340 botnay - Pnl.10 tripped on: Earth Fault Field EFIs: S8558 & S3871 UG cable fault between S3871 Lord Booralee (Sw/B) and S7367 Lord Botany No.2 (Sw/A) See 1448095 1448096 | January | 2017 | 2017Q3 | 2017 | ZN340:PA10 | ZN340:PA10 | ZN00340/000010 | BAYSIDE | UG | Not Veg | 2017-01-08 | N | 55.0476 | N | 2 | N | N | 1.1101 | 39.4971 | 5068.6242
[7 empty] | 9319 | 7757 | 1448071 | 2017-01-09 08:11 | 2017-01-09 13:00 | 289 | 11kV | 1734 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Snow / Hail Storm | N | LID 170144 & 170160 A Phase DOLF : 5 amp Excluded OMS 1448071 & 1448097 | January | 2017 | 2017Q3 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-01-09 | N | 289 | N | 5 | N | N | 1.1101 | 39.4971 | 1267.1561
[7 empty] | 8889 | 2639 | 1448177 | 2017-01-09 12:49 | 2017-01-09 14:25 | 96 | 11kV | 288 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170145 A Phase DOLF Fuse dislodged but not blown. Excluded OMS 1448177 | January | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-01-09 | N | 96 | N | 5 | N | N | 1.1101 | 39.4971 | 210.4619
[7 empty] | 9041 | 4592 | 1448246 | 2017-01-09 16:30 | 2017-01-09 17:16 | 46 | 11kV | 46 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170146 A Phase DOLF : 10 Amp | January | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-01-09 | N | 46 | N | 5 | N | N | 1.1101 | 39.4971 | 33.6154
[7 empty] | 10101 | 17257 | 1448251 | 2017-01-09 16:36 | 2017-01-09 17:44 | 68 | 11kV | 109889 | 1776 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clpvelly - Pnl.4 tripped on: Overcurrent and Earth Fault with EFI Field EFIs: S2963 ,S291 UG cable fault from S291 Marcel Av (Sw/A) to S300 Flood St (Sw/A) to S3294 Dans Av to S35473 Greville Fewings (Sw/A) See 1448481 1448482 | January | 2017 | 2017Q3 | 2017 | ZN2602:PA4 | ZN2602:PA31 | ZN02602/000031 | RANDWICK | UG | Not Veg | 2017-01-09 | N | 61.8744 | N | 5 | N | N | 1.1101 | 39.4971 | 80303.64
[7 empty] | 9559 | 10780 | 1448285 | 2017-01-09 17:52 | 2017-01-09 19:44 | 112 | 11kV | 105250 | 2077 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.12L tripped on: SEL HV bond burnt off at AB30799 on footpath phase - Austral Penshurst side See 1448477 1448478 | January | 2017 | 2017Q3 | 2017 | ZN10994:PA12 | ZN10994:PA12 | ZN10994/000012 | GEORGES RIVER | OH | Not Veg | 2017-01-09 | N | 50.674 | N | 5 | N | N | 1.1101 | 39.4971 | 76913.5957
[7 empty] | 9704 | 12327 | 1448358 | 2017-01-10 06:36 | 2017-01-10 08:00 | 84 | 11kV | 64848 | 772 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 170150 2 fault operations A phase Overcurrent, Earth Fault, Sensitive Earth Fault A ph O/C E/F SEF. Cable fault between Sw 76028 and UGOH. Excluded OMS 1448539 | January | 2017 | 2017Q3 | 2017 | 523:33503 | 523:33503 | ZN00523/033503 | SINGLETON | UG | Not Veg | 2017-01-10 | N | 84 | N | 5 | N | N | 1.1101 | 39.4971 | 47389.0057
[7 empty] | 9382 | 8586 | 1448421 | 2017-01-10 09:46 | 2017-01-10 11:10 | 84 | 11kV | 168 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170155 C Phase DOLF : 10 Amp Dead bird found at sub. Excluded OMS 1448421 | January | 2017 | 2017Q3 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2017-01-10 | N | 84 | N | 5 | N | N | 1.1101 | 39.4971 | 122.7694
[7 empty] | 10085 | 17052 | 1448507 | 2017-01-10 14:50 | 2017-01-10 17:43 | 173 | 11kV | 21974 | 145 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170161 2 fault operations A & B phase Earth Fault; Overcurrent Excluded OMS 1448507 | January | 2017 | 2017Q3 | 2017 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2017-01-10 | N | 151.5448 | N | 5 | N | N | 1.1101 | 39.4971 | 16057.9511
[7 empty] | 9943 | 15249 | 1448540 | 2017-01-10 17:14 | 2017-01-10 18:32 | 78 | 11kV | 56983 | 1952 | HV | Vegetation Blow/Fall In | Vegetation | Bond | Unplanned | No Weather Impact | N | At Zn2635 Epping Panel 38 tripped and reclosed on A and C phase O/C Abnormal Switching: AB1629 Closed, AB831 Open, SW/A closed at S48155, Sw/B @ S8770 Closed, AB790 Open, AB767 Open Tree branch fell on HV near UGOH to SW/A @ S46376. HV bond blown clear 1 Sapn below AB768. Supply dumped from LB1308 @ 1824 to safely open AB768 See OMS 1451277 1451279 1451281 1448540 1448548 1448549 1448565 | January | 2017 | 2017Q3 | 2017 | ZN2635:PA38 | ZN2635:PA38 | ZN02635/000038 | HORNSBY | OH | Veg | 2017-01-10 | N | 29.1921 | N | 5 | N | N | 1.1101 | 39.4971 | 41641.4957
[7 empty] | 9353 | 8102 | 1448557 | 2017-01-10 17:47 | 2017-01-10 21:43 | 236 | 11kV | 3540 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Hot >35C | N | LID 170162 A Phase Oil switch fuse : 80 Amp Fuse blown Sw/F 29777 tee to Tx. All 3 replaced. Job not received in control room until 1907. Excluded OMS 1448557 | January | 2017 | 2017Q3 | 2017 | 504:48027 | 522:83121 | ZN00522/083121 | CESSNOCK | UG | Not Veg | 2017-01-10 | N | 236 | N | 5 | N | N | 1.1101 | 39.4971 | 2586.9276
[7 empty] | 9945 | 15276 | 1448615 | 2017-01-11 06:05 | 2017-01-11 09:55 | 230 | 11kV | 920 | 4 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | Ex Zn12630 Peats RIdge panel 1 "Gunderman" fdr PT11924 Oystershel Wise 4.2 16Amp footpath phase HV DOF operated Possum fried at Air Break Switch - RIP Little One See 1450188 exclude 1448615,8 | January | 2017 | 2017Q3 | 2017 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2017-01-11 | N | 230 | N | 17 | N | N | 1.1101 | 39.4971 | 672.3089
[7 empty] | 8779 | 1160 | 1448679 | 2017-01-11 10:24 | 2017-01-11 11:50 | 86 | 11kV | 258 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170170 A & B phase DOLF : 10 Amp Birds Excluded OMS 1448679 | January | 2017 | 2017Q3 | 2017 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2017-01-11 | N | 86 | N | 17 | N | N | 1.1101 | 39.4971 | 188.5388
[7 empty] | 9171 | 6226 | 1448776 | 2017-01-11 14:55 | 2017-01-11 16:07 | 72 | 11kV | 13736 | 199 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn35335 Royal North Hospital 11kV Panel 16 tripped on Relays: Earth Fault, C phase Timed O/C with 11kV UG fault from S5183 to S35236 to S6720 See OMS 1450458 1450461 1450462 1448776 | January | 2017 | 2017Q3 | 2017 | ZN35335:PA16 | ZN35335:PA16 | ZN35335/000016 | WILLOUGHBY | UG | Not Veg | 2017-01-11 | N | 69.0251 | N | 17 | N | N | 1.1101 | 39.4971 | 10037.8637
[7 empty] | 9712 | 12407 | 1448793 | 2017-01-11 15:09 | 2017-01-11 16:40 | 91 | 11kV | 182 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170181 C Phase DOLF : 10 Amp Excluded OMS 1448793 | January | 2017 | 2017Q3 | 2017 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2017-01-11 | N | 91 | N | 17 | N | N | 1.1101 | 39.4971 | 133.0002
[7 empty] | 10021 | 16270 | 1448799 | 2017-01-11 15:14 | 2017-01-11 17:07 | 113 | 11kV | 143623 | 1271 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn195 Pymble Panel 11 tripped, reclosed tripped and locked out on Relays: A phase IOC and Timed O/C, Lockout and Tinming Relay, EFI and Fault Check Cause: Suspect UG fault from Zn195 Pymble Pannel 11 to S4425 Orana Mona Vale To LB243 See OMS 1448799 1448864 | January | 2017 | 2017Q3 | 2017 | ZN195:PA11 | ZN195:PA11 | ZN00195/000011 | KU-RING-GAI | UG | Not Veg | 2017-01-11 | N | 113 | N | 17 | N | N | 1.1101 | 39.4971 | 104955.4522
[7 empty] | 9968 | 15487 | 1448810 | 2017-01-11 15:43 | 2017-01-11 17:07 | 84 | 11kV | 153391 | 1893 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn187 Crows Nest Panel 30 tripped on Relays: C phase IOC, EFI, Earth Fault, Fault Check, No1 TX Fault Check Cause: UG fault from S5440 to S3383 See OMS 1450398 1450399 1448810 | January | 2017 | 2017Q3 | 2017 | ZN187:PA30 | ZN187:PA30 | ZN00187/000030 | WILLOUGHBY | UG | Not Veg | 2017-01-11 | N | 81.0306 | N | 17 | N | N | 1.1101 | 39.4971 | 112093.6185
[7 empty] | 10357 | 20294 | 1448757 | 2017-01-11 14:16 | 2017-01-11 18:10 | 234 | 11kV | 2106 | 9 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | Ex Zn15002 Narrabeen section of Pa2 "Rickard Anna" PT16267 Dendrobium Cr HVDO Open and insulator broken Insulator failed. supply restored via LV// See 1450441 exclude 1448757 | January | 2017 | 2017Q3 | 2017 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Not Veg | 2017-01-11 | N | 234 | N | 17 | N | N | 1.1101 | 39.4971 | 1539.0027
[7 empty] | 10042 | 16501 | 1448940 | 2017-01-11 18:02 | 2017-01-11 18:33 | 31 | 11kV | 7316 | 236 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | At Zn35500 Top Ryde 11kV no32 feeder tripped reclosed tripped and lockedout on Relays: A and C phase IOC, Timing and Lockout relay Signals: 11kV trip Field EFI's Nil Cause: Tree branch on OH mains See OMS1450193 1450194 | January | 2017 | 2017Q3 | 2017 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Veg | 2017-01-11 | N | 31 | N | 17 | N | N | 1.1101 | 39.4971 | 5346.317
[7 empty] | 9233 | 6864 | 1448938 | 2017-01-11 17:59 | 2017-01-11 19:36 | 97 | 11kV | 121938 | 1860 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 170175 A Phase Overcurrent burnt off tapping to links 19255 section isolated for repair. Pole fire at pole Gw60028 caused by burnt tapping. Grass fire extinguished by Fire Brigade Excluded oms 1448938 | January | 2017 | 2017Q3 | 2017 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2017-01-11 | N | 65.5581 | N | 17 | N | N | 1.1101 | 39.4971 | 89108.6938
[7 empty] | 9273 | 7216 | 1448945 | 2017-01-11 18:08 | 2017-01-11 19:38 | 90 | 11kV | 73890 | 821 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn15006 Dee Why West section of Pa12L "South Creek rd Penrith" RE48234 South Creek Toronto tripped, reclosed, tripped and locked out ABNORMAL: AB22172 open, LB23321 closed Cause: Tree/Branch on Oh Mains. Large tree branch on 11kv mains See 1448945 exclude 1448991 | January | 2017 | 2017Q3 | 2017 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Veg | 2017-01-11 | N | 90 | N | 17 | N | N | 1.1101 | 39.4971 | 53996.6326
[7 empty] | 9762 | 13194 | 1448817 | 2017-01-11 15:54 | 2017-01-11 19:47 | 233 | 11kV | 309905 | 1588 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12580 Erina 11kV VCB Panel 10 fdr tripped on Relays: A, C inst, TImmed EFI EFI's: S13682 S12866 S14189 S18183 Signals: 11kv trip Abnormal: S14719:A closed, S14719:B opened 11kv UG Faultbetween S18183:B to S14225:A See 1450195,6 exclude 1448817,20,9,41,9 | January | 2017 | 2017Q3 | 2017 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | UG | Not Veg | 2017-01-11 | N | 195.1543 | N | 17 | N | N | 1.1101 | 39.4971 | 226469.4333
[7 empty] | 10337 | 20117 | 1448886 | 2017-01-11 17:28 | 2017-01-11 19:55 | 146.8167 | 11kV | 4404.5 | 30 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 170177 A & B phase DOLF : 16 Amp Customer saw tree branch come into contact with 11kV OHM and cleared | January | 2017 | 2017Q3 | 2017 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2017-01-11 | N | 146.8167 | N | 17 | N | N | 1.1101 | 39.4971 | 3218.6787
[7 empty] | 9044 | 4643 | 1448805 | 2017-01-11 15:25 | 2017-01-11 20:14 | 289 | 11kV | 837913 | 3685 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn35800 Bankstown - Pnl.15 tripped on: Overcurrent and Earth Fault, Lockout relay was still up from earlier trip & reclose, hence no reclose Abnormal: S8701 (Sw/B) Closed with S6417 (Sw/A) open - due to UG cable fault 11kV OH feeder low above LB 893 (part of front line section of Pnl.15L) See 1449268 SE: 1449271 1449269 | January | 2017 | 2017Q3 | 2017 | ZN35800:PA15 | ZN2310:PA23 | ZN02310/000023 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-01-11 | N | 227.3848 | N | 17 | N | N | 1.1101 | 39.4971 | 612322.1062
[7 empty] | 10188 | 18340 | 1448973 | 2017-01-11 18:55 | 2017-01-11 20:24 | 89 | 11kV | 169798 | 1910 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Zn15006 Dee Why West Panel 8 "Narraweena" fdr tripped on: Relays: SEL Signals: 11kv trip Other - details provided. LK21603 fell open and badly burned See 1450457,9 exclude 1448973 | January | 2017 | 2017Q3 | 2017 | ZN15006:PA8 | ZN15006:PA8 | ZN15006/000008 | NORTHERN BEACHES | OH | Not Veg | 2017-01-11 | N | 88.8995 | N | 17 | N | N | 1.1101 | 39.4971 | 124083.3702
[7 empty] | 9183 | 6315 | 1448905 | 2017-01-11 17:47 | 2017-01-11 20:30 | 163 | 11kV | 141712 | 879 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Panel 14 S18599" fdr tripped on Relays: 50TAC IOC A+C phase, 51Nm Fault check, EFI EFI's: nil Signals: 11kv UG fault from Zn14892 Chamrhaven Panel 14 to S18599:A. No DNMS indication of Panel 14 tripping at CHarmhaven Zone See 1450220,1 GIS 1448913 exclude 1448905 | January | 2017 | 2017Q3 | 2017 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | UG | Not Veg | 2017-01-11 | N | 161.2196 | N | 17 | N | N | 1.1101 | 39.4971 | 103558.9498
[7 empty] | 8749 | 662 | 1448887 | 2017-01-11 17:30 | 2017-01-11 22:03 | 273 | 11kV | 1092 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 170182 A Phase Live Line Lead burnt off at DOLF Excluded OMS 1448887 | January | 2017 | 2017Q3 | 2017 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2017-01-11 | N | 273 | N | 17 | N | N | 1.1101 | 39.4971 | 798.0014
[7 empty] | 8740 | 402 | 1449068 | 2017-01-12 00:48 | 2017-01-12 07:20 | 392 | 11kV | 15640 | 86 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Hot >35C | N | LID 170185 B Phase Oil Switch fuse : 80 Amp Excluded OMS 1449068 | January | 2017 | 2017Q3 | 2017 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | UG | Not Veg | 2017-01-12 | N | 181.8605 | N | 4 | N | N | 1.1101 | 39.4971 | 11429.2507
[7 empty] | 9475 | 9719 | 1449098 | 2017-01-12 07:44 | 2017-01-12 09:45 | 121 | 11kV | 242 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170187 C Phase DOLF : 10 Amp Excluded OMS 1449098 | January | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-01-12 | N | 121 | N | 4 | N | N | 1.1101 | 39.4971 | 176.8465
[7 empty] | 9756 | 13146 | 1449078 | 2017-01-12 06:32 | 2017-01-12 10:00 | 208 | 11kV | 416 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170188 C Phase DOLF : 10 Amp Excluded OMS 1449078 | January | 2017 | 2017Q3 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-01-12 | N | 208 | N | 4 | N | N | 1.1101 | 39.4971 | 304.0005
[7 empty] | 9538 | 10431 | 1448935 | 2017-01-11 17:54 | 2017-01-12 15:05 | 1271 | 11kV | 208065 | 1815 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn12650 West Gosford 11kv VCB Panel 13 "Hanlan St" fdr tripped on Relays: EFI, Timmer, Lockout, Tx13 EF Check EFI's: Nil Signals: 11kV trip, B Battery trip alarm Cause: 11kV UGOH fault adjacent S14116 Manns Dignity Sw/A side See 1450407,8 exclude 1448935,66,9003,50406 | January | 2017 | 2017Q3 | 2017 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | Unknown | Unknown | 2017-01-11 | N | 114.6364 | N | 17 | N | N | 1.1101 | 39.4971 | 152047.7651
[7 empty] | 9112 | 5497 | 1449485 | 2017-01-12 15:37 | 2017-01-12 15:47 | 10 | 11kV | 21141 | 2255 | HV | Staff Other | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn10999 Kogarah Pnl.39 tripped on SEL Zn10999 Kogarah Pnl.16 tripped on SEL DOp restoring switching across panels 16 & 39 for D/R 396140 after live line work. SEL no made non-auto See 1449485 1449486 | January | 2017 | 2017Q3 | 2017 | ZN10999:PA16 | ZN10999:PA16 | ZN10999/000016 | GEORGES RIVER | Unknown | Not Veg | 2017-01-12 | N | 9.3752 | N | 4 | N | N | 1.1101 | 39.4971 | 15449.2192
[7 empty] | 9958 | 15372 | 1449539 | 2017-01-13 12:38 | 2017-01-13 13:26 | 48 | 11kV | 15600 | 325 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | Ex Zn15014 Mona Vale section of Pa14 "Jubilee Daydream, Walana Mona" fdr Re22381 Lane Cove Walter tripped, reclosed, tripped and locked out on IOC and OC Cause not ascertained | January | 2017 | 2017Q3 | 2017 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2017-01-13 | N | 48 | N | 9 | N | N | 1.1101 | 39.4971 | 11400.0199
[7 empty] | 9771 | 13299 | 1449541 | 2017-01-13 13:20 | 2017-01-13 14:11 | 51 | 11kV | 89913 | 1763 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn12570 Avoca Panel 24 "Woodfield Waldron" fdr tripped and reclosed and tripped on Signals: 11kV trip Relays: B & C phase overcurrent, Lockout EFI's: Cause: Tree branch on 11kv OH mains outside 44 Segura st. DOp reports no apparent damage See 1449541 exclude 1449542,3,5,7,55,6 | January | 2017 | 2017Q3 | 2017 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2017-01-13 | N | 51 | N | 9 | N | N | 1.1101 | 39.4971 | 65705.7684
[7 empty] | 8879 | 2498 | 1449568 | 2017-01-13 14:24 | 2017-01-13 16:00 | 96 | 11kV | 37972 | 428 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn1285 Greenacre Park - Pnl.35 tripped to S2420 (Sw/A) on: Translay, I/T receive and Fault Check @ S2420 bankstown Swaure No.1 - Sw/A tripped on: Translay and I/T Send UG cable fault from Pnl.35 to S4315 Heath St (Sw/A) | January | 2017 | 2017Q3 | 2017 | ZN1285:PA35 | ZN1285:PA35 | ZN01285/000035 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-01-13 | N | 88.7196 | N | 9 | N | N | 1.1101 | 39.4971 | 27748.8176
[7 empty] | 9754 | 13129 | 1449588 | 2017-01-13 15:13 | 2017-01-13 17:16 | 123 | 11kV | 138345 | 1377 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Hot >35C | N | Zn36300 Balgowlah North Panel 19 "Hayes Condamine" fdr tripped, reclosed, tripped and locked out on A/C phase IOC, Reclose Lockout, SEL, EFI EFI's: S16827 S16064 S49927 S16928 S16987 Cross Arm failure at Eileen st Balgowlah See 1450505,6,7 exclude 1449588 | January | 2017 | 2017Q3 | 2017 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2017-01-13 | N | 100.4684 | N | 9 | N | N | 1.1101 | 39.4971 | 101098.4455
[7 empty] | 8742 | 430 | 1449614 | 2017-01-13 16:01 | 2017-01-13 18:25 | 144.3833 | 11kV | 1732.6 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 170207 Single phase DOLF : 32 Amp | January | 2017 | 2017Q3 | 2017 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2017-01-13 | N | 144.3833 | N | 9 | N | N | 1.1101 | 39.4971 | 1266.133
[7 empty] | 10186 | 18321 | 1449663 | 2017-01-13 18:10 | 2017-01-13 18:52 | 42 | 11kV | 21966 | 523 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn36300 Balgowlah Zn section of Panel 19 "Hayes Condamine" fdr footpath bond on UGOH to Balgowlah Pitt - S16928 failed Abnormal: S16916 Sw/B Baringa Koobilya closed with LB20880 open, LB49832 open with PT15227 Woolgoolga Eileen in LV// Cause: Bond on UGOH to Balgowlah Pitt S16928 failed. See 1450520 exclude 1449663 | January | 2017 | 2017Q3 | 2017 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2017-01-13 | N | 42 | N | 9 | N | N | 1.1101 | 39.4971 | 16052.1049
[7 empty] | 10249 | 19021 | 1449691 | 2017-01-13 19:19 | 2017-01-13 21:40 | 141 | 11kV | 33558 | 238 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170216 B Phase DOLF : 40 Amp 240V, loads: Aph 460A, LH 167A, RH 280A Bph 435A, LH 220A, RH 208A Cph 260A, LH 67A, RH 208A Excluded OMS 1449691 | January | 2017 | 2017Q3 | 2017 | 203:8084 | 204:82689 | ZN00204/082689 | NEWCASTLE | OH | Veg | 2017-01-13 | N | 141 | N | 9 | N | N | 1.1101 | 39.4971 | 24523.1966
[7 empty] | 9795 | 13573 | 1449652 | 2017-01-13 17:38 | 2017-01-13 22:10 | 272 | 11kV | 1088 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170215 B Phase DOLF : 10 Amp Excluded OMS 1449652 | January | 2017 | 2017Q3 | 2017 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Veg | 2017-01-13 | N | 272 | N | 9 | N | N | 1.1101 | 39.4971 | 795.0783
[7 empty] | 9377 | 8512 | 1449760 | 2017-01-14 01:11 | 2017-01-14 03:30 | 139 | 11kV | 127497 | 1072 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills panel 6 tripped, reclosed tripped and locked out on Earth Fault, A phase timing, Lockout and EFI Signals: TX1 Group earth, CB 6 Open, CB 6 Closed, CB 6 open Cause: Suspect UGOGH fault from S61072 to Ab453 tee PT1048 See OMS 1451013 1451017 1451019 1449760 | January | 2017 | 2017Q3 | 2017 | ZN965:PA6 | ZN965:PA6 | ZN00965/000006 | HORNSBY | Unknown | Unknown | 2017-01-14 | N | 118.9338 | N | 2 | N | N | 1.1101 | 39.4971 | 93171.0471
[7 empty] | 9471 | 9668 | 1449736 | 2017-01-13 20:26 | 2017-01-14 09:15 | 769 | 11kV | 4614 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170220 B Phase DOLF : 10 Amp Excluded OMS 1449720, 1449736, 1449738 | January | 2017 | 2017Q3 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2017-01-13 | N | 769 | N | 9 | N | N | 1.1101 | 39.4971 | 3371.7751
[7 empty] | 9063 | 4873 | 1449833 | 2017-01-14 14:36 | 2017-01-14 17:00 | 144 | 11kV | 4846 | 39 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa12 RE46228 Ravensdale tripped and locked out on B & C phase overcurrent Cause nto ascertained. DOps patrolled See 1450415,6 exclude 1449833 | January | 2017 | 2017Q3 | 2017 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2017-01-14 | N | 124.2564 | N | 2 | N | N | 1.1101 | 39.4971 | 3541.3139
[7 empty] | 9481 | 9789 | 1449910 | 2017-01-15 02:54 | 2017-01-15 05:00 | 126 | 11kV | 3654 | 29 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Panel 11 "Wyoming" PT12464 Chamberlain Pangara 40Amp C phase (footpath) cause not ascertained See 1450422 exclude 1449910 | January | 2017 | 2017Q3 | 2017 | ZN12600:PA11 | ZN12600:PA11 | ZN12600/000011 | CENTRAL COAST | OH | Veg | 2017-01-15 | N | 126 | N | 2 | N | N | 1.1101 | 39.4971 | 2670.2354
[7 empty] | 9720 | 12539 | 1449914 | 2017-01-15 06:39 | 2017-01-15 08:40 | 121 | 11kV | 57427 | 512 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn35370 Galston ex panel 8 Cause: Bond burnt off at LB32 See OMS 1450959 1449915 1449914 | January | 2017 | 2017Q3 | 2017 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2017-01-15 | N | 112.1621 | N | 2 | N | N | 1.1101 | 39.4971 | 41965.9578
[7 empty] | 10262 | 19112 | 1449994 | 2017-01-16 01:06 | 2017-01-16 03:44 | 158 | 11kV | 513026 | 3247 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn36300 Balgowlah Nth Panel 11R S16980" fdr tripped on Relays: OC, EF, 1.3.1 EFI, 1.3.2 Fault check EFI's: Nil Signals: 11kv trip Abnormal: AB22777 Closed, S16928 Sw/B Opened, LB49832 Opened Cause: DOp aptrolled nothing found. See 1450522 exclude 1449994,6,7 | January | 2017 | 2017Q3 | 2017 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | OH | Veg | 2017-01-16 | N | 158 | N | 8 | N | N | 1.1101 | 39.4971 | 374904.2691
[7 empty] | 9651 | 11783 | 1450038 | 2017-01-16 08:19 | 2017-01-16 09:10 | 51 | 11kV | 5624 | 114 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12650 West Gosford 11kv Panel 5 tripped Relays: Earth Fault, EFI Signals: 11kV CB5 Open, 11kv trip, TX11 Earth Fault Check EFI's: Nil 11kV frontline feeder fault from Zn12650 Panel 5 to S18166 Sw/A tee S18231 See 1450430,1 exclude 1450038 | January | 2017 | 2017Q3 | 2017 | ZN12650:PA5 | ZN12650:PA5 | ZN12650/000005 | CENTRAL COAST | UG | Not Veg | 2017-01-16 | N | 49.3333 | N | 8 | N | N | 1.1101 | 39.4971 | 4109.8533
[7 empty] | 8954 | 3437 | 1450061 | 2017-01-16 09:30 | 2017-01-16 10:40 | 70 | 11kV | 70 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170228 B Phase DOLF : 10 Amp Excluded OMS 1450061 | January | 2017 | 2017Q3 | 2017 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2017-01-16 | N | 70 | N | 8 | N | N | 1.1101 | 39.4971 | 51.1539
[7 empty] | 8736 | 281 | 1450152 | 2017-01-16 13:40 | 2017-01-16 14:42 | 62 | 11kV | 186 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170230 C Phase DOLF : 10 Amp Bird feathers found at sub. Excluded OMS No. 1450152 | January | 2017 | 2017Q3 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2017-01-16 | N | 62 | N | 8 | N | N | 1.1101 | 39.4971 | 135.9233
[7 empty] | 8979 | 3749 | 1450205 | 2017-01-16 15:51 | 2017-01-16 17:14 | 83 | 11kV | 4297 | 69 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S5868 Gore Hill Panel 24 tripped on IOC/ Earth Fault, Fault Check and EFI Cause: At S5868 Gore Hill Panel 24 to S36102 tripped Cause: 1451349 1450205 | January | 2017 | 2017Q3 | 2017 | ZN5868:PA24 | ZN5868:PA24 | ZN05868/000024 | WILLOUGHBY | UG | Not Veg | 2017-01-16 | N | 62.2754 | N | 8 | N | N | 1.1101 | 39.4971 | 3140.1209
[7 empty] | 8833 | 1806 | 1450191 | 2017-01-16 15:09 | 2017-01-16 17:32 | 143 | 11kV | 64207 | 449 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Pnl.9 @ Bass Hill Zone - 11kV Bond off between S8289 and LB2212 | January | 2017 | 2017Q3 | 2017 | ZN1850:PA9 | ZN3472:PA30 | ZN03472/000030 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-01-16 | N | 143 | N | 8 | N | N | 1.1101 | 39.4971 | 46920.5818
[7 empty] | 10120 | 17478 | 1451407 | 2017-01-16 21:21 | 2017-01-16 21:30 | 9 | 11kV | 2367 | 263 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35370 section of Panel 2 from CP3280 tripped on O/C anormal Switching: LB62157 Closed IR50015 Open Cause: Tree branch on OH mains Removed by DOps | January | 2017 | 2017Q3 | 2017 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2017-01-16 | N | 9 | N | 8 | N | N | 1.1101 | 39.4971 | 1729.7338
[7 empty] | 10151 | 17807 | 1450310 | 2017-01-17 01:28 | 2017-01-17 03:07 | 99 | 11kV | 87074 | 1214 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale 11kV Panel 19R tripped on A & B phase, IOC, EFI Fdr patrolled by DOps. Cause not ascertained See 1451339,41,2 exclude 1450310,1 | January | 2017 | 2017Q3 | 2017 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2017-01-17 | N | 71.7249 | N | 7 | N | N | 1.1101 | 39.4971 | 63631.111
[7 empty] | 9283 | 7255 | 1450314 | 2017-01-17 03:52 | 2017-01-17 07:00 | 188 | 11kV | 75721 | 1242 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At S2635 Epping Panel 57 tripped, reclosed, tripped and locked out on A B and C IOC and EFI Cause: Lightning arrestor tail burnt off 11kV UGOH in Essex st South Pembroke See OMS 1451300 1451301 1451302 1450314 1450317 | January | 2017 | 2017Q3 | 2017 | ZN2635:PA57 | ZN2635:PA57 | ZN02635/000057 | PARRAMATTA | OH | Not Veg | 2017-01-17 | N | 60.967 | N | 7 | N | N | 1.1101 | 39.4971 | 55334.6734
[7 empty] | 9271 | 7196 | 1450318 | 2017-01-17 05:15 | 2017-01-17 07:25 | 130 | 11kV | 390 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170235 A Phase DOLF : 10 Amp Excluded oms 1450318,1450326 | January | 2017 | 2017Q3 | 2017 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Veg | 2017-01-17 | N | 130 | N | 7 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 9426 | 9141 | 1450280 | 2017-01-16 21:09 | 2017-01-17 08:15 | 666 | 11kV | 366967 | 2953 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1068 Lidcombe - Pnl.26 tripped on: Timed & Inst Earth Fault, EFI Field EFIs: S2909, S35347 (No Access) Abnormal: Sw/A closed @ S524 energising 11kV bar only. Load moved to new RMI. UG cable fault from S2909 (Sw/B) and S35347 (Sw/A). No Access to S35347 to prove location of fault. No A/P issued as Haz extention required to Pnl.26. See 1451372 1451373 1451376 Secondary: 1451377 1451378 1451379 1451380 1451381 | January | 2017 | 2017Q3 | 2017 | ZN1068:PA26 | ZN1068:PA26 | ZN01068/000026 | CUMBERLAND | UG | Not Veg | 2017-01-16 | N | 124.2692 | N | 8 | N | N | 1.1101 | 39.4971 | 268168.6599
[7 empty] | 9849 | 14155 | 1450357 | 2017-01-17 08:56 | 2017-01-17 12:45 | 229 | 11kV | 198677 | 1668 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15002 Narrabeen Panel 6 "Nareen Narroy etc" fdr opened and locked out on A and B phase overcurrent and earth fault with lock out and reclose relays. Also EFI down and frame leakage fault check. Signals, 11kv trip EFI's: S16441 S16903 S16839 Cause: Fallen Branch (cut by tree trimmers) onto HV overhead causing overhead to come down. Outside 124 Narrabeen Park Pde Mona Vale. HV into LV See 1451808,9,10 exclude 1450357,63,6,72,413,33 | January | 2017 | 2017Q3 | 2017 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | OH | Not Veg | 2017-01-17 | N | 119.1109 | N | 7 | N | N | 1.1101 | 39.4971 | 145187.2916
[7 empty] | 9529 | 10358 | 1450568 | 2017-01-17 15:41 | 2017-01-17 17:45 | 124 | 11kV | 405163 | 3624 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn35800 Bankstown - Pnl.15L tripped, reclosed & locked out on: C phase timed O/C, timing, lockout and EFI Abnormal: S8701 (Sw/B) closed with S6417 9Sw/A) open Overload - C phase overloaded but B phase did not alarm. See 1451390 1451391 | January | 2017 | 2017Q3 | 2017 | ZN35800:PA15 | ZN2310:PA23 | ZN02310/000023 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2017-01-17 | N | 111.7999 | N | 7 | N | N | 1.1101 | 39.4971 | 296081.1701
[7 empty] | 9615 | 11416 | 1450569 | 2017-01-17 17:01 | 2017-01-17 19:05 | 124 | 11kV | 8184 | 66 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170251 C Phase DOLF : 20 Amp Tree branch brought down OHM (no wind) Crossland St x Carolyn St, Adamstown Heights. 2 LVFs blown plus C phase DOLF Excluded OMS 1450595 | January | 2017 | 2017Q3 | 2017 | 205:12213 | 205:12213 | ZN00205/012213 | NEWCASTLE | OH | Veg | 2017-01-17 | N | 124 | N | 7 | N | N | 1.1101 | 39.4971 | 5980.6258
[7 empty] | 9306 | 7512 | 1450779 | 2017-01-18 07:49 | 2017-01-18 09:30 | 100.5167 | 11kV | 7337.7167 | 73 | HV | Animal Bird | Animal | DC-PT Transformer | Unplanned | Hot >35C | N | LID 170261 C Phase DOLF : 31 Amp possibly birds caused fault Replace Blown Dolf | January | 2017 | 2017Q3 | 2017 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Not Veg | 2017-01-18 | N | 100.5167 | N | 14 | N | N | 1.1101 | 39.4971 | 5362.1869
[7 empty] | 9937 | 15202 | 1450938 | 2017-01-18 12:37 | 2017-01-18 13:35 | 57.9167 | 11kV | 57.9167 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Fuse | Unplanned | Hot >35C | N | Replaced Blown Dolf CC1: 11-"Despatch to re-issue" | January | 2017 | 2017Q3 | 2017 |  |  |  | MUSWELLBROOK | OH | Not Veg | 2017-01-18 | N | 57.9167 | N | 14 | N | N | 1.1101 | 39.4971 | 42.3238
[7 empty] | 8845 | 1932 | 1450930 | 2017-01-18 12:29 | 2017-01-18 14:22 | 113 | 11kV | 29633 | 275 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington - Pnl.7 tripped on: Earth Fault, Overcurrent, EFI Front line UG cable fault See 1451409 1451410 | January | 2017 | 2017Q3 | 2017 | ZN2466:PA7 | ZN2466:PA7 | ZN02466/000007 | PARRAMATTA | UG | Not Veg | 2017-01-18 | N | 107.7564 | N | 14 | N | N | 1.1101 | 39.4971 | 21654.9224
[7 empty] | 9492 | 9867 | 1450944 | 2017-01-18 12:43 | 2017-01-18 14:24 | 101 | 11kV | 202 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | Live line lead to Sub 42757 broke off in wind. Repaired & replaced HV fuse at DOLF No LID report | January | 2017 | 2017Q3 | 2017 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2017-01-18 | N | 101 | N | 14 | N | N | 1.1101 | 39.4971 | 147.6156
[7 empty] | 9694 | 12265 | 1450648 | 2017-01-17 18:14 | 2017-01-18 14:25 | 1211 | 11kV | 477428 | 1393 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Hot >35C | N | @ZN1850 Bass Hill - 11kv Panel No.10 "Sub 5081 Bellevue Birdwood" feeder tripped Relays: C phase IOC and timed O/C, EFI Signals: 11kv trip, Zn Earth, No.1 Group Earth Field EFI's: Nil Abnormal: Sw/A closed @ S4898 MWS & BD Coleman Park with LB 1932 open (Sefton 2 D/9) Remarks: end box fault. 11kv endbox failed @ S5081 Bellevue Birdwood | January | 2017 | 2017Q3 | 2017 | ZN1850:PA10 | ZN1850:PA40 | ZN01850/000040 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-01-17 | N | 342.7337 | N | 7 | N | N | 1.1101 | 39.4971 | 348890.3007
[7 empty] | 9231 | 6844 | 1450999 | 2017-01-18 14:41 | 2017-01-18 16:45 | 124 | 11kV | 62762 | 683 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Hot >35C | N | LID 170269 3 fault operations 3 phase Overcurrent defective endbox at lemon tree passage bowling club 29731 Excluded oms ## 1450999 | January | 2017 | 2017Q3 | 2017 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | UG | Not Veg | 2017-01-18 | N | 91.8917 | N | 14 | N | N | 1.1101 | 39.4971 | 45864.6184
[7 empty] | 9144 | 5938 | 1451109 | 2017-01-18 17:51 | 2017-01-18 18:34 | 43 | 11kV | 731 | 17 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170274 1 fault operation 3 phase Overcurrent TREES REMOVED FROM MAINS BETWEEN POLES SF-60031 & SF-60032 | January | 2017 | 2017Q3 | 2017 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2017-01-18 | N | 43 | N | 14 | N | N | 1.1101 | 39.4971 | 534.1932
[7 empty] | 9192 | 6375 | 1451115 | 2017-01-18 18:05 | 2017-01-18 22:15 | 250 | 11kV | 1750 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170289 A & B phase DOLF : 20 Amp Excluded OMS 1451115 | January | 2017 | 2017Q3 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-01-18 | N | 250 | N | 14 | N | N | 1.1101 | 39.4971 | 1278.8484
[7 empty] | 8836 | 1855 | 1451163 | 2017-01-18 21:34 | 2017-01-18 22:30 | 56 | 11kV | 8344 | 149 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Hot >35C | N | LID 170279 A Phase DOLF : 31 Amp Replaced Burnt up DOLF & carrier Excluded OMS 1451163 | January | 2017 | 2017Q3 | 2017 | 202:34245 | 202:34245 | ZN00202/034245 | NEWCASTLE | OH | Not Veg | 2017-01-18 | N | 56 | N | 14 | N | N | 1.1101 | 39.4971 | 6097.5491
[7 empty] | 9913 | 14961 | 1451166 | 2017-01-18 21:27 | 2017-01-18 22:34 | 67 | 11kV | 6668 | 139 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7481 Darling Harbour - Pnl.19 tripped on: Earth fault Field EFIs: S6421, S3044, S3092 UG cable fault from S3044 (Sw/B) to S3092 (Sw/B) to S6488 (Sw/D) See 1451287 1451288 | January | 2017 | 2017Q3 | 2017 | ZN7481:PA19 | ZN7481:PA19 | ZN07481/000019 | SYDNEY | UG | Not Veg | 2017-01-18 | N | 47.9712 | N | 14 | N | N | 1.1101 | 39.4971 | 4872.7777
[7 empty] | 9883 | 14568 | 1451116 | 2017-01-18 18:09 | 2017-01-18 23:00 | 291 | 11kV | 26772 | 92 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170276 4 fault operations 3 phase Overcurrent | January | 2017 | 2017Q3 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-01-18 | N | 291 | N | 14 | N | N | 1.1101 | 39.4971 | 19564.188
[7 empty] | 10020 | 16265 | 1451099 | 2017-01-18 16:51 | 2017-01-18 23:11 | 380 | 11kV | 31876 | 847 | HV | Fire (Non Ausgrid) | UNKNOWN | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 170281 1 fault operation Overcurrent sw 80923 50t ac. fire on fdr section isolated for repairs Excluded oms 1451099 | January | 2017 | 2017Q3 | 2017 | 507:80923 | 507:80923 | ZN00507/080923 | CESSNOCK | OH | Not Veg | 2017-01-18 | N | 37.634 | N | 14 | N | N | 1.1101 | 39.4971 | 23294.0406
[7 empty] | 9525 | 10273 | 1451117 | 2017-01-18 18:12 | 2017-01-18 23:20 | 307.5667 | 11kV | 6151.3333 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LIDv 170287 A & B phase DOLF : 16 Amp | January | 2017 | 2017Q3 | 2017 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2017-01-18 | N | 307.5667 | N | 14 | N | N | 1.1101 | 39.4971 | 4495.213
[7 empty] | 9753 | 13125 | 1451114 | 2017-01-18 17:56 | 2017-01-19 00:05 | 369 | 11kV | 8866 | 110 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 170272 2 fault operations 3 phase Overcurrent mains down beyond pole 9H-90112 twisted mains beyond sub 70173 section isolated for repairs Excluded oms 1451114 | January | 2017 | 2017Q3 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2017-01-18 | N | 80.6 | N | 14 | N | N | 1.1101 | 39.4971 | 6479.0113
[7 empty] | 9755 | 13142 | 1451190 | 2017-01-18 23:33 | 2017-01-19 07:50 | 497 | 11kV | 497 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170292 A Phase DOLF : 10 Amp | January | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-01-18 | N | 497 | N | 14 | N | N | 1.1101 | 39.4971 | 363.1929
[7 empty] | 9194 | 6389 | 1451235 | 2017-01-19 08:29 | 2017-01-19 10:24 | 115 | 11kV | 168160 | 1500 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman 11kV Panel 7 CB labelled "Belmont Myahgah" tripped on: Signals: 11kV trip, Tx1 Group Earth, Zone Earth Relays: EFI's: S47018 S2131 S35066 S2414 S1554 S4245 Suspected UG cable fault between S4245 Crux Somerset Sw/A to S1332 Lower Avenue Rd See 1451815,6 exclude 1451235 | January | 2017 | 2017Q3 | 2017 | ZN180:PA7 | ZN180:PA7 | ZN00180/000007 | MOSMAN | UG | Not Veg | 2017-01-19 | N | 112.1067 | N | 6 | N | N | 1.1101 | 39.4971 | 122886.3681
[7 empty] | 8803 | 1512 | 1451304 | 2017-01-19 10:59 | 2017-01-19 13:00 | 121 | 11kV | 281271 | 2991 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | At S4545 Meadowbank Panel 31 tripped on Relays A phase OC and Earth Fault Signals; 11kV trip, TX3 Group Earth, Zone Earth 11kV UGOH below S4549 and Surge arrestors appear burnt See OMS 1452312 1452313 1451304 | January | 2017 | 2017Q3 | 2017 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | Unknown | Unknown | 2017-01-19 | N | 94.0391 | N | 6 | N | N | 1.1101 | 39.4971 | 205544.5507
[7 empty] | 10302 | 19553 | 1451299 | 2017-01-19 12:00 | 2017-01-19 13:30 | 90 | 11kV | 90 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 170302 A Phase DOLF : 10 Amp Lightning Arrestor | January | 2017 | 2017Q3 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2017-01-19 | N | 90 | N | 6 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 9824 | 13872 | 1451228 | 2017-01-19 08:03 | 2017-01-19 13:35 | 332 | 11kV | 1992 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170304 B Phase DOLF : 10 Amp replaced DOLF and rewired suss LV at tx. Excluded oms 1451228 | January | 2017 | 2017Q3 | 2017 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2017-01-19 | N | 332 | N | 6 | N | N | 1.1101 | 39.4971 | 1455.6948
[7 empty] | 9091 | 5274 | 1451237 | 2017-01-19 13:20 | 2017-01-19 14:20 | 60 | 11kV | 180 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 170307 interrupt to repair wire off pin beyond LF 74249 Excluded oms 1451237 | January | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-01-19 | N | 60 | N | 6 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 9509 | 10053 | 1451497 | 2017-01-19 23:40 | 2017-01-20 07:45 | 485 | 11kV | 1455 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170310 A & B Phase DOLF : 20 Amp | January | 2017 | 2017Q3 | 2017 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2017-01-19 | N | 485 | N | 6 | N | N | 1.1101 | 39.4971 | 1063.2711
[7 empty] | 10291 | 19456 | 1451537 | 2017-01-20 08:12 | 2017-01-20 09:00 | 48 | 11kV | 96 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170312 C Phase DOLF : 10 Amp | January | 2017 | 2017Q3 | 2017 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2017-01-20 | N | 48 | N | 11 | N | N | 1.1101 | 39.4971 | 70.154
[7 empty] | 8881 | 2517 | 1453205 | 2017-01-20 14:30 | 2017-01-20 15:10 | 40 | 11kV | 120 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | At S14891 Wyong Panel 12 Yarramolong Feeder from link 44875 Cause: Tree beanch non OH mains | January | 2017 | 2017Q3 | 2017 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2017-01-20 | N | 40 | N | 11 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 10281 | 19306 | 1451719 | 2017-01-20 13:42 | 2017-01-20 17:30 | 228 | 11kV | 456 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | PT12198 Chittaway Old Chit 0.5 10A HDO blown Cause not ascertained See OMS 1452993 1451719 | January | 2017 | 2017Q3 | 2017 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2017-01-20 | N | 228 | N | 11 | N | N | 1.1101 | 39.4971 | 333.2314
[7 empty] | 10271 | 19230 | 1451774 | 2017-01-20 15:29 | 2017-01-20 17:45 | 136 | 11kV | 864 | 9 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 170325 C Phase DOLF : 16 Amp 11Kv Mains on ground near pole 8N-50109 Excluded oms 1451774 | January | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-01-20 | N | 96 | N | 11 | N | N | 1.1101 | 39.4971 | 631.3857
[7 empty] | 8800 | 1491 | 1451832 | 2017-01-20 18:45 | 2017-01-20 20:50 | 125 | 11kV | 375 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 170326 B Phase DOLF : 16 Amp Excluded OMS 1451832 | January | 2017 | 2017Q3 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-01-20 | N | 125 | N | 11 | N | N | 1.1101 | 39.4971 | 274.0389
[7 empty] | 9506 | 10033 | 1451854 | 2017-01-20 20:12 | 2017-01-20 21:10 | 58 | 11kV | 5162 | 89 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 170327 B Phase DOLF : 40 Amp Replaced DOLF wedge burnt in half, burnt carrier requires replacement ASAP. Excluded OMS 1451854,1451855,1451861 | January | 2017 | 2017Q3 | 2017 | 239:82133 | 239:82133 | ZN00239/082133 | LAKE MACQUARIE | OH | Not Veg | 2017-01-20 | N | 58 | N | 11 | N | N | 1.1101 | 39.4971 | 3772.2373
[7 empty] | 10036 | 16456 | 1451829 | 2017-01-20 18:34 | 2017-01-20 21:30 | 176 | 11kV | 704 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S14144 Wamberal Section of Panel 10 the wamberal Aux- Roadside bond burnt off PT14425 Brooke Entrane 0.4 See OMS 1453006 1451872 1451829 | January | 2017 | 2017Q3 | 2017 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2017-01-20 | N | 176 | N | 11 | N | N | 1.1101 | 39.4971 | 514.4624
[7 empty] | 9404 | 8821 | 1451735 | 2017-01-20 14:09 | 2017-01-20 22:00 | 471 | 11kV | 942 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170328 Single phase DOLF : 10 Amp Replaced 2 x 10 Amp DOLF Excluded OMS 1451735 | January | 2017 | 2017Q3 | 2017 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2017-01-20 | N | 471 | N | 11 | N | N | 1.1101 | 39.4971 | 688.3858
[7 empty] | 9972 | 15571 | 1451919 | 2017-01-21 00:27 | 2017-01-21 01:15 | 48 | 11kV | 528 | 11 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 170332 B Phase DOLF : 10 Amp Fatigued fuse. Excluded OMS 1451919 | January | 2017 | 2017Q3 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2017-01-21 | N | 48 | N | 6 | N | N | 1.1101 | 39.4971 | 385.8468
[7 empty] | 10062 | 16692 | 1451914 | 2017-01-20 23:20 | 2017-01-21 01:35 | 135 | 11kV | 76746 | 1195 | HV | Vegetation Blow/Fall In | Vegetation | Bond | Unplanned | No Weather Impact | N | LID 170331 2 Fault operations Sw 11900 no targets dropped Palm tree grown into 11kV OHM at sub 7179. A & B phase DOLF also blown at sub 7179. Bphase tapping blown top of DOLF assembly, isolated at DOLF and LVF with LV interconnection to restore supply. Repairs requirwed | January | 2017 | 2017Q3 | 2017 | 221:11900 | 221:11900 | ZN00221/011900 | LAKE MACQUARIE | OH | Veg | 2017-01-20 | N | 64.2226 | N | 11 | N | N | 1.1101 | 39.4971 | 56083.7132
[7 empty] | 9012 | 4098 | 1451896 | 2017-01-20 22:19 | 2017-01-21 05:30 | 431 | 11kV | 3017 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 170334 Broken Live Line clamp pole GS-24534. Section isolated & clamp replaced. Note LLC is fitted directly onto tensioned OH mains, requires bail clamp. Excluded OMS 1451896 | January | 2017 | 2017Q3 | 2017 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Not Veg | 2017-01-20 | N | 431 | N | 11 | N | N | 1.1101 | 39.4971 | 2204.7346
[7 empty] | 8848 | 1987 | 1451918 | 2017-01-21 00:12 | 2017-01-21 07:55 | 463 | 11kV | 1389 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170335 A Phase DOLF : 10 Amp Excluded OMS 1451918 | January | 2017 | 2017Q3 | 2017 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2017-01-21 | N | 463 | N | 6 | N | N | 1.1101 | 39.4971 | 1015.0402
[7 empty] | 9620 | 11480 | 1451871 | 2017-01-20 20:58 | 2017-01-21 09:00 | 722 | 11kV | 3610 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | At PT47326 Palmdale Wallaby 0.25 Roadside phase dropout fuse assembly failed. See OMS 1453011 1451938 1451873 1451871 | January | 2017 | 2017Q3 | 2017 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2017-01-20 | N | 722 | N | 11 | N | N | 1.1101 | 39.4971 | 2638.0815
[7 empty] | 9588 | 11107 | 1451987 | 2017-01-21 13:37 | 2017-01-21 17:20 | 223 | 11kV | 668.05 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | At PT63074 Wise Ferry Laven 31.5A fuse road side operated. Roadside fuse failed 31.5 Amp fuse installed. See OMS 1453012 1451987 | January | 2017 | 2017Q3 | 2017 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2017-01-21 | N | 222.6833 | N | 6 | N | N | 1.1101 | 39.4971 | 488.1912
[7 empty] | 9035 | 4488 | 1452020 | 2017-01-21 17:57 | 2017-01-21 18:45 | 48 | 11kV | 144 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170338 C Phase DOLF : 16 Amp Excluded OMS 1452020 | January | 2017 | 2017Q3 | 2017 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2017-01-21 | N | 48 | N | 6 | N | N | 1.1101 | 39.4971 | 105.231
[7 empty] | 10019 | 16262 | 1452013 | 2017-01-21 17:40 | 2017-01-21 20:20 | 160 | 11kV | 56028 | 584 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 170339 A phase Sensitive Earth Fault mains down beyond links 42100 causing Grass Fire at Pole AH31315 Excluded OMS 1452013 | January | 2017 | 2017Q3 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2017-01-21 | N | 95.9384 | N | 6 | N | N | 1.1101 | 39.4971 | 40943.6099
[7 empty] | 9428 | 9190 | 1452008 | 2017-01-21 21:35 | 2017-01-21 22:05 | 30 | 11kV | 420 | 14 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 170340 A Phase Main off pin at pole AI-80198 | January | 2017 | 2017Q3 | 2017 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2017-01-21 | N | 30 | N | 6 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 10338 | 20121 | 1452075 | 2017-01-22 11:04 | 2017-01-22 12:50 | 106 | 11kV | 424 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170343 A Phase DOLF : 10 Amp Excluded OMS 1452075 | January | 2017 | 2017Q3 | 2017 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2017-01-22 | N | 106 | N | 2 | N | N | 1.1101 | 39.4971 | 309.8467
[7 empty] | 8933 | 3097 | 1452126 | 2017-01-22 21:02 | 2017-01-22 23:40 | 158 | 11kV | 632 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 170344 B Phase DOLF : 16 Amp Fuse Fatigue Excluded OMS 1452126 | January | 2017 | 2017Q3 | 2017 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2017-01-22 | N | 158 | N | 2 | N | N | 1.1101 | 39.4971 | 461.847
[7 empty] | 9155 | 6040 | 1452520 | 2017-01-23 08:55 | 2017-01-23 10:15 | 80 | 11kV | 160 | 2 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 170362 replaced pole after base washed away | January | 2017 | 2017Q3 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2017-01-23 | N | 80 | N | 6 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 9438 | 9255 | 1452227 | 2017-01-23 09:42 | 2017-01-23 11:07 | 85 | 11kV | 19295 | 227 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170351 Possum on Transformer at sub 72941 | January | 2017 | 2017Q3 | 2017 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2017-01-23 | N | 85 | N | 6 | N | N | 1.1101 | 39.4971 | 14100.2169
[7 empty] | 9066 | 4962 | 1452240 | 2017-01-23 10:13 | 2017-01-23 11:45 | 91.75 | 11kV | 2018.5 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170352 DOLF : 10 Amp No Fault found Excluded OMS 1452242 CC1: 04-"Non Urgent - refer to OH Mains" | January | 2017 | 2017Q3 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-01-23 | N | 91.75 | N | 6 | N | N | 1.1101 | 39.4971 | 1475.0603
[7 empty] | 9265 | 7146 | 1452183 | 2017-01-23 08:24 | 2017-01-23 12:45 | 261 | 11kV | 44370 | 170 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S3425 Castle Cove Panel 12 tripped on A and B phase O/C Lockout and Reclose Time Delay 8 Bays of 11kV Down in Lord St See OMS 1452855 1452857 1452857 1452860 1452178 1452180 1452181 1452183 1452187 1452187 | January | 2017 | 2017Q3 | 2017 | ZN1193:PA25 | ZN1193:PA25 | ZN01193/000025 | KU-RING-GAI | OH | Veg | 2017-01-23 | N | 261 | N | 6 | N | N | 1.1101 | 39.4971 | 32424.2873
[7 empty] | 9291 | 7371 | 1452143 | 2017-01-23 08:24 | 2017-01-24 00:34 | 970 | 11kV | 162845 | 1212 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S3425 Castle Cove Panel 12 tripped on A and B phase O/C Lockout and Reclose Time Delay 8 Bays of 11kV Down in Lord St See OMS 1452855 1452857 1452857 1452860 1452178 1452180 1452181 1452183 1452187 1452187 | January | 2017 | 2017Q3 | 2017 | ZN3425:PA12 | ZN3425:PA12 | ZN03425/000012 | KU-RING-GAI | OH | Veg | 2017-01-23 | N | 134.3606 | N | 6 | N | N | 1.1101 | 39.4971 | 119002.3229
[7 empty] | 9706 | 12359 | 1452436 | 2017-01-23 22:56 | 2017-01-24 01:00 | 124 | 11kV | 372 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170358 A Phase DOLF : 10 Amp Excluded OMS 1452436 | January | 2017 | 2017Q3 | 2017 | 526:34640 | 526:34640 | ZN00526/034640 | SINGLETON | OH | Veg | 2017-01-23 | N | 124 | N | 6 | N | N | 1.1101 | 39.4971 | 271.8466
[7 empty] | 9866 | 14371 | 1452438 | 2017-01-24 01:27 | 2017-01-24 06:00 | 272.85 | 11kV | 16371 | 60 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 170359 Isolate to repaire broken 11kV tapping near ABS 40567. | January | 2017 | 2017Q3 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2017-01-24 | N | 272.85 | N | 8 | N | N | 1.1101 | 39.4971 | 11963.4439
[7 empty] | 9524 | 10266 | 1452575 | 2017-01-24 13:09 | 2017-01-24 14:00 | 51 | 11kV | 77265 | 1515 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | At Zn12570 Avoca Panel 13 tripped reclosed tripped and locked out on Cause: Tree branch on OH mains 21 Hillside Rd Avoca | January | 2017 | 2017Q3 | 2017 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2017-01-24 | N | 51 | N | 8 | N | N | 1.1101 | 39.4971 | 56462.9831
[7 empty] | 9383 | 8597 | 1452528 | 2017-01-24 11:29 | 2017-01-24 14:20 | 171 | 11kV | 342 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 170370 Broken LL lead top of DOLF Excluded OMS 1452528 | January | 2017 | 2017Q3 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2017-01-24 | N | 171 | N | 8 | N | N | 1.1101 | 39.4971 | 249.9235
[7 empty] | 9570 | 10885 | 1452704 | 2017-01-24 17:37 | 2017-01-24 19:53 | 136 | 11kV | 36576 | 273 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | Zn1610 Homebush Bay - Pnl.11 tripped on: KCGG140 relay Field EFIs: S1427, S5114, S5115, S7662 UG cable fault from S7662 (Sw/A) to S4287 (Sw/A) to S5050 (Sw/A) See 1453004 1453005 | January | 2017 | 2017Q3 | 2017 | ZN1610:PA11 | ZN36000:PA10 | ZN36000/000010 | STRATHFIELD | UG | Not Veg | 2017-01-24 | N | 133.978 | N | 8 | N | N | 1.1101 | 39.4971 | 26728.662
[7 empty] | 9368 | 8322 | 1452776 | 2017-01-24 20:11 | 2017-01-24 21:24 | 73.3667 | 11kV | 12105.5 | 165 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | ex Zn14144 Wamberal Panel 10L Recloser 465254 Coachwood North tripped, reclosed tripped and locked out on overcurrent Cause: Tree branch on OH mains near PT14507 Arundel Milina see OMS 1452776 1452776 | January | 2017 | 2017Q3 | 2017 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2017-01-24 | N | 73.3667 | N | 8 | N | N | 1.1101 | 39.4971 | 8846.3423
[7 empty] | 10132 | 17578 | 1452735 | 2017-01-24 18:24 | 2017-01-24 22:30 | 246 | 11kV | 19771 | 116 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 170373 1 fault operation Sensitive Earth Fault Tree over OHM near pole GW-30048/48 Excluded oms 1452735/80. | January | 2017 | 2017Q3 | 2017 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2017-01-24 | N | 170.4397 | N | 8 | N | N | 1.1101 | 39.4971 | 14448.0637
[7 empty] | 9200 | 6472 | 1452694 | 2017-01-24 17:22 | 2017-01-25 02:40 | 558 | 11kV | 72465 | 316 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170374 2 fault operations 3 phase Overcurrent TREE OVER MAINS BETWEEN POLES JQ-60339 & JQ-60341.SUSPECTED HIGH into LV. Excluded OMS REPORT NO 1452694 & 1452694. | January | 2017 | 2017Q3 | 2017 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2017-01-24 | N | 229.3196 | N | 8 | N | N | 1.1101 | 39.4971 | 52955.2846
[7 empty] | 9039 | 4536 | 1452773 | 2017-01-24 20:42 | 2017-01-25 04:30 | 468 | 11kV | 282125 | 1992 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Zn15008 Harbord Panel 5 "Queenscliff" fdr tripped, reclosed, tripped and locked out on: Relays: A&C phases IOC, Lockout and timing relays Signals: 11kv trip ABnormal: LB63712 and LB63715 open with S15967 isolated and in LV// Cause: Pole top fire at PT15656 the Drive, due to S15967 Ronald ave 14 was isolated and in LV// at time of failure unable to restore supply after feeder restored due to no capacity to supply load via LV network untill PT15656 repaired, customer had long delay in restoring supply. See 1454771,2,3 exclude 1452782,7,95,809,16,7 | January | 2017 | 2017Q3 | 2017 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | OH | Not Veg | 2017-01-24 | N | 141.629 | N | 8 | N | N | 1.1101 | 39.4971 | 206168.6287
[7 empty] | 10150 | 17805 | 1452952 | 2017-01-25 12:06 | 2017-01-25 12:57 | 51 | 11kV | 306 | 6 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.8 tripped on: Earth Fault with Fault Check UG cable fault. Front line section from Pnl.8 to S48724 and S7906 | January | 2017 | 2017Q3 | 2017 | ZN2568:PA8 | ZN2568:PA8 | ZN02568/000008 | SYDNEY | UG | Not Veg | 2017-01-25 | N | 51 | N | 2 | N | N | 1.1101 | 39.4971 | 223.6158
[7 empty] | 8902 | 2779 | 1452987 | 2017-01-25 14:22 | 2017-01-25 21:25 | 423 | 11kV | 423 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170402 A Phase DOLF : 10 Amp Suspect fatigued fuse Excluded 1452987 | January | 2017 | 2017Q3 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2017-01-25 | N | 423 | N | 2 | N | N | 1.1101 | 39.4971 | 309.1159
[7 empty] | 9394 | 8740 | 1453096 | 2017-01-26 03:06 | 2017-01-26 04:17 | 71 | 11kV | 149967 | 2232 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S2310 Punchbowl Panel 65 "S3106 Sylvester King Georges Etc" fdr tripped on Relays - B phase O/C, EFI Signals - 11kv trip Field EFI's operated down to S2509 Remarks: UG fault. 11kv UG cable fault from S2509 Leyland Marie to S2510 Gillies Taylor | January | 2017 | 2017Q3 | 2017 | ZN2310:PA65 | ZN2310:PA14 | ZN02310/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-01-26 | N | 67.1895 | N | 5 | N | N | 1.1101 | 39.4971 | 109591.4603
[7 empty] | 9125 | 5702 | 1453136 | 2017-01-26 11:39 | 2017-01-26 13:22 | 103 | 11kV | 60580 | 800 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170407 1 fault operation A & B phase Overcurrent Targets: RHS prot 50T A/B. feeder patrolled by DOp. No fault found. Excluded OMS 1453136 | January | 2017 | 2017Q3 | 2017 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Veg | 2017-01-26 | N | 75.725 | N | 5 | N | N | 1.1101 | 39.4971 | 44270.0772
[7 empty] | 9515 | 10180 | 1453145 | 2017-01-26 12:24 | 2017-01-26 13:30 | 66 | 11kV | 132 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170408 A Phase DOLF : 10 Amp Excluded OMS 1453145 | January | 2017 | 2017Q3 | 2017 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2017-01-26 | N | 66 | N | 5 | N | N | 1.1101 | 39.4971 | 96.4617
[7 empty] | 10314 | 19773 | 1453082 | 2017-01-26 20:54 | 2017-01-26 22:55 | 121 | 11kV | 605 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170403 C Phase DOLF : 3 Amp Field services Maitland please note. All 3A 11kV dolfs replaced with 10A per TS 4200. Please confirm OK and submit SAO for 10A fuse elements. DQ Excluded oms 1453082 no cause found - | January | 2017 | 2017Q3 | 2017 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Veg | 2017-01-26 | N | 121 | N | 5 | N | N | 1.1101 | 39.4971 | 442.1162
[7 empty] | 8891 | 2655 | 1453192 | 2017-01-26 22:19 | 2017-01-26 23:22 | 63 | 11kV | 127191 | 2112 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S12580 Erina Panel 4 "Point Frederick, Springfield" tripped on: 4R IOC A phase EFI Field EFI's S18397 Remarks: UG fault. 11kv UGOH in section of feeder from LB40351 to AB41684 to S18029 Sw/A tee PT13029 Melbourne Adelaide | January | 2017 | 2017Q3 | 2017 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | UG | Not Veg | 2017-01-26 | N | 60.223 | N | 5 | N | N | 1.1101 | 39.4971 | 92947.4313
[7 empty] | 10136 | 17637 | 1453231 | 2017-01-27 09:15 | 2017-01-27 10:37 | 82 | 11kV | 50174 | 700 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman Panel 34 "Dalton Spit" tripped Relays - A&C phase IOC and timed , EFI, fault check Signals: 11kv trip, Tx4 Group Earth EFI's: S5069 S46611 S48381 Contractor excavating at No.17 Stanton Rd. Dug up cable See 1455026,7,8 exclude 1453231,3,4,6 | January | 2017 | 2017Q3 | 2017 | ZN180:PA34 | ZN180:PA34 | ZN00180/000034 | MOSMAN | UG | Not Veg | 2017-01-27 | N | 71.6771 | N | 4 | N | N | 1.1101 | 39.4971 | 36665.6793
[7 empty] | 9547 | 10591 | 1453283 | 2017-01-27 12:24 | 2017-01-27 14:06 | 101.8833 | 11kV | 3871.5667 | 38 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170411 Installed Line Fuses at 75429 & 74505 to extend protection coverage to the end of feeder since Sw 74466 is not working. | January | 2017 | 2017Q3 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-01-27 | N | 101.8833 | N | 4 | N | N | 1.1101 | 39.4971 | 2829.2267
[7 empty] | 10149 | 17794 | 1453268 | 2017-01-27 11:18 | 2017-01-27 14:45 | 207 | 11kV | 414 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170412 C Phase DOLF : 10 Amp Dead bird at base of pole Excluded OMS 1453268 | January | 2017 | 2017Q3 | 2017 |  |  |  |  | OH | Not Veg | 2017-01-27 | N | 207 | N | 4 | N | N | 1.1101 | 39.4971 | 302.539
[7 empty] | 9539 | 10447 | 1453323 | 2017-01-27 15:39 | 2017-01-27 18:23 | 164 | 11kV | 37072 | 238 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge Panel 11 "Somersby" fdr has tripped Signals: 11kv trip Relays: A-N OC, EF, EFI EFI's:Nil Note:Feeder SEL and Rec were non auto for switching. Switching was not being performed on this feeder when outage occured. Cause not ascertained. See 1454306,9,11,12 exclude 1453323 | January | 2017 | 2017Q3 | 2017 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2017-01-27 | N | 155.7647 | N | 4 | N | N | 1.1101 | 39.4971 | 27091.1242
[7 empty] | 9672 | 12040 | 1453384 | 2017-01-28 08:10 | 2017-01-28 12:20 | 250 | 11kV | 8000 | 32 | HV | Animal Bird | Animal | Bond | Unplanned | No Weather Impact | N | LID 170416 isolate to repair tappings at UGOH pole GW-60205. Dead bird found. See 170415. Excluded oms1453384 | January | 2017 | 2017Q3 | 2017 | 227:13018 | 227:13018 | ZN00227/013018 | LAKE MACQUARIE | OH | Not Veg | 2017-01-28 | N | 250 | N | 2 | N | N | 1.1101 | 39.4971 | 5846.164
[7 empty] | 9974 | 15580 | 1454328 | 2017-01-28 16:23 | 2017-01-28 17:32 | 69 | 11kV | 2484 | 44 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Panel 1 CP44853 Ourimbah Bumble Relays: OC trip Signals: 11kv trip Cause: Tree/Branch on Oh mains. Adjacent to LB44051 See 1454328,9 | January | 2017 | 2017Q3 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2017-01-28 | N | 56.4545 | N | 2 | N | N | 1.1101 | 39.4971 | 1815.2339
[7 empty] | 9610 | 11383 | 1453524 | 2017-01-29 08:32 | 2017-01-29 09:35 | 63 | 11kV | 441 | 7 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170419 A Phase DOLF : 10 Amp 2 dead birds found. Excluded OMS No. 1453524 + 1453527 | January | 2017 | 2017Q3 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2017-01-29 | N | 63 | N | 15 | N | N | 1.1101 | 39.4971 | 322.2698
[7 empty] | 9858 | 14271 | 1453508 | 2017-01-29 02:24 | 2017-01-29 17:00 | 876 | 11kV | 332249 | 2310 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15008 Harbord Panel 1 tripped and reclosed on IOC, reclose lockout and time delay efi. Cause: Large tree in campbell pde - Damaged OH mains, HV/LV pole required to be replaced. See OMS 1454128 1454130 1454131 1453508 1453513 | January | 2017 | 2017Q3 | 2017 | ZN15008:PA1 | ZN15008:PA6 | ZN15008/000006 | NORTHERN BEACHES | OH | Veg | 2017-01-29 | N | 143.8307 | N | 15 | N | N | 1.1101 | 39.4971 | 242797.7695
[7 empty] | 10162 | 17934 | 1453578 | 2017-01-29 16:12 | 2017-01-29 17:25 | 73.1667 | 11kV | 2707.1667 | 37 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170423 A Phase DOLF : 20 Amp | January | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-01-29 | N | 73.1667 | N | 15 | N | N | 1.1101 | 39.4971 | 1978.3176
[7 empty] | 8751 | 680 | 1453579 | 2017-01-29 17:03 | 2017-01-29 19:45 | 162 | 11kV | 648 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 170430 A Phase DOLF : 10 Amp arrestor on tx cut away and needs replacing Excluded oms 1453594 | January | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2017-01-29 | N | 162 | N | 15 | N | N | 1.1101 | 39.4971 | 473.5393
[7 empty] | 9774 | 13319 | 1453607 | 2017-01-29 17:55 | 2017-01-29 19:53 | 118.1167 | 11kV | 4370.3167 | 37 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170432 C Phase DOLF : 20 Amp | January | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-01-29 | N | 118.1167 | N | 15 | N | N | 1.1101 | 39.4971 | 3193.6985
[7 empty] | 9339 | 7923 | 1453574 | 2017-01-29 15:43 | 2017-01-29 20:35 | 292.2 | 11kV | 5259.6 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170422 C Phase DOLF : 16 Amp | January | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-01-29 | N | 292.2 | N | 15 | N | N | 1.1101 | 39.4971 | 3843.5605
[7 empty] | 8737 | 344 | 1453580 | 2017-01-29 16:22 | 2017-01-29 21:20 | 298.2 | 11kV | 5964 | 20 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Electrical Storm | N | 16a DOLF Aph spur fuse CC1: 22-"Refer to SOp" | January | 2017 | 2017Q3 | 2017 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2017-01-29 | N | 298.2 | N | 15 | N | N | 1.1101 | 39.4971 | 4358.3153
[7 empty] | 9448 | 9356 | 1453606 | 2017-01-29 17:50 | 2017-01-29 22:00 | 250 | 11kV | 250 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Electrical Storm | N | LID 170434 A Phase DOLF fell out in storm Excluded OMS 1453606. | January | 2017 | 2017Q3 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2017-01-29 | N | 250 | N | 15 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 9816 | 13792 | 1453628 | 2017-01-29 19:55 | 2017-01-29 22:15 | 140 | 11kV | 280 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170436 A & C Phase DOLF : 5 Amp Excluded OMS 1453628 | January | 2017 | 2017Q3 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-01-29 | N | 140 | N | 15 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 8782 | 1217 | 1453620 | 2017-01-29 19:24 | 2017-01-29 23:20 | 236 | 11kV | 4248 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170441 C Phase DOLF : 31 Amp Excluded OMS 1453620 & 1453621 | January | 2017 | 2017Q3 | 2017 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Veg | 2017-01-29 | N | 236 | N | 15 | N | N | 1.1101 | 39.4971 | 3104.3131
[7 empty] | 9280 | 7235 | 1453615 | 2017-01-29 18:55 | 2017-01-29 23:50 | 295 | 11kV | 590 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170439 B Phase DOLF : 20 Amp Excluded OMS 1453615 | January | 2017 | 2017Q3 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2017-01-29 | N | 295 | N | 15 | N | N | 1.1101 | 39.4971 | 431.1546
[7 empty] | 8893 | 2668 | 1453616 | 2017-01-29 19:04 | 2017-01-29 23:50 | 286 | 11kV | 5720 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170442 A & C phase DOLF : 16 Amp Both beyond LF 74786 B Ph 10A Dolf at S 71245 No fault at S 46947 Excluded OMS 1453622 & 1453616 | January | 2017 | 2017Q3 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2017-01-29 | N | 286 | N | 15 | N | N | 1.1101 | 39.4971 | 4180.0073
[7 empty] | 9010 | 4063 | 1453582 | 2017-01-29 16:21 | 2017-01-29 23:59 | 458 | 11kV | 437281 | 1295 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170435 & 170426 2 fault operations 3 phase Overcurrent Feeder had multiple faults. Also affected due to load shift at ABS 74868 due to faulty ABS 74728. 4 spans down at p. AH-10027. Excluded OMS 1453582, 1453583, 1453593, 1453587,1453645 1453602, 1453648. | January | 2017 | 2017Q3 | 2017 | 813:89065 | 813:89065 | ZN00813/089065 | UPPER HUNTER | OH | Not Veg | 2017-01-29 | N | 337.6687 | N | 15 | N | N | 1.1101 | 39.4971 | 319552.0572
[7 empty] | 9344 | 7979 | 1453613 | 2017-01-29 18:35 | 2017-01-30 02:00 | 445 | 11kV | 13350 | 30 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 170445 Burnt off tapping at pole AG 20083. Tried to contact 3 contacts from the protocol without luck. LF 74087 into Parkville Piggeries will be left OPEN & Warning tagged as 2 DOLFS were blown and damage to a DOLF can be seen within private 11kV network. Please contact network owners to repair. Excluded OMS 1453613 & 1453635 | January | 2017 | 2017Q3 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2017-01-29 | N | 445 | N | 15 | N | N | 1.1101 | 39.4971 | 9755.7862
[7 empty] | 9455 | 9436 | 1453631 | 2017-01-29 19:59 | 2017-01-30 03:55 | 476 | 11kV | 29508 | 102 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Panel 8 CP44995 Kulnura tripped, reclosed and locked out on: Relays: IOC, OC trip Signals: 11kv trip Cause: Tree/Branch brought down on OH HV into LV mains adjacent PT12384 George Downs Kyola See 1454331,2 exclude 1453631,2,6,44 | January | 2017 | 2017Q3 | 2017 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2017-01-29 | N | 289.2941 | N | 15 | N | N | 1.1101 | 39.4971 | 21563.5761
[7 empty] | 8860 | 2224 | 1453719 | 2017-01-30 08:31 | 2017-01-30 10:10 | 99 | 11kV | 99 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170454 Single phase DOLF : 5 Amp excluded OMS 1453719 | January | 2017 | 2017Q3 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-01-30 | N | 99 | N | 15 | N | N | 1.1101 | 39.4971 | 72.3463
[7 empty] | 9979 | 15665 | 1453696 | 2017-01-30 07:48 | 2017-01-30 10:25 | 157 | 11kV | 3140 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 170456 B Phase DOLF : 16 Amp Excluded OMS 1453696 & 1453709 | January | 2017 | 2017Q3 | 2017 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2017-01-30 | N | 157 | N | 15 | N | N | 1.1101 | 39.4971 | 2294.6194
[7 empty] | 8953 | 3420 | 1454184 | 2017-01-30 09:12 | 2017-01-30 10:45 | 93 | 11kV | 279 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 170457/01 3 phase DOLF : 20 Amp Excluded OMS 1453743 | January | 2017 | 2017Q3 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-01-30 | N | 93 | N | 15 | N | N | 1.1101 | 39.4971 | 203.885
[7 empty] | 8781 | 1201 | 1453743 | 2017-01-30 09:12 | 2017-01-30 10:50 | 98 | 11kV | 392 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170457/02 3 phase DOLF : 10 Amp Excluded OMS 1453743 | January | 2017 | 2017Q3 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-01-30 | N | 98 | N | 15 | N | N | 1.1101 | 39.4971 | 286.462
[7 empty] | 9513 | 10112 | 1454164 | 2017-01-30 11:51 | 2017-01-30 11:56 | 5 | 11kV | 245 | 49 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 170460 Sw 74441 tripped when energising suspect tx 64454 after DOLF had operated. See LID #170459/OMS 1454163 | January | 2017 | 2017Q3 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2017-01-30 | N | 5 | N | 15 | N | N | 1.1101 | 39.4971 | 179.0388
[7 empty] | 9904 | 14848 | 1453690 | 2017-01-30 07:37 | 2017-01-30 15:03 | 446 | 11kV | 2230 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 170459 Single phase DOLF : 10 Amp Excluded OMS 1453690 + 1453770 | January | 2017 | 2017Q3 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2017-01-30 | N | 446 | N | 15 | N | N | 1.1101 | 39.4971 | 1629.6182
[7 empty] | 9363 | 8245 | 1453921 | 2017-01-30 15:36 | 2017-01-30 16:30 | 54 | 11kV | 486 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170464 C Phase DOLF : 16 Amp Excluded OMS 1453921 | January | 2017 | 2017Q3 | 2017 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2017-01-30 | N | 54 | N | 15 | N | N | 1.1101 | 39.4971 | 355.1545
[7 empty] | 8997 | 3940 | 1453873 | 2017-01-30 14:13 | 2017-01-30 16:40 | 147 | 11kV | 117973 | 1157 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | At S35800 Bankstown Panel 7 "short fair" feeder tripped on: SEL Remarks: cause not ascertained. Dop patrolled progressively down feeder checking volts all ok | January | 2017 | 2017Q3 | 2017 | ZN35800:PA7 | ZN35800:PA7 | ZN35800/000007 | CANTERBURY-BANKSTOWN | OH | Veg | 2017-01-30 | N | 101.9646 | N | 15 | N | N | 1.1101 | 39.4971 | 86211.1888
[7 empty] | 9308 | 7532 | 1453953 | 2017-01-30 17:45 | 2017-01-30 19:04 | 79 | 11kV | 24859 | 319 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Zn35370 Galston panel 10 tripped on Relays: Protection operations not shown on Basler Relay TPE to investigate Cause: previous fault - caused bond to burn off near AB2270 on pole DU42238 Cnr of Galston and Uralla St. Abnormal Swicthing: CP50015 Open with CP62157 Closed See OMS 1454596 1454598 1453953 | January | 2017 | 2017Q3 | 2017 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2017-01-30 | N | 77.9279 | N | 15 | N | N | 1.1101 | 39.4971 | 18166.224
[7 empty] | 8764 | 929 | 1453848 | 2017-01-30 13:21 | 2017-01-30 19:30 | 369 | 11kV | 3119 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | Ex Zn12650 West Gosford section of Panel 1 "Dogr Trap Rd"fdr RE45010 Palm GRove hasr trapped OH down suspect fallen mains caused a bushfire at 91 Lyrbird Lsane Palm Grove See 1454734,9 | January | 2017 | 2017Q3 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2017-01-30 | N | 173.2778 | N | 15 | N | N | 1.1101 | 39.4971 | 2279.2732
[7 empty] | 8939 | 3171 | 1453959 | 2017-01-30 17:26 | 2017-01-30 19:37 | 131 | 11kV | 136532 | 1157 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | At S35800 Bankstown Panel 7 tripped on SEL Remarks: Cause not ascertained. Load switched to Panel 15L from AB652 ON | January | 2017 | 2017Q3 | 2017 | ZN35800:PA7 | ZN35800:PA7 | ZN35800/000007 | CANTERBURY-BANKSTOWN | OH | Veg | 2017-01-30 | N | 118.0052 | N | 15 | N | N | 1.1101 | 39.4971 | 99773.5586
[7 empty] | 9201 | 6473 | 1453964 | 2017-01-30 17:12 | 2017-01-30 20:15 | 183 | 11kV | 8967 | 49 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ex Zn2400 berowra panel 18 Bond Burnt off AB314 Cause: AB314 Footpath HR connection See OMS 1455089 1453964 1453974 1493979 | January | 2017 | 2017Q3 | 2017 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2017-01-30 | N | 183 | N | 15 | N | N | 1.1101 | 39.4971 | 6552.8191
[7 empty] | 9783 | 13528 | 1453918 | 2017-01-30 15:25 | 2017-01-30 23:13 | 468 | 11kV | 291020 | 704 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170469 3 phase Overcurrent tree on mains after storm, section isolated for tree removal and repair mains Excluded oms 1453954, 1453918,1453924 | January | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-01-30 | N | 413.3807 | N | 15 | N | N | 1.1101 | 39.4971 | 212668.8324
[7 empty] | 9346 | 8028 | 1453944 | 2017-01-30 16:32 | 2017-01-31 08:25 | 953 | 11kV | 63696 | 186 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Hot >35C | N | 11kV recloser CP50015 Quarray Old Northern Tripped reclosed tripped and locked out on Relays: O/C trip ex 11kV feeder panel 10 ZN35370 Cause:07 75 Quarry Rd Pole No DU42063 hit by a truck - Section of 11kV between LB2928 and LB 62156 Isolated with 4 centres interrupted See OMS 1454652 1454563 1453944 1454008 1453947 | January | 2017 | 2017Q3 | 2017 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2017-01-30 | N | 342.4516 | N | 15 | N | N | 1.1101 | 39.4971 | 46547.1581
[7 empty] | 9833 | 13977 | 1454133 | 2017-01-31 08:25 | 2017-01-31 10:15 | 110 | 11kV | 110 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | Ex Zn14143 Somersby section of Panel 6 "pnnacle Trienium" fdr PT49999 Myorra Australian Repitle Park 11kv 63k footpath phase HDO found operated. batch #1004 DOp suspects Fuse Fatigue See 1454754 exclude 1454133,53 | January | 2017 | 2017Q3 | 2017 | ZN14143:PA6 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | OH | Not Veg | 2017-01-31 | N | 110 | N | 6 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 9446 | 9327 | 1454077 | 2017-01-30 23:16 | 2017-01-31 10:40 | 684 | 11kV | 43092 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170472 1 fault operation Single phase Overcurrent Excluded OMS 1454077 | January | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-01-30 | N | 684 | N | 15 | N | N | 1.1101 | 39.4971 | 31490.3626
[7 empty] | 9288 | 7336 | 1454186 | 2017-01-31 10:09 | 2017-01-31 11:40 | 91 | 11kV | 182 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170482 C Phase DOLF : 10 Amp 3 dead birds found at sub. Excluded OMS No. 1454186 | January | 2017 | 2017Q3 | 2017 |  |  |  |  | OH | Not Veg | 2017-01-31 | N | 91 | N | 6 | N | N | 1.1101 | 39.4971 | 133.0002
[7 empty] | 9929 | 15085 | 1454276 | 2017-01-31 12:22 | 2017-01-31 13:43 | 81.1167 | 11kV | 15087.7 | 186 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Recloser CP50015 Quarry Old Northern - Tripped,reclosed tripped and locked out on OC trip Cause: tree branch on OH mains beyond LB62156 See OMS 1454276 1454282 1454335 | January | 2017 | 2017Q3 | 2017 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2017-01-31 | N | 81.1167 | N | 6 | N | N | 1.1101 | 39.4971 | 11025.6461
[7 empty] | 8821 | 1717 | 1454338 | 2017-01-31 14:08 | 2017-01-31 16:34 | 146 | 11kV | 106996 | 849 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | @S874 Concord Panel 17 "Lavelle links" feeder tripped on: spaj 140c #4 L1 L2 efi Field EFIs: down to S7573 sw/b incorrect indication from previous fault no access after hours efi @ S2828 defective | January | 2017 | 2017Q3 | 2017 | ZN874:PA17 | ZN874:PA17 | ZN00874/000017 | CANADA BAY | UG | Not Veg | 2017-01-31 | N | 126.0259 | N | 6 | N | N | 1.1101 | 39.4971 | 78189.521
[7 empty] | 10189 | 18351 | 1454490 | 2017-01-31 20:57 | 2017-01-31 22:35 | 98 | 11kV | 4312 | 44 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn13000 Lake Munmorah section of Panel 2 PT12954 Harding Acacia Roadside HDO operated 31Amp ABB Batch :3428 Flashover caused by possum no further action required See 1459402 exclude 1454492, 1454490 | January | 2017 | 2017Q3 | 2017 | ZN13000:PA2 | ZN13000:PA2 | ZN13000/000002 | CENTRAL COAST | OH | Not Veg | 2017-01-31 | N | 98 | N | 6 | N | N | 1.1101 | 39.4971 | 3151.0824
[7 empty] | 8998 | 3949 | 1454505 | 2017-01-31 22:09 | 2017-02-01 00:16 | 127 | 11kV | 129910 | 1023 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn14143 Somersby Panel 5 "Karion Sth" fdr tripped Relays: A&B Phase O/C, EFI EFI's: S18048, CP45441 DOp patrolled no apparent cause, mains to inspect in daylight. See 1454760,1 exclude 1454505 | January | 2017 | 2017Q3 | 2017 | ZN14143:PA5 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Veg | 2017-01-31 | N | 126.9892 | N | 6 | N | N | 1.1101 | 39.4971 | 94934.3963
[7 empty] | 10234 | 18890 | 1454516 | 2017-02-01 00:36 | 2017-02-01 03:16 | 160 | 11kV | 139908 | 987 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman 11kv fdr Panel 27 fdr tripped Relays: A phase timed o/c, EFI, fault check EFI's S674 S149 Fault in section of 11kv from S149 Melrose Lang SwB to S3703 Prospet Langley SwA to S886 Macpherson st Sw See seperate interruption for Panel 32 at same time. Note: Unable to control C/B No27 or No32 via SCADA, local operation only t/tele to investigate See 1455058,9,60 exclude 1454516,7,20 | February | 2017 | 2017Q3 | 2017 | ZN180:PA27 | ZN180:PA27 | ZN00180/000027 | MOSMAN | UG | Not Veg | 2017-02-01 | N | 141.7508 | N | 9 | N | N | 1.1101 | 39.4971 | 102240.6398
[7 empty] | 9900 | 14827 | 1454517 | 2017-02-01 00:36 | 2017-02-01 03:55 | 199 | 11kV | 490427 | 2693 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman Panel 32 Relays: Fdr protection A relay LEDS :Trip A phase, B Phase and N, IOC, O/C, E/F, TCS Left fdr/B LEDS trip, alarm, IOC, Fault Check, EFI Right: Nil EFI's: S3855 S6727 Abnormal: DMA S48381 to S36174 to S5654 Closed S35392:B Fault in section of 11kv fdr from S6727 SwB to S2240 SwA Note: Unable to control CB27 or CB32 via SCADA, local operation only, t/tele to investigate See 1455080,2,3,4,5,6 1455090 exclude 1454520 | February | 2017 | 2017Q3 | 2017 | ZN180:PA32 | ZN180:PA32 | ZN00180/000032 | MOSMAN | UG | Not Veg | 2017-02-01 | N | 182.1118 | N | 9 | N | N | 1.1101 | 39.4971 | 358389.5865
[7 empty] | 9534 | 10403 | 1454618 | 2017-02-01 09:28 | 2017-02-01 11:35 | 127 | 11kV | 381 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT14591 George DOwn Nanundi No.1 11kv 40Amp footpath phase doropout fuse operated Fuse Fatigue See 1456864 exlcude 1454618 | February | 2017 | 2017Q3 | 2017 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2017-02-01 | N | 127 | N | 9 | N | N | 1.1101 | 39.4971 | 278.4236
[7 empty] | 10287 | 19378 | 1454548 | 2017-02-01 06:53 | 2017-02-01 12:40 | 347 | 11kV | 1735 | 5 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | Rain Light | N | LID 170506 A Phase DOLF Broken stay wire caused by cattle, came into contact with sub Excluded OMS 1454548 | February | 2017 | 2017Q3 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2017-02-01 | N | 347 | N | 9 | N | N | 1.1101 | 39.4971 | 1267.8868
[7 empty] | 9874 | 14472 | 1454703 | 2017-02-01 12:43 | 2017-02-01 14:00 | 77 | 11kV | 77 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 170510 B Phase DOLF : 10 Amp | February | 2017 | 2017Q3 | 2017 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2017-02-01 | N | 77 | N | 9 | N | N | 1.1101 | 39.4971 | 56.2693
[7 empty] | 10146 | 17769 | 1454671 | 2017-02-01 11:13 | 2017-02-01 14:20 | 187 | 11kV | 94158 | 1190 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman Panel 29 fdr tripped on Relays: Earth Fault, EFI, Fault CHeck Signals: 11kv trip, Zone Earth, Tx2 Group Earth EFI'S: S8586 S4657 S3640 S6197 S886 Abnormal: Fdr fault from S886:A top S3703 to S149 11kv UG fault from S2463 to S886 See 1454671 1454706 | February | 2017 | 2017Q3 | 2017 | ZN180:PA29 | ZN180:PA29 | ZN00180/000029 | NORTH SYDNEY | UG | Not Veg | 2017-02-01 | N | 79.1244 | N | 9 | N | N | 1.1101 | 39.4971 | 68807.8892
[7 empty] | 9815 | 13785 | 1454793 | 2017-02-01 16:38 | 2017-02-01 17:10 | 32.1 | 11kV | 353.1 | 11 | HV | Vegetation Grow In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170511 Single phase Tree grown into mains | February | 2017 | 2017Q3 | 2017 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2017-02-01 | N | 32.1 | N | 9 | N | N | 1.1101 | 39.4971 | 258.0351
[7 empty] | 9224 | 6781 | 1454866 | 2017-02-01 21:54 | 2017-02-01 22:57 | 63 | 11kV | 2525 | 44 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170513 3 fault operations Excluded OMS 1454866 | February | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-02-01 | N | 57.3864 | N | 9 | N | N | 1.1101 | 39.4971 | 1845.1955
[7 empty] | 9321 | 7768 | 1454868 | 2017-02-01 21:52 | 2017-02-01 23:00 | 68 | 11kV | 48260 | 1102 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | Lightning | N | Zn10997 Sans Souci - Pnl.1 tripped, reclosed, tripped and locked out on: A, B & C phase IOC, Lockout, timing Bat adjacent to PT10862 Monterey Grand caused flashover. Bat removed no damage evident See outage at S50625 Dist #2 due to LV // failure. See 1454868 SE: 1454876 | February | 2017 | 2017Q3 | 2017 | ZN10997:PA1 | ZN10997:PA1 | ZN10997/000001 | BAYSIDE | OH | Not Veg | 2017-02-01 | N | 43.7931 | N | 9 | N | N | 1.1101 | 39.4971 | 35266.9846
[7 empty] | 9749 | 13029 | 1454934 | 2017-02-02 07:31 | 2017-02-02 10:20 | 169 | 11kV | 676 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170520 A Phase DOLF : 10 Amp Excluded OMS 1454934 | February | 2017 | 2017Q3 | 2017 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2017-02-02 | N | 169 | N | 2 | N | N | 1.1101 | 39.4971 | 494.0009
[7 empty] | 10127 | 17550 | 1455190 | 2017-02-02 22:30 | 2017-02-02 23:27 | 57 | 11kV | 54207 | 951 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn1287 Revesby 11kv feeder Panel No.22 "Macarthur Revesby" feeder tripped Relays: C phase timed O/C, fault check Signals: 11kv trip Field EFI's: Nil Remarks: Cause not ascertained. Bat caused flashover O/S 32 chamberlain Ave Revesby, no damage to mains | February | 2017 | 2017Q3 | 2017 | ZN1287:PA22 | ZN1287:PA22 | ZN01287/000022 | CANTERBURY-BANKSTOWN | OH | Veg | 2017-02-02 | N | 57 | N | 2 | N | N | 1.1101 | 39.4971 | 39612.8768
[7 empty] | 10220 | 18749 | 1455203 | 2017-02-03 06:45 | 2017-02-03 10:30 | 225 | 11kV | 1350 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT47012 Jilliby Jill 0.1 11kv footpath HDO operated due to fuse fatigue 31.5K HDO failed at the crimp See 1456252 exclude 1455208,20 | February | 2017 | 2017Q3 | 2017 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2017-02-03 | N | 225 | N | 1 | N | N | 1.1101 | 39.4971 | 986.5402
[7 empty] | 10339 | 20135 | 1455380 | 2017-02-04 02:45 | 2017-02-04 03:55 | 70 | 11kV | 50806 | 745 | HV | Equipment Failed in Service | Equipment Failure | U/G Link | Unplanned | No Weather Impact | N | LID 170558 4 fault operations A phase Earth Fault U/G cable fault Excluded 1455380 | February | 2017 | 2017Q3 | 2017 | 257:81994 | 257:81994 | ZN00257/081994 | NEWCASTLE | UG | Not Veg | 2017-02-04 | N | 68.196 | N | 31 | Y | Y | 1.1101 | 39.4971 | 37127.5263
[7 empty] | 9296 | 7415 | 1455511 | 2017-02-04 17:04 | 2017-02-04 17:15 | 11 | 11kV | 1210 | 110 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 170611 3 phase Overcurrent Roof into mains near sub 70866. Excluded oms report no 1455657. Note: from 04/02/17 17:15 to 04/02/17 17:21 customers were affected by Feeder area outage - refer to OMS Event 1455509 | February | 2017 | 2017Q3 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-02-04 | N | 11 | N | 31 | Y | Y | 1.1101 | 39.4971 | 884.2323
[7 empty] | 9542 | 10499 | 1455494 | 2017-02-04 16:51 | 2017-02-04 18:40 | 109 | 11kV | 12208 | 112 | HV | Overload LV Parallel | Utility Process Issue | O/H Link | Unplanned | No Weather Impact | N | At PT15169 Sorlie Rd Road side HDO was found blown 40A Cause: PT15169 in LV parallel link 15807 was found closed. See OMS 1456181 1455494 | February | 2017 | 2017Q3 | 2017 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Not Veg | 2017-02-04 | N | 109 | N | 31 | Y | Y | 1.1101 | 39.4971 | 8921.2463
[7 empty] | 9050 | 4775 | 1455539 | 2017-02-04 18:13 | 2017-02-04 20:11 | 118 | 11kV | 118 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170587 Fuse size: 10 AMP. Substation DOLF also refer to 1455539 | February | 2017 | 2017Q3 | 2017 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2017-02-04 | N | 118 | N | 31 | Y | Y | 1.1101 | 39.4971 | 86.2309
[7 empty] | 9916 | 14975 | 1456303 | 2017-02-04 19:14 | 2017-02-04 21:15 | 121 | 11kV | 242 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 170591 B Phase DOLF : 10 Amp | February | 2017 | 2017Q3 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2017-02-04 | N | 121 | N | 31 | Y | Y | 1.1101 | 39.4971 | 176.8465
[7 empty] | 10217 | 18732 | 1455540 | 2017-02-04 18:17 | 2017-02-04 22:15 | 238 | 11kV | 2142 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170604 B & C Phase DOLF 10 Amp Excluded OMS 1455540 | February | 2017 | 2017Q3 | 2017 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2017-02-04 | N | 238 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1565.3104
[7 empty] | 9416 | 9001 | 1455484 | 2017-02-04 15:24 | 2017-02-04 23:04 | 460 | 11kV | 42900 | 185 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 170567 1 fault operation Sensitive Earth Fault 11kv main down to sub 46241. Excluded OMS 1455484 & 1455634. | February | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-02-04 | N | 231.8919 | N | 31 | Y | Y | 1.1101 | 39.4971 | 31350.0547
[7 empty] | 9520 | 10234 | 1455618 | 2017-02-04 20:30 | 2017-02-04 23:08 | 158 | 11kV | 124101 | 864 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 170615 2 fault operations A Phase Overcurrent Abs 8279 hit by probably lightning Excluded oms1455618 | February | 2017 | 2017Q3 | 2017 | 214:8667 | 214:8667 | ZN00214/008667 | LAKE MACQUARIE | OH | Not Veg | 2017-02-04 | N | 143.6354 | N | 31 | Y | Y | 1.1101 | 39.4971 | 90689.3504
[7 empty] | 8886 | 2612 | 1456302 | 2017-02-04 19:14 | 2017-02-04 23:10 | 236 | 11kV | 236 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170614 C Phase DOLF : 10 Amp | February | 2017 | 2017Q3 | 2017 |  |  |  |  | OH | Veg | 2017-02-04 | N | 236 | N | 31 | Y | Y | 1.1101 | 39.4971 | 172.4618
[7 empty] | 9918 | 14978 | 1455621 | 2017-02-04 20:40 | 2017-02-04 23:35 | 175 | 11kV | 9275 | 53 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170616 A Phase DOLF : 20 Amp Excluded OMS 1455621/1455622 | February | 2017 | 2017Q3 | 2017 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Veg | 2017-02-04 | N | 175 | N | 31 | Y | Y | 1.1101 | 39.4971 | 6777.8964
[7 empty] | 8753 | 706 | 1455500 | 2017-02-04 17:14 | 2017-02-04 23:59 | 405 | 11kV | 147423 | 778 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 170592 2 fault operations Earth Fault MAINS DOWN BETWEEN POLES AH-20138,AH-20140 & AH-20111,AH-20112. Excluded OMS REPORT NO 1455512,1455529,1455509,1455510,1455505. | February | 2017 | 2017Q3 | 2017 | 813:89065 | 813:89065 | ZN00813/089065 | UPPER HUNTER | OH | Not Veg | 2017-02-04 | N | 189.4897 | N | 31 | Y | Y | 1.1101 | 39.4971 | 107732.3802
[7 empty] | 10110 | 17355 | 1455509 | 2017-02-04 17:15 | 2017-02-05 00:22 | 427 | 11kV | 206425 | 636 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 170613 2 fault operations HV MAINS DOWN BETWEEN POLES AH-20111 to AH-20112 & AH-20138 to Excluded OMS REPORT NO 1455500 & 1455651 | February | 2017 | 2017Q3 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2017-02-04 | N | 324.5676 | N | 31 | Y | Y | 1.1101 | 39.4971 | 150849.3015
[7 empty] | 9458 | 9542 | 1455604 | 2017-02-04 18:51 | 2017-02-05 01:10 | 379 | 11kV | 6064 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170629 C Phase DOLF : 16 Amp Suspect faulty Tx. Sub interconnected. Excluded oms 1455568. | February | 2017 | 2017Q3 | 2017 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2017-02-04 | N | 379 | N | 31 | Y | Y | 1.1101 | 39.4971 | 4431.3923
[7 empty] | 9634 | 11592 | 1455568 | 2017-02-04 18:51 | 2017-02-05 01:25 | 393.5167 | 11kV | 393.5167 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170632 A & B phase DOLF : 10 Amp | February | 2017 | 2017Q3 | 2017 | 528:83019 | 528:83019 | ZN00528/083019 | PORT STEPHENS | OH | Veg | 2017-02-04 | N | 393.5167 | N | 31 | Y | Y | 1.1101 | 39.4971 | 287.5704
[7 empty] | 9080 | 5203 | 1455600 | 2017-02-04 19:42 | 2017-02-05 01:45 | 363 | 11kV | 4356 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170633 A phase DOLF : 20 Amp Excluded OMS 1455600 | February | 2017 | 2017Q3 | 2017 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2017-02-04 | N | 363 | N | 31 | Y | Y | 1.1101 | 39.4971 | 3183.2363
[7 empty] | 9380 | 8558 | 1455502 | 2017-02-04 17:04 | 2017-02-05 02:05 | 541 | 11kV | 21947 | 126 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 170617 1 fault operation A & B phase Overcurrent, Instantaneous Overcurrent Burnt off tapping at sub 1926 Excluded OMS 1455502 | February | 2017 | 2017Q3 | 2017 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2017-02-04 | N | 174.1825 | N | 31 | Y | Y | 1.1101 | 39.4971 | 16038.2203
[7 empty] | 9501 | 9934 | 1455482 | 2017-02-04 15:10 | 2017-02-05 02:11 | 661 | 11kV | 7755 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 170562 3 fault operations A & B phase Overcurrent Tree on mains at pole 3H-10015 Note This events a 2 part event starting at 15:10 for 14 minutes then again and again 19:17 as these same customers were also affected by a larger area outage on the same feeder upstream that began at 04/02/17 15:24 and finished at 04/02/17 19:17 refer to Event OMS 1456693. | February | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-02-04 | N | 387.75 | N | 31 | Y | Y | 1.1101 | 39.4971 | 5667.1253
[7 empty] | 8832 | 1805 | 1455542 | 2017-02-04 18:21 | 2017-02-05 02:50 | 509 | 11kV | 10689 | 21 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 170631 Single phase DOLF : 31 Amp 11kV mains down at pole FS-30005 Excluded OMS 1455542 | February | 2017 | 2017Q3 | 2017 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Not Veg | 2017-02-04 | N | 509 | N | 31 | Y | Y | 1.1101 | 39.4971 | 7811.2059
[7 empty] | 10048 | 16544 | 1455527 | 2017-02-04 17:43 | 2017-02-05 04:00 | 617 | 11kV | 1234 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170645 A Phase DOLF : 10 Amp Excluded OMS 1455527 | February | 2017 | 2017Q3 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2017-02-04 | N | 617 | N | 31 | Y | Y | 1.1101 | 39.4971 | 901.7708
[7 empty] | 8815 | 1629 | 1455578 | 2017-02-04 19:08 | 2017-02-05 04:00 | 532 | 11kV | 2128 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170646 A Phase DOLF : 10 Amp Excluded OMS 1455578 | February | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-02-04 | N | 532 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1555.0796
[7 empty] | 8824 | 1735 | 1455613 | 2017-02-04 20:29 | 2017-02-05 04:35 | 486 | 11kV | 972 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 170647 llclamp off Excluded oms1455613. | February | 2017 | 2017Q3 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2017-02-04 | N | 486 | N | 31 | Y | Y | 1.1101 | 39.4971 | 710.3089
[7 empty] | 9785 | 13530 | 1455544 | 2017-02-04 18:23 | 2017-02-05 04:50 | 627 | 11kV | 3135 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170648 A Phase DOLF : 10 Amp Excluded oms1455544/62 | February | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-02-04 | N | 627 | N | 31 | Y | Y | 1.1101 | 39.4971 | 2290.9655
[7 empty] | 9812 | 13747 | 1455653 | 2017-02-04 21:57 | 2017-02-05 08:58 | 661 | 11kV | 1322 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170650 B Phase DOLF : 10 Amp staff on site advised they were not given the OMS number. Excluded OMS 1455653, | February | 2017 | 2017Q3 | 2017 | 238:34148 | 508:82576 | ZN00508/082576 | PORT STEPHENS | OH | Veg | 2017-02-04 | N | 661 | N | 31 | Y | Y | 1.1101 | 39.4971 | 966.0786
[7 empty] | 9567 | 10850 | 1455699 | 2017-02-05 09:02 | 2017-02-05 11:00 | 118 | 11kV | 472 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170651 B Phase DOLF : 10 Amp M Brown attendeed no OMS numbers given to Michael, OMS jobs did not arrive at Desk 3 until 30 minutes after the job was completed. Excluded OMS 1455699 and 1455734. | February | 2017 | 2017Q3 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-02-05 | N | 118 | N | 14 | N | N | 1.1101 | 39.4971 | 344.9237
[7 empty] | 9635 | 11593 | 1455662 | 2017-02-04 23:24 | 2017-02-05 11:45 | 741 | 11kV | 1482 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170653 Single phase DOLF : 10 Amp Excluded OMS 1455662 | February | 2017 | 2017Q3 | 2017 | 528:83019 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Veg | 2017-02-04 | N | 741 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1083.0019
[7 empty] | 9219 | 6717 | 1455565 | 2017-02-04 18:45 | 2017-02-05 12:05 | 1040 | 11kV | 5200 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170654 Single phase DOLF : 10 Amp Excluded OMS 1455565 | February | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-02-04 | N | 1040 | N | 31 | Y | Y | 1.1101 | 39.4971 | 3800.0066
[7 empty] | 8907 | 2806 | 1455490 | 2017-02-04 20:00 | 2017-02-05 12:10 | 970 | 11kV | 970 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 170652 No OMS number. Tx change SAO required. | February | 2017 | 2017Q3 | 2017 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2017-02-04 | N | 970 | N | 31 | Y | Y | 1.1101 | 39.4971 | 708.8474
[7 empty] | 9491 | 9866 | 1455635 | 2017-02-04 21:20 | 2017-02-05 12:35 | 915 | 11kV | 3660 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 170655 Single phase DOLF : 10 Amp Excluded OMS 1455635 | February | 2017 | 2017Q3 | 2017 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2017-02-04 | N | 915 | N | 31 | Y | Y | 1.1101 | 39.4971 | 2674.62
[7 empty] | 10168 | 17992 | 1455714 | 2017-02-05 09:51 | 2017-02-05 12:37 | 166 | 11kV | 498 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170657 C Phase DOLF : 16 Amp Excluded OMS 1455714 | February | 2017 | 2017Q3 | 2017 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Veg | 2017-02-05 | N | 166 | N | 14 | N | N | 1.1101 | 39.4971 | 363.9237
[7 empty] | 9437 | 9254 | 1455706 | 2017-02-05 09:19 | 2017-02-05 14:05 | 286 | 11kV | 286 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170659 A Phase DOLF : 10 Amp Excluded OMS 1455706 | February | 2017 | 2017Q3 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2017-02-05 | N | 286 | N | 14 | N | N | 1.1101 | 39.4971 | 209.0004
[7 empty] | 9965 | 15451 | 1455625 | 2017-02-04 20:44 | 2017-02-05 14:40 | 1076 | 11kV | 10760 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170674 Single phase DOLF : 10 Amp DOLF RELACED AND LV TAPPING AT POLE WB-53986. Excluded OMS REPORT NO 1455625. | February | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-02-04 | N | 1076 | N | 31 | Y | Y | 1.1101 | 39.4971 | 7863.0906
[7 empty] | 10172 | 18055 | 1455772 | 2017-02-05 13:17 | 2017-02-05 15:20 | 123 | 11kV | 246 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170662 A Phase DOLF : 10 Amp Excluded OMS 1455772 | February | 2017 | 2017Q3 | 2017 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2017-02-05 | N | 123 | N | 14 | N | N | 1.1101 | 39.4971 | 179.7695
[7 empty] | 8949 | 3334 | 1455707 | 2017-02-05 07:03 | 2017-02-05 15:40 | 517.0167 | 11kV | 517.0167 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 170664 A & B phase DOLF : 20 Amp Mains on ground | February | 2017 | 2017Q3 | 2017 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Not Veg | 2017-02-05 | N | 517.0167 | N | 14 | N | N | 1.1101 | 39.4971 | 377.8205
[7 empty] | 8799 | 1484 | 1455735 | 2017-02-05 10:46 | 2017-02-05 15:45 | 299 | 11kV | 299 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 170666 A Phase DOLF : 10 Amp Burnt off LL Lead. Replaced under AP Excluded oms 1455735 | February | 2017 | 2017Q3 | 2017 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2017-02-05 | N | 299 | N | 14 | N | N | 1.1101 | 39.4971 | 218.5004
[7 empty] | 9435 | 9249 | 1455703 | 2017-02-05 09:13 | 2017-02-05 16:20 | 427 | 11kV | 427 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170669 A Phase DOLF : 10 Amp Excluded OMS 1455703 | February | 2017 | 2017Q3 | 2017 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2017-02-05 | N | 427 | N | 14 | N | N | 1.1101 | 39.4971 | 312.039
[7 empty] | 10256 | 19050 | 1455546 | 2017-02-04 18:16 | 2017-02-05 16:27 | 1331 | 11kV | 49318 | 46 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 170667 2 fault operations 3 phase Overcurrent Broken 11kV x arm and wires down Excluded oms 1455546 | February | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2017-02-04 | N | 1072.1304 | N | 31 | Y | Y | 1.1101 | 39.4971 | 36040.1398
[7 empty] | 8790 | 1339 | 1455602 | 2017-02-04 19:58 | 2017-02-05 16:45 | 1247 | 11kV | 7482 | 6 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 170634 C Phase DOLF : 10 Amp Transformer faulty Excluded OMS 1455602 | February | 2017 | 2017Q3 | 2017 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2017-02-04 | N | 1247 | N | 31 | Y | Y | 1.1101 | 39.4971 | 5467.6249
[7 empty] | 8819 | 1695 | 1455702 | 2017-02-05 09:08 | 2017-02-05 17:06 | 478 | 11kV | 1434 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 170672 A Phase DOLF : 10 Amp TX FAULTY. REPLACED. Excluded OMS 1455702. | February | 2017 | 2017Q3 | 2017 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2017-02-05 | N | 478 | N | 14 | N | N | 1.1101 | 39.4971 | 1047.9249
[7 empty] | 10027 | 16309 | 1455681 | 2017-02-05 07:00 | 2017-02-05 17:15 | 615 | 11kV | 1230 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170671 Single phase DOLF : 10 Amp Excluded OMS 1455681 | February | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-02-05 | N | 615 | N | 14 | N | N | 1.1101 | 39.4971 | 898.8477
[7 empty] | 9043 | 4640 | 1455819 | 2017-02-05 16:45 | 2017-02-05 18:05 | 80 | 11kV | 1120 | 14 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | PT12616 Dog Trap Young 11kv centre phase fuse blown due to 16amp (batch No ABB Last2587) Fuse Fatigue See 1456250 exlcude 1455819 | February | 2017 | 2017Q3 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2017-02-05 | N | 80 | N | 14 | N | N | 1.1101 | 39.4971 | 818.463
[7 empty] | 10082 | 16957 | 1455464 | 2017-02-04 14:29 | 2017-02-05 18:10 | 1661 | 11kV | 116853 | 185 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170561 3 fault operations Sensitive Earth Fault Faulty Tx needed replacement at sub 54405.. SAO required from field crews for Tx change. Excluded OMS REPORT NO 1455464. | February | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2017-02-04 | N | 631.6378 | N | 31 | Y | Y | 1.1101 | 39.4971 | 85392.7258
[7 empty] | 8808 | 1575 | 1455775 | 2017-02-05 13:28 | 2017-02-05 18:30 | 302 | 11kV | 225827 | 2074 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Hot >35C | N | Zn10995 Riverwood - Pnl.7 tripped, reclosed and locked out on: A Phase IOC and timing OC, SEL. EFI Field EFI @ S10161 Cross arm at pole near 30 Flora St failed See 1459901 1459902 | February | 2017 | 2017Q3 | 2017 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Not Veg | 2017-02-05 | N | 108.8848 | N | 14 | N | N | 1.1101 | 39.4971 | 165027.7108
[7 empty] | 10261 | 19101 | 1455853 | 2017-02-05 18:01 | 2017-02-05 20:25 | 144 | 11kV | 297964 | 2162 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At ZN2196 Milperra Pnl 25 tripped on a/c phase ioc, efi fault check efis at S4684, S4276 Remarks: UG fault. S4276 turvey mack to S8790 drove mckenzie | February | 2017 | 2017Q3 | 2017 | ZN2196:PA25 | ZN2196:PA25 | ZN02196/000025 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-02-05 | N | 137.8187 | N | 14 | N | N | 1.1101 | 39.4971 | 217743.3027
[7 empty] | 9256 | 7032 | 1455831 | 2017-02-05 17:07 | 2017-02-05 21:20 | 253 | 11kV | 29686 | 490 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Ex Zn14143 Somersby section of Panel 17 Recloser 45202 pacific Ashbrooke 2.0 tripped on Relays: O/C trip, SEF trip, Lockout Tree/Branch brought down OH OH mains carried out repairs, all supply restored by 2120 See 1456615,6 exclude 1455831,4,65 | February | 2017 | 2017Q3 | 2017 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2017-02-05 | N | 60.5837 | N | 14 | N | N | 1.1101 | 39.4971 | 21693.6532
[7 empty] | 9111 | 5490 | 1455867 | 2017-02-05 22:50 | 2017-02-06 00:20 | 90.2667 | 11kV | 3159.3333 | 35 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Hot >35C | N | LID 170679 no protection operation sub isolated for repairs at pole IU-97052 Excluded oms 1455867 | February | 2017 | 2017Q3 | 2017 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Not Veg | 2017-02-05 | N | 90.2667 | N | 14 | N | N | 1.1101 | 39.4971 | 2308.7476
[7 empty] | 9668 | 11989 | 1456106 | 2017-02-06 09:34 | 2017-02-06 12:40 | 186 | 11kV | 372 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 1463451 A Phase Broken dropper lead Excluded OMS 1456106 | February | 2017 | 2017Q3 | 2017 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2017-02-06 | N | 186 | N | 6 | N | N | 1.1101 | 39.4971 | 271.8466
[7 empty] | 9366 | 8291 | 1456056 | 2017-02-06 08:21 | 2017-02-06 14:30 | 369 | 11kV | 369 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 170686 B Phase DOLF : 10 Amp Excluded OMS 1456056 | February | 2017 | 2017Q3 | 2017 |  |  |  |  | OH | Not Veg | 2017-02-06 | N | 369 | N | 6 | N | N | 1.1101 | 39.4971 | 269.6543
[7 empty] | 9796 | 13596 | 1456196 | 2017-02-06 12:19 | 2017-02-06 17:50 | 331.4667 | 11kV | 662.9333 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Lightning | N | LID 170692 Single phase LIGHTNING DAMAGED L/LINE CLAMP Excluded OMS 1456225. | February | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2017-02-06 | N | 331.4667 | N | 6 | N | N | 1.1101 | 39.4971 | 484.4521
[7 empty] | 9337 | 7905 | 1456408 | 2017-02-06 18:26 | 2017-02-06 19:43 | 77 | 11kV | 108627 | 1419 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At S262 Marrickville - 11kv Panel No.5 "Victoria Mitch 2" tripped on: Relays: Earth fault, EFI, Fault check Signals: 11kv trip EFI's: S35276, S35599 Remarks: UG fault. 11kv ug fault between S35599 Chapel Victoria Sw/B and S7658 Shepherd Chap No.2 Sw/A | February | 2017 | 2017Q3 | 2017 | ZN262:PA5 | ZN262:PA5 | ZN00262/000005 | INNER WEST | UG | Not Veg | 2017-02-06 | N | 76.5518 | N | 6 | N | N | 1.1101 | 39.4971 | 79381.4076
[7 empty] | 9442 | 9295 | 1456447 | 2017-02-06 19:26 | 2017-02-06 21:00 | 94 | 11kV | 7238 | 77 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 170695 No protection operations. LV fuse carriers burning. Sub put in LV //. section isolated for repairs to burnt off tapping to b phase dolf Excluded OMS 1456445 | February | 2017 | 2017Q3 | 2017 | 216:10726 | 216:10726 | ZN00216/010726 | LAKE MACQUARIE | OH | Not Veg | 2017-02-06 | N | 94 | N | 6 | N | N | 1.1101 | 39.4971 | 5289.3169
[7 empty] | 9922 | 15014 | 1456423 | 2017-02-06 18:40 | 2017-02-06 22:10 | 210 | 11kV | 4620 | 22 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 170694 Single phase burnt off 11kv tapping at pole SI-90001. ISOLATED at Links 4251. Excluded oms report 1456423. | February | 2017 | 2017Q3 | 2017 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2017-02-06 | N | 210 | N | 6 | N | N | 1.1101 | 39.4971 | 3376.1597
[7 empty] | 9647 | 11737 | 1456492 | 2017-02-07 00:30 | 2017-02-07 02:13 | 103 | 11kV | 306085 | 2989 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S4545 Meadowbnk Panel 31 tripped Recloser CP46117 Balaclava Vimiera tripped Cause not ascertained for outage See OMS 1457569 1457570 1456492 1455379 | February | 2017 | 2017Q3 | 2017 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Veg | 2017-02-07 | N | 102.4038 | N | 8 | N | N | 1.1101 | 39.4971 | 223677.89
[7 empty] | 10297 | 19526 | 1456700 | 2017-02-07 11:10 | 2017-02-07 12:10 | 60 | 11kV | 180 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170708 A Phase DOLF : 10 Amp No OMS number given call came through from depot. | February | 2017 | 2017Q3 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2017-02-07 | N | 60 | N | 8 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 9108 | 5464 | 1456749 | 2017-02-07 11:54 | 2017-02-07 13:22 | 88 | 11kV | 68112 | 774 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S711 Blackwattle Bay 5kV panel 21 Dangar Beaumont etc tripped on Relays: C phase OC, EFI Signals: 5kV trip Cause: 5kV UG fault between S711 Blackwattle Bay Panel 21 - S7443 Dangar Beaumont SW/A - S4362 Pine Rose SW/B See OMS 1456749 1456771 | February | 2017 | 2017Q3 | 2017 | ZN711:PA21 | ZN711:PA18 | ZN00711/000018 | SYDNEY | UG | Not Veg | 2017-02-07 | N | 88 | N | 8 | N | N | 1.1101 | 39.4971 | 49774.2406
[7 empty] | 10137 | 17640 | 1456789 | 2017-02-07 12:37 | 2017-02-07 14:09 | 92 | 11kV | 140024 | 1522 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN80 Chatswood Panel 25 trippe reclosed trippwed and locked out on Relays: A phase IOC, EFI, Lockout and Timing Signals: 11kV trip Cause: Tree branch on OH mains near PT1537 See OMS 1456789 1458414 | February | 2017 | 2017Q3 | 2017 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Veg | 2017-02-07 | N | 92 | N | 8 | N | N | 1.1101 | 39.4971 | 102325.4092
[7 empty] | 9892 | 14729 | 1456770 | 2017-02-07 12:15 | 2017-02-07 14:36 | 141 | 11kV | 24769 | 244 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | ex S847 Hornsby Panel 45 Recloser CP421 Crosslands Rd Rd tripped reclosed tripped and locked out on Relays: A B and C phase overload Signals: 11kV trip Cause: Tree brought down OH near PT61737 Fishburns Bevans See OMS 1457535 14457536 1457537 1456770 1456773 | February | 2017 | 2017Q3 | 2017 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2017-02-07 | N | 101.5123 | N | 8 | N | N | 1.1101 | 39.4971 | 18100.4546
[7 empty] | 9033 | 4476 | 1456956 | 2017-02-07 17:23 | 2017-02-07 23:15 | 352 | 11kV | 10284 | 42 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 170718 C Phase DOLF : 10 Amp tree fallen onto mains between poles EO-70010 & EO-70057 bringing causing grass fire. Excluded oms 1456956,1456961,1456965,1456974,1456981 | February | 2017 | 2017Q3 | 2017 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2017-02-07 | N | 244.8571 | N | 8 | N | N | 1.1101 | 39.4971 | 7515.2439
[7 empty] | 9511 | 10063 | 1456992 | 2017-02-07 19:51 | 2017-02-07 23:40 | 229 | 11kV | 3874 | 58 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa13 RE46763 Grants Keighly 0.3 tripped and locked out on SEF 11kV on the ground near PT61544. Appears to have come out on cirmp join See 1457249,50 exclude 1456992 | February | 2017 | 2017Q3 | 2017 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2017-02-07 | N | 66.7931 | N | 8 | N | N | 1.1101 | 39.4971 | 2831.0049
[7 empty] | 9466 | 9649 | 1457008 | 2017-02-07 22:47 | 2017-02-07 23:59 | 72 | 11kV | 72 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170719 Single phase DOLF : 10 Amp Excluded OMS 1457008 | February | 2017 | 2017Q3 | 2017 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2017-02-07 | N | 72 | N | 8 | N | N | 1.1101 | 39.4971 | 52.6155
[7 empty] | 9971 | 15560 | 1457022 | 2017-02-08 05:09 | 2017-02-08 06:12 | 63 | 11kV | 101304 | 1608 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn12570 Avoca 11kv fdr panel 22 "Davies WIlima" fdr tripped to lock out X1 Relays: B and C phase overcurrent EFI's Burnt tree branch found adjacent to AB40388 | February | 2017 | 2017Q3 | 2017 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2017-02-08 | N | 63 | N | 4 | N | N | 1.1101 | 39.4971 | 74029.9752
[7 empty] | 9790 | 13554 | 1457014 | 2017-02-08 02:01 | 2017-02-08 07:20 | 319 | 11kV | 149122 | 865 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Heavy | N | iR63273 Sutherland Mitchell tripped, reclosed, tripped and locked out on: IOC trip AB35085 failed. Normally open AB between P24 and P31. See1457012 See 1460002 1460003 1460004 | February | 2017 | 2017Q3 | 2017 | ZN9252:PA24 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Not Veg | 2017-02-08 | N | 172.3954 | N | 4 | N | N | 1.1101 | 39.4971 | 108973.9592
[7 empty] | 9789 | 13553 | 1457012 | 2017-02-08 02:01 | 2017-02-08 07:20 | 319 | 11kV | 104582 | 582 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Heavy | N | iR63274 Soldier Washington tripped and reclosed on: IOC trip PT9077 Soldier Rd - Centre phase HDO operated AB35085 and 11kV UGOH in Wolger Rd near Bulumin St Failed. See 1460009 1460010 | February | 2017 | 2017Q3 | 2017 | ZN9252:PA31 | ZN9252:PA31 | ZN09252/000031 | SUTHERLAND | OH | Not Veg | 2017-02-08 | N | 179.6942 | N | 4 | N | N | 1.1101 | 39.4971 | 76425.441
[7 empty] | 9436 | 9253 | 1457122 | 2017-02-08 10:01 | 2017-02-08 11:17 | 76.0167 | 11kV | 7829.7167 | 103 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 170727 2 fault operations B & C phase Overcurrent Burnt bark found at pole GS-51304. Fault current Bph 853A/Cph 854A | February | 2017 | 2017Q3 | 2017 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2017-02-08 | N | 76.0167 | N | 4 | N | N | 1.1101 | 39.4971 | 5721.726
[7 empty] | 10122 | 17505 | 1457464 | 2017-02-09 10:30 | 2017-02-09 12:15 | 105 | 11kV | 12002 | 133 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn167 Auburn Panel 11 "S.1923 Beaconsfield Silver" feeder has tripped on: Signals: 11kv trip, Tx3 Group Earth Relays: EFI, EF, OC, Fault Check, Field EFis: S1923 Remarks: UG cable damaged by contractor. Nanwal Electrical solutions (#OMS 1457469) was putting in a new private pole at #117-119 Silverwater Rd, Silverwater. Adj S1665 Wiblin St Dop's could see burns marks around hole. 11kv Section of feeder from Sw/A @ S1923 Beaconsfield Silver to Sw/B @ S1665 Wiblin St, to Sw/A @ S35737 Stanley Carnarvon | February | 2017 | 2017Q3 | 2017 | ZN167:PA11 | ZN167:PA11 | ZN00167/000011 | PARRAMATTA | UG | Not Veg | 2017-02-09 | N | 90.2406 | N | 7 | N | N | 1.1101 | 39.4971 | 8770.7076
[7 empty] | 10284 | 19363 | 1457823 | 2017-02-09 08:12 | 2017-02-09 13:50 | 338 | 11kV | 2028 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Planned LID 170741 SINO 17852 | February | 2017 | 2017Q3 | 2017 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2017-02-09 | N | 338 | N | 7 | N | N | 1.1101 | 39.4971 | 1482.0026
[7 empty] | 9156 | 6086 | 1459353 | 2017-02-09 13:28 | 2017-02-09 14:00 | 32 | 11kV | 480 | 15 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 170751/02 A Phase DOLF : 10 Amp Line fuse blew when surge arrestor failed. | February | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-02-09 | N | 32 | N | 7 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 9423 | 9111 | 1459351 | 2017-02-09 12:11 | 2017-02-09 15:40 | 209 | 11kV | 209 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 170751 Single phase DOLF : 10 Amp Faulty LA at sub 71457. Excluded OMS No. 1457515 | February | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-02-09 | N | 209 | N | 7 | N | N | 1.1101 | 39.4971 | 152.731
[7 empty] | 9148 | 5961 | 1457627 | 2017-02-09 16:38 | 2017-02-09 16:59 | 21 | 11kV | 22197 | 1057 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LB497 Roadside Contact melted ex Panel 8 LB497 Galston Cause: Air break switch failed Abnormal Switching: LB62159 Closed, LB3210 opened for work LB1236 Closed, LB8961 Open for Work LB62158 Closed, LB314 Open For Work 1457644 1457643 1457639 1457638 1457636 1457635 1457629 1457627 | February | 2017 | 2017Q3 | 2017 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2017-02-09 | N | 21 | N | 7 | N | N | 1.1101 | 39.4971 | 16220.9129
[7 empty] | 9609 | 11379 | 1457611 | 2017-02-09 16:25 | 2017-02-09 17:45 | 80 | 11kV | 240 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170850 B Phase DOLF : 10 Amp Excluded OMS 1457611 | February | 2017 | 2017Q3 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2017-02-09 | N | 80 | N | 7 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 9574 | 10921 | 1457754 | 2017-02-09 21:11 | 2017-02-09 21:20 | 9 | 11kV | 25398 | 2822 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn15006 Dee Why Zone Panel 15 "Hall Stella" tripped on Sensitive Earth whilst switching out section of Panel 12L due to incorrect plugging due to pins which had fallen out of board Abnormal: AB22172 open AB22011 closed, S16932:B closed, S17057:B open See 1460088 exclude 1457754,81,2,3,4,6,91,2,3 | February | 2017 | 2017Q3 | 2017 | ZN15006:PA15 | ZN15006:PA15 | ZN15006/000015 | NORTHERN BEACHES | Unknown | Not Veg | 2017-02-09 | N | 9 | N | 7 | N | N | 1.1101 | 39.4971 | 18560.1093
[7 empty] | 9650 | 11780 | 1457892 | 2017-02-10 11:37 | 2017-02-10 13:02 | 85 | 11kV | 2618 | 34 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | Hot >35C | N | LID 170771 2 fault operation Overcurrent Stay at pole BN-50018 let go into OH Fdr 48056. Excluded OMS No. 1457892 Line crew in the vicinity heard a load bang and found a broken stay wire laying against 11kV mains. A small fire had broken out and was quickly extinguished by them. It was noticed that the19/2.00 steel stay wire broke where it bends around the thimble the thimble and stay wire showed signs of rust.The stay wire fell down between between the 66kV mains off a vertical term. without making contact or causing an interruption to the 66kV feeder, the 11kV feeder locked out | February | 2017 | 2017Q3 | 2017 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Not Veg | 2017-02-10 | N | 77 | N | 19 | N | N | 1.1101 | 39.4971 | 1913.1572
[7 empty] | 9161 | 6146 | 1457900 | 2017-02-10 11:59 | 2017-02-10 13:13 | 74 | 11kV | 72284 | 1015 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn15014 Mona Vale 11kv Panel 9 "Mona Vale Pittwater etc" CB tripped on Signals: 11kv trip, Zone Earth Relays: Panel 9L, BU, OC - trip, EFI, 150TN, frame leakage EFI's: S17061 S49359 S15853 S16465 11kv UG Fault from S16465:B and S15289:A and LB62890 See 1459495,6 exclude 1457900 | February | 2017 | 2017Q3 | 2017 | ZN15014:PA9 | ZN15014:PA8 | ZN15014/000008 | NORTHERN BEACHES | UG | Not Veg | 2017-02-10 | N | 71.2158 | N | 19 | N | N | 1.1101 | 39.4971 | 52823.0152
[7 empty] | 9644 | 11716 | 1457990 | 2017-02-10 16:24 | 2017-02-10 17:23 | 59 | 11kV | 54781.5667 | 975 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Ex Zn12620 Noraville section of Pa1R "Hutton Rd" 11kV Re47818 Wilfred Barrett Terilbah tripped and locked out NOTe: SEL/REC @RE4788 Wilfred Barrett Terilbah is normally N/A Relays: Earth Fault, IOC, Lockout, Aux, Supply Fail EFI's: Nil Open Bond - bottom roadside phase on the line side to RE47818 WIlfred Berratt Terilbah See 1457990 exclude 1458002 | February | 2017 | 2017Q3 | 2017 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2017-02-10 | N | 56.1862 | N | 19 | N | N | 1.1101 | 39.4971 | 40032.7531
[7 empty] | 9270 | 7189 | 1458059 | 2017-02-10 17:58 | 2017-02-10 18:07 | 9 | 11kV | 17995 | 2517 | HV | Staff Operation | Utility Process Issue | Circuit Breaker | Unplanned | Hot >35C | N | At Zn35800 Bankstown Panel 1L 'S35208' feeder was opned to prevent cable damage Remarks: Overload | February | 2017 | 2017Q3 | 2017 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2017-02-10 | N | 7.1494 | N | 19 | N | N | 1.1101 | 39.4971 | 13150.2152
[7 empty] | 8945 | 3311 | 1458013 | 2017-02-10 17:53 | 2017-02-10 18:10 | 17 | 11kV | 1486 | 134 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 170782 3 phase Earth Fault, Overcurrent ugoh blown at pole FS-92713 Excluded oms 1458018,1458024,1458013 | February | 2017 | 2017Q3 | 2017 | 504:48027 | 522:83130 | ZN00522/083130 | CESSNOCK | OH | Not Veg | 2017-02-10 | N | 11.0896 | N | 19 | N | N | 1.1101 | 39.4971 | 1085.925
[7 empty] | 9822 | 13857 | 1458087 | 2017-02-10 18:25 | 2017-02-10 18:31 | 6 | 11kV | 3264 | 544 | HV | Overload | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 170774 1 fault operation Overcurrent overload during parrallel for load relief on feeder 83309. also see report # 170773/OMS 1459017 | February | 2017 | 2017Q3 | 2017 | 532:83309 | 532:83309 | ZN00532/083309 | PORT STEPHENS | OH | Not Veg | 2017-02-10 | N | 6 | N | 19 | N | N | 1.1101 | 39.4971 | 2385.2349
[7 empty] | 10318 | 19809 | 1459017 | 2017-02-10 18:25 | 2017-02-10 18:32 | 7 | 11kV | 16093 | 2299 | HV | Overload | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 170773 1 fault operation Overcurrent overload during parrallel for load relief on feeder 83309. also see report # 170774 | February | 2017 | 2017Q3 | 2017 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2017-02-10 | N | 7 | N | 19 | N | N | 1.1101 | 39.4971 | 11760.2897
[7 empty] | 8916 | 2891 | 1458080 | 2017-02-10 18:20 | 2017-02-10 18:46 | 26 | 11kV | 36538 | 1504 | HV | Staff Operation | Utility Process Issue | Circuit Breaker | Unplanned | Hot >35C | N | At Zn2835 Burwood Panel 10 'S3315' feeder was opened due to high load. Remarks: Overload | February | 2017 | 2017Q3 | 2017 | ZN2835:PA10 | ZN2835:PA10 | ZN02835/000010 | STRATHFIELD | Unknown | Not Veg | 2017-02-10 | N | 24.2939 | N | 19 | N | N | 1.1101 | 39.4971 | 26700.8927
[7 empty] | 10005 | 16047 | 1458038 | 2017-02-10 17:30 | 2017-02-10 19:35 | 125 | 11kV | 114102 | 1572 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn3154 St Ives 11kV Panel 5 "Collins Killerton" tripped Relays: A Phase timed overcurrent, Earth Fault, EFI EFIs: S4263 S7319 S61479 S8717 S8276 11kv Panel 14 "Carbeen Killerton" tripped Relays: A Phase timed overcurrent, Earth Fault, EFI EFIs: S4917 S4910 S4264 Abnormal: Panel 5 and Panel 14 tied together for replugging to transfer bar for load relief, UGOH fialed on radial section of Panel 5, protection N/A for swithcing. 11kv UGOH failed on section of 11kv fdr from S8276 Warrimoo Priory to AB2514 tee PT1291 Tomah St Sww 1459514,6,7,8,9 exclude 1458038,9,42,3,4,5,75 | February | 2017 | 2017Q3 | 2017 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | Unknown | Unknown | 2017-02-10 | N | 72.584 | N | 19 | N | N | 1.1101 | 39.4971 | 83382.3762
[7 empty] | 8899 | 2751 | 1458066 | 2017-02-10 18:08 | 2017-02-10 19:40 | 92 | 11kV | 552 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Hot >35C | N | LID 170778 A Phase DOLF : 16 Amp dolf carrier broken in half Excluded oms 1458066 | February | 2017 | 2017Q3 | 2017 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2017-02-10 | N | 92 | N | 19 | N | N | 1.1101 | 39.4971 | 403.3853
[7 empty] | 10170 | 18039 | 1458017 | 2017-02-10 17:04 | 2017-02-10 19:48 | 164 | 11kV | 820 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | Ex Zn14891 Wyong section of Pa20 Warnervale West Railway" PT14723 Hue Hue Jilliby 0.2N 11kV HDO 16K Brown Boveri (footpath phase) Fuse Fatigue See 1459523 exclude 1458017,73 | February | 2017 | 2017Q3 | 2017 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2017-02-10 | N | 164 | N | 19 | N | N | 1.1101 | 39.4971 | 599.2318
[7 empty] | 10010 | 16180 | 1458074 | 2017-02-10 18:14 | 2017-02-10 19:50 | 96 | 11kV | 96 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170780 A Phase DOLF : 10 Amp | February | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-02-10 | N | 96 | N | 19 | N | N | 1.1101 | 39.4971 | 70.154
[7 empty] | 9432 | 9229 | 1459920 | 2017-02-10 21:09 | 2017-02-10 21:13 | 4 | 11kV | 3744 | 936 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | Ex Zn12650 West Gosford section of Panel 13 "Hanlan St" 11kV RE62730 Mann Narrara Creek opened Staff Error. DOp switching out of sequence. Miscommunication on relief & restoration switching | February | 2017 | 2017Q3 | 2017 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | Unknown | Not Veg | 2017-02-10 | N | 4 | N | 19 | N | N | 1.1101 | 39.4971 | 2736.0048
[7 empty] | 10121 | 17486 | 1458032 | 2017-02-10 16:58 | 2017-02-10 21:26 | 268 | 11kV | 273847 | 1273 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn12650 West Gosford 11kv Panel 6 "S11794 SCC Racecourse" tripped, reclosed & tripped Relays: delayed operate timer, lockout, EFI, Earth Fault Signals: 11kv trip EFI's: S11794 11kv UGOH Fault leading to S14851:A Lindsey Mann See 1459503,5,6,7,8 Exclude 1458016,40 | February | 2017 | 2017Q3 | 2017 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | Unknown | Unknown | 2017-02-10 | N | 215.1194 | N | 19 | N | N | 1.1101 | 39.4971 | 200119.3105
[7 empty] | 9434 | 9241 | 1458111 | 2017-02-10 19:05 | 2017-02-10 22:00 | 175 | 11kV | 11900 | 68 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | 11kV Bond bond failed on pole EP00481 Abnormal swithcing CB78030 Closed with SW/A open at S2696 Cause: Bond failed See OMS 1463288 1458111 | February | 2017 | 2017Q3 | 2017 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Not Veg | 2017-02-10 | N | 175 | N | 19 | N | N | 1.1101 | 39.4971 | 8696.169
[7 empty] | 9831 | 13961 | 1458076 | 2017-02-10 18:14 | 2017-02-10 22:30 | 256 | 11kV | 207950 | 1552 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Hot >35C | N | At Zn35900 Potts Hill Panel 2L "Ab 2024" feeder has tripped Signals: 11kv trip Relays: SEF trip, EFI, EFC Field EFIs: Nil Remarks: 11kv road side HDO has failed @ PT 1185 Whiting St. 11kv surge arrestor on UGOH above Sw/A @ S3949 Edwin King has failed. AB 2024 fell apart on opening | February | 2017 | 2017Q3 | 2017 | ZN35900:PA2 | ZN35900:PA2 | ZN35900/000002 | CUMBERLAND | OH | Not Veg | 2017-02-10 | N | 133.9884 | N | 19 | N | N | 1.1101 | 39.4971 | 151963.7265
[7 empty] | 8984 | 3807 | 1458173 | 2017-02-10 20:57 | 2017-02-11 03:08 | 371 | 11kV | 8999 | 42 | HV | Vegetation Grow In | Vegetation | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 170790 Overcurrent Tree grown into mains Excluded 1458173 | February | 2017 | 2017Q3 | 2017 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2017-02-10 | N | 214.2619 | N | 19 | N | N | 1.1101 | 39.4971 | 6576.2038
[7 empty] | 9431 | 9222 | 1458235 | 2017-02-11 07:26 | 2017-02-11 09:50 | 144 | 11kV | 576 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170791 A Phase DOLF : 20 Amp Excluded OMS 1458235 | February | 2017 | 2017Q3 | 2017 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2017-02-11 | N | 144 | N | 11 | N | N | 1.1101 | 39.4971 | 420.9238
[7 empty] | 9564 | 10818 | 1458238 | 2017-02-11 07:46 | 2017-02-11 11:50 | 244 | 11kV | 453678 | 3617 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Hot >35C | N | At S35500 Top Ryde Panel 28 tripped, reclosed, tripped and locked out on Relays: Panel 28L. A and B phase IOC timing and lockout Cause: head of Pole snap[ped off section of feeder before AB942 Abnormal swicthing: Load relief, S3991 SW/A closed, SW/B Open See OMS 1459684 1459686 1459687 1458238 1458262 | February | 2017 | 2017Q3 | 2017 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2017-02-11 | N | 125.4294 | N | 11 | N | N | 1.1101 | 39.4971 | 331534.5012
[7 empty] | 9157 | 6096 | 1458088 | 2017-02-10 19:34 | 2017-02-11 12:40 | 1026 | 11kV | 126768 | 1022 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | LID 170788 B Phase Earth Fault blown ugoh at East Maitland Bowling Club Excluded oms 1458130,14458135,1458138 | February | 2017 | 2017Q3 | 2017 | 532:83301 | 532:83301 | ZN00532/083301 | MAITLAND | Unknown | Unknown | 2017-02-10 | N | 124.0391 | N | 19 | N | N | 1.1101 | 39.4971 | 92638.3154
[7 empty] | 9196 | 6405 | 1458123 | 2017-02-10 19:20 | 2017-02-11 14:55 | 1175 | 11kV | 101973 | 1067 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Hot >35C | N | At S847 Hornsby panel 47 tripped, reclosed, tripped and locked out on B and C phase O/C, Lockout, reclose timing Cause: Pole failure O/S 42 Beaumont Rd Mount Kuringai. ( Section of feeder from AB466 to CP1262 tee PT1966) HV into LV See OMS 1460177 1460178 1458498 1458192 | February | 2017 | 2017Q3 | 2017 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Not Veg | 2017-02-10 | N | 95.5698 | N | 19 | N | N | 1.1101 | 39.4971 | 74518.8607
[7 empty] | 8757 | 738 | 1459693 | 2017-02-11 17:35 | 2017-02-11 18:00 | 25 | 11kV | 6775 | 271 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | AOp requested DOp to Open LB797 Intrerrupting 3 DCs and Close SW/B @ S8664. Cause: Feeder wahs shed - Multiple DMA's Dump and Restore | February | 2017 | 2017Q3 | 2017 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | Unknown | Unknown | 2017-02-11 | N | 25 | N | 11 | N | N | 1.1101 | 39.4971 | 4950.9702
[7 empty] | 9486 | 9846 | 1458439 | 2017-02-11 17:23 | 2017-02-11 18:04 | 41 | 11kV | 26204 | 647 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | LID 170799 1 fault operation B Phase Earth Fault FAULTY CABLE TERMINATION AT SW 28993. IEF A & B PROT. Excluded OMS REPORTS 1458439 & 1458445. | February | 2017 | 2017Q3 | 2017 | 532:83295 | 532:83295 | ZN00532/083295 | MAITLAND | UG | Not Veg | 2017-02-11 | N | 40.5008 | N | 11 | N | N | 1.1101 | 39.4971 | 19149.1103
[7 empty] | 9289 | 7350 | 1458524 | 2017-02-11 19:33 | 2017-02-11 20:55 | 82 | 11kV | 91196 | 1313 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | LID 170804 2 Fault Operations 3 phase Overcurrent; Earth Fault FAULTY UGOH AT POLE FS-51403.ERC ADVISED. Excluded OMS REPORTS 1458524,1458547,1458534,1458537,1458526. | February | 2017 | 2017Q3 | 2017 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | Unknown | Unknown | 2017-02-11 | N | 69.4562 | N | 11 | N | N | 1.1101 | 39.4971 | 66643.347
[7 empty] | 8981 | 3765 | 1458433 | 2017-02-11 17:13 | 2017-02-11 21:10 | 237 | 11kV | 1896 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170806 C Phase DOLF : 10 Amp | February | 2017 | 2017Q3 | 2017 | 233:82819 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2017-02-11 | N | 237 | N | 11 | N | N | 1.1101 | 39.4971 | 1385.5409
[7 empty] | 9683 | 12192 | 1458490 | 2017-02-11 18:44 | 2017-02-11 22:00 | 196 | 11kV | 18440 | 194 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 170805 A Phase Hazemeyer fuse : 31 Amp 11kV section deenergised to replace Hazemeyer Switch Fuse. Excluded OMS No. 1458490 | February | 2017 | 2017Q3 | 2017 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2017-02-11 | N | 95.0515 | N | 11 | N | N | 1.1101 | 39.4971 | 13475.4081
[7 empty] | 9536 | 10422 | 1458470 | 2017-02-11 18:52 | 2017-02-11 22:30 | 218 | 11kV | 234614 | 1245 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Hot >35C | N | At Zn847 Hornsby Panelo 46 tripped on SEF, Fault Check, EFI and Lockout Field EFI's NIL at PT2192 Mount Lady - Footpath HDO operated Cause: At PT2192 Mount Lady suspect TX Fault. See OMS 1460184 1460186 1460185 1458498 1458501 1458470 | February | 2017 | 2017Q3 | 2017 | ZN847:PA46 | ZN847:PA46 | ZN00847/000046 | HORNSBY | OH | Not Veg | 2017-02-11 | N | 188.445 | N | 11 | N | N | 1.1101 | 39.4971 | 171448.9913
[7 empty] | 9655 | 11829 | 1459933 | 2017-02-12 00:05 | 2017-02-12 00:10 | 5 | 11kV | 385 | 77 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | Ex Zn14891 Wyong section of Pa5 Re45016 Dickson has tripped and reclosed on OC trip Cause not ascertained. Mains to Patrol | February | 2017 | 2017Q3 | 2017 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2017-02-12 | N | 5 | N | 15 | N | N | 1.1101 | 39.4971 | 281.3466
[7 empty] | 9191 | 6369 | 1458242 | 2017-02-11 17:41 | 2017-02-12 00:47 | 426 | 11kV | 762084 | 3621 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | At Zn35500 Top Ryde Panel 28 tripped and locked out Relays: IOC A and C phase, Lockout and Training Abnormal Switching -S3991 SW/A Open, SW/B Closed - Load Relief -LB797 Open, S8664 SW/B Closed - Load Relief -CP50192 Closed, SW/B open at S49354 - S46858 to CP2173 to CP942 defective - CP1476 Closed Cause: 11kV bond failed at AB1753. Linesman has deemed AB not servicable and bonded through See OMS 1459871 1459872 1459873 1459874 1458330 1458469 1458598 1458461 | February | 2017 | 2017Q3 | 2017 | ZN35500:PA28 | ZN35500:PA36 | ZN35500/000036 | RYDE | OH | Not Veg | 2017-02-11 | N | 210.4623 | N | 11 | N | N | 1.1101 | 39.4971 | 556908.5095
[7 empty] | 9391 | 8710 | 1458538 | 2017-02-11 19:54 | 2017-02-12 01:55 | 361 | 11kV | 19333 | 154 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | ex Panel 6 @ Zn 4545 Meadowbank At S5235 Ryde Eastwood leagues 11kV HV fuse blown Cause: Fuse fatigue Note: PT1714 Anzac Orchard interrupted to replace fuse See OMS 1460218 1460220 1458538 1458616 | February | 2017 | 2017Q3 | 2017 | ZN4545:PA6 | ZN4545:PA6 | ZN04545/000006 | RYDE | OH | Not Veg | 2017-02-11 | N | 125.539 | N | 11 | N | N | 1.1101 | 39.4971 | 14127.9862
[7 empty] | 9769 | 13286 | 1458649 | 2017-02-12 01:50 | 2017-02-12 03:03 | 73 | 11kV | 162133 | 2221 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn12570 Avoca 11kv Panel 21 tripped/reclsoed/tripped on A&B phase IOC, EFI, Rec L/O & 11kv trip EFI's: S64802 Tree/branch on OH Mains. Kings Ave - removed by DOp See 1458649 exclude 1458651 | February | 2017 | 2017Q3 | 2017 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Veg | 2017-02-12 | N | 73 | N | 15 | N | N | 1.1101 | 39.4971 | 118482.0143
[7 empty] | 9719 | 12524 | 1458405 | 2017-02-11 17:03 | 2017-02-12 08:25 | 922 | 11kV | 502189 | 2033 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Hot >35C | N | At Zn1285 Greenacre Park Panel 31 'S4862' Feeder tripped Signals: 11kv trip Relays: A ph timed and IOC, EFI Field EFI's: S4862 Abnormals: Sw/B closed @ S8932, Sw/A Open @ S35888 Remarks: Fire, Haz RMI @ S4867 Acacia Wilbur has caught fire and exploded | February | 2017 | 2017Q3 | 2017 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-02-11 | N | 247.0187 | N | 11 | N | N | 1.1101 | 39.4971 | 366984.9091
[7 empty] | 9031 | 4434 | 1458624 | 2017-02-12 00:05 | 2017-02-12 10:10 | 605 | 11kV | 58919 | 467 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Ex Zn14891 Wyong section of Pa12 IR48838 Yarramalong Maitland 1.2 triped on overcurrent Tree hit HV bringing down conductors & damaging 2 x HV X-arms between CP48838 and AB43742 See 1459928,9,30,1 exclude 1458624 | February | 2017 | 2017Q3 | 2017 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2017-02-12 | N | 126.1649 | N | 15 | N | N | 1.1101 | 39.4971 | 43056.2674
[7 empty] | 10364 | 20390 | 1458734 | 2017-02-12 10:46 | 2017-02-12 12:34 | 108 | 11kV | 81000 | 750 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Ex 11kV Panel 27 Top Ryde 11kV bond burnt off footpath side of UGOH below S4341 Berripa Close Cause: 11kV bond burnt off footpath side of UGOH below S4341 Berripa Close See OMS 1460324 1458734 | February | 2017 | 2017Q3 | 2017 | ZN35500:PA27 | ZN35500:PA27 | ZN35500/000027 | RYDE | OH | Not Veg | 2017-02-12 | N | 108 | N | 15 | N | N | 1.1101 | 39.4971 | 59192.4109
[7 empty] | 9329 | 7834 | 1458735 | 2017-02-12 11:03 | 2017-02-12 15:30 | 267 | 11kV | 801 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 170815 Broken LL lead HV issue. Liveline break at pole 8N60494 Excluded OMS 1458735 | February | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-02-12 | N | 267 | N | 15 | N | N | 1.1101 | 39.4971 | 585.3472
[7 empty] | 9342 | 7955 | 1458789 | 2017-02-12 14:41 | 2017-02-12 16:45 | 124 | 11kV | 5903 | 197 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 170813 1 fault operation Overcurrent; Earth Fault pole & grass fire, mains down at pole SF-10231 Excluded OMS 1458789 | February | 2017 | 2017Q3 | 2017 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2017-02-12 | N | 29.9645 | N | 15 | N | N | 1.1101 | 39.4971 | 4313.7383
[7 empty] | 10100 | 17250 | 1459724 | 2017-02-12 16:47 | 2017-02-12 17:19 | 32 | 11kV | 1152 | 36 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn3288 City South 11kV CB 41/42 K feeder operated on:41K E/F Fuse relay Zn4990 City Central 11kV "D-3" bus section CB, 51/52D, 55/56D operated Staff error. S6510 resotred via LV bus section links (2 Tx Sub) See 1459725 1459724 | February | 2017 | 2017Q3 | 2017 | ZN3288:PA41 42KLM | ZN3288:PA41 42KLM | ZN03288/41 42KLM | SYDNEY | Unknown | Not Veg | 2017-02-12 | N | 32 | N | 15 | N | N | 1.1101 | 39.4971 | 841.8476
[7 empty] | 10001 | 15983 | 1458808 | 2017-02-12 15:55 | 2017-02-12 18:04 | 129 | 11kV | 35629 | 279 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Rec554 Arcadia Rosscommon tripped and locked out on IOC trip. Cause not ascertained - DOp patrolled See OMS 1460332 1460334 1458808 | February | 2017 | 2017Q3 | 2017 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2017-02-12 | N | 127.7025 | N | 15 | N | N | 1.1101 | 39.4971 | 26036.6223
[7 empty] | 8750 | 667 | 1458775 | 2017-02-12 13:31 | 2017-02-12 19:45 | 373.5833 | 11kV | 6350.9167 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 170814 A Phase DOLF : 5 Amp | February | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | SINGLETON | OH | Veg | 2017-02-12 | N | 373.5833 | N | 15 | N | N | 1.1101 | 39.4971 | 4641.0626
[7 empty] | 10034 | 16404 | 1458894 | 2017-02-12 18:27 | 2017-02-12 20:05 | 98 | 11kV | 54771 | 767 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty Zone section of Pa6 "Rhodin Drive" fdr recloser had tripped, reclosed, tripped & locked out RE62166 Watkins Thompson Relays: OC trip Current A phase-53 B Phase-2982 C Phase-3021 Broken HV X-arm between LK43389 to LB61958 to LB42551 to AB40998. Tee PT13399 Anzac Rhodin. 1 span south of HV USL43389, isolation extended for safety beyond USL 43389 See 1459963,9,70,1,2 exclude 1458894 | February | 2017 | 2017Q3 | 2017 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Not Veg | 2017-02-12 | N | 71.4094 | N | 15 | N | N | 1.1101 | 39.4971 | 40025.0313
[7 empty] | 9654 | 11813 | 1458771 | 2017-02-12 13:25 | 2017-02-12 20:50 | 445 | 11kV | 38480 | 98 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 170816 1 fault operation Overcurrent; Earth Fault Tree on OHM at pole 9U-10043 | February | 2017 | 2017Q3 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-02-12 | N | 392.6531 | N | 15 | N | N | 1.1101 | 39.4971 | 28120.049
[7 empty] | 9537 | 10428 | 1458819 | 2017-02-12 15:56 | 2017-02-12 21:05 | 309 | 11kV | 37956 | 724 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Insulated | Unplanned | No Weather Impact | N | Zn14143 Somersby Panel 17 "Somersby Falls" fdr has tripped on Signals: Relays: SEL Trip (SPAC 653 C3 Relays) EFI:Nil Tree Branch on HV Main between HV USL 42146 & PT11872 Wirrinda Debenham, WIre Down See 1458819,49 | February | 2017 | 2017Q3 | 2017 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2017-02-12 | N | 52.4254 | N | 15 | N | N | 1.1101 | 39.4971 | 27737.1253
[7 empty] | 10329 | 19986 | 1458877 | 2017-02-12 17:53 | 2017-02-12 22:05 | 252 | 11kV | 504 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Hot >35C | N | LID 170817 Single phase DOLF : 10 Amp Blown LA changed under AP | February | 2017 | 2017Q3 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2017-02-12 | N | 252 | N | 15 | N | N | 1.1101 | 39.4971 | 368.3083
[7 empty] | 9309 | 7536 | 1458859 | 2017-02-12 17:14 | 2017-02-13 02:15 | 541 | 11kV | 38114 | 244 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Rec 421 Crosslands Rd tripped, reclosed tripped and locked out on O/C trip Cause: tree branch on OH Mains in crosslands rd Galston See OMS146036 1450361 1458859 1458891 1458863 | February | 2017 | 2017Q3 | 2017 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2017-02-12 | N | 156.2049 | N | 15 | N | N | 1.1101 | 39.4971 | 27852.587
[7 empty] | 8871 | 2403 | 1459022 | 2017-02-13 10:09 | 2017-02-13 11:00 | 51 | 11kV | 4845 | 95 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170823 A Phase DOLF : 63Amp Excluded OMS 1459022 | February | 2017 | 2017Q3 | 2017 | 524:33578 | 524:33578 | ZN00524/033578 | CESSNOCK | OH | Veg | 2017-02-13 | N | 51 | N | 7 | N | N | 1.1101 | 39.4971 | 3540.5831
[7 empty] | 10324 | 19872 | 1458956 | 2017-02-13 08:05 | 2017-02-13 11:35 | 210 | 11kV | 210 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 170824 Single phase DOLF : 3 Amp SUB ISOLATED TO REPLACE 2 X ARRESTORS, 2 X DOLFS Excluded OMS 1458956 | February | 2017 | 2017Q3 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2017-02-13 | N | 210 | N | 7 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 9764 | 13234 | 1459026 | 2017-02-13 10:21 | 2017-02-13 12:55 | 154 | 11kV | 154 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 170827 A Phase DOLF : 10 Amp Excluded OMS 1459026 | February | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-02-13 | N | 154 | N | 7 | N | N | 1.1101 | 39.4971 | 112.5387
[7 empty] | 10084 | 16992 | 1458913 | 2017-02-12 21:18 | 2017-02-13 13:50 | 992 | 11kV | 1984 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170828 Single phase DOLF : 5 Amp Excluded OMS 1458913 | February | 2017 | 2017Q3 | 2017 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2017-02-12 | N | 992 | N | 15 | N | N | 1.1101 | 39.4971 | 1449.8487
[7 empty] | 9949 | 15285 | 1459088 | 2017-02-13 12:28 | 2017-02-13 18:45 | 377 | 11kV | 377 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 170830 A Phase A phase LLC burnt off. All 3 replaced under AP. Excluded OMS 1459088 | February | 2017 | 2017Q3 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2017-02-13 | N | 377 | N | 7 | N | N | 1.1101 | 39.4971 | 275.5005
[7 empty] | 10304 | 19608 | 1459180 | 2017-02-13 16:25 | 2017-02-13 18:55 | 150 | 11kV | 300 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | Ex ZN12630 Peats Ridge section of Panel 8 "Kulnura Fdr" PT18214 Springs Greta had to be interrutped for safety due to High Voltage Issue (PT is non paralleling) Fdr had to be interrupted for safety 11kv Bare mains Droppers clashing at PT13229 Greta Springs 0.3 See also SOP arrange #399285A. DAROS 399285 EMERGENCY WORKS - PT13229[R] - GRETA SPRINGS 0.3 Cause mutilple trips of IR49506 Springs Rd. | February | 2017 | 2017Q3 | 2017 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2017-02-13 | N | 150 | N | 7 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 8730 | 170 | 1459202 | 2017-02-13 18:09 | 2017-02-13 19:25 | 76 | 11kV | 15656 | 206 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 51 tripped on SEL Cause Not ascertained Dop Patrolled See OMS 1463220 1459202 | February | 2017 | 2017Q3 | 2017 | ZN129:PA27 | ZN129:PA51 | ZN00129/000051 | HUNTERS HILL | OH | Veg | 2017-02-13 | N | 76 | N | 7 | N | N | 1.1101 | 39.4971 | 11440.943
[7 empty] | 10293 | 19507 | 1459069 | 2017-02-13 15:38 | 2017-02-13 19:30 | 232 | 11kV | 8837 | 77 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 "Wyong" fdr reclsoer has tripped, closed , tripped & locked out on RE45016 Dickson Relays: IOC trip, OC trip Tree on HV OH in bloomfield Rd near tee to CP44787 Bloomfield Rd See 1459991,2 exclude 1459069,187 | February | 2017 | 2017Q3 | 2017 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2017-02-13 | N | 114.7662 | N | 7 | N | N | 1.1101 | 39.4971 | 6457.819
[7 empty] | 9281 | 7242 | 1459256 | 2017-02-14 07:38 | 2017-02-14 08:28 | 50 | 11kV | 26350 | 527 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | EX Panel 1 Clarke Neutral from S847 Hornsby Arcing @ CP2392 Cause: IS2392 Close for Daros 398158. After isolations IS2392 found to be arcing and not suitable to carry load - Switching restored See OMS 1459281 1459270 1459277 1459275 1459272 1459271 1459256 | February | 2017 | 2017Q3 | 2017 | ZN847:PA1 | ZN847:PA1 | ZN00847/000001 | HORNSBY | OH | Not Veg | 2017-02-14 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 19255.8028
[7 empty] | 10227 | 18826 | 1459315 | 2017-02-14 09:35 | 2017-02-14 10:46 | 71 | 11kV | 15407 | 217 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | REC35260 Open & reclosed on: O/C Cause not ascertained | February | 2017 | 2017Q3 | 2017 | ZN9118:PA3 | ZN9118:PA3 | ZN09118/000003 | SUTHERLAND | OH | Veg | 2017-02-14 | N | 71 | N | 5 | N | N | 1.1101 | 39.4971 | 11258.9812
[7 empty] | 9528 | 10348 | 1459449 | 2017-02-14 13:58 | 2017-02-14 14:36 | 38 | 11kV | 38836 | 1022 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14144 Wamberal Panel 2 "Glen Eagles Fairway" fdr tripped and reclosed and tripped on Signals: 11kv trip Relays: A phase 7 B Phase Overcurrent, Reclose EFI: S14885 S11086 S12742 SPanel 2 Cause: tree branch on OH mains. Branch across phases at PT14614 | February | 2017 | 2017Q3 | 2017 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2017-02-14 | N | 38 | N | 5 | N | N | 1.1101 | 39.4971 | 28380.2033
[7 empty] | 10090 | 17139 | 1459566 | 2017-02-14 20:00 | 2017-02-14 22:10 | 130 | 11kV | 520 | 4 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Heavy | N | Ex Pnl20 @ Kirrawee Zone - 11kV feeder from S9764 (Sw/B) to AB 35151 tee PT9458 & PT9191 was interupted for safety AB35151 on pole SU04715 defective. | February | 2017 | 2017Q3 | 2017 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2017-02-14 | N | 130 | N | 5 | N | N | 1.1101 | 39.4971 | 380.0007
[7 empty] | 8780 | 1180 | 1459608 | 2017-02-15 02:39 | 2017-02-15 04:00 | 81 | 11kV | 107892 | 1332 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9252 Jannali - Pnl.30 tripped, reclosed and locked out on: IOC Possum contact 11kV UGOH in Leonay St near Tamar St | February | 2017 | 2017Q3 | 2017 | ZN9252:PA30 | ZN9252:PA30 | ZN09252/000030 | SUTHERLAND | OH | Not Veg | 2017-02-15 | N | 81 | N | 4 | N | N | 1.1101 | 39.4971 | 78844.2913
[7 empty] | 9190 | 6367 | 1459609 | 2017-02-15 04:37 | 2017-02-15 08:45 | 248 | 11kV | 23339 | 1356 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 170845/01/02 Trip & Reclose 1 fault operation B & C phase Overcurrent Bat contacted 11kV on corner of Leanard St and Myra Rd, and 11kV tapping then failed at pole FS-82135. | February | 2017 | 2017Q3 | 2017 | 524:33578 | 524:33572 | ZN00524/033572 | CESSNOCK | OH | Not Veg | 2017-02-15 | N | 17.2117 | N | 4 | N | N | 1.1101 | 39.4971 | 17055.4528
[7 empty] | 9449 | 9363 | 1459654 | 2017-02-15 08:59 | 2017-02-15 14:00 | 301 | 11kV | 301 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170859 A Phase Sectionaliser Suspected faulty sectionaliser as feeder did not have trip and reclose. Firing pin had fired. Please check and advise control room if it needs bypassing to avoid further spontaneous trips.Sect will be black pinned. Excluded OMS 1459654 | February | 2017 | 2017Q3 | 2017 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2017-02-15 | N | 301 | N | 4 | N | N | 1.1101 | 39.4971 | 219.9619
[7 empty] | 9619 | 11477 | 1459594 | 2017-02-14 22:51 | 2017-02-15 15:00 | 969 | 11kV | 33516 | 80 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of Pa24 RE47878 Pacific Palmdale 0.5S tripped and relcosed 3 times and locked out OH resting on cross arm See 1459997,9,60000,1 exclude 1459594,607 | February | 2017 | 2017Q3 | 2017 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2017-02-14 | N | 418.95 | N | 5 | N | N | 1.1101 | 39.4971 | 24492.5042
[7 empty] | 8987 | 3864 | 1459819 | 2017-02-15 17:21 | 2017-02-15 19:00 | 99 | 11kV | 175551 | 2167 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3155 Double Bay - Pnl.23 tripped on 23R leg with O/C, Earth Fault and EFI UG cable fault, front line section of feeder | February | 2017 | 2017Q3 | 2017 | ZN3155:PA23 | ZN3155:PA40 | ZN03155/000040 | WOOLLAHRA | UG | Not Veg | 2017-02-15 | N | 81.0111 | N | 4 | N | N | 1.1101 | 39.4971 | 128287.4929
[7 empty] | 9150 | 5987 | 1459953 | 2017-02-16 13:25 | 2017-02-16 14:22 | 57 | 11kV | 9975 | 175 | HV | Equipment Failed in Service | Equipment Failure | Tap Changer | Unplanned | No Weather Impact | N | LID 170876 Jerrys Plains reg 41021 caught fire. Fdr de energised to isolate reg & intellirupter. Bypass closed | February | 2017 | 2017Q3 | 2017 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | Unknown | Not Veg | 2017-02-16 | N | 57 | N | 5 | N | N | 1.1101 | 39.4971 | 7289.4358
[7 empty] | 9244 | 6954 | 1460013 | 2017-02-16 14:17 | 2017-02-16 15:29 | 72.0167 | 11kV | 1872.4333 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170872 C Phase DOLF : 10 Amp | February | 2017 | 2017Q3 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2017-02-16 | N | 72.0167 | N | 5 | N | N | 1.1101 | 39.4971 | 1368.3191
[7 empty] | 10025 | 16303 | 1460068 | 2017-02-16 15:41 | 2017-02-16 16:30 | 49 | 11kV | 637 | 13 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | No Weather Impact | N | LID 170873 Truck hit pole AN-90522, broke X-arm Excluded OMS 1460068 | February | 2017 | 2017Q3 | 2017 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2017-02-16 | N | 49 | N | 5 | N | N | 1.1101 | 39.4971 | 465.5008
[7 empty] | 8732 | 201 | 1462626 | 2017-02-16 13:25 | 2017-02-16 17:35 | 250 | 11kV | 250 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 170877 C Phase fuse : 64 Amp Excluded OMS 146063 | February | 2017 | 2017Q3 | 2017 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2017-02-16 | N | 250 | N | 5 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 8934 | 3107 | 1459998 | 2017-02-16 13:50 | 2017-02-16 17:51 | 240.75 | 11kV | 123140.75 | 1637 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S80 Chatswood Panel 24 tripped on on C phase OC and EF Cause: UG cable fault: Section of 11kV from S80 Chatswood Pa24 to S6969 to S49280 to S35060 See OMS 1462167 1459998 | February | 2017 | 2017Q3 | 2017 | ZN80:PA24 | ZN80:PA24 | ZN00080/000024 | WILLOUGHBY | UG | Not Veg | 2017-02-16 | N | 75.2234 | N | 5 | N | N | 1.1101 | 39.4971 | 89987.6281
[7 empty] | 8982 | 3773 | 1460155 | 2017-02-17 05:31 | 2017-02-17 05:57 | 26 | 11kV | 2236 | 86 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | Y | LID 170882 B Phase DOLF : 31 Amp Excluded OMS 1460155 | February | 2017 | 2017Q3 | 2017 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Veg | 2017-02-17 | N | 26 | N | 6 | N | N | 1.1101 | 39.4971 | 1634.0028
[7 empty] | 9716 | 12496 | 1460164 | 2017-02-17 07:11 | 2017-02-17 09:25 | 133.55 | 11kV | 133.55 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 170886 Single phase DOLF : 10 Amp Bird contacted mains blew DOLF. excluded OMS 1460163 | February | 2017 | 2017Q3 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2017-02-17 | N | 133.55 | N | 6 | N | N | 1.1101 | 39.4971 | 97.5944
[7 empty] | 10194 | 18473 | 1460225 | 2017-02-17 10:40 | 2017-02-17 11:20 | 40 | 11kV | 960 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 170902 A Phase DOLF : 40 Amp Excluded OMS 1460225 Note: start time amended from 17/02/17 10:39, as customers were affected by Panel level outage prior to this refer to OMS 1469192 | February | 2017 | 2017Q3 | 2017 | 224:80326 | 224:80326 | ZN00224/080326 | LAKE MACQUARIE | OH | Veg | 2017-02-17 | N | 40 | N | 6 | N | N | 1.1101 | 39.4971 | 701.5397
[7 empty] | 10158 | 17876 | 1460382 | 2017-02-17 15:00 | 2017-02-17 15:30 | 30 | 11kV | 30 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | replaced dolf element No LID raised | February | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2017-02-17 | Y | 30 | N | 6 | N | Y | 1.1101 | 39.4971 | 21.9231
[7 empty] | 10219 | 18746 | 1460424 | 2017-02-17 15:51 | 2017-02-17 16:15 | 24 | 11kV | 120 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | Y | LID 170986 Overcurrent; Earth Fault Fdr abnormal. First fault, burnt off tapping. Second fault, blown UGOH P: LI-40016 Excluded OMS 1460461, 1460424 ## | February | 2017 | 2017Q3 | 2017 | 514:18146 | 514:18156 | ZN00514/018156 | MUSWELLBROOK | OH | Not Veg | 2017-02-17 | Y | 24 | N | 6 | N | Y | 1.1101 | 39.4971 | 87.6925
[7 empty] | 8841 | 1896 | 1460401 | 2017-02-17 15:35 | 2017-02-17 16:41 | 66 | 11kV | 24486 | 371 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S35370 Galston Panel 2 tripped and lockout on A and C phase IOC and Lockout with 11kV trip Cause: tree branch on OH mains neae AB63806 | February | 2017 | 2017Q3 | 2017 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2017-02-17 | Y | 66 | N | 6 | N | Y | 1.1101 | 39.4971 | 17893.6466
[7 empty] | 9575 | 10938 | 1460429 | 2017-02-17 15:45 | 2017-02-17 18:00 | 135 | 11kV | 25245 | 187 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S35370 Galston ex Panel 10 IR50015 Quarry Rd Northern tripped and lockout out on OC Cause not ascertained for outage. Section of feeder isolated from LB62156 to IR2691. Feeder in Bushland and required daylight patrol | February | 2017 | 2017Q3 | 2017 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2017-02-17 | Y | 135 | N | 6 | N | Y | 1.1101 | 39.4971 | 18448.3014
[7 empty] | 9425 | 9118 | 1460830 | 2017-02-17 17:46 | 2017-02-17 18:50 | 64 | 11kV | 64 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 170909 A Phase DOLF : 10 Amp Excluded OMS 1460830 | February | 2017 | 2017Q3 | 2017 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2017-02-17 | Y | 64 | N | 6 | N | Y | 1.1101 | 39.4971 | 46.7693
[7 empty] | 10028 | 16311 | 1460696 | 2017-02-17 17:10 | 2017-02-17 19:06 | 116 | 11kV | 15507 | 191 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 170911 Mains on ground to sub 72427. Opened 74434 Riverview RAGCB for safety. At 1906 restored supply from Sw 74434 to all feeder except sub 72427. Will do separate job OMS 1461121 No Protection Operation. | February | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-02-17 | Y | 81.1885 | N | 6 | N | Y | 1.1101 | 39.4971 | 11332.0582
[7 empty] | 8865 | 2300 | 1460392 | 2017-02-17 15:02 | 2017-02-17 19:30 | 268 | 11kV | 64856 | 242 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | Y | Ex panel 21 @ Berowra 11kV bond let go at pole BE77694 (Below tee off to S2986) See OMS 1462826 1460392 1460399 | February | 2017 | 2017Q3 | 2017 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Not Veg | 2017-02-17 | Y | 268 | N | 6 | N | Y | 1.1101 | 39.4971 | 47394.8519
[7 empty] | 10342 | 20184 | 1460922 | 2017-02-17 18:13 | 2017-02-17 20:10 | 117 | 11kV | 819 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 170913 B phase DOLF : 10 Amp 10A B phase DOLF replaced at sub 70654 as well. Incompleted by G Lloyd Muswellbrook. | February | 2017 | 2017Q3 | 2017 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2017-02-17 | Y | 117 | N | 6 | N | Y | 1.1101 | 39.4971 | 598.501
[7 empty] | 10004 | 16046 | 1460422 | 2017-02-17 15:53 | 2017-02-17 20:15 | 262 | 11kV | 143877 | 694 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | Y | Zn3154 St Ives - Pnl.12 tripped, reclosed, tripped and locked out on:Earth Fault Field EFIs: S4112 (S35697 did not operate - defective) When Dop engergised feeder, explosion witnessed on footpath side phase of PT1500 @ HV cross arm (Lightning Arrestor) See 1462578 1462579 1462580 1462582 1462583 | February | 2017 | 2017Q3 | 2017 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Not Veg | 2017-02-17 | N | 207.3156 | N | 6 | N | N | 1.1101 | 39.4971 | 105141.0679
[7 empty] | 8829 | 1774 | 1460430 | 2017-02-17 15:56 | 2017-02-17 20:33 | 277 | 11kV | 90025 | 325 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC22381 Lane Cove Walter tripped on: IOC Trip Stick removed near PT15577 by DOp | February | 2017 | 2017Q3 | 2017 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2017-02-17 | Y | 277 | N | 6 | N | Y | 1.1101 | 39.4971 | 65787.6147
[7 empty] | 10173 | 18059 | 1460543 | 2017-02-17 16:36 | 2017-02-17 21:15 | 279 | 11kV | 13421 | 80 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 170924 2 fault operations Overcurrent Wire of pin repaired at 8M-40061 Excluded OMS 1460543 | February | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-02-17 | Y | 167.7625 | N | 6 | N | Y | 1.1101 | 39.4971 | 9807.6709
[7 empty] | 9748 | 12993 | 1460412 | 2017-02-17 15:50 | 2017-02-17 21:15 | 325 | 11kV | 675 | 6 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 170929 A Phase DOLF : 10 Amp Wire off pin and DOLF at sub 71998 Excluded OMS 1460412 | February | 2017 | 2017Q3 | 2017 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2017-02-17 | Y | 112.5 | N | 6 | N | Y | 1.1101 | 39.4971 | 493.2701
[7 empty] | 9696 | 12283 | 1460559 | 2017-02-17 16:41 | 2017-02-17 21:19 | 278 | 11kV | 33913 | 139 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 170912 A Phase Overcurrent Tripped while ELB 75134 was closed. Excluded OMS 1460559 | February | 2017 | 2017Q3 | 2017 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2017-02-17 | Y | 243.9784 | N | 6 | N | Y | 1.1101 | 39.4971 | 24782.6201
[7 empty] | 10148 | 17792 | 1460517 | 2017-02-17 16:26 | 2017-02-17 21:30 | 304 | 11kV | 605452 | 2111 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | Y | Zn12580 Erina Pa4 "Springfield etc" fdr tripped on Relays - 4L SEF, A phase overcurrent, IOC, EFI L&R UGOH fault near AB44981 See 1462323,5,6 exclude 1460517 | February | 2017 | 2017Q3 | 2017 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | Unknown | Unknown | 2017-02-17 | Y | 286.8081 | N | 6 | N | Y | 1.1101 | 39.4971 | 442446.4638
[7 empty] | 8812 | 1601 | 1460834 | 2017-02-17 17:46 | 2017-02-17 21:40 | 234 | 11kV | 135097 | 707 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 170941 3 phase No Fault found | February | 2017 | 2017Q3 | 2017 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2017-02-17 | N | 191.0849 | N | 6 | N | N | 1.1101 | 39.4971 | 98724.9029
[7 empty] | 8817 | 1672 | 1460530 | 2017-02-17 16:32 | 2017-02-17 21:45 | 313 | 11kV | 41003 | 131 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 170919 & 170926 2 fault operations A & C phase Overcurrent Excluded OMS 1460530 | February | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2017-02-17 | Y | 313 | N | 6 | N | Y | 1.1101 | 39.4971 | 29963.783
[7 empty] | 9142 | 5900 | 1460605 | 2017-02-17 16:50 | 2017-02-17 21:50 | 300 | 11kV | 20400 | 68 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 170978 1 fault operation Excluded OMS 1460605 | February | 2017 | 2017Q3 | 2017 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2017-02-17 | Y | 300 | N | 6 | N | Y | 1.1101 | 39.4971 | 14907.7183
[7 empty] | 9693 | 12254 | 1460633 | 2017-02-17 16:49 | 2017-02-17 22:15 | 326 | 11kV | 51619 | 179 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 170983 1 fault operation Overcurrent | February | 2017 | 2017Q3 | 2017 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2017-02-17 | Y | 288.3743 | N | 6 | N | Y | 1.1101 | 39.4971 | 37721.6427
[7 empty] | 10185 | 18293 | 1460914 | 2017-02-17 16:54 | 2017-02-17 22:30 | 336 | 11kV | 28896 | 86 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 170981 1 fault operation A & C phase Overcurrent | February | 2017 | 2017Q3 | 2017 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2017-02-17 | Y | 336 | N | 6 | N | Y | 1.1101 | 39.4971 | 21116.3445
[7 empty] | 8999 | 3950 | 1460913 | 2017-02-17 16:54 | 2017-02-17 22:42 | 348 | 11kV | 11832 | 34 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 170984 1 fault operation A & VC phase Overcurrent Remove tree from ABS 40900 Excluded OMS 1461073 | February | 2017 | 2017Q3 | 2017 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Veg | 2017-02-17 | Y | 348 | N | 6 | N | Y | 1.1101 | 39.4971 | 8646.4766
[7 empty] | 9358 | 8201 | 1460882 | 2017-02-17 17:58 | 2017-02-17 22:51 | 293 | 11kV | 47759 | 163 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 170940 1 fault operation B & C Phase Overcurrent | February | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-02-17 | Y | 293 | N | 6 | N | Y | 1.1101 | 39.4971 | 34900.8685
[7 empty] | 10212 | 18683 | 1461132 | 2017-02-17 22:04 | 2017-02-17 23:30 | 86 | 11kV | 43516 | 506 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 170985 No Protection operation Tapping at IU-30564 repaired under AP. Restored via LV// Excluded OMS 1461140. | February | 2017 | 2017Q3 | 2017 | 213:33771 | 213:33771 | ZN00213/033771 | NEWCASTLE | OH | Not Veg | 2017-02-17 | N | 86 | N | 6 | N | N | 1.1101 | 39.4971 | 31800.2093
[7 empty] | 10152 | 17809 | 1460661 | 2017-02-17 17:04 | 2017-02-17 23:31 | 387 | 11kV | 112232 | 296 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | Zn12690 Berkeley Vale Panel 26 "S65857 Sanitarium Saint No 5 etc" fdr tripped on Relays - 26R Leg A & C phase overcurrent, EFI Cause: Lightning. Storm See 1462479,80 exclude 1460661 | February | 2017 | 2017Q3 | 2017 | ZN12690:PA26 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Veg | 2017-02-17 | Y | 379.1622 | N | 6 | N | Y | 1.1101 | 39.4971 | 82015.8353
[7 empty] | 8802 | 1503 | 1460666 | 2017-02-17 17:04 | 2017-02-17 23:34 | 390 | 11kV | 88140 | 226 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15013 Terrey Hills - Pnl.6 tripped on: A & C phase IOC, timed OC Several tree branches on mains from Zone to Recloser 20828 | February | 2017 | 2017Q3 | 2017 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2017-02-17 | Y | 390 | N | 6 | N | Y | 1.1101 | 39.4971 | 64410.1123
[7 empty] | 9519 | 10227 | 1461125 | 2017-02-17 19:48 | 2017-02-17 23:35 | 226.8 | 11kV | 303231.6 | 1337 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 170958 Tapping blown at ABS 64202. Section switched to make ABS open. Please arrange repair. DMA raised. | February | 2017 | 2017Q3 | 2017 | 232:11453 | 232:11453 | ZN00232/011453 | PORT STEPHENS | OH | Not Veg | 2017-02-17 | Y | 226.8 | N | 6 | N | Y | 1.1101 | 39.4971 | 221592.7095
[7 empty] | 9836 | 14016 | 1461096 | 2017-02-17 19:21 | 2017-02-18 00:35 | 314 | 11kV | 628 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 170980 B Phase DOLF : 16 Amp Excluded OMS 1461096 | February | 2017 | 2017Q3 | 2017 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2017-02-17 | Y | 314 | N | 6 | N | Y | 1.1101 | 39.4971 | 458.9239
[7 empty] | 9884 | 14571 | 1460640 | 2017-02-17 16:45 | 2017-02-18 01:25 | 520 | 11kV | 514403 | 1118 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | Zn12570 Avoca Panel 26 "S49886 Avoca Aux No1" fdr tripped on Relays - B phase IOC, EFI Lightning/Surge Arrestor Roadside Phase LA Def @ PT14574 Miller Wilson. Isolated & in LV parallel See 1462375,7,8,9,80 exclude 1460640 | February | 2017 | 2017Q3 | 2017 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2017-02-17 | Y | 460.11 | N | 6 | N | Y | 1.1101 | 39.4971 | 375910.5401
[7 empty] | 9170 | 6219 | 1460602 | 2017-02-17 16:44 | 2017-02-18 01:45 | 541 | 11kV | 573436 | 1215 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Zn12690 Berkeley Vale Panel 19 "S18671 Corella Enterprise Etc" fdr tripped on Relays - 19R Leg Sensitive Earth Fault, EFi 11kV Mains down from AB420957 to AB42958 tee PT12315 Bundilla Panorama Lightning See 1462365,7,8,70,1 Exclude 1460602 | February | 2017 | 2017Q3 | 2017 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Not Veg | 2017-02-17 | Y | 471.9638 | N | 6 | N | Y | 1.1101 | 39.4971 | 419050.1153
[7 empty] | 9243 | 6935 | 1460929 | 2017-02-17 18:13 | 2017-02-18 02:41 | 508 | 11kV | 22860 | 45 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | Y | LID 171119 1 fault operation Overcurrent, Earth Fault Snapped pole CN-20021 | February | 2017 | 2017Q3 | 2017 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2017-02-17 | Y | 508 | N | 6 | N | Y | 1.1101 | 39.4971 | 16705.4137
[7 empty] | 9523 | 10264 | 1461061 | 2017-02-17 17:44 | 2017-02-18 08:08 | 864 | 11kV | 653456 | 772 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | Ex Zn12570 Avoca section of Pa33 "McMasters Beach" RE45133 Mcmasters Beach tripped & locked out on Overcurrent Cause not ascertained. DOp has patrolled the feeder See 1462481,2,3 exclude 1461061,189 | February | 2017 | 2017Q3 | 2017 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2017-02-17 | Y | 846.4456 | N | 6 | N | Y | 1.1101 | 39.4971 | 477526.3711
[7 empty] | 9158 | 6106 | 1461143 | 2017-02-18 07:41 | 2017-02-18 09:10 | 89 | 11kV | 267 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170994 A & C Phase DOLF : 10 Amp A phase surge arrestor cut away. dq Excluded oms 1461394 | February | 2017 | 2017Q3 | 2017 | 264:81240 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Veg | 2017-02-18 | N | 89 | N | 33 | Y | Y | 1.1101 | 39.4971 | 195.1157
[7 empty] | 9263 | 7132 | 1460627 | 2017-02-17 16:49 | 2017-02-18 09:12 | 983 | 11kV | 459061 | 467 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Ex Zn14891 Wyong section of Panel 12 "Yarramalong" RE48838 Yarramalong Maitland tripped & locked out on Overcurrent Cause: Lightning. 11kv Down between RE48838 to AB43742 | February | 2017 | 2017Q3 | 2017 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2017-02-17 | Y | 983 | N | 6 | N | Y | 1.1101 | 39.4971 | 335468.2388
[7 empty] | 8763 | 922 | 1461154 | 2017-02-17 20:07 | 2017-02-18 09:40 | 813 | 11kV | 1626 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 170992 A Phase DOLF : 10 Amp Excluded OMS 1461154 | February | 2017 | 2017Q3 | 2017 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2017-02-17 | Y | 813 | N | 6 | N | Y | 1.1101 | 39.4971 | 1188.2328
[7 empty] | 8947 | 3321 | 1461367 | 2017-02-18 06:30 | 2017-02-18 10:22 | 232 | 11kV | 232 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170995 A & B phase DOLF : 10 Amp excluded OMS 1461367 | February | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2017-02-18 | N | 232 | N | 33 | Y | Y | 1.1101 | 39.4971 | 169.5388
[7 empty] | 9089 | 5260 | 1460631 | 2017-02-17 16:58 | 2017-02-18 10:50 | 1072 | 11kV | 1072 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 170916 Single phase DOLF : 10 Amp sEE lid 170911 & oms 1460696 Mains down between pole 8M-80006 & 8M-80008. Exccluded oms 1461121 | February | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-02-17 | Y | 1072 | N | 6 | N | Y | 1.1101 | 39.4971 | 783.386
[7 empty] | 9262 | 7090 | 1461320 | 2017-02-17 23:00 | 2017-02-18 11:20 | 740 | 11kV | 6660 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 170998 C Phase DOLF : 10 Amp Excluded OMS No. 1461348, 1461320, 1461466 | February | 2017 | 2017Q3 | 2017 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2017-02-17 | Y | 740 | N | 6 | N | Y | 1.1101 | 39.4971 | 4866.9316
[7 empty] | 8914 | 2867 | 1461358 | 2017-02-18 08:19 | 2017-02-18 11:25 | 186 | 11kV | 372 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170996 B Phase DOLF : 10 Amp Excluded OMS 1461422 | February | 2017 | 2017Q3 | 2017 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2017-02-18 | N | 186 | N | 33 | Y | Y | 1.1101 | 39.4971 | 271.8466
[7 empty] | 9838 | 14025 | 1461539 | 2017-02-18 11:08 | 2017-02-18 12:05 | 57 | 11kV | 171 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 171000 B Phase DOLF : 10 Amp Excluded OMS 1461539 | February | 2017 | 2017Q3 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2017-02-18 | N | 57 | N | 33 | Y | Y | 1.1101 | 39.4971 | 124.9618
[7 empty] | 10097 | 17228 | 1460875 | 2017-02-17 17:59 | 2017-02-18 12:20 | 1101 | 11kV | 612844 | 879 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 170942 2 fault operations 3 phase Earth Fault Tree brought down 33 & 11kV mains pole MW-60056. Repaired under AP Excluded OMS 1460875 | February | 2017 | 2017Q3 | 2017 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2017-02-17 | Y | 697.2059 | N | 6 | N | Y | 1.1101 | 39.4971 | 447848.3194
[7 empty] | 9977 | 15633 | 1461505 | 2017-02-18 10:04 | 2017-02-18 12:30 | 146 | 11kV | 292 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 171006 C Phase DOLF : 10 Amp Excluded OMS 1461505 | February | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2017-02-18 | N | 146 | N | 33 | Y | Y | 1.1101 | 39.4971 | 213.385
[7 empty] | 9648 | 11766 | 1460584 | 2017-02-17 16:46 | 2017-02-18 13:06 | 1220 | 11kV | 660804 | 966 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Zn12690 Berkeley Vale Panel 6 "S18124 Krone Enterprise" fdr tripped on Relays - EFI, L2 & L3 overurrent, auto reclose, Lockout 11kv Fdr from B41185 to LB42263 to LB63384 tee PT13554 tee PT13076 See 1462401 exclude 1460584,610 | February | 2017 | 2017Q3 | 2017 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Veg | 2017-02-17 | Y | 684.0621 | N | 6 | N | Y | 1.1101 | 39.4971 | 482896.0728
[7 empty] | 8880 | 2503 | 1463053 | 2017-02-18 10:37 | 2017-02-18 13:46 | 189 | 11kV | 30429 | 161 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 171004 interrupt to repair wire off pin sitting on crossarm pole - 7M-60131 started fire | February | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-02-18 | N | 189 | N | 33 | Y | Y | 1.1101 | 39.4971 | 22236.6157
[7 empty] | 8922 | 2920 | 1461447 | 2017-02-18 08:50 | 2017-02-18 13:46 | 296 | 11kV | 296 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 170997 Single phase DOLF : 10 Amp Excluded OMS 1461447 | February | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2017-02-18 | N | 296 | N | 33 | Y | Y | 1.1101 | 39.4971 | 216.3081
[7 empty] | 10076 | 16881 | 1460461 | 2017-02-17 16:15 | 2017-02-18 13:58 | 1303 | 11kV | 6816 | 12 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | Y | LID 170987 1 fault operation Overcurrent; Earth Fault Abs 43808 closed after fault isolated on Fdr 18146. Fdr 18141 tripped at Sw 18156 ( fdr abnormal due to earlier fault) Second fault on 18146 caused 18156 to trip. | February | 2017 | 2017Q3 | 2017 | 514:18141 | 514:18141 | ZN00514/018141 | SINGLETON | OH | Not Veg | 2017-02-17 | Y | 568 | N | 6 | N | Y | 1.1101 | 39.4971 | 4980.9318
[7 empty] | 8830 | 1794 | 1461446 | 2017-02-18 11:06 | 2017-02-18 14:07 | 181 | 11kV | 362 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | No LID report provided see related jobs 1461535;1461446 | February | 2017 | 2017Q3 | 2017 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2017-02-18 | N | 181 | N | 33 | Y | Y | 1.1101 | 39.4971 | 264.5389
[7 empty] | 9811 | 13746 | 1461554 | 2017-02-18 12:28 | 2017-02-18 14:25 | 117 | 11kV | 936 | 8 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 171010 3 phase section of 11kV interupted to repair 33kV OHM see LID170989. dq Excluded OMS 1461596 1461597.## | February | 2017 | 2017Q3 | 2017 | 238:34148 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2017-02-18 | N | 117 | N | 33 | Y | Y | 1.1101 | 39.4971 | 684.0012
[7 empty] | 9691 | 12234 | 1463062 | 2017-02-18 10:37 | 2017-02-18 14:25 | 228 | 11kV | 228 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 171007 A Phase DOLF : 10 Amp | February | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2017-02-18 | N | 228 | N | 33 | Y | Y | 1.1101 | 39.4971 | 166.6157
[7 empty] | 9176 | 6268 | 1460684 | 2017-02-18 08:19 | 2017-02-18 15:00 | 401 | 11kV | 401 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Ex Zn14891 Wyong section of Pa8 PT18430 McPherson Old Maitland 10 Amp Footpath phase HDO blown. Cause not ascertained. Suspect Previous storm See 1462729 exclude 1461421 | February | 2017 | 2017Q3 | 2017 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2017-02-18 | N | 401 | N | 33 | Y | Y | 1.1101 | 39.4971 | 293.039
[7 empty] | 8767 | 975 | 1460717 | 2017-02-17 17:16 | 2017-02-18 15:10 | 1314 | 11kV | 22338 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | Ex Zn12600 Lisarow section of Pa2 PT11789 The Ridgeway Fagans 20Amp footpath HDO blown. Cause not ascertained. Suspect Previous storm See 1462740 exclude 1460717,1549 | February | 2017 | 2017Q3 | 2017 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2017-02-17 | Y | 1314 | N | 6 | N | Y | 1.1101 | 39.4971 | 16323.9515
[7 empty] | 9122 | 5621 | 1460613 | 2017-02-17 16:42 | 2017-02-18 15:43 | 1381 | 11kV | 577446 | 784 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Zn12690 Berkeley Vale Panel 24 LB49474 etc" fdr tripped on Relays: Pa24L A & B phase overcurrent Cause: Lightning 11kv OH down between RE44289 to LV44129 See 1463233,7 exclude 1460636 | February | 2017 | 2017Q3 | 2017 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2017-02-17 | Y | 736.5383 | N | 6 | N | Y | 1.1101 | 39.4971 | 421980.505
[7 empty] | 9772 | 13302 | 1460674 | 2017-02-17 16:55 | 2017-02-18 16:01 | 1386 | 11kV | 61587 | 209 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 170979 1 fault operatiion A & B phase Overcurrent; Earth Fault Remove Tree from mains at pole AN-90530 Cph = 1390A, Aph = 1476A, EF = 1047A Excluded OMS 1460654 | February | 2017 | 2017Q3 | 2017 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2017-02-17 | Y | 294.6746 | N | 6 | N | Y | 1.1101 | 39.4971 | 45005.9631
[7 empty] | 9213 | 6657 | 1460524 | 2017-02-17 16:18 | 2017-02-18 16:19 | 1441 | 11kV | 775258 | 538 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Ex Zn14143 Somersby section of Pa17 RE48437 tripped on relays, OC, IOC 11kv mains down between RE48437 to AB43780 to LB61923 tee PT13468 tee PT13127 See also mains down Peats Ridge LB61923 Control Room Interuption report not created. Data gathered from DMA and DNMS | February | 2017 | 2017Q3 | 2017 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2017-02-17 | Y | 1441 | N | 6 | N | Y | 1.1101 | 39.4971 | 566535.6802
[7 empty] | 9220 | 6733 | 1461459 | 2017-02-18 15:05 | 2017-02-18 16:35 | 90 | 11kV | 90 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171013 A Phase Interrupted to repair HV dropper Excluded OMS 1461459 | February | 2017 | 2017Q3 | 2017 | 502:48010 | 502:48010 | ZN00502/048010 | CESSNOCK | OH | Not Veg | 2017-02-18 | N | 90 | N | 33 | Y | Y | 1.1101 | 39.4971 | 65.7693
[7 empty] | 9167 | 6195 | 1461677 | 2017-02-18 17:06 | 2017-02-18 17:46 | 40 | 11kV | 560 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 171021 B & C Phase DOLF Excluded OMS 1461677 | February | 2017 | 2017Q3 | 2017 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2017-02-18 | N | 40 | N | 33 | Y | Y | 1.1101 | 39.4971 | 409.2315
[7 empty] | 9982 | 15733 | 1461658 | 2017-02-18 16:41 | 2017-02-18 17:50 | 69.2333 | 11kV | 3807.8333 | 55 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Ex Zn12660 Woy Woy section of Pa14 PT11761 Gabaong Goondi 31.5Amp roadside phase HDO blown. Cause not ascertained | February | 2017 | 2017Q3 | 2017 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Veg | 2017-02-18 | N | 69.2333 | N | 33 | Y | Y | 1.1101 | 39.4971 | 2782.6523
[7 empty] | 10163 | 17936 | 1461666 | 2017-02-18 16:49 | 2017-02-18 18:05 | 76 | 11kV | 152 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Ex Zn12660 Woy Woy section of Pa14 PT12575 Woy Woy Corowa 10amp footpath phase HDO blown Cause not ascertained See 1462825 exclude 1461666,89 | February | 2017 | 2017Q3 | 2017 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Veg | 2017-02-18 | N | 76 | N | 33 | Y | Y | 1.1101 | 39.4971 | 111.0771
[7 empty] | 8862 | 2263 | 1461172 | 2017-02-17 20:16 | 2017-02-18 18:18 | 1322.4333 | 11kV | 9254.4333 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Electrical Storm | Y | 18/02/17 14:36 CASS: HV drop out fuse requires replacement on PT 13869. See 1463328 GIS 1461234 Exclude 1461172,309 | February | 2017 | 2017Q3 | 2017 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2017-02-17 | Y | 1322.0619 | N | 6 | N | Y | 1.1101 | 39.4971 | 6762.8669
[7 empty] | 10183 | 18262 | 1462376 | 2017-02-18 12:00 | 2017-02-18 18:30 | 390 | 11kV | 390 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 171012 A Phase DOLF : 16 Amp at Sub A & B Phase DOLF at Line fuse 2048 nil oms spotted by dop passer by. dq A phase surge arrestor blown and replaced by lw at sub12107 | February | 2017 | 2017Q3 | 2017 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2017-02-18 | N | 390 | N | 33 | Y | Y | 1.1101 | 39.4971 | 285.0005
[7 empty] | 9450 | 9374 | 1461729 | 2017-02-18 18:14 | 2017-02-18 18:59 | 45 | 11kV | 11115 | 247 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 171031 2 fault operations 3 phase Overcurrent Tree on mains adjacent ABS 62799 removed by DOp. | February | 2017 | 2017Q3 | 2017 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2017-02-18 | N | 45 | N | 33 | Y | Y | 1.1101 | 39.4971 | 8122.5142
[7 empty] | 9873 | 14471 | 1461727 | 2017-02-18 18:12 | 2017-02-18 19:20 | 68 | 11kV | 3575 | 53 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 171032 1 fault operation Overcurrent Excluded OMS 1461727 | February | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-02-18 | N | 67.4528 | N | 33 | Y | Y | 1.1101 | 39.4971 | 2612.5046
[7 empty] | 8735 | 268 | 1461759 | 2017-02-18 18:52 | 2017-02-18 19:55 | 63 | 11kV | 189 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 171038 A Phase DOLF : 10 Amp Excluded OMS 1461759 | February | 2017 | 2017Q3 | 2017 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2017-02-18 | N | 63 | N | 33 | Y | Y | 1.1101 | 39.4971 | 138.1156
[7 empty] | 10245 | 18987 | 1460953 | 2017-02-17 16:39 | 2017-02-18 20:00 | 1641 | 11kV | 100206 | 76 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Ex Zn14891 Wyong section of Panel 8 RE48425 Kangy Angy tripped & locked out on overcurrent Broken Cross arm and wires down adjacent to PT11272 HV into LV. Insulation Inspector required CTW & AP's issued to lineworker & T-Con See 1462345,7 exclude 1460953 | February | 2017 | 2017Q3 | 2017 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Not Veg | 2017-02-17 | Y | 1318.5 | N | 6 | N | Y | 1.1101 | 39.4971 | 73227.5892
[7 empty] | 10270 | 19225 | 1461718 | 2017-02-18 17:59 | 2017-02-18 21:07 | 188 | 11kV | 376 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 171040 A Phase DOLF : 10 Amp Excluded OMS 1461718 | February | 2017 | 2017Q3 | 2017 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2017-02-18 | N | 188 | N | 33 | Y | Y | 1.1101 | 39.4971 | 274.7697
[7 empty] | 10285 | 19369 | 1461812 | 2017-02-18 20:13 | 2017-02-18 21:20 | 67 | 11kV | 670 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 171041 A & C phase DOLF : 16 Amp excluded OMS 1461812 | February | 2017 | 2017Q3 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-02-18 | N | 67 | N | 33 | Y | Y | 1.1101 | 39.4971 | 489.6162
[7 empty] | 9758 | 13150 | 1461463 | 2017-02-18 09:14 | 2017-02-18 21:43 | 749 | 11kV | 59920 | 80 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty section of Pa16 PT14046 McLachlan The Entrance 40Amp footpath phase HDO blown. cause not ascertained See 1462737 exclude 1461463,5 | February | 2017 | 2017Q3 | 2017 | ZN12610:PA16 | ZN12610:PA16 | ZN12610/000016 | CENTRAL COAST | OH | Veg | 2017-02-18 | N | 749 | N | 33 | Y | Y | 1.1101 | 39.4971 | 43787.7687
[7 empty] | 9018 | 4179 | 1461756 | 2017-02-18 18:46 | 2017-02-18 21:55 | 189 | 11kV | 195811 | 1855 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 171033 2 fault operations 3 phase Intellirupter; Overcurrent Tree on mains pole NB-40191 Excluded OMS 1461756. | February | 2017 | 2017Q3 | 2017 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Veg | 2017-02-18 | N | 105.5585 | N | 33 | Y | Y | 1.1101 | 39.4971 | 143092.9034
[7 empty] | 9611 | 11396 | 1461769 | 2017-02-18 19:01 | 2017-02-18 23:06 | 245 | 11kV | 19960 | 176 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 171039 3 fault operations Earth Fault wire down at pole BJ-70063 tee to sub 71711 Excluded oms 1461769 | February | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2017-02-18 | N | 113.4091 | N | 33 | Y | Y | 1.1101 | 39.4971 | 14586.1793
[7 empty] | 9445 | 9321 | 1461734 | 2017-02-18 18:23 | 2017-02-18 23:20 | 297 | 11kV | 13673 | 151 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 171036 3 phase 11kv main on the ground near pole JS-80052. Customers along the feeder got partial volts since 1823 hours. Excluded OMS 1461734 | February | 2017 | 2017Q3 | 2017 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2017-02-18 | N | 90.5497 | N | 33 | Y | Y | 1.1101 | 39.4971 | 9991.8251
[7 empty] | 9736 | 12825 | 1461702 | 2017-02-18 17:37 | 2017-02-19 01:20 | 463 | 11kV | 926 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 171050 Single phase DOLF : 10 Amp Excluded OMS 1461702 | February | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-02-18 | N | 463 | N | 33 | Y | Y | 1.1101 | 39.4971 | 676.6935
[7 empty] | 9614 | 11407 | 1461846 | 2017-02-18 21:58 | 2017-02-19 01:30 | 212 | 11kV | 212 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 171052 Single phase DOLF : 5 Amp Excluded OMS 1461846 | February | 2017 | 2017Q3 | 2017 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2017-02-18 | N | 212 | N | 33 | Y | Y | 1.1101 | 39.4971 | 154.9233
[7 empty] | 9154 | 6036 | 1461861 | 2017-02-18 23:49 | 2017-02-19 02:35 | 166 | 11kV | 124197 | 772 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa33 "Scaysbrook Waldron" fdr RE45133 MacMastars Beach tripped reclosed and locked out on overcurrent Cause not ascertained Patrolled by DOp See 1462888,9,90,1 exclude 1461861,2,3 | February | 2017 | 2017Q3 | 2017 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2017-02-18 | N | 160.8769 | N | 33 | Y | Y | 1.1101 | 39.4971 | 90759.5044
[7 empty] | 9003 | 3987 | 1461922 | 2017-02-19 09:52 | 2017-02-19 11:30 | 98 | 11kV | 98 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 171059 A Phase DOLF : 10 Amp Excluded OMS 1461922 | February | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-02-19 | N | 98 | N | 11 | N | N | 1.1101 | 39.4971 | 71.6155
[7 empty] | 9991 | 15904 | 1461838 | 2017-02-18 21:27 | 2017-02-19 11:35 | 848 | 11kV | 8664 | 54 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 171045 Overcurrent, Sensitive Earth Fault tx 70287 replaced please provide SAO Excluded OMS 1461838 | February | 2017 | 2017Q3 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2017-02-18 | N | 160.4444 | N | 33 | Y | Y | 1.1101 | 39.4971 | 6331.3957
[7 empty] | 9014 | 4128 | 1461850 | 2017-02-18 22:03 | 2017-02-19 11:45 | 822 | 11kV | 368657 | 1327 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14143 Somersby Panel 12 "Phillips Gindurra" fdr tripped on Relays: IOC A & B phase, Earth Fault & Overcurrent rela, EFi Signals: Transformer 2 GRoup E, 11kv trip Cause: Uunderground Cable fault from S18495 to S18469 to AB44696 to LB40492 See 1462878,80,1,2,3 exclude 1461850 | February | 2017 | 2017Q3 | 2017 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | UG | Not Veg | 2017-02-18 | N | 277.8124 | N | 33 | Y | Y | 1.1101 | 39.4971 | 269403.6621
[7 empty] | 10139 | 17670 | 1461944 | 2017-02-19 11:14 | 2017-02-19 13:03 | 108.75 | 11kV | 1631.25 | 15 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171060 C Phase DOLF : 16 Amp Possum on Tx. | February | 2017 | 2017Q3 | 2017 | 233:82815 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Not Veg | 2017-02-19 | N | 108.75 | N | 11 | N | N | 1.1101 | 39.4971 | 1192.0694
[7 empty] | 9969 | 15533 | 1460683 | 2017-02-17 16:37 | 2017-02-19 13:15 | 2678 | 11kV | 774088 | 855 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Zn12600 Lisarow Panel 13 fdr tripped on Relays - SEF, EF OH down adjacent PT12227 Brush Ourimbah 1.4 See 1462337,40,1,2,3 exclude 1460683,1631,49,837 | February | 2017 | 2017Q3 | 2017 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2017-02-17 | Y | 905.3661 | N | 6 | N | Y | 1.1101 | 39.4971 | 565680.6787
[7 empty] | 8931 | 3033 | 1461948 | 2017-02-19 11:30 | 2017-02-19 14:10 | 160 | 11kV | 480 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 171062 B Phase DOLF : 10 Amp Excluded OMS 1461948 | February | 2017 | 2017Q3 | 2017 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Veg | 2017-02-19 | N | 160 | N | 11 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 9981 | 15703 | 1461964 | 2017-02-19 12:33 | 2017-02-19 15:03 | 150 | 11kV | 115401 | 772 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa33 "McMastars Beach" RE45133 McMasters Beach tripped & locked out on Overcurrent trip & Lockout Cause not ascertained See 1462897,8,9 exclude 1461964 | February | 2017 | 2017Q3 | 2017 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2017-02-19 | N | 149.4832 | N | 11 | N | N | 1.1101 | 39.4971 | 84331.647
[7 empty] | 8823 | 1728 | 1460898 | 2017-02-17 21:11 | 2017-02-19 17:00 | 2629 | 11kV | 281303 | 107 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | Y | Ex Zn12640 Umina section of Pa18 From LB41958 to PT13537 to PT11769 Tree Branch brought down OH See 1463141 exclude 1461924, 1461237 | February | 2017 | 2017Q3 | 2017 | ZN12640:PA18 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Veg | 2017-02-17 | Y | 2629 | N | 6 | N | Y | 1.1101 | 39.4971 | 205567.9354
[7 empty] | 9101 | 5353 | 1460522 | 2017-02-17 16:18 | 2017-02-19 17:30 | 2952 | 11kV | 5904 | 2 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Electrical Storm | Y | Ex Zn14143 Somersby section of Pa17 IR63537 Peats Ridge "Darkinjung" tripped and relcosed and lockout on Overcurrent Lightning Strike to UGOH | February | 2017 | 2017Q3 | 2017 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2017-02-17 | Y | 2952 | N | 6 | N | Y | 1.1101 | 39.4971 | 4314.4691
[7 empty] | 9141 | 5891 | 1461779 | 2017-02-18 19:15 | 2017-02-19 18:00 | 1365 | 11kV | 11608 | 110 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | Rain Wind Storm | N | REC21350 Booralie Kulgoa tripped on: Sensitive Earth Abnormal: AB25194 closed with AB26217 open CCT has come off insulators near USL23634 See 1462701 1462699 | February | 2017 | 2017Q3 | 2017 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Not Veg | 2017-02-18 | N | 105.5273 | N | 33 | Y | Y | 1.1101 | 39.4971 | 8482.784
[7 empty] | 9052 | 4781 | 1461054 | 2017-02-17 23:15 | 2017-02-19 18:45 | 2610 | 11kV | 170666 | 325 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC22381 Lane Cove Walter tripped on: IOC and time O/C Tree branch on CCT between LB21568 to S16061 tee S16178 See 1467377 1467378 Secondary LV outage see 1467379 1467380 | February | 2017 | 2017Q3 | 2017 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2017-02-17 | Y | 525.1262 | N | 6 | N | Y | 1.1101 | 39.4971 | 124717.679
[7 empty] | 9925 | 15067 | 1461151 | 2017-02-17 16:22 | 2017-02-19 19:30 | 3068 | 11kV | 958229 | 566 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Electrical Storm | Y | Zn12630 Peats Ridge Panel 1 "Gunderman" fdr tripped on Relays: A,B,C phase & N timed overcurrent Signals: 11kv trip Tree branch brought down OH. 11kv fdr from AB40574 to LB45187 to RE48437 to AB43780. CCT down nr PT18277 See 1462317,8,9 exclude 1461151,306,530,798,9,845,920 Note: during this outage customers also affected by 33kv outage - see OMS 1462462 | February | 2017 | 2017Q3 | 2017 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2017-02-17 | Y | 1692.9841 | N | 6 | N | Y | 1.1101 | 39.4971 | 700245.4902
[7 empty] | 10303 | 19607 | 1462007 | 2017-02-19 15:08 | 2017-02-19 20:40 | 332 | 11kV | 1992 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge section of Panel 8 "Kulnura" fdr PT13525 Williams Geroge 1.9 footpath phase 31.5Amp HDO blown Cause not ascertained. See 1462896 exclude 1462007,55 | February | 2017 | 2017Q3 | 2017 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2017-02-19 | N | 332 | N | 11 | N | N | 1.1101 | 39.4971 | 1455.6948
[7 empty] | 9354 | 8109 | 1461664 | 2017-02-18 16:19 | 2017-02-19 21:49 | 1770 | 11kV | 290280 | 164 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Ex Zn14143 Somersby section of Pa17 "Somersby Falls" 11kv RE45012 Bar Point opened Interrupted for safety resaons. OH mains have patrolled water crossing See 1461664 exclude 1461999 Note: Actual time that Device operated was 18/02/17 15:00, however, customers were already without supply due to outage on device CP48437 that begun 17/02/2017 16:18:00 and ended at 18/02/2017 16:19:00 - see OMS 1460524 | February | 2017 | 2017Q3 | 2017 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2017-02-18 | N | 1770 | N | 33 | Y | Y | 1.1101 | 39.4971 | 212128.0622
[7 empty] | 9970 | 15558 | 1462074 | 2017-02-19 20:28 | 2017-02-19 22:35 | 127 | 11kV | 82469 | 772 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Zn12570 Avoca section of Panel 33 MacMasters Beach" fdr RE45133 MacMasters Beach tripped, reclosed and locked out on overcurrent Cause not ascertained. DOp patrolled extent of feeder, no cause found all supply restored See 1462893,4 exclude 1462074,7 | February | 2017 | 2017Q3 | 2017 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2017-02-19 | N | 106.8251 | N | 11 | N | N | 1.1101 | 39.4971 | 60265.9128
[7 empty] | 9813 | 13760 | 1461819 | 2017-02-18 20:43 | 2017-02-19 22:50 | 1567 | 11kV | 9456 | 8 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 171047 3 fault operations Sensitive Earth Fault Faulty Tx at sub 72492 Excluded OMS 1461819, 1461970 ## | February | 2017 | 2017Q3 | 2017 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2017-02-18 | N | 1182 | Y | 33 | N | Y | 1.1101 | 39.4971 | 6910.1659
[7 empty] | 9850 | 14167 | 1462062 | 2017-02-19 19:29 | 2017-02-19 22:55 | 206 | 11kV | 6503 | 61 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 171067 2 fault operations Overcurrent Conductor off pin at pole 9N-40037 Excluded OMS 1462062 | February | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-02-19 | N | 106.6066 | N | 11 | N | N | 1.1101 | 39.4971 | 4752.2006
[7 empty] | 10037 | 16461 | 1462088 | 2017-02-19 21:11 | 2017-02-20 00:55 | 224 | 11kV | 224 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 171068 Single phase DOLF : 10 Amp Faulty arresters replaced under AP Excluded OMS 1462088 | February | 2017 | 2017Q3 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2017-02-19 | N | 224 | N | 11 | N | N | 1.1101 | 39.4971 | 163.6926
[7 empty] | 9487 | 9848 | 1462058 | 2017-02-19 16:54 | 2017-02-20 01:50 | 536 | 11kV | 3322 | 1182 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | Zn9245 Engadine - Pnl.3 tripped & reclosed on: B Phase timed O/C Field EFIs: S9279, S9445, S48684, S9075, S9346, S9246, S9586, S9688, S9225 Car hit pole on Princes Hwy, Heathcote (Near Short St) and snapped pole at base. PT9673 Heathcote Oval interrupted to isolate and repair feeder (non paralleling) See 1462193 1462192 | February | 2017 | 2017Q3 | 2017 | ZN9245:PA3 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | OH | Not Veg | 2017-02-19 | N | 2.8105 | N | 11 | N | N | 1.1101 | 39.4971 | 2427.6196
[7 empty] | 9862 | 14347 | 1462082 | 2017-02-19 20:55 | 2017-02-20 02:45 | 350 | 11kV | 88210 | 269 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S1719 Bright Wai - 11kV 60 Amp fuse operated on C phase. Underground mains termination box on side of house has shorted out at 20 Brighton Blvd. HV fuse operated, suspect poor fuse grading. See 1462159 14562160 | February | 2017 | 2017Q3 | 2017 | ZN36100:PA27 | ZN36100:PA25 | ZN36100/000025 | WAVERLEY | UG | Not Veg | 2017-02-19 | N | 327.9182 | N | 11 | N | N | 1.1101 | 39.4971 | 64461.2662
[7 empty] | 9584 | 11047 | 1462201 | 2017-02-20 09:51 | 2017-02-20 11:30 | 99 | 11kV | 34155 | 345 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15014 Mona Vale ex Pnl.11L - AB23513 opened for emergency repairs Palm tree caused molten plastic to melt and drop on footpath. | February | 2017 | 2017Q3 | 2017 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2017-02-20 | N | 99 | N | 6 | N | N | 1.1101 | 39.4971 | 24959.4666
[7 empty] | 9906 | 14867 | 1460607 | 2017-02-18 08:20 | 2017-02-20 19:35 | 3555 | 11kV | 569205 | 166 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor ABC | Unplanned | Rain Wind Storm | N | Ex Pnl.12 Mova Vale Zone - 11kV Feeder from S16528 Elvina Bay Sth - OH mains down 11kV ABC and LV ABC on the ground (4 bays) due to storm. See 1462782 1462785 1462786 1462787 1462788 1462789 | February | 2017 | 2017Q3 | 2017 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | OH | Not Veg | 2017-02-18 | N | 3428.9458 | N | 33 | Y | Y | 1.1101 | 39.4971 | 415958.2253
[7 empty] | 9725 | 12656 | 1462410 | 2017-02-20 16:03 | 2017-02-20 19:45 | 222 | 11kV | 21534 | 97 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S859 Linley Place supply manually interrupted. Cause: Mercedes ateco truck rego# CJ.15.MF hit optus mains bringing down distributor pole#GL 92241. Company nameCentury Couriers. Driver: Sumesh Koirala ph. 0414790982. Dop & O/H mains arrived on site to carry out repairs. Pole to be replaced at a later date. See OMS 1462772 1462410 1462437 1462471 1462472 1462488 | February | 2017 | 2017Q3 | 2017 | ZN129:PA28 | ZN129:PA52 | ZN00129/000052 | LANE COVE | OH | Not Veg | 2017-02-20 | N | 222 | N | 6 | N | N | 1.1101 | 39.4971 | 15736.4121
[7 empty] | 9909 | 14910 | 1462498 | 2017-02-20 18:32 | 2017-02-20 20:34 | 122 | 11kV | 2440 | 20 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 171079 Blown tapping pole HR-91889 Excluded oms 1462498 | February | 2017 | 2017Q3 | 2017 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2017-02-20 | N | 122 | N | 6 | N | N | 1.1101 | 39.4971 | 1783.08
[7 empty] | 10221 | 18762 | 1462523 | 2017-02-20 19:54 | 2017-02-20 20:46 | 52 | 11kV | 79263 | 1679 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7481 Darling Harbour - Pnl.9 tripped on: B Phase OC and Earth Fault on left leg FIeld EFIs: All down to S7759 (left leg) UG cable fault from S7759 to S6341 See 1462810 1462811 | February | 2017 | 2017Q3 | 2017 | ZN7481:PA9 | ZN7481:PA9 | ZN07481/000009 | SYDNEY | UG | Not Veg | 2017-02-20 | N | 47.2085 | N | 6 | N | N | 1.1101 | 39.4971 | 57923.0625
[7 empty] | 10336 | 20116 | 1462536 | 2017-02-20 21:41 | 2017-02-20 23:25 | 104 | 11kV | 3120 | 30 | HV | Animal Frog | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171080 C Phase DOLF : 16 Amp frog on sub 9249, dolf 9249 & LF 18278 found blown | February | 2017 | 2017Q3 | 2017 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2017-02-20 | N | 104 | N | 6 | N | N | 1.1101 | 39.4971 | 2280.004
[7 empty] | 9618 | 11451 | 1462530 | 2017-02-20 23:40 | 2017-02-21 02:40 | 180 | 11kV | 360 | 2 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 171081 no protection operation, section isolated repair ohm at pole CN-80617 Excluded oms 1462530 | February | 2017 | 2017Q3 | 2017 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Not Veg | 2017-02-20 | N | 180 | N | 6 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 10362 | 20333 | 1460652 | 2017-02-19 18:18 | 2017-02-21 12:40 | 2542 | 11kV | 584690 | 355 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Wind Storm | N | Ex Pnl.12 Mona Vale Zone - CP24701 Scotland Island - 11kV and LV mains brought down by tree outside 115 Richardson Rd, Scotland Island Feeder did no trip and was isolated for safety. Mains down between S16614 and S16615 See 1462796 1462797 1462798 | February | 2017 | 2017Q3 | 2017 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | OH | Veg | 2017-02-19 | N | 1647.0141 | N | 11 | N | N | 1.1101 | 39.4971 | 427274.2066
[7 empty] | 9840 | 14059 | 1462650 | 2017-02-21 10:30 | 2017-02-21 14:50 | 259.5167 | 11kV | 2854.6833 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171110 A & B phase DOLF : 20 Amp | February | 2017 | 2017Q3 | 2017 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2017-02-21 | N | 259.5167 | N | 1 | N | N | 1.1101 | 39.4971 | 2086.1184
[7 empty] | 9730 | 12742 | 1463089 | 2017-02-22 08:53 | 2017-02-22 14:15 | 322 | 11kV | 322 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171111 Single phase DOLF : 10 Amp Excluded OMS 1463089 | February | 2017 | 2017Q3 | 2017 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2017-02-22 | N | 322 | N | 8 | N | N | 1.1101 | 39.4971 | 235.3081
[7 empty] | 9205 | 6540 | 1463210 | 2017-02-22 12:05 | 2017-02-22 15:10 | 185 | 11kV | 370 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171112 A Phase DOLF : 10 Amp Excluded OMS 1463210 | February | 2017 | 2017Q3 | 2017 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2017-02-22 | N | 185 | N | 8 | N | N | 1.1101 | 39.4971 | 270.3851
[7 empty] | 9028 | 4356 | 1463296 | 2017-02-22 14:40 | 2017-02-22 16:15 | 95 | 11kV | 380 | 4 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171113 B Phase DOLF : 10 Amp Bird | February | 2017 | 2017Q3 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2017-02-22 | N | 95 | N | 8 | N | N | 1.1101 | 39.4971 | 277.6928
[7 empty] | 9671 | 12030 | 1463307 | 2017-02-22 15:08 | 2017-02-22 16:29 | 81 | 11kV | 56133 | 693 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn13000 Lake Munmorah Panel 1 "S61296" fdr has tripped Signals: 11kv trip Relays: A 7 B OC EFI's:Nil Cause:Tree branch at Pole BU94 See 1463307 exclude 1466324 | February | 2017 | 2017Q3 | 2017 | ZN13000:PA1 | ZN13000:PA1 | ZN13000/000001 | CENTRAL COAST | OH | Veg | 2017-02-22 | N | 81 | N | 8 | N | N | 1.1101 | 39.4971 | 41020.3408
[7 empty] | 9099 | 5348 | 1463494 | 2017-02-22 21:00 | 2017-02-22 22:30 | 90 | 11kV | 450 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kv feeder AB 3290 to LB3296 tee Sub 7267 and Sub 7828 Ex Panel 6 "Lewis St" feeder @ S35900 Potts Hill Remarks: pole fire. 11kv on X arm | February | 2017 | 2017Q3 | 2017 | ZN35900:PA6 | ZN35900:PA6 | ZN35900/000006 | CUMBERLAND | OH | Not Veg | 2017-02-22 | N | 90 | N | 8 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 9875 | 14477 | 1463382 | 2017-02-22 17:54 | 2017-02-22 23:55 | 361 | 11kV | 215854 | 1742 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12600 Lisarow Panel 3 "S12399" fdr tripped Signals: 11kv trip Relays: TImed Earth Fault, EFI EFI's: S14623 S14247 Tree/Branch brought down OH See 1463533,4 exclude 1463382 | February | 2017 | 2017Q3 | 2017 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2017-02-22 | N | 123.9116 | N | 8 | N | N | 1.1101 | 39.4971 | 157739.7366
[7 empty] | 9527 | 10326 | 1463358 | 2017-02-22 17:29 | 2017-02-23 01:08 | 459 | 11kV | 46086 | 318 | HV | Vegetation Blow/Fall In | Vegetation | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa8 RE49506 Springs Rd has tripped Relays: OC trip RE44995 Kulnura has tripped and reclosed Relays: OC trip RE44994 Mangrove Creek has tripped and reclosed Relays: OC trip @1917 RE44995 Kulnura has tripped Relays: OC trip Abnormal: LB45195 Closed, AB43601 open and defective Cause: Branch hit 11kv near PT18718. knocked 11kv off 2 standoff insulators. DOp then broke AB45021 when attempting to isolate. All three reclosers are 80Amp See 1463525,6,7,8,9,30 exclude 1463358,60,435 | February | 2017 | 2017Q3 | 2017 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2017-02-22 | N | 144.9245 | N | 8 | N | N | 1.1101 | 39.4971 | 33678.2895
[7 empty] | 10354 | 20281 | 1463421 | 2017-02-22 20:31 | 2017-02-23 01:20 | 289 | 11kV | 182574 | 2039 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12640 Umina Panel 13 "Patonga" fdr tripped Signals: 11k vtrip Relays: A & C phase Inst and Time, EF timed, EFI Tree/branch brought down OH See 1463540,2,3 | February | 2017 | 2017Q3 | 2017 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Veg | 2017-02-22 | N | 89.541 | N | 8 | N | N | 1.1101 | 39.4971 | 133419.6942
[7 empty] | 10295 | 19519 | 1463516 | 2017-02-23 10:30 | 2017-02-23 14:45 | 255 | 11kV | 1785 | 7 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 171125 Single phase Broken 11kV crosarm at pole DV-91762. | February | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2017-02-23 | N | 255 | N | 9 | N | N | 1.1101 | 39.4971 | 1304.4254
[7 empty] | 8826 | 1749 | 1463599 | 2017-02-23 13:54 | 2017-02-23 14:54 | 60 | 11kV | 28780 | 482 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn1673 Turramurra Pnl.19 tripped on: Earth Fault, EFI Field EFIs All down to S4624 UG cable damaged by contractor at 14 Neringah Ave | February | 2017 | 2017Q3 | 2017 | ZN1673:PA19 | ZN1673:PA19 | ZN01673/000019 | KU-RING-GAI | UG | Not Veg | 2017-02-23 | N | 59.7095 | N | 9 | N | N | 1.1101 | 39.4971 | 21031.5751
[7 empty] | 9649 | 11773 | 1463597 | 2017-02-23 13:56 | 2017-02-23 14:55 | 59 | 11kV | 944 | 16 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 171132 A phase DOLF : Burntup DOLF assembly at sub 52449. Excluded OMS No. 1463597 | February | 2017 | 2017Q3 | 2017 | 507:80917 | 507:80917 | ZN00507/080917 | CESSNOCK | OH | Not Veg | 2017-02-23 | N | 59 | N | 9 | N | N | 1.1101 | 39.4971 | 689.8474
[7 empty] | 10144 | 17754 | 1463671 | 2017-02-23 14:01 | 2017-02-23 16:30 | 149 | 11kV | 116390 | 817 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn5868 Gore Hill - Pnl.27 tripped on: A Phase O/C, EFI Field EFIs: S5623, S6594 UG cable hit by excavator at 486 Pacific Hwy See 1464491 1464494 | February | 2017 | 2017Q3 | 2017 | ZN5868:PA27 | ZN5868:PA23 | ZN05868/000023 | NORTH SYDNEY | UG | Not Veg | 2017-02-23 | N | 142.4602 | N | 9 | N | N | 1.1101 | 39.4971 | 85054.3791
[7 empty] | 10216 | 18720 | 1463506 | 2017-02-23 11:05 | 2017-02-23 18:10 | 425 | 11kV | 1275 | 3 | HV | Fire (Non Ausgrid) | UNKNOWN | 3rd Party Asset | Unplanned | No Weather Impact | N | S62215 Muir Dasea No.2 Interrupted by Dop Farrar for safety as there were concerns that the adjacent building on fire may collapse on kiosk. Abnormal: Sw/A @ S62215 closed, Sw/B @ S.Muir Dasea No.7 open REmarks: fire. Large factory fire at the waste management centre - 15 Muir Rd. 11kv fdr restored. D & R #400748 is issued to make Dist #1 'WDNO' as S.62215 will be decommissioned. | February | 2017 | 2017Q3 | 2017 | ZN35900:PA22 | ZN35900:PA10 | ZN35900/000010 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2017-02-23 | N | 425 | N | 9 | N | N | 1.1101 | 39.4971 | 931.7324
[7 empty] | 8943 | 3286 | 1460642 | 2017-02-23 17:30 | 2017-02-23 18:10 | 40 | 11kV | 48320 | 1208 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa22 AB41815 to extent of feeder Centre phase zone side bond open circuited on AB41815 Lineworker to repair ASAP. LB48040 Closed See 1465223 exclude 1460642,3697 | February | 2017 | 2017Q3 | 2017 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2017-02-23 | N | 40 | N | 9 | N | N | 1.1101 | 39.4971 | 35310.8308
[7 empty] | 9863 | 14352 | 1463728 | 2017-02-23 20:05 | 2017-02-23 20:09 | 4 | 11kV | 1088 | 272 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Section of Pnl.25 @ Chatswood Zone interrupted from S63266 Mindarie Pinnaroo (Sw/B) for emergency repairs. Bamboo was on 11kV mains and burning near 44 Moore St. Cross power source and could not be switched. | February | 2017 | 2017Q3 | 2017 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Veg | 2017-02-23 | N | 4 | N | 9 | N | N | 1.1101 | 39.4971 | 795.0783
[7 empty] | 10213 | 18705 | 1463666 | 2017-02-23 15:55 | 2017-02-23 20:20 | 265 | 11kV | 530 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 171133 Single phase DOLF : 10 Amp Excluded OMS 1463666 | February | 2017 | 2017Q3 | 2017 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2017-02-23 | N | 265 | N | 9 | N | N | 1.1101 | 39.4971 | 387.3084
[7 empty] | 10331 | 20017 | 1463668 | 2017-02-23 19:10 | 2017-02-23 20:20 | 70 | 11kV | 3640 | 52 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171134 Section isolated to repair broken DOLF carrier sub 27803. | February | 2017 | 2017Q3 | 2017 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2017-02-23 | N | 70 | N | 9 | N | N | 1.1101 | 39.4971 | 2660.0046
[7 empty] | 10300 | 19533 | 1463882 | 2017-02-24 13:43 | 2017-02-24 15:55 | 132 | 11kV | 132 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171155 Single phase Loose LL Clamp at pole 9I-40054. Excluded OMS No. 1463882 | February | 2017 | 2017Q3 | 2017 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2017-02-24 | N | 132 | N | 3 | N | N | 1.1101 | 39.4971 | 96.4617
[7 empty] | 9902 | 14839 | 1463960 | 2017-02-24 18:00 | 2017-02-24 20:52 | 171.9 | 11kV | 8595 | 50 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 171156 3 phase interupted by Tom Mcfadgen to replace leaking Tx. dq OMS 1463960 | February | 2017 | 2017Q3 | 2017 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2017-02-24 | N | 171.9 | N | 3 | N | N | 1.1101 | 39.4971 | 6280.9725
[7 empty] | 9463 | 9630 | 1463995 | 2017-02-24 20:46 | 2017-02-24 23:35 | 169 | 11kV | 5746 | 34 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | S164919 Towlers Bay - All customers interrupted due to MG tripping on overload 11kV feeder from S16530 to S16419 out fo service defective with 60kVA MG set supplying S16419 Tcon advised customer to restrict load until 11kV feeder repaired | February | 2017 | 2017Q3 | 2017 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | Unknown | Not Veg | 2017-02-24 | N | 169 | N | 3 | N | N | 1.1101 | 39.4971 | 4199.0073
[7 empty] | 10016 | 16253 | 1464006 | 2017-02-25 04:25 | 2017-02-25 05:21 | 56 | 11kV | 43736 | 781 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Zn80 Chatswood - Pnl.31 tripped, reclosed and locked out on: IOC B and C Phase, reclose, timing, EFI Tree branch on mains adj PT1711 | February | 2017 | 2017Q3 | 2017 | ZN80:PA31 | ZN1193:PA15 | ZN01193/000015 | WILLOUGHBY | OH | Veg | 2017-02-25 | N | 56 | N | 9 | N | N | 1.1101 | 39.4971 | 31960.9788
[7 empty] | 9579 | 10974 | 1464004 | 2017-02-25 03:46 | 2017-02-25 05:40 | 114 | 11kV | 24738 | 217 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Rec35260 Pacific Cres East tripped to lockout relays: IOC trip Section of 11kv feeder Panel No3 "Binaville Ave fdr" @ ZN9118 Cronulla Remarks: tree/branch on OH mains. dop removed branch Bundenna nr Laurence St, supply restored | February | 2017 | 2017Q3 | 2017 | ZN9118:PA3 | ZN9118:PA3 | ZN09118/000003 | SUTHERLAND | OH | Veg | 2017-02-25 | N | 114 | N | 9 | N | N | 1.1101 | 39.4971 | 18077.8008
[7 empty] | 9175 | 6257 | 1464011 | 2017-02-25 05:44 | 2017-02-25 06:55 | 71 | 11kV | 116529 | 1749 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington Zn - Pnl.17 tripped on: Earth Fault Field EFIs: S4194, S50187, S671, S36251 UG cable fault from S36251 Queen Oxford (Sw/A) to S5853 Smith Halls (Sw/A) See 1464534 1464535 | February | 2017 | 2017Q3 | 2017 | ZN342:PA17 | ZN342:PA17 | ZN00342/000017 | WOOLLAHRA | UG | Not Veg | 2017-02-25 | N | 66.6261 | N | 9 | N | N | 1.1101 | 39.4971 | 85155.9562
[7 empty] | 9013 | 4105 | 1464016 | 2017-02-25 07:36 | 2017-02-25 08:23 | 47 | 11kV | 4355 | 93 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2466 Flemington 11kv Pnl 27 "Carter King" feeder tripped on Relays: Earth fault with fault check Signals: 11kv trip, Tx 3 group and zone earth Field efis: Pnl 27 to Sub 3110 Abnormal: sw/B closed at S8594 and Sw/A open at S7599 Remarks: UG fault. 11kv cable fault betwen S7599 Carter Uhrig #2 and S3110 Carter Hill #1 | February | 2017 | 2017Q3 | 2017 | ZN2466:PA27 | ZN2466:PA1 | ZN02466/000001 | CUMBERLAND | UG | Not Veg | 2017-02-25 | N | 46.828 | N | 9 | N | N | 1.1101 | 39.4971 | 3182.5055
[7 empty] | 9960 | 15393 | 1464034 | 2017-02-25 09:01 | 2017-02-25 10:56 | 115 | 11kV | 120090 | 1054 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | At Zn10996 Rockdale 11kv Pnl 9 "Farr Tabrett, etc" feeder tripped on Relays: A phase IOC Signals: 11kv trip, Tx1 group earth Remarks: Broken 11kv cross-arm in Richmond Rd beyond LK 30804. LV isolation at S10788 on separate interruption | February | 2017 | 2017Q3 | 2017 | ZN10996:PA9 | ZN10998:PA8 | ZN10998/000008 | BAYSIDE | OH | Not Veg | 2017-02-25 | N | 113.9374 | N | 9 | N | N | 1.1101 | 39.4971 | 87758.2299
[7 empty] | 9594 | 11177 | 1464083 | 2017-02-25 12:02 | 2017-02-25 12:45 | 43 | 11kV | 43 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171160 Single phase DOLF : 10 Amp RH DOLF replaced Excluded OMS 1464083 | February | 2017 | 2017Q3 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-02-25 | N | 43 | N | 9 | N | N | 1.1101 | 39.4971 | 31.4231
[7 empty] | 9055 | 4804 | 1464059 | 2017-02-25 10:38 | 2017-02-25 15:25 | 287 | 11kV | 108235 | 655 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | Ex Zn12570 Avoca section of pa33 McMasters Beach RE50407 The Scenic Bounty tripped, reclosed, and locked out on: Relays: Overcurrent Signals: Nil Defective AB40455 appears to be shorting to earth on broken phase during rain periods See 1465231,4,5,6,7 exclude 1464059,79 | February | 2017 | 2017Q3 | 2017 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2017-02-25 | N | 165.2443 | N | 9 | N | N | 1.1101 | 39.4971 | 79094.9456
[7 empty] | 8771 | 1040 | 1464134 | 2017-02-25 16:18 | 2017-02-25 17:50 | 92 | 11kV | 184 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 171163 A Phase DOLF : 10 Amp Excluded OMS 1464134 | February | 2017 | 2017Q3 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2017-02-25 | N | 92 | N | 9 | N | N | 1.1101 | 39.4971 | 134.4618
[7 empty] | 9292 | 7378 | 1464187 | 2017-02-26 02:20 | 2017-02-26 03:45 | 85 | 11kV | 5100 | 60 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | Ex Zn12650 West Gosford Panel 9 "Wyoming" PT13893 Dalton West Maidens HDO operated Possum caused flashover at PT damaging fuse assembly. Requires replacement. In cross zone LV parallel See 1465264 exclude 1464187 | February | 2017 | 2017Q3 | 2017 | ZN12650:PA9 | ZN12650:PA9 | ZN12650/000009 | CENTRAL COAST | OH | Not Veg | 2017-02-26 | N | 85 | N | 6 | N | N | 1.1101 | 39.4971 | 3726.9296
[7 empty] | 8913 | 2863 | 1464201 | 2017-02-26 06:40 | 2017-02-26 08:08 | 88 | 11kV | 7040 | 80 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 171167 B Phase DOLF : 40 Amp possum on trans Excluded OMS 1464214 | February | 2017 | 2017Q3 | 2017 | 221:11900 | 221:11900 | ZN00221/011900 | LAKE MACQUARIE | OH | Not Veg | 2017-02-26 | N | 88 | N | 6 | N | N | 1.1101 | 39.4971 | 5144.6244
[7 empty] | 9113 | 5517 | 1464216 | 2017-02-26 07:29 | 2017-02-26 08:34 | 65 | 11kV | 1755 | 27 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Rain Heavy | N | Ex Zn12690 Berkeley Vale section of Pa16 PT14051 Pleasant Valley Manns centere phase and roadside 31Amp HDO's operated Branch rested across HV insulators on transformers. Shrouds on Transformer have been damaged and require replacing See 1465275 exclude 1464216 | February | 2017 | 2017Q3 | 2017 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2017-02-26 | N | 65 | N | 6 | N | N | 1.1101 | 39.4971 | 1282.5022
[7 empty] | 9556 | 10735 | 1464142 | 2017-02-25 17:45 | 2017-02-26 09:05 | 920 | 11kV | 214586 | 1012 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Zn14144 Wamberal 11kV Pa2 Fdr tripped, reclosed, tripped and locked out on Relays: Earth Fault, EFI, SEF, lockout EFI's: S14885 S11086 S12742 S12737 S18448 Signal: 11kv trip Tree branch brought down 11kV overhead between LB45127 and AB45128. Also fault current caused 11kv Overhead to come down between LB4217 and AB4143. AB45127 would not open DMA created See 1465254,5,6,7,8 Exclude 1464142,4,52,79,80,1 | February | 2017 | 2017Q3 | 2017 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2017-02-25 | N | 212.0415 | N | 9 | N | N | 1.1101 | 39.4971 | 156813.1196
[7 empty] | 10069 | 16789 | 1464200 | 2017-02-26 06:05 | 2017-02-26 15:00 | 535 | 11kV | 64139 | 407 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn35800 Bankstown 11kv Pnl 18 "Gibson Atkinson" feeder tripped on Relays: B and C phase IOC Remarks: tree/branch brought down OH. Cnr Enterprise and Watson Rd Padstow | February | 2017 | 2017Q3 | 2017 | ZN35800:PA18 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2017-02-26 | N | 157.5897 | N | 6 | N | N | 1.1101 | 39.4971 | 46870.8894
[7 empty] | 10050 | 16566 | 1464306 | 2017-02-26 16:40 | 2017-02-26 21:50 | 310 | 11kV | 14880 | 48 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 171170 Linesman found 2.5mm2 earth wire on x-arm. X-arm had burnt through at brace bolt. 11kV laying onto service. Services checked out by EMSO's for possible HV into LV. Isolated for safety to replace x-arm | February | 2017 | 2017Q3 | 2017 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2017-02-26 | N | 310 | N | 6 | N | N | 1.1101 | 39.4971 | 10873.8651
[7 empty] | 10274 | 19251 | 1464343 | 2017-02-26 21:40 | 2017-02-26 23:52 | 132 | 11kV | 64356 | 784 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Panel 24R "Burnes Rd" tripped on B & C overcurrent EFI EFI's: Nil Signals: 11kv trip Abnormal: LB63855 open Cause: Cause not ascertained. reports from around #56 Bridge Rd See 1465278,9,80 exclude 1464343,4 | February | 2017 | 2017Q3 | 2017 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2017-02-26 | N | 82.0867 | N | 6 | N | N | 1.1101 | 39.4971 | 47029.4666
[7 empty] | 9886 | 14664 | 1464519 | 2017-02-27 12:57 | 2017-02-27 14:40 | 103 | 11kV | 103 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12640 Umina section of Pa13 PT11051 Juno Point A phase HDO failed fuse failure See 1465281 exclude 1464519 | February | 2017 | 2017Q3 | 2017 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2017-02-27 | N | 103 | N | 2 | N | N | 1.1101 | 39.4971 | 75.2694
[7 empty] | 9115 | 5541 | 1464675 | 2017-02-28 00:47 | 2017-02-28 02:45 | 118 | 11kV | 130184 | 1310 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn15006 Dee Why West - Pnl.13 tripped on: B & C phase O/C Possum on mains outside 16 Suffolk Ave. Repairs required to OH mains. See 1465103 1465104 1465105 | February | 2017 | 2017Q3 | 2017 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | OH | Not Veg | 2017-02-28 | N | 99.3771 | N | 8 | N | N | 1.1101 | 39.4971 | 95134.6274
[7 empty] | 10315 | 19781 | 1464710 | 2017-02-28 08:20 | 2017-02-28 09:43 | 83 | 11kV | 166 | 2 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | @Zn1610 Homebush Bay 11kv Panel #1 labelled "S3735 Hill Rd car Pk" tripped Remarks: 11kv underground fault from Panel #1 @ Zn1610 Homebush Bay to Sw/B @ S3735 Hill Rd Car Pk | February | 2017 | 2017Q3 | 2017 | ZN1610:PA1 | ZN1610:PA1 | ZN01610/000001 | PARRAMATTA | UG | Not Veg | 2017-02-28 | N | 83 | N | 8 | N | N | 1.1101 | 39.4971 | 121.3079
[7 empty] | 9298 | 7429 | 1464704 | 2017-02-28 10:45 | 2017-02-28 12:40 | 115 | 11kV | 1335 | 13 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 171181 No protection operation. Section isolated to repair 11kV xarm pole JU-31876. Excluded OMS 1464768 & 1464704. | February | 2017 | 2017Q3 | 2017 | 203:8082 | 204:82708 | ZN00204/082708 | NEWCASTLE | OH | Not Veg | 2017-02-28 | N | 102.6923 | N | 8 | N | N | 1.1101 | 39.4971 | 975.5786
[7 empty] | 9077 | 5155 | 1464673 | 2017-02-27 23:26 | 2017-02-28 14:45 | 919 | 11kV | 19299 | 21 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12580 Erina section of Pa12 PT12035 Eirina Valley Ports 0.5 broken cross arms and pole large tree down on mains See 1464688 exclude 1464673 | February | 2017 | 2017Q3 | 2017 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Veg | 2017-02-27 | N | 919 | N | 2 | N | N | 1.1101 | 39.4971 | 14103.14
[7 empty] | 9954 | 15343 | 1464720 | 2017-02-28 08:42 | 2017-02-28 14:50 | 367.7333 | 11kV | 140106.4 | 381 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12640 Umina section of Pa13 "Patonga" HV bond burnt off near AB42071 | February | 2017 | 2017Q3 | 2017 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2017-02-28 | N | 367.7333 | N | 8 | N | N | 1.1101 | 39.4971 | 102385.6247
[7 empty] | 9761 | 13190 | 1464772 | 2017-02-28 11:03 | 2017-02-28 15:35 | 272 | 11kV | 162756 | 1223 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Zn2400 berowra - Pnl.15 tripped on: C pHase O/C, Earth Fault, EFI Field EFIs: S4404, S4850, S48076, S4851 S4922 S4921 S49939 Cause not ascertained. Possible UG cable fault developing See 1465081 1465082 | February | 2017 | 2017Q3 | 2017 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Veg | 2017-02-28 | N | 133.0793 | N | 8 | N | N | 1.1101 | 39.4971 | 118937.2843
[7 empty] | 8994 | 3923 | 1464767 | 2017-02-28 10:35 | 2017-02-28 18:35 | 480 | 11kV | 20677 | 58 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | REC1238 Milsons Passage - tripped on: O/C trip Large tree branch on mains beyond LB64398 and before tee off to PT645 See 1465086 1465088 1465087 | February | 2017 | 2017Q3 | 2017 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2017-02-28 | N | 356.5 | N | 8 | N | N | 1.1101 | 39.4971 | 15110.1417
[7 empty] | 10108 | 17309 | 1465030 | 2017-02-28 22:05 | 2017-02-28 23:45 | 100 | 11kV | 4497 | 537 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn12620 Noraville section of Pa11 "Norah Head" RE45053 Norah Head tripped & reclsoed on IOC & Earth Fault Fried possum found at Base of PT See 1465289,90 exclude 1465030,1,2,5,40 | February | 2017 | 2017Q3 | 2017 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2017-02-28 | N | 8.3743 | N | 8 | N | N | 1.1101 | 39.4971 | 3286.275
[7 empty] | 8952 | 3414 | 1464893 | 2017-02-28 17:21 | 2017-03-01 00:40 | 439 | 11kV | 1317 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 171193 Tapping burnt off at pole FR-44790 to sub 47821. | February | 2017 | 2017Q3 | 2017 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Not Veg | 2017-02-28 | N | 439 | N | 8 | N | N | 1.1101 | 39.4971 | 962.4248
[7 empty] | 9058 | 4836 | 1465109 | 2017-03-01 08:30 | 2017-03-01 10:58 | 148 | 11kV | 1712 | 39 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 171209 Tree on LV mains at pole IP-82404. Earlier trip & reclose, see 171208 LV mains down Excluded OMS 1465109 | March | 2017 | 2017Q3 | 2017 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2017-03-01 | N | 43.8974 | N | 3 | N | N | 1.1101 | 39.4971 | 1251.0791
[7 empty] | 8729 | 169 | 1465132 | 2017-03-01 10:09 | 2017-03-01 11:30 | 81 | 11kV | 2239 | 31 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn8000 Macquarie Park - Pnl.10 tripped on: Left side A & B phase O/C, EFI UG cable fault - 10L front line section | March | 2017 | 2017Q3 | 2017 | ZN8000:PA10 | ZN35500:PA14 | ZN35500/000014 | RYDE | UG | Not Veg | 2017-03-01 | N | 72.2258 | N | 3 | N | N | 1.1101 | 39.4971 | 1636.1952
[7 empty] | 9006 | 4019 | 1465263 | 2017-03-01 15:32 | 2017-03-01 21:00 | 328 | 11kV | 97694 | 1077 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN3922 Drummoyne 11kv Pnl 17 "Jersey Barnstable" feeder tripped on Relays: A phase overcurrent with fault check Signals: 11kv trip, Tx 2 group and zone earth with efi Abnnormal: DMA between S49979 to S1487 Remarks: UG fault. Restored S49979 at 1804. Cable fault between S8369 Cookatoo Island #5 to S49979 Longview Bayville | March | 2017 | 2017Q3 | 2017 | ZN3922:PA17 | ZN3922:PA17 | ZN03922/000017 | INNER WEST | UG | Not Veg | 2017-03-01 | N | 90.7094 | N | 3 | N | N | 1.1101 | 39.4971 | 71391.8937
[7 empty] | 8760 | 811 | 1465365 | 2017-03-02 04:34 | 2017-03-02 06:13 | 99 | 11kV | 82715 | 841 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn1673 Turramurra - pnl.13 tripped on: A & C phase IOC 11kV UGOH crossarm above LB35270 failed. See 1465796 1465797 SE: 1465574 | March | 2017 | 2017Q3 | 2017 | ZN1673:PA13 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | OH | Not Veg | 2017-03-02 | N | 98.3532 | N | 5 | N | N | 1.1101 | 39.4971 | 60445.6823
[7 empty] | 10031 | 16366 | 1465373 | 2017-03-02 06:24 | 2017-03-02 08:15 | 111 | 11kV | 111 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Replaced 10A DOLF A phase - field staff suspecting fuse fatigue | March | 2017 | 2017Q3 | 2017 |  |  |  |  | OH | Not Veg | 2017-03-02 | N | 111 | N | 5 | N | N | 1.1101 | 39.4971 | 81.1155
[7 empty] | 9299 | 7440 | 1465520 | 2017-03-02 13:05 | 2017-03-02 14:55 | 110 | 11kV | 220 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171221 Single phase DOLF : 10 Amp Cockatoo contacted mains blew both DOlf's. Excluded OMS 1465520 | March | 2017 | 2017Q3 | 2017 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2017-03-02 | N | 110 | N | 5 | N | N | 1.1101 | 39.4971 | 160.7695
[7 empty] | 9178 | 6272 | 1465528 | 2017-03-02 13:21 | 2017-03-02 15:08 | 107 | 11kV | 124442 | 1224 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | U/G Cable | Unplanned | No Weather Impact | N | At S2835 Burwood 11kv Panel No.31 tripped on Relays: B phase E/F, EFI, fault check Signals: 11kv trip, Tx 3 Group E Abnormal: Sw/B Closed at S49069, Sw/B Opne @ S5392, @ S3746 Sw/D closed, Sw/A open Sw/B Closed @ S1980, Sw/B open @ S3484 Remarks: cause not ascertained. 11kv feeder fault from Sw/B @ S4872 Victoria Homebush to Sw/A @ S2010 Birnan Grove. Note @ S2010 RMI is HAz region to organize extension to enable fault location. Note @ S2010 TCon required to check EFI operation and reset button sticky operation | March | 2017 | 2017Q3 | 2017 | ZN2835:PA31 | ZN2835:PA31 | ZN02835/000031 | STRATHFIELD | UG | Not Veg | 2017-03-02 | N | 101.6683 | N | 5 | N | N | 1.1101 | 39.4971 | 90938.5432
[7 empty] | 9976 | 15609 | 1465554 | 2017-03-02 14:17 | 2017-03-02 16:25 | 127.7667 | 11kV | 15332 | 120 | HV | 3rd Party Vehicle | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171226 A Phase DOLF : 20 Amp A phase distribution : 400 Amp Both DOLf and LVF blew after car hit pole and cross arm failed corner of Maitland and Marlton Rd. | March | 2017 | 2017Q3 | 2017 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2017-03-02 | N | 127.7667 | N | 5 | N | N | 1.1101 | 39.4971 | 11204.1734
[7 empty] | 9406 | 8830 | 1465835 | 2017-03-03 13:28 | 2017-03-03 14:30 | 62 | 11kV | 10075.9 | 163 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | S104 Wooloomooloo - 11kV CB "S47354 feeder" tripped on Intertrip receive Abnormal: Feeder from S206 Cathedral St "S47354 feeder" out of service to S47354 (Sw/B) Staff error: Protection fitter was working on the 11kV CB @ S206 when he inadvetently energised the pilot to S104 which tripped the "S47354 feeder" CB See 1465835 CC1: 22-"Refer to SOp" | March | 2017 | 2017Q3 | 2017 | ZN931:PA25 | ZN931:PA25 | ZN00931/000025 | SYDNEY | Unknown | Not Veg | 2017-03-03 | N | 61.8153 | N | 4 | N | N | 1.1101 | 39.4971 | 7363.1705
[7 empty] | 9177 | 6271 | 1465871 | 2017-03-03 15:05 | 2017-03-03 16:05 | 60 | 11kV | 53338 | 906 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn2835 Burwood 11kv feeder Panel No:27 "Gipps Flavelle" feeder tripped Relays: B phase timed O/C, EFI, fault check Remarks: UG fault. 11kv feeder fault from Sw/B @ S4855 Gipps Flavelle to Sw/A @ S8997 Flavelle Wordsworth | March | 2017 | 2017Q3 | 2017 | ZN2835:PA27 | ZN2835:PA27 | ZN02835/000027 | CANADA BAY | UG | Not Veg | 2017-03-03 | N | 58.872 | N | 4 | N | N | 1.1101 | 39.4971 | 38977.8372
[7 empty] | 10013 | 16216 | 1465872 | 2017-03-03 15:04 | 2017-03-03 16:22 | 78 | 11kV | 24825 | 381 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn711 Blackwattle Bay - Pnl.22 tripped on: Earth Fault with EFI Field EFIs: S5471 & S6509 UG cable fault between S6509 (Sw/B) and S2983 (Sw/A) | March | 2017 | 2017Q3 | 2017 | ZN711:PA22 | ZN384:PA65 | ZN00384/000065 | SYDNEY | UG | Not Veg | 2017-03-03 | N | 65.1575 | N | 4 | N | N | 1.1101 | 39.4971 | 18141.3778
[7 empty] | 9145 | 5942 | 1465956 | 2017-03-03 20:21 | 2017-03-03 22:01 | 100 | 11kV | 68882 | 1205 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | LID 171239 2 fault opweration Instantaneous Earth Fault; Instantaneous Overcurrent Cable fault between Sw 35481 and Sw 28862. Will need cable tested for location as Sw 28862 is a Hazemeyer, Region staff should arrange to extend the area for testing. A prot Inst OC and Inst EF B prot OC and Fault trip. Excluded OMS 1465956 | March | 2017 | 2017Q3 | 2017 | 528:83013 | 528:83013 | ZN00528/083013 | MAITLAND | UG | Not Veg | 2017-03-03 | N | 57.1635 | N | 4 | N | N | 1.1101 | 39.4971 | 50336.9339
[7 empty] | 9304 | 7495 | 1466068 | 2017-03-04 12:20 | 2017-03-04 13:00 | 40 | 11kV | 280 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 171241 A Phase DOLF : 16 Amp Excluded OMS 1466068 | March | 2017 | 2017Q3 | 2017 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2017-03-04 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 8745 | 544 | 1466069 | 2017-03-04 12:19 | 2017-03-04 13:25 | 66 | 11kV | 92928 | 1408 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S187 crows Nest Panel 17 tripped on Relays: E/F, EFI and Faultn Check Signals: 11kV trip and TX11 Group Earth Cause: UG cable fault between S187 Panel 17 and S35756 SW/A dn S3926 SW/A See OMS 1466069 1460753 1466072 1466135 | March | 2017 | 2017Q3 | 2017 | ZN187:PA17 | ZN187:PA17 | ZN00187/000017 | NORTH SYDNEY | UG | Not Veg | 2017-03-04 | N | 66 | N | 4 | N | N | 1.1101 | 39.4971 | 67909.0415
[7 empty] | 9697 | 12303 | 1466111 | 2017-03-04 14:45 | 2017-03-04 16:16 | 91 | 11kV | 31126 | 384 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn15014 Mona Vale 11kv Panel 16 "Pittwater Waratah" tripped on: Relays: Earth Fault. EFI, Fault CHeck Signals: 11kv trip, Zone Earth EFI'S:S15221 UG Fault from S15221:B tp S16825:A to S16277:A See 1466597, 1466599,600 exclude 1466111 | March | 2017 | 2017Q3 | 2017 | ZN15014:PA16 | ZN15014:PA16 | ZN15014/000016 | NORTHERN BEACHES | UG | Not Veg | 2017-03-04 | N | 81.0573 | N | 4 | N | N | 1.1101 | 39.4971 | 22745.9627
[7 empty] | 9870 | 14434 | 1465984 | 2017-03-04 06:32 | 2017-03-04 21:00 | 868 | 11kV | 239244 | 886 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn12600 Lisarow Panel 11 "The Wyoming" fdr tripped and locked out on timed overcurent and earth fault relay, EFI Causes: Tree Brnach brought down OH near: 1. Near 104 chamberlain rd wyoming 2. UGOH to S12348 Calantha Maranoa from LB77509 side See 1466589,91,2,3,4 exclude 1465984,6041,2 Note: customers were alsw prev impacted by subtrans T&R at 04/03/17 06:31- 04/03/17 06:32 see OMS 1466581 | March | 2017 | 2017Q3 | 2017 | ZN12600:PA11 | ZN12600:PA11 | ZN12600/000011 | CENTRAL COAST | OH | Veg | 2017-03-04 | N | 270.0271 | N | 4 | N | N | 1.1101 | 39.4971 | 174832.4587
[7 empty] | 8917 | 2910 | 1466215 | 2017-03-05 06:48 | 2017-03-05 08:25 | 97 | 11kV | 194 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 171244 C Phase DOLF : 10 Amp Excluded OMS 1466215 | March | 2017 | 2017Q3 | 2017 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2017-03-05 | N | 97 | N | 5 | N | N | 1.1101 | 39.4971 | 141.7695
[7 empty] | 9082 | 5217 | 1466223 | 2017-03-05 08:09 | 2017-03-05 14:00 | 351 | 11kV | 10530 | 30 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 171245 Single phase HV down into LV between subs 25619 & 52546 Mount Vincent IR 49357 DID NOT operate, Please investigate Excluded oms 1466238 CC1: 22-"Refer to SOp" | March | 2017 | 2017Q3 | 2017 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2017-03-05 | N | 351 | N | 5 | N | N | 1.1101 | 39.4971 | 7695.0134
[7 empty] | 8834 | 1827 | 1466249 | 2017-03-05 16:50 | 2017-03-05 18:40 | 110 | 11kV | 2420 | 22 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa1 "Gunderman" Between LB40596 to USL44820 tree branch on OH Mains See 1466640 exclude 1466249,309 | March | 2017 | 2017Q3 | 2017 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2017-03-05 | N | 110 | N | 5 | N | N | 1.1101 | 39.4971 | 1768.4646
[7 empty] | 9656 | 11837 | 1466320 | 2017-03-05 19:58 | 2017-03-05 20:45 | 47 | 11kV | 47 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Electrical Storm | N | LID 171255 DOLF : 10 Amp It appears the DOLF may have been fatigued and blown after line fuse 74094 was replaced. Excluded OMS 1466320 | March | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-03-05 | N | 47 | N | 5 | N | N | 1.1101 | 39.4971 | 34.3462
[7 empty] | 10053 | 16608 | 1466324 | 2017-03-05 20:52 | 2017-03-05 22:03 | 71 | 11kV | 35500 | 500 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | S10994 Mortdale Panel 14L "Boundary Gungah" fdr tripped, reclosed, tripped and locked out Relays: IOC, Earth fault, reclose timer, lockout Signals: 11kv trip EFIs - Nil Remarks: Animals/birds. Dead Possum found at base of 11kv UGOH pole on corner of Blackshore st and Boundary Rd Peakhurst. Mains to inspect in day light hours. | March | 2017 | 2017Q3 | 2017 | ZN10994:PA14 | ZN10994:PA14 | ZN10994/000014 | GEORGES RIVER | OH | Not Veg | 2017-03-05 | N | 71 | N | 5 | N | N | 1.1101 | 39.4971 | 25942.3529
[7 empty] | 9237 | 6908 | 1466394 | 2017-03-06 09:26 | 2017-03-06 10:19 | 53 | 11kV | 371 | 7 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S1610 Homebush Bay Panel 5 'S5324 Superdome No 1" fdr tripped on Relays: EF, EFI Signals: 11kv trip, Tx1 GE Remarks: UG fault. 11kv UG fault from S1610 Homebush Panel 5 to S5324 Superdome No 1 | March | 2017 | 2017Q3 | 2017 | ZN1610:PA5 | ZN1610:PA5 | ZN01610/000005 | PARRAMATTA | UG | Not Veg | 2017-03-06 | N | 53 | N | 5 | N | N | 1.1101 | 39.4971 | 271.1159
[7 empty] | 10210 | 18658 | 1466505 | 2017-03-06 12:29 | 2017-03-06 14:00 | 91 | 11kV | 92471 | 2264 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca Panel 35 "Avoca Melville 0.3" tripped, reclosed and locked out on Signals:11kv trip Relays: Basler Relay 51AB: A&B phase OC, lockout EFI's: Nil Abnormal: AB41815 is open and defective, LB48040 closed Cause: Tree was found on the 11kV OH adjacent AB43330 See 1466880,2,3 exclude 1466505,14,48 | March | 2017 | 2017Q3 | 2017 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2017-03-06 | N | 40.8441 | N | 5 | N | N | 1.1101 | 39.4971 | 67575.0794
[7 empty] | 8741 | 429 | 1466472 | 2017-03-06 11:32 | 2017-03-06 15:55 | 263 | 11kV | 11213 | 56 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Panel 12 "Yarramalong" tripped, reclosed and locked out Signals: OC Trip, EF Trip, Lockout Cause: Tree Branch was found on 11kv OH outside 325 brush creeek rd, cedar brush creek. An 11kv Crossarm was also broken See 1466874,6 exclude 1466472,80 | March | 2017 | 2017Q3 | 2017 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2017-03-06 | N | 200.2321 | N | 5 | N | N | 1.1101 | 39.4971 | 8194.1297
[7 empty] | 9373 | 8436 | 1466533 | 2017-03-06 13:04 | 2017-03-06 16:22 | 198 | 11kV | 198 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 171260 DOLF : 10 Amp | March | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-03-06 | N | 198 | N | 5 | N | N | 1.1101 | 39.4971 | 144.6926
[7 empty] | 9773 | 13309 | 1466732 | 2017-03-07 02:24 | 2017-03-07 08:25 | 361 | 11kV | 20863 | 58 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Delay due to: Next available L/men required to patrol,unsafe to patrol through bushland in dark Cause: Lineworks reported large tree on distributor wires o/S 19-23 bridge St. Tree trimming contractor removed with L/W assistance See OMS 1467079 1467080 1466732 | March | 2017 | 2017Q3 | 2017 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2017-03-07 | N | 359.7069 | N | 7 | N | N | 1.1101 | 39.4971 | 15246.065
[7 empty] | 10145 | 17768 | 1466615 | 2017-03-06 15:30 | 2017-03-07 08:40 | 1030 | 11kV | 141288 | 1107 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN3472 Sefton 11kv Panel 35 labelled "S.7032 Rose Cres" tripped Panel 34 @ Zn3472 Sefton tripped & restored @ 1637 Abnormals: closed Sw/A @ S1105 Meroo St, Open Sw/A @ S1921 St John Rd, Open Panel 8 @ Zn3472 Sefton (out of service) Remarks: UG fault. 11kv underground fault from Sw/B @ S6200 park regents Park No.1 to Sw/A @ S7035 Princes Park to Sw/B @ S48886 Alexander Princes. Outage report available upon request | March | 2017 | 2017Q3 | 2017 | ZN3472:PA34 | ZN3472:PA34 | ZN03472/000034 | CUMBERLAND | UG | Not Veg | 2017-03-06 | N | 127.6314 | N | 5 | N | N | 1.1101 | 39.4971 | 103249.1031
[7 empty] | 9295 | 7411 | 1466756 | 2017-03-07 07:36 | 2017-03-07 09:40 | 124 | 11kV | 124 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Zn15002 Narrabeen section of Pa8 "Nareen Tatiora" Zn16217 Warriewood Square #1 Tx3 RMI Cause not ascertained. Suspect TX or cable RMI requires switching to remove fuse to check See 1467404 exclude 1466756 | March | 2017 | 2017Q3 | 2017 |  |  |  | NORTHERN BEACHES | OH | Veg | 2017-03-07 | N | 124 | N | 7 | N | N | 1.1101 | 39.4971 | 90.6155
[7 empty] | 9566 | 10849 | 1466787 | 2017-03-07 09:17 | 2017-03-07 11:25 | 128 | 11kV | 128 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171275 A & B phase : 10 Amp REPLACED 2 x 10amp DOLFS AT SUB 72994 ON A & B PHASES Excluded OMS 1466787 | March | 2017 | 2017Q3 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-03-07 | N | 128 | N | 7 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 9188 | 6353 | 1466862 | 2017-03-07 12:17 | 2017-03-07 13:13 | 56 | 11kV | 34979 | 710 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn10997 Sans Souci - Pnl.11 tripped on: B phase IOC Field EFIs: S10454, S10290, S10103 UG cable fault from S10103 Plimsoll Nelson to S10154 Weelington Plimsoll See 1467050 1467051 | March | 2017 | 2017Q3 | 2017 | ZN10997:PA11 | ZN10997:PA11 | ZN10997/000011 | GEORGES RIVER | UG | Not Veg | 2017-03-07 | N | 49.2662 | N | 7 | N | N | 1.1101 | 39.4971 | 25561.6215
[7 empty] | 10052 | 16598 | 1466772 | 2017-03-07 08:26 | 2017-03-07 13:20 | 294 | 11kV | 76998 | 663 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171277 2 fault operations C Phase Tree fell on mains off Tarean rd near allen Rd. Excluded OMS 1466798 | March | 2017 | 2017Q3 | 2017 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2017-03-07 | N | 116.1357 | N | 7 | N | N | 1.1101 | 39.4971 | 56267.8673
[7 empty] | 9235 | 6891 | 1466878 | 2017-03-07 12:44 | 2017-03-07 13:45 | 61 | 11kV | 61337 | 1700 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn36300 Balgowlah Nth Panel 8 "Innes Condamine" tripped on: 50 T B/C 150 TN EFI EFC. :/O Frame leakage prohibition - Frame leakage panel Abnormal: LB61274 closed SwB S15107 Closed (1 centre) 11kv UGOH to S15107 SwB See 1467407,8 exclude 1466873,8,9,81,88,90 | March | 2017 | 2017Q3 | 2017 | ZN36300:PA8 | ZN36300:PA8 | ZN36300/000008 | NORTHERN BEACHES | Unknown | Unknown | 2017-03-07 | N | 36.0806 | N | 7 | N | N | 1.1101 | 39.4971 | 44823.2705
[7 empty] | 9641 | 11696 | 1467010 | 2017-03-07 23:33 | 2017-03-08 01:11 | 98 | 11kV | 214516 | 2200 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn12650 West Gosford 11kV Panel 17 "Fagans Bay etc.." fdr tripped to lock out X2 Relays: E/F EFI Lockout EFI's: S18185 S12341 (failed restoration attempt EFIs from previous fault) UG Fault in section of 11kv from Zn12650 West Gosford Panel 17. to LB40497 to S18185 SwA See 1467411,2 exclude 1467010 | March | 2017 | 2017Q3 | 2017 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | UG | Not Veg | 2017-03-07 | N | 97.5073 | N | 7 | N | N | 1.1101 | 39.4971 | 156761.9656
[7 empty] | 9032 | 4439 | 1467013 | 2017-03-08 01:15 | 2017-03-08 08:15 | 420 | 11kV | 3360 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | Ex Zn14891 Wyong section of Pa20 "Warnervale West Railway" PT14451 Parkridge Chestwood 0.5 centre HDO operated, 16Amp 11kV 16Amp HDO operated due to Fuse Fatigue | March | 2017 | 2017Q3 | 2017 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2017-03-08 | N | 420 | N | 3 | N | N | 1.1101 | 39.4971 | 2455.3889
[7 empty] | 9439 | 9277 | 1467178 | 2017-03-08 13:55 | 2017-03-08 15:30 | 95 | 11kV | 34907 | 604 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn3154 St Ives Panel 12 "Killeaton Warrimoo etc" fdr tripped, reclosed & locked out on Signals: 11kv trip, No 1 Group Earth Zone Earth EFI's: S4112 S35697 Abnormal: PT1500 DMA LB62194 Open, LB60 Open S8596SwB Bobbin Landings No.2 Closed Cause: UGOH fault short circuit. On Pole MC11942 UGOH to S7338 See 1468211,3,4 exclude 1467178,80,1,7,211 | March | 2017 | 2017Q3 | 2017 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | Unknown | Unknown | 2017-03-08 | N | 57.793 | N | 3 | N | N | 1.1101 | 39.4971 | 25509.006
[7 empty] | 9059 | 4839 | 1467294 | 2017-03-08 22:53 | 2017-03-09 00:04 | 71 | 11kV | 116582 | 1642 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 24 Tripped and reclosed on A and C phase timed Signals: 11kV trip Field EFIs' Nil Cause: Animals - Bat adjacent to LB77071 A See OMS 1467294 1467294 1467297 1467298 | March | 2017 | 2017Q3 | 2017 | ZN129:PA24 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Not Veg | 2017-03-08 | N | 71 | N | 3 | N | N | 1.1101 | 39.4971 | 85194.687
[7 empty] | 9956 | 15359 | 1467553 | 2017-03-09 16:33 | 2017-03-09 22:45 | 372 | 11kV | 77748 | 209 | HV | Staff Other | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Cause: MG appears to have been connected up incorrectly. Phase may have have been connected to earth. See OMS 1467875 1467553. CC1: 22-"Refer to SOp" | March | 2017 | 2017Q3 | 2017 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | Unknown | Not Veg | 2017-03-09 | N | 372 | N | 1 | N | N | 1.1101 | 39.4971 | 56815.9452
[7 empty] | 9608 | 11373 | 1467869 | 2017-03-11 08:39 | 2017-03-11 09:55 | 76 | 11kV | 152 | 2 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171317 C Phase DOLF : 10 Amp Cooked Possum Excluded OMS 1467869 | March | 2017 | 2017Q3 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2017-03-11 | N | 76 | N | 4 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 9208 | 6586 | 1467874 | 2017-03-11 09:14 | 2017-03-11 11:25 | 131 | 11kV | 131 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 171320 Single phase LLC vibrated of OHM Excluded OMS 1467874. | March | 2017 | 2017Q3 | 2017 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Not Veg | 2017-03-11 | N | 131 | N | 4 | N | N | 1.1101 | 39.4971 | 95.7309
[7 empty] | 10103 | 17276 | 1467922 | 2017-03-11 14:41 | 2017-03-11 17:35 | 174 | 11kV | 1637 | 80 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ex S15013 Terrey Hills Recloser 1126 Mona Vale Rd tripped and reclosed on relays: O/C trip, IOC trip. Signals: At Zn15013 Terrey Hills, Zone Earth At PT15672 11kV HVDO operated Anbormal: CP26208 Open, CP20234 Closed Cause: DOp patrolled the feeder and didnt find anything unusual. See OMS 1468255 1468256 1467922 1467925 | March | 2017 | 2017Q3 | 2017 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2017-03-11 | N | 20.4625 | N | 4 | N | N | 1.1101 | 39.4971 | 1196.2713
[7 empty] | 10251 | 19039 | 1467923 | 2017-03-11 15:55 | 2017-03-11 20:30 | 275 | 11kV | 78250 | 1048 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | LID 171322 2 fault operations 3 phase Overcurrent kiosk 28473 burnt down section isolated for repairs Excluded oms 146923 | March | 2017 | 2017Q3 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | UG | Not Veg | 2017-03-11 | N | 74.666 | N | 4 | N | N | 1.1101 | 39.4971 | 57182.792
[7 empty] | 10310 | 19752 | 1467970 | 2017-03-12 00:43 | 2017-03-12 02:25 | 102 | 11kV | 18972 | 186 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Link | Unplanned | No Weather Impact | N | LID 171324 B Phase Links 8486 B phase link found open. Closed & supply checked OK Excluded OMS 1467970 | March | 2017 | 2017Q3 | 2017 | 239:82131 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Not Veg | 2017-03-12 | N | 102 | N | 6 | N | N | 1.1101 | 39.4971 | 13864.178
[7 empty] | 8963 | 3579 | 1468011 | 2017-03-12 12:43 | 2017-03-12 15:19 | 156 | 11kV | 116090 | 753 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36100 Rose Bay - Pnl.15 tripped on: Earth Fault with EFI UG cable fault from S8937 (Sw/B) to S2593 (Sw/A) tee S35907 (Sw/A) See 1468204 1468207 | March | 2017 | 2017Q3 | 2017 | ZN36100:PA15 | ZN36100:PA15 | ZN36100/000015 | WAVERLEY | UG | Not Veg | 2017-03-12 | N | 154.17 | N | 6 | N | N | 1.1101 | 39.4971 | 84835.1479
[7 empty] | 10349 | 20222 | 1468021 | 2017-03-12 13:41 | 2017-03-12 16:40 | 179 | 11kV | 147400 | 985 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Zn3154 St Ives - Pnl.19 tripped on: Instantaneous O/C and Earth Fault with EFI Lightning arrestor failed See 1472012 1472013 1472014 | March | 2017 | 2017Q3 | 2017 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | OH | Not Veg | 2017-03-12 | N | 149.6447 | N | 6 | N | N | 1.1101 | 39.4971 | 107715.5724
[7 empty] | 9861 | 14337 | 1468035 | 2017-03-12 16:04 | 2017-03-12 16:50 | 45.4 | 11kV | 29737 | 655 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12570 section of Panel 33 McmAsters Beach" IR50407 The Scenic Bounty tripped, reclosed, tripped, reclosed, tripped, reclosed, tripped, reclosed, tripped & locked out on Overcurrent DOp removed branch from mains See 1468035 exlcude 1468038,9 | March | 2017 | 2017Q3 | 2017 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2017-03-12 | N | 45.4 | N | 6 | N | N | 1.1101 | 39.4971 | 21730.9225
[7 empty] | 9967 | 15485 | 1468040 | 2017-03-12 16:12 | 2017-03-12 17:00 | 48 | 11kV | 47040 | 980 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7900 Campbell Street - Pnl.6 tripped on: Overcurrent and Earth Fault UG cable fault from Panel 6 at Campbell St Zn to S7263 to S8528 | March | 2017 | 2017Q3 | 2017 | ZN7900:PA6 | ZN7900:PA6 | ZN07900/000006 | SYDNEY | UG | Not Veg | 2017-03-12 | N | 48 | N | 6 | N | N | 1.1101 | 39.4971 | 34375.4446
[7 empty] | 8960 | 3535 | 1468047 | 2017-03-12 16:48 | 2017-03-12 18:55 | 127 | 11kV | 381 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171329 A Phase DOLF : 16 Amp Excluded OMS 1468047 | March | 2017 | 2017Q3 | 2017 | 512:48048 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2017-03-12 | N | 127 | N | 6 | N | N | 1.1101 | 39.4971 | 278.4236
[7 empty] | 8905 | 2788 | 1468090 | 2017-03-13 07:00 | 2017-03-13 08:15 | 75 | 11kV | 150 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171330 C Phase DOLF : 10 Amp Excluded OMS 1468090 | March | 2017 | 2017Q3 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2017-03-13 | N | 75 | N | 14 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 8772 | 1041 | 1468094 | 2017-03-13 07:20 | 2017-03-13 09:15 | 115 | 11kV | 805 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 171331 A Phase DOLF : 20 Amp Excluded OMS 1468094 | March | 2017 | 2017Q3 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2017-03-13 | N | 115 | N | 14 | N | N | 1.1101 | 39.4971 | 588.2703
[7 empty] | 9002 | 3978 | 1468087 | 2017-03-13 06:37 | 2017-03-13 10:30 | 233 | 11kV | 233 | 1 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171337 Single phase DOLF : 5 Amp Possum across HV at TX. Excluded OMS 1468087 | March | 2017 | 2017Q3 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2017-03-13 | N | 233 | N | 14 | N | N | 1.1101 | 39.4971 | 170.2695
[7 empty] | 9166 | 6191 | 1468099 | 2017-03-13 07:41 | 2017-03-13 15:00 | 439 | 11kV | 878 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171341 A Phase DOLF : 20 Amp Excluded OMS 1468099 | March | 2017 | 2017Q3 | 2017 | 512:48048 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2017-03-13 | N | 439 | N | 14 | N | N | 1.1101 | 39.4971 | 641.6165
[7 empty] | 9797 | 13597 | 1468258 | 2017-03-13 13:38 | 2017-03-13 16:30 | 172 | 11kV | 344 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171342 A Phase DOLF : 10 Amp Excluded OMS 1468258 | March | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-03-13 | N | 172 | N | 14 | N | N | 1.1101 | 39.4971 | 251.3851
[7 empty] | 10313 | 19769 | 1468316 | 2017-03-13 16:29 | 2017-03-13 18:03 | 94 | 11kV | 73104 | 1215 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Zn12690 Berkeley Vale Panel 19 fdr tripped & locked out on Relays: 19L, O/C, EF, EFI Signals: 11kv trip EFI's: S18671 S64488 S18560 S18559 Cause: Storm. All Went back after detailed patrol See 1469176,9 exclude 1468316 | March | 2017 | 2017Q3 | 2017 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2017-03-13 | N | 60.1679 | N | 14 | N | N | 1.1101 | 39.4971 | 53422.247
[7 empty] | 10079 | 16931 | 1468372 | 2017-03-13 18:39 | 2017-03-13 19:10 | 31 | 11kV | 558 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | No Weather Impact | N | LID 171344 C Phase DOLF : 31 Amp Excluded OMS 1468372 | March | 2017 | 2017Q3 | 2017 | 513:48057 | 513:83497 | ZN00513/083497 | SINGLETON | UG | Not Veg | 2017-03-13 | N | 31 | N | 14 | N | N | 1.1101 | 39.4971 | 407.7699
[7 empty] | 9990 | 15886 | 1468293 | 2017-03-13 15:24 | 2017-03-13 19:30 | 246 | 11kV | 7452 | 46 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford Panel 1 "Dog Trap Rd" RE44603 Footes rd tripped, relcosed, treipped, relcosed, tripped & locked out on O/C OH Down near PT14359 See 1469130,1 exclude 1468293,1468343 | March | 2017 | 2017Q3 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2017-03-13 | N | 162 | N | 14 | N | N | 1.1101 | 39.4971 | 5445.7018
[7 empty] | 9027 | 4331 | 1468320 | 2017-03-13 16:40 | 2017-03-13 20:00 | 200 | 11kV | 124274 | 938 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | At S2400 Berowra panel 11 tripped beyond CP61454 Toll gates Abnormal Switching: AB33 Closed, AB2122 Open Cause: Arrester at PT834 Defective Restored Via LV Parallel See OMS 1468612 1468613 1468614 1468616 1468332 1468320 | March | 2017 | 2017Q3 | 2017 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2017-03-13 | N | 132.4883 | N | 14 | N | N | 1.1101 | 39.4971 | 90815.7737
[7 empty] | 9303 | 7489 | 1468317 | 2017-03-13 16:29 | 2017-03-13 20:09 | 220 | 11kV | 129659 | 784 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Zn12690 Berkekeley Vale section of Pa24 "Berkeley Rd" fdr tripped & locked out on Relays: 24R, EF, EFI Signals: 11kv trip Cause: Storm. All Back See 1469164,7,8,9 exclude 1468317 | March | 2017 | 2017Q3 | 2017 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2017-03-13 | N | 165.3814 | N | 14 | N | N | 1.1101 | 39.4971 | 94750.9729
[7 empty] | 8731 | 173 | 1468346 | 2017-03-13 17:22 | 2017-03-13 20:30 | 188 | 11kV | 1316 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge section of Pa13 "Peats Ridge Aux" fdr PT11110 Reservior Grants footpath phase 10A HDO fuse operated Cause: Storm, Replaced See 1469241 exclude 1468346 | March | 2017 | 2017Q3 | 2017 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2017-03-13 | N | 188 | N | 14 | N | N | 1.1101 | 39.4971 | 961.694
[7 empty] | 9600 | 11274 | 1468339 | 2017-03-13 21:31 | 2017-03-13 22:00 | 28.8667 | 11kV | 433 | 15 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171345 Misinformation on fdr details Excluded oms 1468339 | March | 2017 | 2017Q3 | 2017 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2017-03-13 | N | 28.8667 | N | 14 | N | N | 1.1101 | 39.4971 | 316.4236
[7 empty] | 10267 | 19205 | 1468313 | 2017-03-13 16:22 | 2017-03-14 01:50 | 568 | 11kV | 178252 | 1327 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | Zn14143 Somersby Panel 12 "CP44633 Phillips Gindurra" fdr tripped & locked out on Relays: EF, EFI, Fault Check Signals: 11kv trip Cause: UG Fault See 1469138,9 exclude 1468313,76,81 | March | 2017 | 2017Q3 | 2017 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | UG | Not Veg | 2017-03-13 | N | 134.3271 | N | 14 | N | N | 1.1101 | 39.4971 | 130261.3041
[7 empty] | 9778 | 13434 | 1468410 | 2017-03-14 02:08 | 2017-03-14 03:34 | 86 | 11kV | 23994 | 279 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Recloser CP554 Arcadia Rosscommon tripped and Lockedout on Relays: Nil due to recloser in SCAN failure Branch from by DOp near PT2136 | March | 2017 | 2017Q3 | 2017 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2017-03-14 | N | 86 | N | 17 | N | N | 1.1101 | 39.4971 | 17534.1075
[7 empty] | 9658 | 11844 | 1468471 | 2017-03-14 08:21 | 2017-03-14 10:15 | 114 | 11kV | 4700 | 57 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Electrical Storm | N | Ex Zn12650 West Gosford Panel 1 "Dog Trap Rd" fdr RE44604 Dog Trap Rd tripped on Relays: OC Trip, IOC Trip Note: Reclosing was N/A at time due to DOp Switching PT11345 Dog Trap Kilkenny 2.3 - 2x10A 11kV HDO's PT13358 Dog Trap Kilkenny 2.6 - 3x10A 11kV HDO's Cause: Lightning. Also see Panel 11 few minutes later. Reclosing was non auto at time due to swithcing for job by DOp See 1469245,6,7 exclude 1468471 | March | 2017 | 2017Q3 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2017-03-14 | N | 82.4561 | N | 17 | N | N | 1.1101 | 39.4971 | 3434.6214
[7 empty] | 8728 | 156 | 1468508 | 2017-03-14 09:57 | 2017-03-14 11:20 | 83 | 11kV | 40286 | 658 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Recloser Cp3228 Berowra Pump Tripped Large tree against 11kV mains near 40 Warrina St See OMS 1468792 1468793 1468508 1468509 1468513 1468528 | March | 2017 | 2017Q3 | 2017 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Veg | 2017-03-14 | N | 61.2249 | N | 17 | N | N | 1.1101 | 39.4971 | 29439.8206
[7 empty] | 9966 | 15478 | 1468473 | 2017-03-14 08:24 | 2017-03-14 11:54 | 210 | 11kV | 48554 | 238 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | Zn12630 Peats RIdge Panel 11 "Somersby" fdr has tripped on: Signals: Relays: 'A' Prot- ABCN IOC 'B' Prot- ABCN IOC, EFI, Reclose Attempt (Note:REC was N/A for switching) EFI: Cause: Lightning See RE44604 Dog Trap Recloser trip few minutes before. See 1469252,3 exclude 1468473 | March | 2017 | 2017Q3 | 2017 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2017-03-14 | N | 204.0084 | N | 17 | N | N | 1.1101 | 39.4971 | 35481.8311
[7 empty] | 9695 | 12272 | 1468576 | 2017-03-14 12:21 | 2017-03-14 12:47 | 26 | 11kV | 17420 | 670 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn14144 Wamberal Panel 10 "Wamberal Aux No.2" fdr has tripped/Reclosed/Tripped on: Relays: 50TAB (Basler), Lockout, EFI EFI: S18844 S18802 S18826 Cause: Tree/Branch on OH Mains Tree Branch on HV near PT13671 Brush Old Gosford See 1468578 exclude 1468576,7,81 | March | 2017 | 2017Q3 | 2017 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2017-03-14 | N | 26 | N | 17 | N | N | 1.1101 | 39.4971 | 12730.0222
[7 empty] | 10334 | 20089 | 1468507 | 2017-03-14 11:46 | 2017-03-14 13:15 | 89 | 11kV | 17088 | 192 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 171356 11kV tapping burnt off at pole FT 23434 Wollombi Rd x Michael St. Excluded oms 1468584, 1468563, 1468507 | March | 2017 | 2017Q3 | 2017 | 504:48034 | 522:83129 | ZN00522/083129 | CESSNOCK | OH | Not Veg | 2017-03-14 | N | 89 | N | 17 | N | N | 1.1101 | 39.4971 | 12487.4064
[7 empty] | 9768 | 13279 | 1468505 | 2017-03-14 09:23 | 2017-03-14 13:35 | 252 | 11kV | 85149 | 1055 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Lightning | N | Zn12610 Long Jetty section of Pa17 "Hume Blvd" fdr PT12110 Hume Brooke Footpath phase HDO operated Cause: Fuse Faiiled. suspect surge arrestor or Failed PT Zn12610 Long Jetty Panel 17 "Hume Blvd" fdr has tripped on: Relays: Earth Fault Check Relay, EFI, A Phase, Earth Fault, SEF DOp patrolling See 1469263 2nd 1469264,5 exclude 1468505,46,94 | March | 2017 | 2017Q3 | 2017 | ZN12610:PA17 | ZN12610:PA17 | ZN12610/000017 | CENTRAL COAST | OH | Not Veg | 2017-03-14 | N | 80.71 | N | 17 | N | N | 1.1101 | 39.4971 | 62224.3777
[7 empty] | 10077 | 16892 | 1468558 | 2017-03-14 11:32 | 2017-03-14 13:39 | 127 | 11kV | 127 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn15013 Terrey Hills section of Pa8 CP24714 Challenger Drive No3 11kv A Phase 80Amp HV fuse blown Cause: not ascertained | March | 2017 | 2017Q3 | 2017 | ZN15013:PA8 | ZN15013:PA8 | ZN15013/000008 | NORTHERN BEACHES | OH | Veg | 2017-03-14 | N | 127 | N | 17 | N | N | 1.1101 | 39.4971 | 92.8079
[7 empty] | 9104 | 5390 | 1468405 | 2017-03-13 22:43 | 2017-03-14 14:20 | 937 | 11kV | 1874 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of Pa13 "Peats Ridge Aux" PT12183 Reservior Grants 0.8 all HDO operated Cause: Lightning/Surge Arrestor Customer has connected to MG to supply to load requires restored ASAP See 1469243 exclude 1468405 | March | 2017 | 2017Q3 | 2017 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2017-03-13 | N | 937 | N | 14 | N | N | 1.1101 | 39.4971 | 1369.4639
[7 empty] | 10055 | 16642 | 1468557 | 2017-03-14 11:27 | 2017-03-14 14:52 | 205 | 11kV | 55866 | 322 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 171357 4 fault operations Wires found twisted together. Excluded oms146557. | March | 2017 | 2017Q3 | 2017 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2017-03-14 | N | 173.4969 | N | 17 | N | N | 1.1101 | 39.4971 | 40825.225
[7 empty] | 9474 | 9712 | 1468661 | 2017-03-14 16:00 | 2017-03-14 17:30 | 90 | 11kV | 450 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 171359 C Phase DOLF : 10 Amp Excluded OMS 1468661 | March | 2017 | 2017Q3 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2017-03-14 | N | 90 | N | 17 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 8733 | 210 | 1468688 | 2017-03-14 17:43 | 2017-03-14 19:10 | 87 | 11kV | 261 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 171362 B Phase DOLF : 20 Amp Excluded OMS 1468688 | March | 2017 | 2017Q3 | 2017 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2017-03-14 | N | 87 | N | 17 | N | N | 1.1101 | 39.4971 | 190.7311
[7 empty] | 9019 | 4233 | 1468704 | 2017-03-14 18:20 | 2017-03-14 19:30 | 69.5833 | 11kV | 2574.5833 | 37 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 171360 A & C phase DOLF : 20 Amp | March | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-03-14 | N | 69.5833 | N | 17 | N | N | 1.1101 | 39.4971 | 1881.4296
[7 empty] | 9505 | 10012 | 1468693 | 2017-03-14 17:59 | 2017-03-14 20:30 | 151 | 11kV | 75422 | 981 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 171364 1 fault operation B Phase Overcurrent B phase blow tapping tail shorted adjacent phase at IU-90605 Outage 1 B Phase tapping 1759 till 1912 subs 49928,5197,20304,28726,12238,25868,24258 Outage 2 Isolated for repairs 1912 till 2030 sub 49928 Outage 3 Isolated for repairs 1930 till 2030 subs 49929,13740,13737 Excluded OMS 1468693 | March | 2017 | 2017Q3 | 2017 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2017-03-14 | N | 76.8828 | N | 17 | N | N | 1.1101 | 39.4971 | 55116.173
[7 empty] | 10026 | 16307 | 1468728 | 2017-03-14 17:00 | 2017-03-14 22:20 | 320 | 11kV | 18337 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171369 2 fault operations Overcurrent; Earth Fault failed to restore after planned outage Excluded oms 1468728 | March | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-03-14 | N | 291.0635 | N | 17 | N | N | 1.1101 | 39.4971 | 13400.1388
[7 empty] | 9782 | 13516 | 1468702 | 2017-03-14 18:16 | 2017-03-15 01:49 | 453 | 11kV | 68 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 171373 A Phase DOLF : 10 Amp Transformer replaced Excluded OMS 1468702 Note: this event ran from 14/03/17 18:16 to 15/03/17 01:49, but the customers were also impacted by event OMS 1471080 which overlapped this one during the time 14/03/17 18:25 to 15/03/17 00:50 | March | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-03-14 | N | 68 | N | 17 | N | N | 1.1101 | 39.4971 | 49.6924
[7 empty] | 9738 | 12871 | 1468707 | 2017-03-14 18:38 | 2017-03-15 04:15 | 577 | 11kV | 577 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 171374 A Phase DOLF : 10 Amp Excluded OMS 1468712 | March | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-03-14 | N | 577 | N | 17 | N | N | 1.1101 | 39.4971 | 421.6546
[7 empty] | 9193 | 6387 | 1468751 | 2017-03-15 03:01 | 2017-03-15 04:34 | 93 | 11kV | 101277 | 1089 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn1673 Turramurra Panel 6 tripped and locked out on Relays: A and B phase timed O/C, Reclose and Lockout Signals: 11kV trip Cause: Tree branch removed on Evans Near Comenerra Parkway | March | 2017 | 2017Q3 | 2017 | ZN1673:PA6 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Veg | 2017-03-15 | N | 93 | N | 4 | N | N | 1.1101 | 39.4971 | 74010.2444
[7 empty] | 9483 | 9816 | 1469707 | 2017-03-14 18:25 | 2017-03-15 14:30 | 1205 | 11kV | 17217 | 49 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 171371 Sensitive Earth Fault Transformer 15869 failed in service | March | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-03-14 | N | 351.3673 | N | 17 | N | N | 1.1101 | 39.4971 | 12581.6758
[7 empty] | 9095 | 5297 | 1468889 | 2017-03-15 12:04 | 2017-03-15 15:45 | 221 | 11kV | 663 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | replace dolf at sub 71069 10amp for 10amp on a phase replace all 3 arrestors, replace all 3 fury drop outs | March | 2017 | 2017Q3 | 2017 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2017-03-15 | N | 221 | N | 4 | N | N | 1.1101 | 39.4971 | 484.5008
[7 empty] | 9599 | 11246 | 1468882 | 2017-03-15 11:58 | 2017-03-15 20:16 | 497.9167 | 11kV | 15435.4167 | 31 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Rain Heavy | N | Ex Zn14891 Wyong section of Pa12 11kV Links 48027 opened by DOp McCabe, large tree on 11kv CCT OH mains, one phase on ground but no protection has tripped. Large tree branch on CCT mains beyond 11kV Links 48027. | March | 2017 | 2017Q3 | 2017 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2017-03-15 | N | 497.9167 | N | 4 | N | N | 1.1101 | 39.4971 | 11279.7472
[7 empty] | 8894 | 2704 | 1469054 | 2017-03-16 04:57 | 2017-03-16 10:15 | 318 | 11kV | 49947 | 374 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of pa8 "Kulnura" IR61340 George Bloodtree tripped and reclosed Cause: Tree/Branch on OH Mains near PT13500 See 1469521,2 Exclude 1469054,65 | March | 2017 | 2017Q3 | 2017 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2017-03-16 | N | 133.5481 | N | 9 | N | N | 1.1101 | 39.4971 | 36499.7944
[7 empty] | 10346 | 20210 | 1470608 | 2017-03-16 02:00 | 2017-03-16 11:36 | 576 | 11kV | 576 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 171393 1 fault operation 3 phase Customer advises this is an ongoing issue with no fault found. District Operator advises Live Line mat has been placed over the control box. PLEASE INSPECT. | March | 2017 | 2017Q3 | 2017 |  |  |  | LAKE MACQUARIE | OH | Veg | 2017-03-16 | N | 576 | N | 9 | N | N | 1.1101 | 39.4971 | 420.9238
[7 empty] | 9848 | 14153 | 1469064 | 2017-03-15 09:21 | 2017-03-16 12:20 | 1619 | 11kV | 1619 | 1 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | Ex Zn15013 Terrey Hills section of Pa8 "Mona Vale Myora" Relays: EFI, Fault Check EFi's: S16961 S16449 S6760 S16474 HV fuse operated at CP24714 Challenger Dr3 80Amp Abnormal: In proving section of feeder at CP24714 fuses operated Cause: UGOH fault. DOp reports centre phase on UGOH pole with efi located on it See 1469512 exclude 1469064,187 | March | 2017 | 2017Q3 | 2017 | ZN15013:PA8 | ZN15013:PA8 | ZN15013/000008 | NORTHERN BEACHES | Unknown | Unknown | 2017-03-15 | N | 1619 | N | 4 | N | N | 1.1101 | 39.4971 | 1183.1174
[7 empty] | 9401 | 8802 | 1469198 | 2017-03-16 12:30 | 2017-03-16 13:29 | 59 | 11kV | 11033 | 187 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | CP50015 Quarry Old Northern Tripped reclosed tripped and locked out Cause: Tree branch found on mains near PT1764 See OMS 1469198 1469207 | March | 2017 | 2017Q3 | 2017 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2017-03-16 | N | 59 | N | 9 | N | N | 1.1101 | 39.4971 | 8062.591
[7 empty] | 10239 | 18928 | 1469157 | 2017-03-16 10:35 | 2017-03-16 14:34 | 239 | 11kV | 10913 | 52 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 171398 A Phase DOLF : 10 Amp Tx failed causing SEF trip. K Garland advised customer not using sub 72807 this week. Please fix system abnormality ASAP. Ken advised depot staff will arrange a time in the future to replace the TX. PD Last customer on at 1434 hours. K Garland isolated sub 72807 and left isolated, customer advised they do not need the tx at present. Excluded OMS 1469157 | March | 2017 | 2017Q3 | 2017 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2017-03-16 | N | 209.8654 | N | 9 | N | N | 1.1101 | 39.4971 | 7974.8985
[7 empty] | 9146 | 5947 | 1469276 | 2017-03-16 15:19 | 2017-03-16 17:50 | 151 | 11kV | 3767 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 171399 DOLF : 20 Amp Dops patrolled entire line tried sections back no cause found. Excluded OMS 1469323 | March | 2017 | 2017Q3 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2017-03-16 | N | 139.5185 | N | 9 | N | N | 1.1101 | 39.4971 | 2752.8125
[7 empty] | 9587 | 11097 | 1469257 | 2017-03-16 14:48 | 2017-03-16 19:10 | 262 | 11kV | 262 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Light | N | LID 171401 3 phase DOLF : 10 Amp Transformer failed in service | March | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2017-03-16 | N | 262 | N | 9 | N | N | 1.1101 | 39.4971 | 191.4619
[7 empty] | 10156 | 17845 | 1469281 | 2017-03-16 15:22 | 2017-03-16 19:20 | 238 | 11kV | 620748 | 4363 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At S80 Chatswood panel 32 tripped and locked out on Relays: IOC, EFI, Fault Check Signals: 11kV Trip. Abnormal Switching: SW/A Open @ S3850, SW/B Closed @ S5705, SW/B Closed @ S4696, SW/A open @ S35322 Cause: UG fault between S4221 and S6443. See OMS 1469609 1469612 1469613 1469618 1469619 1469620 1469281 1469288 1469290 | March | 2017 | 2017Q3 | 2017 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | UG | Not Veg | 2017-03-16 | N | 142.2755 | N | 9 | N | N | 1.1101 | 39.4971 | 453624.3294
[7 empty] | 9864 | 14357 | 1469407 | 2017-03-16 23:52 | 2017-03-17 00:13 | 20.8833 | 11kV | 3675.4667 | 176 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 171404 3 fault operations Feeder patrolled - nothing found. Note IOC target 3000A. Please investigate | March | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-03-16 | N | 20.8833 | N | 9 | N | N | 1.1101 | 39.4971 | 2685.9226
[7 empty] | 8972 | 3669 | 1469454 | 2017-03-17 08:50 | 2017-03-17 10:55 | 124.7333 | 11kV | 3367.8 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 171410 C Phase DOLF : 20 Amp | March | 2017 | 2017Q3 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2017-03-17 | N | 124.7333 | N | 9 | N | N | 1.1101 | 39.4971 | 2461.0889
[7 empty] | 9992 | 15905 | 1469470 | 2017-03-17 09:26 | 2017-03-17 12:10 | 164 | 11kV | 164 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171415 Single phase DOLF : 10 Amp Excluded oms 1469470 | March | 2017 | 2017Q3 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2017-03-17 | N | 164 | N | 9 | N | N | 1.1101 | 39.4971 | 119.8464
[7 empty] | 8828 | 1769 | 1469538 | 2017-03-17 11:41 | 2017-03-17 12:10 | 29 | 11kV | 174 | 6 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | Rain Light | N | remove cockatoo from lightning arrestor No LID report | March | 2017 | 2017Q3 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2017-03-17 | N | 29 | N | 9 | N | N | 1.1101 | 39.4971 | 127.1541
[7 empty] | 8768 | 990 | 1469539 | 2017-03-17 11:38 | 2017-03-17 12:17 | 39 | 11kV | 8697 | 223 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Heavy | N | Ex Zn12610 Long Jetty section of Pa20 "Matcham St" 11kV RE45000 Tumbi Umbi tripped on overcurrent Cause: Tree branch vicinity PT18756 | March | 2017 | 2017Q3 | 2017 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Veg | 2017-03-17 | N | 39 | N | 9 | N | N | 1.1101 | 39.4971 | 6355.5111
[7 empty] | 9780 | 13501 | 1469056 | 2017-03-16 05:52 | 2017-03-17 14:07 | 1935 | 11kV | 136689 | 530 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of Pa1 "Gunderman" 11kV RE45189 Cooks Peats Ridge tripped and reclosed Relays: Overcurrent Cause: Tree/Branch brought down OH near PT13480 Popran Wise Ferry 1.3 DOp left access permit to lineworkers OH conductor snapped and found in the creek No work can be donw today due to weather conditions See 1472101,2,3,4 exclude 1469056,153 | March | 2017 | 2017Q3 | 2017 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2017-03-16 | N | 257.9038 | N | 9 | N | N | 1.1101 | 39.4971 | 99888.2896
[7 empty] | 9397 | 8753 | 1469610 | 2017-03-17 14:58 | 2017-03-17 15:45 | 47 | 11kV | 47 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 171419 A Phase DOLF : 10 Amp Excluded oms 1469610 | March | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-03-17 | N | 47 | N | 9 | N | N | 1.1101 | 39.4971 | 34.3462
[7 empty] | 10115 | 17433 | 1469622 | 2017-03-17 15:06 | 2017-03-17 17:00 | 114 | 11kV | 1026 | 9 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 171420 A Phase DOLF : 16 Amp Possum Excluded OMS 1469622 | March | 2017 | 2017Q3 | 2017 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2017-03-17 | N | 114 | N | 9 | N | N | 1.1101 | 39.4971 | 749.7705
[7 empty] | 9415 | 8967 | 1469784 | 2017-03-17 22:50 | 2017-03-18 01:43 | 173 | 11kV | 187101 | 1579 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S129 Hunters Hill Panel 24 tripped on C phase timed OC. Cause: Suspect trees in Romani Ave See OMS 1470630/632/633/634/635 1469784/785 | March | 2017 | 2017Q3 | 2017 | ZN129:PA24 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Veg | 2017-03-17 | N | 118.4934 | N | 9 | N | N | 1.1101 | 39.4971 | 136727.8923
[7 empty] | 9323 | 7808 | 1469854 | 2017-03-18 03:19 | 2017-03-18 05:47 | 148 | 11kV | 125948 | 851 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S9900 Menai Panel 13 "Old Illawarra" tripped on: earth leakage All field efis down to S9698 (Panel 19) Abnormal: Panel 19 out of service sw/b closed S9760 Remarks: UGOH fault short circuit. 11kv UGOH below S9698 Sw/D Panel 19 restored to service | March | 2017 | 2017Q3 | 2017 | ZN9900:PA13 | ZN9900:PA13 | ZN09900/000013 | SUTHERLAND | Unknown | Unknown | 2017-03-18 | N | 148 | N | 13 | N | N | 1.1101 | 39.4971 | 92039.0836
[7 empty] | 10017 | 16255 | 1469855 | 2017-03-18 03:19 | 2017-03-18 06:47 | 208 | 11kV | 136956 | 705 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At S9900 Menai Panel 19 "S9768 menai Exchange" tripped on: Earth leakage EFI. Recloser was one shot. all field EFIs to S9698 Sw/D Remarks: UG fault. 11kv UGOH in section of 11kv feeder from Sw/D @ S9698 Menai Sewerage pump to LB35919 | March | 2017 | 2017Q3 | 2017 | ZN9900:PA19 | ZN9900:PA19 | ZN09900/000019 | SUTHERLAND | UG | Not Veg | 2017-03-18 | N | 194.2638 | N | 13 | N | N | 1.1101 | 39.4971 | 100083.4053
[7 empty] | 10306 | 19642 | 1469856 | 2017-03-18 03:27 | 2017-03-18 07:49 | 262.5333 | 11kV | 11288.9333 | 43 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 171425 B & C Phase DOLF : 40 Amp OMS 1469856 Wires down from HR 61989 to HR 61991 Odd St Maitland. Fuses OK for this section (PT. 50885) but blew HV fuses for LV clash on other side of open taps. Note sub had 16K fuses in high. All 3 replaced with 40K fuses. | March | 2017 | 2017Q3 | 2017 | 528:83024 | 528:83024 | ZN00528/083024 | MAITLAND | OH | Not Veg | 2017-03-18 | N | 262.5333 | N | 13 | N | N | 1.1101 | 39.4971 | 8249.6195
[7 empty] | 8868 | 2365 | 1469876 | 2017-03-18 05:26 | 2017-03-18 08:05 | 159 | 11kV | 9699 | 61 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Zn12650 West Gosford Pa1 PT13115 Mangrove Narara Valley Cause not ascertained See 1472175 exclude 1469876,7 | March | 2017 | 2017Q3 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2017-03-18 | N | 159 | N | 13 | N | N | 1.1101 | 39.4971 | 7087.7431
[7 empty] | 9942 | 15239 | 1469873 | 2017-03-18 04:54 | 2017-03-18 08:15 | 201 | 11kV | 442236 | 2680 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At S690 Campsie Panel 35 "Schahil St" tripped on: earth leakage Field EFIS to S3261 See Interruption report Panel 21 Enfield in association Remarks: UG fault. Suspected UG or RMI fault in feeder from S3261 Iniana Clarence Sw/A to & via S1979 Jay Ave to S3830 Downes Burwood Sw/B | March | 2017 | 2017Q3 | 2017 | ZN690:PA35 | ZN690:PA35 | ZN00690/000035 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-03-18 | N | 165.0134 | N | 13 | N | N | 1.1101 | 39.4971 | 323173.025
[7 empty] | 9731 | 12752 | 1469805 | 2017-03-18 00:32 | 2017-03-18 10:30 | 598 | 11kV | 54956 | 107 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn44602 West Gosford section of Pa1 Ourimbah Ck Rd tripped, reclosed, twice and tripped on @0:32 RelaysL EF trip, Lockout OH down in Ourimbah Ck Rd nr Moores Point Rd Zn12650 West Gosford Pa1 "Bentley Rd etc" fdr tripped and reclosed and tripped on @1:19 Signals:11kv trip Relays: A7C phase OC, lockout EFI: Nil Tree hit fdr on double circuit pole. 49 Alan st Niagra Park See 1472132,43,4 2nd 1472133,7,8,9,41 Exclude 1469805,18,20,4,76,7,82,70166,86,9,246,54 | March | 2017 | 2017Q3 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2017-03-18 | N | 513.6075 | N | 13 | N | N | 1.1101 | 39.4971 | 40160.2239
[7 empty] | 9606 | 11334 | 1469675 | 2017-03-18 09:05 | 2017-03-18 13:50 | 285 | 11kV | 3420 | 12 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 171429 interrupt to replace broken crossarm at LF 41271 SI - r0028 | March | 2017 | 2017Q3 | 2017 | 512:48048 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2017-03-18 | N | 285 | N | 13 | N | N | 1.1101 | 39.4971 | 2499.2351
[7 empty] | 8875 | 2481 | 1469912 | 2017-03-18 07:16 | 2017-03-18 13:58 | 402 | 11kV | 2010 | 5 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | LID 171428 3 fault operations A & C phases Overcurrent FAULTY UGOH AT POLE AL-60300. | March | 2017 | 2017Q3 | 2017 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | Unknown | Unknown | 2017-03-18 | N | 402 | N | 13 | N | N | 1.1101 | 39.4971 | 1468.8487
[7 empty] | 9741 | 12923 | 1470008 | 2017-03-18 09:04 | 2017-03-18 14:30 | 326 | 11kV | 53464 | 164 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Rec45012 Bar Point (ex Zn14143 somersby Pa17) tripped, reclosed and tripped on Remarks: OH down at lot 8 Lippman Estate (Bar Point). Repaired by lineworkers | March | 2017 | 2017Q3 | 2017 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2017-03-18 | N | 326 | N | 13 | N | N | 1.1101 | 39.4971 | 39069.9143
[7 empty] | 9453 | 9412 | 1469775 | 2017-03-17 22:07 | 2017-03-18 15:20 | 1033 | 11kV | 55416 | 70 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mtn" 11kV IR49206 Mangrove Mtn West tripped & locked out Cause: Tree/Branch brought down OH. Approx 6 bays of HV & LV down Tree near PT11882 Waratah Borrisbrook 0.9 has brought down mains Damaga to amins is between AB43968 and AB44878 Fdr isolated from AB43968 to AB44878 tee PT65652 PT11882 PT18044 See 1472113,4,5 exclude 1469775,97 | March | 2017 | 2017Q3 | 2017 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2017-03-17 | N | 791.6571 | N | 9 | N | N | 1.1101 | 39.4971 | 40496.3783
[7 empty] | 9061 | 4862 | 1469818 | 2017-03-18 01:19 | 2017-03-18 19:55 | 1116 | 11kV | 295926 | 1610 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn44602 West Gosford section of Pa1 Ourimbah Ck Rd tripped, reclosed, twice and tripped on @0:32 RelaysL EF trip, Lockout OH down in Ourimbah Ck Rd nr Moores Point Rd Zn12650 West Gosford Pa1 "Bentley Rd etc" fdr tripped and reclosed and tripped on @1:19 Signals:11kv trip Relays: A7C phase OC, lockout EFI: Nil Tree hit fdr on double circuit pole. 49 Alan st Niagra Park See 1472132,43,4 2nd 1472133,7,8,9,41 Exclude 1469805,18,20,4,76,7,82,70166,86,9,246,54 | March | 2017 | 2017Q3 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2017-03-18 | N | 183.805 | N | 13 | N | N | 1.1101 | 39.4971 | 216253.9925
[7 empty] | 9049 | 4774 | 1470068 | 2017-03-18 11:18 | 2017-03-18 21:40 | 622 | 11kV | 71339 | 240 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of Pa11 RE44938 Somersby Rec has tripped Relays: EF Trip, OC Trip, Lockout Abnormal: LB62744 closed, Re47849 Resvoir Beckford 0.5 Open (West Gosford Pa1) Cause: Not ascertained. 11kV OH down on Dog Trap Rd near tee off to PT64546 See 1472189,91,2,4,5 exclude 1470068 | March | 2017 | 2017Q3 | 2017 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2017-03-18 | N | 297.2458 | N | 13 | N | N | 1.1101 | 39.4971 | 52132.4371
[7 empty] | 10327 | 19934 | 1466130 | 2017-03-18 11:25 | 2017-03-19 00:30 | 785 | 11kV | 33184 | 187 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zone 35370 Galston Panel 10 Recloser CP50015 Quarry Old Northern tripped and locked out on Relays: Overcurrent Signals: TX2 Group Earth Abnormal Switching: LB1478 to Ab1192 tee S5769 defective - No impact to customer numbers Cause: HV and LV are on ground - Tree See OMS 1472371 1472372 1466130/1470070/1470088/1470280/283/285/288 | March | 2017 | 2017Q3 | 2017 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2017-03-18 | N | 177.4545 | N | 13 | N | N | 1.1101 | 39.4971 | 24249.8884
[7 empty] | 8929 | 2984 | 1470340 | 2017-03-19 04:27 | 2017-03-19 05:49 | 82 | 11kV | 50615 | 666 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S187cCrows Nest 11kV panel 14 tripped on Relays: Earth fault, EFI, EF Check Signals: 11kV Trip Group TX2 Earth Cause: 11kV feeder fault from S187 Crows Nest to S1691 to S2995 See OMS 1470883 1470340 | March | 2017 | 2017Q3 | 2017 | ZN187:PA14 | ZN187:PA14 | ZN00187/000014 | NORTH SYDNEY | UG | Not Veg | 2017-03-19 | N | 75.9985 | N | 4 | N | N | 1.1101 | 39.4971 | 36987.9491
[7 empty] | 8882 | 2522 | 1469798 | 2017-03-17 23:59 | 2017-03-19 11:35 | 2136 | 11kV | 3662 | 27 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | LID 171423 A Phase DOLF : 20 Amp Blown UGOH pole HS-74039. ERC advised Also see report 171410 Excluded OMS 1469798, 1469799 & 1469838. | March | 2017 | 2017Q3 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | Unknown | Unknown | 2017-03-17 | N | 135.6296 | N | 9 | N | N | 1.1101 | 39.4971 | 2676.0816
[7 empty] | 9258 | 7049 | 1470298 | 2017-03-18 20:55 | 2017-03-19 12:30 | 935.15 | 11kV | 7481.2 | 8 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 171431 1 fault operation Sensitive Earth Fault Tree on mains at pole EI-20025 | March | 2017 | 2017Q3 | 2017 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2017-03-18 | N | 935.15 | N | 13 | N | N | 1.1101 | 39.4971 | 5467.0403
[7 empty] | 9563 | 10816 | 1470334 | 2017-03-19 02:17 | 2017-03-19 15:10 | 773 | 11kV | 111737 | 907 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S35800 Bankstown 11kv Panel No16 tripped on: Relays: A & C phase overcurrent Signals: see dnms log Field EFI's: down to S5412 Remarks: tree/branch brought down OH. Trees | March | 2017 | 2017Q3 | 2017 | ZN35800:PA16 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | OH | Veg | 2017-03-19 | N | 123.194 | N | 4 | N | N | 1.1101 | 39.4971 | 81654.1039
[7 empty] | 9011 | 4069 | 1470488 | 2017-03-19 13:15 | 2017-03-19 16:41 | 206 | 11kV | 20188 | 98 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | ex Zn2400 Berowra panel 18 Recloser 3227 Berowra Creel tripped and locked out on overcurrent Cause: Dop patrolled feeder and removed tree branch | March | 2017 | 2017Q3 | 2017 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2017-03-19 | N | 206 | N | 4 | N | N | 1.1101 | 39.4971 | 14752.795
[7 empty] | 10232 | 18880 | 1470541 | 2017-03-19 17:02 | 2017-03-19 17:50 | 48 | 11kV | 48 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 171437 C Phase DOLF : 10 Amp Excluded OMS 1470541 | March | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-03-19 | N | 48 | N | 4 | N | N | 1.1101 | 39.4971 | 35.077
[7 empty] | 9999 | 15952 | 1470643 | 2017-03-20 08:20 | 2017-03-20 12:45 | 265 | 11kV | 795 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171441 C Phase BOTTOM OF DOLF BROKEN AWAY FROM DOLF CARRIER. Excluded OMS 1470643 | March | 2017 | 2017Q3 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2017-03-20 | N | 265 | N | 4 | N | N | 1.1101 | 39.4971 | 580.9626
[7 empty] | 8920 | 2916 | 1470813 | 2017-03-20 13:19 | 2017-03-20 14:45 | 86 | 11kV | 172 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171447 A & B phase DOLF : 10 Amp Excluded OMS 1470813 | March | 2017 | 2017Q3 | 2017 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2017-03-20 | N | 86 | N | 4 | N | N | 1.1101 | 39.4971 | 125.6925
[7 empty] | 9136 | 5804 | 1470848 | 2017-03-20 14:00 | 2017-03-20 15:14 | 74 | 11kV | 18484 | 290 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn1850 Bass Hill Panel No.11 "Pasley Rd" feeder tripped on Signals: 11kv trip Relays: SEF EFI: nil Remarks: bond. Centre phase bond burnt off at AB.389 | March | 2017 | 2017Q3 | 2017 | ZN1850:PA11 | ZN1850:PA42 | ZN01850/000042 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-03-20 | N | 63.7379 | N | 4 | N | N | 1.1101 | 39.4971 | 13507.562
[7 empty] | 10190 | 18355 | 1470964 | 2017-03-20 18:06 | 2017-03-20 18:28 | 22 | 11kV | 22 | 1 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Customer reports: no 11 kv high voltage supply to test transformer. ausgrid equipment only. No further information supplied | March | 2017 | 2017Q3 | 2017 |  |  |  | KU-RING-GAI | Unknown | Not Veg | 2017-03-20 | N | 22 | N | 4 | N | N | 1.1101 | 39.4971 | 16.077
[7 empty] | 9320 | 7766 | 1471002 | 2017-03-21 00:53 | 2017-03-21 04:15 | 202 | 11kV | 168787 | 1069 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 47 labelled 2901 tripped on earth fault with EFI lockout and F/C, 11kV trip Cause not ascertainbed for outage - Section of 11kv feeder from S4764 to LB77234 tee PT1803 defective See OMS 1472207 1472207 1472210 1472209 1471002 | March | 2017 | 2017Q3 | 2017 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Not Veg | 2017-03-21 | N | 157.8924 | N | 15 | N | N | 1.1101 | 39.4971 | 123344.5612
[7 empty] | 9064 | 4932 | 1471064 | 2017-03-21 09:34 | 2017-03-21 11:30 | 116 | 11kV | 348 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171459 B Phase DOLF : 20 Amp Excluded OMS 1471064. | March | 2017 | 2017Q3 | 2017 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2017-03-21 | N | 116 | N | 15 | N | N | 1.1101 | 39.4971 | 254.3081
[7 empty] | 8925 | 2934 | 1471025 | 2017-03-21 08:02 | 2017-03-21 13:41 | 338.9667 | 11kV | 338.9667 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 171457 A Phase DOLF TOP OF DOLF CARRIER BROKEN.REPLACE ALL DOLF ASSEMBLEYS. Excluded OMS REPORT NO 1471035. | March | 2017 | 2017Q3 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2017-03-21 | N | 338.9667 | N | 15 | N | N | 1.1101 | 39.4971 | 247.7068
[7 empty] | 9642 | 11698 | 1471158 | 2017-03-21 13:08 | 2017-03-21 13:43 | 35 | 11kV | 20367 | 597 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 171465 1 fault operation 3 phase Overcurrent, Earth Fault 50T ABC SECTION ISOLATED TO REPAIR UGOH POLE JU-512444 | March | 2017 | 2017Q3 | 2017 | 256:80647 | 256:80647 | ZN00256/080647 | NEWCASTLE | Unknown | Unknown | 2017-03-21 | N | 34.1156 | N | 15 | N | N | 1.1101 | 39.4971 | 14883.6029
[7 empty] | 9835 | 14001 | 1471132 | 2017-03-21 11:55 | 2017-03-21 14:05 | 130 | 11kV | 28617 | 253 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171464 3 fault operations Earth Fault TREE ON MAINS AT POLE 9K-60254 Excluded OMS 1471132 | March | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-03-21 | N | 113.1107 | N | 15 | N | N | 1.1101 | 39.4971 | 20912.4595
[7 empty] | 9469 | 9657 | 1471373 | 2017-03-21 20:05 | 2017-03-21 21:00 | 55 | 11kV | 51395 | 1156 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Rain Heavy | N | @Sub3154 St Ives Zn Panel #18 labelled Sub 35629 Porters Lynbara tripped on OC IOC Earth Fault, EFI, 11kv trip Remarks: Sealing end failure at Q type PT1557. Section of 11kv feeder isolated from S6499 Bungalow Telegraph to S4635 Hope Station Sw/A tee PT1557 Graham Telegraph | March | 2017 | 2017Q3 | 2017 | ZN3154:PA18 | ZN3154:PA18 | ZN03154/000018 | KU-RING-GAI | OH | Not Veg | 2017-03-21 | N | 44.4593 | N | 15 | N | N | 1.1101 | 39.4971 | 37557.9501
[7 empty] | 10276 | 19279 | 1471363 | 2017-03-21 19:48 | 2017-03-21 21:21 | 93.4833 | 11kV | 841.35 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 171473 3 phase DOLF : 16 Amp | March | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2017-03-21 | N | 93.4833 | N | 15 | N | N | 1.1101 | 39.4971 | 614.8338
[7 empty] | 9071 | 5048 | 1471292 | 2017-03-21 19:30 | 2017-03-21 22:10 | 160 | 11kV | 4778 | 1204 | HV | 3rd Party Action | 3rd Party Impact | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | LID 171474 Section of feeder isolated for safety to allow gas workers to repair a ruptured main buried with UG cable from pole HR-22489. A star picket had been driven through it. | March | 2017 | 2017Q3 | 2017 | 528:83013 | 528:83013 | ZN00528/083013 | MAITLAND | UG | Not Veg | 2017-03-21 | N | 3.9684 | N | 15 | N | N | 1.1101 | 39.4971 | 3491.6215
[7 empty] | 10141 | 17723 | 1471381 | 2017-03-21 20:24 | 2017-03-21 23:45 | 201 | 11kV | 5672 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 171475 1 fault operation Overcurrent; Instantaneous Earth Fault No Fault found Excluded OMS 1471381 | March | 2017 | 2017Q3 | 2017 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Veg | 2017-03-21 | N | 166.8235 | N | 15 | N | N | 1.1101 | 39.4971 | 4144.9303
[7 empty] | 9287 | 7307 | 1471314 | 2017-03-21 18:38 | 2017-03-22 01:02 | 384 | 11kV | 230508 | 1234 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Lightning | N | At S2400 Beroqra Panel 21 tripped on Relays: A B and C phase O/C, Fault Check, Lockout Signals: TX2 Group Earth abnormal: CP2122 Open, CP33 Closed Cause: Lightning strike on UGOH above AB316 See OMS 1472181 1472185 1472186 1471314 1471336 | March | 2017 | 2017Q3 | 2017 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Not Veg | 2017-03-21 | N | 186.7974 | N | 15 | N | N | 1.1101 | 39.4971 | 168448.4476
[7 empty] | 9946 | 15277 | 1471215 | 2017-03-21 15:37 | 2017-03-22 01:36 | 599 | 11kV | 41902 | 81 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge section of Pa8 "Kulnura" RE44995 Kulnura tripped, reclosed and locked out on OC trip, EF trip, Lockout RE44994 Mangrove Creek: OC trip, EF trip, Lockout Abnormal: LB45195 closed, AB43601 open and defective Cause: Tree/Branch brought down OH. Tree Branch has brought down the 11kV OH adjacent to RE44494 Mangrove Creek See 1472203,4 exclude 1471214,5,7,8 | March | 2017 | 2017Q3 | 2017 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2017-03-21 | N | 517.3086 | N | 15 | N | N | 1.1101 | 39.4971 | 30620.7457
[7 empty] | 9548 | 10607 | 1471248 | 2017-03-21 16:38 | 2017-03-22 02:00 | 562 | 11kV | 2098 | 17 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Electrical Storm | N | The 11kV Recloser CP560 Peebles Nollands tripped, reclosed, tripped and locked out Cause: Lightning strike on PT1922 Restored via generator at 0200 See OMS 1472217 1472218 1471248 | March | 2017 | 2017Q3 | 2017 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2017-03-21 | N | 123.4118 | N | 15 | N | N | 1.1101 | 39.4971 | 1533.1565
[7 empty] | 9682 | 12191 | 1471436 | 2017-03-22 06:56 | 2017-03-22 07:55 | 59 | 11kV | 354 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171478 A Phase DOLF : 16 Amp Excluded OMS 1471436 | March | 2017 | 2017Q3 | 2017 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2017-03-22 | N | 59 | N | 23 | Y | Y | 1.1101 | 39.4971 | 258.6928
[7 empty] | 9302 | 7455 | 1471340 | 2017-03-21 19:11 | 2017-03-22 09:05 | 834 | 11kV | 22518 | 27 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Previous Storm | N | Ex Zn14143 Somersby section of Pa17 "Somersby Falls" PT13610 Bar Point HDO Found Operated (River side) In Bar Point, Water Access only. HDO found blown @PT13616 & PT13610 after lightning Cause: Lightning See 1472243 exclude 1471340 | March | 2017 | 2017Q3 | 2017 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2017-03-21 | N | 834 | N | 15 | N | N | 1.1101 | 39.4971 | 16455.4902
[7 empty] | 9215 | 6674 | 1471476 | 2017-03-22 08:55 | 2017-03-22 09:50 | 55 | 11kV | 660 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 171480 B Phase DOLF : 20 Amp Excluded OMS 1471476 | March | 2017 | 2017Q3 | 2017 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2017-03-22 | N | 55 | N | 23 | Y | Y | 1.1101 | 39.4971 | 482.3085
[7 empty] | 10071 | 16795 | 1472230 | 2017-03-22 11:12 | 2017-03-22 11:23 | 11 | 11kV | 451 | 41 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | CP1061 opeded to isolate PT834 - Safety - allow live line connector to be reinstated. Abnormal Switching: CP21202 Open, CP33 Closed AB1061 opened to isolate PT834 to allow LLC to be reinstated. Customer complaints of Low Volts. LLC cannot be used to energise new equipment. See OMS 1472230 1471471 | March | 2017 | 2017Q3 | 2017 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | Unknown | Unknown | 2017-03-22 | N | 11 | N | 23 | Y | Y | 1.1101 | 39.4971 | 329.5775
[7 empty] | 8725 | 54 | 1471520 | 2017-03-22 10:05 | 2017-03-22 13:45 | 220 | 11kV | 220 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 171491 Single phase DOLF : 10 Amp Excluded OMS 1471520 | March | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2017-03-22 | N | 220 | N | 23 | Y | Y | 1.1101 | 39.4971 | 160.7695
[7 empty] | 10155 | 17829 | 1471330 | 2017-03-21 18:57 | 2017-03-22 14:20 | 1163 | 11kV | 62184 | 381 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn12640 Umina section of pa13 RE47749 Palmtree Neera tripped, reclosed and locked out on EF trip, Lockout Cause: Tree/Branch on OH mains. A large tree branch was found on OH between LB48281 & PT12574 Patonga Bay 0.6 See 1472237,9 exclude 1471330,91,65,413 | March | 2017 | 2017Q3 | 2017 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Veg | 2017-03-21 | N | 163.2126 | N | 15 | N | N | 1.1101 | 39.4971 | 45442.2331
[7 empty] | 9261 | 7089 | 1471580 | 2017-03-22 12:13 | 2017-03-22 14:35 | 142 | 11kV | 426 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 171490 Replace HV Arrestors | March | 2017 | 2017Q3 | 2017 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2017-03-22 | N | 142 | N | 23 | Y | Y | 1.1101 | 39.4971 | 311.3082
[7 empty] | 9422 | 9081 | 1471654 | 2017-03-22 15:15 | 2017-03-22 15:46 | 31 | 11kV | 31924 | 1420 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | Ex Zn14891 Wyong section of Pa14 "WSC Hely" RE45181 McPherson Rd tripped and locked out on OC trip Abnormal: S14742:B Closed S14690:A Open Cause: Hot Humid day. Higher Load than expected See 1472247,8 exclude 1471669 | March | 2017 | 2017Q3 | 2017 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | Unknown | Not Veg | 2017-03-22 | N | 22.4817 | N | 23 | Y | Y | 1.1101 | 39.4971 | 23329.1176
[7 empty] | 8930 | 3001 | 1471619 | 2017-03-22 14:03 | 2017-03-22 15:55 | 112.2167 | 11kV | 2244.3333 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | Electrical Storm | N | LID 171494 A & B Phase DOLF : 16 Amp Replace 2 x 20 A dolfs on spur fuses 74995 | March | 2017 | 2017Q3 | 2017 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2017-03-22 | N | 112.2167 | N | 23 | Y | Y | 1.1101 | 39.4971 | 1640.0926
[7 empty] | 8795 | 1424 | 1471599 | 2017-03-22 15:00 | 2017-03-22 17:05 | 125 | 11kV | 125 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 171497 Replace blown HV arrestors | March | 2017 | 2017Q3 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-03-22 | N | 125 | N | 23 | Y | Y | 1.1101 | 39.4971 | 91.3463
[7 empty] | 9589 | 11120 | 1471731 | 2017-03-22 16:55 | 2017-03-22 17:50 | 55.0833 | 11kV | 1322 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 171498 A & B phase DOLF : 10 Amp | March | 2017 | 2017Q3 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-03-22 | N | 55.0833 | N | 23 | Y | Y | 1.1101 | 39.4971 | 966.0786
[7 empty] | 9275 | 7225 | 1471701 | 2017-03-22 16:27 | 2017-03-22 19:05 | 158 | 11kV | 103964 | 658 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Recloser Cp13228 Berowra Pump Tripped and locked out Cause not ascertained for outage See OMS 1471701 14701851 | March | 2017 | 2017Q3 | 2017 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Veg | 2017-03-22 | N | 158 | N | 23 | Y | Y | 1.1101 | 39.4971 | 75973.8248
[7 empty] | 9993 | 15909 | 1471686 | 2017-03-22 16:10 | 2017-03-22 19:21 | 191 | 11kV | 8997 | 51 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | Recloser Cp705 Knights Chadd tripped and locked out cause: Surge Arrestor blown at PT1851 Knights Bevans See OMS 1472232 1472233 1472235 1471686 Note customers also affected by T&R at 22/03/17 16:09 on CP420 see OMS 1472223 | March | 2017 | 2017Q3 | 2017 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2017-03-22 | N | 176.4118 | N | 23 | Y | Y | 1.1101 | 39.4971 | 6574.7422
[7 empty] | 9387 | 8675 | 1471694 | 2017-03-22 16:16 | 2017-03-22 19:29 | 193 | 11kV | 32981 | 206 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | At S129 Hunters Hill Panel 51 tripped and locked out on Relays: IOC, Earth Fault, EFI amd A B C trip Signals: 11kV Trip, Zone Earth UG fault from S48278 to CP50285 to S6440 to S4516 At S1472950 1472951 1471694 | March | 2017 | 2017Q3 | 2017 | ZN129:PA51 | ZN129:PA51 | ZN00129/000051 | HUNTERS HILL | UG | Not Veg | 2017-03-22 | N | 160.1019 | N | 23 | Y | Y | 1.1101 | 39.4971 | 24101.542
[7 empty] | 10273 | 19248 | 1471676 | 2017-03-22 15:48 | 2017-03-22 21:05 | 317 | 11kV | 317 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | At S4100 Beresford Coventry 80 amp OFHMA HV fuse operated section of Panel No.41 "Leicester Cooper etc" feeder ex Sub 2835 Burwood Remarks: Transformer failure | March | 2017 | 2017Q3 | 2017 | ZN2835:PA41 | ZN2835:PA41 | ZN02835/000041 | STRATHFIELD | OH | Not Veg | 2017-03-22 | N | 317 | N | 23 | Y | Y | 1.1101 | 39.4971 | 231.6543
[7 empty] | 9760 | 13186 | 1471742 | 2017-03-22 17:09 | 2017-03-22 21:09 | 240 | 11kV | 117840 | 491 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn12660 Woy Woy Pa6 "Davistown" CB tripped, reclosed and locked out on: Singals: 11kv trip Relays: IOC, TImed OC C Phase, Lockout, Timing Cause: Tree/Branch on OH Mains A large tree was found on the 11kv OH near UGOH below S18272 Hernderson Irwan 0.5 | March | 2017 | 2017Q3 | 2017 | ZN12660:PA6 | ZN12660:PA6 | ZN12660/000006 | CENTRAL COAST | OH | Veg | 2017-03-22 | N | 240 | N | 23 | Y | Y | 1.1101 | 39.4971 | 86113.9963
[7 empty] | 9029 | 4366 | 1471747 | 2017-03-22 17:12 | 2017-03-22 21:30 | 258 | 11kV | 434145 | 1764 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn12660 Woy Woy Pa10 "Woy Woy Leagues" tripped, reclosed and locked out on: Signals: 11kv trip Relays: 10L - 50 TAN, lockout Tree Branch found on 11kV OH. LV Dist's De-energised at S14713 PT13248 PT11631 due to branches on LV mains See 1472266,7 exclude 1471749,952,3,4,5 | March | 2017 | 2017Q3 | 2017 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | OH | Veg | 2017-03-22 | N | 246.1139 | N | 23 | Y | Y | 1.1101 | 39.4971 | 317260.3609
[7 empty] | 9325 | 7825 | 1471916 | 2017-03-22 21:02 | 2017-03-22 21:45 | 43 | 11kV | 129 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 171501 Single phase DOLF : 10 Amp Excluded OMS 1471916 | March | 2017 | 2017Q3 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-03-22 | N | 43 | N | 23 | Y | Y | 1.1101 | 39.4971 | 94.2694
[7 empty] | 9173 | 6230 | 1471708 | 2017-03-22 16:28 | 2017-03-22 22:04 | 336 | 11kV | 25045 | 94 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | N | REC20852 McCarrs Creek Rd tripped on: OC & Earth Fault Lightning arrestors failed due to lightning. See 1471999 1471998 1471997 1472000 | March | 2017 | 2017Q3 | 2017 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2017-03-22 | N | 266.4362 | N | 23 | Y | Y | 1.1101 | 39.4971 | 18302.1473
[7 empty] | 9686 | 12205 | 1471965 | 2017-03-22 21:33 | 2017-03-22 22:42 | 69 | 11kV | 118101 | 1764 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn12660 Woy WOy 11kV Panel 10 tripped, reclosed, locked out on: Signals: 11kv trip Relays: Panel 10L 50 TAB Cause: Another tree branch found on 11kv OH outside 238 Railway st. LV Dist's De-energised at S14713, PT13248 & PT11631 due to branches on LV mains See 1473056,7 | March | 2017 | 2017Q3 | 2017 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | OH | Veg | 2017-03-22 | N | 66.9507 | N | 23 | Y | Y | 1.1101 | 39.4971 | 86304.7274
[7 empty] | 9464 | 9632 | 1471833 | 2017-03-22 19:07 | 2017-03-23 | 293 | 11kV | 16115 | 55 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | N | Ex Zn12640 Umina section of Pa1 PT11520 Timbertop Veron the 11kV A&B phase surge arrestors were found to blown Cause: Lightning/Surge Arrestor See 1473072 exclude 1471871 | March | 2017 | 2017Q3 | 2017 | ZN12640:PA1 | ZN12640:PA1 | ZN12640/000001 | CENTRAL COAST | OH | Not Veg | 2017-03-22 | N | 293 | N | 23 | Y | Y | 1.1101 | 39.4971 | 11776.3667
[7 empty] | 9312 | 7598 | 1471854 | 2017-03-22 18:35 | 2017-03-23 01:04 | 389 | 11kV | 1167 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 171504 A Phase DOLF : 10 Amp Excluded OMS 1471854 | March | 2017 | 2017Q3 | 2017 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2017-03-22 | N | 389 | N | 23 | Y | Y | 1.1101 | 39.4971 | 852.8092
[7 empty] | 8884 | 2563 | 1471964 | 2017-03-23 05:44 | 2017-03-23 07:55 | 131 | 11kV | 917 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 171505 A Phase DOLF : 10 Amp Excluded OMS 1471964 | March | 2017 | 2017Q3 | 2017 | 513:48056 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2017-03-23 | N | 131 | N | 6 | N | N | 1.1101 | 39.4971 | 670.1166
[7 empty] | 10099 | 17248 | 1471305 | 2017-03-21 18:19 | 2017-03-23 08:45 | 2306 | 11kV | 220629 | 1131 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Lightning | N | At S965 Pennant Hills Panel 4 tripped on Relays: Earth fault, C phase Timed O/C, Timinga dn Lockout Relays with EFI Signals: 11kV trip, Zone Earth, No1 Group Earth Cause: UG fault between S71 - LB772 tee S5673 See OMS 1473064 1473068 1473069 1471421 1471345 1471305 | March | 2017 | 2017Q3 | 2017 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | UG | Not Veg | 2017-03-21 | N | 195.0743 | N | 15 | N | N | 1.1101 | 39.4971 | 161229.1657
[7 empty] | 9465 | 9642 | 1471813 | 2017-03-22 17:40 | 2017-03-23 10:45 | 1025 | 11kV | 29890 | 381 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn14891 WYong section of Pa12 RE50630 Yarramalong Chandlers 0.1 tripped, reclsoed and locked out: Relays: OC trip, (@Zn14891 Wyong) Tx 2 Group Earth, Panel 12 EFI Abnormal: RE45080 closed RE45078 open Cause: Large tree branch found on OH near near autolink 44772. isolated from AB40342 to LK40344. PT18374 PT77053 PT12421 interrupted still See 1473006,7,8 exclude 1471813,933,4,5 | March | 2017 | 2017Q3 | 2017 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2017-03-22 | N | 78.4514 | N | 23 | Y | Y | 1.1101 | 39.4971 | 21842.7304
[7 empty] | 10250 | 19027 | 1471777 | 2017-03-22 17:31 | 2017-03-23 12:00 | 1109 | 11kV | 1109 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At PT1974 NP & WS MT Colah 11kV HDOs left side blown See OMS 1473021 1471983 1471807 1471777 | March | 2017 | 2017Q3 | 2017 |  |  |  | HORNSBY | OH | Veg | 2017-03-22 | N | 1109 | N | 23 | Y | Y | 1.1101 | 39.4971 | 810.4245
[7 empty] | 9079 | 5184 | 1472070 | 2017-03-23 11:19 | 2017-03-23 14:15 | 176 | 11kV | 176 | 1 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 171520 Suspected HV burning up at UGOH. It was reported by L Watters as being LV burning up not HV. All Repaired. Excluded OMS OMS 1472070 | March | 2017 | 2017Q3 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | Unknown | Unknown | 2017-03-23 | N | 176 | N | 6 | N | N | 1.1101 | 39.4971 | 128.6156
[7 empty] | 9573 | 10913 | 1472091 | 2017-03-23 12:02 | 2017-03-23 14:40 | 158 | 11kV | 26228 | 166 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT1013 O'Meara Princes - B Phase HDO fuse failure. Fatigued See 1472567 1472568 1472569 | March | 2017 | 2017Q3 | 2017 | ZN10999:PA16 | ZN10999:PA16 | ZN10999/000016 | GEORGES RIVER | OH | Not Veg | 2017-03-23 | N | 158 | N | 6 | N | N | 1.1101 | 39.4971 | 19166.6488
[7 empty] | 10322 | 19852 | 1471757 | 2017-03-22 18:09 | 2017-03-23 15:00 | 1251 | 11kV | 87570 | 70 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn12650 West Gosford section of Pa17 11kV between AB42026 to LB42140 to PT12339 Wendy Preistly was interrutped for safety reasons Cause: OH Down. 11kV CCT was found on the ground after storm in tee off to PT's See 1473047 exclude 1471825,920,1 | March | 2017 | 2017Q3 | 2017 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | OH | Not Veg | 2017-03-22 | N | 1251 | N | 23 | Y | Y | 1.1101 | 39.4971 | 63993.5731
[7 empty] | 9127 | 5709 | 1472093 | 2017-03-23 12:12 | 2017-03-23 16:00 | 228 | 11kV | 456 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Wind Storm | N | Ex Zn12640 Umina section of Pa13 PT12325 Patonga Fitness Camp centre phase 16K HDO See 1473066 exclude 1472093 | March | 2017 | 2017Q3 | 2017 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2017-03-23 | N | 228 | N | 6 | N | N | 1.1101 | 39.4971 | 333.2314
[7 empty] | 9081 | 5210 | 1472163 | 2017-03-23 14:32 | 2017-03-23 19:00 | 268 | 11kV | 36208 | 254 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 171526 1 fault operation Pole AK-60003 X arm broken and feeder started to burn pole. Pole replaced. Excluded OMS 1472163 | March | 2017 | 2017Q3 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2017-03-23 | N | 142.5512 | N | 6 | N | N | 1.1101 | 39.4971 | 26459.7384
[7 empty] | 9060 | 4854 | 1472324 | 2017-03-24 04:09 | 2017-03-24 05:30 | 81 | 11kV | 69465 | 1015 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Zn9550 Gwawley Bay - Pnl.42 tripped on: Earth Fault cause not ascertained See 1472573 1472574 | March | 2017 | 2017Q3 | 2017 | ZN9550:PA42 | ZN9550:PA42 | ZN09550/000042 | SUTHERLAND | OH | Veg | 2017-03-24 | N | 68.4384 | N | 4 | N | N | 1.1101 | 39.4971 | 50762.9731
[7 empty] | 9975 | 15587 | 1472323 | 2017-03-24 03:40 | 2017-03-24 07:55 | 255 | 11kV | 255 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 171529 A Phase DOLF : 10 Amp Excluded OMS 1472333 | March | 2017 | 2017Q3 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2017-03-24 | N | 255 | N | 4 | N | N | 1.1101 | 39.4971 | 186.3465
[7 empty] | 9989 | 15862 | 1472308 | 2017-03-23 22:13 | 2017-03-24 13:14 | 901 | 11kV | 28424 | 90 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171527 4 fault operations 3 phase Earth Fault; Overcurrent wire down adj usl 27638 Excluded oms 1472308,1472440 & 1472329 | March | 2017 | 2017Q3 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2017-03-23 | N | 315.8222 | N | 6 | N | N | 1.1101 | 39.4971 | 20771.4208
[7 empty] | 9621 | 11487 | 1472544 | 2017-03-24 15:24 | 2017-03-24 17:24 | 120 | 11kV | 94299 | 871 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | Zn10990 Arncliffe - Pnl.12 tripped, reclosed and locked out on: C phase Instantaneous and timed Overcurrent. Appears car has Hit Pole Intersection of Princes Hwy & Forest Rd/Wickham St @ Arncliffe. POLE KO18522 See 1473001 1473002. | March | 2017 | 2017Q3 | 2017 | ZN10990:PA12 | ZN10998:PA9 | ZN10998/000009 | BAYSIDE | OH | Not Veg | 2017-03-24 | N | 108.2652 | N | 4 | N | N | 1.1101 | 39.4971 | 68910.9279
[7 empty] | 9995 | 15919 | 1472563 | 2017-03-24 16:24 | 2017-03-24 18:10 | 106 | 11kV | 106 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Replaced blown DOLF and Arrester. Bypassed meter PRW042447 new meter required. power restored 1810. Note: no LID raised | March | 2017 | 2017Q3 | 2017 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2017-03-24 | N | 106 | N | 4 | N | N | 1.1101 | 39.4971 | 77.4617
[7 empty] | 10109 | 17314 | 1472638 | 2017-03-25 05:48 | 2017-03-25 07:05 | 77 | 11kV | 4861 | 833 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn14144 Wamberal Panel 4 "Wamberal Aux" fdr tripped & reclosed on 50 TC & EFI. EFI @ S18823 @PT121112 Wycomber Hastings Roadside & Centre Phase 31.5 HDO's operated Cause: Animals/Brids. Possum found at Base of PT12112 See 1473081,2 exclude 1472638,41 | March | 2017 | 2017Q3 | 2017 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Not Veg | 2017-03-25 | N | 5.8355 | N | 2 | N | N | 1.1101 | 39.4971 | 3552.2754
[7 empty] | 9047 | 4691 | 1472725 | 2017-03-25 15:43 | 2017-03-25 18:00 | 137 | 11kV | 3432 | 47 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 171537 Tapping burnt off at 11kV Lk 27638. Interrupted at ABS at abs 40588 to repair tapping under AP. Excluded OMS 1472725 | March | 2017 | 2017Q3 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2017-03-25 | N | 73.0213 | N | 2 | N | N | 1.1101 | 39.4971 | 2508.0044
[7 empty] | 9891 | 14704 | 1472808 | 2017-03-26 09:57 | 2017-03-26 15:05 | 308 | 11kV | 616 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171541 llc dropper broken from dolf Excluded oms 1472809,1472808 | March | 2017 | 2017Q3 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2017-03-26 | N | 308 | N | 5 | N | N | 1.1101 | 39.4971 | 450.1546
[7 empty] | 10279 | 19300 | 1473060 | 2017-03-26 18:07 | 2017-03-26 18:14 | 7 | 11kV | 77 | 11 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 171543 Trying dolf 47130:11kV, tripped feeder at IR.63577. see previous event OMS 1473058 LA's replaced under AP. - see OMS 1473059 Excluded OMS 1472856 | March | 2017 | 2017Q3 | 2017 | 802:82225 | 802:82225 | ZN00802/082225 | MID-WESTERN REGIONAL | OH | Not Veg | 2017-03-26 | N | 7 | N | 5 | N | N | 1.1101 | 39.4971 | 56.2693
[7 empty] | 9181 | 6292 | 1472856 | 2017-03-26 15:15 | 2017-03-26 20:45 | 330 | 11kV | 330 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 171543 2 fault operations A phase DOLF : 10 Amp Telstra sub LA's blown. Trying dolf tripped feeder at IR.63577. LA's replaced under AP. Excluded OMS 1472856 | March | 2017 | 2017Q3 | 2017 | 802:82225 | 802:82225 | ZN00802/082225 | MID-WESTERN REGIONAL | OH | Not Veg | 2017-03-26 | N | 330 | N | 5 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 8744 | 479 | 1472887 | 2017-03-26 19:56 | 2017-03-26 22:00 | 124 | 11kV | 248 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171544 A Phase DOLF : 10 Amp Excluded OMS 1472887 | March | 2017 | 2017Q3 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2017-03-26 | N | 124 | N | 5 | N | N | 1.1101 | 39.4971 | 181.2311
[7 empty] | 9301 | 7445 | 1472837 | 2017-03-26 13:34 | 2017-03-26 23:55 | 621 | 11kV | 268724 | 1249 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S195 Pymble panel 25 tripped Relays: Earth Fault, EFI, Fault Check Signals: 11kv trip, TX4 Group Earth Zone Earth Abnormal Switching: SW/B Closed at S4651, S4641 SW/B Open Cause: UG cable fault See OMS 1473181 1473183 1473184 1472837 1472838 1472845 1472861 1472873 | March | 2017 | 2017Q3 | 2017 | ZN195:PA25 | ZN195:PA25 | ZN00195/000025 | KU-RING-GAI | UG | Not Veg | 2017-03-26 | N | 215.1513 | N | 5 | N | N | 1.1101 | 39.4971 | 196375.5732
[7 empty] | 9554 | 10727 | 1472898 | 2017-03-27 04:29 | 2017-03-27 06:44 | 135 | 11kV | 269417 | 2122 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S80 Chatswood panel 21 tripped on Relays: B and C phase OC Abnormal switching SW/B closed @ S653, SW/A Opened at S6433 Cause: Twisted 11kV OH between AB3237 and S6984 Campbell Second See OMS 1473413/414/415 1472902/899/898 | March | 2017 | 2017Q3 | 2017 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | OH | Not Veg | 2017-03-27 | N | 126.9637 | N | 4 | N | N | 1.1101 | 39.4971 | 196881.9971
[7 empty] | 10206 | 18610 | 1472910 | 2017-03-27 06:28 | 2017-03-27 08:10 | 102 | 11kV | 1122 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171545 A Phase DOLF : 16 Amp Excluded OMS 1472910 | March | 2017 | 2017Q3 | 2017 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2017-03-27 | N | 102 | N | 4 | N | N | 1.1101 | 39.4971 | 819.9245
[7 empty] | 9364 | 8276 | 1472969 | 2017-03-27 09:24 | 2017-03-27 13:20 | 236 | 11kV | 797 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn15012 Killarney section of Pa6L "Killarney West" Re26228 Valley Road tripped, reclosed and locked out Relays: Overucrrent, IOC and lockout Cause: Tree Branch on OH mains. DOp patrolled feeder and found tree on mains in Davison Park See 1473360,2 exclude 1472969 | March | 2017 | 2017Q3 | 2017 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2017-03-27 | N | 199.25 | N | 4 | N | N | 1.1101 | 39.4971 | 582.4241
[7 empty] | 9786 | 13532 | 1473221 | 2017-03-27 18:30 | 2017-03-27 20:05 | 95 | 11kV | 1045 | 11 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171554 Single phase Remove branch between poles CV-53681 & CV-53679. | March | 2017 | 2017Q3 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-03-27 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 763.6552
[7 empty] | 8746 | 614 | 1473334 | 2017-03-28 11:09 | 2017-03-28 12:00 | 51 | 11kV | 6426 | 126 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 171557 EMERGENCY REPAIRS REQUIRED AT POLE OR-50147. (white ants , x-arm collapsed) | March | 2017 | 2017Q3 | 2017 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Not Veg | 2017-03-28 | N | 51 | N | 4 | N | N | 1.1101 | 39.4971 | 4695.9313
[7 empty] | 9664 | 11921 | 1473402 | 2017-03-28 14:11 | 2017-03-28 15:57 | 106 | 11kV | 116178 | 1129 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2466 Flemington 11kv feeder Panel No: 20 "S8804 John Hastings" feeder tripped Relays: E/F, EFI Signals: 11kv trip, Zone Earth, No2 Grp Earth Remarks: UG fault. 11kv feeder fault section from S64186 Freitas Freitas (SwB) to S1867 Kerrs Rd (SwA), Note: Between RMIs LV// required for phasing on restoration | March | 2017 | 2017Q3 | 2017 | ZN2466:PA20 | ZN2466:PA20 | ZN02466/000020 | CUMBERLAND | UG | Not Veg | 2017-03-28 | N | 102.9035 | N | 4 | N | N | 1.1101 | 39.4971 | 84899.4557
[7 empty] | 10070 | 16794 | 1473495 | 2017-03-28 21:42 | 2017-03-28 23:20 | 98 | 11kV | 9310 | 95 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171562 A Phase Excluded OMS 1473495 CC1: 22-"Refer to SOp" | March | 2017 | 2017Q3 | 2017 | 243:80078 | 243:80078 | ZN00243/080078 | LAKE MACQUARIE | OH | Not Veg | 2017-03-28 | N | 98 | N | 4 | N | N | 1.1101 | 39.4971 | 6803.4734
[7 empty] | 10014 | 16221 | 1473502 | 2017-03-28 22:12 | 2017-03-29 07:40 | 568 | 11kV | 4544 | 8 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 171565 Live Line Clamp burnt off, replaced under AP Excluded OMS 1473502 | March | 2017 | 2017Q3 | 2017 | 238:34148 | 238:34148 | ZN00238/034148 | MAITLAND | OH | Not Veg | 2017-03-28 | N | 568 | N | 4 | N | N | 1.1101 | 39.4971 | 3320.6212
[7 empty] | 9750 | 13071 | 1473743 | 2017-03-29 19:24 | 2017-03-29 21:30 | 126 | 11kV | 17136 | 136 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @PT1224 IBERIA ST, 11kv 31.5A centre phase HDO operated Section of 11kv Panel 6 "Bankstown Aux No.1" feeder @ ZN35800 Bankstown Remarks: Cause not ascertained. Note: Found in LV//, PT1224 with S1336 Arab Davies No.2. LV ABC link box 16702 could not be opened. L/W to inspect during daylight hours | March | 2017 | 2017Q3 | 2017 | ZN35800:PA6 | ZN35800:PA6 | ZN35800/000006 | CANTERBURY-BANKSTOWN | OH | Veg | 2017-03-29 | N | 126 | N | 5 | N | N | 1.1101 | 39.4971 | 12522.4834
[7 empty] | 9330 | 7838 | 1473759 | 2017-03-29 20:11 | 2017-03-29 22:56 | 165 | 11kV | 175801 | 1415 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn14891 Wyong Panel 5 "Wyong" tripped Relays: SEL Signals: CB5 open, SEL EFI's: Nil Cause not ascertained. Feeder patrolled as per protection operation. Main to Patrol in daylight hours See 1473866,8,9,70,1 exclude 1473759,77 | March | 2017 | 2017Q3 | 2017 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2017-03-29 | N | 124.241 | N | 5 | N | N | 1.1101 | 39.4971 | 128470.1855
[7 empty] | 10299 | 19531 | 1473708 | 2017-03-29 18:00 | 2017-03-29 23:00 | 300 | 11kV | 22200 | 74 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 171578 Replace damaged LV ABC between HW-80223 & HW-80503. Interruption to LH lvf Excluded OMS 1473585 | March | 2017 | 2017Q3 | 2017 | 243:80078 | 243:80078 | ZN00243/080078 | LAKE MACQUARIE | OH | Not Veg | 2017-03-29 | N | 300 | N | 5 | N | N | 1.1101 | 39.4971 | 16223.1052
[7 empty] | 10040 | 16489 | 1473768 | 2017-03-29 22:27 | 2017-03-29 23:58 | 91 | 11kV | 81086 | 1078 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S3425 Castle Cove Panel 22 tripped Relays: Earth Fault, Fault Check, No.4 Tx E/F Check relay, efi Signals; 11kV Trip Cause: UG Fault between S48401 and S63822 See OMS 1473825 1473827 1473831 1473768 Due to defective sludge type efi @ S48401 Panel 18 tripped at Castloe Cove Tripped on restoration | March | 2017 | 2017Q3 | 2017 | ZN3425:PA22 | ZN3425:PA22 | ZN03425/000022 | WILLOUGHBY | UG | Not Veg | 2017-03-29 | N | 75.2189 | N | 5 | N | N | 1.1101 | 39.4971 | 59255.2572
[7 empty] | 10047 | 16541 | 1474827 | 2017-03-29 22:58 | 2017-03-30 11:50 | 772 | 11kV | 23556 | 79 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 "Wyong" RE45017 Whiteman Tripped Relays: EF trip, Lockout Signals: trip OH down approx 2 days back from PT13338 Dooralong Yambo 0.8 Note HV into LV. Fdr isolated from LK43160 to LK43081 tee to PT13338 PT14819 PT13339 PT14994 Alive in conditions beyond LK43081 See 1474827,8,9,30,1 exclude 1473782 | March | 2017 | 2017Q3 | 2017 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2017-03-29 | N | 298.1772 | N | 5 | N | N | 1.1101 | 39.4971 | 17214.03
[7 empty] | 9009 | 4044 | 1473988 | 2017-03-30 14:15 | 2017-03-30 15:05 | 50 | 11kV | 1850 | 37 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 171593 A Phase Main off pin on pole 8M-40035 Excluded OMS 1473988 | March | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-03-30 | N | 50 | N | 7 | N | N | 1.1101 | 39.4971 | 1351.9254
[7 empty] | 10167 | 17985 | 1474016 | 2017-03-30 15:42 | 2017-03-30 17:10 | 88 | 11kV | 176 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 171595 C Phase DOLF : 16 Amp Bird across LA excluded OMS 1474016 | March | 2017 | 2017Q3 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-03-30 | N | 88 | N | 7 | N | N | 1.1101 | 39.4971 | 128.6156
[7 empty] | 10142 | 17728 | 1473945 | 2017-03-30 12:53 | 2017-03-30 18:10 | 316.5333 | 11kV | 140815.4 | 2526 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S187 Crows nest Panel 20 tripped Anbormal switching: SWD @ S6836 Clsoed and SW/A, SW/A at S3195 Cause: 11kV feeder fault from S1894 to S5589 to S6584 See OMS 1474255 1474257 1474258 1473955 1473945 | March | 2017 | 2017Q3 | 2017 | ZN187:PA20 | ZN187:PA20 | ZN00187/000020 | NORTH SYDNEY | UG | Not Veg | 2017-03-30 | N | 55.7464 | N | 7 | N | N | 1.1101 | 39.4971 | 102903.741
[7 empty] | 10175 | 18075 | 1473964 | 2017-03-30 13:26 | 2017-03-30 20:45 | 439 | 11kV | 159845 | 909 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn965 Pennant hills Panel 26 tripped on A and C phase IOC and Timed O/C Timings and Lockout Signals: 11kV trip Cause: HV feeder into LV between S4494 and CP77939 See OMS 1474334 1474335 1473973 1473964 | March | 2017 | 2017Q3 | 2017 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Not Veg | 2017-03-30 | N | 175.8471 | N | 7 | N | N | 1.1101 | 39.4971 | 116810.0114
[7 empty] | 9073 | 5058 | 1474078 | 2017-03-30 18:11 | 2017-03-30 21:20 | 189 | 11kV | 9601 | 182 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | LID 171596 2 fault operations B & C Phases Overcurrent Faulty UGOH pole JS-70282 | March | 2017 | 2017Q3 | 2017 | 265:81648 | 265:81648 | ZN00265/081648 | PORT STEPHENS | Unknown | Unknown | 2017-03-30 | N | 52.7527 | N | 7 | N | N | 1.1101 | 39.4971 | 7016.1276
[7 empty] | 9503 | 9996 | 1474132 | 2017-03-30 21:09 | 2017-03-30 22:55 | 106 | 11kV | 106 | 1 | HV | Customer Installation Fault | Customer Installation | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 171600 A Phase DOLF : 3 Amp faulty LV isolated at central metering. Excluded oms 1474132 1474134 | March | 2017 | 2017Q3 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | Unknown | Unknown | 2017-03-30 | N | 106 | N | 7 | N | N | 1.1101 | 39.4971 | 77.4617
[7 empty] | 9062 | 4865 | 1474106 | 2017-03-30 20:04 | 2017-03-31 01:45 | 341 | 11kV | 21887 | 166 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 171598 tree on OHM & broken xarm adjacent 11kV links 74313 repaired. tapping at 74313 faulty & cut away. Excluded OMS 1474106 | March | 2017 | 2017Q3 | 2017 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2017-03-30 | N | 131.8494 | N | 7 | N | N | 1.1101 | 39.4971 | 15994.374
[7 empty] | 9953 | 15340 | 1474154 | 2017-03-31 02:23 | 2017-03-31 04:23 | 120 | 11kV | 121964 | 1081 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Rain Heavy | N | Zn9245 Engadine - Pnl.1 tripped on: B Phase Overcurrent, lockout timing. Field EFIs: S48147, S9287 S7642, UGOH princes Hwy near Boronia, S9358, S9065 Cause not ascertained See 1474220 1474221 1474222 | March | 2017 | 2017Q3 | 2017 | ZN9245:PA1 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | UG | Not Veg | 2017-03-31 | N | 112.8252 | N | 4 | N | N | 1.1101 | 39.4971 | 89127.6939
[7 empty] | 9357 | 8147 | 1474310 | 2017-03-31 12:56 | 2017-03-31 13:42 | 46 | 11kV | 92 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171612 B Phase DOLF : 16 Amp replaced blown "B" phase 16a fuse - j hug | March | 2017 | 2017Q3 | 2017 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2017-03-31 | N | 46 | N | 4 | N | N | 1.1101 | 39.4971 | 67.2309
[7 empty] | 9613 | 11404 | 1474317 | 2017-03-31 13:26 | 2017-03-31 14:21 | 55 | 11kV | 78595 | 1429 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 171611 1 fault operation Sensitive Earth Fault Removed tree branch pole SW-40112. Excluded OMS 1474319. | March | 2017 | 2017Q3 | 2017 | 239:82129 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Veg | 2017-03-31 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 57434.9078
[7 empty] | 10202 | 18593 | 1474911 | 2017-03-31 13:30 | 2017-03-31 15:15 | 105 | 11kV | 1680 | 16 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa2 Section of fdr from LK41935 to AB41934 tee PT12365 PT47611 interrupted for safety Tree on 11kV mains | March | 2017 | 2017Q3 | 2017 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2017-03-31 | N | 105 | N | 4 | N | N | 1.1101 | 39.4971 | 1227.6944
[7 empty] | 9541 | 10472 | 1474439 | 2017-04-01 01:02 | 2017-04-01 03:06 | 124 | 11kV | 94213 | 1568 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 171614 3 fault operations B phase Dead possum found at ELB 43996. No L/A covers on ELB 43996. 2nd time a possums have gone across L/As this year. Excluded oms1474439/41 | April | 2017 | 2017Q4 | 2017 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2017-04-01 | N | 60.0848 | N | 1 | N | N | 1.1101 | 39.4971 | 68848.0816
[7 empty] | 9407 | 8835 | 1474660 | 2017-04-02 19:30 | 2017-04-02 20:17 | 47 | 11kV | 22944 | 620 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | @ S35168 McEvoy Bowden - Sw/B opened by DOp interrupting supply to S7635 Bowden McEvoy @ Zn8100 Green Square - Pnl.20 tripped on: 3 Phase O/C, Earth Fault, EFI (All field EFIs indicators down) Abnormal: S8193 Sw/B Closed with Sw/A open. Staff error: DOP opened Sw/B @ S35168 instead of S35618 for D/R399491B/1. When earth was applied to S8193 (Sw/A), panel 20 tripped. Subs are 150m apart with similar sub numbers. See 1474665 1474930 | April | 2017 | 2017Q4 | 2017 | ZN8100:PA20 | ZN8100:PA20 | ZN08100/000020 | SYDNEY | Unknown | Not Veg | 2017-04-02 | N | 37.0065 | N | 2 | N | N | 1.1101 | 39.4971 | 16766.7985
[7 empty] | 9578 | 10960 | 1474672 | 2017-04-02 21:46 | 2017-04-02 23:20 | 94 | 11kV | 62698 | 667 | HV | Animal Flying Fox | Animal | O/H Link | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa22 RE46529 Davistown Mundoora tripped & locked out on overcurrent Batt Committed Hari Kari Near USL 42859 | April | 2017 | 2017Q4 | 2017 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2017-04-02 | N | 94 | N | 2 | N | N | 1.1101 | 39.4971 | 45817.8491
[7 empty] | 10002 | 15989 | 1474856 | 2017-04-03 12:08 | 2017-04-03 14:44 | 156 | 11kV | 1404 | 9 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Replaced blown HV fuse on sub 51659 Note: no LID report raised | April | 2017 | 2017Q4 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2017-04-03 | N | 156 | N | 4 | N | N | 1.1101 | 39.4971 | 1026.0018
[7 empty] | 8840 | 1887 | 1474838 | 2017-04-03 11:27 | 2017-04-03 14:55 | 208 | 11kV | 208 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 171635 Single phase LL Clamp failed Excluded OMS 1474838 | April | 2017 | 2017Q4 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2017-04-03 | N | 208 | N | 4 | N | N | 1.1101 | 39.4971 | 152.0003
[7 empty] | 9808 | 13713 | 1474988 | 2017-04-03 17:30 | 2017-04-03 18:40 | 70 | 11kV | 7331.1167 | 105 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa16 PT11042 Stanley Wahroonga 0.4 11kv fotpath side 40Amp Dropout fuse operated Fuse Fatigue See 1474988 GIS 1474991,8 | April | 2017 | 2017Q4 | 2017 | ZN14891:PA16 | ZN14891:PA1 | ZN14891/000001 | CENTRAL COAST | OH | Not Veg | 2017-04-03 | N | 69.8202 | N | 4 | N | N | 1.1101 | 39.4971 | 5357.3638
[7 empty] | 9933 | 15151 | 1475158 | 2017-04-04 12:30 | 2017-04-04 15:00 | 150 | 11kV | 7350 | 49 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Rain Light | N | LID 171644 SI 19558 11kV links 41505 fell apart on closing. Extended isolated area to repair links 41505. | April | 2017 | 2017Q4 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2017-04-04 | N | 150 | N | 4 | N | N | 1.1101 | 39.4971 | 5371.1632
[7 empty] | 10359 | 20329 | 1475229 | 2017-04-04 17:10 | 2017-04-04 18:50 | 100 | 11kV | 400 | 4 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171651 No OMS number appears job called into depot directly around 510pm. Cables were loose allowing a short circuit near the 11kV arrestors. Staff on site advised there was an outage in the area in the next month and recommend more permanent repairs then. | April | 2017 | 2017Q4 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-04-04 | N | 100 | N | 4 | N | N | 1.1101 | 39.4971 | 292.3082
[7 empty] | 10203 | 18595 | 1475149 | 2017-04-04 17:45 | 2017-04-04 19:35 | 110 | 11kV | 3410 | 31 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN14144 Wamberal section of Pa10 "S18827 Wamberal Aux No2" LK43501 to radial interrupted by DOp to allow lineworker to remove tree off 11kV Mains See seperate interruption report for LV PT18556 See 1475242 2nd 1475639 | April | 2017 | 2017Q4 | 2017 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2017-04-04 | N | 110 | N | 4 | N | N | 1.1101 | 39.4971 | 2491.9274
[7 empty] | 9852 | 14202 | 1475267 | 2017-04-04 20:20 | 2017-04-04 22:03 | 103 | 11kV | 47998 | 466 | HV | Animal Bird | Animal | UGOH | Unplanned | Rain Heavy | N | At S3154 St Ives Panel 23 tripped on Relays: B phase IOC and Timed Earth Fault Signals: 11kV trip Cause: 11kV UGOH O/S 11 Catherine St See OMS 1475267 1475277 1475279 01475282 1475285 | April | 2017 | 2017Q4 | 2017 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Not Veg | 2017-04-04 | N | 103 | N | 4 | N | N | 1.1101 | 39.4971 | 35075.5227
[7 empty] | 9350 | 8080 | 1475016 | 2017-04-03 21:24 | 2017-04-05 09:30 | 2166 | 11kV | 110498 | 1023 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12580 Erina section of Pa14 "East Gosford" Recloser 62391 Wells Brougham tripped on timed OC Cause: 66kV Feeder taken down by tree. OH Earth Wire Down. Also from initiating officer 11kv wires down to PT12924 PT12924 was not connected to grid untill organised emergency works on 18/4/17. DAROS 403644 See 1480433,4 exclude 1475016,20,5,422,7793 | April | 2017 | 2017Q4 | 2017 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Veg | 2017-04-03 | N | 108.0137 | N | 4 | N | N | 1.1101 | 39.4971 | 80748.6793
[7 empty] | 10169 | 18024 | 1475406 | 2017-04-05 11:48 | 2017-04-05 13:15 | 87 | 11kV | 609 | 7 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171662 DOLF : 10 Amp Excluded OMS 1475406 Bird contacted mains | April | 2017 | 2017Q4 | 2017 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Not Veg | 2017-04-05 | N | 87 | N | 4 | N | N | 1.1101 | 39.4971 | 445.0392
[7 empty] | 8857 | 2202 | 1475542 | 2017-04-05 21:14 | 2017-04-05 22:10 | 56 | 11kV | 3024 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171664 B Phase DOLF : 31 Amp Excluded OMS 1475542 | April | 2017 | 2017Q4 | 2017 | 223:14397 | 223:14397 | ZN00223/014397 | LAKE MACQUARIE | OH | Veg | 2017-04-05 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 2209.85
[7 empty] | 9721 | 12568 | 1475455 | 2017-04-05 15:46 | 2017-04-05 23:00 | 434 | 11kV | 527 | 94 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | CP20852 McCarrs Creek Rd tripped and reclosed on Relays: IOC and OC Signals:11kV Trip Cause: PT16809 Illawong Bay No.2 has failed, Non Paralleling sub - Transformer failure See OMS 1475804 1475806 1475455 | April | 2017 | 2017Q4 | 2017 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | UG | Not Veg | 2017-04-05 | N | 5.6064 | N | 4 | N | N | 1.1101 | 39.4971 | 385.1161
[7 empty] | 9498 | 9906 | 1475774 | 2017-04-06 11:34 | 2017-04-06 11:38 | 4 | 11kV | 12 | 3 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171671 short interruption due to emergency switching limitations of 11kV links. | April | 2017 | 2017Q4 | 2017 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2017-04-06 | N | 4 | N | 3 | N | N | 1.1101 | 39.4971 | 8.7692
[7 empty] | 10231 | 18866 | 1475436 | 2017-04-05 12:48 | 2017-04-06 13:30 | 1482 | 11kV | 7206 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 171670 Single phase Tree near PT.54055 on LV only but HV needs retensioning. Outage extended to 11kV link 41580. Excluded OMS 1475617 & 1475436 | April | 2017 | 2017Q4 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2017-04-05 | N | 480.4 | N | 4 | N | N | 1.1101 | 39.4971 | 5265.9323
[7 empty] | 9726 | 12659 | 1475673 | 2017-04-06 13:43 | 2017-04-06 19:40 | 357 | 11kV | 139587 | 1320 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15006 Dee Why West Panel 13 tripped on B and C phase OC Signals: 11kV Trip Field EFI's - Nil Cause: Bird brought down 11kV mains O/S 15 Suffollk Ave Collaroy. Also Caused bond to fail adjacent to LK 2494 into a bush which caught fire See OMS 1475875 1475876 1475877 1475878 1475673 | April | 2017 | 2017Q4 | 2017 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | OH | Not Veg | 2017-04-06 | N | 105.7477 | N | 3 | N | N | 1.1101 | 39.4971 | 102006.0625
[7 empty] | 9854 | 14212 | 1475760 | 2017-04-06 23:08 | 2017-04-06 23:35 | 27 | 11kV | 3375 | 125 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 171683 A Phase DOLF : 31 Amp oms 1475760 fuse holder burnt up, replaced by dop. dq | April | 2017 | 2017Q4 | 2017 | 258:80775 | 258:80775 | ZN00258/080775 | NEWCASTLE | OH | Not Veg | 2017-04-06 | N | 27 | N | 3 | N | N | 1.1101 | 39.4971 | 2466.3505
[7 empty] | 10067 | 16760 | 1476053 | 2017-04-07 23:04 | 2017-04-08 10:34 | 690 | 11kV | 19069 | 289 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S35800 Bankstown Panel 21 'S46109 Bankstown Aux No2' fdr tripped on Relays: A & B Phase O/C, EF, EFI Signals: 11kv trip, Tx12GE Field EFI operated @ S46109, 3094 Note: No access to S3095 and S7378 - locked gates to complex Remarks: UG fault. 11kv feeder fault from S3095 Moxon Joyce (Sw/D) to S1108 Wiggs Rd (Sw/A) to Sub 2639 Belgium Wiggs (Sw/B) | April | 2017 | 2017Q4 | 2017 | ZN35800:PA21 | ZN35800:PA21 | ZN35800/000021 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-04-07 | N | 65.9827 | N | 1 | N | N | 1.1101 | 39.4971 | 13935.0628
[7 empty] | 9703 | 12325 | 1476148 | 2017-04-08 15:03 | 2017-04-08 15:57 | 54 | 11kV | 62964 | 1197 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington - Pnl.28 tripped on: A & C phase O/C with EFI Fiedl EFIs: S1526, S65403, S8395, S4567 UG cable fault from S45667 tee Tx No.1 to S1681 (Sw/A) See 1476438 1476440 | April | 2017 | 2017Q4 | 2017 | ZN342:PA28 | ZN342:PA28 | ZN00342/000028 | SYDNEY | UG | Not Veg | 2017-04-08 | N | 52.6015 | N | 2 | N | N | 1.1101 | 39.4971 | 46012.2341
[7 empty] | 9545 | 10527 | 1476182 | 2017-04-08 23:03 | 2017-04-09 01:24 | 140.8167 | 11kV | 2534.7 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171700 1 fault operation 3 phase Line DOLF CC1: 22-"Refer to SOp" | April | 2017 | 2017Q4 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2017-04-08 | N | 140.8167 | N | 2 | N | N | 1.1101 | 39.4971 | 1852.284
[7 empty] | 9168 | 6199 | 1476252 | 2017-04-09 12:02 | 2017-04-09 12:28 | 26 | 11kV | 283 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S12630 Peats Ridge Ex Panel 8 Recloser 44995 Kulnurra Tripped on OC Abnromal Switching: CP49195 Closed, CP43601 Open and Defective Cause not ascertained for outage See OMS 1476660 1476642 1476252 | April | 2017 | 2017Q4 | 2017 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2017-04-09 | N | 21.7692 | N | 10 | N | N | 1.1101 | 39.4971 | 206.8081
[7 empty] | 8773 | 1046 | 1476213 | 2017-04-09 09:40 | 2017-04-09 12:33 | 173 | 11kV | 88661 | 640 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 171708 No protection operations. B ph ABS 17732 burning badly. ABS opened & backfed. | April | 2017 | 2017Q4 | 2017 | 243:80080 | 243:80080 | ZN00243/080080 | LAKE MACQUARIE | OH | Not Veg | 2017-04-09 | N | 138.5328 | N | 10 | N | N | 1.1101 | 39.4971 | 64790.8437
[7 empty] | 9947 | 15278 | 1476250 | 2017-04-09 11:36 | 2017-04-09 14:09 | 153 | 11kV | 8858 | 68 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ex S12630 Peats Ridge Panel 8 Peats Ridge Recloser CP44994 Mangrove Creek Tripped on Overcurrent Abnormal Switching: CP45195 Closed, CP43601 Open and Defectve (Abnormal Had No impact on outage) Cause not ascertained for outage See OMS 1476623 1476624 1476625 1476250 | April | 2017 | 2017Q4 | 2017 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2017-04-09 | N | 130.2647 | N | 10 | N | N | 1.1101 | 39.4971 | 6473.1651
[7 empty] | 10358 | 20306 | 1476262 | 2017-04-09 12:07 | 2017-04-09 14:20 | 133 | 11kV | 399 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 171710 Single phase LL lead broken away from clamp. Excluded OMS No. 1476262 | April | 2017 | 2017Q4 | 2017 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2017-04-09 | N | 133 | N | 10 | N | N | 1.1101 | 39.4971 | 291.5774
[7 empty] | 9372 | 8400 | 1476319 | 2017-04-09 17:49 | 2017-04-09 18:57 | 68 | 11kV | 64396 | 947 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At ZN2196 Milperra Panel #3 'S4449 Beaconfield' feeder has tripped on: Signals: 11kv trip Relays: IOC, lockout timing, Remarks: tree branch contact - other. Burnt tree branch found resting on HV near #186 Marco Ave, Panania | April | 2017 | 2017Q4 | 2017 | ZN2196:PA3 | ZN2196:PA3 | ZN02196/000003 | CANTERBURY-BANKSTOWN | OH | Veg | 2017-04-09 | N | 68 | N | 10 | N | N | 1.1101 | 39.4971 | 47058.6974
[7 empty] | 8890 | 2646 | 1476251 | 2017-04-09 11:39 | 2017-04-09 19:01 | 442 | 11kV | 18434 | 90 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171709 B Phase mains on ground at pole SF-50044 Excluded OMS No. 1476251 | April | 2017 | 2017Q4 | 2017 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2017-04-09 | N | 204.8222 | N | 10 | N | N | 1.1101 | 39.4971 | 13471.0235
[7 empty] | 9430 | 9212 | 1476375 | 2017-04-09 19:24 | 2017-04-09 21:07 | 103 | 11kV | 55357 | 619 | HV | Vegetation Blow/Fall In | Vegetation | O/H Link | Unplanned | Rain Wind Storm | N | iR62165 Point Larkin tripped, reclosed and locked out on: OC trip Ex Pnl.2 Long Jetty Branch found acorrs 11kV USL 41757 See 1476489 1476490 1476491 | April | 2017 | 2017Q4 | 2017 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Veg | 2017-04-09 | N | 89.4297 | N | 10 | N | N | 1.1101 | 39.4971 | 40453.2628
[7 empty] | 9757 | 13147 | 1476383 | 2017-04-09 19:49 | 2017-04-09 23:35 | 226 | 11kV | 226 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 171714 B Phase DOLF : 10 Amp Private LV mains on ground, isolated at pole 8M-30388, advised get contractor. Excluded OMS 1476383. | April | 2017 | 2017Q4 | 2017 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | Unknown | Not Veg | 2017-04-09 | N | 226 | N | 10 | N | N | 1.1101 | 39.4971 | 165.1541
[7 empty] | 9327 | 7828 | 1476382 | 2017-04-09 21:40 | 2017-04-10 02:15 | 275 | 11kV | 1975 | 9 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | Lightning | N | 11kV AB43855 Opened For Safety 11kV feeder isolated from AB 43855 to LB48675 to Rec45050 te PT13221 Cause: exposed HV CCT, OH down between Poles WY2997 and WY2995. Tree on wires. Insulation has been damaged and conductor is visible. Exposed section 1.8m above ground. Broken Cross Arm. See OMS 1476608 1476405 1476404 1476382 | April | 2017 | 2017Q4 | 2017 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2017-04-09 | N | 219.4444 | N | 10 | N | N | 1.1101 | 39.4971 | 1443.2717
[7 empty] | 9185 | 6331 | 1476417 | 2017-04-10 03:38 | 2017-04-10 04:58 | 80 | 11kV | 96927 | 1332 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn10994 Mortdale -Pnl.1- tripped, reclosed and locked out on: C phase O/C, E/F, Lockout Field EFIs: S10123 S10949 Abnormal: S10654 (Sw/B) Closed with AB31154 Open and Defective UGOH near S10949 Lorraine Pindari (Sw/B side) failed explosively. See 1476467 1476468 | April | 2017 | 2017Q4 | 2017 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | Unknown | Unknown | 2017-04-10 | N | 72.768 | N | 2 | N | N | 1.1101 | 39.4971 | 70831.3927
[7 empty] | 9409 | 8861 | 1476296 | 2017-04-09 15:53 | 2017-04-10 10:45 | 1132 | 11kV | 31286 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | LID 171712 22kV Wires found down beyond ABS 40975. Brought down by a tree. Pole 8V-50094. Due to lateness in the day conductor was repaired the next morning. Incident caused a grass fire Excluded OMS 1476296 & 1476333 & 1476392 | April | 2017 | 2017Q4 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-04-09 | N | 319.2449 | N | 10 | N | N | 1.1101 | 39.4971 | 22862.886
[7 empty] | 9197 | 6411 | 1476635 | 2017-04-10 14:39 | 2017-04-10 21:00 | 381.1333 | 11kV | 1905.6667 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 171721 no protection operation lead off to DOLF 27329 Excluded OMS 1476648 | April | 2017 | 2017Q4 | 2017 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2017-04-10 | N | 381.1333 | N | 2 | N | N | 1.1101 | 39.4971 | 1392.605
[7 empty] | 8811 | 1588 | 1476972 | 2017-04-11 20:49 | 2017-04-11 22:35 | 106 | 11kV | 3286 | 31 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 171741 B Phase DOLF : 16 Amp Possum. Volts = 243, 243, 244 Excluded OMS 1476972. | April | 2017 | 2017Q4 | 2017 | 221:11898 | 220:8687 | ZN00220/008687 | LAKE MACQUARIE | OH | Not Veg | 2017-04-11 | N | 106 | N | 2 | N | N | 1.1101 | 39.4971 | 2401.3119
[7 empty] | 9595 | 11198 | 1476963 | 2017-04-11 19:54 | 2017-04-12 00:40 | 286 | 11kV | 65780 | 230 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 171742 No protection operations. Burnt tapping ABS 64944. Excluded OMS 1476963. | April | 2017 | 2017Q4 | 2017 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2017-04-11 | N | 286 | N | 2 | N | N | 1.1101 | 39.4971 | 48070.0838
[7 empty] | 10311 | 19755 | 1477239 | 2017-04-13 10:28 | 2017-04-13 12:00 | 92.1 | 11kV | 1289.4 | 14 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn14891 Wyong section of Pa20 "Warnervale West Railway" fdr LK42103 interrupted by DOp to allow lineworker to remove tree of 11kV Mains adjacent to LK42103 See 1477264 exclude 1477239 | April | 2017 | 2017Q4 | 2017 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2017-04-13 | N | 92.1 | N | 3 | N | N | 1.1101 | 39.4971 | 942.2555
[7 empty] | 9581 | 10988 | 1477816 | 2017-04-13 12:00 | 2017-04-13 13:10 | 70 | 11kV | 140 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171763 C Phase DOLF : 10 Amp also sub 51446 cph 10A dolf | April | 2017 | 2017Q4 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-04-13 | N | 70 | N | 3 | N | N | 1.1101 | 39.4971 | 102.3079
[7 empty] | 10126 | 17549 | 1477399 | 2017-04-13 22:37 | 2017-04-14 00:42 | 125 | 11kV | 106799 | 859 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1287 Revesby Panel No.6 'River Blamey' feeder tripped and reclosed and tripped on Signals: 11kv trip, Tx3 Grou Earth, Zone Earth Relays: A ph OC, A ph IOC, earth fault, fault check, timing relay, lockout EFi: Pa6, S6634 Remarks: UG fault. UG fault between S6634 River Blamey Sw/B and S35801 Doyle School Sw/A | April | 2017 | 2017Q4 | 2017 | ZN1287:PA6 | ZN1287:PA6 | ZN01287/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-04-13 | N | 124.3295 | N | 3 | N | N | 1.1101 | 39.4971 | 78045.5592
[7 empty] | 9735 | 12813 | 1477454 | 2017-04-14 13:56 | 2017-04-14 15:10 | 74 | 11kV | 148 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171765 A & B Phase DOLF's : 16 Amp Excluded OMS 1477454 | April | 2017 | 2017Q4 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-04-14 | N | 74 | N | 2 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 9662 | 11900 | 1477499 | 2017-04-14 23:00 | 2017-04-15 00:57 | 117 | 11kV | 3042 | 26 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S4545 Meadowbank pan el 9 tripped Relays: Earth fault, EFI, Fault Check Signals: 11kV Trip, Zone Earth EFI's - NIL Cause: Front line feeder fault from Panel 9 Meadowbank to S8283 | April | 2017 | 2017Q4 | 2017 | ZN4545:PA9 | ZN4545:PA9 | ZN04545/000009 | CANADA BAY | UG | Not Veg | 2017-04-14 | N | 117 | N | 2 | N | N | 1.1101 | 39.4971 | 2223.0039
[7 empty] | 9723 | 12619 | 1477609 | 2017-04-16 02:03 | 2017-04-16 03:45 | 102 | 11kV | 78340 | 1015 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15014 Mona Vale Pa9 left "Mona Vale Pittwater" fdr tripped on Relays: E/F, fault check, EFI Signals: 11kV, Zone Earth EFI's: S17061 S49359 S15853 UG fault S15853 to S16465 tee PT15395 See 1477909,10,1 exclude 1477609 | April | 2017 | 2017Q4 | 2017 | ZN15014:PA9 | ZN15014:PA8 | ZN15014/000008 | NORTHERN BEACHES | UG | Not Veg | 2017-04-16 | N | 77.1823 | N | 3 | N | N | 1.1101 | 39.4971 | 57248.5614
[7 empty] | 10286 | 19373 | 1477603 | 2017-04-16 00:13 | 2017-04-16 10:05 | 592 | 11kV | 100547 | 700 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 171768 MVA broke pole JU-15205. Replaced under AP. Excluded OMS 147702. | April | 2017 | 2017Q4 | 2017 | 210:83465 | 210:83465 | ZN00210/083465 | LAKE MACQUARIE | OH | Not Veg | 2017-04-16 | N | 143.6386 | N | 3 | N | N | 1.1101 | 39.4971 | 73476.782
[7 empty] | 9076 | 5146 | 1477618 | 2017-04-16 07:01 | 2017-04-16 19:55 | 774 | 11kV | 73449 | 531 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa1 "Gunderman fdr" RE45189 Cooks Peats Ridge tripped on SEF Tree/branch brought down OH at 4450 Wisemans Ferry Road. HV mains into LV and PT damaged. See 1477919,21,2 exclude 1477618,26,30,33,40,1,2,3 | April | 2017 | 2017Q4 | 2017 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2017-04-16 | N | 138.322 | N | 3 | N | N | 1.1101 | 39.4971 | 53674.3628
[7 empty] | 9938 | 15207 | 1477705 | 2017-04-17 07:00 | 2017-04-17 08:05 | 65 | 11kV | 260 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171771 C Phase DOLF : 20 Amp Operators did check the job out. Operators have requested depot staff check the tension of a long span of LV crossing a nearby dam not far from the sub. Excluded OMS 1477705 | April | 2017 | 2017Q4 | 2017 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2017-04-17 | N | 65 | N | 1 | N | N | 1.1101 | 39.4971 | 190.0003
[7 empty] | 9669 | 12005 | 1477853 | 2017-04-18 10:10 | 2017-04-18 13:40 | 210 | 11kV | 210 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171778 Burnt connection on 11kV dropper had to be repaired. Excluded OMS 1477853 | April | 2017 | 2017Q4 | 2017 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-04-18 | N | 210 | N | 2 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 10193 | 18437 | 1478018 | 2017-04-18 18:20 | 2017-04-18 20:00 | 100 | 11kV | 800 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171779 interrupt to retension low HV OHM | April | 2017 | 2017Q4 | 2017 | 512:48048 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2017-04-18 | N | 100 | N | 2 | N | N | 1.1101 | 39.4971 | 584.6164
[7 empty] | 10066 | 16719 | 1478121 | 2017-04-19 10:40 | 2017-04-19 12:02 | 82 | 11kV | 137942 | 1907 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.30 tripped on: IOC, FC with EFI Field EFIs: S46847, S8981, S2132, S8570, S3928, S8851 UG cable fault between S8851 , S4017 & S3355 See 1478325 1478326 | April | 2017 | 2017Q4 | 2017 | ZN2602:PA30 | ZN36800:PA58 | ZN36800/000058 | WAVERLEY | UG | Not Veg | 2017-04-19 | N | 72.3346 | N | 3 | N | N | 1.1101 | 39.4971 | 100803.945
[7 empty] | 9494 | 9887 | 1478137 | 2017-04-19 11:35 | 2017-04-19 12:24 | 49 | 11kV | 98 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171787 B Phase DOLF : 10 Amp Tx Volts: 246V Excluded OMS No. 1478137 | April | 2017 | 2017Q4 | 2017 | 513:48056 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2017-04-19 | N | 49 | N | 3 | N | N | 1.1101 | 39.4971 | 71.6155
[7 empty] | 8959 | 3527 | 1478211 | 2017-04-19 09:15 | 2017-04-19 20:35 | 680 | 11kV | 2276 | 4 | HV | Vandalism | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171790 Stolen earths. Outage continued from report 171783 planned outage. Excluded oms1478211. | April | 2017 | 2017Q4 | 2017 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2017-04-19 | N | 569 | N | 3 | N | N | 1.1101 | 39.4971 | 1663.2337
[7 empty] | 9331 | 7842 | 1478570 | 2017-04-21 03:16 | 2017-04-21 05:12 | 116 | 11kV | 175988 | 1630 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn12620 Noraville Pa11 "Norah head" fdr tripped on: Relays: Earth Fault, Timing and lockout Signals: 11kv trip and EFI EFI's: nil UGOH fault between Zn12620 Pa11 to LB40203 See 1479085,6,7 exclude 1478570 | April | 2017 | 2017Q4 | 2017 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | Unknown | Unknown | 2017-04-21 | N | 107.9681 | N | 2 | N | N | 1.1101 | 39.4971 | 128606.8396
[7 empty] | 9728 | 12677 | 1478680 | 2017-04-21 14:39 | 2017-04-21 16:02 | 83 | 11kV | 5559 | 68 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland Pnl.22 tripped on: B Phase Earth Fault and C phase Overcurrent, EFI Field EFIs: S3696 UG cable fault from S35664 (Sw/B) to S5152 (Sw/A) | April | 2017 | 2017Q4 | 2017 | ZN188:PA22 | ZN188:PA22 | ZN00188/000022 | SYDNEY | UG | Not Veg | 2017-04-21 | N | 81.75 | N | 2 | N | N | 1.1101 | 39.4971 | 4062.3532
[7 empty] | 9184 | 6318 | 1478761 | 2017-04-22 07:13 | 2017-04-22 16:15 | 542 | 11kV | 84918 | 254 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171817 2 fault operations A & C phase Overcurrent, Earth Fault swan hit mains beyond pole FR-62004 to Potter sub 54002 bringing down wires. section isolated for repair to mains. Excluded OMS 1478761 | April | 2017 | 2017Q4 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2017-04-22 | N | 334.3228 | N | 2 | N | N | 1.1101 | 39.4971 | 62055.5697
[7 empty] | 10094 | 17190 | 1478751 | 2017-04-22 04:06 | 2017-04-22 22:12 | 1086 | 11kV | 117860 | 1030 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN1290 Leightonfield 11kv Pnl 12 "Miller Bil #1" tripped on C phase IOC with timing and lock out Signals: 11kv trip, Zone and group 3 earth with efi Remarks: 11kv feeder fault between S528 Miller Bill no.3 to open span of O/H mains on pole no.FA01111 tee to CP176 Bennett Miller span of 11kv O/H was removed to energise and restore feeder to S-163 Biloela Mill | April | 2017 | 2017Q4 | 2017 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-04-22 | N | 114.4272 | N | 2 | N | N | 1.1101 | 39.4971 | 86128.6117
[7 empty] | 9139 | 5884 | 1478945 | 2017-04-24 06:34 | 2017-04-24 08:22 | 108 | 11kV | 232416 | 2152 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN3472 Sefton 11kv Panel #30 labelled "S4411 Roayl Gas & S4114 Royal well" tripped, reclosed & tripped: Remarks: 11kv underground feeder fault from P30 @ ZN3472 Sefton to Sw/A @ S4411 Royal Gas tee S4114 Royal Well | April | 2017 | 2017Q4 | 2017 | ZN3472:PA30 | ZN3472:PA30 | ZN03472/000030 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-04-24 | N | 108 | N | 3 | N | N | 1.1101 | 39.4971 | 169842.7577
[7 empty] | 8878 | 2493 | 1478963 | 2017-04-24 08:52 | 2017-04-24 14:10 | 318 | 11kV | 7684.25 | 46 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171823 1 fault operation 3 phase Sensitive Earth Fault tree on mains near 3624 Whitlock sub. | April | 2017 | 2017Q4 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-04-24 | N | 167.0489 | N | 3 | N | N | 1.1101 | 39.4971 | 5615.4233
[7 empty] | 9984 | 15767 | 1479123 | 2017-04-24 23:44 | 2017-04-25 00:50 | 66 | 11kV | 66 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171826 B Phase DOLF : 10 Amp Excluded OMS 1479123 | April | 2017 | 2017Q4 | 2017 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2017-04-24 | N | 66 | N | 3 | N | N | 1.1101 | 39.4971 | 48.2309
[7 empty] | 9169 | 6215 | 1479125 | 2017-04-25 03:05 | 2017-04-25 04:15 | 70 | 11kV | 47559 | 899 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman Pa 33 S4891 fdr tripped on: Relays: C phase timmed overcurrent, C phase Inst Overcurrent, EFI, Fault check relay EFI's: Nil Signals: 11kv trip, Tx2 Group Earth Cause: 11kv fdr fault between S293 Bydown st Sw/A and S3839 Yeo Barry Sw/B. EFI did not operate at S293Sw/D. See seperate interruption on Pa 31 See 1479353,4,5 exclude 1479125 | April | 2017 | 2017Q4 | 2017 | ZN180:PA33 | ZN180:PA33 | ZN00180/000033 | NORTH SYDNEY | UG | Not Veg | 2017-04-25 | N | 52.9021 | N | 2 | N | N | 1.1101 | 39.4971 | 34754.7144
[7 empty] | 9015 | 4147 | 1479228 | 2017-04-25 18:09 | 2017-04-26 02:11 | 482 | 11kV | 24894 | 122 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 171832 3 Fault Operations Note suspect Sw74606 faulty - bypassed. Equip defect & gas alarms URGENT ATTENTION REQ Subsequent sectionalising trips Sw 42268. Sw 74606 1-3 trips? Sw 42268 2 trips Wire off pin ins at pole 9L-30010 Excluded OMS 1479228 | April | 2017 | 2017Q4 | 2017 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2017-04-25 | N | 204.0492 | N | 2 | N | N | 1.1101 | 39.4971 | 18191.801
[7 empty] | 8885 | 2607 | 1479313 | 2017-04-26 10:14 | 2017-04-26 11:20 | 66 | 11kV | 6468 | 98 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171848 customers interupted to repair broken strands | April | 2017 | 2017Q4 | 2017 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2017-04-26 | N | 66 | N | 13 | N | N | 1.1101 | 39.4971 | 4726.6236
[7 empty] | 8855 | 2145 | 1479358 | 2017-04-26 10:46 | 2017-04-26 15:10 | 264 | 11kV | 5946 | 38 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of Pa17 RE45037 Reeves Soemrsby tripped and locked out on Signals: SEF Trip, Lockout Cause not ascertained See 1479711,2 exclude 1479358,82 | April | 2017 | 2017Q4 | 2017 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Veg | 2017-04-26 | N | 156.4737 | N | 13 | N | N | 1.1101 | 39.4971 | 4345.1614
[7 empty] | 9986 | 15798 | 1479432 | 2017-04-26 14:30 | 2017-04-26 15:29 | 59 | 11kV | 53631 | 909 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S35800 Bankstown 11kv panel No.16 tripped on; Relays: IOC ABC phase Signals: 11kv trip Remarks: tree branch found on ground after falling off of OH HV mains, mains appear to be in good condition | April | 2017 | 2017Q4 | 2017 | ZN35800:PA16 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | OH | Veg | 2017-04-26 | N | 59 | N | 13 | N | N | 1.1101 | 39.4971 | 39191.953
[7 empty] | 10039 | 16483 | 1479493 | 2017-04-26 15:38 | 2017-04-26 17:20 | 102 | 11kV | 141932 | 1414 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 171857 2 fault operations A & C phase Overcurrent wires down Wangi st Cessnock. EFI down at cessnock west PS sub. 3000 A fault current. Excluded OMS 1479519 | April | 2017 | 2017Q4 | 2017 | 504:48034 | 522:83129 | ZN00522/083129 | CESSNOCK | OH | Not Veg | 2017-04-26 | N | 100.3762 | N | 13 | N | N | 1.1101 | 39.4971 | 103719.7193
[7 empty] | 9810 | 13744 | 1479544 | 2017-04-26 16:56 | 2017-04-26 18:55 | 119 | 11kV | 119 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 171860 LLC broken on A phase. Excluded OMS 1479544 | April | 2017 | 2017Q4 | 2017 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2017-04-26 | N | 119 | N | 13 | N | N | 1.1101 | 39.4971 | 86.9617
[7 empty] | 9165 | 6184 | 1479497 | 2017-04-26 15:39 | 2017-04-26 20:08 | 269 | 11kV | 73380 | 404 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 171858 3 fault operation A & B phase Overcurrent Excluded OMS 1479497 | April | 2017 | 2017Q4 | 2017 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2017-04-26 | N | 181.6337 | N | 13 | N | N | 1.1101 | 39.4971 | 53623.9397
[7 empty] | 9626 | 11528 | 1479654 | 2017-04-26 15:39 | 2017-04-26 20:40 | 301 | 11kV | 40032.7333 | 133 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Wind Strong | N | PT10743 Gungah Bay Mulga - 11kV Roadside HDO 50A operated Old style HDO fuse holder broken (No replacement found) Restored via LV //'s 2677, 118, 271, 230, 702, 1809 Note: Tx may be faulty See 1479659 others: 1476954 1479655 1479657 | April | 2017 | 2017Q4 | 2017 | ZN10994:PA1 | ZN10994:PA1 | ZN10994/000001 | GEORGES RIVER | OH | Not Veg | 2017-04-26 | N | 300.998 | N | 13 | N | N | 1.1101 | 39.4971 | 29254.7408
[7 empty] | 9843 | 14076 | 1479524 | 2017-04-26 16:21 | 2017-04-26 21:04 | 283.2167 | 11kV | 5097.9 | 18 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 171862 A Phase DOLF : 20 Amp possible lightening strike 1 span past LF 47027. | April | 2017 | 2017Q4 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Not Veg | 2017-04-26 | N | 283.2167 | N | 13 | N | N | 1.1101 | 39.4971 | 3725.395
[7 empty] | 9034 | 4477 | 1479516 | 2017-04-26 16:03 | 2017-04-26 21:20 | 316.9333 | 11kV | 5704.8 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 171863 B Phase DOLF : 10 Amp CC1: 22-"Refer to SOp" | April | 2017 | 2017Q4 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2017-04-26 | N | 316.9333 | N | 13 | N | N | 1.1101 | 39.4971 | 4168.8996
[7 empty] | 9137 | 5819 | 1479558 | 2017-04-26 17:19 | 2017-04-26 22:35 | 316 | 11kV | 4424 | 14 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 171865 OHM down near 70267. No protection ops CCT cable. | April | 2017 | 2017Q4 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2017-04-26 | N | 316 | N | 13 | N | N | 1.1101 | 39.4971 | 3232.9287
[7 empty] | 9053 | 4791 | 1479582 | 2017-04-26 19:32 | 2017-04-26 22:55 | 203 | 11kV | 1827 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 171866 A Phase DOLF : 10 Amp | April | 2017 | 2017Q4 | 2017 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2017-04-26 | N | 203 | N | 13 | N | N | 1.1101 | 39.4971 | 1335.1177
[7 empty] | 9920 | 15009 | 1479443 | 2017-04-26 15:26 | 2017-04-27 08:50 | 1044.0333 | 11kV | 78302.5 | 75 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | PT9431 Genista St - 11kV roadside 50A HDO fuse operated Fuse fatigue and also a branch took down 1 full bay of DIstributor wire on Browillia Cres. | April | 2017 | 2017Q4 | 2017 | ZN9252:PA22 | ZN9252:PA22 | ZN09252/000022 | SUTHERLAND | OH | Veg | 2017-04-26 | N | 1044.0333 | N | 13 | N | N | 1.1101 | 39.4971 | 57221.1575
[7 empty] | 8887 | 2617 | 1479614 | 2017-04-27 07:48 | 2017-04-27 11:50 | 242 | 11kV | 242 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 171880 A Phase DOLF : 10 Amp Excluded OMS 1479614 | April | 2017 | 2017Q4 | 2017 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2017-04-27 | N | 242 | N | 5 | N | N | 1.1101 | 39.4971 | 176.8465
[7 empty] | 8901 | 2778 | 1479741 | 2017-04-27 12:30 | 2017-04-27 13:10 | 40 | 11kV | 240 | 6 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 171881 Cable re attached to pin insulator at pole BP-60001. | April | 2017 | 2017Q4 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2017-04-27 | N | 40 | N | 5 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 9784 | 13529 | 1479534 | 2017-04-26 16:44 | 2017-04-27 14:30 | 1305.7667 | 11kV | 13057.6667 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 171868 Tree on ohm near 52787. Excluded OMS 1479571 | April | 2017 | 2017Q4 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-04-26 | N | 1305.7667 | N | 13 | N | N | 1.1101 | 39.4971 | 9542.1577
[7 empty] | 8784 | 1253 | 1479782 | 2017-04-27 15:02 | 2017-04-27 17:00 | 118 | 11kV | 173067 | 1948 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn9700 Kirrawee - Pnl.11 tripped, reclosed, tripped & locked out on: Earth Fault. Field EFIs: S9518, S9325 ,S9242 ,S9448, S9340, S9394 UG cable hit by excavator. See 1479907 1479908 1479909 | April | 2017 | 2017Q4 | 2017 | ZN9700:PA11 | ZN9700:PA18 | ZN09700/000018 | SUTHERLAND | UG | Not Veg | 2017-04-27 | N | 88.8434 | N | 5 | N | N | 1.1101 | 39.4971 | 126472.259
[7 empty] | 9676 | 12100 | 1479827 | 2017-04-27 17:10 | 2017-04-27 21:25 | 255 | 11kV | 765 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171885 Repair dropper lead Excluded OMS 1479827 | April | 2017 | 2017Q4 | 2017 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Not Veg | 2017-04-27 | N | 255 | N | 5 | N | N | 1.1101 | 39.4971 | 559.0394
[7 empty] | 10029 | 16354 | 1479878 | 2017-04-27 23:10 | 2017-04-28 00:40 | 90 | 11kV | 2655 | 32 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171886/02 emergency isolation for repair of 33kV downed mains. | April | 2017 | 2017Q4 | 2017 | 228:7490 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Not Veg | 2017-04-27 | N | 82.9688 | N | 5 | N | N | 1.1101 | 39.4971 | 1940.1957
[7 empty] | 9877 | 14505 | 1479880 | 2017-04-28 00:52 | 2017-04-28 01:47 | 55 | 11kV | 31020 | 564 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 22 tripped on Relays: A and B phase Overcurrent Cause: Possum found dead at the base of PT1667 Westwood Stevens. Appears to have flashed over. T/Con required to check in daylight hours See OMS 1479880 1479881 | April | 2017 | 2017Q4 | 2017 | ZN965:PA22 | ZN965:PA22 | ZN00965/000022 | HORNSBY | OH | Not Veg | 2017-04-28 | N | 55 | N | 2 | N | N | 1.1101 | 39.4971 | 22668.5011
[7 empty] | 9209 | 6588 | 1479983 | 2017-04-28 10:30 | 2017-04-28 11:40 | 70 | 11kV | 280 | 4 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 171897 Stay rubbing on tank no protection operation. Excluded OMS 1479904 | April | 2017 | 2017Q4 | 2017 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2017-04-28 | N | 70 | N | 2 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 9800 | 13641 | 1480098 | 2017-04-29 12:51 | 2017-04-29 13:15 | 24 | 11kV | 144 | 6 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | LID 171904 interrupt to replace crossarm pole EO-90227 near sub 51360 Excluded OMS 1480098 | April | 2017 | 2017Q4 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | Unknown | Not Veg | 2017-04-29 | N | 24 | N | 1 | N | N | 1.1101 | 39.4971 | 105.231
[7 empty] | 8831 | 1799 | 1480182 | 2017-04-30 03:04 | 2017-04-30 07:00 | 236 | 11kV | 398852 | 1909 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15006 Dee Why West Panel 8 tripped, reclosed, tripped and locked out on Relays: B and C phase O/C, Reclose and Lockout Cause: Bat found near PT15350 On re energuising feeder defective bond found at USL20956 See OMS 1480292 1480296 1480182 | April | 2017 | 2017Q4 | 2017 | ZN15006:PA8 | ZN15006:PA8 | ZN15006/000008 | NORTHERN BEACHES | OH | Not Veg | 2017-04-30 | N | 208.9324 | N | 2 | N | N | 1.1101 | 39.4971 | 291469.2775
[7 empty] | 9351 | 8086 | 1480293 | 2017-05-01 01:29 | 2017-05-01 02:20 | 51 | 11kV | 39767 | 805 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn9700 Kirrawee Pnl.11 tripped on: B pahse Earth Fault Abnormal: S9394 (Sw/B) and S9054 (Sw/A) Open with S9544 (Sw/B) Closed and PT9583 in LV // from previous fault. 11kV Feeder repairs failed. See D/R (SOp arranged) #404222 Subs 9242, 9448, 9340, 9214 & 9394 restored via LV // See 1480293 1480295 | May | 2017 | 2017Q4 | 2017 | ZN9700:PA11 | ZN9700:PA11 | ZN09700/000011 | SUTHERLAND | Unknown | Unknown | 2017-05-01 | N | 49.4 | N | 2 | N | N | 1.1101 | 39.4971 | 29060.5507
[7 empty] | 9908 | 14893 | 1480414 | 2017-04-30 23:58 | 2017-05-01 13:30 | 812 | 11kV | 61426 | 1402 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn10996 Rockdale - pnl.12 tripped and reclosed on: Earth Fault with EFI Field EFIs: S10612, S10688 Car hit 3 poles causing wires to clash and brought LV mains down. See 1481283 LV // failures 1481284 1481285 1481287 1481288 | April | 2017 | 2017Q4 | 2017 | ZN10990:PA12 | ZN10998:PA10 | ZN10998/000010 | BAYSIDE | OH | Not Veg | 2017-04-30 | N | 43.8131 | N | 2 | N | N | 1.1101 | 39.4971 | 44888.309
[7 empty] | 9159 | 6116 | 1480579 | 2017-05-01 08:15 | 2017-05-01 16:40 | 505 | 11kV | 68175 | 135 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Planned LID 171912 SINO 19587 | May | 2017 | 2017Q4 | 2017 | 257:82006 | 257:82006 | ZN00257/082006 | NEWCASTLE | OH | Veg | 2017-05-01 | N | 505 | N | 2 | N | N | 1.1101 | 39.4971 | 49820.2792
[7 empty] | 9799 | 13621 | 1480580 | 2017-05-02 09:26 | 2017-05-02 15:30 | 364 | 11kV | 526017 | 2759 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.30 tripped on: B Phase Earth Fault, Faule with and EFI Field EFIs: S2141, S8949, S1968, S4261, CP1561, S2344, S1399, S4277 (S35730 DID NOT WORK) Abnormal: CP1561 (Sw/D) found closed with S76799 (Sw/B) open (Panel 12) 11kV UG cable fault from S4278 to S8076 to S4049. Multiple LV parallel failures occurred due to the 11kV outage. See1480861 1480861 1480862 1480863 1480864 1480865 LV // failures: 1480875 1480876 1480877 1480878 1480879 | May | 2017 | 2017Q4 | 2017 | ZN690:PA12 | ZN690:PA12 | ZN00690/000012 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-05-02 | N | 190.6549 | N | 3 | N | N | 1.1101 | 39.4971 | 384397.7087
[7 empty] | 9855 | 14240 | 1480795 | 2017-05-02 19:25 | 2017-05-02 20:50 | 85 | 11kV | 142267 | 1847 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Zn9118 Cronulla - Pnl.11 tripped on: EFI (DOp advised relay had reset button pressed in and stuck, no relay operation to go off) REC35756 Bundeena tripped and reclosed to de-energised on O/C Field EFIs: S9755 On 11kV UGOH from REC 35756 to Submarine cable - Surge arrestors defective. See 1480850 1480851 | May | 2017 | 2017Q4 | 2017 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2017-05-02 | N | 77.026 | N | 3 | N | N | 1.1101 | 39.4971 | 103964.5274
[7 empty] | 9911 | 14938 | 1480805 | 2017-05-02 20:09 | 2017-05-02 21:30 | 81 | 11kV | 8790 | 2070 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn10995 Riverwood - Pnl.1 tripped & reclosed on: C phase IOC, E/F, EFI Field EFIs: S10758, S61175 (no flag), S10947 Possum on HDO fuses at PT10515 Olive Bonds See 1480855 1480856 | May | 2017 | 2017Q4 | 2017 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | OH | Not Veg | 2017-05-02 | N | 4.2464 | N | 3 | N | N | 1.1101 | 39.4971 | 6423.4727
[7 empty] | 9186 | 6337 | 1480841 | 2017-05-03 08:00 | 2017-05-03 10:20 | 140.2667 | 11kV | 1683.2 | 12 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171936 Repair stranded OHM at pole HQ-72107 planned outage 1481116 for sub 50705 effected during this unplanned event | May | 2017 | 2017Q4 | 2017 | 511:29876 | 511:29876 | ZN00511/029876 | MAITLAND | OH | Not Veg | 2017-05-03 | N | 140.2667 | N | 3 | N | N | 1.1101 | 39.4971 | 1230.0329
[7 empty] | 10282 | 19320 | 1480904 | 2017-05-03 10:15 | 2017-05-03 14:23 | 248 | 11kV | 28272 | 114 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 171939 Broken X arm pole MN-53933 Excluded OMS 1480904 | May | 2017 | 2017Q4 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2017-05-03 | N | 248 | N | 3 | N | N | 1.1101 | 39.4971 | 20660.3437
[7 empty] | 10214 | 18714 | 1481042 | 2017-05-03 21:04 | 2017-05-03 21:35 | 31 | 11kV | 93 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 171943 A Phase No protection operation. Isolated for Live Line crew to repair tapping on line side of A phase DOLF. Excluded OMS 1481042 | May | 2017 | 2017Q4 | 2017 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2017-05-03 | N | 31 | N | 3 | N | N | 1.1101 | 39.4971 | 67.9617
[7 empty] | 10176 | 18090 | 1481163 | 2017-05-04 12:47 | 2017-05-04 16:15 | 208 | 11kV | 10238 | 110 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171956 1 fault operation C Phase DOLF : 20 Amp Sensitive Earth Fault, Overcurrent, Intellirupter Customer trimming tree 11 Lieberts Lane advised they dropped a tree or branch into the 11kV. 20A Cph Line DOLF 47387 blown. Excluded OMS 1481163+1481167 | May | 2017 | 2017Q4 | 2017 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2017-05-04 | N | 93.0727 | N | 1 | N | N | 1.1101 | 39.4971 | 7481.6284
[7 empty] | 9413 | 8921 | 1481443 | 2017-05-05 18:01 | 2017-05-05 20:10 | 129 | 11kV | 74049 | 827 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171969 2 fault operations OHM down across Dora Creek pole HW-40495 to HW-40702 Excluded OMS 1481443 | May | 2017 | 2017Q4 | 2017 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2017-05-05 | N | 89.5393 | N | 2 | N | N | 1.1101 | 39.4971 | 54112.8251
[7 empty] | 9348 | 8048 | 1481465 | 2017-05-05 23:45 | 2017-05-06 01:34 | 109 | 11kV | 1308 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 171973 B Phase DOLF : 20 Amp | May | 2017 | 2017Q4 | 2017 | 511:29876 | 511:29876 | ZN00511/029876 | MAITLAND | OH | Veg | 2017-05-05 | N | 109 | N | 2 | N | N | 1.1101 | 39.4971 | 955.8478
[7 empty] | 9860 | 14336 | 1481484 | 2017-05-06 09:35 | 2017-05-06 11:47 | 132 | 11kV | 396 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171975 DOLF : 10 Amp All three outages ended up being the same PT. Excluded OMS 1481484 | May | 2017 | 2017Q4 | 2017 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2017-05-06 | N | 132 | N | 3 | N | N | 1.1101 | 39.4971 | 289.3851
[7 empty] | 10033 | 16389 | 1481449 | 2017-05-06 15:50 | 2017-05-06 16:15 | 25 | 11kV | 2275 | 91 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 171976 Interr caused by removal of island gen installed on emerg SI 05/05/2017 - installed the night before due to 11kV main damage, see OMS 1481443. See report 171969/OMS 1481678 | May | 2017 | 2017Q4 | 2017 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2017-05-06 | N | 25 | N | 3 | N | N | 1.1101 | 39.4971 | 1662.5029
[7 empty] | 9017 | 4162 | 1481555 | 2017-05-06 17:40 | 2017-05-07 01:15 | 455 | 11kV | 6133 | 39 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 171978 2 fault operations C Phase Overcurrent; Earth Fault; Sectionaliser Broken crossarm at burnct OHM at pole GM-20002. Excluded OMS No. 1481555 + 1481573 | May | 2017 | 2017Q4 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2017-05-06 | N | 157.2564 | N | 3 | N | N | 1.1101 | 39.4971 | 4481.8155
[7 empty] | 8805 | 1544 | 1481583 | 2017-05-07 05:21 | 2017-05-07 08:10 | 169 | 11kV | 2366 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171979 B & C phase DOLF : 20 Amp Excluded OMS 1481583 | May | 2017 | 2017Q4 | 2017 | 206:34437 | 206:34437 | ZN00206/034437 | LAKE MACQUARIE | OH | Veg | 2017-05-07 | N | 169 | N | 3 | N | N | 1.1101 | 39.4971 | 1729.003
[7 empty] | 9733 | 12783 | 1481638 | 2017-05-07 16:18 | 2017-05-07 17:35 | 77 | 11kV | 154 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 171983 Single phase DOLF : 10 Amp Excluded OMS 1481638 | May | 2017 | 2017Q4 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2017-05-07 | N | 77 | N | 3 | N | N | 1.1101 | 39.4971 | 112.5387
[7 empty] | 10275 | 19272 | 1481632 | 2017-05-07 17:56 | 2017-05-07 20:50 | 174 | 11kV | 3306 | 19 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa8 Supply between LB40546 and IR63734 Goerge Downes Bloodtree 2.45 interrupted for safety 11kv mains resting on cross arm after car hit pole. Car hit pole CM236 at 638 George Downes Dr. See 1481811 exclude 1481644,5,6,9,51 | May | 2017 | 2017Q4 | 2017 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2017-05-07 | N | 174 | N | 3 | N | N | 1.1101 | 39.4971 | 2415.9273
[7 empty] | 10064 | 16698 | 1481662 | 2017-05-08 04:11 | 2017-05-08 06:24 | 133 | 11kV | 228172 | 1729 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.19 tripped on: A & B phase O.C, EFI Field EFIs: S50482 S50483 S0040 S10954 S10898 S10605 Abnormal: S1283 (Sw/A) closed with LB48122 open and defective. S10654 (Sw/B) closed with AB31154 open. Bond burnt off LB 31183 See 1481677 1481754 | May | 2017 | 2017Q4 | 2017 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2017-05-08 | N | 131.9676 | N | 2 | N | N | 1.1101 | 39.4971 | 166741.3677
[7 empty] | 9603 | 11302 | 1481839 | 2017-05-08 14:45 | 2017-05-08 16:05 | 80 | 11kV | 2000 | 25 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 171995 B Phase DOLF : 31 Amp Burnt up DOLF carrier. Excluded OMS 1481839 | May | 2017 | 2017Q4 | 2017 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2017-05-08 | N | 80 | N | 2 | N | N | 1.1101 | 39.4971 | 1461.541
[7 empty] | 9591 | 11157 | 1481919 | 2017-05-09 01:00 | 2017-05-09 21:15 | 1215 | 11kV | 243879 | 561 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn263 Dalley St - 33/34 "J" feeder interrupted for safety due to defective pilots Abnormal: 31/32G defective, 33/34H defective, 33/34E defective, 35/37E defective Explosion in pit in George St on 33/34G, 33/34H was already out defective which then caused 33/34J pilots to be damaged. S4612 & S1848 load restricted with S1042 left interrupted until 21:15 due to damage to the LV bus bar links which also occurred at the same time. See 1482191 1482192 | May | 2017 | 2017Q4 | 2017 | ZN263:PA33 34GHJ | ZN8700:PA63 64KLM | ZN08700/63 64KLM | SYDNEY | UG | Not Veg | 2017-05-09 | N | 434.7219 | N | 1 | N | N | 1.1101 | 39.4971 | 178219.58
[7 empty] | 9114 | 5535 | 1483029 | 2017-05-11 08:16 | 2017-05-11 08:22 | 6 | 11kV | 4452 | 742 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S15002 Narrabeen apenl 6 tripped on relays: Earth Fault and fault check and EFI Signals: 11kv trip, Zone Earth Abnormal Switching: SW/B Closed @ S16686, AB24376 Open, SW/A Closed @ S16879, SW/A Open @ S46741. Cause: As part of D&R 39963 Narrabeen, At S49277 DOp opened SW.A instead of SW/B and applied earth to live feeder. Which tripped Panel 6 | May | 2017 | 2017Q4 | 2017 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | Unknown | Not Veg | 2017-05-11 | N | 6 | N | 1 | N | N | 1.1101 | 39.4971 | 3253.3903
[7 empty] | 9681 | 12171 | 1482576 | 2017-05-12 04:50 | 2017-05-12 05:29 | 39 | 11kV | 9243 | 237 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | IR64824 Deepwater Holly Tripped and Locked out on O/C Cause: Possum on LB62056 - DOp removed and checked Load Break switch | May | 2017 | 2017Q4 | 2017 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | OH | Not Veg | 2017-05-12 | N | 39 | N | 1 | N | N | 1.1101 | 39.4971 | 6754.5118
[7 empty] | 9707 | 12369 | 1482761 | 2017-05-13 03:58 | 2017-05-13 10:34 | 396 | 11kV | 17303 | 203 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 172043 2 fault operations Earth Fault, Overcurrent Fdr 81645 switched abnormally, section Fdr 81648 also involved in outage. Faulty LA at UGOH JS-50390 replaced Excluded OMS 1482761 | May | 2017 | 2017Q4 | 2017 | 265:81648 | 265:81648 | ZN00265/081648 | PORT STEPHENS | OH | Not Veg | 2017-05-13 | N | 85.2365 | N | 1 | N | N | 1.1101 | 39.4971 | 12644.522
[7 empty] | 10135 | 17608 | 1482971 | 2017-05-15 05:38 | 2017-05-15 10:58 | 320 | 11kV | 165299 | 1445 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn15012 Killarney Panel 6 tripped on Relays: 6L A and C phasen O/C and EFI Signals; 11kV trip and Zone Earth Cause: 11kV UGOH fault - Section of feeder to Recloser 26228 Valley Rd See OMS 1483699 1483701 1483702 1482979 1482971 | May | 2017 | 2017Q4 | 2017 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | Unknown | Unknown | 2017-05-15 | N | 114.3938 | N | 1 | N | N | 1.1101 | 39.4971 | 120795.6337
[7 empty] | 10248 | 19009 | 1483378 | 2017-05-16 14:15 | 2017-05-16 17:20 | 185 | 11kV | 370 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172087 Single phase DOLF : 10 Amp Excluded OMS 1483378 | May | 2017 | 2017Q4 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2017-05-16 | N | 185 | N | 3 | N | N | 1.1101 | 39.4971 | 270.3851
[7 empty] | 10264 | 19130 | 1483452 | 2017-05-16 18:26 | 2017-05-16 19:21 | 55 | 11kV | 81730 | 1486 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 172065 B Phase Blown B phase tapping pole JU-61266 first call 1827hrs ABS 17513 opened 1921hrs Sw 76237 closed 1921hrs | May | 2017 | 2017Q4 | 2017 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2017-05-16 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 59725.8734
[7 empty] | 9553 | 10696 | 1483486 | 2017-05-16 22:46 | 2017-05-16 23:45 | 59 | 11kV | 114991 | 1949 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9552 Jannali - Pnl.24 tripped on: IOC, EFI Possum found at bottom of UGOH pole in Sutherland Rd near Mitchell Ave See 1483486 1483489 | May | 2017 | 2017Q4 | 2017 | ZN9252:PA24 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Not Veg | 2017-05-16 | N | 59 | N | 3 | N | N | 1.1101 | 39.4971 | 84032.0311
[7 empty] | 9328 | 7833 | 1483734 | 2017-05-18 10:20 | 2017-05-18 11:22 | 62 | 11kV | 70742 | 1141 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn3922 Drummoyne Panel 17 "S35126 Jersey Barnstaple" feeder has tripped on: Signals: 11kv trip, No.2 Group earth, Zone Earth Relays: C phase timed O/C, EFI, Fault Check Abnormals: sw/B @ 49979 open. Sw/B @ S1487 Closed Remarks: UG fault. Dop's proving feeder between S8369 Cockatoo Island No.5 (Sw/B) & S49979 Longiview Bayville (Sw/B) (#405473A) after feeder fault repairs & cable failed shortly after energisation, tripping Pa17 Drummoyne. Pa17 @ Drummoyne then kept shooting through, delaying restoration. Feeder eventually restored from S1467 Grove St | May | 2017 | 2017Q4 | 2017 | ZN3922:PA17 | ZN3922:PA17 | ZN03922/000017 | INNER WEST | UG | Not Veg | 2017-05-18 | N | 62 | N | 1 | N | N | 1.1101 | 39.4971 | 51696.1671
[7 empty] | 9065 | 4934 | 1484002 | 2017-05-19 08:00 | 2017-05-19 09:55 | 115 | 11kV | 115 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172110 Single phase DOLF : 10 Amp Reported from field no other OMS job. | May | 2017 | 2017Q4 | 2017 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-05-19 | N | 115 | N | 5 | N | N | 1.1101 | 39.4971 | 84.0386
[7 empty] | 9476 | 9757 | 1484107 | 2017-05-19 14:29 | 2017-05-19 18:50 | 261 | 11kV | 16751 | 73 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172115 4 fault operations 3 phase Earth Fault No Fault found on fdr - please patrol Excluded OMS 1484107 | May | 2017 | 2017Q4 | 2017 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-05-19 | N | 229.4658 | N | 5 | N | N | 1.1101 | 39.4971 | 12241.1367
[7 empty] | 9119 | 5590 | 1484153 | 2017-05-19 17:29 | 2017-05-19 19:27 | 118 | 11kV | 219028 | 1901 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172116 3 fault operation A Phase Overcurrent Small branch found below Fdr at GW-60017 damage to OHM please check ASAP Excluded OMS 1484453 | May | 2017 | 2017Q4 | 2017 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2017-05-19 | N | 115.2173 | N | 5 | N | N | 1.1101 | 39.4971 | 160059.2022
[7 empty] | 9023 | 4263 | 1484159 | 2017-05-19 18:10 | 2017-05-19 20:27 | 137 | 11kV | 11156.6667 | 82 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Light | N | PT10411 Emmaline Grand - Footpath phase HDO blown Suspect 300kVA Transformer is defective. Restored via LV parallel. See 1484159 | May | 2017 | 2017Q4 | 2017 | ZN10997:PA2 | ZN10997:PA2 | ZN10997/000002 | BAYSIDE | UG | Not Veg | 2017-05-19 | N | 136.0569 | N | 5 | N | N | 1.1101 | 39.4971 | 8152.9629
[7 empty] | 10259 | 19092 | 1484188 | 2017-05-19 22:14 | 2017-05-19 23:54 | 100 | 11kV | 105500 | 1097 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | @ZN2310 Punchbowl - 11KV Panel No.54 "Sub 1349 Roseview Ave" feeder tripped Relays: Earth fault & EFI Signals: 11kv trip, Zone Earth, No.2 Group Earth Remarks: UG fault. 11kv UG fault from Sub 2868 Grove Penshurst to Sub 47752 Grahame Nanowie | May | 2017 | 2017Q4 | 2017 | ZN2310:PA54 | ZN2310:PA30 | ZN02310/000030 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-05-19 | N | 96.1714 | N | 5 | N | N | 1.1101 | 39.4971 | 77096.2883
[7 empty] | 9359 | 8205 | 1484198 | 2017-05-20 03:28 | 2017-05-20 09:48 | 380 | 11kV | 34720 | 129 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 172117 Burnt tapping at pole FR- 64706. Caused outages to various single phase customers from 0328hr. Excluded oms 1484198 & 1484206. | May | 2017 | 2017Q4 | 2017 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2017-05-20 | N | 269.1473 | N | 2 | N | N | 1.1101 | 39.4971 | 25372.3519
[7 empty] | 8961 | 3551 | 1484286 | 2017-05-20 14:45 | 2017-05-20 15:10 | 25 | 11kV | 975 | 39 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172119 Isolate to repair low 11kV due to broken insulator at links 5534 Excluded oms1484286 | May | 2017 | 2017Q4 | 2017 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2017-05-20 | N | 25 | N | 2 | N | N | 1.1101 | 39.4971 | 712.5012
[7 empty] | 9639 | 11664 | 1484387 | 2017-05-21 12:59 | 2017-05-21 14:49 | 110 | 11kV | 203280 | 1848 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.10 tripped and locked out on: B & C phase overcurrent Party balloon in 11kV at 19 New Illawarra Rd Bexley See 1484381 | May | 2017 | 2017Q4 | 2017 | ZN10999:PA10 | ZN10999:PA10 | ZN10999/000010 | BAYSIDE | OH | Veg | 2017-05-21 | N | 110 | N | 2 | N | N | 1.1101 | 39.4971 | 148551.0283
[7 empty] | 9290 | 7369 | 1484378 | 2017-05-21 12:35 | 2017-05-21 19:00 | 385 | 11kV | 177634 | 1124 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa9 "Wyoming South" fdr RE47607 Toomeys Rd tripped reclosed tripped and locked out on Earth Fault Cause: Tree/Branch brought down OH. At tee between AB41424 and AB44252 See 1486415,6,7 exclude 1484378,9,84,99 | May | 2017 | 2017Q4 | 2017 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2017-05-21 | N | 158.0374 | N | 2 | N | N | 1.1101 | 39.4971 | 129809.6879
[7 empty] | 10340 | 20159 | 1484432 | 2017-05-22 04:51 | 2017-05-22 06:20 | 89 | 11kV | 178 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172124 Single phase DOLF : 10 Amp Sub has had similar faults recently. Please check sub equipment. Excluded OMS 1484432. | May | 2017 | 2017Q4 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2017-05-22 | N | 89 | N | 2 | N | N | 1.1101 | 39.4971 | 130.0771
[7 empty] | 8976 | 3730 | 1484735 | 2017-05-22 10:00 | 2017-05-22 12:00 | 120 | 11kV | 240 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 172129 B Phase DOLF : 10 Amp HV dropper detached from OH mains. Caused DOLF to Blow. | May | 2017 | 2017Q4 | 2017 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2017-05-22 | N | 120 | N | 2 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 9887 | 14685 | 1484979 | 2017-05-24 05:55 | 2017-05-24 07:55 | 120 | 11kV | 1080 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 172154 Single phase DOLF : 10 Amp Excluded OMS 1484979 | May | 2017 | 2017Q4 | 2017 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2017-05-24 | N | 120 | N | 7 | N | N | 1.1101 | 39.4971 | 789.2321
[7 empty] | 9405 | 8824 | 1484983 | 2017-05-24 06:06 | 2017-05-24 08:15 | 129 | 11kV | 200637 | 2463 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 172153 1 Fault operation B & C Phase Overcurrent, Earth Fault BlownUGOH at pole JU-61270 Excluded OMS 1484983 | May | 2017 | 2017Q4 | 2017 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | Unknown | Unknown | 2017-05-24 | N | 81.4604 | N | 7 | N | N | 1.1101 | 39.4971 | 146619.6018
[7 empty] | 9692 | 12239 | 1484984 | 2017-05-24 05:55 | 2017-05-24 08:35 | 160 | 11kV | 480 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 172155 Single phase DOLF : 16 Amp Excluded OMS 1484984 | May | 2017 | 2017Q4 | 2017 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2017-05-24 | N | 160 | N | 7 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 8873 | 2443 | 1484962 | 2017-05-24 05:17 | 2017-05-24 09:20 | 243 | 11kV | 276956.25 | 1623 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 172156 Blown Lightning arrestor UGOH IV-64016 Earth Fault, Overcurrent Targets at 0517 A-C overcurrent. Targets at 0727 Earth Fault. | May | 2017 | 2017Q4 | 2017 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Not Veg | 2017-05-24 | N | 170.6446 | N | 7 | N | N | 1.1101 | 39.4971 | 202391.4587
[7 empty] | 9305 | 7500 | 1485193 | 2017-05-24 15:42 | 2017-05-24 17:42 | 119.9167 | 11kV | 81423.4167 | 679 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At LB3133 phase bond burnt off Section of Panel No.3 "Beaconsfield Hornsby etc" ex S1296 Milperra Remarks: bond off main line after tee to PT2164 | May | 2017 | 2017Q4 | 2017 | ZN2196:PA3 | ZN1287:PA19 | ZN01287/000019 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-05-24 | N | 119.9167 | N | 7 | N | N | 1.1101 | 39.4971 | 59501.8313
[7 empty] | 9347 | 8040 | 1485229 | 2017-05-24 17:08 | 2017-05-24 19:02 | 114 | 11kV | 126287 | 1115 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn15013 Terrey Hills panel 6 tripped on Signals: 11kV trip Relays: A and Cphase OC, A and Cphase IOC Field EFI's Nil Cause: Bond Burnt off CP24464 Anormrmal Swicthing: AB25104 Closed, Panel 4 Open @ Terrey Hills AB20850 Closed, Panel 2 @ terrey Hills Open CP25194 Closed, SW/A at S16464 Golf Club brookvale Open See OMS 1485397 1485229 1485230 1485231 1485229 | May | 2017 | 2017Q4 | 2017 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Not Veg | 2017-05-24 | N | 113.2619 | N | 7 | N | N | 1.1101 | 39.4971 | 92286.8148
[7 empty] | 9326 | 7826 | 1485123 | 2017-05-24 12:33 | 2017-05-25 01:00 | 747 | 11kV | 25698 | 224 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 172176 Sensitive Earth Fault Transformer in sub 71667 failed and replaced Blown arrestors at sub 71087 as well as sub 71507 Excluded OMS 1485123 | May | 2017 | 2017Q4 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-05-24 | N | 114.7232 | N | 7 | N | N | 1.1101 | 39.4971 | 18779.3404
[7 empty] | 9090 | 5266 | 1485382 | 2017-05-25 10:38 | 2017-05-25 15:25 | 287 | 11kV | 1435 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172185 B Phase DOLF : 16 Amp Excluded OMS 1485382 | May | 2017 | 2017Q4 | 2017 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2017-05-25 | N | 287 | N | 3 | N | N | 1.1101 | 39.4971 | 1048.6557
[7 empty] | 9857 | 14268 | 1485453 | 2017-05-25 14:12 | 2017-05-25 16:05 | 113.2833 | 11kV | 4644.6167 | 41 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S2061 Shakespeare St - No 2 11kV/415V Transformer HV fuse operated. Transformer failure. | May | 2017 | 2017Q4 | 2017 | ZN690:PA15 | ZN690:PA34 | ZN00690/000034 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-05-25 | N | 113.2833 | N | 3 | N | N | 1.1101 | 39.4971 | 3394.1489
[7 empty] | 9652 | 11793 | 1485547 | 2017-05-25 21:58 | 2017-05-26 00:45 | 167 | 11kV | 179648 | 1955 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Panel 10 "Wamberal" fdr has tripped reclosed tripped on: Signals: Relays: C phase IOC, EFI, EF check, Reclose Relay Remote: Enclosed LB61730 (SEF defective) EFI's: S14246 S18381 (Did not operate) S14467 S14241 S14122 S18080 Cause: UG Fault in HV UGOH to S14210 Sw/A See 1486604,5,6,7 exclude 1485547,8,51,2 | May | 2017 | 2017Q4 | 2017 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | UG | Not Veg | 2017-05-25 | N | 91.8916 | N | 3 | N | N | 1.1101 | 39.4971 | 131281.4597
[7 empty] | 9801 | 13649 | 1485559 | 2017-05-26 04:23 | 2017-05-26 07:20 | 177 | 11kV | 708 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | Y | LID 172190 DOLF : 10 Amp No fault found Excluded OMS 1485559 | May | 2017 | 2017Q4 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2017-05-26 | Y | 177 | N |  | N | Y | 1.1101 | 39.4971 | 517.3855
[7 empty] | 9794 | 13568 | 1485584 | 2017-05-26 08:18 | 2017-05-26 10:10 | 112 | 11kV | 124560 | 1218 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | No Weather Impact | Y | At S129 Hunters Hill Panel 38 tripped Cause: Cockatoo on surge arrestor @ PT1170 Huntleys Rd See OMS 1486338 1486340 1485584 | May | 2017 | 2017Q4 | 2017 | ZN129:PA38 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Not Veg | 2017-05-26 | Y | 102.266 | N |  | N | Y | 1.1101 | 39.4971 | 91024.7741
[7 empty] | 10240 | 18936 | 1486205 | 2017-05-26 12:25 | 2017-05-26 15:35 | 190 | 11kV | 190 | 1 | HV | Customer Installation Fault | Customer Installation | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | LID 172197 Emerg isolation required for contractor to make repairs to UGOH & metering point. | May | 2017 | 2017Q4 | 2017 |  |  |  | NEWCASTLE | Unknown | Unknown | 2017-05-26 | Y | 190 | N |  | N | Y | 1.1101 | 39.4971 | 138.8464
[7 empty] | 9996 | 15921 | 1485935 | 2017-05-26 21:36 | 2017-05-26 21:44 | 8 | 11kV | 4760 | 595 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Circuit Breaker | Unplanned | No Weather Impact | Y | Zn9700 Kirrawee - Pnl.11 tripped on: A & C phase IOC, EFI Field EFIs: S9518, S9325, S9242, S9448 Abnormal: S9544 (Sw/B) Closed with S9394 (Sw/A) open. Incorrect labelling: S9448 Princes Acacia feeder end boxed are incorrectly labelled. DOp had to isolate 11kV feeder from S9448 via S9340 tee to S9214 to S9394. He then applied the earth to Sw/B at @9448 which caused panel 11 to trip. | May | 2017 | 2017Q4 | 2017 | ZN9700:PA11 | ZN9700:PA11 | ZN09700/000011 | SUTHERLAND | Unknown | Unknown | 2017-05-26 | Y | 8 | N |  | N | Y | 1.1101 | 39.4971 | 3478.4676
[7 empty] | 10199 | 18535 | 1485880 | 2017-05-26 17:36 | 2017-05-27 01:10 | 454 | 11kV | 138924 | 306 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | Y | S4656 Caroline Everleigh 11kV/415V Transformer failed Failed to clear via trip bar, Subs to investigate. LV parallels are were in and also failed. See 1486233 LV // failures see: 1485897 1486235 | May | 2017 | 2017Q4 | 2017 | ZN384:PA22 | ZN384:PA22 | ZN00384/000022 | SYDNEY | UG | Not Veg | 2017-05-26 | Y | 454 | N |  | N | Y | 1.1101 | 39.4971 | 101521.5616
[7 empty] | 9915 | 14969 | 1485949 | 2017-05-27 05:43 | 2017-05-27 10:40 | 297 | 11kV | 3861 | 13 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172209 3 fault operations B & C phase Earth Fault MAINS ON GROUND AT POLE AK-88111. Excluded oms 1485950. | May | 2017 | 2017Q4 | 2017 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2017-05-27 | N | 297 | N | 3 | N | N | 1.1101 | 39.4971 | 2821.5049
[7 empty] | 9470 | 9667 | 1485867 | 2017-05-26 16:30 | 2017-05-27 11:05 | 1115 | 11kV | 1115 | 1 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | LID 172210 B & C Phase DOLF : 20 Amp BIRD FOUND AT POLE FR-71601. CUSTOMER REQUESTED APPOINTMENT FOR 29/05/2017. D/Operator in area 27/05/2017. Excluded OMS REPORT NO 1485867. | May | 2017 | 2017Q4 | 2017 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2017-05-26 | Y | 1115 | N |  | N | Y | 1.1101 | 39.4971 | 814.8091
[7 empty] | 9485 | 9838 | 1486057 | 2017-05-27 20:53 | 2017-05-27 22:16 | 83 | 11kV | 35856 | 432 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa37L "Avoca Beach" fdr LK41334 Roadside bond burnt off See 1486613 ex 1486057,9,61,3,5,7 | May | 2017 | 2017Q4 | 2017 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2017-05-27 | N | 83 | N | 3 | N | N | 1.1101 | 39.4971 | 26202.5072
[7 empty] | 9540 | 10469 | 1486070 | 2017-05-27 23:54 | 2017-05-28 00:35 | 41 | 11kV | 20213 | 493 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172213 3 fault operations B & C phase Overcurrent B phase = 2980A, C phase = 3012A. Removed possum from 11kV ohm at pole IV-20918 Macquarie Dr. | May | 2017 | 2017Q4 | 2017 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Not Veg | 2017-05-27 | N | 41 | N | 3 | N | N | 1.1101 | 39.4971 | 14771.0642
[7 empty] | 9212 | 6656 | 1486157 | 2017-05-28 18:50 | 2017-05-28 21:00 | 130 | 11kV | 130 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 172216 A Phase LLC arcing. excluded OMS 1486157 | May | 2017 | 2017Q4 | 2017 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2017-05-28 | N | 130 | N | 2 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 10309 | 19653 | 1486180 | 2017-05-28 20:23 | 2017-05-28 21:20 | 57 | 11kV | 37335 | 655 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa33 "McMasters Beach" fdr IR50407 The Scenic Bounty tripped, reclosed, tripped & locked out on overcurrent brnach removed by DOp near LB64811 | May | 2017 | 2017Q4 | 2017 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2017-05-28 | N | 57 | N | 2 | N | N | 1.1101 | 39.4971 | 27283.3168
[7 empty] | 10157 | 17851 | 1486465 | 2017-05-30 03:07 | 2017-05-30 12:05 | 538 | 11kV | 7435 | 78 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of Pa24L "Berkeley Rd" RE45117 Glenning Valley tripped reclosed and tripped Relays: OC IOC and lockout Cause: broken HV Crossarm near PT14319 | May | 2017 | 2017Q4 | 2017 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2017-05-30 | N | 95.3205 | N | 7 | N | N | 1.1101 | 39.4971 | 5433.2787
[7 empty] | 10003 | 16005 | 1486514 | 2017-05-30 09:14 | 2017-05-30 16:30 | 436 | 11kV | 2438 | 31 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Sub 2196 Milperra Panel No.13 "marigold Armour No.1" feeder opened on Timed earth fault, sealing contactor, fault check & EFI 11kv trip, Zone earth & No.3 Group Earth Remarks: UG cable damaged by contractor. UG cable fault from CP 1394 Marigold Mil to Sub 1763 Marigold Mil No.2 | May | 2017 | 2017Q4 | 2017 | ZN2196:PA13 | ZN2196:PA13 | ZN02196/000013 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-05-30 | N | 78.6452 | N | 7 | N | N | 1.1101 | 39.4971 | 1781.6185
[7 empty] | 9625 | 11526 | 1486703 | 2017-05-30 20:25 | 2017-05-30 20:30 | 5 | 11kV | 145 | 29 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 172242 No protection operations. B ph DOLF 15925 arcing horns burning. Sub off loaded to open DOLFS (ferroresonance). Excluded OMS 1486703. | May | 2017 | 2017Q4 | 2017 | 264:81236 | 264:81236 | ZN00264/081236 | PORT STEPHENS | OH | Not Veg | 2017-05-30 | N | 5 | N | 7 | N | N | 1.1101 | 39.4971 | 105.9617
[7 empty] | 10209 | 18654 | 1486632 | 2017-05-30 14:30 | 2017-05-30 20:40 | 370 | 11kV | 9894 | 90 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172243 1 fault operation Overcurrent Overhead Mains on ground near sub 8764 | May | 2017 | 2017Q4 | 2017 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2017-05-30 | N | 109.9333 | N | 7 | N | N | 1.1101 | 39.4971 | 7230.2434
[7 empty] | 9132 | 5768 | 1486694 | 2017-05-30 18:15 | 2017-05-30 22:15 | 240 | 11kV | 53410 | 225 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Section of 11kV Panel 13 @ Zn15006 Dee Why West Customers Experienced Low volts between LB64167 and LK24947 (Open and Defective) HV Bond Burnt off beyond LB64147 Abnormal Switching: LK 24947 Open and Defedctive and SW/A closed at S16618 DOp and lineworker isolated and repaired mains. See 1487023 1487021 1487018 NOTE:Distributor 1 @ PT15330 was in parallel with S6684 See OMS 1487018 1487021 1487023 | May | 2017 | 2017Q4 | 2017 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | OH | Not Veg | 2017-05-30 | N | 237.3778 | N | 7 | N | N | 1.1101 | 39.4971 | 39030.4527
[7 empty] | 9451 | 9398 | 1486728 | 2017-05-30 23:48 | 2017-05-31 00:35 | 47 | 11kV | 4935 | 105 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 172246 A Phase DOLF : 40 Amp Fuse carrier burnt. Excluded OMS 1486728. | May | 2017 | 2017Q4 | 2017 | 222:33597 | 222:33597 | ZN00222/033597 | LAKE MACQUARIE | OH | Not Veg | 2017-05-30 | N | 47 | N | 7 | N | N | 1.1101 | 39.4971 | 3606.3524
[7 empty] | 10341 | 20160 | 1486726 | 2017-05-30 23:17 | 2017-05-31 02:35 | 198 | 11kV | 396 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172247 C Phase DOLF : 10 Amp T/R on Fdr see report 172245/ OMS 1486770 Excluded OMS 1486726. | May | 2017 | 2017Q4 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2017-05-30 | N | 198 | N | 7 | N | N | 1.1101 | 39.4971 | 289.3851
[7 empty] | 10059 | 16668 | 1486812 | 2017-05-31 10:11 | 2017-05-31 10:51 | 40 | 11kV | 27240 | 681 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa22 "Davies Wilma" tripped, reclosed, tripped and locked out Cause: Tree/Branch on OH mains near AB44423 | May | 2017 | 2017Q4 | 2017 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2017-05-31 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 19906.1886
[7 empty] | 9004 | 3996 | 1486829 | 2017-05-31 10:44 | 2017-05-31 11:25 | 41 | 11kV | 61623 | 1503 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12600 Lisarow Pa9 "Wyoming South" triiped reclosed tripped on Relays: C Phase OC Signals: 11kv trip Cause: Tree Branch on OH mains near AB45045 | May | 2017 | 2017Q4 | 2017 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2017-05-31 | N | 41 | N | 4 | N | N | 1.1101 | 39.4971 | 45032.2708
[7 empty] | 10096 | 17205 | 1486882 | 2017-05-31 12:37 | 2017-05-31 18:30 | 353 | 11kV | 706 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 172262 Single phase DOLF : 10 Amp Replaced transformer Excluded OMS 1486882 | May | 2017 | 2017Q4 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2017-05-31 | N | 353 | N | 4 | N | N | 1.1101 | 39.4971 | 515.924
[7 empty] | 9199 | 6465 | 1486986 | 2017-05-31 19:19 | 2017-05-31 20:45 | 86 | 11kV | 14624 | 172 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12580 Erina Pa7 "Nth Gosford" tripped Relays: Earth Fault 'A' Phase instantaneous, EFI Signals: 11kv trip EFI's: Nil Cause: UG fault, Frontline Feeder Fault See 1487417,8 exclude 1486986 | May | 2017 | 2017Q4 | 2017 | ZN12580:PA7 | ZN12580:PA7 | ZN12580/000007 | CENTRAL COAST | UG | Not Veg | 2017-05-31 | N | 85.0233 | N | 4 | N | N | 1.1101 | 39.4971 | 10686.7879
[7 empty] | 9030 | 4396 | 1486999 | 2017-06-01 00:08 | 2017-06-01 03:25 | 197 | 11kV | 45676 | 506 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 172265 Broken link 40677. Section 40597/64789 interrupted/isolated at 0145hrs for repairs. Emerg SI R0045. Excluded OMS 1486999 | June | 2017 | 2017Q4 | 2017 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2017-06-01 | N | 90.2688 | N | 2 | N | N | 1.1101 | 39.4971 | 33378.6736
[7 empty] | 9379 | 8544 | 1487160 | 2017-06-01 14:29 | 2017-06-01 15:20 | 51 | 11kV | 102 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172275 C Phase DOLF : 10 Amp Volts 241/241/242 Excluded OMS 1487160. | June | 2017 | 2017Q4 | 2017 | 235:2857 | 235:2857 | ZN00235/002857 | MAITLAND | OH | Veg | 2017-06-01 | N | 51 | N | 2 | N | N | 1.1101 | 39.4971 | 74.5386
[7 empty] | 9711 | 12401 | 1487250 | 2017-06-02 06:45 | 2017-06-02 08:30 | 105 | 11kV | 315 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172278 B Phase DOLF : 10 Amp Excluded OMS 1487250 | June | 2017 | 2017Q4 | 2017 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2017-06-02 | N | 105 | N | 3 | N | N | 1.1101 | 39.4971 | 230.1927
[7 empty] | 10235 | 18899 | 1487337 | 2017-06-02 11:45 | 2017-06-02 13:15 | 90 | 11kV | 1620 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172285 Isolated to repair stranded conductor | June | 2017 | 2017Q4 | 2017 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2017-06-02 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 1183.8482
[7 empty] | 8734 | 218 | 1487435 | 2017-06-02 18:34 | 2017-06-02 20:30 | 116 | 11kV | 464 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172288 B Phase DOLF : 10 Amp Excluded OMS 1487435 | June | 2017 | 2017Q4 | 2017 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2017-06-02 | N | 116 | N | 3 | N | N | 1.1101 | 39.4971 | 339.0775
[7 empty] | 10102 | 17267 | 1487687 | 2017-06-04 16:29 | 2017-06-04 19:00 | 151 | 11kV | 99135 | 1299 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | ZN.1193 Lindfield 11KV Panel#12 labelled ""S.7228 Wolseley Pacific"" tripped , re-closed , tripped & locked-out : RELAYS O/C +E/F Relay - 50TVC (IOC) , 150TN (EFI) , EFI - FC/UF REC lock-out relay SIGNALS Tx.2 ""B"" Prot. Group earth , CB.12 closed , CB.12 open , CB.12 auto-reclose lock-out 11KV trip , group earth FIELD EFI's S.7228" Fault 1 - 11kV Roadside + Footpath side HDOS @ PT1916 Have caught on fire Fault 2 - 11kV UGOH fault from S7228 to LB1363 See OMS 1487743 1487744 1487687 1487689 1487688 | June | 2017 | 2017Q4 | 2017 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | Unknown | Unknown | 2017-06-04 | N | 76.3164 | N | 2 | N | N | 1.1101 | 39.4971 | 72444.934
[7 empty] | 9689 | 12224 | 1487716 | 2017-06-04 20:18 | 2017-06-04 21:45 | 87 | 11kV | 100170 | 1160 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 11 tripped on Relays: TX1 UV, A phase IOC, A and B phase timed, Lockout, Timing and EFI Signals: TX2 Group earth, Zone Earth, 11kV Trip, CB 11 Open + Close + POpen 11kV feeder front line fault. See OMS 1487822 1487716 | June | 2017 | 2017Q4 | 2017 | ZN965:PA11 | ZN965:PA17 | ZN00965/000017 | HORNSBY | UG | Not Veg | 2017-06-04 | N | 86.3534 | N | 2 | N | N | 1.1101 | 39.4971 | 73201.2815
[7 empty] | 8797 | 1475 | 1487843 | 2017-06-05 11:34 | 2017-06-05 13:55 | 141 | 11kV | 141 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172305 Single phase DOLF : 10 Amp Dead bird at sub Excluded OMS 1487843 | June | 2017 | 2017Q4 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2017-06-05 | N | 141 | N | 2 | N | N | 1.1101 | 39.4971 | 103.0386
[7 empty] | 9623 | 11503 | 1487770 | 2017-06-05 09:17 | 2017-06-05 22:45 | 808 | 11kV | 7272 | 9 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of Pa17 PT11371 Pacific Ashbrooke 0.7 Neutral & Earthin Cable has been removed & or damaged Neutral disconnected. | June | 2017 | 2017Q4 | 2017 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | UG | Not Veg | 2017-06-05 | N | 808 | N | 2 | N | N | 1.1101 | 39.4971 | 5314.1631
[7 empty] | 10179 | 18174 | 1488240 | 2017-06-06 22:59 | 2017-06-07 00:34 | 95 | 11kV | 81071 | 1265 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Zn15005 Belrose Pa6 "Davidson Park" tripped and reclosed on EF LED, ZE 11kv trip, Timing relay lockout, Frame L and Fault check, EFI EFI's S16965 Recloser 24831 opened and locked out on IOC overcurrent Cause: Not ascertained. DOp patrolled See 1488322,3 exclude 1488240 | June | 2017 | 2017Q4 | 2017 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | OH | Veg | 2017-06-06 | N | 64.0877 | N | 1 | N | N | 1.1101 | 39.4971 | 59244.2956
[7 empty] | 9345 | 8004 | 1488271 | 2017-06-07 06:25 | 2017-06-07 07:23 | 58 | 11kV | 4060 | 70 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN12570 Avoca section of PA 33 "McMasters Beach" IR44797 Bouddi tripped & locked out Relays: O/C trip, Lockout Signals: Avoca 66kV Batt "B" charger, 11kV CP44797 CB open Cause: Tree/Branch on OH mains. Adjacent to PT13951 Bombi Scenic 0.2 ABC TV | June | 2017 | 2017Q4 | 2017 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2017-06-07 | N | 58 | N | 7 | N | N | 1.1101 | 39.4971 | 2966.9283
[7 empty] | 9550 | 10631 | 1488265 | 2017-06-07 06:12 | 2017-06-07 08:30 | 138.45 | 11kV | 8168.55 | 59 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 172322 C Phase DOLF : 20 Amp C phase LA faulty made safe supply back on 0830hrs A & C phase LA need to be replaced asap | June | 2017 | 2017Q4 | 2017 | 225:13446 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | OH | Not Veg | 2017-06-07 | N | 138.45 | N | 7 | N | N | 1.1101 | 39.4971 | 5969.3354
[7 empty] | 9663 | 11908 | 1488365 | 2017-06-07 09:24 | 2017-06-07 11:06 | 102 | 11kV | 76052 | 857 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn12600 Lisarow Panel 13 "Brush Rd" tripped Relays: IOC B+C phase Signals: CB13 open, Cap. Bank Step 1 open, Cap. Bank Step 2 open 11kv CP42086 Volt Detect, Tx2 thermal, CB13 spring discharge, RTU Prot. trip NL, RTU Prot. Timer, RTU Prot. Trip latched EFI's: Cause: Tree Branch on OH Mains. Adjacent to PT11064 Brush Ourimbah 0.5 See 1488967,9 exclude 1488365 | June | 2017 | 2017Q4 | 2017 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2017-06-07 | N | 88.7421 | N | 7 | N | N | 1.1101 | 39.4971 | 55576.5584
[7 empty] | 10181 | 18203 | 1488462 | 2017-06-07 12:40 | 2017-06-07 14:00 | 80 | 11kV | 4480 | 56 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172323 C Phase DOLF : 31 Amp Inadequate maintenance C phase dolf blown 31.5a no cause found substation in poor condition needs maintenance supply back on 1400hrs CC1: 22-"Refer to SOp" | June | 2017 | 2017Q4 | 2017 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2017-06-07 | N | 80 | N | 7 | N | N | 1.1101 | 39.4971 | 3273.8519
[7 empty] | 10171 | 18041 | 1488480 | 2017-06-07 13:22 | 2017-06-07 14:36 | 74 | 11kV | 12504 | 172 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn12580 Erina 11kV panel 7 "North Gosford" tripped Relays: Earth Fault Signals: 11kv trip, Zone Earth No2 Group Earth, CB 7 open, 11kv gtrip RTU Prot. trip latched, RTU Prot. trip NL, RTU Prot. trip timer EFI's: Cause: UG Fault. Zn12580 Erina Pa7 to S18675 to LB61759 See 1488996,7 exclude 1488480 | June | 2017 | 2017Q4 | 2017 | ZN12580:PA7 | ZN12580:PA7 | ZN12580/000007 | CENTRAL COAST | UG | Not Veg | 2017-06-07 | N | 72.6977 | N | 7 | N | N | 1.1101 | 39.4971 | 9137.5544
[7 empty] | 9118 | 5586 | 1488655 | 2017-06-07 18:45 | 2017-06-07 22:45 | 240 | 11kV | 64920 | 935 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12650 West Gosford section of Panel 13 Recloser 62730 Manns Narara Creek opened on OC Cause: Tree/Branch brought down OH. Adjacent USL 44106 See 1488655,718 | June | 2017 | 2017Q4 | 2017 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2017-06-07 | N | 69.4332 | N | 7 | N | N | 1.1101 | 39.4971 | 47441.6212
[7 empty] | 9643 | 11710 | 1488714 | 2017-06-07 21:16 | 2017-06-07 23:40 | 144 | 11kV | 1008 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | PT13117 palmdale Pacific 1.8 Footpath HDO 16Amp Fuse Fatigue See 1489001 exdude 1488714 | June | 2017 | 2017Q4 | 2017 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2017-06-07 | N | 144 | N | 7 | N | N | 1.1101 | 39.4971 | 736.6167
[7 empty] | 10074 | 16839 | 1488740 | 2017-06-08 02:06 | 2017-06-08 06:06 | 240 | 11kV | 193658 | 808 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S8000 Macquarie Park panel 4 tripped and locked out on A and B phase timed OC, timing relay, Lockout, 11kV Trip Abnormal Switching: AB1277 Open, LB1276 Closed. Cause Not ascertained for outage See OMS 1491555 1491556 1488740 | June | 2017 | 2017Q4 | 2017 | ZN8000:PA4 | ZN129:PA64 | ZN00129/000064 | HUNTERS HILL | OH | Veg | 2017-06-08 | N | 239.6757 | N | 5 | N | N | 1.1101 | 39.4971 | 141519.5545
[7 empty] | 9297 | 7421 | 1488835 | 2017-06-08 09:00 | 2017-06-08 10:30 | 90 | 11kV | 270 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | Ex Zn12580 Erina section of PT11278 Pateman Entrance 11kv HDO fuse footpath phase replaced 50K Fuse fatigue See 1489202 exclude 1488835 | June | 2017 | 2017Q4 | 2017 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | OH | Not Veg | 2017-06-08 | N | 90 | N | 5 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 8776 | 1075 | 1488849 | 2017-06-08 09:29 | 2017-06-08 12:58 | 208.9667 | 11kV | 71290.4333 | 1157 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 172331 2 fault operations Faulty L/A at UGOH pole IV-61122 Excluded OMS 1488849 | June | 2017 | 2017Q4 | 2017 | 206:34432 | 206:34432 | ZN00206/034432 | LAKE MACQUARIE | OH | Not Veg | 2017-06-08 | N | 61.6166 | N | 5 | N | N | 1.1101 | 39.4971 | 52096.946
[7 empty] | 9562 | 10811 | 1489016 | 2017-06-08 15:50 | 2017-06-08 18:54 | 184 | 11kV | 184 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 172339 A Phase DOLF : 10 Amp Blown L/A. Excluded OMS 1489016 | June | 2017 | 2017Q4 | 2017 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2017-06-08 | N | 184 | N | 5 | N | N | 1.1101 | 39.4971 | 134.4618
[7 empty] | 8849 | 2025 | 1489128 | 2017-06-09 07:18 | 2017-06-09 09:25 | 126.8667 | 11kV | 253.7333 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 172343 Single phase RECONNECTED LIVE LINE LEAD. | June | 2017 | 2017Q4 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2017-06-09 | N | 126.8667 | N | 6 | N | N | 1.1101 | 39.4971 | 185.4208
[7 empty] | 9393 | 8723 | 1489050 | 2017-06-08 16:49 | 2017-06-09 14:47 | 1318 | 11kV | 70051 | 417 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge section of Pa3 "Mangrove Mtn" fdt tripped, reclosed, tripped & locked out on Relays: B phase overcurrent, EFI, Reclose Signals: 11kv trip Cause: not ascertained. Unable to patrol feeder from Pa 3 to LB61085 due to inaccessible locations at night and flooded creeks. linerworkers to patrol AM fr 9/6 See 1489946,8,9 exclude 1489050,91,2 | June | 2017 | 2017Q4 | 2017 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2017-06-08 | N | 167.988 | N | 5 | N | N | 1.1101 | 39.4971 | 51191.2046
[7 empty] | 10277 | 19294 | 1489342 | 2017-06-09 18:18 | 2017-06-09 20:15 | 117 | 11kV | 82052 | 730 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | LID 172352 5 fault operations A Phase Instantaneous Earth Fault, Instantaneous Overcurrent Excluded OMS 1489342 | June | 2017 | 2017Q4 | 2017 | 528:83024 | 528:83024 | ZN00528/083024 | MAITLAND | UG | Not Veg | 2017-06-09 | N | 112.4 | N | 6 | N | N | 1.1101 | 39.4971 | 59961.1815
[7 empty] | 8864 | 2291 | 1489340 | 2017-06-09 18:20 | 2017-06-09 20:45 | 145 | 11kV | 9135 | 63 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 172354 Section isolated to repair blown 33kV tapping at JV-50211 under AP. Excluded OMS 1489340. | June | 2017 | 2017Q4 | 2017 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2017-06-09 | N | 145 | N | 6 | N | N | 1.1101 | 39.4971 | 6675.5886
[7 empty] | 8950 | 3376 | 1489372 | 2017-06-09 21:22 | 2017-06-09 22:36 | 74 | 11kV | 82658 | 1117 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Ex Zn12610 Long Jetty section of pa11 "Lucinda Ave" At AB44025 burned off A phase bond See 1489953 exclude 1489372 | June | 2017 | 2017Q4 | 2017 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2017-06-09 | N | 74 | N | 6 | N | N | 1.1101 | 39.4971 | 60404.0284
[7 empty] | 9638 | 11655 | 1489393 | 2017-06-09 23:26 | 2017-06-10 00:34 | 68 | 11kV | 8364 | 123 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP21350 Booralie Kalgoa tripped Cause: Tree on OH mains See OMS 1490726 1489393 | June | 2017 | 2017Q4 | 2017 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2017-06-09 | N | 68 | N | 6 | N | N | 1.1101 | 39.4971 | 6112.1645
[7 empty] | 9355 | 8110 | 1489323 | 2017-06-09 10:47 | 2017-06-10 11:40 | 1493 | 11kV | 1493 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Light | N | LID 172351 A Phase DOLF : 10 Amp DOLF & LA found blown during Fdr Patrol. Sub isolated to make repairs. Txf found faulty. Excluded OMS 1489323. | June | 2017 | 2017Q4 | 2017 | 220:8691 | 220:8691 | ZN00220/008691 | LAKE MACQUARIE | OH | Not Veg | 2017-06-09 | N | 1493 | N | 6 | N | N | 1.1101 | 39.4971 | 1091.0404
[7 empty] | 9400 | 8792 | 1489400 | 2017-06-10 01:39 | 2017-06-10 19:15 | 1056 | 11kV | 523423 | 1489 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | At S80 Chatswood the 11kV panel 25 ""murray ralston"" feeder tripped, reclosed, tripped and locked out on: Relays-B & C phase IOC, A, B, C Phase OC, EFI, FC, L/O, Timing Signals-11kV trip, Zone Earth, Tx11 & Tx12 Group Earth Field EFIs-S3431, S36096, S65176, S64871, S64872, S61568, S65080, 66046, S64933, S63266 Faulty section was isolated and feeder tried back but tripped again due to burned off bond on: Relays-SEF Signals-Tx11 Group Earth, Zone Earth, 11kV trip Cause HV bond failed - section between S63266 and 5353 See OMS 1491013/022/024 1489402 1489401 1489400 | June | 2017 | 2017Q4 | 2017 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Not Veg | 2017-06-10 | N | 351.5265 | N | 2 | N | N | 1.1101 | 39.4971 | 382502.09
[7 empty] | 9919 | 14981 | 1489570 | 2017-06-10 20:56 | 2017-06-11 00:28 | 212 | 11kV | 117450 | 1219 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | At S129 Hunters Hill anel 38 tripped on Relays: A relay - A phase Earth fault, Cause: Lightning arrestor failed at PT1170 See OMS 1490993 1490996 1490998 1490999 1491000 1489570 | June | 2017 | 2017Q4 | 2017 | ZN129:PA38 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Not Veg | 2017-06-10 | N | 96.3495 | N | 2 | N | N | 1.1101 | 39.4971 | 85828.9958
[7 empty] | 9133 | 5793 | 1489583 | 2017-06-11 02:41 | 2017-06-11 04:16 | 95 | 11kV | 117420 | 1236 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | LID 172357 5 fault operations A Phase Overcurrent, Earth Fault Cable fault between Sw's 34151 & 17704. | June | 2017 | 2017Q4 | 2017 | 238:34151 | 238:34136 | ZN00238/034136 | MAITLAND | UG | Not Veg | 2017-06-11 | N | 95 | N | 1 | N | N | 1.1101 | 39.4971 | 85807.0727
[7 empty] | 9267 | 7172 | 1489814 | 2017-06-12 14:46 | 2017-06-12 18:47 | 241 | 11kV | 461216 | 1925 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn3672 Maroubra Pnl.44 tripped on: C phase timed O/C, E/F, EFI Cable end box Failure at S6038 which caused sub to burn to the ground. See 11kV outage on Matraville Zn Pnl.30 at the same time. See 1470478 1470479 | June | 2017 | 2017Q4 | 2017 | ZN3672:PA44 | ZN3672:PA44 | ZN03672/000044 | RANDWICK | UG | Not Veg | 2017-06-12 | N | 239.5927 | N | 3 | N | N | 1.1101 | 39.4971 | 337043.0492
[7 empty] | 10215 | 18718 | 1489847 | 2017-06-12 17:50 | 2017-06-12 19:06 | 76 | 11kV | 79368 | 1086 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn36800 Waverley - Pnl.46 tripped on: A , B & C phase O/C with EFI En box failure at S1738 Pine Lane No.1 See 1490281 1490282 | June | 2017 | 2017Q4 | 2017 | ZN36800:PA46 | ZN36800:PA46 | ZN36800/000046 | WAVERLEY | UG | Not Veg | 2017-06-12 | N | 73.0829 | N | 3 | N | N | 1.1101 | 39.4971 | 57999.7934
[7 empty] | 9985 | 15771 | 1489821 | 2017-06-12 14:35 | 2017-06-12 20:55 | 380 | 11kV | 340055 | 1307 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn1788 Matraville Pnl.30 tripped on: A Phase timed O/C, Earth Fault and EFI All EFIs down to S6038 (Whole panel) End box fault at S6038 causing sub to burn to the ground. See also 11kV feeder outage at Maroubra Zn Pnl.44 See 1490470 1490471 149073 1490474 1490475 SUB 6038 BURNT TO GROUND DIST #1 #2 #3 RESTORED UNFORTUNATELY 2 BLOCKS OFF #1 DISTRIBUTOR CANNOT BE SUPPLIED TONIGHT UNTIL FURTHER WORK BY JOINTERS AM TUESDAY | June | 2017 | 2017Q4 | 2017 | ZN1788:PA30 | ZN1788:PA44 | ZN01788/000044 | RANDWICK | UG | Not Veg | 2017-06-12 | N | 260.1798 | N | 3 | N | N | 1.1101 | 39.4971 | 248502.1641
[7 empty] | 10123 | 17510 | 1489971 | 2017-06-13 11:10 | 2017-06-13 11:48 | 38 | 11kV | 1938 | 51 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | ZS STS Secondary Equip | Unplanned | No Weather Impact | N | Zn630 Mascot Pnl.15 opened with no relay flags. Cause not ascertained. Staff working on adjacent protection panel. | June | 2017 | 2017Q4 | 2017 | ZN630:PA15 | ZN8100:PA34 | ZN08100/000034 | BAYSIDE | Exclude | Not Veg | 2017-06-13 | N | 38 | N | 3 | N | N | 1.1101 | 39.4971 | 1416.2332
[7 empty] | 9518 | 10224 | 1490024 | 2017-06-13 13:03 | 2017-06-13 13:47 | 44 | 11kV | 35900 | 997 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12580 Erina Pa16 "Barralond Rd" fdrr tripped and locked out Relays: 16R IOC reclosed and lockout relays Signals: 11kv trip Abnormal: LB42550 closed and AB44487 open LB44838 closed and AB42542 open Cause: Tree/Branch on OH mains. Tree branch on PT 14306 See 1490337 exclude 1490024,6,30 | June | 2017 | 2017Q4 | 2017 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2017-06-13 | N | 36.008 | N | 3 | N | N | 1.1101 | 39.4971 | 26234.6611
[7 empty] | 9502 | 9942 | 1489938 | 2017-06-13 09:37 | 2017-06-13 15:55 | 378 | 11kV | 17892 | 459 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172369 2 fault operations Intelliruptor, Overcurrent Forklift ran into 11kV OHM near sub 77011. Excluded OMS No. 1489940 + 1489938 | June | 2017 | 2017Q4 | 2017 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2017-06-13 | N | 38.9804 | N | 3 | N | N | 1.1101 | 39.4971 | 13074.9459
[7 empty] | 9765 | 13235 | 1490190 | 2017-06-14 08:03 | 2017-06-14 10:40 | 157 | 11kV | 69865 | 445 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Section of 11kV Panel 27 ex Zn35500 Top Ryde 11kV middle Phase burnt off at AB 3197 with Low Volts beyond | June | 2017 | 2017Q4 | 2017 | ZN35500:PA27 | ZN35500:PA27 | ZN35500/000027 | RYDE | OH | Not Veg | 2017-06-14 | N | 157 | N | 3 | N | N | 1.1101 | 39.4971 | 51055.2813
[7 empty] | 9349 | 8078 | 1490288 | 2017-06-14 11:59 | 2017-06-14 13:10 | 71 | 11kV | 71 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172375 C Phase DORF : 10 Amp Excluded OMS 1490288 | June | 2017 | 2017Q4 | 2017 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2017-06-14 | N | 71 | N | 3 | N | N | 1.1101 | 39.4971 | 51.8847
[7 empty] | 10112 | 17382 | 1490403 | 2017-06-14 18:26 | 2017-06-14 19:06 | 40 | 11kV | 95440 | 2903 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty section of Pa6 "Rhodin Dr" Abnormal: DMA AB40909 with AB40824 closed Cause: 11kV roadside bond at LK41006. section of 11kv fdr from Zn12610 Long Jetty Pa6 to LK41587 to LB41089 tee PT13922 Mayfair Bloomfield via LK41006 See 1490515,8,9 exclude 1490403,7 | June | 2017 | 2017Q4 | 2017 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Not Veg | 2017-06-14 | N | 32.8763 | N | 3 | N | N | 1.1101 | 39.4971 | 69744.737
[7 empty] | 10307 | 19644 | 1490445 | 2017-06-15 05:59 | 2017-06-15 15:00 | 541 | 11kV | 5194 | 409 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong Pa2 "Wyong" RE40082 Jilliby tripped and reclosed on Overcurrent Cause: Tree Branch on OH mains. DOp Patrolling feeder. Car hit PT11367 Pole. Linesman given details See 1490843,5,6 exclude 1490449,52 | June | 2017 | 2017Q4 | 2017 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2017-06-15 | N | 12.6993 | N | 2 | N | N | 1.1101 | 39.4971 | 3795.622
[7 empty] | 10266 | 19170 | 1490773 | 2017-06-15 22:41 | 2017-06-15 23:50 | 69 | 11kV | 109855 | 1606 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | zn10991 Blakehurst - Pnl.7 tripped on: A Phase timed Overcurrent with EFI UG cabel fault from S10155 (Sw/B) to S10599 (Sw/A) See 1490844 1490847 | June | 2017 | 2017Q4 | 2017 | ZN10991:PA7 | ZN10991:PA7 | ZN10991/000007 | GEORGES RIVER | UG | Not Veg | 2017-06-15 | N | 68.4029 | N | 2 | N | N | 1.1101 | 39.4971 | 80278.7938
[7 empty] | 9745 | 12966 | 1491137 | 2017-06-17 00:40 | 2017-06-17 01:40 | 60 | 11kV | 16440 | 274 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172400 2 fault operation 3 phase Overcurrent, Earth Fault No cause found Excluded OMS 1491138 | June | 2017 | 2017Q4 | 2017 | 813:89059 | 813:89059 | ZN00813/089059 | UPPER HUNTER | OH | Veg | 2017-06-17 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 12013.8671
[7 empty] | 9403 | 8816 | 1491144 | 2017-06-17 06:21 | 2017-06-17 08:25 | 124 | 11kV | 60692 | 702 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Pa9 "Advance Crowe" tripped on Relays: SEF, fault check Signals: Tx1 Group Earth and EFI EFI's: Pa9 to S14638 Cause: Local Transformer failure at S14724 Derby Ascot See 1491765,6 exclude 1491141,4 | June | 2017 | 2017Q4 | 2017 | ZN14892:PA9 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | UG | Not Veg | 2017-06-17 | N | 86.4558 | N | 4 | N | N | 1.1101 | 39.4971 | 44351.9235
[7 empty] | 8787 | 1329 | 1491167 | 2017-06-17 09:18 | 2017-06-17 12:45 | 207 | 11kV | 207 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 172402 A Phase faulty LL Clamp replaced Excluded oms 1491167 | June | 2017 | 2017Q4 | 2017 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2017-06-17 | N | 207 | N | 4 | N | N | 1.1101 | 39.4971 | 151.2695
[7 empty] | 10289 | 19405 | 1491254 | 2017-06-17 18:32 | 2017-06-18 06:05 | 693 | 11kV | 14352 | 131 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172404 4 fault operations A & B phase Overcurrent; Earth Fault Pelican struck 11kV and brought mains down between poles JP-95006 and JP-95067. Excluded OMS 1491254 | June | 2017 | 2017Q4 | 2017 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2017-06-17 | N | 109.5573 | N | 4 | N | N | 1.1101 | 39.4971 | 10488.0183
[7 empty] | 8918 | 2912 | 1491287 | 2017-06-18 08:19 | 2017-06-18 10:10 | 111 | 11kV | 5772 | 52 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | LID 172409 section isolated to make repairs at UGOH SW-80140 see report # 172408/OMS 1491440 | June | 2017 | 2017Q4 | 2017 | 223:14398 | 223:14398 | ZN00223/014398 | LAKE MACQUARIE | OH | Not Veg | 2017-06-18 | N | 111 | N | 6 | N | N | 1.1101 | 39.4971 | 4218.0074
[7 empty] | 10046 | 16538 | 1491297 | 2017-06-18 09:21 | 2017-06-18 11:00 | 99 | 11kV | 99 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 172410 B Phase DOLF : 15 Amp possible fuse fatigue Excluded OMS 1491297 | June | 2017 | 2017Q4 | 2017 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2017-06-18 | N | 99 | N | 6 | N | N | 1.1101 | 39.4971 | 72.3463
[7 empty] | 8869 | 2389 | 1491281 | 2017-06-18 07:52 | 2017-06-18 15:21 | 449 | 11kV | 1347 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REPLACED HV FUSE no more information supplied, no control room report (LID) | June | 2017 | 2017Q4 | 2017 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2017-06-18 | N | 449 | N | 6 | N | N | 1.1101 | 39.4971 | 984.3479
[7 empty] | 10244 | 18980 | 1491386 | 2017-06-18 18:45 | 2017-06-18 20:24 | 99 | 11kV | 112674 | 1193 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12580 Erina Panel 1 "Green Point" tripped relays: lock out + timer, IOC A phase, EFI Signals: CB1 open, 11kv trip EFI's: S18318 Cause: UG Fault section of 11kV fdr from AB40380 to S18217/A to S12873/A See 1491787,91,3,4 exclude 1491386 | June | 2017 | 2017Q4 | 2017 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | UG | Not Veg | 2017-06-18 | N | 94.4459 | N | 6 | N | N | 1.1101 | 39.4971 | 82338.8359
[7 empty] | 10160 | 17903 | 1491378 | 2017-06-18 17:58 | 2017-06-18 20:30 | 152.0833 | 11kV | 456.25 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 172415 Single phase LLC off mains at sun 54130 | June | 2017 | 2017Q4 | 2017 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2017-06-18 | N | 152.0833 | N | 6 | N | N | 1.1101 | 39.4971 | 333.414
[7 empty] | 9551 | 10648 | 1491276 | 2017-06-18 06:08 | 2017-06-19 01:45 | 1177 | 11kV | 114499 | 2168 | HV | Equipment Failed in Service | Equipment Failure | U/G Link | Unplanned | No Weather Impact | N | LID 172406 3 fault operations A & B phase Overcurrent, Earth Fault faulty hazemeyer at sub 28927 generator connected at private service pillar Excluded oms 1491276 | June | 2017 | 2017Q4 | 2017 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | UG | Not Veg | 2017-06-18 | N | 52.8132 | N | 6 | N | N | 1.1101 | 39.4971 | 83672.4921
[7 empty] | 9103 | 5369 | 1491506 | 2017-06-19 10:21 | 2017-06-19 11:10 | 49 | 11kV | 4753 | 97 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 172426 A Phase DOLF : 40 Amp Blown Arrestor Excluded OMS 1491506 | June | 2017 | 2017Q4 | 2017 | 261:81886 | 261:81886 | ZN00261/081886 | NEWCASTLE | OH | Not Veg | 2017-06-19 | N | 49 | N | 1 | N | N | 1.1101 | 39.4971 | 3473.3522
[7 empty] | 8977 | 3737 | 1491703 | 2017-06-20 03:19 | 2017-06-20 04:52 | 93 | 11kV | 64623 | 805 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1648 Enfield 11kv feeder Panel No.19 "Wynnstay Ave" feeder tripped and lock out: Relays: time E/F, EFI Signals: 11kv trip, zone earth, No2 Grp Earth Field EFI's: S2014, S2431, S1926 Remarks: UG fault. UG faul in section of 11kv feeder from S1926 Daisy St (note: Compund Endbox) to S2692 Ardgryffee St (note: Haz) : Region to organise LV//s to enable cut-out extensions for A/Ps | June | 2017 | 2017Q4 | 2017 | ZN1648:PA19 | ZN4853:PA2 | ZN04853/000002 | BURWOOD | UG | Not Veg | 2017-06-20 | N | 80.277 | N | 2 | N | N | 1.1101 | 39.4971 | 47224.5823
[7 empty] | 9338 | 7921 | 1491716 | 2017-06-20 07:16 | 2017-06-20 12:00 | 284 | 11kV | 852 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 172440 Single phase DOLF : 10 Amp replace blown LA"s Excluded oms 1491716 & 1491723 | June | 2017 | 2017Q4 | 2017 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2017-06-20 | N | 284 | N | 2 | N | N | 1.1101 | 39.4971 | 622.6165
[7 empty] | 9057 | 4835 | 1491971 | 2017-06-21 04:42 | 2017-06-21 06:45 | 123 | 11kV | 29074 | 465 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1610 Homebush bay Zone Panel #3 'S.65269, CP.1818, etc" feeder has tripped on: Signals: 11kv trip, Tx1 Group earth Relays: earth fault, efi Field EFI's: Remarks: UG fault. 11kv UG feeder fault from CP.1818 Burroway Rd to S.65706 Burroway Hill Temp (Sw/B), tee. S.3893 Burroway Rd No.1 | June | 2017 | 2017Q4 | 2017 | ZN1610:PA3 | ZN1610:PA3 | ZN01610/000003 | PARRAMATTA | UG | Not Veg | 2017-06-21 | N | 62.5247 | N | 8 | N | N | 1.1101 | 39.4971 | 21246.4217
[7 empty] | 9395 | 8742 | 1491969 | 2017-06-21 03:24 | 2017-06-21 09:29 | 365.25 | 11kV | 16436.25 | 45 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172444 2 fault operations Overcurrent Branch on OHM at pole DV-43623 | June | 2017 | 2017Q4 | 2017 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-06-21 | N | 365.25 | N | 8 | N | N | 1.1101 | 39.4971 | 12011.1267
[7 empty] | 8908 | 2819 | 1492024 | 2017-06-21 10:49 | 2017-06-21 13:25 | 156 | 11kV | 624 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172447 LL lead off top of DOLF. Excluded OMS 1492024 | June | 2017 | 2017Q4 | 2017 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2017-06-21 | N | 156 | N | 8 | N | N | 1.1101 | 39.4971 | 456.0008
[7 empty] | 9174 | 6250 | 1492132 | 2017-06-21 16:41 | 2017-06-21 17:45 | 64 | 11kV | 2624 | 41 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa2 "Holgate" AB41933 found with 2 broken post insulators RE42120 Holgate interrupted for safety | June | 2017 | 2017Q4 | 2017 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2017-06-21 | N | 64 | N | 8 | N | N | 1.1101 | 39.4971 | 1917.5418
[7 empty] | 9565 | 10846 | 1492119 | 2017-06-21 15:59 | 2017-06-21 18:10 | 130.9167 | 11kV | 3534.75 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172450 A Phase DOLF : 20 Amp | June | 2017 | 2017Q4 | 2017 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2017-06-21 | N | 130.9167 | N | 8 | N | N | 1.1101 | 39.4971 | 2583.091
[7 empty] | 9069 | 5014 | 1492150 | 2017-06-21 18:00 | 2017-06-21 19:15 | 75 | 11kV | 9900 | 132 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172451 A Phase DOLF : 40 Amp Excluded OMS 1492150 CC1: 22-"Refer to SOp" | June | 2017 | 2017Q4 | 2017 | 243:80081 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | OH | Veg | 2017-06-21 | N | 75 | N | 8 | N | N | 1.1101 | 39.4971 | 7234.628
[7 empty] | 9936 | 15189 | 1492162 | 2017-06-21 19:16 | 2017-06-21 21:14 | 118 | 11kV | 61217 | 1691 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172452 2 fault operations 3 phase Overcurrent, Earth Fault possum on ELBS 43996 please arrange to have covers fitted as this is the second time a possum has gotten on this switch. 11kV links 8424 damaged from the passage of fault current. dq Excluded OMS 1492163 | June | 2017 | 2017Q4 | 2017 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | OH | Not Veg | 2017-06-21 | N | 36.2017 | N | 8 | N | N | 1.1101 | 39.4971 | 44735.578
[7 empty] | 9247 | 6971 | 1492179 | 2017-06-21 22:12 | 2017-06-22 03:40 | 328 | 11kV | 16400 | 50 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 172453 A Phase tapping burnt off pole 9L-40295 CC1: 22-"Refer to SOp" | June | 2017 | 2017Q4 | 2017 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2017-06-21 | N | 328 | N | 8 | N | N | 1.1101 | 39.4971 | 11984.6363
[7 empty] | 9412 | 8904 | 1492186 | 2017-06-22 06:21 | 2017-06-22 07:25 | 64 | 11kV | 576 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | PT15672 Tumbledown dick 11kV 31.5K centre phase HDO was found operated. cause not ascertained | June | 2017 | 2017Q4 | 2017 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2017-06-22 | N | 64 | N | 2 | N | N | 1.1101 | 39.4971 | 420.9238
[7 empty] | 9845 | 14120 | 1492404 | 2017-06-22 18:13 | 2017-06-22 19:17 | 64 | 11kV | 14784 | 231 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | 11kV Feeder from S4248 PMG Darlinghurst to S3237 Pennys Lane (Sw/C) via S2199 (Sw/B) to S8599 (Sw/A) tripped on translay, I/T, EFI UG cable fault between S4248 to S2199 (Sw/A) to S8599 (Sw/A) Supply was interruped to S2199 McElhorne Ham See 1492524 | June | 2017 | 2017Q4 | 2017 | ZN931:PA11 | ZN931:PA11 | ZN00931/000011 | SYDNEY | UG | Not Veg | 2017-06-22 | N | 64 | N | 2 | N | N | 1.1101 | 39.4971 | 10803.7111
[7 empty] | 9636 | 11645 | 1492669 | 2017-06-23 22:43 | 2017-06-24 01:45 | 182 | 11kV | 215430 | 1504 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.19 tripped on: B & C phase IOC, with EFI Abnormal: LB48122 Open with Sw/A @ S10283 Closed due to Defective mains. Inital cause unable to be located. Suspect through fault current cause open circuit of 11kV bond on Roberts Rd. See 1493314 1493315 | June | 2017 | 2017Q4 | 2017 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2017-06-23 | N | 143.238 | N | 1 | N | N | 1.1101 | 39.4971 | 157429.8899
[7 empty] | 8911 | 2844 | 1492685 | 2017-06-24 06:46 | 2017-06-24 07:46 | 60 | 11kV | 44184 | 974 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn167 Auburn - Pnl.21 tripped on: Earth Fault with EFI UG cable fault from Pnl.21 to S6868 (Sw/A) to S7148 (Sw/A) - Front line section. See 1493220 1493221 | June | 2017 | 2017Q4 | 2017 | ZN167:PA21 | ZN167:PA21 | ZN00167/000021 | CUMBERLAND | UG | Not Veg | 2017-06-24 | N | 45.3634 | N | 1 | N | N | 1.1101 | 39.4971 | 32288.364
[7 empty] | 9871 | 14440 | 1492834 | 2017-06-25 11:13 | 2017-06-25 11:50 | 37 | 11kV | 148 | 4 | HV | 3rd Party Vehicle | 3rd Party Impact | Bond | Unplanned | No Weather Impact | N | LID 172470 B Phase MVA pole JQ-60008 Newline Rd. SOp Advised by Essential Energy 0831hrs. EE took initial call & EE staff initial response. MVA approx 0600hrs, no Sw operation. Section isolated to repair broken ties, Emerg SI R0051. | June | 2017 | 2017Q4 | 2017 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2017-06-25 | N | 37 | N | 2 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 9228 | 6806 | 1492916 | 2017-06-25 23:42 | 2017-06-26 00:17 | 35 | 11kV | 29750 | 850 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca Pa34 "terrigal" fdr tripped, reclsoed, tripped & locked out on Relays: B & C phase overucrrent, lockout, EFI Signals: 11kv trip Cause: tree/branch on OH mains DOp removed branch from 11kV mains near PT12363 in francis st See 1492916,7 | June | 2017 | 2017Q4 | 2017 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2017-06-25 | N | 35 | N | 2 | N | N | 1.1101 | 39.4971 | 21740.4225
[7 empty] | 9777 | 13385 | 1493095 | 2017-06-26 14:27 | 2017-06-26 21:05 | 398 | 11kV | 369150 | 1710 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn72 Five Dock - Pnl.31 tripped on: B Phase Overcurrent with EFI UG cable fault from Pnl.31 to S1528 (Sw/A) to S46285 (Sw/A) - Front line section See 1493231 1493233 LV parallel Failures: 1493237 1493235 1493236 | June | 2017 | 2017Q4 | 2017 | ZN72:PA31 | ZN35555:PA20 | ZN35555/000020 | INNER WEST | UG | Not Veg | 2017-06-26 | N | 215.8772 | N | 1 | N | N | 1.1101 | 39.4971 | 269763.9319
[7 empty] | 9427 | 9162 | 1493352 | 2017-06-27 16:39 | 2017-06-27 19:30 | 171 | 11kV | 684 | 4 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 172498 oms 1493352 reattach 1 LLC and retighten 2 LLC at sub | June | 2017 | 2017Q4 | 2017 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2017-06-27 | N | 171 | N | 2 | N | N | 1.1101 | 39.4971 | 499.847
[7 empty] | 9217 | 6712 | 1493397 | 2017-06-27 19:34 | 2017-06-27 20:25 | 51 | 11kV | 53805 | 1055 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12570 Avoca Panel 35 "Kincumber" tripped, reclosed and locked out Relays: E/F and EFI, reclosed and lock out Signals: 11kv trip Cause: UG Fault, 11kV underground feeder fault from Zn12570 Avoca to S48848 Avoca Melville SwA tee AB44670 N/O See 1493397 exclude 1493407 | June | 2017 | 2017Q4 | 2017 | ZN12570:PA35 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | UG | Not Veg | 2017-06-27 | N | 51 | N | 2 | N | N | 1.1101 | 39.4971 | 39319.107
[7 empty] | 10165 | 17953 | 1493412 | 2017-06-28 05:13 | 2017-06-28 07:50 | 157 | 11kV | 628 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172500 Single phase DOLF : 10 Amp Volts = 235. Amps = 65. Excluded OMS 1493412. | June | 2017 | 2017Q4 | 2017 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2017-06-28 | N | 157 | N | 2 | N | N | 1.1101 | 39.4971 | 458.9239
[7 empty] | 9571 | 10898 | 1493638 | 2017-06-28 19:26 | 2017-06-28 20:47 | 81 | 11kV | 70885 | 1068 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn847 Hornsby Panel 47 tripped reclosed tripped and locked out on Signals: 11kV Trip, Zone Earth, TX3 Group Earth Relays: O/C, Lockout, Reclose Timing, Fault Check Cause: Bond Burnt off and Created short at UGOH to S4843 1493955 1493638 1493640 | June | 2017 | 2017Q4 | 2017 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Not Veg | 2017-06-28 | N | 66.3717 | N | 2 | N | N | 1.1101 | 39.4971 | 51800.6672
[7 empty] | 9332 | 7851 | 1494076 | 2017-06-29 17:57 | 2017-06-29 18:01 | 4 | 11kV | 5936 | 1484 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At Zn9900 Menai Panel 13 tripped on SEL Signals; 11kV Trip, Battery defect, Clc Defect, No1 and No2 TX No volt5s Abnormal Switching: Pa2 OOS At Zn9900, S9066 SW A Open, SW/B Closed @ S9108 Cause: At the time of trip. DOp was closing SW/A 9166 to Open Panel 2 @ Zn9900 Feeder Tripped on Circulating current | June | 2017 | 2017Q4 | 2017 | ZN9900:PA13 | ZN9900:PA13 | ZN09900/000013 | SUTHERLAND | Unknown | Unknown | 2017-06-29 | N | 4 | N | 5 | N | N | 1.1101 | 39.4971 | 4337.8537
[7 empty] | 10111 | 17368 | 1493899 | 2017-06-29 18:29 | 2017-06-29 20:10 | 101 | 11kV | 63717.1833 | 635 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | CP3048 (Ex Zn35500 Top Ryde Pa28L) 11kV Bond Burnt Off Signals: Nil Cause: 11kV Centre phase bond burnt off at AB3048 See OMS 1493899 1493968 1493900 1493901 1493908 1493931 | June | 2017 | 2017Q4 | 2017 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2017-06-29 | N | 100.342 | N | 5 | N | N | 1.1101 | 39.4971 | 46562.6382
[7 empty] | 8791 | 1340 | 1493913 | 2017-06-29 19:07 | 2017-06-29 21:35 | 148 | 11kV | 89309 | 1154 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn340 Botany Zn - Pnl.20 tripped on: IOC (No Phase indication), EFI UG Cable fault from Pnl.20 to S49251 (Sw/A) to S65342 (Sw/A) - Front line section See 1493969 1493974 1493975 | June | 2017 | 2017Q4 | 2017 | ZN340:PA20 | ZN340:PA44 | ZN00340/000044 | BAYSIDE | UG | Not Veg | 2017-06-29 | N | 77.3908 | N | 5 | N | N | 1.1101 | 39.4971 | 65264.383
[7 empty] | 8992 | 3904 | 1493902 | 2017-06-29 18:35 | 2017-06-29 22:35 | 240 | 11kV | 816 | 50 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 172518 replaced LV transformer leads Excluded oms1493887,1493902 | June | 2017 | 2017Q4 | 2017 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2017-06-29 | N | 16.32 | N | 5 | N | N | 1.1101 | 39.4971 | 596.3087
[7 empty] | 9222 | 6752 | 1493807 | 2017-06-29 18:53 | 2017-06-29 23:20 | 267 | 11kV | 801 | 3 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172519 3 phase MVA hit pole OR-90571, section 63949/7156 isolated to repair. No Sw operation. Excluded OMS 1493807 | June | 2017 | 2017Q4 | 2017 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2017-06-29 | N | 267 | N | 5 | N | N | 1.1101 | 39.4971 | 585.3472
[7 empty] | 9673 | 12065 | 1494090 | 2017-06-30 15:27 | 2017-06-30 17:40 | 133 | 11kV | 137254 | 1264 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn847 Hornsby Panbel 46 tripped, reclosed tripped and locked out on Signals: 11kV trip, Protectionn UV, Hight Low Volts Relays: C phase IOC, C phase OC, Lockout and Timing Abnormal Switching: AB459 Open and Defective CP2275 Closed OH Patrolled, No cause found See OMS 1494839 1494840 1494841 1494090 | June | 2017 | 2017Q4 | 2017 | ZN847:PA46 | ZN847:PA46 | ZN00847/000046 | HORNSBY | OH | Veg | 2017-06-30 | N | 108.587 | N | 3 | N | N | 1.1101 | 39.4971 | 100301.1749
[7 empty] | 9088 | 5257 | 1494137 | 2017-06-30 18:57 | 2017-06-30 20:16 | 79 | 11kV | 7821 | 99 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 172535 B Phase DOLF : 31 Amp Blown Bph DOLF & burnt up carrier. Replaced 3ph DOLFs & carriers. Reported by customer and Fire and Rescue NSW that D/W's / Tx on pole was on fire, Fire brigade put fire out Excluded OMS 1494137 | June | 2017 | 2017Q4 | 2017 | 221:11894 | 221:11894 | ZN00221/011894 | LAKE MACQUARIE | OH | Not Veg | 2017-06-30 | N | 79 | N | 3 | N | N | 1.1101 | 39.4971 | 5715.3561
[7 empty] | 9596 | 11206 | 1494114 | 2017-06-30 16:56 | 2017-06-30 20:24 | 208.0333 | 11kV | 10401.6667 | 50 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 172534 cow rubbing on stay wire has caused 11kv tapping to burn off, second time this has happened | June | 2017 | 2017Q4 | 2017 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2017-06-30 | N | 208.0333 | N | 3 | N | N | 1.1101 | 39.4971 | 7601.2312
[7 empty] | 8167 | 13342 | 1494177 | 2017-07-01 07:50 | 2017-07-01 11:25 | 215.35 | 11kV | 3230.25 | 15 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 172538 A Phase DOLF : 20 Amp hv fuse carrier repaired live line | July | 2017 | 2018Q1 | 2018 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2017-07-01 | N | 215.35 | N | 4 | N | N | 1.1101 | 39.4971 | 2360.5714
[7 empty] | 7833 | 9117 | 1494191 | 2017-07-01 08:36 | 2017-07-01 13:45 | 309 | 11kV | 618 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172539 SUB ISOLATED TO REPAIR DAMAGED LV LEADS Excluded OMS 1494191 | July | 2017 | 2018Q1 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-07-01 | N | 309 | N | 4 | N | N | 1.1101 | 39.4971 | 451.6162
[7 empty] | 8059 | 11916 | 1494257 | 2017-07-01 13:48 | 2017-07-01 14:40 | 52 | 11kV | 520 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172540 B Phase DOLF : 31 Amp Excluded OMS 1494257 | July | 2017 | 2018Q1 | 2018 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2017-07-01 | N | 52 | N | 4 | N | N | 1.1101 | 39.4971 | 380.0007
[7 empty] | 8248 | 14398 | 1494232 | 2017-07-01 12:30 | 2017-07-01 21:50 | 560 | 11kV | 20613 | 251 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mtn" fdr 11kv OH from LB46215 to LK42797 tee PT13151 Niclins Wise Ferry 1.4 is isiolated see 1494912,20,2 exclude 1494232,52,3,5 | July | 2017 | 2018Q1 | 2018 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2017-07-01 | N | 82.1235 | N | 4 | N | N | 1.1101 | 39.4971 | 15063.3724
[7 empty] | 8263 | 14516 | 1494399 | 2017-07-02 16:40 | 2017-07-02 18:55 | 135 | 11kV | 24570 | 182 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172544 No protection operation, section isolated to remove tree from 11kV OH CCT. Excluded OMS 1494410 | July | 2017 | 2018Q1 | 2018 | 233:82815 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Veg | 2017-07-02 | N | 135 | N | 1 | N | N | 1.1101 | 39.4971 | 17955.0313
[7 empty] | 7663 | 6940 | 1494930 | 2017-07-04 12:23 | 2017-07-04 14:40 | 137 | 11kV | 2740 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa40 PT14619 Davistown Coomal Roadside Phase 31.5 HDO operated Cause not ascertained See 1495745 ex 1494930 | July | 2017 | 2018Q1 | 2018 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Veg | 2017-07-04 | N | 137 | N | 2 | N | N | 1.1101 | 39.4971 | 2002.3112
[7 empty] | 8512 | 17727 | 1494962 | 2017-07-04 13:11 | 2017-07-04 15:55 | 164 | 11kV | 328 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172565 A Phase LLC snapped off. Excluded OMS 1494962 | July | 2017 | 2018Q1 | 2018 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2017-07-04 | N | 164 | N | 2 | N | N | 1.1101 | 39.4971 | 239.6927
[7 empty] | 7446 | 4597 | 1495297 | 2017-07-05 13:08 | 2017-07-05 21:10 | 482 | 11kV | 964 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 172580 Faulty Transformer replaced - blown 3phase 63 kva / replaced / cause internal windings Note: Job Began time amended to first customer No Supply call also see previous event 1494191 | July | 2017 | 2018Q1 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-07-05 | N | 482 | N | 3 | N | N | 1.1101 | 39.4971 | 704.4628
[7 empty] | 7724 | 7723 | 1495439 | 2017-07-05 20:27 | 2017-07-05 21:55 | 88 | 11kV | 115624 | 1441 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9118 Cronulla Pa22 "Franklin King" fdr tripped, reclosedm tripped and locked out Relays: A phase IOC, A & C phase ovedrcurrent, EFI, lock out, reclose timer Signals: 11kV trip, Zone Earth, Tx1 Group Earth EFi's: S9786 S9787 11kv UGoh defective after possum caused flashover in between section of feeder from S76761 to S46317 See 1495763,4 ex 145439,41,2 | July | 2017 | 2018Q1 | 2018 | ZN9118:PA22 | ZN9118:PA22 | ZN09118/000022 | SUTHERLAND | OH | Not Veg | 2017-07-05 | N | 80.2387 | N | 3 | N | N | 1.1101 | 39.4971 | 84494.6089
[7 empty] | 7591 | 6188 | 1495412 | 2017-07-05 18:25 | 2017-07-05 23:35 | 310 | 11kV | 14760 | 145 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 172581 1 fault operation B Phase Overcurrent Burnt off tapping pole GR-62010 towards ABS 9101. Excluded OMS 1495412, 1495458 | July | 2017 | 2018Q1 | 2018 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2017-07-05 | N | 101.7931 | N | 3 | N | N | 1.1101 | 39.4971 | 10786.1727
[7 empty] | 8321 | 15186 | 1495564 | 2017-07-06 10:57 | 2017-07-06 13:02 | 125 | 11kV | 10335 | 84 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn35400 North Sydney - Pnl.67 tripped on: A & B phase Earth Fault with EFI Excavator dug into HV cables in Napier St, North Sydney See 1495854 1495855 | July | 2017 | 2018Q1 | 2018 | ZN35400:PA67 | ZN35400:PA67 | ZN35400/000067 | NORTH SYDNEY | UG | Not Veg | 2017-07-06 | N | 123.0357 | N | 1 | N | N | 1.1101 | 39.4971 | 7552.5132
[7 empty] | 8623 | 19145 | 1495802 | 2017-07-07 00:22 | 2017-07-07 01:41 | 79 | 11kV | 42014 | 656 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn384 Camperdown - Pnl.81 tripped on: Earth Fault with EFI Field EFIs: All down to S2389 UG cabel fault between S2389 McMasters Lan (Sw/B) to S824 Sydney University (Sw/A) See 1495847 1495848 | July | 2017 | 2018Q1 | 2018 | ZN384:PA81 | ZN384:PA81 | ZN00384/000081 | SYDNEY | UG | Not Veg | 2017-07-07 | N | 64.0457 | N | 5 | N | N | 1.1101 | 39.4971 | 30702.592
[7 empty] | 8182 | 13509 | 1495804 | 2017-07-07 07:13 | 2017-07-07 08:25 | 72 | 11kV | 2304 | 32 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172600 B Phase DOLF : 16 Amp Excluded OMS 1495804 | July | 2017 | 2018Q1 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-07-07 | N | 72 | N | 5 | N | N | 1.1101 | 39.4971 | 1683.6952
[7 empty] | 8690 | 19920 | 1495939 | 2017-07-07 15:19 | 2017-07-07 22:25 | 425.55 | 11kV | 2553.3 | 6 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172616 B & C phase DOLF : 20 Amp 2 x 11kV mains on ground, repairs completed. Excluded oms 1495939,1495944 | July | 2017 | 2018Q1 | 2018 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2017-07-07 | N | 425.55 | N | 5 | N | N | 1.1101 | 39.4971 | 1865.8763
[7 empty] | 8234 | 14247 | 1495989 | 2017-07-07 19:10 | 2017-07-07 22:40 | 210 | 11kV | 630 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | EX 14143 Somersby Panel 17 Tree leaning against CCT near LB40976 2 Centres Interrupted for safety (PT12803 PT11673) See OMS 1496604 1496605 1495989 1495990 1495994 1495996 | July | 2017 | 2018Q1 | 2018 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2017-07-07 | N | 210 | N | 5 | N | N | 1.1101 | 39.4971 | 460.3854
[7 empty] | 8646 | 19443 | 1496339 | 2017-07-08 | 2017-07-08 00:54 | 54 | 11kV | 1728 | 32 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172620 A Phase DOLF : 16 Amp Also see OMS 1496337 | July | 2017 | 2018Q1 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-07-08 | N | 54 | N | 2 | N | N | 1.1101 | 39.4971 | 1262.7714
[7 empty] | 8118 | 12795 | 1496017 | 2017-07-08 08:37 | 2017-07-08 09:10 | 33 | 11kV | 66 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 172621 Repair Live Line Clamp Excluded OMS 1496017 | July | 2017 | 2018Q1 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2017-07-08 | N | 33 | N | 2 | N | N | 1.1101 | 39.4971 | 48.2309
[7 empty] | 7504 | 5424 | 1495982 | 2017-07-07 18:24 | 2017-07-08 12:00 | 1056 | 11kV | 20063 | 63 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172617 4 fault operations Overcurrent, Earth Fault Faulty Transformer sub 54077 Excluded OMS 1495982 | July | 2017 | 2018Q1 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2017-07-07 | N | 318.4603 | N | 5 | N | N | 1.1101 | 39.4971 | 14661.4486
[7 empty] | 8081 | 12197 | 1496147 | 2017-07-09 01:34 | 2017-07-09 05:50 | 256 | 11kV | 216649 | 1629 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn847 Hornsby Panel 15 tripped on Relays: C phase O/C, EFI, Fault Check. Abnormal Switching: DMA - S4714 to S4715 to S4721 to LB 65270 Closed Cause: Fault in Section of 11kV Feeder from SW/A @ S4465 to SW/B @ S7920 tee PT2046 NOTE: Delayed Restoration due to abnormal above. Abnormal was fixed on 07/03/2017 See OMS 1496680 1496681 1496682 1496147 1496148 | July | 2017 | 2018Q1 | 2018 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | UG | Not Veg | 2017-07-09 | N | 132.9951 | N | 3 | N | N | 1.1101 | 39.4971 | 158320.6991
[7 empty] | 8063 | 11977 | 1496165 | 2017-07-09 08:09 | 2017-07-09 09:06 | 57 | 11kV | 3394 | 72 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn8000 Macquarie Park Pa 34 has tripped on Signals: 11kv trip, TX3 Group Earth, Zone Earth Relays: 34L Protetion, Earth fault and EFI Cause: 11kV UG feeder fault from S8090 to S7894 to S35319 See OMS 1496704 1496705 1496706 | July | 2017 | 2018Q1 | 2018 | ZN8000:PA34 | ZN8000:PA3 | ZN08000/000003 | RYDE | UG | Not Veg | 2017-07-09 | N | 47.1389 | N | 3 | N | N | 1.1101 | 39.4971 | 2480.2351
[7 empty] | 7901 | 9962 | 1496188 | 2017-07-09 10:24 | 2017-07-09 12:35 | 131 | 11kV | 3144 | 24 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Section of 11kV Feeder of 11kV Feeder off Panel 10 Entrance Feeder beyond USL CP42048 Bond Off @ Long Jetty Zone. 11kV Bond @ USL 42048. See OMS 1496601 1496188 1496208 1496210 149196 | July | 2017 | 2018Q1 | 2018 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Not Veg | 2017-07-09 | N | 131 | N | 3 | N | N | 1.1101 | 39.4971 | 2297.5425
[7 empty] | 7651 | 6820 | 1496276 | 2017-07-10 00:33 | 2017-07-10 01:35 | 62 | 11kV | 6608 | 142 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At Zn13000 Lake Munmorah - 11kv Feeder Panel 8 tripped and reclosed on Relays: B and C phase IOC. 11kV IR62487 Scenic Wills tripped and reclosed to lockout on OC Trip, SEF Trip Cause: MVA into pole BU761 - Damaged Cross Arm - Lowering of HV mains offf cross arm See OMS 1496622 1496624 1496276 | July | 2017 | 2018Q1 | 2018 | ZN13000:PA8 | ZN13000:PA8 | ZN13000/000008 | CENTRAL COAST | OH | Not Veg | 2017-07-10 | N | 46.5352 | N | 3 | N | N | 1.1101 | 39.4971 | 4828.9315
[7 empty] | 8010 | 11242 | 1496420 | 2017-07-10 15:35 | 2017-07-10 17:00 | 85 | 11kV | 850 | 10 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172629 A & B phase links 26925 opened to repair stranded conductors | July | 2017 | 2018Q1 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2017-07-10 | N | 85 | N | 3 | N | N | 1.1101 | 39.4971 | 621.1549
[7 empty] | 7779 | 8440 | 1496545 | 2017-07-10 20:06 | 2017-07-10 21:30 | 84 | 11kV | 18564 | 221 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 172631 4 fault operations Earth Fault, Overcurrent 11kV main on crossarm at pole GS-71225 Excluded OMS 1496545 | July | 2017 | 2018Q1 | 2018 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2017-07-10 | N | 84 | N | 3 | N | N | 1.1101 | 39.4971 | 13566.0237
[7 empty] | 7194 | 363 | 1496642 | 2017-07-11 11:23 | 2017-07-11 14:00 | 157 | 11kV | 1099 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172643 A Phase DOLF : 16 Amp | July | 2017 | 2018Q1 | 2018 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2017-07-11 | N | 157 | N | 2 | N | N | 1.1101 | 39.4971 | 803.1168
[7 empty] | 7739 | 7890 | 1496685 | 2017-07-11 12:45 | 2017-07-11 17:10 | 265 | 11kV | 7690 | 46 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 172641 interrupt to repair tapping at pole EM-20118 to sub 53277 martin sub Excluded OMS 1496685 | July | 2017 | 2018Q1 | 2018 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2017-07-11 | N | 167.1739 | N | 2 | N | N | 1.1101 | 39.4971 | 5619.6252
[7 empty] | 8212 | 13853 | 1496786 | 2017-07-12 02:43 | 2017-07-12 04:45 | 122 | 11kV | 183790 | 1580 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S2196 Milperra panel 5 tripped on Relays: SEL, Lockout Field EFI's Nil Signals: 11kV Trip Cause: AB2800 Roadside phase bond burnt off See OMS 1496924 1496925 1496928 | July | 2017 | 2018Q1 | 2018 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-07-12 | N | 116.3228 | N | 4 | N | N | 1.1101 | 39.4971 | 134308.3111
[7 empty] | 8233 | 14200 | 1496869 | 2017-07-12 09:50 | 2017-07-12 12:02 | 132 | 11kV | 163784 | 1241 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn4545 Meadowbank Panel 17 tripped reclosed tripped and locked out on Relays: B phase timed overcurrent, Earth fault, EFI, Timing Relay, Lockout No2 TX protection panel and fault check. Signals: Group Earth, Zone Earth, 11kV trip. Field EFI's @ S35438 and S64731. Note: PT1962 was in LV parallel with panel 17 at the time of interruption. 11kV UG feeder fault from S64731 Consititution Hamilton SW/B to S64730 Constiotution Belmore SW/A See OMS 1499766 1499768 1499769 1499771 1496869 1496880 1496891 | July | 2017 | 2018Q1 | 2018 | ZN4545:PA17 | ZN129:PA36 | ZN00129/000036 | RYDE | UG | Not Veg | 2017-07-12 | N | 131.9774 | N | 4 | N | N | 1.1101 | 39.4971 | 119688.5164
[7 empty] | 8441 | 16821 | 1496896 | 2017-07-12 11:06 | 2017-07-12 12:30 | 84 | 11kV | 1344 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 172654 A Phase DOLF : 40 Amp reading 60-70-140 amps Excluded oms 1496896 | July | 2017 | 2018Q1 | 2018 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | OH | Veg | 2017-07-12 | N | 84 | N | 4 | N | N | 1.1101 | 39.4971 | 982.1556
[7 empty] | 7554 | 5873 | 1497054 | 2017-07-12 19:38 | 2017-07-12 20:50 | 71.2667 | 11kV | 712.6667 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 172657 C Phase DOLF : 20 Amp fuse fatigue | July | 2017 | 2018Q1 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | OH | Not Veg | 2017-07-12 | N | 71.2667 | N | 4 | N | N | 1.1101 | 39.4971 | 520.7958
[7 empty] | 7555 | 5903 | 1497093 | 2017-07-13 07:41 | 2017-07-13 08:20 | 39 | 11kV | 4173 | 107 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172660 A Phase No protection operations. Dropper to DOLF burnt off. Excluded OMS 1497093 | July | 2017 | 2018Q1 | 2018 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Not Veg | 2017-07-13 | N | 39 | N | 2 | N | N | 1.1101 | 39.4971 | 3049.5053
[7 empty] | 7344 | 2849 | 1497289 | 2017-07-13 19:08 | 2017-07-13 21:59 | 171 | 11kV | 16074 | 94 | HV | 3rd Party Vehicle | 3rd Party Impact | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S2189 C'Connor Barton custometers experienced voltages issures on C phase Suspect Tap Changer issue. Supply rectified by putting in LV parallels See OMS 1497289 1498273 | July | 2017 | 2018Q1 | 2018 | ZN72:PA26 | ZN35555:PA13 | ZN35555/000013 | INNER WEST | Unknown | Not Veg | 2017-07-13 | N | 171 | N | 2 | N | N | 1.1101 | 39.4971 | 11746.4051
[7 empty] | 7328 | 2694 | 1497490 | 2017-07-14 18:55 | 2017-07-14 19:50 | 55 | 11kV | 811 | 15 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Pa4 "Apprentice Craftsmen" fdr open on Earth Fault with EFI down at S18446 only. UG Fault between S18446 to S14766 to S18323 See 1497805,6 ex 1497490 | July | 2017 | 2018Q1 | 2018 | ZN12690:PA4 | ZN12690:PA4 | ZN12690/000004 | CENTRAL COAST | UG | Not Veg | 2017-07-14 | N | 54.0667 | N | 1 | N | N | 1.1101 | 39.4971 | 592.6549
[7 empty] | 7801 | 8741 | 1497505 | 2017-07-15 04:07 | 2017-07-15 05:04 | 57 | 11kV | 117813 | 2229 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2310 Punchbowl Panel 65 tripped on Relays: B phase OC and EFI Signals: 11kV trip, Zone Earth and TX3 Group Earth. Cause: 11kV UG cable fault from S48550 to S3528 to S2198 See OMS 1498026 1498028 1497505 | July | 2017 | 2018Q1 | 2018 | ZN2310:PA65 | ZN2310:PA14 | ZN02310/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-07-15 | N | 52.8546 | N | 1 | N | N | 1.1101 | 39.4971 | 86094.2655
[7 empty] | 8257 | 14487 | 1497715 | 2017-07-16 18:00 | 2017-07-16 20:00 | 120 | 11kV | 14400 | 120 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | Zn13000 Lake Munmorah sectino of Pa4 "Pacific Hwy North" 11kV isolated from LB62014 to LB41889 tee PT14245 PT12031 PT13585 Cause: Broken insulator with 11kV mains on cross-arm Cause: Pole at corner chain valley and pacific Hwy reported by M strong (compliance officer) Insulator failed See 1497827 ex 1497715,6 | July | 2017 | 2018Q1 | 2018 | ZN13000:PA4 | ZN13000:PA4 | ZN13000/000004 | CENTRAL COAST | OH | Not Veg | 2017-07-16 | N | 120 | N | 1 | N | N | 1.1101 | 39.4971 | 10523.0953
[7 empty] | 8109 | 12605 | 1497854 | 2017-07-17 14:29 | 2017-07-17 16:35 | 126 | 11kV | 105171 | 1314 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn9700 Kirrawee Pnl.18 tripped on Earth Fault Field EFIs: S48939 S9146 S9430 Crane hit 11kV OH mains at Building site in Auburn St Kirrawee. Section of 11kV feeder isolated from AB35761 to AB35959 tee S9157 for Lineworker to inspect for damage and Workcover investigation. See 1498005 1498006 | July | 2017 | 2018Q1 | 2018 | ZN9700:PA18 | ZN9700:PA18 | ZN09700/000018 | SUTHERLAND | OH | Not Veg | 2017-07-17 | N | 80.0388 | N | 2 | N | N | 1.1101 | 39.4971 | 76855.8648
[7 empty] | 7826 | 9013 | 1497950 | 2017-07-17 19:46 | 2017-07-17 22:00 | 134 | 11kV | 101283 | 1109 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.19 tripped on Earth Fault and B & C phase Overcurrent with EFI Field EFI: S35080 only UG cable fault from S35080 (Sw/B) to S5795 (Sw/A) See 1498319 1498320 | July | 2017 | 2018Q1 | 2018 | ZN2568:PA19 | ZN2568:PA19 | ZN02568/000019 | INNER WEST | UG | Not Veg | 2017-07-17 | N | 91.3282 | N | 2 | N | N | 1.1101 | 39.4971 | 74014.6291
[7 empty] | 8213 | 13859 | 1497998 | 2017-07-18 08:35 | 2017-07-18 10:31 | 116 | 11kV | 9860 | 85 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172696 3 fault operations No cause found | July | 2017 | 2018Q1 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2017-07-18 | N | 116 | N | 4 | N | N | 1.1101 | 39.4971 | 7205.3972
[7 empty] | 7634 | 6659 | 1498076 | 2017-07-18 12:48 | 2017-07-18 14:20 | 92 | 11kV | 62284 | 701 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Pa9 fdr has tripped/reclosed/tripped & locked out Signals: 11kv Trip, Tx1 Group Earth Relays: Basler, 50TAC, A+C Phase IOC, EFI, Fault CHeck, Reclose Timing, Reclose Lockout EFI's: S14513 S14237 Cause: UG Fault. DOp's Patrolled OH & HV UGOH to S14678 & found no obvious damage. OMS Reports about 2 explosions heard near S14678. Nothing Obvious sighted See 1498612,4,5 exclude 1498076,8,87 | July | 2017 | 2018Q1 | 2018 | ZN14892:PA9 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | UG | Not Veg | 2017-07-18 | N | 88.8502 | N | 4 | N | N | 1.1101 | 39.4971 | 45515.3101
[7 empty] | 8296 | 14945 | 1498080 | 2017-07-18 12:59 | 2017-07-18 18:00 | 301 | 11kV | 189190 | 932 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn3154 St Ives Pa17 "Rosedale Shinfield" fdr tripped, reclosed and locked out on: Relays: Earth Leakage, Lockout/Lockout Time Delay, EFI EFI's: S62840 S35868 S4914 S4020 S7416 S7417 Cause: Tree Branch on OH Mains near PT39 Waterhouse Torrens CB17 will not close after fault, PE to overhaul/repair Bond off AB1388 See 1498619,20 Ex 1498080,136,46,7,61,70 | July | 2017 | 2018Q1 | 2018 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Veg | 2017-07-18 | N | 202.9936 | N | 4 | N | N | 1.1101 | 39.4971 | 138254.4718
[7 empty] | 8290 | 14864 | 1498188 | 2017-07-18 19:53 | 2017-07-18 20:44 | 51 | 11kV | 91137 | 1787 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 3 tripped on Signals: 11kV trip relays: Timed EF Field EFI's - Nil Cause: Bat found O/S 76 Carranya Rd Lane Cove At S4472 Ross Smith Bridge 400A fuse blown on A B and C phase of distributor 1. At S2287 Cope St 400A fuse blown on A B and C phase of distributor 4 At S2287 Cope St 400A fuse blown on B and C phase of distributor 2 At S2287 Cope St 400A fuse blown on A B and C phase of distributor 1. Cause: LV parallel failure during feeder trip See OMS 1498188 149832/24/26/28 1498194/206/203 | July | 2017 | 2018Q1 | 2018 | ZN129:PA3 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Not Veg | 2017-07-18 | N | 51 | N | 4 | N | N | 1.1101 | 39.4971 | 66600.2315
[7 empty] | 7283 | 1873 | 1498296 | 2017-07-19 10:29 | 2017-07-19 11:54 | 85 | 11kV | 187935 | 2211 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3922 Drummoyne - Pnl.2 tripped on: Earth Fault with EFI UG cable fault from S49130 (Sw/B) to S2232 (Sw/A) See 1498296 | July | 2017 | 2018Q1 | 2018 | ZN3922:PA2 | ZN3922:PA2 | ZN03922/000002 | INNER WEST | UG | Not Veg | 2017-07-19 | N | 85 | N | 2 | N | N | 1.1101 | 39.4971 | 137337.3549
[7 empty] | 7932 | 10229 | 1498367 | 2017-07-19 13:33 | 2017-07-19 14:39 | 66 | 11kV | 660 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ex S35370 Galston Panel 8 Galston Picnic Reserve Recloser 741 Bloodwood Nollands tripped on SEF and Lockout Cause: Tree on Mains | July | 2017 | 2018Q1 | 2018 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2017-07-19 | N | 66 | N | 2 | N | N | 1.1101 | 39.4971 | 482.3085
[7 empty] | 7902 | 9963 | 1498769 | 2017-07-21 11:32 | 2017-07-21 12:43 | 71 | 11kV | 25375 | 361 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S35400 North Sydney Panel 68 tripped Relays - A C and N phase trip, Earth Fault and EFI Signals: 11kV Trip, Zone Earth Cause; Front line feeder fault from S35400 North Sydney Panel 68 to CP3337 to S3931 See OMS 1499570 1498769 | July | 2017 | 2018Q1 | 2018 | ZN35400:PA68 | ZN35400:PA68 | ZN35400/000068 | NORTH SYDNEY | UG | Not Veg | 2017-07-21 | N | 70.2909 | N | 3 | N | N | 1.1101 | 39.4971 | 18543.3016
[7 empty] | 7780 | 8474 | 1499547 | 2017-07-21 22:53 | 2017-07-22 01:30 | 157 | 11kV | 19625 | 125 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn10990 Arncliffe Pa12 "Wickham St" S10036 Kyle Duncan no protection operation Cause: transformer winding failure at S10036 Aph=210V Bph=242 Cph=243 Dop closed N/O dist 2 @ S65433 Kyle Charles | July | 2017 | 2018Q1 | 2018 | ZN10990:PA12 | ZN10998:PA9 | ZN10998/000009 | BAYSIDE | OH | Not Veg | 2017-07-21 | N | 157 | N | 3 | N | N | 1.1101 | 39.4971 | 14341.3712
[7 empty] | 8049 | 11743 | 1498882 | 2017-07-21 21:59 | 2017-07-22 01:52 | 233 | 11kV | 29016 | 191 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172758 2 fault operations 3 phase Earth Fault A phase wire down pole 8N-20024. Replaced under AP Excluded OMS 1498882. | July | 2017 | 2018Q1 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-07-21 | N | 151.9162 | N | 3 | N | N | 1.1101 | 39.4971 | 21204.037
[7 empty] | 7997 | 11002 | 1498993 | 2017-07-22 16:34 | 2017-07-22 19:10 | 156 | 11kV | 468 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 172762 C Phase DOLF : 10 Amp Bird contacted 11kV. Volts check 241V 242v 241V Excluded OMS # 1498993. | July | 2017 | 2018Q1 | 2018 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2017-07-22 | N | 156 | N | 1 | N | N | 1.1101 | 39.4971 | 342.0006
[7 empty] | 7493 | 5216 | 1499152 | 2017-07-24 01:47 | 2017-07-24 08:45 | 418 | 11kV | 10869 | 27 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn9534 Kurnell South Panel 18 Tripped and reclosed on A phase O/C and Lockout Signals: 11kV trip Cause: Roadside bond on 11kV burnt off LB35488 See OMS 1499561 1499564 1499152 1499170 1499171 1499175 1499203 | July | 2017 | 2018Q1 | 2018 | ZN9534:PA18 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2017-07-24 | N | 402.5556 | N | 2 | N | N | 1.1101 | 39.4971 | 7942.7446
[7 empty] | 8455 | 17055 | 1499294 | 2017-07-24 11:41 | 2017-07-24 12:45 | 64 | 11kV | 85248 | 1332 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12660 Woy Woy Pa8 "North Burge Rd" tripped, reclosed & tripped Relays: IOC, Timed OC, Earth Fault Signals: 11kv trip, CB8 open, CB8 closed, CB* open EFI's: Nil UG cable damaged by contractor. Frontline feeder fault from Pa8 to S18313 tee LB40616 See 1499294 ex 1499307 | July | 2017 | 2018Q1 | 2018 | ZN12660:PA8 | ZN12660:PA8 | ZN12660/000008 | CENTRAL COAST | UG | Not Veg | 2017-07-24 | N | 64 | N | 2 | N | N | 1.1101 | 39.4971 | 62296.724
[7 empty] | 7289 | 1997 | 1499556 | 2017-07-25 13:30 | 2017-07-25 14:35 | 65 | 11kV | 1690 | 26 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S4545 Meadowbank panel 9 tripped on Relays: EF, EFI and fault check Signals: 11kV trip, group earth EFI's NIl At S4545 Meadowbank Panel 9 to S8283 front line feeder fault. | July | 2017 | 2018Q1 | 2018 | ZN4545:PA9 | ZN4545:PA9 | ZN04545/000009 | CANADA BAY | UG | Not Veg | 2017-07-25 | N | 65 | N | 3 | N | N | 1.1101 | 39.4971 | 1235.0022
[7 empty] | 7510 | 5509 | 1499504 | 2017-07-25 10:40 | 2017-07-25 16:00 | 320 | 11kV | 17280 | 54 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa1 "Gunderman" PT49014 Lavender Wise Ferry the center phase HDO blew See 1499869 ex 1499504 | July | 2017 | 2018Q1 | 2018 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2017-07-25 | N | 320 | N | 3 | N | N | 1.1101 | 39.4971 | 12627.7143
[7 empty] | 7455 | 4719 | 1499518 | 2017-07-25 11:32 | 2017-07-25 19:50 | 498 | 11kV | 996 | 2 | HV | Equipment Failed in Service | Equipment Failure | 3rd Party Asset | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of Pa12 "Craftsman Ave" PT14505 Old Chittaway the HV fuse blew Cause: Customers installation. Private Pole at 61 chittaway rd has fallen against tree and private bare aerials have clashed together blowing HV fuse at PT. PT tank (winding) defective subs to source MG to connect to LV PT cannot be isolated on 11kv fdr due to defective AB42921 See 1499574 ex 1499518 | July | 2017 | 2018Q1 | 2018 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | Unknown | Not Veg | 2017-07-25 | N | 498 | N | 3 | N | N | 1.1101 | 39.4971 | 727.8474
[7 empty] | 8590 | 18697 | 1499663 | 2017-07-26 05:34 | 2017-07-26 08:22 | 168 | 11kV | 61164 | 368 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.42 tripped on: IOC with Fault Check and EFI Field EFIs: NIL UG Cable fault between S65207 (Sw/B) and S35331 (Sw/A) See 1500045 1500046 | July | 2017 | 2018Q1 | 2018 | ZN2568:PA42 | ZN2568:PA42 | ZN02568/000042 | INNER WEST | UG | Not Veg | 2017-07-26 | N | 166.2065 | N | 5 | N | N | 1.1101 | 39.4971 | 44696.8472
[7 empty] | 7487 | 5141 | 1499718 | 2017-07-26 09:58 | 2017-07-26 11:10 | 71.7667 | 11kV | 62221.7 | 867 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Wind Strong | N | At Zn9252 Jannali 11kv feeder Panel No: 25 "Woronora" feeder tripped to lock out Relays: SEL, Lockout Signals: SEF trip, Prot trip, Sub prot trip pulse, fdr relay management Neutral Field EFI's: nil Remarks: UGOH fault open circuit. 11kv UGOH bond failure on Cnr Grand Pde and Oatwood St - Section of 11kv feeder ZN9252 PA: 25 to LB35248 to LB35362 | July | 2017 | 2018Q1 | 2018 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | Unknown | Unknown | 2017-07-26 | N | 71.7667 | N | 5 | N | N | 1.1101 | 39.4971 | 45469.7831
[7 empty] | 7384 | 3637 | 1499795 | 2017-07-26 13:08 | 2017-07-26 14:45 | 97 | 11kV | 776 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 172807 A PHASE HV LEAD BROKEN OFF IN WIND. Excluded OMS REPORT NO 1499795. | July | 2017 | 2018Q1 | 2018 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2017-07-26 | N | 97 | N | 5 | N | N | 1.1101 | 39.4971 | 567.0779
[7 empty] | 8637 | 19323 | 1499848 | 2017-07-26 16:07 | 2017-07-26 17:24 | 77 | 11kV | 54109 | 755 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36100 Rose Bay - Pnl.15 tripped on: Earth Fault with EFI Field EFIs: S2222 & S8937 UG cable fault between S8937 (Sw/B) and S35907 (Sw/A) and S2593 (Sw/A) See 1500172 1500173 | July | 2017 | 2018Q1 | 2018 | ZN36100:PA15 | ZN36100:PA15 | ZN36100/000015 | WAVERLEY | UG | Not Veg | 2017-07-26 | N | 71.6675 | N | 5 | N | N | 1.1101 | 39.4971 | 39541.2613
[7 empty] | 7317 | 2505 | 1499832 | 2017-07-26 15:24 | 2017-07-26 18:30 | 186 | 11kV | 186 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 172808 A Phase Burnt off HV LL lead on A phase. Excluded OMS 1499832. | July | 2017 | 2018Q1 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2017-07-26 | N | 186 | N | 5 | N | N | 1.1101 | 39.4971 | 135.9233
[7 empty] | 7666 | 7008 | 1499919 | 2017-07-27 06:31 | 2017-07-27 07:28 | 57 | 11kV | 1311 | 23 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn2466 Flemington 11kv VCB panel 19 "S-7306" feeder tripped on - Relays: B phase O/C, EFI, Fault check Field EFI's - Nil Signals: 11kv trip Remarks: UG fault. 11kv UG feeder fault from ZN2466 Flemington 11kv VCB panel 19 "S-7306" feeder to S-7306 Carter Hill No.2 "Sw-A" | July | 2017 | 2018Q1 | 2018 | ZN2466:PA19 | ZN2466:PA19 | ZN02466/000019 | CUMBERLAND | UG | Not Veg | 2017-07-27 | N | 57 | N | 4 | N | N | 1.1101 | 39.4971 | 958.0401
[7 empty] | 8079 | 12179 | 1500057 | 2017-07-27 14:39 | 2017-07-27 15:15 | 36 | 11kV | 3960 | 110 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.42 tripped Abnormal: 11kV feeder fault from S65207 to S35331 - S7775 (Sw/B closed) UG cable fault from Pnl.42 to S65207 | July | 2017 | 2018Q1 | 2018 | ZN2568:PA42 | ZN2568:PA42 | ZN02568/000042 | INNER WEST | UG | Not Veg | 2017-07-27 | N | 36 | N | 4 | N | N | 1.1101 | 39.4971 | 2893.8512
[7 empty] | 7771 | 8339 | 1500001 | 2017-07-27 10:04 | 2017-07-27 16:00 | 356 | 11kV | 282358 | 2314 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14143 Somersby 11kV Pa5 fdr cb tripped on: Re;ays: EFI Signals: Group Earth EFI's: S18048 CP45441 S14863 S18785 S14471 S14413 S14530 S14532 S14398 S14221 S14220 Abnormal: S14220:B closed AB44163 open & defective Cause: UG Fault 11kV fdr from S65410 to S64883 to S14863 tee PT43585 to LB40492 See 1500620,6,8,9 ex 1500001,2,11,41,122 | July | 2017 | 2018Q1 | 2018 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | UG | Not Veg | 2017-07-27 | N | 122.0216 | N | 4 | N | N | 1.1101 | 39.4971 | 206338.8982
[7 empty] | 7372 | 3430 | 1500052 | 2017-07-27 12:47 | 2017-07-27 16:15 | 208 | 11kV | 208 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | No Weather Impact | N | LID 172827 B Phase Striker Fuse : 80 Amp striker did not trip switch all 3 fuses replaced Excluded oms 1500052 | July | 2017 | 2018Q1 | 2018 | 238:34150 | 238:34150 | ZN00238/034150 | MAITLAND | UG | Not Veg | 2017-07-27 | N | 208 | N | 4 | N | N | 1.1101 | 39.4971 | 152.0003
[7 empty] | 7671 | 7048 | 1500243 | 2017-07-28 14:06 | 2017-07-28 16:55 | 169 | 11kV | 169 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 172846 faulty sectionaliser sw 46886 darley stud tripped while fdr alive. Second occurance, sw already has dma tag excluded oms 1500243 | July | 2017 | 2018Q1 | 2018 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2017-07-28 | N | 169 | N | 2 | N | N | 1.1101 | 39.4971 | 123.5002
[7 empty] | 8442 | 16826 | 1500239 | 2017-07-28 13:55 | 2017-07-28 21:10 | 434.7667 | 11kV | 9665.35 | 23 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 172847 Bushfire caused tree to fall on Fdr at IT-48274 section isolated for repairs Excluded oms 1500239 | July | 2017 | 2018Q1 | 2018 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2017-07-28 | N | 420.2326 | N | 2 | N | N | 1.1101 | 39.4971 | 7063.1527
[7 empty] | 7949 | 10361 | 1500437 | 2017-07-30 06:52 | 2017-07-30 07:45 | 53 | 11kV | 60526 | 1142 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36800 Waverley - Pnl.40 tripped on: Overcurrent and Earth Fault with EFI Field EFI : S64932 UG cable fault between S34932 (Sw/B) and S1872 (Sw/A) See 1500622 1500623 | July | 2017 | 2018Q1 | 2018 | ZN36800:PA40 | ZN36800:PA56 | ZN36800/000056 | WAVERLEY | UG | Not Veg | 2017-07-30 | N | 53 | N | 2 | N | N | 1.1101 | 39.4971 | 44230.6156
[7 empty] | 8654 | 19518 | 1500518 | 2017-07-30 23:57 | 2017-07-31 01:54 | 117 | 11kV | 107874 | 922 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie Panel 24 "Eighth Fourth" feeder tripped on: Relays: E/F, B phase timed O/C EFI and fault check relay Signals: 11kv trip and group earth Remarks: UG fault. EFI at S46907 Eighth Fourth is defective. EFI's along feeder not reset after previous fault and where down. 11kv UG feeder defective from Zn690 Campsie Panel 24 to S46907 Eigth fourth to S3129 Third Eighth | July | 2017 | 2018Q1 | 2018 | ZN690:PA24 | ZN690:PA24 | ZN00690/000024 | STRATHFIELD | UG | Not Veg | 2017-07-30 | N | 117 | N | 2 | N | N | 1.1101 | 39.4971 | 78831.1375
[7 empty] | 8397 | 16284 | 1500683 | 2017-07-31 12:13 | 2017-07-31 19:25 | 432 | 11kV | 29974 | 475 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 172872 1 fault operation A Phase Instantaneous Earth Fault, Instantaneous Overcurrent 11kV UG cable dug up at roundabout. Mitchel Dr x Stronach Ave. East MAitland Excluded OMS 1500683 | July | 2017 | 2018Q1 | 2018 | 532:83312 | 532:83312 | ZN00532/083312 | MAITLAND | UG | Not Veg | 2017-07-31 | N | 63.1032 | N | 1 | N | N | 1.1101 | 39.4971 | 21904.1151
[7 empty] | 8652 | 19490 | 1501018 | 2017-08-01 18:55 | 2017-08-02 00:05 | 310 | 11kV | 6180 | 21 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn9534 Kurnell South Pa18 AB35709 opened @ 21:40 to carry out repairs Abnormal: IS35910 closed, LB35488 open (defective with roadside bond off) Cause: 11kv bond off @ AB35183 See 1501144,5 ex 1501018,25,9 | August | 2017 | 2018Q1 | 2018 | ZN9534:PA18 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2017-08-01 | N | 294.2857 | N | 1 | N | N | 1.1101 | 39.4971 | 4516.1617
[7 empty] | 7414 | 4014 | 1501056 | 2017-08-02 06:45 | 2017-08-02 08:10 | 85 | 11kV | 123930 | 1458 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN874 Concord 11kv feeder Panel No: 4 "Mepunga St" feeder tripped Relays: E/F and EFI Note: Following EFIs failed to operate delaying restoration S35549, S6493, S65412 Remarks: UG fault. 11kv UG cable fault from S65412 Hilly Edwin No3 (SWB) to S3883 Northcote Bennett (SWB), between RMIs LV// required for phasing on restoration. Note: See seperate interruption @ 0816hrs ZN2835 PA:24 operated due following EFIs failed to operate delaying restoration S35549, S64913, S65412 | August | 2017 | 2018Q1 | 2018 | ZN874:PA4 | ZN874:PA4 | ZN00874/000004 | CANADA BAY | UG | Not Veg | 2017-08-02 | N | 85 | N | 1 | N | N | 1.1101 | 39.4971 | 90564.3887
[7 empty] | 8439 | 16808 | 1501261 | 2017-08-03 04:55 | 2017-08-03 06:41 | 106 | 11kV | 118248 | 1180 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Pa18 "Forresters Beach" fdr tripped to lock out x2 Relays: B & C phase OC, IOC, EFI, Lockout EFI's: nil Cause: not ascertained DOps patrolled feeder no cause ascetained See 1501355,6,7 ex 1501261.70 | August | 2017 | 2018Q1 | 2018 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Veg | 2017-08-03 | N | 100.2102 | N | 4 | N | N | 1.1101 | 39.4971 | 86412.1507
[7 empty] | 7619 | 6460 | 1501406 | 2017-08-03 14:47 | 2017-08-03 14:51 | 4 | 11kV | 1020 | 255 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | S.O open circuit breaker to bypass faulty broads crossing regulator | August | 2017 | 2018Q1 | 2018 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | Unknown | Not Veg | 2017-08-03 | N | 4 | N | 4 | N | N | 1.1101 | 39.4971 | 745.3859
[7 empty] | 8425 | 16643 | 1501481 | 2017-08-03 18:57 | 2017-08-04 00:27 | 330 | 11kV | 87846 | 275 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 172912 4 Fault operations Instantaneous Overcurrent, Overcurrent Pole WT-20419 2 x wires off pins, resulting in mains on cross arm | August | 2017 | 2018Q1 | 2018 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2017-08-03 | N | 319.44 | N | 4 | N | N | 1.1101 | 39.4971 | 64195.2658
[7 empty] | 8312 | 15128 | 1501493 | 2017-08-03 20:23 | 2017-08-04 00:50 | 267 | 11kV | 60976 | 1397 | HV | Animal Bird | Animal | Recloser / Sectionaliser | Unplanned | Rain Heavy | N | LID 172911 2 Fault Operations A Phase, Earth Fault birds nest on IR 64158 louth park caused fire. Insulators on disconnector damaged by fire, bridges out intellirupter | August | 2017 | 2018Q1 | 2018 | 532:83307 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Not Veg | 2017-08-03 | N | 43.6478 | N | 4 | N | N | 1.1101 | 39.4971 | 44559.4623
[7 empty] | 7519 | 5566 | 1501507 | 2017-08-04 00:02 | 2017-08-04 02:25 | 143 | 11kV | 24584 | 190 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | zn14891 Wyong fdr Pa6 "Dulmison Dulsmison" fdr tripped to lockout x2 Relays: 51N (E/F & OC) E/F, EFI fault check, lockout timing EFI'S: S18495 S18493 S4826 S18464 S14404 S14881 S11362 Cause: UG Fault between section of fdr from S11362 Sw/A to S12265 Sw/A to LB41294. Fdr contains 2 seperate UG section of fdr/UGOH mains req to earth. Attention subs: EFI@S12265 maintain/replace. Also labelling requires to be updated as switch found with old style labelling and has been relabelled to system diagram by DOp and proven See 1501563,5,6 ex 1501507 | August | 2017 | 2018Q1 | 2018 | ZN14891:PA6 | ZN14891:PA6 | ZN14891/000006 | CENTRAL COAST | UG | Not Veg | 2017-08-04 | N | 129.3895 | N | 4 | N | N | 1.1101 | 39.4971 | 17965.2621
[7 empty] | 8143 | 13104 | 1501556 | 2017-08-04 10:13 | 2017-08-04 11:52 | 99 | 11kV | 114780 | 1160 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN35800 Bankstown - 11kv Panel No.7 "Sub 2703 Short Fair No.1" feeder tripped Relays: B & C phase IOC Signals: CB No.7 Open Remarks: UG fault. 11kv UG fault from S49916 Canterbury Gow No2 Sw/B to S3579 Warren Fortril Sw/A Tester/Jointer Permit Left at S | August | 2017 | 2018Q1 | 2018 | ZN35800:PA7 | ZN35800:PA7 | ZN35800/000007 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-08-04 | N | 98.9483 | N | 4 | N | N | 1.1101 | 39.4971 | 83877.8386
[7 empty] | 8437 | 16779 | 1501589 | 2017-08-04 11:21 | 2017-08-04 12:58 | 97 | 11kV | 5626 | 58 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 172923 Phase A: 20 Amp fuse. Fuse fatigue, supply back on 1258hrs | August | 2017 | 2018Q1 | 2018 | 258:80793 | 258:80793 | ZN00258/080793 | NEWCASTLE | OH | Not Veg | 2017-08-04 | N | 97 | N | 4 | N | N | 1.1101 | 39.4971 | 4111.3149
[7 empty] | 7600 | 6316 | 1501675 | 2017-08-04 16:16 | 2017-08-04 20:05 | 229 | 11kV | 48662 | 881 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At ZN14892 Charmhaven, 11kv panel 14 feeder C/B 'S.18599 Tavern Pacific' tripped on; Relays: B, C Phase O/C, EFI Signals: 11kv trip, Group Earth Field EFI's: Nil Remarks: tree/branch brought down OH. Mains down near USL 40891. Dop and L/Worker to repair | August | 2017 | 2018Q1 | 2018 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Veg | 2017-08-04 | N | 55.235 | N | 4 | N | N | 1.1101 | 39.4971 | 35560.7543
[7 empty] | 8458 | 17097 | 1501800 | 2017-08-05 12:12 | 2017-08-05 13:45 | 93 | 11kV | 152080 | 1864 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9035 Caringbah - Pnl.11 tripped on: 11R Earth Fault with EFI Field EFIs: S9420 S9836 UG cable fault from S9836 (Sw/B) to S9357 (Sw/A) tee S9709 See 1502027 1502028 1502029 | August | 2017 | 2018Q1 | 2018 | ZN9035:PA11 | ZN9035:PA11 | ZN09035/000011 | SUTHERLAND | UG | Not Veg | 2017-08-05 | N | 81.588 | N | 1 | N | N | 1.1101 | 39.4971 | 111135.5784
[7 empty] | 7873 | 9612 | 1501857 | 2017-08-06 01:28 | 2017-08-06 02:53 | 85 | 11kV | 105211 | 1534 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Pnl.1 Blakehurst Zone - AB31134 Centre phase bond went open circuit. Panel 1 at Blakehurst Zone opened at 2:46 to allow DOp to open AB31134 de-energised due to possible flashover. See 1502040 1502041 | August | 2017 | 2018Q1 | 2018 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2017-08-06 | N | 68.586 | N | 3 | N | N | 1.1101 | 39.4971 | 76885.0956
[7 empty] | 8204 | 13806 | 1501863 | 2017-08-06 03:32 | 2017-08-06 04:52 | 80 | 11kV | 4240 | 53 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 172927 B Phase 31 Amp Fuse. Substation DOLF Fatigued fuse, readings as left 252v @ 30A, 60A, 130A | August | 2017 | 2018Q1 | 2018 | 223:14397 | 223:14397 | ZN00223/014397 | LAKE MACQUARIE | OH | Not Veg | 2017-08-06 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 3098.4669
[7 empty] | 7628 | 6570 | 1501934 | 2017-08-06 16:14 | 2017-08-06 17:45 | 91 | 11kV | 109214 | 1212 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn3472 Sefton 11kv feeder Panel No : 8 "Park regents Park No1 etc" feeder tripped Relays: IOC, A B and C phase, fault check, EFI Remarks: UG fault. Cable fault in section of 11kv feeder from S7035 Princes Park (SwD) to S1921 St John Rd (SwA) to S1105 Meroo St (SwA) | August | 2017 | 2018Q1 | 2018 | ZN3472:PA8 | ZN3472:PA8 | ZN03472/000008 | CUMBERLAND | UG | Not Veg | 2017-08-06 | N | 90.1106 | N | 3 | N | N | 1.1101 | 39.4971 | 79810.3699
[7 empty] | 7497 | 5366 | 1502345 | 2017-08-08 13:26 | 2017-08-08 15:23 | 117 | 11kV | 91013 | 1197 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington - Pnl.28 tripped on: P28R - Earth Fault with EFI 11kV front line UG cable fault from P28 to S.36093 (Sw/A) to S.1526 (Sw/A) | August | 2017 | 2018Q1 | 2018 | ZN342:PA28 | ZN342:PA28 | ZN00342/000028 | SYDNEY | UG | Not Veg | 2017-08-08 | N | 76.0343 | N | 1 | N | N | 1.1101 | 39.4971 | 66509.616
[7 empty] | 7322 | 2550 | 1502474 | 2017-08-09 08:26 | 2017-08-09 21:00 | 754 | 11kV | 754 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | HV bond burnt off UGOH between CP1745 Dasea Muir and S61279 Dasea St No 2. Cause: HV bond burnt off UGOH between CP1745 and S61279. See OMS 1502958 1502474 | August | 2017 | 2018Q1 | 2018 |  |  |  | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-08-09 | N | 754 | N | 1 | N | N | 1.1101 | 39.4971 | 551.001
[7 empty] | 7869 | 9577 | 1502690 | 2017-08-10 10:40 | 2017-08-10 12:45 | 125 | 11kV | 64836 | 651 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay - Pnl.9 tripped on: Earth Fault, C phase Overcurrent with EFI Field EFIs: S9370 & S9278 Contractor (Mick 0407 777 200 of National Rock Sawing) drilled through UG cable at 160 Parraweena Rd. S9958 in LV parallel with PT9419 See 1502891 1502894 1502893 | August | 2017 | 2018Q1 | 2018 | ZN9550:PA9 | ZN9550:PA9 | ZN09550/000009 | SUTHERLAND | UG | Not Veg | 2017-08-10 | N | 99.5945 | N | 1 | N | N | 1.1101 | 39.4971 | 47380.2365
[7 empty] | 7226 | 845 | 1502851 | 2017-08-11 08:36 | 2017-08-11 09:42 | 66 | 11kV | 51533 | 983 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9118 Cronulla - Pnl.7 tripped on: B Phase Overcurrent with EFI Field EFIs: S9723, S9067 UG cable fault between S9067 (Sw/B) and S65712 (Sw/A) and S9537 (Sw/A) See 1503282 1503283 1503284 | August | 2017 | 2018Q1 | 2018 | ZN9118:PA7 | ZN9118:PA7 | ZN09118/000007 | SUTHERLAND | UG | Not Veg | 2017-08-11 | N | 52.4242 | N | 3 | N | N | 1.1101 | 39.4971 | 37658.7964
[7 empty] | 7603 | 6351 | 1502951 | 2017-08-11 13:57 | 2017-08-11 15:58 | 121 | 11kV | 159252 | 1476 | HV | Animal Bird | Animal | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | At S15011 Beacon Hill Panel 10 tripped on A and C phase OC Trip and and sensitive Earth Cause: Dead bird found near recloser 21799 which caused bond to burn off between UGOH from S46679 and tee to recloser 21799 See OMS 1503329 1503330 1502951 1502956 | August | 2017 | 2018Q1 | 2018 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Not Veg | 2017-08-11 | N | 107.8943 | N | 3 | N | N | 1.1101 | 39.4971 | 116376.6645
[7 empty] | 8089 | 12277 | 1502916 | 2017-08-11 12:10 | 2017-08-11 21:10 | 540 | 11kV | 60459 | 1374 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 173007 1 Fault operation Sensitive Earth Fault ohm down at pole JU-31063 near sub 43040 shackle bolt rusted through crossarm & broke connection. Excluded oms 1502916 | August | 2017 | 2018Q1 | 2018 | 203:8090 | 204:82699 | ZN00204/082699 | NEWCASTLE | OH | Not Veg | 2017-08-11 | N | 44.0022 | N | 3 | N | N | 1.1101 | 39.4971 | 44181.654
[7 empty] | 7990 | 10901 | 1503112 | 2017-08-12 18:44 | 2017-08-12 20:13 | 89 | 11kV | 138751 | 1559 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde panel 34 tripped on Relays: C phase OC timed, Earth Fault, EFI, Under frequency, Fault check Signals: 11kV trip Cause: Possum found at the base of HV UGOH pole on TEE off to S5427 Helcyan Peliacan See OMS1503112 1503378 1503115 1503120 1503126 Note: PT1506#1 and S5480#2 were in LV with Pa34 Top Ryde | August | 2017 | 2018Q1 | 2018 | ZN35500:PA34 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Not Veg | 2017-08-12 | N | 89 | N | 1 | N | N | 1.1101 | 39.4971 | 101395.1383
[7 empty] | 8012 | 11264 | 1503134 | 2017-08-13 04:07 | 2017-08-13 05:15 | 68 | 11kV | 103224 | 1518 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN116 Leichhardt Panel 73 "Ilka Cath" tripped on Relays: - Timed earth fault Signals: Zn earth, Tx 4 Group earth and 11kv trip Field EFI's: S5521 Remarks: UG fault. 11kv UG feeder fault from S5521 Moore Cath to Sub 3662 John Hill | August | 2017 | 2018Q1 | 2018 | ZN116:PA73 | ZN116:PA29 | ZN00116/000029 | INNER WEST | UG | Not Veg | 2017-08-13 | N | 68 | N | 2 | N | N | 1.1101 | 39.4971 | 75433.0546
[7 empty] | 8185 | 13526 | 1503188 | 2017-08-13 14:19 | 2017-08-13 16:55 | 156 | 11kV | 134850 | 3467 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.36 tripped on: A phase Instantaneous Overcurrent with EFI 11kV UG cable fault from S3527 (Sw/B) to S818 (Sw/C) - Normally Open No Field EFIs operated on Pnl.36. On attempted restoration from P14 via Sw/C @ S818, O/C protection did not operate at S818 (Sw/C) causing Pnl.14 to trip on: A phase inst O/C. See 1503289 1503291 1503293 1503294 P14 1503295 LV // 1503296 | August | 2017 | 2018Q1 | 2018 | ZN690:PA36 | ZN690:PA36 | ZN00690/000036 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-08-13 | N | 38.8953 | N | 2 | N | N | 1.1101 | 39.4971 | 98544.4026
[7 empty] | 8490 | 17482 | 1503356 | 2017-08-14 11:48 | 2017-08-14 13:05 | 77 | 11kV | 77 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173025 A Phase DOLF : 10 Amp Excluded OMS 1503356 | August | 2017 | 2018Q1 | 2018 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Veg | 2017-08-14 | N | 77 | N | 1 | N | N | 1.1101 | 39.4971 | 56.2693
[7 empty] | 7767 | 8275 | 1503719 | 2017-08-15 06:17 | 2017-08-15 10:59 | 282 | 11kV | 28009 | 130 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 173036 C Phase Overcurrent Pelican into OHM Excluded OMS 1503719 | August | 2017 | 2018Q1 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2017-08-15 | N | 215.4538 | N | 1 | N | N | 1.1101 | 39.4971 | 20468.1511
[7 empty] | 7718 | 7664 | 1504060 | 2017-08-16 09:15 | 2017-08-16 10:11 | 56 | 11kV | 45748 | 839 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.4 tripped on: earth leakage, B Phase IOC, EFI UG cable hit by digger outside 168 James St Redfern See 1504500 1504501 | August | 2017 | 2018Q1 | 2018 | ZN188:PA4 | ZN188:PA4 | ZN00188/000004 | SYDNEY | UG | Not Veg | 2017-08-16 | N | 54.5268 | N | 10 | N | N | 1.1101 | 39.4971 | 33431.2891
[7 empty] | 8504 | 17676 | 1504058 | 2017-08-16 09:11 | 2017-08-16 10:42 | 91 | 11kV | 1272 | 14 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley vale Pa4 tripped on: Relays: ACph Instantaneous. EF, EFI Signals: 11kv trip, Tx12 Group Earth EFI's: S18446 Cause: UG fault from S18446 to S14766 to S18323 See 1504489,91 ex 1504058 | August | 2017 | 2018Q1 | 2018 | ZN12690:PA4 | ZN12690:PA4 | ZN12690/000004 | CENTRAL COAST | UG | Not Veg | 2017-08-16 | N | 90.8571 | N | 10 | N | N | 1.1101 | 39.4971 | 929.5401
[7 empty] | 8031 | 11445 | 1504106 | 2017-08-16 10:18 | 2017-08-16 12:14 | 116 | 11kV | 182468 | 1573 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn847 Hornsby section of Pa21 tripped reclosed and locked out on earth fault, reclose time delay and lockout relay Crane into HV bouvardia and peatsferry rd asquith as well LV// found in mains burnt down at amor st and ida st | August | 2017 | 2018Q1 | 2018 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Not Veg | 2017-08-16 | N | 116 | N | 10 | N | N | 1.1101 | 39.4971 | 133342.2325
[7 empty] | 7621 | 6482 | 1504151 | 2017-08-16 11:03 | 2017-08-16 12:45 | 102 | 11kV | 10911 | 114 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC20828 Cooyong Rd - tripped, relcosed, tripped and locked out. Tree branch brought down OH mains in Kinka Rd. See 1504507 1504509 | August | 2017 | 2018Q1 | 2018 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2017-08-16 | N | 95.7105 | N | 10 | N | N | 1.1101 | 39.4971 | 7973.437
[7 empty] | 8104 | 12556 | 1504202 | 2017-08-16 11:50 | 2017-08-16 13:30 | 100 | 11kV | 177000 | 1770 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn12570 Avoca Pa24 tripped on Signals: ACph O/C lockout Relays: 11kv trip Cause: Large tree branch found below a section of OH mains. DOp suspects this was the cause, No damage to the mains. | August | 2017 | 2018Q1 | 2018 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2017-08-16 | N | 100 | N | 10 | N | N | 1.1101 | 39.4971 | 129346.3794
[7 empty] | 7915 | 10064 | 1504190 | 2017-08-16 11:33 | 2017-08-16 15:00 | 207 | 11kV | 7011 | 94 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge Pa13 "Peats Ridge Aux" fdr has tripped Signals: 11kv trip Relays: SEL EFI's: Nil RE46763 Grants Keighley 0.3w has also tripped on SEL Cause: Tree/Branch brought down OH. 11kv on ground after LK42028 See 1504523,4,5,6 ex 1504190,5,207,73 | August | 2017 | 2018Q1 | 2018 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2017-08-16 | N | 74.5851 | N | 10 | N | N | 1.1101 | 39.4971 | 5123.432
[7 empty] | 7431 | 4241 | 1504322 | 2017-08-16 17:10 | 2017-08-16 17:25 | 15 | 11kV | 990 | 66 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section off 11kV feeder from LB64868 to AB901 tee PT240 Keats Rd - Interrupted to allow safe removal of tree branch from OH mains. Ex Pnl.12 St Ives Zn | August | 2017 | 2018Q1 | 2018 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Veg | 2017-08-16 | N | 15 | N | 10 | N | N | 1.1101 | 39.4971 | 723.4628
[7 empty] | 7533 | 5688 | 1504169 | 2017-08-16 11:26 | 2017-08-16 18:05 | 399 | 11kV | 116623 | 924 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn36200 Empire bay Pa4 "Bensville" fdr tripped Signals: 11kv trip Relays: Reclose Lockout, B Phase Instantaneous, EFI Cause: Tree Branch on OH Mains adjacent to AB44383. Linesman required to repair. See 1504506,8,10 ex 1504169,276,7 | August | 2017 | 2018Q1 | 2018 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2017-08-16 | N | 126.2154 | N | 10 | N | N | 1.1101 | 39.4971 | 85224.6486
[7 empty] | 7638 | 6695 | 1504107 | 2017-08-16 10:22 | 2017-08-16 18:16 | 474 | 11kV | 44689 | 371 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn35370 Galston Pa2 tripped reclosed and locked out on BC phase overcurrent, reclosed lockout, EFI EFI at CP2381 Cause: Tree/Branch brought down OH. Gilligans Rd Galston - Haycolec Autolink defective/flashed over CP443 See 1505546,7,8 ex 1504107,241,2 | August | 2017 | 2018Q1 | 2018 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2017-08-16 | N | 120.4555 | N | 10 | N | N | 1.1101 | 39.4971 | 32657.4031
[7 empty] | 8052 | 11776 | 1504342 | 2017-08-16 15:34 | 2017-08-16 21:10 | 336 | 11kV | 57641 | 773 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa33 RE45133 McMasters Beach tripped, reclosed, tripped & locked out on overcurrent with EFI's on Pa35 & Pa35 Tree/Branch on OH Mains near AB41277. 11kV into LV at PT13296 on Dist 1 See 1504537,8,9,40 ex 1504342,5,7 | August | 2017 | 2018Q1 | 2018 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2017-08-16 | N | 74.5679 | N | 10 | N | N | 1.1101 | 39.4971 | 42122.3427
[7 empty] | 7946 | 10350 | 1504562 | 2017-08-17 14:26 | 2017-08-17 14:31 | 5 | 11kV | 6055 | 1211 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kv feeder Panel 12 the "Eastern Valley Ford" feeder was interrupted for safety to remove large branch Remarks: interrupted for safety reasons. Large branch removed at 45 Park Rd Roseville | August | 2017 | 2018Q1 | 2018 | ZN3425:PA12 | ZN3425:PA12 | ZN03425/000012 | KU-RING-GAI | OH | Veg | 2017-08-17 | N | 5 | N | 4 | N | N | 1.1101 | 39.4971 | 4424.8154
[7 empty] | 8077 | 12172 | 1504591 | 2017-08-17 14:35 | 2017-08-17 14:50 | 15 | 11kV | 3525 | 235 | HV | Vegetation Blow/Fall In | Vegetation | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Rec 64824 Deepwater Holly tripped and locked on OC trip Ex panel 33 the "Warrane McCabe etc" feeder Remarks: treen branch came in contact nr UGOH to S1720 Castle Golf Club | August | 2017 | 2018Q1 | 2018 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | OH | Veg | 2017-08-17 | N | 15 | N | 4 | N | N | 1.1101 | 39.4971 | 2575.966
[7 empty] | 7757 | 8118 | 1504559 | 2017-08-17 17:24 | 2017-08-17 17:31 | 6.9667 | 11kV | 1142.5333 | 164 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of Pa17 RE45012 Bar Point opened for safe removal of tree of 11kV Mains Tree Branch resting on 11kV between PT13610 Bar Point 0.2 and PT13611 Bar Point 0.7 | August | 2017 | 2018Q1 | 2018 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2017-08-17 | N | 6.9667 | N | 4 | N | N | 1.1101 | 39.4971 | 834.9297
[7 empty] | 8147 | 13154 | 1504554 | 2017-08-17 16:15 | 2017-08-17 18:30 | 135 | 11kV | 270 | 2 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 173069 Tree on OHM Excluded OMS 1504554 | August | 2017 | 2018Q1 | 2018 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Veg | 2017-08-17 | N | 135 | N | 4 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 8016 | 11287 | 1504703 | 2017-08-18 06:18 | 2017-08-18 07:00 | 42 | 11kV | 3654 | 87 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | Y | LID 173074 B Phase DOLF : 40 Amp B phase LA blown. excluded OMS 1504703 | August | 2017 | 2018Q1 | 2018 | 210:83465 | 210:83465 | ZN00210/083465 | NEWCASTLE | OH | Not Veg | 2017-08-18 | N | 42 | N | 9 | N | N | 1.1101 | 39.4971 | 2670.2354
[7 empty] | 7356 | 3022 | 1504733 | 2017-08-18 08:42 | 2017-08-18 09:40 | 58 | 11kV | 6032 | 104 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | Y | REC44790 Hansens Rd tripped, reclosed and tripped on: O/C Wind Storm | August | 2017 | 2018Q1 | 2018 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Not Veg | 2017-08-18 | Y | 58 | N | 9 | N | Y | 1.1101 | 39.4971 | 4408.0077
[7 empty] | 7278 | 1824 | 1504781 | 2017-08-18 10:32 | 2017-08-18 11:26 | 54 | 11kV | 43254 | 801 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind Strong | Y | REC35756 Bundeena tripped & locked out on: O/C Wind Storm | August | 2017 | 2018Q1 | 2018 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2017-08-18 | Y | 54 | N | 9 | N | Y | 1.1101 | 39.4971 | 31608.7474
[7 empty] | 8630 | 19244 | 1504822 | 2017-08-18 10:46 | 2017-08-18 12:22 | 96 | 11kV | 82368 | 858 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | Y | Zn9252 Janali - Pnl.21 tripped on: A & C phase O/C Wind Storm | August | 2017 | 2018Q1 | 2018 | ZN9252:PA21 | ZN9252:PA21 | ZN09252/000021 | SUTHERLAND | OH | Not Veg | 2017-08-18 | Y | 96 | N | 9 | N | Y | 1.1101 | 39.4971 | 60192.105
[7 empty] | 8057 | 11899 | 1504763 | 2017-08-18 09:54 | 2017-08-18 12:24 | 150 | 11kV | 123390 | 829 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | Y | Zn9037 Miranda - Pnl.9 tripped on: A & C phase Overcurrent Cause not ascertained Extended outage due to Port Hacking STS(new) outage. See 1506128 | August | 2017 | 2018Q1 | 2018 | ZN9037:PA9 | ZN9037:PA9 | ZN09037/000009 | SUTHERLAND | OH | Not Veg | 2017-08-18 | Y | 148.842 | N | 9 | N | Y | 1.1101 | 39.4971 | 90169.7726
[7 empty] | 7564 | 5983 | 1504969 | 2017-08-18 11:56 | 2017-08-18 13:58 | 122 | 11kV | 3294 | 27 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | Y | Zn9534 Kurnell - Pnl.18 tripped on: O/C with EFI Field EFIs: S48890 OH mains down from S48890 (Sw/B) to S9535 (Sw/A) See 1506172 1506173 | August | 2017 | 2018Q1 | 2018 | ZN9534:PA18 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2017-08-18 | Y | 122 | N | 9 | N | Y | 1.1101 | 39.4971 | 2407.158
[7 empty] | 8695 | 19971 | 1505088 | 2017-08-18 12:35 | 2017-08-18 14:17 | 102 | 11kV | 26724 | 262 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | Y | REC1126 tripped, reclosed & locked out on: O/C Wind Storm | August | 2017 | 2018Q1 | 2018 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2017-08-18 | N | 102 | N | 9 | N | N | 1.1101 | 39.4971 | 19529.111
[7 empty] | 7260 | 1438 | 1504702 | 2017-08-18 01:38 | 2017-08-18 14:25 | 767 | 11kV | 4602 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Wind Strong | Y | Tree brought down OH mains adjacent to PT13306. No protection operated, found live on ground | August | 2017 | 2018Q1 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2017-08-18 | Y | 767 | N | 9 | N | Y | 1.1101 | 39.4971 | 3363.0059
[7 empty] | 8224 | 14057 | 1504867 | 2017-08-18 11:22 | 2017-08-18 14:30 | 187.9333 | 11kV | 141325.8667 | 752 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | No Weather Impact | Y | REC40425 Kurrawyba Cadell - 11kV load side links have fallen apart on footpath phase. Tripped on SEF | August | 2017 | 2018Q1 | 2018 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2017-08-18 | Y | 187.9333 | N | 9 | N | Y | 1.1101 | 39.4971 | 103276.775
[7 empty] | 8370 | 15792 | 1504982 | 2017-08-18 12:12 | 2017-08-18 15:00 | 168 | 11kV | 336 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | Y | LID 173088 B Phase LL Lead off HV Mains Excluded OMS 1504982 | August | 2017 | 2018Q1 | 2018 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Not Veg | 2017-08-18 | N | 168 | N | 9 | N | N | 1.1101 | 39.4971 | 245.5389
[7 empty] | 8072 | 12117 | 1505236 | 2017-08-18 13:54 | 2017-08-18 15:35 | 101 | 11kV | 104059 | 1159 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Wind Strong | Y | Zn35800 Pnl.7 - Supply lost beyond AB2576. Pnl.7 de-energised by AOp to allow lineworker to Open AB2576 (Suspect defective) See 1506228 1506230 | August | 2017 | 2018Q1 | 2018 | ZN35800:PA7 | ZN35800:PA7 | ZN35800/000007 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-08-18 | N | 89.7834 | N | 9 | N | N | 1.1101 | 39.4971 | 76043.248
[7 empty] | 7550 | 5815 | 1505046 | 2017-08-18 12:25 | 2017-08-18 15:40 | 195 | 11kV | 255990 | 1492 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | Y | REC44936 Bently Rd tripped on: O/C OH mains down adj AB40343 See 1506207 1506208 | August | 2017 | 2018Q1 | 2018 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2017-08-18 | Y | 171.5751 | N | 9 | N | Y | 1.1101 | 39.4971 | 187069.9416
[7 empty] | 7539 | 5726 | 1505455 | 2017-08-18 11:40 | 2017-08-18 15:53 | 253 | 11kV | 12743 | 558 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | LID 173089 Tree blown onto mains at Vincet St. Pole FT-23113. No Protection Op Excluded OMS 1504830 | August | 2017 | 2018Q1 | 2018 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2017-08-18 | N | 22.8369 | N | 9 | N | N | 1.1101 | 39.4971 | 9312.2085
[7 empty] | 8353 | 15589 | 1505193 | 2017-08-18 13:10 | 2017-08-18 17:00 | 230 | 11kV | 41450 | 811 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | Y | Zn9118 Cronulla - Pnl.2 tripped on: A Phase O/C, Earth Fault, EFI Large tree fell on PT9616 Belair Ave. Dop removed but could not cloase HDO. SUpply restored via LV // #922 and#1120 See 1506157 1506158 | August | 2017 | 2018Q1 | 2018 | ZN9118:PA2 | ZN9118:PA2 | ZN09118/000002 | SUTHERLAND | OH | Veg | 2017-08-18 | Y | 51.1097 | N | 9 | N | Y | 1.1101 | 39.4971 | 30290.4374
[7 empty] | 8121 | 12828 | 1505159 | 2017-08-18 13:04 | 2017-08-18 17:20 | 256 | 11kV | 745228 | 3158 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | Y | Zn10999 Kogarah Pnl.12 tripped on: B & C phase IOC, EFI Field EFIs: 10139 & S10811 Cause not ascertained. Wind storm at the time See 1506181 1506182 1506183 | August | 2017 | 2018Q1 | 2018 | ZN10999:PA12 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | OH | Veg | 2017-08-18 | Y | 235.981 | N | 9 | N | Y | 1.1101 | 39.4971 | 544590.6419
[7 empty] | 8075 | 12130 | 1504898 | 2017-08-18 11:36 | 2017-08-18 17:24 | 348 | 11kV | 384958 | 1134 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | Y | Zn10990 Arncliffe - Pnl.11 tripped on: A phase IOC, reclose, lockout, EFI Field EFIs:10957 Cause not ascertained. Wind Storm at the time. See 1506179 1506180 | August | 2017 | 2018Q1 | 2018 | ZN10990:PA11 | ZN10998:PA17 | ZN10998/000017 | BAYSIDE | OH | Veg | 2017-08-18 | Y | 339.4691 | N | 9 | N | Y | 1.1101 | 39.4971 | 281315.9521
[7 empty] | 8479 | 17379 | 1506217 | 2017-08-18 12:15 | 2017-08-18 18:10 | 355 | 11kV | 8165 | 23 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | 11kV feeder from LB40866 to LB44275 interrupted to remove tree branch from OH mains. PT46693 & PT18001 interrupted | August | 2017 | 2018Q1 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2017-08-18 | Y | 355 | N | 9 | N | Y | 1.1101 | 39.4971 | 5966.7412
[7 empty] | 7649 | 6803 | 1504935 | 2017-08-18 11:52 | 2017-08-18 18:20 | 388 | 11kV | 186510 | 1770 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | Y | Zn12570 Avoca - Pnl.24 tripped on: A & C phase O/C REC made N.A at Pnl.24 due to multiple trip & recloses 11kV OH mains clashing at tee off to PT11831 Koorabel Branga See 1506531 1506530 | August | 2017 | 2018Q1 | 2018 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2017-08-18 | Y | 105.3729 | N | 9 | N | Y | 1.1101 | 39.4971 | 136296.0069
[7 empty] | 8428 | 16682 | 1505128 | 2017-08-18 12:52 | 2017-08-18 18:55 | 363 | 11kV | 13842 | 76 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | REC 48425 Kangy Angy tripped on: Earth Fault Tree branch on OH mains. See 1506194 1506195 | August | 2017 | 2018Q1 | 2018 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2017-08-18 | Y | 182.1316 | N | 9 | N | Y | 1.1101 | 39.4971 | 10115.3253
[7 empty] | 8177 | 13460 | 1505380 | 2017-08-18 14:15 | 2017-08-18 19:00 | 285 | 11kV | 203490 | 900 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | Zn10994 Mortdale - Pnl.19 tripped on: B & C phase Instantaneous O/C Tree branch on OH mains cnr Forest Rd near Old Forest Se 1506174 1506175 | August | 2017 | 2018Q1 | 2018 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Veg | 2017-08-18 | N | 226.1 | N | 9 | N | N | 1.1101 | 39.4971 | 148704.4901
[7 empty] | 7302 | 2144 | 1505808 | 2017-08-18 17:53 | 2017-08-18 19:15 | 82 | 11kV | 10414 | 127 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | Y | Ex Pnl.1 West Gosford - AB43847 Bond burnt off | August | 2017 | 2018Q1 | 2018 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2017-08-18 | Y | 82 | N | 9 | N | Y | 1.1101 | 39.4971 | 7610.244
[7 empty] | 7461 | 4814 | 1505524 | 2017-08-18 15:12 | 2017-08-18 21:25 | 373 | 11kV | 2554 | 47 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | LID 173090 2 fault operations 3 phase Overcurrent; Intellirupter branch brought 11kv mains down between OR-70205 & OR-70255. Repaired under AP Excluded OMS 1505565. | August | 2017 | 2018Q1 | 2018 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2017-08-18 | N | 54.3404 | N | 9 | N | N | 1.1101 | 39.4971 | 1866.3879
[7 empty] | 7300 | 2124 | 1505828 | 2017-08-18 13:38 | 2017-08-18 23:01 | 563 | 11kV | 570279 | 1535 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | Y | Zn10991 Blakehurst - Pnl.1 tripped to lockout on: C phase O/C Field EFIs: NIL 11kV Bond failed on cnr Carwar Ave and Allawah Ave on Pole KO 16551 (between AB31134 to S1028 to S10137 tee PT10934) See 1506169 1506170 | August | 2017 | 2018Q1 | 2018 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2017-08-18 | N | 371.5173 | N | 9 | N | N | 1.1101 | 39.4971 | 416743.0728
[7 empty] | 7856 | 9388 | 1504945 | 2017-08-18 12:48 | 2017-08-19 02:00 | 792 | 11kV | 69696 | 88 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Wind Strong | Y | At PT 9527 Grevillea Gr defective tail or transformer supply C phase LV ONLY ISOLATED restored via LV// LK# 808,#806,#1211 | August | 2017 | 2018Q1 | 2018 | ZN9245:PA4 | ZN9245:PA4 | ZN09245/000004 | SUTHERLAND | OH | Not Veg | 2017-08-18 | Y | 792 | N | 9 | N | Y | 1.1101 | 39.4971 | 50931.7811
[7 empty] | 8521 | 17835 | 1505944 | 2017-08-19 01:07 | 2017-08-19 02:30 | 83 | 11kV | 57602 | 694 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Ex Pnl.3 Charmhaven Zn - Bond off beyond AB42481 on pole TO134 | August | 2017 | 2018Q1 | 2018 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Not Veg | 2017-08-19 | N | 83 | N | 3 | N | N | 1.1101 | 39.4971 | 42093.8426
[7 empty] | 7552 | 5844 | 1505936 | 2017-08-18 23:05 | 2017-08-19 03:35 | 270 | 11kV | 18360 | 68 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | Ex Pnl.10 Terrey Hills - USL24299 isolated Tree branch on mains i gully beyond USL24299 | August | 2017 | 2018Q1 | 2018 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2017-08-18 | N | 270 | N | 9 | N | N | 1.1101 | 39.4971 | 13416.9465
[7 empty] | 7485 | 5131 | 1505843 | 2017-08-18 17:21 | 2017-08-19 07:40 | 859 | 11kV | 12026 | 14 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Wind Strong | Y | PT13767 Toomeys Taylors 0.3 Middle and Footpath phase HDO operated Evidence of tree branches hitting bottom of HDOS See 1506212 | August | 2017 | 2018Q1 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2017-08-18 | Y | 859 | N | 9 | N | Y | 1.1101 | 39.4971 | 8788.2461
[7 empty] | 8584 | 18624 | 1505239 | 2017-08-18 13:29 | 2017-08-19 12:25 | 1376 | 11kV | 23286 | 106 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | Y | REC44602 Ourimbah Creek Rd tripped on: SEF 11kV OH mains down at pole OU661 between PT61456 and PT14453 Repaired SAT 19/8/17 See 1506565 1506566 | August | 2017 | 2018Q1 | 2018 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2017-08-18 | Y | 219.6792 | N | 9 | N | Y | 1.1101 | 39.4971 | 17016.722
[7 empty] | 7991 | 10914 | 1506071 | 2017-08-19 10:36 | 2017-08-19 13:05 | 149 | 11kV | 32571 | 469 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Ex Zn14891 Wyong section of Pa12 "Cedar NorthCott" HV bond burnt off 4 bays beyond recloser 48838 Yarramalong Maitland 1.2 and tee off to PT12717 Henry Yarra See 1506509 ex 1506071,4 | August | 2017 | 2018Q1 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2017-08-19 | N | 69.4478 | N | 3 | N | N | 1.1101 | 39.4971 | 23801.9261
[7 empty] | 7453 | 4710 | 1505973 | 2017-08-19 07:18 | 2017-08-19 16:00 | 522 | 11kV | 17483.9167 | 55 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @ZN9118 Cronulla exiting Panel 17 labelled "Wilga Rd" PT9420 Allambie Rd Remarks: interrupted for safety reasons. Line worker to remove large branch | August | 2017 | 2018Q1 | 2018 | ZN9118:PA17 | ZN9118:PA17 | ZN09118/000017 | SUTHERLAND | OH | Veg | 2017-08-19 | N | 317.8894 | N | 3 | N | N | 1.1101 | 39.4971 | 12776.7306
[7 empty] | 7617 | 6457 | 1506384 | 2017-08-20 18:44 | 2017-08-20 21:20 | 156 | 11kV | 39735 | 275 | HV | Burnt Contacts | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 173094 2 fault operationsw Overcurrent, Instantaneous Overcurrent links 40948 found burnt up need repair/replacement, sw 48067 was closed from control room and received control fail alarm however staff found sw 48067 to be closed on site. please investigate. fdr restored via abs 40804 from sw 48066 Excluded oms 1506384 | August | 2017 | 2018Q1 | 2018 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2017-08-20 | N | 144.4909 | N | 4 | N | N | 1.1101 | 39.4971 | 29037.166
[7 empty] | 7346 | 2864 | 1506392 | 2017-08-20 20:32 | 2017-08-20 21:26 | 54 | 11kV | 84354 | 1715 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn9252 Jannali Panel 27 "Toronto Buller" Relays: Sel and protection trip Signals: 11kv trip Field EFI's: Nil Remarks: Oh down. 11kv OH mains down in Carvers Rd | August | 2017 | 2018Q1 | 2018 | ZN9252:PA27 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | OH | Not Veg | 2017-08-20 | N | 49.186 | N | 4 | N | N | 1.1101 | 39.4971 | 61643.4152
[7 empty] | 7566 | 5991 | 1506354 | 2017-08-20 20:40 | 2017-08-20 21:26 | 46 | 11kV | 30176 | 656 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa33 RE50407 The Scenice Bounty tripped, reclosed and locked out on Overcurrent trip Cause: Tree Branch found on 11kv OH adjacent PT13664 See 1506393 ex 1506354,98 | August | 2017 | 2018Q1 | 2018 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2017-08-20 | N | 46 | N | 4 | N | N | 1.1101 | 39.4971 | 22051.7308
[7 empty] | 7835 | 9185 | 1506401 | 2017-08-20 21:06 | 2017-08-20 22:30 | 84 | 11kV | 98774 | 1211 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Panel 19 "Corella Enterprise etc" CB tripped on: Signals: 11kv trip Relays: Earth Fault, EFI EFI's: UGOH in bundilla ave nr Karen Ave Cause: not ascertained Patrolled and nothing found See 1506520,1 ex 1506401 | August | 2017 | 2018Q1 | 2018 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2017-08-20 | N | 81.564 | N | 4 | N | N | 1.1101 | 39.4971 | 72181.1259
[7 empty] | 7675 | 7066 | 1506416 | 2017-08-21 03:37 | 2017-08-21 04:47 | 70 | 11kV | 82390 | 1177 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn965 Pennant Hills Panel 3 fdr tripped on Relays: Trip Flag, EFI Signals: Zone Earth, Tx 3 Group Earth EFI: S4440 S4945 Cause: Possum on UGOH to PT1069 See 1506416 ex 1506418 | August | 2017 | 2018Q1 | 2018 | ZN965:PA3 | ZN965:PA3 | ZN00965/000003 | HORNSBY | OH | Not Veg | 2017-08-21 | N | 70 | N | 3 | N | N | 1.1101 | 39.4971 | 60208.1819
[7 empty] | 8685 | 19856 | 1506496 | 2017-08-21 11:40 | 2017-08-21 12:25 | 45 | 11kV | 135 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 173104 Repair Live Line Lead Excluded OMS 1506496 | August | 2017 | 2018Q1 | 2018 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2017-08-21 | N | 45 | N | 3 | N | N | 1.1101 | 39.4971 | 98.654
[7 empty] | 7776 | 8398 | 1506796 | 2017-08-21 19:01 | 2017-08-21 23:15 | 254 | 11kV | 97274 | 1302 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | Zn15012 Killarney Pa8 "Forestville" tripped on Relays: B Phase Earth Fault, EFI, Fault Check and lock out Signals: 11kv trip EFI'S: S16789 S16846 Cause: Possum on 11kv UGOH to S16031 currie rd Cnr of Maxwell Pde and Currie Rd. Pa8 did not close remotely or locally. DOp was asked to rack CB 8 down then back up again S16801 Forest War Rabbett Dist 3 "Forestway South OH" ABC phase fuse blown due to LV// during feeder trip See 1506982,3 LV// 1506984,5 Ex 1506796,802,4,5,8,10,11,12 | August | 2017 | 2018Q1 | 2018 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Not Veg | 2017-08-21 | N | 74.7112 | N | 3 | N | N | 1.1101 | 39.4971 | 71084.9701
[7 empty] | 7722 | 7718 | 1506836 | 2017-08-22 00:47 | 2017-08-22 01:26 | 38.8167 | 11kV | 78215.5833 | 2015 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North Pa3 "Jackson White" tripped on: Relays: EF, EFI Signals: 11kv trip, Tx1, Group Earth Cause: Possum at LB61276 See 1506836 ex 1506838 | August | 2017 | 2018Q1 | 2018 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2017-08-22 | N | 38.8167 | N | 3 | N | N | 1.1101 | 39.4971 | 57157.6413
[7 empty] | 7363 | 3140 | 1506911 | 2017-08-22 10:35 | 2017-08-22 13:12 | 157.05 | 11kV | 6124.95 | 39 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 173120 Replace insulators pole AH-42163 | August | 2017 | 2018Q1 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2017-08-22 | N | 157.05 | N | 3 | N | N | 1.1101 | 39.4971 | 4475.9328
[7 empty] | 8450 | 17014 | 1507079 | 2017-08-22 22:25 | 2017-08-22 23:54 | 89 | 11kV | 24068 | 274 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn80 Chatswood - Pnl.36 tripped on Translay with EFI @ S7712 (Sw/A) tripped on Translay Field EFIs: S47513, S4059, S7588, S47852 UG cable fault between S47513 (Sw/B) and S4059 (Sw/A) See 1507169 1507171 | August | 2017 | 2018Q1 | 2018 | ZN80:PA36 | ZN80:PA36 | ZN00080/000036 | WILLOUGHBY | UG | Not Veg | 2017-08-22 | N | 87.8394 | N | 3 | N | N | 1.1101 | 39.4971 | 17588.1845
[7 empty] | 8413 | 16510 | 1507136 | 2017-08-23 09:42 | 2017-08-23 12:15 | 153 | 11kV | 3366 | 22 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa12 "Yarramalong" recloser has tripped RE48813 Yarramalong Boyds 3.7 Relays: SEF Abnormal: LB40899 closed, LB42548 Open, PT13249 & PT18473 Part of planned interruption Cause: Restricted Operator was performing final isolation for DAROS job 409524A/1 by opening LV41096 at around this time, he had difficulty operating switch. DOp had been requested to make reclosing N/A @ IR48813 Yarramalong Boyds 3.7 this was achieved by applying Hot line tag. HV patrolled clear between REC & Job site, job isolation also patrolled clear. See 1508273 ex 1507136 | August | 2017 | 2018Q1 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2017-08-23 | N | 153 | N | 6 | N | N | 1.1101 | 39.4971 | 2459.7735
[7 empty] | 7219 | 689 | 1507216 | 2017-08-23 13:29 | 2017-08-23 13:34 | 5 | 11kV | 30 | 6 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173138 Outage on sub 1067 to remove birds nest | August | 2017 | 2018Q1 | 2018 | 224:80329 | 224:80329 | ZN00224/080329 | LAKE MACQUARIE | OH | Not Veg | 2017-08-23 | N | 5 | N | 6 | N | N | 1.1101 | 39.4971 | 21.9231
[7 empty] | 7514 | 5533 | 1507182 | 2017-08-23 12:07 | 2017-08-23 16:30 | 263 | 11kV | 81683 | 655 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn630 Mascot - pnl.15 tripped on A, B & C phase O/C, E/F with EFI Field EFIs: S50284 , S6965, S6966, S49071, S8070 Abnormal: Panel 31 to S35284 (Sw/A) out for D/R 410083 with S49071 (Sw/B) closed UG cable fault between S6458 (Sw/B) and S5937 (Sw/A) and S8070 (Sw/A) See 1507481 1407483 1507484 | August | 2017 | 2018Q1 | 2018 | ZN630:PA31 | ZN630:PA31 | ZN00630/000031 | BAYSIDE | UG | Not Veg | 2017-08-23 | N | 124.7069 | N | 6 | N | N | 1.1101 | 39.4971 | 59691.5272
[7 empty] | 7766 | 8258 | 1507331 | 2017-08-23 21:58 | 2017-08-24 01:20 | 202 | 11kV | 48434 | 292 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of pa12 "Yarramalong" tripped RE48813 Yarramalong Boyds 3.7 Tree branch contact LV mains at PT14274. possibly clashed HV mains due to shock load. LW to inspect See 1508278,80,1,2,3,4 ex 1507331 | August | 2017 | 2018Q1 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2017-08-23 | N | 165.8699 | N | 6 | N | N | 1.1101 | 39.4971 | 35394.1386
[7 empty] | 8509 | 17699 | 1507345 | 2017-08-23 22:59 | 2017-08-24 02:00 | 181 | 11kV | 11222 | 62 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa3 RE46895 Wise Ferry Ironbank Cause: Not ascertained. Feeder Patrolled | August | 2017 | 2018Q1 | 2018 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2017-08-23 | N | 181 | N | 6 | N | N | 1.1101 | 39.4971 | 8200.7066
[7 empty] | 8615 | 19079 | 1507350 | 2017-08-24 03:23 | 2017-08-24 04:09 | 46 | 11kV | 88228 | 1918 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 173147 2 fault operations B & C Phase Overcurrent see report 173146 dead possum pole IV-32099 Excluded oms 1507350 | August | 2017 | 2018Q1 | 2018 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2017-08-24 | N | 46 | N | 2 | N | N | 1.1101 | 39.4971 | 64474.4201
[7 empty] | 7720 | 7680 | 1507383 | 2017-08-24 07:58 | 2017-08-24 11:50 | 232 | 11kV | 62544 | 292 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa12 "Yarramlong" RE48813 Yarramalong Boyds 3.7 Relays: SEF trip (Trip currents 8,22,25) Cause: Protection Malfunction Suspect defective IR48813 Yarramalong Boyds 3.7 Feeder patrolled with no obvious cause. Recloser bypassed See 1508288 ex 1507383 | August | 2017 | 2018Q1 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | Unknown | Not Veg | 2017-08-24 | N | 214.1918 | N | 2 | N | N | 1.1101 | 39.4971 | 45705.3105
[7 empty] | 7277 | 1820 | 1507326 | 2017-08-23 20:08 | 2017-08-24 15:30 | 1162 | 11kV | 48600 | 50 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa13 "Brush Rd" isolated for safety from RE42086 North Lisarow to AB44309 inluding 4 PT's Emergency replacement to PT11108 Corrara Pildra See 1507329 1508314 ex 1507426 | August | 2017 | 2018Q1 | 2018 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2017-08-23 | N | 972 | N | 6 | N | N | 1.1101 | 39.4971 | 35515.4465
[7 empty] | 7191 | 179 | 1507681 | 2017-08-25 10:37 | 2017-08-25 12:30 | 113 | 11kV | 226 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173169 A Phase DOLF : 16 Amp Excluded OMS 1507681 | August | 2017 | 2018Q1 | 2018 | 512:48048 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2017-08-25 | N | 113 | N | 5 | N | N | 1.1101 | 39.4971 | 165.1541
[7 empty] | 8687 | 19873 | 1507624 | 2017-08-25 09:00 | 2017-08-25 12:50 | 230 | 11kV | 460 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 173174 A Phase live line lead broken away Excluded oms 1507624 | August | 2017 | 2018Q1 | 2018 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2017-08-25 | N | 230 | N | 5 | N | N | 1.1101 | 39.4971 | 336.1544
[7 empty] | 8660 | 19617 | 1507689 | 2017-08-25 11:20 | 2017-08-25 15:25 | 245 | 11kV | 2900 | 12 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa21 "Virginia Rd" fdr Interrupted for safety from AB44996 to AB444422 tee PT12970 & PT11019 Abnormal: RE45070 sparks is closed, AB44422 is open Cause: interrutped for safety reasons. Interrutped for emergency repairs to condemned pole WY408 outside 79 Railway Rd Warnervale DAROS Job 412158A See 1507698,9 | August | 2017 | 2018Q1 | 2018 | ZN14891:PA21 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2017-08-25 | N | 241.6667 | N | 5 | N | N | 1.1101 | 39.4971 | 2119.2345
[7 empty] | 7314 | 2430 | 1507731 | 2017-08-25 13:51 | 2017-08-25 15:40 | 109 | 11kV | 96765 | 1081 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.21 tripped on: IOC A & B phase Tree branch on 11kV OH mains cauing damage. | August | 2017 | 2018Q1 | 2018 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Veg | 2017-08-25 | N | 89.5143 | N | 5 | N | N | 1.1101 | 39.4971 | 70713.0079
[7 empty] | 8576 | 18558 | 1507696 | 2017-08-25 13:00 | 2017-08-25 22:18 | 558 | 11kV | 558 | 1 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 173179 Main off pin on croosarm at pole IV-60446 Section 25123/9809/9811/21445 isolated for repair Excluded OMS 1507696 | August | 2017 | 2018Q1 | 2018 | 206:34432 | 206:34432 | ZN00206/034432 | LAKE MACQUARIE | OH | Not Veg | 2017-08-25 | N | 558 | N | 5 | N | N | 1.1101 | 39.4971 | 407.7699
[7 empty] | 8393 | 16230 | 1507980 | 2017-08-27 11:17 | 2017-08-27 13:50 | 153 | 11kV | 90344 | 1027 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14143 Somersby Pa5 "Wisemans Sulo" opened on B & C phase OC with EFI No1 Tx Group Earth EFI's: S18048 CP45441 S65140 S14863 S18785 S14471 S14413 S 14530 S14532 S14398 S14300 S14223 Cause: UG cable Fault from Zn14300 Langford Truscott to S14222 tee S14226 See 1508596,7,8 ex 1507980 | August | 2017 | 2018Q1 | 2018 | ZN14143:PA5 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | UG | Not Veg | 2017-08-27 | N | 87.9688 | N | 4 | N | N | 1.1101 | 39.4971 | 66020.7305
[7 empty] | 8266 | 14553 | 1508023 | 2017-08-27 16:42 | 2017-08-27 18:01 | 79 | 11kV | 122134 | 1546 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn1193 Lindfield Panel 26 tripped reclosed tripped and locked out on Relays: B and C phase OC and EF Field EFI's - Nil Cause: Branch on mains, removed by DOp adjacent to PT25 1508023 1508028 1508029 | August | 2017 | 2018Q1 | 2018 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | OH | Veg | 2017-08-27 | N | 79 | N | 4 | N | N | 1.1101 | 39.4971 | 89251.9249
[7 empty] | 7416 | 4045 | 1508019 | 2017-08-27 18:07 | 2017-08-27 19:00 | 53 | 11kV | 7293 | 157 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 173185 A & C phase ABS 43397 Burning up. Left OPEN. Needs to be replaced. Small grass fire in vivcinity of ABS approx 30m sq. Excluded OMS 1508019 | August | 2017 | 2018Q1 | 2018 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2017-08-27 | N | 46.4522 | N | 4 | N | N | 1.1101 | 39.4971 | 5329.5093
[7 empty] | 7221 | 737 | 1508065 | 2017-08-27 19:25 | 2017-08-27 20:40 | 75 | 11kV | 9075 | 121 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 173186 B Phase DOLF : 50 Amp Fuse fatigue Excluded OMS 1508065 | August | 2017 | 2018Q1 | 2018 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Not Veg | 2017-08-27 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 6631.7423
[7 empty] | 8039 | 11539 | 1508083 | 2017-08-28 06:56 | 2017-08-28 12:15 | 319 | 11kV | 225042 | 2001 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn931 Darlinghurst - Pnl.10 tripped on: Earth Fault, IOC B phase, EFI Field EFIs: S48459, S7939, CP603, S5224, S830 & S36098 UG cable fault from S36098 to S5998 See 1508812 1508814 1508815 1508102 1508094 | August | 2017 | 2018Q1 | 2018 | ZN931:PA10 | ZN931:PA10 | ZN00931/000010 | SYDNEY | UG | Not Veg | 2017-08-28 | N | 112.4648 | N | 2 | N | N | 1.1101 | 39.4971 | 164454.056
[7 empty] | 7658 | 6888 | 1508206 | 2017-08-28 11:53 | 2017-08-28 15:30 | 217 | 11kV | 29512 | 136 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S3982 Blanch Cosgrove Ex S690 Campsie Panel 24 "eighth Fourth" the 63A HV fuse blew Remarks: OH down. B phase 63A OQFRN HV fuse operated | August | 2017 | 2018Q1 | 2018 | ZN690:PA24 | ZN4853:PA26 | ZN04853/000026 | STRATHFIELD | OH | Not Veg | 2017-08-28 | N | 217 | N | 2 | N | N | 1.1101 | 39.4971 | 21566.4991
[7 empty] | 7482 | 5106 | 1508382 | 2017-08-29 02:23 | 2017-08-29 04:22 | 119 | 11kV | 139670 | 1326 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman Pa43 fdr tripped on Relays: C phase o/c timmed, EFI, Fault check EFI's: S65259 S5188 S5508 S7950 S36129 S8065 S8066 Signals: 11kv trip 11kv fdr fault between S6771:B to S546:A Electronic EFI's not indicating at S47402 S46998 S35976 Note: No EFI at S6771 See 1508602,3,4 ex 1508382,1508416 | August | 2017 | 2018Q1 | 2018 | ZN180:PA43 | ZN180:PA43 | ZN00180/000043 | WILLOUGHBY | UG | Not Veg | 2017-08-29 | N | 105.3318 | N | 3 | N | N | 1.1101 | 39.4971 | 102066.7164
[7 empty] | 7575 | 6075 | 1508608 | 2017-08-29 16:48 | 2017-08-29 18:05 | 77 | 11kV | 58905 | 765 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S15008 Harbord Panel 7 No relay operations HV bond HR beyond LB23632 See OMS 1508810 1508608 | August | 2017 | 2018Q1 | 2018 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2017-08-29 | N | 77 | N | 3 | N | N | 1.1101 | 39.4971 | 43046.0366
[7 empty] | 8464 | 17220 | 1508663 | 2017-08-30 00:26 | 2017-08-30 02:19 | 113 | 11kV | 163102 | 1484 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn931 Darlinghurst - Pnl.25 tripped on: Earth Fault with EFI Field EFIs all down S7278 UG cable fault between S4278 (Sw/A) and S1565 (Sw/A) See 1508819 1508820 | August | 2017 | 2018Q1 | 2018 | ZN931:PA25 | ZN931:PA25 | ZN00931/000025 | SYDNEY | UG | Not Veg | 2017-08-30 | N | 109.907 | N | 3 | N | N | 1.1101 | 39.4971 | 119190.1309
[7 empty] | 7818 | 8910 | 1508657 | 2017-08-29 21:38 | 2017-08-30 08:22 | 644 | 11kV | 15820 | 77 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn180 Mosman Panel 17 Hornsell Field Rec1014 Suakin Drive tripped on O/C Cause: Flying fox shorted across 11kV mains on tee to S2113 Chowder Bay. Dop unable to access area due to overgrown bush. Lineworker crew needed to cut across track to remove flying fox See OMS 1508846 1508852 1508657 1508661 | August | 2017 | 2018Q1 | 2018 | ZN180:PA17 | ZN180:PA17 | ZN00180/000017 | MOSMAN | OH | Not Veg | 2017-08-29 | N | 205.4545 | N | 3 | N | N | 1.1101 | 39.4971 | 11560.7894
[7 empty] | 7559 | 5920 | 1508928 | 2017-08-30 21:34 | 2017-08-30 23:00 | 86 | 11kV | 84108 | 978 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 46 tripped on Relays: A B and C phase of OC Field EFI's - S5848 Signals: 11kV Trip Cause: Dead Possum found at the base of PT704. Verney Chelsea - Panel 46 is shooting through See OMS 1508928 1508930 1508929 | August | 2017 | 2018Q1 | 2018 | ZN965:PA46 | ZN965:PA46 | ZN00965/000046 | HORNSBY | OH | Not Veg | 2017-08-30 | N | 86 | N | 3 | N | N | 1.1101 | 39.4971 | 61463.6456
[7 empty] | 7781 | 8476 | 1508667 | 2017-08-30 04:39 | 2017-08-31 02:30 | 1311 | 11kV | 316158 | 1366 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford Pa1 "Dog Trap Rd" RE44936 Betnley Rd tripped on Overcurrent Abnormal: USL43847 open & Def, AB44606 closed Cause: Vehicle Hit Pole See 1509233,5 ex 1508667,90 | August | 2017 | 2018Q1 | 2018 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2017-08-30 | N | 231.448 | N | 3 | N | N | 1.1101 | 39.4971 | 231038.9413
[7 empty] | 8430 | 16712 | 1508939 | 2017-08-31 06:16 | 2017-08-31 10:00 | 224 | 11kV | 10528 | 47 | HV | Animal Bird | Animal | Fuse | Unplanned | No Weather Impact | N | Ex Zn15001 Brookvale section of pa11 CP46904 Old Pittwwater Cross because 71 amp HV fuses operated Animals/Birds Old Pittwater See 1509240 ex 1508939,54,9 | August | 2017 | 2018Q1 | 2018 | ZN15001:PA11 | ZN15001:PA11 | ZN15001/000011 | NORTHERN BEACHES | OH | Not Veg | 2017-08-31 | N | 224 | N | 2 | N | N | 1.1101 | 39.4971 | 7693.5519
[7 empty] | 7945 | 10347 | 1508994 | 2017-08-31 10:39 | 2017-08-31 10:58 | 19 | 11kV | 21147 | 1113 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | SAO410471 When restoring the above abnormal switching S77001 Albany York Sw/A was found to be Open Abnormal: S11142:A Open LB41684 closed Staff Error. Abnormal Switching See 1509245 ex 1508994 | August | 2017 | 2018Q1 | 2018 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | Unknown | Not Veg | 2017-08-31 | N | 19 | N | 2 | N | N | 1.1101 | 39.4971 | 15453.6039
[7 empty] | 8278 | 14706 | 1509161 | 2017-09-01 06:49 | 2017-09-01 08:35 | 106 | 11kV | 862 | 10 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35900 Potts Hill Panel 11 "Worth Muir No 2" tripped on Relays: E/F, O/C and EFI Signals: 11kv trip, Tx 1 group earth Remarks: 11kv UG feeder fault from S64422 Worth Beaufort to Sub 77514 Hume Tennyson No2 to Sub 2611 Hume Shellcote No.1 | September | 2017 | 2018Q1 | 2018 | ZN35900:PA11 | ZN35900:PA11 | ZN35900/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-09-01 | N | 86.2 | N | 1 | N | N | 1.1101 | 39.4971 | 629.9242
[7 empty] | 7810 | 8849 | 1509474 | 2017-09-03 06:22 | 2017-09-03 08:00 | 98 | 11kV | 2744 | 28 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 173260 B Phase DOLF : 20 Amp B Phase fuse carrier at line fuse 40534 had burnt up, carrier and fuse repalced at 8am. Excluded OMS 1509474 | September | 2017 | 2018Q1 | 2018 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2017-09-03 | N | 98 | N | 5 | N | N | 1.1101 | 39.4971 | 2005.2343
[7 empty] | 8327 | 15243 | 1509514 | 2017-09-03 12:09 | 2017-09-03 14:18 | 129 | 11kV | 111198 | 862 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | iR63273 Sutherland Mitchell tripped on: O/C trip Tree branch on mains outside 12 Mulyan St Como | September | 2017 | 2018Q1 | 2018 | ZN9252:PA24 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Veg | 2017-09-03 | N | 129 | N | 5 | N | N | 1.1101 | 39.4971 | 81260.2186
[7 empty] | 8358 | 15635 | 1509549 | 2017-09-03 14:26 | 2017-09-03 17:30 | 184 | 11kV | 184 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Wind Strong | N | At S2835 Burwood 132kv Substation Zone Earth and Tx3 Group earth were received. Relays: - Panel 41 EFI Signals: - Zone earth. Tx3 Group Earth Field EFis: S64159, S7528, S39001 At S4100 Beresford Coventry 11kv HV fuses blown B phase OHFMA 80A Remarks: transformer failure. S4100 Beresford Coventry Tx failed. Possible grading issue | September | 2017 | 2018Q1 | 2018 | ZN2835:PA41 | ZN2835:PA41 | ZN02835/000041 | STRATHFIELD | UG | Not Veg | 2017-09-03 | N | 184 | N | 5 | N | N | 1.1101 | 39.4971 | 134.4618
[7 empty] | 8419 | 16573 | 1509555 | 2017-09-03 16:57 | 2017-09-03 18:38 | 101 | 11kV | 31596 | 322 | HV | Animal Bird | Animal | O/H Link | Unplanned | Wind Strong | N | LID 173263 2 fault operations B & C Phase 2 MAGPIES ON MAINS AT POLE DR-40145. Excluded OMS 1509555 & 1509556. | September | 2017 | 2018Q1 | 2018 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2017-09-03 | N | 98.1242 | N | 5 | N | N | 1.1101 | 39.4971 | 23089.4249
[7 empty] | 8545 | 18161 | 1509567 | 2017-09-03 18:28 | 2017-09-03 22:30 | 242 | 11kV | 30544 | 162 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 173264 3 fault operations C phase Overcurrent Magpie & wire removed from sub 72978. Excluded OMS REPORT NO 1509567. | September | 2017 | 2018Q1 | 2018 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2017-09-03 | N | 188.5432 | N | 5 | N | N | 1.1101 | 39.4971 | 22320.6543
[7 empty] | 7637 | 6690 | 1509641 | 2017-09-04 09:17 | 2017-09-04 11:00 | 103 | 11kV | 116088 | 1140 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 Matraville - Pnl.20 tripped on: C phase O/C and E/F Field EFI down @ S1170 UG cable fault between S1170 (Sw/B) and S7934 (Sw/A) See 1509960 1509961 | September | 2017 | 2018Q1 | 2018 | ZN1788:PA20 | ZN1788:PA61 | ZN01788/000061 | RANDWICK | UG | Not Veg | 2017-09-04 | N | 101.8316 | N | 3 | N | N | 1.1101 | 39.4971 | 84833.6864
[7 empty] | 8206 | 13814 | 1509621 | 2017-09-04 08:57 | 2017-09-04 11:50 | 173 | 11kV | 346 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173277 Single phase DOLF : 10 Amp Excluded OMS 1509621 | September | 2017 | 2018Q1 | 2018 | 228:7490 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Veg | 2017-09-04 | N | 173 | N | 3 | N | N | 1.1101 | 39.4971 | 252.8466
[7 empty] | 7262 | 1528 | 1509731 | 2017-09-04 12:41 | 2017-09-04 13:56 | 75 | 11kV | 117870 | 1582 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 Matraville - Pnl.17 tripped on: Earth Fault Field EFIs S4631 S768 S6061 UG cable fault between S768 (Sw/B) and S6061 (Sw/A) See 1509962 1509963 | September | 2017 | 2018Q1 | 2018 | ZN1788:PA17 | ZN1788:PA17 | ZN01788/000017 | BAYSIDE | UG | Not Veg | 2017-09-04 | N | 74.507 | N | 3 | N | N | 1.1101 | 39.4971 | 86135.9194
[7 empty] | 8648 | 19457 | 1509917 | 2017-09-05 08:12 | 2017-09-05 14:15 | 363 | 11kV | 2541 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 173294 A & B phase DOLF : 31 Amp Excluded OMS 1509917 | September | 2017 | 2018Q1 | 2018 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2017-09-05 | N | 363 | N | 3 | N | N | 1.1101 | 39.4971 | 1856.8879
[7 empty] | 7918 | 10105 | 1510033 | 2017-09-05 12:01 | 2017-09-05 20:28 | 507 | 11kV | 144472 | 1413 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S2635 Epping the 11kV panel 57 tripped, reclosed, tripped and locked out on Relays: IOC, B phase earth fault Signals: 11kV trip Cause: Tree hit HV and LV network affecting PT46301 and PT2406 High into Low See OMS 1510295 1510166 1510299 1510300 1510033 1510085 1510168 1510036 1510038 1510043 Based on customer calls - suspect S48151#1 was in parallel with Epping Pa57 during interruption | September | 2017 | 2018Q1 | 2018 | ZN2635:PA57 | ZN2635:PA57 | ZN02635/000057 | PARRAMATTA | OH | Veg | 2017-09-05 | N | 102.2449 | N | 3 | N | N | 1.1101 | 39.4971 | 105575.8764
[7 empty] | 8560 | 18348 | 1510213 | 2017-09-05 23:53 | 2017-09-06 01:15 | 82 | 11kV | 72453 | 1059 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Panel 17 fdr tripped to lock out x 2 Relays: IOC, EFI, fault check EFI's: Nil Cause: Frontline Feeder fault from Zn12610 Long Jetty Pa17 to LK4399 tee PT11021. Feeder isolated and earthed at Zone only with switching tag See 1511272,3 ex 1510213 | September | 2017 | 2018Q1 | 2018 | ZN12610:PA17 | ZN12610:PA17 | ZN12610/000017 | CENTRAL COAST | UG | Not Veg | 2017-09-05 | N | 68.4164 | N | 3 | N | N | 1.1101 | 39.4971 | 52946.5154
[7 empty] | 8225 | 14058 | 1510281 | 2017-09-06 09:58 | 2017-09-06 11:31 | 93 | 11kV | 558 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Bond burnt off centre phase @ 11kv AB24. Section of 11kv Panel No.11 "S.7614, S.5013' feeder @ ZN1290 Leightonfield Abnormal: Load relief for section of Panel 12 DMA: Sw/A open @ S.7614 Biloela Gurr No.2. LB 145 closed Remarks: Bond burnt off centre phase @ 11kv AB24 | September | 2017 | 2018Q1 | 2018 | ZN1290:PA11 | ZN1290:PA11 | ZN01290/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-09-06 | N | 93 | N | 1 | N | N | 1.1101 | 39.4971 | 407.7699
[7 empty] | 7632 | 6649 | 1510449 | 2017-09-07 00:31 | 2017-09-07 15:00 | 869 | 11kV | 219756 | 1373 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At S1673 Turramurra 11kV Panel 11 tripped on Relays: A phase oc, fault check, EFI Signals: 11kV trip, TX2 Group Earth Cause: S8642 Pacific Ada has suffered irreparable fire damage 1510700 1510701 1501702 1510449 41510454 | September | 2017 | 2018Q1 | 2018 | ZN1673:PA1 | ZN1673:PA1 | ZN01673/000001 | KU-RING-GAI | UG | Not Veg | 2017-09-07 | N | 160.0554 | N | 3 | N | N | 1.1101 | 39.4971 | 160591.2031
[7 empty] | 8271 | 14597 | 1510564 | 2017-09-07 14:52 | 2017-09-07 15:50 | 58 | 11kV | 4814 | 83 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 173329 A Phase DOLF : 40 Amp Blown DOLF at sub. DOp also found LV fuse assy broken. Sub interconnected & assy replaced under AP Excluded OMS 1510564. | September | 2017 | 2018Q1 | 2018 | 258:80785 | 258:80785 | ZN00258/080785 | NEWCASTLE | OH | Not Veg | 2017-09-07 | N | 58 | N | 3 | N | N | 1.1101 | 39.4971 | 3517.9292
[7 empty] | 7464 | 4885 | 1510647 | 2017-09-07 22:09 | 2017-09-07 23:40 | 91 | 11kV | 105014 | 1154 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn3154 St Ives Panel 5 tripped and locked out on Relays: E/F IOC and Timed C phase, EFI, Timing Cause: 11kV UG cable fault in feeder section from S3154 St Ives to SWA @ S4263 Collins Killeaton | September | 2017 | 2018Q1 | 2018 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | UG | Not Veg | 2017-09-07 | N | 91 | N | 3 | N | N | 1.1101 | 39.4971 | 76741.1338
[7 empty] | 7561 | 5959 | 1510616 | 2017-09-08 18:31 | 2017-09-08 18:43 | 12 | 11kV | 3316 | 1017 | HV | Arcing | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 173330 Fdr 31414 interupted for safety due to arcing B phase switch blade. Excluded OMS 1510616 | September | 2017 | 2018Q1 | 2018 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2017-09-08 | N | 3.2606 | N | 2 | N | N | 1.1101 | 39.4971 | 2423.235
[7 empty] | 7584 | 6125 | 1510801 | 2017-09-08 17:56 | 2017-09-08 20:22 | 146.2 | 11kV | 6725.2 | 46 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ex Zn12630 Peats Ridge section of pa10 centre phase bond burnt off adjacent to LK40108 See 1510801 ex 1510817,8 CC1: 22-"Refer to SOp" | September | 2017 | 2018Q1 | 2018 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2017-09-08 | N | 146.2 | N | 2 | N | N | 1.1101 | 39.4971 | 4914.5778
[7 empty] | 7778 | 8420 | 1510830 | 2017-09-09 03:59 | 2017-09-09 05:30 | 91 | 11kV | 105469 | 1159 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn3154 St Ives Panel 18 Tripped on Signals: 11kV Trip, TX3 Group Earth Relays: A phase OC and IOC, Earth Fault and EFI Cause: Possum on PT1450 Bannockburn Pacific | September | 2017 | 2018Q1 | 2018 | ZN3154:PA18 | ZN3154:PA18 | ZN03154/000018 | KU-RING-GAI | Unknown | Unknown | 2017-09-09 | N | 91 | N | 2 | N | N | 1.1101 | 39.4971 | 77073.6344
[7 empty] | 8629 | 19243 | 1510932 | 2017-09-09 19:23 | 2017-09-09 20:50 | 87 | 11kV | 33689 | 451 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN35800 Bankstown panel #18 'S47787 Gibson Atkinson' feeder has tripped on: Signals: 11kv trip, Tx2 Group earth Relays: B+C phase IOC, earth fault check, EFI Remarks: UG fault. Suspect UG fault between S4043 Enterprise Ave. Sth (Sw/B) to S50018 Stuart Arab (Sw/A) tee S6201 Watson fairford | September | 2017 | 2018Q1 | 2018 | ZN35800:PA18 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-09-09 | N | 74.6984 | N | 2 | N | N | 1.1101 | 39.4971 | 24618.9275
[7 empty] | 7785 | 8505 | 1510962 | 2017-09-10 07:59 | 2017-09-10 09:10 | 71 | 11kV | 426 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Planned LID 173347 B Phase DOLF : 31 Amp CASS NUMBER PROVIDED 308423 Could not find a job in OMS. Technician advised was called at 8am to attend the job. Excluded OMS 1510962 | September | 2017 | 2018Q1 | 2018 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2017-09-10 | N | 71 | N | 3 | N | N | 1.1101 | 39.4971 | 311.3082
[7 empty] | 8281 | 14751 | 1511003 | 2017-09-10 12:36 | 2017-09-10 14:19 | 103 | 11kV | 47423 | 470 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN7900 Campbell St Panel 15 tripped on Earth Faul and EFI Signals: 11kV Trip, No2 Group Earth Field EFI's - NIl Cause: Suspected UG fault between Zn7900 Campbell St and S64388 and S6833 See OMS 1511754 1511755 1511003 | September | 2017 | 2018Q1 | 2018 | ZN7900:PA15 | ZN7900:PA15 | ZN07900/000015 | SYDNEY | UG | Not Veg | 2017-09-10 | N | 100.9 | N | 3 | N | N | 1.1101 | 39.4971 | 34655.3297
[7 empty] | 8282 | 14754 | 1510995 | 2017-09-10 15:09 | 2017-09-10 16:18 | 68.65 | 11kV | 34805.55 | 507 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35370 panel 10 tripped and locked out on A and B phase IOC with timing and lockout relays 11kV Trip Cause: Tree branch on OH mains O/S488 Galston Rd Dural. See OMS 1511022 1511030 | September | 2017 | 2018Q1 | 2018 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2017-09-10 | N | 68.65 | N | 3 | N | N | 1.1101 | 39.4971 | 25434.8694
[7 empty] | 7792 | 8663 | 1511305 | 2017-09-11 18:56 | 2017-09-11 20:01 | 65 | 11kV | 70016 | 1220 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 38 tripped on C-N O/C and Earth Fault Cause: Possum removed from 11kV UGOH near PT327 See OMS 1511647 1511648 1511647 1511648 1511305 | September | 2017 | 2018Q1 | 2018 | ZN129:PA38 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Not Veg | 2017-09-11 | N | 57.3902 | N | 2 | N | N | 1.1101 | 39.4971 | 51165.6277
[7 empty] | 8372 | 15822 | 1511329 | 2017-09-11 21:53 | 2017-09-11 23:07 | 74 | 11kV | 45066 | 609 | HV | Animal Flying Fox | Animal | Air Break Switch | Unplanned | No Weather Impact | N | Ex Zn3154 St Ives section of Pa16 RE1622 Eastern Arterial tripped reclosed tripped and locked out on overcurrent Cause: Flying Fox removed adjacent AB2660 | September | 2017 | 2018Q1 | 2018 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Not Veg | 2017-09-11 | N | 74 | N | 2 | N | N | 1.1101 | 39.4971 | 32932.9036
[7 empty] | 8383 | 16038 | 1511416 | 2017-09-12 12:25 | 2017-09-12 17:30 | 305 | 11kV | 171860 | 1848 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 173383 B Phase Earth Fault ugoh fault at pole IV-50178 Excluded oms 1511416,1511417,1511438,1511522 | September | 2017 | 2018Q1 | 2018 | 224:80332 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | Unknown | Unknown | 2017-09-12 | N | 92.9978 | N | 3 | N | N | 1.1101 | 39.4971 | 125590.219
[7 empty] | 7297 | 2102 | 1511528 | 2017-09-12 19:58 | 2017-09-12 21:05 | 66.6333 | 11kV | 2865.2333 | 43 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 173385 Mains low at pole GR-73207 | September | 2017 | 2018Q1 | 2018 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2017-09-12 | N | 66.6333 | N | 3 | N | N | 1.1101 | 39.4971 | 2093.828
[7 empty] | 8305 | 15032 | 1511527 | 2017-09-12 19:50 | 2017-09-12 21:37 | 107 | 11kV | 1498 | 14 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 173384 Tree across CCT mains at pole FQ-95110. Not sure how we got the job. Can't find previous OMS job. E. Arlitsch may have more info. Excluded OMS 1511527 | September | 2017 | 2018Q1 | 2018 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2017-09-12 | N | 107 | N | 3 | N | N | 1.1101 | 39.4971 | 1094.6942
[7 empty] | 8112 | 12698 | 1511652 | 2017-09-13 11:48 | 2017-09-13 13:40 | 112 | 11kV | 8848 | 79 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn35370 Galston Panel 2, Recloser 3280 Hunt Ave Tripped and locked out Reloser 3280 Hunt Ave Relays: O/C Trip, Lockout Cause not ascertained | September | 2017 | 2018Q1 | 2018 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2017-09-13 | N | 112 | N | 8 | N | N | 1.1101 | 39.4971 | 6465.8574
[7 empty] | 8331 | 15258 | 1511669 | 2017-09-13 12:45 | 2017-09-13 13:52 | 67 | 11kV | 335 | 5 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 173397 B & C Phase DOLF : 31 Amp Branch over 11kV mains Excluded OMS 1511669 & 1511670 | September | 2017 | 2018Q1 | 2018 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2017-09-13 | N | 67 | N | 8 | N | N | 1.1101 | 39.4971 | 244.8081
[7 empty] | 8519 | 17819 | 1511568 | 2017-09-13 09:53 | 2017-09-13 15:05 | 312 | 11kV | 14086 | 108 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Ex Zn12690 Berkeley Vale section of Pa16 Recloser 45026 Fountaindale tripped, reclosed and locked out on: Relays: Overcurrent, Earth Fault, Lockout Signals: Tx13 Group Earth Cause: Tree/Branch brought down OH. Tree Branch hit HV mains and LB45167. Lineworker to repair. See 1511920,1 ex 1511568,77,83,601,3 | September | 2017 | 2018Q1 | 2018 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2017-09-13 | N | 130.4259 | N | 8 | N | N | 1.1101 | 39.4971 | 10293.6333
[7 empty] | 7749 | 8027 | 1511666 | 2017-09-13 12:36 | 2017-09-13 15:35 | 179 | 11kV | 33294 | 186 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn35370 Galston Panel 10 - IR50015 Quarry Old Northern tripped, reclosed tripped and locked out on IR500015 Quarry Old Northern Cause; Tree branch on OH mains, Removed By DOp O/S No.3 Hemmers Rd. | September | 2017 | 2018Q1 | 2018 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2017-09-13 | N | 179 | N | 8 | N | N | 1.1101 | 39.4971 | 24330.2732
[7 empty] | 7411 | 3966 | 1511584 | 2017-09-13 10:12 | 2017-09-13 16:50 | 398 | 11kV | 189254 | 778 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn15055 Belrose Panel 10 tripped pm Signals: 11kV trip, Zone Earth Relays: Timed Earth Fault, Fault Check and EFI. Cause: UGOH fault short circuit UGOH fault on UGOH between SW/B @ S65242, S?A @ Sub 16494 and LB22982 See OMS 1511993 1511994 1511996 1511584 1511743 1511720 | September | 2017 | 2018Q1 | 2018 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | Unknown | Unknown | 2017-09-13 | N | 243.2571 | N | 8 | N | N | 1.1101 | 39.4971 | 138301.2412
[7 empty] | 8048 | 11729 | 1511766 | 2017-09-13 16:06 | 2017-09-13 17:45 | 99 | 11kV | 6732 | 68 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Ex 847 Hornsby Panel 1 Recloser 2196 Milner Rampart tripped, reclosed tripped and locked out on OC and IOC Cause: possible 11kV UGOH fault adjacent to PT1987 UGOH was on fire when Dop Arrived. See OMS 1511980 1511768 1511766 | September | 2017 | 2018Q1 | 2018 | ZN847:PA1 | ZN847:PA1 | ZN00847/000001 | HORNSBY | Unknown | Unknown | 2017-09-13 | N | 99 | N | 8 | N | N | 1.1101 | 39.4971 | 4919.547
[7 empty] | 7503 | 5422 | 1511765 | 2017-09-13 14:02 | 2017-09-13 19:20 | 318 | 11kV | 318 | 1 | HV | Customer Installation Fault | Customer Installation | Fuse | Unplanned | No Weather Impact | N | Zn2835 Burwood No protection operation. Zone earth and Tx3 Group earth. Sub 4100 Beresford Coventry B phase 80 amp OHFMA fuse operated. Remarks: fault on customers equipment. Apporoximately 35 amps lost at the time from panel 41. Known fault, polly loggers installed | September | 2017 | 2018Q1 | 2018 | ZN2835:PA41 | ZN2835:PA41 | ZN02835/000041 | STRATHFIELD | Unknown | Unknown | 2017-09-13 | N | 318 | N | 8 | N | N | 1.1101 | 39.4971 | 232.385
[7 empty] | 8151 | 13206 | 1511824 | 2017-09-14 01:01 | 2017-09-14 01:56 | 55 | 11kV | 52525 | 955 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | @Zn1287 Revesby 11kv Panel No.22 'S.3939 Macarthur Revesby' feeder tripped Relays: 'A' phase timed O/C, F/C, efi Signals: 11kv trip, ZE Remarks: animals/birds, possum on UGOH o/s 115 Alma Rd | September | 2017 | 2018Q1 | 2018 | ZN1287:PA22 | ZN1287:PA22 | ZN01287/000022 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-09-14 | N | 55 | N | 5 | N | N | 1.1101 | 39.4971 | 38383.7208
[7 empty] | 7429 | 4204 | 1511793 | 2017-09-13 16:00 | 2017-09-14 02:55 | 655 | 11kV | 9825 | 15 | HV | Fire (Non Ausgrid) | UNKNOWN | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 173402 section isolated to make repairs at pole HT-12414 after bush fire | September | 2017 | 2018Q1 | 2018 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2017-09-13 | N | 655 | N | 8 | N | N | 1.1101 | 39.4971 | 7179.8202
[7 empty] | 7383 | 3630 | 1511830 | 2017-09-14 02:26 | 2017-09-14 04:10 | 104 | 11kV | 14244 | 156 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay - Pnl.4 tripped on: A, B & C phase O/C with EFI Field EFIs: S9474, NO Access to EFI @ S9899, S9266 is coroded and full of water Possum was wedged on UGOH and clear of mains at PT9745. Centre phase fuse of PT9745 required replacing. See 1511882 1511883 | September | 2017 | 2018Q1 | 2018 | ZN9550:PA9 | ZN9550:PA9 | ZN09550/000009 | SUTHERLAND | OH | Not Veg | 2017-09-14 | N | 91.3077 | N | 5 | N | N | 1.1101 | 39.4971 | 10409.0951
[7 empty] | 7713 | 7604 | 1511840 | 2017-09-14 05:58 | 2017-09-14 09:35 | 217 | 11kV | 572 | 7 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 173407 Stay wire broken at Sub 53390 Excluded OMS 1511840 | September | 2017 | 2018Q1 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2017-09-14 | N | 81.7143 | N | 5 | N | N | 1.1101 | 39.4971 | 418.0007
[7 empty] | 7572 | 6045 | 1511826 | 2017-09-14 01:28 | 2017-09-14 13:05 | 697 | 11kV | 21865 | 171 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 173400 1 fault operation Sensitive Earth Fault tree into ohm & HV wires down at pole JR-25091 Excluded oms 1511826 | September | 2017 | 2018Q1 | 2018 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2017-09-14 | N | 127.8655 | N | 5 | N | N | 1.1101 | 39.4971 | 15978.2971
[7 empty] | 7674 | 7065 | 1512273 | 2017-09-14 22:31 | 2017-09-15 00:50 | 139 | 11kV | 173723 | 1382 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn36300 Balwolah Nth Pa19 "Hayes Condamine" fdr tripped, reclosed & tripped Relays: 'A&C' phase IOC, F/C, L/O, EFI, SEL Signals: 11kv trip EFI's: S16827 S16064 S49927 S16928, UGOH in Myrtle St, S16987, Unable to read EFI at UGOH un Urunga St (full of water) Tx1 Prot. Panel: F/C @LB49832: SEF Detection Cause: Centre phase bond burnt off at corner of Rickard and Balgowlah Rd. Section of 11kV OH directly beneath S16928 on the System Diagram See 1512336,7,8 ex 1512273,4 | September | 2017 | 2018Q1 | 2018 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2017-09-14 | N | 125.7041 | N | 5 | N | N | 1.1101 | 39.4971 | 126951.6444
[7 empty] | 8008 | 11213 | 1512295 | 2017-09-15 07:59 | 2017-09-15 10:20 | 141 | 11kV | 705 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173421 Single phase DOLF : 20 Amp Excluded OMS 1512295 | September | 2017 | 2018Q1 | 2018 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2017-09-15 | N | 141 | N | 4 | N | N | 1.1101 | 39.4971 | 515.1932
[7 empty] | 7965 | 10530 | 1512300 | 2017-09-15 08:22 | 2017-09-15 12:20 | 238 | 11kV | 71360 | 956 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Pa8 tripped, reclosed, tripped and locked out on: Relays: B-C OC, EF, EFI, Recloser L/O Cause: insulator failed. 11kv Insulator on pole failed See 1513020,1,2 ex 1512300,4,8,9,11,47 | September | 2017 | 2018Q1 | 2018 | ZN12690:PA8 | ZN12690:PA8 | ZN12690/000008 | CENTRAL COAST | OH | Not Veg | 2017-09-15 | N | 74.6444 | N | 4 | N | N | 1.1101 | 39.4971 | 52147.7832
[7 empty] | 7795 | 8691 | 1512373 | 2017-09-15 13:12 | 2017-09-15 15:12 | 120 | 11kV | 102798 | 888 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN36800 Waverly (New) exiting Panel #33 labelled "S.977 Angelsea St" Section of 11kv feeder tripped from "Tx#1/feeder" @ S.339 Glenayr Av to "Tx#2/Sw.C" @ S.354 Hastings Pde via S.36067 Curlewis Glen RELAYS @ S.339 Glenayr Av: T/Lay, I/T send, EFI @ S.354 Hastings Parade: I/T receive @ S.36067 Curlewis Glen: EFI Remarks: UG fault. 11kv Underground feeder fault from "SW/B" @ S.36067 Curlewis Glen to "Tx#2/Sw.C" feeder @ S.354 Hastings Pde | September | 2017 | 2018Q1 | 2018 | ZN36800:PA33 | ZN36800:PA33 | ZN36800/000033 | WAVERLEY | UG | Not Veg | 2017-09-15 | N | 115.7635 | N | 4 | N | N | 1.1101 | 39.4971 | 75121.7464
[7 empty] | 7889 | 9859 | 1512450 | 2017-09-15 21:23 | 2017-09-15 22:17 | 54 | 11kV | 57942 | 1073 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn14891 Wyong Pa10 tripped, reclosed, tripped on Relays: ABC Phase IOC, EFI, Fault check, reclose, timmer, lockout EFI's: S14857 Alarms: 11kv trip Cause: Possum 1st UGOH out form S14857. removed by DOP no apparent damage | September | 2017 | 2018Q1 | 2018 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Not Veg | 2017-09-15 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 42342.3046
[7 empty] | 7321 | 2548 | 1512459 | 2017-09-16 03:05 | 2017-09-16 05:30 | 145 | 11kV | 7395 | 51 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong Pa16 "Wyongah" fdr PT13099 Palmer Woolsley 11kV Footpath 31Amp HVDO operated Cause: Possum found at base of PT13099 no damage cause See 1513037 ex 1512459 | September | 2017 | 2018Q1 | 2018 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2017-09-16 | N | 145 | N | 3 | N | N | 1.1101 | 39.4971 | 5404.0479
[7 empty] | 7274 | 1665 | 1512544 | 2017-09-16 18:10 | 2017-09-16 20:00 | 110 | 11kV | 770 | 7 | HV | Animal Other | Animal | Stay Wire | Unplanned | No Weather Impact | N | LID 173435 Repair broken stay wire | September | 2017 | 2018Q1 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2017-09-16 | N | 110 | N | 3 | N | N | 1.1101 | 39.4971 | 562.6933
[7 empty] | 7190 | 178 | 1512561 | 2017-09-16 22:37 | 2017-09-16 23:06 | 29 | 11kV | 13882 | 708 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Panel 12 interrupted for safety 2:57AM to restore feeder after repairs See 1513049,50,1,2,3 ex 1512561,3,4 | September | 2017 | 2018Q1 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2017-09-16 | N | 19.6073 | N | 3 | N | N | 1.1101 | 39.4971 | 10144.5562
[7 empty] | 8506 | 17690 | 1513052 | 2017-09-17 02:57 | 2017-09-17 03:25 | 28 | 11kV | 12076 | 708 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Cause: Vehicle Hit Pole. Pa12 interrutped for safety @22:37PM 11kv down beyond autolinks 44778 Section of 11kv fdr isolated between LK43741 and LB41278 to allow repairs Panel 12 interrupted for safety 2:57AM to restore feeder after repairs See 1513049,50,1,2,3 ex 1512561,3,4 | September | 2017 | 2018Q1 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2017-09-17 | N | 17.0565 | N | 1 | N | N | 1.1101 | 39.4971 | 8824.7846
[7 empty] | 8427 | 16671 | 1512653 | 2017-09-18 02:46 | 2017-09-18 05:24 | 158 | 11kV | 267766 | 2114 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | At S36300 Balgowlah North Panel 5 tripped on Relays: B and C phase OC, Fault Check and EFI Signals: 11kV trip, No1 TX Group Earth Abnormal Switching: SW/B Closed @ S16916, SW/B open @ S16928, AW/A Open @ S16508 Cause: Possum found at the base of LB49832 See OMS 1513078 1513081 1512654 1512653 | September | 2017 | 2018Q1 | 2018 | ZN36300:PA5 | ZN36300:PA5 | ZN36300/000005 | NORTHERN BEACHES | OH | Not Veg | 2017-09-18 | N | 126.6632 | N | 4 | N | N | 1.1101 | 39.4971 | 195675.495
[7 empty] | 8342 | 15394 | 1512696 | 2017-09-18 08:48 | 2017-09-18 09:58 | 70 | 11kV | 98350 | 1405 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S10997 San Souci Panel 12 "Clareville ave Feeder" tripped on: A & C phase overcurrent rec time delay. Lockout note panel 12 CB would not close up, left for tpe Remarks: Animals/birds. Cocky on 11kv overhead pole #CR 09234 | September | 2017 | 2018Q1 | 2018 | ZN10997:PA12 | ZN10997:PA12 | ZN10997/000012 | BAYSIDE | OH | Not Veg | 2017-09-18 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 71871.2792
[7 empty] | 7313 | 2395 | 1512689 | 2017-09-18 08:31 | 2017-09-18 11:25 | 174 | 11kV | 174 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 173442 C Phase DOLF : 10 Amp Blown Cph L/A replaced Excluded OMS 1512689 | September | 2017 | 2018Q1 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2017-09-18 | N | 174 | N | 4 | N | N | 1.1101 | 39.4971 | 127.1541
[7 empty] | 7480 | 5076 | 1512899 | 2017-09-18 22:18 | 2017-09-19 00:18 | 120 | 11kV | 129348 | 1119 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 42 tripped and should have reclosed on Relays: B phase Overcurrent, Reclose Timer, Lockout. Feeder was patrolled and no cause found. Pa42 spring charge defective Tries to charge but discharges half way. See OMS 1513106 1512899 See OMS 1513106 1512899 | September | 2017 | 2018Q1 | 2018 | ZN4545:PA42 | ZN4545:PA42 | ZN04545/000042 | RYDE | OH | Veg | 2017-09-18 | N | 115.5925 | N | 4 | N | N | 1.1101 | 39.4971 | 94523.7033
[7 empty] | 7672 | 7062 | 1512907 | 2017-09-19 04:02 | 2017-09-19 05:18 | 76 | 11kV | 91238 | 2114 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | At S36300 Balgowlah North panel 5 tripped Relays: A phase Overcurrent, EFI, Fault Check Abnormal Switching: SW/B @ S16916 Closed, SW/B @ S16928 Open, SW/A @ S16508 Open Cause: 2 dead possums found at the base of LB49832 1513088 1513090 1512908 1512907 | September | 2017 | 2018Q1 | 2018 | ZN36300:PA5 | ZN36300:PA5 | ZN36300/000005 | NORTHERN BEACHES | OH | Not Veg | 2017-09-19 | N | 43.1589 | N | 2 | N | N | 1.1101 | 39.4971 | 66674.0393
[7 empty] | 8568 | 18447 | 1513135 | 2017-09-19 20:14 | 2017-09-19 23:59 | 225 | 11kV | 17018 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn195 Pymble section of Pa10 "S4943 & S35422" S4424 Fern Mona Vale 11kv OQFRN 40Amp HV fuse (B Phase) replaced Interrupted @ 2201 Restored @ 2345 Cause: Tree/Branch brought down OH. Outside 25 Fern Street Pymble. OH services to 16, 18 & 27 Fern Street to be restored Wednesday Business Hours See 1513460,1 ex 1513135 | September | 2017 | 2018Q1 | 2018 | ZN195:PA10 | ZN195:PA10 | ZN00195/000010 | KU-RING-GAI | OH | Veg | 2017-09-19 | N | 218.1795 | N | 2 | N | N | 1.1101 | 39.4971 | 12436.2525
[7 empty] | 7897 | 9947 | 1513148 | 2017-09-20 04:45 | 2017-09-20 05:37 | 52 | 11kV | 29540 | 2114 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North Pa5 Relays Signals: Tx1 Group Earth, CB5 open EFI's: S17148 S16515 S16916 S15943 S16513 UGOH Clontarf/Urunga @LB49832 (Panel 19 SHt 3 D5) Overcurrent ABC + Earth Fault Abnormal: S16916:B Closed S16928:B Open S16509:A Closed S16508:A Open Cause: 3 dead possums on ground below LB49832 Region to inspect gumtree across the road nesting family of possums 53 Woodbine street See 1513487,8 ex 1513148,9 | September | 2017 | 2018Q1 | 2018 | ZN36300:PA5 | ZN36300:PA5 | ZN36300/000005 | NORTHERN BEACHES | OH | Not Veg | 2017-09-20 | N | 13.9735 | N | 3 | N | N | 1.1101 | 39.4971 | 21586.9607
[7 empty] | 7631 | 6617 | 1513172 | 2017-09-20 07:45 | 2017-09-20 09:17 | 92 | 11kV | 7084 | 77 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S16829 Wattle mitchell No1 80A C phase HV fuse operaqted Section of Panel 16 ex S15001 Brookvale Cause: HV fuse operated when carrying out switching for disconnect 410604 | September | 2017 | 2018Q1 | 2018 | ZN15001:PA16 | ZN15001:PA16 | ZN15001/000016 | NORTHERN BEACHES | OH | Veg | 2017-09-20 | N | 92 | N | 3 | N | N | 1.1101 | 39.4971 | 5176.7783
[7 empty] | 8028 | 11423 | 1513257 | 2017-09-20 13:27 | 2017-09-20 16:15 | 168 | 11kV | 455843 | 3923 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At Zn.180 Mosman Panel #32 'S.3855 Spit Punch, S.4269 Parraween Paling, Etc.' Feeder has Tripped on: Signals: Zone Earth, Tx4 Group Earth, 11kV Trip. Relays: 32 Fdr Prot 'A' C+N Phase, 32 Left Fdr Prot 'B' Relay :- Trip Signal, Earth Fault, Fault Check, EFI. FIELD EFI'S: S.3855, S.204 Cause:11kV feeder damaged between S204 Awaba St to S37854 to S35392. BRP directional drilling trilled throug UG cables near 32 Awaba St Abnormal Switching: SW/B Closed at S3578 and Panel 18 Open See OMS 1513684 1513317 1513322 1513687 1513688 1513689 1513257 1513261/3275/3260/3270/3272/3274 | September | 2017 | 2018Q1 | 2018 | ZN180:PA32 | ZN180:PA32 | ZN00180/000032 | NORTH SYDNEY | UG | Not Veg | 2017-09-20 | N | 116.1976 | N | 3 | N | N | 1.1101 | 39.4971 | 333116.6193
[7 empty] | 7681 | 7114 | 1513570 | 2017-09-21 21:45 | 2017-09-21 23:26 | 101 | 11kV | 63392 | 751 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | The 11kV panel 36 Bowen Mobray CB @ Zn80 Chatswood tripped on Signals: 11kV trip, TX13 Group Earth, Zone Earth and Protection defect Relays: Translay, Fault Check and EFI Sub 7712 Artarmon Edward tripped on Translay At S546 Artarmon Rd SW/B is closed and SWA is open Cause: 11kV Feeder fault from S47513 Burra Pyrl to S4059 Artarmon Lucknow See OMS 1513702 1513704 1513707 1513573 1513570 | September | 2017 | 2018Q1 | 2018 | ZN80:PA36 | ZN80:PA36 | ZN00080/000036 | WILLOUGHBY | UG | Not Veg | 2017-09-21 | N | 84.4101 | N | 1 | N | N | 1.1101 | 39.4971 | 46325.0039
[7 empty] | 8475 | 17350 | 1513588 | 2017-09-22 06:23 | 2017-09-22 08:15 | 112 | 11kV | 112 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173516 3 phase DOLF : 10 Amp Three dolfs blown at sub 72873 not 50497 as per OMS. Suspect this fault may have caused a mains clash upstream of Sw 74495. Chris Pengelly patrolled the feeder but we were unable to find the cause. Excluded OMS 1513588 | September | 2017 | 2018Q1 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-09-22 | N | 112 | N | 3 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 8392 | 16225 | 1513721 | 2017-09-22 17:05 | 2017-09-22 17:47 | 42 | 11kV | 37758 | 899 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 173530 2 fault operations C Phase Overcurrent; Earth Fault UGOH IR 83188 faulty | September | 2017 | 2018Q1 | 2018 | 238:34137 | 532:83301 | ZN00532/083301 | MAITLAND | Unknown | Unknown | 2017-09-22 | N | 42 | N | 3 | N | N | 1.1101 | 39.4971 | 27592.4327
[7 empty] | 8423 | 16613 | 1513755 | 2017-09-22 23:49 | 2017-09-23 01:05 | 76 | 11kV | 85956 | 1131 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa22 11kv bond burnt off at AB44655 Abnormal: AB44423 open and defective Cause: bond burnt C phase at AB44655 See 1514265 ex 1513755,60,3 | September | 2017 | 2018Q1 | 2018 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2017-09-22 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 62814.1095
[7 empty] | 7220 | 716 | 1513840 | 2017-09-23 14:52 | 2017-09-23 15:59 | 67 | 11kV | 8777 | 131 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 173535 A Phase Burnt tapping on ABS 5993. created small fire. | September | 2017 | 2018Q1 | 2018 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2017-09-23 | N | 67 | N | 2 | N | N | 1.1101 | 39.4971 | 6413.9727
[7 empty] | 7345 | 2856 | 1513843 | 2017-09-23 15:00 | 2017-09-23 19:17 | 257 | 11kV | 66200 | 275 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 173537 Overcurrent 2 x B IsntantaneousOC AC Inst OC BC 2703 amps S 2658 amps Excluded OMS 1513843 | September | 2017 | 2018Q1 | 2018 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2017-09-23 | N | 240.7273 | N | 2 | N | N | 1.1101 | 39.4971 | 48377.0074
[7 empty] | 8068 | 12049 | 1513902 | 2017-09-24 04:02 | 2017-09-24 05:30 | 88 | 11kV | 90323 | 1181 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Pa18 "Entrance Yakkalla" tripped on Relays: C Phase IOC, EFI, F/C L/O Timing, Zone Earth and Group Earth 11kv trip EFI'S: S12806-S18070 UG fault from Zn18070 the entrance leagues to USL44277 to S14117 Bateau Bay STW Tee PT11743 See 1514275,7,8,9,80 ex 1513902 | September | 2017 | 2018Q1 | 2018 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | UG | Not Veg | 2017-09-24 | N | 76.4801 | N | 8 | N | N | 1.1101 | 39.4971 | 66005.3843
[7 empty] | 8485 | 17455 | 1513903 | 2017-09-24 04:06 | 2017-09-24 07:05 | 179 | 11kV | 168421 | 1911 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15005 Belrose 11kv Pa2 tripped, reclosed & tripped on: Relays: Overcurrent, Lockout, Timing on Panel 2R Alarams: 11kV CB trip Cause: OH cables twisted together See 1514282,3,4 ex 1513903 | September | 2017 | 2018Q1 | 2018 | ZN15005:PA2 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | OH | Not Veg | 2017-09-24 | N | 88.1324 | N | 8 | N | N | 1.1101 | 39.4971 | 123077.0992
[7 empty] | 8657 | 19558 | 1513919 | 2017-09-24 07:38 | 2017-09-24 08:35 | 57 | 11kV | 66063 | 1159 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 173539 1 fault operation B & C phase Overcurrent Tree on mains pole IV-10093. Removed by DOP | September | 2017 | 2018Q1 | 2018 | 270:83590 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Veg | 2017-09-24 | N | 57 | N | 8 | N | N | 1.1101 | 39.4971 | 48276.8919
[7 empty] | 8193 | 13644 | 1513922 | 2017-09-24 07:53 | 2017-09-24 10:45 | 172 | 11kV | 306686 | 1847 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 173541 1 fault operation B & C Phase Instantaneous Overcurrent Patrolled but no fault found | September | 2017 | 2018Q1 | 2018 | 224:80332 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | OH | Veg | 2017-09-24 | N | 166.0455 | N | 8 | N | N | 1.1101 | 39.4971 | 224117.0831
[7 empty] | 8697 | 19985 | 1513923 | 2017-09-24 07:59 | 2017-09-24 11:30 | 211 | 11kV | 1055 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 173545 A Phase DOLF : 10 Amp Steel wire fatigue Excluded OMS 1513923 | September | 2017 | 2018Q1 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2017-09-24 | N | 211 | N | 8 | N | N | 1.1101 | 39.4971 | 770.9629
[7 empty] | 7362 | 3120 | 1513967 | 2017-09-24 10:32 | 2017-09-24 13:30 | 178 | 11kV | 356 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | LID 173546 B Phase DOLF : 80 Amp Fuse fatigue. Excluded OMS 1513967. | September | 2017 | 2018Q1 | 2018 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2017-09-24 | N | 178 | N | 8 | N | N | 1.1101 | 39.4971 | 260.1543
[7 empty] | 7758 | 8138 | 1514029 | 2017-09-24 19:08 | 2017-09-24 20:39 | 91 | 11kV | 171637 | 1900 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15014 Mona Vale Pa19 "The Harkeith Barrenjoey" fdr tripped reclsoed and locked out on IOC, EFI, Fault check, reclose time delay and lockout relays EFI's S16727 S15225 S16696 UG fault for DArley Stanley S16696 to Terror Cr - S16214 to Golf Surview S46757 See 1514287,9 ex 1514029 | September | 2017 | 2018Q1 | 2018 | ZN15014:PA19 | ZN15014:PA19 | ZN15014/000019 | NORTHERN BEACHES | UG | Not Veg | 2017-09-24 | N | 90.3353 | N | 8 | N | N | 1.1101 | 39.4971 | 125427.2572
[7 empty] | 7602 | 6336 | 1514036 | 2017-09-24 20:06 | 2017-09-24 21:10 | 64.05 | 11kV | 2497.95 | 39 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 173549 B Phase DOLF : 31 Amp interrupt to remove brushtail possum - possum alive and taken to WIRES. EFI's on feeder reset. EFI on sub 39593 did not operate - please investigate | September | 2017 | 2018Q1 | 2018 | 217:33612 | 217:33605 | ZN00217/033605 | LAKE MACQUARIE | OH | Not Veg | 2017-09-24 | N | 64.05 | N | 8 | N | N | 1.1101 | 39.4971 | 1825.4282
[7 empty] | 7342 | 2820 | 1514051 | 2017-09-25 05:31 | 2017-09-25 09:10 | 219 | 11kV | 8322 | 38 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby Panel 17 "Somersby Falls" fdr 11kV Roadside bon burnt off at LK44388 Cause: bond burnt repaired See 1514472 ex 1514051,5 | September | 2017 | 2018Q1 | 2018 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2017-09-25 | N | 219 | N | 4 | N | N | 1.1101 | 39.4971 | 6081.4721
[7 empty] | 7327 | 2683 | 1514148 | 2017-09-25 10:41 | 2017-09-25 12:09 | 88 | 11kV | 5192 | 59 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 RE45083 Durren tripped, reclosed and tripped Relays: Overcurrent trip, Lockout Cause: Tree hit mains outside 15 cottesloe Rd Jilliby. Pole no DD733 | September | 2017 | 2018Q1 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2017-09-25 | N | 88 | N | 4 | N | N | 1.1101 | 39.4971 | 3794.1605
[7 empty] | 8547 | 18188 | 1514204 | 2017-09-25 13:12 | 2017-09-25 14:15 | 63 | 11kV | 4536 | 72 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173567 B Phase DOLF : 40 Amp 247 volts Excluded OMS 1514204 | September | 2017 | 2018Q1 | 2018 | 261:81876 | 261:81876 | ZN00261/081876 | NEWCASTLE | OH | Veg | 2017-09-25 | N | 63 | N | 4 | N | N | 1.1101 | 39.4971 | 3314.775
[7 empty] | 7486 | 5133 | 1514225 | 2017-09-25 13:57 | 2017-09-25 16:50 | 173 | 11kV | 519 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 173569 LLC pulled out of DOLF Excluded OMS 1514225 | September | 2017 | 2018Q1 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2017-09-25 | N | 173 | N | 4 | N | N | 1.1101 | 39.4971 | 379.2699
[7 empty] | 8329 | 15248 | 1514962 | 2017-09-26 16:45 | 2017-09-26 16:50 | 5 | 11kV | 1350 | 270 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Zn8700 City North Pa63A and 63B @Bridge & George sts S428 Dop bumped 11kV pull off gear causing 63A & 63C B&S I&E switch to trip Abnormal: 63B was already isolated Cause: Staff Error | September | 2017 | 2018Q1 | 2018 | ZN8700:PA63 64ABC | ZN8700:PA63 64ABC | ZN08700/63 64ABC | SYDNEY | Unknown | Not Veg | 2017-09-26 | N | 5 | N | 2 | N | N | 1.1101 | 39.4971 | 986.5402
[7 empty] | 8525 | 17909 | 1514590 | 2017-09-26 17:02 | 2017-09-26 18:37 | 95 | 11kV | 161090 | 2028 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12650 West Gosford Pa12 "North Gosford etc" fdr tripped, reclosed, tripped and locked out Relays: 51N (EF), 150TN (EFI), lockout, timing Signals: Tx13B Group Earth EFI's: S11973 S14883 Cause: not ascertained HV fault between S14883 SwB and AB43065. Lineworker to inspect OH section and UGOH in daylight See 1514963,4 ex 1514590,6 | September | 2017 | 2018Q1 | 2018 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Veg | 2017-09-26 | N | 79.4329 | N | 2 | N | N | 1.1101 | 39.4971 | 117719.8206
[7 empty] | 8165 | 13316 | 1514924 | 2017-09-27 13:00 | 2017-09-27 15:00 | 120 | 11kV | 1680 | 14 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 173605 Pole falling over BI-60358. Replaced as emergency. Excluded OMS 1514924 | September | 2017 | 2018Q1 | 2018 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2017-09-27 | N | 120 | N | 1 | N | N | 1.1101 | 39.4971 | 1227.6944
[7 empty] | 7393 | 3789 | 1515051 | 2017-09-28 07:23 | 2017-09-28 09:25 | 122 | 11kV | 134787 | 1786 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2635 Epping Pa31 "Essec Pembroke" trippe don Relays: A Phase IOC, Earth Fault & EFI Signals: 11kv trip EFI's: S3794 S4845 S7061 Cause: 11kv fdr UG fault from S7061 to S6227. See seperate interruption due to LV//'s See 1515408,10 LV// 1515067,413 ex 1515051,9,62,71 | September | 2017 | 2018Q1 | 2018 | ZN2635:PA31 | ZN2635:PA31 | ZN02635/000031 | PARRAMATTA | UG | Not Veg | 2017-09-28 | N | 75.4686 | N | 2 | N | N | 1.1101 | 39.4971 | 98498.3641
[7 empty] | 8103 | 12553 | 1515220 | 2017-09-28 14:53 | 2017-09-28 16:45 | 112 | 11kV | 112 | 1 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173625 1 fault operation A Phase DOLF : 10 Amp dead possum found at sub Excluded oms 1515220 | September | 2017 | 2018Q1 | 2018 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2017-09-28 | N | 112 | N | 2 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 8286 | 14809 | 1515294 | 2017-09-29 03:38 | 2017-09-29 05:41 | 123 | 11kV | 267037 | 3509 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15006 Dee Why West Panel 16 tripped on Basler 51 AB, 11kV trip. Abnormal Switching: SW/A closed at S16848 and SW/B Closed at S46679 Cause: Tree branch on OH mains See OMS 1516151 1516154 1516155 1515295 1515297 1515294 | September | 2017 | 2018Q1 | 2018 | ZN15006:PA16 | ZN15006:PA16 | ZN15006/000016 | NORTHERN BEACHES | OH | Veg | 2017-09-29 | N | 76.1006 | N | 3 | N | N | 1.1101 | 39.4971 | 195142.7633
[7 empty] | 7276 | 1777 | 1515326 | 2017-09-29 08:42 | 2017-09-29 13:35 | 293 | 11kV | 1465 | 5 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 173627 pole 9H-50077 requires urgent replacement under AP | September | 2017 | 2018Q1 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2017-09-29 | N | 293 | N | 3 | N | N | 1.1101 | 39.4971 | 1070.5788
[7 empty] | 7218 | 653 | 1515388 | 2017-09-29 11:47 | 2017-09-29 13:36 | 109 | 11kV | 133089 | 1221 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Panel 38 tripped on A to N IOC with Earth Fault Cause: 11kv front line feeder fault. DOp reported Dirt blown out near a Road Plate in Meriton St. (Between Pole GL48927 and GL48928) w | September | 2017 | 2018Q1 | 2018 | ZN129:PA38 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | UG | Not Veg | 2017-09-29 | N | 109 | N | 3 | N | N | 1.1101 | 39.4971 | 97257.5157
[7 empty] | 7804 | 8758 | 1515865 | 2017-09-30 00:38 | 2017-09-30 12:20 | 702 | 11kV | 240084 | 342 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | IR50008 Tripped and Reclosed on O/C Ex panel 3 "S4312 Edgar Marion fdr from ZN1850 Bass Hill" Remarks: AB140 center phase bond found burnt off by line worker | September | 2017 | 2018Q1 | 2018 | ZN1850:PA3 | ZN1850:PA41 | ZN01850/000041 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-09-30 | N | 702 | N | 2 | N | N | 1.1101 | 39.4971 | 175446.3059
[7 empty] | 8429 | 16705 | 1515570 | 2017-09-30 11:07 | 2017-09-30 18:35 | 448 | 11kV | 23679 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn35370 Galston ex Panel 8 from CP559 tripped, reclosed tripped and locked out on overcurrent Cause: Tree branch on OH mains adjacent to PT142 Peebles Noll See OMS 1516162 1516163 1515570 | September | 2017 | 2018Q1 | 2018 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2017-09-30 | N | 241.6224 | N | 2 | N | N | 1.1101 | 39.4971 | 17303.9148
[7 empty] | 7812 | 8856 | 1515647 | 2017-10-01 00:16 | 2017-10-01 04:00 | 224 | 11kV | 2912 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 173645 Fuse saver 40848 found open. LF 40848 closed. Customers reported no reclose. Fuse saver not set non auto for TFB. Please investigate operation. Excluded OMS 1515647. | October | 2017 | 2018Q2 | 2018 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-10-01 | N | 224 | N | 2 | N | N | 1.1101 | 39.4971 | 2128.0037
[7 empty] | 8603 | 18896 | 1515673 | 2017-10-01 11:26 | 2017-10-01 12:25 | 59 | 11kV | 177 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173646 B Phase DOLF : 31 Amp Excluded OMS 1515673 | October | 2017 | 2018Q2 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2017-10-01 | N | 59 | N | 2 | N | N | 1.1101 | 39.4971 | 129.3464
[7 empty] | 8045 | 11684 | 1515724 | 2017-10-02 03:12 | 2017-10-02 07:10 | 238 | 11kV | 145881 | 1701 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 29 tripped on O/C 50T A-C Cause Not ascertained - Mains to Patrol. See OMS 151263 151265 151266 1515725 | October | 2017 | 2018Q2 | 2018 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Veg | 2017-10-02 | N | 85.7619 | N | 1 | N | N | 1.1101 | 39.4971 | 106605.532
[7 empty] | 7815 | 8879 | 1515933 | 2017-10-03 11:30 | 2017-10-03 22:20 | 650 | 11kV | 5200 | 8 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 173661 A car or trailer hit pole GT-10141. ABS 62295 was opened for safety and to allow repairs. DOPS D Robertson and A Mills were also involved in the disconnection. Excluded OMS 1515887 | October | 2017 | 2018Q2 | 2018 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2017-10-03 | N | 650 | N | 1 | N | N | 1.1101 | 39.4971 | 3800.0066
[7 empty] | 7845 | 9297 | 1516107 | 2017-10-04 05:27 | 2017-10-04 08:00 | 153 | 11kV | 140237 | 1765 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Pa19 "S14809 Lakehaven Wyong Leagues" fdr tripped, reclosed, triped & locked out on Relays: 50T ABC, FC, REC LO, REC TIMER SIGNALS: 11kv trip Cause: vehicle hit pole See 1517156,60,2,3,4 ex 1516107,36,7 | October | 2017 | 2018Q2 | 2018 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | OH | Not Veg | 2017-10-04 | N | 79.4544 | N | 5 | N | N | 1.1101 | 39.4971 | 102481.0633
[7 empty] | 8250 | 14411 | 1516315 | 2017-10-04 16:02 | 2017-10-04 16:13 | 11 | 11kV | 24068 | 2188 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn36100 Rose Bay Pa19 "S3357" fdr tripped Signals: 11kv trip, TX2 Group Earth Relays: IOC ABC, EFI EFI's: As Expected Abnormal: S3017 Wallis Pde was in LV// and isolated in preparation for D&R 412978 Cause: 11kV Endboxes incorrectly labelled Sw/A was labelled Sw/B and Sw/B was labelled Sw/A | October | 2017 | 2018Q2 | 2018 | ZN36100:PA19 | ZN36100:PA19 | ZN36100/000019 | WAVERLEY | Unknown | Unknown | 2017-10-04 | N | 11 | N | 5 | N | N | 1.1101 | 39.4971 | 17588.1845
[7 empty] | 7477 | 5034 | 1516292 | 2017-10-04 15:30 | 2017-10-04 16:20 | 50 | 11kV | 1400 | 28 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 173683 Large tre fell into mains near sub 70995 . Tree removed. Interruption safety only. | October | 2017 | 2018Q2 | 2018 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2017-10-04 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 1023.0787
[7 empty] | 7368 | 3263 | 1516360 | 2017-10-04 19:53 | 2017-10-04 21:15 | 81.7333 | 11kV | 2043.3333 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 173684 A Phase DOLF : 40 Amp | October | 2017 | 2018Q2 | 2018 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2017-10-04 | N | 81.7333 | N | 5 | N | N | 1.1101 | 39.4971 | 1493.2077
[7 empty] | 7646 | 6759 | 1516426 | 2017-10-05 08:39 | 2017-10-05 10:55 | 136 | 11kV | 4057 | 35 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 173689 2 fault operation A & C Phase Instantaneous Overcurrent | October | 2017 | 2018Q2 | 2018 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Veg | 2017-10-05 | N | 115.9143 | N | 3 | N | N | 1.1101 | 39.4971 | 2964.7359
[7 empty] | 7586 | 6149 | 1516350 | 2017-10-04 18:21 | 2017-10-05 14:15 | 1194 | 11kV | 45534 | 50 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 173685 Unable to locate SEF fault beyond ABS 77510. Fdr fully patrolled for safety, SEF left off at Sw 42081. Further investigation required. Excluded OMS 1516350 | October | 2017 | 2018Q2 | 2018 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2017-10-04 | N | 910.68 | N | 5 | N | N | 1.1101 | 39.4971 | 33274.9042
[7 empty] | 7719 | 7676 | 1516586 | 2017-10-05 19:19 | 2017-10-05 20:03 | 44 | 11kV | 10880 | 274 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn80 Chatswood 11kV Panel 36+ tripped on Relays: Panel 36 Translay, Fault Check, EFI Panel 39: Fault Check and EFI Signals: nZE, TX13 Group Earth @ S7712 Artarmon Edward 11kV SW/A tripped on translay Cause: Feeder fault from S47513 to S4059 THIRD FAILURE IN 3 WEEKS IN SAME SECTION See OMS 1517317 1516586 | October | 2017 | 2018Q2 | 2018 | ZN80:PA36 | ZN80:PA36 | ZN00080/000036 | WILLOUGHBY | UG | Not Veg | 2017-10-05 | N | 39.708 | N | 3 | N | N | 1.1101 | 39.4971 | 7950.7831
[7 empty] | 7430 | 4227 | 1516596 | 2017-10-05 21:55 | 2017-10-06 00:58 | 183 | 11kV | 276920 | 1634 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @ZN10994 Mortdale, 11kv Panel 10 'Roberts Ave' feeder tripped, reclosed & tripped Relays: 'B & C' phase O/C. L/O Signals: 11kv trip Abnormal: Sw/B closed at S10654 Lime Kiln Woodlands AB 31165 Open Remarks: Customer reports saw bat fly into HV lines at river crossing Brittany Place Peakhurst Heights. Difficult for staff to see full extent of HV lines across river. Maints to inspect during the day. | October | 2017 | 2018Q2 | 2018 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Not Veg | 2017-10-05 | N | 169.4737 | N | 3 | N | N | 1.1101 | 39.4971 | 202364.9682
[7 empty] | 7800 | 8739 | 1516749 | 2017-10-06 14:27 | 2017-10-06 16:05 | 98 | 11kV | 94903 | 1162 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN2310 Punchbowl Panel 67 'S1055 Penshurst Rd' fdr tripped on Relays: C phase IOC, EFI Signals: 11kv trip Field EFI's operated @ 1055, 1612, 3544 Remarks: UG fault. 11kv UG cable fault from S3544 Moodani Av to S2376 Kerry rogers to S1040 Booragul Street tee S35670 Alkoomie Elouera | October | 2017 | 2018Q2 | 2018 | ZN2310:PA67 | ZN2310:PA25 | ZN02310/000025 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-10-06 | N | 81.6721 | N | 1 | N | N | 1.1101 | 39.4971 | 69352.3132
[7 empty] | 8718 | 20311 | 1516900 | 2017-10-07 18:00 | 2017-10-07 21:08 | 188 | 11kV | 13353 | 72 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Bond | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa9 CP42989 DOp interrutped for lineworkers to replace HDO PT12910 Ferntree Blackbutt HDO was HR See 1517177,9 ex 1516900,3 | October | 2017 | 2018Q2 | 2018 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2017-10-07 | N | 185.4583 | N | 1 | N | N | 1.1101 | 39.4971 | 9757.9786
[7 empty] | 7899 | 9958 | 1517033 | 2017-10-08 21:42 | 2017-10-09 13:00 | 918.35 | 11kV | 11938.55 | 13 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa13 "PEats Ridge Aux" beyond LB61387 Cause:Tree Branch brought down bays of 11kV OH Outisde 10 Lackersteen Rd DOp and lineworkers made safe and Access permits issued | October | 2017 | 2018Q2 | 2018 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2017-10-08 | N | 918.35 | N | 2 | N | N | 1.1101 | 39.4971 | 8724.3402
[7 empty] | 7605 | 6374 | 1517431 | 2017-10-10 04:05 | 2017-10-10 07:10 | 185 | 11kV | 7030 | 38 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty section of pa2 "Bateau Bay" footpath phase burnt off LB40854 See 1517956 ex 1517431 | October | 2017 | 2018Q2 | 2018 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Not Veg | 2017-10-10 | N | 185 | N | 4 | N | N | 1.1101 | 39.4971 | 5137.3167
[7 empty] | 7860 | 9408 | 1517429 | 2017-10-10 02:43 | 2017-10-10 07:35 | 292 | 11kV | 16352 | 56 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 173734 Corrosion Pole fire at pole OS-20186 Pacific St Fishermans Bay. Excluded OMS REPORT NO 1517429. | October | 2017 | 2018Q2 | 2018 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2017-10-10 | N | 292 | N | 4 | N | N | 1.1101 | 39.4971 | 11949.5593
[7 empty] | 8586 | 18652 | 1516997 | 2017-10-08 17:12 | 2017-10-10 13:40 | 2668 | 11kV | 19116 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 173719 Wire down between pole GD-60034 to GD-60033 | October | 2017 | 2018Q2 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2017-10-08 | N | 1274.4 | N | 2 | N | N | 1.1101 | 39.4971 | 13969.409
[7 empty] | 7280 | 1829 | 1517762 | 2017-10-10 16:50 | 2017-10-10 17:20 | 30 | 11kV | 240 | 8 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 173748 Interruption to repair pin insulator pole CI-90209 | October | 2017 | 2018Q2 | 2018 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2017-10-10 | N | 30 | N | 4 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 8721 | 20362 | 1517718 | 2017-10-10 15:23 | 2017-10-10 18:10 | 167 | 11kV | 167 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173750 B Phase DOLF : 10 Amp Excluded OMS 1517718 | October | 2017 | 2018Q2 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2017-10-10 | N | 167 | N | 4 | N | N | 1.1101 | 39.4971 | 122.0387
[7 empty] | 7936 | 10283 | 1517871 | 2017-10-11 07:41 | 2017-10-11 10:25 | 164 | 11kV | 7390 | 68 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge section of Pa8 RE44994 Mangrove Creek has tripped on: Relays: OC trip, Lock out Signals: LB44577 BC phase Overcurrent Cause: not ascertained. fdr patrolled by DOp See 1518340,1,2 ex 1517871 | October | 2017 | 2018Q2 | 2018 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2017-10-11 | N | 108.6765 | N | 3 | N | N | 1.1101 | 39.4971 | 5400.394
[7 empty] | 7956 | 10449 | 1517944 | 2017-10-11 10:07 | 2017-10-11 11:30 | 83 | 11kV | 20431 | 450 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 173758 2 fault operation 3 phase Overcurrent Network rearranged for planned work at time of fault. Sw 40549 closed, ABS 63146 open Excluded OMS 1517944 | October | 2017 | 2018Q2 | 2018 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2017-10-11 | N | 45.4022 | N | 3 | N | N | 1.1101 | 39.4971 | 14930.3722
[7 empty] | 8605 | 18915 | 1518238 | 2017-10-12 04:25 | 2017-10-12 07:25 | 180 | 11kV | 243592 | 1628 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15015 North Head Pa5 "Manly Hospital/FIU" fdr has tripped Signals: 11kv trip, Zone Earth Relays: B phase Earth Fault, EFI EFI's: S16194 S16136 S16721 HV UGOH Addison rd West of Darly Rd S15820 @S16194:B has tripped Relays: Earth trip Cause: UG Fault. Section of 11kv UG Fault is defective from S1582 SwB to S50491 SwA See 1519041,3,4,5,6 ex 1518238 | October | 2017 | 2018Q2 | 2018 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | UG | Not Veg | 2017-10-12 | N | 149.6265 | N | 8 | N | N | 1.1101 | 39.4971 | 178009.8489
[7 empty] | 7635 | 6687 | 1518329 | 2017-10-12 08:05 | 2017-10-12 08:55 | 50 | 11kV | 300 | 6 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 173679 C phase DOLF : 16 Amp Mark said the depot also had a second job sent to them we did not receive 1518249 whish was the same outage. Two dead birds were found and it was determined this was the likely cause of the outage. Excluded OMS 1518294, | October | 2017 | 2018Q2 | 2018 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2017-10-12 | N | 50 | N | 8 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 8265 | 14540 | 1517863 | 2017-10-11 06:27 | 2017-10-12 10:50 | 1703 | 11kV | 3406 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa8 PT13322 George Downes Kyola 2.1 B phase HDO was found to have operated Cause not ascertained See 1519036 ex 1518145 1517863 | October | 2017 | 2018Q2 | 2018 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2017-10-11 | N | 1703 | N | 3 | N | N | 1.1101 | 39.4971 | 2489.0043
[7 empty] | 7273 | 1655 | 1518292 | 2017-10-12 08:01 | 2017-10-12 11:22 | 201 | 11kV | 402 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT11402 FRC1: 329-"High Voltage Fuse - Requires replacement" See 1518292 ex 1522163 | October | 2017 | 2018Q2 | 2018 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2017-10-12 | N | 201 | N | 8 | N | N | 1.1101 | 39.4971 | 293.7697
[7 empty] | 7998 | 11070 | 1518275 | 2017-10-12 06:58 | 2017-10-12 11:23 | 265 | 11kV | 86151 | 1729 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 173829 3 fault operations A & C phase Overcurrent, Earth Fault Cable fault between UGOH ans Sw 56661 Dora Ck WWTW No 2. Excluded OMS 1518275 | October | 2017 | 2018Q2 | 2018 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | UG | Not Veg | 2017-10-12 | N | 49.8271 | N | 8 | N | N | 1.1101 | 39.4971 | 62956.6098
[7 empty] | 7560 | 5939 | 1518393 | 2017-10-12 10:58 | 2017-10-12 13:33 | 155 | 11kV | 2325 | 15 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 173774 3 fault operations Overcurrent Excavating property brought down mains on tee to sub 48061. 2 spans removed and A Regan sending in SAO to decommission sub 48061 as customer said sub no longer required. | October | 2017 | 2018Q2 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2017-10-12 | N | 155 | N | 8 | N | N | 1.1101 | 39.4971 | 1699.0414
[7 empty] | 8677 | 19774 | 1518443 | 2017-10-12 14:36 | 2017-10-12 16:10 | 94 | 11kV | 27067 | 1915 | HV | Animal Possum | Animal | Pole | Unplanned | No Weather Impact | N | LID 173787 Pole fire - de-energised for safety Excluded OMS 1518453 | October | 2017 | 2018Q2 | 2018 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2017-10-12 | N | 14.1342 | N | 8 | N | N | 1.1101 | 39.4971 | 19779.7653
[7 empty] | 7955 | 10420 | 1518450 | 2017-10-12 14:35 | 2017-10-12 17:00 | 145 | 11kV | 2900 | 20 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173788 B & C phase DOLF : 10 Amp Tree fell onto mains blew both B and C phase fuses, A phase fuse was opened momentarily when clearing tree from mains. Excluded OMS 1518450, 1518454 | October | 2017 | 2018Q2 | 2018 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2017-10-12 | N | 145 | N | 8 | N | N | 1.1101 | 39.4971 | 2119.2345
[7 empty] | 7337 | 2786 | 1518458 | 2017-10-12 15:07 | 2017-10-12 23:11 | 484 | 11kV | 141968 | 1504 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 173789 Pole fire JV-40015 Section isolated for repairs | October | 2017 | 2018Q2 | 2018 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2017-10-12 | N | 94.3936 | N | 8 | N | N | 1.1101 | 39.4971 | 103746.0271
[7 empty] | 7495 | 5261 | 1518578 | 2017-10-13 07:29 | 2017-10-13 09:30 | 121 | 11kV | 242 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173793 A Phase DOLF : 10 Amp Excluded OMS 1518578 | October | 2017 | 2018Q2 | 2018 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2017-10-13 | N | 121 | N | 2 | N | N | 1.1101 | 39.4971 | 176.8465
[7 empty] | 8468 | 17238 | 1518744 | 2017-10-13 23:25 | 2017-10-14 02:35 | 190 | 11kV | 11336 | 62 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2196 Milperra Panel #6 'S.6224 Carrington Violet' feeder has tripped on: Signals: 11kv trip, TX3 GE, Zone earth Relays: Earth fault, fault check, EFI Remarks: UG fault. 11kv UG feeder fault - 11kv UG feeder I&E'd from S.8115 Violet St No.6(Sw/B) to S.5071 Violet St No.3 (Sw/A) | October | 2017 | 2018Q2 | 2018 | ZN2196:PA6 | ZN2196:PA6 | ZN02196/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-10-13 | N | 182.8387 | N | 2 | N | N | 1.1101 | 39.4971 | 8284.0144
[7 empty] | 8676 | 19757 | 1518859 | 2017-10-14 19:04 | 2017-10-14 22:05 | 181 | 11kV | 101360 | 560 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | Ex Zn15009 Manly section of Pa7 "Birkley Raglan" 11kv LK23505 centre phase hinge on link burnt off Low Volts to S17080 PT15206 and PT15551 See 1519061 ex 1518859 | October | 2017 | 2018Q2 | 2018 | ZN15009:PA7 | ZN15009:PA7 | ZN15009/000007 | NORTHERN BEACHES | OH | Not Veg | 2017-10-14 | N | 181 | N | 1 | N | N | 1.1101 | 39.4971 | 74070.8984
[7 empty] | 7340 | 2804 | 1518908 | 2017-10-15 09:22 | 2017-10-15 10:55 | 93 | 11kV | 279 | 3 | HV | Animal Frog | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173808 A Phase DOLF : 10 Amp Excluded OMS 1518908 | October | 2017 | 2018Q2 | 2018 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2017-10-15 | N | 93 | N | 4 | N | N | 1.1101 | 39.4971 | 203.885
[7 empty] | 8703 | 20114 | 1518911 | 2017-10-15 09:33 | 2017-10-15 13:30 | 237 | 11kV | 711 | 3 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa33 "Holgate" fdr PT11479 The Ridgeway Paroo 1.2 2X16A HDO's Cause: Tree branch contact other See 1519068 ex 1518911,3,9064 | October | 2017 | 2018Q2 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2017-10-15 | N | 237 | N | 4 | N | N | 1.1101 | 39.4971 | 519.5778
[7 empty] | 7507 | 5461 | 1518981 | 2017-10-15 23:19 | 2017-10-16 00:52 | 93 | 11kV | 96348 | 1036 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1673 Turramurra Panel 7 tripped on Relays: C phase IOC Signals: TX2 Group Earth, Fault Check and efi Cause: Possum on PT1561 - Mains down at 86 Billyard due to LV parallel See OMS 1515981 1518983 1518984 1518982 | October | 2017 | 2018Q2 | 2018 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Not Veg | 2017-10-15 | N | 93 | N | 4 | N | N | 1.1101 | 39.4971 | 70408.2766
[7 empty] | 7840 | 9240 | 1518979 | 2017-10-15 23:00 | 2017-10-16 15:25 | 984.5833 | 11kV | 3938.3333 | 4 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 173812 pole fire & broken xarm at sub 72141 section isolated to make repairs Excluded oms 1518979 | October | 2017 | 2018Q2 | 2018 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2017-10-15 | N | 984.5833 | N | 4 | N | N | 1.1101 | 39.4971 | 2878.0178
[7 empty] | 8578 | 18563 | 1519306 | 2017-10-16 13:45 | 2017-10-16 19:05 | 320 | 11kV | 640 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173828 A Phase DOLF : 10 Amp Bird nest Excluded OMS 1519153 | October | 2017 | 2018Q2 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2017-10-16 | N | 320 | N | 1 | N | N | 1.1101 | 39.4971 | 467.6931
[7 empty] | 8532 | 17972 | 1519279 | 2017-10-17 03:33 | 2017-10-17 05:15 | 102 | 11kV | 134515 | 1577 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Panel 3 tripped on Relays: A and C phase OC Signals 11kV Trip Field EFI's Nil Cause: Suspected defective surge arrestor @ PT1273 Tambourine Bay Rd - To Inspect in Daylight See OMS 1519311 1519312 1519313 1519280 1519279 | October | 2017 | 2018Q2 | 2018 | ZN129:PA3 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Not Veg | 2017-10-17 | N | 85.298 | N | 5 | N | N | 1.1101 | 39.4971 | 98299.5945
[7 empty] | 7309 | 2313 | 1519291 | 2017-10-17 08:02 | 2017-10-17 08:50 | 48 | 11kV | 5856 | 122 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 173833 A Phase DOLF : 40 Amp 40 amp A phase DOLF carrier burnt up replaced supply back on 0850hrs Excluded OMS 1519291 | October | 2017 | 2018Q2 | 2018 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2017-10-17 | N | 48 | N | 5 | N | N | 1.1101 | 39.4971 | 4279.3921
[7 empty] | 8088 | 12268 | 1519328 | 2017-10-17 11:01 | 2017-10-17 14:11 | 190 | 11kV | 8740 | 46 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 173837 A Phase No protection deviced operates, cross arm burnt through and one conductor fell just above ground level at pole FP-90647. Interription for safety and to allow repairs. Cross arm and 3 insulators were replaced. Excluded OMS 1519328 | October | 2017 | 2018Q2 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2017-10-17 | N | 190 | N | 5 | N | N | 1.1101 | 39.4971 | 6386.9342
[7 empty] | 8024 | 11338 | 1519423 | 2017-10-17 14:40 | 2017-10-17 16:45 | 125 | 11kV | 80840 | 715 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn9700 Kirrawee - Ex Pnl.23 iR63641 Manchester View - tripped, reclosed and tripped on: O/C Suspected UG cable fault. Contractors found digging on corner Walker Ave & Forest Rd PT77682 restored via LV //'s 232, 233 & 244 See 1519546 1519547 | October | 2017 | 2018Q2 | 2018 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | UG | Not Veg | 2017-10-17 | N | 113.0629 | N | 5 | N | N | 1.1101 | 39.4971 | 59075.4876
[7 empty] | 7993 | 10953 | 1519519 | 2017-10-17 23:23 | 2017-10-18 00:26 | 63 | 11kV | 206741 | 3307 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde Panel 24 tripped on Signals: 11kV Trip Relays: 24R A/B phase OC Cause Not ascertained for outage See OMS 1519938 1519939 1519520 1519521 1519519 | October | 2017 | 2018Q2 | 2018 | ZN35500:PA24 | ZN35500:PA24 | ZN35500/000024 | RYDE | OH | Veg | 2017-10-17 | N | 62.5162 | N | 5 | N | N | 1.1101 | 39.4971 | 151080.225
[7 empty] | 8377 | 15887 | 1519618 | 2017-10-18 15:30 | 2017-10-18 16:30 | 60 | 11kV | 2880 | 48 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow panel 13 "brush rd" Tree on CT adj to AB44309 isolated between RE42086 North Lisarow to LB40982 for linesman to remove tree | October | 2017 | 2018Q2 | 2018 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2017-10-18 | N | 60 | N | 1 | N | N | 1.1101 | 39.4971 | 2104.6191
[7 empty] | 7820 | 8935 | 1519735 | 2017-10-19 00:34 | 2017-10-19 07:06 | 392 | 11kV | 29400 | 75 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173851 C Phase DOLF : 50 Amp Extended outage due to despatch not despatching job till 0617hrs Sub 49556 C phase 50A DOLF cause possum supply back on 0706hrs Excluded OMS 1519735 | October | 2017 | 2018Q2 | 2018 | 224:80341 | 224:80341 | ZN00224/080341 | LAKE MACQUARIE | OH | Not Veg | 2017-10-19 | N | 392 | N | 6 | N | N | 1.1101 | 39.4971 | 21484.6528
[7 empty] | 8515 | 17783 | 1519748 | 2017-10-19 07:12 | 2017-10-19 09:04 | 112 | 11kV | 222825 | 2299 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zb10999 Kogarah - Pn.38 tripped on: IOC (A & B phase), Earth Fault Field EFIs: S62735 Truck hit pole corner West Botany St and Bermal Lane (Rego TB26YT) See 1520173 1520174 | October | 2017 | 2018Q2 | 2018 | ZN10999:PA38 | ZN10999:PA38 | ZN10999/000038 | BAYSIDE | OH | Not Veg | 2017-10-19 | N | 96.9226 | N | 6 | N | N | 1.1101 | 39.4971 | 162833.9378
[7 empty] | 7238 | 1073 | 1519793 | 2017-10-19 10:09 | 2017-10-19 11:12 | 63 | 11kV | 3839 | 63 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2196 Milperra Panel 6 "S6224" feeder has tripped Signals: 11kv trip Relays: EFOC, EFI, LO Field EFI's: As expected Remarks: UG fault between Sw/B @ S3688 Violet Peters, Sw/A @ S6182 Violet St No.5 and sw/B @ S4570 Carrington Fitz | October | 2017 | 2018Q2 | 2018 | ZN2196:PA6 | ZN2196:PA6 | ZN02196/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-10-19 | N | 60.9365 | N | 6 | N | N | 1.1101 | 39.4971 | 2805.428
[7 empty] | 8242 | 14360 | 1519816 | 2017-10-19 11:38 | 2017-10-19 12:18 | 40 | 11kV | 85710 | 2419 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9252 jannali - Pnl.28 tripped on: Overcurrent wit EFI Abnormal: Sw/B @ S9034 Open with LB46625 closed. Sw/A @ S9240 Closed with AB3517 Open UG cable fault from S9343 (Sw/A) to S9689 (Sw/A) See1520220 150221 1520224 | October | 2017 | 2018Q2 | 2018 | ZN9252:PA28 | ZN9252:PA28 | ZN09252/000028 | SUTHERLAND | UG | Not Veg | 2017-10-19 | N | 35.432 | N | 6 | N | N | 1.1101 | 39.4971 | 62634.34
[7 empty] | 7821 | 8948 | 1519834 | 2017-10-19 11:48 | 2017-10-19 14:50 | 182 | 11kV | 46212 | 678 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1673 Turramurraq Panel 18 tripped and locked out on Relays: A and B phase OC and timingt lockout Signals: A and B phase 11kV trip Cause: Tree branch brought down 11kV OH OS 137-147 Comenarra Pkwy Section of 11kV down from LB238 to NO AB2209 tee PT1334 Hicks Ave High into Low at PT1334 See OMS 1520842 1520843 1520844 1519834/9858/9839/9840 | October | 2017 | 2018Q2 | 2018 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Veg | 2017-10-19 | N | 68.1593 | N | 6 | N | N | 1.1101 | 39.4971 | 33770.3666
[7 empty] | 8416 | 16528 | 1519969 | 2017-10-19 20:34 | 2017-10-19 20:54 | 20 | 11kV | 72560 | 3628 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At S187 Crows Nest Panel 16 tripped on Relays: Pa16 Crows Nest tripped on B phase OC S3382 West Church. Diff fuse relay. IT Send Signals: 11kV Trip Cause: Suspect TX Fault @ S3382 or UG cable Fault At S187 Crows Nest 11kV Panel 20 tripped on Relays: IT Receive Cause: I/T Link left closed on Panel 20 See OMS 1520852 1519970 1519969 | October | 2017 | 2018Q2 | 2018 | ZN187:PA20 | ZN187:PA20 | ZN00187/000020 | NORTH SYDNEY | UG | Not Veg | 2017-10-19 | N | 20 | N | 6 | N | N | 1.1101 | 39.4971 | 53024.7078
[7 empty] | 7451 | 4687 | 1520110 | 2017-10-20 07:25 | 2017-10-20 09:10 | 105 | 11kV | 89051 | 1073 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde Panel 22 tripped on Signals: 11kV trip, TX2 Group Earth Relays: Earth Fault, EFI, Reclose Lockout Relay Field EFI's Nil Cause: 11kV UGOH damage adjacent to S6898 Smalls Fawcett UGOH Short Circuit See OMS 1520883 1520884 1520886 1520110 1520128 | October | 2017 | 2018Q2 | 2018 | ZN35500:PA22 | ZN35500:PA22 | ZN35500/000022 | RYDE | Unknown | Unknown | 2017-10-20 | N | 82.9925 | N | 4 | N | N | 1.1101 | 39.4971 | 65075.8442
[7 empty] | 8243 | 14361 | 1520064 | 2017-10-20 06:40 | 2017-10-20 10:56 | 256 | 11kV | 834991 | 3674 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | At S10995 Riverwood - 11kv Panel 2 "Bonds Rd" tripped, reclosed & locked out on: Relays: C phase IOC & Timed, Lockout, Timing Signals: 11kv trip Abnormal: close at S10720 Penshurts Nicholson, Open at LB30062 Remarks: transformer failure. Multiple faults found on feeder. Possible PT63013 failure has caused HV Oh to twist together adj PT63013. Trying back feeder after first issue was rectified has caused an open circuit bond at UGOH adj USL30458 due to high in rush current. Possum also found bridging phases at PT10896 Bassett Warwick | October | 2017 | 2018Q2 | 2018 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | OH | Not Veg | 2017-10-20 | N | 227.2703 | N | 4 | N | N | 1.1101 | 39.4971 | 610186.7947
[7 empty] | 8498 | 17591 | 1520497 | 2017-10-20 23:19 | 2017-10-21 02:20 | 181 | 11kV | 146530 | 978 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 44 tripped, relosed tripped and locked out on Signals: 11kV Trip, TX1 Group Earth, Zone Earth Relays: Earth Fault, Timing, Lockout, EFI, Fault Check, TX1 Protection Panel B: EF Check. Cause: MVA into pole near HV UGOH to CP1305. See OMS 1520960 1520963 1520962 1520497 | October | 2017 | 2018Q2 | 2018 | ZN847:PA44 | ZN847:PA44 | ZN00847/000044 | HORNSBY | OH | Not Veg | 2017-10-20 | N | 149.8262 | N | 4 | N | N | 1.1101 | 39.4971 | 107079.8021
[7 empty] | 8511 | 17715 | 1520495 | 2017-10-20 23:09 | 2017-10-21 05:15 | 366 | 11kV | 37707 | 154 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of Pa3 "manbgrove Mtn" RE45071 Central Mangrove tripped/reclosed/tripped Relays: EF Trip Cause: vehicle hit pole on wisemans Ferry Rd, HV Mains isolated from RE45071 to LB49261 to LB49207 for repairs by LW See 1520975,6,7 ex 1520495,9,502 | October | 2017 | 2018Q2 | 2018 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2017-10-20 | N | 244.8506 | N | 4 | N | N | 1.1101 | 39.4971 | 27555.1634
[7 empty] | 8694 | 19955 | 1520503 | 2017-10-21 03:45 | 2017-10-21 11:25 | 460 | 11kV | 85810 | 892 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 173874 2 fault operations A & B phase Instantaneous Overcurrent Sw 49154 also locked out at same time O/C. CAR HIT POLE VP- 10395 Fishery Point Rd, Morisset. Repairs completed Excluded OMS REPORT 1520505, 1520504, 1520503. | October | 2017 | 2018Q2 | 2018 | 243:80084 | 243:80084 | ZN00243/080084 | LAKE MACQUARIE | OH | Not Veg | 2017-10-21 | N | 96.1996 | N | 2 | N | N | 1.1101 | 39.4971 | 62707.417
[7 empty] | 8561 | 18366 | 1520622 | 2017-10-21 18:53 | 2017-10-22 09:35 | 882 | 11kV | 14988 | 135 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | U/G Cable | Unplanned | No Weather Impact | N | At ZN2196 Milperra 11kv Panel 20 "Marigold Milperra #3" tripped on: Relays: earth fault Signals: 11kv trip, Tx2 group, Zone earth with efi Field EFI's: Panel 20 to S4175 Abnormal: Sw/B closed at S1611 and Sw/A opened at S6182 Remarks: not known. Difficult access to substations. No access to S6182. No fault found - for RTS | October | 2017 | 2018Q2 | 2018 | ZN2196:PA20 | ZN2196:PA20 | ZN02196/000020 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-10-21 | N | 111.0222 | N | 2 | N | N | 1.1101 | 39.4971 | 10952.7883
[7 empty] | 8461 | 17144 | 1520671 | 2017-10-22 11:23 | 2017-10-22 13:35 | 132 | 11kV | 528 | 4 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 173882 B Phase DOLF : 10 Amp Rainbow Parrot Excluded oms 1520671. | October | 2017 | 2018Q2 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2017-10-22 | N | 132 | N | 3 | N | N | 1.1101 | 39.4971 | 385.8468
[7 empty] | 7968 | 10569 | 1520653 | 2017-10-22 08:25 | 2017-10-22 18:45 | 620 | 11kV | 10540 | 17 | HV | Arcing | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 173884 Pole fire Excluded OMS 1520653, 1520644 | October | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2017-10-22 | N | 620 | N | 3 | N | N | 1.1101 | 39.4971 | 7702.3211
[7 empty] | 7691 | 7249 | 1520756 | 2017-10-22 23:18 | 2017-10-23 00:36 | 78 | 11kV | 2734 | 37 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S129 Hunters Hill panel 4 tripped on Relays: A phase O/C, Inst, Timed Signals: 11kV trip Cause: UG fault from S4166 to S3941 to S6348 See OMS 1520863 1520865 15207856 | October | 2017 | 2018Q2 | 2018 | ZN129:PA4 | ZN129:PA63 | ZN00129/000063 | LANE COVE | UG | Not Veg | 2017-10-22 | N | 73.8919 | N | 3 | N | N | 1.1101 | 39.4971 | 1997.9266
[7 empty] | 8009 | 11214 | 1520805 | 2017-10-23 01:12 | 2017-10-23 03:10 | 118 | 11kV | 354 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 173890 A Phase DOLF : 10 Amp see also FDR trip & reclose Excluded oms report no 1520805. report no 173887. | October | 2017 | 2018Q2 | 2018 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2017-10-23 | N | 118 | N | 4 | N | N | 1.1101 | 39.4971 | 258.6928
[7 empty] | 7569 | 6025 | 1520903 | 2017-10-23 03:45 | 2017-10-23 05:45 | 120 | 11kV | 38040 | 317 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | Related to LID 173892 1 fault operation Tree into mains at 90 old belmont rd (Pole # 308371) .11kv isolated for safety reasons refer to LV job OMS 1520902 | October | 2017 | 2018Q2 | 2018 | 220:8687 | 220:8687 | ZN00220/008687 | LAKE MACQUARIE | OH | Veg | 2017-10-23 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 27798.51
[7 empty] | 8399 | 16305 | 1520950 | 2017-10-23 01:30 | 2017-10-23 10:30 | 540 | 11kV | 6480 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 173898 B & C Phase DOLF : 20 Amp Please patrol. All 3 ph LF replaced. No clause found. Storm last night Excluded OMS:1520950 | October | 2017 | 2018Q2 | 2018 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2017-10-23 | N | 540 | N | 4 | N | N | 1.1101 | 39.4971 | 4735.3929
[7 empty] | 7522 | 5587 | 1520809 | 2017-10-23 02:44 | 2017-10-23 17:00 | 856 | 11kV | 33807 | 115 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 173891 Mains down at pole MG-50037 spur to sub 16317. Restored rest of feeder. Opened taps at pole MG-50032 to repair mains. S.A. Excluded oms 1520809. 1520937, 1520874 | October | 2017 | 2018Q2 | 2018 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2017-10-23 | N | 293.9739 | N | 4 | N | N | 1.1101 | 39.4971 | 24705.1585
[7 empty] | 7662 | 6931 | 1521130 | 2017-10-24 05:05 | 2017-10-24 08:10 | 185 | 11kV | 132815 | 1000 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35900 Potts Hills Panel 20 tripped on Relays: Earth Fault, EFI Signals: TX2 Group Earth, 11kV Trip Cause: UG fault in section of 11kV feededr between S4475 to AB505 to LB1412 tee PT2408 See OMS 15121696 1521697 1521699 15121130 1521132 1521142 | October | 2017 | 2018Q2 | 2018 | ZN35900:PA20 | ZN35900:PA20 | ZN35900/000020 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-10-24 | N | 132.815 | N | 2 | N | N | 1.1101 | 39.4971 | 97057.2846
[7 empty] | 8090 | 12286 | 1521225 | 2017-10-24 12:09 | 2017-10-24 19:00 | 411 | 11kV | 225743 | 1723 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill - Pnl.15 tripped on: Earth Leakage with EFI Field EFIs: S5048 & S2583 After replacemet of RMI @ S2583 - UG cable fault from S2583 (Sw/B) to S8972 (Sw/A) to S5067 (Sw/A) See 1521457 1521458 1521459 | October | 2017 | 2018Q2 | 2018 | ZN398:PA15 | ZN398:PA15 | ZN00398/000015 | INNER WEST | UG | Not Veg | 2017-10-24 | N | 131.0174 | N | 2 | N | N | 1.1101 | 39.4971 | 164966.3261
[7 empty] | 7336 | 2767 | 1521380 | 2017-10-25 07:33 | 2017-10-25 08:28 | 55 | 11kV | 2520 | 46 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 173913 1 fault operation 3 phase Overcurrent Excluded OMS 1521380 | October | 2017 | 2018Q2 | 2018 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2017-10-25 | N | 54.7826 | N | 4 | N | N | 1.1101 | 39.4971 | 1841.5417
[7 empty] | 8101 | 12536 | 1521370 | 2017-10-25 06:22 | 2017-10-25 14:15 | 472.9167 | 11kV | 9458.3333 | 20 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of pa12 Autolink 44778 16 Amp HDO operated Relays: SEL, EFI, Fault Check, TX2 EF, Fault Check Signals: Group Earth EFI's: S47609 S18485 S18630 S47409 Cause: UG Fault. Surge Diverters and UGOH failed. Lineworker to repairs CC1: 22-"Refer to SOp" FRC1: 329-"High Voltage Fuse - Requires replacement" | October | 2017 | 2018Q2 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | Unknown | Unknown | 2017-10-25 | N | 472.9167 | N | 4 | N | N | 1.1101 | 39.4971 | 6911.871
[7 empty] | 7597 | 6261 | 1521486 | 2017-10-25 14:07 | 2017-10-25 19:00 | 293 | 11kV | 30668 | 326 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Ex Zn15014 Mona Vale section of Pa14 RE22381 Lane Cove Walter tripped, reclosed and locked out on overcurrent trip, IOC trip Cause: DOp found broken HV cross arm adjacent to PT15577 on Walter Rd at Ingleside See 1521748,50,1 ex 1521486,517 | October | 2017 | 2018Q2 | 2018 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Not Veg | 2017-10-25 | N | 94.0736 | N | 4 | N | N | 1.1101 | 39.4971 | 22411.2698
[7 empty] | 7323 | 2560 | 1521569 | 2017-10-25 21:23 | 2017-10-25 22:05 | 42 | 11kV | 39144 | 932 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | 11kV Bond open circuit on first UGOH beyond LB30715 Ex Pnl.12 Sans Souci | October | 2017 | 2018Q2 | 2018 | ZN10997:PA12 | ZN10997:PA12 | ZN10997/000012 | BAYSIDE | OH | Not Veg | 2017-10-25 | N | 42 | N | 4 | N | N | 1.1101 | 39.4971 | 28605.2806
[7 empty] | 7471 | 4988 | 1521584 | 2017-10-26 03:26 | 2017-10-26 05:40 | 134 | 11kV | 134 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 173929 Single phase DOLF : 10 Amp REPLACED DOLF & CARRIER. Excluded OMS 1521584. | October | 2017 | 2018Q2 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-10-26 | N | 134 | N | 21 | Y | Y | 1.1101 | 39.4971 | 97.9232
[7 empty] | 8418 | 16534 | 1521596 | 2017-10-26 06:58 | 2017-10-26 09:27 | 149 | 11kV | 70063 | 515 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35800 Bankstown Panel 19 "S6696 and S3050 feeer has tripped Signals: 11kv trip Relays: B, C phase O/C, Earth fault, EFI Field EFI's: S3050, S2468, S64351, S6413 EFI's did not operate at UGOH fairford/Gow and S3514 Kylie Joyce REmarks: UG fault cause not ascertained. 11kv feeder isolated S3514 Kylie Joyce Sw/B to S6413 Carlton Blenmans Sw/A. See separrate interruption on panel 21 at ZN35800 Bankstown due to failed restoration on closing Sw/B at S2468. | October | 2017 | 2018Q2 | 2018 | ZN35800:PA19 | ZN35800:PA19 | ZN35800/000019 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-10-26 | N | 136.0447 | N | 21 | Y | Y | 1.1101 | 39.4971 | 51199.9739
[7 empty] | 8501 | 17647 | 1521665 | 2017-10-26 14:02 | 2017-10-26 18:45 | 283 | 11kV | 283 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 173945 Single phase sub 72269 isolated to replace tx | October | 2017 | 2018Q2 | 2018 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2017-10-26 | N | 283 | N | 21 | Y | Y | 1.1101 | 39.4971 | 206.8081
[7 empty] | 7349 | 2888 | 1521811 | 2017-10-26 19:16 | 2017-10-26 20:00 | 44 | 11kV | 88 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 173950 A Phase DOLF : 10 Amp Excluded OMS 1521811 | October | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-10-26 | N | 44 | N | 21 | Y | Y | 1.1101 | 39.4971 | 64.3078
[7 empty] | 7456 | 4725 | 1521806 | 2017-10-26 18:56 | 2017-10-26 20:05 | 69 | 11kV | 345 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 173952 B Phase DOLF : 10 Amp Excluded OMS 1521806 | October | 2017 | 2018Q2 | 2018 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2017-10-26 | N | 69 | N | 21 | Y | Y | 1.1101 | 39.4971 | 252.1158
[7 empty] | 7271 | 1626 | 1521829 | 2017-10-26 21:10 | 2017-10-26 21:50 | 40 | 11kV | 560 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 173982 C Phase DOLF : 20 Amp Excluded OMS 1521829 | October | 2017 | 2018Q2 | 2018 | 265:81648 | 265:81648 | ZN00265/081648 | PORT STEPHENS | OH | Veg | 2017-10-26 | N | 40 | N | 21 | Y | Y | 1.1101 | 39.4971 | 409.2315
[7 empty] | 7198 | 401 | 1521819 | 2017-10-26 19:54 | 2017-10-26 21:51 | 117 | 11kV | 38142 | 326 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 173998 2 fault operations B & C Phase Overcurrent Excluded OMS 1521819 | October | 2017 | 2018Q2 | 2018 | 233:82813 | 233:82813 | ZN00233/082813 | PORT STEPHENS | OH | Not Veg | 2017-10-26 | N | 117 | N | 21 | Y | Y | 1.1101 | 39.4971 | 27873.0486
[7 empty] | 7847 | 9320 | 1521815 | 2017-10-26 19:45 | 2017-10-26 22:38 | 173 | 11kV | 92804 | 568 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 173959 2 fault operations A & B phase Overcurrent Excluded OMS 1521815 & 1521818 | October | 2017 | 2018Q2 | 2018 | 264:81238 | 264:81238 | ZN00264/081238 | PORT STEPHENS | OH | Veg | 2017-10-26 | N | 163.3873 | N | 21 | Y | Y | 1.1101 | 39.4971 | 67818.4259
[7 empty] | 7399 | 3826 | 1521859 | 2017-10-27 00:15 | 2017-10-27 01:23 | 68 | 11kV | 111285 | 1914 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174010 2 fault operations 3 phase Overcurrent Excluded OMS 1521859 | October | 2017 | 2018Q2 | 2018 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Veg | 2017-10-27 | N | 58.1426 | N | 21 | Y | Y | 1.1101 | 39.4971 | 81323.7956
[7 empty] | 7745 | 7989 | 1521844 | 2017-10-26 23:04 | 2017-10-27 01:30 | 146 | 11kV | 30708 | 213 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174007 2 fault operations Overcurrent Excluded OMS 1521844 | October | 2017 | 2018Q2 | 2018 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2017-10-26 | N | 144.169 | N | 21 | Y | Y | 1.1101 | 39.4971 | 22440.5007
[7 empty] | 7436 | 4411 | 1521848 | 2017-10-26 23:38 | 2017-10-27 01:49 | 131 | 11kV | 33606 | 522 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174008 2 fault operations Instantaneous Overcurrent Excluded OMS 1521848 | October | 2017 | 2018Q2 | 2018 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-10-26 | N | 64.3793 | N | 21 | Y | Y | 1.1101 | 39.4971 | 24558.2736
[7 empty] | 7633 | 6654 | 1521876 | 2017-10-27 01:17 | 2017-10-27 01:59 | 42.2167 | 11kV | 40401.35 | 957 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | Zn12690 Berkeley Vale Panel 8 tripped, reclosed and locked out on: Relays: A&B Phase IOC lock out and timing Signals: 11kv trip Cause: Tree/Branch on OH mains on LB44564 See 1521876 ex 1521879 | October | 2017 | 2018Q2 | 2018 | ZN12690:PA8 | ZN12690:PA8 | ZN12690/000008 | CENTRAL COAST | OH | Veg | 2017-10-27 | N | 42.2167 | N | 21 | Y | Y | 1.1101 | 39.4971 | 29524.1149
[7 empty] | 7909 | 10002 | 1521830 | 2017-10-26 21:34 | 2017-10-27 04:45 | 431 | 11kV | 130884 | 1074 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 174016 2 fault operations Overcurrent; Earth Fault 33kv mains into 11kv mains at pole OR-8270 Anna Bay. Excluded oms report no 1521830. | October | 2017 | 2018Q2 | 2018 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2017-10-26 | N | 121.8659 | N | 21 | Y | Y | 1.1101 | 39.4971 | 95646.1668
[7 empty] | 7361 | 3091 | 1521885 | 2017-10-27 01:26 | 2017-10-27 06:06 | 280 | 11kV | 93629 | 1505 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 174013 2 fault operations A Phase Overcurrent, Earth Fault broken pin insulator pole JV-40027. Excluded oms 1521904 & 1521885. | October | 2017 | 2018Q2 | 2018 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2017-10-27 | N | 62.212 | N | 21 | Y | Y | 1.1101 | 39.4971 | 68421.3116
[7 empty] | 7472 | 4998 | 1522696 | 2017-10-26 23:54 | 2017-10-27 06:50 | 416 | 11kV | 34112 | 82 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 174053 3 fault operations Earth Fault Faulty L/A pole IP-74621 excluded OMS 1521853, 1522011 | October | 2017 | 2018Q2 | 2018 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2017-10-26 | N | 416 | N | 21 | Y | Y | 1.1101 | 39.4971 | 24928.0435
[7 empty] | 7969 | 10590 | 1521913 | 2017-10-27 05:41 | 2017-10-27 07:20 | 99 | 11kV | 198 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174017 A Phase DOLF : 10 Amp Excluded OMS 1521913 | October | 2017 | 2018Q2 | 2018 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2017-10-27 | N | 99 | N | 21 | Y | Y | 1.1101 | 39.4971 | 144.6926
[7 empty] | 7972 | 10647 | 1521858 | 2017-10-27 00:16 | 2017-10-27 07:21 | 425 | 11kV | 128591 | 1015 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 174011 2 fault operations A Phase Overcurrent; Instantaneous Overcurrent Excluded OMS 1521858 | October | 2017 | 2018Q2 | 2018 | 203:8084 | 204:82689 | ZN00204/082689 | NEWCASTLE | OH | Not Veg | 2017-10-27 | N | 126.6906 | N | 21 | Y | Y | 1.1101 | 39.4971 | 93970.51
[7 empty] | 7573 | 6061 | 1521849 | 2017-10-26 23:42 | 2017-10-27 08:30 | 528 | 11kV | 42920 | 164 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 174029 3 fault operations C phase Earth Fault Defective Lightning arrestor pole FR-42414 Excluded OMS 1521849 & 1521966 | October | 2017 | 2018Q2 | 2018 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2017-10-26 | N | 261.7073 | N | 21 | Y | Y | 1.1101 | 39.4971 | 31364.6701
[7 empty] | 7282 | 1856 | 1521933 | 2017-10-27 07:16 | 2017-10-27 08:40 | 84 | 11kV | 84 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174026 Single phase DOLF : 10 Amp Excluded OMS 1521933 | October | 2017 | 2018Q2 | 2018 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-10-27 | N | 84 | N | 21 | Y | Y | 1.1101 | 39.4971 | 61.3847
[7 empty] | 7540 | 5728 | 1521843 | 2017-10-26 23:06 | 2017-10-27 08:55 | 588.55 | 11kV | 12359.55 | 21 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Electrical Storm | N | LID 174028 B & C phase 20A fuses replaced Line fuses 63353 | October | 2017 | 2018Q2 | 2018 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Not Veg | 2017-10-26 | N | 588.55 | N | 21 | Y | Y | 1.1101 | 39.4971 | 9031.9946
[7 empty] | 7468 | 4978 | 1521854 | 2017-10-27 00:13 | 2017-10-27 09:00 | 527 | 11kV | 2108 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174024 B Phase DOLF : 10 Amp Excluded OMS 1521854 | October | 2017 | 2018Q2 | 2018 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2017-10-27 | N | 527 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1540.4642
[7 empty] | 8019 | 11303 | 1521954 | 2017-10-27 07:08 | 2017-10-27 09:00 | 112 | 11kV | 784 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174025 A & B phase DOLF : 20 Amp Excluded OMS 1521954 | October | 2017 | 2018Q2 | 2018 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2017-10-27 | N | 112 | N | 21 | Y | Y | 1.1101 | 39.4971 | 572.9241
[7 empty] | 8422 | 16597 | 1521912 | 2017-10-27 05:28 | 2017-10-27 09:00 | 212 | 11kV | 848 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174022 A & B Phase DOLF : 16 Amp Excluded OMS 1521912 | October | 2017 | 2018Q2 | 2018 | 813:89065 | 813:89065 | ZN00813/089065 | UPPER HUNTER | OH | Veg | 2017-10-27 | N | 212 | N | 21 | Y | Y | 1.1101 | 39.4971 | 619.6934
[7 empty] | 7782 | 8483 | 1521842 | 2017-10-26 22:58 | 2017-10-27 10:35 | 697 | 11kV | 36312 | 180 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174041 2 fault operations Sensitive Earth Fault Tx Faulty. Too wet to replace OMS jobs incompleted. DMA tag attached to sub in DNMS. All customers restored by 27/10/17 @ 847hrs. Except faulty sub. Excluded OMS 1521948 1521842 | October | 2017 | 2018Q2 | 2018 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2017-10-26 | N | 201.7333 | N | 21 | Y | Y | 1.1101 | 39.4971 | 26535.7386
[7 empty] | 8612 | 19008 | 1521971 | 2017-10-27 07:44 | 2017-10-27 11:00 | 196 | 11kV | 196 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174031 C Phase DOLF : 10 Amp Excluded OMS 1521971 | October | 2017 | 2018Q2 | 2018 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2017-10-27 | N | 196 | N | 21 | Y | Y | 1.1101 | 39.4971 | 143.231
[7 empty] | 8362 | 15672 | 1521838 | 2017-10-26 22:21 | 2017-10-27 11:15 | 774 | 11kV | 25383 | 146 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174009 2 fault operations A Phase DOLF : 10 Amp Overcurrent, Earth Fault, Substation DOLF Faulty Tx at R Ellis sub 71825. SAO required Excluded OMS No. 1521838 + 1521893 | October | 2017 | 2018Q2 | 2018 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2017-10-26 | N | 173.8562 | N | 21 | Y | Y | 1.1101 | 39.4971 | 18549.1477
[7 empty] | 7647 | 6770 | 1521960 | 2017-10-27 07:16 | 2017-10-27 11:20 | 244 | 11kV | 244 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 174056 Single phase DOLF : 10 Amp Replaced Lightning Arrestors Excluded OMS 1521960 | October | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2017-10-27 | N | 244 | N | 21 | Y | Y | 1.1101 | 39.4971 | 178.308
[7 empty] | 7973 | 10665 | 1521943 | 2017-10-27 06:59 | 2017-10-27 11:35 | 276 | 11kV | 276 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174035 Single phase DOLF : 10 Amp Excluded OMS 1521943 | October | 2017 | 2018Q2 | 2018 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2017-10-27 | N | 276 | N | 21 | Y | Y | 1.1101 | 39.4971 | 201.6927
[7 empty] | 7723 | 7722 | 1522064 | 2017-10-27 10:21 | 2017-10-27 12:00 | 99 | 11kV | 89448 | 1577 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 11 tripped on Relays: timed earth fault Signals: 11kV Trip EFI's Nil. Cause: Water Loaded Palm coming into contact with HV mains at 56 Carranya Rd. See OMS 1522606 1522607 1522064 | October | 2017 | 2018Q2 | 2018 | ZN129:PA3 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Veg | 2017-10-27 | N | 56.7204 | N | 21 | Y | Y | 1.1101 | 39.4971 | 65365.9601
[7 empty] | 8650 | 19474 | 1522018 | 2017-10-27 09:05 | 2017-10-27 12:15 | 190 | 11kV | 2850 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174039 Single phase DOLF : 16 Amp Excluded OMS 1522018 1522053 1522083 | October | 2017 | 2018Q2 | 2018 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2017-10-27 | N | 190 | N | 21 | Y | Y | 1.1101 | 39.4971 | 2082.6959
[7 empty] | 7258 | 1358 | 1521877 | 2017-10-27 05:57 | 2017-10-27 13:30 | 453 | 11kV | 453 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174042 Single phase DOLF : 10 Amp Excluded OMS 1521877 | October | 2017 | 2018Q2 | 2018 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Veg | 2017-10-27 | N | 453 | N | 21 | Y | Y | 1.1101 | 39.4971 | 331.039
[7 empty] | 7816 | 8897 | 1521846 | 2017-10-26 23:20 | 2017-10-27 13:50 | 870 | 11kV | 15542 | 63 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174020 2 fault operations Sensitive Earth Fault Faulty Tx 51692 | October | 2017 | 2018Q2 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2017-10-26 | N | 246.6984 | N | 21 | Y | Y | 1.1101 | 39.4971 | 11357.6352
[7 empty] | 7876 | 9674 | 1521847 | 2017-10-26 23:26 | 2017-10-27 14:25 | 899 | 11kV | 1798 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174045 Single phase DOLF : 10 Amp Replace Tx SAO required Excluded OMS 1521847 | October | 2017 | 2018Q2 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2017-10-26 | N | 899 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1313.9254
[7 empty] | 7727 | 7761 | 1521850 | 2017-10-26 23:48 | 2017-10-27 15:20 | 932 | 11kV | 25700 | 85 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174048 Sensitive Earth Fault Defective transformer 53372 replaced Excluded OMS 1521850 & 1521944 | October | 2017 | 2018Q2 | 2018 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2017-10-26 | N | 302.3529 | N | 21 | Y | Y | 1.1101 | 39.4971 | 18780.802
[7 empty] | 8339 | 15329 | 1522060 | 2017-10-27 10:19 | 2017-10-27 15:25 | 306 | 11kV | 612 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174050 B & C Phase DOLF : 3 Amp #a Boric Acid Excluded OMS 1522060 | October | 2017 | 2018Q2 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2017-10-27 | N | 306 | N | 21 | Y | Y | 1.1101 | 39.4971 | 447.2315
[7 empty] | 7324 | 2567 | 1522022 | 2017-10-27 09:15 | 2017-10-27 15:55 | 400 | 11kV | 1200 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174052 C Phase DOLF : 10 Amp Excluded OMS 1522022 | October | 2017 | 2018Q2 | 2018 | 238:34137 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Veg | 2017-10-27 | N | 400 | N | 21 | Y | Y | 1.1101 | 39.4971 | 876.9246
[7 empty] | 7850 | 9342 | 1521983 | 2017-10-27 08:04 | 2017-10-27 17:50 | 586 | 11kV | 4461 | 135 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge Section of Pa8 PT13320 Foest Bumble 1.6 Road Side HDO 31.5Amp Blown Lightning Arrestor Cause: Lightning/Surge Arrestor. See trip on IR49506 Springs Rd See 1522525 ex 1521983 | October | 2017 | 2018Q2 | 2018 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2017-10-27 | N | 33.0444 | N | 21 | Y | Y | 1.1101 | 39.4971 | 3259.9672
[7 empty] | 8029 | 11435 | 1521820 | 2017-10-26 19:57 | 2017-10-27 19:00 | 1383 | 11kV | 17913 | 19 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 173954 4 fault operations C phase Earth Fault 250 Amp C-E L/A failed ELB 47991 | October | 2017 | 2018Q2 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2017-10-26 | N | 942.7895 | N | 21 | Y | Y | 1.1101 | 39.4971 | 13090.2921
[7 empty] | 8276 | 14681 | 1521853 | 2017-10-26 23:54 | 2017-10-27 21:00 | 1266 | 11kV | 154412 | 295 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174047 C Phase DOLF : 10 Amp Excluded OMS 1522011 | October | 2017 | 2018Q2 | 2018 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2017-10-26 | N | 523.4305 | N | 21 | Y | Y | 1.1101 | 39.4971 | 112839.7352
[7 empty] | 7645 | 6741 | 1522217 | 2017-10-27 19:26 | 2017-10-27 21:05 | 99 | 11kV | 87990 | 902 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | At S10994 Mortdale Zn P19 the Roberts Fairway No.1 fdr tripped reclosed locked out on B/C phase IOC, reclose lockout and time delay, e/f Remarks: Pole defective/failure. X arm failure lorraine ave peakhurst | October | 2017 | 2018Q2 | 2018 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2017-10-27 | N | 97.5499 | N | 21 | Y | Y | 1.1101 | 39.4971 | 64300.4967
[7 empty] | 7921 | 10150 | 1522232 | 2017-10-27 20:43 | 2017-10-27 22:35 | 112 | 11kV | 672 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 174061 Single phase DOLF : 10 Amp 11kV links 65027 1 phase found not closed fully, also replaced 2 x 10A DOLF sub 51382 1 x 10A DOLF sub 43816. Excluded OMS 1522232 | October | 2017 | 2018Q2 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2017-10-27 | N | 112 | N | 21 | Y | Y | 1.1101 | 39.4971 | 491.0778
[7 empty] | 8390 | 16148 | 1522046 | 2017-10-27 09:58 | 2017-10-27 23:30 | 812 | 11kV | 4060 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 174060 B Phase DOLF : 10 Amp sub isolated for repairs Replaced B phase DOLF & L/A. Excluded oms 1522046 | October | 2017 | 2018Q2 | 2018 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2017-10-27 | N | 812 | N | 21 | Y | Y | 1.1101 | 39.4971 | 2966.9283
[7 empty] | 7951 | 10383 | 1522248 | 2017-10-28 00:03 | 2017-10-28 01:20 | 77 | 11kV | 64830 | 1086 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | @ZN262 Marrickville, 11kv Panel No.27 'Marrickville Aux No.1' feeder tripped Relays: B phase instantaneous E/F, Fault check, E/F relay Signals: 11kv trip, ZE, Tx1 GE, No.2 AC board trip Remarks: UG fault. LV// usl 15674 for S5132. 11kv UG fault from S49749 Marrickville Aux No.1 to S5259 Coronation Park to S2062 Yabsley Av tee S5132 Centennial St Nth | October | 2017 | 2018Q2 | 2018 | ZN262:PA27 | ZN262:PA27 | ZN00262/000027 | INNER WEST | UG | Not Veg | 2017-10-28 | N | 59.6961 | N | 6 | N | N | 1.1101 | 39.4971 | 47375.8518
[7 empty] | 8544 | 18136 | 1522252 | 2017-10-28 04:54 | 2017-10-28 05:35 | 41 | 11kV | 41 | 1 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | S76843 West Connex St Peters Temp No.1 - 11kV RMCB tripped on A Phase O/C Suspected overload. No RTI in sub to confirm settings, appears to have been an overload due to lack of EFI/EF trip | October | 2017 | 2018Q2 | 2018 |  |  |  |  | Unknown | Not Veg | 2017-10-28 | N | 41 | N | 6 | N | N | 1.1101 | 39.4971 | 29.9616
[7 empty] | 7374 | 3451 | 1522302 | 2017-10-28 10:23 | 2017-10-28 12:00 | 97 | 11kV | 194 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174062 A Phase DOLF : 10 Amp Excluded OMS 1522302 | October | 2017 | 2018Q2 | 2018 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2017-10-28 | N | 97 | N | 6 | N | N | 1.1101 | 39.4971 | 141.7695
[7 empty] | 8556 | 18318 | 1522320 | 2017-10-28 11:11 | 2017-10-28 14:00 | 169 | 11kV | 676 | 4 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 174063 Isolated to remove tree branch on OHM adjacent pole FO-60252. Excluded OMS No. 1522320 + 1522327 | October | 2017 | 2018Q2 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2017-10-28 | N | 169 | N | 6 | N | N | 1.1101 | 39.4971 | 494.0009
[7 empty] | 8617 | 19095 | 1522381 | 2017-10-28 17:00 | 2017-10-28 17:48 | 48 | 11kV | 22704 | 473 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex 11kv Panel No.12 "Claireville Ave" feeder from Zn10997 Sans Souci 11kv Centre phase bond off @ AB31158 Abnormal: LB 31157 closed with LB 30715 Open Remarks: bond. 11kv centre phase bond off @ AB31158 | October | 2017 | 2018Q2 | 2018 | ZN10997:PA12 | ZN10997:PA12 | ZN10997/000012 | BAYSIDE | OH | Not Veg | 2017-10-28 | N | 48 | N | 6 | N | N | 1.1101 | 39.4971 | 16591.4135
[7 empty] | 7496 | 5333 | 1522370 | 2017-10-28 15:47 | 2017-10-28 20:01 | 254 | 11kV | 58259 | 481 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 174067 1 fault operation Sensitive Earth Fault Sw 47695 Maitland Vale RAGCB tripped on SEF (12A). 11kV links 41585 failed. Excluded OMS No. 1522370 + 1522373 | October | 2017 | 2018Q2 | 2018 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2017-10-28 | N | 121.1206 | N | 6 | N | N | 1.1101 | 39.4971 | 42573.9589
[7 empty] | 7459 | 4766 | 1522413 | 2017-10-29 02:20 | 2017-10-29 04:53 | 153 | 11kV | 153 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | S36093 Syd Cricket Ground No.2 - 11kV RMCB tripped Sign of moisture in CDG relay. Cause not ascertained at the time. See further interruption when relay needed to be replaced. | October | 2017 | 2018Q2 | 2018 |  |  |  | SYDNEY | UG | Not Veg | 2017-10-29 | N | 153 | N | 7 | N | N | 1.1101 | 39.4971 | 111.8079
[7 empty] | 8080 | 12181 | 1522419 | 2017-10-29 06:57 | 2017-10-29 07:57 | 60 | 11kV | 6462 | 122 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 Matraville - Pnl.15 tripped on: Earth Fault Field EFIs: S7668, S8393 S6778 Abnormal: S2887 (Sw/A) open / S6778 (Sw/B) closed (Switching for feeder transfer to Port Botany which is delayed) UG cable fault from S6778 (Sw/B) to S8536 (Sw/B) See 1522558 1522559 | October | 2017 | 2018Q2 | 2018 | ZN1788:PA15 | ZN1788:PA15 | ZN01788/000015 | RANDWICK | UG | Not Veg | 2017-10-29 | N | 52.9672 | N | 7 | N | N | 1.1101 | 39.4971 | 4722.239
[7 empty] | 7195 | 376 | 1522415 | 2017-10-29 06:01 | 2017-10-29 09:40 | 219 | 11kV | 219 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | S36093 Syd Cricket Ground No.2 - 11KV RMCB tripped Fault CDG relay, TPE replaced | October | 2017 | 2018Q2 | 2018 |  |  |  | SYDNEY | UG | Not Veg | 2017-10-29 | N | 219 | N | 7 | N | N | 1.1101 | 39.4971 | 160.0387
[7 empty] | 8156 | 13225 | 1522457 | 2017-10-29 13:15 | 2017-10-29 16:40 | 205 | 11kV | 15176 | 108 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 174075 C Phase DOLF : 16 Amp Faulty LA at Coningsby sub 70179. Excluded OMS 1522457 + 1522466 | October | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2017-10-29 | N | 140.5185 | N | 7 | N | N | 1.1101 | 39.4971 | 11090.1732
[7 empty] | 7350 | 2895 | 1522489 | 2017-10-29 16:44 | 2017-10-29 17:26 | 42.05 | 11kV | 35279.95 | 839 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1673 Turramurra panel 13 has tripped Signals: 11kV Trip Relays: A and B phase O/C Cause; Tree branch on OH mains in Page Ave. See OMS 1522493 For additional details See OMS 1522489 1522493 | October | 2017 | 2018Q2 | 2018 | ZN1673:PA13 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | OH | Veg | 2017-10-29 | N | 42.05 | N | 7 | N | N | 1.1101 | 39.4971 | 25781.5469
[7 empty] | 8722 | 20425 | 1522510 | 2017-10-29 20:42 | 2017-10-29 23:10 | 148 | 11kV | 4292 | 29 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 174076 /01 C Phase DOLF : 20 Amp Replaced C phase 20A LF 40534 & A phase 10A LF 40521. Excluded oms 1522511, 152210,152219 | October | 2017 | 2018Q2 | 2018 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2017-10-29 | N | 148 | N | 7 | N | N | 1.1101 | 39.4971 | 3136.467
[7 empty] | 7520 | 5572 | 1522520 | 2017-10-29 23:07 | 2017-10-30 01:50 | 163 | 11kV | 113705 | 869 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7900 Campbell Street - Pnl.7 tripped on: B phase Earth Fault. Field EFIs: S1358 S3536 S4191 UG cable fault from S4191 to S7242 See 1522545 1522546 1522547 | October | 2017 | 2018Q2 | 2018 | ZN7900:PA7 | ZN7900:PA7 | ZN07900/000007 | SYDNEY | UG | Not Veg | 2017-10-29 | N | 130.8458 | N | 7 | N | N | 1.1101 | 39.4971 | 83092.2603
[7 empty] | 8571 | 18464 | 1522522 | 2017-10-30 02:58 | 2017-10-30 08:40 | 342 | 11kV | 27884 | 1968 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North Pa19 "Goulburn Pelican" tripped on Relays: A and C phase overcurrent Signals: 11kv trip with efi EFI's: pa19 to EFI at Uranga and Contarf Abnormal: S48811:B to S17020:A Cause: CP24719 middle and footpath side bonds to HDO's burnt off. Tee off to PT15941. See 1523188,9 ex 1522521,2 | October | 2017 | 2018Q2 | 2018 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2017-10-30 | N | 14.1687 | N | 17 | N | N | 1.1101 | 39.4971 | 20376.8048
[7 empty] | 7967 | 10549 | 1522554 | 2017-10-30 07:30 | 2017-10-30 09:30 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174079 3 Phase DOLF : 10 Amp Excluded OMS 1522554 | October | 2017 | 2018Q2 | 2018 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2017-10-30 | N | 120 | N | 17 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 7213 | 575 | 1522624 | 2017-10-30 09:54 | 2017-10-30 11:35 | 101 | 11kV | 303 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174087 A Phase DOLF : 10 Amp Excluded OMS 1522624 | October | 2017 | 2018Q2 | 2018 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2017-10-30 | N | 101 | N | 17 | N | N | 1.1101 | 39.4971 | 221.4235
[7 empty] | 7994 | 10962 | 1522647 | 2017-10-30 10:28 | 2017-10-30 13:30 | 182 | 11kV | 50332 | 326 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | Ex Zn15014 Mona Vale section of Pa14 Recloser CP22381 Lane Cove Walter tripped on Relays: O/C trip, IOC Signals: Lockout Cause: not ascertained. Feeder patrolled by DOps, no fault found See 1522647 1522724 | October | 2017 | 2018Q2 | 2018 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2017-10-30 | N | 154.3926 | N | 17 | N | N | 1.1101 | 39.4971 | 36781.1411
[7 empty] | 7623 | 6526 | 1522713 | 2017-10-30 12:47 | 2017-10-30 14:06 | 79 | 11kV | 11218 | 142 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | CP555 Arcadia Park tripped and locked out on Relays: Overload, Lockout Cause: Tree branch on OH mains 23 Bay Rd | October | 2017 | 2018Q2 | 2018 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2017-10-30 | N | 79 | N | 17 | N | N | 1.1101 | 39.4971 | 8197.7835
[7 empty] | 7206 | 491 | 1522792 | 2017-10-30 15:11 | 2017-10-30 15:59 | 48 | 11kV | 19934 | 458 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 174091 B & C phase Tree branch on mains Excluded oms 1522792,1522797 | October | 2017 | 2018Q2 | 2018 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2017-10-30 | N | 43.524 | N | 17 | N | N | 1.1101 | 39.4971 | 14567.1792
[7 empty] | 7242 | 1113 | 1522773 | 2017-10-30 14:30 | 2017-10-30 16:09 | 99 | 11kV | 136620 | 1380 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S2400 Berowra Panel 22 Tripped Reclosed Tripped and Locked out on A and C phase IOC Signals: 11kV Trip EFI's Nil Cause: Tree on OH mains - 713 Pacific Highway | October | 2017 | 2018Q2 | 2018 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Veg | 2017-10-30 | N | 99 | N | 17 | N | N | 1.1101 | 39.4971 | 99837.8664
[7 empty] | 7700 | 7390 | 1522828 | 2017-10-30 15:29 | 2017-10-30 18:00 | 151 | 11kV | 1661 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174093 C Phase DOLF Excluded OMS 1522828 | October | 2017 | 2018Q2 | 2018 | 504:48029 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2017-10-30 | N | 151 | N | 17 | N | N | 1.1101 | 39.4971 | 1213.8098
[7 empty] | 7944 | 10345 | 1522914 | 2017-10-30 17:48 | 2017-10-30 18:31 | 43 | 11kV | 7267 | 169 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn12570 Avoca Pa35 "S48848 Avoca Melville 0.3" Intellirupter 61952 Ballorok Avoca has tripped Relays: OC trip and lock out Cause: Tree/Branch on OH mains adjacent LK41349 | October | 2017 | 2018Q2 | 2018 | ZN12570:PA35 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | OH | Veg | 2017-10-30 | N | 43 | N | 17 | N | N | 1.1101 | 39.4971 | 5310.5093
[7 empty] | 8570 | 18462 | 1522729 | 2017-10-30 13:35 | 2017-10-30 18:40 | 305 | 11kV | 3675 | 21 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | Ex Zn14891 Wyong Section of Pa12 From TCAT48839 Yarramlong Maitland 1.3 to AB43742 tee PT12717, PT13819, PT13234 interrupted for emergency repairs. OH resting on cross arm. See 1523219,20 ex 1522729,31,2 | October | 2017 | 2018Q2 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2017-10-30 | N | 175 | N | 17 | N | N | 1.1101 | 39.4971 | 2685.5816
[7 empty] | 8719 | 20315 | 1522882 | 2017-10-30 16:54 | 2017-10-30 18:40 | 106 | 11kV | 157830 | 2015 | HV | Arcing | Equipment Failure | UGOH | Unplanned | Wind Strong | N | Zn36300 Balgowlah North Pa3 "Jackson White etc" fdr tripped Relays: overcurrent and earth fault Signals: 11kv trip EFI's Pa3 to S17092 Cause: Flashover/Arcing Suspect UGOH Vic. Sandy Bay road and Peronne towards S16998 See 1523259,60,1 ex 1522882,94 | October | 2017 | 2018Q2 | 2018 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2017-10-30 | N | 78.3275 | N | 17 | N | N | 1.1101 | 39.4971 | 115337.5088
[7 empty] | 8683 | 19821 | 1523005 | 2017-10-30 21:18 | 2017-10-30 22:05 | 47 | 11kV | 47 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174096 C Phase DOLF Excluded OMS 1523005 | October | 2017 | 2018Q2 | 2018 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2017-10-30 | N | 47 | N | 17 | N | N | 1.1101 | 39.4971 | 34.3462
[7 empty] | 8382 | 16021 | 1523001 | 2017-10-30 21:01 | 2017-10-30 23:45 | 164 | 11kV | 328 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 174097 Broken Live Line Lead Excluded OMS 1523001 | October | 2017 | 2018Q2 | 2018 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2017-10-30 | N | 164 | N | 17 | N | N | 1.1101 | 39.4971 | 239.6927
[7 empty] | 8194 | 13645 | 1523278 | 2017-10-30 20:34 | 2017-10-30 23:55 | 201 | 11kV | 8442 | 42 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 174095 interrupt to repair pole fire JT-10550 Excluded oms 1522982 | October | 2017 | 2018Q2 | 2018 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2017-10-30 | N | 201 | N | 17 | N | N | 1.1101 | 39.4971 | 6169.1646
[7 empty] | 7524 | 5592 | 1522795 | 2017-10-30 14:49 | 2017-10-31 02:30 | 701 | 11kV | 119724 | 719 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35370 Galston Panel 8 tripped, reclosed tripped and locked out on Relays: A phase OC, EFI, Reclose, Lockout Signals: 11kV Trip Cause: tree branch brought down wires Near PT2216 Wylds Rd See OMS 1523509 1523510 1523511 1522795 1522910 1522810 1522800 | October | 2017 | 2018Q2 | 2018 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2017-10-30 | N | 166.5146 | N | 17 | N | N | 1.1101 | 39.4971 | 87490.7679
[7 empty] | 8055 | 11854 | 1522813 | 2017-10-30 15:16 | 2017-10-31 10:20 | 1144.4333 | 11kV | 83569.2 | 372 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | At S35370 Galston Panel 2 tripped, reclosed , tripped and locked out on Relays: B phase OC, EFI, Reclose and Lockout Signals: 11kV trip Cause: Broken Cross arm near PT2138 OH resting on crosarm See OMS 1522813 1522918 | October | 2017 | 2018Q2 | 2018 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2017-10-30 | N | 224.6484 | N | 17 | N | N | 1.1101 | 39.4971 | 61069.9065
[7 empty] | 7884 | 9796 | 1523124 | 2017-10-31 09:32 | 2017-10-31 11:20 | 108 | 11kV | 108 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174106 C Phase DOLF : 10 Amp Excluded OMS 1523124 | October | 2017 | 2018Q2 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2017-10-31 | N | 108 | N | 4 | N | N | 1.1101 | 39.4971 | 78.9232
[7 empty] | 7716 | 7655 | 1522970 | 2017-10-30 13:05 | 2017-10-31 12:40 | 1415 | 11kV | 49259 | 79 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | At Zn187 Corws Nest S6616 James Ridge HV TX HRC fuse Tripped Signals: TX2 Group Earth and Panel 4R EFI at S187 Water Flooded at customers premisis (1 James Place) (Note: Long Outage on Distributor 1) | October | 2017 | 2018Q2 | 2018 | ZN187:PA4 | ZN187:PA4 | ZN00187/000004 | NORTH SYDNEY | Unknown | Not Veg | 2017-10-30 | N | 623.5316 | N | 17 | N | N | 1.1101 | 39.4971 | 35997.0243
[7 empty] | 7406 | 3908 | 1523298 | 2017-10-31 15:31 | 2017-10-31 16:45 | 74 | 11kV | 222 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174111 C Phase DOLF : 10 Amp Eastern Rozella Excluded OMS 1523298 | October | 2017 | 2018Q2 | 2018 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2017-10-31 | N | 74 | N | 4 | N | N | 1.1101 | 39.4971 | 162.2311
[7 empty] | 7995 | 10963 | 1523321 | 2017-10-31 16:17 | 2017-10-31 17:13 | 56 | 11kV | 18256 | 326 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn15014 Mona Vale section of Panel 14 CP22381 Lane Cove Walter tripped on: Relays: Overcurrent trip, IOC trip Signals: Lockout Cause: Tree/Branch on OH mains knocked off by DOp | October | 2017 | 2018Q2 | 2018 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2017-10-31 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 13340.9463
[7 empty] | 8303 | 15019 | 1523389 | 2017-11-01 07:08 | 2017-11-01 07:30 | 22 | 11kV | 37840 | 1720 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn12620 Noraville section of Pa1L "Noraville Aux" Sw/D was opened by DOp Cause: Staff Error. Due to unclear labelling of RMI's within Noraville Zone. DOp opened SwD on No.2 RMI at Zn14068 Noraville Aux instead of SwD at No.2 RMI at Noraville Zone See 1523794 ex 1523389 | November | 2017 | 2018Q2 | 2018 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | Unknown | Not Veg | 2017-11-01 | N | 22 | N | 4 | N | N | 1.1101 | 39.4971 | 27652.3559
[7 empty] | 8102 | 12551 | 1523291 | 2017-10-31 15:12 | 2017-11-01 08:00 | 1008.25 | 11kV | 1008.25 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Replaced 5 amp fuse Note: customers were then impacted from 01/11/17 08:00 with Planned outage - refer to OMS 1523725 | October | 2017 | 2018Q2 | 2018 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-10-31 | N | 1008.25 | N | 4 | N | N | 1.1101 | 39.4971 | 736.7994
[7 empty] | 7209 | 540 | 1523478 | 2017-11-01 11:13 | 2017-11-01 13:00 | 107 | 11kV | 107 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174118 C Phase DOLF : 10 Amp no animal found , DOLF replaced OK Excluded oms 1523478 | November | 2017 | 2018Q2 | 2018 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2017-11-01 | N | 107 | N | 4 | N | N | 1.1101 | 39.4971 | 78.1924
[7 empty] | 7712 | 7571 | 1523546 | 2017-11-01 14:29 | 2017-11-01 17:25 | 176 | 11kV | 99960 | 843 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S5868 Gore Hill Pa27 tripped on OC and Earth Fault, EFI, Fault Check Contractor Caused Fault on feeder Cause - Fault 1: UG cable fault from S6769 -S36048 Fault 2: S3505 - S5335 - S6743 | November | 2017 | 2018Q2 | 2018 | ZN5868:PA27 | ZN5868:PA23 | ZN05868/000023 | NORTH SYDNEY | UG | Not Veg | 2017-11-01 | N | 118.5765 | N | 4 | N | N | 1.1101 | 39.4971 | 73047.8197
[7 empty] | 7654 | 6865 | 1523608 | 2017-11-01 19:23 | 2017-11-01 20:22 | 59 | 11kV | 49986 | 908 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Pa20 "LB41498" fdr has tripped Signals: 11kv trip Relays: Overcurrent B & C phase Cause: Air Break switch failed on C phase and flashed over requires replacement See 1523796,7 ex 1523608,9 | November | 2017 | 2018Q2 | 2018 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Not Veg | 2017-11-01 | N | 55.0507 | N | 4 | N | N | 1.1101 | 39.4971 | 36528.2945
[7 empty] | 8317 | 15150 | 1523620 | 2017-11-02 03:30 | 2017-11-02 07:35 | 245 | 11kV | 12740 | 52 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174126 B Phase DOLF : 31 Amp B phase 31.5A DOLF no cause found supply backon 0735hrs Extended outage due to despatch not despatching job till 0631hrs Excluded 1523620 | November | 2017 | 2018Q2 | 2018 | 214:8669 | 214:8669 | ZN00214/008669 | LAKE MACQUARIE | OH | Veg | 2017-11-02 | N | 245 | N | 5 | N | N | 1.1101 | 39.4971 | 9310.0162
[7 empty] | 8061 | 11967 | 1523649 | 2017-11-02 08:25 | 2017-11-02 10:50 | 145 | 11kV | 25096 | 458 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 174129 B Phase Earth Fault Contractor dug up cable Excluded OMS 1523649,1523653 | November | 2017 | 2018Q2 | 2018 | 523:33509 | 523:33509 | ZN00523/033509 | SINGLETON | UG | Not Veg | 2017-11-02 | N | 54.7948 | N | 5 | N | N | 1.1101 | 39.4971 | 18339.4166
[7 empty] | 8191 | 13578 | 1523826 | 2017-11-02 18:15 | 2017-11-02 18:30 | 15 | 11kV | 2025 | 135 | HV | Arcing | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn36300 Balgowlah North section of Pa11 PT15479 Brighton St 7 isolated by DOp due to Middle Phase HV bond burnt at 20 rickard st Between LB77738 to AB22777 to S16962 tee PT15479 See 1525036 ex 1523826,47,4000 | November | 2017 | 2018Q2 | 2018 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | OH | Not Veg | 2017-11-02 | N | 15 | N | 5 | N | N | 1.1101 | 39.4971 | 1479.8103
[7 empty] | 7394 | 3794 | 1524013 | 2017-11-02 21:03 | 2017-11-02 22:15 | 72 | 11kV | 57816 | 803 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN1673 Turramurra Panel 2 tripped on B and C phase O/C Cause: Tree branch on OH mains Burnt tree branch found on Comenarra Parkway | November | 2017 | 2018Q2 | 2018 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | OH | Veg | 2017-11-02 | N | 72 | N | 5 | N | N | 1.1101 | 39.4971 | 42250.2275
[7 empty] | 8473 | 17317 | 1523837 | 2017-11-02 17:12 | 2017-11-03 07:00 | 828 | 11kV | 285490 | 1756 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 2 tripped on A and C phase IOC, Cphase timed, EFI and Fault Check. Zone Earth, TX1 Group Earth, CB 2 Open, 11kV trip Cause: UG cable fault - Section of feeder from S7288 to S1274 to S35715 1524082 152084 152085 (1524101 1524096 1524100) 15238371523837 1524025 1523842 1524014 | November | 2017 | 2018Q2 | 2018 | ZN4545:PA2 | ZN4545:PA2 | ZN04545/000002 | RYDE | UG | Not Veg | 2017-11-02 | N | 162.5797 | N | 5 | N | N | 1.1101 | 39.4971 | 208627.6715
[7 empty] | 8548 | 18190 | 1524048 | 2017-11-03 08:15 | 2017-11-03 12:00 | 225 | 11kV | 675 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 174142 A Phase Live Line Clamp burnt off Excluded OMS 1524048 | November | 2017 | 2018Q2 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2017-11-03 | N | 225 | N | 2 | N | N | 1.1101 | 39.4971 | 493.2701
[7 empty] | 8127 | 12960 | 1524139 | 2017-11-03 13:32 | 2017-11-03 14:59 | 87 | 11kV | 2736 | 61 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 174146 1 fault operation B Phase Overcurrent; Earth Fault Targets 50TB & 50TN EFI's @ 67796,66879,69971,56019,56011,58061. Failed EFI's @ 58205,75503. Please attend to repair. UG cable fault between Sw 56010 Spitfire Pl No 1 and Sw 59359 Spitfire Pl No 2. Excluded OMS 1524139 | November | 2017 | 2018Q2 | 2018 | 511:29869 | 511:29869 | ZN00511/029869 | MAITLAND | UG | Not Veg | 2017-11-03 | N | 44.8525 | N | 2 | N | N | 1.1101 | 39.4971 | 1999.3881
[7 empty] | 7535 | 5706 | 1524369 | 2017-11-04 20:55 | 2017-11-04 22:01 | 66 | 11kV | 4554 | 69 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn36200 Empire Bay section of pa4 IR63686 opened on Overcurrent & locked out Cause: tree branch on 11kv near PT12880 | November | 2017 | 2018Q2 | 2018 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2017-11-04 | N | 66 | N | 2 | N | N | 1.1101 | 39.4971 | 3327.9289
[7 empty] | 8197 | 13705 | 1524387 | 2017-11-05 03:08 | 2017-11-05 04:36 | 88 | 11kV | 6952 | 79 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Zn180 Mosman section of Pa17 "Vista Short" RE1014 Suakin Drive tripped & locked out Cause: not ascertained. DOp patrolled nothing identified | November | 2017 | 2018Q2 | 2018 | ZN180:PA17 | ZN180:PA17 | ZN00180/000017 | MOSMAN | OH | Veg | 2017-11-05 | N | 88 | N | 6 | N | N | 1.1101 | 39.4971 | 5080.3166
[7 empty] | 7239 | 1077 | 1524343 | 2017-11-04 16:51 | 2017-11-05 06:45 | 834 | 11kV | 88135 | 1718 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Pole | Unplanned | Rain Light | N | LID 174149 Sop open Sw 7490 for pole KT-70837 fire Excluded oms 1524335 | November | 2017 | 2018Q2 | 2018 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2017-11-04 | N | 51.3009 | N | 2 | N | N | 1.1101 | 39.4971 | 64406.4585
[7 empty] | 8658 | 19590 | 1524384 | 2017-11-05 01:07 | 2017-11-05 11:22 | 615 | 11kV | 27134 | 130 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 174151 3 fault operations Earth Fault Replaced arrestors at UGOH pole HT-25770 Excluded OMS 1524384, 1524394 | November | 2017 | 2018Q2 | 2018 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2017-11-05 | N | 208.7231 | N | 6 | N | N | 1.1101 | 39.4971 | 19828.7269
[7 empty] | 7545 | 5785 | 1524454 | 2017-11-05 11:48 | 2017-11-05 14:25 | 157 | 11kV | 298337 | 3090 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn36300 Balgowlah Nth Panel 11 "Candamine Sydney, Sydney Waratah" fdr tripped Relays: 11R Earth Fault, EFI, Trip Led, Overcurrent + Earth Fault Signals: 11kv trip, zone earth, Tx1 Group Earth EFI's: Nil Abnormal: S16509 SwA Closed S16509SwB Opened Cause: UG Fault Section of 11kv fdr from S17011SwB to S16993SwA to S16708SwB Note: EFI's operated possible due to a LV// in place for S16701 and backfeeding into fault. Note: 11L switched away to Pa18L prior to trying back form Zn16980 to reduce further interruption See 1525098,9,101,2 ex 1524454 | November | 2017 | 2018Q2 | 2018 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | UG | Not Veg | 2017-11-05 | N | 96.5492 | N | 6 | N | N | 1.1101 | 39.4971 | 218015.8801
[7 empty] | 8432 | 16737 | 1524531 | 2017-11-05 22:00 | 2017-11-05 22:35 | 35 | 11kV | 3185 | 91 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 174152 A Phase DOLF : 31 Amp Sub 12301 A phase 31.5 A DOLF cause possum supply back on 2235hrs Excluded OMS 1524533 & 1524534 | November | 2017 | 2018Q2 | 2018 | 256:80644 | 256:80644 | ZN00256/080644 | NEWCASTLE | OH | Not Veg | 2017-11-05 | N | 35 | N | 6 | N | N | 1.1101 | 39.4971 | 2327.5041
[7 empty] | 7563 | 5980 | 1524519 | 2017-11-05 15:30 | 2017-11-05 23:05 | 455 | 11kV | 6370 | 14 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | Ex Zn14143 Somersby section of pa17 section of 11kv fdr between S18639 to USL41695 to AB40511, tee PT18476 PT13459 PT11619 Cause: Vehicle Hit Pole 1 bay form LB41992 | November | 2017 | 2018Q2 | 2018 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2017-11-05 | N | 455 | N | 6 | N | N | 1.1101 | 39.4971 | 4655.0081
[7 empty] | 8042 | 11545 | 1524544 | 2017-11-05 23:26 | 2017-11-06 | 34 | 11kV | 1020 | 30 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn14144 Wamberal section of Pa5 PT11588 Beaufort Wycombe roadside dropout NGK63A Cause: Pssible Fuse fatigue See 1525111 ex 1524544 | November | 2017 | 2018Q2 | 2018 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Not Veg | 2017-11-05 | N | 34 | N | 6 | N | N | 1.1101 | 39.4971 | 745.3859
[7 empty] | 8106 | 12581 | 1524548 | 2017-11-06 02:17 | 2017-11-06 03:16 | 59 | 11kV | 67909 | 1151 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9037 Miranda Pnl.8 tripped, reclosed & tripped on: Inst Overcurrent Field EFIs: S9521 Abnormal LB35118 OPEN Possum found adjacent to PT61805 on UGOH | November | 2017 | 2018Q2 | 2018 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Not Veg | 2017-11-06 | N | 59 | N | 31 | Y | Y | 1.1101 | 39.4971 | 49625.8942
[7 empty] | 7246 | 1188 | 1524555 | 2017-11-06 05:47 | 2017-11-06 08:45 | 178 | 11kV | 1424 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174159 B Phase DOLF : 16 Amp Excluded OMS 1524555 | November | 2017 | 2018Q2 | 2018 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2017-11-06 | N | 178 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1040.6172
[7 empty] | 8587 | 18665 | 1524573 | 2017-11-06 08:15 | 2017-11-06 11:40 | 205 | 11kV | 2440 | 13 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 174161 C Phase Tapping burnt off at AI-80065. Also blew DOLF's at PT 50390 and 71699. Both C phase. Excluded OMS 1524595/1524573 | November | 2017 | 2018Q2 | 2018 | 814:82283 | 814:82283 | ZN00814/082283 | CESSNOCK | OH | Not Veg | 2017-11-06 | N | 187.6923 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1783.08
[7 empty] | 7319 | 2537 | 1524676 | 2017-11-06 11:07 | 2017-11-06 12:13 | 66 | 11kV | 10164 | 154 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC.45071 Central Mangrove tripped, reclosed, tripped and locked out Large tree branch on mains adjacent AB43582 | November | 2017 | 2018Q2 | 2018 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2017-11-06 | N | 66 | N | 31 | Y | Y | 1.1101 | 39.4971 | 7427.5514
[7 empty] | 8714 | 20269 | 1524644 | 2017-11-06 06:11 | 2017-11-06 15:30 | 559 | 11kV | 1677 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174169 A & B phase DOLF : 10 Amp | November | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-11-06 | N | 559 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1225.5021
[7 empty] | 7548 | 5799 | 1524891 | 2017-11-06 14:44 | 2017-11-06 16:47 | 123 | 11kV | 3279 | 33 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174171 2 fault operations Overcurrent Excluded OMS 1524891 | November | 2017 | 2018Q2 | 2018 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2017-11-06 | N | 99.3636 | N | 31 | Y | Y | 1.1101 | 39.4971 | 2396.1965
[7 empty] | 7642 | 6731 | 1525390 | 2017-11-06 16:51 | 2017-11-06 16:59 | 8 | 11kV | 6024 | 753 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | Zn12600 Lisarow - Pnl.2 tripped on Earth Fault Lightning arrestor failed a PT13304 due to weather event | November | 2017 | 2018Q2 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2017-11-06 | N | 8 | N | 31 | Y | Y | 1.1101 | 39.4971 | 4402.1615
[7 empty] | 8700 | 20083 | 1524760 | 2017-11-06 14:13 | 2017-11-06 17:35 | 202 | 11kV | 808 | 4 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Heavy | N | PT18738 Paroo Wattle Tree 0.3 - 10 Amps Footpath phase HDO operated Weather related | November | 2017 | 2018Q2 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2017-11-06 | N | 202 | N | 31 | Y | Y | 1.1101 | 39.4971 | 590.4626
[7 empty] | 7334 | 2755 | 1524855 | 2017-11-06 14:32 | 2017-11-06 18:09 | 217 | 11kV | 61545 | 457 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174186 2 fault operations A Phase Overcurrent Excluded OMS 1524855 | November | 2017 | 2018Q2 | 2018 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2017-11-06 | N | 134.6718 | N | 31 | Y | Y | 1.1101 | 39.4971 | 44975.2707
[7 empty] | 8527 | 17939 | 1524987 | 2017-11-06 15:22 | 2017-11-06 18:16 | 174 | 11kV | 6313 | 44 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174221 2 fault operations Earth fault Excluded OMS OMS 1524987 | November | 2017 | 2018Q2 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-11-06 | N | 143.4773 | N | 31 | Y | Y | 1.1101 | 39.4971 | 4613.3542
[7 empty] | 7187 | 158 | 1524921 | 2017-11-06 14:58 | 2017-11-06 18:17 | 199.3167 | 11kV | 78730.0833 | 395 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174168 2 fault operations 3 phase Overcurrent tree branch removed. dq | November | 2017 | 2018Q2 | 2018 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2017-11-06 | N | 199.3167 | N | 31 | Y | Y | 1.1101 | 39.4971 | 57533.6228
[7 empty] | 7537 | 5718 | 1524928 | 2017-11-06 14:58 | 2017-11-06 18:27 | 209 | 11kV | 27715 | 133 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174190 2 fault operation B & C phase Overcurrent Excluded OMS 1524928 | November | 2017 | 2018Q2 | 2018 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2017-11-06 | N | 208.3835 | N | 31 | Y | Y | 1.1101 | 39.4971 | 20253.3045
[7 empty] | 8600 | 18835 | 1525139 | 2017-11-06 17:25 | 2017-11-06 19:10 | 105 | 11kV | 315 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174196 A Phase DOLF : 5 Amp Excluded OMS 1525139 | November | 2017 | 2018Q2 | 2018 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Veg | 2017-11-06 | N | 105 | N | 31 | Y | Y | 1.1101 | 39.4971 | 230.1927
[7 empty] | 8173 | 13433 | 1525196 | 2017-11-06 18:55 | 2017-11-06 20:45 | 110 | 11kV | 110 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174220 Single phase DOLF :10 Amp Excluded OMS 1525196 | November | 2017 | 2018Q2 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-11-06 | N | 110 | N | 31 | Y | Y | 1.1101 | 39.4971 | 80.3848
[7 empty] | 7576 | 6078 | 1525029 | 2017-11-06 16:13 | 2017-11-06 21:30 | 317 | 11kV | 317 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174223 A & B phase DOLF : 16 Amp Excluded OMS 1525061 | November | 2017 | 2018Q2 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2017-11-06 | N | 317 | N | 31 | Y | Y | 1.1101 | 39.4971 | 231.6543
[7 empty] | 7270 | 1625 | 1524863 | 2017-11-06 14:33 | 2017-11-06 23:20 | 527 | 11kV | 130294 | 846 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 174202 2 fault operations 11kV OHM down between poles IR-12217 & IR-12216. Excluded OMS No. 1524863 | November | 2017 | 2018Q2 | 2018 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2017-11-06 | N | 154.0118 | N | 31 | Y | Y | 1.1101 | 39.4971 | 95215.0122
[7 empty] | 7243 | 1145 | 1524906 | 2017-11-06 14:54 | 2017-11-07 00:35 | 581 | 11kV | 377581 | 1277 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 174229 Tree On Mains pole FT-30718 | November | 2017 | 2018Q2 | 2018 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Veg | 2017-11-06 | N | 295.6782 | N | 31 | Y | Y | 1.1101 | 39.4971 | 275925.058
[7 empty] | 7281 | 1839 | 1524997 | 2017-11-06 15:28 | 2017-11-07 02:45 | 677 | 11kV | 3385 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174232 B Phase DOLF : 31 Amp Excluded OMS 1524997 | November | 2017 | 2018Q2 | 2018 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Veg | 2017-11-06 | N | 677 | N | 31 | Y | Y | 1.1101 | 39.4971 | 2473.6582
[7 empty] | 8231 | 14190 | 1524947 | 2017-11-06 15:06 | 2017-11-07 02:57 | 711 | 11kV | 1422 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174233 A Phase DOLF : 10 Amp Excluded OMS 1524947 | November | 2017 | 2018Q2 | 2018 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2017-11-06 | N | 711 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1039.1557
[7 empty] | 7682 | 7137 | 1524764 | 2017-11-06 14:04 | 2017-11-07 04:28 | 864 | 11kV | 12957 | 42 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 174217 1 fault operation A & C phase Overcurrent TREES BROUGHT DOWN MAINS NEAR THE ZONE SUB. PROTECTION 51T AC Excluded OMS 1524764 | November | 2017 | 2018Q2 | 2018 | 507:80926 | 507:80926 | ZN00507/080926 | CESSNOCK | OH | Veg | 2017-11-06 | N | 308.5 | N | 31 | Y | Y | 1.1101 | 39.4971 | 9468.5934
[7 empty] | 8066 | 12024 | 1524756 | 2017-11-06 14:04 | 2017-11-07 05:30 | 926 | 11kV | 500459 | 1242 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 174199 2 fault operations Overcurrent Mains on Road Governemnt Rd near Eigth and Tenth Streets. Protection 50T ABC. Wayne Morgans crew carried out repairs. Excluded OMS 1524752 AND 1524757. | November | 2017 | 2018Q2 | 2018 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2017-11-06 | N | 402.9461 | N | 31 | Y | Y | 1.1101 | 39.4971 | 365720.6762
[7 empty] | 8424 | 16639 | 1524749 | 2017-11-06 14:10 | 2017-11-07 05:53 | 943 | 11kV | 37889 | 83 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174227 CHAD JONES ISOLATED lv AT SUB 42553, NOT REPAIRED YET AS OF 6/11/17. Taps left broken at pole GS-54142. restored 7/11 05:53 Excluded OMS 1524751 | November | 2017 | 2018Q2 | 2018 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Veg | 2017-11-06 | N | 456.494 | N | 31 | Y | Y | 1.1101 | 39.4971 | 27688.1637
[7 empty] | 7315 | 2441 | 1525305 | 2017-11-06 23:45 | 2017-11-07 07:55 | 490 | 11kV | 14890 | 37 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | Wind Strong | N | LID 174235 CCT on ground adj ABS 43648 | November | 2017 | 2018Q2 | 2018 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2017-11-06 | N | 402.4324 | N | 31 | Y | Y | 1.1101 | 39.4971 | 10881.1728
[7 empty] | 7370 | 3303 | 1524750 | 2017-11-06 14:05 | 2017-11-07 10:30 | 1225 | 11kV | 671198 | 1269 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 174239 Tree in mains 108 Aberdare St Kurri Overcurrent; Earth Fault | November | 2017 | 2018Q2 | 2018 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2017-11-06 | N | 528.9188 | N | 31 | Y | Y | 1.1101 | 39.4971 | 490491.7014
[7 empty] | 7396 | 3812 | 1524784 | 2017-11-06 14:19 | 2017-11-07 11:00 | 1241 | 11kV | 42470 | 77 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 174225 Overcurrent Tress on the ground Sternbeck Rd. Excluded oms 1524784, 1524963 | November | 2017 | 2018Q2 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-11-06 | N | 551.5584 | N | 31 | Y | Y | 1.1101 | 39.4971 | 31035.8233
[7 empty] | 8288 | 14828 | 1525380 | 2017-11-07 08:52 | 2017-11-07 11:30 | 158 | 11kV | 158 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 174246 B Phase DOLF : 10 Amp Excluded OMS 1525380 | November | 2017 | 2018Q2 | 2018 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2017-11-07 | N | 158 | N | 8 | N | N | 1.1101 | 39.4971 | 115.4617
[7 empty] | 7803 | 8747 | 1525239 | 2017-11-06 20:23 | 2017-11-07 12:00 | 937 | 11kV | 13118 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | LID 174242 A & C Phase DOLF : 10 Amp Excluded OMS 1525239 | November | 2017 | 2018Q2 | 2018 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2017-11-06 | N | 937 | N | 31 | Y | Y | 1.1101 | 39.4971 | 9586.2475
[7 empty] | 8336 | 15305 | 1525494 | 2017-11-07 12:49 | 2017-11-07 12:56 | 7 | 11kV | 4071 | 678 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 174243 Opened ABS 1148 due to faulty contacts. Dump & restore fdr for safety. Excluded OMS 1525494, 1525503, 1525517 | November | 2017 | 2018Q2 | 2018 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2017-11-07 | N | 6.0044 | N | 8 | N | N | 1.1101 | 39.4971 | 2974.9667
[7 empty] | 8553 | 18291 | 1525489 | 2017-11-07 12:05 | 2017-11-07 13:35 | 90 | 11kV | 4476 | 54 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Previous Storm | N | Ex Zn14143 Somersby section of Pa6 "Pinnacle Trennium" tripped Signals: 11kv trip, CB 6 EFI Relays: Earth Fault, EFI EFIs S18379 S14634 S18540 S18454 11kV UG Fault between S18454:B & S18253:A see 1526179,81 ex 1525489,92 | November | 2017 | 2018Q2 | 2018 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | UG | Not Veg | 2017-11-07 | N | 82.8889 | N | 8 | N | N | 1.1101 | 39.4971 | 3270.9288
[7 empty] | 8076 | 12157 | 1525288 | 2017-11-06 20:23 | 2017-11-07 13:50 | 1047 | 11kV | 2094 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Wind Storm | N | LID 174250 A Phase DOLF : 10 Amp Excluded OMS 1525288 | November | 2017 | 2018Q2 | 2018 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2017-11-06 | N | 1047 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1530.2334
[7 empty] | 7330 | 2709 | 1524860 | 2017-11-06 14:37 | 2017-11-07 14:55 | 1458 | 11kV | 8748 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 174226 3 phase DOLF : 20 Amp Mains down on ground Excluded OMS 1524860, 1525087 | November | 2017 | 2018Q2 | 2018 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2017-11-06 | N | 1458 | N | 31 | Y | Y | 1.1101 | 39.4971 | 6392.7804
[7 empty] | 8689 | 19917 | 1525433 | 2017-11-07 07:50 | 2017-11-07 15:15 | 445 | 11kV | 445 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa20 PT18774 Hue Hue WSC Tip A phase burnt off bond. See 1526167 ex 1525433 | November | 2017 | 2018Q2 | 2018 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2017-11-07 | N | 445 | N | 8 | N | N | 1.1101 | 39.4971 | 325.1929
[7 empty] | 8368 | 15788 | 1525285 | 2017-11-06 16:13 | 2017-11-07 15:15 | 1382 | 11kV | 2764 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174252 3 phase DOLF : 10 Amp faulty Tx excluded OMS 1525029 | November | 2017 | 2018Q2 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2017-11-06 | N | 1382 | N | 31 | Y | Y | 1.1101 | 39.4971 | 2019.8497
[7 empty] | 8332 | 15279 | 1525298 | 2017-11-06 23:49 | 2017-11-07 15:25 | 936 | 11kV | 74451 | 846 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 174231 2 fault operations Earth Fault Faulty trans or LAs, sub 52517 left isolated. Excluded oms 1525298 & 1525496 | November | 2017 | 2018Q2 | 2018 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2017-11-06 | N | 88.0035 | N | 31 | Y | Y | 1.1101 | 39.4971 | 54406.5949
[7 empty] | 7616 | 6446 | 1525370 | 2017-11-07 08:19 | 2017-11-07 16:15 | 476 | 11kV | 952 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174253 C Phase DOLF : 10 Amp Excluded OMS 1525370 | November | 2017 | 2018Q2 | 2018 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Veg | 2017-11-07 | N | 476 | N | 8 | N | N | 1.1101 | 39.4971 | 695.6935
[7 empty] | 7620 | 6466 | 1524781 | 2017-11-06 14:10 | 2017-11-07 16:20 | 1570 | 11kV | 568507 | 1080 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn12620 Noraville Pa3 fdr opneed, reclosed & locked out Relays: C pHase OC, C phase IOC, Lockout, Timing Singals: 11kv trip Cause: Weather related Rain Heavy 11kV down between LB63494, LB40278 & LB40187 11kV down between LB40958 & S11948 See 1526147,8,50,1,2 ex 1525248,9 | November | 2017 | 2018Q2 | 2018 | ZN12620:PA3 | ZN12620:PA3 | ZN12620/000003 | CENTRAL COAST | OH | Not Veg | 2017-11-06 | N | 526.3954 | N | 31 | Y | Y | 1.1101 | 39.4971 | 415448.1475
[7 empty] | 7731 | 7799 | 1526175 | 2017-11-07 15:59 | 2017-11-07 17:15 | 76 | 11kV | 745 | 10 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa20 11kv section of fdr was interrupted from LK45008 to LB44914 tee PT13927, PT12418, PT14257, BS18862 to repair burnt off 11kV bond Note: PT18774 Hue Hue WSC Tip was running on a generator at teh time of the interruption A burnt off bond was found on A phase 11kV adjacent to PT13927 See seperate inerruption for PT18774 See 1526175,6 | November | 2017 | 2018Q2 | 2018 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2017-11-07 | N | 74.5 | N | 8 | N | N | 1.1101 | 39.4971 | 544.424
[7 empty] | 8226 | 14061 | 1525340 | 2017-11-07 07:23 | 2017-11-07 17:45 | 622 | 11kV | 622 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174254 A & C Phase DOLF : 10 Amp Excluded OMS 1525340 | November | 2017 | 2018Q2 | 2018 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2017-11-07 | N | 622 | N | 8 | N | N | 1.1101 | 39.4971 | 454.5393
[7 empty] | 7378 | 3526 | 1525761 | 2017-11-07 19:01 | 2017-11-07 20:55 | 114 | 11kV | 114 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174255 A Phase DOLF : 10 Amp Excluded OMS 1525761 | November | 2017 | 2018Q2 | 2018 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2017-11-07 | N | 114 | N | 8 | N | N | 1.1101 | 39.4971 | 83.3078
[7 empty] | 7214 | 582 | 1526058 | 2017-11-09 03:00 | 2017-11-09 12:00 | 540 | 11kV | 4860 | 9 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 174269 MVA pole HS-30009. No protection operation 11 & 33kV isolated to replace pole. Excluded oms 1526058 | November | 2017 | 2018Q2 | 2018 | 532:83307 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Not Veg | 2017-11-09 | N | 540 | N | 2 | N | N | 1.1101 | 39.4971 | 3551.5447
[7 empty] | 8060 | 11950 | 1526184 | 2017-11-09 11:53 | 2017-11-09 20:33 | 520 | 11kV | 90890 | 640 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Snow / Hail Storm | N | At S965 Pennant Hills Panel 13 tripped on Signals: 11kV trip. Relays: A and B phase overcurrent Vehicle Hit pole in David street near Westminster - HV into LV. At PT1852 Aven David 400A fuse blown on A B and C phase of distributor 2 Cause: Truck hit pole in David Rd See OMS 1526825 1526828 1526829 15826831 1526184 1526242 | November | 2017 | 2018Q2 | 2018 | ZN965:PA13 | ZN965:PA13 | ZN00965/000013 | HORNSBY | OH | Not Veg | 2017-11-09 | N | 142.0156 | N | 2 | N | N | 1.1101 | 39.4971 | 66419.7312
[7 empty] | 8138 | 13047 | 1526318 | 2017-11-10 02:16 | 2017-11-10 08:40 | 384 | 11kV | 287118 | 2258 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S156006 Harbord Panel 9 Tripped, Reclosed Tripped and Lockout out on A and C phase OC Reclose Timing and Lockout Cause: 2 HV Faults, Tree touching HV - removed by DOp HV on ground at 13 MacDonald St See OMS1526932 1526933 1526318 152619 1526344 1526326 | November | 2017 | 2018Q2 | 2018 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Veg | 2017-11-10 | N | 127.1559 | N | 5 | N | N | 1.1101 | 39.4971 | 209817.3659
[7 empty] | 8023 | 11329 | 1526321 | 2017-11-10 05:37 | 2017-11-10 09:00 | 203 | 11kV | 19894 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At PT15327 Austral Ave 11kV Bond off At S156006 Harbord Panel 9 Tripped, Reclosed Tripped and Lockout out on A and C phase OC Reclose Timing and Lockout Cause: 2 HV Faults, Tree touching HV - removed by DOp HV on ground at 13 MacDonald St See OMS1526932 1526933 1526318 152619 1526344 1526326 | November | 2017 | 2018Q2 | 2018 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Veg | 2017-11-10 | N | 203 | N | 5 | N | N | 1.1101 | 39.4971 | 14537.9484
[7 empty] | 7982 | 10791 | 1526396 | 2017-11-10 11:23 | 2017-11-10 15:00 | 217 | 11kV | 35235.6667 | 999 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 174297 1 fault operation C Phase Earth Fault Excavator hit mains between poles IT-50139 & IT-50141 at Fletcher. | November | 2017 | 2018Q2 | 2018 | 213:33773 | 213:33773 | ZN00213/033773 | NEWCASTLE | OH | Not Veg | 2017-11-10 | N | 35.2709 | N | 5 | N | N | 1.1101 | 39.4971 | 25749.1859
[7 empty] | 7426 | 4124 | 1526368 | 2017-11-10 10:00 | 2017-11-10 17:00 | 420 | 11kV | 420 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174299 C Phase DOLF : 10 Amp Excluded OMS 1526368 | November | 2017 | 2018Q2 | 2018 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Veg | 2017-11-10 | N | 420 | N | 5 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 7893 | 9905 | 1526510 | 2017-11-10 23:57 | 2017-11-11 00:56 | 59 | 11kV | 103014 | 1746 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2310 Punchbowl 11kv feeder Panel No.59 "Berring Ave" feeder tripped Relays: B phase O/C and EFI Abnormal: DMA S48550-S3528-S2198 feeder failure with Sw/B @ S2187 Phillip Hill CLOSED Remarks: UG fault. Feeder fault in section from S77612 Thompson Wilson (Sw/A) to S77726 Chapel Wilson (Sw/B) Note see separate DMA feeder failure Ex PA:14 | November | 2017 | 2018Q2 | 2018 | ZN2310:PA59 | ZN2310:PA19 | ZN02310/000019 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-11-10 | N | 59 | N | 5 | N | N | 1.1101 | 39.4971 | 75279.5928
[7 empty] | 7824 | 8993 | 1526514 | 2017-11-11 01:05 | 2017-11-11 10:55 | 590 | 11kV | 5310 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Enclosed Load Break Switch | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 PT14540 Buangi Hills Mand 0.1 11kV centre phase 16Amp dropout fuse found operated. Cause not ascertained See 1526836 ex 1526514,32 | November | 2017 | 2018Q2 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2017-11-11 | N | 590 | N | 3 | N | N | 1.1101 | 39.4971 | 3880.3914
[7 empty] | 8115 | 12716 | 1526556 | 2017-11-11 10:53 | 2017-11-11 11:45 | 52 | 11kV | 44096 | 848 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7900 Campbell St - Pnl.11 tripped on: A & C phase O.C, Earth Fault with EFI UG cable fault between S832 (Sw/A) and S35320 (Sw/A) | November | 2017 | 2018Q2 | 2018 | ZN7900:PA11 | ZN7900:PA11 | ZN07900/000011 | SYDNEY | UG | Not Veg | 2017-11-11 | N | 52 | N | 3 | N | N | 1.1101 | 39.4971 | 32224.0562
[7 empty] | 8520 | 17820 | 1526624 | 2017-11-11 22:33 | 2017-11-12 00:31 | 118 | 11kV | 42255 | 451 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn14891 Wyong Pa14 "WSC Hely, etc" fdr tripped on: Realys: EFI, EF check, 50TC, 150TN Signals: Trip EFI's: S14799 S14630 Cause: not ascertained. DOp patrolled feeder See 1526855,7,8,9 ex 1526624 | November | 2017 | 2018Q2 | 2018 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | OH | Veg | 2017-11-11 | N | 93.6918 | N | 3 | N | N | 1.1101 | 39.4971 | 30878.7077
[7 empty] | 7931 | 10216 | 1526646 | 2017-11-12 08:43 | 2017-11-12 09:45 | 62 | 11kV | 682 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174307 A Phase DOLF : 10 Amp Excluded OMS 1526646 & 1526651. | November | 2017 | 2018Q2 | 2018 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Veg | 2017-11-12 | N | 62 | N | 2 | N | N | 1.1101 | 39.4971 | 498.3855
[7 empty] | 7926 | 10195 | 1526654 | 2017-11-12 09:54 | 2017-11-12 12:05 | 131 | 11kV | 87783 | 693 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.5 tripped on: Earth leakage Field EFI S61717 S2894 S8356 S6309 UG cable fault from S8356 (Sw/B) to S6309 9Sw/B) to S888 (Sw/B) See 1526767 1526768 | November | 2017 | 2018Q2 | 2018 | ZN690:PA5 | ZN690:PA5 | ZN00690/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-11-12 | N | 126.671 | N | 2 | N | N | 1.1101 | 39.4971 | 64149.2272
[7 empty] | 7216 | 645 | 1527298 | 2017-11-13 04:52 | 2017-11-13 06:20 | 88 | 11kV | 48664 | 553 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty section of pa11 "Lucinda Ave" LK42072 Burnt of 11kV bond Pole BV2122 | November | 2017 | 2018Q2 | 2018 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2017-11-13 | N | 88 | N | 3 | N | N | 1.1101 | 39.4971 | 35562.2159
[7 empty] | 7294 | 2044 | 1526998 | 2017-11-13 08:20 | 2017-11-13 11:20 | 180 | 11kV | 180 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 174320 B Phase DOLF : 10 Amp Blown ligntning arrestor | November | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2017-11-13 | N | 180 | N | 3 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 7613 | 6430 | 1526965 | 2017-11-13 18:15 | 2017-11-13 19:58 | 103 | 11kV | 136269 | 1323 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman Panel 28 "Cowles Belmont, etc" fdr tripped Relays: A phase Earth Fault, F/C, EFI Signals: 11kv trip, Zone Earth, Tx4 Group Earth EFI's: Nil Cause: UG Fault. Frontline feeder fault | November | 2017 | 2018Q2 | 2018 | ZN180:PA28 | ZN180:PA28 | ZN00180/000028 | NORTH SYDNEY | UG | Not Veg | 2017-11-13 | N | 103 | N | 3 | N | N | 1.1101 | 39.4971 | 99581.3659
[7 empty] | 7953 | 10415 | 1528164 | 2017-11-15 03:18 | 2017-11-15 12:15 | 537 | 11kV | 17169 | 148 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Ironbark Kirks section of Pa3 RE46935 Ironbark Kirks tripped, reclosed and tripped and locked out on overcurrent Cause: Large tree branch brought down OH HV and LV see 1528164,6 | November | 2017 | 2018Q2 | 2018 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2017-11-15 | N | 116.0068 | N | 1 | N | N | 1.1101 | 39.4971 | 12546.5988
[7 empty] | 7380 | 3589 | 1527413 | 2017-11-16 04:16 | 2017-11-16 05:33 | 77 | 11kV | 7854 | 102 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats section of Pa8 RE44995 Kulnura tripped and locked out on overcurrent Bat | November | 2017 | 2018Q2 | 2018 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2017-11-16 | N | 77 | N | 4 | N | N | 1.1101 | 39.4971 | 5739.4715
[7 empty] | 7454 | 4716 | 1527448 | 2017-11-16 08:15 | 2017-11-16 09:35 | 80 | 11kV | 13120 | 164 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 174350 no protection operation section isolated to make repairs at abs 6725 Excluded oms 1527448 | November | 2017 | 2018Q2 | 2018 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Not Veg | 2017-11-16 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 9587.709
[7 empty] | 8680 | 19792 | 1527427 | 2017-11-16 07:41 | 2017-11-16 10:13 | 151.85 | 11kV | 14273.9 | 94 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of 11kv fdr 13L 'Peats Ridge Aux' (S77279) Lost load due to open bond adjacent first HV UGOH from S77279 Peats Ridge Aux 1 Cause: Bond burnt at Pole PR500. Live lineworker to investigate ASAP CC1: 22-"Refer to SOp" | November | 2017 | 2018Q2 | 2018 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2017-11-16 | N | 151.85 | N | 4 | N | N | 1.1101 | 39.4971 | 10430.9451
[7 empty] | 7473 | 5012 | 1527440 | 2017-11-16 08:00 | 2017-11-16 16:05 | 485.15 | 11kV | 3881.2 | 8 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 174371 Single phase DOLF : 10 Amp It is alledged that an excavator has damaged several spans of mains beyond pole DN-80100. Repaired 11kV mains beyond pole DM80054 suspected of being brought down by excavator. | November | 2017 | 2018Q2 | 2018 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2017-11-16 | N | 485.15 | N | 4 | N | N | 1.1101 | 39.4971 | 2836.2665
[7 empty] | 7479 | 5046 | 1527628 | 2017-11-17 03:38 | 2017-11-17 10:05 | 387 | 11kV | 93941 | 618 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At Zn965 Pennant Hill Panel 13 tripped on Relays: Timed O/C A phase Signals: 11kV Trip, Zone Earth. No 2 Group Earth. Cause: Flash over at UGOH to S6756 - possum See OMS 1528188 1528189 1528190 1527628 1527632 1527719 | November | 2017 | 2018Q2 | 2018 | ZN965:PA13 | ZN965:PA13 | ZN00965/000013 | HORNSBY | OH | Not Veg | 2017-11-17 | N | 152.0081 | N | 4 | N | N | 1.1101 | 39.4971 | 68649.312
[7 empty] | 8541 | 18047 | 1527694 | 2017-11-17 11:31 | 2017-11-17 13:10 | 99 | 11kV | 297 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174377 Single phase DOLF : 10 Amp Excluded OMS 1527694 | November | 2017 | 2018Q2 | 2018 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-11-17 | N | 99 | N | 4 | N | N | 1.1101 | 39.4971 | 217.0388
[7 empty] | 8160 | 13285 | 1527738 | 2017-11-17 14:34 | 2017-11-17 15:46 | 72 | 11kV | 109368 | 1519 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S1193 Lindfield Panel 26 tripped on Relays: IOC Signals: 11kV trip Cause: branch removed by DOp @ PT25 | November | 2017 | 2018Q2 | 2018 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | OH | Veg | 2017-11-17 | N | 72 | N | 4 | N | N | 1.1101 | 39.4971 | 79922.9086
[7 empty] | 7941 | 10321 | 1527779 | 2017-11-17 18:30 | 2017-11-17 20:05 | 95 | 11kV | 1140 | 12 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 174380 HV dropper pulled out of dolf. Put minto LV parallel at 2005hrs. Excluded OMS 1527779 | November | 2017 | 2018Q2 | 2018 | 509:33397 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2017-11-17 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 833.0784
[7 empty] | 7673 | 7064 | 1527805 | 2017-11-18 00:04 | 2017-11-18 00:32 | 28 | 11kV | 60200 | 2150 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North Pa19 tripped, reclosed & tripped Relays: Lock out, O/C, E+F, trip, Fault Check, EFI, Under Frequency, IOC-ABC, Prot trip Signals: EFI, IOC ABC, CB19 open EFI's: S16827 S16064 S16928, 16 Myrtle St, S16987 Cause: Dead Possum found base of pole. 47 woodbine street, North Balgowlah See 1527805 ex 1527806 | November | 2017 | 2018Q2 | 2018 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2017-11-18 | N | 28 | N | 7 | N | N | 1.1101 | 39.4971 | 43992.3844
[7 empty] | 8152 | 13209 | 1527810 | 2017-11-18 02:01 | 2017-11-18 03:50 | 109 | 11kV | 109 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174383 A Phase DOLF : 3 Amp Excluded OMS 1527810 | November | 2017 | 2018Q2 | 2018 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2017-11-18 | N | 109 | N | 7 | N | N | 1.1101 | 39.4971 | 79.654
[7 empty] | 7593 | 6221 | 1527854 | 2017-11-18 11:21 | 2017-11-18 11:47 | 26 | 11kV | 29198 | 1123 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa9 RE47607 Toomeys Rd tripped on overcurrent Cause: tree/branch on OH mains vicinity LB43463 See 1527854 ex 1527855 | November | 2017 | 2018Q2 | 2018 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2017-11-18 | N | 26 | N | 7 | N | N | 1.1101 | 39.4971 | 21337.0372
[7 empty] | 7961 | 10505 | 1527875 | 2017-11-18 13:15 | 2017-11-18 13:48 | 33 | 11kV | 363 | 11 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 174385 3 phase section isolated for mains repair pole 8M-40061 Yarrawa Rd | November | 2017 | 2018Q2 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-11-18 | N | 33 | N | 7 | N | N | 1.1101 | 39.4971 | 265.2697
[7 empty] | 7515 | 5536 | 1527883 | 2017-11-18 14:15 | 2017-11-18 15:10 | 55 | 11kV | 43185 | 823 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9118 Cronulla - Pnl.2 tripped, reclosed and locked out on: Earth Fault Field EFIs: S9091 UG Cable fault between S9091 (Sw/B) and S9463 (Sw/A) See 1528073 1528074 | November | 2017 | 2018Q2 | 2018 | ZN9118:PA2 | ZN9118:PA2 | ZN09118/000002 | SUTHERLAND | UG | Not Veg | 2017-11-18 | N | 52.4727 | N | 7 | N | N | 1.1101 | 39.4971 | 31558.3243
[7 empty] | 7797 | 8713 | 1527863 | 2017-11-18 12:16 | 2017-11-18 15:30 | 194 | 11kV | 334380 | 3223 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde Panel 28 Tripped, Reclosed, Tripped and locked out on Relays: A and B phase IOC, Timing and Lockout. Abnormal Switching: CP3048 Open and LB1476 Closed AB1116 Open with LB1276 Closed. Cause: Tree brought down OH in Quarry Rd. See OMS: 1528298 1528299 1528330 1527863 1527865 1527870 1527873 1527886 | November | 2017 | 2018Q2 | 2018 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Veg | 2017-11-18 | N | 103.7481 | N | 7 | N | N | 1.1101 | 39.4971 | 244355.0415
[7 empty] | 7574 | 6066 | 1527934 | 2017-11-18 21:26 | 2017-11-18 23:35 | 129 | 11kV | 1290 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa6L "Central Mangrove" PT13539 Hoipios Hensons 0.6 16k footpath phase replaced See 1528193 ex 1527934,40 | November | 2017 | 2018Q2 | 2018 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2017-11-18 | N | 129 | N | 7 | N | N | 1.1101 | 39.4971 | 942.694
[7 empty] | 7928 | 10201 | 1527945 | 2017-11-19 00:40 | 2017-11-19 04:10 | 210 | 11kV | 12402 | 86 | HV | Wind Blown Debris | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 174387 3 fault operations Earth Fault Light plant into 11kV OHM between links 3894 & pole FS-14404. Note Fdr abnormally switched ABS 40321 open & Sw 3821 closed. Excluded OMS 1527945, 1527946, 1527947 | November | 2017 | 2018Q2 | 2018 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2017-11-19 | N | 144.2093 | N | 2 | N | N | 1.1101 | 39.4971 | 9063.0158
[7 empty] | 8144 | 13105 | 1527832 | 2017-11-19 03:12 | 2017-11-19 04:31 | 79 | 11kV | 159817 | 2023 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | @ZN35800 Bankstown 11kv Panel 14 labelled "S64012 Hoskins Cottam" Relays: earth fault, B+C phase IOC, 11kv trip Signals: B+C phase IOC, prot trip, CB#14 open Remarks: Animals/birds. Section of overhead feeder below Sw/B @ S5762 Dewitt Chapel | November | 2017 | 2018Q2 | 2018 | ZN35800:PA14 | ZN35800:PA14 | ZN35800/000014 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-11-19 | N | 79 | N | 2 | N | N | 1.1101 | 39.4971 | 116789.5498
[7 empty] | 7607 | 6384 | 1528581 | 2017-11-22 11:24 | 2017-11-22 13:00 | 96 | 11kV | 36214 | 484 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9037 Gwawley Bay - Pnl.33 tripped on: Earth Fault Field EFIs: All down to S9486 UG cabel fault from S9486 to S9554 tee PT9451. Location found by DOp, Telstra contractor advised of location. Jointer to inspect. See 1528721 1528722 | November | 2017 | 2018Q2 | 2018 | ZN9550:PA33 | ZN9550:PA33 | ZN09550/000033 | SUTHERLAND | UG | Not Veg | 2017-11-22 | N | 74.8223 | N | 1 | N | N | 1.1101 | 39.4971 | 26464.1231
[7 empty] | 7506 | 5438 | 1528718 | 2017-11-23 06:19 | 2017-11-23 07:40 | 81 | 11kV | 324 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174419 Single phase DOLF : 16 Amp OMS 1528700 WAS OROGINAL LATER RECEIVED OMS JOB 1528718. BLOWN DOLF NO CAUSE FOUND.. Excluded OMS 1528718 | November | 2017 | 2018Q2 | 2018 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2017-11-23 | N | 81 | N | 4 | N | N | 1.1101 | 39.4971 | 236.7696
[7 empty] | 8002 | 11147 | 1528745 | 2017-11-23 09:25 | 2017-11-23 11:05 | 100 | 11kV | 100 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174433 A Phase DOLF : 10 Amp Excluded OMS 1528745 | November | 2017 | 2018Q2 | 2018 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2017-11-23 | N | 100 | N | 4 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 8128 | 12975 | 1528849 | 2017-11-23 15:31 | 2017-11-23 16:24 | 53 | 11kV | 38576 | 736 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @ZN2196 Milperra 11kv Panel #2 labelled "S61792 Bullecourt Horsley UWSNo.2" tripped: Relays: SEL, EFI, Signals: Zone earth, Tx3 group earth, CB#2 open, 11kv trip Remarks: cause not ascertained | November | 2017 | 2018Q2 | 2018 | ZN2196:PA2 | ZN2196:PA2 | ZN02196/000002 | CANTERBURY-BANKSTOWN | OH | Veg | 2017-11-23 | N | 52.413 | N | 4 | N | N | 1.1101 | 39.4971 | 28190.203
[7 empty] | 7895 | 9925 | 1528913 | 2017-11-23 23:53 | 2017-11-24 00:40 | 46.8167 | 11kV | 5852.0833 | 125 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 174444 A phase DOLF : 40 Amp Cap missing from 11kV LA, daylight inspection required to check condition of LA. CC1: 22-"Refer to SOp" | November | 2017 | 2018Q2 | 2018 | 210:83466 | 210:83466 | ZN00210/083466 | NEWCASTLE | OH | Not Veg | 2017-11-23 | N | 46.8167 | N | 4 | N | N | 1.1101 | 39.4971 | 4276.5299
[7 empty] | 8038 | 11538 | 1528917 | 2017-11-24 00:51 | 2017-11-24 03:12 | 141 | 11kV | 101743 | 1027 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn14143 Somersby Pa5 "Karion Sth" tripped on: Relays: EFI, E/F Signals: 11kv trip EFI's: S18048 SCP45441 S65410 Cause not ascertained See 1530288,9,90 ex 1528917 | November | 2017 | 2018Q2 | 2018 | ZN14143:PA5 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Veg | 2017-11-24 | N | 99.0682 | N | 7 | N | N | 1.1101 | 39.4971 | 74350.7835
[7 empty] | 8201 | 13763 | 1528941 | 2017-11-24 09:00 | 2017-11-24 13:30 | 270 | 11kV | 60750 | 225 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 174458 Fdr interr. to repair broken pole being held by crane after vehicle impact. See LID #174445 (Trip & Reclose). Excluded OMS No. 1528941 | November | 2017 | 2018Q2 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2017-11-24 | N | 270 | N | 7 | N | N | 1.1101 | 39.4971 | 44394.3082
[7 empty] | 7939 | 10302 | 1529012 | 2017-11-24 14:48 | 2017-11-24 16:40 | 112 | 11kV | 57388 | 937 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Giosford section of Pa13 "HanlanSt" IR62730 Manns Narara Creek tripped, reclosed and tripped Relays: OC trip, SEF trip, Lockout Signals: 11kV trip Tree Branch brought down OH. 11kV fdr isolated from LB41126 to LB44907 tee PT12886 & PT18265 See 1529571,2,3 ex 1529012,44,5 | November | 2017 | 2018Q2 | 2018 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2017-11-24 | N | 61.2465 | N | 7 | N | N | 1.1101 | 39.4971 | 41937.4577
[7 empty] | 7859 | 9405 | 1529592 | 2017-11-24 18:26 | 2017-11-24 18:36 | 10 | 11kV | 190 | 19 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa12 "Yarramalong" fdr Between LB41158 to LB41096 tee PT11519 PT113248 PT11232 PT13507 PT14083 PT12204 Cause: tree on mains | November | 2017 | 2018Q2 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2017-11-24 | N | 10 | N | 7 | N | N | 1.1101 | 39.4971 | 138.8464
[7 empty] | 7255 | 1337 | 1529079 | 2017-11-24 18:52 | 2017-11-24 19:55 | 63 | 11kV | 693 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174464 A Phase DOLF : 31 Amp no clause found. excluded oms 1529083 | November | 2017 | 2018Q2 | 2018 | 524:33578 | 524:33578 | ZN00524/033578 | CESSNOCK | OH | Veg | 2017-11-24 | N | 63 | N | 7 | N | N | 1.1101 | 39.4971 | 506.424
[7 empty] | 7678 | 7106 | 1529108 | 2017-11-24 21:37 | 2017-11-25 00:12 | 155 | 11kV | 240715 | 1553 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN1287 Revesby Zone 11kv feeder Panel No.3 "Mars Virginius etc" feeder TRIPPED to LOCK OUT Relays: A and C phase timed O/C, C phase IOC, Lockout, Timing, F/C, EFI Signals: 11kv trip, Zn earth Remarks: Flash/Arcing, Possum casued flashover at UGOH pole PE6627, no visable damage referrred to O/H mains to inspect | November | 2017 | 2018Q2 | 2018 | ZN1287:PA3 | ZN1287:PA3 | ZN01287/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-11-24 | N | 155 | N | 7 | N | N | 1.1101 | 39.4971 | 175907.4221
[7 empty] | 7257 | 1356 | 1529099 | 2017-11-24 20:49 | 2017-11-25 08:30 | 701 | 11kV | 1402 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174466 B Phase DOLF : 10 Amp Excluded OMS 1529099 | November | 2017 | 2018Q2 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2017-11-24 | N | 701 | N | 7 | N | N | 1.1101 | 39.4971 | 1024.5402
[7 empty] | 8044 | 11660 | 1529127 | 2017-11-25 07:27 | 2017-11-25 09:28 | 121 | 11kV | 321964 | 2978 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN690 Campsie 11kv VCB panel 4 "S-76910" feeder tripped on: Relays: C phase O/C & EF, EFI, fault check Remarks: Abnormal Sw/B Closed @ S310, Sw/A opened @ S35519 Remarks: 11kv UG feeder fault between S2532 William Main to CP1555 Hood ave Sw/A tee to S310 Bexley Rd. During switching after DOp switched D& R 416790 fault occured also LV// failed see separate interruptions report | November | 2017 | 2018Q2 | 2018 | ZN690:PA11 | ZN690:PA11 | ZN00690/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-11-25 | N | 108.1142 | N | 3 | N | N | 1.1101 | 39.4971 | 235281.7949
[7 empty] | 8096 | 12367 | 1529115 | 2017-11-25 03:11 | 2017-11-25 14:45 | 694 | 11kV | 24044 | 152 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 174465 2 fault operations B & C Phase Overcurrent Dop reported 11kV mains stolen between poles JS-60043 & JS-60046. Excluded OMS 1529115 | November | 2017 | 2018Q2 | 2018 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2017-11-25 | N | 158.1842 | N | 3 | N | N | 1.1101 | 39.4971 | 17570.646
[7 empty] | 7838 | 9213 | 1529192 | 2017-11-25 10:54 | 2017-11-25 15:30 | 275.9 | 11kV | 11863.7 | 43 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn2400 Berowra ex Panel 11 has been opened. Emergency Works / Un-planned Interruption : Dead tree ready to fall on 11KV O.H Mains | November | 2017 | 2018Q2 | 2018 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2017-11-25 | N | 275.9 | N | 3 | N | N | 1.1101 | 39.4971 | 8669.642
[7 empty] | 7699 | 7379 | 1529281 | 2017-11-26 05:22 | 2017-11-26 06:50 | 88 | 11kV | 12848 | 166 | HV | Fire (Non Ausgrid) | UNKNOWN | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12580 Erina section of Pa4 Btw AB41402 to S40361 to AB41619 interrupted due to pole on fire See 1529594,5 ex 1529281 | November | 2017 | 2018Q2 | 2018 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Not Veg | 2017-11-26 | N | 77.3976 | N | 4 | N | N | 1.1101 | 39.4971 | 9388.9394
[7 empty] | 8259 | 14490 | 1529301 | 2017-11-26 15:40 | 2017-11-26 15:55 | 15 | 11kV | 75 | 5 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of Feeder from ZB3343 to LB493 tee PT1890, PT1941 and PT1969 Has been Interrupted Cause; Tree branch on OH mains - 148 Arcadia Road See OMS 1529337 1529338 1529339 1529301 | November | 2017 | 2018Q2 | 2018 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2017-11-26 | N | 15 | N | 4 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 7186 | 151 | 1529345 | 2017-11-26 16:16 | 2017-11-26 17:10 | 54 | 11kV | 108 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174473 C Phase DOLF : 10 Amp dead bird at base of pole. Excluded OMS 1529345 | November | 2017 | 2018Q2 | 2018 | 235:2857 | 235:2857 | ZN00235/002857 | MAITLAND | OH | Not Veg | 2017-11-26 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 78.9232
[7 empty] | 8616 | 19088 | 1529336 | 2017-11-26 15:16 | 2017-11-26 17:16 | 120 | 11kV | 181117 | 1582 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn15005 Belrose Panel 8 tripped on Signals: 11kV Trip, TX1 and Tx2 Fault Check. Relays: OCEF Relay, EFI and Trip, Fault Check, Reclose Timer, Reclose Lockout Cause: UG fault between Panel 8 @ Belrose and SW/A @ S15655. See OMS 1529506 1529506 | November | 2017 | 2018Q2 | 2018 | ZN15005:PA8 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | UG | Not Veg | 2017-11-26 | N | 114.4861 | N | 4 | N | N | 1.1101 | 39.4971 | 132354.9616
[7 empty] | 7966 | 10538 | 1529531 | 2017-11-27 13:08 | 2017-11-27 19:00 | 352 | 11kV | 139972 | 1279 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 19 Opened on Relays: EFI, Fault Check, B phase O/C Signals: Zone Earth, No2 Group Earth, 11kV trip. Cause: 11kV UG cable fault from S6191 to S8497 tee S740 See OMS 1530382 1530383 1529575 1529531 | November | 2017 | 2018Q2 | 2018 | ZN847:PA19 | ZN847:PA19 | ZN00847/000019 | HORNSBY | UG | Not Veg | 2017-11-27 | N | 109.4386 | N | 1 | N | N | 1.1101 | 39.4971 | 102287.4091
[7 empty] | 8562 | 18374 | 1529874 | 2017-11-28 16:43 | 2017-11-28 18:04 | 81 | 11kV | 61803 | 1032 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly Pnl.8 tripped on: C phase O/C with EFI Field EFIs: S35539, S8812, S2861 UG cable fault between S2861 (Sw/B) and S7368 (SwA) to S3998(Sw/A). Pitt cover dislodged after explosion ajacent 101 Birrell Rd See 1530029 1530030 | November | 2017 | 2018Q2 | 2018 | ZN2602:PA8 | ZN2602:PA46 | ZN02602/000046 | WAVERLEY | UG | Not Veg | 2017-11-28 | N | 59.8866 | N | 2 | N | N | 1.1101 | 39.4971 | 45163.8095
[7 empty] | 8000 | 11106 | 1529915 | 2017-11-28 21:49 | 2017-11-28 22:42 | 53 | 11kV | 62767 | 1394 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Pa9 "Denning" feeder tripped on: Relays: EFI, OC, EF Check, MICOM Relay 4/4 B Phase 5/5 ABC EFI's: nil Signals: 11kv trip Cause: UGOH fault short circtui. Birds nest on UGOH flashed over ADJ to S14430 Ozone Denning section of 11kv fdr between AB41784 to S14430 Ozone Denning to S11011 SwA See 1530295,7 ex 1529915,8 | November | 2017 | 2018Q2 | 2018 | ZN12610:PA9 | ZN12610:PA9 | ZN12610/000009 | CENTRAL COAST | Unknown | Unknown | 2017-11-28 | N | 45.0265 | N | 2 | N | N | 1.1101 | 39.4971 | 45868.2723
[7 empty] | 8159 | 13249 | 1529926 | 2017-11-29 05:33 | 2017-11-29 07:40 | 127 | 11kV | 2286 | 18 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174509 B Phase DOLF : 10 Amp Possum Excluded OMS 1529926 | November | 2017 | 2018Q2 | 2018 | 229:34986 | 229:34986 | ZN00229/034986 | PORT STEPHENS | OH | Not Veg | 2017-11-29 | N | 127 | N | 3 | N | N | 1.1101 | 39.4971 | 1670.5414
[7 empty] | 8572 | 18496 | 1529959 | 2017-11-29 08:25 | 2017-11-29 09:52 | 87 | 11kV | 48147 | 591 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill - Pnl.10 tripped on: Earth leakage with EFI Field EFIs: S63468 S65167 S1514 UG cable fault between S1514 (Sw/A) and S49246 (Sw/A) and S8607 (Sw/A). Fault location outside 2 Smith St, Dulwich Hill See 1530180 1530181 | November | 2017 | 2018Q2 | 2018 | ZN398:PA10 | ZN398:PA10 | ZN00398/000010 | INNER WEST | UG | Not Veg | 2017-11-29 | N | 81.467 | N | 3 | N | N | 1.1101 | 39.4971 | 35184.4075
[7 empty] | 7747 | 8008 | 1530143 | 2017-11-29 23:40 | 2017-11-30 08:20 | 520 | 11kV | 10676 | 123 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 174525 11kV OHM down near ABS 8278 Possible high into low at sub 8128 Section interrupted at Sw 2108 2340hrs to 2343hrs ABS 13610 Opened 2341hrs to 0440hrs Sub 8128 LVF left isolated EMSO required to check customer instillations in daylight EMSO completed checks left 1 customer isolated & LVF 8128 closed @ 0820hrs Excluded OMS 1530143 & 1530149 | November | 2017 | 2018Q2 | 2018 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2017-11-29 | N | 86.7967 | N | 3 | N | N | 1.1101 | 39.4971 | 7801.7059
[7 empty] | 7595 | 6255 | 1530263 | 2017-11-30 13:53 | 2017-11-30 13:59 | 6 | 11kV | 1587 | 310 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 174537/01 Sw 74180 Denman sub tripped due to faulty ABS 47729 connections on line side caused short between B & Cph conductors following item 13 of RSI 24608. Excluded OMS 1530263 | November | 2017 | 2018Q2 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2017-11-30 | N | 5.1194 | N | 4 | N | N | 1.1101 | 39.4971 | 1159.7328
[7 empty] | 7261 | 1461 | 1530398 | 2017-11-30 19:16 | 2017-11-30 19:20 | 4 | 11kV | 172 | 43 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 174543 Operating error | November | 2017 | 2018Q2 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-11-30 | N | 4 | N | 4 | N | N | 1.1101 | 39.4971 | 125.6925
[7 empty] | 8186 | 13531 | 1530284 | 2017-11-30 16:07 | 2017-11-30 19:30 | 203 | 11kV | 609 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174539 Single Phase DOLF : 10 Amp Excluded OMS 1530284 | November | 2017 | 2018Q2 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2017-11-30 | N | 203 | N | 4 | N | N | 1.1101 | 39.4971 | 445.0392
[7 empty] | 8653 | 19502 | 1530323 | 2017-11-30 19:11 | 2017-12-01 00:26 | 315 | 11kV | 16651 | 57 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 174540 Sw 75117 Load leads faulty flashed over RAGCB by passed Excluded OMS REPORT NO 1530323. | November | 2017 | 2018Q2 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-11-30 | N | 292.1228 | N | 4 | N | N | 1.1101 | 39.4971 | 12168.0597
[7 empty] | 8114 | 12703 | 1530412 | 2017-12-01 09:40 | 2017-12-01 13:15 | 215 | 11kV | 21715 | 101 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S2097 Queens Park Alt 31.5A HV fuse operated Cause: Tree branch on Mains on the Cnr of Queens Park Rd and Baronga Ave See OMS 1530412 1530415 | December | 2017 | 2018Q2 | 2018 | ZN2602:PA28 | ZN2602:PA28 | ZN02602/000028 | WAVERLEY | OH | Veg | 2017-12-01 | N | 215 | N | 6 | N | N | 1.1101 | 39.4971 | 15868.6815
[7 empty] | 7636 | 6688 | 1530476 | 2017-12-01 13:17 | 2017-12-01 18:08 | 291 | 11kV | 333336 | 1766 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S7481 Darling Harbour Panel 9 tripped on Overcurrent and Earth Fault Signals: 11kV Trip, TX11 Group Earth Cause: Front line feeder fault see OMS 1531098 1530476 | December | 2017 | 2018Q2 | 2018 | ZN7481:PA9 | ZN7481:PA9 | ZN07481/000009 | SYDNEY | UG | Not Veg | 2017-12-01 | N | 188.752 | N | 6 | N | N | 1.1101 | 39.4971 | 243592.1171
[7 empty] | 7502 | 5421 | 1530489 | 2017-12-01 14:25 | 2017-12-01 18:45 | 260 | 11kV | 780 | 3 | HV | Overload | Utility Process Issue | DC Transformer | Unplanned | No Weather Impact | N | At Zone 2835 Burwood: Ex 11kv panel 41 feeder panel 'S64159 etc' Sub 4100 Beresford Coventry tripped OHFMA 80 amp HV fuse operated. Remarks: overload. At S4100 Beresford Coventry: Dist Tx tripped, investigations required | December | 2017 | 2018Q2 | 2018 | ZN2835:PA31 | ZN2835:PA31 | ZN02835/000031 | STRATHFIELD | UG | Not Veg | 2017-12-01 | N | 260 | N | 6 | N | N | 1.1101 | 39.4971 | 570.001
[7 empty] | 8385 | 16049 | 1530591 | 2017-12-01 21:18 | 2017-12-01 23:05 | 107 | 11kV | 57217 | 621 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn3154 St Ives Panel 13 tripped on earth fault Signals: 11kV trip, Zone Earth, TX2 Group earth with efi Suspect fault on 11kV UGOH at IR63174 towards S49969 See OMS 1531627 1531629 1531630 1530591 1530593 1530596 | December | 2017 | 2018Q2 | 2018 | ZN3154:PA13 | ZN3154:PA13 | ZN03154/000013 | KU-RING-GAI | Unknown | Unknown | 2017-12-01 | N | 92.1369 | N | 6 | N | N | 1.1101 | 39.4971 | 41812.496
[7 empty] | 7925 | 10194 | 1530609 | 2017-12-01 23:58 | 2017-12-02 01:26 | 88 | 11kV | 18409 | 820 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At S36300 Balgowlah North Panel 8 tripped, reclosed, tripped and locked out on 3 phase IOC, EFI, UF, Abnormal Switching: link 78698 Open, SW/B at S44811 Closed Cause: Centre phase lightning/surge arrestorfailed at LB61274 See OMS 1531639 1531640 1530609 | December | 2017 | 2018Q2 | 2018 | ZN36300:PA8 | ZN15008:PA3 | ZN15008/000003 | NORTHERN BEACHES | OH | Not Veg | 2017-12-01 | N | 22.45 | N | 6 | N | N | 1.1101 | 39.4971 | 13452.7542
[7 empty] | 8472 | 17308 | 1530572 | 2017-12-01 19:45 | 2017-12-02 05:35 | 590 | 11kV | 291777 | 901 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S4990 City Central 55/56L Tripped on Relays: 55L Earth Fault Signals: 11kV Trip Abnormal Swithching: 55/56K and 55/56M Open (Feeder Tripped Earlier) Cause: Jointers suspect fault in underground Near S6018 Market George See OMS 1531067 1530572 | December | 2017 | 2018Q2 | 2018 | ZN4990:PA55 56KLM | ZN4990:PA55 56KLM | ZN04990/55 56KLM | SYDNEY | UG | Not Veg | 2017-12-01 | N | 323.8368 | N | 6 | N | N | 1.1101 | 39.4971 | 213222.0256
[7 empty] | 8346 | 15449 | 1530621 | 2017-12-02 06:20 | 2017-12-02 07:00 | 40 | 11kV | 9440 | 236 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Pa14 "S18478 Westfield Cobbs" fdr has tripped on: Signals: 11kv trip, Tx13 Group Earth Relays: Earth Fault, EFI EFI's: Nil UG Frontline feeder fault. Zn12690 Berkeley Vale pa14 to S18478 Westfield Cobbs (SwA) | December | 2017 | 2018Q2 | 2018 | ZN12690:PA14 | ZN12690:PA14 | ZN12690/000014 | CENTRAL COAST | UG | Not Veg | 2017-12-02 | N | 40 | N | 6 | N | N | 1.1101 | 39.4971 | 6898.4736
[7 empty] | 8337 | 15309 | 1530651 | 2017-12-02 10:23 | 2017-12-02 13:40 | 197 | 11kV | 15147 | 201 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 174556 2 fault operations B Phase Overcurrent Wire down at sub 77212 Victoria St - 11kV into LV Excluded oms 1530653, 1530652, 1530663, 1530654 | December | 2017 | 2018Q2 | 2018 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2017-12-02 | N | 75.3582 | N | 6 | N | N | 1.1101 | 39.4971 | 11068.9808
[7 empty] | 8239 | 14322 | 1530685 | 2017-12-02 15:14 | 2017-12-02 20:30 | 316 | 11kV | 307455 | 1929 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | N | Zn9550 Gwawley Bay - Pnl.43 tripped on: B & C phase Overcurrent with EFI Abnormal: LB35327 Closed with Sw/A @ S62079 Open Roadside Bond off @ LB35407 See 1531564 1531565 1531566 | December | 2017 | 2018Q2 | 2018 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Not Veg | 2017-12-02 | N | 159.3857 | N | 6 | N | N | 1.1101 | 39.4971 | 224679.0456
[7 empty] | 7301 | 2137 | 1530785 | 2017-12-02 20:26 | 2017-12-02 22:06 | 100.3333 | 11kV | 32708.6667 | 326 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser22381 Lane Cove Walter tripped, reclosed, tripped and locked out on IOC Cause: Bark removed Near PT15577 | December | 2017 | 2018Q2 | 2018 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2017-12-02 | N | 100.3333 | N | 6 | N | N | 1.1101 | 39.4971 | 23902.5289
[7 empty] | 7449 | 4657 | 1530764 | 2017-12-02 18:26 | 2017-12-02 22:42 | 256 | 11kV | 11060 | 72 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 174559 3 fault operations 3 phase Earth Fault Excluded oms 1530764 please patrol in daylight. dq | December | 2017 | 2018Q2 | 2018 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2017-12-02 | N | 153.6111 | N | 6 | N | N | 1.1101 | 39.4971 | 8082.3218
[7 empty] | 7906 | 9971 | 1530806 | 2017-12-02 23:41 | 2017-12-03 09:50 | 609 | 11kV | 12714 | 52 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 174561 3 fault operations Earth Fault Centre phase down pole DN-30312 possible HV into LV for 2 houses Excluded OMS 1530806 | December | 2017 | 2018Q2 | 2018 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2017-12-02 | N | 244.5 | N | 6 | N | N | 1.1101 | 39.4971 | 9291.0162
[7 empty] | 7657 | 6884 | 1530886 | 2017-12-03 13:00 | 2017-12-03 14:52 | 112 | 11kV | 112 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174563 A Phase DOLF : 10 Amp Excluded OMS 1530886 | December | 2017 | 2018Q2 | 2018 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2017-12-03 | N | 112 | N | 3 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 8176 | 13451 | 1530838 | 2017-12-03 09:10 | 2017-12-03 17:33 | 503 | 11kV | 175448 | 507 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 174564 trailer hit and broke pole HV OHM on ground Excluded oms 1530838,1530839,1530862,1530867,1530876 | December | 2017 | 2018Q2 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2017-12-03 | N | 346.0513 | N | 3 | N | N | 1.1101 | 39.4971 | 128212.2236
[7 empty] | 8344 | 15429 | 1530924 | 2017-12-03 20:26 | 2017-12-03 21:40 | 74 | 11kV | 6512 | 88 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | EX Zn12610 Long Jetty section of Pa18 PT14594 Alistair Lowanna 11kV Roadside & Footpath HDO's operated Cause: not ascertained See 1531311 ex 1530924,32,5 | December | 2017 | 2018Q2 | 2018 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Veg | 2017-12-03 | N | 74 | N | 3 | N | N | 1.1101 | 39.4971 | 4758.7775
[7 empty] | 7777 | 8415 | 1531030 | 2017-12-04 10:19 | 2017-12-04 15:55 | 336 | 11kV | 336 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 174574 Single phase DOLF : 10 Amp Replace Blown LA's. Excluded OMS No. 1531030 | December | 2017 | 2018Q2 | 2018 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2017-12-04 | N | 336 | N | 3 | N | N | 1.1101 | 39.4971 | 245.5389
[7 empty] | 8355 | 15603 | 1531185 | 2017-12-04 20:30 | 2017-12-04 22:00 | 90 | 11kV | 180 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 174580 Single phase DOLF : 3 Amp fuse fatigued. Excluded oms 1531185 | December | 2017 | 2018Q2 | 2018 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2017-12-04 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 7348 | 2882 | 1531196 | 2017-12-04 23:19 | 2017-12-05 00:07 | 48 | 11kV | 15468 | 382 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | LID 174581 2 fault operations 3 phase Overcurrent FAULTY HV CABLE AT POLE JT-73086. Excluded OMS 1531196 & 1531197. | December | 2017 | 2018Q2 | 2018 | 258:80773 | 258:80773 | ZN00258/080773 | NEWCASTLE | UG | Not Veg | 2017-12-04 | N | 40.4921 | N | 3 | N | N | 1.1101 | 39.4971 | 11303.5582
[7 empty] | 8552 | 18279 | 1531245 | 2017-12-05 09:06 | 2017-12-05 10:35 | 89 | 11kV | 126736 | 1424 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2466 Flemington Ex Panel 16 S814 Platform St the "Ann John" feeder tripped on - Relays: EFI, fault check Signals: Zone E, Group 2 E Field EFI's: Nil At S814 Platform St "S2390 Ann John" feeder - Relays: O/C, E/F Remarks: UG fault. UG fault from S814 Platform St to S2390 Ann John Sw/A | December | 2017 | 2018Q2 | 2018 | ZN2466:PA16 | ZN2466:PA16 | ZN02466/000016 | CUMBERLAND | UG | Not Veg | 2017-12-05 | N | 89 | N | 4 | N | N | 1.1101 | 39.4971 | 92614.9307
[7 empty] | 7698 | 7345 | 1531296 | 2017-12-05 11:09 | 2017-12-05 14:45 | 216 | 11kV | 357319 | 2010 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S35800 Bankstown 11kv "Gow Gibson" feeder panel No1 tripped on- Relays: B phase E/F Signals: Nil Field EFI's: S35208 Abnormal: sw/B closed @ S48207, LB 53 open Remarks: UG fault. Suspect UG cable fault from S35208 Gow Gibson Sw/A to LB1789 to AB1797 tee PT1206 Irvine Street | December | 2017 | 2018Q2 | 2018 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-12-05 | N | 177.7706 | N | 4 | N | N | 1.1101 | 39.4971 | 261118.1861
[7 empty] | 7354 | 2968 | 1531359 | 2017-12-05 15:01 | 2017-12-05 17:15 | 134 | 11kV | 134 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174595 Single Phase DOLF : 10 Amp Excluded OMS 1531359 | December | 2017 | 2018Q2 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2017-12-05 | N | 134 | N | 4 | N | N | 1.1101 | 39.4971 | 97.9232
[7 empty] | 7529 | 5626 | 1531480 | 2017-12-05 23:27 | 2017-12-06 09:55 | 628 | 11kV | 947 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 174599 Single phase DOLF : 5 Amp DOLF 71926 ALSO FOUND BLOWN. Sub 70731 left isolated staff to attend in daylight. Excluded oms report no 1531480. | December | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2017-12-05 | N | 315.6667 | N | 4 | N | N | 1.1101 | 39.4971 | 692.0397
[7 empty] | 8328 | 15244 | 1531628 | 2017-12-06 13:36 | 2017-12-06 14:55 | 79 | 11kV | 139336 | 2169 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Lightning | N | Zn9252 Jannali - Pnl.27 tripped on: Earth Fault Abnormal:AB35498 Closed, AB35626 Closed, S9130 (Sw/B) open, AB35847 and AB35805 Open (D/R 416643) Lightning struck PT9713 Ingrid Rd Note: PT9759 was isolated and in LV // but still received an interruption due to the paralleling DC's losing supply. See 1531782 1531783 1531786 | December | 2017 | 2018Q2 | 2018 | ZN9252:PA27 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | OH | Not Veg | 2017-12-06 | N | 64.2397 | N | 3 | N | N | 1.1101 | 39.4971 | 101822.6391
[7 empty] | 7656 | 6872 | 1531697 | 2017-12-06 16:54 | 2017-12-06 23:20 | 386 | 11kV | 8391 | 81 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 174619 Tree onto OHM pole JS-60135. 33kV involved, see #174618/OMS 1531759. Protection malgrade, conductor on ground, fdr did not trip. Grass fire also present in this location. Excluded OMS 1531697, 1531702 | December | 2017 | 2018Q2 | 2018 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Veg | 2017-12-06 | N | 103.5926 | N | 3 | N | N | 1.1101 | 39.4971 | 6131.8953
[7 empty] | 7985 | 10843 | 1531732 | 2017-12-06 22:25 | 2017-12-06 23:45 | 80 | 11kV | 160 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174621 C Phase DOLF : 10 Amp Excluded OMS 1531732 | December | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-12-06 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 7296 | 2093 | 1531758 | 2017-12-07 08:24 | 2017-12-07 11:05 | 161 | 11kV | 1610 | 10 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | 11kV feeder beyond AB173 interrupted after car backed into pole, snapping down rod and cauing AB to Open | December | 2017 | 2018Q2 | 2018 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Not Veg | 2017-12-07 | N | 161 | N | 3 | N | N | 1.1101 | 39.4971 | 1176.5405
[7 empty] | 8699 | 20072 | 1531867 | 2017-12-07 18:00 | 2017-12-07 19:20 | 80 | 11kV | 480 | 6 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 174632 Replace X arm pole 2J-30042 Excluded OMS 1531867 | December | 2017 | 2018Q2 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-12-07 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 7879 | 9728 | 1531916 | 2017-12-07 21:18 | 2017-12-08 02:20 | 302 | 11kV | 24432 | 156 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S1695 Powell Ford - 11kV Fuse "A" phase operated. Striker Pin failed to operated. B & C phase fuses were replaced interrupting supply to whole sub. HV and LV fuses failed to grade for a LV service fault at 613 New South Head Rd. Jointers cut away service and terminated inot service box to enable restoration of Dist #2. See 1531989 1531990 | December | 2017 | 2018Q2 | 2018 | ZN3155:PA22 | ZN3155:PA22 | ZN03155/000022 | WOOLLAHRA | UG | Not Veg | 2017-12-07 | N | 156.6154 | N | 3 | N | N | 1.1101 | 39.4971 | 17854.185
[7 empty] | 7358 | 3084 | 1532025 | 2017-12-08 12:39 | 2017-12-08 14:15 | 96 | 11kV | 140320 | 1462 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.18 tripped on: C Phase O/C with EFI Field EFIs S1346 UG cable fault from S1346 (Sw/B) to S1688 (Sw/A) to S65993 (Sw/B) See 1532476 1532477 | December | 2017 | 2018Q2 | 2018 | ZN690:PA18 | ZN690:PA18 | ZN00690/000018 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-12-08 | N | 95.9781 | N | 4 | N | N | 1.1101 | 39.4971 | 102541.7173
[7 empty] | 7896 | 9943 | 1532065 | 2017-12-08 16:21 | 2017-12-08 17:50 | 89 | 11kV | 10899 | 457 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 174638 2 fault operations Overcurrent fork lift into mains pole JT-40009. Excluded OMS 1532065 | December | 2017 | 2018Q2 | 2018 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2017-12-08 | N | 23.849 | N | 4 | N | N | 1.1101 | 39.4971 | 7964.6677
[7 empty] | 7325 | 2641 | 1532085 | 2017-12-08 17:37 | 2017-12-08 18:45 | 68.2167 | 11kV | 1227.9 | 18 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 174640 Cause conductor on x arm pole GS-24258. | December | 2017 | 2018Q2 | 2018 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Not Veg | 2017-12-08 | N | 68.2167 | N | 4 | N | N | 1.1101 | 39.4971 | 897.3131
[7 empty] | 8222 | 14036 | 1531953 | 2017-12-08 08:42 | 2017-12-08 19:05 | 623 | 11kV | 1246 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 174641 Replaced defective transformer excluded OMS 1531953 | December | 2017 | 2018Q2 | 2018 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2017-12-08 | N | 623 | N | 4 | N | N | 1.1101 | 39.4971 | 910.54
[7 empty] | 7844 | 9283 | 1532180 | 2017-12-09 11:41 | 2017-12-09 13:30 | 109 | 11kV | 133704 | 1228 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At Zn2635 Epping - Panel 55 tripped on C phase IOC Signals: 11kV Trip with efi Cause: Cable damaged by contractors 11kV Cable damaged from S66047 to S66082 to S5702 See OMS 1532473 1532475 1532180 | December | 2017 | 2018Q2 | 2018 | ZN2635:PA55 | ZN2635:PA55 | ZN02635/000055 | PARRAMATTA | UG | Not Veg | 2017-12-09 | N | 108.8795 | N | 5 | N | N | 1.1101 | 39.4971 | 97706.9396
[7 empty] | 7388 | 3740 | 1532199 | 2017-12-09 12:56 | 2017-12-09 16:40 | 223.5667 | 11kV | 3129.9333 | 14 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 174650 A & B Phase DOLF : 20 Amp tree brought down OHM | December | 2017 | 2018Q2 | 2018 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2017-12-09 | N | 223.5667 | N | 5 | N | N | 1.1101 | 39.4971 | 2287.263
[7 empty] | 7680 | 7110 | 1532234 | 2017-12-09 17:28 | 2017-12-09 18:31 | 63 | 11kV | 43281 | 687 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 20 opened on Relays: Earth Fault, EFI Signals: 11kV trip, Zone Earth, TX3 Group Earth Cause: UG fault - 11kV feeder fault from S5388 Franklin New Line to S63055 Gumnut Holly See OMS 1532465 1532466 1532234 | December | 2017 | 2018Q2 | 2018 | ZN965:PA20 | ZN965:PA20 | ZN00965/000020 | HORNSBY | UG | Not Veg | 2017-12-09 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 31628.4782
[7 empty] | 7735 | 7840 | 1532238 | 2017-12-09 17:45 | 2017-12-09 19:35 | 110 | 11kV | 80928 | 886 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 174652 1 fault operation Earth Fault SCADA reclose did not operate. Prot Op Indication not received in SCADA events. Excluded oms 1532238 | December | 2017 | 2018Q2 | 2018 | 216:10724 | 216:10724 | ZN00216/010724 | LAKE MACQUARIE | OH | Not Veg | 2017-12-09 | N | 91.3409 | N | 5 | N | N | 1.1101 | 39.4971 | 59139.7954
[7 empty] | 8440 | 16816 | 1532253 | 2017-12-09 20:44 | 2017-12-09 23:19 | 155 | 11kV | 136301 | 1156 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | At Zn12570 Avoca Pa26 fdr "Avoca Aux" tripped on: Relays: EFI and trip lights, 50T BC, 150 TN EFI, EF check Signals: 11kv trip EFI'S: S49886 S14846 S49472 S1285 S1412 Recloser 40425 tripped on relays: OC IOC Signals: 11kV Lockout Cause: Animals/Birds Possum at base of RE40425 Kurrawyba Cadell Either Possum has physically damaged the recloser or the recloser has had an issue as a result of the fault. When the recloser has more than 10Amps or so it trips. Please inspect See 1532735,6,7 ex 1532253,5 | December | 2017 | 2018Q2 | 2018 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2017-12-09 | N | 117.9074 | N | 5 | N | N | 1.1101 | 39.4971 | 99604.7506
[7 empty] | 8579 | 18568 | 1532262 | 2017-12-10 00:11 | 2017-12-10 01:28 | 77 | 11kV | 96789 | 1257 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn12620 Noraville Paenl 8 "Manoa Av' fdr tripped Signals: 11kv trip Relays: EF EFI Reclose relay, Lockout EFI's: as expected Cause: Animals/Birds Possum found on UGOH near PT11147 Noela Natuna See 1532262 ex 1532266,7 | December | 2017 | 2018Q2 | 2018 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2017-12-10 | N | 77 | N | 3 | N | N | 1.1101 | 39.4971 | 70730.5464
[7 empty] | 7526 | 5611 | 1532265 | 2017-12-10 00:17 | 2017-12-10 03:39 | 202 | 11kV | 169056 | 1160 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 11 tripped on: Signals: 11kV trip, No2 Group Earth, Zone Earth relays: A and C phase IOC, C phase timed, Timer, Lockout, EFI Feeder: Cause not ascertained. See OMS 1532516 1532517 1532518 1532520 1532521 1532265 | December | 2017 | 2018Q2 | 2018 | ZN965:PA11 | ZN965:PA17 | ZN00965/000017 | HORNSBY | OH | Veg | 2017-12-10 | N | 145.7379 | N | 3 | N | N | 1.1101 | 39.4971 | 123541.1385
[7 empty] | 7615 | 6444 | 1532360 | 2017-12-10 20:34 | 2017-12-11 01:20 | 286 | 11kV | 79752 | 850 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14143 Somersby Pa17 "Somersby Falls" fdr tripped on: Relays: SEF Signals: 11kv trip Cause: OH down See 1532748,50 ex 1532360 | December | 2017 | 2018Q2 | 2018 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2017-12-10 | N | 93.8259 | N | 3 | N | N | 1.1101 | 39.4971 | 58280.4093
[7 empty] | 8471 | 17302 | 1532393 | 2017-12-11 08:31 | 2017-12-11 11:20 | 169 | 11kV | 338 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 174660 C Phase dolf fell out. fuse ok. Excluded OMS 1532393 | December | 2017 | 2018Q2 | 2018 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2017-12-11 | N | 169 | N | 2 | N | N | 1.1101 | 39.4971 | 247.0004
[7 empty] | 7630 | 6608 | 1532585 | 2017-12-11 21:35 | 2017-12-11 23:40 | 125 | 11kV | 1125 | 9 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174673 A Phase DOLF : 16 Amp Dead possum found at sub Excluded OMS 1532585 | December | 2017 | 2018Q2 | 2018 | 512:48046 | 512:83741 | ZN00512/083741 | CESSNOCK | OH | Not Veg | 2017-12-11 | N | 125 | N | 2 | N | N | 1.1101 | 39.4971 | 822.1168
[7 empty] | 7341 | 2817 | 1532720 | 2017-12-12 14:47 | 2017-12-12 15:29 | 42 | 11kV | 35694 | 1040 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 174687 2 fault operations 3 phase Overcurrent Tree branch in 11kV OHM at pole HR-31549. Excluded OMS No. 1532720 | December | 2017 | 2018Q2 | 2018 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2017-12-12 | N | 34.3212 | N | 6 | N | N | 1.1101 | 39.4971 | 26084.1224
[7 empty] | 7687 | 7207 | 1532592 | 2017-12-12 00:12 | 2017-12-12 16:00 | 948 | 11kV | 159995 | 1090 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S16673 Turramurra Panel 6 tripped reclosed tripped and locked out on A B and C phase IOC Cause: Large Tree brought down 11kV and LV See OMS 1533185 1533187 1533189 1532592 1532593 15321532604 | December | 2017 | 2018Q2 | 2018 | ZN1673:PA6 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Veg | 2017-12-12 | N | 146.7844 | N | 6 | N | N | 1.1101 | 39.4971 | 116919.6269
[7 empty] | 7375 | 3454 | 1532612 | 2017-12-12 08:05 | 2017-12-12 18:00 | 595 | 11kV | 1785 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 174688 A & B phase DOLF : 10 Amp Hole in tx tank, No Oil & faulty Tx. Tx replaced. Excluded OMS No. 1532612 | December | 2017 | 2018Q2 | 2018 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2017-12-12 | N | 595 | N | 6 | N | N | 1.1101 | 39.4971 | 1304.4254
[7 empty] | 8313 | 15134 | 1532790 | 2017-12-12 19:12 | 2017-12-12 19:46 | 34 | 11kV | 68 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 174691 A phase DOLF : 31 Amp Replaced A phase fuse carrier. Excluded OMS 1532790 | December | 2017 | 2018Q2 | 2018 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2017-12-12 | N | 34 | N | 6 | N | N | 1.1101 | 39.4971 | 49.6924
[7 empty] | 7516 | 5539 | 1532797 | 2017-12-12 19:42 | 2017-12-12 22:05 | 143 | 11kV | 87879 | 1246 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12650 West Gosford - Pnl.3 tripped on: C Phase O/C, Earth Fault with EFI Field EFIs: S18075 S18198 S14823 Possible UG cable fault from LB77993 t S14118 to S11172 See 1533183 1533184 1533186 1533188 | December | 2017 | 2018Q2 | 2018 | ZN12650:PA3 | ZN12650:PA3 | ZN12650/000003 | CENTRAL COAST | UG | Not Veg | 2017-12-12 | N | 70.5289 | N | 6 | N | N | 1.1101 | 39.4971 | 64219.3812
[7 empty] | 7329 | 2706 | 1532679 | 2017-12-12 12:20 | 2017-12-12 22:40 | 620 | 11kV | 34368 | 259 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 174685 car hit pole KR-80001 section isolated for pole repair Excluded oms 1532679 | December | 2017 | 2018Q2 | 2018 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2017-12-12 | N | 132.695 | N | 6 | N | N | 1.1101 | 39.4971 | 25115.1207
[7 empty] | 7365 | 3208 | 1532944 | 2017-12-13 14:16 | 2017-12-13 14:42 | 26.3 | 11kV | 15937.8 | 606 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Hot >35C | N | LID 174709 2 fault operations Instantaneous Earth Fault; Instantaneous Overcurrent faulty arrestors at ugoh pole AK-61110. Section isolated for repairs 14/12/17 | December | 2017 | 2018Q2 | 2018 | 801:74120 | 801:74120 | ZN00801/074120 | MUSWELLBROOK | OH | Not Veg | 2017-12-13 | N | 26.3 | N | 6 | N | N | 1.1101 | 39.4971 | 11646.8742
[7 empty] | 7693 | 7266 | 1532948 | 2017-12-13 14:21 | 2017-12-13 15:30 | 69 | 11kV | 3328 | 72 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Hot >35C | N | LID 174710 3 phase fdr 35198 off loaded to break taps both sides of ABS 1766 so that fdr could be rearranged and restored. Excluded oms1532926 | December | 2017 | 2018Q2 | 2018 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2017-12-13 | N | 46.2222 | N | 6 | N | N | 1.1101 | 39.4971 | 2432.0042
[7 empty] | 8256 | 14460 | 1532981 | 2017-12-13 16:20 | 2017-12-13 18:05 | 105 | 11kV | 236487 | 2335 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN3922 Drummoyne - 11kv Panel No.2 "Sub 1212 Edenholme" feeder tripped Relays: Earth fault, fault check, efi Signals: 11kv trip, Zone Earth, No.1 Group Earth Remarks: UG fault. 11kv UG feeder fault from S5565 Beattie Llewellyn to S2467 Johnston Pear to S49038 Church Darling | December | 2017 | 2018Q2 | 2018 | ZN3922:PA2 | ZN3922:PA2 | ZN03922/000002 | INNER WEST | UG | Not Veg | 2017-12-13 | N | 101.2792 | N | 6 | N | N | 1.1101 | 39.4971 | 172817.7244
[7 empty] | 7180 | 42 | 1533004 | 2017-12-13 17:05 | 2017-12-13 18:37 | 92 | 11kV | 224676 | 2728 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.1 tripped on: Earth Fault Field EFIs: All from Pnl.1L to S36061 See 1533111 1533112 | December | 2017 | 2018Q2 | 2018 | ZN35600:PA1 | ZN35600:PA1 | ZN35600/000001 | RANDWICK | UG | Not Veg | 2017-12-13 | N | 82.3592 | N | 6 | N | N | 1.1101 | 39.4971 | 164186.594
[7 empty] | 7829 | 9044 | 1533051 | 2017-12-13 22:23 | 2017-12-13 23:34 | 71 | 11kV | 74905 | 1055 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | At S4545 Meadowbank Recloser CP46118 Dalton Blaxland Tripped on Earth fault and Lockoutout Cause: Possum found ontop of recloser 46118 See OMS 1533051 1533054 | December | 2017 | 2018Q2 | 2018 | ZN4545:PA36 | ZN4545:PA36 | ZN04545/000036 | RYDE | OH | Not Veg | 2017-12-13 | N | 71 | N | 6 | N | N | 1.1101 | 39.4971 | 54738.3647
[7 empty] | 7376 | 3494 | 1533049 | 2017-12-13 22:19 | 2017-12-14 00:06 | 107 | 11kV | 1177 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At PT1752 Quarry Eloura EReserve HDO blown Roadside phase Cause not ascertained for outage See OMS 1533199 1533050 1533049 | December | 2017 | 2018Q2 | 2018 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2017-12-13 | N | 107 | N | 6 | N | N | 1.1101 | 39.4971 | 860.1169
[7 empty] | 7744 | 7970 | 1533211 | 2017-12-14 13:53 | 2017-12-14 15:39 | 106 | 11kV | 4610 | 50 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At Zn1610 Homebush Panel 10 'S7130' feeder has tripped Signals: 11kv trip Relays: C phase EF, EFI Field EFI's: S7138 Remarks: end box fault. End box of Sw/D @ Sub 7138 Slough Holker has failed | December | 2017 | 2018Q2 | 2018 | ZN1610:PA10 | ZN1610:PA10 | ZN01610/000010 | PARRAMATTA | Unknown | Not Veg | 2017-12-14 | N | 92.2 | N | 6 | N | N | 1.1101 | 39.4971 | 3368.852
[7 empty] | 8335 | 15292 | 1533255 | 2017-12-14 16:04 | 2017-12-14 17:40 | 96 | 11kV | 12148 | 131 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1610 Homebush Bay Panel 23 'S7566' feeder has tripped Signals: 11kv trip Relays: OC and EF Field EFI's: as expected Remarks: UG fault. UG fault between sw/B @ S63667 and Sw/A S2421 | December | 2017 | 2018Q2 | 2018 | ZN1610:PA23 | ZN2466:PA7 | ZN02466/000007 | PARRAMATTA | UG | Not Veg | 2017-12-14 | N | 92.7328 | N | 6 | N | N | 1.1101 | 39.4971 | 8877.4001
[7 empty] | 8632 | 19249 | 1533242 | 2017-12-14 15:15 | 2017-12-14 18:05 | 170 | 11kV | 170 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | HV Fuse found blown @ S4100 Beresford Coventry 80A OHFMA Remarks: customer's installation. See DMA issue with telstra | December | 2017 | 2018Q2 | 2018 | ZN2835:PA41 | ZN2835:PA41 | ZN02835/000041 | STRATHFIELD | Unknown | Not Veg | 2017-12-14 | N | 170 | N | 6 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 8021 | 11318 | 1533289 | 2017-12-14 16:00 | 2017-12-14 19:25 | 205 | 11kV | 16605 | 81 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 174732 A Phase DOLF : 40 Amp Excluded oms 1533289,1533291,1533314,1533301 | December | 2017 | 2018Q2 | 2018 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2017-12-14 | N | 205 | N | 6 | N | N | 1.1101 | 39.4971 | 12134.4442
[7 empty] | 7181 | 60 | 1533339 | 2017-12-14 19:48 | 2017-12-14 21:20 | 92 | 11kV | 1288 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174735 Fuse Size 10 Amp Substation DOLF Electrical Storm., also see OMS 1533339 | December | 2017 | 2018Q2 | 2018 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2017-12-14 | N | 92 | N | 6 | N | N | 1.1101 | 39.4971 | 941.2324
[7 empty] | 7753 | 8069 | 1533309 | 2017-12-14 18:35 | 2017-12-14 21:40 | 185 | 11kV | 185 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S5235 Ryde Eastwood B phase 80A SIBA fuse operated. Cause: HV fuse replaced and supply restore NOTE: All distributors normally open except dikstributor 1 | December | 2017 | 2018Q2 | 2018 | ZN4545:PA6 | ZN4545:PA6 | ZN04545/000006 | RYDE | OH | Veg | 2017-12-14 | N | 185 | N | 6 | N | N | 1.1101 | 39.4971 | 135.1925
[7 empty] | 7592 | 6214 | 1533382 | 2017-12-15 01:48 | 2017-12-15 02:55 | 67 | 11kV | 9778 | 170 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn4990 City Central - Pnl.57L tripped on: Earth Fault Radial 11kV feeder fed from City Central - Not triplex Field EFIs: S6812 S8847 UG cable fault from S8847 (Sw/D) to S7709 (Sw/D) to S8214 (Sw/A) See 1533439 1533440 | December | 2017 | 2018Q2 | 2018 | ZN4990:PA57L | ZN4990:PA57K | ZN04990/00057K | SYDNEY | UG | Not Veg | 2017-12-15 | N | 57.5176 | N | 5 | N | N | 1.1101 | 39.4971 | 7145.474
[7 empty] | 8158 | 13248 | 1533548 | 2017-12-15 18:53 | 2017-12-15 20:00 | 67 | 11kV | 67 | 1 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 174748 Fuse Size 3 Amp Substation DOLF Bird Contacted Mains Also refer to OM S1533548 | December | 2017 | 2018Q2 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2017-12-15 | N | 67 | N | 5 | N | N | 1.1101 | 39.4971 | 48.9616
[7 empty] | 7871 | 9587 | 1533559 | 2017-12-15 21:29 | 2017-12-15 23:16 | 107.2667 | 11kV | 3968.8667 | 37 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174753 A & C Phase - Fuse 20 Amp Line DOLF Electrical Storm | December | 2017 | 2018Q2 | 2018 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-12-15 | N | 107.2667 | N | 5 | N | N | 1.1101 | 39.4971 | 2900.3307
[7 empty] | 7877 | 9694 | 1533539 | 2017-12-15 17:52 | 2017-12-16 00:17 | 385 | 11kV | 770 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Replaced Dolf | December | 2017 | 2018Q2 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2017-12-15 | N | 385 | N | 5 | N | N | 1.1101 | 39.4971 | 562.6933
[7 empty] | 8611 | 18994 | 1533572 | 2017-12-15 21:45 | 2017-12-16 02:30 | 285 | 11kV | 1225 | 21 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174754 Single phase DOLF : 10 Amp POSSUM ON POLE. & FAULTY L/LINE CLAMP. FDR ISOLATED AT SW 42011 TO REPLACE LLC. Excluded OMS REPORT NO 1533572. | December | 2017 | 2018Q2 | 2018 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2017-12-15 | N | 58.3333 | N | 5 | N | N | 1.1101 | 39.4971 | 895.1939
[7 empty] | 8402 | 16339 | 1533610 | 2017-12-16 09:58 | 2017-12-16 11:35 | 97 | 11kV | 105148 | 1084 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | Trip & reclose 1 fault operation 3 phase Overcurrent Most customers part supply after tapping burnt off at ABS 40057. 3 phase supply restored at 1135hrs by feeding from Sw 48004. Repairs completed 1600hrs approx. System returned to normal. | December | 2017 | 2018Q2 | 2018 | 502:48008 | 502:48008 | ZN00502/048008 | MAITLAND | OH | Not Veg | 2017-12-16 | N | 97 | N | 7 | N | N | 1.1101 | 39.4971 | 76839.0571
[7 empty] | 8559 | 18346 | 1533625 | 2017-12-16 10:10 | 2017-12-16 12:00 | 110 | 11kV | 13200 | 120 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Electrical Storm | N | LID 174768C Phase DOLF : 40 Amp DOLF fuse wedge burning, replaced. Excluded OMS 1533625, 1533627, 1533630, 1533631 | December | 2017 | 2018Q2 | 2018 | 528:83013 | 528:83013 | ZN00528/083013 | MAITLAND | OH | Not Veg | 2017-12-16 | N | 110 | N | 7 | N | N | 1.1101 | 39.4971 | 9646.1707
[7 empty] | 7547 | 5798 | 1533612 | 2017-12-16 10:11 | 2017-12-16 12:00 | 109 | 11kV | 74251 | 1053 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174766 1 fault operation Sensitive Earth Fault Feeder Patrolled. Found Faulty Tx 54191. Excluded OMS 1533612 & 1533628 | December | 2017 | 2018Q2 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2017-12-16 | N | 70.5138 | N | 7 | N | N | 1.1101 | 39.4971 | 54260.4408
[7 empty] | 7802 | 8746 | 1533628 | 2017-12-16 10:11 | 2017-12-16 18:05 | 474 | 11kV | 2370 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174769 Single phase DOLF : 10 Amp Possible Tx Fault. Feeder Restored after full patrol.. Excluded OMS 1533628 OMS 1533612 | December | 2017 | 2018Q2 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2017-12-16 | N | 474 | N | 7 | N | N | 1.1101 | 39.4971 | 1731.9261
[7 empty] | 7609 | 6393 | 1533686 | 2017-12-16 14:34 | 2017-12-16 21:45 | 431 | 11kV | 3592 | 14 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 174771 2 fault operations Sensitive Earth fault; Earth Fault Please PAtrol First Fault SEF. 2nd Fault E/F Excluded OMS 1533686 | December | 2017 | 2018Q2 | 2018 | 813:89058 | 813:89058 | ZN00813/089058 | UPPER HUNTER | OH | Not Veg | 2017-12-16 | N | 256.5714 | N | 7 | N | N | 1.1101 | 39.4971 | 2624.9277
[7 empty] | 8537 | 18027 | 1533753 | 2017-12-17 01:39 | 2017-12-17 02:25 | 46 | 11kV | 44574 | 969 | HV | Animal Flying Fox | Animal | UGOH | Unplanned | No Weather Impact | N | At ZN3425 Castle Cove Panel 44 tripped on Relays: A phase OC Signals: 11kV trip Field EFI's NIL Cause: Bat caused flash over at UGOH @ PT2218 Linden High Tor, No apparent damage to mains See OMS 1533753 1534195 1533763 1533754 CC1: 22-"Refer to SOp" | December | 2017 | 2018Q2 | 2018 | ZN3425:PA44 | ZN3425:PA44 | ZN03425/000044 | WILLOUGHBY | OH | Not Veg | 2017-12-17 | N | 46 | N | 12 | N | N | 1.1101 | 39.4971 | 32573.3645
[7 empty] | 7463 | 4846 | 1533764 | 2017-12-17 04:22 | 2017-12-17 07:00 | 158.3333 | 11kV | 1583.3333 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174777 C Phase DOLF : 10 Amp | December | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-12-17 | N | 158.3333 | N | 12 | N | N | 1.1101 | 39.4971 | 1157.0533
[7 empty] | 7601 | 6319 | 1533779 | 2017-12-17 06:39 | 2017-12-17 07:49 | 70 | 11kV | 3920 | 56 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Lightning | N | At Zn2400 Berowra panel 13 feeder tripped Relauys: B and C phase timed O/C, EFI Fault Check Cause: AB1262 hit by lightning (Common AB with Hornsby panel 47) | December | 2017 | 2018Q2 | 2018 | ZN2400:PA13 | ZN2400:PA13 | ZN02400/000013 | HORNSBY | OH | Not Veg | 2017-12-17 | N | 70 | N | 12 | N | N | 1.1101 | 39.4971 | 2864.6204
[7 empty] | 8073 | 12118 | 1533652 | 2017-12-16 11:32 | 2017-12-17 09:30 | 1318 | 11kV | 1318 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174781 B Phase Fuse 10 Amp Substation DOLF Electrical Storm delay due to storm going through the area | December | 2017 | 2018Q2 | 2018 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Veg | 2017-12-16 | N | 1318 | N | 7 | N | N | 1.1101 | 39.4971 | 963.1555
[7 empty] | 7310 | 2362 | 1533804 | 2017-12-17 09:20 | 2017-12-17 18:45 | 565 | 11kV | 10170 | 18 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 174784 Broken crossarm | December | 2017 | 2018Q2 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2017-12-17 | N | 565 | N | 12 | N | N | 1.1101 | 39.4971 | 7431.936
[7 empty] | 7512 | 5516 | 1533885 | 2017-12-17 17:30 | 2017-12-17 19:15 | 105 | 11kV | 399983 | 3841 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn35800 bankstown Panel 14 'S64012' feeder has tripped Signals: 11kv trip Relays: 51T AB Field EFI's: Nil Abnormal: AB54 closed with LB 1789 Open Remarks: cause not ascertained | December | 2017 | 2018Q2 | 2018 | ZN35800:PA14 | ZN35800:PA14 | ZN35800/000014 | CANTERBURY-BANKSTOWN | OH | Veg | 2017-12-17 | N | 104.1351 | N | 12 | N | N | 1.1101 | 39.4971 | 292295.7789
[7 empty] | 7784 | 8502 | 1533908 | 2017-12-17 19:59 | 2017-12-17 21:20 | 81 | 11kV | 1296 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174787 A & C phase DOLF : 20 Amp Excluded OMS 1533908 | December | 2017 | 2018Q2 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-12-17 | N | 81 | N | 12 | N | N | 1.1101 | 39.4971 | 947.0786
[7 empty] | 7791 | 8658 | 1533909 | 2017-12-17 20:40 | 2017-12-17 21:45 | 65 | 11kV | 65 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174791 A Phase DOLF : 10 Amp Excluded OMS 1533909 | December | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-12-17 | N | 65 | N | 12 | N | N | 1.1101 | 39.4971 | 47.5001
[7 empty] | 8507 | 17696 | 1533935 | 2017-12-17 21:38 | 2017-12-17 22:18 | 40 | 11kV | 2136 | 55 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 174793 Earth Fault Blown arrestors at RAGCB 6C986 Excluded OMS 1533935 | December | 2017 | 2018Q2 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-12-17 | N | 38.8364 | N | 12 | N | N | 1.1101 | 39.4971 | 1560.9258
[7 empty] | 8607 | 18923 | 1533923 | 2017-12-17 21:01 | 2017-12-17 22:50 | 109 | 11kV | 185249 | 1797 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3155 Double Bay - Pnl.29 tripped on: Earth Fault Field EFIs: S1859 S64497 S2993 S3167 S3641 S783 UG cable fault from S783 (Sw/A) to S36254 (Sw/A) See 1534209 1534210 | December | 2017 | 2018Q2 | 2018 | ZN3155:PA29 | ZN3155:PA29 | ZN03155/000029 | WOOLLAHRA | UG | Not Veg | 2017-12-17 | N | 103.0879 | N | 12 | N | N | 1.1101 | 39.4971 | 135374.5053
[7 empty] | 7986 | 10848 | 1533929 | 2017-12-17 21:15 | 2017-12-17 23:20 | 125.2 | 11kV | 125.2 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174803 3 phase DOLF : 10 Amp Excluded OMS 1533930 | December | 2017 | 2018Q2 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-12-17 | N | 125.2 | N | 12 | N | N | 1.1101 | 39.4971 | 91.4925
[7 empty] | 8273 | 14627 | 1533932 | 2017-12-17 21:35 | 2017-12-18 00:50 | 195 | 11kV | 390 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174808 Single phase DOLF : 10 Amp Excluded OMS 1533932 | December | 2017 | 2018Q2 | 2018 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2017-12-17 | N | 195 | N | 12 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 8696 | 19972 | 1533916 | 2017-12-17 20:35 | 2017-12-18 01:00 | 265.1333 | 11kV | 1855.9333 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 174806 A Phase BURNT OFF TAPPING AT ABS 75026.REPAIRED LIVE LINE Excluded OMS 1533925 | December | 2017 | 2018Q2 | 2018 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2017-12-17 | N | 265.1333 | N | 12 | N | N | 1.1101 | 39.4971 | 1356.2613
[7 empty] | 8154 | 13218 | 1533950 | 2017-12-18 00:46 | 2017-12-18 04:15 | 209 | 11kV | 62722 | 1276 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 174811 2 HV MAINS ON GROUND FROM POLE FS-92760 TO 50401 CURRY ST NORTH SUB. (ALIVE ON BACKFEED) ALSO SEE UPO/REPORT NO 174805. PLEASE CHECK FAULT LEVELS. Excluded OMS REPORT NO 1533951,1533943,1533945. | December | 2017 | 2018Q2 | 2018 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2017-12-18 | N | 49.1552 | N | 20 | Y | Y | 1.1101 | 39.4971 | 45835.3876
[7 empty] | 8536 | 18023 | 1533972 | 2017-12-18 06:04 | 2017-12-18 10:00 | 236 | 11kV | 236 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174835 Single phase DOLF : 10 Amp Excluded OMS 1533972 | December | 2017 | 2018Q2 | 2018 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2017-12-18 | N | 236 | N | 20 | Y | Y | 1.1101 | 39.4971 | 172.4618
[7 empty] | 7684 | 7167 | 1534019 | 2017-12-18 08:58 | 2017-12-18 10:20 | 82 | 11kV | 164 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174831 C Phase, 10 Amp fuse substation DOLF Electrical Storm, also refer to 1534019 | December | 2017 | 2018Q2 | 2018 |  |  |  |  | OH | Veg | 2017-12-18 | N | 82 | N | 20 | Y | Y | 1.1101 | 39.4971 | 119.8464
[7 empty] | 8384 | 16041 | 1533975 | 2017-12-18 06:18 | 2017-12-18 11:30 | 312 | 11kV | 624 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174833 Single phase DOLF : 3 Amp Excluded OMS 1533975 | December | 2017 | 2018Q2 | 2018 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2017-12-18 | N | 312 | N | 20 | Y | Y | 1.1101 | 39.4971 | 456.0008
[7 empty] | 8181 | 13491 | 1533999 | 2017-12-18 08:08 | 2017-12-18 11:35 | 207 | 11kV | 149985 | 1686 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn847 Hornsby Panel 21 tripped and locked out Relays: Earth Fault, EFI, Lockout and Timing and Fault Check Signals: TX2 Group Earth and Zone Earth. Cause: Crane hit OH at 325 Peats Ferry Rd section of 11kV feeder isolated from AB3088 to S65771 to LB2701 See OMS 1534511 1534516 1534518 1534517 1533999 1534003 1534004 1534038 | December | 2017 | 2018Q2 | 2018 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Not Veg | 2017-12-18 | N | 88.9591 | N | 20 | Y | Y | 1.1101 | 39.4971 | 109604.6142
[7 empty] | 8092 | 12330 | 1534117 | 2017-12-18 12:35 | 2017-12-18 13:59 | 84 | 11kV | 4056 | 52 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde Panel 14 tripped on Relays: Earth Fault, Fault Check and EFI Signals: Zone and TX2 earth and 11kV trip. Cause: UG fault from ZN35500 Top Ryde Panel 14 to S6142 to S8899 See OMS 1534539 1534117 | December | 2017 | 2018Q2 | 2018 | ZN35500:PA14 | ZN35500:PA14 | ZN35500/000014 | RYDE | UG | Not Veg | 2017-12-18 | N | 78 | N | 20 | Y | Y | 1.1101 | 39.4971 | 2964.0052
[7 empty] | 7710 | 7560 | 1534235 | 2017-12-18 16:43 | 2017-12-18 18:50 | 127 | 11kV | 119395 | 1405 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35500 Top Ryde Panel 34 tripped on Signals: 11kV Trip Relays: Basley Relay - 51ABC Inverse timed OC EFI Cause: Lightning appears to have truck OH on pole GL41308 outside 87 Monash Rd. The 11kV insulator is damaged. Section of feeder is between AB2618 to LB444 to PT2356 see OMS 1534545 1534547 1534548 1534549 | December | 2017 | 2018Q2 | 2018 | ZN35500:PA34 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Not Veg | 2017-12-18 | N | 84.9786 | N | 20 | Y | Y | 1.1101 | 39.4971 | 87250.3444
[7 empty] | 7594 | 6231 | 1534249 | 2017-12-18 17:34 | 2017-12-18 19:10 | 96 | 11kV | 6746 | 96 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | At S15013 terrey Hills section of Panel 10 from CP20852 tripped and reclosed on OC and IOC Cause: Lightning - Patrolled Clear. See OMS 1534605 1534608 1534249 | December | 2017 | 2018Q2 | 2018 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2017-12-18 | N | 70.2708 | N | 20 | Y | Y | 1.1101 | 39.4971 | 4929.7778
[7 empty] | 7978 | 10740 | 1534256 | 2017-12-18 18:01 | 2017-12-18 20:13 | 132 | 11kV | 10428 | 79 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Ex Zn14891 Wyong section of Pa5 "Wyong" RE45017 Whiteman tripped and locked out on OC and Earthfault Cause: lightning. Cause not ascertained mains patrolled | December | 2017 | 2018Q2 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2017-12-18 | N | 132 | N | 20 | Y | Y | 1.1101 | 39.4971 | 7620.4748
[7 empty] | 8051 | 11770 | 1534247 | 2017-12-18 18:00 | 2017-12-18 20:19 | 139 | 11kV | 199111 | 1477 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn3425 Castle Cove Pabel 30 tripped, reclosed, Tripped and locked out on Signals: 11kV trip Relays: Fault Checkm EFIm Lockout, Earth Fault, Timing Cause: UG fault in the section of 11kV Feeder from LB77095 to S5680 See OMS 1535182 1535184 1534247 1534288 | December | 2017 | 2018Q2 | 2018 | ZN3425:PA30 | ZN3425:PA30 | ZN03425/000030 | WILLOUGHBY | UG | Not Veg | 2017-12-18 | N | 134.8077 | N | 20 | Y | Y | 1.1101 | 39.4971 | 145504.446
[7 empty] | 8462 | 17176 | 1534254 | 2017-12-18 17:58 | 2017-12-18 20:45 | 167 | 11kV | 118077 | 709 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Zn14891 Wyong Pa12 "Yarramlong" tripped and reclosed on 51AB, EFI, Recloser/timing/lockout, 11kv trip Cause: Lightning. Cause not found patrolled by mains See 1534911,2 ex 1534254 | December | 2017 | 2018Q2 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2017-12-18 | N | 166.5402 | N | 20 | Y | Y | 1.1101 | 39.4971 | 86287.1889
[7 empty] | 7768 | 8287 | 1534259 | 2017-12-18 18:21 | 2017-12-18 21:00 | 159 | 11kV | 477 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174864 A Phase DOLF : 10 Amp Excluded OMS 1534259 | December | 2017 | 2018Q2 | 2018 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2017-12-18 | N | 159 | N | 20 | Y | Y | 1.1101 | 39.4971 | 348.5775
[7 empty] | 7870 | 9580 | 1534253 | 2017-12-18 17:58 | 2017-12-18 21:29 | 211 | 11kV | 422 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Replaced Dolf | December | 2017 | 2018Q2 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2017-12-18 | N | 211 | N | 20 | Y | Y | 1.1101 | 39.4971 | 308.3852
[7 empty] | 7373 | 3441 | 1534918 | 2017-12-18 20:46 | 2017-12-18 23:15 | 149 | 11kV | 10124 | 79 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | Ex Zn14891 Wyong section of Pa5 RE45017 Whiteman tripped and locked out on Overcurrent and Earthfault Cause: Tree Bark on 11kV Mains adjacent LK42504. Bark removed by DOp See 1534918,9 | December | 2017 | 2018Q2 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2017-12-18 | N | 128.1519 | N | 20 | Y | Y | 1.1101 | 39.4971 | 7398.3206
[7 empty] | 8122 | 12839 | 1534300 | 2017-12-18 20:50 | 2017-12-19 00:10 | 200 | 11kV | 200 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174863 A Phase 10 Amp Fuse Substation DOLF Electrical Storm also refer to 1534300 | December | 2017 | 2018Q2 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2017-12-18 | N | 200 | N | 20 | Y | Y | 1.1101 | 39.4971 | 146.1541
[7 empty] | 7626 | 6539 | 1534304 | 2017-12-18 21:13 | 2017-12-19 01:20 | 247.35 | 11kV | 2226.15 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174865 A phase 14 Amp fuse Line DOLF | December | 2017 | 2018Q2 | 2018 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Veg | 2017-12-18 | N | 247.35 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1626.8048
[7 empty] | 8340 | 15358 | 1534328 | 2017-12-19 03:30 | 2017-12-19 09:40 | 370.1833 | 11kV | 4072.0167 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 174877 DOLF Suspect outage from alst nights storm. | December | 2017 | 2018Q2 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | OH | Veg | 2017-12-19 | N | 370.1833 | N | 13 | N | N | 1.1101 | 39.4971 | 2975.7097
[7 empty] | 8277 | 14695 | 1534365 | 2017-12-18 11:20 | 2017-12-19 11:05 | 1425 | 11kV | 4275 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa12 PT12332 YARRAMALONG KIDDMAN 2.3 L/H side 10A HVDO operated Fus Fialure Possible lightning strik See 1534878 ex 1534365 Note: customers also affected by T&R OMS 1534907 and also wider area outage see OMS 1534911 | December | 2017 | 2018Q2 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2017-12-18 | N | 1425 | N | 20 | Y | Y | 1.1101 | 39.4971 | 3124.0439
[7 empty] | 8597 | 18783 | 1534400 | 2017-12-19 08:59 | 2017-12-19 11:55 | 176 | 11kV | 352 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174893 Single phase DOLF : 10 Amp Both DOLF's replaced. Excluded OMS 1534400 | December | 2017 | 2018Q2 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-12-19 | N | 176 | N | 13 | N | N | 1.1101 | 39.4971 | 257.2312
[7 empty] | 7469 | 4980 | 1534335 | 2017-12-19 06:10 | 2017-12-19 12:05 | 355 | 11kV | 5030 | 17 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 174892 3 fault operation Overcurrent Also Lightning arrestors replaced at subs 72702:12.7kV and 70353:12.7kV Excluded OMS 1534335 | December | 2017 | 2018Q2 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2017-12-19 | N | 295.8824 | N | 13 | N | N | 1.1101 | 39.4971 | 3675.7756
[7 empty] | 7763 | 8244 | 1534417 | 2017-12-19 09:43 | 2017-12-19 12:30 | 167 | 11kV | 501 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 174894/02 A & C phase DOLF : 20 Amp - Line fuse for sub 52128 - OMS 1534807 also LID 174894 C Phase DOLF : 16 Amp sub 52185:11kV | December | 2017 | 2018Q2 | 2018 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2017-12-19 | N | 167 | N | 13 | N | N | 1.1101 | 39.4971 | 366.116
[7 empty] | 7546 | 5797 | 1534465 | 2017-12-19 11:40 | 2017-12-19 13:22 | 102 | 11kV | 197572 | 1991 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S10002 Blakehurst Panel No8 opened on No8 opened on Earth Fault, EFI 11kV Trip, Zone Earth, No 1 Group Earth. Cause: 11kV Feeder from S10624 Derwent to S49021 to AB31246 damaged by contractor See OMS 1534811 1534819 1534465 1534469 Name Comment SUIR EXCAVATIONS: ADRIAN RIGUEZ SUIR EXCAVATIONS DUG THROUGH THE U/G CABLE AT CORNER OF KING GEORGES AND SOUTH HURSTVILLE - USING EXCAVATOR | December | 2017 | 2018Q2 | 2018 | ZN10991:PA8 | ZN10991:PA8 | ZN10991/000008 | GEORGES RIVER | UG | Not Veg | 2017-12-19 | N | 99.2325 | N | 13 | N | N | 1.1101 | 39.4971 | 144379.7902
[7 empty] | 7234 | 1019 | 1534498 | 2017-12-19 12:29 | 2017-12-19 14:10 | 101 | 11kV | 101 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174895 Single phase DOLF : 10 Amp Excluded OMS 1534498 | December | 2017 | 2018Q2 | 2018 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2017-12-19 | N | 101 | N | 13 | N | N | 1.1101 | 39.4971 | 73.8078
[7 empty] | 8420 | 16576 | 1534351 | 2017-12-19 07:20 | 2017-12-19 14:20 | 419.7833 | 11kV | 2518.7 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 174903 2 fault operations Overcurrent wire down at pole FD-30148 - repaired - Waddy | December | 2017 | 2018Q2 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2017-12-19 | N | 419.7833 | N | 13 | N | N | 1.1101 | 39.4971 | 1840.5917
[7 empty] | 7900 | 9961 | 1534248 | 2017-12-18 17:33 | 2017-12-19 15:30 | 1317 | 11kV | 37970 | 124 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Ex Zn12630 Peats Ridge section of Pa11 "Somersby" RE46803 Wise Ferry Dogtrap 0.1 tripped and locked out on OC Earth Fault Lightning Blew Multiple HDO+Surge Arrestors. PT12239 Henson Hoipos - Roadside HVDO blown PT18051 Konda Wiseferry 0.9 16A footpath HVDO blown restored See DMA created for Peats Ridge on 18/12/17 See 1534892,4,5,6,7,8,900,1 ex 1534248,57,73,305,25,39,95,97,443,541 | December | 2017 | 2018Q2 | 2018 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2017-12-18 | N | 306.2097 | N | 20 | Y | Y | 1.1101 | 39.4971 | 27747.3561
[7 empty] | 7937 | 10296 | 1534636 | 2017-12-19 15:54 | 2017-12-19 17:35 | 101 | 11kV | 40450 | 728 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zone 3425 Castle Cove the 11KV Panel 34 CB ""Malvern Havlah etc"" tripped on: Signals: 11KV trip, Tx 4 cooling failure, CLC defect, Batt Charger defect, Tx 1 415V No Volts, Tx 2 415V No Volts, Tx 3 415V No Volts, Tx 4 415V No Volts, Tx 1 Group Earth Relays: B phase EF, Fault Check, EFI Field EFI's: S 35780, S 7159, S 6969 Cause: Frontline feeder fault See OMS 1535124 1534636 | December | 2017 | 2018Q2 | 2018 | ZN3425:PA34 | ZN3425:PA34 | ZN03425/000034 | WILLOUGHBY | UG | Not Veg | 2017-12-19 | N | 55.5632 | N | 13 | N | N | 1.1101 | 39.4971 | 29559.6669
[7 empty] | 8412 | 16509 | 1534266 | 2017-12-18 18:33 | 2017-12-19 17:50 | 1397 | 11kV | 5588 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174854 A Phase DOLF : 10 Amp Defective Transformer Excluded OMS 1534266 | December | 2017 | 2018Q2 | 2018 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2017-12-18 | N | 1397 | N | 20 | Y | Y | 1.1101 | 39.4971 | 4083.5456
[7 empty] | 8155 | 13220 | 1534632 | 2017-12-19 16:22 | 2017-12-19 17:54 | 92 | 11kV | 84732 | 921 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 26 tripped, Reclosed, Tripped and Locked out on Signals: 11kV Trip. Relays: A and C phase IOC, A &C Phase IOC, A and B phased Timed, Timing, Lockout and EFI Cause: A tree was foun on the 11kV OH outside 2 Wareemba Ave Thornleigh See OMS 1534649 4534632 1534655 | December | 2017 | 2018Q2 | 2018 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Veg | 2017-12-19 | N | 92 | N | 13 | N | N | 1.1101 | 39.4971 | 61919.6464
[7 empty] | 8251 | 14416 | 1534667 | 2017-12-19 16:45 | 2017-12-19 18:10 | 85 | 11kV | 106367 | 1267 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn14891 Wyong Pa6 fdr has tripped/reclosed/tripped on: Signals: 11kV trip Tx1 Group Earth Relays: Basler 1.2.1, 51N (Earth Fault), EFI, Trip. Frame Leakage Prohibition Relay, Tx1 Earth Fault Check. EFI's: Nil Abnormal: S14857:A Open, AB40096 Closed Cause: Frontline UG Fault from from Zn14891 Wyong Pa6 to S12333:A See 1535055,6 ex 1534667,70 | December | 2017 | 2018Q2 | 2018 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | UG | Not Veg | 2017-12-19 | N | 83.9519 | N | 13 | N | N | 1.1101 | 39.4971 | 77729.8663
[7 empty] | 7403 | 3878 | 1534275 | 2017-12-18 19:04 | 2017-12-19 18:25 | 1401 | 11kV | 5604 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174872 A Phase DOLF : 16 Amp Excluded OMS 1534275 | December | 2017 | 2018Q2 | 2018 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2017-12-18 | N | 1401 | N | 20 | Y | Y | 1.1101 | 39.4971 | 4095.2379
[7 empty] | 8119 | 12797 | 1534662 | 2017-12-19 16:36 | 2017-12-19 21:15 | 279 | 11kV | 21318 | 224 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Ex Zn12600 Lisarow section of Pa2 RE41845 North Erina has tripped reclosed tripped reclosed tripped Relays: OC trip Abnormal: LB44470 Defective & Open, RE40239 is closed Cause: Tree/Branch brought down OH In Talbingo Rd, Holgate. Brought down HV down beyond 11kV USL 41345. Radial to PT11409 PT11410. LK41345 found to be defective & recquired bonding through for restoration of PT11410 & PT11409. This meant re-interrupting 11kV fdr from AB42920 to LB44470 to LB43440 tee PT's13059 & PT11387 were interrupted @ 1950 for this to happen See 1534937,8,9,40,1 ex 1534662,6,94,708,45 | December | 2017 | 2018Q2 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2017-12-19 | N | 95.1696 | N | 13 | N | N | 1.1101 | 39.4971 | 15578.5656
[7 empty] | 7425 | 4120 | 1534756 | 2017-12-19 21:03 | 2017-12-19 23:50 | 167 | 11kV | 668 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 174912 A & C Phase DOLF : 20 Amp Excluded OMS 1534756 | December | 2017 | 2018Q2 | 2018 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2017-12-19 | N | 167 | N | 13 | N | N | 1.1101 | 39.4971 | 488.1547
[7 empty] | 7764 | 8246 | 1534714 | 2017-12-19 18:19 | 2017-12-20 03:25 | 546 | 11kV | 1092 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 174905 Replaced faulty Tx. Customer reports lightning strike to sub during previous storm. Excluded OMS No. 1534714 | December | 2017 | 2018Q2 | 2018 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2017-12-19 | N | 546 | N | 13 | N | N | 1.1101 | 39.4971 | 798.0014
[7 empty] | 7685 | 7181 | 1534786 | 2017-12-20 07:51 | 2017-12-20 08:52 | 61 | 11kV | 108508 | 1968 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Pa10 "Wamberal" fdr tripped to lock out Relays: A pHase IOC, EFI, E/F Check, lockout, timing Fault indication at ELB61730 EFI's: Nil Cause: UGOH on corner Entrance Rd and Venturia failed See 1535932,4 ex 1534786 | December | 2017 | 2018Q2 | 2018 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | Unknown | Unknown | 2017-12-20 | N | 55.1362 | N | 32 | Y | Y | 1.1101 | 39.4971 | 79294.446
[7 empty] | 7444 | 4586 | 1534795 | 2017-12-20 08:12 | 2017-12-20 09:05 | 53.2667 | 11kV | 2237.2 | 42 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 174914 OMS 1534795 Stranded wire 1 span past LF 40617. rEPAIRED UNDER ap. | December | 2017 | 2018Q2 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2017-12-20 | N | 53.2667 | N | 32 | Y | Y | 1.1101 | 39.4971 | 1634.8798
[7 empty] | 8482 | 17389 | 1534791 | 2017-12-20 08:10 | 2017-12-20 09:45 | 95 | 11kV | 1045 | 11 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 174916 Transformer faulty. Replaced under permit. Excluded OMS 1534791 | December | 2017 | 2018Q2 | 2018 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2017-12-20 | N | 95 | N | 32 | Y | Y | 1.1101 | 39.4971 | 763.6552
[7 empty] | 7395 | 3798 | 1534792 | 2017-12-20 08:06 | 2017-12-20 10:10 | 124 | 11kV | 124 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 174917 B Phase DOLF : 16 Amp Fuse Fatigue Excluded OMS 1534792 | December | 2017 | 2018Q2 | 2018 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2017-12-20 | N | 124 | N | 32 | Y | Y | 1.1101 | 39.4971 | 90.6155
[7 empty] | 7208 | 525 | 1534830 | 2017-12-20 09:20 | 2017-12-20 11:10 | 110 | 11kV | 1980 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 174923 B Phase DOLF : 16 Amp Excluded OMS 1534830 | December | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-12-20 | N | 110 | N | 32 | Y | Y | 1.1101 | 39.4971 | 1446.9256
[7 empty] | 7798 | 8714 | 1534933 | 2017-12-20 11:31 | 2017-12-20 13:34 | 123 | 11kV | 2573 | 26 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | At S9534 Kurnell South Panel 18 Opened on B pgase Overcurrent, reclose and Lockout, 11kV UGOH to S9736 short circuit. See 1538796,7,9 ex 1534933,5886,7,933,6,40 Note: Panel 15 @ Cronulla Tripped on Restoration. | December | 2017 | 2018Q2 | 2018 | ZN9534:PA18 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | Unknown | Unknown | 2017-12-20 | N | 98.9615 | N | 32 | Y | Y | 1.1101 | 39.4971 | 1880.2725
[7 empty] | 7542 | 5741 | 1534999 | 2017-12-20 13:39 | 2017-12-20 14:38 | 59 | 11kV | 52533 | 1051 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | LID 174927 A Phase sw 81885 No 1 prot 50TN cable fault between sw 39323 and sw 28239 section isolated TAP LEFT . POWER RESTORED TO ALL OF FDR Excluded oms 1534999 | December | 2017 | 2018Q2 | 2018 | 261:81885 | 261:81885 | ZN00261/081885 | LAKE MACQUARIE | UG | Not Veg | 2017-12-20 | N | 49.9838 | N | 32 | Y | Y | 1.1101 | 39.4971 | 38389.5669
[7 empty] | 8704 | 20127 | 1535007 | 2017-12-20 13:59 | 2017-12-20 15:35 | 95.9667 | 11kV | 575.8 | 6 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174933 A & B Phase DOLF : 20 Amp Replaced Blown Dolf | December | 2017 | 2018Q2 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2017-12-20 | N | 95.9667 | N | 32 | Y | Y | 1.1101 | 39.4971 | 420.7777
[7 empty] | 7814 | 8878 | 1534834 | 2017-12-20 09:23 | 2017-12-20 16:00 | 397 | 11kV | 142802 | 516 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | UGOH | Unplanned | Hot >35C | N | LID 174918 3 phase Overcurrent ugoh blown at pole VP-50208 section isolated for repair Excluded oms 1534834 | December | 2017 | 2018Q2 | 2018 | 243:80080 | 243:80080 | ZN00243/080080 | LAKE MACQUARIE | OH | Not Veg | 2017-12-20 | N | 276.7481 | N | 32 | Y | Y | 1.1101 | 39.4971 | 104355.4897
[7 empty] | 7475 | 5024 | 1535115 | 2017-12-20 16:16 | 2017-12-20 17:07 | 51 | 11kV | 61812 | 1212 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At Zn12690 Berkeley Vale Pa19 Fdr has tripped on: Signals: 11kv trip Relays: 19 Right - Micom Relay B+C phase OC, trip+alarm LED's EFI's Nil Cause: tree branch on OH mains near PT13552 See 1535115 ex 1535122 | December | 2017 | 2018Q2 | 2018 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2017-12-20 | N | 51 | N | 32 | Y | Y | 1.1101 | 39.4971 | 45170.3865
[7 empty] | 7903 | 9964 | 1535496 | 2017-12-20 15:02 | 2017-12-20 17:20 | 138 | 11kV | 138 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174931 C Phase DOLF : 10 Amp Excluded OMS 1535058 | December | 2017 | 2018Q2 | 2018 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2017-12-20 | N | 138 | N | 32 | Y | Y | 1.1101 | 39.4971 | 100.8463
[7 empty] | 7984 | 10823 | 1535097 | 2017-12-20 15:50 | 2017-12-20 17:39 | 109 | 11kV | 79672 | 739 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn10994 Mortdale - Pnl.11 tripped, reclosed and locked out on: A & B Phase IOC Field EFIs: NIL Tree branch (Stringy bark) across two phases near PT10958 See 1535559 1535560 | December | 2017 | 2018Q2 | 2018 | ZN10994:PA11 | ZN10994:PA11 | ZN10994/000011 | GEORGES RIVER | OH | Veg | 2017-12-20 | N | 107.8106 | N | 32 | Y | Y | 1.1101 | 39.4971 | 58221.9477
[7 empty] | 7222 | 772 | 1535194 | 2017-12-20 17:01 | 2017-12-20 17:46 | 45 | 11kV | 3465 | 77 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174937 DOLF : 20 Amp Excluded OMS 1535194 | December | 2017 | 2018Q2 | 2018 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Veg | 2017-12-20 | N | 45 | N | 32 | Y | Y | 1.1101 | 39.4971 | 2532.1198
[7 empty] | 7892 | 9897 | 1535135 | 2017-12-20 15:30 | 2017-12-20 17:50 | 140 | 11kV | 8960 | 64 | HV | Arcing | Equipment Failure | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | N | Ex Zn14143 Somersby section of Pa12 11kV AB44696 went high resistance & was arcing/burning up looks like it started happening around 1530 per DNMS trends after heatwave See 1535948 ex 1535087,256 | December | 2017 | 2018Q2 | 2018 | ZN14143:PA12 | ZN14143:PA12 | ZN14143/000012 | CENTRAL COAST | OH | Not Veg | 2017-12-20 | N | 140 | N | 32 | Y | Y | 1.1101 | 39.4971 | 6547.7037
[7 empty] | 8601 | 18842 | 1535283 | 2017-12-20 17:54 | 2017-12-20 18:30 | 36 | 11kV | 15084 | 419 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174938 Trip & Reclose 3 phase Overcurrent branch on OHM P: GT-92458 Excluded OMS 1535285 ## | December | 2017 | 2018Q2 | 2018 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2017-12-20 | N | 36 | N | 32 | Y | Y | 1.1101 | 39.4971 | 11022.9423
[7 empty] | 8036 | 11498 | 1535217 | 2017-12-20 17:07 | 2017-12-20 18:39 | 92 | 11kV | 121164 | 1317 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | At S36300 Balgowlah North Panel 7 tripped on A B and C phase IOC and EFI Abnormal Switching: SW/B at S16708 Open, S16962 SW/B Closed Cause: Lightning Near Brighton St See OMS 1535513 1535272 1535222 1535217 | December | 2017 | 2018Q2 | 2018 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | OH | Not Veg | 2017-12-20 | N | 92 | N | 32 | Y | Y | 1.1101 | 39.4971 | 88543.0775
[7 empty] | 7437 | 4425 | 1534855 | 2017-12-20 09:51 | 2017-12-20 19:10 | 559 | 11kV | 1676.9667 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Ex Zn14891 Wyong section of Pa12 PT14375 Yarramalong Linga 0.6 11kV roadside 16A HVDO has operated Cause not ascertained. Previous Lightning Storms HOT See 1535939 GIS 1534855 | December | 2017 | 2018Q2 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2017-12-20 | N | 558.9889 | N | 32 | Y | Y | 1.1101 | 39.4971 | 1225.4778
[7 empty] | 8236 | 14267 | 1535247 | 2017-12-20 18:31 | 2017-12-20 19:50 | 79 | 11kV | 6211 | 119 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge section of Pa11 "Somersby" fdr REC has tripped/Reclosed/Tripped & Locked out: RE46803 Wise Ferry Dogtrap 0.1 Relays: OC trip Cause: not ascertained DOp aptrolled, found nothing obvious See 1535959,60,1 ex 1535247 | December | 2017 | 2018Q2 | 2018 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2017-12-20 | N | 52.1933 | N | 32 | Y | Y | 1.1101 | 39.4971 | 4538.8156
[7 empty] | 7988 | 10875 | 1535275 | 2017-12-20 17:48 | 2017-12-20 20:00 | 132 | 11kV | 148691 | 1333 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Wind Storm | N | At Zn847 Hornsby Panel 15 Tripped on Relays: B and Cphase IOC, EFI, E/F Cause: Lightning arrestor @ PT78660 hit by lightning See OMS 1535602/603/605 1535275 1535347 | December | 2017 | 2018Q2 | 2018 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | OH | Not Veg | 2017-12-20 | N | 111.5461 | N | 32 | Y | Y | 1.1101 | 39.4971 | 108658.9972
[7 empty] | 7447 | 4604 | 1535288 | 2017-12-20 18:02 | 2017-12-20 20:00 | 118 | 11kV | 34134 | 433 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Wind Strong | N | LID 174936 3 fault operations B & C phase Overcurrent Suspect txf 13982. Sub interconnected. Txf to be replaced 21/17. Excluded OMS 1535288. | December | 2017 | 2018Q2 | 2018 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Not Veg | 2017-12-20 | N | 78.8314 | N | 32 | Y | Y | 1.1101 | 39.4971 | 24944.1204
[7 empty] | 8645 | 19421 | 1535331 | 2017-12-20 18:53 | 2017-12-20 20:30 | 97 | 11kV | 97 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174954 DOLF : 10 Amp Excluded OMS 1535331 | December | 2017 | 2018Q2 | 2018 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2017-12-20 | N | 97 | N | 32 | Y | Y | 1.1101 | 39.4971 | 70.8847
[7 empty] | 8489 | 17481 | 1535152 | 2017-12-20 16:40 | 2017-12-20 20:45 | 245 | 11kV | 504214 | 3838 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | At Zn35800 Bankstown Panel No.14 'Hoskins Cottam' feeder tripped on Signals: 11kv trip Relays: A + B ph IOC Abnormal: AB.54 closed, LB1789 Open (Fault on Pa1L feeder) Remarks: UGOH fault sort circuit. UGOH to S7287 Shenton Northam Sw/A had burn marks | December | 2017 | 2018Q2 | 2018 | ZN35800:PA14 | ZN35800:PA14 | ZN35800/000014 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2017-12-20 | N | 131.3742 | N | 32 | Y | Y | 1.1101 | 39.4971 | 368464.7194
[7 empty] | 8480 | 17385 | 1535363 | 2017-12-20 19:43 | 2017-12-20 21:25 | 102 | 11kV | 306 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174960 DOLF : 16 Amp Excluded OMS 1535363 | December | 2017 | 2018Q2 | 2018 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Veg | 2017-12-20 | N | 102 | N | 32 | Y | Y | 1.1101 | 39.4971 | 223.6158
[7 empty] | 8214 | 13867 | 1535313 | 2017-12-20 18:21 | 2017-12-20 22:10 | 229 | 11kV | 1145 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 174963 Substation DOLF Excluded OMS 1535313 | December | 2017 | 2018Q2 | 2018 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2017-12-20 | N | 229 | N | 32 | Y | Y | 1.1101 | 39.4971 | 836.7322
[7 empty] | 7786 | 8541 | 1535333 | 2017-12-20 18:55 | 2017-12-20 22:14 | 199.3667 | 11kV | 797.4667 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 174961 B Phase DOLF : 10 Amp replaced line dolf and dolf at sub 51107 | December | 2017 | 2018Q2 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2017-12-20 | N | 199.3667 | N | 32 | Y | Y | 1.1101 | 39.4971 | 582.7651
[7 empty] | 7963 | 10520 | 1535319 | 2017-12-20 18:40 | 2017-12-21 00:30 | 350 | 11kV | 700 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 174967 No protection operations. Sub isolated to repair broken LL lead under A/P. Excluded OMS 1535319. | December | 2017 | 2018Q2 | 2018 | 238:34148 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2017-12-20 | N | 350 | N | 32 | Y | Y | 1.1101 | 39.4971 | 511.5394
[7 empty] | 8007 | 11207 | 1535289 | 2017-12-20 18:00 | 2017-12-21 02:00 | 480 | 11kV | 23714 | 134 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 174972 1 fault operation 3 phase Sensitve Earth Fault 11kV mains down pole JP-85043 repaired under AP Excluded OMS 1535289. | December | 2017 | 2018Q2 | 2018 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2017-12-20 | N | 176.9701 | N | 32 | Y | Y | 1.1101 | 39.4971 | 17329.4918
[7 empty] | 7924 | 10193 | 1535432 | 2017-12-21 01:56 | 2017-12-21 03:00 | 64 | 11kV | 67653 | 1577 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S10999 Kogarah Panel 32 tripped and locked out on Relays: 51ABC, EFI, Lockout, Fault Check. Signals: 11kV trip Cause: Possum found on UGOH below LB 31108 - See OMS 1535878 1535879 1535880 1535432 1535434 1535436 | December | 2017 | 2018Q2 | 2018 | ZN10999:PA32 | ZN10999:PA32 | ZN10999/000032 | BAYSIDE | OH | Not Veg | 2017-12-21 | N | 42.8998 | N | 10 | N | N | 1.1101 | 39.4971 | 49438.817
[7 empty] | 7839 | 9214 | 1535384 | 2017-12-20 23:55 | 2017-12-21 04:45 | 290 | 11kV | 14790 | 51 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 174969 Sub interrupted to replace burning pole & broken crossarm at KT-70839. Emergency switching sheet R0085 Excluded OMS No. 1535384 + 1535424 | December | 2017 | 2018Q2 | 2018 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2017-12-20 | N | 290 | N | 32 | Y | Y | 1.1101 | 39.4971 | 10808.0958
[7 empty] | 8686 | 19870 | 1535445 | 2017-12-21 06:43 | 2017-12-21 08:35 | 112 | 11kV | 336 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174974 Single phase DOLF : 10 Amp Excluded OMS 1535445 | December | 2017 | 2018Q2 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2017-12-21 | N | 112 | N | 10 | N | N | 1.1101 | 39.4971 | 245.5389
[7 empty] | 7457 | 4738 | 1535443 | 2017-12-21 05:58 | 2017-12-21 09:15 | 197 | 11kV | 197 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174975 A Phase DOLF : 10 Amp Excluded OMS 1535443 | December | 2017 | 2018Q2 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2017-12-21 | N | 197 | N | 10 | N | N | 1.1101 | 39.4971 | 143.9618
[7 empty] | 8644 | 19410 | 1535507 | 2017-12-20 05:30 | 2017-12-21 10:00 | 1710 | 11kV | 3420 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174976 B Phase DOLF : 10 Amp Excluded OMS 1535507 | December | 2017 | 2018Q2 | 2018 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Veg | 2017-12-20 | N | 1710 | N | 32 | Y | Y | 1.1101 | 39.4971 | 2499.2351
[7 empty] | 7670 | 7020 | 1535818 | 2017-12-21 11:58 | 2017-12-21 12:02 | 4 | 11kV | 716 | 179 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 174978 sw 42029 tripped while closing dolf for sub 51584 after previous storm. sub isolated and fdr restored | December | 2017 | 2018Q2 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2017-12-21 | N | 4 | N | 10 | N | N | 1.1101 | 39.4971 | 523.2317
[7 empty] | 7959 | 10480 | 1535446 | 2017-12-21 06:47 | 2017-12-21 13:30 | 403 | 11kV | 2015 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 174983 A Phase DOLF : 10 Amp Excluded OMS 1535446 | December | 2017 | 2018Q2 | 2018 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2017-12-21 | N | 403 | N | 10 | N | N | 1.1101 | 39.4971 | 1472.5026
[7 empty] | 8229 | 14117 | 1535201 | 2017-12-20 17:10 | 2017-12-21 13:35 | 1225 | 11kV | 54205 | 79 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At PT1059 31.5A HVDO operated Cause: Tree on distributor 2 O/S62 Eastern Rd. See OMS 1535214 1535201 1535259 1535309 1535332 NOTE: Distrtibutor fuse and HV fuse didnt grade | December | 2017 | 2018Q2 | 2018 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Veg | 2017-12-20 | N | 686.1392 | N | 32 | Y | Y | 1.1101 | 39.4971 | 39611.4152
[7 empty] | 8208 | 13830 | 1535323 | 2017-12-20 19:20 | 2017-12-21 14:25 | 1145 | 11kV | 1145 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174973 B Phase DOLF : 10 Amp Suspect txf to be replaced am 21/12. 3 X LA replaced power restored Excluded OMS 1535346. | December | 2017 | 2018Q2 | 2018 | 512:48046 | 512:83736 | ZN00512/083736 | CESSNOCK | OH | Not Veg | 2017-12-20 | N | 1145 | N | 32 | Y | Y | 1.1101 | 39.4971 | 836.7322
[7 empty] | 7245 | 1166 | 1535625 | 2017-12-21 11:30 | 2017-12-21 14:30 | 180 | 11kV | 1440 | 8 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa12 Section of fdr from LB40905 to LB40899 tee PT11302,11039,12894 Lightning Arrestor failure @ ELB 62447 | December | 2017 | 2018Q2 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2017-12-21 | N | 180 | N | 10 | N | N | 1.1101 | 39.4971 | 1052.3095
[7 empty] | 7957 | 10456 | 1535601 | 2017-12-21 12:20 | 2017-12-21 14:40 | 140 | 11kV | 4060 | 29 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 174986 Repairs on pole JR-25078 wires down Excluded OMS oms 1535601, 1535604. | December | 2017 | 2018Q2 | 2018 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2017-12-21 | N | 140 | N | 10 | N | N | 1.1101 | 39.4971 | 2966.9283
[7 empty] | 8349 | 15509 | 1535314 | 2017-12-20 18:34 | 2017-12-21 15:30 | 1256 | 11kV | 3768 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174989 3 phase sub isolated for tx replacement Excluded oms 1535314 | December | 2017 | 2018Q2 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2017-12-20 | N | 1256 | N | 32 | Y | Y | 1.1101 | 39.4971 | 2753.5433
[7 empty] | 8656 | 19555 | 1535695 | 2017-12-21 15:21 | 2017-12-21 16:40 | 79 | 11kV | 92667 | 1173 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca Pa40 "Davistown" fdr tripped, reclosed, tripped & locked out on Relays: B&C phase O/C, Timer, Lockout, Fault check, UF Signals: 11kv trip Cause: Tree/Branch on OH mains. Near PT12045 removed by DOp | December | 2017 | 2018Q2 | 2018 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Veg | 2017-12-21 | N | 79 | N | 10 | N | N | 1.1101 | 39.4971 | 67718.3104
[7 empty] | 7987 | 10868 | 1535700 | 2017-12-21 15:36 | 2017-12-21 18:17 | 161 | 11kV | 171941 | 1117 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S690 Campsie 11kv No.6 CB "Rod Kingsgrove" tripped on: Relays: A phase timed & IOC, EFI, Fault Check Signals: Group earth, (11kv trip did not flag) Remarks: UG fault. 11kv UG fault between S61328 Wirega Garema Sw/A to S7569 Garema Wirega Sw/B | December | 2017 | 2018Q2 | 2018 | ZN690:PA6 | ZN690:PA6 | ZN00690/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-12-21 | N | 153.9311 | N | 10 | N | N | 1.1101 | 39.4971 | 125649.4114
[7 empty] | 7256 | 1343 | 1535462 | 2017-12-21 15:44 | 2017-12-21 20:58 | 313.9167 | 11kV | 8475.75 | 27 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Outage created by SOp from LB44965. No report provided. Unknown outage CC1: 22-"Refer to SOp" | December | 2017 | 2018Q2 | 2018 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | Unknown | Unknown | 2017-12-21 | N | 313.9167 | N | 10 | N | N | 1.1101 | 39.4971 | 6193.8281
[7 empty] | 8205 | 13813 | 1535792 | 2017-12-22 06:45 | 2017-12-22 08:10 | 85 | 11kV | 510 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 174991 A Phase DOLF : 16 Amp A PHASE 248 VOLTS, 3 AMPS. B PHASE 248 VOLTS , 3 AMPS. C PHASE 247 VOLTS 4 AMPS. Excluded oms # 1535792 | December | 2017 | 2018Q2 | 2018 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2017-12-22 | N | 85 | N | 3 | N | N | 1.1101 | 39.4971 | 372.693
[7 empty] | 7379 | 3567 | 1535840 | 2017-12-22 11:05 | 2017-12-22 11:35 | 30 | 11kV | 60 | 2 | HV | Arcing | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 174993 A Phase links 75072 arcing Excluded OMS 1535840 | December | 2017 | 2018Q2 | 2018 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2017-12-22 | N | 30 | N | 3 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 8666 | 19668 | 1536066 | 2017-12-22 22:50 | 2017-12-23 01:10 | 140 | 11kV | 89263 | 1197 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12580 Erina - Pnl.1 tripped, reclosed, tripped & locked out on: Overcurrent with Earth Fault and EFI Field EFIs: S18318 S18217 S18864 S14272 S18865 S11628 UG cable fault from LB62719 to S19486 (Sw/A) tee PT11929 See 1536811 1536812 1536813 1536814 1536815 1536816 1536818 | December | 2017 | 2018Q2 | 2018 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | UG | Not Veg | 2017-12-22 | N | 74.5723 | N | 3 | N | N | 1.1101 | 39.4971 | 65230.7676
[7 empty] | 8058 | 11906 | 1536121 | 2017-12-23 11:40 | 2017-12-23 13:45 | 125 | 11kV | 3841 | 45 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14143 Somersby - Pnl.21 tripped on: O/C & E/F Field EFIs: S18108 S8849 S4902 S14956 (S18270 did not operate, S18052 No EFI) UG cable fault from S14956 (Sw/A) to AB45422 tee PT14454 See 1536824 1536825 1536826 1536827 | December | 2017 | 2018Q2 | 2018 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | UG | Not Veg | 2017-12-23 | N | 85.3556 | N | 3 | N | N | 1.1101 | 39.4971 | 2806.8895
[7 empty] | 8456 | 17066 | 1536170 | 2017-12-23 18:00 | 2017-12-23 18:10 | 10 | 11kV | 480 | 48 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 175004 Tree on mains Excluded OMS 1536170 | December | 2017 | 2018Q2 | 2018 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2017-12-23 | N | 10 | N | 3 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 7610 | 6404 | 1536204 | 2017-12-23 22:16 | 2017-12-24 00:06 | 110 | 11kV | 131193 | 1243 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn847 Hornsby Pnl.23 tripped, relcosed and locked out on: A & C phase IOC, C Phase timed O/C with EFI Field EFIs: S7795 S6978 UG cable fault from S6978 (Sw/B) to S8630 (Sw/A) to S4254 (Sw/A) See 1536760 1536761 1536762 | December | 2017 | 2018Q2 | 2018 | ZN847:PA23 | ZN847:PA23 | ZN00847/000023 | HORNSBY | UG | Not Veg | 2017-12-23 | N | 105.5455 | N | 3 | N | N | 1.1101 | 39.4971 | 95871.9749
[7 empty] | 8716 | 20305 | 1536213 | 2017-12-24 02:43 | 2017-12-24 06:41 | 238 | 11kV | 11424 | 48 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 175008 C Phase DOLF : 31 Amp Excluded OMS 1536213 | December | 2017 | 2018Q2 | 2018 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2017-12-24 | N | 238 | N | 11 | N | N | 1.1101 | 39.4971 | 8348.3222
[7 empty] | 8647 | 19453 | 1536270 | 2017-12-24 11:49 | 2017-12-24 12:47 | 58 | 11kV | 84970 | 1465 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36800 Waverley Pnl.49 tripped on: Earth Fault with EFI Field EFIs: NIL UG Cable fault in front line section of feeder from Pnl.49 to S7971 (Sw/A) | December | 2017 | 2018Q2 | 2018 | ZN36800:PA49 | ZN36800:PA49 | ZN36800/000049 | WAVERLEY | UG | Not Veg | 2017-12-24 | N | 58 | N | 11 | N | N | 1.1101 | 39.4971 | 62093.5698
[7 empty] | 7483 | 5110 | 1536326 | 2017-12-24 15:13 | 2017-12-24 17:00 | 107 | 11kV | 283969 | 2924 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn35800 Bankstown - Pnl.2 tripped on: IOC with Earth Fault and EFI UG cable fault in front line section of feeder from Pnl.2 to S48790 (Sw/A) to S1230 (Sw/A) to S278 (Sw/A) | December | 2017 | 2018Q2 | 2018 | ZN35800:PA2 | ZN35800:PA2 | ZN35800/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2017-12-24 | N | 97.1166 | N | 11 | N | N | 1.1101 | 39.4971 | 207516.1695
[7 empty] | 7865 | 9457 | 1536306 | 2017-12-24 14:17 | 2017-12-24 18:30 | 253 | 11kV | 25300 | 100 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT10310 Churchill Huchinson - 11kV roadside HDO Operated T/Con to replace HDOs Restored via LV // 2461 & 23573 | December | 2017 | 2018Q2 | 2018 | ZN10999:PA10 | ZN10998:PA17 | ZN10998/000017 | BAYSIDE | OH | Not Veg | 2017-12-24 | N | 253 | N | 11 | N | N | 1.1101 | 39.4971 | 18488.4938
[7 empty] | 7428 | 4160 | 1536355 | 2017-12-24 16:33 | 2017-12-24 18:49 | 136 | 11kV | 53038 | 391 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 175022 2 fault operations 11KV tapping hit by lightning. DO is isolating 11kv and interconnecting LV as per SO Excluded OMS 1536355 | December | 2017 | 2018Q2 | 2018 | 504:48032 | 522:83121 | ZN00522/083121 | CESSNOCK | OH | Not Veg | 2017-12-24 | N | 135.6471 | N | 11 | N | N | 1.1101 | 39.4971 | 38758.606
[7 empty] | 8117 | 12757 | 1537775 | 2017-12-24 16:11 | 2017-12-24 19:00 | 169 | 11kV | 2028 | 12 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 175030 3 phase DOLF : 20 Amp | December | 2017 | 2018Q2 | 2018 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2017-12-24 | N | 169 | N | 11 | N | N | 1.1101 | 39.4971 | 1482.0026
[7 empty] | 8491 | 17488 | 1536382 | 2017-12-24 17:36 | 2017-12-24 19:04 | 88 | 11kV | 107624 | 1223 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 175026 2 fault operations A & B phase Overcurrent | December | 2017 | 2018Q2 | 2018 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | OH | Veg | 2017-12-24 | N | 88 | N | 11 | N | N | 1.1101 | 39.4971 | 78648.4448
[7 empty] | 8503 | 17671 | 1536405 | 2017-12-24 19:01 | 2017-12-24 20:45 | 104 | 11kV | 13520 | 130 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Ex Zn3472 Sefton Pnl.28 - AB435 open circuit roadside phase Bond (PT2446 side) | December | 2017 | 2018Q2 | 2018 | ZN3472:PA28 | ZN1850:PA40 | ZN01850/000040 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2017-12-24 | N | 104 | N | 11 | N | N | 1.1101 | 39.4971 | 9880.0172
[7 empty] | 8255 | 14457 | 1536339 | 2017-12-24 17:21 | 2017-12-24 20:46 | 205 | 11kV | 46485 | 1051 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 175029 2 fault operations B Phase main down Earth fault Removed tree on 11kV OHM pole IR-94004 Excluded OMS 1536339, 1536370, 1536377, 4536386 | December | 2017 | 2018Q2 | 2018 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2017-12-24 | N | 44.2293 | N | 11 | N | N | 1.1101 | 39.4971 | 33969.8669
[7 empty] | 8261 | 14499 | 1536289 | 2017-12-24 13:46 | 2017-12-24 21:15 | 449 | 11kV | 13187 | 53 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC44945 Lower Mangrove tripped Tree branch brought down OH mains near PT12514 See 1536830 1536831 1536832 | December | 2017 | 2018Q2 | 2018 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2017-12-24 | N | 248.8113 | N | 11 | N | N | 1.1101 | 39.4971 | 9636.6706
[7 empty] | 8669 | 19696 | 1536358 | 2017-12-24 16:39 | 2017-12-25 00:15 | 456 | 11kV | 17255 | 134 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 175023 3 fault operations Mains down adjacent sub 63100 Excluded OMS 1536358 & 1536426 | December | 2017 | 2018Q2 | 2018 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2017-12-24 | N | 128.7687 | N | 11 | N | N | 1.1101 | 39.4971 | 12609.4451
[7 empty] | 7787 | 8575 | 1536464 | 2017-12-25 08:35 | 2017-12-25 10:26 | 111 | 11kV | 333 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 175041 Single phase DOLF : 16 Amp excluded OMS 1536464 | December | 2017 | 2018Q2 | 2018 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2017-12-25 | N | 111 | N | 3 | N | N | 1.1101 | 39.4971 | 243.3466
[7 empty] | 8444 | 16856 | 1536452 | 2017-12-25 06:56 | 2017-12-25 10:50 | 234 | 11kV | 468 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 175040 Surge arrestor was damaged and had to be replaced. Customer last night thought he was with Essential not Ausgrid and this caused delays. Ausgrid did not appear to receive the job until 643am this morning. Excluded OMS 1536452. | December | 2017 | 2018Q2 | 2018 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Not Veg | 2017-12-25 | N | 234 | N | 3 | N | N | 1.1101 | 39.4971 | 342.0006
[7 empty] | 8706 | 20134 | 1536478 | 2017-12-25 10:59 | 2017-12-25 12:12 | 73 | 11kV | 6497 | 89 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | PT15836 Macquarie St 58 - 11kV Roadside HV drop out fuse carrier defective. Restored via LV // 19740 34830 20874 | December | 2017 | 2018Q2 | 2018 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Not Veg | 2017-12-25 | N | 73 | N | 3 | N | N | 1.1101 | 39.4971 | 4747.816
[7 empty] | 7304 | 2213 | 1536544 | 2017-12-26 02:59 | 2017-12-26 04:21 | 82 | 11kV | 112984 | 1384 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North - Pnl.19 tripped, reclosed & tripped on: A & C phase IOC and Earth Fault Field EFIS: S16827 S6064 S49927 S16928 UGOH & S16987 Possum found at base of pole at LB49832. Also bond burnt off at UGOH on pole MO38908 (Corner Kitchener & Rickard Sts) See 1536739 1536740 | December | 2017 | 2018Q2 | 2018 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2017-12-26 | N | 81.6358 | N | 10 | N | N | 1.1101 | 39.4971 | 82565.3747
[7 empty] | 7793 | 8670 | 1536586 | 2017-12-26 12:09 | 2017-12-26 14:20 | 130.95 | 11kV | 3142.8 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 175054 A & C DOLF : 10 Amp CC1: 22-"Refer to SOp" | December | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2017-12-26 | N | 130.95 | N | 10 | N | N | 1.1101 | 39.4971 | 2296.6655
[7 empty] | 8476 | 17352 | 1536609 | 2017-12-26 14:02 | 2017-12-26 15:26 | 84 | 11kV | 252 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 175057 A Phase DOLF : 10 Amp Excluded OMS 1536609 | December | 2017 | 2018Q2 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-12-26 | N | 84 | N | 10 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 7866 | 9463 | 1536587 | 2017-12-26 12:44 | 2017-12-26 17:12 | 268 | 11kV | 15276 | 57 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 175056 FDR ISOLATED FOR POLE 4I-40036 REPLACEMENT | December | 2017 | 2018Q2 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2017-12-26 | N | 268 | N | 10 | N | N | 1.1101 | 39.4971 | 11163.2502
[7 empty] | 7470 | 4981 | 1536585 | 2017-12-26 12:02 | 2017-12-26 18:30 | 388 | 11kV | 388 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 175063 A & B phase DOLF : 10 Amp Excluded OMS 1536585 | December | 2017 | 2018Q2 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2017-12-26 | N | 388 | N | 10 | N | N | 1.1101 | 39.4971 | 283.539
[7 empty] | 7832 | 9109 | 1536592 | 2017-12-26 12:23 | 2017-12-26 18:30 | 367 | 11kV | 367 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 175061 DOLF : 10 Amp Excluded OMS 1536592 | December | 2017 | 2018Q2 | 2018 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2017-12-26 | N | 367 | N | 10 | N | N | 1.1101 | 39.4971 | 268.1928
[7 empty] | 8378 | 15944 | 1536623 | 2017-12-26 17:24 | 2017-12-26 19:15 | 111 | 11kV | 10935 | 925 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn1193 Lindfield - Pnl.21 tripped & reclosed on: B & C phase O/C Field EFIs: S49295 Suspect vehicle hit pole on Cnr Pacific Hwy and Shirley See 1536768 1536769 | December | 2017 | 2018Q2 | 2018 | ZN1193:PA15 | ZN1193:PA15 | ZN01193/000015 | KU-RING-GAI | OH | Not Veg | 2017-12-26 | N | 11.8216 | N | 10 | N | N | 1.1101 | 39.4971 | 7990.9755
[7 empty] | 7251 | 1262 | 1536643 | 2017-12-26 19:51 | 2017-12-26 21:15 | 84 | 11kV | 252 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 175069 A Phase DOLF : 10 Amp Excluded OMS 1536643 | December | 2017 | 2018Q2 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2017-12-26 | N | 84 | N | 10 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 7303 | 2197 | 1536599 | 2017-12-26 13:03 | 2017-12-26 22:20 | 557 | 11kV | 557 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 175067 Single phase DOLF : 10 Amp Excluded OMS 1536599 | December | 2017 | 2018Q2 | 2018 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2017-12-26 | N | 557 | N | 10 | N | N | 1.1101 | 39.4971 | 407.0392
[7 empty] | 7481 | 5085 | 1536647 | 2017-12-26 20:07 | 2017-12-26 22:20 | 133 | 11kV | 7847 | 59 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 175068 OMS 1536647, Outage to replace x-arm pole 5M-80039 & Tx 72519. See report 175067/OMS 1538118 | December | 2017 | 2018Q2 | 2018 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2017-12-26 | N | 133 | N | 10 | N | N | 1.1101 | 39.4971 | 5734.3562
[7 empty] | 7326 | 2653 | 1536920 | 2017-12-27 04:41 | 2017-12-27 05:46 | 65 | 11kV | 4576 | 96 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC20852 McCarrs Ck Rd tripped & reclosed on O/C Seconalisaer CP49122 tripped on O/C Bark down on OH mains. Removed by DOp See 1536954 1536955 | December | 2017 | 2018Q2 | 2018 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2017-12-27 | N | 47.6667 | N | 2 | N | N | 1.1101 | 39.4971 | 3344.0058
[7 empty] | 7999 | 11087 | 1533746 | 2017-12-16 14:52 | 2017-12-27 10:45 | 15593 | 11kV | 17186 | 7 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 174773 3 phase DOLF 3 x Blown Dolfs & L/A sub 64461 3 x Blown Line Fuse 75479. Blown Tx 64461 replaced after xmas as only irrigation pump supply - cleared with customer Excluded OMS 1533688 | December | 2017 | 2018Q2 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2017-12-16 | N | 2455.1429 | N | 7 | N | N | 1.1101 | 39.4971 | 12559.0219
[7 empty] | 7756 | 8103 | 1536870 | 2017-12-27 16:00 | 2017-12-27 17:05 | 65 | 11kV | 1210 | 26 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3288 City South 43/44G tripped on: Earth Fault (43G) UG cable fault S6495, S9223 & S6933 received interruptions due to not being city triplex type subs. See 1536950 1536870 1536872 1536873 | December | 2017 | 2018Q2 | 2018 | ZN3288:PA43 44GHJ | ZN3288:PA43 44GHJ | ZN03288/43 44GHJ | SYDNEY | UG | Not Veg | 2017-12-27 | N | 46.5385 | N | 2 | N | N | 1.1101 | 39.4971 | 884.2323
[7 empty] | 7954 | 10418 | 1537017 | 2017-12-28 14:23 | 2017-12-28 16:17 | 114 | 11kV | 83202 | 931 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn3154 St Ives - Pnl.17 tripped , reclosed, tripped and locked out on: A Phase O/C Field EFIs: S4914 S7416 Tree hit mains near PT1402 See 1537133 1537134 | December | 2017 | 2018Q2 | 2018 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Veg | 2017-12-28 | N | 89.3684 | N | 2 | N | N | 1.1101 | 39.4971 | 60801.5676
[7 empty] | 7855 | 9387 | 1537012 | 2017-12-28 14:05 | 2017-12-28 16:57 | 172 | 11kV | 29263 | 320 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 175079 1 fault operation Sensitive Earth Fault Excluded OMS 1537012 & 1537032 | December | 2017 | 2018Q2 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2017-12-28 | N | 91.4469 | N | 2 | N | N | 1.1101 | 39.4971 | 21384.5373
[7 empty] | 7240 | 1092 | 1537105 | 2017-12-29 01:52 | 2017-12-29 03:29 | 97 | 11kV | 17487 | 187 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC50015 Quarry Old Northern - tripped to lock out on: O/C trip Tree branch removed by DOp adjacent LB1013 See 1537128 1537129 | December | 2017 | 2018Q2 | 2018 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2017-12-29 | N | 93.5134 | N | 6 | N | N | 1.1101 | 39.4971 | 12778.9838
[7 empty] | 7688 | 7217 | 1537109 | 2017-12-29 04:26 | 2017-12-29 05:27 | 61 | 11kV | 50264 | 824 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC 48234 South Creek Toronto - tripped to lock out on O/C trip Cause not ascertained | December | 2017 | 2018Q2 | 2018 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Veg | 2017-12-29 | N | 61 | N | 6 | N | N | 1.1101 | 39.4971 | 36731.4487
[7 empty] | 8149 | 13175 | 1537110 | 2017-12-29 04:39 | 2017-12-29 06:37 | 118 | 11kV | 144316 | 1225 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn2400 Berowra Pnl.15 tripped to Lock out on: A phase O/C and E/F Cause not ascertained See 1537130 1537132 | December | 2017 | 2018Q2 | 2018 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Veg | 2017-12-29 | N | 117.809 | N | 6 | N | N | 1.1101 | 39.4971 | 105461.8762
[7 empty] | 8284 | 14769 | 1537144 | 2017-12-29 08:29 | 2017-12-29 09:36 | 67 | 11kV | 81083 | 1225 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn2400 Berowra 11kv fdr pa15 "Kauri Bambil" fdr tripped and locked out on: Relays: Earth Fault, EFI, reclose, lockout EFI's: S4404 Signals: 11kv trip, Zone Earth, Tx2, Group Earth Cause: UGOH fault short circuit 11kV UGOH fault between AB437 and S4860 SwA. Region to extend feeder. Fault can be seen on UGOH pole is on railway corridor See 1537798,9 ex 1537144 | December | 2017 | 2018Q2 | 2018 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | Unknown | Unknown | 2017-12-29 | N | 66.1902 | N | 6 | N | N | 1.1101 | 39.4971 | 59253.0649
[7 empty] | 7360 | 3088 | 1537156 | 2017-12-29 09:03 | 2017-12-29 11:50 | 167 | 11kV | 501 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 175085 B Phase DOLF : 63 Amp Excluded OMS 1537156 | December | 2017 | 2018Q2 | 2018 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2017-12-29 | N | 167 | N | 6 | N | N | 1.1101 | 39.4971 | 366.116
[7 empty] | 8307 | 15046 | 1537249 | 2017-12-29 16:23 | 2017-12-29 17:10 | 47 | 11kV | 235 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Hot >35C | N | LID 175086 Substation DOLF The DOLF had just dropped out, possibly a loose contact, the fuse had not blown. Excluded OMS 1537263. | December | 2017 | 2018Q2 | 2018 | 511:29872 | 511:29872 | ZN00511/029872 | MAITLAND | OH | Not Veg | 2017-12-29 | N | 47 | N | 6 | N | N | 1.1101 | 39.4971 | 171.7311
[7 empty] | 7676 | 7067 | 1537322 | 2017-12-30 04:48 | 2017-12-30 06:51 | 123 | 11kV | 104720 | 1075 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn965 Penneant Hills Pa6 fdr has tripped Signals: 11kv trip Relays: EF, EFI, Timer, Lockout EFI's: As Expected Cause: UG Fault UG Fault between S4181SwB & S2697SwA DOp was having issues with accessing S2697 See 1537842,4,5 ex 1537322 | December | 2017 | 2018Q2 | 2018 | ZN965:PA6 | ZN965:PA6 | ZN00965/000006 | HORNSBY | UG | Not Veg | 2017-12-30 | N | 97.414 | N | 5 | N | N | 1.1101 | 39.4971 | 76526.2873
[7 empty] | 8379 | 15946 | 1537421 | 2017-12-30 16:37 | 2017-12-30 17:40 | 62.9667 | 11kV | 1259.3333 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 175094 A & B phase DOLF : 20 Amp replaced A&B phase LV fuses 20A | December | 2017 | 2018Q2 | 2018 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2017-12-30 | N | 62.9667 | N | 5 | N | N | 1.1101 | 39.4971 | 920.2837
[7 empty] | 7249 | 1244 | 1537373 | 2017-12-30 16:15 | 2017-12-30 19:45 | 210 | 11kV | 3150 | 15 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa11 "Somersby" Feeder between AB41410 and AL46841 isolated for repairs to be carried out Cause: Vehicle Hit Pole See 1537787 ex 1537373 1537418 | December | 2017 | 2018Q2 | 2018 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2017-12-30 | N | 210 | N | 5 | N | N | 1.1101 | 39.4971 | 2301.9271
[7 empty] | 8558 | 18345 | 1537474 | 2017-12-30 22:20 | 2017-12-31 02:00 | 220 | 11kV | 880 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 175100 Single phase DOLF : 10 Amp Excluded OMS 1537474 | December | 2017 | 2018Q2 | 2018 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2017-12-30 | N | 220 | N | 5 | N | N | 1.1101 | 39.4971 | 643.078
[7 empty] | 7551 | 5825 | 1537484 | 2017-12-31 04:12 | 2017-12-31 05:16 | 64 | 11kV | 9600 | 150 | HV | Animal Frog | Animal | FIU Plant | Unplanned | No Weather Impact | N | LID 175101 1 fault operation A & C phase Instantaneous Overcurrent frog on af plant systerm abnormal 2140 closed 43397 open Excluded OMS 1537484 | December | 2017 | 2018Q2 | 2018 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | Exclude | Not Veg | 2017-12-31 | N | 64 | N | 5 | N | N | 1.1101 | 39.4971 | 7015.3968
[7 empty] | 8269 | 14591 | 1537488 | 2017-12-31 05:40 | 2017-12-31 11:20 | 340 | 11kV | 1700 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 175104 C Phase DOLF : 31 Amp C ph L/A cut away Excluded OMS 1537488 + 1537524 + 1537499 | December | 2017 | 2018Q2 | 2018 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Veg | 2017-12-31 | N | 340 | N | 5 | N | N | 1.1101 | 39.4971 | 1242.3099
[7 empty] | 8099 | 12491 | 1537535 | 2017-12-31 12:34 | 2017-12-31 13:30 | 56 | 11kV | 1904 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of Pa12 "Craftsman Ave" PT48816 Wolseley McDonagh centre phase 63A HDO Fuse operated Cause: not ascertained See 1537792 ex 1537535 | December | 2017 | 2018Q2 | 2018 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Veg | 2017-12-31 | N | 56 | N | 5 | N | N | 1.1101 | 39.4971 | 1391.387
[7 empty] | 8199 | 13749 | 1537410 | 2017-12-30 15:52 | 2017-12-31 14:10 | 1338 | 11kV | 180855 | 457 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 175091 3 fault operations B & C phase Overcurrent, Sensitive Earth fault Tree branch on sub 52106, LV OHM down beyond poles IQ-10007 & IQ-42028. Tree on LV OHM beyond LVF 52928. Replaced faulty Tx 50791. Excluded OMS No. 1537410, 1537414, 1537419, 1537416, 1537477, 1537483. | December | 2017 | 2018Q2 | 2018 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2017-12-30 | N | 395.744 | N | 5 | N | N | 1.1101 | 39.4971 | 132163.4997
[7 empty] | 8003 | 11154 | 1537521 | 2017-12-31 10:20 | 2017-12-31 16:10 | 350 | 11kV | 202122 | 1498 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn15012 Killarney - Pnl.6 tripped on Earth Fault with EFI Field EFI S16651 UG cabel fault from S16651 (Sw/B) to S17146 (Sw/A) to S15635 (Sw/A) ME: 1537905 1537907 SE: 1537906 1537911 | December | 2017 | 2018Q2 | 2018 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | UG | Not Veg | 2017-12-31 | N | 134.9279 | N | 5 | N | N | 1.1101 | 39.4971 | 147704.796
[7 empty] | 8531 | 17971 | 1537565 | 2017-12-31 17:17 | 2017-12-31 18:39 | 82 | 11kV | 42158 | 536 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn965 pennant Hills Pa2 "Bishop Boyd" tripped Realys: E/F and EFI Signals: 11kv trip and zone and Tx1 Group Earth EFI S4968 S4965 Cause: UG Fault. 11kv UG fdr fault from S4965 to S4964 See 1537855,6 ex 1537565 | December | 2017 | 2018Q2 | 2018 | ZN965:PA2 | ZN965:PA2 | ZN00965/000002 | HORNSBY | UG | Not Veg | 2017-12-31 | N | 78.653 | N | 5 | N | N | 1.1101 | 39.4971 | 30807.8229
[7 empty] | 8394 | 16235 | 1537599 | 2018-01-01 01:53 | 2018-01-01 02:35 | 42 | 11kV | 5544 | 132 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185107 B & C Phase DOLF : 40 Amp Possum Excluded OMS 1537599 | January | 2018 | 2018Q3 | 2018 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2018-01-01 | N | 42 | N | 5 | N | N | 1.1101 | 39.4971 | 4051.3917
[7 empty] | 7831 | 9097 | 1537604 | 2018-01-01 05:09 | 2018-01-01 06:40 | 91 | 11kV | 11618 | 128 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn901 Surry Hills - pnl.8 tripped on: B phase E/F (Left) Field EFIs: S8825 UG cable fault from S8825 (Sw/B) to S1077 | January | 2018 | 2018Q3 | 2018 | ZN901:PA8 | ZN901:PA8 | ZN00901/000008 | SYDNEY | UG | Not Veg | 2018-01-01 | N | 90.7656 | N | 5 | N | N | 1.1101 | 39.4971 | 8490.0917
[7 empty] | 7188 | 163 | 1537615 | 2018-01-01 08:53 | 2018-01-01 10:45 | 112 | 11kV | 224 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185109 C Phase DOLF : 10 Amp Excluded OMS 1537615 | January | 2018 | 2018Q3 | 2018 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2018-01-01 | N | 112 | N | 5 | N | N | 1.1101 | 39.4971 | 163.6926
[7 empty] | 7415 | 4032 | 1537680 | 2018-01-01 16:17 | 2018-01-01 20:09 | 232 | 11kV | 28145 | 193 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 185112 section isolated to repair mains pole 8N-20021 Martindale Rd Excluded oms 1537680 | January | 2018 | 2018Q3 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2018-01-01 | N | 145.829 | N | 5 | N | N | 1.1101 | 39.4971 | 20567.5359
[7 empty] | 8599 | 18834 | 1537710 | 2018-01-01 19:48 | 2018-01-01 21:00 | 72 | 11kV | 216 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185114 A Phase DOLF : 10 Amp Excluded OMS 1537710 | January | 2018 | 2018Q3 | 2018 | 264:81240 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Veg | 2018-01-01 | N | 72 | N | 5 | N | N | 1.1101 | 39.4971 | 157.8464
[7 empty] | 7589 | 6158 | 1537725 | 2018-01-02 00:37 | 2018-01-02 07:35 | 418 | 11kV | 42916 | 580 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1610 Homebush Bay - Pnl.2 tripped on: C Phase O/C and E/F with EFI Field EFIs: S7057 UG cable fault from S7057 (Sw/B) to S63790 (Sw/A) tee S3281 (N// DC) DOp reports evidence of cable failure in fenced off joint bay in Hill Rd near Verona Dr. See 1538135 1538137 | January | 2018 | 2018Q3 | 2018 | ZN1610:PA2 | ZN1610:PA2 | ZN01610/000002 | PARRAMATTA | UG | Not Veg | 2018-01-02 | N | 73.9931 | N | 3 | N | N | 1.1101 | 39.4971 | 31361.747
[7 empty] | 8365 | 15689 | 1537755 | 2018-01-02 09:06 | 2018-01-02 15:05 | 359 | 11kV | 1969 | 24 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 185120 A & C phase DOLF : 10 Amp Dolfs blown at 70395 due to LA's blown. Line dolf blown on restoration attempt. Excluded OMS 1537755 | January | 2018 | 2018Q3 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2018-01-02 | N | 82.0417 | N | 3 | N | N | 1.1101 | 39.4971 | 1438.8871
[7 empty] | 8183 | 13521 | 1537986 | 2018-01-02 15:09 | 2018-01-02 16:55 | 106 | 11kV | 9540 | 90 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | PT13703 Glen Ryans - 11kV HVDO (50A) footpath phase operated Fuse fatigue. | January | 2018 | 2018Q3 | 2018 | ZN12640:PA10 | ZN12640:PA10 | ZN12640/000010 | CENTRAL COAST | OH | Not Veg | 2018-01-02 | N | 106 | N | 3 | N | N | 1.1101 | 39.4971 | 6971.5506
[7 empty] | 7462 | 4819 | 1538079 | 2018-01-03 07:14 | 2018-01-03 10:40 | 206 | 11kV | 618 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185130 C Phase DOLF : 10 Amp OMS 1538079 and 1538123 for common outage not the subs listed on the OMS reports. Both jobs in Singleton queue as requested. Excluded OMS 1538079, 1538123 | January | 2018 | 2018Q3 | 2018 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2018-01-03 | N | 206 | N | 3 | N | N | 1.1101 | 39.4971 | 451.6162
[7 empty] | 7474 | 5016 | 1538555 | 2018-01-03 17:18 | 2018-01-03 17:23 | 5 | 11kV | 15764 | 3493 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ZN 4545 Meadowbank 11kV Panel 29 " Blaxland Beattie" tripped on: Realys: Sensitive Earth Fault Signals: 11kV Trip EFI's: Nil Abnormals: Closed @ AB.260 Open @ Panel 31 Closed @ S.35129 Open @ Rec.46117 11kV AB.260 has HR contact causing SEF to operate when load was switched onto Panel 29 ME: 1538555 and 1538556 | January | 2018 | 2018Q3 | 2018 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Not Veg | 2018-01-03 | N | 4.513 | N | 3 | N | N | 1.1101 | 39.4971 | 11519.8662
[7 empty] | 8567 | 18428 | 1538315 | 2018-01-04 00:23 | 2018-01-04 07:35 | 432.15 | 11kV | 5617.95 | 13 | HV | Animal Possum | Animal | Fuse | Unplanned | No Weather Impact | N | Ex Panel 4 at Empire Bay At PT.13517 Doyle Scenic 2 x HDO's 31.5 amps Possum on PT CC1: 22-"Refer to SOp" CC2: 22-"Refer to SOp" FRC1: 322-"No Supply at Point of Attachment - Other Services affected - District Operator required" FRC2: 329-"High Voltage Fuse - Requires replacement" | January | 2018 | 2018Q3 | 2018 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Not Veg | 2018-01-04 | N | 432.15 | N | 3 | N | N | 1.1101 | 39.4971 | 4105.4322
[7 empty] | 7556 | 5904 | 1538277 | 2018-01-03 17:20 | 2018-01-04 12:17 | 1137 | 11kV | 20158 | 26 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 185141 A Phase tree fell onto ohm bringing down 2 span at pole GE-50030 Excluded oms 1538277 | January | 2018 | 2018Q3 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2018-01-03 | N | 775.3077 | N | 3 | N | N | 1.1101 | 39.4971 | 14730.8718
[7 empty] | 8421 | 16578 | 1538448 | 2018-01-04 12:24 | 2018-01-04 13:37 | 73 | 11kV | 191056 | 2883 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN398 Dulwich Hill - 11kV Panel 2 "Sub 4320 Cobar Old" feeder tripped Relays: Earth Fault EFI Signals: 11kV trip, Zone Earth, No.1 Group Earth Field EFI's: Sub 4230, Sub 1995 11kV UG faut from Sub 1995 Dunstaffenage to Sub 64654 Charles Canterbury No.1 to Sub 1678 Marcia St to Sub 1807 High Fore See: 1538762, 1538463, 1538765 Withdrawn: 1538448 | January | 2018 | 2018Q3 | 2018 | ZN398:PA2 | ZN398:PA2 | ZN00398/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-01-04 | N | 66.2699 | N | 3 | N | N | 1.1101 | 39.4971 | 139618.0896
[7 empty] | 7390 | 3753 | 1538693 | 2018-01-04 20:43 | 2018-01-05 00:55 | 252.3167 | 11kV | 1513.9 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 185145 A & B phase DOLF : 16 Amp Excluded OMS 1538694/96 | January | 2018 | 2018Q3 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2018-01-04 | N | 252.3167 | N | 3 | N | N | 1.1101 | 39.4971 | 1106.3135
[7 empty] | 8078 | 12175 | 1538708 | 2018-01-05 05:17 | 2018-01-05 06:47 | 90 | 11kV | 38473 | 571 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 185146 1 fault operations A Phase Earth Fault - EFI Excluded OMS 1538708 | January | 2018 | 2018Q3 | 2018 | 523:33507 | 523:33507 | ZN00523/033507 | SINGLETON | UG | Not Veg | 2018-01-05 | N | 67.3783 | N | 3 | N | N | 1.1101 | 39.4971 | 28114.9336
[7 empty] | 7410 | 3952 | 1538754 | 2018-01-05 09:54 | 2018-01-05 10:31 | 37 | 11kV | 24605 | 665 | HV | Excavation 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12650 West Gosford pa14R "Hargraves Holden" tripped on Earth Fault Signals: 11kv trip, EFI EFI's: S65693 Cause: contractor error caused failure. Cran Hit 11kv mains between LB42067 and AB40398 | January | 2018 | 2018Q3 | 2018 | ZN12650:PA14 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | UG | Not Veg | 2018-01-05 | N | 37 | N | 3 | N | N | 1.1101 | 39.4971 | 17980.6083
[7 empty] | 8608 | 18939 | 1538774 | 2018-01-05 11:02 | 2018-01-05 14:45 | 223 | 11kV | 223 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185154 Single Phase DOLF : 10 Amp Excluded OMS 1538774 | January | 2018 | 2018Q3 | 2018 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2018-01-05 | N | 223 | N | 3 | N | N | 1.1101 | 39.4971 | 162.9618
[7 empty] | 7933 | 10238 | 1538957 | 2018-01-06 16:37 | 2018-01-06 18:00 | 83 | 11kV | 140014 | 1974 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15004 Newport - 11kv Panel 9 "Avalon feeder" tripped on: Relays: B & C phase IOC (50TBC) Signals: 11kv trip Remarks: Animals/birds. Magpie flew into 11kv adj PT16016 Howell Cl | January | 2018 | 2018Q3 | 2018 | ZN15004:PA9 | ZN15004:PA9 | ZN15004/000009 | NORTHERN BEACHES | OH | Not Veg | 2018-01-06 | N | 70.9291 | N | 4 | N | N | 1.1101 | 39.4971 | 102318.1015
[7 empty] | 7318 | 2530 | 1538997 | 2018-01-06 19:26 | 2018-01-06 22:09 | 162.3833 | 11kV | 2273.3667 | 14 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Hot >35C | N | LID 185160 B Phase DOLF : 10 Amp replaced dolf and carrier CC1: 22-"Refer to SOp" | January | 2018 | 2018Q3 | 2018 | 526:34641 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Not Veg | 2018-01-06 | N | 162.3833 | N | 4 | N | N | 1.1101 | 39.4971 | 1661.3093
[7 empty] | 8345 | 15433 | 1539001 | 2018-01-06 20:45 | 2018-01-06 22:20 | 95 | 11kV | 89205 | 939 | HV | Staff Operation | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kv fdr (Ex Panel 5 New Port) from S16222 Hudson Hansford Sw/B t o S16234 Lower Plateau Bilwara Sw/B to S16224 Hudson Delecta Sw/A Abnormal: Closed at S16252 Bilwara Bilambee Sw/A, open at S16234 Lower Plateau Bilwara Sw/B, Closed at S15978 Hudson hilltop Sw/B, Open at S16224 Hudson delecta Sw/A Remarks: interrupted for safety reasons. To repair burnt off neutral at PT15630 Hudson Georgia Lee Dist #2 (see separate interruption report) PT is a "Q" type which required isolation of 11kv feeder to repair. Isolation was extended down to S16234 due to current ban on operating live hazermeyer switches | January | 2018 | 2018Q3 | 2018 | ZN15004:PA5 | ZN15004:PA5 | ZN15004/000005 | NORTHERN BEACHES | OH | Not Veg | 2018-01-06 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 65188.3829
[7 empty] | 7224 | 807 | 1539021 | 2018-01-06 23:42 | 2018-01-07 00:51 | 69 | 11kV | 77226 | 1187 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | @S3922 Drummoyne Zn Panel #10 labelled Edenholme Warreemba tripped on Earth fault, fault check / EFI Remarks: UG fault. Section of 11kv feeder from S3790 Myaldra Lea Sw/B t o S2258 Potter St Sw/A to S366 Barnstaple Rd Sw/A UG fault | January | 2018 | 2018Q3 | 2018 | ZN3922:PA10 | ZN3922:PA10 | ZN03922/000010 | CANADA BAY | UG | Not Veg | 2018-01-06 | N | 65.0598 | N | 4 | N | N | 1.1101 | 39.4971 | 56434.483
[7 empty] | 8005 | 11184 | 1539028 | 2018-01-07 00:41 | 2018-01-07 01:36 | 55 | 11kV | 112530 | 2046 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn12640 umina Panel 13 "umina Aux" tripped reclosed tripped and locked out on IOC B & C phase reclose/timing/lockout 11kv trip Cause: animals/birds See 1539028 ex 1539029 | January | 2018 | 2018Q3 | 2018 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2018-01-07 | N | 55 | N | 24 | Y | Y | 1.1101 | 39.4971 | 82233.6049
[7 empty] | 8375 | 15858 | 1539071 | 2018-01-07 12:18 | 2018-01-07 13:26 | 68 | 11kV | 98213 | 1777 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmahven Paenl 19 "The Lake haven Wyong Leagues" fdr tripped reclosed and locke dout on Cause: UGOH fault short circuit between S14809 to S14816 to LB63042 to AB41422 (UGOH to S14816). Switch Tag at S14816 See 1540384,6,7,8,9 ex 1539071 | January | 2018 | 2018Q3 | 2018 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | UG | Not Veg | 2018-01-07 | N | 55.269 | N | 24 | Y | Y | 1.1101 | 39.4971 | 71771.1636
[7 empty] | 7754 | 8081 | 1539080 | 2018-01-07 12:34 | 2018-01-07 15:25 | 171 | 11kV | 119478 | 825 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Ex Zn12620 Noraville section of Pa11 RE45054 Noraville has tripped Relays: IOC trip and LO Cause: UGOH Fault Short Circuit on tee to S14394. Located between between LB40970 and LB43092 on Panel 11 See 1540393,5,6 ex 1539080 | January | 2018 | 2018Q3 | 2018 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | Unknown | Unknown | 2018-01-07 | N | 144.8218 | N | 24 | Y | Y | 1.1101 | 39.4971 | 87310.9984
[7 empty] | 7813 | 8869 | 1539107 | 2018-01-07 13:28 | 2018-01-07 15:50 | 142 | 11kV | 91015 | 830 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn10997 Sans Souci - Pnl.5 tripped, reclosed and locked out on: B phase IOC Field EFIs: S10996 S0237 S10083 S10940 UGOH fault short circuit on UGOH below S10940. See 1539589 1539590 GIS: 1539110 | January | 2018 | 2018Q3 | 2018 | ZN10997:PA5 | ZN10997:PA5 | ZN10997/000005 | BAYSIDE | Unknown | Unknown | 2018-01-07 | N | 109.6566 | N | 24 | Y | Y | 1.1101 | 39.4971 | 66511.0775
[7 empty] | 8126 | 12940 | 1539727 | 2018-01-07 14:04 | 2018-01-07 16:18 | 134 | 11kV | 210390 | 1824 | HV | Fire (Non Ausgrid) | UNKNOWN | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12650 West Gosford 11kv Pa13 "Narara" tripped and lockout Relays: ABC phase IOC, Reclose and timing, Fault Check, EFI, TX2 B Protection EF/Check EFI: Cnr racecourse rd, S14116 Cause: Bushfire reported adj AB44565, 110 Manns Rd near Maliwa. Bond burnt off foorpath phase at AB44565 See 1539727,8,9 | January | 2018 | 2018Q3 | 2018 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2018-01-07 | N | 115.3454 | N | 24 | Y | Y | 1.1101 | 39.4971 | 153746.8065
[7 empty] | 8035 | 11494 | 1539143 | 2018-01-07 14:56 | 2018-01-07 16:29 | 93 | 11kV | 55505 | 645 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn12660 Woy WOy Pa13 tripped to lockout Relays: OC, EF, EFI, Rec and Lockout EFI's: S18544 S12776 S14706 S48917 S12563 Cause: UG Fault section of 11kv fdr from S12563:B to S12618:A is defective See 1540428,31 ex 1539143,52,96,225 | January | 2018 | 2018Q3 | 2018 | ZN12660:PA13 | ZN12660:PA13 | ZN12660/000013 | CENTRAL COAST | UG | Not Veg | 2018-01-07 | N | 86.0543 | N | 24 | Y | Y | 1.1101 | 39.4971 | 40561.4169
[7 empty] | 8438 | 16801 | 1539165 | 2018-01-07 16:00 | 2018-01-07 16:48 | 48 | 11kV | 16742 | 507 | HV | Overload Operational | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | Zn35370 Galston - Pnl.10L tripped on: C phase O/C Abnormal: S6680 (Sw/B) closed with S5928 (Sw/B) open - S6203 (Sw/B) closed with S5927 (Sw/A) open - Abnormals restored via Pnl.38 outage restoration. While trying to do emergency load relief on Pnl.10L (high load due to Pnl.38 restoration), S8401 (Sw/A) was closed tying Pnl.10 and Pennant Hills P4 together. Before the next switch could be opened, both feeders tripped. See Pennant Hills Pnl.4 outage. See 1539641 1539642 1539643 | January | 2018 | 2018Q3 | 2018 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | Unknown | Not Veg | 2018-01-07 | N | 33.0217 | N | 24 | Y | Y | 1.1101 | 39.4971 | 12234.5598
[7 empty] | 8640 | 19391 | 1539199 | 2018-01-07 16:32 | 2018-01-07 16:50 | 18 | 11kV | 51134 | 3495 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | At Zn35800 bankstown 11kv feeder Panel No:15 "AB 748" feeder tripped and reclosed onL Relays: C phase timed O/C, lockout, timing Abnormal: DMA AB 2576 Open, closed AB2110 Remarks:High loads due to excessive heat, DNMS reading B phase @ 385 amps, protection relay locally reading 409, 385, 450 amps C phase O/L cause of failure. See seperate interruption @ 15:19 hrs | January | 2018 | 2018Q3 | 2018 | ZN35800:PA15 | ZN2310:PA23 | ZN02310/000023 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2018-01-07 | N | 14.6306 | N | 24 | Y | Y | 1.1101 | 39.4971 | 37367.219
[7 empty] | 7929 | 10205 | 1539125 | 2018-01-07 14:09 | 2018-01-07 16:56 | 167 | 11kV | 180463 | 1205 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn965 Pennant Hills - Pnl.38 tripped on: A & B phase O/C Field EFIs: S5613 S929 S6109 Abnormal: S5942 (Sw/B) closed with S63055 (Sw/A) open UG cable fault from S6109 (Sw/B) to S5927 (Sw/A) See 1539618 1539619 | January | 2018 | 2018Q3 | 2018 | ZN965:PA38 | ZN965:PA38 | ZN00965/000038 | HORNSBY | UG | Not Veg | 2018-01-07 | N | 149.7618 | N | 24 | Y | Y | 1.1101 | 39.4971 | 131877.0376
[7 empty] | 7696 | 7310 | 1539160 | 2018-01-07 15:12 | 2018-01-07 17:09 | 117 | 11kV | 6843 | 356 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | LID 185162 1 fault operation Damaged UGOH Conductor pulled away at pole JV-10615 Excluded 1539160 | January | 2018 | 2018Q3 | 2018 | 221:11898 | 221:11898 | ZN00221/011898 | LAKE MACQUARIE | Unknown | Unknown | 2018-01-07 | N | 19.2219 | N | 24 | Y | Y | 1.1101 | 39.4971 | 5000.6626
[7 empty] | 7598 | 6287 | 1539181 | 2018-01-07 16:00 | 2018-01-07 17:31 | 91 | 11kV | 42196 | 1108 | HV | Overload Operational | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | Zn965 Pennant Hills - pnl.4 tripped on: C phase O/C Abnormal: S8401 (Sw/A) closed - Pn.4 and Galston Pnl10L tied. While trying to do emergency load relief on Pnl.10L Galston (high load due to Pnl.38 restoration), S8401 (Sw/A) was closed tying Pnl.10 and Pennant Hills P4 together. Before the next switch could be opened, both feeders tripped. See Galston Pnl.10L outage. See 1539658 1539660 | January | 2018 | 2018Q3 | 2018 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | Unknown | Not Veg | 2018-01-07 | N | 38.083 | N | 24 | Y | Y | 1.1101 | 39.4971 | 30835.5922
[7 empty] | 7489 | 5185 | 1539221 | 2018-01-07 16:50 | 2018-01-07 17:31 | 41 | 11kV | 13625 | 515 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | Ex Pnl.46 Pennant Hills - section of 11kV feeder from 6385 (Sw/A) interrupted for safety Due to Haz operating restriction, section of feeder needed to be de-energised to safely insert caps at S6280 & S7291 to allow restoration of P38 feeder fault. See 1539624 1539625 | January | 2018 | 2018Q3 | 2018 | ZN965:PA46 | ZN965:PA46 | ZN00965/000046 | HORNSBY | Unknown | Unknown | 2018-01-07 | N | 26.4563 | N | 24 | Y | Y | 1.1101 | 39.4971 | 9956.7481
[7 empty] | 7343 | 2833 | 1539161 | 2018-01-07 15:47 | 2018-01-07 18:30 | 163 | 11kV | 50367 | 309 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | CP428 Bayfield Rd (Ex Panel 4L Galston) tripped on: Relays: B & C phase OC Signals: 11kv trip Remarks: tree/branch on OH mains | January | 2018 | 2018Q3 | 2018 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2018-01-07 | N | 163 | N | 24 | Y | Y | 1.1101 | 39.4971 | 36806.718
[7 empty] | 8184 | 13522 | 1539216 | 2018-01-07 16:40 | 2018-01-07 19:10 | 150 | 11kV | 155364 | 1582 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Hot >35C | N | At Zn Hunter Hills Panel 57 "S48279" feeder has tripped Signals: 11kv trip Relays: B feeder side IOC, EFI, Trip - B phase to netural Remarks: end box fault. Sw/A endbox @ S5585 Best Brdige has failed explosively | January | 2018 | 2018Q3 | 2018 | ZN129:PA57 | ZN129:PA57 | ZN00129/000057 | LANE COVE | UG | Not Veg | 2018-01-07 | N | 98.2073 | N | 24 | Y | Y | 1.1101 | 39.4971 | 113535.4287
[7 empty] | 8230 | 14131 | 1539082 | 2018-01-07 12:39 | 2018-01-07 19:20 | 401 | 11kV | 516992 | 1968 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn12610 Long Jetty Pa10 "Wamberal" fdr tripped reclosed and locke dout on: Relays: AB&C phase OC, EF, EFI, Lockout and timing EFI's: S14246 S18381 S14467 S4241 S14122 S8080 Cause: UGOH fault short circuit at section of 11kV from S18080:B to AB44355 tee PT14216 is defective See 1540411,7,8,9,22 ex 1539082 | January | 2018 | 2018Q3 | 2018 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | Unknown | Unknown | 2018-01-07 | N | 262.6992 | N | 24 | Y | Y | 1.1101 | 39.4971 | 377802.5049
[7 empty] | 8494 | 17540 | 1539233 | 2018-01-07 17:02 | 2018-01-07 19:20 | 138 | 11kV | 201286 | 1703 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn14892 Charmhaven Pa6 "Doyalson" fdr tripped to lockout Relays: B7C phase OC, EF, EFI, Fault Check, Rec & Lokcout EFI" S14980 S104987 Cause: UG Fault section of 11kv fdr from S14987:B to S18059 tee PT12051 is defective See 1539718,20,1,2 ex 1539233 | January | 2018 | 2018Q3 | 2018 | ZN14892:PA6 | ZN14892:PA6 | ZN14892/000006 | CENTRAL COAST | UG | Not Veg | 2018-01-07 | N | 118.195 | N | 24 | Y | Y | 1.1101 | 39.4971 | 147093.8719
[7 empty] | 7582 | 6115 | 1539242 | 2018-01-07 19:04 | 2018-01-07 20:10 | 66 | 11kV | 88902 | 1347 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn2635 Epping - Pnl.52 tripped, reclosed & locked out on: A & C Phase O/C Tree branch on mains near PT1386 Pinner Close | January | 2018 | 2018Q3 | 2018 | ZN2635:PA52 | ZN2635:PA52 | ZN02635/000052 | HORNSBY | OH | Veg | 2018-01-07 | N | 66 | N | 24 | Y | Y | 1.1101 | 39.4971 | 64966.9594
[7 empty] | 8053 | 11804 | 1539293 | 2018-01-07 18:09 | 2018-01-07 21:15 | 186 | 11kV | 19958 | 226 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 185164 B Phase HV Cartridge fuse : 31 Amp interrupt additonal sub 24666 to replace hezemeyer sub fuse at sub 24280 deenergised. Dop's safety concerns. Excluded OMS 1539293 & 1539372 | January | 2018 | 2018Q3 | 2018 | 240:34846 | 240:34846 | ZN00240/034846 | NEWCASTLE | OH | Veg | 2018-01-07 | N | 88.3097 | N | 24 | Y | Y | 1.1101 | 39.4971 | 14584.7177
[7 empty] | 8295 | 14932 | 1539121 | 2018-01-07 19:32 | 2018-01-07 21:35 | 123 | 11kV | 198836 | 1632 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa13 RE62730 Manns Narara Creek tripped on: OC, SEF RE62731 Narara Creek Manns tripped on: OC, SEF Abnormal: AB44565 open, LB62728 closed Cause: OH Down between S63690 Strand Lunderston SwA to AB44565. HV mains on the ground. Both Reclosers tripped on SEL down stream of fault See 1539647,9,50 ex 1539121,231,324,7,35 | January | 2018 | 2018Q3 | 2018 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2018-01-07 | N | 121.8358 | N | 24 | Y | Y | 1.1101 | 39.4971 | 145303.4841
[7 empty] | 8030 | 11439 | 1539248 | 2018-01-07 17:14 | 2018-01-08 00:30 | 436 | 11kV | 648364 | 2024 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Cold <10C | N | At Zn35800 Bankstown 11kv feeder Panel No.16 "Canterbury Fair" feeder tripped on: Relays: E/F, E/F check, EFI Abnormal: LB2576 Open and defective, opened LB2992, closed LB3070 switching to enable LB2576 to be by passed closed sw/b @ S6512, opened sw/a @ S47192 Remarks: 11kv endbox failure on Sw/B @ S5946 Arkley Stacey, section of 11kv feeder from S5946 Arkley Stacey (Sw/B) to S6417 Seddon Street West (Sw/A) tee S35925 Boxley Crescent Note: delay restoring due DMA's and load required to have DMA LB2576 Bypassed closed to enable restoration. | January | 2018 | 2018Q3 | 2018 | ZN35800:PA16 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-01-07 | N | 320.3379 | N | 24 | Y | Y | 1.1101 | 39.4971 | 473805.2877
[7 empty] | 7692 | 7252 | 1539235 | 2018-01-07 17:05 | 2018-01-08 00:45 | 460 | 11kV | 322510 | 1308 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn80 Chatswood - pNl.31 tripped on: SEL UGOH fault on pole GL-37173. See 1540449 150450 1540541 1540452 | January | 2018 | 2018Q3 | 2018 | ZN80:PA32 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | Unknown | Unknown | 2018-01-07 | N | 246.5673 | N | 24 | Y | Y | 1.1101 | 39.4971 | 235680.7956
[7 empty] | 7848 | 9330 | 1539626 | 2018-01-08 01:40 | 2018-01-08 02:12 | 32 | 11kV | 7232 | 226 | HV | Staff Operation | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | Dop deenergized 11kv feeder from S3901 Beresford Duke Sw/B to S4896 Heyde Oxford Sw/A to S440 Rochester St Sw/B (via S4100 Beresford Coventry and S2011 Merley Rd) Remarks: inerrupted for safety reasons. Feeder interrupted due to operating restrictions on changing fuses in oil filled switches and live operation of hazemeyer switches. See seperate interruption report for restoration of S4100 | January | 2018 | 2018Q3 | 2018 | ZN2835:PA41 | ZN2835:PA41 | ZN02835/000041 | STRATHFIELD | OH | Not Veg | 2018-01-08 | N | 32 | N | 4 | N | N | 1.1101 | 39.4971 | 5284.9323
[7 empty] | 7435 | 4329 | 1539397 | 2018-01-08 01:43 | 2018-01-08 03:10 | 87 | 11kV | 6699 | 77 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | Y | PT48161 Darton Grand - HDO failed explosively. Suspect transformer failure | January | 2018 | 2018Q3 | 2018 | ZN10999:PA15 | ZN10999:PA15 | ZN10999/000015 | BAYSIDE | OH | Not Veg | 2018-01-08 | N | 87 | N | 4 | N | N | 1.1101 | 39.4971 | 4895.4316
[7 empty] | 7306 | 2268 | 1539342 | 2018-01-07 19:53 | 2018-01-08 08:10 | 737 | 11kV | 5791 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | CP.1835 - All 3 11kV HDOs operated Tree brought down 4 bays of HV and snapped pole in Plassy Rd. See 1540458 1540459 | January | 2018 | 2018Q3 | 2018 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Veg | 2018-01-07 | N | 723.875 | N | 24 | Y | Y | 1.1101 | 39.4971 | 4231.892
[7 empty] | 8180 | 13481 | 1539418 | 2018-01-08 07:52 | 2018-01-08 08:25 | 33 | 11kV | 66 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Hot >35C | Y | LID 185170 Single Phase Dolf : 10 Amp Excluded OMS 1539418 | January | 2018 | 2018Q3 | 2018 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2018-01-08 | N | 33 | N | 4 | N | N | 1.1101 | 39.4971 | 48.2309
[7 empty] | 7570 | 6032 | 1539402 | 2018-01-08 04:27 | 2018-01-08 10:00 | 333 | 11kV | 333 | 1 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | No Weather Impact | Y | Ex Zn12570 Aovca section of Pa33 At PT18004 Dajani Little Valley 16Amp HDO fuse was found by DOp as having operated DOp found tree branch had shorted across the TX LV bushings See 1540932 ex 1539402 | January | 2018 | 2018Q3 | 2018 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2018-01-08 | Y | 333 | N | 4 | N | Y | 1.1101 | 39.4971 | 243.3466
[7 empty] | 8678 | 19783 | 1539408 | 2018-01-08 06:24 | 2018-01-08 10:20 | 236 | 11kV | 130294 | 866 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | @Zn 9252 Jannali - 11kv Panel No.25 'Woronora' feeder tripped, reclosed and locked out Relays: A + C phase timed O/C, Earth fault, Lockout relay, EFI Signals: 11kv trip Remarks: UG fault. 11kv UG fault from S9987 Warrangarree Wylah to S9985 Spoonbill Harrier tee S9990 Jabiru Warrangarree | January | 2018 | 2018Q3 | 2018 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | UG | Not Veg | 2018-01-08 | Y | 150.455 | N | 4 | N | Y | 1.1101 | 39.4971 | 95215.0122
[7 empty] | 7837 | 9205 | 1539393 | 2018-01-08 00:55 | 2018-01-08 11:20 | 625 | 11kV | 625 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | Y | S4332 PMG Pennant Hills - Tx No.2 found tripped. 11kV fuse operated Possiblt Tx failure. LV //'s were in place maintaining supply. LV//'s were not sufficient for load causing Telstra system to change over to Generators. Voltage was 220V with no load on Dist. | January | 2018 | 2018Q3 | 2018 | ZN965:PA47 | ZN965:PA47 | ZN00965/000047 | HORNSBY | UG | Not Veg | 2018-01-08 | Y | 625 | N | 4 | N | Y | 1.1101 | 39.4971 | 456.7316
[7 empty] | 7587 | 6154 | 1539389 | 2018-01-07 23:52 | 2018-01-08 12:15 | 743 | 11kV | 84915 | 380 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa2 "Manns Rd" RE50247 Blackett Faunce tripped Suspected UG Fault in section of 11kV fdr between RE50247 & S14933 tee to S14136 See 1540927,8,9 ex 1539389,409 | January | 2018 | 2018Q3 | 2018 | ZN12650:PA2 | ZN12650:PA2 | ZN12650/000002 | CENTRAL COAST | UG | Not Veg | 2018-01-07 | N | 223.4605 | N | 24 | Y | Y | 1.1101 | 39.4971 | 62053.3774
[7 empty] | 7911 | 10015 | 1539562 | 2018-01-08 13:21 | 2018-01-08 15:20 | 119 | 11kV | 149604 | 1274 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | Zn12650 West Gosford Pa6 "SCC Racecourse" tripped and locked out on: Signals: 11kv trip Relays: EF, EFI Lockout and timing Cause: UG fault at section of pa6 to S11794 Sw A is defective See 1540944,5,6 ex 1539562 | January | 2018 | 2018Q3 | 2018 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | UG | Not Veg | 2018-01-08 | Y | 117.4286 | N | 4 | N | Y | 1.1101 | 39.4971 | 109326.1906
[7 empty] | 7851 | 9343 | 1540950 | 2018-01-08 15:30 | 2018-01-08 15:35 | 5 | 11kV | 2745 | 549 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Hot >35C | Y | Ex Zn12630 Peats Ridge section of Pa8 "Kulnura" IR63734 Goerge Downes Blood 2.45 tripped on overcurrent. Abnormal" LB40899 closed, LB46264 open Cause: overload. Higher than expeced feeder loads caused O/C trip | January | 2018 | 2018Q3 | 2018 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | Unknown | Not Veg | 2018-01-08 | Y | 5 | N | 4 | N | Y | 1.1101 | 39.4971 | 2005.965
[7 empty] | 8546 | 18164 | 1539573 | 2018-01-08 13:38 | 2018-01-08 17:00 | 202 | 11kV | 202 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | Y | LID 185179 Single phase DOLF : 10 Amp Excluded OMS 1539573 | January | 2018 | 2018Q3 | 2018 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2018-01-08 | N | 202 | N | 4 | N | N | 1.1101 | 39.4971 | 147.6156
[7 empty] | 8043 | 11633 | 1539848 | 2018-01-08 17:58 | 2018-01-08 18:59 | 61 | 11kV | 2135 | 35 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Lightning | Y | At S9037 Miranda 11kv 'Manchester Rd' feeder panel No.17 tripped on - Relays: timed O/C "A" phase, efi Signals: 11kv, No.3 Tx Group E Remarks: dop patrolled OH, no obvious cause | January | 2018 | 2018Q3 | 2018 | ZN9037:PA17 | ZN9037:PA17 | ZN09037/000017 | SUTHERLAND | OH | Veg | 2018-01-08 | Y | 61 | N | 4 | N | Y | 1.1101 | 39.4971 | 1560.195
[7 empty] | 7521 | 5580 | 1539846 | 2018-01-08 17:58 | 2018-01-08 19:11 | 73 | 11kV | 48253 | 661 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | At S9037 Miranda 11kv 'Bates Drive' feeder panel No 7 tripped on: Relays: IOC 'A' phase, IOC "C" phase, EFI, sealing contactor Signals: 11kv trip, Zone E, Tx No.1 group E Remarks: Lightning. Dop patrolled feeder, no obvious caused found | January | 2018 | 2018Q3 | 2018 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Not Veg | 2018-01-08 | Y | 73 | N | 4 | N | Y | 1.1101 | 39.4971 | 35261.8692
[7 empty] | 7203 | 478 | 1540473 | 2018-01-08 19:30 | 2018-01-08 19:40 | 10 | 11kV | 540 | 54 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 185232 open by field staff. | January | 2018 | 2018Q3 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-01-08 | Y | 10 | N | 4 | N | Y | 1.1101 | 39.4971 | 394.6161
[7 empty] | 7445 | 4590 | 1539870 | 2018-01-08 18:18 | 2018-01-08 19:45 | 87 | 11kV | 348 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 185193 A Phase DOLF : 10 Amp blown DOLF Excluded OMS 1539870 | January | 2018 | 2018Q3 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-01-08 | Y | 87 | N | 4 | N | Y | 1.1101 | 39.4971 | 254.3081
[7 empty] | 7264 | 1543 | 1539890 | 2018-01-08 18:48 | 2018-01-08 20:56 | 127.5167 | 11kV | 91174.4167 | 715 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 185229 | January | 2018 | 2018Q3 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2018-01-08 | Y | 127.5167 | N | 4 | N | Y | 1.1101 | 39.4971 | 66627.5745
[7 empty] | 7212 | 565 | 1539909 | 2018-01-08 19:14 | 2018-01-08 21:23 | 129 | 11kV | 387 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 185226 B Phase DOLF : 10 Amp Excluded OMS 1539909 | January | 2018 | 2018Q3 | 2018 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2018-01-08 | Y | 129 | N | 4 | N | Y | 1.1101 | 39.4971 | 282.8082
[7 empty] | 8260 | 14492 | 1539860 | 2018-01-08 18:09 | 2018-01-08 21:28 | 199 | 11kV | 53308 | 276 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 185195 2 fault operations A & C Phase Overcurrent | January | 2018 | 2018Q3 | 2018 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2018-01-08 | Y | 193.1449 | N | 4 | N | Y | 1.1101 | 39.4971 | 38955.9141
[7 empty] | 7611 | 6418 | 1539921 | 2018-01-08 19:18 | 2018-01-08 21:32 | 134 | 11kV | 82342 | 1757 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 185216/02 Isolated below 33kV faulty insulator at pole KT-70118 | January | 2018 | 2018Q3 | 2018 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2018-01-08 | Y | 46.8651 | N | 4 | N | Y | 1.1101 | 39.4971 | 60173.1049
[7 empty] | 7253 | 1305 | 1540830 | 2018-01-08 19:28 | 2018-01-08 22:00 | 152 | 11kV | 912 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 185222 | January | 2018 | 2018Q3 | 2018 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2018-01-08 | Y | 152 | N | 4 | N | Y | 1.1101 | 39.4971 | 666.4627
[7 empty] | 8287 | 14816 | 1541272 | 2018-01-08 22:16 | 2018-01-08 22:24 | 8 | 11kV | 14056 | 1757 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | Y | Zn12610 Long Jetty section of Pa6 "Rhodin Drive" tripped on SW, 11kv trip Cause: Weather related | January | 2018 | 2018Q3 | 2018 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Veg | 2018-01-08 | Y | 8 | N | 4 | N | Y | 1.1101 | 39.4971 | 10271.7102
[7 empty] | 7796 | 8701 | 1539955 | 2018-01-08 19:35 | 2018-01-08 22:45 | 190 | 11kV | 570 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 185220 C Phase DOLF : 10 Amp Excluded OMS 1539955 | January | 2018 | 2018Q3 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-01-08 | Y | 190 | N | 4 | N | Y | 1.1101 | 39.4971 | 416.5392
[7 empty] | 8406 | 16467 | 1539938 | 2018-01-08 19:31 | 2018-01-08 22:55 | 204 | 11kV | 385356 | 1889 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 185235 1 fault operation C phase Overcurrent 1st fault found 8/1/18 tapping blown between JU30133 and ABS1371 supply restored 08/01/18 22:55 2nd fault found on the 9th center phase tapping blown UGOH pole JU-30831 and CB 8086 fault overhaul and endbox inspection. - refer to OMS 1540891 Excluded OMS 1539938 | January | 2018 | 2018Q3 | 2018 | 203:8086 | 204:82697 | ZN00204/082697 | NEWCASTLE | OH | Not Veg | 2018-01-08 | Y | 204 | N | 4 | N | Y | 1.1101 | 39.4971 | 281606.7987
[7 empty] | 8417 | 16531 | 1539756 | 2018-01-08 17:34 | 2018-01-08 23:10 | 336 | 11kV | 283427 | 2106 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn12610 Long Jetty Panel 13 "Blue Bay" fdr tripped on EF, EFI, FC Cause: lightning HV mains down from LB40898 to LK40385 to AB40273 tee PT12774 See 1541105,6,7,8,9 ex 1539756 | January | 2018 | 2018Q3 | 2018 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2018-01-08 | Y | 134.5807 | N | 4 | N | Y | 1.1101 | 39.4971 | 207120.0919
[7 empty] | 8684 | 19848 | 1539971 | 2018-01-08 19:54 | 2018-01-08 23:15 | 200.75 | 11kV | 18268.25 | 91 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 185207 A Phase DOLF : 10 Amp Excluded OMS 1539971 | January | 2018 | 2018Q3 | 2018 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Veg | 2018-01-08 | Y | 200.75 | N | 4 | N | Y | 1.1101 | 39.4971 | 13349.8983
[7 empty] | 8380 | 15950 | 1540005 | 2018-01-08 20:15 | 2018-01-08 23:20 | 184.6833 | 11kV | 5355.8167 | 29 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 185197 A & C phase DOLF : 20 Amp CC1: 22-"Refer to SOp" | January | 2018 | 2018Q3 | 2018 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2018-01-08 | Y | 184.6833 | N | 4 | N | Y | 1.1101 | 39.4971 | 3913.8729
[7 empty] | 7980 | 10757 | 1539980 | 2018-01-08 18:00 | 2018-01-08 23:20 | 320 | 11kV | 640 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 185202 B & C phase DOLF : 40 Amp CC1: 22-"Refer to SOp" | January | 2018 | 2018Q3 | 2018 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2018-01-08 | Y | 320 | N | 4 | N | Y | 1.1101 | 39.4971 | 467.6931
[7 empty] | 7351 | 2954 | 1539978 | 2018-01-08 19:42 | 2018-01-09 00:18 | 276 | 11kV | 178007 | 888 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 185233 2 fault operations B & C phase Overcurrent, Earth Fault Passer by reported DW down on Davis Rd, Swan Bay Excluded OMS 1539978 | January | 2018 | 2018Q3 | 2018 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2018-01-08 | Y | 200.4583 | N | 4 | N | Y | 1.1101 | 39.4971 | 130082.2653
[7 empty] | 8717 | 20307 | 1540076 | 2018-01-08 18:33 | 2018-01-09 00:52 | 379 | 11kV | 758 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 185203 Single phase DOLF : 10 Amp Feeder 35192 had outage. Abnormally switched. Replaced L/As Excluded OMS 1540076 | January | 2018 | 2018Q3 | 2018 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2018-01-08 | Y | 379 | N | 4 | N | Y | 1.1101 | 39.4971 | 553.924
[7 empty] | 7215 | 608 | 1539924 | 2018-01-08 19:22 | 2018-01-09 01:05 | 343 | 11kV | 262403 | 1977 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 185225 11kVOHM storm damage at JU-63510 & ohm down JU61279 to JU-61278 | January | 2018 | 2018Q3 | 2018 | 202:34254 | 202:34254 | ZN00202/034254 | NEWCASTLE | OH | Not Veg | 2018-01-08 | Y | 132.7279 | N | 4 | N | Y | 1.1101 | 39.4971 | 191756.3728
[7 empty] | 8034 | 11472 | 1540024 | 2018-01-08 20:30 | 2018-01-09 01:10 | 280 | 11kV | 840 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 185223 A Phase DOLF : 10 Amp Excluded OMS 1540024 | January | 2018 | 2018Q3 | 2018 | 264:81240 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Veg | 2018-01-08 | Y | 280 | N | 4 | N | Y | 1.1101 | 39.4971 | 613.8472
[7 empty] | 8196 | 13704 | 1540102 | 2018-01-09 00:19 | 2018-01-09 01:41 | 82 | 11kV | 6478 | 79 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | REC.1014 Suakin Drive - tripped on: A & B phase O/C Cause not ascertained. Rec is 0 shot. ( Non reclosing ) | January | 2018 | 2018Q3 | 2018 | ZN180:PA17 | ZN180:PA17 | ZN00180/000017 | MOSMAN | OH | Veg | 2018-01-09 | N | 82 | N | 24 | Y | Y | 1.1101 | 39.4971 | 4733.9313
[7 empty] | 8649 | 19466 | 1540107 | 2018-01-09 00:36 | 2018-01-09 02:22 | 106 | 11kV | 154598 | 1650 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Previous Storm | N | Zn14892 Charmhaven Pa14 "Submarine Cable" fdr has tripped Signals: 11kv trip Relays: E/F, EFI EFI's: As Expected Abnormal: S14797:B closed S14987:B Open due to DMA. LB44170 closed, S14740:B Open for LR switching for DMA See 1541276,8,9 ex 1540107 | January | 2018 | 2018Q3 | 2018 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | UG | Not Veg | 2018-01-09 | N | 93.6958 | N | 24 | Y | Y | 1.1101 | 39.4971 | 112975.6585
[7 empty] | 7974 | 10679 | 1540026 | 2018-01-08 20:32 | 2018-01-09 02:45 | 373 | 11kV | 5595 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 185230 A Phase DOLF : 10 Amp Excluded OMS 1540026 | January | 2018 | 2018Q3 | 2018 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Veg | 2018-01-08 | Y | 373 | N | 4 | N | Y | 1.1101 | 39.4971 | 4088.661
[7 empty] | 7913 | 10034 | 1539936 | 2018-01-08 19:33 | 2018-01-09 02:50 | 436.7667 | 11kV | 27953.0667 | 64 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 185241 A Phase Lightning Arrestor | January | 2018 | 2018Q3 | 2018 | 213:33774 | 213:33774 | ZN00213/033774 | NEWCASTLE | OH | Not Veg | 2018-01-08 | Y | 436.7667 | N | 4 | N | Y | 1.1101 | 39.4971 | 20427.2766
[7 empty] | 7705 | 7496 | 1539968 | 2018-01-08 19:46 | 2018-01-09 03:00 | 433.6167 | 11kV | 8238.7167 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 185231 A Phase DOLF : 16 Amp | January | 2018 | 2018Q3 | 2018 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2018-01-08 | Y | 433.6167 | N | 4 | N | Y | 1.1101 | 39.4971 | 6020.6111
[7 empty] | 7809 | 8814 | 1540134 | 2018-01-09 04:58 | 2018-01-09 05:55 | 57 | 11kV | 36537 | 641 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Lightning | N | REC.49995 Holly Kendall tripped on: O/C Possible iR defect. Storm at the time also. | January | 2018 | 2018Q3 | 2018 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | OH | Not Veg | 2018-01-09 | N | 57 | N | 24 | Y | Y | 1.1101 | 39.4971 | 26700.1619
[7 empty] | 7424 | 4119 | 1539983 | 2018-01-08 20:00 | 2018-01-09 07:50 | 710 | 11kV | 37630 | 53 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | Y | LID 185260 A & B phase DOLF : 20 Amp TX 11910 REPLACED. | January | 2018 | 2018Q3 | 2018 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2018-01-08 | Y | 710 | N | 4 | N | Y | 1.1101 | 39.4971 | 27498.8941
[7 empty] | 8505 | 17683 | 1540127 | 2018-01-09 04:38 | 2018-01-09 07:59 | 201 | 11kV | 101232 | 1020 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Zn965 Pennant Hills - Pnl. 43 tripped on: B & C phase O/C with EFI Roadside HDO found blown at PT1649 Eucalyptus Gum. Lightning strike suspected. See 1541268 1541269 | January | 2018 | 2018Q3 | 2018 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Not Veg | 2018-01-09 | N | 99.2471 | N | 24 | Y | Y | 1.1101 | 39.4971 | 73977.3598
[7 empty] | 7513 | 5525 | 1540179 | 2018-01-09 06:45 | 2018-01-09 08:40 | 115 | 11kV | 68506 | 641 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | N | REC.49995 Holly Kendall tripped on: A & B Pahse O/C Middle phase damaged on 11kV UGOH to S5367 See 1541280 1541281 | January | 2018 | 2018Q3 | 2018 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | Unknown | Unknown | 2018-01-09 | N | 106.8736 | N | 24 | Y | Y | 1.1101 | 39.4971 | 50062.1642
[7 empty] | 8445 | 16864 | 1540192 | 2018-01-09 06:58 | 2018-01-09 08:48 | 110 | 11kV | 135214 | 1320 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 185262 2 fault operations A & C phase Overcurrent NO FAULT FOUND PLEASE PATROL. Excluded OMS REPORT NO 1540192. | January | 2018 | 2018Q3 | 2018 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Veg | 2018-01-09 | N | 102.4348 | N | 24 | Y | Y | 1.1101 | 39.4971 | 98810.4031
[7 empty] | 8622 | 19139 | 1540249 | 2018-01-09 07:54 | 2018-01-09 08:49 | 55 | 11kV | 5720 | 104 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex Zn12690 Berkeley Vale section of pa7 RE44790 Hansens Rd tripped, relcosed and locked out on: OC trip Cause: tree/branch on OH mains. burnt tree branch was found on 11kV near LB43317 | January | 2018 | 2018Q3 | 2018 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Veg | 2018-01-09 | N | 55 | N | 24 | Y | Y | 1.1101 | 39.4971 | 4180.0073
[7 empty] | 8249 | 14410 | 1540025 | 2018-01-08 20:31 | 2018-01-09 08:55 | 744 | 11kV | 20832 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 185264 C Phase DOLF : 20 Amp readings as left 244v on 3 phases Excluded OMS 1540025 | January | 2018 | 2018Q3 | 2018 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Veg | 2018-01-08 | Y | 744 | N | 4 | N | Y | 1.1101 | 39.4971 | 15223.4112
[7 empty] | 7549 | 5810 | 1539915 | 2018-01-08 19:21 | 2018-01-09 09:00 | 819 | 11kV | 13401 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 185269 B & C Phase fuse : 32 Amp A and C phase DOLF's blown on PT. 48351 as well. Suggest Line fuse may have blown in sympathy. No other causes found. | January | 2018 | 2018Q3 | 2018 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2018-01-08 | Y | 788.2941 | N | 4 | N | Y | 1.1101 | 39.4971 | 9793.0555
[7 empty] | 7703 | 7457 | 1540186 | 2018-01-09 06:54 | 2018-01-09 09:25 | 151 | 11kV | 220641 | 1775 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn12600 Lisarow Pa12 "Parsons Newlings" CB tripped, reclosed and locked out on: Signals: 11kv trip Relays: A phase IOC, Timed OC, EFI EFI's: S65860 S64111 S64112 S18078 S18011 S18624 S14947 Abnormal: S14947:A Closed, RE44936 Open Cause: UGOH fault short circuit near S14947 between LB41131 & LB41121 & S14947:A See 1541303,6,7 ex 1540184,6 | January | 2018 | 2018Q3 | 2018 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | Unknown | Unknown | 2018-01-09 | N | 124.3048 | N | 24 | Y | Y | 1.1101 | 39.4971 | 161237.935
[7 empty] | 8304 | 15022 | 1540060 | 2018-01-09 01:10 | 2018-01-09 09:30 | 500 | 11kV | 1500 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 185266 Single phase Main tapping found burnt off at LF 40889. Repaired live line by J. Carey. | January | 2018 | 2018Q3 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-01-09 | N | 500 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1096.1558
[7 empty] | 8675 | 19753 | 1540172 | 2018-01-09 08:20 | 2018-01-09 09:39 | 79 | 11kV | 62870 | 830 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn129 Hunters Hill - Pnl.47 tripped on: C Phase IOC Field EFIs: S36125 S5739 S4271 S35708 S4272 UG cable fault from S4272 (Sw/A) to S8996 (Sw/B) Note: S8996 Dist #3 was already out of service due to LV UG cable fault (0644 - 1110) See 1541290 See 1541291 1541292 1541293 | January | 2018 | 2018Q3 | 2018 | ZN129:PA47 | ZN129:PA47 | ZN00129/000047 | HUNTERS HILL | UG | Not Veg | 2018-01-09 | N | 75.747 | N | 24 | Y | Y | 1.1101 | 39.4971 | 45943.5416
[7 empty] | 8120 | 12816 | 1539905 | 2018-01-08 19:09 | 2018-01-09 10:01 | 892 | 11kV | 2676 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | Y | LID 185268 A Phase LLC burnt off. Replaced Live line. Excluded OMS 1540210 1539905, 1540070, 1540280 | January | 2018 | 2018Q3 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2018-01-08 | Y | 892 | N | 4 | N | Y | 1.1101 | 39.4971 | 1955.5419
[7 empty] | 7505 | 5432 | 1539892 | 2018-01-08 18:43 | 2018-01-09 10:20 | 937 | 11kV | 67977 | 343 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | Y | LID 185270 1 fault operation Faulty 11kV UGOH at pole IQ-73776. Restored by generator and LV//. Excluded OMS 1539896. | January | 2018 | 2018Q3 | 2018 | 528:83014 | 508:82576 | ZN00508/082576 | MAITLAND | Unknown | Unknown | 2018-01-08 | Y | 198.1837 | N | 4 | N | Y | 1.1101 | 39.4971 | 49675.5866
[7 empty] | 7567 | 6007 | 1540219 | 2018-01-09 07:20 | 2018-01-09 11:10 | 230 | 11kV | 690 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 185271 A & B phase DOLF : 16 Amp Not sub 52185 as OMS sugests. Excluded OMS 1540219 | January | 2018 | 2018Q3 | 2018 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2018-01-09 | N | 230 | N | 24 | Y | Y | 1.1101 | 39.4971 | 504.2316
[7 empty] | 7725 | 7736 | 1540402 | 2018-01-09 07:04 | 2018-01-09 12:20 | 316 | 11kV | 34495 | 1939 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 185235 Center phase tapping blown UGOH pole JU-30831 CB 8086 fault overhaul and endbox inspection. Note: refer to OMS 1540890 for first fault (tapping blown between JU30133 and ABS1371) found @ 08/01/2018 19:31 and supply restored 08/01/2018 22:55. Network left in abnormal configuration overnight. During early hours of morning, another fault was found (tapping blown UGOH pole JU-30831 and oil at CB 8086) and included on the same LID report as the first fault. Switching instructions included in Unplanned LID folder Excluded OMS 1540402, 1540405, 1540407 | January | 2018 | 2018Q3 | 2018 | 203:8086 | 204:82697 | ZN00204/082697 | NEWCASTLE | OH | Not Veg | 2018-01-09 | N | 17.7901 | N | 24 | Y | Y | 1.1101 | 39.4971 | 25207.9286
[7 empty] | 8322 | 15208 | 1540474 | 2018-01-09 12:44 | 2018-01-09 14:00 | 76 | 11kV | 76 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185275 C Phase DOLF : 10 Amp Excluded OMS 1540474 | January | 2018 | 2018Q3 | 2018 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2018-01-09 | N | 76 | N | 24 | Y | Y | 1.1101 | 39.4971 | 55.5386
[7 empty] | 8320 | 15183 | 1539775 | 2018-01-08 17:24 | 2018-01-09 14:16 | 1252 | 11kV | 1467160 | 1349 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | Y | Ex Zn14891 Wyong Pa16 IR40118 Murrawal tripped/reclsoed/tripped on OC, SE, field EFI's Cause: Lightning/Surge Arrestor Feeder isolated at LB40962 4xPT's interrupted DOp Lman to look for blown surge arrestors in daylight. Fault awas blown surge arrestor @PT11042 Tanley Wahroonga 0.4 See 1541257,8 ex 1539775,40116 | January | 2018 | 2018Q3 | 2018 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2018-01-08 | Y | 1087.5908 | N | 4 | N | Y | 1.1101 | 39.4971 | 1072157.2541
[7 empty] | 7686 | 7195 | 1539689 | 2018-01-08 16:12 | 2018-01-09 14:35 | 1343 | 11kV | 71836 | 110 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Ex Zn12690 Berkeley Vale section of Pa16 "Catamaran Sailcraft etc" 11kV RE45026 Fountaindale tripped and locked out on Overcurrent Cause: lightning Section of fdr isolated from lB43368 to LB45169 to LB43843 with PT12538 interrupted 11kV down Also PT11397 interrutped on HV and LV2xLV poles down See 1541064,5,6,7 ex 1539684 | January | 2018 | 2018Q3 | 2018 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Not Veg | 2018-01-08 | Y | 653.0545 | N | 4 | N | Y | 1.1101 | 39.4971 | 52495.63
[7 empty] | 7962 | 10517 | 1540461 | 2018-01-09 12:05 | 2018-01-09 15:20 | 195 | 11kV | 585 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185278 A Phase DOLF : 10 Amp Excluded OMS 1540461 | January | 2018 | 2018Q3 | 2018 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2018-01-09 | N | 195 | N | 24 | Y | Y | 1.1101 | 39.4971 | 427.5007
[7 empty] | 7408 | 3943 | 1539827 | 2018-01-08 17:17 | 2018-01-09 16:18 | 1381 | 11kV | 476968 | 361 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | Y | Ex Zn14891 Wyong section of Pa5 "Dooralong" fdr Re45101 Jilliby Dunks tripped to lockout on OC and EF Cause: Burnt off bond adj RE45101, damaged surge arrestors at PT12539 See 1541117,9,20,1,2,3,4,5,6,7,8 ex 1539767,827,40214 | January | 2018 | 2018Q3 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2018-01-08 | Y | 1321.241 | N | 4 | N | Y | 1.1101 | 39.4971 | 348554.1462
[7 empty] | 7741 | 7900 | 1540533 | 2018-01-09 14:47 | 2018-01-09 16:31 | 104 | 11kV | 181421 | 1868 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | Zn9035 Caringbah - Pnl.11 tripped, reclosed, tripped & locked out on: 11R Earth Fault Field EFIs: ALL to S9529 UG cable fault from S9529 (Sw/A) to S9503 (Sw/B) to S9449 (Sw/B) See 1540606 1540896 CC1: 11-"Despatch to re-issue" | January | 2018 | 2018Q3 | 2018 | ZN9035:PA11 | ZN9035:PA11 | ZN09035/000011 | SUTHERLAND | UG | Not Veg | 2018-01-09 | N | 97.1204 | N | 24 | Y | Y | 1.1101 | 39.4971 | 132577.1158
[7 empty] | 8299 | 14984 | 1539960 | 2018-01-08 17:34 | 2018-01-09 16:40 | 1386 | 11kV | 70317 | 70 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Ex Zn12630 Peats Ridge section of pa3 RE49206 Mangrve Mtn West was opened fdue to 11kv on ground RE49206 open at 0313 to earth feeder on ground beyond USL43969 Cause: OH down. 4 bays of 11kv down between USL43969 and PT11681 OH Down See 1541296,1541295 ex 1539791,960,40120,491 | January | 2018 | 2018Q3 | 2018 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2018-01-08 | Y | 1004.5286 | N | 4 | N | Y | 1.1101 | 39.4971 | 51385.5896
[7 empty] | 8097 | 12398 | 1539693 | 2018-01-08 16:18 | 2018-01-09 17:05 | 1487 | 11kV | 342026 | 786 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn12690 Berkeley Vale Panel 24 "Berkeley Rd" fdr tripped Relays: 24L SEL Signals: 11kv trip Cause: OH down 11kv mains down from LB63855 Feeder from AB44733 to be patrolled in daylight Also PT12499 isolated Tree on mains with 11kv down past RE47878 See 1541075,6,7,8,9,80 Ex 1539693 | January | 2018 | 2018Q3 | 2018 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2018-01-08 | Y | 435.1476 | N | 4 | N | Y | 1.1101 | 39.4971 | 249942.5127
[7 empty] | 8634 | 19275 | 1540563 | 2018-01-09 16:30 | 2018-01-09 17:35 | 65 | 11kV | 8125 | 125 | HV | Animal Insect | Animal | Pole | Unplanned | Hot >35C | N | LID 185280 Termite infested pole Emergency replacement of pole 8H-20055. | January | 2018 | 2018Q3 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2018-01-09 | N | 65 | N | 24 | Y | Y | 1.1101 | 39.4971 | 5937.5104
[7 empty] | 7338 | 2799 | 1540562 | 2018-01-09 16:22 | 2018-01-09 17:45 | 83 | 11kV | 124863 | 1520 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | Zn1193 Lindafield - Pnl.26 tripped on: B & C Phase IOC, A & B phase O/C Tree branch contacted mains - suspect in tee off to PT25 See 1541300 1541302 | January | 2018 | 2018Q3 | 2018 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | OH | Veg | 2018-01-09 | N | 82.1467 | N | 24 | Y | Y | 1.1101 | 39.4971 | 91246.1976
[7 empty] | 7624 | 6530 | 1539129 | 2018-01-07 14:24 | 2018-01-09 18:00 | 3096 | 11kV | 284405 | 1946 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Hot >35C | N | Zn5868 Gore Hill - Pnl.14 tripped on: Earth Fault S8002 George Place Sw/B end box exploded. Sub left de-energised as buiding appears uninhabited. Repaired and restored 18:00 9/1/18 See 1541235 1541239 1541238 | January | 2018 | 2018Q3 | 2018 | ZN5868:PA14 | ZN5868:PA14 | ZN05868/000014 | WILLOUGHBY | UG | Not Veg | 2018-01-07 | N | 146.1485 | N | 24 | Y | Y | 1.1101 | 39.4971 | 207834.7855
[7 empty] | 7585 | 6126 | 1539685 | 2018-01-08 15:52 | 2018-01-09 18:05 | 1573 | 11kV | 89764 | 323 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Zn12630 Peats Ridge section of Pa10 "Peats Ridge" fdr tripped on B&C IOC, B&C OC, EFI, Rec and Lock Out Cause: Tree Branch brought down OH. Mains down between LB43055 and AB40537 tee PT49311 & PT13875 See 1541033,5,6,7,8 ex 1539666,85 | January | 2018 | 2018Q3 | 2018 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2018-01-08 | Y | 277.9071 | N | 4 | N | Y | 1.1101 | 39.4971 | 65596.8836
[7 empty] | 7427 | 4127 | 1540588 | 2018-01-09 17:52 | 2018-01-09 20:31 | 159.1833 | 11kV | 21330.5667 | 134 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 185285 3 phase A Reagan closed sw 63939 after interrogating relay | January | 2018 | 2018Q3 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2018-01-09 | N | 159.1833 | N | 24 | Y | Y | 1.1101 | 39.4971 | 15587.749
[7 empty] | 8484 | 17447 | 1540633 | 2018-01-09 19:41 | 2018-01-09 20:39 | 58 | 11kV | 15018 | 259 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | @ S10925 Forest Waterboard - 11kV panels Sw/A & Sw/B tripped on A & C phase O/C Storm related. See 1541545 15451544 | January | 2018 | 2018Q3 | 2018 | ZN10999:PA7 | ZN10999:PA7 | ZN10999/000007 | GEORGES RIVER | OH | Not Veg | 2018-01-09 | N | 57.9846 | N | 24 | Y | Y | 1.1101 | 39.4971 | 10974.7114
[7 empty] | 7858 | 9404 | 1539661 | 2018-01-08 15:44 | 2018-01-09 20:40 | 1736 | 11kV | 59017 | 149 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | Y | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mtn" fdr Re46935 Ironbark Kirks 0.75 tripped on earth fault Cause: 4 bays 11kv down beyond autolink 46938 ironbark kirks Also 11kv down between RE46895 to LK4095 tee PT18733 & PT13138 See 1541020,1,2,4 ex 1539661,8,40089 | January | 2018 | 2018Q3 | 2018 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2018-01-08 | Y | 396.0872 | N | 4 | N | Y | 1.1101 | 39.4971 | 43127.8829
[7 empty] | 7825 | 9007 | 1539500 | 2018-01-08 10:54 | 2018-01-09 21:25 | 2071 | 11kV | 112891 | 1146 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | At Zn262 Marrickville 11kv Pnl 41 'Victoria Meeks' tripped on B and C phase IOC with fault check Signals: 11kv trip, Zone and Group #1 earth Field efi's: Pnl41 to S35735 Remarks: UG fault. Defective efi at S47271 (did not operate), see separate trip on Pnl 12 @ Campsie. Cable fault between S47271 Richardson Bayview to S8076 Undercliff Bayview tee to S5808 Waterworth Park (N//) | January | 2018 | 2018Q3 | 2018 | ZN262:PA41 | ZN262:PA41 | ZN00262/000041 | INNER WEST | UG | Not Veg | 2018-01-08 | Y | 98.5087 | N | 4 | N | Y | 1.1101 | 39.4971 | 82497.4131
[7 empty] | 8227 | 14106 | 1540597 | 2018-01-09 19:20 | 2018-01-09 21:39 | 139 | 11kV | 81047 | 594 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | Ex Zn14143 Somersby section of Pa17 RE45202 Pacific Ashbrooke 2.0 tripped, reclsoed and locked out on: OC trip Cause:Tree Branch contact - other Tree branch hit and fell clear adj Re50001 See 1541343 2nd 1541345,7,8 ex 1540570,97,728 | January | 2018 | 2018Q3 | 2018 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2018-01-09 | N | 136.4428 | N | 24 | Y | Y | 1.1101 | 39.4971 | 59226.7571
[7 empty] | 7265 | 1552 | 1540670 | 2018-01-09 20:52 | 2018-01-09 21:51 | 59 | 11kV | 16461 | 279 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC.554 Rosscommon Rd tripped on: O/C Tree branch on mains outside 99 Arcadia Rd Galston | January | 2018 | 2018Q3 | 2018 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2018-01-09 | N | 59 | N | 24 | Y | Y | 1.1101 | 39.4971 | 12029.2133
[7 empty] | 8046 | 11691 | 1540668 | 2018-01-09 21:42 | 2018-01-10 00:45 | 183 | 11kV | 30868 | 931 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Electrical Storm | N | LID 185290 4 fault operations C Phase Overcurrent Damaged 11kV end box at fuse switch unit in Homebush Drive sub 19862. Excluded LID 1540668 and 1540692 | January | 2018 | 2018Q3 | 2018 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | UG | Not Veg | 2018-01-09 | N | 33.1557 | N | 24 | Y | Y | 1.1101 | 39.4971 | 22557.4239
[7 empty] | 8318 | 15165 | 1540730 | 2018-01-10 02:11 | 2018-01-10 05:11 | 180 | 11kV | 8740 | 50 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn1610 Homebush Bay 11kv feeder Panel No: 10 "Slough Holker etc" feeder tripped on: Relays: E/F, EFI Remarks: cause not ascertained.EFIs failed to give positive indication of fault mains required testedL 11kv No1 RMI @ S7138 Slough Holker 11kv feeder from S1610 Homebush Bay Panel No10 to Sw/A @ S3889 SPS 1082 to Sw/B @ S7138 Slough Holker and including No1 RMI | January | 2018 | 2018Q3 | 2018 | ZN1610:PA10 | ZN1610:PA10 | ZN01610/000010 | PARRAMATTA | OH | Veg | 2018-01-10 | N | 174.8 | N | 9 | N | N | 1.1101 | 39.4971 | 6386.9342
[7 empty] | 7377 | 3517 | 1540756 | 2018-01-10 06:47 | 2018-01-10 08:00 | 73 | 11kV | 219 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185312 B Phase DOLF : 10 Amp | January | 2018 | 2018Q3 | 2018 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2018-01-10 | N | 73 | N | 9 | N | N | 1.1101 | 39.4971 | 160.0387
[7 empty] | 7788 | 8578 | 1540732 | 2018-01-10 02:29 | 2018-01-10 09:45 | 436 | 11kV | 1744 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 185315 A Phase DOLF : 10 Amp Excluded OMS 1540732 | January | 2018 | 2018Q3 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-01-10 | N | 436 | N | 9 | N | N | 1.1101 | 39.4971 | 1274.4638
[7 empty] | 7629 | 6579 | 1540757 | 2018-01-10 06:49 | 2018-01-10 09:45 | 176 | 11kV | 138089 | 2477 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 185311 1 fault operation HV into LV, HV xarm burnt through & fell into LV. Excluded OMS 1540757,1540752, 1540765, 1540791 | January | 2018 | 2018Q3 | 2018 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2018-01-10 | N | 55.7485 | N | 9 | N | N | 1.1101 | 39.4971 | 100911.3683
[7 empty] | 8153 | 13214 | 1540460 | 2018-01-09 09:07 | 2018-01-10 10:15 | 1508 | 11kV | 15080 | 10 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Previous Storm | N | Ex Zn14143 Somersby section of Pa17 PT18484 Pacific Ashbrooke 1.2 the 11kv roadside phase hdo was found to be operated Cause: lightning/surge arrestor. Dop found roadside phase surge arrestor blown See 1541343 2nd 1541345,7,8 ex 1540570,97,728 | January | 2018 | 2018Q3 | 2018 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2018-01-09 | N | 1508 | N | 24 | Y | Y | 1.1101 | 39.4971 | 11020.0192
[7 empty] | 8087 | 12267 | 1540700 | 2018-01-09 21:29 | 2018-01-10 10:53 | 804 | 11kV | 22512 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 185316 A Phase DOLF : 20 Amp Excluded oms 1540700, 1540705 & 1540794 | January | 2018 | 2018Q3 | 2018 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | UG | Not Veg | 2018-01-09 | N | 804 | N | 24 | Y | Y | 1.1101 | 39.4971 | 16451.1056
[7 empty] | 8037 | 11524 | 1540754 | 2018-01-10 06:43 | 2018-01-10 12:05 | 322 | 11kV | 644 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 185319 3 phase DOLF : 10 Amp Excluded OMS 1540754 | January | 2018 | 2018Q3 | 2018 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Not Veg | 2018-01-10 | N | 322 | N | 9 | N | N | 1.1101 | 39.4971 | 470.6162
[7 empty] | 7588 | 6157 | 1539691 | 2018-01-08 16:24 | 2018-01-10 12:10 | 2626 | 11kV | 7878 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | Y | Ex Zn12630 Peats Ridge section of Pa3 PT14268 Goolara Niclins 1.05 the 11kV HO was found to have operated Cause: Lightning Surge Arrestor. DOp found the 11kv surge arrestor and LV fuse assemblies damaged See 1540879 ex 1539691 | January | 2018 | 2018Q3 | 2018 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2018-01-08 | Y | 2626 | N | 4 | N | Y | 1.1101 | 39.4971 | 5757.01
[7 empty] | 7231 | 957 | 1540963 | 2018-01-10 12:05 | 2018-01-10 13:50 | 105 | 11kV | 34440 | 328 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 185322 Isolation for repairs to TM9 fdr 33kV | January | 2018 | 2018Q3 | 2018 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2018-01-10 | N | 105 | N | 9 | N | N | 1.1101 | 39.4971 | 25167.7362
[7 empty] | 8135 | 13027 | 1540815 | 2018-01-10 08:20 | 2018-01-10 14:35 | 375 | 11kV | 112058 | 1291 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn847 Hornsby - Pnl.46 tripped, reclosed, tripped & locked out on: Earth Fault Crane from construction site (36-40 Lords Ave, Asquith - Calibre Construction Group) hit HV & LV mains. Section of feeder from AB.694 to S.64281 to S65482 LV Dist from S5658 Dist #2 also hit. EMSO to check for High into Low damage. See 1541305 1541308 1541309 | January | 2018 | 2018Q3 | 2018 | ZN847:PA46 | ZN847:PA46 | ZN00847/000046 | HORNSBY | OH | Not Veg | 2018-01-10 | N | 86.7994 | N | 9 | N | N | 1.1101 | 39.4971 | 81888.6812
[7 empty] | 7531 | 5673 | 1540909 | 2018-01-10 10:55 | 2018-01-10 14:40 | 225 | 11kV | 2250 | 10 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | @S6748 Slough Rachael No.2 Tx 11kv/415v is very hot and appears to be cooking up inside. Ex Panel 26 'S63496 Fariola Wetherill' fdr from S1610 HOmebush Bay Abnormal: Sw/B open @ S7138 & Sw/A Closed @ S8282 Remarks: transformer failure. Suspect Tx Fault | January | 2018 | 2018Q3 | 2018 | ZN1610:PA10 | ZN1610:PA10 | ZN01610/000010 | PARRAMATTA | UG | Not Veg | 2018-01-10 | N | 225 | N | 9 | N | N | 1.1101 | 39.4971 | 1644.2336
[7 empty] | 7458 | 4747 | 1540747 | 2018-01-10 06:24 | 2018-01-10 15:20 | 536 | 11kV | 1071.0167 | 2 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex Zn12570 section of Pa33 "Macmasters Beach" PT18004 Dajani Little Valley Roadside 16Amp HDO found blown due to Possum found on Tx Tank See 1541366 GIS 1540747 | January | 2018 | 2018Q3 | 2018 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2018-01-10 | N | 535.5083 | N | 9 | N | N | 1.1101 | 39.4971 | 782.6674
[7 empty] | 7862 | 9417 | 1541167 | 2018-01-11 02:39 | 2018-01-11 10:46 | 487 | 11kV | 45124 | 412 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 185332 1 fault operation C Phase Overcurrent sw 42039 operated at the same time,please check gradings. 2 grassfires started. 1 at pole SF-40699 & 1at Sw 42039 approximately 20 sq metres burnt. Excluded oms report no 1541167 & 1541168 & 1541170. | January | 2018 | 2018Q3 | 2018 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2018-01-11 | N | 109.5243 | N | 6 | N | N | 1.1101 | 39.4971 | 32975.2883
[7 empty] | 7950 | 10381 | 1541237 | 2018-01-11 09:55 | 2018-01-11 11:30 | 95 | 11kV | 380 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185337 C Phase DOLF : 10 Amp 240, 241, 231 volts 2, 1, 48 amps Excluded oms 1541252 | January | 2018 | 2018Q3 | 2018 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2018-01-11 | N | 95 | N | 6 | N | N | 1.1101 | 39.4971 | 277.6928
[7 empty] | 7979 | 10756 | 1541174 | 2018-01-11 04:53 | 2018-01-11 13:35 | 522 | 11kV | 265980 | 1036 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14144 Wamberal Pa7 AB44987 fdr triped on: Relays: B&C Phase OC, SEF, Lockout Signals: 11kv trip EFI's: Nil Cause: OH Down. Multiple faults on feeder. 11kV don on cnr of Ocean View Dr & Wairakei, 11kv bonds off at tee off to PT12549 and on tee of beyond AB44382 Cause 1542883,9,90,8 ex 1541174,5,88,9,283,7,8,310,29,30 | January | 2018 | 2018Q3 | 2018 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Veg | 2018-01-11 | N | 256.7375 | N | 6 | N | N | 1.1101 | 39.4971 | 194370.3389
[7 empty] | 7907 | 9978 | 1541217 | 2018-01-11 08:59 | 2018-01-11 13:50 | 291 | 11kV | 22362 | 380 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa2 "Manns Rd" fdr RE50247 Blackett Faunce tripped on timed O/C Cause: Pole Defective/Failure. Broken 11kV Crossarm adjacent UGOH near AB44692 See 15412147,259 ex 1541223 | January | 2018 | 2018Q3 | 2018 | ZN12650:PA2 | ZN12650:PA2 | ZN12650/000002 | CENTRAL COAST | OH | Not Veg | 2018-01-11 | N | 58.8474 | N | 6 | N | N | 1.1101 | 39.4971 | 16341.49
[7 empty] | 7266 | 1564 | 1541452 | 2018-01-11 16:58 | 2018-01-11 18:25 | 87 | 11kV | 135470 | 1733 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn8000 Macquarie Park - Pnl.4 tripped on: O/C & E/F Field EFIs; S2004 Abnormal: LB1276 Closed with AB1116 Open and LB720 Closed with AB2618 open. UGOH fault below S2004 (Sw/D) See 1541532 1541533 1541534 | January | 2018 | 2018Q3 | 2018 | ZN8000:PA4 | ZN129:PA64 | ZN00129/000064 | RYDE | Unknown | Unknown | 2018-01-11 | N | 78.1708 | N | 6 | N | N | 1.1101 | 39.4971 | 98997.4803
[7 empty] | 8175 | 13443 | 1541481 | 2018-01-11 18:37 | 2018-01-11 20:00 | 83 | 11kV | 166 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185345 A Phase DOLF : 10 Amp Excluded OMS 1541481 | January | 2018 | 2018Q3 | 2018 | 235:2857 | 235:2857 | ZN00235/002857 | MAITLAND | OH | Veg | 2018-01-11 | N | 83 | N | 6 | N | N | 1.1101 | 39.4971 | 121.3079
[7 empty] | 8270 | 14593 | 1541505 | 2018-01-12 04:27 | 2018-01-12 09:15 | 288 | 11kV | 96588 | 1084 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At Zn36800 Waverley Panel #46L 'S62998 Anglesea Aux No.1' feeder has tripped on: Relays: OC/EF, efi Remarks: end box fault. Endbox exploded Sw/A @ S3358 Fletcher Raine. 11kv feeder isolated from S61488 Fletcher Figtree to Sw/A @ S5372 Bon Accord Flood, Tee S3358 | January | 2018 | 2018Q3 | 2018 | ZN36800:PA46 | ZN36800:PA46 | ZN36800/000046 | WAVERLEY | Unknown | Not Veg | 2018-01-12 | N | 89.1033 | N | 12 | N | N | 1.1101 | 39.4971 | 70583.6615
[7 empty] | 7912 | 10020 | 1541536 | 2018-01-12 09:04 | 2018-01-12 09:15 | 11 | 11kV | 12903 | 1173 | HV | Overload | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 185348 3 phase Overcurrent sw 63632 frame drv tripped on overload during SI 24984 (fdr abnormal for switching abs 41323 closed & abs 40285 open) Excluded OMS 1541536 | January | 2018 | 2018Q3 | 2018 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Not Veg | 2018-01-12 | N | 11 | N | 12 | N | N | 1.1101 | 39.4971 | 9429.1318
[7 empty] | 8574 | 18517 | 1541508 | 2018-01-12 06:21 | 2018-01-12 09:59 | 218.1667 | 11kV | 40142.6667 | 184 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 185350 3 Fault operations A & C phase Overcurrent Tree fell on mains between poles MN-53933 and MN-53932. Mains were also damaged and needed repairs before restoration. | January | 2018 | 2018Q3 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2018-01-12 | N | 218.1667 | N | 12 | N | N | 1.1101 | 39.4971 | 29335.0768
[7 empty] | 7421 | 4108 | 1541531 | 2018-01-12 08:49 | 2018-01-12 10:01 | 72 | 11kV | 205392 | 3004 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S35600 Kingsford Zn P9 the forsyth st etc fdr tripped on (rh leg) e/f, f/check, f/leakage efi's at S2276 Remarks: UG damaged by contractors. S2276 forsyth st to S4743 Harbourne rainbow | January | 2018 | 2018Q3 | 2018 | ZN35600:PA9 | ZN35600:PA9 | ZN35600/000009 | RANDWICK | UG | Not Veg | 2018-01-12 | N | 68.3728 | N | 12 | N | N | 1.1101 | 39.4971 | 150094.4156
[7 empty] | 8047 | 11692 | 1541612 | 2018-01-12 12:14 | 2018-01-12 13:55 | 101 | 11kV | 202 | 2 | HV | Animal Goanna | Animal | UGOH | Unplanned | No Weather Impact | N | LID 185354 HV Fuse : 80 Amp Goanna caused fault at UGOH on pole DP-70156. Excluded OMS 1541612 | January | 2018 | 2018Q3 | 2018 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2018-01-12 | N | 101 | N | 12 | N | N | 1.1101 | 39.4971 | 147.6156
[7 empty] | 8032 | 11450 | 1541628 | 2018-01-12 13:00 | 2018-01-12 14:15 | 74.7333 | 11kV | 1943.0667 | 26 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 185356 3 phase Insulators on steel x arm pole DP-50409 failed necessitating immediate repairs. Repairs could nto be done safely without the outage. | January | 2018 | 2018Q3 | 2018 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2018-01-12 | N | 74.7333 | N | 12 | N | N | 1.1101 | 39.4971 | 1419.9358
[7 empty] | 8306 | 15045 | 1541618 | 2018-01-12 12:31 | 2018-01-12 14:50 | 139 | 11kV | 278 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185357 C Phase DOLF : 31 Amp Suspect fuse was old and heat caused it to fail. Excluded OMS 1541618. | January | 2018 | 2018Q3 | 2018 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2018-01-12 | N | 139 | N | 12 | N | N | 1.1101 | 39.4971 | 203.1542
[7 empty] | 8142 | 13096 | 1541663 | 2018-01-12 14:39 | 2018-01-12 15:24 | 45 | 11kV | 1350 | 30 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | S2568 St Peters Zn P33 the euston sydney park oval fdr tripped on 'b' phase oc/ef, f/check zn earth, group earth efis at S61901, S5418, S7571 Remarks: UG cable damaged by contractor. S7571 custom rd 154 no2 to S2457 custom campbell no2 to s7426 euston rd 134 alex | January | 2018 | 2018Q3 | 2018 | ZN2568:PA33 | ZN2568:PA33 | ZN02568/000033 | SYDNEY | UG | Not Veg | 2018-01-12 | N | 45 | N | 12 | N | N | 1.1101 | 39.4971 | 986.5402
[7 empty] | 7917 | 10089 | 1541746 | 2018-01-12 20:55 | 2018-01-12 21:11 | 16 | 11kV | 640 | 40 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 185364 Trees in mains near sub 78784 | January | 2018 | 2018Q3 | 2018 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2018-01-12 | N | 16 | N | 12 | N | N | 1.1101 | 39.4971 | 467.6931
[7 empty] | 7557 | 5916 | 1541759 | 2018-01-12 20:59 | 2018-01-12 21:45 | 46 | 11kV | 3588 | 78 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn180 Mosman section of Pa17 fdr panel RE1014 Suakin Drive tripped on Relays: O/C trip Signals: Lockout Cause: animals/birds Dead bats found outside 7 commonwealth av where explosion was reported from See 1541759 ex 1541762 | January | 2018 | 2018Q3 | 2018 | ZN180:PA17 | ZN180:PA17 | ZN00180/000017 | MOSMAN | OH | Not Veg | 2018-01-12 | N | 46 | N | 12 | N | N | 1.1101 | 39.4971 | 2622.0046
[7 empty] | 8027 | 11387 | 1541752 | 2018-01-12 20:43 | 2018-01-12 22:10 | 86.9667 | 11kV | 5739.8 | 66 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT10365 Macken Cr Road Side 50 Amp HVDO operated Remarks: fuse fatigue | January | 2018 | 2018Q3 | 2018 | ZN10994:PA1 | ZN10994:PA1 | ZN10994/000001 | GEORGES RIVER | OH | Not Veg | 2018-01-12 | N | 86.9667 | N | 12 | N | N | 1.1101 | 39.4971 | 4194.4765
[7 empty] | 7789 | 8585 | 1541769 | 2018-01-12 22:51 | 2018-01-13 00:15 | 84 | 11kV | 5544 | 66 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | PT10365 Mackn Cr road side HVDO found operated again Remarks: transformer failure. @ PT10365 Mackn Cr road side HVDO has operated twice DOp placed PT in LV// and isolated from HVDO's | January | 2018 | 2018Q3 | 2018 | ZN10994:PA1 | ZN10994:PA1 | ZN10994/000001 | GEORGES RIVER | UG | Not Veg | 2018-01-12 | N | 84 | N | 12 | N | N | 1.1101 | 39.4971 | 4051.3917
[7 empty] | 8237 | 14280 | 1541782 | 2018-01-13 08:00 | 2018-01-13 10:05 | 124.5667 | 11kV | 124.5667 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | Ex Zn12630 Peats Ridge section of pa11 PT14429 Wise Ferry Meldrum left side 16A HDO has blown. Cause not ascertained. See 1542928 ex 1541782 | January | 2018 | 2018Q3 | 2018 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2018-01-13 | N | 124.5667 | N | 4 | N | N | 1.1101 | 39.4971 | 91.0296
[7 empty] | 7938 | 10300 | 1541797 | 2018-01-13 09:38 | 2018-01-13 11:20 | 102 | 11kV | 149751 | 1705 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 185366 1 fault operation Sensitive Earth Fault Cause burnt tapping centre phase load side of ABS 25959. Excluded OMS 1541797 & 1541800. | January | 2018 | 2018Q3 | 2018 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2018-01-13 | N | 87.8305 | N | 4 | N | N | 1.1101 | 39.4971 | 109433.6139
[7 empty] | 8110 | 12654 | 1541851 | 2018-01-13 13:25 | 2018-01-13 16:55 | 210 | 11kV | 55815 | 792 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Hot >35C | N | LID 185369 ABS 74636 burnt up had to be replaced. Had to open abs 43215 due to fire at abs 74636. Had to restore the feeder in sections. Excluded OMS 1541833 1541851 1541857 | January | 2018 | 2018Q3 | 2018 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Not Veg | 2018-01-13 | N | 70.4735 | N | 4 | N | N | 1.1101 | 39.4971 | 40787.9557
[7 empty] | 8301 | 14994 | 1541875 | 2018-01-13 14:42 | 2018-01-13 17:55 | 193 | 11kV | 29232 | 275 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 185368 A Phase Burnt tapping at pole SI-90897. No protection operated. Excluded OMS 1541875. | January | 2018 | 2018Q3 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2018-01-13 | N | 106.2982 | N | 4 | N | N | 1.1101 | 39.4971 | 21361.8834
[7 empty] | 8497 | 17570 | 1541980 | 2018-01-14 05:28 | 2018-01-14 11:05 | 337 | 11kV | 1348 | 4 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @ZN2400 Berowra exiting Panel 18 labelled "Berowra Waters" PT2278 Bay Neale 11kv HDO fuse replaced 16.5 amp fuse (singe phase) Remarks: possum at base ot PT2278 | January | 2018 | 2018Q3 | 2018 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2018-01-14 | N | 337 | N | 9 | N | N | 1.1101 | 39.4971 | 985.0786
[7 empty] | 7952 | 10391 | 1542005 | 2018-01-14 09:15 | 2018-01-14 13:10 | 235 | 11kV | 470 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 185375 Single phase DOLF Suspect previous storm. Excluded OMS 1452005 | January | 2018 | 2018Q3 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2018-01-14 | N | 235 | N | 9 | N | N | 1.1101 | 39.4971 | 343.4621
[7 empty] | 7366 | 3220 | 1542017 | 2018-01-14 10:00 | 2018-01-14 13:10 | 190 | 11kV | 205666 | 1436 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 185374 3 fault operations A & C Phase Earth Fault UG cable fault between switches 56227,39023 and ABS 42929. Excluded OMS 1542017. | January | 2018 | 2018Q3 | 2018 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | UG | Not Veg | 2018-01-14 | N | 143.2214 | N | 9 | N | N | 1.1101 | 39.4971 | 150294.6467
[7 empty] | 8220 | 14020 | 1542120 | 2018-01-14 13:23 | 2018-01-14 14:20 | 57 | 11kV | 57 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 185376 Single phase DOLF : 16 Amp Fuse was weather affected and fatigued still arcing when staff arrived. Excluded OMS 1542120. | January | 2018 | 2018Q3 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-01-14 | N | 57 | N | 9 | N | N | 1.1101 | 39.4971 | 41.6539
[7 empty] | 8466 | 17236 | 1542128 | 2018-01-14 13:38 | 2018-01-14 15:26 | 108 | 11kV | 4050 | 38 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At Zn2466 Flemington Panel 32 "Birnie Parr No.3" feeder tripped Relays: B phase timed OC EFI and F/C Signals: 11kv trip Remarks: UG fault, front line feeder fault from S2466 Flemington Zn panel #32 to S8125 Burnie Parr #3 Sw/A | January | 2018 | 2018Q3 | 2018 | ZN2466:PA32 | ZN2466:PA6 | ZN02466/000006 | CUMBERLAND | UG | Not Veg | 2018-01-14 | N | 106.5789 | N | 9 | N | N | 1.1101 | 39.4971 | 2959.6205
[7 empty] | 7807 | 8798 | 1542942 | 2018-01-14 12:20 | 2018-01-14 16:33 | 253 | 11kV | 63756 | 252 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap Gully" section of 11KV Oh mains near RE44937 Alan st HV bond burnt off Trip & Reclose Pa1 @ Lisarow burnt off bond | January | 2018 | 2018Q3 | 2018 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2018-01-14 | N | 253 | N | 9 | N | N | 1.1101 | 39.4971 | 46591.0043
[7 empty] | 8673 | 19740 | 1542054 | 2018-01-14 12:50 | 2018-01-14 20:15 | 445 | 11kV | 141826 | 1135 | HV | Arcing | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn10990 Arncliffe, 11kv Panel 11 'Dowling Hirst' feeder tripped Relays: Inst A phase timing/lockout field efi S10957 Signals: 11kv trip Remarks: flashover/arcing. HV for PT10242 Gipps Dowling went into LV of S10957 #4 dist due to sagging (poles have moved) | January | 2018 | 2018Q3 | 2018 | ZN10990:PA11 | ZN10998:PA17 | ZN10998/000017 | BAYSIDE | OH | Not Veg | 2018-01-14 | N | 124.9568 | N | 9 | N | N | 1.1101 | 39.4971 | 103642.2576
[7 empty] | 7890 | 9878 | 1543180 | 2018-01-15 00:47 | 2018-01-15 00:58 | 11 | 11kV | 8283 | 753 | HV | Staff Operation | Utility Process Issue | O/H Conductor Unknown | Unplanned | Wind Strong | N | Sect 11KV fdr on Panel 7 (and P23 due to abnormal switching) interrupted by Dop from S35814 Pretoria Pacific No.2 to N/O points and open points per above abnormal switching to all Dop to clsoe Sw/B @ S5063 Valley Rosemead (Haz RMI) Abnormal: LB1079 Open, Sw/B closed @ S5292, AB875 closed, Sw/A open @ S8630 Remarks: to allow Dop to close N/O point on HAZ RMI @ S5063 to allow restoration of Panel 5 after fault on HV UGOH to PT2431 | January | 2018 | 2018Q3 | 2018 | ZN847:PA23 | ZN847:PA23 | ZN00847/000023 | HORNSBY | OH | Not Veg | 2018-01-15 | N | 11 | N | 6 | N | N | 1.1101 | 39.4971 | 6052.9721
[7 empty] | 8113 | 12699 | 1542383 | 2018-01-14 23:16 | 2018-01-15 01:20 | 124 | 11kV | 105652 | 1258 | HV | Animal Possum | Animal | UGOH | Unplanned | Wind Strong | N | At S847 Hornsby 11kv Panel No5 "S2886 Linda George" feeder tripped on: Relays: A phase O/C Signals: see log Field EFi's: nil Abnormal: sw/b closed @ S4446, Sw/A open @ S4254 Remarks: possum on HV UGOH to PT2431 Lisgar Rd. Centre phase UGOH connection blown off. See seperate interruption report for Panel 7 (&23) due to HAZ RMI at S5063 | January | 2018 | 2018Q3 | 2018 | ZN847:PA5 | ZN847:PA5 | ZN00847/000005 | HORNSBY | OH | Not Veg | 2018-01-14 | N | 83.9841 | N | 9 | N | N | 1.1101 | 39.4971 | 77207.3654
[7 empty] | 8387 | 16100 | 1542360 | 2018-01-14 20:50 | 2018-01-15 01:29 | 279 | 11kV | 11296 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 185380 1 fault operation Sensitive Earth Fault Excluded OMS 1542360 | January | 2018 | 2018Q3 | 2018 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2018-01-14 | N | 209.1852 | N | 9 | N | N | 1.1101 | 39.4971 | 8254.7836
[7 empty] | 8481 | 17387 | 1542416 | 2018-01-15 06:45 | 2018-01-15 08:25 | 100 | 11kV | 300 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 185382 Single Phase DOLF : 10 Amp Excluded OMS 1542416 | January | 2018 | 2018Q3 | 2018 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2018-01-15 | N | 100 | N | 6 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 8446 | 16867 | 1542438 | 2018-01-15 08:02 | 2018-01-15 09:10 | 68 | 11kV | 68 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185383 B Phase DOLF : 16 Amp readings 240 volts & 58amps per phase Excluded oms 1542438 | January | 2018 | 2018Q3 | 2018 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Veg | 2018-01-15 | N | 68 | N | 6 | N | N | 1.1101 | 39.4971 | 49.6924
[7 empty] | 8668 | 19682 | 1542642 | 2018-01-15 15:24 | 2018-01-15 21:06 | 342 | 11kV | 262816 | 1252 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2466 Flemington Panel No.5 'Swete st' feeder tripped on Signals: 11kv trip, Tx2 group earth, zone earth Relays: E/F Abnormal: S65220 Birnie Bachell No.5 Sw/A closed, S8580 Birnie Pippita Sw/A open (feeder fault Pa.32) Remarks: UG fault. UG fault between S1922 Martin Raw Sw/B and CP110 Bachell Dalley Sw/A | January | 2018 | 2018Q3 | 2018 | ZN2466:PA5 | ZN2466:PA5 | ZN02466/000005 | CUMBERLAND | UG | Not Veg | 2018-01-15 | N | 209.9169 | N | 6 | N | N | 1.1101 | 39.4971 | 192058.181
[7 empty] | 7460 | 4808 | 1542688 | 2018-01-15 17:48 | 2018-01-15 21:20 | 212.0667 | 11kV | 16753.2667 | 79 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Wind Strong | N | ZN.1673 Turramurra 11kV Ex. Panel 7 " Harrington Ave" feeder at S.4708 Ancona Trentino 11kV HV fuse 40A Ocion B phase Protection Malfunction - LV dist fault grading issue, restored via LV // see DMA ME:1542688 Withdrawn:1542692 | January | 2018 | 2018Q3 | 2018 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | Unknown | Not Veg | 2018-01-15 | N | 212.0667 | N | 6 | N | N | 1.1101 | 39.4971 | 12242.7931
[7 empty] | 7650 | 6818 | 1542771 | 2018-01-16 00:54 | 2018-01-16 02:12 | 78 | 11kV | 62634 | 803 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca Pa41 "Avoca Aux no2" fdr tripped to lock out on: Relays: A & B Phase IOC, reclosing and lockout EFI's: Nil Cause: tree brnach on OH mains. Tree branch removed by DOp outside 13 charles Kay Dr Terrigal See 1542771 ex 1542772,4 | January | 2018 | 2018Q3 | 2018 | ZN12570:PA41 | ZN12570:PA41 | ZN12570/000041 | CENTRAL COAST | OH | Veg | 2018-01-16 | N | 78 | N | 5 | N | N | 1.1101 | 39.4971 | 45771.0798
[7 empty] | 7834 | 9132 | 1542779 | 2018-01-16 03:22 | 2018-01-16 04:14 | 52.4167 | 11kV | 3616.75 | 69 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn36200 Empire Bay section of panel 4 IR63686 Bundaleer Empire Bay 0.2 tripped, reclosed, tripped and locked out on: Relays: Overcurrent Cause: tree branch removed from mains adj PT14608, supply restored See 1542779 ex 1542782 | January | 2018 | 2018Q3 | 2018 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2018-01-16 | N | 52.4167 | N | 5 | N | N | 1.1101 | 39.4971 | 2643.0142
[7 empty] | 7704 | 7490 | 1542761 | 2018-01-15 23:00 | 2018-01-16 13:00 | 840 | 11kV | 97833 | 786 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale pa24 "Burns Rd & Berkeley" fdr tripped and locked out on Relays: 24R panel, timed O/C on A&B phases Signals: Nil EFI's: Nil Cause: Tree/Branch on OH Mains section of 11kv mains required to be patrolled in daylight beyond LB49513 to LB48784 to LB41533 tee PT11510 tee PT14079 restored via LV// See 1543210,1,2,3 ex 1542761,9,76 | January | 2018 | 2018Q3 | 2018 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2018-01-15 | N | 124.4695 | N | 6 | N | N | 1.1101 | 39.4971 | 71493.4708
[7 empty] | 8161 | 13296 | 1542964 | 2018-01-16 12:15 | 2018-01-16 13:45 | 90 | 11kV | 1440 | 16 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 185398 A Phase DOLF : 10 Amp DOLF found broken following SI 24896. - Scott Thoroughgood to investigate previously involvled in planned outage | January | 2018 | 2018Q3 | 2018 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2018-01-16 | N | 90 | N | 5 | N | N | 1.1101 | 39.4971 | 1052.3095
[7 empty] | 7465 | 4939 | 1543048 | 2018-01-16 15:32 | 2018-01-16 17:40 | 128 | 11kV | 128 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 185401 B Phase DOLF : 50 Amp Fuse fatigued Excluded OMS 1543048. | January | 2018 | 2018Q3 | 2018 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2018-01-16 | N | 128 | N | 5 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 7320 | 2540 | 1543066 | 2018-01-16 15:56 | 2018-01-16 18:15 | 139 | 11kV | 278 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 185402 B Phase LLC Burnt off. Fixed under AP. Excluded OMS 1543066 | January | 2018 | 2018Q3 | 2018 | 238:34148 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2018-01-16 | N | 139 | N | 5 | N | N | 1.1101 | 39.4971 | 203.1542
[7 empty] | 7888 | 9834 | 1543083 | 2018-01-17 03:57 | 2018-01-17 04:55 | 58 | 11kV | 150949 | 2616 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn36300 Balgowlah Nth Zone pa8 "Innes Condamine" tripped and locked out on IOC 11kV Trip Cause: not ascertained Large tree branch on wires See 1544495,6 ex 1543083,134,44 | January | 2018 | 2018Q3 | 2018 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Veg | 2018-01-17 | N | 57.7022 | N | 3 | N | N | 1.1101 | 39.4971 | 110309.077
[7 empty] | 8013 | 11265 | 1543365 | 2018-01-17 15:58 | 2018-01-17 23:13 | 435.8167 | 11kV | 14881.9833 | 323 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge Panel 10 "Peats Ridge" fdr tripped on Relays: A & B Phase Overcurrent Signals: 11kv trip Abnormal: Panel 10 & 11 SE/REC was N/A for switching Cause: Large Tree/Branch brought down on OH mains past USL40550 See 1543365,96 CC1: 22-"Refer to SOp" | January | 2018 | 2018Q3 | 2018 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2018-01-17 | N | 46.0743 | N | 3 | N | N | 1.1101 | 39.4971 | 10875.3145
[7 empty] | 8223 | 14037 | 1543476 | 2018-01-17 22:18 | 2018-01-17 23:50 | 92 | 11kV | 368 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 185410 C Phase DOLF : 10 Amp Fatigued fuse Excluded OMS 1543476 | January | 2018 | 2018Q3 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-01-17 | N | 92 | N | 3 | N | N | 1.1101 | 39.4971 | 268.9235
[7 empty] | 8410 | 16505 | 1543777 | 2018-01-18 19:15 | 2018-01-18 23:30 | 255 | 11kV | 59507 | 825 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn12620 Noraville section of Pa11 "Norah Head" RE45054 Noraville no protection operation Cause: Vehicle hit pole with normally closed AB41649 on it. Pole is in need of replacement 2xPT's in LV// See 1544504,5,6,7,8 ex 1543777,91,811,2 | January | 2018 | 2018Q3 | 2018 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2018-01-18 | N | 72.1297 | N | 1 | N | N | 1.1101 | 39.4971 | 43485.9604
[7 empty] | 7830 | 9045 | 1543826 | 2018-01-19 01:42 | 2018-01-19 08:30 | 408 | 11kV | 1632 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of Pa17 PT46384 Ashbrooke Pacific 1.4 centre phase HDO was blown 16Amp Fuse Fatigue See 1544518 ex 1543826,38,45 | January | 2018 | 2018Q3 | 2018 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2018-01-19 | N | 408 | N | 6 | N | N | 1.1101 | 39.4971 | 1192.6175
[7 empty] | 7942 | 10322 | 1543864 | 2018-01-19 10:46 | 2018-01-19 12:30 | 104 | 11kV | 2232 | 30 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 185436 tree branch fell on 11kV OHM near sub 48104/ S.O. open Sw 43321. Excluded oms 1543864 | January | 2018 | 2018Q3 | 2018 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2018-01-19 | N | 74.4 | N | 6 | N | N | 1.1101 | 39.4971 | 1631.0798
[7 empty] | 8026 | 11375 | 1543913 | 2018-01-19 11:52 | 2018-01-19 14:10 | 138 | 11kV | 138 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185441 Single phase DOLF : 10 Amp Excluded OMS 1543913 | January | 2018 | 2018Q3 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2018-01-19 | N | 138 | N | 6 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 7794 | 8676 | 1543953 | 2018-01-19 14:26 | 2018-01-19 15:27 | 61 | 11kV | 1342 | 22 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 185443 section isolated form repair of tie pole GE-50019 causing low hv mains to sub 73213 | January | 2018 | 2018Q3 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2018-01-19 | N | 61 | N | 6 | N | N | 1.1101 | 39.4971 | 980.694
[7 empty] | 7405 | 3886 | 1543962 | 2018-01-19 15:50 | 2018-01-19 16:25 | 35 | 11kV | 9380 | 268 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 185444 interrupt to retire wire on pin at HW-40049 Excluded oms 1543962 | January | 2018 | 2018Q3 | 2018 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2018-01-19 | N | 35 | N | 6 | N | N | 1.1101 | 39.4971 | 6854.6273
[7 empty] | 7543 | 5756 | 1544022 | 2018-01-19 18:44 | 2018-01-19 19:30 | 46 | 11kV | 1012 | 22 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 185446 No protection opertated outage was due to an interruption being required to perform the repairs. Note earlier interruption on lid job 185442, but supply restored until gear arrived to complete repairs. Low 12.7kv conductor near pole GE-50019. | January | 2018 | 2018Q3 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2018-01-19 | N | 46 | N | 6 | N | N | 1.1101 | 39.4971 | 739.5398
[7 empty] | 7880 | 9779 | 1544217 | 2018-01-21 05:47 | 2018-01-21 07:15 | 88 | 11kV | 4708 | 619 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex Zn12660 Woy Woy section of Pa14 "South Woy Woy" PT11667 Taylor Bassan 0.5 roadside 31.5K HVDO operated Cause: Possum foundat base of PT11667 no apparent damage See 1544217 ex 1544219 | January | 2018 | 2018Q3 | 2018 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2018-01-21 | N | 7.6058 | N | 2 | N | N | 1.1101 | 39.4971 | 3440.4675
[7 empty] | 7714 | 7616 | 1544292 | 2018-01-21 20:15 | 2018-01-21 21:15 | 60 | 11kV | 420 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Hot >35C | N | LID 185455 Broken DOLF at sub 71355 Excluded OMS 1544323 | January | 2018 | 2018Q3 | 2018 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2018-01-21 | N | 60 | N | 2 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 8014 | 11275 | 1544417 | 2018-01-22 09:22 | 2018-01-22 10:48 | 86.4667 | 11kV | 86.4667 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185461 C Phase DOLF : 10 Amp Excluded OMS 1544476 | January | 2018 | 2018Q3 | 2018 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2018-01-22 | N | 86.4667 | N | 4 | N | N | 1.1101 | 39.4971 | 63.1873
[7 empty] | 8015 | 11282 | 1544609 | 2018-01-22 00:05 | 2018-01-22 16:32 | 987 | 11kV | 1974 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185468 DOLF : 20 Amp Excluded OMS 1544609 | January | 2018 | 2018Q3 | 2018 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Veg | 2018-01-22 | N | 987 | N | 4 | N | N | 1.1101 | 39.4971 | 1442.541
[7 empty] | 7201 | 459 | 1544691 | 2018-01-22 19:27 | 2018-01-22 20:23 | 56.4167 | 11kV | 7164.9167 | 127 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | LID 185471 C Phase DOLF : 40 Amp Fuse Fatigue Excluded OMS 1544694 | January | 2018 | 2018Q3 | 2018 | 504:48034 | 522:83129 | ZN00522/083129 | CESSNOCK | OH | Not Veg | 2018-01-22 | N | 56.4167 | N | 4 | N | N | 1.1101 | 39.4971 | 5235.9098
[7 empty] | 7971 | 10635 | 1544730 | 2018-01-23 00:52 | 2018-01-23 01:52 | 60 | 11kV | 5700 | 95 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185474 A Phase DOLF : 31 Amp possum on transformer Excluded oms 1544730 & 1544731. | January | 2018 | 2018Q3 | 2018 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Not Veg | 2018-01-23 | N | 60 | N | 7 | N | N | 1.1101 | 39.4971 | 4165.3919
[7 empty] | 7808 | 8804 | 1544723 | 2018-01-22 23:17 | 2018-01-23 09:45 | 628 | 11kV | 63459 | 709 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn14891 Wyong Pa12 "Yarramalong" tripped and locked ou S St Relays: ABC phase OC, reclose and timing, fault check, EFI and Tx2 Fault check Signals: 11kv trip, Zone Earth and Tx2 Group Earth EFI's: S47609 S18485 S18630 S47409 Cause: vehicle hit pole. Section of isolated from AB43742 to AB43930 due to vehicle into pole outside 478 Yarramalong Rd Wyong and wires down. 13xPT's affected in between isolation point AB's EMSO required for HV into LV inspection. DOp isolated PT13242 See 1545170,1,2 ex 1544723,6,9,39 | January | 2018 | 2018Q3 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2018-01-22 | N | 89.5049 | N | 4 | N | N | 1.1101 | 39.4971 | 46373.9655
[7 empty] | 8720 | 20357 | 1544929 | 2018-01-23 14:06 | 2018-01-23 15:35 | 89 | 11kV | 6942 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Insulated | Unplanned | No Weather Impact | N | Ex ZN14891 Wyong section of Pa5 CP45016 Dickson Rec tripped on OC and lockout Cause: tree/branch on OH mains. Pole D04 dooralong | January | 2018 | 2018Q3 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2018-01-23 | N | 89 | N | 7 | N | N | 1.1101 | 39.4971 | 5073.0088
[7 empty] | 7331 | 2727 | 1545012 | 2018-01-23 15:19 | 2018-01-23 18:20 | 180.9833 | 11kV | 1266.8833 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 185490 Burnt off tapping at ABS 75026 Repaired via Live Line technique | January | 2018 | 2018Q3 | 2018 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2018-01-23 | N | 180.9833 | N | 7 | N | N | 1.1101 | 39.4971 | 925.801
[7 empty] | 8302 | 15010 | 1544947 | 2018-01-23 14:39 | 2018-01-23 19:25 | 286 | 11kV | 858 | 3 | HV | 3rd Party Vehicle | 3rd Party Impact | Stay Wire | Unplanned | Hot >35C | N | LID 185492 Truck hit pole. Broken stay wire at sub 51461 Excluded OMS 1544947, 1544961 | January | 2018 | 2018Q3 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-01-23 | N | 286 | N | 7 | N | N | 1.1101 | 39.4971 | 627.0011
[7 empty] | 7625 | 6538 | 1545041 | 2018-01-23 18:53 | 2018-01-23 20:00 | 66.6167 | 11kV | 599.55 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 185493 A Phase DOLF : 16 Amp | January | 2018 | 2018Q3 | 2018 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Veg | 2018-01-23 | N | 66.6167 | N | 7 | N | N | 1.1101 | 39.4971 | 438.1335
[7 empty] | 8577 | 18562 | 1545024 | 2018-01-23 18:11 | 2018-01-23 21:30 | 199 | 11kV | 199 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 185495 Replace blown arrestor Excluded OMS 1545024 | January | 2018 | 2018Q3 | 2018 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Not Veg | 2018-01-23 | N | 199 | N | 7 | N | N | 1.1101 | 39.4971 | 145.4233
[7 empty] | 7353 | 2967 | 1545051 | 2018-01-23 20:59 | 2018-01-23 22:09 | 70 | 11kV | 70 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185496 A Phase DOLF : 10 Amp Excluded OMS 1545051 | January | 2018 | 2018Q3 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2018-01-23 | N | 70 | N | 7 | N | N | 1.1101 | 39.4971 | 51.1539
[7 empty] | 8140 | 13085 | 1545093 | 2018-01-24 06:58 | 2018-01-24 08:24 | 86 | 11kV | 12197 | 142 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn167 Auburn 11kv Pnl 12 "Hunter Braemar" feeder tripped on earth fault. Signals: 11kv trip with zone earth and efi Field EFI's: S48135 Remarks: UG fault. Cable fault between S48135 Hunter Braemar to S2618 Braemar Ave | January | 2018 | 2018Q3 | 2018 | ZN167:PA12 | ZN167:PA12 | ZN00167/000012 | CUMBERLAND | UG | Not Veg | 2018-01-24 | N | 85.8944 | N | 2 | N | N | 1.1101 | 39.4971 | 8913.2078
[7 empty] | 7805 | 8759 | 1545323 | 2018-01-24 21:33 | 2018-01-24 23:01 | 88 | 11kV | 70296 | 825 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1850 Bass Hill Panel No.4 "Carnarvon Heron etc" feeder opened on earth fault, efi, 11kv trip, field efis, S4344-S4343 Remarks: UG fault. Faulty section of 11kv feeder from S4344 Cantrell St Sw/B S4343 Saurine Sw/A | January | 2018 | 2018Q3 | 2018 | ZN1850:PA4 | ZN1850:PA32 | ZN01850/000032 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-01-24 | N | 85.2073 | N | 2 | N | N | 1.1101 | 39.4971 | 51370.2434
[7 empty] | 8565 | 18387 | 1545346 | 2018-01-25 00:59 | 2018-01-25 02:29 | 90 | 11kV | 141480 | 1572 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S874 Concord Panel 4 labelled "Mepunga St" feeder tripped and locked out on: Relays: earth fault, efi Signals: 11kv trip Field EFI's: all field efis to and including sub 65412 Remarks: UG fault. Section 11kv feeder from S65412 Hilly Edwin #2 to S64950 Northcote Hilly #2SWB | January | 2018 | 2018Q3 | 2018 | ZN874:PA4 | ZN874:PA4 | ZN00874/000004 | CANADA BAY | UG | Not Veg | 2018-01-25 | N | 90 | N | 8 | N | N | 1.1101 | 39.4971 | 103389.411
[7 empty] | 8431 | 16724 | 1545379 | 2018-01-25 08:51 | 2018-01-25 09:50 | 59 | 11kV | 124372 | 2108 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Pa13 fdr has tripped on: Signals: 11kv trip Relays: B+C Phase O/C EFI's :Nil ELBS61960: B+C Phase O/C (indication only) Cause: Bond 11kv middle phase tie bond off @ HVpole TE913 (tee off to PT14025. section of Pa13 Long Jetty from LB40272 to S18360swB tee PT14025 PT14025 was already isolated & in LV// for defective surge arrestors See 1545379 ex 1545382,3,4 | January | 2018 | 2018Q3 | 2018 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2018-01-25 | N | 59 | N | 8 | N | N | 1.1101 | 39.4971 | 90887.3892
[7 empty] | 8188 | 13546 | 1546171 | 2018-01-25 01:00 | 2018-01-25 12:35 | 695 | 11kV | 11120 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 185519 B Phase DOLF : 10 Amp no oms. call came straight to ausgrid staff A.Regan | January | 2018 | 2018Q3 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2018-01-25 | N | 695 | N | 8 | N | N | 1.1101 | 39.4971 | 8126.168
[7 empty] | 8595 | 18771 | 1545515 | 2018-01-25 16:20 | 2018-01-25 18:10 | 110 | 11kV | 110 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185529 Single phase DOLF : 10 Amp Excluded OMS 1545515 | January | 2018 | 2018Q3 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2018-01-25 | N | 110 | N | 8 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 7192 | 277 | 1545543 | 2018-01-25 17:33 | 2018-01-25 21:15 | 222 | 11kV | 222 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185532 Single phase DOLF : 10 Amp REplace 2 x 3.15 A with 10A fuses Excluded OMS 1545543 | January | 2018 | 2018Q3 | 2018 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2018-01-25 | N | 222 | N | 8 | N | N | 1.1101 | 39.4971 | 162.2311
[7 empty] | 8116 | 12737 | 1545577 | 2018-01-25 21:26 | 2018-01-25 22:45 | 79.3167 | 11kV | 6186.7 | 78 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa24 PT11950 Pueblo Delmar 11kV HDO footpath side dropout operated 31.5k Possum on lightning arrestor See 1545578 ex 1545577,81,6 CC1: 22-"Refer to SOp" | January | 2018 | 2018Q3 | 2018 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2018-01-25 | N | 79.3167 | N | 8 | N | N | 1.1101 | 39.4971 | 4521.0579
[7 empty] | 7369 | 3298 | 1545530 | 2018-01-25 17:07 | 2018-01-25 23:25 | 378 | 11kV | 378 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185533 Single phase DOLF : Excluded OMS 1545530 | January | 2018 | 2018Q3 | 2018 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2018-01-25 | N | 378 | N | 8 | N | N | 1.1101 | 39.4971 | 276.2313
[7 empty] | 7254 | 1313 | 1545524 | 2018-01-25 16:49 | 2018-01-25 23:35 | 406 | 11kV | 812 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185535 Single phase DOLF : 10 Amp Excluded OMS 1545524 | January | 2018 | 2018Q3 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2018-01-25 | N | 406 | N | 8 | N | N | 1.1101 | 39.4971 | 593.3857
[7 empty] | 8094 | 12332 | 1545604 | 2018-01-26 04:45 | 2018-01-26 06:10 | 85 | 11kV | 20958.25 | 247 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S353 Council St - 11kV CB to "S47625 Donal Birell" tripped. No relay operations, EFI only. Filed EFIs: S47625 S1686 UG cable fault between S1686 (Sw/B ) and S2770 (Sw/A) N/O See 1545604 | January | 2018 | 2018Q3 | 2018 | ZN2602:PA29 | ZN36800:PA39 | ZN36800/000039 | WAVERLEY | UG | Not Veg | 2018-01-26 | N | 84.8512 | N | 5 | N | N | 1.1101 | 39.4971 | 15315.6709
[7 empty] | 7872 | 9609 | 1545662 | 2018-01-26 11:40 | 2018-01-26 14:45 | 185 | 11kV | 65075 | 941 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa13 RE62730 Manns Narara Creek has tripped/reclosed/tripped & locked out on: Relays: OC trip, SEF trip, Lockout Cause: Tree/Branch on OH Mains Tree branch on 11kv between tee off PT13681 & LK44108. 1 Bay of 11kv wires came down on corner of Deane street & Hanlan St S as a result o fault current between 11kv fdr between LK41827 & S63690 Feeder isolated from AB44718 to LK41828 to S63690swA & PT11853 Potential HV into LV. Despatch organising EMSO to inspect See 1547218,9,20,1 ex 1545662,74,9 | January | 2018 | 2018Q3 | 2018 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2018-01-26 | N | 69.1552 | N | 5 | N | N | 1.1101 | 39.4971 | 47554.8906
[7 empty] | 8516 | 17803 | 1545719 | 2018-01-26 18:09 | 2018-01-26 21:10 | 181 | 11kV | 60045 | 633 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9900 Menai - Pnl.2 tripped on: Earth Fault UG cable fault from S9024 (Sw/B) to S9175 (Sw/A) See 1546495 1546498 LV //: 1546496 1546497 | January | 2018 | 2018Q3 | 2018 | ZN9900:PA2 | ZN9900:PA2 | ZN09900/000002 | SUTHERLAND | UG | Not Veg | 2018-01-26 | N | 94.8578 | N | 5 | N | N | 1.1101 | 39.4971 | 43879.115
[7 empty] | 8347 | 15450 | 1545729 | 2018-01-26 18:41 | 2018-01-26 21:20 | 159 | 11kV | 477 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185550 Single phase DOLF : 10 Amp Excluded OMS 1545729 | January | 2018 | 2018Q3 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2018-01-26 | N | 159 | N | 5 | N | N | 1.1101 | 39.4971 | 348.5775
[7 empty] | 7433 | 4304 | 1545800 | 2018-01-27 07:00 | 2018-01-27 07:53 | 53 | 11kV | 17278 | 326 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15014 Mona Vale section of Panel 4 - CP22231 the lane cove walter recloser tripped reclosed tripped and locked out on OC and IOC Cause: Tree branch on OH mains - near PT15577 | January | 2018 | 2018Q3 | 2018 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2018-01-27 | N | 53 | N | 7 | N | N | 1.1101 | 39.4971 | 12626.2528
[7 empty] | 8209 | 13837 | 1545784 | 2018-01-27 12:17 | 2018-01-27 14:50 | 153 | 11kV | 49725 | 325 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | 11kV Bond off after tee off to S4669 Gordon Lansdowne See OMS 1546609 1545853 | January | 2018 | 2018Q3 | 2018 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Not Veg | 2018-01-27 | N | 153 | N | 7 | N | N | 1.1101 | 39.4971 | 36337.5634
[7 empty] | 8216 | 13893 | 1546221 | 2018-01-26 19:43 | 2018-01-27 18:11 | 1348 | 11kV | 1348 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Electrical Storm | N | LID 185549 1 fault operation Overcurrent 2744Amps. o/c . Operating Agreement issed 2100. Fault is on private network. Customer will call Ausgrid when their network is fixed. | January | 2018 | 2018Q3 | 2018 |  |  |  | UPPER HUNTER | Unknown | Not Veg | 2018-01-26 | N | 1348 | N | 5 | N | N | 1.1101 | 39.4971 | 985.0786
[7 empty] | 7822 | 8971 | 1545675 | 2018-01-27 18:39 | 2018-01-27 18:48 | 9 | 11kV | 1503 | 167 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | Section of 11kV feeder from CP24702 switch/5995 interrupted to allow mains to remove tree from HV ABC Supply interrupted to allow mains to remove tree from HV ABC | January | 2018 | 2018Q3 | 2018 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | OH | Veg | 2018-01-27 | N | 9 | N | 7 | N | N | 1.1101 | 39.4971 | 1098.3481
[7 empty] | 7689 | 7229 | 1545903 | 2018-01-27 16:30 | 2018-01-27 19:10 | 160 | 11kV | 4877 | 54 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 185560 1 fault operation Earth Fault L/A's at PT 70289. Excluded OMS 1545903 | January | 2018 | 2018Q3 | 2018 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2018-01-27 | N | 90.3148 | N | 7 | N | N | 1.1101 | 39.4971 | 3563.9678
[7 empty] | 7292 | 2027 | 1545939 | 2018-01-27 18:46 | 2018-01-27 20:30 | 104 | 11kV | 208 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185563 Single phase DOLF : 10 Amp then ungrouped to OMS 1545939. Jobs rolled up but this was an individual sub. Excluded OMS 1545917 | January | 2018 | 2018Q3 | 2018 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2018-01-27 | N | 104 | N | 7 | N | N | 1.1101 | 39.4971 | 152.0003
[7 empty] | 7332 | 2730 | 1545940 | 2018-01-27 18:27 | 2018-01-27 21:00 | 153 | 11kV | 153 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185564 Single phase DOLF : 10 Amp Excluded OMS 1545940 | January | 2018 | 2018Q3 | 2018 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2018-01-27 | N | 153 | N | 7 | N | N | 1.1101 | 39.4971 | 111.8079
[7 empty] | 8357 | 15614 | 1545917 | 2018-01-27 18:27 | 2018-01-27 23:52 | 325 | 11kV | 1300 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 185565 DOLF : 10 Amp 11kV line down going to pole BL-20012. | January | 2018 | 2018Q3 | 2018 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2018-01-27 | N | 325 | N | 7 | N | N | 1.1101 | 39.4971 | 950.0017
[7 empty] | 8619 | 19111 | 1545956 | 2018-01-28 00:02 | 2018-01-28 04:15 | 253 | 11kV | 170313 | 1316 | HV | Arcing | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 46 tripped on SEF Signals: 11kV trip and efi Cause: HV flash over at S5842 New Farm Cherrybrook - Restored via S5842 via LV parallel Anormal Switching: SW/A opened @ S6904, SW/B Closed @S6280, SW/A opened @S5111, SW/A opened @ S5927, SW/B Closed @S5942, SW/A Opened @ S63055 See OMS 1546655 1546658 1545968 1546656 1545956 1545960 1545957 | January | 2018 | 2018Q3 | 2018 | ZN965:PA46 | ZN965:PA46 | ZN00965/000046 | HORNSBY | OH | Not Veg | 2018-01-28 | N | 129.4172 | N | 13 | N | N | 1.1101 | 39.4971 | 124459.717
[7 empty] | 8366 | 15692 | 1546000 | 2018-01-28 08:43 | 2018-01-28 10:08 | 85 | 11kV | 170 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185566 C Phase DOLF : 10 Amp Excluded oms 1546000 | January | 2018 | 2018Q3 | 2018 | 235:2857 | 235:2857 | ZN00235/002857 | MAITLAND | OH | Not Veg | 2018-01-28 | N | 85 | N | 13 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 8672 | 19707 | 1545965 | 2018-01-28 01:19 | 2018-01-28 10:10 | 531 | 11kV | 143003 | 1036 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn14144 Wamberal Pa7 "Forresters Beach" fdr tripped on earth fault Signals: 11kv trip with EFI EFI:S11934 Cause: crossarm broken and HV into LV mains in vicinity of LB42954 See 1547290,2,3 ex 1545965,6,77 | January | 2018 | 2018Q3 | 2018 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Not Veg | 2018-01-28 | N | 138.0338 | N | 13 | N | N | 1.1101 | 39.4971 | 104502.3745
[7 empty] | 8292 | 14887 | 1546055 | 2018-01-28 13:51 | 2018-01-28 14:21 | 30 | 11kV | 583 | 119 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa11 "Somersby" fdr RE46803 Wise Ferry Dog Trap 0. tripped @13:51:39:501 & reclosed on: Relays: OC Trip, IOC Trip RE44938 Somersby tripped @13:51:37:419 reclosed, tripped, reclosed, tripped & locked out on Relays: OC trip, Lockout Cause: Tree branch on 11kv OH near PT13360 Haycolec Auto link 48652 failed to operate to clear fault??? See 1547298,9 ex 1546055 | January | 2018 | 2018Q3 | 2018 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2018-01-28 | N | 4.8992 | N | 13 | N | N | 1.1101 | 39.4971 | 426.0392
[7 empty] | 8361 | 15668 | 1546065 | 2018-01-28 14:54 | 2018-01-28 15:30 | 36 | 11kV | 108 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185572 C Phase DOLF : 10 Amp Excluded OMS 1546065 | January | 2018 | 2018Q3 | 2018 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2018-01-28 | N | 36 | N | 13 | N | N | 1.1101 | 39.4971 | 78.9232
[7 empty] | 8628 | 19234 | 1546086 | 2018-01-28 15:39 | 2018-01-28 17:05 | 86 | 11kV | 86 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185575 C Phase DOLF : 10 Amp Not sub 43185 Excluded OMS 1546086. | January | 2018 | 2018Q3 | 2018 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2018-01-28 | N | 86 | N | 13 | N | N | 1.1101 | 39.4971 | 62.8463
[7 empty] | 7441 | 4540 | 1546064 | 2018-01-28 14:55 | 2018-01-28 17:25 | 150 | 11kV | 150 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 185576 Single phase DOLF : 10 AMP 1 LA replaced. Excluded OMS 1546064. | January | 2018 | 2018Q3 | 2018 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2018-01-28 | N | 150 | N | 13 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 8573 | 18503 | 1546069 | 2018-01-28 14:58 | 2018-01-28 17:50 | 172 | 11kV | 172 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185578 DOLF : 10 Amp Excluded OMS 1546069 | January | 2018 | 2018Q3 | 2018 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2018-01-28 | N | 172 | N | 13 | N | N | 1.1101 | 39.4971 | 125.6925
[7 empty] | 7852 | 9347 | 1546076 | 2018-01-28 15:58 | 2018-01-28 17:50 | 112 | 11kV | 112 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185580 DOLF : 10 Amp Excluded OMS 1546076 | January | 2018 | 2018Q3 | 2018 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2018-01-28 | N | 112 | N | 13 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 8065 | 12006 | 1546102 | 2018-01-28 18:50 | 2018-01-28 19:30 | 40 | 11kV | 280 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185584 DOLF : 10 Amp Excluded OMS 1546102 | January | 2018 | 2018Q3 | 2018 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Veg | 2018-01-28 | N | 40 | N | 13 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 7359 | 3087 | 1546104 | 2018-01-28 19:09 | 2018-01-28 20:05 | 56 | 11kV | 56 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185585 Single phase DOLF : 10 Amp Excluded OMS 1546104 | January | 2018 | 2018Q3 | 2018 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2018-01-28 | N | 56 | N | 13 | N | N | 1.1101 | 39.4971 | 40.9231
[7 empty] | 7736 | 7856 | 1546096 | 2018-01-28 18:33 | 2018-01-28 21:35 | 182 | 11kV | 364 | 2 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185587 HV CONNECTION TO ONE 11kV BUSHING ON TX HAD BURNT OFF. Excluded OMS 1546096. | January | 2018 | 2018Q3 | 2018 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2018-01-28 | N | 182 | N | 13 | N | N | 1.1101 | 39.4971 | 266.0005
[7 empty] | 8163 | 13300 | 1546105 | 2018-01-28 19:22 | 2018-01-28 21:45 | 143 | 11kV | 143 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185588 DOLF : 10 Amp Sub was sub 71394 not 70832 but both subs are in same location. 3.15 amp HV fuses replaced with 10A fuses. Excluded OMS 1546105 . | January | 2018 | 2018Q3 | 2018 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2018-01-28 | N | 143 | N | 13 | N | N | 1.1101 | 39.4971 | 104.5002
[7 empty] | 7863 | 9442 | 1546141 | 2018-01-29 06:10 | 2018-01-29 08:30 | 140 | 11kV | 4480 | 32 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185590 A Phase Fuse: 10 Amp Substation DOLF Issued to DOP Aphase 10A DOLF blown, possum found at base of pole | January | 2018 | 2018Q3 | 2018 | 221:11898 | 220:8687 | ZN00220/008687 | LAKE MACQUARIE | OH | Not Veg | 2018-01-29 | N | 140 | N | 3 | N | N | 1.1101 | 39.4971 | 3273.8519
[7 empty] | 7817 | 8899 | 1546295 | 2018-01-29 12:11 | 2018-01-29 14:23 | 132 | 11kV | 264 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 185594 A Phase Fuse 10 Amp, Substation DOLF No cause found, not storm conditions | January | 2018 | 2018Q3 | 2018 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2018-01-29 | N | 132 | N | 3 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 7729 | 7788 | 1546437 | 2018-01-29 21:21 | 2018-01-29 22:22 | 61 | 11kV | 227781 | 3735 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At Zn15006 Dee Why West Panel 12L Tripped on Relays: Left side Timed OC A and C phase, Fault Check and EFI Signals: 11kV Trip, Zone Earth and Group Earth. Cause: Possum at the base of UGOH pole near the corner of Northcott and Macquarie St. See OMS 1546437 1546439 1546441 | January | 2018 | 2018Q3 | 2018 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Not Veg | 2018-01-29 | N | 60.9855 | N | 3 | N | N | 1.1101 | 39.4971 | 166455.6364
[7 empty] | 8610 | 18983 | 1546479 | 2018-01-30 08:05 | 2018-01-30 09:37 | 92 | 11kV | 179328 | 2046 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly Pnl.15 tripped on: Inst Earth leakage Field EFIs: S46310 S47004 S47823 S2538 UG cable fault from S2538 (Sw/B) to S4227 (Sw/A) See 1546642 1546643 | January | 2018 | 2018Q3 | 2018 | ZN2602:PA15 | ZN36800:PA40 | ZN36800/000040 | RANDWICK | UG | Not Veg | 2018-01-30 | N | 87.6481 | N | 4 | N | N | 1.1101 | 39.4971 | 131047.6131
[7 empty] | 7977 | 10732 | 1546591 | 2018-01-30 12:47 | 2018-01-30 14:09 | 82 | 11kV | 151044 | 1842 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3472 Sefton - Pnl.33 tripped on: Earth Fault UG cable fault. Front line section to S2771 (Sw/A) | January | 2018 | 2018Q3 | 2018 | ZN3472:PA33 | ZN3472:PA33 | ZN03472/000033 | CUMBERLAND | UG | Not Veg | 2018-01-30 | N | 82 | N | 4 | N | N | 1.1101 | 39.4971 | 110378.5002
[7 empty] | 8308 | 15052 | 1546558 | 2018-01-30 09:23 | 2018-01-30 14:32 | 309 | 11kV | 39430 | 870 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 185604 1 Fault operation, B & C Phase Overcurrent Cross arm down at IR - 42296 | January | 2018 | 2018Q3 | 2018 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2018-01-30 | N | 45.3218 | N | 4 | N | N | 1.1101 | 39.4971 | 28814.281
[7 empty] | 7653 | 6852 | 1546751 | 2018-01-30 21:59 | 2018-01-31 01:00 | 181 | 11kV | 43584 | 1029 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S1193 Lindfield Panel 21 trippd and reclosed on B and C phase overcurrent EFI and 11kV trip. Tripped and reclosed on B and C phase Overcurrent Cause NOt ascertained At S46543 Eton Pacific 400A fuse blown on B phase of distributor 4 At S46326 Ortona Bayswater 400A fuse blown on B phase of distributor 4 At S3420 Pacific Shirley 400A fuse blown on B and C phase of distributor 2 At S3420 Pacific Shirley 400A based on customer calls, assumed supply lost ofdistributor 1. Cause: In LV parallel with feeder See OMS 1547383 1547529 1547530 1546756 1547384 1546752/754/758/761/751/757/764/753/760/762 | January | 2018 | 2018Q3 | 2018 | ZN1193:PA15 | ZN1193:PA15 | ZN01193/000015 | KU-RING-GAI | OH | Veg | 2018-01-30 | N | 42.3557 | N | 4 | N | N | 1.1101 | 39.4971 | 31849.9017
[7 empty] | 7286 | 1971 | 1546869 | 2018-01-31 04:00 | 2018-01-31 05:30 | 90 | 11kV | 9990 | 111 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 185611 A phase Fuse size 31 Amp Possum | January | 2018 | 2018Q3 | 2018 | 239:82132 | 239:82132 | ZN00239/082132 | LAKE MACQUARIE | OH | Not Veg | 2018-01-31 | N | 90 | N | 8 | N | N | 1.1101 | 39.4971 | 7300.3973
[7 empty] | 8040 | 11541 | 1546915 | 2018-01-31 05:47 | 2018-01-31 07:01 | 74 | 11kV | 88874 | 1201 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP62774 Kentwall Pittwater tripped, reclosed, tripped and locked out on B and C phase overcurrent, Lockout Signals: Nil Cause: Bark on mains was removed by DOp near PT15781 | January | 2018 | 2018Q3 | 2018 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Veg | 2018-01-31 | N | 74 | N | 8 | N | N | 1.1101 | 39.4971 | 64946.4979
[7 empty] | 8131 | 12990 | 1546898 | 2018-01-31 05:25 | 2018-01-31 07:40 | 135 | 11kV | 284162 | 2272 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | Zn12640 Umina Pa12 "Oscar West" fdr tripped Relays- Band C Phase IOC, Earth Fault check Signals: 11kv trip Abnormal: AB415767 open LB42267 closed Cause: Lightning/SUrge Arresotr failed at first UGOH beyond LB40719 See 1547595,6,7,8 exclude 1546898 | January | 2018 | 2018Q3 | 2018 | ZN12640:PA12 | ZN12640:PA12 | ZN12640/000012 | CENTRAL COAST | OH | Not Veg | 2018-01-31 | N | 125.0713 | N | 8 | N | N | 1.1101 | 39.4971 | 207657.2082
[7 empty] | 7891 | 9895 | 1547194 | 2018-01-31 09:57 | 2018-01-31 11:15 | 78 | 11kV | 20406 | 322 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1610 Homebush Bay - Pnl.13 tripped on: Earth Fault Field EFIs: S6662 UG cable fault. Front line section from Pnl.13 to S6648, S7637 & S3481 | January | 2018 | 2018Q3 | 2018 | ZN1610:PA13 | ZN1610:PA13 | ZN01610/000013 | PARRAMATTA | UG | Not Veg | 2018-01-31 | N | 63.3727 | N | 8 | N | N | 1.1101 | 39.4971 | 14912.1029
[7 empty] | 7878 | 9711 | 1546880 | 2018-01-31 04:51 | 2018-01-31 11:35 | 404 | 11kV | 318930 | 2822 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Lightning | N | LID 185618 1 Fault operations Fuse size 63 Amp Instantaneous Overcurrent, Earth Fault, substation DOLF 33kV crossarm failure at Pole JV-40003 caused 33kV into 11kV OHM LA and C phase DOLF also replaced at sub 64265 | January | 2018 | 2018Q3 | 2018 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2018-01-31 | N | 113.0156 | N | 8 | N | N | 1.1101 | 39.4971 | 233064.6372
[7 empty] | 7422 | 4110 | 1547306 | 2018-01-31 13:23 | 2018-01-31 14:30 | 67 | 11kV | 332 | 5 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington - Pnl.4 tripped on, O/C & E/F Contractor hit cable in Murray Rose Ave. Fault located outside S4802. | January | 2018 | 2018Q3 | 2018 | ZN2466:PA4 | ZN36000:PA6 | ZN36000/000006 | PARRAMATTA | UG | Not Veg | 2018-01-31 | N | 66.4 | N | 8 | N | N | 1.1101 | 39.4971 | 242.6158
[7 empty] | 8671 | 19706 | 1547427 | 2018-01-31 17:09 | 2018-01-31 20:45 | 216 | 11kV | 155868 | 1518 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35500 Macquarie Park Panel 4 tripped on Signals: 11kv Trip, relays: B phase Time OC and EFI Abnormal Switching: AB1116 Open, LB1276 (Defective) Cause: Tree branch on OH mains Large Tree branch on 11kV tee to PT2414 Finch Cilento See OMS 1547996 1547997 1547998 1547427/29/38/42 | January | 2018 | 2018Q3 | 2018 | ZN8000:PA4 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Veg | 2018-01-31 | N | 102.6798 | N | 8 | N | N | 1.1101 | 39.4971 | 113903.7371
[7 empty] | 8388 | 16124 | 1546954 | 2018-01-31 05:55 | 2018-01-31 22:25 | 990 | 11kV | 147272 | 846 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Previous Storm | N | LID 185631 2 Fault Operations, Pole Fire SW-80210 | January | 2018 | 2018Q3 | 2018 | 223:14398 | 223:14398 | ZN00223/014398 | LAKE MACQUARIE | OH | Not Veg | 2018-01-31 | N | 174.0804 | N | 8 | N | N | 1.1101 | 39.4971 | 107622.0338
[7 empty] | 7371 | 3385 | 1547524 | 2018-02-01 09:03 | 2018-02-01 11:00 | 117 | 11kV | 78934 | 846 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 185641 Earth Fault Blown tappings and arrestors at UGOH Pole SW-80134 also refer to OMS 1547524 | February | 2018 | 2018Q3 | 2018 | 223:14398 | 223:14398 | ZN00223/014398 | LAKE MACQUARIE | OH | Not Veg | 2018-02-01 | N | 93.3026 | N | 4 | N | N | 1.1101 | 39.4971 | 57682.639
[7 empty] | 7509 | 5496 | 1547571 | 2018-02-01 11:16 | 2018-02-01 12:35 | 79 | 11kV | 119104 | 1508 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.15 tripped, relcosed, tripped & locked out on: IOC A & B phase Field EFIs: S10267. EFI @ S10863 appeared to have operated. UG cable hit by contractor outside 21 Garden St, Kogarah. Between S10267 and S10863. See 1547981 1547982 | February | 2018 | 2018Q3 | 2018 | ZN10999:PA15 | ZN10999:PA15 | ZN10999/000015 | BAYSIDE | UG | Not Veg | 2018-02-01 | N | 78.9814 | N | 4 | N | N | 1.1101 | 39.4971 | 87037.6902
[7 empty] | 8192 | 13626 | 1547626 | 2018-02-01 14:18 | 2018-02-01 16:00 | 102 | 11kV | 106206 | 1063 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 47 tripped, reclosed tripped and locked out on A and Cphase IOC, EFI, Fault Check Recloser Timing and Lockout Caus not ascertained for outage See OMS 1548086 1548089 1547626 | February | 2018 | 2018Q3 | 2018 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Veg | 2018-02-01 | N | 99.9116 | N | 4 | N | N | 1.1101 | 39.4971 | 77612.2123
[7 empty] | 7773 | 8375 | 1547728 | 2018-02-01 20:34 | 2018-02-01 22:02 | 88 | 11kV | 136956 | 1824 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12650 West Gosford Panel 13 "Hanlan St" fdr tripped, reclosed and locked out on: Relays: ABC phase OC, Lockout, Timing Signals: 11kv trip PT11117 HDO's operated A&B phases 31.5amp fuses replaced Abnormal: S12073 SwA and SwD amp are open. see DMA Cause: Branch on top of HDO's at PT11117 See 1547988,9 ex 1547728 | February | 2018 | 2018Q3 | 2018 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2018-02-01 | N | 75.0855 | N | 4 | N | N | 1.1101 | 39.4971 | 100083.4053
[7 empty] | 8477 | 17374 | 1547851 | 2018-02-02 01:56 | 2018-02-02 05:28 | 212 | 11kV | 43537 | 282 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14144 Wamberal Pa5 "Beufort Blue View" tripped and reclosed Relays: A&B Phse O/C, lockout Signals: 11kv trip Cause: Tree/Branch on OH mains Tree on mains @ PT12277 AB44638 two phases open bond on load side of AB See seperate interruption on Pa4 trip and reclose See 1548746,7 ex 1547851,75 | February | 2018 | 2018Q3 | 2018 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2018-02-02 | N | 154.3865 | N | 4 | N | N | 1.1101 | 39.4971 | 31815.5555
[7 empty] | 7290 | 2002 | 1547832 | 2018-02-02 | 2018-02-02 09:20 | 560 | 11kV | 188670 | 1770 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn12570 Avoca Panel 24 "Woodfield Waldron" tripped on Relays: O/C B & C Phase, SEF, lock out & EFI Signals: 11kv trip LB77911 O/C B & C Phase and SEF detected See 1548752,4,5 ex 1547832,47 | February | 2018 | 2018Q3 | 2018 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2018-02-02 | N | 106.5932 | N | 4 | N | N | 1.1101 | 39.4971 | 137874.4712
[7 empty] | 7819 | 8928 | 1547941 | 2018-02-02 09:02 | 2018-02-02 12:05 | 183 | 11kV | 366 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 185649 A and B Phases DOLF No cause found, not storm conditions also see OMS 154791 | February | 2018 | 2018Q3 | 2018 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2018-02-02 | N | 183 | N | 4 | N | N | 1.1101 | 39.4971 | 267.462
[7 empty] | 7478 | 5037 | 1548138 | 2018-02-02 15:24 | 2018-02-02 18:16 | 172 | 11kV | 16512 | 96 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 185654 2 Fault operations, Earth Fault HV Reported down, OHM down between poles DM-60087 and DM-60086 | February | 2018 | 2018Q3 | 2018 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2018-02-02 | N | 172 | N | 4 | N | N | 1.1101 | 39.4971 | 12066.4826
[7 empty] | 8596 | 18775 | 1548351 | 2018-02-03 06:30 | 2018-02-03 09:00 | 150 | 11kV | 140027 | 1152 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn15008 Harbord Paenl 5 "Queenscliff" fdr tripped Signals: Zone Earth, 11kv trip Relays: Timed OC, EFC, EFI, Timer, Lockout EFI's: as expected Cause: UGOH fault short circuit 11kV UGOH (older cast type) located electrically between S65754:D & LB63712 tee PT1565, appears to have failed LV//'s15357 29206 See 1548770,1,2 ex 1548329,51 | February | 2018 | 2018Q3 | 2018 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | Unknown | Unknown | 2018-02-03 | N | 121.5512 | N | 4 | N | N | 1.1101 | 39.4971 | 102327.6015
[7 empty] | 8499 | 17616 | 1548356 | 2018-02-03 07:36 | 2018-02-03 15:05 | 449.1 | 11kV | 35478.9 | 79 | HV | Vegetation Blow/Fall In | Vegetation | Fuse Assembly | Unplanned | No Weather Impact | N | At PT2032 Alston Turner footpath side and centre phase HDOs have blown Cause: tree branch has hit near pt causing footpath side dropper to fall off and hit transformer causing damage to the roadside 11kV TX bushing See OMS 1548356 1548358 | February | 2018 | 2018Q3 | 2018 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2018-02-03 | N | 449.1 | N | 4 | N | N | 1.1101 | 39.4971 | 25926.9337
[7 empty] | 8460 | 17142 | 1548481 | 2018-02-03 14:09 | 2018-02-03 19:00 | 291 | 11kV | 3424 | 105 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 185657 1 Fault operations HV Reported down, tree @ sub 64757 Note: Feeder abnormal ABS 2140 closed, ABS 43397 open | February | 2018 | 2018Q3 | 2018 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2018-02-03 | N | 32.6095 | N | 4 | N | N | 1.1101 | 39.4971 | 2502.1582
[7 empty] | 7284 | 1943 | 1548550 | 2018-02-03 21:07 | 2018-02-03 23:24 | 136.4667 | 11kV | 48582.1333 | 356 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Ex Zn15014 Mona Vale section of Pa12 "Minmai Rd" CP24701 Scotland Island Sw6000 tripped 80Amp OQFRN HV fuse replaced See 1548550 ex 1548558,9,60 CC1: 22-"Refer to SOp" | February | 2018 | 2018Q3 | 2018 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | Unknown | Unknown | 2018-02-03 | N | 136.4667 | N | 4 | N | N | 1.1101 | 39.4971 | 35502.3901
[7 empty] | 8017 | 11296 | 1548573 | 2018-02-04 00:36 | 2018-02-04 01:50 | 74 | 11kV | 7918 | 107 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 185661 B and C Phase 50 Amp fuse Possum on transformer | February | 2018 | 2018Q3 | 2018 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2018-02-04 | N | 74 | N | 3 | N | N | 1.1101 | 39.4971 | 5786.2409
[7 empty] | 8609 | 18968 | 1548595 | 2018-02-04 07:30 | 2018-02-04 08:55 | 85 | 11kV | 255 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 185666 A Phase Substation DOLF, Failure also see OMS 1548595 and 1548596 | February | 2018 | 2018Q3 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2018-02-04 | N | 85 | N | 3 | N | N | 1.1101 | 39.4971 | 186.3465
[7 empty] | 8411 | 16508 | 1548591 | 2018-02-04 07:59 | 2018-02-04 10:50 | 171 | 11kV | 1539 | 9 | HV | Animal Possum | Animal | Fuse Assembly | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa8 "Kulnura" PT14542 Finns Greta 0.4 Roadside HDO operated 16Amp Cause: Possum found at base of pole See 1548780 ex 1548591,613 | February | 2018 | 2018Q3 | 2018 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2018-02-04 | N | 171 | N | 3 | N | N | 1.1101 | 39.4971 | 1124.6558
[7 empty] | 7382 | 3622 | 1548973 | 2018-02-05 05:17 | 2018-02-05 05:21 | 4 | 11kV | 23500 | 5875 | HV | Staff Operation | Utility Process Issue | Circuit Breaker | Unplanned | No Weather Impact | N | LID 185668, 185669, 185670, 185673, 185674 Staff Error (Operating) Switching Error SI 25529 | February | 2018 | 2018Q3 | 2018 | 256:80647 | 256:80647 | ZN00256/080647 | NEWCASTLE | Unknown | Not Veg | 2018-02-05 | N | 4 | N | 7 | N | N | 1.1101 | 39.4971 | 17173.1069
[7 empty] | 8253 | 14445 | 1549021 | 2018-02-05 09:31 | 2018-02-05 09:36 | 5 | 11kV | 4360 | 872 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 185675 1 Fault operations, Earth Fault Truck hit pole JU-10947. Trip and Reclose (refer to OMS 1548723), then received report from AG employee of a truck hiting a pole, pole leaning and OHM hanging low cnr of Croudace Rd and Newcastle Rd, trip & reclose on Fdr. De-energised feeder @ 09:31 for safety until DOp confirmed it is a street light pole. Made safe | February | 2018 | 2018Q3 | 2018 | 210:83474 | 210:83474 | ZN00210/083474 | NEWCASTLE | OH | Not Veg | 2018-02-05 | N | 5 | N | 7 | N | N | 1.1101 | 39.4971 | 3186.1594
[7 empty] | 7287 | 1984 | 1548834 | 2018-02-05 14:19 | 2018-02-05 15:59 | 100 | 11kV | 200 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Broken live line clamp/connection | February | 2018 | 2018Q3 | 2018 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2018-02-05 | N | 100 | N | 7 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 7618 | 6459 | 1548843 | 2018-02-05 14:51 | 2018-02-05 16:02 | 70.9167 | 11kV | 47230.5 | 666 | HV | Excavation 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12650 West Gosford Panel 14 "Kirriong Erina St" fdr tripped, reclosed and lcoked out Relays: On the Erina St fdr - Earth Fault, EFI, Timing and Reclose Relay Signals: 11kv trip EFI's S65693 Cause: Vehicle Hit mains. Crane hit 11kv Mains ouitside 18-22 Kendall st Gosford See 1548843 ex 1548846 | February | 2018 | 2018Q3 | 2018 | ZN12650:PA14 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | UG | Not Veg | 2018-02-05 | N | 70.9167 | N | 7 | N | N | 1.1101 | 39.4971 | 34514.6563
[7 empty] | 7442 | 4558 | 1548893 | 2018-02-05 17:00 | 2018-02-05 18:30 | 90 | 11kV | 99531 | 1311 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn14891 Wyong Pa9 Amy Pacific" fdr tripped, reclosed and locked out Relays: Earth Fault, ABC phase IOC, EFI, Fault Check (TX1 Panel) Signals: 11kv trip, No1 Group Earth EFI:S S18620 S14753 Cause: UGOH Fault Short Circuit Fault on UGOH between S14753 to AB44463 tee PT14364 See 1549012,3,4,5 ex 1548892,3 | February | 2018 | 2018Q3 | 2018 | ZN14891:PA9 | ZN14891:PA9 | ZN14891/000009 | CENTRAL COAST | Unknown | Unknown | 2018-02-05 | N | 75.9199 | N | 7 | N | N | 1.1101 | 39.4971 | 72734.3191
[7 empty] | 8298 | 14982 | 1548921 | 2018-02-05 18:40 | 2018-02-05 23:00 | 260 | 11kV | 5036 | 58 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa13L "Peats Ridge Aux" RE46763 Grants Keighley 0.3W tripped, reclosed and locked out on IOC and Timed O/C Cause: Tree BRanch clipped 11kv mains and brought down stay wire See 1549007,8 ex 1548907,21 | February | 2018 | 2018Q3 | 2018 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2018-02-05 | N | 86.8276 | N | 7 | N | N | 1.1101 | 39.4971 | 3680.1603
[7 empty] | 7494 | 5218 | 1548934 | 2018-02-05 22:33 | 2018-02-06 00:40 | 127 | 11kV | 52295 | 495 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 185686 3Fault operations Earth Fault UG Fault FDR 82000 | February | 2018 | 2018Q3 | 2018 | 257:82000 | 257:82000 | ZN00257/082000 | NEWCASTLE | UG | Not Veg | 2018-02-05 | N | 105.6465 | N | 7 | N | N | 1.1101 | 39.4971 | 38215.6436
[7 empty] | 8454 | 17034 | 1548938 | 2018-02-06 01:14 | 2018-02-06 10:25 | 551 | 11kV | 1102 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 185692 Live Line lead broke Please have crew attend and replace ABB H.V. fuse assembly on PT sub 50513. The top contact on fuse assembly has broken off. Both H.V and L.V. fuses have been open removed and danger tagged. Good access for EWP. Top of dolf broke off with live line lead. replace both dolfs and reattach leads | February | 2018 | 2018Q3 | 2018 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2018-02-06 | N | 551 | N | 2 | N | N | 1.1101 | 39.4971 | 805.3091
[7 empty] | 8098 | 12434 | 1549000 | 2018-02-06 11:01 | 2018-02-06 12:09 | 68 | 11kV | 2788 | 41 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn15001 Brookvale Panel 16 has tripped on Signals: 11kV trip Relays: Basler Relay - 51N(Earth Fault), EFI, Fault Check Cause: 11kV UG feeder fault. Feeder isolated and earthed from S49078 to S16693 See OMS 1549149 1549150 1549000 | February | 2018 | 2018Q3 | 2018 | ZN15001:PA16 | ZN15001:PA16 | ZN15001/000016 | NORTHERN BEACHES | UG | Not Veg | 2018-02-06 | N | 68 | N | 2 | N | N | 1.1101 | 39.4971 | 2037.3882
[7 empty] | 8371 | 15818 | 1549151 | 2018-02-07 08:46 | 2018-02-07 09:40 | 54 | 11kV | 702 | 13 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 185706 B and C Fuse 10 Amp, substation DOLF Bird contacted mains blowing the fuses Customer heard an explosion - cockatoo has shortcircuited the transformer which is on the pole outside property this has resulted in no power. cockatoo on the ground | February | 2018 | 2018Q3 | 2018 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2018-02-07 | N | 54 | N | 6 | N | N | 1.1101 | 39.4971 | 513.0009
[7 empty] | 7769 | 8325 | 1549141 | 2018-02-07 07:06 | 2018-02-07 10:44 | 218 | 11kV | 436 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 185707 A Phase HV LLC Dropper lead open circuited Cable has snapped off line side on live line clamp at PT62513 (Freeman). On ok from SOp, opened HV & LV fuses and warning tagged. | February | 2018 | 2018Q3 | 2018 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2018-02-07 | N | 218 | N | 6 | N | N | 1.1101 | 39.4971 | 318.6159
[7 empty] | 7443 | 4574 | 1549230 | 2018-02-07 12:17 | 2018-02-07 13:10 | 53 | 11kV | 53 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 185711 A Phase 10 Amp substation DOLF also see OMS 1549230 Dave advised sub that actually had blown dolf and the sub reported by mistake are on the same property | February | 2018 | 2018Q3 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2018-02-07 | N | 53 | N | 6 | N | N | 1.1101 | 39.4971 | 38.7308
[7 empty] | 7783 | 8487 | 1549227 | 2018-02-07 12:12 | 2018-02-07 15:40 | 208 | 11kV | 156468 | 1713 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12650 West Gosford Pa1 "Dog Trap Rd" tripped on Relays: SEF, Timed O/C A & B phase and EFI Signals: 11kv trip Cause: OH Down. THree Bays of OH fdr on the ground beyond AB43611 See 1549423,4 ex 1549227,42,57 | February | 2018 | 2018Q3 | 2018 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2018-02-07 | N | 91.3415 | N | 6 | N | N | 1.1101 | 39.4971 | 114342.1994
[7 empty] | 7948 | 10357 | 1549265 | 2018-02-07 14:05 | 2018-02-07 17:00 | 175 | 11kV | 367075 | 2922 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Sub 35800 Bankstown Zn Panel #2 labelled Rossmore Ave tripped on earth fault, EFI, ZE and GE, 11kv trip Remarks: UG fault. Section of 11kv feeder from S278 Rossmore to S2786 Hillcrest arthur to S2105 Bonds Cant tee to S3244 Charlescotte Christian | February | 2018 | 2018Q3 | 2018 | ZN35800:PA2 | ZN35800:PA2 | ZN35800/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-02-07 | N | 125.6246 | N | 6 | N | N | 1.1101 | 39.4971 | 268247.5831
[7 empty] | 7846 | 9317 | 1549279 | 2018-02-07 20:00 | 2018-02-07 20:40 | 40 | 11kV | 120 | 3 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Tap Changer | Unplanned | No Weather Impact | N | LID 185715 Tap dropped from Tap 8 to Tap 4 Actual address 120 Giribil track Buckety.Volts at arrival A-N =259.9. F/L A-N = 0.09 ohms. A-E = 1.9 ohms. current split active =15.1A. N= 15A. earth =0.01A. Tx supplying 3 house, superintendant advised to leave customer on, tap change required. Spoke to customer on phone, new solar install today & found high volts & isolated solar system, customer advised multiple appliances have stop working over the years after only having them for a short time, advised customer he would have to bring that up with the claims department, provided customer with the claims number | February | 2018 | 2018Q3 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | Unknown | Not Veg | 2018-02-07 | N | 40 | N | 6 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 8518 | 17810 | 1549398 | 2018-02-08 08:40 | 2018-02-08 10:32 | 112 | 11kV | 5208 | 69 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.22 tripped on: Earth Fault Field EFIs: S3696 UG cable fault from S35664 (Sw/B) to S5152 (Sw/A) NOTE: EFI @ S35664 did not operate again. Previous DMA reported 21/4/17. See 1549665 1549666 1549667 | February | 2018 | 2018Q3 | 2018 | ZN188:PA22 | ZN188:PA22 | ZN00188/000022 | SYDNEY | UG | Not Veg | 2018-02-08 | N | 75.4783 | N | 4 | N | N | 1.1101 | 39.4971 | 3805.8528
[7 empty] | 8157 | 13242 | 1549386 | 2018-02-08 08:21 | 2018-02-08 12:08 | 227 | 11kV | 72974 | 822 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 185724 1 fault operation Sensitive Earth Fault ABS 74212 did not open fully as part of planned switching 25733. Sw 46641 tripped at the same time, section of feeder was patrolled & went back into service. Excluded OMS 1549386, 1549387, 1549402 ## | February | 2018 | 2018Q3 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2018-02-08 | N | 88.7762 | N | 4 | N | N | 1.1101 | 39.4971 | 53327.2468
[7 empty] | 7207 | 498 | 1549435 | 2018-02-08 10:25 | 2018-02-08 13:10 | 165 | 11kV | 165 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185725 C Phase DOLF : 10 Amp Excluded OMS 1549435 | February | 2018 | 2018Q3 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2018-02-08 | N | 165 | N | 4 | N | N | 1.1101 | 39.4971 | 120.5771
[7 empty] | 7827 | 9019 | 1549446 | 2018-02-08 10:47 | 2018-02-08 15:40 | 293 | 11kV | 57923 | 2737 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn9035 Caringbah - Pnl.4 tripped and reclosed on: Pnl.4L O/C, E/F with EFI Field EFIs: S9082 S9418 S9315 S9338 S9524 S9552 S9283 Abnormal: Sw/B @ S63370 Closed with Pnl.2 Open UGOH Fault located between S9283 and AB35309 See 1549658 1549659 1549660 | February | 2018 | 2018Q3 | 2018 | ZN9035:PA4 | ZN9035:PA4 | ZN09035/000004 | SUTHERLAND | Unknown | Unknown | 2018-02-08 | N | 21.163 | N | 4 | N | N | 1.1101 | 39.4971 | 42328.42
[7 empty] | 8070 | 12086 | 1539873 | 2018-01-08 18:34 | 2018-02-09 12:45 | 45731.4667 | 11kV | 82952 | 76 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | Ex Zn13000 Lake Mummorah section o fPa2 PT11314 Queens Anita 11kV centre phase 31.5Amp drop out fuse operated Cause: not ascertained Storm at time of interruption | January | 2018 | 2018Q3 | 2018 | ZN13000:PA2 | ZN13000:PA2 | ZN13000/000002 | CENTRAL COAST | OH | Veg | 2018-01-08 | Y | 1091.4737 | N | 4 | N | Y | 1.1101 | 39.4971 | 60618.8749
[7 empty] | 8221 | 14035 | 1549700 | 2018-02-09 13:50 | 2018-02-09 14:15 | 25 | 11kV | 75 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185747 B Phase DOLF : 10 Amp Excluded OMS 1549700 | February | 2018 | 2018Q3 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2018-02-09 | N | 25 | N | 8 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 8588 | 18668 | 1549705 | 2018-02-09 10:51 | 2018-02-09 17:15 | 384 | 11kV | 2688 | 7 | HV | Excavation 3rd Party | 3rd Party Impact | DC-PT Transformer | Unplanned | Hot >35C | N | LID 185748 C Phase DOLF : 10 Amp Excavator hit LV mains which destroyed transformer. Blew HV fuse. Excluded OMS 1549680 1549705 | February | 2018 | 2018Q3 | 2018 | 532:83307 | 532:83307 | ZN00532/083307 | MAITLAND | UG | Not Veg | 2018-02-09 | N | 384 | N | 8 | N | N | 1.1101 | 39.4971 | 1964.3111
[7 empty] | 8395 | 16243 | 1549764 | 2018-02-09 17:48 | 2018-02-09 20:02 | 134 | 11kV | 41406 | 309 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Recloser CP428 Bayfield Rd (Ex Zn35370 Galston, Panel 4L) Tripped to lockout on OC trip and lockout Cause: Tree on HV mains outside 19 Smalls Rd See OMS 1549764 1549778 | February | 2018 | 2018Q3 | 2018 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2018-02-09 | N | 134 | N | 8 | N | N | 1.1101 | 39.4971 | 30258.2835
[7 empty] | 7947 | 10353 | 1549793 | 2018-02-09 19:09 | 2018-02-09 20:20 | 71 | 11kV | 13933 | 1193 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Rain Heavy | N | At S1290 Leightonfield the 11kv Panel 11 "S5013 etc" tripped and reclosed Relays: C phase inst & timed OC, EFI, L/O Signals: 11kv trip, Tx3 Group Earth, Zone Earth, 11kv trip At PT108 Mundamatta St 3 x HDO blew Remarks: weather related. Lightning strike to PT108. Supply restored to PT108 via LV// | February | 2018 | 2018Q3 | 2018 | ZN1290:PA11 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-02-09 | N | 11.679 | N | 8 | N | N | 1.1101 | 39.4971 | 10181.8254
[7 empty] | 7864 | 9444 | 1549794 | 2018-02-09 19:23 | 2018-02-09 20:50 | 87 | 11kV | 137373 | 1579 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At S129 HUnters Hill Panel 57 tripped on A B and C phase IOC and Earth Fault. Cause not ascertained. | February | 2018 | 2018Q3 | 2018 | ZN129:PA57 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Veg | 2018-02-09 | N | 87 | N | 8 | N | N | 1.1101 | 39.4971 | 100388.1366
[7 empty] | 7730 | 7796 | 1549818 | 2018-02-09 20:27 | 2018-02-09 23:00 | 153.1667 | 11kV | 919 | 6 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 185750 B & C Phase DOLF : 16 Amp Spur fuses 74777 replaced B & C phase 16A Sub 71160 Volts: Aph - 246V, Bph - 246V, Cph - 248V Excluded OMS 1549820 | February | 2018 | 2018Q3 | 2018 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2018-02-09 | N | 153.1667 | N | 8 | N | N | 1.1101 | 39.4971 | 671.5781
[7 empty] | 7579 | 6109 | 1549832 | 2018-02-09 20:59 | 2018-02-09 23:20 | 141 | 11kV | 54353 | 416 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Ex Zn12630 Peats Ridge section pa1 "Gunderman" RE45189 Cooks Peats Ridge tripped and locked out on "no inication" at ELB61924 B & C phase fault detection See 1550280,1,2 ex 1549832 | February | 2018 | 2018Q3 | 2018 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2018-02-09 | N | 130.6562 | N | 8 | N | N | 1.1101 | 39.4971 | 39719.5693
[7 empty] | 8291 | 14885 | 1549781 | 2018-02-09 18:32 | 2018-02-10 00:55 | 383 | 11kV | 224457 | 1065 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Lightning | N | Zn9245 Engadine - pnl.1 tripped, reclosed & locked out on: B Phase O/C Field EFIs: S48147 9287 S9642, UGOH (Princess Hwy & Boronia), S9358 S9065 Lightning strike to UGOH below S9642 (Sw/B) on Princess Hwy cnr Boronia. Bonds cut away to enable supply to be restored to Non // sub S9380. (region to organise interruption for repairs) Also HV mains to PT9347 on the ground. See 1550264 1550265 1550270 | February | 2018 | 2018Q3 | 2018 | ZN9245:PA1 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Not Veg | 2018-02-09 | N | 210.7577 | N | 8 | N | N | 1.1101 | 39.4971 | 164026.5552
[7 empty] | 7230 | 914 | 1549983 | 2018-02-10 21:21 | 2018-02-10 22:35 | 74 | 11kV | 84508 | 1142 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | Lightning | N | At Zn4545 Meadowbank Panel 41 tripped on Signals: 11kV Trip Relays: A and Cphase OC Caise: Possum on mains, Denman St See OMS 1549983 1549984 | February | 2018 | 2018Q3 | 2018 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | OH | Not Veg | 2018-02-10 | N | 74 | N | 1 | N | N | 1.1101 | 39.4971 | 61755.9538
[7 empty] | 7614 | 6431 | 1550010 | 2018-02-11 00:24 | 2018-02-11 01:36 | 72 | 11kV | 42328 | 602 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.5 tripped on: A Phase O/C. Field EFIs: S61717 S2894 S8356 UG cable fault between S8356 (Sw/B) and S6309 (Sw/B) and S888 (Sw/B) See 1550274 1550275 | February | 2018 | 2018Q3 | 2018 | ZN690:PA5 | ZN690:PA5 | ZN00690/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-02-11 | N | 70.3123 | N | 6 | N | N | 1.1101 | 39.4971 | 30932.0539
[7 empty] | 7541 | 5740 | 1550015 | 2018-02-11 02:03 | 2018-02-11 10:01 | 478 | 11kV | 105035 | 1185 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 185751 storm damage pole JU-71478 2nd fault at LA at PT-17996 Protection = 51N Excluded oms 155001 | February | 2018 | 2018Q3 | 2018 | 261:81882 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | OH | Not Veg | 2018-02-11 | N | 88.6371 | N | 6 | N | N | 1.1101 | 39.4971 | 76756.48
[7 empty] | 7760 | 8179 | 1550048 | 2018-02-11 12:03 | 2018-02-11 13:11 | 68 | 11kV | 16252 | 239 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn3154 St Ives section of Pa23 RE527 Catherine Paul tripped, reclosed and locked out on OC trip IOC trip Lockout Cause: Tree/Branch on OH mains. A burnt tree was found on the 11kv OH on the corner of Mariana Close and Cassandra Ave St Ives See 1550048 ex 1550049,50 | February | 2018 | 2018Q3 | 2018 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Veg | 2018-02-11 | N | 68 | N | 6 | N | N | 1.1101 | 39.4971 | 11876.4822
[7 empty] | 7571 | 6039 | 1550052 | 2018-02-11 12:28 | 2018-02-11 13:12 | 44 | 11kV | 77762 | 1770 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12570 Avoca Pa24 "Kincumber" tripped reclosed tripped on B&C phase IOC Reclose/lockout 11kv trip Cause: not ascertained. Patrolled by Dop See 1550293,4 ex 1550052 | February | 2018 | 2018Q3 | 2018 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2018-02-11 | N | 43.9333 | N | 6 | N | N | 1.1101 | 39.4971 | 56826.176
[7 empty] | 7604 | 6366 | 1550078 | 2018-02-11 17:06 | 2018-02-11 22:05 | 299 | 11kV | 32101 | 405 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 185758 Overcurrent section isolated for repairs pole KS-62000 Excluded oms 1550078 | February | 2018 | 2018Q3 | 2018 | 229:34983 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Not Veg | 2018-02-11 | N | 79.2617 | N | 6 | N | N | 1.1101 | 39.4971 | 23458.464
[7 empty] | 7452 | 4697 | 1550091 | 2018-02-11 17:06 | 2018-02-11 22:30 | 324 | 11kV | 324 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185759 sub isolated for repair after fdr trip sw 34983 Williamtown see report 185758/OMS 1550393 Excluded oms 1550091 | February | 2018 | 2018Q3 | 2018 | 229:34983 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Not Veg | 2018-02-11 | N | 324 | N | 6 | N | N | 1.1101 | 39.4971 | 236.7696
[7 empty] | 7790 | 8642 | 1550105 | 2018-02-12 02:01 | 2018-02-12 04:06 | 125 | 11kV | 134875 | 1079 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.21L tripped, reclosed and locked out on: A & B phase IOC Tree branch on 11kV mains in Boronia Pde, Lugarno near PT10513 Boronia Woodlands | February | 2018 | 2018Q3 | 2018 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Veg | 2018-02-12 | N | 125 | N | 3 | N | N | 1.1101 | 39.4971 | 98562.6719
[7 empty] | 8502 | 17654 | 1550347 | 2018-02-12 19:20 | 2018-02-12 22:10 | 170 | 11kV | 170 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185764 Single phase DOLF : 10 Amp Dead bird found below sub Excluded 1550347 | February | 2018 | 2018Q3 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2018-02-12 | N | 170 | N | 3 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 8575 | 18540 | 1550372 | 2018-02-13 01:02 | 2018-02-13 01:29 | 27 | 11kV | 24430 | 2290 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | Zn12580 Erina 11kv No.3 Bar was interrupted for safety due to fire concern Abnormal: Tx3 11kv OOS with 11kV 2-3 B/S CB closed LB78040 closed, Pa16 open (Double Banked) with S18039:B open, S18654:A Closed Cause: Interrupted for safety reasons In the middle of returning the no.3 11kv busbar & feeders to service, whole switchroom & zone substation befgan filling with smoke. A solenoid for 11kv pa13 CB appears to have been the cause See 1550754,5 ex 1550372 | February | 2018 | 2018Q3 | 2018 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | Unknown | Not Veg | 2018-02-13 | N | 10.6681 | N | 7 | N | N | 1.1101 | 39.4971 | 17852.7234
[7 empty] | 8168 | 13343 | 1550405 | 2018-02-13 07:43 | 2018-02-13 10:03 | 140.3333 | 11kV | 140.3333 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185777 B Phase DOLF : 10 Amp Replace blown 11kv dolf, B phase Excluded OMS 1550405 | February | 2018 | 2018Q3 | 2018 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2018-02-13 | N | 140.3333 | N | 7 | N | N | 1.1101 | 39.4971 | 102.5515
[7 empty] | 7701 | 7408 | 1550501 | 2018-02-13 12:30 | 2018-02-13 13:45 | 75 | 11kV | 8177 | 113 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn9035 Caringbah 11kv feeder Panel No.8 "Kirimbla Kareena" feeder tripped Relays: EF and EFI Signals: 11kv trip and Tx2 Group earth Field EFIs: Nil Remarks: UG fault. 11kv feeder fault from ZN9035 Caringbah Panel No8 to S9017 Kirimbla Kareena Sw/A due to HAZ RMI @ S9017 extended to S9411 Kreena Suth Hosp No1 Sw/A | February | 2018 | 2018Q3 | 2018 | ZN9035:PA8 | ZN9035:PA8 | ZN09035/000008 | SUTHERLAND | UG | Not Veg | 2018-02-13 | N | 72.3628 | N | 7 | N | N | 1.1101 | 39.4971 | 5975.5104
[7 empty] | 8343 | 15425 | 1550510 | 2018-02-13 12:55 | 2018-02-13 15:00 | 125 | 11kV | 500 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185781 DOLF : 16 Amp Excluded OMS 1550510 | February | 2018 | 2018Q3 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2018-02-13 | N | 125 | N | 7 | N | N | 1.1101 | 39.4971 | 365.3853
[7 empty] | 7770 | 8327 | 1550298 | 2018-02-12 16:25 | 2018-02-13 20:10 | 1665 | 11kV | 10443 | 71 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12630 Peazts Ridge section of Pa3 "Mangrove Mtn" RE49206 Mangrove Mtn West Relays: A&C Phase OC trip, lockout (A-502 B-21A C-532A) Remote Indications: Zn12630 Peats Ridge Pa3 EFI ELBS61085: A+B O/C (Detection) EF_Detection Cause: Tree/Branch brought down OH Large tree has brought down multiple spans of HV, including broken x-arms. Near 435 Waratah Rd, Mangrove Mountain (Ex Pa3 Peats Ridge beyond recloser RE49206 Mangrove Mtn West) Note: PT14944 PT13945 & PT13974 were interrupted at 1230 and restored at 1950 on the 13/2/18 from 11kV LK42143 to carry out above repairs See 1550298,340,52 ex 1550554 | February | 2018 | 2018Q3 | 2018 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2018-02-12 | N | 147.0845 | N | 3 | N | N | 1.1101 | 39.4971 | 7631.4364
[7 empty] | 8514 | 17779 | 1550652 | 2018-02-13 22:50 | 2018-02-13 23:02 | 12.5 | 11kV | 2975 | 238 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of Pa17 "Somersby Falls" 11kV Intelliruptor 61922 Pacific bar Point was interrupted for safety Branch on mains near 11kv LK43257, interrupted for Lineworker to remove branch | February | 2018 | 2018Q3 | 2018 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2018-02-13 | N | 12.5 | N | 7 | N | N | 1.1101 | 39.4971 | 2174.0423
[7 empty] | 8452 | 17030 | 1550597 | 2018-02-13 16:54 | 2018-02-14 01:30 | 516 | 11kV | 93294 | 1185 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 185790 Car hit pole JU-70021 open sw 81870 & sw 81882 for safety oms 1550595 also see LID report 185789 Excluded OMS 1550595 | February | 2018 | 2018Q3 | 2018 | 261:81882 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | OH | Not Veg | 2018-02-13 | N | 78.7291 | N | 7 | N | N | 1.1101 | 39.4971 | 68176.5035
[7 empty] | 7930 | 10214 | 1550595 | 2018-02-13 16:46 | 2018-02-14 02:05 | 559 | 11kV | 165675 | 1825 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 185789 Car hit pole JU-70021 open sw 81870 & sw 81882 for safety oms 1550595 also see LID report 185790 | February | 2018 | 2018Q3 | 2018 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2018-02-13 | N | 90.7808 | N | 7 | N | N | 1.1101 | 39.4971 | 121070.4034
[7 empty] | 8330 | 15252 | 1550665 | 2018-02-14 07:19 | 2018-02-14 08:45 | 86 | 11kV | 172 | 2 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 185785 Single phase DOLF : 20 Amp pelicans in area Excluded oms 1550665 | February | 2018 | 2018Q3 | 2018 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2018-02-14 | N | 86 | N | 11 | N | N | 1.1101 | 39.4971 | 125.6925
[7 empty] | 7250 | 1245 | 1550710 | 2018-02-14 09:16 | 2018-02-14 11:08 | 112 | 11kV | 112 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of pa11 PT12069 Silvester Gore 3516 HDO operated 10amp type:NGK stinger AK1 No cause ascertained supply restored and checked ok See 1551130 ex 1550710 | February | 2018 | 2018Q3 | 2018 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2018-02-14 | N | 112 | N | 11 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 8707 | 20137 | 1550750 | 2018-02-14 11:26 | 2018-02-14 13:20 | 114 | 11kV | 342 | 3 | HV | Animal Goanna | Animal | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 185794 Single phase DOLF : 10 Amp goanna removed from tx Excluded oms 1550750 | February | 2018 | 2018Q3 | 2018 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2018-02-14 | N | 114 | N | 11 | N | N | 1.1101 | 39.4971 | 249.9235
[7 empty] | 7894 | 9917 | 1550844 | 2018-02-14 16:44 | 2018-02-14 17:40 | 56 | 11kV | 168 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 185798 A Phase DOLF : 10 Amp Excluded OMS 1550844 | February | 2018 | 2018Q3 | 2018 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2018-02-14 | N | 56 | N | 11 | N | N | 1.1101 | 39.4971 | 122.7694
[7 empty] | 8359 | 15636 | 1550814 | 2018-02-14 14:48 | 2018-02-14 17:50 | 182 | 11kV | 182 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Hot >35C | N | @Sub 4100 Beresford Coventry HV fuse operated HV fuse details: 80A B phase Remarks: Customer's installation. Customer's installation is overloading and does not grade with Ausgrids Network | February | 2018 | 2018Q3 | 2018 | ZN2835:PA41 | ZN2835:PA41 | ZN02835/000041 | STRATHFIELD | Unknown | Not Veg | 2018-02-14 | N | 182 | N | 11 | N | N | 1.1101 | 39.4971 | 133.0002
[7 empty] | 8354 | 15598 | 1550863 | 2018-02-14 17:25 | 2018-02-14 18:00 | 35 | 11kV | 2275 | 65 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Hot >35C | N | LID 185799 DOLF : 20 Amp Fuse carrier had burnt up and fallen apart, B Lindsay replaced with new fuse carrier and fuse. Excluded OMS 1550864 | February | 2018 | 2018Q3 | 2018 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2018-02-14 | N | 35 | N | 11 | N | N | 1.1101 | 39.4971 | 1662.5029
[7 empty] | 8535 | 18005 | 1550835 | 2018-02-14 15:54 | 2018-02-14 18:16 | 142 | 11kV | 23621 | 1017 | HV | Overload | Utility Process Issue | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Zn1850 Bass Hill 11kv 'Carnarvon heron' fdr Panel 4 from Rec 49253 Rex McClean relay OC trip Abnormal: Sw/B closed @ S47485 & Sw/A opened @ S63043 Remarks: overload. Due to hot weather 40 deg + and feeder abnormally switched for DAROS #420529 SAO #420534 | February | 2018 | 2018Q3 | 2018 | ZN1850:PA10 | ZN1850:PA40 | ZN01850/000040 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-02-14 | N | 23.2262 | N | 11 | N | N | 1.1101 | 39.4971 | 17261.5301
[7 empty] | 8693 | 19938 | 1550902 | 2018-02-14 19:29 | 2018-02-14 20:35 | 66 | 11kV | 107056 | 1776 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn14892 Charmhaven 11kv Pa19 "Lakehaven Wyong Leagues" fdr tripped, reclosed & tripped Relays: 50TB, EF, FC, L/O, EFI Signals: 11kV trip, Tx2 GE EFI's Nil Cause: UG Cable Fault. Front Line Feeder Fault See 1551135,6 ex 1550902 | February | 2018 | 2018Q3 | 2018 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | UG | Not Veg | 2018-02-14 | N | 60.2793 | N | 11 | N | N | 1.1101 | 39.4971 | 78233.3672
[7 empty] | 8267 | 14562 | 1550913 | 2018-02-14 19:47 | 2018-02-14 21:38 | 111 | 11kV | 260936 | 2420 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn3472 Sefton Panel 27 'Gascoigne Rodd' tripped on Relays: C phase earth fault, fault check and EFI Signals: 11kv trip zone earth and Tx2 Group earth Field EFI's: S4003, S8762 Abnormal: Sw/A closed @ S4390 & Sw/A open @ S35465. @ S47559 Sw/B closed and Sw/A open Remarks: 11kv feeder fault from S4003 Gascoigne Rodd to S8762 Wood batt. See interruption on Panel 28 protection malfunction. Dop found EFI down at S8762 | February | 2018 | 2018Q3 | 2018 | ZN3472:PA27 | ZN3472:PA27 | ZN03472/000027 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-02-14 | N | 107.8248 | N | 11 | N | N | 1.1101 | 39.4971 | 190684.3325
[7 empty] | 7960 | 10482 | 1550929 | 2018-02-14 20:22 | 2018-02-14 22:00 | 98 | 11kV | 103102 | 1118 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36100 Rose bay - Pnl.12 tripped on: 3 Phase IOC with EFI Field EFIs: S882 S3360 S48295 S35766 S2714 @ S882 Nortcote St - "Chamberlain Towers" feeder had tripped on: A Phase O/C UG cable fault from S2714 (Sw/A) to S35070 (Sw/B) See 1551106 1551107 | February | 2018 | 2018Q3 | 2018 | ZN36100:PA12 | ZN36100:PA12 | ZN36100/000012 | WAVERLEY | UG | Not Veg | 2018-02-14 | N | 92.22 | N | 11 | N | N | 1.1101 | 39.4971 | 75343.9006
[7 empty] | 7237 | 1068 | 1550960 | 2018-02-14 23:02 | 2018-02-15 01:41 | 159 | 11kV | 193745 | 1228 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn9900 Menai - Pnl.1 tripped on: O/C Tree flicked into 11kV OH mains betwen S9983 (Sw/A) , S9891 (Sw/B) and S9889 (Sw/B) Mains clashed and caused damage. To be assessed in daylight. | February | 2018 | 2018Q3 | 2018 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | OH | Veg | 2018-02-14 | N | 157.7728 | N | 11 | N | N | 1.1101 | 39.4971 | 141583.1315
[7 empty] | 7236 | 1051 | 1550984 | 2018-02-15 02:05 | 2018-02-15 02:22 | 17 | 11kV | 799 | 47 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Hot >35C | N | LID 185804 B & C Phase ABS 4754 2 phases burning up Excluded OMS 1550984 | February | 2018 | 2018Q3 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2018-02-15 | N | 17 | N | 5 | N | N | 1.1101 | 39.4971 | 583.8856
[7 empty] | 8405 | 16424 | 1550995 | 2018-02-15 06:50 | 2018-02-15 10:54 | 244 | 11kV | 732 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 185809 Connection to dolf was burnt off, fuses changed from 20A to 16A , DEPOT to send in SAO. Excluded OMS 1550995 | February | 2018 | 2018Q3 | 2018 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2018-02-15 | N | 244 | N | 5 | N | N | 1.1101 | 39.4971 | 534.924
[7 empty] | 8083 | 12242 | 1551191 | 2018-02-15 15:09 | 2018-02-15 15:57 | 48 | 11kV | 288 | 6 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2635 Epping - Panel 33 tripped on Relays: 50TB - IOC, 150TN - EF - EFI Cause: UG cable fault from Panel 33 to S2635 to S7740 | February | 2018 | 2018Q3 | 2018 | ZN2635:PA33 | ZN2635:PA33 | ZN02635/000033 | RYDE | UG | Not Veg | 2018-02-15 | N | 48 | N | 5 | N | N | 1.1101 | 39.4971 | 210.4619
[7 empty] | 8661 | 19620 | 1551247 | 2018-02-15 18:27 | 2018-02-15 20:22 | 115 | 11kV | 233482 | 2158 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14891 Wyong Pa16 "Wadalba" fdr tirpped Relays: Basler (51n) EF, FC, LO, EFI Signals: 11kv trip, Tx2 GE EFI's: All EFI's to including S64795 First Attempt: Protection as above EFI's: Nil (Electronic EFI could not be diagnosed) Second Attempt: Protection as above EFI's: Nil Cause: UG Fault. Front Line Feeder Fault See 1551353,4,5 | February | 2018 | 2018Q3 | 2018 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | UG | Not Veg | 2018-02-15 | N | 108.1937 | N | 5 | N | N | 1.1101 | 39.4971 | 170621.759
[7 empty] | 8670 | 19699 | 1551265 | 2018-02-15 22:41 | 2018-02-16 04:03 | 322.4 | 11kV | 8060 | 25 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 185822 B & C Phase DOLF : 40 Amp 11kV OHM down at pole FR-61533. CC1: 22-"Refer to SOp" | February | 2018 | 2018Q3 | 2018 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2018-02-15 | N | 322.4 | N | 5 | N | N | 1.1101 | 39.4971 | 5890.0103
[7 empty] | 7916 | 10070 | 1551283 | 2018-02-16 02:07 | 2018-02-16 04:57 | 170 | 11kV | 17000 | 100 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185823 A Phase DOLF : 31 Amp Dead possum on sub Excluded OMS 1551283 | February | 2018 | 2018Q3 | 2018 | 221:11894 | 221:11894 | ZN00221/011894 | LAKE MACQUARIE | OH | Not Veg | 2018-02-16 | N | 170 | N | 1 | N | N | 1.1101 | 39.4971 | 12423.0986
[7 empty] | 7940 | 10317 | 1551613 | 2018-02-17 14:46 | 2018-02-17 18:16 | 210 | 11kV | 2478 | 19 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mountain" fdr from AB40560 to USL41190 tee PT12147 PT11238 PT12272 PT13521 interrutped for emergrency works. Cause: interrupted for safety reasons. Glider Club Cable across 11kv mains See 1552309,10 ex 1551613,29,31 | February | 2018 | 2018Q3 | 2018 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2018-02-17 | N | 130.4211 | N | 2 | N | N | 1.1101 | 39.4971 | 1810.8493
[7 empty] | 8508 | 17698 | 1551647 | 2018-02-17 18:10 | 2018-02-17 18:49 | 39 | 11kV | 9087 | 233 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mountain" RE46992 Goolara Holy Cross tripped and locked out (note rec defective & scan failed) Cause: staff error - mis communication between AOp and DOp over recloser status See 1552313 ex 1551647,61 | February | 2018 | 2018Q3 | 2018 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | Unknown | Not Veg | 2018-02-17 | N | 39 | N | 2 | N | N | 1.1101 | 39.4971 | 6640.5116
[7 empty] | 8367 | 15739 | 1551798 | 2018-02-18 17:05 | 2018-02-18 17:10 | 5 | 11kV | 4120 | 824 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | LID 185841 Load Shedding Load on Sw 83129 was approaching Prot setting of 348Amps. To prevent tripping feeders while in parallel we dropped of load from ABS 40356. LID and OMS customer count may be incorrect due to recent feeder work at Cessnock South sub. Excluded OMS 1551798 | February | 2018 | 2018Q3 | 2018 | 504:48034 | 522:83129 | ZN00522/083129 | CESSNOCK | Unknown | Unknown | 2018-02-18 | N | 5 | N | 1 | N | N | 1.1101 | 39.4971 | 3010.7745
[7 empty] | 8033 | 11469 | 1552225 | 2018-02-19 07:20 | 2018-02-19 14:40 | 440 | 11kV | 49280 | 112 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Planned LID 185846 SINO 25878 | February | 2018 | 2018Q3 | 2018 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2018-02-19 | N | 440 | N | 5 | N | N | 1.1101 | 39.4971 | 36012.3705
[7 empty] | 8164 | 13306 | 1552044 | 2018-02-19 17:05 | 2018-02-19 18:08 | 63 | 11kV | 1197 | 19 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa2 "Holgate" fdr beyond LB45185 to LB45186 interrupted tree branch on OH mains. tree across 11kv fdr See 1552324 ex 1552044,6 | February | 2018 | 2018Q3 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2018-02-19 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 874.7323
[7 empty] | 8084 | 12246 | 1551837 | 2018-02-19 00:02 | 2018-02-19 19:25 | 1163 | 11kV | 289422 | 2366 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn12570 Avoca Panel 24 "Kincumber" tripped reclosed tripped on Earth Fault, EFi, Recloser lockout and timing Cause: vehicle hit pole. Pole Broken. Hot water load effected restoration time See 1552333,4,6 ex 1551837,40,4,5,6,953 | February | 2018 | 2018Q3 | 2018 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2018-02-19 | N | 122.3254 | N | 5 | N | N | 1.1101 | 39.4971 | 211501.0611
[7 empty] | 7643 | 6736 | 1552074 | 2018-02-19 20:07 | 2018-02-19 21:00 | 53 | 11kV | 106 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185855 B Phase DOLF : 10 Amp Excluded OMS 1552074 | February | 2018 | 2018Q3 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2018-02-19 | N | 53 | N | 5 | N | N | 1.1101 | 39.4971 | 77.4617
[7 empty] | 8591 | 18708 | 1552075 | 2018-02-19 20:08 | 2018-02-19 23:20 | 192 | 11kV | 576 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 185856 DOLF : 16 Amp | February | 2018 | 2018Q3 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2018-02-19 | N | 192 | N | 5 | N | N | 1.1101 | 39.4971 | 420.9238
[7 empty] | 8050 | 11750 | 1552122 | 2018-02-20 00:45 | 2018-02-20 02:19 | 94 | 11kV | 47431 | 508 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35370 Galston Panel 10 tripped, reclosed, tripped and locked out on Relays: A phase overcurrent and earth fault Signals: 11kV trip Cause: Tree branch on 11kV near PT1983, Removed by DOp See OMS 1552688 1552690 1552122 | February | 2018 | 2018Q3 | 2018 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2018-02-20 | N | 93.3681 | N | 7 | N | N | 1.1101 | 39.4971 | 34661.1758
[7 empty] | 7530 | 5638 | 1552137 | 2018-02-20 03:59 | 2018-02-20 09:32 | 333 | 11kV | 121105 | 382 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | Ex Zn14891 Wyong section of Pa12 "Yarramalong" IR50630 Yarramalong Chand tripped and locked out on: Relays: Overcurrent, SEF, Lockout, Alarm Cause: Lightning/Surge Arrestor Suspected damaged lightning arrestor pole WK193 Nearest PT12021 Yarramalong Kiddman 3.8 See 1552472,3,4 ex 1552137 | February | 2018 | 2018Q3 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2018-02-20 | N | 317.0288 | N | 7 | N | N | 1.1101 | 39.4971 | 88499.962
[7 empty] | 7316 | 2448 | 1552163 | 2018-02-20 07:21 | 2018-02-20 12:30 | 309 | 11kV | 70861 | 929 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 185860 C Phase Overcurrent 33kV pole fire IS-35128 Excluded oms 1552163 | February | 2018 | 2018Q3 | 2018 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Not Veg | 2018-02-20 | N | 76.2766 | N | 7 | N | N | 1.1101 | 39.4971 | 51783.1288
[7 empty] | 7755 | 8097 | 1552250 | 2018-02-20 11:25 | 2018-02-20 12:30 | 65.4333 | 11kV | 21331.2667 | 326 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn15014 Mona Vale section of Pa14 RE22381 Lane Cove Walter tripped, relcosed and locked out on OC trip, IOC trip, Lockout Cause: not ascertained See 1552250 ex 1552255,9 | February | 2018 | 2018Q3 | 2018 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2018-02-20 | N | 65.4333 | N | 7 | N | N | 1.1101 | 39.4971 | 15588.2605
[7 empty] | 7229 | 893 | 1552162 | 2018-02-20 12:16 | 2018-02-20 14:35 | 139 | 11kV | 4587 | 33 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 185866 Outage to repair insulators on 33kV above Excluded OMS 1552162 | February | 2018 | 2018Q3 | 2018 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2018-02-20 | N | 139 | N | 7 | N | N | 1.1101 | 39.4971 | 3352.0443
[7 empty] | 8374 | 15830 | 1552130 | 2018-02-20 02:16 | 2018-02-20 16:25 | 849 | 11kV | 103103 | 1490 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of pa1 "Dog Trap Rd" RE44936 Bentley Rd tripped reclosed tripped and locked out on: Relays: overcurrent Cause: tree/branch brought down oh 11kV on ground HV into LV section of 11kV from AB45434 to AB44473 to AB47645 isolated with PT12211 isolated & PT13230 interrupted on Dist 1 only See 1552466,8,9,70,1 ex 1552130,3,4,42,295,7 | February | 2018 | 2018Q3 | 2018 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2018-02-20 | N | 69.1966 | N | 7 | N | N | 1.1101 | 39.4971 | 75344.6314
[7 empty] | 7908 | 9989 | 1552365 | 2018-02-20 16:54 | 2018-02-20 17:20 | 26 | 11kV | 4534 | 299 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At Zn35400 North Sydney Panel 61 tripped Signals: 11kV trip Relays: ITR Cause: During Trip Checks of (D&R-421268) Intertrip receives have operated on Panel 61 @ S35400 North Sydney and SW/A @ S2975. See OMS 1552705 1552706 1552365 | February | 2018 | 2018Q3 | 2018 | ZN35400:PA61 | ZN35400:PA61 | ZN35400/000061 | NORTH SYDNEY | Unknown | Unknown | 2018-02-20 | N | 15.1639 | N | 7 | N | N | 1.1101 | 39.4971 | 3313.3135
[7 empty] | 7335 | 2764 | 1552522 | 2018-02-21 14:00 | 2018-02-21 14:50 | 50 | 11kV | 50 | 1 | HV | Excavation Ausgrid Staff | Utility Process Issue | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 185878 Faulty LA's replaced Excluded OMS 1552522 | February | 2018 | 2018Q3 | 2018 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | UG | Not Veg | 2018-02-21 | N | 50 | N | 2 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 8179 | 13479 | 1552553 | 2018-02-21 15:04 | 2018-02-21 17:45 | 161 | 11kV | 1654 | 54 | HV | Animal Goanna | Animal | Fuse | Unplanned | No Weather Impact | N | Ex Zn15013 Tearrey Hills section of Pa10 RE1126 Mona Vale Rd Recloser has tripped & reclsoed Relays: IOC trip, OC Trip PT15672 Tumbledown Dick 11kV ABB HVDO LAS 20A Blown (RIght side) Lizard found dead at base of PT15672 with HDO blown See 1552711,2 ex 1552553 | February | 2018 | 2018Q3 | 2018 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2018-02-21 | N | 30.6296 | N | 2 | N | N | 1.1101 | 39.4971 | 1208.6944
[7 empty] | 8132 | 12991 | 1552634 | 2018-02-22 01:41 | 2018-02-22 02:57 | 76 | 11kV | 167904 | 2276 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12640 Umina Pa12 "Oscar West" fdr tripped on: Relays: B & C Phase IOC EFI's:Nil Abnormal: LB42267 closed DMA AB41567 open Cause: not ascertained. Dop patrolled supply restored See 1552848,51 ex 1552634,5 | February | 2018 | 2018Q3 | 2018 | ZN12640:PA12 | ZN12640:PA12 | ZN12640/000012 | CENTRAL COAST | OH | Veg | 2018-02-22 | N | 73.7715 | N | 5 | N | N | 1.1101 | 39.4971 | 122699.2909
[7 empty] | 8710 | 20193 | 1552637 | 2018-02-22 02:25 | 2018-02-22 11:10 | 525 | 11kV | 424115.4167 | 1676 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S16194 Manly Hospital No1: SW/B Tripped on Relays: A and C phase O/C Cause:11kV OH fell onto LV in Osbourne St Section of 11kV feeder from S16721 to LK22305 tee S15525 See OMS 1554181 1554183 1554184 1554186 1554185 1552701 1552661 1552660 1552659 1552658 1552657 1552652 1552650 1552642 1552639 1552637 | February | 2018 | 2018Q3 | 2018 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | OH | Not Veg | 2018-02-22 | N | 253.0522 | N | 5 | N | N | 1.1101 | 39.4971 | 309931.0372
[7 empty] | 7612 | 6419 | 1552654 | 2018-02-22 04:58 | 2018-02-22 15:00 | 602 | 11kV | 243460 | 1951 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 185880 2 fault operations C Phase Overcurrent; Earth Fault Flying Fox in OHM pole JU-30633, causing HV into LV OHM. Sub 11908 LH LVF had A & B phase blown 400A. Excluded OMS No. 1552654 + 1552655 | February | 2018 | 2018Q3 | 2018 | 203:8085 | 204:82705 | ZN00204/082705 | NEWCASTLE | OH | Not Veg | 2018-02-22 | N | 124.7873 | N | 5 | N | N | 1.1101 | 39.4971 | 177913.3871
[7 empty] | 8067 | 12035 | 1552844 | 2018-02-22 14:29 | 2018-02-22 16:20 | 111 | 11kV | 70516 | 830 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At Zn9550 Gwawley Bay Panel 1 tripped on - Earth fault and EFI. Signals: 11kV Trip Cause: UG cable damaged by contractor from S9176 to S9114 See OMS 1553027 1553029 1553030 1552844 | February | 2018 | 2018Q3 | 2018 | ZN9550:PA1 | ZN9550:PA1 | ZN09550/000001 | SUTHERLAND | UG | Not Veg | 2018-02-22 | N | 84.959 | N | 5 | N | N | 1.1101 | 39.4971 | 51531.0129
[7 empty] | 8624 | 19147 | 1552936 | 2018-02-22 18:13 | 2018-02-22 19:38 | 85 | 11kV | 69530 | 818 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington - Pnl.35 tripped on: Earth Fault UG cable fault in front line section of feeder from Pnl.35 to S4371 to S1681. See 1552936 | February | 2018 | 2018Q3 | 2018 | ZN342:PA35 | ZN342:PA35 | ZN00342/000035 | SYDNEY | UG | Not Veg | 2018-02-22 | N | 85 | N | 5 | N | N | 1.1101 | 39.4971 | 50810.4732
[7 empty] | 7882 | 9793 | 1552986 | 2018-02-23 05:08 | 2018-02-23 13:00 | 472 | 11kV | 410309 | 3725 | HV | Fire (Non Ausgrid) | UNKNOWN | DC Not Transformer | Unplanned | No Weather Impact | N | At ZN2310 Punchbowl Panel 15 'S4689' feeder has tripped Signals: 11kv trip Relays: 3 phase timed OC, EFI Field EFI's: As expected Abnormal: sw/A closed @ S2625 and Sw/A is open @ S1196 for UG cable fault on Panel 9L out of Bankstown Zone Remarks: Sub4689 Roselands No.4 has burnt itself to the ground. Fire | February | 2018 | 2018Q3 | 2018 | ZN2310:PA15 | ZN2310:PA15 | ZN02310/000015 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-02-23 | N | 110.1501 | N | 3 | N | N | 1.1101 | 39.4971 | 299841.7151
[7 empty] | 8238 | 14290 | 1553174 | 2018-02-23 19:18 | 2018-02-23 20:27 | 69 | 11kV | 38532 | 568 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN965 Pennant Hills Panel 2 tripped on Rignals: 11kV trip, TX1 Group Earth, Zone Earth, Relays: B phase earth leakage and EFI. Cause: UG cable fault between S4965 and S4964. Seen OMS 1553732 1553733 1553174 1553179 | February | 2018 | 2018Q3 | 2018 | ZN965:PA2 | ZN965:PA2 | ZN00965/000002 | HORNSBY | OH | Not Veg | 2018-02-23 | N | 67.838 | N | 3 | N | N | 1.1101 | 39.4971 | 28158.0491
[7 empty] | 7413 | 3997 | 1553181 | 2018-02-23 19:48 | 2018-02-23 22:24 | 156 | 11kV | 4680 | 30 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn15014 Mona Vale section of pa12 "Minmai Rd" S16468 Loquat Valley Rd 11kV HV Fuse failed Cause: Tree/Branch on OH mains. A Large tree brnach was found on the LV mains adjacent to pole MV04539 No lV fuses blown. HV fuses burnt, did not operate striker pin. See attached photo S16468 in LV// USL's 44860 19030 See 1553897 ex 1553181,91 | February | 2018 | 2018Q3 | 2018 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | OH | Veg | 2018-02-23 | N | 156 | N | 3 | N | N | 1.1101 | 39.4971 | 3420.006
[7 empty] | 8517 | 17808 | 1553202 | 2018-02-24 02:57 | 2018-02-24 04:10 | 73 | 11kV | 88111 | 1207 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Pa19L "Corella Enterprise" fdr tripped Relays: OC 'ABC' phase, EF, EFI Signals: 11kv trip, TX12 GE EFI's S18761 S64488 S18560 S18559 Cause: UG Fault. 11kv feeder isolated from S18559 to LB43329 to AB44724 | February | 2018 | 2018Q3 | 2018 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | UG | Not Veg | 2018-02-24 | N | 73 | N | 4 | N | N | 1.1101 | 39.4971 | 64388.92
[7 empty] | 7412 | 3995 | 1553272 | 2018-02-24 13:50 | 2018-02-24 15:00 | 70 | 11kV | 59319 | 1405 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 185916 1 fault operation Sensitive Earth Fault 11kV tapping fail at pole KT-70089 Excluded OMS 1553272 | February | 2018 | 2018Q3 | 2018 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2018-02-24 | N | 42.2199 | N | 4 | N | N | 1.1101 | 39.4971 | 43348.5756
[7 empty] | 8311 | 15107 | 1553287 | 2018-02-24 15:40 | 2018-02-24 15:50 | 10 | 11kV | 50 | 5 | HV | Wind Blown Debris | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 185917 B Phase metal/tin on 11kV feeder at pole IQ-62839 Excluded OMS 1553277 | February | 2018 | 2018Q3 | 2018 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2018-02-24 | N | 10 | N | 4 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 7989 | 10895 | 1553275 | 2018-02-24 14:08 | 2018-02-24 16:01 | 113 | 11kV | 77295 | 709 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14891 Wyong Panel 12 "Yarramalong" fdr tripped, reclosed tripped and locked out on: Relays: A Phase OC, EFI, Timer, LO, Tx Group FC EFI's: Nil Cause: tree/branch on OH mains Tree branch on 11kv mains adj pole WY135. OMS job forwarded to depot for region to follow up tree trimming See 1553902,3,4 ex 1553275 | February | 2018 | 2018Q3 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2018-02-24 | N | 109.0197 | N | 4 | N | N | 1.1101 | 39.4971 | 56484.9062
[7 empty] | 8723 | 20434 | 1553350 | 2018-02-25 03:16 | 2018-02-25 04:50 | 94 | 11kV | 7990 | 85 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 185920 C Phase DOLF : 20 Amp Issued to Dop C phase 20A DOLF Possum supply back on 0450hrs Excluded OMS 1553350 | February | 2018 | 2018Q3 | 2018 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2018-02-25 | N | 94 | N | 12 | N | N | 1.1101 | 39.4971 | 5838.8563
[7 empty] | 7417 | 4057 | 1553410 | 2018-02-25 12:26 | 2018-02-25 13:34 | 68.4167 | 11kV | 98725.25 | 1443 | HV | Vegetation Blow/Fall In | Vegetation | 3rd Party Asset | Unplanned | Rain Heavy | N | Zn15005 Belrose 11kv fdr Panel 12 "Belrose" fdr tripped to lock out x Relays: IOC A & C phase timing, lockout Signals: Trip LED EFI's: Nil Cause: tree branch on contact - other. outside 3 Trentbridge rd Belrose, no damage to mains. See 1553410 ex 1553414 | February | 2018 | 2018Q3 | 2018 | ZN15005:PA12 | ZN15005:PA12 | ZN15005/000012 | NORTHERN BEACHES | OH | Veg | 2018-02-25 | N | 68.4167 | N | 12 | N | N | 1.1101 | 39.4971 | 72145.5008
[7 empty] | 8606 | 18921 | 1553421 | 2018-02-25 13:03 | 2018-02-25 14:30 | 87 | 11kV | 23950 | 276 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S847 Hornsby panel 38 tripped on Relays: C phase OC and EFI Signals: 11kV trip, TX3 Group Earth and Zone Earth Cause: Frontline 11kV UG feeder fault between ZN847 Hornsby Pa38 and S6485 See OMS 1553931 1553421 | February | 2018 | 2018Q3 | 2018 | ZN847:PA38 | ZN847:PA38 | ZN00847/000038 | HORNSBY | UG | Not Veg | 2018-02-25 | N | 86.7754 | N | 12 | N | N | 1.1101 | 39.4971 | 17501.9536
[7 empty] | 8217 | 13932 | 1553450 | 2018-02-25 15:18 | 2018-02-25 18:10 | 172 | 11kV | 17895 | 164 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 185924 1 fault operation Overcurrent live line lead on xarm Please patrol. Excluded OMS 1553452, 1553450. | February | 2018 | 2018Q3 | 2018 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2018-02-25 | N | 109.1159 | N | 12 | N | N | 1.1101 | 39.4971 | 13077.1382
[7 empty] | 8564 | 18377 | 1553505 | 2018-02-25 17:23 | 2018-02-25 19:01 | 98 | 11kV | 115507 | 1331 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.36 tripped on: B phase O/C and Earth Fault UG cable fault in section between S49242 (Sw/B) to S8811 (Sw/A) to S4318 (Sw/B) See 1553749 1553750 | February | 2018 | 2018Q3 | 2018 | ZN2602:PA36 | ZN35600:PA11 | ZN35600/000011 | RANDWICK | UG | Not Veg | 2018-02-25 | N | 86.7821 | N | 12 | N | N | 1.1101 | 39.4971 | 84409.1087
[7 empty] | 7841 | 9257 | 1553456 | 2018-02-25 17:07 | 2018-02-25 20:15 | 188 | 11kV | 23876 | 127 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | Rain Heavy | N | Zn9245 Engadine - Pn.19 tripped & reclosed on: A & B phase O/C (tripped & reclosed at 14:37 & 15:30) Air Break Switch 35920 road side phase flashing over. @ 17:07 isolation of AB35583 to LB65675 to allow repairs. See 15533765 1553767 | February | 2018 | 2018Q3 | 2018 | ZN9245:PA19 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | OH | Not Veg | 2018-02-25 | N | 188 | N | 12 | N | N | 1.1101 | 39.4971 | 17447.8766
[7 empty] | 8569 | 18460 | 1553563 | 2018-02-25 20:18 | 2018-02-25 21:24 | 66 | 11kV | 90420 | 1370 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn15008 Harbord Panel 6 "Campbell Pde" tripped, reclosed and locked out on: Signals: 11kv trip Relays: Recloser timed, recloser lockout, OC & EF Relay trip & IOC EFI's: Nil Note Harbord Zone was on standby supply. After panel 6 tripped, the zone lost aux supply. This was switched over to normal supply to restore supply to the zone. See DNMS log for alarms Cause: tree/branch on OH Mains. A large palm frond was found on the 11kv OH outside 42 Harbord Rd, Freshwater See 1553563 ex 1553565,6,7,71,3 | February | 2018 | 2018Q3 | 2018 | ZN15008:PA6 | ZN15008:PA6 | ZN15008/000006 | NORTHERN BEACHES | OH | Veg | 2018-02-25 | N | 66 | N | 12 | N | N | 1.1101 | 39.4971 | 66076.2691
[7 empty] | 8172 | 13423 | 1553548 | 2018-02-25 19:04 | 2018-02-25 22:10 | 186 | 11kV | 186 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 185929 Single phase DOLF : 10 Amp sub 16286 also had 2 10ADOLFs blown, when restored LF 75433 blew. see upo # 185931 also Excluded OMS 1553548 | February | 2018 | 2018Q3 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2018-02-25 | N | 186 | N | 12 | N | N | 1.1101 | 39.4971 | 135.9233
[7 empty] | 7467 | 4963 | 1553880 | 2018-02-25 20:15 | 2018-02-25 22:10 | 115 | 11kV | 1725 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 185931 C Phase DOLF : 10 Amp see also upo # 185929 Sub 16286 DOLFs also blown. Excluded oms 1553548 | February | 2018 | 2018Q3 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2018-02-25 | N | 115 | N | 12 | N | N | 1.1101 | 39.4971 | 1260.5791
[7 empty] | 8692 | 19935 | 1553579 | 2018-02-25 20:50 | 2018-02-25 22:22 | 92 | 11kV | 17296 | 188 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | The 11kV Recloser CP50015 tripped, reclosed, tripped and locked out on OC trip and Lockout Cause: Branch fell on OH adjacent to PT2108 Dons Quarry. | February | 2018 | 2018Q3 | 2018 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2018-02-25 | N | 92 | N | 12 | N | N | 1.1101 | 39.4971 | 12639.4067
[7 empty] | 8123 | 12897 | 1553485 | 2018-02-25 16:38 | 2018-02-26 02:18 | 580 | 11kV | 23036 | 287 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn14892 Charmhaven 11kv Pa5 "S14804 Arizona Borg" fdr tripped on Relays: A+B phase O/C, EFI, Tx1 Group E Signals: 11kv trip EFI's: S14804 S14758 S14416 S65925 note Electronic EFI S18601 did not operate Cause: not ascertained. OH 11kv mains appear to be missing (stolen) from LB44168 to LB44170 to AB44169. Needs further investigation in daylight hours. Note: LB44170 and LB44168 are sioalted, no access to AB44169 See 1553909,11,3 ex 1553485,1553535 | February | 2018 | 2018Q3 | 2018 | ZN14892:PA5 | ZN14892:PA5 | ZN14892/000005 | CENTRAL COAST | OH | Not Veg | 2018-02-25 | N | 80.2648 | N | 12 | N | N | 1.1101 | 39.4971 | 16834.0294
[7 empty] | 8389 | 16145 | 1553595 | 2018-02-25 23:02 | 2018-02-26 11:36 | 754 | 11kV | 47253 | 550 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | LID 185933 1 fault operation 3 phase Sensitive Earth Fault faulty transformer replaced under AP. Excluded OMS 1553595 | February | 2018 | 2018Q3 | 2018 | 213:33777 | 213:33777 | ZN00213/033777 | NEWCASTLE | OH | Not Veg | 2018-02-25 | N | 85.9145 | N | 12 | N | N | 1.1101 | 39.4971 | 34531.0987
[7 empty] | 7419 | 4090 | 1553693 | 2018-02-26 08:26 | 2018-02-26 12:30 | 244 | 11kV | 347608 | 3081 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | Zn10990 Arncliffe - Pnl.2 tripped on: B & C phase O/C Abnormal: LB31125 closed with AB3114 Open Garbage truck appears to have knocked pole KO-20366 on Cook St, Barwell Valley twice while emptying bin. See 1554192 1554195 LV//: 1554194 1554198 | February | 2018 | 2018Q3 | 2018 | ZN10990:PA2 | ZN10998:PA29 | ZN10998/000029 | BAYSIDE | OH | Not Veg | 2018-02-26 | N | 112.8231 | N | 4 | N | N | 1.1101 | 39.4971 | 254021.6737
[7 empty] | 7211 | 551 | 1553761 | 2018-02-26 09:40 | 2018-02-26 12:40 | 180 | 11kV | 103207 | 865 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 185941 1 fault operation A Phase Intellirupter, Overcurrent Burnt off tapping at UGOH pole VP-20656. Excluded OMS 1553761 | February | 2018 | 2018Q3 | 2018 | 243:80084 | 243:80084 | ZN00243/080084 | LAKE MACQUARIE | OH | Not Veg | 2018-02-26 | N | 119.3145 | N | 4 | N | N | 1.1101 | 39.4971 | 75420.6315
[7 empty] | 8011 | 11247 | 1553667 | 2018-02-26 11:50 | 2018-02-26 12:59 | 69 | 11kV | 1104 | 16 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Rain Heavy | N | Ex Zn12600 Lisarow section of Pa2 "Chamberlain Taylor 0.1" Fdr From LK41935 to AB41934 interrupted for safety reasons. Large tree resting on CCT See 1554217 ex 1553842,3 | February | 2018 | 2018Q3 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2018-02-26 | N | 69 | N | 4 | N | N | 1.1101 | 39.4971 | 806.7706
[7 empty] | 7268 | 1596 | 1553727 | 2018-02-26 09:12 | 2018-02-26 14:45 | 333 | 11kV | 4663 | 58 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 185942 2 fault operations Earth Fault Broken xarm sub 2899 Excluded OMS 1553727, 1553839 | February | 2018 | 2018Q3 | 2018 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2018-02-26 | N | 80.3966 | N | 4 | N | N | 1.1101 | 39.4971 | 3407.5829
[7 empty] | 7721 | 7712 | 1554129 | 2018-02-27 09:33 | 2018-02-27 11:00 | 87 | 11kV | 87 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 185946 Single phase DOLF : 10 Amp Excluded OMS 1554129 | February | 2018 | 2018Q3 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2018-02-27 | N | 87 | N | 3 | N | N | 1.1101 | 39.4971 | 63.577
[7 empty] | 8542 | 18067 | 1554231 | 2018-02-27 12:37 | 2018-02-27 16:10 | 213.1167 | 11kV | 2557.4 | 12 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 185952 Single phase 11kV wire on ground between S.70386 and 70586. Repaired under AP. | February | 2018 | 2018Q3 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2018-02-27 | N | 213.1167 | N | 3 | N | N | 1.1101 | 39.4971 | 1868.8725
[7 empty] | 8488 | 17471 | 1554345 | 2018-02-27 18:00 | 2018-02-27 19:33 | 93 | 11kV | 116994 | 1379 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn36200 Empire Bay Pa1 "Empire Bay Aux" fdr tripped, reclosed, tripped and locked out Relays: 50TBC Cause: tree/branch on OH mains. Branch on 11kv mains near PT12286 See 1554645 ex 1554345 | February | 2018 | 2018Q3 | 2018 | ZN36200:PA1 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Veg | 2018-02-27 | N | 84.8397 | N | 3 | N | N | 1.1101 | 39.4971 | 85495.7645
[7 empty] | 8254 | 14454 | 1554501 | 2018-02-28 14:56 | 2018-02-28 15:51 | 55 | 11kV | 55 | 1 | HV | Fire (Non Ausgrid) | UNKNOWN | DC Not Transformer | Unplanned | No Weather Impact | N | At S167 Auburn 11kv Panel No.17 "S8103 Derby Sutter No3" feeder tripped on Relays: A+B+C O/C, EFI, Fault Check Signals: Tx5 group E, 11kv trip, Batt Charge defect Remarks: Fire. S8993 Derby Stutter No4 has caught on fire, Sw/A is normally open, see seperate interruption report @ S2466 Flemington Panel No.7 | February | 2018 | 2018Q3 | 2018 | ZN167:PA17 | ZN167:PA17 | ZN00167/000017 | PARRAMATTA | UG | Not Veg | 2018-02-28 | N | 55 | N | 2 | N | N | 1.1101 | 39.4971 | 40.1924
[7 empty] | 8086 | 12261 | 1554500 | 2018-02-28 14:56 | 2018-02-28 15:54 | 58 | 11kV | 15851 | 275 | HV | Fire (Non Ausgrid) | UNKNOWN | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S2466 Flemington 11kv Panel No.7 "S8376 Carnarvon Day" feeder tripped on: Relays: O/C, EFI, Trip Signals: 11kv trip, Tx4 Group E Remarks: fire. See seperate interruption report on panel No17 @ Auburn, S8993 Derby Sutter No.4 caught fire | February | 2018 | 2018Q3 | 2018 | ZN2466:PA7 | ZN2466:PA7 | ZN02466/000007 | PARRAMATTA | Unknown | Not Veg | 2018-02-28 | N | 57.64 | N | 2 | N | N | 1.1101 | 39.4971 | 11583.4433
[7 empty] | 8169 | 13377 | 1554609 | 2018-03-01 07:06 | 2018-03-01 10:35 | 209 | 11kV | 63395 | 1317 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At 847 Hornsby Panel 46 tripped on A and C phase IOC with timing , lockout and fault check Signals: Zone and TX3 Group Earth with EFI. Cause: Crane into 11kV mains cnr Mills and Pacific at Hornsby See OMS 1556882 1556883 1556884 1554609 1554632 | March | 2018 | 2018Q3 | 2018 | ZN847:PA46 | ZN847:PA46 | ZN00847/000046 | HORNSBY | OH | Not Veg | 2018-03-01 | N | 48.1359 | N | 1 | N | N | 1.1101 | 39.4971 | 46327.1962
[7 empty] | 7420 | 4104 | 1554816 | 2018-03-02 08:42 | 2018-03-02 08:55 | 13 | 11kV | 5304 | 408 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | ZN2466 Flemington: Ex 11kv feeder Panel 12 '698 Mons St' Sw/A at S3620 Tooheys Lidcombe tripped on Relays: B phase IOC, Directional O/C and E/F Signals: nil Abnormal: 11kv Panel 12 at Zn2466 Flemington was open for SAO 421396 Remarks: cause not ascertained. 11kv Underground fault from S3620 Tooheys Lidcombe Sw/A to S4025 Frances Edith to S1653 Edith Frances. Strange noise in S3620 Tooheys Lidcombe coming from Sw/A 11kv C/B. Substation danger tagged tilled interruption with Tooheys HVC can be arranged. Sw/tag for feeder on Sw/A at S3620 | March | 2018 | 2018Q3 | 2018 | ZN2466:PA12 | ZN2466:PA12 | ZN02466/000012 | CUMBERLAND | UG | Not Veg | 2018-03-02 | N | 13 | N | 5 | N | N | 1.1101 | 39.4971 | 3876.0068
[7 empty] | 8435 | 16754 | 1554864 | 2018-03-02 11:53 | 2018-03-02 13:30 | 97.5 | 11kV | 975 | 10 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 185981 C Phase DOLF : 20 Amp CHANGED CROSSARM 11KV | March | 2018 | 2018Q3 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2018-03-02 | N | 97.5 | N | 5 | N | N | 1.1101 | 39.4971 | 712.5012
[7 empty] | 8324 | 15220 | 1554911 | 2018-03-02 16:10 | 2018-03-02 19:10 | 180 | 11kV | 360 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 185987 May have neen the cause of earlier blown Line Dolf at LF 10381. LID # 185981 Excluded OMS 1554911. | March | 2018 | 2018Q3 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2018-03-02 | N | 180 | N | 5 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 8171 | 13413 | 1555753 | 2018-03-02 17:15 | 2018-03-02 19:25 | 130 | 11kV | 130 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | At S76843 West Connex NO1 HVC tripped on on A phase OC Cause: Interruption has happened before, Customer states Ausgrid know about the issue and need to look at protection settings. T/PE notified by DOp to investigate | March | 2018 | 2018Q3 | 2018 |  |  |  |  | UG | Not Veg | 2018-03-02 | N | 130 | N | 5 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 7392 | 3767 | 1554973 | 2018-03-02 20:00 | 2018-03-03 16:25 | 1225 | 11kV | 22855 | 55 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 185991 Fdr interrupted to extinguish fire at sub 70601. Fdr interrupted to replace burnt pole & sub. Excluded OMS No. 1554973 + 1554998 | March | 2018 | 2018Q3 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2018-03-02 | N | 415.5455 | N | 5 | N | N | 1.1101 | 39.4971 | 16701.7599
[7 empty] | 7291 | 2004 | 1555837 | 2018-03-03 17:25 | 2018-03-03 17:55 | 30 | 11kV | 180 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of pa2 CB44323 to CP44605 interrupted for safety/repair LV fuse assembly melting @ PT13306 The Ridgeway Awabakil | March | 2018 | 2018Q3 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2018-03-03 | N | 30 | N | 3 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 8125 | 12925 | 1555100 | 2018-03-03 20:23 | 2018-03-03 22:50 | 147 | 11kV | 1764 | 12 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa1 "Dog Trap Gully" PT12706 Excelsior Ourimbah 11kv HDO fuse roadside phase 10amp Cause: fuse fatigue, replaced See 1555841 ex 1555100 | March | 2018 | 2018Q3 | 2018 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Not Veg | 2018-03-03 | N | 147 | N | 3 | N | N | 1.1101 | 39.4971 | 1289.0792
[7 empty] | 8258 | 14488 | 1555095 | 2018-03-03 19:24 | 2018-03-04 00:50 | 326 | 11kV | 28695 | 250 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn13000 Lake Munmorah Pa4 "pacific Hwy North" tripped, reclosed & tripped Relays: Signals: B phase O/C, OC trip, Prot trip NL, Prot trip timer/latched, SEL, AR Lockout EFI's Cause: OH Down before PT13515 See 1555838,9,40 ex 1555095 | March | 2018 | 2018Q3 | 2018 | ZN13000:PA4 | ZN13000:PA4 | ZN13000/000004 | CENTRAL COAST | OH | Not Veg | 2018-03-03 | N | 114.78 | N | 3 | N | N | 1.1101 | 39.4971 | 20969.4596
[7 empty] | 8555 | 18305 | 1555123 | 2018-03-04 02:36 | 2018-03-04 03:58 | 82 | 11kV | 45018 | 549 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington @0236 Pa1 Tripped on Earth Fault and EFI @0350 Pa20 Tripped @0426 Pa11 Tripped on OC and EF @0426 Pa32 tripped on B phase OC @0426 Pa29 tripped on A phase OC @0426 TX3A and TX3B Tripped with No relay indications Abnormal Switching: SW/A @ S65220 Closed, SW/B @ CP110 Open (Cable Fault) Cause: 5 11kV Feeders failed (fire event) in cable tunnel under the M4 roadway south of Flemington Zone See OMS 1556124 - 1556357 | March | 2018 | 2018Q3 | 2018 | ZN2466:PA1 | ZN36000:PA26 | ZN36000/000026 | STRATHFIELD | UG | Not Veg | 2018-03-04 | N | 82 | N | 23 | Y | Y | 1.1101 | 39.4971 | 32897.8266
[7 empty] | 7182 | 108 | 1555282 | 2018-03-04 14:14 | 2018-03-04 15:34 | 80 | 11kV | 27040 | 338 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186002 2 fault operations | March | 2018 | 2018Q3 | 2018 | 513:48057 | 513:83497 | ZN00513/083497 | SINGLETON | OH | Veg | 2018-03-04 | N | 80 | N | 23 | Y | Y | 1.1101 | 39.4971 | 19760.0345
[7 empty] | 8062 | 11968 | 1556239 | 2018-03-04 14:08 | 2018-03-04 18:36 | 268 | 11kV | 94492 | 457 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186001 2 fault operations B Phase Overcurrent OMS None. System not working. Please Patrol Targets Required | March | 2018 | 2018Q3 | 2018 | 523:33509 | 523:33509 | ZN00523/033509 | SINGLETON | OH | Veg | 2018-03-04 | N | 206.7659 | N | 23 | Y | Y | 1.1101 | 39.4971 | 69051.9666
[7 empty] | 7861 | 9416 | 1555549 | 2018-03-04 14:24 | 2018-03-04 19:20 | 296 | 11kV | 120176 | 502 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186007 2 fault operations Various feeder hazards | March | 2018 | 2018Q3 | 2018 | 513:48058 | 513:83504 | ZN00513/083504 | SINGLETON | OH | Veg | 2018-03-04 | N | 239.3944 | N | 23 | Y | Y | 1.1101 | 39.4971 | 87821.0762
[7 empty] | 7886 | 9825 | 1555528 | 2018-03-04 19:27 | 2018-03-04 20:20 | 53 | 11kV | 71119 | 1781 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Panel 64 tripped on SEF Signals: 11kV trip with EFI Cause: Balloon on 11kV UGOH at S2560 Park High - Suspect UGO damage See OMS 1556806 1556807 1556808 1555528/31/32/33/34/36/38 | March | 2018 | 2018Q3 | 2018 | ZN129:PA64 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Veg | 2018-03-04 | N | 39.9321 | N | 23 | Y | Y | 1.1101 | 39.4971 | 51971.6675
[7 empty] | 8533 | 17983 | 1555251 | 2018-03-04 13:55 | 2018-03-04 21:05 | 430 | 11kV | 146200 | 340 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 186013 2 fault operations B & C Phase Overcurrent Excluded OMS 1555251 | March | 2018 | 2018Q3 | 2018 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2018-03-04 | N | 430 | N | 23 | Y | Y | 1.1101 | 39.4971 | 106838.6478
[7 empty] | 8100 | 12506 | 1555740 | 2018-03-04 16:12 | 2018-03-04 22:36 | 384 | 11kV | 25214 | 71 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Electrical Storm | N | LID 186030 1 fault operation Burnt up ABS 4803 | March | 2018 | 2018Q3 | 2018 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2018-03-04 | N | 355.1268 | N | 23 | Y | Y | 1.1101 | 39.4971 | 18425.6475
[7 empty] | 7544 | 5770 | 1555564 | 2018-03-04 20:27 | 2018-03-04 23:20 | 173 | 11kV | 692 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186028 Single phase DOLF : 10 Amp | March | 2018 | 2018Q3 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2018-03-04 | N | 173 | N | 23 | Y | Y | 1.1101 | 39.4971 | 505.6932
[7 empty] | 8602 | 18871 | 1555286 | 2018-03-04 14:20 | 2018-03-05 01:34 | 674 | 11kV | 206914 | 321 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186006 2 Fault operations | March | 2018 | 2018Q3 | 2018 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2018-03-04 | N | 644.5919 | N | 23 | Y | Y | 1.1101 | 39.4971 | 151206.6483
[7 empty] | 8526 | 17913 | 1555503 | 2018-03-04 18:59 | 2018-03-05 02:05 | 426 | 11kV | 13057 | 37 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186026 B & C Phase DOLF : 20 Amp Excluded OMS 1555503 | March | 2018 | 2018Q3 | 2018 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2018-03-04 | N | 352.8919 | N | 23 | Y | Y | 1.1101 | 39.4971 | 9541.6705
[7 empty] | 8203 | 13796 | 1555300 | 2018-03-04 14:32 | 2018-03-05 02:07 | 695 | 11kV | 88965 | 144 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 186011 2 fault operations Various feeder hazards | March | 2018 | 2018Q3 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-03-04 | N | 617.8125 | N | 23 | Y | Y | 1.1101 | 39.4971 | 65012.998
[7 empty] | 8297 | 14965 | 1555527 | 2018-03-04 14:06 | 2018-03-05 03:23 | 797 | 11kV | 125818 | 199 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186000 2 fault operations Overcurrent trees on mians Excluded OMS 1555527 | March | 2018 | 2018Q3 | 2018 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2018-03-04 | N | 632.2513 | N | 23 | Y | Y | 1.1101 | 39.4971 | 91944.0834
[7 empty] | 7919 | 10130 | 1555542 | 2018-03-04 19:59 | 2018-03-05 03:31 | 452 | 11kV | 2260 | 5 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186034 C Phase DOLF : 10 Amp Excluded OMS 1555542 | March | 2018 | 2018Q3 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-03-04 | N | 452 | N | 23 | Y | Y | 1.1101 | 39.4971 | 1651.5413
[7 empty] | 8539 | 18036 | 1555526 | 2018-03-04 19:32 | 2018-03-05 04:22 | 530.3 | 11kV | 50378.5 | 95 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 186032 B Phase wire down at pole GU-53188 wire down pole gu-53188. section isolated for repair | March | 2018 | 2018Q3 | 2018 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2018-03-04 | N | 530.3 | N | 23 | Y | Y | 1.1101 | 39.4971 | 36815.1219
[7 empty] | 7910 | 10010 | 1555126 | 2018-03-04 04:17 | 2018-03-05 07:50 | 1653 | 11kV | 742226 | 999 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington @0236 Pa1 Tripped on Earth Fault and EFI @0350 Pa20 Tripped @0426 Pa11 Tripped on OC and EF @0426 Pa32 tripped on B phase OC @0426 Pa29 tripped on A phase OC @0426 TX3A and TX3B Tripped with No relay indications Abnormal Switching: SW/A @ S65220 Closed, SW/B @ CP110 Open (Cable Fault) Cause: 5 11kV Feeders failed (fire event) in cable tunnel under the M4 roadway south of Flemington Zone See OMS 1556124 - 1556357 | March | 2018 | 2018Q3 | 2018 | ZN2466:PA1 | ZN36000:PA26 | ZN36000/000026 | CUMBERLAND | UG | Not Veg | 2018-03-04 | N | 742.969 | N | 23 | Y | Y | 1.1101 | 39.4971 | 542396.8688
[7 empty] | 8285 | 14784 | 1562715 | 2018-03-05 07:46 | 2018-03-05 08:45 | 59 | 11kV | 84975 | 1535 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.3 tripped on: Earth Leakage Field EFIs: S3682 S2275 S1831 S3364 UG cable fault from S3364 to S2548 See 1562715 1562716 | March | 2018 | 2018Q3 | 2018 | ZN2602:PA3 | ZN2602:PA29 | ZN02602/000029 | RANDWICK | UG | Not Veg | 2018-03-05 | N | 55.3583 | N | 5 | N | N | 1.1101 | 39.4971 | 62097.2237
[7 empty] | 7854 | 9386 | 1555573 | 2018-03-04 17:38 | 2018-03-05 11:40 | 1082 | 11kV | 3246 | 3 | HV | Wind Blown Debris | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186036 A Phase DOLF : 16 Amp sheet of iron on mains Excluded oms 1555573,1555580 | March | 2018 | 2018Q3 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2018-03-04 | N | 1082 | N | 23 | Y | Y | 1.1101 | 39.4971 | 2372.0811
[7 empty] | 8433 | 16742 | 1555611 | 2018-03-04 14:00 | 2018-03-05 12:00 | 1320 | 11kV | 11880 | 9 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186029 Mains down between subs s51928 & s. 51953 tree into 11kV, 1 span down. work complete, cannot close until device is closed. | March | 2018 | 2018Q3 | 2018 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2018-03-04 | N | 1320 | N | 23 | Y | Y | 1.1101 | 39.4971 | 8681.5536
[7 empty] | 8376 | 15861 | 1555294 | 2018-03-04 14:19 | 2018-03-05 12:24 | 1325 | 11kV | 56040 | 285 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186019 2 fault operations Excluded OMS 1555294 | March | 2018 | 2018Q3 | 2018 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2018-03-04 | N | 196.6316 | N | 23 | Y | Y | 1.1101 | 39.4971 | 40952.3791
[7 empty] | 7299 | 2107 | 1556280 | 2018-03-04 14:13 | 2018-03-05 13:30 | 1397 | 11kV | 150583 | 232 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186003 2 fault operations | March | 2018 | 2018Q3 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2018-03-04 | N | 649.0647 | N | 23 | Y | Y | 1.1101 | 39.4971 | 110041.615
[7 empty] | 8470 | 17298 | 1555253 | 2018-03-04 13:52 | 2018-03-05 14:48 | 1496 | 11kV | 404337 | 520 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 186015 2 fault operations mains on arm pole MT-90570 Excluded OMS 1555253, 1555290 | March | 2018 | 2018Q3 | 2018 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2018-03-04 | N | 777.5712 | N | 23 | Y | Y | 1.1101 | 39.4971 | 295477.5537
[7 empty] | 7438 | 4506 | 1555628 | 2018-03-05 05:44 | 2018-03-05 15:00 | 556 | 11kV | 1112 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 186045 C Phase DOLF : 10 Amp Excluded OMS 1555628 | March | 2018 | 2018Q3 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2018-03-05 | N | 556 | N | 5 | N | N | 1.1101 | 39.4971 | 812.6168
[7 empty] | 8398 | 16301 | 1563125 | 2018-03-05 00:04 | 2018-03-05 16:00 | 956 | 11kV | 12428 | 13 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 186046 A & C Phase DOLF : 10 Amp tree on mains at poles FO-60252 & FO-60251 beyond links 43155. links opened and line fuses restored. section beyond links requires repair Note: all customers were a part of larger wider area outage that began at 04/03/2018 14:32 see OMS 1556574 | March | 2018 | 2018Q3 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2018-03-05 | N | 956 | N | 5 | N | N | 1.1101 | 39.4971 | 9082.0158
[7 empty] | 8369 | 15789 | 1555510 | 2018-03-04 14:30 | 2018-03-05 16:30 | 1560 | 11kV | 57710 | 116 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 186010 1 fault operation Broken crossarm at pole FO-10180 | March | 2018 | 2018Q3 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-03-04 | N | 497.5 | N | 23 | Y | Y | 1.1101 | 39.4971 | 42172.7658
[7 empty] | 8198 | 13718 | 1555625 | 2018-03-05 04:43 | 2018-03-05 19:01 | 858 | 11kV | 3432 | 4 | HV | Wind Blown Debris | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Replaced 10A DOLF Note: No LID raised, info based on record 1555625 | March | 2018 | 2018Q3 | 2018 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2018-03-05 | N | 858 | N | 5 | N | N | 1.1101 | 39.4971 | 2508.0044
[7 empty] | 7590 | 6172 | 1556056 | 2018-03-05 19:52 | 2018-03-05 20:27 | 35 | 11kV | 57505 | 1643 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN9245 Engadine 11kv P19 "AB35583" tripped to lockout on: Relays: A&B phase IOC, EF, EFI, Timing and Lockout Signals: 11kv trip Field EFI's: Latana Rd near Kingswood, S46983 Abnormal: Sw/A closed at S9356 Mannikin Willaroo, Sw/B open at S9985 Spoonbill Harrier Remarks: Animals/Birds. Possum on HV UGOH. CNR Kingswood and Geneva | March | 2018 | 2018Q3 | 2018 | ZN9245:PA19 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | OH | Not Veg | 2018-03-05 | N | 35 | N | 5 | N | N | 1.1101 | 39.4971 | 42022.9579
[7 empty] | 7774 | 8392 | 1555266 | 2018-03-04 13:54 | 2018-03-05 20:48 | 1854 | 11kV | 41538 | 70 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186014 2 fault operations Various hazards on feeder | March | 2018 | 2018Q3 | 2018 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2018-03-04 | N | 593.4 | N | 23 | Y | Y | 1.1101 | 39.4971 | 30354.7452
[7 empty] | 7418 | 4061 | 1556100 | 2018-03-06 04:43 | 2018-03-06 06:27 | 104 | 11kV | 216275 | 2211 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 186055 2 fault operations B & C Phase Overcurrent Excluded OMS 1556100 | March | 2018 | 2018Q3 | 2018 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Veg | 2018-03-06 | N | 97.8177 | N | 1 | N | N | 1.1101 | 39.4971 | 158047.391
[7 empty] | 7193 | 293 | 1555522 | 2018-03-04 14:44 | 2018-03-06 13:00 | 2776 | 11kV | 41230 | 54 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186012 2 fault operations various defects beyond ABS 40716 | March | 2018 | 2018Q3 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-03-04 | N | 763.5185 | N | 23 | Y | Y | 1.1101 | 39.4971 | 30129.6679
[7 empty] | 7339 | 2803 | 1556508 | 2018-03-07 09:44 | 2018-03-07 12:40 | 176 | 11kV | 1056 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186068 A & C Phase DOLF : 10 Amp Excluded OMS 1556508 | March | 2018 | 2018Q3 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-03-07 | N | 176 | N | 2 | N | N | 1.1101 | 39.4971 | 771.6937
[7 empty] | 7677 | 7084 | 1556595 | 2018-03-07 15:05 | 2018-03-07 17:29 | 144 | 11kV | 14026 | 100 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN2196 Milperra 11kv VCB panel 20 "S7056" feeder tripped on - Relays: EFI, B phase earth fault Field EFI's: 7056, 2347 Signals: 11kv trip Remarks: UG fault. Ex Zn2196 Milperra 11kv VCB panel 20 "S7056" feeder. 11kv UG fault between S2347 Woorang St to S2484 Milperra Woo No.1 | March | 2018 | 2018Q3 | 2018 | ZN2196:PA20 | ZN2196:PA20 | ZN02196/000020 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-03-07 | N | 140.26 | N | 2 | N | N | 1.1101 | 39.4971 | 10249.7871
[7 empty] | 7534 | 5690 | 1556801 | 2018-03-08 13:30 | 2018-03-08 15:15 | 105.3833 | 11kV | 105.3833 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Fuse Assembly | Unplanned | No Weather Impact | N | dolf line side contact arced to failure CC1: 22-"Refer to SOp" | March | 2018 | 2018Q3 | 2018 |  |  |  | MUSWELLBROOK | OH | Not Veg | 2018-03-08 | N | 105.3833 | N | 1 | N | N | 1.1101 | 39.4971 | 77.011
[7 empty] | 8356 | 15607 | 1556924 | 2018-03-09 06:37 | 2018-03-09 07:49 | 72 | 11kV | 84958 | 1188 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn15001 Brookvale 11kV panel 8 tripped on Relays: IOC Trip Field EFI's NIL DMA: 11kV Feeder between S49078 to S16693 - Closed SW/A @ S46569 Cause: Flash Over caused by Brid @ UGOH, Cnr of Harbord and Abbot Rd - No apparent damage See OMS 1557337 1557339 1556924 | March | 2018 | 2018Q3 | 2018 | ZN15001:PA8 | ZN15001:PA8 | ZN15001/000008 | NORTHERN BEACHES | OH | Not Veg | 2018-03-09 | N | 71.5135 | N | 2 | N | N | 1.1101 | 39.4971 | 62084.8006
[7 empty] | 8679 | 19785 | 1557070 | 2018-03-09 18:45 | 2018-03-09 20:41 | 116 | 11kV | 134917 | 1191 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | At Zn15010 11kV panel 21 (Bus Tie feeder) tripped on Relays: A and C phase Inst OC Cause: 11kV UG fault from ZN15010 Careel Bay Panel 12 to S17095 See OMS 1557350 1557382 1557070 | March | 2018 | 2018Q3 | 2018 | ZN15010:PA21 | ZN15010:PA28 | ZN15010/000028 | NORTHERN BEACHES | UG | Not Veg | 2018-03-09 | N | 113.2804 | N | 2 | N | N | 1.1101 | 39.4971 | 98593.3642
[7 empty] | 8400 | 16316 | 1557123 | 2018-03-10 11:27 | 2018-03-10 12:40 | 73 | 11kV | 73 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186096 C phase DOLF Excluded OMS 1557123 | March | 2018 | 2018Q3 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2018-03-10 | N | 73 | N | 1 | N | N | 1.1101 | 39.4971 | 53.3462
[7 empty] | 7743 | 7914 | 1557184 | 2018-03-11 04:40 | 2018-03-11 05:57 | 77 | 11kV | 69223 | 899 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.19 tripped to lock out on: B & C Phase IOC Field EFIs: S50482 S0483 S10040 S10954 S10898 S10605 Possum caused flashover at UGOH to S10082. No apparent damage. | March | 2018 | 2018Q3 | 2018 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2018-03-11 | N | 77 | N | 1 | N | N | 1.1101 | 39.4971 | 50586.1267
[7 empty] | 7668 | 7016 | 1557312 | 2018-03-12 11:50 | 2018-03-12 14:25 | 155 | 11kV | 42780 | 276 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186100 no protection operation section isolated to repair ohm pole HW-80085 Excluded oms # 1557312 & 1557348 | March | 2018 | 2018Q3 | 2018 | 243:80078 | 243:80078 | ZN00243/080078 | LAKE MACQUARIE | OH | Not Veg | 2018-03-12 | N | 155 | N | 4 | N | N | 1.1101 | 39.4971 | 31262.3622
[7 empty] | 8688 | 19882 | 1557402 | 2018-03-12 15:04 | 2018-03-12 17:15 | 131 | 11kV | 167288 | 2193 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.4 tripped, reclosed and locked out on: B & C phase IOC Field EFIs: S49537 S50745 S48983 UGOH adjacent to LB30349 failed explosively. See 1557713 1557714 | March | 2018 | 2018Q3 | 2018 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | Unknown | Unknown | 2018-03-12 | N | 76.2827 | N | 4 | N | N | 1.1101 | 39.4971 | 122249.1362
[7 empty] | 8643 | 19406 | 1557472 | 2018-03-12 17:10 | 2018-03-12 21:48 | 278 | 11kV | 1946 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 186108 Blown tapping at pole JP-85042. No protection operated. Low volts beyond above pole, just upstream of ABS 25953. Excluded OMS 1557472 | March | 2018 | 2018Q3 | 2018 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2018-03-12 | N | 278 | N | 4 | N | N | 1.1101 | 39.4971 | 1422.0794
[7 empty] | 8146 | 13138 | 1557520 | 2018-03-12 21:47 | 2018-03-12 23:03 | 76 | 11kV | 153368 | 2018 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn36300 Balgowlah North 11kV panel 3 tripped on Relays: A and B phase IOC, Fault Check, EFI Cause: Customer reports pf dead possum at the base of pole near 1 Lauderdale Ave See OMS 1557520 1557530 1557528 1557527 | March | 2018 | 2018Q3 | 2018 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Veg | 2018-03-12 | N | 76 | N | 4 | N | N | 1.1101 | 39.4971 | 112076.8108
[7 empty] | 8334 | 15291 | 1557556 | 2018-03-13 06:49 | 2018-03-13 07:57 | 68 | 11kV | 476 | 7 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn1610 Homebush Bay - 11kv Panel No.5 "Sub 5324 Superdome No.1" feeder tripped Relays: Earth fault, EFI Signals: 11kv Trip, No.1 Group Earth Field EFI's: Nil Remarks: UG fault. 11kv UG fault from Zn 1610 Homebush Bay Panel No.5 to S5324 Superdome No.1 | March | 2018 | 2018Q3 | 2018 | ZN1610:PA5 | ZN1610:PA5 | ZN01610/000005 | PARRAMATTA | UG | Not Veg | 2018-03-13 | N | 68 | N | 4 | N | N | 1.1101 | 39.4971 | 347.8468
[7 empty] | 8338 | 15320 | 1557666 | 2018-03-13 12:31 | 2018-03-13 16:30 | 239 | 11kV | 6156 | 114 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | zn12650 West Gosford Pa5 fdr has tripped Signals: 11kv trip Relays: IOC C Phase, Earth Fautl, EFI, FC EFI's: Nil Abnormal: West gosford was on standby supply with normal offloaded Cause: Excavator hit cables outside 75 holden rd Located electrically between Pa5 to S18166SwA tee S18231, No.1 Cap See 1557666 ex 1557671 | March | 2018 | 2018Q3 | 2018 | ZN12650:PA5 | ZN12650:PA5 | ZN12650/000005 | CENTRAL COAST | UG | Not Veg | 2018-03-13 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 4498.6232
[7 empty] | 8715 | 20284 | 1557588 | 2018-03-13 08:42 | 2018-03-13 18:05 | 563 | 11kV | 73714.9333 | 133 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of Panel 21 Lindfield Panel 21 from SW/B @ S50198 to LB185 tee PT61979 Shirley Glen and PT116 Toongarrah Shirley interrupted for emergency repairs. Cause: Large Tree fallen over in Glen Rd Lindfield. See OMS 1557588 1557641 1557641 1557585 | March | 2018 | 2018Q3 | 2018 | ZN1193:PA21 | ZN1193:PA21 | ZN01193/000021 | KU-RING-GAI | OH | Veg | 2018-03-13 | N | 554.2476 | N | 4 | N | N | 1.1101 | 39.4971 | 53868.6991
[7 empty] | 8279 | 14707 | 1557853 | 2018-03-13 20:19 | 2018-03-13 21:30 | 71 | 11kV | 1352 | 22 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Rain Heavy | N | @ZN3600 Olympic Park, 11kv Panel 12 'Olympic Park Aux No.2' feeder tripped Relays: ABC O/C, ABC O/C Instantaneous Signals: 11kv trip Remarks: end box fault. End box sw/r on No.2 RMI failed at S6564 John Sands Underwood Rd | March | 2018 | 2018Q3 | 2018 | ZN36000:PA12 | ZN36000:PA12 | ZN36000/000012 | PARRAMATTA | Unknown | Not Veg | 2018-03-13 | N | 61.4545 | N | 4 | N | N | 1.1101 | 39.4971 | 988.0017
[7 empty] | 8465 | 17223 | 1557880 | 2018-03-14 03:44 | 2018-03-14 04:55 | 71 | 11kV | 72988 | 1028 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn14143 Somersby Pa5 labelled Karion fdr tripped on A & B phase Earth Fautl 11kv trip Cause: animals/birds. possum removed from UGOH near LB40492 CC1: 22-"Refer to SOp" | March | 2018 | 2018Q3 | 2018 | ZN14143:PA5 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Not Veg | 2018-03-14 | N | 71 | N | 3 | N | N | 1.1101 | 39.4971 | 53337.4776
[7 empty] | 7508 | 5470 | 1557935 | 2018-03-14 08:25 | 2018-03-14 12:13 | 228 | 11kV | 228 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | At S5318 Eldridge sim N02 11kv RMI tripped on - HV fuse 75A OEFMA "A" phase Remarks: customers main switch was also tripped, advised to get own electrician to restore supply | March | 2018 | 2018Q3 | 2018 | ZN1850:PA3 | ZN2196:PA26 | ZN02196/000026 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2018-03-14 | N | 228 | N | 3 | N | N | 1.1101 | 39.4971 | 166.6157
[7 empty] | 8105 | 12572 | 1557972 | 2018-03-14 09:48 | 2018-03-14 15:30 | 342 | 11kV | 3585 | 48 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Rain Heavy | N | At S1290 Leightonfield 11kv Panel 17 "S7102 Birmingham Chris No1" feeder tripped on: Relays: EFI, No other flag down on relay Signals: 11kv trip, Zone e , Group tx3 earth At S736 Taubmans 11kv RMCB tripped on: Relays: A phase timed O/C, EFI Remarks: At S736 Taubmans, Fault on HVC, customers switchgear is damaged beyond metering unit. T/PE notified of grading issue and nil flag down on Panel 17 | March | 2018 | 2018Q3 | 2018 | ZN1290:PA17 | ZN1290:PA17 | ZN01290/000017 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2018-03-14 | N | 74.6875 | N | 3 | N | N | 1.1101 | 39.4971 | 2619.8123
[7 empty] | 8625 | 19160 | 1558162 | 2018-03-15 02:53 | 2018-03-15 05:44 | 171 | 11kV | 194760 | 1508 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 186136 Targets Sw 80364 = A phase O/C, E/F Fdr back on load with no fault found. Daylight patrol required. Excluded oms 1558162 | March | 2018 | 2018Q3 | 2018 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2018-03-15 | N | 129.1512 | N | 4 | N | N | 1.1101 | 39.4971 | 142324.8636
[7 empty] | 8407 | 16479 | 1558216 | 2018-03-15 08:22 | 2018-03-15 08:31 | 9 | 11kV | 3582 | 398 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.42 tripped on: A & C phase O/C All Field EFIs down to S49289 Abnormal: S49289 (Sw/B) open for D/R421950. Work to commission new sub failed on energising from S49289 | March | 2018 | 2018Q3 | 2018 | ZN2568:PA42 | ZN2568:PA42 | ZN02568/000042 | INNER WEST | UG | Not Veg | 2018-03-15 | N | 9 | N | 4 | N | N | 1.1101 | 39.4971 | 2617.6199
[7 empty] | 7248 | 1229 | 1558214 | 2018-03-15 08:19 | 2018-03-15 10:38 | 139 | 11kV | 834 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Replaced Dolf Note: No LID report raised, based info from record OMS 1558214 | March | 2018 | 2018Q3 | 2018 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2018-03-15 | N | 139 | N | 4 | N | N | 1.1101 | 39.4971 | 609.4626
[7 empty] | 8583 | 18612 | 1558164 | 2018-03-15 03:05 | 2018-03-15 16:50 | 825 | 11kV | 97675 | 1171 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 186137 1 fault operation B Phase Instantaneous overcurrent Target Sw 8691 = B phase 50T Blown tapping pole JV-70035. Excluded OMS 1558164 1558182 | March | 2018 | 2018Q3 | 2018 | 220:8691 | 220:8691 | ZN00220/008691 | LAKE MACQUARIE | OH | Not Veg | 2018-03-15 | N | 83.4116 | N | 4 | N | N | 1.1101 | 39.4971 | 71378.0091
[7 empty] | 8350 | 15526 | 1558404 | 2018-03-16 02:05 | 2018-03-16 03:27 | 82 | 11kV | 80770 | 985 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S3154 St Ives panel 10 tripped on A phase IOC and Timed OC and EFI Cause: Possum at PT297 The Mail Surrey | March | 2018 | 2018Q3 | 2018 | ZN3154:PA10 | ZN3154:PA10 | ZN03154/000010 | KU-RING-GAI | OH | Not Veg | 2018-03-16 | N | 82 | N | 2 | N | N | 1.1101 | 39.4971 | 59024.3337
[7 empty] | 8351 | 15537 | 1559200 | 2018-03-16 21:03 | 2018-03-16 22:30 | 87 | 11kV | 87 | 1 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | S.76843 West Connex St Peters Temp No.1 - 11kV RMCB tripped on: O/C Overload. Customer suspects grading issue. To be investigated | March | 2018 | 2018Q3 | 2018 |  |  |  |  | Unknown | Not Veg | 2018-03-16 | N | 87 | N | 2 | N | N | 1.1101 | 39.4971 | 63.577
[7 empty] | 7279 | 1826 | 1559204 | 2018-03-17 04:00 | 2018-03-17 05:55 | 115 | 11kV | 115 | 1 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | S.76843 West Connex St Peters Temp No.1 - 11kV RMCB tripped on: O/C Overload. Customer suspects grading issue. To be investigated | March | 2018 | 2018Q3 | 2018 |  |  |  |  | Unknown | Not Veg | 2018-03-17 | N | 115 | N | 4 | N | N | 1.1101 | 39.4971 | 84.0386
[7 empty] | 8708 | 20140 | 1558561 | 2018-03-17 02:21 | 2018-03-17 07:50 | 329 | 11kV | 174258 | 1350 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 186166 2 fault operations 3 Phase Earth Fault Broken insulator string IS-62325 Excluded OMS 1558561. | March | 2018 | 2018Q3 | 2018 | 235:2123 | 235:2123 | ZN00235/002123 | NEWCASTLE | OH | Not Veg | 2018-03-17 | N | 129.08 | N | 4 | N | N | 1.1101 | 39.4971 | 127342.6067
[7 empty] | 8294 | 14917 | 1558615 | 2018-03-17 11:58 | 2018-03-17 14:33 | 154.9667 | 11kV | 17356.2667 | 112 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn15008 Harbord section of pa10 PT15283 Wyadra Av Centre phase HDO and carrier blown Cause: fuse fatigue. DOp isolated and restored via lv parrallel See 1558615 ex 1558616,8,23,32 | March | 2018 | 2018Q3 | 2018 | ZN15008:PA10 | ZN15008:PA10 | ZN15008/000010 | NORTHERN BEACHES | OH | Not Veg | 2018-03-17 | N | 154.9667 | N | 4 | N | N | 1.1101 | 39.4971 | 12683.4478
[7 empty] | 7217 | 647 | 1558586 | 2018-03-17 10:18 | 2018-03-17 21:00 | 642 | 11kV | 80908 | 1178 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 186169 2 fault operations A & C Phase Overcurrent Defective UGOH JU-71090 Excluded oms 1558586 | March | 2018 | 2018Q3 | 2018 | 261:81864 | 261:81864 | ZN00261/081864 | LAKE MACQUARIE | Unknown | Unknown | 2018-03-17 | N | 68.6825 | N | 4 | N | N | 1.1101 | 39.4971 | 59125.18
[7 empty] | 8064 | 11992 | 1558722 | 2018-03-18 12:57 | 2018-03-18 13:55 | 58 | 11kV | 116 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 186171 B Phase DOLF : 10 Amp excluded OMS 1558722, 1558727. | March | 2018 | 2018Q3 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2018-03-18 | N | 58 | N | 10 | N | N | 1.1101 | 39.4971 | 84.7694
[7 empty] | 8448 | 16934 | 1558725 | 2018-03-18 12:47 | 2018-03-18 15:10 | 143 | 11kV | 88143 | 877 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | At Zn1673 Turraqmurra Panel 13 tripped on Relays: A and B phase OC Signals: 11kV trip Field EFI's Nil Cause: OH down. 11kV Phase down See OMS 1559222 1559224 1558725 | March | 2018 | 2018Q3 | 2018 | ZN1673:PA13 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | OH | Not Veg | 2018-03-18 | N | 100.5051 | N | 10 | N | N | 1.1101 | 39.4971 | 64412.3046
[7 empty] | 8626 | 19212 | 1558796 | 2018-03-18 15:53 | 2018-03-18 17:50 | 117 | 11kV | 193167 | 1651 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | Zn12610 Long Jetty section of Pa23 CP61579 Wyong Cornish Rec tripped and locked out on Overcurrent, SEF and lockout Abnormal: Zn12610 Long Jetty Pa20 LB63553 open and def with LB61289 closed Cause: not ascertained. 11kv bond off at USL 40219 See 159194 ex 1558796,9 | March | 2018 | 2018Q3 | 2018 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Veg | 2018-03-18 | N | 117 | N | 10 | N | N | 1.1101 | 39.4971 | 141160.7461
[7 empty] | 8391 | 16183 | 1558861 | 2018-03-18 17:51 | 2018-03-18 19:27 | 96 | 11kV | 44988 | 526 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At S35400 North Sydney Panel 77 tripped on RelaysL A protection: A phase OC, Neutral, Earth Fault B Protection: A phase OC, Neutral, Earth Fault and EFI Cause: 11kV Endbox failed @ S6659 Edward Riley (SW/A) Dop inspected endbox and found cable fault with RMI intact. See OMS 1559209 1559210 1558861 | March | 2018 | 2018Q3 | 2018 | ZN35400:PA77 | ZN35400:PA77 | ZN35400/000077 | NORTH SYDNEY | UG | Not Veg | 2018-03-18 | N | 85.5285 | N | 10 | N | N | 1.1101 | 39.4971 | 32875.9035
[7 empty] | 8124 | 12921 | 1558765 | 2018-03-18 14:34 | 2018-03-18 19:35 | 301.4333 | 11kV | 11755.9 | 39 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Ex Zn14891 Wyong section of Pa12 CP46228 Ravensdale Recloser tripped and locked out on C phase and Earth Fault Cause: tree branch brought down oh CC1: 22-"Refer to SOp" | March | 2018 | 2018Q3 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2018-03-18 | N | 301.4333 | N | 10 | N | N | 1.1101 | 39.4971 | 8590.865
[7 empty] | 8709 | 20177 | 1558869 | 2018-03-18 17:59 | 2018-03-18 20:25 | 146 | 11kV | 206736 | 1416 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | The 11KV bond was found burnt off at AB30040 on the footpath side (Ex Zn10995 Riverwood - Panel 2) Remarks: The 11kv bond was found burnt off at AB30040 on the footpath side (Ex Zn10995 Riverwood - Panel 2) | March | 2018 | 2018Q3 | 2018 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | OH | Not Veg | 2018-03-18 | N | 146 | N | 10 | N | N | 1.1101 | 39.4971 | 151076.5711
[7 empty] | 7996 | 10999 | 1558943 | 2018-03-18 19:22 | 2018-03-18 21:50 | 148 | 11kV | 198135 | 1890 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn2602 Clovelly - Pnl.32 tripped on: Earth Fault Field EFIs: S4080 S6958 S35188 S4592 S2678 (S8965 & S5019 did not operate) Abnormal: S4592 (Sw/A) closed with S8811 (Sw/A) open. UG cable fault between S8476 and S2678 tee S3016. See 1559212 1559213 | March | 2018 | 2018Q3 | 2018 | ZN2602:PA32 | ZN2602:PA32 | ZN02602/000032 | RANDWICK | UG | Not Veg | 2018-03-18 | N | 104.8333 | N | 10 | N | N | 1.1101 | 39.4971 | 144791.214
[7 empty] | 8426 | 16665 | 1558767 | 2018-03-18 14:45 | 2018-03-18 22:00 | 435 | 11kV | 77555 | 253 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | 11kV Bond burnt off main line to PT231 High Blaxland (Ex hunters Hill Panel 64) Note: LV parallels failure between PT231 - S2560 and S5269 See OMS 1559235 1558935 1559241 1558910 1558767 | March | 2018 | 2018Q3 | 2018 | ZN129:PA64 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Not Veg | 2018-03-18 | N | 306.5415 | N | 10 | N | N | 1.1101 | 39.4971 | 56674.9065
[7 empty] | 8190 | 13562 | 1558826 | 2018-03-18 16:34 | 2018-03-18 22:39 | 365 | 11kV | 295220 | 1643 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Zn9245 Engadine - Pnl.19 tripped on: B & C phase IOC Note: Reclosing Non-auto due to fire ban Abnormal: S9356 (Sw/A) closed with S9985 (Sw/A) open 11kV Bond burnt off at 114 Kingswood Rd, Engadine See 1559242 1559244 | March | 2018 | 2018Q3 | 2018 | ZN9245:PA19 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | OH | Not Veg | 2018-03-18 | N | 179.6835 | N | 10 | N | N | 1.1101 | 39.4971 | 215738.0685
[7 empty] | 7523 | 5591 | 1559020 | 2018-03-18 23:51 | 2018-03-19 01:04 | 73 | 11kV | 20367 | 279 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | CP554 Arcadia Ross Common tripped on Relays: Unknown (SCAN fail) Cause: Tree on OH cnr of Arcadia and Rosscommon | March | 2018 | 2018Q3 | 2018 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2018-03-18 | N | 73 | N | 10 | N | N | 1.1101 | 39.4971 | 14883.6029
[7 empty] | 7697 | 7311 | 1559025 | 2018-03-19 00:32 | 2018-03-19 03:05 | 153 | 11kV | 22491 | 147 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | 11kv Bond off at UGOH adj S10500 Thurlow Romilly road side phase | March | 2018 | 2018Q3 | 2018 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Not Veg | 2018-03-19 | N | 153 | N | 8 | N | N | 1.1101 | 39.4971 | 16435.7594
[7 empty] | 7726 | 7748 | 1559035 | 2018-03-19 03:29 | 2018-03-19 04:30 | 61 | 11kV | 110594 | 2471 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186179 1 fault operation C Phase Earth Fault Possum at sub 43340. HV arresters look suspect. Sub left isolated restored via LV// Excluded 1559035 | March | 2018 | 2018Q3 | 2018 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2018-03-19 | N | 44.7568 | N | 8 | N | N | 1.1101 | 39.4971 | 80818.8332
[7 empty] | 7679 | 7108 | 1559046 | 2018-03-19 05:25 | 2018-03-19 07:21 | 116 | 11kV | 154396 | 1331 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn36300 Balgowlah North pa13 fdr tripped, reclosed, tripped and locked out Relays - IOC C Phase, Reclose and lock out Signals: 11kv trip, Group Earth & Lock Out EFI's: Nil Cause: Tree/Branch on OH Mains Quirk Rd Manly West Park S16991 Balgowlah Quirk Dist 4 "Balgowlah Rd" Interrutped for safety Tree/Branch on OH Mains See 1559426 ex 1559046,63 | March | 2018 | 2018Q3 | 2018 | ZN36300:PA13 | ZN36300:PA13 | ZN36300/000013 | NORTHERN BEACHES | OH | Veg | 2018-03-19 | N | 116 | N | 8 | N | N | 1.1101 | 39.4971 | 112828.0429
[7 empty] | 8082 | 12200 | 1559080 | 2018-03-19 08:25 | 2018-03-19 10:45 | 140 | 11kV | 45879 | 430 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1673 Turramurra 11kV Panel 9 tripped on Relays: Earth Fault, Fault Check, EFI Signals: 11kV Trip, TX1 Group Earth Cause: 11kV Feeder Fault from S4241 SW/B to S47871 tee PT30 See OMS 1559444 1559445 1559448 1559446 1559447 1559080 | March | 2018 | 2018Q3 | 2018 | ZN1673:PA9 | ZN1673:PA9 | ZN01673/000009 | KU-RING-GAI | UG | Not Veg | 2018-03-19 | N | 106.6953 | N | 8 | N | N | 1.1101 | 39.4971 | 33527.02
[7 empty] | 7391 | 3757 | 1559104 | 2018-03-19 09:10 | 2018-03-19 12:25 | 195 | 11kV | 38075 | 351 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12580 Erina Panel 12 fdr tripped, reclosed & locked out Relays: AB phase timed O/C, EFI, lockout relay Signals: 11kv trip EFI's: Nil Cause: tree/branch on oh mains. The Entrane rd near Terrigal Dr See 1559436,7,9 ex 1559104,5,11,67,8 | March | 2018 | 2018Q3 | 2018 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Veg | 2018-03-19 | N | 108.4758 | N | 8 | N | N | 1.1101 | 39.4971 | 27824.087
[7 empty] | 8453 | 17032 | 1559195 | 2018-03-19 12:48 | 2018-03-19 18:25 | 337 | 11kV | 10102 | 50 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186188 1 fault operation Earth Fault Tree fell onto mains which fell onto fence. Fire started 50m up hill on star picket. Burnt out approx 50m2 of grass and a boat. Excluded OMS 1559195 | March | 2018 | 2018Q3 | 2018 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2018-03-19 | N | 202.04 | N | 8 | N | N | 1.1101 | 39.4971 | 7382.2436
[7 empty] | 7652 | 6837 | 1559342 | 2018-03-19 20:18 | 2018-03-20 00:55 | 277 | 11kV | 224952 | 2371 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | @ZN10999 Kogarah 11kv Panel #36 labelled "S.10669 Buchanan Hampton" tripped: Relays: Earth fault check relay, EFI Signals: 11kv trip, CB.36 open Remarks: 11kv feeder from Sw/B @ S47631 Andover Bembridge to Sw/A @ S10106 Andover Tanner tee Sw/A @ S10383 Rutland Andover | March | 2018 | 2018Q3 | 2018 | ZN10999:PA36 | ZN10999:PA36 | ZN10999/000036 | GEORGES RIVER | UG | Not Veg | 2018-03-19 | N | 94.8764 | N | 8 | N | N | 1.1101 | 39.4971 | 164388.2866
[7 empty] | 8145 | 13108 | 1559363 | 2018-03-20 05:48 | 2018-03-20 08:40 | 172 | 11kV | 11706 | 80 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 RE45017 Whiteman tripped, reclosed & locked out Relays: A+B ph OC Signals: 11kv trip EFI: nil Cause: not ascertained. DOP patrolled feeder. no cause found See 1559756,7,8,60 ex 1559363 | March | 2018 | 2018Q3 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2018-03-20 | N | 146.325 | N | 9 | N | N | 1.1101 | 39.4971 | 8554.3995
[7 empty] | 8364 | 15683 | 1559359 | 2018-03-20 04:13 | 2018-03-20 10:35 | 382 | 11kV | 78315 | 811 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty section of Pa11 IR61580 Yimbala Cornish tripped, reclosed & locekd out Relays: OC Singals: 11kv trip EFI's:Nil Cause: OH Down. 11kv roadside phase wire down on source side of LB61581 See 1559742,3,5,6,7 ex 1559359,61,2,5,6,92 | March | 2018 | 2018Q3 | 2018 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2018-03-20 | N | 96.566 | N | 9 | N | N | 1.1101 | 39.4971 | 57230.2921
[7 empty] | 8409 | 16504 | 1559348 | 2018-03-19 22:38 | 2018-03-20 12:48 | 850 | 11kV | 137226 | 165 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex14144 Wamberal section of Pa2 CP44946 Kunarra Rd tripped, reclosed & locked out on: Relays: OC, EF Signals: 11kv trip EFI's:nil Cause: Large Gum brought down OH adj AB43318 See 1559724,5 ex 1559348,51,2 | March | 2018 | 2018Q3 | 2018 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2018-03-19 | N | 831.6727 | N | 8 | N | N | 1.1101 | 39.4971 | 100280.7133
[7 empty] | 7357 | 3023 | 1559454 | 2018-03-20 10:55 | 2018-03-20 18:45 | 470 | 11kV | 1410 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186201 B Phase dropper broken Excluded OMS 1559454 | March | 2018 | 2018Q3 | 2018 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2018-03-20 | N | 470 | N | 9 | N | N | 1.1101 | 39.4971 | 1030.3864
[7 empty] | 8593 | 18712 | 1559488 | 2018-03-20 14:54 | 2018-03-20 20:29 | 335 | 11kV | 55215 | 511 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 186198 Broken 11kV crossarm at pole LQ-30124 Reported by Passer By Excluded OMS 1559488, 1559504 | March | 2018 | 2018Q3 | 2018 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2018-03-20 | N | 108.0528 | N | 9 | N | N | 1.1101 | 39.4971 | 40349.4934
[7 empty] | 7981 | 10776 | 1559560 | 2018-03-20 18:13 | 2018-03-20 21:30 | 197 | 11kV | 252266 | 2278 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.11L tripped on: Earth Fault Field EFIs: S10163 S10076 S10730 UGOH fault between LB30157 to S10630 (Sw/A) tee PPT10032 See 1559915 1559916 1559917 1559920 | March | 2018 | 2018Q3 | 2018 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | Unknown | Unknown | 2018-03-20 | N | 110.7401 | N | 9 | N | N | 1.1101 | 39.4971 | 184348.5522
[7 empty] | 7389 | 3752 | 1559551 | 2018-03-20 17:42 | 2018-03-20 21:45 | 243 | 11kV | 729 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 186202 Broken Live Line Clamp Excluded OMS 1559551 | March | 2018 | 2018Q3 | 2018 | 512:48048 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2018-03-20 | N | 243 | N | 9 | N | N | 1.1101 | 39.4971 | 532.7317
[7 empty] | 8655 | 19525 | 1559544 | 2018-03-20 17:07 | 2018-03-20 23:05 | 358 | 11kV | 716 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 186203 no protection operation Faulty LL Clamp replaced Excluded oms 1559544 | March | 2018 | 2018Q3 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2018-03-20 | N | 358 | N | 9 | N | N | 1.1101 | 39.4971 | 523.2317
[7 empty] | 7440 | 4539 | 1559526 | 2018-03-20 15:16 | 2018-03-20 23:15 | 479 | 11kV | 18068 | 108 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 186200 3 fault operation Sensitive Earth Fault Faulty TX at PT 70211 W Campbell. Excluded OMS 1559522. | March | 2018 | 2018Q3 | 2018 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2018-03-20 | N | 167.2963 | N | 9 | N | N | 1.1101 | 39.4971 | 13203.5615
[7 empty] | 7583 | 6120 | 1559929 | 2018-03-20 23:54 | 2018-03-21 00:50 | 56 | 11kV | 56 | 1 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | S76843 West Connex St Peters Temo No.1 - HVC tripped on C Phase O/C Customer's tunnelling equipment operating overload setting. O/C set at 250Amps | March | 2018 | 2018Q3 | 2018 |  |  |  |  | Unknown | Not Veg | 2018-03-20 | N | 56 | N | 9 | N | N | 1.1101 | 39.4971 | 40.9231
[7 empty] | 7695 | 7289 | 1559599 | 2018-03-21 00:59 | 2018-03-21 02:45 | 106 | 11kV | 256230 | 2505 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15008 Harbord Panel 9 tripped and locked out on Relays: B and C phase OC and LOckout Signals: 11kV Trip. Cause: Tree branch removed from 11kV Near AB62773 and Bond Burnt off Abnormal Switching: AB25221 Closed, LB20548 Open See OMS 1559691 1559692 1559608/606/604/602/600/599 | March | 2018 | 2018Q3 | 2018 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Veg | 2018-03-21 | N | 102.2874 | N | 16 | N | N | 1.1101 | 39.4971 | 187245.3265
[7 empty] | 7761 | 8210 | 1559598 | 2018-03-21 00:48 | 2018-03-21 02:46 | 118 | 11kV | 5192 | 44 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa1 "Dog trap rd" RE44853 Ourimbah bumble tripped & locked out on O/C tree/branch removed from OH near AB44060 | March | 2018 | 2018Q3 | 2018 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2018-03-21 | N | 118 | N | 16 | N | N | 1.1101 | 39.4971 | 3794.1605
[7 empty] | 7223 | 802 | 1559611 | 2018-03-21 03:10 | 2018-03-21 03:53 | 43 | 11kV | 62350 | 1450 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @S1287 Revesby Panel 11 'S4452 Hodgkinson Cres' fdr tripped & locked out on Relays: A & C phase inst, C phase timed, lockout, timing Signals: 11kv trip Remarks: tree/branch on OH mains. Removed by Dop cnr elliott & lambeth | March | 2018 | 2018Q3 | 2018 | ZN1287:PA11 | ZN1287:PA11 | ZN01287/000011 | CANTERBURY-BANKSTOWN | OH | Veg | 2018-03-21 | N | 43 | N | 16 | N | N | 1.1101 | 39.4971 | 45563.541
[7 empty] | 8594 | 18766 | 1559601 | 2018-03-21 01:11 | 2018-03-21 09:39 | 508 | 11kV | 177828 | 383 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa12 "Yarramalong" fdr IR50630 Yarramalong Chandlers 0.1 tripped & locked out on SEF, O/C Cause: not ascertained. IR48813 no communication. IR44753 RTU Fial See 1560190,1,2 ex 1559601 | March | 2018 | 2018Q3 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2018-03-21 | N | 464.3029 | N | 16 | N | N | 1.1101 | 39.4971 | 129951.4574
[7 empty] | 7655 | 6866 | 1559652 | 2018-03-21 07:48 | 2018-03-21 11:41 | 233 | 11kV | 72161 | 763 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | LID 186205 3 fault operations 3 phase Overcurrent Faulty insulators & crossarm at poles KT-70289 & KT-70398 replaced under AP. Excluded OMS 1559652. | March | 2018 | 2018Q3 | 2018 | 228:7491 | 228:85415 | ZN00228/085415 | NEWCASTLE | OH | Not Veg | 2018-03-21 | N | 94.5754 | N | 16 | N | N | 1.1101 | 39.4971 | 52733.1304
[7 empty] | 8550 | 18215 | 1559768 | 2018-03-21 11:01 | 2018-03-21 15:30 | 269 | 11kV | 34680 | 383 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa12 "Yarramalong" fdr IR50630 Yarramalong Chandlers 0.1 tripped & locked out on SEF, O/C Cause: insulator failed. Stand off insulator failed at Pole DO00800 See 1560258,9 ex 1559768,78,86 | March | 2018 | 2018Q3 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2018-03-21 | N | 90.5483 | N | 16 | N | N | 1.1101 | 39.4971 | 25343.1211
[7 empty] | 7935 | 10270 | 1559657 | 2018-03-21 05:15 | 2018-03-21 17:15 | 720 | 11kV | 10370 | 18 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | LID 186209/01 33kv ohm hit 11KV. all Substaion DOLFS and arrestors Blown and Replaced. TX change at sub 46108. Excluded oms: 1559618, 1559657, 1559893 | March | 2018 | 2018Q3 | 2018 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2018-03-21 | N | 576.1111 | N | 16 | N | N | 1.1101 | 39.4971 | 7578.0901
[7 empty] | 8618 | 19098 | 1559835 | 2018-03-21 13:23 | 2018-03-21 18:20 | 297 | 11kV | 7746 | 54 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | LID 186210 1 fault operation A Phase Sensitive Earth Fault 11kv on xarm at FO-70287. but also dolfs down at subs 2293, 51293 Excluded oms 1559835, 1559836. | March | 2018 | 2018Q3 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-03-21 | N | 143.4444 | N | 16 | N | N | 1.1101 | 39.4971 | 5660.5483
[7 empty] | 7914 | 10036 | 1559966 | 2018-03-21 15:13 | 2018-03-21 18:45 | 212 | 11kV | 22896 | 108 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn14891 Wyong section of Pa12 "Yarramlong" CP48838 Yarramalong Maitland 4.2 operated by DOp from bypass LB48839z Abnormal: LB40899 closed & AB40818 open for preswitch job and Auto link 44773 open and def with mains down Cause: tree/branch on oh mains at CP48838 See 1560263 ex 1559894 1559966 | March | 2018 | 2018Q3 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2018-03-21 | N | 212 | N | 16 | N | N | 1.1101 | 39.4971 | 16731.7215
[7 empty] | 7196 | 388 | 1559906 | 2018-03-21 15:13 | 2018-03-21 18:45 | 212 | 11kV | 2120 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn14891 Wyong section of Pa12 "Yarramalong" fdr CP44773 Chandlers auto links Cause: Tree/branch brought down OH near LK42507 See 1560264 ex 1559906 | March | 2018 | 2018Q3 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2018-03-21 | N | 212 | N | 16 | N | N | 1.1101 | 39.4971 | 1549.2335
[7 empty] | 7285 | 1970 | 1560002 | 2018-03-21 18:19 | 2018-03-21 21:00 | 161 | 11kV | 134827 | 1294 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | LID 186222 1 fault operation Faulty UGOH at pole NR-60344. Excluded OMS No. 1560002 | March | 2018 | 2018Q3 | 2018 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | Unknown | Unknown | 2018-03-21 | N | 104.194 | N | 16 | N | N | 1.1101 | 39.4971 | 98527.5949
[7 empty] | 7501 | 5381 | 1559766 | 2018-03-21 11:05 | 2018-03-21 21:15 | 610 | 11kV | 80520 | 132 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | N | S5573 Mitchell Centennial - 11kV/415V Tx was interrupted for safety at 13:40 to allow emergency repairs on LV broken cross arm & termite affected pole. First call of No Supply received at 11:05. | March | 2018 | 2018Q3 | 2018 | ZN342:PA17 | ZN342:PA17 | ZN00342/000017 | SYDNEY | OH | Not Veg | 2018-03-21 | N | 610 | N | 16 | N | N | 1.1101 | 39.4971 | 58841.6411
[7 empty] | 7228 | 864 | 1560021 | 2018-03-21 22:20 | 2018-03-22 01:37 | 197 | 11kV | 5713 | 29 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | LID 186213 MVA pole JR-25006 section isolated for repairs Excluded OMS 1560021 | March | 2018 | 2018Q3 | 2018 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2018-03-21 | N | 197 | N | 16 | N | N | 1.1101 | 39.4971 | 4174.8919
[7 empty] | 7263 | 1529 | 1560055 | 2018-03-21 20:40 | 2018-03-22 02:00 | 320 | 11kV | 33600 | 105 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | N | Ex Zn13000 Lake Mummorah section of Pa7 from AB43823 to AB43824 tee PT13586 PT11654 PT14452 PT13857 Cause: interrutped for safety reasons. broken cross arm at link 41687 See 1560308 ex 1560055 | March | 2018 | 2018Q3 | 2018 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2018-03-21 | N | 320 | N | 16 | N | N | 1.1101 | 39.4971 | 24553.889
[7 empty] | 7199 | 405 | 1560077 | 2018-03-22 00:09 | 2018-03-22 12:54 | 765 | 11kV | 50628 | 238 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186223 2 fault operations Tree into HV &LV adjacent sub 49026 Excluded OMS 1560077 | March | 2018 | 2018Q3 | 2018 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2018-03-22 | N | 212.7227 | N | 6 | N | N | 1.1101 | 39.4971 | 36997.4491
[7 empty] | 8698 | 20007 | 1560095 | 2018-03-22 06:09 | 2018-03-22 13:20 | 431 | 11kV | 3448 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn14891 Wyong section of Pa12 "Yarramalong" fdr 11kV 15A HDO fuses 78535 Kidman North operated Cause: OH Down. 11kv OH into LV See 1561493 ex 1560095 | March | 2018 | 2018Q3 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2018-03-22 | N | 431 | N | 6 | N | N | 1.1101 | 39.4971 | 2519.6967
[7 empty] | 8232 | 14197 | 1559806 | 2018-03-21 12:20 | 2018-03-22 13:30 | 1510 | 11kV | 66178 | 59 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Recloser CP1238 Milsons Passage tripped on on OC Cause: Lineworker to repair - tree branch brought down OH Difficult access long restoration See OMS 1560572 1560573 1559806 1550064 1560482 | March | 2018 | 2018Q3 | 2018 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2018-03-21 | N | 1121.661 | N | 16 | N | N | 1.1101 | 39.4971 | 48360.9305
[7 empty] | 7775 | 8395 | 1560081 | 2018-03-22 04:29 | 2018-03-22 13:30 | 541 | 11kV | 84131 | 1336 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | LID 186217 2 fault operations Car hit pole IV-50750 Excluded OMS 1560085 | March | 2018 | 2018Q3 | 2018 | 206:34434 | 206:34434 | ZN00206/034434 | LAKE MACQUARIE | OH | Not Veg | 2018-03-22 | N | 62.9723 | N | 6 | N | N | 1.1101 | 39.4971 | 61480.4534
[7 empty] | 7307 | 2283 | 1560133 | 2018-03-21 19:40 | 2018-03-22 15:15 | 1175.35 | 11kV | 10578.15 | 9 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 186219 LV ohm on ground, faulty Tx 47273 | March | 2018 | 2018Q3 | 2018 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2018-03-21 | N | 1175.35 | N | 16 | N | N | 1.1101 | 39.4971 | 7730.2
[7 empty] | 7397 | 3813 | 1560331 | 2018-03-22 19:19 | 2018-03-22 20:05 | 46.15 | 11kV | 830.7 | 18 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186227 Single phase Tree on mains. No Protection operated | March | 2018 | 2018Q3 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2018-03-22 | N | 46.15 | N | 6 | N | N | 1.1101 | 39.4971 | 607.0511
[7 empty] | 8642 | 19403 | 1560371 | 2018-03-22 21:03 | 2018-03-22 22:45 | 101.85 | 11kV | 5601.75 | 55 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 186228 C Phase DOLF : 20 Amp Sub 13202 C phase 10A DOLF no cause found supply bak on 2245hrs Excluded 1560371 | March | 2018 | 2018Q3 | 2018 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2018-03-22 | N | 101.85 | N | 6 | N | N | 1.1101 | 39.4971 | 4093.5937
[7 empty] | 7708 | 7538 | 1560417 | 2018-03-23 07:47 | 2018-03-23 09:13 | 86 | 11kV | 172 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | Replaced 10a Hv fuse Note: No LID report raised, info based off record OMS 1560417 | March | 2018 | 2018Q3 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-03-23 | N | 86 | N | 3 | N | N | 1.1101 | 39.4971 | 125.6925
[7 empty] | 7904 | 9966 | 1560381 | 2018-03-22 21:26 | 2018-03-23 12:50 | 924 | 11kV | 25064 | 62 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mountain" CP45035 Mangrove Mountain tripped, reclosed & locked out on: Relays: Earth Fault Signals: 11kv trip EFI's:nil Cause: OH Down 2 bays 11kv down a few spans away from PT77272 lillicraps wise 0.6 See 1561513,6 ex 1560381,92,3,4,5 | March | 2018 | 2018Q3 | 2018 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2018-03-22 | N | 404.2581 | N | 6 | N | N | 1.1101 | 39.4971 | 18316.0319
[7 empty] | 8522 | 17854 | 1560482 | 2018-03-23 10:50 | 2018-03-23 13:22 | 152 | 11kV | 106552 | 701 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | Zn2400 Berowra Panel 11 "Brooklyn" one phase down from IR77184 to AB204 S1586 Brooklyn Causeway 66kV fuse operated Abnormal: S1586 clsoed and supply taken from fdr 831 Sydney Trains Cause: Fuse Fatigue Also see interruption on PT1516 due to MG tripping off See 1561573 ex 1560482 1560487 | March | 2018 | 2018Q3 | 2018 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2018-03-23 | N | 152 | N | 3 | N | N | 1.1101 | 39.4971 | 77865.0588
[7 empty] | 7308 | 2306 | 1560635 | 2018-03-23 22:28 | 2018-03-23 23:20 | 52 | 11kV | 416 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186236 B Phase DOLF : 10 Amp Excluded OMS 1560635 | March | 2018 | 2018Q3 | 2018 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2018-03-23 | N | 52 | N | 3 | N | N | 1.1101 | 39.4971 | 304.0005
[7 empty] | 7898 | 9954 | 1560806 | 2018-03-25 00:31 | 2018-03-25 02:05 | 94 | 11kV | 109633 | 1177 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn965 Pennant Hills Panel 3 fdr tripped on Relays: EF EFI Signals: 11kv trip Abrnoaml: Pennant Hills DIU 68,69,70 Fail RTU DIU Fail Cause: UG fault. 11kv UG cable fault from S4440 to S4945 See 1561577,9 ex 1560806 | March | 2018 | 2018Q3 | 2018 | ZN965:PA3 | ZN965:PA3 | ZN00965/000003 | HORNSBY | UG | Not Veg | 2018-03-25 | N | 93.1461 | N | 7 | N | N | 1.1101 | 39.4971 | 80116.5628
[7 empty] | 8170 | 13395 | 1560821 | 2018-03-25 07:38 | 2018-03-25 08:15 | 37 | 11kV | 2442 | 66 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of Pa12 PT11662 Arunta Carringa roadside 31.5k HVDO operated Cause: Fuse Fatigue See 1561533 ex 1560821 | March | 2018 | 2018Q3 | 2018 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Not Veg | 2018-03-25 | N | 37 | N | 7 | N | N | 1.1101 | 39.4971 | 1784.5416
[7 empty] | 7748 | 8025 | 1560859 | 2018-03-25 11:18 | 2018-03-25 13:36 | 138 | 11kV | 36171 | 279 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn35370 Galston section of Pa8 RE554 Arcadia Rosscommon tripped on Relays - Nil, DOp unable to read events from screen Sginals - Recloser CP554 Arcadia Rosscommon is in scan fail, no indication was recieved in the control room cause not ascertained See 1561584,5,6,7 ex 1560859 | March | 2018 | 2018Q3 | 2018 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2018-03-25 | N | 129.6452 | N | 7 | N | N | 1.1101 | 39.4971 | 26432.6999
[7 empty] | 7312 | 2380 | 1560912 | 2018-03-25 15:49 | 2018-03-25 16:25 | 36 | 11kV | 36 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186244 Single phase DOLF : 10 Amp Excluded OMS 1560912 | March | 2018 | 2018Q3 | 2018 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Veg | 2018-03-25 | N | 36 | N | 7 | N | N | 1.1101 | 39.4971 | 26.3077
[7 empty] | 7577 | 6090 | 1560969 | 2018-03-25 18:19 | 2018-03-25 19:40 | 81 | 11kV | 63605 | 1129 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Rec 50008 Simmat Townsend (ex Zn1850 Bass Ill Panel 3 'S4312 Edgar Marion') tripped, reclosed and locked out on: Relays: OC trip, lockout Field EFI's: nil Remarks: tree/branch on OH mains. Tree branch on mains adj PT1230 Sixth Railway. 11kv feeder isolated from AB821 to LB1947 tee PT1230 Sixth Railway. | March | 2018 | 2018Q3 | 2018 | ZN1850:PA3 | ZN1850:PA41 | ZN01850/000041 | CANTERBURY-BANKSTOWN | OH | Veg | 2018-03-25 | N | 56.3375 | N | 7 | N | N | 1.1101 | 39.4971 | 46480.658
[7 empty] | 8451 | 17018 | 1560929 | 2018-03-25 17:23 | 2018-03-25 20:00 | 157 | 11kV | 310369 | 3849 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At ZN10999 KOGARAH 11kv Pnl10 "LB 31314, etc" tripped on earth fault Signals: 11kv trip with efi Field efi's: nil Abnormal: Sw/A closed at S10157 and LB 31204 opened Remarks: UGOH fault short circuit. Defective 11kv uOGH to S65059 Preddys Crown | March | 2018 | 2018Q3 | 2018 | ZN10999:PA10 | ZN10999:PA10 | ZN10999/000010 | BAYSIDE | Unknown | Unknown | 2018-03-25 | N | 80.6363 | N | 7 | N | N | 1.1101 | 39.4971 | 226808.5109
[7 empty] | 8360 | 15658 | 1561022 | 2018-03-26 02:22 | 2018-03-26 03:29 | 67 | 11kV | 133456 | 2062 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Zn12650 West Gosford Pa12 "North Gosford" tripped on NIL Protection, Lockout and timing relay, 11kv trip cause: not ascertained note second time panel 12 has trip with no protection operations See 1561539,40 ex 1561022,9 | March | 2018 | 2018Q3 | 2018 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Veg | 2018-03-26 | N | 64.7216 | N | 8 | N | N | 1.1101 | 39.4971 | 97525.7085
[7 empty] | 8069 | 12062 | 1561551 | 2018-03-26 04:05 | 2018-03-26 05:45 | 100 | 11kV | 24276 | 345 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Zn12650 West Gosford section of Pa12 Recloser 46929 Jarrett Kirkness tripped on Earth fault Abnormal: AB40310 closed, S18658swA opened cause: not ascertained. please investigate 11kv UGOH below s18658 See 1561551,2,3 | March | 2018 | 2018Q3 | 2018 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Veg | 2018-03-26 | N | 70.3652 | N | 8 | N | N | 1.1101 | 39.4971 | 17740.1848
[7 empty] | 7799 | 8730 | 1561039 | 2018-03-26 07:28 | 2018-03-26 10:40 | 192 | 11kV | 16128 | 84 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | No Weather Impact | N | ex Zn15008 Harbord section of Pa5 LK23561 beyond interrupted for safet. Fire on 11kv UGOH pole possibly due to lightning strike See 1561559 ex 1561039,56 | March | 2018 | 2018Q3 | 2018 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | OH | Not Veg | 2018-03-26 | N | 192 | N | 8 | N | N | 1.1101 | 39.4971 | 11785.8667
[7 empty] | 7448 | 4637 | 1561113 | 2018-03-26 14:15 | 2018-03-26 14:35 | 20 | 11kV | 440 | 22 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of Pa16 PT12637 Heathcliffe Valerie no protection operation cause: interrupted for safety. remove tree branch off the lv mains See 1561562 ex 1561234 | March | 2018 | 2018Q3 | 2018 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2018-03-26 | N | 20 | N | 8 | N | N | 1.1101 | 39.4971 | 321.539
[7 empty] | 7578 | 6092 | 1561304 | 2018-03-26 18:26 | 2018-03-26 19:15 | 49 | 11kV | 2877.7 | 59 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn195 Pymble section of Pa28 PT2193 Warwick SPencer - centre phase HVDO assembly broken and became HR after supporting. LV//'s removed causing fluctuating volts/ no supply DOps removing LV//'s as part of LV// Audit Program. PT2193 isolated & put in LV// See 1561304 GIS 1561310 CC1: 22-"Refer to SOp" | March | 2018 | 2018Q3 | 2018 | ZN195:PA28 | ZN195:PA28 | ZN00195/000028 | KU-RING-GAI | OH | Not Veg | 2018-03-26 | N | 48.7746 | N | 8 | N | N | 1.1101 | 39.4971 | 2102.9383
[7 empty] | 8202 | 13791 | 1561299 | 2018-03-26 18:07 | 2018-03-26 20:15 | 128 | 11kV | 128 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186251 Single phase DOLF : 10 Amp second outage in two days. Bruce changed LA's under AP. Excluded OMS 1561299 | March | 2018 | 2018Q3 | 2018 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Veg | 2018-03-26 | N | 128 | N | 8 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 7500 | 5380 | 1560300 | 2018-03-25 13:11 | 2018-03-26 22:40 | 2009 | 11kV | 161804 | 2021 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At ZN116 Leichhardt 11kv Pnl12 "Balmain Derby" tripped on earth fault Signals: 11kv trip with efi Field efis: Pnl 12 to ugoh at S1436 Remarks: cause not ascertained. Suspect cable fault. Feeder tried back at 2301 after tests couldn't test from UGOH to S1436 | March | 2018 | 2018Q3 | 2018 | ZN116:PA12 | ZN116:PA12 | ZN00116/000012 | INNER WEST | OH | Veg | 2018-03-25 | N | 80.0614 | N | 7 | N | N | 1.1101 | 39.4971 | 118241.5908
[7 empty] | 7185 | 147 | 1561390 | 2018-03-26 23:05 | 2018-03-27 01:30 | 145 | 11kV | 4930 | 34 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 186252 A Phase Issued to J Frazer fault at CS-30046 isolated from ABS6793 at 2305hrs supply back on 0130hrs | March | 2018 | 2018Q3 | 2018 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2018-03-26 | N | 145 | N | 8 | N | N | 1.1101 | 39.4971 | 3602.6986
[7 empty] | 7690 | 7246 | 1561395 | 2018-03-27 02:11 | 2018-03-27 04:14 | 123 | 11kV | 229132 | 2016 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | Zn36300 Balgowlah Nth Panel 3 "Jackson White" tripped on ABC Inst Protection Zone Earth Group Earth EFI fault check 11kv trip Possum at LB61276. mains to inspect LB for damage in daylight See 1561565 ex 1561395, 1561566 | March | 2018 | 2018Q3 | 2018 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2018-03-27 | N | 113.6567 | N | 3 | N | N | 1.1101 | 39.4971 | 167442.9074
[7 empty] | 8289 | 14841 | 1561233 | 2018-03-26 14:11 | 2018-03-27 13:00 | 1369 | 11kV | 6706 | 58 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186250 1 fault operation Single phase Sensitive Earth Fault Mains down beyond links 3527 | March | 2018 | 2018Q3 | 2018 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2018-03-26 | N | 115.6207 | N | 8 | N | N | 1.1101 | 39.4971 | 4900.547
[7 empty] | 7305 | 2260 | 1561544 | 2018-03-27 14:53 | 2018-03-27 16:55 | 122 | 11kV | 244 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186261 C Phase DOLF : 10 Amp Bird Excluded OMS 1561544 | March | 2018 | 2018Q3 | 2018 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2018-03-27 | N | 122 | N | 3 | N | N | 1.1101 | 39.4971 | 178.308
[7 empty] | 7386 | 3695 | 1561582 | 2018-03-27 16:21 | 2018-03-27 18:25 | 124 | 11kV | 213022 | 2611 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn630 Mascot - 11kv Panel #38 'S2286 Hughes Bot' fdr CB tripped on: Signals: 11kv trip Relays: C phase IOC, EFI Remarks: UG fault 11kv feeder fault from S7879 Botany hughes (Sw/B) to S46275 Botany Coward (Sw/A) to S2163 Aloha Street (Sw/A) | March | 2018 | 2018Q3 | 2018 | ZN630:PA38 | ZN630:PA38 | ZN00630/000038 | BAYSIDE | UG | Not Veg | 2018-03-27 | N | 81.5864 | N | 3 | N | N | 1.1101 | 39.4971 | 155670.1945
[7 empty] | 8129 | 12979 | 1561652 | 2018-03-28 03:57 | 2018-03-28 05:15 | 78 | 11kV | 5148 | 66 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of Pa12 PT11662 Arunta Curringa HDO operated 31.5Amp rodaside Cause: Fuse Fatigue | March | 2018 | 2018Q3 | 2018 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Not Veg | 2018-03-28 | N | 78 | N | 5 | N | N | 1.1101 | 39.4971 | 3762.0066
[7 empty] | 8022 | 11321 | 1561648 | 2018-03-28 02:54 | 2018-03-28 07:23 | 269 | 11kV | 90204 | 696 | HV | Vandalism | 3rd Party Impact | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 186262 C Phase Earth Fault Copper Theft Excluded OMS 1561648 | March | 2018 | 2018Q3 | 2018 | 270:83593 | 270:83593 | ZN00270/083593 | LAKE MACQUARIE | OH | Not Veg | 2018-03-28 | N | 129.6034 | N | 5 | N | N | 1.1101 | 39.4971 | 65918.4226
[7 empty] | 7244 | 1147 | 1561650 | 2018-03-28 03:47 | 2018-03-28 07:23 | 216 | 11kV | 15441 | 72 | HV | Vandalism | 3rd Party Impact | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 186263 Sensitive Earth Fault Copper theft Excluded OMS 1561650 | March | 2018 | 2018Q3 | 2018 | 270:83591 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Not Veg | 2018-03-28 | N | 214.4583 | N | 5 | N | N | 1.1101 | 39.4971 | 11283.8274
[7 empty] | 8314 | 15138 | 1561720 | 2018-03-28 14:25 | 2018-03-28 22:15 | 470 | 11kV | 940 | 2 | HV | 3rd Party Vehicle | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186277 Truck hit substation S-25462 isolated to create isolation to damaged kiosk housing at S-23885 Excluded OMS 1561720 | March | 2018 | 2018Q3 | 2018 | 239:82132 | 239:82132 | ZN00239/082132 | LAKE MACQUARIE | OH | Not Veg | 2018-03-28 | N | 470 | N | 5 | N | N | 1.1101 | 39.4971 | 686.9243
[7 empty] | 8495 | 17551 | 1561855 | 2018-03-28 21:32 | 2018-03-29 00:11 | 159 | 11kV | 135838 | 920 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 26 tripped on Relays: B phase Timed overcurrent, Timing and Lockout with EFI Signals: Zone Earth, TX3 Group Earth 11kv Trip. Cause: 11kV Feeder fault from S6153 to S2696 to S4988 to S4491 See OMS 1562012 1561855 | March | 2018 | 2018Q3 | 2018 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | UG | Not Veg | 2018-03-28 | N | 147.65 | N | 5 | N | N | 1.1101 | 39.4971 | 99266.4039
[7 empty] | 8228 | 14108 | 1561870 | 2018-03-29 07:37 | 2018-03-29 07:56 | 19 | 11kV | 37202 | 1958 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Section of 11kV Pa41 and Pa29 de energised from recloser46120 Lovell Russell to LV 1044 to S4669 Abnormal Switching: Closed LB62449, Open LB1044, Closed at AB260, Open at SW/A S4669 CauseL: AOP was intending to make auto reclose N/A but instead opened CP46120 See OMS 1563048 1561870 1561871 1561901 | March | 2018 | 2018Q3 | 2018 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | Unknown | Not Veg | 2018-03-29 | N | 19 | N | 4 | N | N | 1.1101 | 39.4971 | 27186.1243
[7 empty] | 8627 | 19227 | 1561954 | 2018-03-29 10:19 | 2018-03-29 11:40 | 81 | 11kV | 81 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 186282 A Phase DOLF : 10 Amp Excluded OMS 1561954 | March | 2018 | 2018Q3 | 2018 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2018-03-29 | N | 81 | N | 4 | N | N | 1.1101 | 39.4971 | 59.1924
[7 empty] | 8211 | 13845 | 1562036 | 2018-03-29 16:43 | 2018-03-29 22:45 | 362 | 11kV | 165321 | 1313 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 46 tripped on Relays: B phase Earth Fault, Fault Check, Rec timer, Rec Lockout Signals: Group Earth, Zone Earth, 11kV trip, Battery Defect Cause: Crane Hit 11kV OH mains O/S 455 Pacific highway Asquith. See OMS 1562733 1562736 1562737 1562036 1562115 1562923 | March | 2018 | 2018Q3 | 2018 | ZN847:PA46 | ZN847:PA46 | ZN00847/000046 | HORNSBY | OH | Not Veg | 2018-03-29 | N | 125.9109 | N | 4 | N | N | 1.1101 | 39.4971 | 120811.7107
[7 empty] | 8348 | 15497 | 1562114 | 2018-03-29 23:34 | 2018-03-30 00:40 | 66 | 11kV | 73458 | 1113 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.18 tripped, reclosed and tripped on: B & C phase IOC Field EFIs: S10783 S1098 S10648 S10375 Possum on Line side of LB31282 | March | 2018 | 2018Q3 | 2018 | ZN10994:PA18 | ZN10994:PA18 | ZN10994/000018 | GEORGES RIVER | OH | Not Veg | 2018-03-29 | N | 66 | N | 4 | N | N | 1.1101 | 39.4971 | 53680.9398
[7 empty] | 8280 | 14739 | 1562122 | 2018-03-30 06:30 | 2018-03-30 10:35 | 245 | 11kV | 34375 | 218 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 186286 No protection operated. Car hit pole GS-73398 breaking cross arm and dropping 11kV to possibly touch LV. EMSO on site advised DOP all installations safe. For safety DOP initially interrupted all customers beyond ABS 43987, after 0640 only customers between ABS 43987 and 40277 remained interrupted until 1035 am. Excluded OMS 1562119, 1562121 & 1562123. | March | 2018 | 2018Q3 | 2018 | 522:83131 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2018-03-30 | N | 157.6835 | N | 5 | N | N | 1.1101 | 39.4971 | 25120.2361
[7 empty] | 8641 | 19392 | 1562132 | 2018-03-30 09:09 | 2018-03-30 13:05 | 236 | 11kV | 22491 | 179 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186287 No protection operated. Dropper cable disconnected from top of DOLF and had to be re-attached. Fore safety area between ABS 41311 and 6161 had to be isolated increasing the interruption area. Excluded OMS 1562132. | March | 2018 | 2018Q3 | 2018 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2018-03-30 | N | 125.648 | N | 5 | N | N | 1.1101 | 39.4971 | 16435.7594
[7 empty] | 8162 | 13297 | 1562173 | 2018-03-30 12:40 | 2018-03-30 14:40 | 120 | 11kV | 15960 | 133 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 186288 C Phase DOLF : 16 Amp Suspected fuse fatigue Excluded OMS 1562173 | March | 2018 | 2018Q3 | 2018 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Not Veg | 2018-03-30 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 11663.0973
[7 empty] | 8659 | 19594 | 1562245 | 2018-03-30 20:55 | 2018-03-30 22:50 | 115 | 11kV | 28134 | 251 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa3 Mangrove Mtn fdr RE46992 Goolara Holy Cross tripped on O/C & locked out cause: not ascertained. Feeder patrolled by DOps. No cause found. L/W to patrol during daylight hours See 1562779,81,2,3 ex 1562245 | March | 2018 | 2018Q3 | 2018 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2018-03-30 | N | 112.0876 | N | 5 | N | N | 1.1101 | 39.4971 | 20559.4974
[7 empty] | 7272 | 1627 | 1562232 | 2018-03-30 19:55 | 2018-03-31 01:03 | 308 | 11kV | 101212 | 1459 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186289 2 fault operation Earth Fault wires down at pole IT-90453 Excluded oms 1562232 | March | 2018 | 2018Q3 | 2018 | 258:80793 | 258:80793 | ZN00258/080793 | NEWCASTLE | OH | Not Veg | 2018-03-30 | N | 69.3708 | N | 5 | N | N | 1.1101 | 39.4971 | 73962.7444
[7 empty] | 8150 | 13201 | 1562313 | 2018-03-31 14:22 | 2018-03-31 16:00 | 98 | 11kV | 3893 | 116 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 186291 Outage for safety clearances. Sub found with brooken dolf x arm. recloser opened to safely operate, and section isolated with AP to repair x arm due to clearances. Excluded OMS 1562313 and 1562317 | March | 2018 | 2018Q3 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-03-31 | N | 33.5603 | N | 1 | N | N | 1.1101 | 39.4971 | 2844.8896
[7 empty] | 8543 | 18108 | 1562412 | 2018-04-01 15:28 | 2018-04-01 16:46 | 78 | 11kV | 125580 | 1610 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | @Zn2196 Milperra 11kv Panel No.5 "S8696 Marigold Amour No.4" feeder tripped reclosed and locked out Relays: C phase timed O/C, C phase IOC, timing/reclose relays Signals: 11kv trip Field EFI's: Nil Remarks: tree/branch on OH mains. Tree branch on 11kv Mains in Pziers St nr Newport St. Removed by Dop | April | 2018 | 2018Q4 | 2018 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Veg | 2018-04-01 | N | 78 | N | 2 | N | N | 1.1101 | 39.4971 | 91770.16
[7 empty] | 7232 | 974 | 1562425 | 2018-04-01 17:37 | 2018-04-01 19:55 | 138 | 11kV | 6624 | 48 | HV | Vandalism | 3rd Party Impact | Air Break Switch | Unplanned | No Weather Impact | N | Ex Zn12630 section of pa1 "Gunderman" fdr DOp found lock cut off AB42293 & LB Open Cause: Vandalism See 1562838 ex 1562425,31 | April | 2018 | 2018Q4 | 2018 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2018-04-01 | N | 138 | N | 2 | N | N | 1.1101 | 39.4971 | 4840.6238
[7 empty] | 8309 | 15065 | 1562451 | 2018-04-02 02:28 | 2018-04-02 05:20 | 172 | 11kV | 85712 | 736 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35400 North Sydney Panel 53 feeder tripped on Signals: 11kV Trip Relays: IT receive, B phase and neutral, phase O/C, eartth fault, EFI Cause: 11kV feeder fault from ZN35400 North Sydney to S6443 to S4041 to S2758 See OMS 1563038 1562451 | April | 2018 | 2018Q4 | 2018 | ZN35400:PA53 | ZN35400:PA53 | ZN35400/000053 | NORTH SYDNEY | UG | Not Veg | 2018-04-02 | N | 116.4565 | N | 21 | Y | Y | 1.1101 | 39.4971 | 62635.8015
[7 empty] | 7640 | 6702 | 1562456 | 2018-04-02 06:40 | 2018-04-02 08:05 | 85 | 11kV | 110406 | 1738 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 186293 open circuit bi metal lug at ugoh or-67112. section interrupted to back feed 0731hrs open 61169 0734hrs close 3975 Excluded OMS 1562456 | April | 2018 | 2018Q4 | 2018 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | Unknown | Unknown | 2018-04-02 | N | 63.5247 | N | 21 | Y | Y | 1.1101 | 39.4971 | 80681.4484
[7 empty] | 7596 | 6259 | 1562803 | 2018-04-02 08:05 | 2018-04-02 08:10 | 5 | 11kV | 9018 | 2121 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 186296 Sensitive Earth Fault open circuit bi metal lug at ugoh or-67112. sef trip when back feeding no fault found auto open 0805hrs 10072 close 0809hrs close 10072 | April | 2018 | 2018Q4 | 2018 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | Unknown | Unknown | 2018-04-02 | N | 4.2518 | N | 21 | Y | Y | 1.1101 | 39.4971 | 6590.0884
[7 empty] | 8664 | 19657 | 1562455 | 2018-04-02 06:38 | 2018-04-02 08:55 | 137 | 11kV | 59893 | 673 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S129 HUnters Hill Pa47 tripped on Relays: SEL, A trip Lamp, A phase Lamp, Neutral lamp, IOC lamp Nicom Fdr B Relay: Trip Alarm, IOC, EFI A - N Abnormal Switching: SW/A closed at S1893, SW/B Open at S8996 Cause: UG cable fault from S4271 to S35708 to S2294 See OMS 1562958 1562959 1562960 1562961 1562455 1562476 1562477 1562472 | April | 2018 | 2018Q4 | 2018 | ZN129:PA47 | ZN129:PA47 | ZN00129/000047 | HUNTERS HILL | UG | Not Veg | 2018-04-02 | N | 88.9941 | N | 21 | Y | Y | 1.1101 | 39.4971 | 43768.0379
[7 empty] | 7885 | 9809 | 1562530 | 2018-04-02 14:26 | 2018-04-02 15:35 | 69 | 11kV | 88087 | 1437 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn14891 Wyong Pa5 "Wyong" fdr tripped, reclosed & locked out Relays: B&C phase timed O/C fault check, timing, lockout relays Signals: 11kv trip, No.1 Gfroup Earth EFI's: Nil Cause: UGOH fault short circuit. Fault on 11kv UGOH at S18164 Owen Ingram See 1562842,3,4 ex 1562526,30 | April | 2018 | 2018Q4 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | Unknown | Unknown | 2018-04-02 | N | 61.2992 | N | 21 | Y | Y | 1.1101 | 39.4971 | 64371.3815
[7 empty] | 7407 | 3916 | 1562571 | 2018-04-02 18:20 | 2018-04-02 19:25 | 65 | 11kV | 77740 | 1197 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Lightning | N | Zn12580 Erina Pa1 "Entrance Avoca" fdr tripped and locked out Relays: ABC phase IOC, Earth Fault, Reclose timing and lockout relays Signals: 11kv trip EFI's S18318 Cause: Lightning hit 11kv UGOH outside 13 Avoca St Erina See 1562945,6 ex 1562571 | April | 2018 | 2018Q4 | 2018 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | OH | Not Veg | 2018-04-02 | N | 64.9457 | N | 21 | Y | Y | 1.1101 | 39.4971 | 56810.0991
[7 empty] | 8187 | 13541 | 1562608 | 2018-04-02 20:13 | 2018-04-02 20:40 | 27 | 11kV | 810 | 30 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 186306 A Phase DOLF : 31 Amp Excluded OMS 1562608, 1562609 | April | 2018 | 2018Q4 | 2018 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2018-04-02 | N | 27 | N | 21 | Y | Y | 1.1101 | 39.4971 | 591.9241
[7 empty] | 8136 | 13036 | 1562570 | 2018-04-02 18:19 | 2018-04-02 20:50 | 151 | 11kV | 251542 | 1802 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | N | Zn12640 Umina Pa14 fdr tripped, reclsoed and locked out Relays: AB phase IOC & timed O/C, EFI, Reclose, timings and lockout relays SIgnals: 1kkv trip EFI's: Nil Cause: bond off above tee PT11995 See 1562940,1 ex 1562570 | April | 2018 | 2018Q4 | 2018 | ZN12640:PA14 | ZN12640:PA14 | ZN12640/000014 | CENTRAL COAST | OH | Not Veg | 2018-04-02 | N | 139.5905 | N | 21 | Y | Y | 1.1101 | 39.4971 | 183819.4744
[7 empty] | 8326 | 15242 | 1562606 | 2018-04-02 20:07 | 2018-04-02 21:14 | 67 | 11kV | 34371 | 513 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | iR63275 Washington Lincoln tripped on O/C Bat on 11kV near PT66057 | April | 2018 | 2018Q4 | 2018 | ZN9252:PA24 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Not Veg | 2018-04-02 | N | 67 | N | 21 | Y | Y | 1.1101 | 39.4971 | 25117.313
[7 empty] | 8352 | 15555 | 1563095 | 2018-04-02 21:12 | 2018-04-02 21:22 | 10 | 11kV | 15190 | 1519 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12610 Lng Jetty section of Pa24 "Hammond Park" Recloser 61590 Fishermans Bend Margherita tripped and reclosed on timed O/C Abnormal: AB44165 closed with LB63553 open, S14803:A closed with LK42048 open Cause: not ascertained. fdr to be patrolled during daylight hours | April | 2018 | 2018Q4 | 2018 | ZN12610:PA24 | ZN12610:PA24 | ZN12610/000024 | CENTRAL COAST | OH | Veg | 2018-04-02 | N | 10 | N | 21 | Y | Y | 1.1101 | 39.4971 | 11100.404
[7 empty] | 7267 | 1571 | 1562607 | 2018-04-02 20:09 | 2018-04-02 21:48 | 99 | 11kV | 172094 | 1883 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 186305 2 fault operations 3 phase Overcurrent, Earth Fault Blown LA UGOH pole VP-17014 Excluded OMS 1562607 | April | 2018 | 2018Q4 | 2018 | 243:80081 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | Unknown | Unknown | 2018-04-02 | N | 91.3935 | N | 21 | Y | Y | 1.1101 | 39.4971 | 125761.2193
[7 empty] | 8613 | 19016 | 1562588 | 2018-04-02 19:41 | 2018-04-02 22:00 | 138.5 | 11kV | 9141 | 66 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | Ex Zn12580 Erina section of Pa1 PT13494 Lexington Avoca blown HDO road side 20Amp Branch on HDO caused it blow cleared by DOp See 1562593 ex 1562588 1562594 1562602 | April | 2018 | 2018Q4 | 2018 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | OH | Veg | 2018-04-02 | N | 138.5 | N | 21 | Y | Y | 1.1101 | 39.4971 | 6679.9732
[7 empty] | 8474 | 17330 | 1562563 | 2018-04-02 17:58 | 2018-04-02 22:00 | 242 | 11kV | 484 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 186307 C Phase DOLF : 10 Amp Excluded OMS 1562563 | April | 2018 | 2018Q4 | 2018 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2018-04-02 | N | 242 | N | 21 | Y | Y | 1.1101 | 39.4971 | 353.6929
[7 empty] | 8598 | 18828 | 1562577 | 2018-04-02 18:58 | 2018-04-02 22:22 | 204 | 11kV | 123276 | 901 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | Zn12690 Berkeley Vale Pa24 fdr tripped and locked out Relays: 24R AB phase timed o/c, EFI Signals: 11kv trip EFI's Cause not ascertained See 1562952,4,5,6 ex 1562577 | April | 2018 | 2018Q4 | 2018 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2018-04-02 | N | 136.8213 | N | 21 | Y | Y | 1.1101 | 39.4971 | 90086.4648
[7 empty] | 7751 | 8059 | 1562611 | 2018-04-02 20:18 | 2018-04-02 23:40 | 201.9833 | 11kV | 807.9333 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186309 Single phase DOLF : 20 Amp | April | 2018 | 2018Q4 | 2018 | 227:13015 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2018-04-02 | N | 201.9833 | N | 21 | Y | Y | 1.1101 | 39.4971 | 590.4139
[7 empty] | 8528 | 17958 | 1562581 | 2018-04-02 19:14 | 2018-04-03 00:35 | 321 | 11kV | 963 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Enclosed Load Break Switch | Unplanned | Lightning | N | Ex Zn12650 West Gosford section of Pa1 PT13887 Kadija Mangrove 10Amp HDO operated Cause: lightning | April | 2018 | 2018Q4 | 2018 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2018-04-02 | N | 321 | N | 21 | Y | Y | 1.1101 | 39.4971 | 703.732
[7 empty] | 7235 | 1032 | 1562656 | 2018-04-03 01:21 | 2018-04-03 02:10 | 49 | 11kV | 98735 | 2015 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | Rain Heavy | N | At Zn3600 Balgowlah North Panel 3 tripped on Signals: 11kV trip, TX1 Group Earth Relays: A B and C phase, EFI,TX1B Fault Check, Frame Leakage Prohibition Cause: Possum Found at base of enclosed load break LB61276 | April | 2018 | 2018Q4 | 2018 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2018-04-03 | N | 49 | N | 10 | N | N | 1.1101 | 39.4971 | 72152.6258
[7 empty] | 7660 | 6915 | 1562648 | 2018-04-02 23:02 | 2018-04-03 03:28 | 266 | 11kV | 31460 | 199 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 186310 1 fault operation Patrolled, nothing found & suply restored. As per Michael Judge, ferroresonance caused a flashover on a lightning arrestor whilst they were changing a HV fuse at the Army Camp This caused 2 more outages on the 3rd April Excluded OMS 1562648 | April | 2018 | 2018Q4 | 2018 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | Unknown | Not Veg | 2018-04-02 | N | 158.0905 | N | 21 | Y | Y | 1.1101 | 39.4971 | 22990.0401
[7 empty] | 8459 | 17099 | 1562634 | 2018-04-02 21:20 | 2018-04-03 04:15 | 415 | 11kV | 232467 | 1344 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Lightning | N | Zn12610 Long Jetty Panel 25 "Long Jetty Aux No.2" fdr tripped and locke dout Relays: SEF, EFI, Earth Fault check relay, 11kv frame leakage panel - prohibitions relay Signals: 11kv trip EFI's: Nil Cause: OH down 11kv mains down +multiple HV bonds off on section of Panel 25 Between mainline feeder & HV USL 40871 See 1563096,7,8,9,100,1 ex 1562634,57 | April | 2018 | 2018Q4 | 2018 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2018-04-02 | N | 172.9665 | N | 21 | Y | Y | 1.1101 | 39.4971 | 169880.027
[7 empty] | 7857 | 9401 | 1563057 | 2018-04-03 05:10 | 2018-04-03 05:17 | 7 | 11kV | 10423 | 1489 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Panel 35 tripped on Signals: 11KV TRIP. Relays: A Prot Relay: LED: TRIP, A PHASE, Neutral, EARTH FAULT. 'B' Prot: LED - Trip, Alarm, Earth Fault, EFI, E-N. Abnormal switching - 2 11kV feeder faults 1) S4271 to S2294 to S35708 defective 2) S8996 to S4272 defective Dop proved faulted feeder after repairs between S.8996 (SW/B) & S.4272 (SW/A), successfully. When SW/B was Closed @ S.4272 to energise the de-energised section of mains (mains de-energised between 2 HV Faults) feeder tripped. Appears to be a further fault from S.4272 (SW/B) to S.35708 (SW/A). | April | 2018 | 2018Q4 | 2018 | ZN129:PA35 | ZN129:PA35 | ZN00129/000035 | HUNTERS HILL | UG | Not Veg | 2018-04-03 | N | 7 | N | 10 | N | N | 1.1101 | 39.4971 | 7616.821
[7 empty] | 8006 | 11190 | 1562619 | 2018-04-02 20:42 | 2018-04-03 07:30 | 648 | 11kV | 5184 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | Ex Zn12630 Peats Ridge section of pa11 PT13257 Silvester Anembo 11kv hdo BC phase 16Amp fuse blown cause: lightning See 1563118 ex 1562619 | April | 2018 | 2018Q4 | 2018 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2018-04-02 | N | 648 | N | 21 | Y | Y | 1.1101 | 39.4971 | 3788.3143
[7 empty] | 7661 | 6916 | 1562663 | 2018-04-03 05:20 | 2018-04-03 09:12 | 232 | 11kV | 36940 | 199 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 186311 1 fault operation Sensitive Earth Fault Feeder completely patrolled in daylight. Nothing found to indicate SEF. As per Michael Judge, ferroresonance caused a flashover on a lightning arrestor in the army camp, whilst they were replacing one of their HV fuse Excluded OMS 1562663 | April | 2018 | 2018Q4 | 2018 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | Unknown | Not Veg | 2018-04-03 | N | 185.6281 | N | 10 | N | N | 1.1101 | 39.4971 | 26994.6625
[7 empty] | 8404 | 16396 | 1562666 | 2018-04-03 06:04 | 2018-04-03 09:55 | 231 | 11kV | 1155 | 5 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | Ex Zn12690 Berkeley Vale section of Pa24 PT47326 Palmdale Wallaby 0.25 11kv HDO footpath phase 10Amp fuse blown Cause: lightning See 1563126 ex 1562666 1562679 | April | 2018 | 2018Q4 | 2018 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2018-04-03 | N | 231 | N | 10 | N | N | 1.1101 | 39.4971 | 844.0399
[7 empty] | 7423 | 4114 | 1562644 | 2018-04-02 22:14 | 2018-04-03 10:25 | 731 | 11kV | 2924 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Lightning | N | Ex Zn14891 Wyong section of Pa8 PT11393 Old Maitland Prest 0.7 11kv HDO roadside phase 16Amp fuse blown Cause: lightning See 1563132 ex 1562707 1562644 | April | 2018 | 2018Q4 | 2018 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Not Veg | 2018-04-02 | N | 731 | N | 21 | Y | Y | 1.1101 | 39.4971 | 2136.773
[7 empty] | 7492 | 5198 | 1562719 | 2018-04-03 08:50 | 2018-04-03 10:26 | 96 | 11kV | 192 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 186314 Single phase DOLF : 10 Amp Excluded OMS 1562719 | April | 2018 | 2018Q4 | 2018 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2018-04-03 | N | 96 | N | 10 | N | N | 1.1101 | 39.4971 | 140.3079
[7 empty] | 8554 | 18301 | 1562667 | 2018-04-02 20:42 | 2018-04-03 12:50 | 968 | 11kV | 6776 | 7 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Lightning | N | Ex Zn12600 Lisarow section of Pa2 PT11346 Croton Katandra 11kv HDO roadside phase 10Amp fuse blown due to lightning See 1563128 ex 1562671,4 1562618 | April | 2018 | 2018Q4 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2018-04-02 | N | 968 | N | 21 | Y | Y | 1.1101 | 39.4971 | 4951.7009
[7 empty] | 7667 | 7009 | 1562858 | 2018-04-03 12:48 | 2018-04-03 13:30 | 42 | 11kV | 808 | 20 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2466 Flemington Panel No.32 "Birnie Par No.3" feeder tripped on Earth fault, fault check relay & EFI. Zone earth, No.3 Group earth & 11kv trip EFI operated @ S8125 Abnormal: Sw/A @ S65220 Birnie Bachell No.5 closed & Sw/B @ S8580 Birnie Pippita open for load relief Panel No.5 Remarks: 11kv feeder fault between S8125 Birnie Par No.3 to S61885 Birnioe Par No.3 | April | 2018 | 2018Q4 | 2018 | ZN2466:PA32 | ZN2466:PA6 | ZN02466/000006 | CUMBERLAND | UG | Not Veg | 2018-04-03 | N | 40.4 | N | 10 | N | N | 1.1101 | 39.4971 | 590.4626
[7 empty] | 7683 | 7154 | 1562688 | 2018-04-03 07:55 | 2018-04-03 13:50 | 355 | 11kV | 696 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186315 3 phase DOLF : 80 Amp 3 X DOLFS BLOWN 40938 (80A) 1 x DOLF Blown sub 53471 (10A) A phase RMI @ 38360 Dyno Nobel sub put under AP to check for internal fault before restoring supply from LF 40938. Excluded oms 1562688 | April | 2018 | 2018Q4 | 2018 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Veg | 2018-04-03 | N | 348 | N | 10 | N | N | 1.1101 | 39.4971 | 508.6163
[7 empty] | 7404 | 3881 | 1562866 | 2018-04-03 13:07 | 2018-04-03 15:17 | 130 | 11kV | 19420 | 199 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 186320 1 fault operation Sensitive Earth Fault 3rd SEF trip today. Feeder has been split into three to narrow down fault area. As per Michael Judge, ferroresonance caused a flashover on a lightning arrestor in the army camp, whilst they were replacing one of their HV fuse See also LID # 186310 &186311. Excluded OMS 1562866. | April | 2018 | 2018Q4 | 2018 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | Unknown | Not Veg | 2018-04-03 | N | 97.5879 | N | 10 | N | N | 1.1101 | 39.4971 | 14191.5632
[7 empty] | 7740 | 7896 | 1562921 | 2018-04-03 14:45 | 2018-04-03 16:40 | 115 | 11kV | 4510 | 40 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 LK42504 interrupted & isolated to remove tree branch on 11kv & LV at LK44841 need to be removed See 1563129 ex 1563130 1562921 | April | 2018 | 2018Q4 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2018-04-03 | N | 112.75 | N | 10 | N | N | 1.1101 | 39.4971 | 3295.775
[7 empty] | 7476 | 5033 | 1562922 | 2018-04-03 15:07 | 2018-04-03 20:45 | 337.5833 | 11kV | 5401.3333 | 16 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 186323 Bph tapping burnt off at ABS 62965 | April | 2018 | 2018Q4 | 2018 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2018-04-03 | N | 337.5833 | N | 10 | N | N | 1.1101 | 39.4971 | 3947.1351
[7 empty] | 7853 | 9364 | 1563001 | 2018-04-04 05:36 | 2018-04-04 07:15 | 99 | 11kV | 8613 | 87 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 186324 C Phase DOLF : 50 Amp Possum. Volts = 246. Amps = 64,116,100 Excluded OMS 1563016. | April | 2018 | 2018Q4 | 2018 | 205:12213 | 205:12213 | ZN00205/012213 | NEWCASTLE | OH | Not Veg | 2018-04-04 | N | 99 | N | 5 | N | N | 1.1101 | 39.4971 | 6294.1264
[7 empty] | 7843 | 9276 | 1563040 | 2018-04-04 08:24 | 2018-04-04 10:03 | 99 | 11kV | 495 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of 24R "Burns Rd" PT12439 Palmdale Pacific 3.2 the roadside 16Amp HDO blew | April | 2018 | 2018Q4 | 2018 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2018-04-04 | N | 99 | N | 5 | N | N | 1.1101 | 39.4971 | 361.7314
[7 empty] | 8604 | 18907 | 1563135 | 2018-04-04 11:28 | 2018-04-04 12:40 | 72 | 11kV | 278 | 4 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 186338 2 fault operations A & B phase Overcurrent 11kV crossarm on fire & broke at pole KT-70096. Excluded OMS 1563135, 1563138, 1563139, 1563142 | April | 2018 | 2018Q4 | 2018 | 228:7486 | 228:85407 | ZN00228/085407 | NEWCASTLE | OH | Not Veg | 2018-04-04 | N | 69.5 | N | 5 | N | N | 1.1101 | 39.4971 | 203.1542
[7 empty] | 8041 | 11543 | 1563185 | 2018-04-04 14:22 | 2018-04-04 16:46 | 144 | 11kV | 143528 | 1176 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | LID 186340 3 phase Instantaneous Overcurrent Lightning Strike A prot...3Ph Inst O/C B prot...BCN Inst O/C Excluded OMS 1563185 | April | 2018 | 2018Q4 | 2018 | 532:83298 | 532:83298 | ZN00532/083298 | MAITLAND | OH | Veg | 2018-04-04 | N | 122.0476 | N | 5 | N | N | 1.1101 | 39.4971 | 104886.029
[7 empty] | 7881 | 9784 | 1563276 | 2018-04-04 20:02 | 2018-04-04 21:35 | 93 | 11kV | 3501 | 41 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa2 RE42120 Holgate tripped Relays: Nil control panel appears to be faulty and is scan fail. PT11789 The Ridgeway Fagans 2 HVDOs (footpath and centre) operated Cause: transformer failed at PT11789 and appears to be leaking oil. Isolated and restored by LV// See 1563458,9 ex 1563276,82 | April | 2018 | 2018Q4 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2018-04-04 | N | 85.3902 | N | 5 | N | N | 1.1101 | 39.4971 | 2558.4275
[7 empty] | 8638 | 19349 | 1563325 | 2018-04-05 08:30 | 2018-04-05 11:20 | 170 | 11kV | 170 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa13 "Peats Ridge Aux" PT11802 Keighly Grants 1.4 blew centre phase 16A HDO Cause not ascertained See 1563956 ex 1563325 | April | 2018 | 2018Q4 | 2018 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2018-04-05 | N | 170 | N | 2 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 8667 | 19673 | 1563492 | 2018-04-05 23:46 | 2018-04-06 01:50 | 124 | 11kV | 80453 | 687 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn9534 Kurnell South - Pnl.17 tripped, reclosed & locked out on: A & B Phase O/C DOp advised Bats flying around 11kV mains at time of patrol. See 1563509 1563512 1563513 1563514 | April | 2018 | 2018Q4 | 2018 | ZN9534:PA17 | ZN9534:PA17 | ZN09534/000017 | SUTHERLAND | OH | Not Veg | 2018-04-05 | N | 117.1077 | N | 2 | N | N | 1.1101 | 39.4971 | 58792.6794
[7 empty] | 8500 | 17642 | 1563561 | 2018-04-06 10:14 | 2018-04-06 11:26 | 72 | 11kV | 85848 | 1210 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15008 Harbord Panel 5 "Queenscliff" fdr tripped on Relays: B Phase IOC, EFI, EF check, timing, lokcout Singals: Zone Earth 11kv trip EFI: S16800 Cause: UG fault from Zn16800 Albert Moore SwA to S77556 SwA See 1564034,5 ex 1563561,93,604 | April | 2018 | 2018Q4 | 2018 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | UG | Not Veg | 2018-04-06 | N | 70.9488 | N | 2 | N | N | 1.1101 | 39.4971 | 62735.1863
[7 empty] | 8272 | 14613 | 1563595 | 2018-04-06 11:39 | 2018-04-06 18:57 | 438 | 11kV | 220061 | 3039 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15008 Harbord Pa1 "Park District" fdr tripped on Relays: SEL Abnormal: S16950:A closed S77556:A Open Cause: contractor hit UG cable from S65754 to LB63712 tee PT15656. 11kv bond burnt off on UGOH connection on Pa5 below LB21623. Cable was hit by contractor while cable was de-energised from previous fault on Pa5. See 1564053,4,5,6 ex 1563595 | April | 2018 | 2018Q4 | 2018 | ZN15008:PA1 | ZN15008:PA1 | ZN15008/000001 | NORTHERN BEACHES | UG | Not Veg | 2018-04-06 | N | 72.4123 | N | 2 | N | N | 1.1101 | 39.4971 | 160814.0881
[7 empty] | 7836 | 9201 | 1563804 | 2018-04-07 18:29 | 2018-04-07 22:15 | 226 | 11kV | 904 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Ex Zn14891 Wyong section of Pa12 "Yarramalong" fdr PT11302 Summerless Yarram No.1 western phase HDO blown Cause: tree branch removed by DOp See 1563961 ex 1563804 | April | 2018 | 2018Q4 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2018-04-07 | N | 226 | N | 2 | N | N | 1.1101 | 39.4971 | 660.6165
[7 empty] | 7528 | 5617 | 1563816 | 2018-04-07 23:10 | 2018-04-08 01:33 | 143 | 11kV | 103464 | 1063 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Panel 21 "Glading Bisshop" fdr tripped on earth fault EFI fault check Cause: UG fault in section of cable from Zn14271:B to S14270:A defective EFI at S14271 See 1563969,71,3 ex 1563816 | April | 2018 | 2018Q4 | 2018 | ZN14892:PA21 | ZN14892:PA21 | ZN14892/000021 | CENTRAL COAST | UG | Not Veg | 2018-04-07 | N | 97.3321 | N | 2 | N | N | 1.1101 | 39.4971 | 75608.4395
[7 empty] | 8633 | 19255 | 1563822 | 2018-04-08 05:01 | 2018-04-08 06:35 | 94 | 11kV | 104775 | 1122 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 40 tripped on Relays A and B phase OC and IOC, EFI Signals: CB 40 Open, Prot Trip, Fault Flag Cause: UG cable fault - SW/B @ S35386 to S/A @ s3322 See OMS 1564280 1564281 1563822 | April | 2018 | 2018Q4 | 2018 | ZN129:PA40 | ZN129:PA40 | ZN00129/000040 | RYDE | UG | Not Veg | 2018-04-08 | N | 93.3824 | N | 2 | N | N | 1.1101 | 39.4971 | 76566.4797
[7 empty] | 7565 | 5989 | 1563896 | 2018-04-08 20:48 | 2018-04-08 21:35 | 47 | 11kV | 2585 | 55 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 186372 C phase DOLF : 31 Amp HV DOLF CARRIER BURNT IN HALF. REPLACED CARRIER. Volts =245. Load A=80 B= 70 C=80 Excluded OMS REPORTS 1563896, 1563900, 1563987, 1563899. | April | 2018 | 2018Q4 | 2018 | 235:2123 | 235:2123 | ZN00235/002123 | NEWCASTLE | OH | Not Veg | 2018-04-08 | N | 47 | N | 2 | N | N | 1.1101 | 39.4971 | 1889.0418
[7 empty] | 8557 | 18329 | 1563906 | 2018-04-09 00:03 | 2018-04-09 01:48 | 105 | 11kV | 294385 | 3089 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36300 Balgowlah Pa11 tripped on: Signals: 11kv trip, Tx1 Group Earth Relays: 11L Earth Fault, EFI EFI's S16400 S17117 S15534 S15385 S16510 Abnormal: S16509 SwA closed SwB open Cause: 11kv fdr from Zn16512:b to S16511:B See 1564065,6 ex 1563906,7 | April | 2018 | 2018Q4 | 2018 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | UG | Not Veg | 2018-04-09 | N | 95.3011 | N | 4 | N | N | 1.1101 | 39.4971 | 215127.8751
[7 empty] | 7883 | 9794 | 1564024 | 2018-04-09 12:51 | 2018-04-09 14:35 | 104 | 11kV | 122639 | 1413 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn10998 Rockdale - Pnl.32 tripped, reclosed and locked out on: B & C phase IOC UGOH fault short circuit - Marsh St near Innesdale St See 1564469 1564470 1564471 | April | 2018 | 2018Q4 | 2018 | ZN10998:PA32 | ZN10998:PA32 | ZN10998/000032 | BAYSIDE | Unknown | Unknown | 2018-04-09 | N | 86.7933 | N | 4 | N | N | 1.1101 | 39.4971 | 89620.964
[7 empty] | 8496 | 17567 | 1564121 | 2018-04-09 15:52 | 2018-04-09 16:55 | 63 | 11kV | 19362 | 1062 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | LID 186376 1 fault operation A Phase Earth Fault appears to be a TX or LV tails fault. fault current 283A/103B/115C/183N Isolations extended to include fdr endboxes as they have no bottom cover plates. Excluded OMS 1564143 | April | 2018 | 2018Q4 | 2018 | 213:33773 | 213:33773 | ZN00213/033773 | NEWCASTLE | UG | Not Veg | 2018-04-09 | N | 18.2316 | N | 4 | N | N | 1.1101 | 39.4971 | 14149.1785
[7 empty] | 7205 | 485 | 1564016 | 2018-04-09 12:42 | 2018-04-09 23:20 | 638 | 11kV | 7013 | 97 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa2 "Holgate" fdr RE41066 MacDonalds Rd has tripped Relays: OC trip and LO Cause: vehicle hit pole See OMS Job See 1564745,6 ex 1564016,31,44 | April | 2018 | 2018Q4 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2018-04-09 | N | 72.299 | N | 4 | N | N | 1.1101 | 39.4971 | 5124.8936
[7 empty] | 7202 | 460 | 1564205 | 2018-04-10 05:19 | 2018-04-10 08:18 | 179 | 11kV | 1432 | 8 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 186377 LL lead had become detached. No protection operated. Excluded OMS 1564205 & 1564209. | April | 2018 | 2018Q4 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2018-04-10 | N | 179 | N | 3 | N | N | 1.1101 | 39.4971 | 1046.4634
[7 empty] | 8363 | 15680 | 1564271 | 2018-04-10 12:30 | 2018-04-10 17:15 | 285 | 11kV | 570 | 2 | HV | 3rd Party Vehicle | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186381 11kV Fdr isolated for motor vehicle accident adjacent 66kV pole AL-10114. Excluded OMS No. 1564271 | April | 2018 | 2018Q4 | 2018 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2018-04-10 | N | 285 | N | 3 | N | N | 1.1101 | 39.4971 | 416.5392
[7 empty] | 7648 | 6786 | 1564221 | 2018-04-10 08:20 | 2018-04-10 20:30 | 730 | 11kV | 166702 | 1487 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 Matraville - Pnl.26 tripped on: B Phase O.C Abnormal: S8626 (Sw/A) closed with S8624 (Sw/A) open UG cable damaged by contractor. Section of feeder from S8626 to S8627 to 5393 tee S5970 & S2086 - Non Paralleling subs See 1564481 1564482 1564232 | April | 2018 | 2018Q4 | 2018 | ZN1788:PA26 | ZN1788:PA42 | ZN01788/000042 | RANDWICK | UG | Not Veg | 2018-04-10 | N | 112.1063 | N | 3 | N | N | 1.1101 | 39.4971 | 121820.9047
[7 empty] | 7664 | 6967 | 1564419 | 2018-04-11 05:34 | 2018-04-11 08:45 | 191 | 11kV | 191 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At CP1634 North Head Quarantine Customer's internal network is OH and has a recloser 1 span from a HV ugoh near CP1623. Customers HV ASP patrolled private network and gave clearance DOP replaced fuses and energised up to customers recloser. See OMS 1564630 1564419 | April | 2018 | 2018Q4 | 2018 |  |  |  | NORTHERN BEACHES | OH | Veg | 2018-04-11 | N | 191 | N | 3 | N | N | 1.1101 | 39.4971 | 139.5772
[7 empty] | 8436 | 16769 | 1564450 | 2018-04-11 08:21 | 2018-04-11 12:07 | 226 | 11kV | 41650 | 393 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn340 Botany Pnl.18 tripped on: B Phase O/C Field EFIs: S2913 S5545 S8672 S35992 Abnormal: S6371 (Sw/D) Closed with CP62150 Open UG cable fault. Section of feeder from S35992 (Sw/B) to S6371 (Sw/D) to S2150 (Sw/A). Section of feeder from S8708 to CP62150 was out of service for development work and had to recalled, proven and phased prior to restoration of 3 DCs. See 1564731 1564732 1564734 1564735 | April | 2018 | 2018Q4 | 2018 | ZN340:PA18 | ZN340:PA34 | ZN00340/000034 | BAYSIDE | UG | Not Veg | 2018-04-11 | N | 105.9796 | N | 3 | N | N | 1.1101 | 39.4971 | 30436.5915
[7 empty] | 8219 | 14007 | 1564609 | 2018-04-11 23:11 | 2018-04-12 03:45 | 274 | 11kV | 105145 | 1344 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn2635 Epping Panel 52 "York Dorset" fdr tripped, reclsoed and locked out Relays: Minor Alarm, E/F, O/C C phase and lock out timing EFI Signals: 11kv trip EFI: S48155 Cause: POssum found at 11kv UGOH before S8770 Malton Boundary Fault cause 11kv OH before UGOH HR and one phase was found on the ground before PT2382 Cotton Downes See 1564762,4,5,6 ex 1564609,10,6 | April | 2018 | 2018Q4 | 2018 | ZN2635:PA52 | ZN2635:PA52 | ZN02635/000052 | HORNSBY | OH | Not Veg | 2018-04-11 | N | 78.2329 | N | 3 | N | N | 1.1101 | 39.4971 | 76836.8647
[7 empty] | 8592 | 18709 | 1564703 | 2018-04-12 12:05 | 2018-04-12 12:57 | 52.5 | 11kV | 52.5 | 1 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186407 A Phase DOLF : 10 Amp Excluded OMS 1564706 | April | 2018 | 2018Q4 | 2018 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2018-04-12 | N | 52.5 | N | 3 | N | N | 1.1101 | 39.4971 | 38.3655
[7 empty] | 7233 | 996 | 1564753 | 2018-04-12 14:25 | 2018-04-12 16:45 | 140 | 11kV | 44240 | 316 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | LID 186411 Lucy switchgear tracking at sub 16276, also Low Oil. Excluded oms 1564753 | April | 2018 | 2018Q4 | 2018 | 261:81864 | 261:81864 | ZN00261/081864 | LAKE MACQUARIE | UG | Not Veg | 2018-04-12 | N | 140 | N | 3 | N | N | 1.1101 | 39.4971 | 32329.2871
[7 empty] | 8492 | 17494 | 1564779 | 2018-04-12 15:12 | 2018-04-12 17:19 | 127 | 11kV | 108448 | 896 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Pa8 "O Hart Pacific" CB tripped reclosed and locked out on: Signals: 11kv trip, Tx1 Group Earth Relays: Basler EF * OC Relay: 51N Fault Check, Timing, Lockout EFI's: Cause: UG Fault Suspected UG Fault in section of 11kv fdr from AB44857 to LB77428 to S18399 stratford Lakehaven no SwB tee to PT12361 Moala Stratford See 1565628,9,30 ex 1564779 | April | 2018 | 2018Q4 | 2018 | ZN14892:PA8 | ZN14892:PA8 | ZN14892/000008 | CENTRAL COAST | UG | Not Veg | 2018-04-12 | N | 121.0357 | N | 3 | N | N | 1.1101 | 39.4971 | 79250.5997
[7 empty] | 7599 | 6302 | 1564846 | 2018-04-13 02:58 | 2018-04-13 04:09 | 70.5833 | 11kV | 63525 | 900 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn15014 Mona Vale Pa22 "Pondersa Mona Vale" tripped on Earth Fault, EFI, F/C & F/C #1 Tx, 11kV trip Cause: Dead POssum at Base of UGOH near S16395 See 1564846 ex 1564847 | April | 2018 | 2018Q4 | 2018 | ZN15014:PA22 | ZN15014:PA22 | ZN15014/000022 | NORTHERN BEACHES | OH | Not Veg | 2018-04-13 | N | 70.5833 | N | 5 | N | N | 1.1101 | 39.4971 | 46422.1963
[7 empty] | 8563 | 18375 | 1564959 | 2018-04-13 13:29 | 2018-04-13 15:12 | 103 | 11kV | 77 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186425 3 phase Protection malgrade at Newcastle Uni sub 1 MC Mullin 258/5 D2 E/F Trip occured on CB 90976 at the same time at a trip and lockout on fdr 80781 Jesmond sub 0917hrs A subsequent OC trip occured on CB 90975 interupting Newcastle Uni sub when the fdr 80781 tripped under fault current at 1413hrs. John Donkin is aware of the problem and has a theory. dq Excluded OMS 1564967/1564966## | April | 2018 | 2018Q4 | 2018 |  |  |  | NEWCASTLE | OH | Not Veg | 2018-04-13 | N | 77 | N | 5 | N | N | 1.1101 | 39.4971 | 56.2693
[7 empty] | 8071 | 12095 | 1564924 | 2018-04-13 11:00 | 2018-04-13 17:05 | 365 | 11kV | 2190 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kVfeeder from AB2421 to LB298 interrupted by DOp to remove tree branch about to fall on 11kV Mains. See OMS 1564924 1564925 | April | 2018 | 2018Q4 | 2018 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2018-04-13 | N | 365 | N | 5 | N | N | 1.1101 | 39.4971 | 1600.3874
[7 empty] | 8403 | 16376 | 1564889 | 2018-04-13 09:17 | 2018-04-13 18:59 | 582 | 11kV | 230797 | 1513 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186426 3 phase Earth Fault possible arrester fault at pole jt 82202, test suspect cable between pole JT 82202 and pole JT 80969. dq Excluded oms 1564889, 1564959 | April | 2018 | 2018Q4 | 2018 | 258:80781 | 258:80781 | ZN00258/080781 | NEWCASTLE | OH | Not Veg | 2018-04-13 | N | 152.5426 | N | 5 | N | N | 1.1101 | 39.4971 | 168659.6402
[7 empty] | 7728 | 7781 | 1565038 | 2018-04-13 21:46 | 2018-04-13 23:59 | 133 | 11kV | 6650 | 50 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of Pa19R PT11738 Bundilla Wyong 31.5Amp HDO blew Cause: Fuse Fatigue See 1565646 ex 1565038 | April | 2018 | 2018Q4 | 2018 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Not Veg | 2018-04-13 | N | 133 | N | 5 | N | N | 1.1101 | 39.4971 | 4859.6239
[7 empty] | 8111 | 12669 | 1565043 | 2018-04-14 03:36 | 2018-04-14 05:45 | 128.5167 | 11kV | 8610.6167 | 67 | HV | Animal Flying Fox | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn15012 Killarney Ex Panel 8 11kV HDO road and centre pahse 31.5Amp fuse blown A bat was found below PT15429 Mavor See 1565043 ex 1565044 | April | 2018 | 2018Q4 | 2018 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Not Veg | 2018-04-14 | N | 128.5167 | N | 19 | N | N | 1.1101 | 39.4971 | 6292.3847
[7 empty] | 8316 | 15144 | 1565056 | 2018-04-14 08:10 | 2018-04-14 10:30 | 140 | 11kV | 420 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186428 Single phase DOLF : 10 Amp Excluded OMS 1565056 | April | 2018 | 2018Q4 | 2018 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2018-04-14 | N | 140 | N | 19 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 7707 | 7518 | 1565063 | 2018-04-14 09:13 | 2018-04-14 11:12 | 119 | 11kV | 18789 | 159 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1290 Leightonfield 11kv Panel No.13 "S7858 Christina Birmingham No.2" feeder tripped on- Relays: E/fault, EFI Signals: 11kv trip, No3 tx group E, Zone E EFIs: S7858, S50149, S8449, S5236 (No access) Remarks: UG fault. 11kv feeder from S5236 Birmingham Ave Sw/B to S50149 Birmingham Ave No.5 Sw/A. Likely earthing issues on feeder after false EFI inductions and burst water pipe o/s No.7 Birmingham Ave Villawood | April | 2018 | 2018Q4 | 2018 | ZN1290:PA13 | ZN1290:PA13 | ZN01290/000013 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-04-14 | N | 118.1698 | N | 19 | N | N | 1.1101 | 39.4971 | 13730.447
[7 empty] | 7197 | 400 | 1565091 | 2018-04-14 11:54 | 2018-04-14 13:45 | 110.9667 | 11kV | 8988.3 | 81 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186430 A Phase Broken Aph LLC Dropper | April | 2018 | 2018Q4 | 2018 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2018-04-14 | N | 110.9667 | N | 19 | N | N | 1.1101 | 39.4971 | 6568.3845
[7 empty] | 8631 | 19246 | 1565081 | 2018-04-14 11:15 | 2018-04-14 15:10 | 235 | 11kV | 235 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186431 Single phase Broken LLC Dropper Excluded OMS 1565081 | April | 2018 | 2018Q4 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2018-04-14 | N | 235 | N | 19 | N | N | 1.1101 | 39.4971 | 171.7311
[7 empty] | 8341 | 15387 | 1565129 | 2018-04-14 14:37 | 2018-04-14 15:47 | 70 | 11kV | 5460 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn14891 Wyong section of Pa5 "Wyong" RE45016 Dickson tripped to lockout Relays: O/C trip, IOC trip Cause: Tree/Branch on OH mains. Removed by DOp outside 898 Dickson rd Dooralong See 1565129 ex 1565148,9 | April | 2018 | 2018Q4 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2018-04-14 | N | 70 | N | 19 | N | N | 1.1101 | 39.4971 | 3990.007
[7 empty] | 8415 | 16526 | 1565170 | 2018-04-14 16:02 | 2018-04-14 17:13 | 71 | 11kV | 13433 | 345 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186433 4 fault operations 3 phase Overcurrent Trees on mains at sub 47064 Excluded OMS 1565170 | April | 2018 | 2018Q4 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2018-04-14 | N | 38.9362 | N | 19 | N | N | 1.1101 | 39.4971 | 9816.4402
[7 empty] | 7491 | 5197 | 1565191 | 2018-04-14 16:59 | 2018-04-14 17:53 | 54 | 11kV | 108 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 186452 DOLF : 10 Amp Excluded OMS 1565191 | April | 2018 | 2018Q4 | 2018 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2018-04-14 | N | 54 | N | 19 | N | N | 1.1101 | 39.4971 | 78.9232
[7 empty] | 8133 | 12992 | 1565179 | 2018-04-14 16:39 | 2018-04-14 18:39 | 120 | 11kV | 600 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 186450 3 phase distribution fuses : 100 Amp Excluded OMS 1565179 | April | 2018 | 2018Q4 | 2018 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2018-04-14 | N | 120 | N | 19 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 8447 | 16886 | 1565198 | 2018-04-14 17:17 | 2018-04-14 20:05 | 168 | 11kV | 672 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186453 Single phase DOLF : 20 Amp Excluded OMS 1565210 | April | 2018 | 2018Q4 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2018-04-14 | N | 168 | N | 19 | N | N | 1.1101 | 39.4971 | 491.0778
[7 empty] | 7970 | 10625 | 1565197 | 2018-04-14 17:17 | 2018-04-14 20:05 | 168 | 11kV | 336 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 186454 Single Phase DOLF : 16 Amp Blown L/A's Excluded OMS 1565197 | April | 2018 | 2018Q4 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-04-14 | N | 168 | N | 19 | N | N | 1.1101 | 39.4971 | 245.5389
[7 empty] | 8674 | 19746 | 1565252 | 2018-04-14 20:21 | 2018-04-14 20:30 | 9 | 11kV | 648 | 72 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12640 Umina section of Pa14 PT12778 Myall Bourke 11kv centre phase HDO 31.5 operated type BBC Cause: fuse failure. appears fuse fatigue. Replaced all supply restored checked ok See 1565661 ex 1565652,6,60,2,3 | April | 2018 | 2018Q4 | 2018 | ZN12640:PA14 | ZN12640:PA14 | ZN12640/000014 | CENTRAL COAST | OH | Not Veg | 2018-04-14 | N | 9 | N | 19 | N | N | 1.1101 | 39.4971 | 473.5393
[7 empty] | 7943 | 10328 | 1565155 | 2018-04-14 15:48 | 2018-04-14 23:00 | 432 | 11kV | 58897 | 410 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa1 "Gunderman" RE45189 Cooks Peat Ridge 0.5 tripped and reclsoed to lockout Relays: IOC, O/C trip Cause: Tree/Branch on OH Mains on section of 11kv fdr from AB40602 toRE44945 tee PT14968 Non Parallel and PT13482 Non Parallel See 1565652,4,5 ex 1565155,8,69,82,249 | April | 2018 | 2018Q4 | 2018 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2018-04-14 | N | 143.6512 | N | 19 | N | N | 1.1101 | 39.4971 | 43040.1904
[7 empty] | 7765 | 8250 | 1565235 | 2018-04-14 19:29 | 2018-04-14 23:05 | 216 | 11kV | 4784 | 169 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 186461 2 fault operations Span down near PT 72628 Dellosta. Excluded OMS 1565235 | April | 2018 | 2018Q4 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2018-04-14 | N | 28.3077 | N | 19 | N | N | 1.1101 | 39.4971 | 3496.0061
[7 empty] | 7702 | 7450 | 1565201 | 2018-04-14 17:23 | 2018-04-14 23:30 | 367 | 11kV | 31371 | 108 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 186460 2 fault operations 3 phase Overcurrent; Sensitive Earth Fault BLOWN DOLF at PT 70171. Excluded OMS 1565201. | April | 2018 | 2018Q4 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2018-04-14 | N | 290.4722 | N | 19 | N | N | 1.1101 | 39.4971 | 22925.0015
[7 empty] | 7385 | 3664 | 1565186 | 2018-04-14 16:53 | 2018-04-14 23:45 | 412 | 11kV | 7992 | 36 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Electrical Storm | N | LID 186451 Darren thinks maybe RMI faulty as supply was restored ok after opening Sw 11243 and closing Sw 11244. Please investigate. D Pascoe since found defective ABS 65217. RMI now OK. Excluded OMS 1565186 | April | 2018 | 2018Q4 | 2018 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2018-04-14 | N | 222 | N | 19 | N | N | 1.1101 | 39.4971 | 5840.3179
[7 empty] | 7874 | 9647 | 1565276 | 2018-04-14 23:05 | 2018-04-14 23:47 | 42 | 11kV | 37464 | 892 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn3154 St Ives section of Pa12 "Killeaton Warrimoo, etc" fdr tripped on C phase IOC Signals:11kv trip EFI's:nil Abnormal: IR63174 open and LB63181 closed Cause: Tree/Branch on oh mains at AB267 See 1565710 ex 1565276 | April | 2018 | 2018Q4 | 2018 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Veg | 2018-04-14 | N | 42 | N | 19 | N | N | 1.1101 | 39.4971 | 27377.5862
[7 empty] | 7352 | 2966 | 1565193 | 2018-04-14 17:01 | 2018-04-15 00:35 | 454 | 11kV | 6526 | 70 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 186441 1 fault operation 3 phase Overcurrent; Earth Fault CCt LA's blown pole DP-50015. Excluded OMS 1565193 | April | 2018 | 2018Q4 | 2018 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2018-04-14 | N | 93.2286 | N | 19 | N | N | 1.1101 | 39.4971 | 4769.0083
[7 empty] | 8662 | 19651 | 1565213 | 2018-04-14 17:42 | 2018-04-15 00:35 | 413 | 11kV | 181588 | 737 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 186455 3 fault operations 3 phase Removed number of tree branches from 11kV & LV OHMs. LVF 14337 isolated to repairs LV mains brought down in winds by roof in Sunset Bvd pole OR-10085. Excluded OMS 1565213 | April | 2018 | 2018Q4 | 2018 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Veg | 2018-04-14 | N | 246.3881 | N | 19 | N | N | 1.1101 | 39.4971 | 132699.1545
[7 empty] | 8386 | 16066 | 1565292 | 2018-04-15 06:55 | 2018-04-15 09:45 | 170 | 11kV | 170 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 186465 C Phase DOLF : 10 Amp Excluded OMS 1565292 | April | 2018 | 2018Q4 | 2018 | 807:74179 | 807:74179 | ZN00807/074179 | UPPER HUNTER | OH | Veg | 2018-04-15 | N | 170 | N | 10 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 8636 | 19296 | 1565308 | 2018-04-15 09:09 | 2018-04-15 10:05 | 56 | 11kV | 38864 | 694 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 186467 2 fault operations 3 phase Overcurrent System switched abnormal Sw 61185 CLOSED Links 9424 OPEN Branch removed from Fdr near NR-60201 supply back on 1005hrs Excluded OMS 1565308 | April | 2018 | 2018Q4 | 2018 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2018-04-15 | N | 56 | N | 10 | N | N | 1.1101 | 39.4971 | 28400.6649
[7 empty] | 8529 | 17963 | 1566099 | 2018-04-15 08:08 | 2018-04-15 10:36 | 148 | 11kV | 148 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 186466 1 fault operation Overcurrent line patrolled by mine staff, no visible faults | April | 2018 | 2018Q4 | 2018 |  |  |  | SINGLETON | OH | Veg | 2018-04-15 | N | 148 | N | 10 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 7293 | 2042 | 1565297 | 2018-04-15 07:43 | 2018-04-15 12:40 | 297 | 11kV | 297 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 186469 Single phase DOLF : 10 Amp Blown L/A's Excluded OMS 1565297 | April | 2018 | 2018Q4 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2018-04-15 | N | 297 | N | 10 | N | N | 1.1101 | 39.4971 | 217.0388
[7 empty] | 7225 | 831 | 1566113 | 2018-04-15 13:20 | 2018-04-15 15:12 | 112 | 11kV | 112 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 186470 1 fault operation Overcurrent | April | 2018 | 2018Q4 | 2018 |  |  |  | SINGLETON | OH | Veg | 2018-04-15 | N | 112 | N | 10 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 7887 | 9833 | 1565313 | 2018-04-15 09:27 | 2018-04-15 16:00 | 393 | 11kV | 194170 | 951 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Wind Strong | N | LID 186475 A & C Phase Burnt up 11kV links 40604 Excluded oms 1565378 | April | 2018 | 2018Q4 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-04-15 | N | 204.1746 | N | 10 | N | N | 1.1101 | 39.4971 | 141893.709
[7 empty] | 7355 | 2976 | 1565376 | 2018-04-15 10:45 | 2018-04-15 18:10 | 445 | 11kV | 695 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 186479 Repair blown 11kV lead at LF 22512. Excluded OMS 1565376 | April | 2018 | 2018Q4 | 2018 | 242:81533 | 242:81533 | ZN00242/081533 | PORT STEPHENS | OH | Not Veg | 2018-04-15 | N | 115.8333 | N | 10 | N | N | 1.1101 | 39.4971 | 507.8855
[7 empty] | 8614 | 19049 | 1565285 | 2018-04-15 03:09 | 2018-04-15 18:45 | 936 | 11kV | 23814 | 45 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186464 4 fault operations C Phase Earth Fault tree brought down mains adj sub 52791 Excluded OMS 1562585 | April | 2018 | 2018Q4 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2018-04-15 | N | 529.2 | N | 10 | N | N | 1.1101 | 39.4971 | 17402.5688
[7 empty] | 7347 | 2881 | 1565526 | 2018-04-15 15:50 | 2018-04-15 18:55 | 185 | 11kV | 370 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 186478 C Phase DOLF : 10 Amp Excluded OMS 1565526 | April | 2018 | 2018Q4 | 2018 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2018-04-15 | N | 185 | N | 10 | N | N | 1.1101 | 39.4971 | 270.3851
[7 empty] | 8283 | 14767 | 1565562 | 2018-04-15 19:10 | 2018-04-16 01:35 | 385 | 11kV | 103684 | 1075 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | LID 186481 3 fault operations C phase Earth fault, Overcurrent Suspect cable fault between UGOH poles OS-20181 & OS-20183. Section Left isolated. Excluded OMS 1565562 | April | 2018 | 2018Q4 | 2018 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | UG | Not Veg | 2018-04-15 | N | 96.4502 | N | 10 | N | N | 1.1101 | 39.4971 | 75769.209
[7 empty] | 7367 | 3258 | 1565590 | 2018-04-16 00:41 | 2018-04-16 03:12 | 151 | 11kV | 117780 | 780 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At S9550 Gwawley Bay Panel 36 "LB47770 etc" tripped on Relays: E/F(50 TBC) Signals: EFI, 11kv trip Remarks: Animals/birds. Possum on UG/OH adj to PT9692 Ellis St | April | 2018 | 2018Q4 | 2018 | ZN9550:PA36 | ZN9550:PA36 | ZN09550/000036 | SUTHERLAND | OH | Not Veg | 2018-04-16 | N | 151 | N | 5 | N | N | 1.1101 | 39.4971 | 86070.1501
[7 empty] | 8139 | 13055 | 1565597 | 2018-04-16 05:28 | 2018-04-16 13:35 | 487 | 11kV | 2922 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn15010 Careeel Bay Ex Pa28 "Barrenjoey Wahle" CP23616 Beach Barrenjoey tee off 11kv fuse blown 71 amp Cause: not ascertained See 1566385 ex 1565597,722 | April | 2018 | 2018Q4 | 2018 | ZN15010:PA28 | ZN15010:PA28 | ZN15010/000028 | NORTHERN BEACHES | OH | Veg | 2018-04-16 | N | 487 | N | 5 | N | N | 1.1101 | 39.4971 | 2135.3114
[7 empty] | 8585 | 18646 | 1565643 | 2018-04-16 08:58 | 2018-04-16 18:00 | 542 | 11kV | 1028 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | PT9189 Koonya Willarong No.2 -HV Centre phase fuse blown (80A Sieba) 11kV/415V Tx failed @ PT9189. Dist #1 restored via LV // to N/O Dist @ S65384. See 1566037 1566038 | April | 2018 | 2018Q4 | 2018 | ZN9035:PA1 | ZN9035:PA1 | ZN09035/000001 | SUTHERLAND | OH | Not Veg | 2018-04-16 | N | 257 | N | 5 | N | N | 1.1101 | 39.4971 | 751.2321
[7 empty] | 8210 | 13838 | 1566389 | 2018-04-16 18:15 | 2018-04-16 19:44 | 89 | 11kV | 89 | 1 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn15012 Killarney Ex Panel 8 "Forrestville" Section of S17136 SwB to S77260 SwA to LB48934 to S15775 SwA isolated S15775 is in LV// 11kV direct buried UG cable between 11kV UGOH and SwA S77260 has been damaged No1 HVC (stand by supply) interrupted at S15162 MWS & DB Panorama Cr | April | 2018 | 2018Q4 | 2018 |  |  |  |  | UG | Not Veg | 2018-04-16 | N | 89 | N | 5 | N | N | 1.1101 | 39.4971 | 65.0386
[7 empty] | 7252 | 1283 | 1565901 | 2018-04-16 20:34 | 2018-04-16 22:10 | 96 | 11kV | 1056 | 11 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 186495 x-ar failure at pole CN-80623 Archerfield Excluded oms 1565901 | April | 2018 | 2018Q4 | 2018 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Not Veg | 2018-04-16 | N | 96 | N | 5 | N | N | 1.1101 | 39.4971 | 771.6937
[7 empty] | 8540 | 18038 | 1566779 | 2018-04-17 01:31 | 2018-04-17 02:39 | 68 | 11kV | 62134 | 980 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 38 tripped on Signals: 11kV Trip, Tx2 Group Earth Relays: Overcurrent 51N and EFI UG Fault - UG fault between S6290 Kentia Willie and S6516 Kentia Teddick See OMS 1566779 1566780 | April | 2018 | 2018Q4 | 2018 | ZN965:PA38 | ZN965:PA38 | ZN00965/000038 | HORNSBY | UG | Not Veg | 2018-04-17 | N | 63.402 | N | 5 | N | N | 1.1101 | 39.4971 | 45405.6946
[7 empty] | 7665 | 7000 | 1566060 | 2018-04-17 08:42 | 2018-04-17 09:40 | 58 | 11kV | 44256 | 885 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn9900 Menai - Pnl.3 tripped on: Earth leakage Field EFIs: S9141 S9219 Contractor damaged UG cable CNr Carter & Nicholson. Section of feeder from S9219 (Sw/B) to S9293 (Sw/A) See 1566331 1566332 | April | 2018 | 2018Q4 | 2018 | ZN9900:PA3 | ZN9900:PA3 | ZN09900/000003 | SUTHERLAND | UG | Not Veg | 2018-04-17 | N | 50.0068 | N | 5 | N | N | 1.1101 | 39.4971 | 32340.9795
[7 empty] | 8085 | 12258 | 1566142 | 2018-04-17 11:53 | 2018-04-17 12:51 | 58 | 11kV | 7946 | 147 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay - Pnl.27 tripped on: Earth Fault, IOC B phase Field EFIs: S910 S9618 S9330 S9272 S9641 UG cable fault from S9641 (Sw/A) and S9419 (Sw/B) See 1566359 1566360 | April | 2018 | 2018Q4 | 2018 | ZN9550:PA27 | ZN9550:PA27 | ZN09550/000027 | SUTHERLAND | UG | Not Veg | 2018-04-17 | N | 54.0544 | N | 5 | N | N | 1.1101 | 39.4971 | 5806.7024
[7 empty] | 8240 | 14349 | 1566217 | 2018-04-17 15:15 | 2018-04-17 17:25 | 130 | 11kV | 6500 | 50 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 186502 Sub interrupted to make repairs to x arm pole JU-10239 Excluded oms 1566217 | April | 2018 | 2018Q4 | 2018 | 210:83474 | 210:83474 | ZN00210/083474 | NEWCASTLE | OH | Not Veg | 2018-04-17 | N | 130 | N | 5 | N | N | 1.1101 | 39.4971 | 4750.0083
[7 empty] | 7742 | 7911 | 1566258 | 2018-04-17 18:42 | 2018-04-17 22:05 | 203 | 11kV | 406 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186507 A Phase DOLF : 10 Amp Blown DOLF Excluded OMS 1566258 | April | 2018 | 2018Q4 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2018-04-17 | N | 203 | N | 5 | N | N | 1.1101 | 39.4971 | 296.6928
[7 empty] | 7964 | 10528 | 1566269 | 2018-04-18 02:26 | 2018-04-18 04:14 | 108 | 11kV | 86184 | 798 | HV | Animal Flying Fox | Animal | UGOH | Unplanned | No Weather Impact | N | Zn10998 Rockdale - pnl.25 tripped on: B & C phase IOC Bat on UGOH phase to earth (UGOH above S47040) | April | 2018 | 2018Q4 | 2018 | ZN10998:PA25 | ZN10998:PA25 | ZN10998/000025 | BAYSIDE | OH | Not Veg | 2018-04-18 | N | 108 | N | 3 | N | N | 1.1101 | 39.4971 | 62980.7252
[7 empty] | 7934 | 10259 | 1566272 | 2018-04-18 05:44 | 2018-04-18 07:33 | 109 | 11kV | 174411 | 1742 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | At S15011 Beacon Hill Panel 2 tripped, reclosed tripped and locked out on Relays: A protection - A B and C EF trip, A B and C phase IOC LH Protection - A B and C and EF OC, IOC, Reclose Timer and Lockout Signals: 11kV Trip, Zone Earth At S16011 Alambie Rd 252 RMI failed. See OMS 1566564 1566565 1566278 1566272 | April | 2018 | 2018Q4 | 2018 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | UG | Not Veg | 2018-04-18 | N | 100.1211 | N | 3 | N | N | 1.1101 | 39.4971 | 127454.4145
[7 empty] | 8483 | 17424 | 1566545 | 2018-04-18 22:08 | 2018-04-18 23:38 | 90 | 11kV | 37923 | 427 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | ON Panel 39 "North Avoca" at S12570 Avoca Rec44855 Lake Tramway tripped on E/F & L/O Remarks: cause not ascertained. Dop patrolled extent of feeder, no cause found | April | 2018 | 2018Q4 | 2018 | ZN12570:PA39 | ZN12570:PA39 | ZN12570/000039 | CENTRAL COAST | OH | Veg | 2018-04-18 | N | 88.8126 | N | 3 | N | N | 1.1101 | 39.4971 | 27713.0099
[7 empty] | 7227 | 855 | 1566693 | 2018-04-19 17:55 | 2018-04-19 18:33 | 38 | 11kV | 15694 | 413 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186537 2 Fault operations, Phases A & C, Overcurrent | April | 2018 | 2018Q4 | 2018 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2018-04-19 | N | 38 | N | 6 | N | N | 1.1101 | 39.4971 | 11468.7123
[7 empty] | 8333 | 15284 | 1566717 | 2018-04-19 18:43 | 2018-04-19 20:25 | 102 | 11kV | 102 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186567 A Phase, 16Amp fuse Line DOLF | April | 2018 | 2018Q4 | 2018 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2018-04-19 | N | 102 | N | 6 | N | N | 1.1101 | 39.4971 | 74.5386
[7 empty] | 7532 | 5674 | 1566685 | 2018-04-19 17:16 | 2018-04-19 22:45 | 329 | 11kV | 225285 | 1209 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 186570 wire down at pole SW30281 CB 33596 tripping free suggest fault overhaul AP left. dq Excluded oms 1566685 | April | 2018 | 2018Q4 | 2018 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2018-04-19 | N | 186.34 | N | 6 | N | N | 1.1101 | 39.4971 | 164631.6332
[7 empty] | 7975 | 10680 | 1566729 | 2018-04-19 19:25 | 2018-04-19 22:45 | 200 | 11kV | 1800 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 186571 Phase B 16 Amp fuse Substation dolf | April | 2018 | 2018Q4 | 2018 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Veg | 2018-04-19 | N | 200 | N | 6 | N | N | 1.1101 | 39.4971 | 1315.3869
[7 empty] | 8663 | 19655 | 1566713 | 2018-04-19 18:31 | 2018-04-19 23:59 | 328 | 11kV | 20664 | 63 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 186577 A Phase DOLF : 40 Amp suspect defective tx or arrestor fuse failed on try back. dq | April | 2018 | 2018Q4 | 2018 | 261:81876 | 261:81876 | ZN00261/081876 | NEWCASTLE | OH | Not Veg | 2018-04-19 | N | 328 | N | 6 | N | N | 1.1101 | 39.4971 | 15100.6417
[7 empty] | 7992 | 10927 | 1566764 | 2018-04-19 23:36 | 2018-04-20 00:22 | 46 | 11kV | 29256 | 636 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | At S9550 Gwawley Bay 11kv Panel No.9 "S9370 Port Hacking Box No.3" feeder tripped on Relays: E/F, EFI Signals: 11kv trip Remarks: animals/birds. Possum caused flash over on UGOH at PT9745 Shirley Gwawley, mains to inspect in daylight hours | April | 2018 | 2018Q4 | 2018 | ZN9550:PA9 | ZN9550:PA9 | ZN09550/000009 | SUTHERLAND | OH | Not Veg | 2018-04-19 | N | 46 | N | 6 | N | N | 1.1101 | 39.4971 | 21379.4219
[7 empty] | 8215 | 13883 | 1566822 | 2018-04-20 11:40 | 2018-04-20 17:56 | 376 | 11kV | 752 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 186589 Substation DOLF, Sub isolated for repairs FOUND 2 BLOWN HV DOF AT TX 20601. TRYBACK FAILED. PROBABLE BLOWN HV ARRESTOR. OPENED AND REMOVED LV TX FUSES AND OPENED AND REMOVED HV TX FUSES AND APPLIED WARNING TAG ON POLE. DIFFICULT IF NOT IMPOSSIBLE TOWER ACCESS ON ACCESS TRACK ON SCHOOL DRIVE.BUT TOWER COULD ACCESS THROUGH ALCAN SITE AFTER CHECKING IN WITH SECURITY AT FRONT GATE. OTHERWISE COULD BE DONE OFF LADDERS. TX FEEDS POLLUTION MONITORING STATION FOR ALCAN SMELTER. (HV FUSES RELOADED WITH 10 AMP FUSES.) | April | 2018 | 2018Q4 | 2018 | 265:81649 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Not Veg | 2018-04-20 | N | 376 | N | 4 | N | N | 1.1101 | 39.4971 | 549.5394
[7 empty] | 8538 | 18029 | 1566891 | 2018-04-20 17:51 | 2018-04-20 19:10 | 79 | 11kV | 632 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge ex Panel 8 PT18718 Williams George 0.9 has a blown roadside HDO fuse NK-10A Cause: fuse fatigue. Dop reports fuse very old See 1567130 ex 1566891,3 | April | 2018 | 2018Q4 | 2018 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2018-04-20 | N | 79 | N | 4 | N | N | 1.1101 | 39.4971 | 461.847
[7 empty] | 7269 | 1622 | 1566901 | 2018-04-20 18:32 | 2018-04-20 19:14 | 42 | 11kV | 50652 | 1206 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At ZN15001 Brookvale 11kV panel 6L tripped on O/C + E/F, EFI, Trip, IOC Frame Leakage Fault Check Cause: Possum found at base of 11kV UGOH below SW/B @ S16933 | April | 2018 | 2018Q4 | 2018 | ZN15001:PA6 | ZN15001:PA6 | ZN15001/000006 | NORTHERN BEACHES | OH | Not Veg | 2018-04-20 | N | 42 | N | 4 | N | N | 1.1101 | 39.4971 | 37014.9876
[7 empty] | 8246 | 14389 | 1566909 | 2018-04-20 19:22 | 2018-04-20 20:55 | 93 | 11kV | 47709 | 513 | HV | Animal Flying Fox | Animal | UGOH | Unplanned | No Weather Impact | N | IR63275 Washington Lincoln Ex S9252 Janalli Panel 24 "Victoria Alice, etc" tripped reclosed, tripped and locked out Remarks: Animals/birds. Dead bat found near UGOH to S9547 CC1: 22-"Refer to SOp" | April | 2018 | 2018Q4 | 2018 | ZN9252:PA24 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Not Veg | 2018-04-20 | N | 93 | N | 4 | N | N | 1.1101 | 39.4971 | 34864.33
[7 empty] | 7538 | 5724 | 1566921 | 2018-04-21 00:10 | 2018-04-21 01:03 | 53 | 11kV | 14628 | 276 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186592 A phase blown termination at HW-80083 Section isolated for repairs subs 4856, 27474, 21103 off 0010hrs supply back on 0103hrs Broken deadend on HV, Footpath side. HV main hanging by tapping only. Urgent attention required. | April | 2018 | 2018Q4 | 2018 | 243:80078 | 243:80078 | ZN00243/080078 | LAKE MACQUARIE | OH | Not Veg | 2018-04-21 | N | 53 | N | 2 | N | N | 1.1101 | 39.4971 | 10689.7109
[7 empty] | 7466 | 4959 | 1567000 | 2018-04-21 13:02 | 2018-04-21 15:30 | 148 | 11kV | 1184 | 8 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge section of Pa11 PT13257 Silvester Anembo 11kv 16Amp footpath phase HDO blown. Suspect due to previous ightning strike. Also blown arrestors at PT13257 See 1567132 ex 1567000,9 | April | 2018 | 2018Q4 | 2018 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2018-04-21 | N | 148 | N | 2 | N | N | 1.1101 | 39.4971 | 865.2323
[7 empty] | 7669 | 7018 | 1567059 | 2018-04-22 11:06 | 2018-04-22 12:20 | 74 | 11kV | 592 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14891 Wyong Ex Panel 5 "Wyong" PT13502 Moores Dooralong 0.8 16Amp HV Drop out fuse replaced (footpath pahse) Customers installation service wire to 1575 Mandalong RD Dooralong See 1567135 ex 1567059,61,62 | April | 2018 | 2018Q4 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2018-04-22 | N | 74 | N | 1 | N | N | 1.1101 | 39.4971 | 432.6161
[7 empty] | 8310 | 15094 | 1567104 | 2018-04-23 00:28 | 2018-04-23 02:40 | 132 | 11kV | 93627 | 892 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S 3154 St Ives Panel; 12 tripped and reclosed on Relays: A Phase IOC and Timed OC/EF/LOCKOUT, timing EFI Abnormal Switching: CP63181 Closed, Recloser 63174 Open Cause: Vehicle hit pole MC07595 between CP1663 - AB1855 tee S2171 See OMS 1567232 1567234 1567235 1567105 1567104 1567106 | April | 2018 | 2018Q4 | 2018 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Veg | 2018-04-23 | N | 104.963 | N | 2 | N | N | 1.1101 | 39.4971 | 68419.8501
[7 empty] | 8589 | 18684 | 1567347 | 2018-04-23 17:35 | 2018-04-23 20:05 | 150 | 11kV | 104376 | 855 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @S9252 Jannali Panel 21 'S9014 Roberts Box' fdr tripped on Relays: O/C, A & B trip phase, reclose, lockout Signals: 11kv trip Remarks: cause not ascertained. Patrolled | April | 2018 | 2018Q4 | 2018 | ZN9252:PA21 | ZN9252:PA21 | ZN09252/000021 | SUTHERLAND | OH | Veg | 2018-04-23 | N | 122.0772 | N | 2 | N | N | 1.1101 | 39.4971 | 76274.9022
[7 empty] | 7737 | 7875 | 1567370 | 2018-04-24 00:27 | 2018-04-24 02:59 | 152 | 11kV | 267802 | 2081 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @S3472 Sefton Zn Panel #22 labelled Virgil av tripped on A phase overcurrent 11kv trip Abnormal: LB2105 closed with Sw/A open at S7472 Miller Christina (leightfield Sht 1 F1) Remarks: mains to patrol. Note LV network damaged due to LV// in cnr virgil ave and Grevillea st bay of Lv cut away. LV network in vicinity grevilea annealed and hanging low need urgent mains attention AM tuesday | April | 2018 | 2018Q4 | 2018 | ZN1290:PA9 | ZN1290:PA3 | ZN01290/000003 | CANTERBURY-BANKSTOWN | OH | Veg | 2018-04-24 | N | 128.6891 | N | 1 | N | N | 1.1101 | 39.4971 | 195701.8028
[7 empty] | 8315 | 15142 | 1567539 | 2018-04-25 03:00 | 2018-04-25 06:50 | 230 | 11kV | 1150 | 5 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 186615 Car brought pole HW-30046 down SW 19360 T & R EARLIER SEE REPORT186609/OMS 1567696 SECTION ISOLATED LATER | April | 2018 | 2018Q4 | 2018 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2018-04-25 | N | 230 | N | 3 | N | N | 1.1101 | 39.4971 | 840.3861
[7 empty] | 7867 | 9512 | 1567546 | 2018-04-25 04:21 | 2018-04-25 08:05 | 223.7 | 11kV | 19685.6 | 88 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 186610 B Phase DOLF : 31 Amp live possum on 11kv arrestor. Excluded oms report 1567552, 1567554, 1567553. | April | 2018 | 2018Q4 | 2018 | 205:12213 | 205:12213 | ZN00205/012213 | LAKE MACQUARIE | OH | Not Veg | 2018-04-25 | N | 223.7 | N | 3 | N | N | 1.1101 | 39.4971 | 14385.6559
[7 empty] | 8207 | 13818 | 1567548 | 2018-04-25 05:35 | 2018-04-25 10:10 | 275 | 11kV | 825 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 186612 Single phase DOLF : 10 Amp DOLF did not operate. Base broke. Excluded OMS 1567548 | April | 2018 | 2018Q4 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2018-04-25 | N | 275 | N | 3 | N | N | 1.1101 | 39.4971 | 602.8857
[7 empty] | 7364 | 3147 | 1567640 | 2018-04-26 04:27 | 2018-04-26 06:26 | 119 | 11kV | 142660 | 1367 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S2196 Milperra - 11kv Panel 18 "Lachlan Cant" tripped on: Relays: Basler (50T ABC) instant OC ABC phase EFI Signals: 11kv trip, zone earth, Tx2 group earth Efis: S4860, all following electronic EFIs did not flag Remarks: cause not ascertained | April | 2018 | 2018Q4 | 2018 | ZN2196:PA18 | ZN2196:PA18 | ZN02196/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2018-04-26 | N | 104.3599 | N | 5 | N | N | 1.1101 | 39.4971 | 104251.7202
[7 empty] | 7381 | 3612 | 1567656 | 2018-04-26 08:47 | 2018-04-26 11:05 | 138 | 11kV | 276 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At S12630 Peats Ridge Zn section of P3 from Ironbark Kirks 2.4 - PT47654 footpath phase 10a hdo Remarks: fuse fatigue | April | 2018 | 2018Q4 | 2018 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2018-04-26 | N | 138 | N | 5 | N | N | 1.1101 | 39.4971 | 201.6927
[7 empty] | 7746 | 8001 | 1567709 | 2018-04-26 11:46 | 2018-04-26 12:20 | 34 | 11kV | 28504 | 851 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12570 Avoca Zn P34 the terriagal fdr tripped reclosed and locked out on a/b ioc relay, reclose lockout Remarks: tree/branch on OH mains. Near tee off to PT12363 removed by Dop | April | 2018 | 2018Q4 | 2018 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2018-04-26 | N | 33.4947 | N | 5 | N | N | 1.1101 | 39.4971 | 20829.8825
[7 empty] | 8401 | 16333 | 1567780 | 2018-04-26 01:30 | 2018-04-26 16:40 | 910 | 11kV | 463230 | 873 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn10990 Arncliffe, Panel 12 'Wickham St' feeder between sw/B @ S10718 Argyle Princes No.2 to Sw/B @ S10147 Princes Brodie Spark to S65351 Innesdale Robert was isolated to effect repair. Abnormal: At Rockdale Sht 2, AB31268 to AB 31269 to Sw/A @ S49857 tee PT10536 is OOS defective with Sw/A @ S64835 closed. At Arncliffe at S10147 Sw/A was closed with Sw/B open (switched prior to interruption) Remarks: OH resting on cross arm. Emergency repairs due to middle bare hv mains resting on roadside insulator. Corner of Gertrude and Princes Highway Wolli Creek | April | 2018 | 2018Q4 | 2018 | ZN10990:PA12 | ZN10998:PA9 | ZN10998/000009 | BAYSIDE | OH | Not Veg | 2018-04-26 | N | 530.6186 | N | 5 | N | N | 1.1101 | 39.4971 | 338514.821
[7 empty] | 8620 | 19116 | 1567841 | 2018-04-26 19:39 | 2018-04-26 20:25 | 46 | 11kV | 28130 | 1130 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ZN1287 Revesby Panel 5 'Davis banks' fdr tripped and reclosed Relay: A & C phase O/C Signal: 11kv trip Remarks: after HV feeder tripped off and reclosed dop found bond off at pole 21909 in Alma Rd opposite Yates Cres. Mains to patrol after feeder trip and reclose | April | 2018 | 2018Q4 | 2018 | ZN1287:PA5 | ZN1287:PA5 | ZN01287/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-04-26 | N | 24.8938 | N | 5 | N | N | 1.1101 | 39.4971 | 20556.5743
[7 empty] | 7734 | 7836 | 1567873 | 2018-04-27 04:24 | 2018-04-27 05:15 | 50.9333 | 11kV | 5348 | 105 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | No Weather Impact | N | At PT48429 Springfield Dolly 50amp footpath phase HDO blown Remarks: cause not ascertained | April | 2018 | 2018Q4 | 2018 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2018-04-27 | N | 50.9333 | N | 3 | N | N | 1.1101 | 39.4971 | 3908.1607
[7 empty] | 7580 | 6111 | 1568015 | 2018-04-27 15:50 | 2018-04-28 01:05 | 555 | 11kV | 2220 | 4 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 186632 Feeder isolated for urgent pole replacement of sub pole HR-95406. | April | 2018 | 2018Q4 | 2018 | 532:83307 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Not Veg | 2018-04-27 | N | 555 | N | 3 | N | N | 1.1101 | 39.4971 | 1622.3105
[7 empty] | 8551 | 18220 | 1568070 | 2018-04-27 23:48 | 2018-04-28 01:10 | 82 | 11kV | 88888 | 1084 | HV | Animal Bird | Animal | UGOH | Unplanned | Rain Heavy | N | Zn14891 Wyong Pa10 "Wyongah" fdr tripped and reclosed and tripped on Singals: 11kv trip, Tx1, Group Earth, AR Lockout Relays: Earth Fault, O/C ABC 50T, Timing, Lockout, Fault CHeck EFI's: Pa10 S14857 Cause: Animals/Birds. Possum on first UGOH past S14857 Pacific Masonic | April | 2018 | 2018Q4 | 2018 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Not Veg | 2018-04-27 | N | 82 | N | 3 | N | N | 1.1101 | 39.4971 | 64956.7286
[7 empty] | 8705 | 20130 | 1568073 | 2018-04-28 00:26 | 2018-04-28 01:40 | 74 | 11kV | 54760 | 740 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN195 Pymble ex panel 30 - CP46113 Fiddens Wharf Coronga tripped and reclosed on Relays: IOC trip, OC trip, Lockout Cause: Branch across 11kV conductors near AB2303 See OMS 1568073 1568074 | April | 2018 | 2018Q4 | 2018 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2018-04-28 | N | 74 | N | 5 | N | N | 1.1101 | 39.4971 | 40016.9929
[7 empty] | 7717 | 7663 | 1568077 | 2018-04-28 01:28 | 2018-04-28 02:59 | 91 | 11kV | 68783 | 836 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Zn14144 Wamberal Pa4L "Wamberal Aux" fdr tripped and reclosed and tripped on Singals: 11kv trip (415 aux supply alarms) Relays: A & B ph IOC EFI's: Pa4 Cause: tree branch on OH mains on conductors at LB40403 See 1568400,1 ex 1568077 | April | 2018 | 2018Q4 | 2018 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2018-04-28 | N | 82.2763 | N | 5 | N | N | 1.1101 | 39.4971 | 50264.5876
[7 empty] | 8252 | 14439 | 1568096 | 2018-04-28 06:00 | 2018-04-28 07:46 | 106 | 11kV | 79740 | 778 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36100 Rose Bay Zn - Pnl.8 tripped on : O/C and E/F with EFI. UG cable fault between S8611 (Sw/B) and S78659 9Sw/B) and S2710 (Sw/A) See 1568325 1568326 | April | 2018 | 2018Q4 | 2018 | ZN36100:PA8 | ZN36100:PA8 | ZN36100/000008 | WOOLLAHRA | UG | Not Veg | 2018-04-28 | N | 102.4936 | N | 5 | N | N | 1.1101 | 39.4971 | 58271.6401
[7 empty] | 8054 | 11848 | 1568124 | 2018-04-28 08:55 | 2018-04-28 09:12 | 17 | 11kV | 1224 | 72 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | LID 186635 Sub isolated to safely remove traped truck driver. LV access to kiosk was blocked. | April | 2018 | 2018Q4 | 2018 | 221:11894 | 221:11894 | ZN00221/011894 | LAKE MACQUARIE | OH | Not Veg | 2018-04-28 | N | 17 | N | 5 | N | N | 1.1101 | 39.4971 | 894.4631
[7 empty] | 8134 | 12999 | 1568088 | 2018-04-28 05:08 | 2018-04-28 20:20 | 912 | 11kV | 133431 | 2131 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Heavy | N | At Zn965 Pennant Hill panel 4 tripped, reclosed , tripped and locked out on Signals: 11kV trip, TX1 Group Earth, Zone Earth Relays: O/C, E/F and EFI Cause: fire at S7291 Wilkinson Pykett At S965 Pennant Hills - Panel 46 tripped on Signals: 11kV Trip, TX1 Group Earth, Zone Earth EFI's - All operated. See OMS 1568366/367/368/532/533 1568088 1568089 1568090 1568092 1568094 | April | 2018 | 2018Q4 | 2018 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | UG | Not Veg | 2018-04-28 | N | 62.6143 | N | 5 | N | N | 1.1101 | 39.4971 | 97507.4393
[7 empty] | 8091 | 12297 | 1568208 | 2018-04-29 08:48 | 2018-04-29 11:40 | 172 | 11kV | 1204 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186639 B & C Phase DOLF : 20 Amp Excluded OMS 1568208 | April | 2018 | 2018Q4 | 2018 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2018-04-29 | N | 172 | N | 3 | N | N | 1.1101 | 39.4971 | 879.8477
[7 empty] | 8443 | 16853 | 1568287 | 2018-04-29 22:17 | 2018-04-30 03:15 | 297.9667 | 11kV | 251185.9 | 843 | HV | Equipment Failed in Service | Equipment Failure | Busbar | Unplanned | Rain Heavy | N | S315 Plumber Rd - Tx 2 & Tx 3 tripped due to LV busbar fault. Water leaked through roof at S315 onto LV busbar. | April | 2018 | 2018Q4 | 2018 | ZN3155:PA23 | ZN3155:PA40 | ZN03155/000040 | WOOLLAHRA | Unknown | Not Veg | 2018-04-29 | N | 297.9667 | N | 3 | N | N | 1.1101 | 39.4971 | 183559.247
[7 empty] | 8148 | 13163 | 1568197 | 2018-04-29 06:43 | 2018-04-30 09:00 | 1577 | 11kV | 5513 | 83 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Panel 8 fdr tripped, reclosed and locked out Relays: Pa8, Earth Fault, EFI, reclose, timing & lockout relays, Fault check relay The No.1 Tx B Protection Panel - Earth fault check Signals: 11kv trip, No1 Group Earth EFI: S18058 Abnormal: AB44857 open (DMA) with LB41171 closed Cause: UG fault from S18058 O'Hart Pacific to AB44857 to S14107. S14107 was fed via generator, changeover supply at 0900. See 1568675,6 ex 1568197,201 | April | 2018 | 2018Q4 | 2018 | ZN14892:PA8 | ZN14892:PA8 | ZN14892/000008 | CENTRAL COAST | UG | Not Veg | 2018-04-29 | N | 66.4217 | N | 3 | N | N | 1.1101 | 39.4971 | 4028.7378
[7 empty] | 7927 | 10199 | 1568545 | 2018-04-30 15:06 | 2018-04-30 18:05 | 179 | 11kV | 16560 | 196 | HV | Equipment Failed in Service | Equipment Failure | Tap Changer | Unplanned | No Weather Impact | N | LID 186656 4 fault operation Earth Fault Faulty regulator 72824 Sw 64057 tripped simultaneous with 74147 Excluded OMS 1568545 | April | 2018 | 2018Q4 | 2018 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | Unknown | Not Veg | 2018-04-30 | N | 84.4898 | N | 2 | N | N | 1.1101 | 39.4971 | 12101.5596
[7 empty] | 8093 | 12331 | 1568582 | 2018-04-30 17:33 | 2018-04-30 19:24 | 111 | 11kV | 78105 | 721 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ex Zn3425 Castlle Cove Panel 28 Fault 1 - Recloser 49995 Holly Kendall tripped on OC and IOC - suspect UG cable fault between S1723 and LB62055 Fault 2 - @ AB3229 Roadside bond blown off See OMS 1568636 1568582 1568585 | April | 2018 | 2018Q4 | 2018 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | UG | Not Veg | 2018-04-30 | N | 108.3287 | N | 2 | N | N | 1.1101 | 39.4971 | 57076.8303
[7 empty] | 8712 | 20256 | 1568755 | 2018-05-01 15:56 | 2018-05-01 16:35 | 39 | 11kV | 1911 | 49 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186669 C Phase DOLF : 31 Amp replaced c phase dolf Excluded oms 1568755 | May | 2018 | 2018Q4 | 2018 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Veg | 2018-05-01 | N | 39 | N | 2 | N | N | 1.1101 | 39.4971 | 1396.5024
[7 empty] | 7568 | 6009 | 1568692 | 2018-05-01 12:32 | 2018-05-01 18:57 | 385 | 11kV | 385 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 186671 Faulty Transformer Excluded OMS 1568692 | May | 2018 | 2018Q4 | 2018 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2018-05-01 | N | 385 | N | 2 | N | N | 1.1101 | 39.4971 | 281.3466
[7 empty] | 8457 | 17085 | 1568889 | 2018-05-02 10:18 | 2018-05-02 12:11 | 113 | 11kV | 85957 | 827 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186675 2 fault operation A & C Phase Overcurrent Exccluded OMS 1568889 | May | 2018 | 2018Q4 | 2018 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2018-05-02 | N | 103.9383 | N | 3 | N | N | 1.1101 | 39.4971 | 62814.8403
[7 empty] | 7298 | 2103 | 1569027 | 2018-05-02 21:14 | 2018-05-02 22:20 | 66 | 11kV | 4620 | 70 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT47322 Buffalo providence footpath side HV dropout fuse broken Cause: Footpath side HV DOP broken See OMS 1569634 1569030 1569029 | May | 2018 | 2018Q4 | 2018 | ZN35500:PA28 | ZN35500:PA36 | ZN35500/000036 | RYDE | OH | Not Veg | 2018-05-02 | N | 66 | N | 3 | N | N | 1.1101 | 39.4971 | 3376.1597
[7 empty] | 8293 | 14909 | 1569034 | 2018-05-02 22:57 | 2018-05-03 08:05 | 548 | 11kV | 104818 | 881 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Remarks: bond. S2196 Milperra 11kv panel No.5 "S8696 Marigold Armour No4" feeder, 11kv bond off @ AB36, footpath side (on load side) | May | 2018 | 2018Q4 | 2018 | ZN2196:PA5 | ZN2196:PA3 | ZN02196/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-05-02 | N | 118.9762 | N | 3 | N | N | 1.1101 | 39.4971 | 76597.9028
[7 empty] | 7527 | 5612 | 1569114 | 2018-05-03 14:40 | 2018-05-03 19:10 | 270 | 11kV | 24150 | 112 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186699 3 Fault operations Overcurrent, Sensitive Earth Fault tree pushed over by someone at HS-92079. mains clear of tree when dops arrived Excluded oms 1569114 | May | 2018 | 2018Q4 | 2018 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2018-05-03 | N | 215.625 | N | 2 | N | N | 1.1101 | 39.4971 | 17648.1077
[7 empty] | 8241 | 14350 | 1569158 | 2018-05-03 20:23 | 2018-05-03 20:50 | 27 | 11kV | 891 | 33 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186700 C Phase DOLF : 40 Amp Excluded OMS 1569165 | May | 2018 | 2018Q4 | 2018 | 270:83590 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | OH | Veg | 2018-05-03 | N | 27 | N | 2 | N | N | 1.1101 | 39.4971 | 651.1165
[7 empty] | 7694 | 7288 | 1569329 | 2018-05-04 13:53 | 2018-05-04 15:09 | 76 | 11kV | 2144 | 29 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2466 Flemington Panel No.29 "Birnie Par No.2" opened on earth fault, fault check relay & EFI Zone earth, No.3 Group earth, 11kv trip EFIs operated @ S6456 Abnormal: S8125 Birnie Par No.3 to S61885 Birnie Par No.4 defective. N/O sw/A @ S7407 HVC diary farmers No.2 close, N/O sw/A @ S65220 Birnie Bachell No.5 closed, Sw/B @ Birnie Pippita open Remarks: UG fault. Sub 6456 to S7407 | May | 2018 | 2018Q4 | 2018 | ZN2466:PA32 | ZN2466:PA6 | ZN02466/000006 | CUMBERLAND | UG | Not Veg | 2018-05-04 | N | 73.931 | N | 3 | N | N | 1.1101 | 39.4971 | 1566.772
[7 empty] | 8701 | 20109 | 1569420 | 2018-05-04 16:48 | 2018-05-04 18:35 | 107 | 11kV | 214 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 186714 A Phase DOLF : 10 Amp Excluded oms 1569420 | May | 2018 | 2018Q4 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-05-04 | N | 107 | N | 3 | N | N | 1.1101 | 39.4971 | 156.3849
[7 empty] | 8681 | 19794 | 1569384 | 2018-05-04 15:44 | 2018-05-04 20:30 | 286 | 11kV | 218166 | 1229 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S2400 Berowra Panel 15 Kauri Bambil tripped and reclosed on Relays: Earth Fault, Fault Check, EFI Signals: 11kV Trip Cause: OH Down - S2400 Berowra Ex Panel 15 Kauri Bambil live line connector failed adjacent to PT2190 Janita Stonehaven. The connector fell into the adjacent LV distributor neutral See OMS 1569733 1569734 1569738 1569737 See OMS 1569385 1569439 | May | 2018 | 2018Q4 | 2018 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Not Veg | 2018-05-04 | N | 177.5151 | N | 3 | N | N | 1.1101 | 39.4971 | 159429.278
[7 empty] | 8434 | 16752 | 1569454 | 2018-05-05 06:41 | 2018-05-05 06:48 | 7 | 11kV | 4319 | 617 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn12600 Lisarow Pa1 "Dog Trap Gully" fdr tripped Relays: 50T, Instantaneous Overcurrent A,B&C, Lockout, Timing Signals: 11kv trip Cause: Animals Bird Dead Possum found at base UGOH pole | May | 2018 | 2018Q4 | 2018 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Not Veg | 2018-05-05 | N | 7 | N | 5 | N | N | 1.1101 | 39.4971 | 3156.1978
[7 empty] | 8130 | 12982 | 1569480 | 2018-05-05 10:05 | 2018-05-05 10:51 | 46 | 11kV | 26056 | 579 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186717 2 fault operations 3 phase Overcurrent Dead Crow confirmed within private network beyond Primo RAGCB 11974. Sw 89055 Scone sub: A/B/Cph OC (Fault Current A:3850A, B:4136A, C:3024A) Sw 11974 Prim RAGCB: A/B/Cph OC (Counter 242) Excluded OMS No. 1569480+1569481 | May | 2018 | 2018Q4 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2018-05-05 | N | 45.0017 | N | 5 | N | N | 1.1101 | 39.4971 | 19040.9563
[7 empty] | 7288 | 1995 | 1569473 | 2018-05-05 09:34 | 2018-05-05 11:50 | 136 | 11kV | 2720 | 20 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa26 S14126 Peppers Kurrawyba 11kv/415V Tx2 tripped on Buchholz Oil leaking slowly form tap changer of Tx2. Low oil on transformer See 1569933 ex 1569473 | May | 2018 | 2018Q4 | 2018 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | UG | Not Veg | 2018-05-05 | N | 136 | N | 5 | N | N | 1.1101 | 39.4971 | 1987.6958
[7 empty] | 7200 | 458 | 1569495 | 2018-05-05 12:13 | 2018-05-05 14:20 | 127 | 11kV | 635 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186718 Reattach LL Clamp lead that came loose. Excluded OMS No. 1569495 | May | 2018 | 2018Q4 | 2018 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2018-05-05 | N | 127 | N | 5 | N | N | 1.1101 | 39.4971 | 464.0393
[7 empty] | 7409 | 3944 | 1569520 | 2018-05-05 18:00 | 2018-05-05 18:28 | 28 | 11kV | 140 | 5 | HV | Vandalism | 3rd Party Impact | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of pa5 PT12663 Dickson Bloomfield interrupted for safety to replace stolen copper earthing on the PT See 1569934 ex 1569520 | May | 2018 | 2018Q4 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | Unknown | Not Veg | 2018-05-05 | N | 28 | N | 5 | N | N | 1.1101 | 39.4971 | 102.3079
[7 empty] | 8174 | 13436 | 1569551 | 2018-05-06 10:13 | 2018-05-06 11:50 | 97 | 11kV | 2328 | 24 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn14144 Wamberal section of Pa5 PT13421 Serpentine Terrigal 0.4 11kv 31.5A HDO footpath side HV Fuse operated Tree branch contact on HV bushings on transformer. Transformer shrouds are burnt and require replacing See 1570262 ex 1569548 1569551 | May | 2018 | 2018Q4 | 2018 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2018-05-06 | N | 97 | N | 1 | N | N | 1.1101 | 39.4971 | 1701.2337
[7 empty] | 8107 | 12583 | 1569606 | 2018-05-07 00:25 | 2018-05-07 01:45 | 80 | 11kV | 98800 | 1235 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9700 Kirrawee - Pnl.15 tripped, reclosed, tripped & locked out on: Earth Fault Field EFIs: S9783 S9154 S9156 Possum on UGOH beyond tee to S9156 and S9921 (POLE SU-12708). Possum removed by DOp, burn marks on UGOH to be inspected in daylight. | May | 2018 | 2018Q4 | 2018 | ZN9700:PA15 | ZN9700:PA15 | ZN09700/000015 | SUTHERLAND | OH | Not Veg | 2018-05-07 | N | 80 | N | 1 | N | N | 1.1101 | 39.4971 | 72200.1259
[7 empty] | 8414 | 16519 | 1569857 | 2018-05-08 02:45 | 2018-05-08 04:03 | 78 | 11kV | 95784 | 1228 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S1287 revesby Panel 17 "Hinemoa St" tripped on Relays: C phase IOC, reclose and lockout Signals: 11kv trip Field EFI's: none Remarks: cause not ascertained CC1: 22-"Refer to SOp" | May | 2018 | 2018Q4 | 2018 | ZN1287:PA17 | ZN1287:PA17 | ZN01287/000017 | CANTERBURY-BANKSTOWN | OH | Veg | 2018-05-08 | N | 78 | N | 5 | N | N | 1.1101 | 39.4971 | 69996.1221
[7 empty] | 7772 | 8365 | 1569877 | 2018-05-08 07:13 | 2018-05-08 07:40 | 27 | 11kV | 4077 | 151 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | ZS STS Secondary Equip | Unplanned | No Weather Impact | N | Zn10998 Rockdale - Pnl.24 tripped on: Low Set EF Abnormal: Pnl.24 (Normally open) was closed with S10646 (Sw/A) open Protection malfunction: While switching across Pnl.24 Rockdale and Pnl.38L Kogarah, N/O pnl.24 was closed. When DOp opened S10646 (Sw/A), Pnl.24 tripped. All SEL and Rec was Non Auto during switching. PE to investigate. | May | 2018 | 2018Q4 | 2018 | ZN10999:PA38 | ZN10998:PA24 | ZN10998/000024 | BAYSIDE | Exclude | Not Veg | 2018-05-08 | N | 27 | N | 5 | N | N | 1.1101 | 39.4971 | 2979.3513
[7 empty] | 7750 | 8055 | 1569871 | 2018-05-08 06:51 | 2018-05-08 07:50 | 58.7667 | 11kV | 4583.8 | 78 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At PT1506 Watt Pratten 400A fuse blown on B phase of distributor 1. Cause: Vehicle Hit pole | May | 2018 | 2018Q4 | 2018 | ZN35500:PA24 | ZN35500:PA24 | ZN35500/000024 | RYDE | OH | Not Veg | 2018-05-08 | N | 58.7667 | N | 5 | N | N | 1.1101 | 39.4971 | 3349.7058
[7 empty] | 7958 | 10476 | 1570037 | 2018-05-08 16:33 | 2018-05-08 23:45 | 432 | 11kV | 34495 | 219 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186744 1 fault operation Earth Fault 11kV main on ground near pole GQ-47483. Excluded OMS 1570019 & 1570037. | May | 2018 | 2018Q4 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2018-05-08 | N | 157.5114 | N | 5 | N | N | 1.1101 | 39.4971 | 25207.9286
[7 empty] | 7976 | 10688 | 1570050 | 2018-05-08 22:57 | 2018-05-09 00:11 | 74 | 11kV | 52836 | 744 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters Zn Pnl.21 tripped on: B phase O/C Field EFIs: S3979 S8836 S138 S4739 S2785 Contractor for WestConnex cut into live feeder adj Pole LE19482. Contract sent to hospital by foreman. Section of feeder from S2785 (Sw/B) to S7426 (Sw/A) See 1570243 1570244 | May | 2018 | 2018Q4 | 2018 | ZN2568:PA21 | ZN2568:PA21 | ZN02568/000021 | SYDNEY | UG | Not Veg | 2018-05-08 | N | 71.0161 | N | 5 | N | N | 1.1101 | 39.4971 | 38610.9904
[7 empty] | 8262 | 14513 | 1570155 | 2018-05-09 15:47 | 2018-05-09 16:35 | 48 | 11kV | 5520 | 115 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186751 section deenergised for safety tree on OHM at pole MG-50038 Excluded oms # 1570158, | May | 2018 | 2018Q4 | 2018 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2018-05-09 | N | 48 | N | 3 | N | N | 1.1101 | 39.4971 | 4033.8532
[7 empty] | 7204 | 480 | 1570204 | 2018-05-09 19:55 | 2018-05-09 20:40 | 45 | 11kV | 2430 | 54 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186755 OUTAGE to retension mains after tree fell on mains earlier. see UPOR-186751 Excluded oms 1570158 | May | 2018 | 2018Q4 | 2018 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2018-05-09 | N | 45 | N | 3 | N | N | 1.1101 | 39.4971 | 1775.7723
[7 empty] | 7639 | 6699 | 1570212 | 2018-05-09 23:47 | 2018-05-10 00:19 | 32 | 11kV | 2144 | 67 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186754 B Phase DOLF : 20 Amp Excluded OMS 1570212 | May | 2018 | 2018Q4 | 2018 | 205:12213 | 205:12213 | ZN00205/012213 | NEWCASTLE | OH | Veg | 2018-05-09 | N | 32 | N | 3 | N | N | 1.1101 | 39.4971 | 1566.772
[7 empty] | 7627 | 6565 | 1570424 | 2018-05-10 17:29 | 2018-05-10 21:50 | 261 | 11kV | 470650 | 2386 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Wind Strong | N | Zn10999 Kogarah - Pnl.39L tripped on: A & B phase IOC Abnormal: S10208 (Sw/A) closed with S10863 (Sw/A) open (defective UG cable) Aluminium steamer found on OH mains near Bowns & Garden St. (11kV OH between S10863 to LB 31109 tee S10905. Lineworkers to repair OH & remove steamer See 1570456 1570457 1570458 1570459 | May | 2018 | 2018Q4 | 2018 | ZN10999:PA15 | ZN10999:PA15 | ZN10999/000015 | BAYSIDE | OH | Not Veg | 2018-05-10 | N | 197.2548 | N | 1 | N | N | 1.1101 | 39.4971 | 343937.1382
[7 empty] | 8200 | 13762 | 1570461 | 2018-05-11 08:51 | 2018-05-11 10:25 | 94 | 11kV | 282 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 186765 A & B Phase DOLF : 10 Amp Excluded OMS 1570461 | May | 2018 | 2018Q4 | 2018 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2018-05-11 | N | 94 | N | 3 | N | N | 1.1101 | 39.4971 | 206.0773
[7 empty] | 7923 | 10178 | 1570520 | 2018-05-11 11:54 | 2018-05-11 13:03 | 69 | 11kV | 91770 | 1334 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 186771 2 fault operations B & C phases Overcurrent Branch on mains MW-70011 Excluded OMS 1570520 | May | 2018 | 2018Q4 | 2018 | 233:82815 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Veg | 2018-05-11 | N | 68.7931 | N | 3 | N | N | 1.1101 | 39.4971 | 67062.8092
[7 empty] | 7517 | 5543 | 1570490 | 2018-05-11 10:15 | 2018-05-11 18:50 | 515 | 11kV | 252921 | 1792 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Wind Strong | N | LID 186773 2 fault operations 3 phase Overcurrent, Earth fault Large tree down adjacent to PT 12287 Banks St. broken x arm pole JR-90228. Excluded OMS 1570553 & 1570557 & 1570490 | May | 2018 | 2018Q4 | 2018 | 264:81236 | 264:81236 | ZN00264/081236 | PORT STEPHENS | OH | Veg | 2018-05-11 | N | 141.139 | N | 3 | N | N | 1.1101 | 39.4971 | 184827.2069
[7 empty] | 8651 | 19475 | 1570629 | 2018-05-12 00:23 | 2018-05-12 00:56 | 33 | 11kV | 15015 | 455 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 186775 3 fault operations 3 phase Overcurrent Branch on mains JT-40052 Excluded OMS 1570630 | May | 2018 | 2018Q4 | 2018 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Veg | 2018-05-12 | N | 33 | N | 5 | N | N | 1.1101 | 39.4971 | 10972.5191
[7 empty] | 7536 | 5707 | 1571003 | 2018-05-12 08:33 | 2018-05-12 09:03 | 30 | 11kV | 30 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 186779 1 fault operation Overcurrent Mains clashing in HVC installation | May | 2018 | 2018Q4 | 2018 |  |  |  | SINGLETON | OH | Veg | 2018-05-12 | N | 30 | N | 5 | N | N | 1.1101 | 39.4971 | 21.9231
[7 empty] | 7608 | 6386 | 1570658 | 2018-05-12 08:59 | 2018-05-12 09:51 | 52 | 11kV | 30888 | 594 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | At Zn8000 Macquarie Park Panel 1 tripped on A and Cphase overcurrent Signals: Tx2 Group earth with EFI Cause Not ascertained for outage | May | 2018 | 2018Q4 | 2018 | ZN8000:PA1 | ZN8000:PA2 | ZN08000/000002 | RYDE | OH | Veg | 2018-05-12 | N | 52 | N | 5 | N | N | 1.1101 | 39.4971 | 22572.0394
[7 empty] | 7920 | 10140 | 1570688 | 2018-05-12 10:27 | 2018-05-12 11:48 | 81 | 11kV | 60183 | 743 | HV | Excavation Ausgrid Staff | Utility Process Issue | U/G Cable | Unplanned | No Weather Impact | N | At Zn5868 Gore HIll 11kV Pasnel 5 tripped on overcurrent withf ault check. Signals: 11kV Trip, TX2 group and zone earth with efi Cause: Suspect cable damaged by Gore Hill jointers in the vicinity of S2626 Campbell Clarendon | May | 2018 | 2018Q4 | 2018 | ZN5868:PA5 | ZN5868:PA5 | ZN05868/000005 | WILLOUGHBY | UG | Not Veg | 2018-05-12 | N | 81 | N | 5 | N | N | 1.1101 | 39.4971 | 43979.9613
[7 empty] | 8702 | 20110 | 1570921 | 2018-05-12 11:47 | 2018-05-12 12:07 | 20 | 11kV | 400 | 20 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 186777 interupted by dop to remove tree branch off pole HU-90065, reported by LW. nil oms. dq | May | 2018 | 2018Q4 | 2018 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2018-05-12 | N | 20 | N | 5 | N | N | 1.1101 | 39.4971 | 292.3082
[7 empty] | 8178 | 13478 | 1570802 | 2018-05-13 08:11 | 2018-05-13 09:45 | 94.2167 | 11kV | 1319.0333 | 14 | HV | Animal Bird | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | At PT15278 Cooyong Rd 50A HV roadside HDO blown Cause: Animals/Birds @ PT15278 | May | 2018 | 2018Q4 | 2018 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Not Veg | 2018-05-13 | N | 94.2167 | N | 4 | N | N | 1.1101 | 39.4971 | 963.9107
[7 empty] | 8325 | 15223 | 1570817 | 2018-05-13 08:10 | 2018-05-13 13:00 | 289.9167 | 11kV | 5218.5 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186784 DOLF : 5 Amp | May | 2018 | 2018Q4 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | SINGLETON | OH | Veg | 2018-05-13 | N | 289.9167 | N | 4 | N | N | 1.1101 | 39.4971 | 3813.5259
[7 empty] | 7842 | 9267 | 1570871 | 2018-05-13 11:20 | 2018-05-13 18:50 | 450 | 11kV | 895 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Ex Zn14143 Somersby Ex Pa12 PT132828 Mt Penang Pacific No1, Left hand Side and Middle phase HDO's blown (40A) Broken fuse assembly, requires replacement S12155 Mt Penang Pacific No2 was interrupted @ 1535by DOp for fuse assembly to be replaced LK42746 opened by DOp Cause: not ascertained. Fuse assembly changed by T/Con See 1571142 1571143 ex 1570871 | May | 2018 | 2018Q4 | 2018 | ZN14143:PA12 | ZN14143:PA12 | ZN14143/000012 | CENTRAL COAST | OH | Veg | 2018-05-13 | N | 447.5 | N | 4 | N | N | 1.1101 | 39.4971 | 654.0396
[7 empty] | 8580 | 18577 | 1570904 | 2018-05-13 21:40 | 2018-05-14 05:05 | 445 | 11kV | 7563 | 45 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 186786 C Phase DOLF : 10 Amp Car into pole JR-25096. Replaced pole under AP. LV mains clashed. C ph DOLF blown only. Excluded OMS 1570904 | May | 2018 | 2018Q4 | 2018 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Not Veg | 2018-05-13 | N | 168.0667 | N | 4 | N | N | 1.1101 | 39.4971 | 5526.8173
[7 empty] | 7183 | 126 | 1571169 | 2018-05-14 19:54 | 2018-05-14 21:25 | 91 | 11kV | 102848 | 1533 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill Pnl.15 tripped on Earth Fault and A phase IOC Field EFIs: S5048 S2583 UG cable fault in section between S2583 (Sw/B) to S8972 (Sw/A) tee S5067. See 1571419 1571420 1571422 | May | 2018 | 2018Q4 | 2018 | ZN398:PA15 | ZN398:PA15 | ZN00398/000015 | INNER WEST | UG | Not Veg | 2018-05-14 | N | 67.0894 | N | 1 | N | N | 1.1101 | 39.4971 | 75158.2849
[7 empty] | 7525 | 5603 | 1571180 | 2018-05-15 01:15 | 2018-05-15 05:45 | 270 | 11kV | 3240 | 12 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186796 wires down at pole JR-72422 (return side) section isolated for repairs. see report # 186795/OMS 1571195 Excluded oms 1571180 | May | 2018 | 2018Q4 | 2018 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2018-05-15 | N | 270 | N | 3 | N | N | 1.1101 | 39.4971 | 2367.6964
[7 empty] | 7387 | 3704 | 1571289 | 2018-05-15 13:11 | 2018-05-15 17:05 | 234 | 11kV | 234 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 186810 A Phase Broken Live Line Clamp Excluded OMS 1571289 | May | 2018 | 2018Q4 | 2018 | 532:83298 | 532:83298 | ZN00532/083298 | MAITLAND | OH | Not Veg | 2018-05-15 | N | 234 | N | 3 | N | N | 1.1101 | 39.4971 | 171.0003
[7 empty] | 8493 | 17530 | 1571357 | 2018-05-15 19:47 | 2018-05-15 20:40 | 53 | 11kV | 4929 | 93 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186813 Stranded mains at pole GW-50034 section isolated to repair mains at pole GW-50034 Excluded oms 1571357 | May | 2018 | 2018Q4 | 2018 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2018-05-15 | N | 53 | N | 3 | N | N | 1.1101 | 39.4971 | 3601.9678
[7 empty] | 7295 | 2048 | 1571586 | 2018-05-17 01:54 | 2018-05-17 04:00 | 126 | 11kV | 15534 | 270 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 186822 2 fault operation A Phase Overcurrent Faulty UGOH AH-20558 left isolated Protection details A phase OC Excluded OMS 1571586 | May | 2018 | 2018Q4 | 2018 | 813:89059 | 813:89059 | ZN00813/089059 | UPPER HUNTER | Unknown | Unknown | 2018-05-17 | N | 57.5333 | N | 3 | N | N | 1.1101 | 39.4971 | 11351.789
[7 empty] | 8268 | 14589 | 1571588 | 2018-05-17 03:41 | 2018-05-17 05:27 | 106 | 11kV | 93386 | 881 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | 11kv feeder ex ZN1287 Revesby Panel 15 (S47211) from 11kv AB2985 to S8172 amberdale picnic Remarks: cause not ascertained. Possible burnt off bond or defective airbreak (2985) | May | 2018 | 2018Q4 | 2018 | ZN1287:PA15 | ZN1287:PA15 | ZN01287/000015 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-05-17 | N | 106 | N | 3 | N | N | 1.1101 | 39.4971 | 68243.7344
[7 empty] | 8166 | 13336 | 1571753 | 2018-05-17 17:45 | 2018-05-18 11:40 | 1075 | 11kV | 47182 | 81 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14891 Wyng Ex Pa5 "Dooralong" feeder RE45017 "Whiteman" tripped reclosed and locked out on: Relays: OC trip, Lockout Cause: tree branch brought down OH mains adajcent PT13337 Dooralong Hitchock 2.6 Section of 11kV fdr from LK42504 to AB44350 tee PT14965, PT12283, PT12157, PT13337 isolated to make repairs. See 1571753,69 ex 1571754 | May | 2018 | 2018Q4 | 2018 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2018-05-17 | N | 582.4938 | N | 3 | N | N | 1.1101 | 39.4971 | 34479.214
[7 empty] | 8691 | 19923 | 1571878 | 2018-05-18 14:04 | 2018-05-18 15:40 | 96 | 11kV | 288 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186840 Single phase Repair broken LL Lead to sub 27923. Excluded OMS No. 1571878 | May | 2018 | 2018Q4 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-05-18 | N | 96 | N | 3 | N | N | 1.1101 | 39.4971 | 210.4619
[7 empty] | 7983 | 10806 | 1571914 | 2018-05-18 16:27 | 2018-05-18 16:48 | 21 | 11kV | 14721 | 701 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | IR 61454 Berowra Tollgates Tripped Relays: Overcurrent , SEL, Lockout Signals: 11kV trip Cause: DOPp patrolled at Night - L/W to patrol in daylight - Cause not ascertained | May | 2018 | 2018Q4 | 2018 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2018-05-18 | N | 21 | N | 3 | N | N | 1.1101 | 39.4971 | 10757.6726
[7 empty] | 8004 | 11160 | 1571932 | 2018-05-18 18:32 | 2018-05-19 02:20 | 468 | 11kV | 230283 | 1584 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Panel 57 Tripped on Relays: A B and Cphase O/C Cause: Bat shorted 11kV mains and brought down a phase of 11kV into the LV mains adjacent to LB77071 See OMS 1572510 1572511 1572512 1572513 1571932 1571946 1571957 1571958 1571968 | May | 2018 | 2018Q4 | 2018 | ZN129:PA57 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Not Veg | 2018-05-18 | N | 145.3807 | N | 3 | N | N | 1.1101 | 39.4971 | 168284.0242
[7 empty] | 8469 | 17264 | 1572030 | 2018-05-19 12:17 | 2018-05-19 13:35 | 78 | 11kV | 156 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 186843 DOLF :10 Amp Bird contacted mains. Excluded OMS 1572030. | May | 2018 | 2018Q4 | 2018 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2018-05-19 | N | 78 | N | 2 | N | N | 1.1101 | 39.4971 | 114.0002
[7 empty] | 7641 | 6716 | 1571978 | 2018-05-19 06:25 | 2018-05-19 15:30 | 545.1667 | 11kV | 9813 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186842 DOLF : 5 Amp 11kV main down between subs 54170 & 50735. | May | 2018 | 2018Q4 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | SINGLETON | OH | Not Veg | 2018-05-19 | N | 545.1667 | N | 2 | N | N | 1.1101 | 39.4971 | 7171.051
[7 empty] | 8020 | 11304 | 1572283 | 2018-05-21 12:45 | 2018-05-21 15:45 | 180 | 11kV | 900 | 5 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 186857 A Phase burnt off Live line clamp Excluded oms 1572283 | May | 2018 | 2018Q4 | 2018 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2018-05-21 | N | 180 | N | 2 | N | N | 1.1101 | 39.4971 | 657.6935
[7 empty] | 7450 | 4678 | 1572322 | 2018-05-21 15:00 | 2018-05-21 19:15 | 255 | 11kV | 111224 | 1112 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | @ S4545 Meadowbank span of 11kV OH down near LB1052 See OMS 1572496 1572497 1572322 | May | 2018 | 2018Q4 | 2018 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | PARRAMATTA | OH | Not Veg | 2018-05-21 | N | 100.0216 | N | 2 | N | N | 1.1101 | 39.4971 | 81279.2186
[7 empty] | 7400 | 3844 | 1572452 | 2018-05-22 09:57 | 2018-05-22 11:44 | 107 | 11kV | 215741 | 2082 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn8471 Darling Harbour - Pnl.1 tripped on: Right C & N Earth Fault Front line UG cable fault from Pnl.1 to S6532 to 64022 to S5786. | May | 2018 | 2018Q4 | 2018 | ZN7481:PA1 | ZN7481:PA1R | ZN07481/000001 | SYDNEY | UG | Not Veg | 2018-05-22 | N | 103.622 | N | 4 | N | N | 1.1101 | 39.4971 | 157657.1595
[7 empty] | 7622 | 6516 | 1572474 | 2018-05-22 10:48 | 2018-05-22 12:05 | 77 | 11kV | 4158 | 54 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn14892 Charmhaven Pa17 PT13095 Crangee Wowera 63Amp roads side HVDO operated See 1574351 ex 1572474 | May | 2018 | 2018Q4 | 2018 | ZN14892:PA17 | ZN14892:PA9 | ZN14892/000009 | CENTRAL COAST | OH | Not Veg | 2018-05-22 | N | 77 | N | 4 | N | N | 1.1101 | 39.4971 | 3038.5438
[7 empty] | 8713 | 20262 | 1572524 | 2018-05-22 13:05 | 2018-05-22 13:42 | 37 | 11kV | 11546 | 320 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15001 Brookvale Panel 4 "Windbourne Pittwater" tripped on IOC, 51N 50 TA EFI Cause: UG fault. Suspected Underground cable fault between S16106/SwB to S16838/SwA See 1572873,4 GIS 1572529 ex 1572524 | May | 2018 | 2018Q4 | 2018 | ZN15001:PA4 | ZN15001:PA4 | ZN15001/000004 | NORTHERN BEACHES | UG | Not Veg | 2018-05-22 | N | 36.0812 | N | 4 | N | N | 1.1101 | 39.4971 | 8437.4763
[7 empty] | 8245 | 14377 | 1572549 | 2018-05-22 15:01 | 2018-05-22 17:30 | 149 | 11kV | 11365 | 137 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186867 1 fault operation A & B phase Sensitive Earth Fault Recloser tripped on SEF. DOp found 2x dolfs down at LF 76775. Excluded OMS 1572549 & 1572551 | May | 2018 | 2018Q4 | 2018 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2018-05-22 | N | 82.9562 | N | 4 | N | N | 1.1101 | 39.4971 | 8305.2068
[7 empty] | 8141 | 13090 | 1572623 | 2018-05-23 02:22 | 2018-05-23 15:45 | 803 | 11kV | 14576 | 60 | HV | 3rd Party Vehicle | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186869 3 fault operations Overcurrent truck hit sub pole 7L-10008.(sub 70700) Excluded OMS 1572624 & 1572623 | May | 2018 | 2018Q4 | 2018 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2018-05-23 | N | 242.9333 | N | 2 | N | N | 1.1101 | 39.4971 | 10651.7109
[7 empty] | 7868 | 9517 | 1572791 | 2018-05-23 19:07 | 2018-05-23 20:15 | 68.4 | 11kV | 3488.4 | 51 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 186883 interrupt to repair burnt up Cph Dolf CC1: 22-"Refer to SOp" | May | 2018 | 2018Q4 | 2018 | 223:14397 | 223:14397 | ZN00223/014397 | LAKE MACQUARIE | OH | Not Veg | 2018-05-23 | N | 68.4 | N | 2 | N | N | 1.1101 | 39.4971 | 2549.2198
[7 empty] | 7811 | 8852 | 1573169 | 2018-05-26 09:37 | 2018-05-26 12:30 | 173 | 11kV | 346 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 186912 B phase sub isolated to replace b phase dolf assembly Excluded oms 1573169 | May | 2018 | 2018Q4 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2018-05-26 | N | 173 | N | 2 | N | N | 1.1101 | 39.4971 | 252.8466
[7 empty] | 8025 | 11350 | 1573174 | 2018-05-26 10:28 | 2018-05-26 15:45 | 317 | 11kV | 10342 | 49 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186915 3 phase mains down pole 9L-70377 section isolated for repairs Excluded oms 1573174, 1573192 | May | 2018 | 2018Q4 | 2018 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2018-05-26 | N | 211.0612 | N | 2 | N | N | 1.1101 | 39.4971 | 7557.6286
[7 empty] | 7606 | 6376 | 1573308 | 2018-05-28 06:54 | 2018-05-28 09:15 | 141 | 11kV | 141360 | 2746 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 186918 1 fault operation B & C Phase Overcurrent Bird in OHM at JU-66380 Fdr 80646 Trip BC O/C Note: Sw 2418 Closed ABS 64530 Open LV Links 2284 1157 4562 Closed Fdr 64530/2418 back on 0736hrs Fdr 80646 back on 0747hrs ABC 400A LH LVF 65020 back on 0828hrs ABC 315A RH LVF 12102 back on 0915hrs Excluded OMS 1573308 etc | May | 2018 | 2018Q4 | 2018 | 256:80646 | 256:80646 | ZN00256/080646 | NEWCASTLE | OH | Not Veg | 2018-05-28 | N | 51.4785 | N | 3 | N | N | 1.1101 | 39.4971 | 103301.7186
[7 empty] | 8530 | 17965 | 1573579 | 2018-05-28 21:31 | 2018-05-28 22:30 | 59 | 11kV | 1888 | 32 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 186923 B Phase DOLF : 16 Amp Fatigued fuse. Readings as left 48A, 100A, 25A. Excluded OMS 1573579 | May | 2018 | 2018Q4 | 2018 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2018-05-28 | N | 59 | N | 3 | N | N | 1.1101 | 39.4971 | 1379.6947
[7 empty] | 8566 | 18395 | 1573583 | 2018-05-28 23:30 | 2018-05-29 01:40 | 130 | 11kV | 37830 | 291 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn14891 Wyong Ex Pa12 RE48813 opened & locked out on OC & SEF Abnormal: Bypass AB cloased @ Recloser 44753 Bunnings Creek (DMA) Cause: Weather related | May | 2018 | 2018Q4 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | Unknown | Not Veg | 2018-05-28 | N | 130 | N | 3 | N | N | 1.1101 | 39.4971 | 27645.0482
[7 empty] | 8074 | 12127 | 1573609 | 2018-05-29 08:57 | 2018-05-29 11:31 | 154 | 11kV | 44814 | 291 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn14891 Wyong Pa12 "Yarramalong" fdr IR48813 Yarramalong Boyds 3.7 tripped and locked out Relays: OC trip, SEF, Lockout Cause: Protection malfunction IR48813 Yarramalong Boyds 3.7 was RTS on the 28/5/18 after repairs for nuisance tripping. has tripped twice since being RTS, see also interruption on 28/5/18 at 2330. Suspected protection malfunction | May | 2018 | 2018Q4 | 2018 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | Unknown | Not Veg | 2018-05-29 | N | 154 | N | 5 | N | N | 1.1101 | 39.4971 | 32748.7494
[7 empty] | 7659 | 6901 | 1573664 | 2018-05-29 11:01 | 2018-05-29 13:50 | 169 | 11kV | 1859 | 11 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 186934 B Phase Bph lead from bail clamp broken away at DOLF. Excluded OMS No. 1573664 + 1573684 | May | 2018 | 2018Q4 | 2018 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2018-05-29 | N | 169 | N | 5 | N | N | 1.1101 | 39.4971 | 1358.5024
[7 empty] | 7210 | 550 | 1573675 | 2018-05-29 11:29 | 2018-05-29 14:30 | 181 | 11kV | 92434 | 954 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | LID 186933 1 fault operation A & B phase Overcurrent No AR, Faulty CB Closing Supply Rectifier Excluded oms 1573675 & 1573696 | May | 2018 | 2018Q4 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | Unknown | Not Veg | 2018-05-29 | N | 96.891 | N | 5 | N | N | 1.1101 | 39.4971 | 67548.0409
[7 empty] | 8275 | 14676 | 1573710 | 2018-05-29 14:51 | 2018-05-29 20:35 | 344 | 11kV | 344 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 186938 SUB ISOLATED TO REPLACE BURNT UP LLC Excluded OMS 1573710 | May | 2018 | 2018Q4 | 2018 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2018-05-29 | N | 344 | N | 5 | N | N | 1.1101 | 39.4971 | 251.3851
[7 empty] | 8486 | 17462 | 1573772 | 2018-05-29 20:20 | 2018-05-29 21:19 | 59 | 11kV | 46728 | 792 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | Rain Heavy | N | Zn180 Mosman Panel 17 "S62490" fdr has tripped Signals: A phase inst, C Ph inst timed, EFI, FC EFI's: As expected Cause: Deceased possum found burnt at base of recloser 229 Middle Head Rd See 1573772 ex 1573773,5,6,7 | May | 2018 | 2018Q4 | 2018 | ZN180:PA17 | ZN180:PA17 | ZN00180/000017 | MOSMAN | OH | Not Veg | 2018-05-29 | N | 59 | N | 5 | N | N | 1.1101 | 39.4971 | 34147.4442
[7 empty] | 7275 | 1767 | 1573819 | 2018-05-30 07:42 | 2018-05-30 10:05 | 143 | 11kV | 429 | 3 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Rain Heavy | N | LID 186942 BAIL CLAMP BROKE NO PROTECTION TRIPPED. Excluded OMS 1573819, 1573824 | May | 2018 | 2018Q4 | 2018 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | Unknown | Not Veg | 2018-05-30 | N | 143 | N | 2 | N | N | 1.1101 | 39.4971 | 313.5005
[7 empty] | 8001 | 11144 | 1573972 | 2018-05-30 17:23 | 2018-05-30 17:36 | 13 | 11kV | 21411 | 1647 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.2 tripped. No details provided by Control Room regarding outage. Outage times derived from DNMS trends. AOp now on extended leave, unable to gain details. | May | 2018 | 2018Q4 | 2018 | ZN10994:PA2 | ZN10994:PA2 | ZN10994/000002 | GEORGES RIVER | OH | Veg | 2018-05-30 | N | 13 | N | 2 | N | N | 1.1101 | 39.4971 | 15646.5273
[7 empty] | 7752 | 8067 | 1574114 | 2018-05-31 13:12 | 2018-05-31 13:40 | 28 | 11kV | 28 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 186977 A Phase Burnt 11kV tapping at ugoh pole IV-90723 Excluded oms 1574114 | May | 2018 | 2018Q4 | 2018 | 206:34432 | 206:34432 | ZN00206/034432 | LAKE MACQUARIE | OH | Not Veg | 2018-05-31 | N | 28 | N | 5 | N | N | 1.1101 | 39.4971 | 20.4616
[7 empty] | 8523 | 17856 | 1574078 | 2018-05-31 10:59 | 2018-05-31 14:35 | 216 | 11kV | 73676 | 869 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 186972 B Phase Overcurrent, Earth Fault NBN contractor drilled hole through telstra pit into 11kV cable. Contractor injured. Not all customers restored until investigations were carried out by work cover. Excluded OMS 1574078, 1574105 | May | 2018 | 2018Q4 | 2018 | 202:34262 | 202:34262 | ZN00202/034262 | NEWCASTLE | UG | Not Veg | 2018-05-31 | N | 84.7825 | N | 5 | N | N | 1.1101 | 39.4971 | 53840.2477
[7 empty] | 7711 | 7570 | 1574136 | 2018-05-31 14:16 | 2018-05-31 15:50 | 94 | 11kV | 159554 | 1788 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9118 Cronulla - Pnl.6 tripped on: Earth Fault Field EFIs: S9508 S9009 S9610 S9581 S65225 S9029 UG cable fault between S9029 (Sw/B), S9059 (Sw/A) and S9289 (Sw/B) See 1574258 1574259 | May | 2018 | 2018Q4 | 2018 | ZN9118:PA6 | ZN9118:PA6 | ZN09118/000006 | SUTHERLAND | UG | Not Veg | 2018-05-31 | N | 89.236 | N | 5 | N | N | 1.1101 | 39.4971 | 116597.3572
[7 empty] | 8682 | 19802 | 1574214 | 2018-05-31 18:59 | 2018-05-31 21:20 | 141 | 11kV | 73663 | 733 | HV | Animal Possum | Animal | UGOH | Unplanned | Wind Strong | N | Zn10993 Hurstville North - Pnl.23 tripped & reclosed on: A, B & C phase O/C Possum on UGOH below LB61550, damaged and blown open circuit. Feeder reclosed successfully to open circuit UGOH. See 1574264 1574266 | May | 2018 | 2018Q4 | 2018 | ZN10993:PA23 | ZN10993:PA23 | ZN10993/000023 | GEORGES RIVER | OH | Not Veg | 2018-05-31 | N | 100.4952 | N | 5 | N | N | 1.1101 | 39.4971 | 53830.7477
[7 empty] | 7733 | 7818 | 1574222 | 2018-05-31 22:45 | 2018-06-01 01:05 | 140 | 11kV | 70755 | 961 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 186982 3 fault operations Overcurrent, Earth fault Suspect underground cable fault. from Sw 56059 to UGOH. Excluded OMS 1574222. | May | 2018 | 2018Q4 | 2018 | 507:80923 | 507:80923 | ZN00507/080923 | CESSNOCK | UG | Not Veg | 2018-05-31 | N | 73.6264 | N | 5 | N | N | 1.1101 | 39.4971 | 51705.6671
[7 empty] | 7247 | 1219 | 1574241 | 2018-06-01 06:57 | 2018-06-01 07:43 | 46 | 11kV | 31418 | 683 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15001 Brookvale Pa8 "Harbord Rd" fdr tripped Relays: A+B+C phase IOC, EFI, Fault Check Relay Signals: 11kv trip EFI's: Nil Cause: Animals/Birds. Magpie Across 11kv mains on corner tee pole below S16821 See 1574241 ex 157424,3 | June | 2018 | 2018Q4 | 2018 | ZN15001:PA8 | ZN15001:PA8 | ZN15001/000008 | NORTHERN BEACHES | OH | Not Veg | 2018-06-01 | N | 46 | N | 4 | N | N | 1.1101 | 39.4971 | 22959.3477
[7 empty] | 8189 | 13555 | 1574415 | 2018-06-01 14:07 | 2018-06-01 16:55 | 168 | 11kV | 3192 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 187110 refer SI 27232 fuse saver opened when returning this switching, no cause found Excluded oms 1574415 | June | 2018 | 2018Q4 | 2018 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2018-06-01 | N | 168 | N | 4 | N | N | 1.1101 | 39.4971 | 2332.6195
[7 empty] | 7709 | 7540 | 1574428 | 2018-06-01 14:57 | 2018-06-01 20:15 | 318 | 11kV | 198145 | 1734 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15008 Harbord Ex Pa7 IR63175 Griffin Adam tripped on Relays: OC trip @Harbord Zn: Zone Earth Cause: OH Down. 11kv conductors fell outside 7 Molong st, North Curl Curl See 1574924,5,6 ex 1574426,8,9,30,1,2,3,5,42,60,7 | June | 2018 | 2018Q4 | 2018 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Veg | 2018-06-01 | N | 114.2705 | N | 4 | N | N | 1.1101 | 39.4971 | 144798.5217
[7 empty] | 7333 | 2741 | 1574487 | 2018-06-01 21:32 | 2018-06-01 23:05 | 93 | 11kV | 68169 | 733 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10993 Hurstville North - Pnl.23 front line section of UG feeder has gone open circuit on "C" phase. | June | 2018 | 2018Q4 | 2018 | ZN10993:PA23 | ZN10993:PA23 | ZN10993/000023 | GEORGES RIVER | UG | Not Veg | 2018-06-01 | N | 93 | N | 4 | N | N | 1.1101 | 39.4971 | 49815.8946
[7 empty] | 8381 | 16006 | 1574495 | 2018-06-02 02:34 | 2018-06-02 03:43 | 69 | 11kV | 106329 | 1541 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn15004 Newport Panel 9 "Avalon" fdr tripped Relays: IOC B & C Phase Signals: 11kv trip EFI's: Nil Cause: not ascertained. DOp patrolled at night, next available linesman to atrol in daylight | June | 2018 | 2018Q4 | 2018 | ZN15004:PA9 | ZN15004:PA9 | ZN15004/000009 | NORTHERN BEACHES | OH | Veg | 2018-06-02 | N | 69 | N | 6 | N | N | 1.1101 | 39.4971 | 77702.097
[7 empty] | 8513 | 17747 | 1574515 | 2018-06-02 09:29 | 2018-06-02 10:05 | 36 | 11kV | 46872 | 1302 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | Cold <10C | N | REC 35756 Bundeena tripped on: O/C Abnormal: REC62657 closed with LB35391 Open. 11kV from LB35391 to REC35078 also out of service with DCs in // and on Generator. Bat on wires at 15 Liverpool Rd, Bundeena. Generators restored at 12:00 | June | 2018 | 2018Q4 | 2018 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2018-06-02 | N | 36 | N | 6 | N | N | 1.1101 | 39.4971 | 34252.6751
[7 empty] | 7498 | 5376 | 1574549 | 2018-06-02 11:14 | 2018-06-02 12:30 | 76 | 11kV | 13956 | 201 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.30 tripped on Earth Fault No Field EFIs. Only 2 DCs on feeder at Open Points. Suspected UG cable fault in front line section. See 1574901 1574902 | June | 2018 | 2018Q4 | 2018 | ZN10999:PA30 | ZN10999:PA30 | ZN10999/000030 | GEORGES RIVER | UG | Not Veg | 2018-06-02 | N | 69.4328 | N | 6 | N | N | 1.1101 | 39.4971 | 10198.6332
[7 empty] | 8373 | 15824 | 1574574 | 2018-06-02 12:53 | 2018-06-02 13:54 | 60.6 | 11kV | 19755.6 | 326 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15014 Mona Vale Ex Pa14 "Walana Mona, etc" tripped, reclosed, tripped and locked out due to tree on 11KV OH See 1574574 ex 1574577,80,95 | June | 2018 | 2018Q4 | 2018 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2018-06-02 | N | 60.6 | N | 6 | N | N | 1.1101 | 39.4971 | 14436.8098
[7 empty] | 7488 | 5164 | 1574502 | 2018-06-02 12:55 | 2018-06-02 15:30 | 155 | 11kV | 21855 | 141 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15014 Mona Vale Ex Panel 12 "Minmai Rd" from S16528 Elvina Bay South SwB to S16419 Towlers bay Interrutped for emergency tree trimming outside 38 Wirringulla Ave, Elvina Bay See 1574575 ex 1574502 | June | 2018 | 2018Q4 | 2018 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | OH | Veg | 2018-06-02 | N | 155 | N | 6 | N | N | 1.1101 | 39.4971 | 15970.9894
[7 empty] | 8095 | 12338 | 1574590 | 2018-06-02 13:35 | 2018-06-02 15:50 | 135.2167 | 11kV | 10006.0333 | 74 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | LID 186997 A Phase DOLF : 20 Amp FATIGUED FUSE. READINGS AS LEFT 238V, 238V, 242V. Excluded oms 1574596, 1574597 CC1: 22-"Refer to SOp" | June | 2018 | 2018Q4 | 2018 | 242:81538 | 242:81538 | ZN00242/081538 | PORT STEPHENS | OH | Not Veg | 2018-06-02 | N | 135.2167 | N | 6 | N | N | 1.1101 | 39.4971 | 7312.114
[7 empty] | 7558 | 5918 | 1574675 | 2018-06-03 07:15 | 2018-06-03 08:31 | 76 | 11kV | 135432 | 1782 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN1287 Revesby Panel 312 'S4582 Tyalgum Av' feeder has tripped on: Signals: 11kv trip Relays: C phase O/C & IOC Field EFI's: nil Abnormal: AB2985 open & defective Sw/B closed @ S8172 Remarks: animals/birds. Dead crow found at base of HV pole PE14939, near open AB2985 | June | 2018 | 2018Q4 | 2018 | ZN1287:PA12 | ZN1287:PA12 | ZN01287/000012 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-06-03 | N | 76 | N | 2 | N | N | 1.1101 | 39.4971 | 98969.711
[7 empty] | 7738 | 7884 | 1574737 | 2018-06-03 12:25 | 2018-06-03 14:15 | 110 | 11kV | 106722 | 1845 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Rain Light | N | LID 187009 2 fault operations A & B phase Overcurrent50T AB targets plus EFI's at 55613, 59979, 55933. Hazemeyer RMI burnt at S.24117 Rebecca Rd. Excluded OMS 1574737 | June | 2018 | 2018Q4 | 2018 | 511:29873 | 502:48004 | ZN00502/048004 | MAITLAND | Unknown | Not Veg | 2018-06-03 | N | 57.8439 | N | 2 | N | N | 1.1101 | 39.4971 | 77989.2898
[7 empty] | 8247 | 14390 | 1574805 | 2018-06-04 03:21 | 2018-06-04 05:50 | 149 | 11kV | 11026 | 74 | HV | Animal Possum | Animal | Fuse Assembly | Unplanned | No Weather Impact | N | PT9514 Caravan Farrer - 11kV Roadside HDO blown Possum on Tx Bushing (Blown clear) Restored via LV // 524, 1397 | June | 2018 | 2018Q4 | 2018 | ZN9252:PA28 | ZN9252:PA28 | ZN09252/000028 | SUTHERLAND | OH | Not Veg | 2018-06-04 | N | 149 | N | 3 | N | N | 1.1101 | 39.4971 | 8057.4756
[7 empty] | 8408 | 16500 | 1574921 | 2018-06-04 12:48 | 2018-06-04 13:50 | 62 | 11kV | 189816 | 3510 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde - 11kV panel 28 tripped, reclosed tripped and locked out Panel 28 - Recloser Lockout Relay Panel 28 R - A and C phase IOC Signals 11kV trip Cause: Plastic Hanging From 11kV Outside 40A Jones St Ryde See OMS 1575422 1574523 1574934 1574921 1574923 | June | 2018 | 2018Q4 | 2018 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Veg | 2018-06-04 | N | 54.0786 | N | 3 | N | N | 1.1101 | 39.4971 | 138711.9342
[7 empty] | 8487 | 17466 | 1574887 | 2018-06-04 15:30 | 2018-06-04 16:10 | 40 | 11kV | 1640 | 41 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 187028 SUB 27101 isolated for repair to lv fuse box. Excluded oms 1574887 | June | 2018 | 2018Q4 | 2018 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2018-06-04 | N | 40 | N | 3 | N | N | 1.1101 | 39.4971 | 1198.4636
[7 empty] | 7434 | 4325 | 1575087 | 2018-06-05 03:26 | 2018-06-05 05:20 | 114 | 11kV | 114 | 1 | HV | Customer Installation Fault | Customer Installation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 187027 Single phase DOLF : 3 Amp Sub 4148 replaced 3.15a DOLF and 100a LVF supply back on 0520hrs Private consumer OHM found faulty isolated and refered to contractor | June | 2018 | 2018Q4 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | Unknown | Unknown | 2018-06-05 | N | 114 | N | 7 | N | N | 1.1101 | 39.4971 | 83.3078
[7 empty] | 7484 | 5112 | 1575093 | 2018-06-05 07:02 | 2018-06-05 07:53 | 51 | 11kV | 459 | 9 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn384 Camperdown (11kV) - Pnl.66 tripped on: O/C & E/F Front line UG section of feeder failed. | June | 2018 | 2018Q4 | 2018 | ZN384:PA66 | ZN384:PA66 | ZN00384/000066 | SYDNEY | UG | Not Veg | 2018-06-05 | N | 51 | N | 7 | N | N | 1.1101 | 39.4971 | 335.4237
[7 empty] | 8056 | 11890 | 1575223 | 2018-06-05 14:34 | 2018-06-05 15:55 | 81 | 11kV | 78325 | 1952 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn9035 Caringbah - Pnl.4 tripped/ reclosed/ locked out on: A Phase IOC Abnormal: S9203 (Sw/B) closed with S9283 (Sw/B) and AB35309 Open. Broken Cross arm in Cawarra Rd near Captain Cook Dr. Section of 11kV between S9192 (Sw/B) to AB35376 tee PT9105. See 1575490 1575491 1575492 | June | 2018 | 2018Q4 | 2018 | ZN9035:PA4 | ZN9035:PA4 | ZN09035/000004 | SUTHERLAND | OH | Not Veg | 2018-06-05 | N | 40.1255 | N | 7 | N | N | 1.1101 | 39.4971 | 57237.5998
[7 empty] | 8108 | 12603 | 1575282 | 2018-06-05 17:11 | 2018-06-05 17:49 | 38 | 11kV | 2888 | 76 | HV | Vegetation Blow/Fall In | Vegetation | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn14891 Wyong Ex Pa8 RE48425 Kangy Angy tripped, reclosed, trrpped and locked out on overcurrent Cause: tree branch contact other Stick removed by DOp adj PT14879. no apparent damage CC1: 22-"Refer to SOp" | June | 2018 | 2018Q4 | 2018 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2018-06-05 | N | 38 | N | 7 | N | N | 1.1101 | 39.4971 | 2110.4652
[7 empty] | 7828 | 9037 | 1575273 | 2018-06-05 17:05 | 2018-06-05 18:50 | 105 | 11kV | 4155 | 46 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 187044 ABS broke. Unable to open 1ph of ABS, without Live Line assistance. Part of SI 27365. Excluded OMS 1575273, 1575274 | June | 2018 | 2018Q4 | 2018 | 512:48046 | 512:83736 | ZN00512/083736 | CESSNOCK | OH | Not Veg | 2018-06-05 | N | 90.3261 | N | 7 | N | N | 1.1101 | 39.4971 | 3036.3514
[7 empty] | 8581 | 18600 | 1575495 | 2018-06-05 16:35 | 2018-06-05 19:55 | 200 | 11kV | 20797 | 107 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | UGOH | Unplanned | No Weather Impact | N | Zn9035 Caringbah - Pnl.4 -Section of 11kV feeder from S9797 (Sw/B) interrupted for safety. PT9504 , S9472 7 S9192 interrupted due to abnormal switching below. Abnormal: S9192 (Sw/B) to AB35376 tee PT9105 (in LV//) out of service from previous outage. UGOH bond beyond S9797 (Sw/B) found haning very low. See 1575495 1575496 | June | 2018 | 2018Q4 | 2018 | ZN9035:PA4 | ZN9035:PA4 | ZN09035/000004 | SUTHERLAND | OH | Not Veg | 2018-06-05 | N | 194.3645 | N | 7 | N | N | 1.1101 | 39.4971 | 15197.8342
[7 empty] | 7311 | 2375 | 1575317 | 2018-06-05 18:29 | 2018-06-05 22:35 | 246 | 11kV | 30012 | 122 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Radial section of 11kV feeder out of service from REC35078 Maianbar to LB35391. (D/R426920 A/1) S9451, S50281 & S49687 running in LV parallel with 2 x MG connected. 1 MG tripped off causing low volts to customers. | June | 2018 | 2018Q4 | 2018 | ZN9118:PA3 | ZN9118:PA3 | ZN09118/000003 | SUTHERLAND | Unknown | Unknown | 2018-06-05 | N | 246 | N | 7 | N | N | 1.1101 | 39.4971 | 21931.8844
[7 empty] | 8467 | 17237 | 1575368 | 2018-06-06 02:46 | 2018-06-06 04:30 | 104 | 11kV | 122471 | 1252 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn3922 Drummoyne 11kv feeder Panel No: 13 "Formosa Day No1" feeder tripped on: Relays: C phase O/C trip, EFI, fault check Field EFIs: S65610, S65611 Remarks: UG fault. UG cable fault in 11kv feeder from S65611 Formosa Day No2 (SwB) to S49764 Sorrie Booth (Sw/A) to S1464 Fitzroy Ave (Sw/A) | June | 2018 | 2018Q4 | 2018 | ZN3922:PA13 | ZN3922:PA13 | ZN03922/000013 | INNER WEST | UG | Not Veg | 2018-06-06 | N | 97.8203 | N | 3 | N | N | 1.1101 | 39.4971 | 89498.1945
[7 empty] | 8635 | 19285 | 1575541 | 2018-06-06 14:39 | 2018-06-06 16:21 | 102.15 | 11kV | 2247.3 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S36000 Olympic Park 11kv C busbar from B-C bus section to C-D bus section to Tx2 2C cb to P12 the olympic park no.2 aux fdr tripped on 11kv bus zn 3 prot panel busbar prot b, IOC - a phase trip, e/f trip, b prot trip tr 1b, tr 2b Remarks: 11kv tx2 2c cb open, b-c bus sect cb closed Remarks: cause not ascertained. PE to investigate. | June | 2018 | 2018Q4 | 2018 | ZN36000:PA12 | ZN36000:PA12 | ZN36000/000012 | PARRAMATTA | OH | Veg | 2018-06-06 | N | 102.15 | N | 3 | N | N | 1.1101 | 39.4971 | 1642.2606
[7 empty] | 8218 | 13971 | 1575634 | 2018-06-06 18:48 | 2018-06-06 22:00 | 192 | 11kV | 23424 | 122 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Rain Heavy | N | (Ex Pa3 Zn9118 Cronulla Zone) Radial feeder from S9451 Pacific Maianbar No.2 is deenergised with 3 subs in LV // with 2 x Agrekko generator running unmanned Abnormal: 11kv feeder oos from rec 35078 Maianbar to LB35391 tee Sw/A @ S9451 Pacific Maianbar no.2 (with S9451, S50281, S49687 running in LV//, with 2x MG sets) Remarks: MG set tripped off. D&R #426920A/1 Cronulla to replace river crossing from Cronulla - Maianbar , radial section of feeder running on 2x Aggrekko MG syncd to network. 1 MG tripped off. Called Aggrekko technician who was on his way out to site already | June | 2018 | 2018Q4 | 2018 | ZN9118:PA3 | ZN9118:PA3 | ZN09118/000003 | SUTHERLAND | Unknown | Unknown | 2018-06-06 | N | 192 | N | 3 | N | N | 1.1101 | 39.4971 | 17117.5683
[7 empty] | 7432 | 4298 | 1575807 | 2018-06-07 15:24 | 2018-06-07 16:24 | 60 | 11kV | 60 | 1 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 187074 Single Phase Repair broken stay wire at sub pole DN-10162 | June | 2018 | 2018Q4 | 2018 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2018-06-07 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 7241 | 1110 | 1575905 | 2018-06-07 19:54 | 2018-06-07 21:10 | 76 | 11kV | 124142 | 1707 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 39 tripped on SEL Signals: 11kV Trip Field EFI's - Nil Cause: AB1164 is defective See OMS 1576652 1576653 1575905 1575907 | June | 2018 | 2018Q4 | 2018 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Not Veg | 2018-06-07 | N | 72.7252 | N | 3 | N | N | 1.1101 | 39.4971 | 90719.312
[7 empty] | 7259 | 1390 | 1575927 | 2018-06-07 23:31 | 2018-06-08 01:11 | 100 | 11kV | 128460 | 1466 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36800 Waverley - Pnl.49 tripped on: Earth Fault, EFI Field EFIs: S7971 S4507 S48628 S7207 S35303 UG cable fault between S35303 (Sw.B) and S8831 (Sw.A) See 1576486 1576487 | June | 2018 | 2018Q4 | 2018 | ZN36800:PA49 | ZN36800:PA49 | ZN36800/000049 | WAVERLEY | UG | Not Veg | 2018-06-07 | N | 87.6262 | N | 3 | N | N | 1.1101 | 39.4971 | 93874.7791
[7 empty] | 7849 | 9335 | 1576037 | 2018-06-08 14:14 | 2018-06-08 17:15 | 181 | 11kV | 362 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S568 Tech College No.1 - 11kV Sw/A, Tx No1, Tx No2 & Tx No3 found tripped on: IT Send, A & B phase Diff relay. Tx No.3 appears to have failed. | June | 2018 | 2018Q4 | 2018 | ZN901:PA10 | ZN901:PA10 | ZN00901/000010 | SYDNEY | UG | Not Veg | 2018-06-08 | N | 181 | N | 2 | N | N | 1.1101 | 39.4971 | 264.5389
[7 empty] | 7401 | 3861 | 1576097 | 2018-06-08 20:47 | 2018-06-08 21:53 | 66 | 11kV | 121110 | 1835 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN3922 Drummoyne 11kv feeder Panel No.7 "Hampden Coralie" feeder tripped on Relays: A phase O/C, E/F Field EFI's: Nil Remarks: UG fault. Section of 11kv feeder from Zn3922 Drummoyne Panel No.7 to S3713 Hampden Coralie (Sw/A) to S1666 Gartfern Ave (Sw/B) Note: S3713 is HAZ RMI, LV// required to extend ISOLATION | June | 2018 | 2018Q4 | 2018 | ZN3922:PA7 | ZN3922:PA7 | ZN03922/000007 | CANADA BAY | UG | Not Veg | 2018-06-08 | N | 66 | N | 2 | N | N | 1.1101 | 39.4971 | 88503.6159
[7 empty] | 8018 | 11299 | 1576234 | 2018-06-10 06:01 | 2018-06-10 12:45 | 404 | 11kV | 2392 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 187091 A Phase HV Wire down pole DJ10018 Excluded OMS 1576234 & 1576243 | June | 2018 | 2018Q4 | 2018 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2018-06-10 | N | 299 | N | 2 | N | N | 1.1101 | 39.4971 | 1748.003
[7 empty] | 7922 | 10161 | 1576274 | 2018-06-10 13:31 | 2018-06-11 01:05 | 694 | 11kV | 81889 | 281 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 187093/02 2 fault operations B Phase Earth Fault 11kV into LV & pole fire at pole IV-70525 Excluded OMS 1576274 | June | 2018 | 2018Q4 | 2018 | 224:80332 | 224:80332 | ZN00224/080332 | LAKE MACQUARIE | OH | Not Veg | 2018-06-10 | N | 291.4199 | N | 2 | N | N | 1.1101 | 39.4971 | 59842.0659
[7 empty] | 7511 | 5511 | 1576478 | 2018-06-12 08:41 | 2018-06-12 11:10 | 149 | 11kV | 1341 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge Ex Pa8 PT13500 barnes George Downe 0.6 10Amp HDO blown on footpath phase Cause: not ascertained See 1576963 ex 1576478 1576561 | June | 2018 | 2018Q4 | 2018 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2018-06-12 | N | 149 | N | 1 | N | N | 1.1101 | 39.4971 | 979.9632
[7 empty] | 8524 | 17893 | 1577019 | 2018-06-14 12:38 | 2018-06-14 16:20 | 222 | 11kV | 7386 | 113 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12600 Lisarow Ex pa2 "Chamerlain taylor 0.1 RE41020 Wattle Tree Raod North opened, Reclosed, Opened & Locked out Cause: tree/branch brought down oh Wattle Tree rd & Patterson Close See 1577183,4,5 ex 1577019,26,9 | June | 2018 | 2018Q4 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2018-06-14 | N | 65.3628 | N | 3 | N | N | 1.1101 | 39.4971 | 5397.4709
[7 empty] | 8300 | 14985 | 1576992 | 2018-06-14 10:39 | 2018-06-14 20:30 | 591.2667 | 11kV | 21876.8667 | 37 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Panel 2 from Zn15002 Narrabeen Section Of Panel Beyond LB25608 Interrupted Cause: Interrupted to allow emergency repair @ LB25609 | June | 2018 | 2018Q4 | 2018 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Not Veg | 2018-06-14 | N | 591.2667 | N | 3 | N | N | 1.1101 | 39.4971 | 15986.9689
[7 empty] | 7806 | 8783 | 1577113 | 2018-06-14 21:07 | 2018-06-14 21:45 | 38 | 11kV | 38 | 1 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 187128 Dead possum found. Tx volts - 243V Excluded OMS 1577113 | June | 2018 | 2018Q4 | 2018 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2018-06-14 | N | 38 | N | 3 | N | N | 1.1101 | 39.4971 | 27.7693
[7 empty] | 8639 | 19376 | 1577139 | 2018-06-15 07:52 | 2018-06-15 13:10 | 318 | 11kV | 954 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge Ex Pa11 PT11757 Silvester Wiseferry 0.3 11kV phase HDO was found to have operated Cause: not ascertained | June | 2018 | 2018Q4 | 2018 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2018-06-15 | N | 318 | N | 3 | N | N | 1.1101 | 39.4971 | 697.1551
[7 empty] | 7439 | 4519 | 1577235 | 2018-06-15 13:28 | 2018-06-15 19:00 | 332 | 11kV | 3953 | 29 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 187145 Burnt off tapping pole FR-74767 Excluded OMS 1577235 | June | 2018 | 2018Q4 | 2018 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2018-06-15 | N | 136.3103 | N | 3 | N | N | 1.1101 | 39.4971 | 2888.7358
[7 empty] | 8510 | 17711 | 1577192 | 2018-06-15 10:51 | 2018-06-15 19:21 | 509.5333 | 11kV | 18852.7333 | 37 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | section of panel 2 "rickard anana" feeder beyond AB 25608 interupted to effect emergency repairs to pole (Note: restoration time not provided on Blue outage from. Restoration time based on Job Log) | June | 2018 | 2018Q4 | 2018 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Not Veg | 2018-06-15 | N | 509.5333 | N | 3 | N | N | 1.1101 | 39.4971 | 13777.0215
[7 empty] | 8582 | 18607 | 1577352 | 2018-06-16 08:19 | 2018-06-16 11:25 | 186 | 11kV | 1302 | 7 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 187147 Stay wire broken pole DP-30883 Excluded OMS 1577352 | June | 2018 | 2018Q4 | 2018 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2018-06-16 | N | 186 | N | 2 | N | N | 1.1101 | 39.4971 | 951.4632
[7 empty] | 7823 | 8980 | 1577434 | 2018-06-16 17:31 | 2018-06-16 19:20 | 109 | 11kV | 12571.1667 | 116 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Transformer | Unplanned | No Weather Impact | N | S4865 Odonnel Ave "B" phase LV tx tail burnt. Tx is isolated and earthed, with switching tag in place. Customers restored by LV parallels. LV parallels 17195, 19651, 9460, 4758, 12640 | June | 2018 | 2018Q4 | 2018 | ZN1285:PA33 | ZN1285:PA33 | ZN01285/000033 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-06-16 | N | 108.3721 | N | 2 | N | N | 1.1101 | 39.4971 | 9186.6378
[7 empty] | 7715 | 7618 | 1577468 | 2018-06-17 07:34 | 2018-06-17 09:25 | 111 | 11kV | 111 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 187151 Single phase broken LLC dropper Excluded oms 1577468 | June | 2018 | 2018Q4 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-06-17 | N | 111 | N | 4 | N | N | 1.1101 | 39.4971 | 81.1155
[7 empty] | 7398 | 3822 | 1577487 | 2018-06-17 10:40 | 2018-06-17 11:40 | 60 | 11kV | 3840 | 64 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 187155 A Phase DOLF : 40 Amp | June | 2018 | 2018Q4 | 2018 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Veg | 2018-06-17 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 2806.1587
[7 empty] | 7562 | 5974 | 1577970 | 2018-06-17 11:36 | 2018-06-17 12:22 | 46 | 11kV | 46 | 1 | HV | Customer Installation Fault | Customer Installation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 187156 1 fault operation Single phase Earth Fault | June | 2018 | 2018Q4 | 2018 |  |  |  | SINGLETON | Unknown | Unknown | 2018-06-17 | N | 46 | N | 4 | N | N | 1.1101 | 39.4971 | 33.6154
[7 empty] | 7189 | 164 | 1577584 | 2018-06-18 02:04 | 2018-06-18 03:50 | 106 | 11kV | 1886 | 35 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9037 Miranda - Pnl.17 tripped onL Earth fault with EFI Field EFIs: NIL UG cable fault from S9080 (Sw/D) to S9078 (Sw/F)-Normally Open Note: EFI @ S9081 did not operate & no EFI on S9080. See 1577907 1577908 | June | 2018 | 2018Q4 | 2018 | ZN9037:PA17 | ZN9037:PA17 | ZN09037/000017 | SUTHERLAND | UG | Not Veg | 2018-06-18 | N | 53.8857 | N | 5 | N | N | 1.1101 | 39.4971 | 1378.2332
[7 empty] | 7875 | 9658 | 1577586 | 2018-06-18 02:46 | 2018-06-18 03:54 | 68 | 11kV | 82144 | 1208 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn15001 Brookvale Pa6 "Windbourne rd" tripped Relays: Pa6L: IOC (B+C phase), EFI, Frame leakage Signals 11kv trip, CB6 open EFI's: S16892 S15189 S16948 S61988 S16636 S16816 S50675 S16933 Cause: Possum below 11kv ugoh beyond SwB@S16933 Burne Mooramba | June | 2018 | 2018Q4 | 2018 | ZN15001:PA6 | ZN15001:PA6 | ZN15001/000006 | NORTHERN BEACHES | OH | Not Veg | 2018-06-18 | N | 68 | N | 5 | N | N | 1.1101 | 39.4971 | 60028.4124
[7 empty] | 8235 | 14264 | 1577583 | 2018-06-18 01:55 | 2018-06-18 07:55 | 360 | 11kV | 164520 | 457 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn15011 Beacon Hill Ex Pa4 "Warringah Rd Oxford Falls" Bond Burnt off HV bond between S4667SwA and tee off. See 1578039 ex 1577583 | June | 2018 | 2018Q4 | 2018 | ZN15011:PA4 | ZN15011:PA4 | ZN15011/000004 | NORTHERN BEACHES | OH | Not Veg | 2018-06-18 | N | 360 | N | 5 | N | N | 1.1101 | 39.4971 | 120226.3635
[7 empty] | 8396 | 16282 | 1577580 | 2018-06-17 21:22 | 2018-06-18 10:44 | 802 | 11kV | 7218 | 9 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn14891 Wyong Ex Pa20 "Warnervale West Railway" RE45203 Butt Gas Generator tripped on: trip & lockout Cause: Bond Comments: RE47302 Hue Hue Sparks 0.1 open for safety/repair @2328 Switching Tad @ RE47302 Open Bond @ Pole DD449 | June | 2018 | 2018Q4 | 2018 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2018-06-17 | N | 802 | N | 4 | N | N | 1.1101 | 39.4971 | 5274.7015
[7 empty] | 8319 | 15172 | 1577651 | 2018-06-18 09:50 | 2018-06-18 14:00 | 250 | 11kV | 3750 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 187165 A Phase Aph LL clamp lead broken to DOLF. Excluded OMS No. 1577651 | June | 2018 | 2018Q4 | 2018 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-06-18 | N | 250 | N | 5 | N | N | 1.1101 | 39.4971 | 2740.3894
[7 empty] | 7518 | 5547 | 1577826 | 2018-06-18 18:22 | 2018-06-18 21:15 | 173 | 11kV | 15051 | 87 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Zn180 Mosman Ex Pa10 "Mandalong Military" S8225 Thompson Ruby HV fuse operated B phase 40Amp Tyre QFRN Cause: HV fuse operated. DOp patrolled dist and inspected TX @ S8225 no cause ascertained. See 1578056 ex 1577828 1577826 | June | 2018 | 2018Q4 | 2018 | ZN180:PA10 | ZN180:PA10 | ZN00180/000010 | MOSMAN | OH | Veg | 2018-06-18 | N | 173 | N | 5 | N | N | 1.1101 | 39.4971 | 10998.8269
[7 empty] | 7184 | 136 | 1577885 | 2018-06-19 07:28 | 2018-06-19 09:00 | 92 | 11kV | 184 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 187169 DOLF : 10 Amp Excluded OMS 1577885 | June | 2018 | 2018Q4 | 2018 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2018-06-19 | N | 92 | N | 6 | N | N | 1.1101 | 39.4971 | 134.4618
[7 empty] | 8195 | 13689 | 1578002 | 2018-06-19 12:38 | 2018-06-19 18:55 | 377 | 11kV | 8416 | 113 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12600 Lisarow ex Pa2 RE41020 Wattle Tree Rd North tripped on earth fault Cause: tree/branch brought down oh 11kV wires down from LB45186 to AB44336 tee PT64478 Patterson Wattle tree See 1578932,4,5 ex 1578002,3,33 | June | 2018 | 2018Q4 | 2018 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2018-06-19 | N | 74.4779 | N | 6 | N | N | 1.1101 | 39.4971 | 6150.1646
[7 empty] | 7732 | 7809 | 1578097 | 2018-06-19 16:00 | 2018-06-19 19:48 | 228.2667 | 11kV | 18261.3333 | 80 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 187173 B Phase DOLF : 40 Amp HV dropper to tx arcing to LV bundle conductor. To be repaired under AP. Left in LV//. V = 229 with HWC pump running. W/O 1300094654 | June | 2018 | 2018Q4 | 2018 | 258:80775 | 258:80775 | ZN00258/080775 | NEWCASTLE | OH | Not Veg | 2018-06-19 | N | 228.2667 | N | 6 | N | N | 1.1101 | 39.4971 | 13344.8438
[7 empty] | 7759 | 8153 | 1578129 | 2018-06-19 17:06 | 2018-06-19 20:20 | 194 | 11kV | 98835 | 856 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | Zn12600 Lisarow Panel 13 "Bursh Rd" tripped on Relays: B&C phase timed O/C Singals: 11kv trip EFI's: Nil Cause: tree/branch brought down OH Tree on the 33kV then into the 11kV panel 13. See interruption on 33kV 799 fdr tripped at the sametime See 1578936,8 ex 1578129,47,205 | June | 2018 | 2018Q4 | 2018 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2018-06-19 | N | 115.4614 | N | 6 | N | N | 1.1101 | 39.4971 | 72225.7029
[7 empty] | 8323 | 15210 | 1578208 | 2018-06-19 19:16 | 2018-06-19 22:30 | 194 | 11kV | 234533 | 1382 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | Zn36200 Empire Bay Pa1 "Empire Bay Awinya" tripped and locked out Relays: IOC A & C phases, E/F left, Reclose and lock out and EFI Signals: trip Alarm EFI's: S50257, UGOH EFI's damaged Cause: weather related PT12286 Awinya Empire bay two HDO's operated, TX requires testing (100kva) Also defective 11kv bonds from ABC to Bare copper beyond AB44616 See 1578949,50,1,2 ex 1578208 | June | 2018 | 2018Q4 | 2018 | ZN36200:PA1 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2018-06-19 | N | 169.7055 | N | 6 | N | N | 1.1101 | 39.4971 | 171389.7988
[7 empty] | 8449 | 17012 | 1578184 | 2018-06-19 18:57 | 2018-06-19 23:35 | 278 | 11kV | 37530 | 135 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At PT1562 Landra Annabelle - Footpath phase 31.5k HDO blown Suspected lightning strike Based on Customer calls - suspect distributor 2 @ PT2233 iws in LV parallel with PT1562 See OMS 1578440 1578442 1578184 1578199 | June | 2018 | 2018Q4 | 2018 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Not Veg | 2018-06-19 | N | 278 | N | 6 | N | N | 1.1101 | 39.4971 | 27425.8171
[7 empty] | 7553 | 5845 | 1578573 | 2018-06-21 04:01 | 2018-06-21 06:55 | 174 | 11kV | 20532 | 118 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | Zn15008 Harbord Ex Pa9L "Soldiers Av" fdr 11kV link 24902 HR footpath phase Cause: Underslung Links LK24902 High Resistance footpath phase. being replaced See 1578958 ex 1578573,9 | June | 2018 | 2018Q4 | 2018 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Not Veg | 2018-06-21 | N | 174 | N | 4 | N | N | 1.1101 | 39.4971 | 15004.18
[7 empty] | 7706 | 7517 | 1578575 | 2018-06-21 04:37 | 2018-06-21 12:00 | 443 | 11kV | 195152 | 1605 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | No Weather Impact | N | LID 187193 1 fault operation A and C O/C RH LVF 52475 3 x 315A fuses. Truck hit pole FS-82483 Excluded oms 1578575 | June | 2018 | 2018Q4 | 2018 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2018-06-21 | N | 121.59 | N | 4 | N | N | 1.1101 | 39.4971 | 142611.3256
[7 empty] | 8665 | 19660 | 1578734 | 2018-06-21 12:20 | 2018-06-21 14:00 | 100 | 11kV | 100 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 187201 substation DOLF Excluded OMS 1578734 | June | 2018 | 2018Q4 | 2018 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2018-06-21 | N | 100 | N | 4 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 7490 | 5187 | 1578797 | 2018-06-21 15:24 | 2018-06-21 16:00 | 36.4333 | 11kV | 109.3 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 187202 Repair stranded conductor pole MD-90780 | June | 2018 | 2018Q4 | 2018 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2018-06-21 | N | 36.4333 | N | 4 | N | N | 1.1101 | 39.4971 | 79.8732
[7 empty] | 7644 | 6740 | 1578882 | 2018-06-22 02:04 | 2018-06-22 03:36 | 92 | 11kV | 92984 | 1018 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | S10994 Mortdale Panel 19L "Roberts Fairway No.1" fdr tripped, reclosed, tripped and locked out Relays: B and C phase overcurrent, EFI, Reclose Timer, Lockout Signals - 11kv trip, Tx3 Group Earth Remarks: cause not ascertained. Dop patrolled but could not find a cause | June | 2018 | 2018Q4 | 2018 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Veg | 2018-06-22 | N | 91.3399 | N | 3 | N | N | 1.1101 | 39.4971 | 67949.9646
[7 empty] | 8274 | 14632 | 1578922 | 2018-06-22 09:17 | 2018-06-22 10:40 | 83 | 11kV | 5312 | 64 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 187205 A Phase DOLF : 40 Amp Load. LH RH. A 50,45. B 44,40. C 50, 45 Volts 245v DOPs fibre glass Dolf replaced with new one. Excluded oms 1578922, 1578923, 1578929, 1578943 | June | 2018 | 2018Q4 | 2018 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Veg | 2018-06-22 | N | 83 | N | 3 | N | N | 1.1101 | 39.4971 | 3881.8529
[7 empty] | 8137 | 13046 | 1579005 | 2018-06-22 14:27 | 2018-06-22 16:19 | 112 | 11kV | 39088 | 349 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn1850 Bass Hill Panel 11 "Georgina St" tripped on Relays: A phase IOC and EFI Signals: 11kv Abnormal: Sw/B closed @ S36110, Sw/A Open @ S78785 Remarks: UGOH fault short circuit. Zn1850 Bass Hill Panel 11 to LB 3063 UGOH defective | June | 2018 | 2018Q4 | 2018 | ZN1850:PA11 | ZN1850:PA42 | ZN01850/000042 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2018-06-22 | N | 112 | N | 3 | N | N | 1.1101 | 39.4971 | 28564.3575
[7 empty] | 8534 | 18003 | 1579202 | 2018-06-23 20:57 | 2018-06-24 01:32 | 275 | 11kV | 7118 | 196 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 187218 Trip & Reclose 1 fault operation Overcurrent trip and reclose - then interrupted to repair blown off tapping at ABS 43759. Excluded oms1579202 | June | 2018 | 2018Q4 | 2018 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2018-06-23 | N | 36.3163 | N | 1 | N | N | 1.1101 | 39.4971 | 5201.6245
[7 empty] | 7402 | 3863 | 1579266 | 2018-06-24 14:09 | 2018-06-24 14:40 | 31 | 11kV | 410 | 17 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | ZN167 Auburn Panel 8 "Parramatta John" tripped on Relays: OC EFI and fault check Signals: 11kv trip, Tx 3 Group earth Remarks: end box fault. @ S6693 Silverwater Fariola Sw/A endbox damaged HR | June | 2018 | 2018Q4 | 2018 | ZN167:PA8 | ZN167:PA8 | ZN00167/000008 | PARRAMATTA | UG | Not Veg | 2018-06-24 | N | 24.1176 | N | 2 | N | N | 1.1101 | 39.4971 | 299.6159
[7 empty] | 7762 | 8242 | 1579312 | 2018-06-24 19:02 | 2018-06-24 21:20 | 138 | 11kV | 67631 | 657 | HV | Overload LV Parallel | Utility Process Issue | O/H Link | Unplanned | Cold <10C | N | Zn180 Mosman Ex Pa35 "S35148 Belgrave Cooper Feeder" S646 Grasmere Rd - Transformers was isolated with LV Board in LV// for maintenance Cause: LV parallel failure See 425308A/1 HV+LV Cb maintenances. High Loads due to cold weather. LV// collpase. Other subs affected. LV//'s that were in #4057 (S2461 D2) #12553 (S5588 D1) @11279 (S1590 D1) #7743 (S4894 D3) See 1579455,6,7,8,9 ex 1579312,36 | June | 2018 | 2018Q4 | 2018 | ZN180:PA35 | ZN180:PA35 | ZN00180/000035 | NORTH SYDNEY | OH | Not Veg | 2018-06-24 | N | 102.9391 | N | 2 | N | N | 1.1101 | 39.4971 | 49422.74
[7 empty] | 8621 | 19125 | 1579557 | 2018-06-25 17:16 | 2018-06-25 19:35 | 139 | 11kV | 180635 | 1345 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10990 Arncliffe - Pnl.7 tripped, reclosed and locked out on: Earth Fault with EFI Field EFIs; NIL UG cable fault in front line section of feeder from Pnl.7 to LB62006 to S48227 (Sw/A) See 1579653 1579654 GIS 1579547 | June | 2018 | 2018Q4 | 2018 | ZN10990:PA7 | ZN10998:PA18 | ZN10998/000018 | BAYSIDE | UG | Not Veg | 2018-06-25 | N | 134.3011 | N | 1 | N | N | 1.1101 | 39.4971 | 132002.7302
[7 empty] | 7499 | 5379 | 1579689 | 2018-06-26 11:40 | 2018-06-26 13:35 | 115 | 11kV | 575 | 5 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 187256 3 phase interrupted by dop due to large tree contacting 11kV OHM at pole GV-70001. dq | June | 2018 | 2018Q4 | 2018 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2018-06-26 | N | 115 | N | 1 | N | N | 1.1101 | 39.4971 | 420.193
[7 empty] | 8463 | 17187 | 1579823 | 2018-06-27 05:57 | 2018-06-27 09:32 | 215 | 11kV | 125969 | 899 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 187260 Defective UGOH at pole IR-87035 Excluded OMS 1579823 | June | 2018 | 2018Q4 | 2018 | 238:34137 | 532:83301 | ZN00532/083301 | MAITLAND | Unknown | Unknown | 2018-06-27 | N | 140.1212 | N | 4 | N | N | 1.1101 | 39.4971 | 92054.4297
[7 empty] | 8711 | 20238 | 1579826 | 2018-06-27 06:37 | 2018-06-27 11:10 | 273 | 11kV | 114086 | 1324 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14143 Somersby Pa12 fdr CB tripped on: Relays: Overcurrent, Earth FAult, EFI, Fault Check Signals: 11kv trip EFI's: CP44663 S18442 S18171 S18495 Cause: UG Fault from AB40491 to USL43119 to tee S12394 MT Penang Pacific No4 See 1581163,5,7,8,9,70 ex 1579826,46 | June | 2018 | 2018Q4 | 2018 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | UG | Not Veg | 2018-06-27 | N | 86.1677 | N | 4 | N | N | 1.1101 | 39.4971 | 83370.6838
[7 empty] | 8549 | 18202 | 1579942 | 2018-06-27 11:43 | 2018-06-27 12:17 | 34.0833 | 11kV | 2113.1667 | 62 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Transformer | Unplanned | Rain Light | N | Zn4990 City Central - 51/52 "C" feeder tripped. Abnormal: 51C LV ACB @ S6785 Kent Liverpool No.2 Open for TPE restricted operating. Appears 51C Tx @ S6785 Differential relay blown on energising TX for return to service. See 1579942 1580121 | June | 2018 | 2018Q4 | 2018 | ZN4990:PA51 52ABC | ZN4990:PA51 52ABC | ZN04990/51 52ABC | SYDNEY | UG | Not Veg | 2018-06-27 | N | 34.0833 | N | 4 | N | N | 1.1101 | 39.4971 | 1544.2399
[7 empty] | 8264 | 14533 | 1580022 | 2018-06-27 15:39 | 2018-06-27 16:30 | 51 | 11kV | 61076 | 1423 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 187277 2 fault operations 3 phase Earth Fault A & C phase dolf blown sub 48650 Merdith Fullerton Fdr 7490 tripped on: Earth Fault Excluded OMS 1580022 | June | 2018 | 2018Q4 | 2018 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2018-06-27 | N | 42.9206 | N | 4 | N | N | 1.1101 | 39.4971 | 44632.5394
[7 empty] | 8244 | 14362 | 1580119 | 2018-06-28 08:08 | 2018-06-28 08:48 | 40 | 11kV | 41785 | 1116 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 187279 Earth Fault; Overcurrent pothead faulty pole AK-60684 Section isloated for repairs Excluded oms 1580119, 1580127 | June | 2018 | 2018Q4 | 2018 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | Unknown | Unknown | 2018-06-28 | N | 37.4418 | N | 3 | N | N | 1.1101 | 39.4971 | 30535.2456
[7 empty] | 8478 | 17375 | 1580180 | 2018-06-28 10:59 | 2018-06-28 11:38 | 39 | 11kV | 78232 | 2008 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 187283 2 fault operations B & C Phases Overcurrent magpie at pole JU-10478 protection = 50TBC Excluded oms 1580180 | June | 2018 | 2018Q4 | 2018 | 258:80775 | 258:80775 | ZN00258/080775 | NEWCASTLE | OH | Not Veg | 2018-06-28 | N | 38.9602 | N | 3 | N | N | 1.1101 | 39.4971 | 57169.6381
[7 empty] | 7905 | 9969 | 1580262 | 2018-06-28 15:09 | 2018-06-29 12:10 | 1261 | 11kV | 15663 | 53 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn12630 Peatsz Ridge Ex Pa1 RE44945 "Lower Mangrove" tripped & locked out (out of scan) Relays: SEF Cause: tree branch borught down OH near PT14543. Section of 11kV fdr from AB44079 to AB44077 tee PT12530 PT14543 is defective See 1581184,5,6,8 ex 1580262,366 | June | 2018 | 2018Q4 | 2018 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2018-06-28 | N | 295.5283 | N | 3 | N | N | 1.1101 | 39.4971 | 11446.0584
[7 empty] | 7581 | 6114 | 1580412 | 2018-06-29 10:39 | 2018-06-29 12:25 | 106 | 11kV | 61960 | 810 | HV | Excavation Ausgrid Staff | Utility Process Issue | U/G Cable | Unplanned | No Weather Impact | N | LID 187307 3 fault operation Earth Fault EF Right Hand side. 50TN Cable damaged by crew working adjacent. G Knipe advised. Possibley near UGOH pole JR-90533 Glenelg St Raymond Terrace. Excluded OMS 1580412 | June | 2018 | 2018Q4 | 2018 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | UG | Not Veg | 2018-06-29 | N | 76.4938 | N | 1 | N | N | 1.1101 | 39.4971 | 45278.5405
[7 empty] | 6118 | 9072 | 1580827 | 2018-07-02 10:19 | 2018-07-02 11:34 | 75 | 11kV | 78900 | 1126 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1195 Pymble 11kV Panel 4 tripped on Relays: Earth Fault, C phase OC, EFI and Fault Check Signals: 11kV Trip, TX2 Groupo Earth, Zone Earth Field EFI's NIL Section of 11kV defective from Zn195 Pa4 tpo S63697 to S1314 | July | 2018 | 2019Q1 | 2019 | ZN195:PA4 | ZN195:PA4 | ZN00195/000004 | KU-RING-GAI | UG | Not Veg | 2018-07-02 | N | 70.071 | N | 2 | N | N | 1.1101 | 39.4971 | 57657.7928
[7 empty] | 5668 | 4320 | 1581025 | 2018-07-02 20:05 | 2018-07-03 01:50 | 345 | 11kV | 386279 | 2648 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15008 harbord Pa7 "Curl Curl" tripped on Relays: SEF trip Signals: Zone Earth, trip alarm EFI's: Nil Cause: OH down 11kv OH down in foam st 11kv USL 22845 defective and to be replaced tonight S17028 Oliver Wyondora Dist 1 "Oliver st & Wyuna Ave" abc phase fuses failed due to lv parallel during fdr trip See 1581311,4,5,6,7,8 ex 1581025,7,8,9,30,47,8 | July | 2018 | 2019Q1 | 2019 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Veg | 2018-07-02 | N | 145.8758 | N | 2 | N | N | 1.1101 | 39.4971 | 282281.2999
[7 empty] | 6908 | 17658 | 1581056 | 2018-07-03 06:43 | 2018-07-03 08:10 | 87 | 11kV | 522 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 187332 A Phase DOLF : 63 Amp replaced broken fuse and carrier Excluded oms 1581056 | July | 2018 | 2019Q1 | 2019 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2018-07-03 | N | 87 | N | 4 | N | N | 1.1101 | 39.4971 | 381.4622
[7 empty] | 5769 | 5345 | 1581075 | 2018-07-03 09:03 | 2018-07-03 10:08 | 65 | 11kV | 80470 | 1238 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 187334 2 fault operations C phase Instantaneous Earth Fault NBN contractor drilled into U/G cable. Excluded OMS 1581075 | July | 2018 | 2019Q1 | 2019 | 270:83587 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | UG | Not Veg | 2018-07-03 | N | 65 | N | 4 | N | N | 1.1101 | 39.4971 | 58805.1025
[7 empty] | 6029 | 7906 | 1581083 | 2018-07-03 09:18 | 2018-07-03 10:36 | 78 | 11kV | 100892 | 1359 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN262 Marrickville - 11kv Panel No.31 "S7989 Ohara Calvert" feeder tripped Relays: EF, EFI, Fault check Signals: 11kv trip, zone earth, No.1 Group earth Remarks: 11kv UG fault from S8771 Marrickville Livingston to S63324 Livingston francis | July | 2018 | 2019Q1 | 2019 | ZN262:PA31 | ZN262:PA31 | ZN00262/000031 | INNER WEST | UG | Not Veg | 2018-07-03 | N | 74.2399 | N | 4 | N | N | 1.1101 | 39.4971 | 73728.8978
[7 empty] | 6112 | 8982 | 1581253 | 2018-07-03 22:33 | 2018-07-04 00:41 | 128 | 11kV | 896 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 187343 B Phase DOLF : 16 Amp Excluded OMS 1581253 | July | 2018 | 2019Q1 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2018-07-03 | N | 128 | N | 4 | N | N | 1.1101 | 39.4971 | 654.7704
[7 empty] | 6344 | 11371 | 1581255 | 2018-07-04 00:59 | 2018-07-04 02:05 | 66 | 11kV | 7854 | 119 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Zn14891 Wyong Ex Pa16 PT13606 Tuggerwong Cadonia C phase HDO 31.5 Fatigue Cause: Fuse Fatigue See 1581330 ex 1581255,6 | July | 2018 | 2019Q1 | 2019 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2018-07-04 | N | 66 | N | 3 | N | N | 1.1101 | 39.4971 | 5739.4715
[7 empty] | 5980 | 7267 | 1581350 | 2018-07-04 11:05 | 2018-07-04 13:02 | 117 | 11kV | 5767 | 71 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 187354 2 fault operations B & C phase John and Luke checked all hazard report locations as well as those given to them by the public in the street. No cause found, feeder was patrolled and put back in sections. Luke and John thanks for your help. Excluded OMS 1581350. 1581353, 1581358 7 1581364. | July | 2018 | 2019Q1 | 2019 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Veg | 2018-07-04 | N | 81.2254 | N | 3 | N | N | 1.1101 | 39.4971 | 4214.3535
[7 empty] | 6486 | 13130 | 1581486 | 2018-07-04 18:48 | 2018-07-04 20:42 | 114 | 11kV | 183084 | 1606 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At Zn10991 Blakehurst Panel #1 'Waterview Woids, etc' feeder has tripped/reclosed/tripped on: Signals: 11kv trip Relays: B phase, earth fault, reclose timing, reclose lockout, EFI Field EFI's: S10137 Remarks: possum on HV ugoh to s10313 Gnarbo Ave.(LV//s were still in from S10851 Mt Vernon Centre from earlier in the afternoon causing interruptions @ S62451 Joseph Empire Dist #4 & PT10338 Pacific Stuart Dist #2) | July | 2018 | 2019Q1 | 2019 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2018-07-04 | N | 114 | N | 3 | N | N | 1.1101 | 39.4971 | 133792.3871
[7 empty] | 6662 | 14942 | 1581523 | 2018-07-05 07:27 | 2018-07-05 09:17 | 110 | 11kV | 80138 | 1176 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 187365 1 fault operation B & C phase Overcurrent A Protection B & C trip, (Code BCT) B Protection B & C Overcurrent. Initial indications are that the auto reclose function may not have operated on Sw 83298. Cause was a magpie contacting the 11kV near pole IR-54123 Thursby St near Korbel St. Excluded OMS 1581523. | July | 2018 | 2019Q1 | 2019 | 532:83298 | 532:83298 | ZN00532/083298 | MAITLAND | OH | Not Veg | 2018-07-05 | N | 68.1446 | N | 2 | N | N | 1.1101 | 39.4971 | 58562.4867
[7 empty] | 6288 | 10768 | 1581691 | 2018-07-05 16:15 | 2018-07-05 18:30 | 135 | 11kV | 1080 | 8 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 187375 C Phase DOLF : 40 Amp Surge arrestor and fuse blew. sub isolated to replace c phase arrestor Excluded OMS 1581691 | July | 2018 | 2019Q1 | 2019 | 532:83298 | 532:83298 | ZN00532/083298 | MAITLAND | OH | Not Veg | 2018-07-05 | N | 135 | N | 2 | N | N | 1.1101 | 39.4971 | 789.2321
[7 empty] | 6613 | 14475 | 1582357 | 2018-07-06 10:08 | 2018-07-06 10:15 | 7 | 11kV | 7 | 1 | HV | Customer Installation Fault | Customer Installation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 187378 Overcurrent Garry Thompson from Liddell Control Room requested to Close Sw 43764 | July | 2018 | 2019Q1 | 2019 |  |  |  | SINGLETON | Unknown | Unknown | 2018-07-06 | N | 7 | N | 5 | N | N | 1.1101 | 39.4971 | 5.1154
[7 empty] | 6878 | 17311 | 1581840 | 2018-07-06 13:17 | 2018-07-06 15:56 | 159 | 11kV | 160669 | 1361 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn4545 Meadowbank Panel 4 tripped on: Relays: EF, EFI & Fault Check Signals: 11kv trip, Tx1 Gruop Earth, Zone Earth EFI" S4401 S2147 S5300 S5264 Cause: UG cable damaged by contractor from S5264 to S2115 to S35596. Contractor hit feeder outside 547 victoria rd. Contractor details: Telstra/Visionstream. LE Serve - David Wilson Ph: 86783281 See 1583170,2,4 ex 1581840,50,940 | July | 2018 | 2019Q1 | 2019 | ZN4545:PA4 | ZN4545:PA4 | ZN04545/000004 | RYDE | UG | Not Veg | 2018-07-06 | N | 118.0522 | N | 5 | N | N | 1.1101 | 39.4971 | 117412.1663
[7 empty] | 6445 | 12620 | 1581888 | 2018-07-06 15:08 | 2018-07-06 16:05 | 57 | 11kV | 73986 | 1298 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills -Panel 33 tripped, reclosed, tripped and locked out on Relays: Cphase IOC, Earth Fault, EFI and Lockout and Timing Signals: 11kV tip Field EFI's NIL Cause: Tree branch on 11kV OH outside 55 Laurence Street | July | 2018 | 2019Q1 | 2019 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Veg | 2018-07-06 | N | 57 | N | 5 | N | N | 1.1101 | 39.4971 | 54066.7866
[7 empty] | 6484 | 13119 | 1581968 | 2018-07-06 23:20 | 2018-07-07 00:55 | 95 | 11kV | 35613 | 675 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 187389 2 fault operations 3 phase DOLF :40 Amp B ph DOLF 16302 blew but did not drop - caught fire. Faulty tx 16302. Excluded OMS 1581968 & 1581970 | July | 2018 | 2019Q1 | 2019 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2018-07-06 | N | 52.76 | N | 5 | N | N | 1.1101 | 39.4971 | 26024.93
[7 empty] | 6096 | 8722 | 1582053 | 2018-07-07 15:30 | 2018-07-07 16:55 | 85 | 11kV | 85 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge Ex Pa10 PT14896 Peats Ridge Euloo 0.2 DOp isolated HDO's for safety Cause: Tree/Branch on OH mains. DOp and lineowker made safe See 1583098 ex 1582051,3 | July | 2018 | 2019Q1 | 2019 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2018-07-07 | N | 85 | N | 5 | N | N | 1.1101 | 39.4971 | 62.1155
[7 empty] | 6524 | 13629 | 1582100 | 2018-07-07 18:10 | 2018-07-07 18:45 | 35 | 11kV | 140 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 187396 Wire off pin Excluded OMS 1582100 | July | 2018 | 2019Q1 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2018-07-07 | N | 35 | N | 5 | N | N | 1.1101 | 39.4971 | 102.3079
[7 empty] | 6051 | 8165 | 1582034 | 2018-07-07 11:38 | 2018-07-07 20:00 | 502 | 11kV | 6156 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 187393 A & B Phase DOLF : 5 Amp tree fallen on ohm mains. Excluded oms 1582034, 1582036. | July | 2018 | 2019Q1 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2018-07-07 | N | 342 | N | 5 | N | N | 1.1101 | 39.4971 | 4498.6232
[7 empty] | 7131 | 19787 | 1582078 | 2018-07-07 15:26 | 2018-07-07 22:25 | 419 | 11kV | 112898 | 1351 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14891 Wyong Ex Pa16 "Wadalba" fdr RE40118 Murrawal Kilpa 0.2 tripped on overcurrent Signals: Tx2 Group Earth Cause: Tree/Branch on OH Mains. Broken LV and HV Crossarm See 1583092,3,4,6 ex 1582078,108,31 | July | 2018 | 2019Q1 | 2019 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Veg | 2018-07-07 | N | 83.5662 | N | 5 | N | N | 1.1101 | 39.4971 | 82502.5285
[7 empty] | 6316 | 11060 | 1582212 | 2018-07-08 14:16 | 2018-07-08 16:10 | 114 | 11kV | 1756 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12650 West Gosford Ex Pa1 "Dog Trap Rd" RE45010 Palm Grove tripped, reclosed and locked out on timed o/c Cause: not ascertained. feeder patrolled by DOp See 1583100,1 ex 1582212 | July | 2018 | 2019Q1 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2018-07-08 | N | 97.5556 | N | 2 | N | N | 1.1101 | 39.4971 | 1283.233
[7 empty] | 6748 | 15534 | 1582273 | 2018-07-08 23:25 | 2018-07-09 00:50 | 85 | 11kV | 3910 | 46 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Cold <10C | N | Zn12620 Noraville Ex Pa10 PT14385 Scenic Laelana Blown HDO 31.5 A phase roadside Cause: Fuse Fatigue See 1583102 ex 1582273 | July | 2018 | 2019Q1 | 2019 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Not Veg | 2018-07-08 | N | 85 | N | 2 | N | N | 1.1101 | 39.4971 | 2857.3127
[7 empty] | 7168 | 20285 | 1581987 | 2018-07-07 07:47 | 2018-07-09 07:40 | 2873 | 11kV | 9153 | 11 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN35900 Potts Hill 11kv Panel #10 labelled "S78432 Muir Worth No.2" tripped: Relays: Prot trip, EFI, Basler Relay - 50TN + 51N Signals: CB#10 open, Tx.1 Group earth, Earth fault Remarks: UG fault. 11kv Underground fault from Sw/A @ S785 Anzac unilever to Sw/B @ S6593 Anzac Meapro tee S2339 Brunker Rd tester/jointer permit issued @ 0930 . AP receptacle @ S6593 Anzac Meapro | July | 2018 | 2019Q1 | 2019 | ZN35900:PA10 | ZN35900:PA10 | ZN35900/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-07-07 | N | 832.0909 | N | 5 | N | N | 1.1101 | 39.4971 | 6688.7424
[7 empty] | 6575 | 14158 | 1581749 | 2018-07-06 05:32 | 2018-07-09 08:20 | 4488 | 11kV | 178321 | 1034 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | @ZN1290 Leightonfield 11kv VCB Panel 12 "S-3043" feeder tripped re-closed tripped and locked out on Relays: A phase IOC + timed, EFI, Lockout, Timing relay Signals: 11kv trip, CB 12 open, Remarks: 11kv UGOH section of feeder from Sw/B @ S528 Miller Bil No.3 to Sw/A @ S7430 Biloela Gurr to Sw/A @ CP176 Bennett Miller tee S1631 Biloela Mill. Test and ancillary permit issued @ 1000. Supply available to S1631 from 0120 07/07/18 but dop unable to restore as customer not onsite to check phase rotation. They have requested 1200 07/07/18 appointment to carry out checks/restore supply. | July | 2018 | 2019Q1 | 2019 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2018-07-06 | N | 172.4574 | N | 5 | N | N | 1.1101 | 39.4971 | 130311.7272
[7 empty] | 6659 | 14926 | 1582505 | 2018-07-09 19:07 | 2018-07-09 20:50 | 103 | 11kV | 115775 | 1182 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Pa18 "Forresters Beach" fdr tripped, reclosed and locked out Relays: A Phase IOC, Earth Fault, EFI Signals: 11kv trip, Zone Earth, No3 Group Earth EFIs: S12806 S18070 S11788 S12134 Cause: UG Fault from S18070 to S14117 to LK44277 tee PT11743 See 1583106,9,10 Ex 1582505 | July | 2018 | 2019Q1 | 2019 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | UG | Not Veg | 2018-07-09 | N | 97.9484 | N | 1 | N | N | 1.1101 | 39.4971 | 84604.9552
[7 empty] | 5921 | 6616 | 1582520 | 2018-07-10 04:14 | 2018-07-10 08:18 | 244 | 11kV | 408757 | 2261 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn9700 Kirrawee - Pnl.17 tripped, reclosed, tripped & locked out on: Earth Fault, SEL with EFI Bond failed near AB35743 See 1582764 1582765 1582766 1582767 1582768 | July | 2018 | 2019Q1 | 2019 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Not Veg | 2018-07-10 | N | 180.7859 | N | 4 | N | N | 1.1101 | 39.4971 | 298707.5593
[7 empty] | 6189 | 9939 | 1582535 | 2018-07-10 08:03 | 2018-07-10 10:54 | 171 | 11kV | 342 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 187413 Single Phase LLC broken pole DI-80044. | July | 2018 | 2019Q1 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2018-07-10 | N | 171 | N | 4 | N | N | 1.1101 | 39.4971 | 249.9235
[7 empty] | 5509 | 2082 | 1582592 | 2018-07-10 11:13 | 2018-07-10 12:34 | 81 | 11kV | 236 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | LID 187414 Intertrip Buchholz Trip Denison Street Sub Fdr 34243 | July | 2018 | 2019Q1 | 2019 | 202:34238 43 48 | 202:34238 43 48 | ZN00202/34238 43 48 | NEWCASTLE | UG | Not Veg | 2018-07-10 | N | 39.3333 | N | 4 | N | N | 1.1101 | 39.4971 | 172.4618
[7 empty] | 5944 | 6887 | 1582702 | 2018-07-10 17:40 | 2018-07-10 19:15 | 95 | 11kV | 380 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 187426 No fuse blew, just a failed bail clamp open circuiting. | July | 2018 | 2019Q1 | 2019 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2018-07-10 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 277.6928
[7 empty] | 6402 | 12061 | 1582985 | 2018-07-11 21:13 | 2018-07-12 13:10 | 957 | 11kV | 8625 | 157 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 187449 2 fault operations B Phase Earth Fault UGOH ER-053002 Faulty isolated at 35213 Excluded OMS 1582985 | July | 2018 | 2019Q1 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | UG | Not Veg | 2018-07-11 | N | 54.9363 | N | 1 | N | N | 1.1101 | 39.4971 | 6302.8956
[7 empty] | 7112 | 19662 | 1583089 | 2018-07-12 11:31 | 2018-07-12 16:30 | 299 | 11kV | 1495 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 187476 A & B phase : 10 Amp Live mains on ground Sub isolated Excluded oms 1583089 | July | 2018 | 2019Q1 | 2019 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2018-07-12 | N | 299 | N | 1 | N | N | 1.1101 | 39.4971 | 1092.5019
[7 empty] | 6360 | 11587 | 1583242 | 2018-07-13 00:37 | 2018-07-13 02:23 | 106 | 11kV | 267130 | 2705 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN12620 Noraville 11kv VCB panel 1L "S14068" feeder tripped on Relays: B phase O/C, E fault, EFI Signals: 11kv trip Remarks: UG fault between S14068 Noraville aux sw/c and rec 41873 woolana Woodlawn | July | 2018 | 2019Q1 | 2019 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | UG | Not Veg | 2018-07-13 | N | 98.7542 | N | 4 | N | N | 1.1101 | 39.4971 | 195210.725
[7 empty] | 5896 | 6370 | 1583245 | 2018-07-13 04:21 | 2018-07-13 05:44 | 83 | 11kV | 277809 | 3803 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn35500 Top Ryde - Pnl.28R tripped, reclosed and locked out on: O/C and Earth Fault with EFI Field EFIs: S8724 S5334 Abnormal: S61827 (Sw/B) closed with S2115 (Sw/A) open Possum caused damage to UGOH between S49473 and S8328 See 1583263 1583264 | July | 2018 | 2019Q1 | 2019 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2018-07-13 | N | 73.05 | N | 4 | N | N | 1.1101 | 39.4971 | 203014.6232
[7 empty] | 6421 | 12301 | 1583440 | 2018-07-13 23:46 | 2018-07-14 01:30 | 104 | 11kV | 149960 | 2101 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | The 11kv Panel 13 "Blue Bay" feeder at S12610 Long jetty tripped on: Relays: A & B phase OC Signals: 11kv trip Remarks: tree branch contact, palm found touching mains. Dop cut away | July | 2018 | 2019Q1 | 2019 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Veg | 2018-07-13 | N | 71.3755 | N | 4 | N | N | 1.1101 | 39.4971 | 109586.3449
[7 empty] | 5982 | 7284 | 1583428 | 2018-07-13 21:12 | 2018-07-14 03:50 | 398 | 11kV | 137614 | 607 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @ZN3154 St Ives, 11kv Panel 25 'Mona Vale Stanley No.2' feeder tripped Relays: 'A' phase O/C instantaneous & timed, L/O Signals: 11kv trip Remarks: animals/birds. Possum on mains adj Ab2413. LV mains out of S4751 Dist 2 burned down due to LV parallel, see seperate interruption report for S35798 - interrupted for safety. HV feeder restored from LB77243 as CB at zone would not close. | July | 2018 | 2019Q1 | 2019 | ZN3154:PA25 | ZN3154:PA25 | ZN03154/000025 | KU-RING-GAI | OH | Not Veg | 2018-07-13 | N | 226.7117 | N | 4 | N | N | 1.1101 | 39.4971 | 100564.2523
[7 empty] | 5442 | 1326 | 1583449 | 2018-07-14 07:09 | 2018-07-14 08:50 | 101 | 11kV | 505 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 187495 A Phase DOLF : 10 Amp Excluded OMS 1583449 | July | 2018 | 2019Q1 | 2019 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Veg | 2018-07-14 | N | 101 | N | 1 | N | N | 1.1101 | 39.4971 | 369.0391
[7 empty] | 5547 | 2711 | 1583608 | 2018-07-15 15:07 | 2018-07-15 18:35 | 208 | 11kV | 3952 | 19 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S10269 Vanessa The Crescent No.2 - 11kV/415V Tx No.1 tripped (2 x HRC fuse operations) Suspect Tx No.1 failure. Restored via 415V Bus Section Links. | July | 2018 | 2019Q1 | 2019 | ZN10993:PA33 | ZN10993:PA33 | ZN10993/000033 | GEORGES RIVER | UG | Not Veg | 2018-07-15 | N | 208 | N | 2 | N | N | 1.1101 | 39.4971 | 2888.005
[7 empty] | 5976 | 7215 | 1583646 | 2018-07-15 21:30 | 2018-07-15 22:40 | 70 | 11kV | 5670 | 81 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | No Weather Impact | N | At PT1143 Merrivale Lane (ex Zn3154 St Ives Pa18) 11kv HVDO fuse operated, Roadside 31.5K At Zn3154 St Ives: Signals: zone earth, Tx3 Group earth, EFi panel 18 Remarks: cause not ascertained | July | 2018 | 2019Q1 | 2019 | ZN3154:PA18 | ZN3154:PA18 | ZN03154/000018 | KU-RING-GAI | OH | Veg | 2018-07-15 | N | 70 | N | 2 | N | N | 1.1101 | 39.4971 | 4143.4688
[7 empty] | 6353 | 11482 | 1583656 | 2018-07-16 03:31 | 2018-07-16 04:15 | 44 | 11kV | 63580 | 1445 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | At Zn15005 belrose Panel No.12 'Belrose' feeder tripped on: Signals: 11kv trip Relays: nil EFI: nil Remarks: cause not ascertained. no relays or flags. CB did not reclose. Possible CB mechanical faults. | July | 2018 | 2019Q1 | 2019 | ZN15005:PA12 | ZN15005:PA12 | ZN15005/000012 | NORTHERN BEACHES | Unknown | Not Veg | 2018-07-16 | N | 44 | N | 5 | N | N | 1.1101 | 39.4971 | 46462.3887
[7 empty] | 5876 | 6148 | 1583682 | 2018-07-16 06:49 | 2018-07-16 11:15 | 266 | 11kV | 1330 | 5 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Transformer | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow 11kv VCB panel 5 @ S12462 Albany int pacific no.2 Tx Buchholz trip due to low oil Remarks: low oil in transformer. Transformer trip due to low oil in conservator at S12462. Topped up by T/PE | July | 2018 | 2019Q1 | 2019 | ZN12600:PA5 | ZN12600:PA5 | ZN12600/000005 | CENTRAL COAST | UG | Not Veg | 2018-07-16 | N | 266 | N | 5 | N | N | 1.1101 | 39.4971 | 971.9248
[7 empty] | 6282 | 10734 | 1583900 | 2018-07-16 17:15 | 2018-07-16 18:46 | 91 | 11kV | 130313 | 1445 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S15005 belrose, 11kv Panel No12 "Belrose" feeder tripped on relays: nil Signals: 11kv protection defect remarks: protection malfunction. S15005 Belrose 11kv Panel 12 suspect protection malfunction, second time in 24hrs period that the CB has opeed with no protection relay operations. DMA created | July | 2018 | 2019Q1 | 2019 | ZN15005:PA12 | ZN15005:PA12 | ZN15005/000012 | NORTHERN BEACHES | Unknown | Unknown | 2018-07-16 | N | 90.182 | N | 5 | N | N | 1.1101 | 39.4971 | 95228.8968
[7 empty] | 6264 | 10545 | 1583933 | 2018-07-16 20:26 | 2018-07-16 21:50 | 84 | 11kV | 79576 | 1313 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn4545 Meadowbank - Pnl.17 tripped on: A phase IOC, Earth fault with EFI Abnormal: S3636 Sw/B closed with Sw/A open UG cable fault between S64730 (Sw/B) and S8805 (Sw/A) tee S5400 See 1583994 1583995 1583996 SE1583934 | July | 2018 | 2019Q1 | 2019 | ZN4545:PA17 | ZN129:PA36 | ZN00129/000036 | RYDE | UG | Not Veg | 2018-07-16 | N | 60.6062 | N | 5 | N | N | 1.1101 | 39.4971 | 58151.7937
[7 empty] | 5803 | 5571 | 1583950 | 2018-07-16 22:46 | 2018-07-17 00:36 | 110 | 11kV | 540 | 5 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.8 tripped on: Timed O/C with EFI UG cable fault between Pnl.8, S48724, S35713 and S7906. | July | 2018 | 2019Q1 | 2019 | ZN2568:PA8 | ZN2568:PA8 | ZN02568/000008 | SYDNEY | UG | Not Veg | 2018-07-16 | N | 108 | N | 5 | N | N | 1.1101 | 39.4971 | 394.6161
[7 empty] | 6322 | 11132 | 1584009 | 2018-07-17 11:12 | 2018-07-17 13:50 | 158 | 11kV | 1106 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 187526 B Phase Tapping burnt over PT 64461 affecting all other downstream PT's. Fixed under AP. Excluded OMS 1584044 | July | 2018 | 2019Q1 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2018-07-17 | N | 158 | N | 1 | N | N | 1.1101 | 39.4971 | 808.2322
[7 empty] | 6644 | 14779 | 1584173 | 2018-07-18 00:06 | 2018-07-18 04:00 | 234 | 11kV | 390738 | 2545 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn80 Chatswood Panel 40 tripoped on Signals: 11kV Trip, Zone Earth, TX13 Group Earth Relays: A and B phase OC/ EFI, Fault Check 2nd Trip - Signals: 11kV Trip, Zone Earth, TX13 group Earth Relays: E/F, EFI, Fault Check Cause: Pole fire with 11kV UGOH caught on fire - also UG fault between S76755 and S5641 See OMS 1584273 1584274 1584275 1584173 1584177 | July | 2018 | 2019Q1 | 2019 | ZN80:PA40 | ZN80:PA40 | ZN00080/000040 | LANE COVE | UG | Not Veg | 2018-07-18 | N | 153.5316 | N | 3 | N | N | 1.1101 | 39.4971 | 285539.8056
[7 empty] | 5358 | 215 | 1584196 | 2018-07-18 08:25 | 2018-07-18 12:35 | 250 | 11kV | 1000 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 187543 B Phase DOLF : 10 Amp Excluded OMS 1584196 | July | 2018 | 2019Q1 | 2019 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2018-07-18 | N | 250 | N | 3 | N | N | 1.1101 | 39.4971 | 730.7705
[7 empty] | 6640 | 14741 | 1584353 | 2018-07-18 16:30 | 2018-07-18 18:25 | 115 | 11kV | 460 | 4 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 187552 X arms faulty & tie broken at poles BM-60005 & BM-60006. D Schmierer to repair. | July | 2018 | 2019Q1 | 2019 | 514:18156 | 514:18156 | ZN00514/018156 | MUSWELLBROOK | OH | Not Veg | 2018-07-18 | N | 115 | N | 3 | N | N | 1.1101 | 39.4971 | 336.1544
[7 empty] | 5588 | 3431 | 1584399 | 2018-07-19 01:35 | 2018-07-19 03:28 | 113 | 11kV | 67930 | 1590 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 187557 1 Fault Operation 3 phase Overcurrent Excluded OMS 1584400 | July | 2018 | 2019Q1 | 2019 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2018-07-19 | N | 42.7233 | N | 2 | N | N | 1.1101 | 39.4971 | 49641.2404
[7 empty] | 6011 | 7758 | 1584535 | 2018-07-19 15:40 | 2018-07-19 17:20 | 100 | 11kV | 122950 | 1432 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 187575 1 fault operation C Phase Earth Fault 11kv cable to sub 11795 faulty, section isolated for cut away taps ugoh pole KT-70131. G Fletcher advised sub was listed for decommissioning. sub and ugoh to be removed at later date. SCADA RECLOSE FAILED TO WORK. Excluded OMS 1584535 | July | 2018 | 2019Q1 | 2019 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | Unknown | Unknown | 2018-07-19 | N | 85.8589 | N | 2 | N | N | 1.1101 | 39.4971 | 89848.2336
[7 empty] | 6537 | 13696 | 1584651 | 2018-07-20 10:33 | 2018-07-20 15:15 | 282 | 11kV | 564 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 187590 A Phase DOLF : 16 Amp Excluded OMS 1584651 | July | 2018 | 2019Q1 | 2019 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-07-20 | N | 282 | N | 4 | N | N | 1.1101 | 39.4971 | 412.1546
[7 empty] | 5447 | 1364 | 1584679 | 2018-07-20 16:44 | 2018-07-20 20:02 | 198 | 11kV | 12672 | 64 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Wind Strong | N | LID 187593 MVA -car hit & snapped pole, section isolated to replace pole WB-55201 Excluded OMS 1584679 | July | 2018 | 2019Q1 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2018-07-20 | N | 198 | N | 4 | N | N | 1.1101 | 39.4971 | 9260.3238
[7 empty] | 6326 | 11186 | 1584759 | 2018-07-20 15:09 | 2018-07-20 21:45 | 396 | 11kV | 27607 | 142 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ex Zn35370 Galston Panel 4L CP555 Arcadia Park Tripped on OC trip and Lockout Cause: OH down - 11kV into LV near PT746 S 131 Arcadia Rd, Arcadia just past fire station. Pin on footpath side has come out of xarm and is resting on the 415V neutral. Mains please attend urgently. See OMS 1585328 1585330 1584759 | July | 2018 | 2019Q1 | 2019 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2018-07-20 | N | 194.4155 | N | 4 | N | N | 1.1101 | 39.4971 | 20174.3813
[7 empty] | 5388 | 668 | 1584707 | 2018-07-20 12:59 | 2018-07-21 15:40 | 1601 | 11kV | 22332 | 92 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 187592 3 Phase Earth fault; Sensitive Earth Fault mains down pole EV-41717 section isolated for repairs Excluded oms1584775 | July | 2018 | 2019Q1 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2018-07-20 | N | 242.7391 | N | 4 | N | N | 1.1101 | 39.4971 | 16319.5669
[7 empty] | 6529 | 13659 | 1585026 | 2018-07-22 10:09 | 2018-07-22 11:30 | 81 | 11kV | 16848 | 208 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Ex Pnl.4 @ Mortdale Zn - AB31141 - one phase has broken away and is unserviceable. | July | 2018 | 2019Q1 | 2019 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | OH | Not Veg | 2018-07-22 | N | 81 | N | 1 | N | N | 1.1101 | 39.4971 | 12312.0215
[7 empty] | 6459 | 12811 | 1585180 | 2018-07-23 11:18 | 2018-07-23 13:30 | 132 | 11kV | 142881 | 1376 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn15006 Dee Why West Panel 13 "S47595 Orland Villers" tripped on: Relays: 51A&B Phase OC Signals: 11kv trip EFI's: Nil Cause: not ascertained DOp found during patrol, 2x Burnt off 11kv bonds between LB64167 to LK24947 tee S16684 tee PT15398 See 1585462,3,5,6 ex 1585180,2,3,205 | July | 2018 | 2019Q1 | 2019 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | OH | Not Veg | 2018-07-23 | N | 103.8379 | N | 1 | N | N | 1.1101 | 39.4971 | 104413.2205
[7 empty] | 6456 | 12725 | 1585511 | 2018-07-24 12:52 | 2018-07-24 15:39 | 167 | 11kV | 8363 | 159 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 187631 & Planned 187630 1 fault operation B Phase Earth Fault Excluded OMS 1585511 | July | 2018 | 2019Q1 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2018-07-24 | N | 52.5975 | N | 2 | N | N | 1.1101 | 39.4971 | 6111.4337
[7 empty] | 6263 | 10525 | 1585434 | 2018-07-24 08:57 | 2018-07-24 16:10 | 433 | 11kV | 44599 | 103 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 187629 A Phase DOLF : 31 Amp Live Line Lead broken off Tx primary bushing On return 244v on all 3. A=12amp, B=6Amp, C=8Amp. Excluded OMS 1585434 | July | 2018 | 2019Q1 | 2019 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Not Veg | 2018-07-24 | N | 433 | N | 2 | N | N | 1.1101 | 39.4971 | 32591.6338
[7 empty] | 5894 | 6352 | 1585689 | 2018-07-25 02:24 | 2018-07-25 03:40 | 76 | 11kV | 99940 | 1315 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At Zn847 Hornsby 11kV Panel 7 tripped on: Relays: MiCom Relay - (Combined OC + E/F + EFI) - Trip, EFI, B phase Signalls: 11KV trip, TX1 Group Earth, Zone Earth, CB 7 Open Field EFI's NIL Cause: Possum @ UGOH leading into S5292 Hammond Milson. | July | 2018 | 2019Q1 | 2019 | ZN847:PA7 | ZN847:PA7 | ZN00847/000007 | HORNSBY | OH | Not Veg | 2018-07-25 | N | 76 | N | 2 | N | N | 1.1101 | 39.4971 | 73033.2043
[7 empty] | 6001 | 7585 | 1585867 | 2018-07-25 13:53 | 2018-07-25 17:25 | 212 | 11kV | 1272 | 6 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 187644 B Phase 40Amp Fuse Arrestor replaced | July | 2018 | 2019Q1 | 2019 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-07-25 | N | 212 | N | 2 | N | N | 1.1101 | 39.4971 | 929.5401
[7 empty] | 5965 | 7061 | 1586029 | 2018-07-26 02:40 | 2018-07-26 04:35 | 115 | 11kV | 211062 | 2017 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S36300 Balgowlah Nortth 11KV Panel labelled S17119 Jackson White and LB 61276 tripped Relays: IOC A B C and EFI, Signals:TX1 Group Earth, CB3 Open Battery A Charger Fail. B Baterry Charger Fail Cause not ascertained for outage | July | 2018 | 2019Q1 | 2019 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Veg | 2018-07-26 | N | 104.6415 | N | 4 | N | N | 1.1101 | 39.4971 | 154237.8843
[7 empty] | 6901 | 17597 | 1586032 | 2018-07-26 03:33 | 2018-07-26 04:58 | 85 | 11kV | 71910 | 846 | HV | Animal Possum | Animal | Circuit Breaker | Unplanned | No Weather Impact | N | LID 187649 Tapping open at pole IU-80673, after previous T/R (see OMS 1586671 and 1586672, and related LID reports 187647 and 187648) | July | 2018 | 2019Q1 | 2019 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2018-07-26 | N | 85 | N | 4 | N | N | 1.1101 | 39.4971 | 52549.707
[7 empty] | 6844 | 16844 | 1586185 | 2018-07-26 16:21 | 2018-07-26 18:40 | 139 | 11kV | 4791 | 173 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 187668 Car hit pole adjacent to sub 48245 No Protection operated | July | 2018 | 2019Q1 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-07-26 | N | 27.6936 | N | 4 | N | N | 1.1101 | 39.4971 | 3501.1215
[7 empty] | 5450 | 1387 | 1586184 | 2018-07-26 16:17 | 2018-07-26 21:23 | 306 | 11kV | 11016 | 36 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 187670 single phase Broken Cross Arm. Pole GP-43105 | July | 2018 | 2019Q1 | 2019 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-07-26 | N | 306 | N | 4 | N | N | 1.1101 | 39.4971 | 8050.1679
[7 empty] | 7153 | 20024 | 1586237 | 2018-07-27 06:10 | 2018-07-27 15:20 | 550 | 11kV | 12741 | 41 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 187673 1 Fault operations, ABC, Earth Fault Ducks caused fault at sub 70970 resulting in wire down | July | 2018 | 2019Q1 | 2019 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2018-07-27 | N | 310.7561 | N | 3 | N | N | 1.1101 | 39.4971 | 9310.747
[7 empty] | 5988 | 7317 | 1586380 | 2018-07-27 18:40 | 2018-07-27 23:20 | 280 | 11kV | 4200 | 15 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S9350 Macmahon Allison - 11kV/415V Tx - C phase LV bushing high resistance Restored via LV // 23572, 1728, 1713 McDonalds first called regarding fluctuating supply 26/7/18, EMSO turned away due to lunch rush and referred them to EC. Further calls of part supply received 27/7 which escalated the job to Control Room. CC1: 08-"Urgent - U.G Mains - No others" FRC1: 381-"Fluctuating Supply - Underground - No Other Service affected - UG Mains required" | July | 2018 | 2019Q1 | 2019 | ZN9900:PA20 | ZN9900:PA20 | ZN09900/000020 | SUTHERLAND | UG | Not Veg | 2018-07-27 | N | 280 | N | 3 | N | N | 1.1101 | 39.4971 | 3069.2361
[7 empty] | 6962 | 18126 | 1586395 | 2018-07-27 21:50 | 2018-07-28 03:54 | 364 | 11kV | 3263 | 13 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 187684 3 Fault operations, C phase, pole mounted RAGCB, Earth Fault 11kV Main on ground at Pole 2J-30043 | July | 2018 | 2019Q1 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2018-07-27 | N | 251 | N | 3 | N | N | 1.1101 | 39.4971 | 2384.5042
[7 empty] | 6976 | 18286 | 1586487 | 2018-07-28 21:38 | 2018-07-28 23:22 | 104 | 11kV | 313456 | 3014 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Zn4545 Meadowbank - Pnl.31 tripped and locked out on: C phase O/C with EFI Field EFIs: S1829 S49273 S49274 S6579 S7356 S46360 S1572 Possum found at base of pole at REC 46117. No apparent damage | July | 2018 | 2019Q1 | 2019 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Not Veg | 2018-07-28 | N | 104 | N | 1 | N | N | 1.1101 | 39.4971 | 229064.3994
[7 empty] | 5773 | 5368 | 1586497 | 2018-07-29 04:24 | 2018-07-29 06:55 | 151 | 11kV | 15553 | 103 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | OMS 1586497 Possum found on Tx tank.. Readings as left 244V, 243V, 241V . 63A, 93A, 230A | July | 2018 | 2019Q1 | 2019 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2018-07-29 | N | 151 | N | 2 | N | N | 1.1101 | 39.4971 | 11365.6737
[7 empty] | 6642 | 14757 | 1586540 | 2018-07-29 13:59 | 2018-07-29 14:34 | 35 | 11kV | 33495 | 957 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Pole | Unplanned | No Weather Impact | N | Pole cap pole JU-26088 Curly Rd touching OHM, cap removed & supply restored. Requires new pole cap. Also see report 187694 - LID 187694 | July | 2018 | 2019Q1 | 2019 | 257:81999 | 257:81999 | ZN00257/081999 | NEWCASTLE | OH | Not Veg | 2018-07-29 | N | 35 | N | 2 | N | N | 1.1101 | 39.4971 | 24477.1581
[7 empty] | 7122 | 19714 | 1586857 | 2018-07-30 16:50 | 2018-07-30 18:40 | 110 | 11kV | 24490 | 257 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2835 Burwood 11kv Panel No24 "S8461 Parramatta Neich" feeder tripped on Relays: E/fault, EFI, fault check Signals: 11kv trip EFI's: S8461 Abnormal: Sw/A opened @ S3530 Noongah Pl, Sw/D closed @ S370 William St Remarks: 11kv ug cable fault from S8461 Parramatta Neich to S3552 Walker Thornton tee S5817 Bennett Par. (All 3 subs were found to be in LV//) S5817 was never interrupted due to LV // | July | 2018 | 2019Q1 | 2019 | ZN2835:PA24 | ZN2835:PA24 | ZN02835/000024 | CANADA BAY | UG | Not Veg | 2018-07-30 | N | 95.2918 | N | 2 | N | N | 1.1101 | 39.4971 | 17896.5697
[7 empty] | 6201 | 10024 | 1586788 | 2018-07-30 15:02 | 2018-07-30 20:30 | 328 | 11kV | 328 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 187706 Single Phase 10 Amp Fuse Dolf Base broken, both replaced under AP | July | 2018 | 2019Q1 | 2019 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2018-07-30 | N | 328 | N | 2 | N | N | 1.1101 | 39.4971 | 239.6927
[7 empty] | 6030 | 7907 | 1586925 | 2018-07-31 02:20 | 2018-07-31 03:25 | 65 | 11kV | 87659 | 1477 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.14 tripped on: IOC Field EFIs: S4794 S8867 UG cable fault between S8867 (Sw/B) and S2026 (Sw/A) See 1586946 1586947 | July | 2018 | 2019Q1 | 2019 | ZN2568:PA14 | ZN2568:PA14 | ZN02568/000014 | SYDNEY | UG | Not Veg | 2018-07-31 | N | 59.3494 | N | 5 | N | N | 1.1101 | 39.4971 | 64058.6117
[7 empty] | 5889 | 6305 | 1586927 | 2018-07-31 02:41 | 2018-07-31 03:58 | 77 | 11kV | 74710 | 1051 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn9037 Miranda - Pnl.2 tripped on: A Phase IOC with EFI Field EFIs: NIL Note: PE to check reclosing as it failed to reclose Cause not ascertained, patrolled clear See 1586948 1586949 1586950 | July | 2018 | 2019Q1 | 2019 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Veg | 2018-07-31 | N | 71.0847 | N | 5 | N | N | 1.1101 | 39.4971 | 54595.8644
[7 empty] | 5600 | 3560 | 1586933 | 2018-07-31 07:30 | 2018-07-31 08:45 | 75.4167 | 11kV | 8145 | 108 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 187708 A Phase 40 Amp fuse no cause found, not storm conditions 246V, A= 200A, B=180A, C=170A | July | 2018 | 2019Q1 | 2019 | 220:8691 | 220:8691 | ZN00220/008691 | LAKE MACQUARIE | OH | Veg | 2018-07-31 | N | 75.4167 | N | 5 | N | N | 1.1101 | 39.4971 | 5952.1258
[7 empty] | 6145 | 9379 | 1586970 | 2018-07-31 10:25 | 2018-07-31 10:48 | 23 | 11kV | 13219 | 1153 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Zn3154 St Ives Panel 5 "Collins Killeaton" tripped and locked out Relays: C Phase IOC, lock out and timing relay Singals: 11kv trip and group earth EFI Cause: Air Break Switch AB2647 arcing and flashover See 1587239,42 ex 1586970,1,95 | July | 2018 | 2019Q1 | 2019 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | OH | Not Veg | 2018-07-31 | N | 11.4649 | N | 5 | N | N | 1.1101 | 39.4971 | 9660.0553
[7 empty] | 6823 | 16625 | 1587051 | 2018-07-31 13:45 | 2018-07-31 14:56 | 71 | 11kV | 162645 | 2602 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15006 Dee Why Panel 9 "Lagoon" fdr tripped Relays: Earth Fault, EFI Signals: 11kv trip, Zone Earth EFI: S16792 S17031 S16733 Cause: UG Fualt between S16733:B to S16924:A to S16734:A See 1587243,4,5,6 ex 1587051 | July | 2018 | 2019Q1 | 2019 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | UG | Not Veg | 2018-07-31 | N | 62.5077 | N | 5 | N | N | 1.1101 | 39.4971 | 118856.1688
[7 empty] | 6308 | 10979 | 1587156 | 2018-08-01 01:56 | 2018-08-01 02:51 | 55 | 11kV | 107172 | 1962 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn9700 Kirrawee - Pnl.11 tripped, reclosed and tripped on: Earth Fault Field EFIs: S9518 S9325 S9242 UG cable hit by excavator between S9242 (Sw/B) and S9548 (Sw/B) See 1587168 1587169 | August | 2018 | 2019Q1 | 2019 | ZN9700:PA11 | ZN9700:PA18 | ZN09700/000018 | SUTHERLAND | UG | Not Veg | 2018-08-01 | N | 54.6239 | N | 2 | N | N | 1.1101 | 39.4971 | 78318.1366
[7 empty] | 6641 | 14752 | 1588103 | 2018-08-01 13:25 | 2018-08-01 13:29 | 4 | 11kV | 7144 | 1786 | HV | Staff Other | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 187725 Protection staff closed E/Sw on Fdr 33572 while working on racked out CB and prot panel in error. ABS 16699 was closed for the Cb maintenance job which caused Sw 33576 to trip. | August | 2018 | 2019Q1 | 2019 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2018-08-01 | N | 4 | N | 2 | N | N | 1.1101 | 39.4971 | 5220.6245
[7 empty] | 7170 | 20318 | 1587491 | 2018-08-02 12:48 | 2018-08-02 14:20 | 92 | 11kV | 69253 | 791 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn3154 St Ives Ex Panel 16 "Linbara Shinfield" Re1622 Eastern Arterial Opened & Locked on OC trip Abnormal: LB62191 Closed, AB155 Open & Defective Cause: not ascertained Suspect Bushfire in gully between LB3238 and LB62189 caused outage. Lineworkers to patrol friday morning after fire is out to check for damage. Already referred to E. Jobson See 1587628,1587782 ex 1587491 CC1: 04-"Non Urgent - refer to OH Mains" FRC1: 345-"Overhead Service Line - Hanging low - Requires adjustment" | August | 2018 | 2019Q1 | 2019 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Veg | 2018-08-02 | N | 87.5512 | N | 1 | N | N | 1.1101 | 39.4971 | 50608.0498
[7 empty] | 6793 | 16241 | 1587757 | 2018-08-03 01:24 | 2018-08-03 07:30 | 366 | 11kV | 12804.9 | 35 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Zn13000 Lake Munmorah Ex Pa1 PT18783 Elabana Lloyd Roadside Phase 31.5k HDO was found to have operated Fuae Fatigue See 1587757 ex 1587763 | August | 2018 | 2019Q1 | 2019 | ZN13000:PA1 | ZN13000:PA1 | ZN13000/000001 | CENTRAL COAST | OH | Not Veg | 2018-08-03 | N | 365.8543 | N | 2 | N | N | 1.1101 | 39.4971 | 9357.4432
[7 empty] | 5482 | 1700 | 1587830 | 2018-08-03 13:15 | 2018-08-03 13:45 | 30 | 11kV | 300 | 10 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 187744 Stay broke at pole SI-40507. Isolated for safety, no protection operations. | August | 2018 | 2019Q1 | 2019 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2018-08-03 | N | 30 | N | 2 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 5372 | 439 | 1587997 | 2018-08-05 09:17 | 2018-08-05 13:20 | 243 | 11kV | 486 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 187754 Single phase LL Lead broken off at DOLF end. Excluded OMS 1587997. | August | 2018 | 2019Q1 | 2019 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2018-08-05 | N | 243 | N | 2 | N | N | 1.1101 | 39.4971 | 355.1545
[7 empty] | 5492 | 1891 | 1588033 | 2018-08-05 15:19 | 2018-08-05 17:03 | 104 | 11kV | 135408 | 1302 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.36 tripped on: A Phase OC and EF Field EFIs S4925 S1999 S8754 S3339 S3557 (note S2498 EFI did not operate) UG cable fault between S3557 (Sw/B) and S1678 (Sw/B). HV joint has failed in pit outside 17 Wardell Rd Earlwood. | August | 2018 | 2019Q1 | 2019 | ZN690:PA36 | ZN690:PA36 | ZN00690/000036 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-08-05 | N | 104 | N | 2 | N | N | 1.1101 | 39.4971 | 98952.1725
[7 empty] | 6782 | 16091 | 1588209 | 2018-08-06 13:58 | 2018-08-06 14:58 | 60 | 11kV | 60 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 187765 B Phase DOLF : 10 Amp Excluded OMS 1588209 | August | 2018 | 2019Q1 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2018-08-06 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 5457 | 1464 | 1588289 | 2018-08-06 20:49 | 2018-08-06 22:14 | 85 | 11kV | 86530 | 1018 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.19 tripped on: A & B phase IOC Field EFIs: S50482 50483 S10040 S10954 S10898 S10675 Possum on UGOH near S10675 | August | 2018 | 2019Q1 | 2019 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2018-08-06 | N | 85 | N | 4 | N | N | 1.1101 | 39.4971 | 63233.5718
[7 empty] | 5864 | 6037 | 1588282 | 2018-08-06 19:10 | 2018-08-07 01:20 | 370 | 11kV | 373894 | 2300 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn12570 Avoca Panel 21" "LB49826" tripped, reclosed & tripped Relays: EFI, EF Signals: CB21 open, closed, open, AR L/O 415V Tx11 AC Board - AC Changeover fail, CB trip, AC Supply fail EFI'S: S64802 S77326 S14890 S14356 S14357 S14355 Cause: UG fault from S77326SwB to S14890SwA to S18349SwA to AB42870 Note: 1. Suspected EFI's not reset from previous trip & reclose. Dead possum found @ Base of UGOH beyond S14355SwB 2. No EFI located S14858 3. EFI located S14355 4. See outage report Panel 41 @ Zn12570 Avoca 5. See outage on section of Pa21 for repairs on AB42870 See 1588586,7 ex 1588282 | August | 2018 | 2019Q1 | 2019 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Not Veg | 2018-08-06 | N | 162.5626 | N | 4 | N | N | 1.1101 | 39.4971 | 273230.7072
[7 empty] | 6315 | 11038 | 1588590 | 2018-08-06 23:50 | 2018-08-07 01:20 | 90 | 11kV | 4230 | 47 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn12570 Avoca Ex Pa21: from LB49826 to AB41357 interrupted by DOp to repair brunt off bond @ AB41357 S64802 was still interrupted from earlier outage with UG fault below feeder See seperate interruption report on Panel 21L | August | 2018 | 2019Q1 | 2019 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Not Veg | 2018-08-06 | N | 90 | N | 4 | N | N | 1.1101 | 39.4971 | 3091.1592
[7 empty] | 6356 | 11517 | 1588299 | 2018-08-07 00:39 | 2018-08-07 01:40 | 61 | 11kV | 92659 | 1519 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn10991 Blakehurst - Pnl.1 tripped on: Earth Fault with EFI Field EFIs: S10137 S10860 Possum on UGOH to S10860 | August | 2018 | 2019Q1 | 2019 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2018-08-07 | N | 61 | N | 4 | N | N | 1.1101 | 39.4971 | 67712.4642
[7 empty] | 5806 | 5597 | 1588434 | 2018-08-07 11:29 | 2018-08-07 12:54 | 85 | 11kV | 71992 | 853 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca Panel 34 "Terrigal" tripped , reclosed & tripped Relays: A+B Phase IOC, A/R Lockout Signals CB34 open, closed, trip, Auto Reclose Lockout Tx12 AC board AC Supply Fail, Tx13 AC baord Changeover Fail Cause: Tree Trimming Area. Neighbours reported private tree trimmer was in area below LB41002 See 1588683,4 ex 1588434 | August | 2018 | 2019Q1 | 2019 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Not Veg | 2018-08-07 | N | 84.3986 | N | 4 | N | N | 1.1101 | 39.4971 | 52609.6302
[7 empty] | 6865 | 17088 | 1588471 | 2018-08-07 13:08 | 2018-08-07 17:25 | 257 | 11kV | 57820 | 385 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14891 Wyong Ex pa12 "Yarramalong" IR50630 Yarrmalong Chandlers 0.1 tripped & locked out Relays: Overcurrent trip, lock out Signals: CP50630 CB open, lockout Abnormal: RE48838 open & bypassed. RE48813 Open & Bypassed, IR44753 open & Bypassed Cause: 11kv OH Down from IR44753 to LB42675 to Auto link 47340 tee PT11505 See 1588689,90 ex 1588471 | August | 2018 | 2019Q1 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2018-08-07 | N | 150.1818 | N | 4 | N | N | 1.1101 | 39.4971 | 42253.1506
[7 empty] | 6463 | 12856 | 1588576 | 2018-08-07 16:32 | 2018-08-07 23:00 | 388 | 11kV | 776 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 187779 repair LL lead excluded oms 1588576 | August | 2018 | 2019Q1 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-08-07 | N | 388 | N | 4 | N | N | 1.1101 | 39.4971 | 567.0779
[7 empty] | 6726 | 15339 | 1588630 | 2018-08-08 01:09 | 2018-08-08 04:28 | 199 | 11kV | 274090 | 1510 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn9245 Engadine - Pnl.15 tripped on: IOC B & C Phase Abnormal : LB35873 Closed with AB35951 Open All Pnl.15 field EFIs operated, Pnl.1 EFIs were sludge type and did not operate Cause not ascertained See 1588663 1588664 1588665 | August | 2018 | 2019Q1 | 2019 | ZN9245:PA15 | ZN9245:PA15 | ZN09245/000015 | SUTHERLAND | OH | Veg | 2018-08-08 | N | 181.5166 | N | 3 | N | N | 1.1101 | 39.4971 | 200296.8877
[7 empty] | 5834 | 5771 | 1588801 | 2018-08-08 14:56 | 2018-08-08 17:10 | 134 | 11kV | 126376 | 1662 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35555 Croydon Panel 20 'S46285 Alt Ramsay" feeder has tripped on: Signal: 11kv trip Relays: earth fault, EFI Remarks: UG fault. Ex Pa20 Zn35555 Croydon - 11kv UG fault from S49765 Allum St No.1 (Sw/A) to S6318 Wosleley Parra (Sw/B), tee S1907 Tiana St. | August | 2018 | 2019Q1 | 2019 | ZN35555:PA20 | ZN35555:PA20 | ZN35555/000020 | INNER WEST | UG | Not Veg | 2018-08-08 | N | 76.0385 | N | 3 | N | N | 1.1101 | 39.4971 | 92351.8533
[7 empty] | 5827 | 5719 | 1588800 | 2018-08-08 14:52 | 2018-08-08 17:50 | 178 | 11kV | 101232 | 1043 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman Panel 24 fdr tripped on: Relays: Timed O/C B Phase, E/F, Fault check, Tx Panel 3B Earth leakage and EFI EFI: S1340 S372 S7807 CP575 S2743 Signals: 11kv trip & group Earth Cause: UG Cable damaged by Contractor outside 6 Weemala St Section of UG defective after contractor damaged from S2743 to S49773 See 1589049,50 ex 1588800,10,11 | August | 2018 | 2019Q1 | 2019 | ZN180:PA24 | ZN180:PA24 | ZN00180/000024 | WILLOUGHBY | UG | Not Veg | 2018-08-08 | N | 97.0585 | N | 3 | N | N | 1.1101 | 39.4971 | 73977.3598
[7 empty] | 6519 | 13590 | 1588894 | 2018-08-09 00:46 | 2018-08-09 01:49 | 63 | 11kV | 75053 | 1510 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn901 Surry Hills - Pnl.20 tripped on: B phase Earth Fault UG cable fault from S7237 (Sw/B) to S3821 (Sw/B) to S8947 (Sw/B) See 1588923 1588924 | August | 2018 | 2019Q1 | 2019 | ZN901:PA20 | ZN901:PA29 | ZN00901/000029 | SYDNEY | UG | Not Veg | 2018-08-09 | N | 49.704 | N | 1 | N | N | 1.1101 | 39.4971 | 54846.5187
[7 empty] | 6182 | 9837 | 1589211 | 2018-08-10 14:55 | 2018-08-10 16:20 | 85 | 11kV | 170 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 187805 Single phase Section isolated for repairs to pole 3I-70194 Excluded OMS 1589211 | August | 2018 | 2019Q1 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2018-08-10 | N | 85 | N | 2 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 6084 | 8460 | 1589259 | 2018-08-10 18:08 | 2018-08-10 20:15 | 127 | 11kV | 62761 | 615 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S262 Marrickville Panel 20 'S6398 Smith Victoria' fdr tripped on Relays: EF, EFI, Fault check Remarks: UG fault. 11kv UG cable fault. from S7364 Brompton Rich to S7071 Jabez Denby Tee S2648 Browns Newington | August | 2018 | 2019Q1 | 2019 | ZN262:PA20 | ZN262:PA20 | ZN00262/000020 | INNER WEST | UG | Not Veg | 2018-08-10 | N | 102.0504 | N | 2 | N | N | 1.1101 | 39.4971 | 45863.8877
[7 empty] | 5535 | 2501 | 1589488 | 2018-08-11 12:11 | 2018-08-11 13:45 | 94 | 11kV | 94 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 187810 1 fault operation Overcurrent | August | 2018 | 2019Q1 | 2019 |  |  |  | SINGLETON | OH | Veg | 2018-08-11 | N | 94 | N | 5 | N | N | 1.1101 | 39.4971 | 68.6924
[7 empty] | 6133 | 9230 | 1589334 | 2018-08-11 15:00 | 2018-08-11 15:45 | 45 | 11kV | 135 | 3 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 187811 Repair damaged OHM after bird had been between HV & LV adj sub 53188 Excluded OMS 1589334 | August | 2018 | 2019Q1 | 2019 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2018-08-11 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 98.654
[7 empty] | 6129 | 9217 | 1589341 | 2018-08-11 14:55 | 2018-08-11 16:58 | 123 | 11kV | 59011 | 1591 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 187812 1 fault operation Overcurrent, Earth Fault, Sensitive Earth Fault faulty UGOH feed to sub 13258 Excluded oms 1589341 | August | 2018 | 2019Q1 | 2019 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | Unknown | Unknown | 2018-08-11 | N | 37.0905 | N | 5 | N | N | 1.1101 | 39.4971 | 43123.4983
[7 empty] | 6511 | 13437 | 1589371 | 2018-08-11 20:56 | 2018-08-11 22:06 | 70 | 11kV | 77560 | 1108 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.10 tripped, reclosed and locked out. Field EFIs: S10123 Possum found in UGOH below S10123 Lorraine Peace | August | 2018 | 2019Q1 | 2019 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Not Veg | 2018-08-11 | N | 70 | N | 5 | N | N | 1.1101 | 39.4971 | 56678.5604
[7 empty] | 6842 | 16831 | 1589330 | 2018-08-11 12:31 | 2018-08-12 15:35 | 1624 | 11kV | 264712 | 163 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn14143 Somersby Ex Panel 17 "Somersby Falls" RE45012 Bar POint" has trippedreclosed/tripped/reclosed/tripped & locked out Relays: Oc trip, lockout Signlas: EFI operated on Panel 17 @ Zn14143 Somersby Cause: tree/branch brought down oh Large tree on HV mains located in section of 11kv fdr from RE45012 to LK40589 to LK40588 tee PT13610, PT13611, PT13612. DOp reports large tree still resting on HV mains above private structure (storage shed). Aborist to be arranged for sunday 12/8 to remove safely See 1589329 ex 1589330,2,3 CC1: 22-"Refer to SOp" | August | 2018 | 2019Q1 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2018-08-11 | N | 1624 | N | 5 | N | N | 1.1101 | 39.4971 | 193443.7219
[7 empty] | 6960 | 18104 | 1589432 | 2018-08-12 14:38 | 2018-08-12 21:45 | 427 | 11kV | 11539 | 128 | HV | Fire (Non Ausgrid) | UNKNOWN | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 187814 4 fault operations Bushfire affecting pole MS10011 Fallen and burnt Excluded OMS 1589432 | August | 2018 | 2019Q1 | 2019 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2018-08-12 | N | 90.1484 | N | 2 | N | N | 1.1101 | 39.4971 | 8432.3609
[7 empty] | 6386 | 11877 | 1589508 | 2018-08-13 08:59 | 2018-08-13 10:10 | 71 | 11kV | 284 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 187820 C Phase DOLF : 10 Amp Excluded OMS 1589508 | August | 2018 | 2019Q1 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2018-08-13 | N | 71 | N | 1 | N | N | 1.1101 | 39.4971 | 207.5388
[7 empty] | 5948 | 6924 | 1589450 | 2018-08-12 18:49 | 2018-08-14 01:00 | 1811 | 11kV | 191862 | 2111 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3155 Double Bay - Pnl.29 tripped on: O/C and E/F Field EFIs: S1859 S64997 S2993 S3167 S3641 Abnormal: S35225 (Sw/B) closed with (Sw/A) open UG cable fault between S3641 (Sw/A) and S783 (Sw/B) LV parallel failures along with LV UG fault occured at the same time. See 1589703 1589705 LV: 1589704 1589452 1589520 1589704 | August | 2018 | 2019Q1 | 2019 | ZN3155:PA29 | ZN3155:PA29 | ZN03155/000029 | WOOLLAHRA | UG | Not Veg | 2018-08-12 | N | 90.8868 | N | 2 | N | N | 1.1101 | 39.4971 | 140207.0906
[7 empty] | 5962 | 7037 | 1589691 | 2018-08-14 03:49 | 2018-08-14 17:10 | 801 | 11kV | 801 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 187828 A & B phase DOLF : 10 Amp Faulty txf replaced under AP Excluded OMS 1589691 | August | 2018 | 2019Q1 | 2019 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Not Veg | 2018-08-14 | N | 801 | N | 1 | N | N | 1.1101 | 39.4971 | 585.3472
[7 empty] | 6864 | 17076 | 1589886 | 2018-08-15 07:26 | 2018-08-15 08:15 | 49 | 11kV | 98 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 187840 C Phase IPC on TX tail burning up. Replaced. Excluded OMS 1589886 | August | 2018 | 2019Q1 | 2019 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2018-08-15 | N | 49 | N | 4 | N | N | 1.1101 | 39.4971 | 71.6155
[7 empty] | 5882 | 6198 | 1589895 | 2018-08-15 11:15 | 2018-08-15 11:40 | 25 | 11kV | 45 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge Ex Pa8 11kv USL 41280 interrupted for safety to replace 11kv cross arm on pole KA323 See 1590292,3 ex 1589943,1589895 | August | 2018 | 2019Q1 | 2019 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2018-08-15 | N | 22.5 | N | 4 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 6466 | 12930 | 1589982 | 2018-08-15 12:59 | 2018-08-15 13:55 | 56 | 11kV | 75376 | 1346 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 42 tripped on Relays: B phase OC, lockout Signals: 11kV trip Field EFI NIL Cause: tree branch on OH mains. tree on mains near AB1694 See OMS 1589982 1589986 | August | 2018 | 2019Q1 | 2019 | ZN4545:PA42 | ZN4545:PA42 | ZN04545/000042 | RYDE | OH | Veg | 2018-08-15 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 55082.5576
[7 empty] | 6502 | 13305 | 1590018 | 2018-08-15 14:24 | 2018-08-15 19:20 | 296 | 11kV | 12256 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn12600 Lisarow Ex Panel 2 "Holgate" IR41066 MacDonalds Rd tripped, reclosed & tripped Relays: O/C lock out, O/C trip Signals: O/C trip, CP41066 open, CP41066 lockout Cause: Tree/branch brought down OH Outisde the Ridgeway rd, lisarow. 2 OH bays before USL 41373 See 1590295,6 ex 1590018,9,34 | August | 2018 | 2019Q1 | 2019 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2018-08-15 | N | 125.0612 | N | 4 | N | N | 1.1101 | 39.4971 | 8956.3233
[7 empty] | 6811 | 16512 | 1590199 | 2018-08-16 01:01 | 2018-08-16 07:20 | 379 | 11kV | 44343 | 117 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT9506 Cranberry national - C phase 50Amps HDO Blown Possum on PT9506 | August | 2018 | 2019Q1 | 2019 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2018-08-16 | N | 379 | N | 4 | N | N | 1.1101 | 39.4971 | 32404.5565
[7 empty] | 6577 | 14182 | 1590201 | 2018-08-16 05:02 | 2018-08-16 07:30 | 148 | 11kV | 89246 | 1114 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn12620 Noraville Pa10 "Buff point" fdr tripped Signals: 11kv trip Relays: IOC, SEL, Timed OC, E/F, EFI, Timer, lockout EFI's: as expected Cause: HV UGOH to S14815 Bruce Monday needs replacing HV Bond burnt off at LB41944 See 1591093,5,6,7 ex 1590201,2,4 | August | 2018 | 2019Q1 | 2019 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | Unknown | Unknown | 2018-08-16 | N | 80.1131 | N | 4 | N | N | 1.1101 | 39.4971 | 65218.3445
[7 empty] | 5377 | 476 | 1590499 | 2018-08-16 17:24 | 2018-08-16 18:40 | 76 | 11kV | 76 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 187858 A Phaqse Live line lead broke Excluded oms 1590499. | August | 2018 | 2019Q1 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-08-16 | N | 76 | N | 4 | N | N | 1.1101 | 39.4971 | 55.5386
[7 empty] | 5641 | 4018 | 1590503 | 2018-08-16 18:15 | 2018-08-16 20:46 | 151 | 11kV | 62574 | 490 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 187859 1 fault operation B & C Phase Overcurrent No Cause Found | August | 2018 | 2019Q1 | 2019 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2018-08-16 | N | 127.702 | N | 4 | N | N | 1.1101 | 39.4971 | 45727.2336
[7 empty] | 6714 | 15260 | 1590583 | 2018-08-17 10:40 | 2018-08-17 11:49 | 69 | 11kV | 183954 | 2666 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn10995 Riverwood - Pnl.7 - Loss of supply from AB30590 Abnormal: LB30061 closed with AB31318 Open and Defective. LB62364 opened (load relief) Bond failed on Roadside phase at AB30590 | August | 2018 | 2019Q1 | 2019 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Not Veg | 2018-08-17 | N | 69 | N | 1 | N | N | 1.1101 | 39.4971 | 134428.1575
[7 empty] | 5977 | 7251 | 1590697 | 2018-08-18 07:03 | 2018-08-18 12:45 | 342 | 11kV | 29880 | 169 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S80 Chatswood 11kV panel 30R tripped on Relays: 30R side - C phase IOC Signals: 11kV Trip EFI's NIL Cause: UG Fault from Chatswood to S7847 LV UGOH out of S7847 due to LV Parallels See OMS 1591612 1591613 1590697 1590709 1590732 | August | 2018 | 2019Q1 | 2019 | ZN80:PA30 | ZN80:PA30 | ZN00080/000030 | WILLOUGHBY | UG | Not Veg | 2018-08-18 | N | 176.8047 | N | 4 | N | N | 1.1101 | 39.4971 | 21835.4227
[7 empty] | 6290 | 10773 | 1590792 | 2018-08-18 15:41 | 2018-08-18 16:32 | 51 | 11kV | 2712 | 56 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | Zn14143 Somersby Pa6 trippe don earth fault EFI's: S18379 S14634 Cause: UG fault between S14634 to S1854 See 1591100,2 ex 1590792 | August | 2018 | 2019Q1 | 2019 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | UG | Not Veg | 2018-08-18 | N | 48.4286 | N | 4 | N | N | 1.1101 | 39.4971 | 1981.8496
[7 empty] | 6040 | 8044 | 1590841 | 2018-08-18 21:53 | 2018-08-18 22:58 | 65 | 11kV | 65594 | 1225 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9700 Kirrawee - Pnl.17 tripped on: A phase IOC Field EFIs down to S9807 Abnormal: AB35674 Closed with AB35743 Opened and defective Possum on UGOH at 162 Gymea Bay Rd. Between S9807 and AB35356 tee PT63623. See 1591188 1591189 1591190 | August | 2018 | 2019Q1 | 2019 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Not Veg | 2018-08-18 | N | 53.5461 | N | 4 | N | N | 1.1101 | 39.4971 | 47934.1605
[7 empty] | 6339 | 11285 | 1590850 | 2018-08-19 05:48 | 2018-08-19 06:36 | 48 | 11kV | 3264 | 68 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn36200 Empire Bay Ex Pa4 "Bensville" fdr IR63686 Bundaleer Empire Bay 0.2 tripped, reclosed, tripped and locked out on overcurrent Cause: tree branch removed from overhead near PT11478 See 1590850 ex 1590851 | August | 2018 | 2019Q1 | 2019 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2018-08-19 | N | 48 | N | 4 | N | N | 1.1101 | 39.4971 | 2385.2349
[7 empty] | 6566 | 14004 | 1590856 | 2018-08-19 06:51 | 2018-08-19 12:45 | 354 | 11kV | 708 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 187879 B Phase DOLF : 10 Amp Faulty arrestor replaced under AP Excluded OMS 187879. | August | 2018 | 2019Q1 | 2019 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Not Veg | 2018-08-19 | N | 354 | N | 4 | N | N | 1.1101 | 39.4971 | 517.3855
[7 empty] | 6796 | 16267 | 1590824 | 2018-08-18 17:23 | 2018-08-19 17:35 | 1452 | 11kV | 29932 | 545 | HV | Fire (Non Ausgrid) | UNKNOWN | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 187875 B Phase DOLF 16 Amp Sw 81438 opened for pole fires. DOLF sub 48617 found blown Excluded oms 1590799 | August | 2018 | 2019Q1 | 2019 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Not Veg | 2018-08-18 | N | 54.9211 | N | 4 | N | N | 1.1101 | 39.4971 | 21873.4228
[7 empty] | 6712 | 15257 | 1590898 | 2018-08-19 13:35 | 2018-08-19 18:16 | 281 | 11kV | 1967 | 7 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 187887 Wire broken to DOLF. Report entered by BOB next day. Excluded OMS 1590898. | August | 2018 | 2019Q1 | 2019 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2018-08-19 | N | 281 | N | 4 | N | N | 1.1101 | 39.4971 | 1437.4256
[7 empty] | 6094 | 8686 | 1590955 | 2018-08-19 17:49 | 2018-08-19 19:00 | 71 | 11kV | 1065 | 15 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 187885 Isolated at 11kV Links 75084 to replace xarm braces pole 3H-50051. See reports 187878, 187880,187881, 187884. | August | 2018 | 2019Q1 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2018-08-19 | N | 71 | N | 4 | N | N | 1.1101 | 39.4971 | 778.2706
[7 empty] | 6610 | 14448 | 1590997 | 2018-08-20 07:46 | 2018-08-20 08:03 | 17 | 11kV | 7922 | 901 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn14143 Somersby Pa17 "Somersby Falls" fdr tripped on Relays: ABC phase timed overcurrent EFI: Nil Abnormal: SwB S14023 Closed, SwA S18540 Open (Ex Pa6 fdr defective) Overload due to abnormal switching for defective See 1591317,8 ex 1590997 | August | 2018 | 2019Q1 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | Unknown | Not Veg | 2018-08-20 | N | 8.7925 | N | 2 | N | N | 1.1101 | 39.4971 | 5789.1639
[7 empty] | 5577 | 3288 | 1591202 | 2018-08-20 15:55 | 2018-08-20 17:30 | 95 | 11kV | 36083 | 383 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn711 Blackwattle Bay - Pnl.22 tripped on: Earth fault with EFI Field EFIs: S76757 & S6509 UG cable fault between S6509 (Sw/B) and S2983 (Sw/A) See 1591284 1591285 | August | 2018 | 2019Q1 | 2019 | ZN711:PA22 | ZN384:PA65 | ZN00384/000065 | SYDNEY | UG | Not Veg | 2018-08-20 | N | 94.2115 | N | 2 | N | N | 1.1101 | 39.4971 | 26368.3921
[7 empty] | 7065 | 19313 | 1591258 | 2018-08-21 01:18 | 2018-08-21 02:32 | 74 | 11kV | 420 | 6 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2635 Epping Panel 65 Tripped on Relays: OC and EF, EFI Signals: 11kV trip Cause: 11kV UG Fault from S7391 Macquarie University No.6 SW/B to S6154 Talavera Christie SW/A to S47529 Talavera Technology SW/A See OMS 1591575 1591576 1591258 | August | 2018 | 2019Q1 | 2019 | ZN2635:PA65 | ZN2635:PA65 | ZN02635/000065 | RYDE | UG | Not Veg | 2018-08-21 | N | 70 | N | 1 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 7025 | 18760 | 1591666 | 2018-08-22 14:36 | 2018-08-22 15:25 | 49 | 11kV | 2891 | 59 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 187912 C Phase DOLF : 20 Amp Excluded OMS 1591667. 1591666, 1591673, 1591676 & 1591677. | August | 2018 | 2019Q1 | 2019 | 532:83307 | 532:83300 | ZN00532/083300 | MAITLAND | OH | Veg | 2018-08-22 | N | 49 | N | 2 | N | N | 1.1101 | 39.4971 | 2112.6575
[7 empty] | 6285 | 10746 | 1593578 | 2018-08-22 23:35 | 2018-08-23 01:56 | 141 | 11kV | 159594 | 1510 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN874 Concord Panel No.22 'Norman majors' feeder tripped on Signals: 11kv trip, Tx1 Group Earth, Zone Earth Relays: B phase Overcurrent, EFI Remarks: UG fault. UG fault between S7817 Phillips St No.2 and S3196 Phillips St No.1 | August | 2018 | 2019Q1 | 2019 | ZN874:PA22 | ZN874:PA22 | ZN00874/000022 | CANADA BAY | UG | Not Veg | 2018-08-22 | N | 105.6914 | N | 2 | N | N | 1.1101 | 39.4971 | 116626.588
[7 empty] | 5549 | 2832 | 1591995 | 2018-08-23 22:53 | 2018-08-23 23:35 | 41.9667 | 11kV | 3735.0333 | 89 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 187922 C Phase DOLF : 40 Amp POSSUM AT SUB POLE. Excluded OMS 1591999. | August | 2018 | 2019Q1 | 2019 | 258:80784 | 258:80784 | ZN00258/080784 | NEWCASTLE | OH | Not Veg | 2018-08-23 | N | 41.9667 | N | 1 | N | N | 1.1101 | 39.4971 | 2729.4522
[7 empty] | 6821 | 16618 | 1592006 | 2018-08-24 05:47 | 2018-08-24 09:25 | 218 | 11kV | 872 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP26228 Valley Rd tripped, reclosed tripped and locked out on IOC trip, OC trip and lockout Cause: tree branch on OH mains under Roseville Bridge | August | 2018 | 2019Q1 | 2019 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2018-08-24 | N | 218 | N | 2 | N | N | 1.1101 | 39.4971 | 637.2319
[7 empty] | 7158 | 20071 | 1592188 | 2018-08-24 17:09 | 2018-08-24 17:56 | 47 | 11kV | 52734 | 1122 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 187941 burnt off tapping pole JT-80432 Excluded OMS 1592189, 1592190 | August | 2018 | 2019Q1 | 2019 | 258:80781 | 258:80781 | ZN00258/080781 | NEWCASTLE | OH | Not Veg | 2018-08-24 | N | 47 | N | 2 | N | N | 1.1101 | 39.4971 | 38536.4518
[7 empty] | 6515 | 13513 | 1592228 | 2018-08-25 07:41 | 2018-08-25 10:40 | 179 | 11kV | 179 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 187943 Burnt off tapping to DOLF. Customer reports pump motor is now burnt out. Excluded OMS 1592228 | August | 2018 | 2019Q1 | 2019 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2018-08-25 | N | 179 | N | 5 | N | N | 1.1101 | 39.4971 | 130.8079
[7 empty] | 6532 | 13679 | 1592251 | 2018-08-25 10:09 | 2018-08-25 12:46 | 157 | 11kV | 142716 | 933 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S3154 St Ives Panel 17 tripped on Relays: Earth Fault, EFI, Lockout and Timer. Signals: 11kV Tirp, TX3 Group Earth, Zone Earth Cause: At PT39 Waterhouse Torrens, tree branch was across surge arrestors. Removed by DOP. Secondary problem was caused by suspect relay malfunction a2 S3154 St ives See OMS 1593377 1592251 | August | 2018 | 2019Q1 | 2019 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Veg | 2018-08-25 | N | 152.9646 | N | 5 | N | N | 1.1101 | 39.4971 | 104292.6434
[7 empty] | 5840 | 5828 | 1592401 | 2018-08-25 13:53 | 2018-08-25 16:37 | 164 | 11kV | 35231 | 216 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn1489 Wyong Ex Pa5 "Wyong" RE62705 Jilliby Durren has tripped Relays: IOC trip, OC trip and Lock out Cause: Tree/Branch on OH Mains Branch @ USL 43990. AL44784 did not grade during fault See 1592966,7,8 ex 1592401,2 | August | 2018 | 2019Q1 | 2019 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2018-08-25 | N | 163.1065 | N | 5 | N | N | 1.1101 | 39.4971 | 25745.7757
[7 empty] | 6522 | 13605 | 1592441 | 2018-08-25 15:30 | 2018-08-25 17:17 | 107 | 11kV | 963 | 9 | HV | Lightning Strike | Adverse Weather/Environment | OTHER - REFER COMMENTS | Unplanned | Rain Wind Storm | N | Zn12650 West Gosford Ex Pa1 "Dog Trap Road" fdr PT12166 Glen Boorawa 0.2 has blown footpath side fuse (16A 100kVA) Cause: lightning. Storm in area See 1592974 ex 1592441,51 | August | 2018 | 2019Q1 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | Unknown | Not Veg | 2018-08-25 | N | 107 | N | 5 | N | N | 1.1101 | 39.4971 | 703.732
[7 empty] | 6250 | 10423 | 1592429 | 2018-08-25 14:45 | 2018-08-25 18:15 | 210 | 11kV | 630 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 187948 Single phase DOLF : 10 Amp replaced 2 x 10A Dolfs, 2 x la's and lvf assembly Excluded OMS 1592429 | August | 2018 | 2019Q1 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2018-08-25 | N | 210 | N | 5 | N | N | 1.1101 | 39.4971 | 460.3854
[7 empty] | 5382 | 535 | 1592542 | 2018-08-26 14:57 | 2018-08-26 16:40 | 103 | 11kV | 103 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 187963 Single phase DOLF : 10 Amp Excluded OMS 1592542 | August | 2018 | 2019Q1 | 2019 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Veg | 2018-08-26 | N | 103 | N | 3 | N | N | 1.1101 | 39.4971 | 75.2694
[7 empty] | 5607 | 3610 | 1592549 | 2018-08-26 16:27 | 2018-08-26 17:45 | 78 | 11kV | 7878 | 101 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 187965 A Phase DOLF : 40 Amp Excluded OMS 1592549 | August | 2018 | 2019Q1 | 2019 | 524:33578 | 524:33578 | ZN00524/033578 | CESSNOCK | OH | Veg | 2018-08-26 | N | 78 | N | 3 | N | N | 1.1101 | 39.4971 | 5757.01
[7 empty] | 5419 | 1090 | 1592570 | 2018-08-26 19:54 | 2018-08-26 21:03 | 69 | 11kV | 80568 | 1872 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Zn9118 Cronulla - Pnl.11 tripped on: ABC IOC and EFI Field EFIs: S9755 S9596 S9367 S9751 S9853 S9846 Possum on REC35756 Bundeena - Cleared by DOP | August | 2018 | 2019Q1 | 2019 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2018-08-26 | N | 43.0385 | N | 3 | N | N | 1.1101 | 39.4971 | 58876.718
[7 empty] | 6391 | 11922 | 1592712 | 2018-08-27 11:36 | 2018-08-27 12:40 | 64 | 11kV | 24704 | 386 | HV | Vandalism | 3rd Party Impact | Air Break Switch | Unplanned | No Weather Impact | N | LID 187973 no protection operation ABS 16051 opened by member of the public. Excluded oms # 1592712 & 1592715 | August | 2018 | 2019Q1 | 2019 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Not Veg | 2018-08-27 | N | 64 | N | 5 | N | N | 1.1101 | 39.4971 | 18052.9546
[7 empty] | 6558 | 13877 | 1592588 | 2018-08-27 07:24 | 2018-08-27 13:20 | 356 | 11kV | 1424 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 187974 A Phase Repair broken away lead to 11kV links 6069. Excluded OMS No. 1592588 | August | 2018 | 2019Q1 | 2019 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2018-08-27 | N | 356 | N | 5 | N | N | 1.1101 | 39.4971 | 1040.6172
[7 empty] | 7000 | 18546 | 1592740 | 2018-08-27 12:42 | 2018-08-27 13:45 | 63.15 | 11kV | 4104.75 | 65 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 187975 B Phase Bph broken lead to sub DOLF. CC1: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" | August | 2018 | 2019Q1 | 2019 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | OH | Not Veg | 2018-08-27 | N | 63.15 | N | 5 | N | N | 1.1101 | 39.4971 | 2999.6302
[7 empty] | 5893 | 6350 | 1592879 | 2018-08-27 22:36 | 2018-08-27 23:53 | 77 | 11kV | 3234 | 42 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At Zn8000 Macquarie Pak Panel 24 tripped on Signals: 11kV trip Relays: 51N E/F, EFI and Fault Check Cause: UG Cable damaged by contractor See OMS 1593472 1592874 Mustafa (0407416826) has hit cable during excavation opposite Rennie St (North Side of Delhi Rd). Fault Located electrically on the right leg of Panel 24 to S35682 | August | 2018 | 2019Q1 | 2019 | ZN8000:PA24 | ZN8000:PA24 | ZN08000/000024 | RYDE | UG | Not Veg | 2018-08-27 | N | 77 | N | 5 | N | N | 1.1101 | 39.4971 | 2363.3118
[7 empty] | 7020 | 18713 | 1592953 | 2018-08-28 12:25 | 2018-08-28 13:40 | 75 | 11kV | 2175 | 29 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 187977 emergency repair to x arm pole LQ-30330 Tareen Rd Karuah. | August | 2018 | 2019Q1 | 2019 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2018-08-28 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 1589.4258
[7 empty] | 7086 | 19482 | 1593019 | 2018-08-28 14:50 | 2018-08-28 15:40 | 50 | 11kV | 450 | 9 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 187981 Interruption required to safely reconnect 11kV main on cross arm and attach to insulator. No protection operation. | August | 2018 | 2019Q1 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-08-28 | N | 50 | N | 3 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 5433 | 1202 | 1593052 | 2018-08-28 17:00 | 2018-08-28 22:15 | 315 | 11kV | 9369 | 34 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 187983 11kV OH link on pole ES-34962 pole ES-34962 needed replacing urgently. Excluded OMS 1593052 | August | 2018 | 2019Q1 | 2019 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2018-08-28 | N | 275.5588 | N | 3 | N | N | 1.1101 | 39.4971 | 6846.5889
[7 empty] | 5516 | 2237 | 1593177 | 2018-08-29 11:05 | 2018-08-29 13:15 | 130 | 11kV | 260 | 2 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Fuse Assembly | Unplanned | No Weather Impact | N | LID 187992 C Phase loose fuse reset power restored Excluded oms 1593177 | August | 2018 | 2019Q1 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Not Veg | 2018-08-29 | N | 130 | N | 3 | N | N | 1.1101 | 39.4971 | 190.0003
[7 empty] | 6650 | 14814 | 1592741 | 2018-08-27 12:49 | 2018-08-29 13:40 | 2931 | 11kV | 12785 | 161 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1290 Leightonfield Panel No.13 'Christina Birmingham No.2' feeder tripped on Signals: 11kv Trip, Zone Earth, Tx1 Group earth, Tx3 Group earth Relays: Earth fault Remarks: UG fault | August | 2018 | 2019Q1 | 2019 | ZN1290:PA13 | ZN1290:PA13 | ZN01290/000013 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-08-27 | N | 79.4099 | N | 5 | N | N | 1.1101 | 39.4971 | 9342.9009
[7 empty] | 6078 | 8363 | 1593370 | 2018-08-29 16:32 | 2018-08-29 16:37 | 5 | 11kV | 6465 | 1293 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 187999 C Phase Overcurrent fdr tripped when trying to restore,sub 50693 had not been isolated as assumed. Poor communication with operator by AOP. | August | 2018 | 2019Q1 | 2019 | 522:83123 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2018-08-29 | N | 5 | N | 3 | N | N | 1.1101 | 39.4971 | 4724.4313
[7 empty] | 7095 | 19545 | 1593223 | 2018-08-29 14:57 | 2018-08-29 17:20 | 143 | 11kV | 7722 | 54 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 188000 faulty sub 50693 isolated for replacement and replace lv x-arm, sub interconnected for repairs see report187998/OMS 1593369 & 187999/OMS 1593370 | August | 2018 | 2019Q1 | 2019 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2018-08-29 | N | 143 | N | 3 | N | N | 1.1101 | 39.4971 | 5643.0098
[7 empty] | 5470 | 1600 | 1593301 | 2018-08-30 07:40 | 2018-08-30 09:14 | 94 | 11kV | 14799 | 159 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 188007 1 fault operation 3 phase Sensitive Earth Fault 11kV UGM damaged by tractor digging holes. Excluded OMS No. 1593301 + 1593306 | August | 2018 | 2019Q1 | 2019 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | UG | Not Veg | 2018-08-30 | N | 93.0755 | N | 5 | N | N | 1.1101 | 39.4971 | 10814.6727
[7 empty] | 7165 | 20167 | 1593327 | 2018-08-30 07:46 | 2018-08-30 09:30 | 104 | 11kV | 5200 | 50 | HV | Animal Bird | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Ex pa24 "Hammond Park" PT14128 Jessica Cynthia roadside 31.5k HDO blown due to cockatoo on transformer See 1593314 ex 1593313,5,27 | August | 2018 | 2019Q1 | 2019 | ZN12610:PA24 | ZN12610:PA24 | ZN12610/000024 | CENTRAL COAST | OH | Not Veg | 2018-08-30 | N | 104 | N | 5 | N | N | 1.1101 | 39.4971 | 3800.0066
[7 empty] | 6909 | 17660 | 1593290 | 2018-08-30 05:39 | 2018-08-30 10:34 | 295 | 11kV | 106325 | 375 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Cold <10C | N | LID 188002 2 fault operation 3 phase Earth Fault; Overcurrent IQ-42101 11kV mains down Excluded OMS 1593290 | August | 2018 | 2019Q1 | 2019 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2018-08-30 | N | 283.5333 | N | 5 | N | N | 1.1101 | 39.4971 | 77699.1739
[7 empty] | 6280 | 10706 | 1593379 | 2018-08-30 11:09 | 2018-08-30 12:15 | 66 | 11kV | 1122 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 188008 B Phase DOLF : 31 Amp Excluded OMS 1593379 | August | 2018 | 2019Q1 | 2019 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2018-08-30 | N | 66 | N | 5 | N | N | 1.1101 | 39.4971 | 819.9245
[7 empty] | 6491 | 13205 | 1593505 | 2018-08-30 21:52 | 2018-08-30 22:54 | 62 | 11kV | 82832 | 1336 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | At ZN9118 Cronulla 11kv feeder Panel No.21 "Carona Ave West" feeder tripped and locked out on: Relays: E/F, sealing contactor, EFI Remarks: flashover at Q type PT9563 by possum. Note Panel NO21 CB failed to close tpe to attend | August | 2018 | 2019Q1 | 2019 | ZN9118:PA21 | ZN9118:PA21 | ZN09118/000021 | SUTHERLAND | OH | Not Veg | 2018-08-30 | N | 62 | N | 5 | N | N | 1.1101 | 39.4971 | 60531.1825
[7 empty] | 6361 | 11602 | 1593545 | 2018-08-31 11:30 | 2018-08-31 13:15 | 105 | 11kV | 105 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188021 Fdr isolated to repair broken 11kV OHM at pole HQ-345513. In association with planned SI 29173. Excluded OMS 1593545 | August | 2018 | 2019Q1 | 2019 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2018-08-31 | N | 105 | N | 2 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 5992 | 7446 | 1593568 | 2018-08-31 14:35 | 2018-08-31 15:50 | 75 | 11kV | 75 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 188024 Single phase DOLF : 10 Amp | August | 2018 | 2019Q1 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2018-08-31 | N | 75 | N | 2 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 6658 | 14904 | 1593674 | 2018-09-01 08:21 | 2018-09-01 09:30 | 69 | 11kV | 3450 | 50 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty Ex pa24 PT14128 footpath phase 31.5 HDO operated Signals: EFI Fault Check Cause: animals/birds. strike at PT14128 mains to check for damage See 1593674 ex 1593675 CC1: 22-"Refer to SOp" | September | 2018 | 2019Q1 | 2019 | ZN12610:PA24 | ZN12610:PA24 | ZN12610/000024 | CENTRAL COAST | OH | Not Veg | 2018-09-01 | N | 69 | N | 2 | N | N | 1.1101 | 39.4971 | 2521.1582
[7 empty] | 5847 | 5858 | 1593750 | 2018-09-01 19:26 | 2018-09-01 21:50 | 144 | 11kV | 5485 | 40 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35700 Port Botany - Pnl.13 tripped on: Earth Fault Field EFIs: S49323 S50353 S50569 S5211 S5022 S6134 S455 S492 S8356 (S8139 no access) UG cable fault between S8536 (Sw/B) and S6778 (Sw/B) See 1594163 1594166 | September | 2018 | 2019Q1 | 2019 | ZN35700:PA13 | ZN35700:PA13 | ZN35700/000013 | RANDWICK | UG | Not Veg | 2018-09-01 | N | 137.125 | N | 2 | N | N | 1.1101 | 39.4971 | 4008.2762
[7 empty] | 5675 | 4357 | 1593797 | 2018-09-02 12:31 | 2018-09-03 08:15 | 1184 | 11kV | 1184 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188031 B Phase DOLF : 10 Amp Suspect a bird contacted the mains casing the DOLF to blow. Customer advised ok to leave overnight and restore on Monday morning. Excluded OMS 1593797. | September | 2018 | 2019Q1 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2018-09-02 | N | 1184 | N | 1 | N | N | 1.1101 | 39.4971 | 865.2323
[7 empty] | 5632 | 3816 | 1593881 | 2018-09-03 09:15 | 2018-09-03 10:15 | 60 | 11kV | 2446 | 47 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 188034 Pin off 11kV insulator, interruption only to allow repairs. No protection operations. Excluded OMS 1593881. | September | 2018 | 2019Q1 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2018-09-03 | N | 52.0426 | N | 4 | N | N | 1.1101 | 39.4971 | 1787.4647
[7 empty] | 5399 | 819 | 1593916 | 2018-09-03 11:10 | 2018-09-03 12:05 | 55 | 11kV | 80937 | 1519 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Zn12570 Avoca Pa37 "Avoca Beach" fdr tripped Relays: SEL EFI: Nil Cause: bond 11kv roadside bond burnt off LK43385 See 1594126,7,8 ex 1593916 | September | 2018 | 2019Q1 | 2019 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2018-09-03 | N | 53.2831 | N | 4 | N | N | 1.1101 | 39.4971 | 59146.3724
[7 empty] | 6141 | 9323 | 1593990 | 2018-09-03 15:18 | 2018-09-03 17:33 | 135 | 11kV | 270 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 188044 B Phase Open circuit dropper cable at top of DOLF No protection operated. Excluded oms 1593990 and 1593992 | September | 2018 | 2019Q1 | 2019 | 512:83732 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2018-09-03 | N | 135 | N | 4 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 5884 | 6216 | 1594077 | 2018-09-03 22:46 | 2018-09-03 23:50 | 64 | 11kV | 54976 | 859 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn398 Dulwich Hill Zone Panel 25 labelled Prospect Cant tripped on B phase overcurrent and earth fault EFI 11kv trip Efi's Nil Cause: UG Fault section of 11kv fdr from Panel 25 to S7751 SwA | September | 2018 | 2019Q1 | 2019 | ZN398:PA25 | ZN398:PA25 | ZN00398/000025 | INNER WEST | UG | Not Veg | 2018-09-03 | N | 64 | N | 4 | N | N | 1.1101 | 39.4971 | 40174.8393
[7 empty] | 6604 | 14384 | 1594084 | 2018-09-04 06:00 | 2018-09-04 11:50 | 350 | 11kV | 1050 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188051 Open circuit dolf dropper cable. No fuse blew. Excluded OMS 1594084. | September | 2018 | 2019Q1 | 2019 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2018-09-04 | N | 350 | N | 2 | N | N | 1.1101 | 39.4971 | 767.309
[7 empty] | 6680 | 15077 | 1594160 | 2018-09-04 21:05 | 2018-09-04 21:20 | 15 | 11kV | 15 | 1 | HV | Vandalism | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188060 earths found stolen at sub 20066. Sub isolated for repair under AP. Excluded OMS 1594160 | September | 2018 | 2019Q1 | 2019 | 243:80075 | 243:80075 | ZN00243/080075 | CENTRAL COAST | OH | Not Veg | 2018-09-04 | N | 15 | N | 2 | N | N | 1.1101 | 39.4971 | 10.9616
[7 empty] | 5742 | 5125 | 1594284 | 2018-09-05 09:05 | 2018-09-05 09:32 | 27 | 11kV | 27 | 1 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn8700 City North - "B" group bar tripped on: BB Earth Fault 56/66B Panel tripped on: 50T B & C, 51N Staff error, Normally open point left closed when identifying feeder 56/66B. Planned feeder transfer work | September | 2018 | 2019Q1 | 2019 |  |  |  |  | Unknown | Not Veg | 2018-09-05 | N | 27 | N | 1 | N | N | 1.1101 | 39.4971 | 19.7308
[7 empty] | 5422 | 1114 | 1594516 | 2018-09-06 12:39 | 2018-09-06 13:40 | 61 | 11kV | 83504 | 1496 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.20 tripped on: Overcurrent Field EFI:S 48367 S77073 UG cable fault between S77073 (sw/B) and S48848 (Sw/A) See 1594649 1594650 | September | 2018 | 2019Q1 | 2019 | ZN2602:PA20 | ZN36800:PA54 | ZN36800/000054 | WAVERLEY | UG | Not Veg | 2018-09-06 | N | 55.8182 | N | 1 | N | N | 1.1101 | 39.4971 | 61022.2602
[7 empty] | 7014 | 18651 | 1594621 | 2018-09-07 01:39 | 2018-09-07 03:32 | 113 | 11kV | 6441 | 57 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 188078 Possum flashed over at EL-80011 | September | 2018 | 2019Q1 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2018-09-07 | N | 113 | N | 7 | N | N | 1.1101 | 39.4971 | 4706.8928
[7 empty] | 5469 | 1583 | 1594646 | 2018-09-07 07:54 | 2018-09-07 11:55 | 241 | 11kV | 241 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 188083 B Phase DOLF : 16 Amp Surge arrestor Excluded OMS 1594646 | September | 2018 | 2019Q1 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2018-09-07 | N | 241 | N | 7 | N | N | 1.1101 | 39.4971 | 176.1157
[7 empty] | 5362 | 292 | 1594675 | 2018-09-07 09:39 | 2018-09-07 16:15 | 396 | 11kV | 3627 | 29 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 188085 DOLF burning up & Stranded mains Excluded OMS 1594675 & 1594744 | September | 2018 | 2019Q1 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Not Veg | 2018-09-07 | N | 125.069 | N | 7 | N | N | 1.1101 | 39.4971 | 2650.5046
[7 empty] | 5985 | 7290 | 1594783 | 2018-09-07 17:40 | 2018-09-07 21:10 | 210 | 11kV | 226510 | 1942 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Lightning | N | At ZN3472 Sefton 11kv feeder Panel No.30 "Royal Gas etc" feeder tripped and locked out on: Relays: micom relay A - C phase O/C, EFI Remarks: storm, Note: T and Rec earlier @ 17:33 *11kv AB2354 damaged by lightning - section of 11kv feeder from AB2354 to LB2210 tee PT2466 Higgins Manaham | September | 2018 | 2019Q1 | 2019 | ZN3472:PA30 | ZN3472:PA30 | ZN03472/000030 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-09-07 | N | 116.6375 | N | 7 | N | N | 1.1101 | 39.4971 | 165526.8271
[7 empty] | 5383 | 578 | 1594790 | 2018-09-07 17:49 | 2018-09-07 21:10 | 201 | 11kV | 120642 | 1017 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | N | Zn10994 Mortdale - Pnl.19 tripped on: A & C phase IOC Field EFIs: All down to S10040 Bond burnt off pole PE12179 (cnr Linden and Valencia Sts) Between PT64515 and LB31303. Reports of lightning strike. See 1595395 1595397 1595400 | September | 2018 | 2019Q1 | 2019 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2018-09-07 | N | 118.6254 | N | 7 | N | N | 1.1101 | 39.4971 | 88161.6153
[7 empty] | 5499 | 1964 | 1594846 | 2018-09-07 20:10 | 2018-09-07 23:00 | 170 | 11kV | 124428 | 810 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn9035 Caringbah - Pnl.2 tripped on: IOC B phase O/C UG cable fault betwen S9342 (Sw/B) and S9574 (Sw/B) and S9905 (Sw/D) See 1595404 1595407 GIS 1594879 | September | 2018 | 2019Q1 | 2019 | ZN9035:PA2 | ZN9035:PA2 | ZN09035/000002 | SUTHERLAND | UG | Not Veg | 2018-09-07 | N | 153.6148 | N | 7 | N | N | 1.1101 | 39.4971 | 90928.3124
[7 empty] | 6685 | 15111 | 1594852 | 2018-09-07 20:39 | 2018-09-08 01:05 | 266 | 11kV | 62466 | 651 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Lightning | N | Ex Zn10990 Arncliffe - Pnl.12 AB31051 struck by lightning. Loss of supply to customers downstream from AB31051. Isolated section for repair. | September | 2018 | 2019Q1 | 2019 | ZN10990:PA12 | ZN10998:PA9 | ZN10998/000009 | BAYSIDE | OH | Not Veg | 2018-09-07 | N | 95.9539 | N | 7 | N | N | 1.1101 | 39.4971 | 45648.3104
[7 empty] | 6325 | 11183 | 1594921 | 2018-09-08 07:37 | 2018-09-08 08:35 | 58 | 11kV | 6206 | 107 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 188091 Sub 9261 transformer faulty & crossarm broken interconnected for repairs Excluded OMS 1594921 | September | 2018 | 2019Q1 | 2019 | 221:11900 | 221:11900 | ZN00221/011900 | LAKE MACQUARIE | OH | Not Veg | 2018-09-08 | N | 58 | N | 5 | N | N | 1.1101 | 39.4971 | 4535.1618
[7 empty] | 5676 | 4379 | 1594903 | 2018-09-08 00:33 | 2018-09-08 15:33 | 900 | 11kV | 39600 | 44 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Snow / Hail Storm | N | Zn12650 West Gosford Ex Pa1 "Bentley Rd" RE44853 "bentley Rd" tripped and locked out Abnormal: rec was one shot with CI inhibit alarm Cause: OH Down. 11kV overhead down in bush near pole OU 689 near 617 ourimbah creeek rd 1594903 ex 1594905,6 | September | 2018 | 2019Q1 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2018-09-08 | N | 900 | N | 5 | N | N | 1.1101 | 39.4971 | 28938.512
[7 empty] | 5665 | 4309 | 1594955 | 2018-09-08 11:02 | 2018-09-08 15:59 | 297 | 11kV | 2460 | 11 | HV | Staff Operation | Utility Process Issue | 3rd Party Asset | Unplanned | No Weather Impact | N | Ex 11kv Panel No.31 "S2265, S5392, etc" feeder from Zn2835 Burwood Section of feeder from S4130 Weeroona Rd North to S3746 Weeroona Centenary no.2 tee Sub 850 Rookwood Cemetery No.2 & S879 Rookwood Cemetery No.3 interrupted by Dop. Interrupted for safety reasons. Feeder interrupted by Dop due to fault @ S879 Rookwood Cemetery No.3. Note: Auto changeover did not work @ S3746 Weeroona Centenary No.2 | September | 2018 | 2019Q1 | 2019 | ZN2835:PA31 | ZN2835:PA31 | ZN02835/000031 | CUMBERLAND | Unknown | Not Veg | 2018-09-08 | N | 223.6364 | N | 5 | N | N | 1.1101 | 39.4971 | 1797.6954
[7 empty] | 5694 | 4602 | 1594982 | 2018-09-08 11:13 | 2018-09-08 17:05 | 351.5833 | 11kV | 351.5833 | 1 | HV | Burnt Contacts | Equipment Failure | O/H Conductor Insulated | Unplanned | No Weather Impact | N | LID 188090 A Phase 10 Amp fuse Repaired burnt LVF assembly and wiring at sub due to cable insulation breakdown | September | 2018 | 2019Q1 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2018-09-08 | N | 351.5833 | N | 5 | N | N | 1.1101 | 39.4971 | 256.9267
[7 empty] | 5816 | 5652 | 1595049 | 2018-09-08 19:23 | 2018-09-09 01:40 | 377 | 11kV | 377 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 188092 A Phase DOLF : 10 Amp Smoke coming from Tx. Transformer faulty. 240V, 240V, 180V. Excluded OMS 1595049 | September | 2018 | 2019Q1 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2018-09-08 | N | 377 | N | 5 | N | N | 1.1101 | 39.4971 | 275.5005
[7 empty] | 6794 | 16252 | 1595155 | 2018-09-10 01:46 | 2018-09-10 06:08 | 262 | 11kV | 649426 | 4381 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15008 Harbord Panel 7 Tripped, reclosed tripped and locked pout on Relays: B and Cphase IOC, EF, SEF, Reclose, Timing and Lockout Signals: 11kV trip Pa7 and Pa10 Secondary Trip : SEF Cause: Possum on OH mains adjacent to PT15714 - This led to secondary 11kV Bond off and LV bay of mains down. See OMS 1595581 1595597 1595596 1595582 1595155 | September | 2018 | 2019Q1 | 2019 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2018-09-10 | N | 148.2369 | N | 6 | N | N | 1.1101 | 39.4971 | 474581.366
[7 empty] | 6696 | 15171 | 1595242 | 2018-09-10 11:26 | 2018-09-10 12:18 | 52 | 11kV | 1274 | 34 | HV | 3rd Party Vehicle | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 188106 1 fault operation Earth Fault, Overcurrent Third party has drilled into 11kV & LV cable. Excluded OMS 1595242 | September | 2018 | 2019Q1 | 2019 | 202:34231 37 42 | 202:34231 37 42 | ZN00202/34231 37 42 | NEWCASTLE | UG | Not Veg | 2018-09-10 | N | 37.4706 | N | 6 | N | N | 1.1101 | 39.4971 | 931.0016
[7 empty] | 6230 | 10254 | 1595226 | 2018-09-10 10:05 | 2018-09-10 12:30 | 145 | 11kV | 241533 | 2663 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.1 tripped on: (Pnl.1 Right) Earth Fault, C phase O/C Earth stake driven through Optus pit be Beldan Communications outside 367 Anzac Pde, Kensington See 1593305 | September | 2018 | 2019Q1 | 2019 | ZN35600:PA1 | ZN35600:PA1 | ZN35600/000001 | RANDWICK | UG | Not Veg | 2018-09-10 | N | 90.6996 | N | 6 | N | N | 1.1101 | 39.4971 | 176505.1924
[7 empty] | 6709 | 15245 | 1595277 | 2018-09-10 12:34 | 2018-09-10 14:40 | 126 | 11kV | 201230 | 1683 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At ZN35900 Potts Hill 11kv feeder Panel No.24 "Potts Hill Aux No2" feeder tripped on: Relays: Basler Relay: minor alrm, 50TN & 51AB Signals: 11kv trip Field EFI's: Nil Remarks: Vehicle hit pole. A car hit pole on Joseph St nr Amy St, Lidcombe. This caused the 11kv cross arm to snap | September | 2018 | 2019Q1 | 2019 | ZN35900:PA24 | ZN35900:PA24 | ZN35900/000024 | CUMBERLAND | OH | Not Veg | 2018-09-10 | N | 119.5663 | N | 6 | N | N | 1.1101 | 39.4971 | 147052.9487
[7 empty] | 6460 | 12841 | 1595156 | 2018-09-10 04:14 | 2018-09-10 17:35 | 801 | 11kV | 616671 | 1811 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15015 North Head Ex Panel 5 S16194 Manly Hospital No.1 11kv CB "B" tripped on: Relays: EF EFI: S16194 S16136 S16721 S15820 Cause: UG Fault. 11kV UG Cable fault from S15820 to S50491 See 1595538,9,40,1,2 GIS 1595161 ex 1595156,9,66,70,205,6,7,522,3,4 | September | 2018 | 2019Q1 | 2019 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | UG | Not Veg | 2018-09-10 | N | 340.5141 | N | 6 | N | N | 1.1101 | 39.4971 | 450644.9781
[7 empty] | 6938 | 17908 | 1595563 | 2018-09-11 11:47 | 2018-09-11 12:26 | 39 | 11kV | 4524 | 116 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | 11kV panel 5 - S15166 Holden Gosford Hospital etc tripped under fault protection relay A phase overcurrent trip Earth fault trip TX11 earth fault trip Signal Operations @ Zone sub 11kV trip Cause: UG cable fault See OMS 1597095 1595563 | September | 2018 | 2019Q1 | 2019 | ZN12650:PA5 | ZN12650:PA5 | ZN12650/000005 | CENTRAL COAST | UG | Not Veg | 2018-09-11 | N | 39 | N | 1 | N | N | 1.1101 | 39.4971 | 3306.0058
[7 empty] | 5639 | 3927 | 1595460 | 2018-09-10 20:06 | 2018-09-11 17:42 | 1296 | 11kV | 29268 | 151 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn711 Blackwattle Bay - Pnl.22 tripped on: Earth Fault with EFI Abnormal: S2983 (Sw/B) closed with (Sw/A) Open. Defective UG cable from S2983 (Sw/A) to S6509 (Sw/B) - Pnl.22 radial UG cable fault on front line section of feeder from Pnl.22 to S76757 (Sw/A). Note: S76757 - construction site with no access, also a N// sub. Delayed restoration due to existing UG defective needing tobe repaired in order to restore supply. See 1595724 1595725 1595726 | September | 2018 | 2019Q1 | 2019 | ZN711:PA22 | ZN7481:PA12 | ZN07481/000012 | SYDNEY | UG | Not Veg | 2018-09-10 | N | 193.8278 | N | 6 | N | N | 1.1101 | 39.4971 | 21388.1911
[7 empty] | 5404 | 871 | 1595811 | 2018-09-12 14:20 | 2018-09-12 15:08 | 48 | 11kV | 59000 | 1253 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 188130 1 fault operation A & C phase Overcurrent, Earth Fault Cable fault at ugoh pole JS-31596 Excluded oms 1595811 | September | 2018 | 2019Q1 | 2019 | 238:34151 | 238:34136 | ZN00238/034136 | MAITLAND | Unknown | Unknown | 2018-09-12 | N | 47.087 | N | 4 | N | N | 1.1101 | 39.4971 | 43115.4598
[7 empty] | 6671 | 15026 | 1595827 | 2018-09-12 14:59 | 2018-09-12 16:40 | 101.2167 | 11kV | 36842.8667 | 364 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP18742 Jilliby Dunks opened and locked out Cause: Tree branch on OH mains near PT12572 See 1595827 ex 1595831,58 CC1: 22-"Refer to SOp" | September | 2018 | 2019Q1 | 2019 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2018-09-12 | N | 101.2167 | N | 4 | N | N | 1.1101 | 39.4971 | 26923.6803
[7 empty] | 5640 | 3951 | 1595891 | 2018-09-12 17:45 | 2018-09-12 21:04 | 199 | 11kV | 43119 | 256 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 188132 A & C Phase Overcurrent fdr 74121 tripped om A 7 C overcurrent, sw 43515 Utah Lane RAGCB overcurent alarm picked up but did not trip. Sw 43515 by passed and power restored. Please investigate sw 43515 Excluded OMS 1595891 | September | 2018 | 2019Q1 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2018-09-12 | N | 168.4336 | N | 4 | N | N | 1.1101 | 39.4971 | 31510.0934
[7 empty] | 5966 | 7068 | 1595929 | 2018-09-12 23:07 | 2018-09-13 01:03 | 116 | 11kV | 214229 | 1984 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S15011 Beacon Hill Panel 4 tripped on Earth Fault,Reclose timer, Lockout, Fault Check and EFI Cause: UG cable fault between S16333 to S16565 to S17066 See OMS 1597298 1597302 1595929 1595931 | September | 2018 | 2019Q1 | 2019 | ZN15011:PA4 | ZN15011:PA4 | ZN15011/000004 | NORTHERN BEACHES | UG | Not Veg | 2018-09-12 | N | 107.9783 | N | 4 | N | N | 1.1101 | 39.4971 | 156552.2345
[7 empty] | 6508 | 13376 | 1596063 | 2018-09-13 14:06 | 2018-09-13 19:45 | 339 | 11kV | 78806 | 922 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 26 tripped on EFI, Lockout, timing relay, A phase IOC and timed O/C, B phase timed O/C Signals: 11kV trip, Group Earth, Protetcion UV Cause: Large tree branch has brought down HV mains from S4494 Bungowen Kooringal tee PT1137 to LB77939 See OMS 1597289 1597290 1597291 1597292 1596063 1596066 1596070 CC1: 22-"Refer to SOp" | September | 2018 | 2019Q1 | 2019 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Veg | 2018-09-13 | N | 85.4729 | N | 1 | N | N | 1.1101 | 39.4971 | 57589.1004
[7 empty] | 6894 | 17502 | 1596229 | 2018-09-14 14:44 | 2018-09-14 15:25 | 41 | 11kV | 67867 | 2135 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 188151 1 fault operation Sensitive Earth Fault Feeder tripped on SEF, 1 blown DOLF found at sub 54081, appears TX tested faulty, being replaced. Excluded OMS 1596229 AND 1596243. | September | 2018 | 2019Q1 | 2019 | 511:29876 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2018-09-14 | N | 31.7878 | N | 1 | N | N | 1.1101 | 39.4971 | 49595.2019
[7 empty] | 6717 | 15287 | 1596541 | 2018-09-15 13:06 | 2018-09-15 15:45 | 159 | 11kV | 477 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188154 Broken Live Line lead Excluded OMS 1596541 | September | 2018 | 2019Q1 | 2019 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2018-09-15 | N | 159 | N | 2 | N | N | 1.1101 | 39.4971 | 348.5775
[7 empty] | 5933 | 6776 | 1596616 | 2018-09-15 22:15 | 2018-09-16 00:10 | 115 | 11kV | 107501 | 1114 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12620 Noraville 11kv feeder panel 10 "Buff Point" fdr tripped Relays: A & B Phase Overload EFI Nil Cause: Not ascertained. Next available linesmen to patrol See 1597029,30,1 ex 1596616,7 | September | 2018 | 2019Q1 | 2019 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Veg | 2018-09-15 | N | 96.5 | N | 2 | N | N | 1.1101 | 39.4971 | 78558.5601
[7 empty] | 5416 | 1058 | 1596955 | 2018-09-18 00:52 | 2018-09-18 02:55 | 123 | 11kV | 99683 | 1590 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188170 2 fault operations Earth Fault Targets = 51N Broken OHM between poles IU-33102 & IU-33112 Lewis St. Excluded OMS 1596955 | September | 2018 | 2019Q1 | 2019 | 258:80785 | 258:80785 | ZN00258/080785 | NEWCASTLE | OH | Not Veg | 2018-09-18 | N | 62.6937 | N | 2 | N | N | 1.1101 | 39.4971 | 72845.3962
[7 empty] | 6317 | 11091 | 1596956 | 2018-09-18 00:49 | 2018-09-18 12:55 | 726 | 11kV | 136478 | 896 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188171 2 fault operations Earth Fault OHM on ground at pole IR-12269 Flat Rd. Excluded OMS 1596956 | September | 2018 | 2019Q1 | 2019 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2018-09-18 | N | 152.3192 | N | 2 | N | N | 1.1101 | 39.4971 | 99734.097
[7 empty] | 6274 | 10626 | 1597150 | 2018-09-19 06:13 | 2018-09-19 07:15 | 62 | 11kV | 3038 | 49 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 188182 C Phase DOLF : 40 Amp Faulty arrestor replaced under AP. Excluded OMS 1597153. | September | 2018 | 2019Q1 | 2019 | 223:14397 | 223:14397 | ZN00223/014397 | LAKE MACQUARIE | OH | Not Veg | 2018-09-19 | N | 62 | N | 2 | N | N | 1.1101 | 39.4971 | 2220.0808
[7 empty] | 5414 | 1013 | 1597223 | 2018-09-19 14:35 | 2018-09-19 15:00 | 25 | 11kV | 75 | 3 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 188189 Coach bolt missing from xarm braces. Excluded OMS 1597276 & 1597223. | September | 2018 | 2019Q1 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2018-09-19 | N | 25 | N | 2 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 6241 | 10354 | 1597449 | 2018-09-20 10:52 | 2018-09-20 13:00 | 128 | 11kV | 94063 | 1035 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kv Panel No.12 at S1290 Leightonfield tripped under fault. Relay: operations at 11kv Pnl#12 @ Zone Sub: SEF trip, EFI, lockout Signal operations at Zone sub: 11kv trip, #3 Tx Group earth Remarks: OH down. Section of 11kv O/H down between LB169 and LB93 tee to PT63837 Hynes St | September | 2018 | 2019Q1 | 2019 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-09-20 | N | 90.8821 | N | 3 | N | N | 1.1101 | 39.4971 | 68738.466
[7 empty] | 7092 | 19522 | 1597522 | 2018-09-20 14:12 | 2018-09-20 14:59 | 47 | 11kV | 1551 | 33 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188200 Stranded mains in steel conductors between poles WB-51907 & WB-51908 Isolated to repair | September | 2018 | 2019Q1 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2018-09-20 | N | 47 | N | 3 | N | N | 1.1101 | 39.4971 | 1133.4251
[7 empty] | 6202 | 10037 | 1597619 | 2018-09-20 17:36 | 2018-09-20 18:20 | 44 | 11kV | 5060 | 115 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188202 B Phase DOLF : 40 Amp Excluded OMS 1597619 1597623, | September | 2018 | 2019Q1 | 2019 | 507:80931 | 507:80931 | ZN00507/080931 | CESSNOCK | OH | Veg | 2018-09-20 | N | 44 | N | 3 | N | N | 1.1101 | 39.4971 | 3697.6988
[7 empty] | 6972 | 18243 | 1597933 | 2018-09-23 01:05 | 2018-09-23 09:05 | 480 | 11kV | 488432 | 2339 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S9035 Caringbah 11kv panel No4 "S9757 Cawarra Dan ETC" feeder tripped on Relays: Panel No.4 right "C" phase, timed O/Current, timing relay, lockout, EFI Signals: 11kv trip Abnormal: Sw/B closed @ S63370 Wurbrock CCT No2, Sw/B opened @ S9574 Captain Woodfield Remarks: UG fault. At S9035 Caringbah ex panel No.4 Right, UGOH is damaged in C awarra Rd North NR sidone place, 11kv wires have come down, lineworkers have ben called to maike repairs. Second UGOH fault located in Cawarra Rd near Parraweena Rd | September | 2018 | 2019Q1 | 2019 | ZN9035:PA4 | ZN9035:PA4 | ZN09035/000004 | SUTHERLAND | UG | Not Veg | 2018-09-23 | N | 208.8209 | N | 1 | N | N | 1.1101 | 39.4971 | 356931.6993
[7 empty] | 6701 | 15196 | 1598013 | 2018-09-24 00:08 | 2018-09-24 01:25 | 77 | 11kV | 81771 | 1381 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2635 Epping Panel 55 tripped on Relays: A phase ioc and EFI Cause: Suspect UG cable fault from S4626 to S64667 to S77015 to S65872 tee PT64863 See OMS 1598817 1598818 1598820 1598013 | September | 2018 | 2019Q1 | 2019 | ZN2635:PA55 | ZN2635:PA55 | ZN02635/000055 | PARRAMATTA | UG | Not Veg | 2018-09-24 | N | 59.2114 | N | 1 | N | N | 1.1101 | 39.4971 | 59755.835
[7 empty] | 5671 | 4332 | 1598301 | 2018-09-25 11:30 | 2018-09-25 11:54 | 24 | 11kV | 3384 | 141 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At PT1472 Hawkesbury River Station was supplied by MG running isolated which tripped on Overload. Cause: MG tripped off 11kV Network and PT1472 Restored. See OMS 1598801 1598301 | September | 2018 | 2019Q1 | 2019 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | Unknown | Unknown | 2018-09-25 | N | 24 | N | 2 | N | N | 1.1101 | 39.4971 | 2472.9274
[7 empty] | 6487 | 13152 | 1598386 | 2018-09-25 19:18 | 2018-09-25 20:25 | 67 | 11kV | 74705 | 1115 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 4 tripped, reclosed tripped and locked out on Relays: A phase overcurrent, A phase IOC and EFI Signals: 11kV trip, zone earth, TX1 group earth Cause: possum came into contact with UGOH near LB65496 | September | 2018 | 2019Q1 | 2019 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | OH | Not Veg | 2018-09-25 | N | 67 | N | 2 | N | N | 1.1101 | 39.4971 | 54592.2106
[7 empty] | 5741 | 5117 | 1598520 | 2018-09-26 11:10 | 2018-09-26 13:20 | 130 | 11kV | 390 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 188236 B Phase DOLF : 10 Amp Excluded OMS 1598520 | September | 2018 | 2019Q1 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2018-09-26 | N | 130 | N | 4 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 6131 | 9226 | 1598561 | 2018-09-26 11:59 | 2018-09-26 13:45 | 106 | 11kV | 2756 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188238 B & C Phase DOLF : 10 Amp T/R at Sw 29878 at 1159hrs as per # 188232 excluded OMS 1598561 | September | 2018 | 2019Q1 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2018-09-26 | N | 106 | N | 4 | N | N | 1.1101 | 39.4971 | 2014.0035
[7 empty] | 5722 | 4975 | 1598575 | 2018-09-26 12:56 | 2018-09-26 14:15 | 79 | 11kV | 158 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 188239 Single phase DOLF : 10 Amp Excluded OMS 1598580 & 1598575 | September | 2018 | 2019Q1 | 2019 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2018-09-26 | N | 79 | N | 4 | N | N | 1.1101 | 39.4971 | 115.4617
[7 empty] | 5587 | 3421 | 1598671 | 2018-09-26 21:48 | 2018-09-26 22:44 | 56 | 11kV | 55888 | 998 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn10994 Mortdale 11kv Panel 18 "Boundary Rd Sth" fdr tripped, reclosed and locked out Relays: A+B phase IOC, I E/Fault, EFI, Timing & Lockout relays Singals: 11kv trip No.3 Group Earth EFI: S10783 S10981 S10648 S10375 Cause: Possum on 11kv ugoh to lb31282 | September | 2018 | 2019Q1 | 2019 | ZN10994:PA18 | ZN10994:PA18 | ZN10994/000018 | GEORGES RIVER | OH | Not Veg | 2018-09-26 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 40841.302
[7 empty] | 5837 | 5791 | 1598680 | 2018-09-27 03:06 | 2018-09-27 04:45 | 99 | 11kV | 173951 | 1941 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S5868 Gore Hill Panel 14 tripped on Relays; Earth fault, Fault Check and EFI Signals: 11kV trip, Zone Earth and No3 Group Earth Cause: 11kV UG fault from S5649 to S804 to S4458 to S3231 See OMS 1598829 1598833 1598680 | September | 2018 | 2019Q1 | 2019 | ZN5868:PA14 | ZN5868:PA14 | ZN05868/000014 | WILLOUGHBY | UG | Not Veg | 2018-09-27 | N | 89.6193 | N | 3 | N | N | 1.1101 | 39.4971 | 127118.2601
[7 empty] | 6605 | 14393 | 1598740 | 2018-09-27 10:58 | 2018-09-27 12:23 | 85 | 11kV | 60095 | 821 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10993 Hurstville North - Pnl.39L tripped, reclosed & locked out on: O/C Field EFIs S48420 S47506 S10543 S10750 UG cable fault from S10750 (Sw/B) to S10941 (Sw/B) to S62944 (Sw/A) See 1598929 1598930 1598931 | September | 2018 | 2019Q1 | 2019 | ZN10993:PA39 | ZN10993:PA39 | ZN10993/000039 | GEORGES RIVER | UG | Not Veg | 2018-09-27 | N | 73.1973 | N | 3 | N | N | 1.1101 | 39.4971 | 43915.6535
[7 empty] | 6634 | 14683 | 1598837 | 2018-09-27 15:50 | 2018-09-27 17:10 | 80 | 11kV | 188896 | 2906 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn10991 Blakehurst - Pnl.6 tripped, reclosed & locked out on: IOC & Timed O/C - A & C phase Field EFIs: S10548 S10576 S10479 S10626 S10595 S10347 Abnormal: Pnl.5 at Blackehurst open with S10576 (Sw/B) closed (LB30244 Defective) UG fault to S1089 Illawarra Norman See 1598920 1598922 | September | 2018 | 2019Q1 | 2019 | ZN10991:PA5 | ZN10991:PA5 | ZN10991/000005 | GEORGES RIVER | Unknown | Unknown | 2018-09-27 | N | 65.0021 | N | 3 | N | N | 1.1101 | 39.4971 | 138039.6253
[7 empty] | 5354 | 184 | 1598946 | 2018-09-28 10:05 | 2018-09-28 12:40 | 154.85 | 11kV | 3097 | 20 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge Ex Pa3 "The mangrove mtn" fdr Cp46938 Ironbark Kirks 0.9 operated Cause: defective links | September | 2018 | 2019Q1 | 2019 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2018-09-28 | N | 154.85 | N | 1 | N | N | 1.1101 | 39.4971 | 2263.1963
[7 empty] | 6674 | 15047 | 1599093 | 2018-09-29 06:04 | 2018-09-29 15:55 | 591 | 11kV | 46349 | 1205 | HV | Vandalism | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 188259 2 fault operations B Phase Earth Fault UGM damaged by attempted theft at SW-30281 Protection 3 phase OC & B phase EF Fault levels A 500a B 10160a C 489a 0642hrs all back on except 0648hrs Sw 12817 back on 1555hrs sub 7936 back on Excluded OMS 1599093 & 1599095 | September | 2018 | 2019Q1 | 2019 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | UG | Not Veg | 2018-09-29 | N | 38.4639 | N | 2 | N | N | 1.1101 | 39.4971 | 33870.4821
[7 empty] | 5987 | 7301 | 1599165 | 2018-09-29 15:12 | 2018-09-29 16:23 | 71 | 11kV | 3124 | 44 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Zn12650 West Gosford Ex Panel 1 "Dog Trap Rd" RE44853 Ourimbah Bumble tripped Relays: O/C trip, lockout Cause: not ascertained See 1599165 ex 1599166 | September | 2018 | 2019Q1 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2018-09-29 | N | 71 | N | 2 | N | N | 1.1101 | 39.4971 | 2282.9271
[7 empty] | 7019 | 18698 | 1599212 | 2018-09-30 06:57 | 2018-09-30 08:00 | 63 | 11kV | 6363 | 101 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188260 A Phase DOLF : 40 Amp Possum 0657hrs A phase 40A DOLF sub 15190 supply back on 0800hrs Excluded OMS 1599212 | September | 2018 | 2019Q1 | 2019 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2018-09-30 | N | 63 | N | 2 | N | N | 1.1101 | 39.4971 | 4649.8927
[7 empty] | 6159 | 9475 | 1599279 | 2018-09-30 23:21 | 2018-10-01 02:29 | 188 | 11kV | 3384 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 188262 Single phase DOLF : 5 Amp Excluded OMS 1599279 | September | 2018 | 2019Q1 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2018-09-30 | N | 188 | N | 2 | N | N | 1.1101 | 39.4971 | 2472.9274
[7 empty] | 6881 | 17349 | 1599304 | 2018-10-01 11:32 | 2018-10-01 12:20 | 48 | 11kV | 576 | 12 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188264 C Phase DOLF : 10 Amp Magpie Excluded OMS 1599304 & 1599308 | October | 2018 | 2019Q2 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2018-10-01 | N | 48 | N | 1 | N | N | 1.1101 | 39.4971 | 420.9238
[7 empty] | 6082 | 8433 | 1599360 | 2018-10-02 00:05 | 2018-10-02 00:48 | 43 | 11kV | 16813 | 391 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN847 Hornsby Panel 14 - feeder tripped on. Signals: 11 kV trip, Zone Earth. Tx1 group Relays: C phase IOC, EFI, Fault check Possum Came across HV UGOH between S8556 and AB1714. | October | 2018 | 2019Q2 | 2019 | ZN847:PA14 | ZN847:PA14 | ZN00847/000014 | HORNSBY | OH | Not Veg | 2018-10-02 | N | 43 | N | 3 | N | N | 1.1101 | 39.4971 | 12286.4445
[7 empty] | 5902 | 6403 | 1599399 | 2018-10-02 08:43 | 2018-10-02 10:07 | 84 | 11kV | 82918 | 1317 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3155 Double Bay - Pnl.23 tripped on: O/C & E/F Field EFIs: S3694 Abnormal: S315 plumber Rd - Sw/K & Sw/H open with Sw/J closed. Sw/A @ S318 Closed UG cable fault between S3694 Sw/B & S1871 Sw/A & S6628 Sw/A See 1599626 1599627 | October | 2018 | 2019Q2 | 2019 | ZN3155:PA23 | ZN3155:PA23 | ZN03155/000023 | WOOLLAHRA | UG | Not Veg | 2018-10-02 | N | 62.9598 | N | 3 | N | N | 1.1101 | 39.4971 | 60594.0287
[7 empty] | 6759 | 15681 | 1599428 | 2018-10-02 13:05 | 2018-10-02 14:10 | 65 | 11kV | 195 | 3 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 188272 TX 70525 LEAKING. HV cable loosened off to stop leaking. Excluded OMS 1599428 | October | 2018 | 2019Q2 | 2019 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2018-10-02 | N | 65 | N | 3 | N | N | 1.1101 | 39.4971 | 142.5002
[7 empty] | 7159 | 20081 | 1599812 | 2018-10-03 16:33 | 2018-10-03 17:50 | 77 | 11kV | 539 | 7 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 188279 Repair loose stay wire at pole SF-80469. | October | 2018 | 2019Q2 | 2019 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2018-10-03 | N | 77 | N | 1 | N | N | 1.1101 | 39.4971 | 393.8853
[7 empty] | 6661 | 14929 | 1599975 | 2018-10-04 14:27 | 2018-10-04 22:07 | 460 | 11kV | 196665 | 1153 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @ Zn15012 killarney Panel 8 tripped on C phase overcurrent, Timing relay and Lockout relay Cause: Tree branch on OH mains adjacent to PT16199 Secondary fault on section of feeder fromAB21109 to S16789 See OMS 1601620 1601621 1601622 1599975 1600758 1599981 1599983 | October | 2018 | 2019Q2 | 2019 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Veg | 2018-10-04 | N | 170.5681 | N | 1 | N | N | 1.1101 | 39.4971 | 143716.9814
[7 empty] | 6917 | 17721 | 1600083 | 2018-10-05 00:11 | 2018-10-05 02:34 | 143 | 11kV | 171593 | 1281 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S12650 West Gosford Panel 9 right tripped on Earth fault Signals: 11kV Trip Cause: Cable Fault Panel 9 right to Sub18466 Gertrude Dwyer tee S13582 to PT12013 See OMS 1601212 1601228 12601229 1600083 | October | 2018 | 2019Q2 | 2019 | ZN12650:PA9 | ZN12650:PA9 | ZN12650/000009 | CENTRAL COAST | UG | Not Veg | 2018-10-05 | N | 133.9524 | N | 14 | N | N | 1.1101 | 39.4971 | 125395.1033
[7 empty] | 5867 | 6059 | 1600114 | 2018-10-05 04:46 | 2018-10-05 05:45 | 59 | 11kV | 20001 | 339 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Section of Panel 10 @ Zn12620 Noraville 11kV Bond burnt off between LB49313 and PT13202 Bruce Buff Point See OMS 1601207 1600114 | October | 2018 | 2019Q2 | 2019 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Not Veg | 2018-10-05 | N | 59 | N | 14 | N | N | 1.1101 | 39.4971 | 14616.1409
[7 empty] | 6550 | 13810 | 1600118 | 2018-10-05 05:27 | 2018-10-05 08:45 | 198 | 11kV | 6534 | 33 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At PT14687 Conserve Merinee 0.2 Footpath HDO blown Cause: Possuum found burnt at the base of PT pole See OMS 1601238 1600118 | October | 2018 | 2019Q2 | 2019 | ZN12650:PA2 | ZN12650:PA2 | ZN12650/000002 | CENTRAL COAST | OH | Not Veg | 2018-10-05 | N | 198 | N | 14 | N | N | 1.1101 | 39.4971 | 4774.8545
[7 empty] | 6973 | 18244 | 1600131 | 2018-10-05 06:20 | 2018-10-05 08:49 | 149 | 11kV | 60782 | 437 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn1285 Greenacre Park - Pnl.35 tripped on: Translay I/T receive to S2420 Bankstown Sq No.1 UG cable fault between pnl.35 and S4315 Heath St (Sw/A) Note: No EFIs on ring feeder and fault was intermittent, hence multiple restoration attempts See 1601022 1601024 1601025 | October | 2018 | 2019Q2 | 2019 | ZN1285:PA35 | ZN1285:PA35 | ZN01285/000035 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-10-05 | N | 139.0892 | N | 14 | N | N | 1.1101 | 39.4971 | 44417.6928
[7 empty] | 5420 | 1098 | 1600116 | 2018-10-05 05:10 | 2018-10-05 09:08 | 238 | 11kV | 159829 | 861 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 188289 2 fault operations Excluded OMS 1600116 | October | 2018 | 2019Q2 | 2019 | 221:11897 | 221:11897 | ZN00221/011897 | LAKE MACQUARIE | OH | Veg | 2018-10-05 | N | 185.6318 | N | 14 | N | N | 1.1101 | 39.4971 | 116798.319
[7 empty] | 7078 | 19401 | 1600291 | 2018-10-05 11:29 | 2018-10-05 12:48 | 79 | 11kV | 11139 | 141 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188293 Interruption to allow repairs on damaged strands of OH conductor. | October | 2018 | 2019Q2 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2018-10-05 | N | 79 | N | 14 | N | N | 1.1101 | 39.4971 | 8140.0527
[7 empty] | 6722 | 15316 | 1600240 | 2018-10-05 04:40 | 2018-10-05 14:55 | 615 | 11kV | 152286 | 1615 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 188288 2 fault operation A & B phase Instantaneous Overcurrent HV reported down Excluded OMS 1600110, 1600115 & 1600242 | October | 2018 | 2019Q2 | 2019 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Not Veg | 2018-10-05 | N | 94.2947 | N | 14 | N | N | 1.1101 | 39.4971 | 111286.1171
[7 empty] | 6922 | 17791 | 1600348 | 2018-10-05 14:38 | 2018-10-05 15:15 | 36.6 | 11kV | 2488.8 | 68 | HV | Vegetation Blow/Fall In | Vegetation | Lightning Arrestor | Unplanned | Rain Heavy | N | At PT14306 River Muloora footpath/centre phase 31Amp HDO fuses were found to have operated Cause: a stick was found across the 11kV surge arrestors at PT14306 Miver Muloora See OMS 1600348 1600350 1600352 CC1: 22-"Refer to SOp" | October | 2018 | 2019Q2 | 2019 | ZN12580:PA16 | ZN12580:PA8 | ZN12580/000008 | CENTRAL COAST | OH | Veg | 2018-10-05 | N | 36.6 | N | 14 | N | N | 1.1101 | 39.4971 | 1818.7416
[7 empty] | 7161 | 20104 | 1600381 | 2018-10-05 15:58 | 2018-10-05 17:25 | 87 | 11kV | 609 | 7 | HV | Vegetation Blow/Fall In | Vegetation | Lightning Arrestor | Unplanned | No Weather Impact | N | At PT13221 Old Maitland Collies the 10A roadside HDO was found to have operated Cause: Small stick found on the 11kV surge arrestors See OMS 1601246 1600376 1600381 | October | 2018 | 2019Q2 | 2019 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2018-10-05 | N | 87 | N | 14 | N | N | 1.1101 | 39.4971 | 445.0392
[7 empty] | 5573 | 3252 | 1600368 | 2018-10-05 15:27 | 2018-10-05 18:20 | 173 | 11kV | 1038 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 188298 A Phase DOLF : 16 Amp | October | 2018 | 2019Q2 | 2019 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2018-10-05 | N | 173 | N | 14 | N | N | 1.1101 | 39.4971 | 758.5398
[7 empty] | 6251 | 10434 | 1600430 | 2018-10-05 19:30 | 2018-10-05 20:06 | 36 | 11kV | 21960 | 610 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn2635 Epping Panel 46 tripped, reclosed, tripped and locked out on Relays: A and B phase IOC, IOC trip, Reclose and Lockout and EFI Signals: 11kV Trip Abnormal Switching: AB240 Open and Defective LB 77225 Closed See OMS 1601261 1600430 16004031 1600435 1600434 | October | 2018 | 2019Q2 | 2019 | ZN2635:PA46 | ZN2635:PA46 | ZN02635/000046 | RYDE | OH | Veg | 2018-10-05 | N | 36 | N | 14 | N | N | 1.1101 | 39.4971 | 16047.7203
[7 empty] | 6749 | 15546 | 1600369 | 2018-10-05 15:23 | 2018-10-05 22:50 | 447 | 11kV | 50070 | 1030 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Recloser CP62391 Wells Brougham tripped, reclosed tripped and locked out on OC trip Cause: A large tree branch has brought down the 11kV OH adjacent to PT11160 Waratah Denver See OMS 1601250 1601251 1600369 1600386 1600413 | October | 2018 | 2019Q2 | 2019 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Veg | 2018-10-05 | N | 48.6117 | N | 14 | N | N | 1.1101 | 39.4971 | 36589.6792
[7 empty] | 6797 | 16308 | 1600393 | 2018-10-05 16:51 | 2018-10-05 22:55 | 363.7333 | 11kV | 16368 | 45 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | LID 188299 A Phase Open tapping at DV-43613. Please patrol. | October | 2018 | 2019Q2 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2018-10-05 | N | 363.7333 | N | 14 | N | N | 1.1101 | 39.4971 | 11961.2516
[7 empty] | 7045 | 19017 | 1600453 | 2018-10-05 22:03 | 2018-10-06 03:30 | 327 | 11kV | 129717 | 1179 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | Rain Heavy | N | At S12580 Erina Panel 1 tripped, reclosed tripped and lockoed out. Cause: Vehicle has hit S14986 Avoca Christian Scool and caused it to catch fire See OMS1601254 1601256 1601257 1600447 | October | 2018 | 2019Q2 | 2019 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | Unknown | Not Veg | 2018-10-05 | N | 110.0229 | N | 14 | N | N | 1.1101 | 39.4971 | 94793.3576
[7 empty] | 7145 | 19952 | 1600474 | 2018-10-06 03:16 | 2018-10-06 04:37 | 81 | 11kV | 79209 | 993 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2635 Epping Panel 44 tripped on Relays: 50TC, 150TN, Trip EFI Signals: 11kV Trip UG cable faut between S65631 and S1796 See OMS 1601546 1601547 1600474 | October | 2018 | 2019Q2 | 2019 | ZN2635:PA44 | ZN2635:PA44 | ZN02635/000044 | RYDE | UG | Not Veg | 2018-10-06 | N | 79.7674 | N | 3 | N | N | 1.1101 | 39.4971 | 57883.6009
[7 empty] | 6765 | 15751 | 1600505 | 2018-10-06 09:08 | 2018-10-06 09:55 | 47 | 11kV | 47 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 188301 B Phase DOLF : 10 Amp Excluded OMS 1600505 | October | 2018 | 2019Q2 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2018-10-06 | N | 47 | N | 3 | N | N | 1.1101 | 39.4971 | 34.3462
[7 empty] | 6526 | 13639 | 1600477 | 2018-10-06 05:23 | 2018-10-06 10:35 | 312 | 11kV | 936 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 188302 A Phase DOLF : 10 Amp Excluded OMS 1600477 | October | 2018 | 2019Q2 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2018-10-06 | N | 312 | N | 3 | N | N | 1.1101 | 39.4971 | 684.0012
[7 empty] | 6119 | 9080 | 1600632 | 2018-10-07 07:09 | 2018-10-07 14:13 | 424 | 11kV | 281707 | 3984 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 188306 1 fault operation Busbar Protection car hit pole Main protection did not operate. Back up o/c & e/f trip 11kV section 3 BBP Sw 80337, Sw 80339, Sw 80340, Sw 80341 Opened. Excluded oms 1600631 | October | 2018 | 2019Q2 | 2019 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | OH | Not Veg | 2018-10-07 | N | 70.7096 | N | 5 | N | N | 1.1101 | 39.4971 | 205863.1667
[7 empty] | 6183 | 9860 | 1600777 | 2018-10-07 21:13 | 2018-10-07 22:40 | 87 | 11kV | 59502 | 1566 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | At Zn2635 Epping Panel 57 tripped and reclosed on Signals: 11kV trip Relays: C phase IOC Abnormal Switching: AB240 Open and Defective AB77225 Closed Cause: Flash over on centre phase at CP240 See OMS 1601559 1601562 1600790 | October | 2018 | 2019Q2 | 2019 | ZN2635:PA57 | ZN2635:PA57 | ZN02635/000057 | PARRAMATTA | OH | Not Veg | 2018-10-07 | N | 37.9962 | N | 5 | N | N | 1.1101 | 39.4971 | 43482.3066
[7 empty] | 7062 | 19282 | 1600788 | 2018-10-07 21:13 | 2018-10-07 22:45 | 92 | 11kV | 24056 | 610 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | Rain Heavy | N | At Zn2635 Epping Panel 46 tripped and reclosed on Signals: 11kV Trip Relays: IOC A and B phase Abnormal Switching: AB240 is open and defective with AB77225 Closed Cause: Flashover on centre phase at AB240 1601579 1601581 1600788 | October | 2018 | 2019Q2 | 2019 | ZN2635:PA46 | ZN2635:PA46 | ZN02635/000046 | RYDE | OH | Not Veg | 2018-10-07 | N | 39.4361 | N | 5 | N | N | 1.1101 | 39.4971 | 17579.4153
[7 empty] | 6410 | 12170 | 1600804 | 2018-10-07 22:26 | 2018-10-07 23:35 | 69 | 11kV | 2829 | 41 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188309 A & B phase DOLF : 63 Amp Possum 2226hrs A & B 63A DOLF supply back on 2335hrs Excluded OMS 1600804 | October | 2018 | 2019Q2 | 2019 | 256:80638 | 256:80638 | ZN00256/080638 | NEWCASTLE | OH | Not Veg | 2018-10-07 | N | 69 | N | 5 | N | N | 1.1101 | 39.4971 | 2067.3498
[7 empty] | 6862 | 17046 | 1600829 | 2018-10-08 04:53 | 2018-10-08 07:28 | 155 | 11kV | 6200 | 40 | HV | Vandalism | 3rd Party Impact | Air Break Switch | Unplanned | Rain Heavy | N | EX11kV panel 4L from feeder ZN35370 Galston AB954 found open by DOp with lock cut off - interrupting section of feeder Cause; Vandalism/Phantom operation | October | 2018 | 2019Q2 | 2019 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2018-10-08 | N | 155 | N | 2 | N | N | 1.1101 | 39.4971 | 4530.7771
[7 empty] | 6936 | 17904 | 1600859 | 2018-10-08 07:52 | 2018-10-08 08:54 | 62 | 11kV | 3364 | 56 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S14143 Somersby Panel 6 tripped on Relays: Earth Fault, EFI Signals: 11kV trip, Zone Earth TX1 Group Earth Cause: 11kV UG fault between S18454 to S18253 See 1602000 1602002 1600859 | October | 2018 | 2019Q2 | 2019 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | UG | Not Veg | 2018-10-08 | N | 60.0714 | N | 2 | N | N | 1.1101 | 39.4971 | 2458.312
[7 empty] | 6276 | 10650 | 1600785 | 2018-10-07 20:45 | 2018-10-08 16:00 | 1155 | 11kV | 4500 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP26228 Valley Rd tripped on IOC and OC trip Cause: Tree branch brought down OH adjacent to USL 22297 See OMS 1601623 1601624 1601625 1600785 | October | 2018 | 2019Q2 | 2019 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2018-10-07 | N | 1125 | N | 5 | N | N | 1.1101 | 39.4971 | 3288.4673
[7 empty] | 6301 | 10926 | 1601130 | 2018-10-09 07:49 | 2018-10-09 09:02 | 73 | 11kV | 25094 | 449 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay - Pnl.11 tripped on Earth Leakage Field EFIs: All down to S9491 End box fault at S9896 (Sw/A) See 1601332 1601333 1601334 | October | 2018 | 2019Q2 | 2019 | ZN9550:PA11 | ZN9550:PA11 | ZN09550/000011 | SUTHERLAND | UG | Not Veg | 2018-10-09 | N | 55.8886 | N | 4 | N | N | 1.1101 | 39.4971 | 18337.9551
[7 empty] | 6014 | 7775 | 1601325 | 2018-10-09 07:27 | 2018-10-09 13:00 | 333 | 11kV | 1665 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 188326 Replace defective, leaking Tx. Replaced blown TX three phase 25kva, cause posibily previous rian & some lightning ? Excluded OMS 1601126 | October | 2018 | 2019Q2 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2018-10-09 | N | 333 | N | 4 | N | N | 1.1101 | 39.4971 | 1216.7329
[7 empty] | 6401 | 12059 | 1601112 | 2018-10-09 06:15 | 2018-10-09 18:40 | 745.2667 | 11kV | 176628.2 | 237 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | AB42508 Found on fire Recloser 61922 Pacific Bar Point Opened by AOp CC1: 22-"Refer to SOp" | October | 2018 | 2019Q2 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2018-10-09 | N | 745.2667 | N | 4 | N | N | 1.1101 | 39.4971 | 129074.6789
[7 empty] | 7003 | 18571 | 1601269 | 2018-10-09 17:10 | 2018-10-09 18:47 | 97 | 11kV | 16005 | 165 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | LB77731 Was opened for safety CP61922 Pacific Bar point would not close after fire on AB42508 (Faulty control boards and an emergency cutout was required to brond trough the intellirupted to restore supply to radial feeder. | October | 2018 | 2019Q2 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2018-10-09 | N | 97 | N | 4 | N | N | 1.1101 | 39.4971 | 11695.9819
[7 empty] | 6754 | 15621 | 1601373 | 2018-10-10 10:04 | 2018-10-10 11:05 | 61 | 11kV | 244 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188343 Single Phase - Fuse 10 Amp substation DOLF | October | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-10-10 | N | 61 | N | 11 | N | N | 1.1101 | 39.4971 | 178.308
[7 empty] | 5755 | 5199 | 1601384 | 2018-10-10 10:31 | 2018-10-10 11:35 | 64.2833 | 11kV | 2121.35 | 33 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 188352 A and B Phases, DOLF LIGHTNING STRUCK POLE AND CERAMIC FUSE blown LA | October | 2018 | 2019Q2 | 2019 | 261:81882 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | OH | Not Veg | 2018-10-10 | N | 64.2833 | N | 11 | N | N | 1.1101 | 39.4971 | 1550.22
[7 empty] | 5870 | 6088 | 1601419 | 2018-10-10 11:34 | 2018-10-10 13:25 | 111 | 11kV | 13542 | 122 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188351 B Phase 40 Amp Substation DOLF Electrical Storm Refer to oms 1601419 | October | 2018 | 2019Q2 | 2019 | 210:83466 | 210:83466 | ZN00210/083466 | NEWCASTLE | OH | Veg | 2018-10-10 | N | 111 | N | 11 | N | N | 1.1101 | 39.4971 | 9896.0942
[7 empty] | 6065 | 8299 | 1601411 | 2018-10-10 11:18 | 2018-10-10 13:28 | 130 | 11kV | 72258 | 735 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 188345 1 fault operation A & C phase DOLF : 31 Amp Intellirupter, Sensitive Earth Fault; Faulty Tx or LA at Wallawa Rd sub 18998. Customers from Sub 11898 reported no supply at 1118hrs. Intellirupter tripped on SEF at 1123hrs. Excluded OMS 1601411 | October | 2018 | 2019Q2 | 2019 | 242:81538 | 242:81538 | ZN00242/081538 | PORT STEPHENS | OH | Not Veg | 2018-10-10 | N | 98.3102 | N | 11 | N | N | 1.1101 | 39.4971 | 52804.0151
[7 empty] | 6820 | 16603 | 1601453 | 2018-10-10 12:51 | 2018-10-10 13:50 | 59 | 11kV | 4012 | 68 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | At PT14306 Miver Muloora 11kV Roadside HDO operated Cause: Lightning/Suge arrestor See OMS 1601453 1601452 1601459 | October | 2018 | 2019Q2 | 2019 | ZN12580:PA16 | ZN12580:PA8 | ZN12580/000008 | CENTRAL COAST | OH | Not Veg | 2018-10-10 | N | 59 | N | 11 | N | N | 1.1101 | 39.4971 | 2931.8513
[7 empty] | 5673 | 4342 | 1601584 | 2018-10-10 16:56 | 2018-10-10 19:00 | 124 | 11kV | 124 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 188359 C Phase DOLF : 10 Amp Excluded OMS 1601584 | October | 2018 | 2019Q2 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2018-10-10 | N | 124 | N | 11 | N | N | 1.1101 | 39.4971 | 90.6155
[7 empty] | 6073 | 8340 | 1601340 | 2018-10-10 11:30 | 2018-10-10 19:50 | 500 | 11kV | 2500 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | No Weather Impact | N | pt14505 cHITTAWAY rD wEST WAS interrupted to isolate fallen 11kVCovered conductor. OH down. 13 Reliance Drive tuggerah | October | 2018 | 2019Q2 | 2019 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2018-10-10 | N | 500 | N | 11 | N | N | 1.1101 | 39.4971 | 1826.9263
[7 empty] | 6833 | 16770 | 1601449 | 2018-10-10 11:27 | 2018-10-10 20:30 | 543 | 11kV | 95799 | 568 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | N | Zn10993 Hurstville North - Pnl.39L tripped on: B & C phase O/C Abnormal: Feeder out of service between S10750 Sw/B & S62944 Sw/A & S10941 Sw/B Lightninig strike blew surge arrestor and damaged UGOH near S47506 (Sw/A side) Lightning strike damaged UGOH near S10543 (Sw/A side) See 1601918 1601919 | October | 2018 | 2019Q2 | 2019 | ZN10993:PA39 | ZN10993:PA39 | ZN10993/000039 | GEORGES RIVER | OH | Not Veg | 2018-10-10 | N | 168.6602 | N | 11 | N | N | 1.1101 | 39.4971 | 70007.0836
[7 empty] | 7080 | 19432 | 1601512 | 2018-10-10 15:02 | 2018-10-10 23:15 | 493 | 11kV | 63253 | 322 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 188362 3 fault operations tree on ohm near sub 47597 | October | 2018 | 2019Q2 | 2019 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2018-10-10 | N | 196.4379 | N | 11 | N | N | 1.1101 | 39.4971 | 46223.4268
[7 empty] | 5930 | 6757 | 1601647 | 2018-10-10 21:13 | 2018-10-11 00:10 | 177 | 11kV | 15930 | 90 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 188364 section isolated to make repairs, wire down at pole 5I-40110 Excluded oms 1601647 | October | 2018 | 2019Q2 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2018-10-10 | N | 177 | N | 11 | N | N | 1.1101 | 39.4971 | 11641.1741
[7 empty] | 7032 | 18851 | 1601642 | 2018-10-10 22:45 | 2018-10-11 00:10 | 85 | 11kV | 5610 | 66 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 188363 no protection operation see report # 188361/OMS 1601719 section isolated for clearance Excluded oms 1601651 | October | 2018 | 2019Q2 | 2019 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Not Veg | 2018-10-10 | N | 85 | N | 11 | N | N | 1.1101 | 39.4971 | 4099.6225
[7 empty] | 5520 | 2328 | 1601656 | 2018-10-11 06:15 | 2018-10-11 07:52 | 97 | 11kV | 582 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188366 B Phase DOLF : 16 Amp Excluded OMS 1601656 | October | 2018 | 2019Q2 | 2019 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2018-10-11 | N | 97 | N | 2 | N | N | 1.1101 | 39.4971 | 425.3084
[7 empty] | 5712 | 4805 | 1601852 | 2018-10-11 21:48 | 2018-10-11 23:15 | 87 | 11kV | 1131 | 13 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At PT14525 Beachview Ocean 0.2 Section of Panel 33 Avoca Cause: Tree on OH mains, Small branch hanging near base of drop-out fuse. See OMS 1602949 1601852 | October | 2018 | 2019Q2 | 2019 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2018-10-11 | N | 87 | N | 2 | N | N | 1.1101 | 39.4971 | 826.5014
[7 empty] | 6465 | 12909 | 1601861 | 2018-10-12 01:47 | 2018-10-12 07:00 | 312.8333 | 11kV | 2189.8333 | 7 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn12650 West Gosford Ex Panel 1 "Dog Trap Rd" fdr 11kv auto links 42941 operated Cause: tree/branch on OH mains as above | October | 2018 | 2019Q2 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2018-10-12 | N | 312.8333 | N | 4 | N | N | 1.1101 | 39.4971 | 1600.2656
[7 empty] | 7076 | 19397 | 1601864 | 2018-10-12 04:47 | 2018-10-12 13:20 | 513 | 11kV | 70728 | 419 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn12630 Peats Ridge Ex Panel 1 "Gunderman" fdr 11kV RE45189 Cooks Peats Ridge 0.5 tripped Cause: tree/branch brought down OH wiresdown near PT13482 See 1602446,9,50,1 Ex 1601864,5,73,4 | October | 2018 | 2019Q2 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2018-10-12 | N | 168.8019 | N | 4 | N | N | 1.1101 | 39.4971 | 51685.9363
[7 empty] | 6547 | 13788 | 1602034 | 2018-10-12 17:37 | 2018-10-12 18:40 | 63 | 11kV | 63 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188375 Single phase DOLF : 10 Amp Excluded OMS 1602034 | October | 2018 | 2019Q2 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2018-10-12 | N | 63 | N | 4 | N | N | 1.1101 | 39.4971 | 46.0385
[7 empty] | 5888 | 6295 | 1602082 | 2018-10-13 06:55 | 2018-10-13 09:45 | 170 | 11kV | 72132 | 762 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn965 Pennant hills Panel 29 tripped and reclosed tripped and locked out on Signals: TX1 group earth and zone earth Relays: earth fault Cause: 11kV UG fault on section of feeder from S35078 to S5503 to S1736 See OMS 1602957 1602958 1602959 1602082 | October | 2018 | 2019Q2 | 2019 | ZN965:PA29 | ZN965:PA29 | ZN00965/000029 | HORNSBY | UG | Not Veg | 2018-10-13 | N | 94.6614 | N | 4 | N | N | 1.1101 | 39.4971 | 52711.9381
[7 empty] | 6437 | 12563 | 1602075 | 2018-10-13 04:20 | 2018-10-13 14:10 | 590 | 11kV | 351363 | 1523 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn12570 Avoca Panel 37 'Avoca Beach' Fdr tripped Signals:11kV trip Tx12 AC Board CB trip, Tx12 AC Supply failed, Tx12 415 No Volts Alarm, Tx13 AC changeover failed, B battery charger failed alarm, B battery charger defect alarm. Relays: 1.2.1 150TN, 51AB, EFI, FC, Timer, Lockout EFI's: S18439, S49066, 18135 subsequently tripped on SEL with lockout Cause: Phase failure relay @ Avoca zone on 415v ac board appears to have issues holding in after feeder fault. Also burnt off bond in section of feeder from S49066 to AB 44670 to S18135 SwA tee pt18112 & pt77604 See 1602594,5,6,7,9,600 Ex 1602073,5 | October | 2018 | 2019Q2 | 2019 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2018-10-13 | N | 230.7045 | N | 4 | N | N | 1.1101 | 39.4971 | 256765.7169
[7 empty] | 6951 | 18030 | 1601967 | 2018-10-12 13:39 | 2018-10-13 14:40 | 1501 | 11kV | 74191 | 414 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge Ex Panel 3 "Mangrove Mountain" fdr tripped on: Relays: E/F, EFI EFI: nil Signals: 11kv trip Cause: OH down 7 spans of 11kv OH 11kv fdr down between AB44253 & IR61085. 11kv fdr isolated and earthed between LB45199 AB44115 AB40570 AB42937 & LB43765 See 1602577,81,2 ex 1601967,91,2023,5,6 | October | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2018-10-12 | N | 179.2053 | N | 4 | N | N | 1.1101 | 39.4971 | 54216.5945
[7 empty] | 6197 | 9994 | 1602440 | 2018-10-13 17:47 | 2018-10-13 18:47 | 60 | 11kV | 60 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Rain Light | N | LID 188389 1 fault operation Sensitive Earth Fault | October | 2018 | 2019Q2 | 2019 |  |  |  | LAKE MACQUARIE | Unknown | Not Veg | 2018-10-13 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 6731 | 15377 | 1602178 | 2018-10-13 21:43 | 2018-10-13 23:55 | 132 | 11kV | 145052 | 1595 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn36100 Rose Bay - Pnl.27 tripped on: 51N Field EFIs: S64895 S4896 S49818 S193 UG cable fault from S193 (SW/B) and S7353 (SW/A) tee S2489 See 1602760 1602761 1602762 | October | 2018 | 2019Q2 | 2019 | ZN36100:PA27 | ZN36100:PA25 | ZN36100/000025 | WAVERLEY | UG | Not Veg | 2018-10-13 | N | 90.9417 | N | 4 | N | N | 1.1101 | 39.4971 | 105999.7233
[7 empty] | 6002 | 7634 | 1602205 | 2018-10-14 07:59 | 2018-10-14 10:05 | 125.8333 | 11kV | 125.8333 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 188394 LL Clamp became detached, needed replacing. No protection operation. Excluded OMS 1602209 | October | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-10-14 | N | 125.8333 | N | 3 | N | N | 1.1101 | 39.4971 | 91.9553
[7 empty] | 6860 | 17020 | 1602289 | 2018-10-14 15:40 | 2018-10-14 17:45 | 125 | 11kV | 132197 | 1201 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.25 tripped on Earth Fault UG cable fault between S10320 and S10526 and S10943 See 1602665 1602667 | October | 2018 | 2019Q2 | 2019 | ZN10999:PA25 | ZN10999:PA25 | ZN10999/000025 | GEORGES RIVER | UG | Not Veg | 2018-10-14 | N | 110.0724 | N | 3 | N | N | 1.1101 | 39.4971 | 96605.6684
[7 empty] | 5507 | 2047 | 1602296 | 2018-10-14 16:24 | 2018-10-14 18:35 | 131 | 11kV | 260429 | 2044 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | Zn2602 Clovelly - Pnl.15 tripped on: Earth Fault Field EFIs; S46310 S60 UG cable fault between S60 (Sw/D) and S1874 (Sw/A) See 1602767 1602768 | October | 2018 | 2019Q2 | 2019 | ZN2602:PA15 | ZN36800:PA40 | ZN36800/000040 | RANDWICK | UG | Not Veg | 2018-10-14 | N | 127.4114 | N | 3 | N | N | 1.1101 | 39.4971 | 190313.8318
[7 empty] | 5898 | 6378 | 1602614 | 2018-10-15 23:18 | 2018-10-16 00:05 | 47 | 11kV | 12925 | 275 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 188403 1 fault operation Possum at pole AH-20558 | October | 2018 | 2019Q2 | 2019 | 813:89059 | 813:89059 | ZN00813/089059 | UPPER HUNTER | OH | Not Veg | 2018-10-15 | N | 47 | N | 2 | N | N | 1.1101 | 39.4971 | 9445.2088
[7 empty] | 6747 | 15515 | 1602615 | 2018-10-16 01:11 | 2018-10-16 02:15 | 64 | 11kV | 66900 | 1152 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35900 Potts Hill - Pnl.4 tripped on: Earth fault and IOC Field EFIs; All to S77369 UG cable fault between S77369 (Sw/B) and S35714 (Sw/A) See 1602972 1602973 | October | 2018 | 2019Q2 | 2019 | ZN35900:PA4 | ZN35900:PA4 | ZN35900/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-10-16 | N | 58.0729 | N | 6 | N | N | 1.1101 | 39.4971 | 48888.5468
[7 empty] | 6142 | 9329 | 1602622 | 2018-10-16 08:55 | 2018-10-16 13:20 | 265 | 11kV | 7420 | 28 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12600 Lisarow Ex Panel 2 "Holgate" fdr From LB41935 to AB41934 interrupted to allow mains to remove large tree off 11kv CCT Cause: Tree/Branch on OH mains. Large tree resting on CCT See 1603464 ex 1602622,45,58,69 | October | 2018 | 2019Q2 | 2019 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2018-10-16 | N | 265 | N | 6 | N | N | 1.1101 | 39.4971 | 5422.3171
[7 empty] | 6931 | 17875 | 1602746 | 2018-10-16 14:34 | 2018-10-16 15:55 | 81 | 11kV | 243 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188412 A Phase DOLF : 10 Amp Bird hit Mains Excluded OMS 1602746 | October | 2018 | 2019Q2 | 2019 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2018-10-16 | N | 81 | N | 6 | N | N | 1.1101 | 39.4971 | 177.5772
[7 empty] | 6350 | 11425 | 1602659 | 2018-10-16 09:40 | 2018-10-16 17:45 | 485 | 11kV | 965 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Rain Light | N | @ PT9008 Farnell Ave - HDO found corroded. REC35006 National Park interrupted @ 1345 for repairs. All PTs beyong REC N//. See 1602964 1602965 | October | 2018 | 2019Q2 | 2019 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2018-10-16 | N | 321.6667 | N | 6 | N | N | 1.1101 | 39.4971 | 705.1935
[7 empty] | 6729 | 15364 | 1602752 | 2018-10-16 14:48 | 2018-10-16 18:12 | 204 | 11kV | 98426 | 1515 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 188410 3 phase Earth Fault 11kV off pin JV40025 High into LV Excluded OMS 1602752 | October | 2018 | 2019Q2 | 2019 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2018-10-16 | N | 64.9677 | N | 6 | N | N | 1.1101 | 39.4971 | 71926.8177
[7 empty] | 5528 | 2461 | 1602821 | 2018-10-16 20:29 | 2018-10-16 21:40 | 71 | 11kV | 710 | 10 | HV | Vandalism | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Section of 11kV feeder from LB2903 to extents isolated to allow isolations and earthing of vandalised pole. | October | 2018 | 2019Q2 | 2019 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2018-10-16 | N | 71 | N | 6 | N | N | 1.1101 | 39.4971 | 518.8471
[7 empty] | 6091 | 8625 | 1602868 | 2018-10-17 07:05 | 2018-10-17 08:12 | 67 | 11kV | 73424 | 1136 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Zn3154 St Ives Ex Pa23 RE527 Catherine Paul tripped Relays: SEL, LO Abnormal: LB64433 closed, S62840 open (fdr Zn3154:Pa17 to S62840 defective) Cause: Bond Footpath side bond burnt off @ AB2081 on PT1270 Side See 1603496,7 GIS 1602901 ex 1602848,50,68 | October | 2018 | 2019Q2 | 2019 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Not Veg | 2018-10-17 | N | 64.6338 | N | 11 | N | N | 1.1101 | 39.4971 | 53656.0936
[7 empty] | 5728 | 5019 | 1602980 | 2018-10-17 09:20 | 2018-10-17 10:35 | 75 | 11kV | 825 | 11 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188417 Damaged mains between DH-70001 & DH- 70002 Near sub 73094 | October | 2018 | 2019Q2 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2018-10-17 | N | 75 | N | 11 | N | N | 1.1101 | 39.4971 | 602.8857
[7 empty] | 6268 | 10575 | 1603017 | 2018-10-17 11:20 | 2018-10-17 12:55 | 95 | 11kV | 1235 | 13 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188419 mains stranded near sub 71142 | October | 2018 | 2019Q2 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2018-10-17 | N | 95 | N | 11 | N | N | 1.1101 | 39.4971 | 902.5016
[7 empty] | 6235 | 10316 | 1603059 | 2018-10-17 13:33 | 2018-10-17 14:05 | 32 | 11kV | 288 | 9 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 188421 tree branch on mains near sub 72571 | October | 2018 | 2019Q2 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2018-10-17 | N | 32 | N | 11 | N | N | 1.1101 | 39.4971 | 210.4619
[7 empty] | 6162 | 9519 | 1603028 | 2018-10-17 11:35 | 2018-10-17 14:30 | 175 | 11kV | 202958 | 2330 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3555 Croydon - Pnl5 tripped on: Earth Fault Abnormal: S6318 Wholsey Parra (Sw/A) closed with (Sw/B) open UG cable fault See 1603334 1603335 | October | 2018 | 2019Q2 | 2019 | ZN35555:PA5 | ZN35555:PA5 | ZN35555/000005 | INNER WEST | UG | Not Veg | 2018-10-17 | N | 87.1064 | N | 11 | N | N | 1.1101 | 39.4971 | 148315.7202
[7 empty] | 6777 | 15978 | 1602512 | 2018-10-15 14:22 | 2018-10-17 15:45 | 2963 | 11kV | 290374 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Recloser CP3227 Berowra Creek Tripped and Locked out on OC and SEF S Lawton - HV mains have been repaired and the tree removed. DOPs restoring power. Large gum tree fell on HV mains and ended up snapping all 3. The HV mains wer repaired and the tree cut up. The ties were redone and all wires affected retensioned. Extensive repairs required with very difficult access Water transport required Hornsby Duty officer is organising lineworkes to attend | October | 2018 | 2019Q2 | 2019 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2018-10-15 | N | 2963 | N | 2 | N | N | 1.1101 | 39.4971 | 212196.7546
[7 empty] | 6024 | 7860 | 1603158 | 2018-10-17 16:38 | 2018-10-17 18:15 | 97 | 11kV | 10873 | 121 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 188424 1 fault operation A & B phase Overcurrent T/R Please PAtrol Burnt off tapping on load side of ABS 42723. SIngle phasing beyond ABS 42723 until 1815hrs. Excluded OMS 1603158 | October | 2018 | 2019Q2 | 2019 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2018-10-17 | N | 89.8595 | N | 11 | N | N | 1.1101 | 39.4971 | 7945.6677
[7 empty] | 5630 | 3804 | 1603151 | 2018-10-17 17:29 | 2018-10-17 19:05 | 95.5 | 11kV | 191 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 188428 Single phase DOLF : 10 Amp Excluded OMS 1603151 | October | 2018 | 2019Q2 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2018-10-17 | N | 95.5 | N | 11 | N | N | 1.1101 | 39.4971 | 139.5772
[7 empty] | 6736 | 15434 | 1603189 | 2018-10-17 19:56 | 2018-10-17 20:01 | 5 | 11kV | 525 | 105 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188433 2 fault operations A & C phase Overcurrent While trying to restore supply via 74460 I had I had not successfully iopened Sw 75262. All the feeder was energised back to Sw 74180. Restored to normal. On Call to get targets and do a patrol to Sw 75262. PLEASE Patrol. Flags Required | October | 2018 | 2019Q2 | 2019 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2018-10-17 | N | 5 | N | 11 | N | N | 1.1101 | 39.4971 | 383.6545
[7 empty] | 5651 | 4115 | 1603105 | 2018-10-17 16:04 | 2018-10-17 20:55 | 291 | 11kV | 84681 | 291 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | S4212 Cromwell St - 11kV/415V Tx and LV board interrupted at 16:10 for emergency repairs Tx Neutral burnt off | October | 2018 | 2019Q2 | 2019 | ZN35555:PA2 | ZN35555:PA2 | ZN35555/000002 | INNER WEST | UG | Not Veg | 2018-10-17 | N | 291 | N | 11 | N | N | 1.1101 | 39.4971 | 61882.3771
[7 empty] | 5473 | 1648 | 1603200 | 2018-10-17 21:38 | 2018-10-17 23:03 | 85 | 11kV | 105570 | 1242 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Zn1287 Revesby - Pnl.17 tripped on: A & C phase IOC, C phase O/C, EFI Field EFIs: S5036 S5035 S77151 Storm. Lightning at the time | October | 2018 | 2019Q2 | 2019 | ZN1287:PA17 | ZN1287:PA17 | ZN01287/000017 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-10-17 | N | 85 | N | 11 | N | N | 1.1101 | 39.4971 | 77147.4422
[7 empty] | 6875 | 17192 | 1603327 | 2018-10-18 01:13 | 2018-10-18 01:24 | 11 | 11kV | 242 | 22 | HV | Staff Other | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn3288 City South - 41/42 "L" tripped after T/PE knocked relay while trying to change cover on inservice equipment. Relay cover found upside down (relay would not function) T/PE tried to correct while feeder was in service. 2 Tx S6510 supplied by 41/42L lost supply to "L" Tx See 1603329 1603327 | October | 2018 | 2019Q2 | 2019 | ZN3288:PA41 42KLM | ZN3288:PA41 42KLM | ZN03288/41 42KLM | SYDNEY | Unknown | Not Veg | 2018-10-18 | N | 11 | N | 26 | Y | Y | 1.1101 | 39.4971 | 176.8465
[7 empty] | 6805 | 16407 | 1603234 | 2018-10-18 07:10 | 2018-10-18 08:40 | 90 | 11kV | 90 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 188445 A & B Phase DOLF : 10 Amp Excluded OMS 1603234 | October | 2018 | 2019Q2 | 2019 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Veg | 2018-10-18 | N | 90 | N | 26 | Y | Y | 1.1101 | 39.4971 | 65.7693
[7 empty] | 6884 | 17394 | 1603245 | 2018-10-18 08:12 | 2018-10-18 10:30 | 138 | 11kV | 138 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 188447 Single phase DOLF : 3 Amp Excluded OMS 1603245 | October | 2018 | 2019Q2 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2018-10-18 | N | 138 | N | 26 | Y | Y | 1.1101 | 39.4971 | 100.8463
[7 empty] | 6278 | 10694 | 1603221 | 2018-10-18 02:02 | 2018-10-18 10:50 | 528 | 11kV | 55387 | 513 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | IR63275 Washington Lincoln - tripped on: O/C trip Large treee fallen against 11kV mains over the top of LB35697 See 1603698 1603699 | October | 2018 | 2019Q2 | 2019 | ZN9252:PA24 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Veg | 2018-10-18 | N | 107.9669 | N | 26 | Y | Y | 1.1101 | 39.4971 | 40475.186
[7 empty] | 6411 | 12174 | 1603681 | 2018-10-18 12:20 | 2018-10-18 12:30 | 10 | 11kV | 340 | 34 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | Zn1600 City North - 22B tripped on :Bz protection. At S3177 Law Courts Maquarie 22B misc protect operated Abnormal: 22A feeder out of service Suspect protection malfunction at S3177. S1849 Mena House is a 2 x Tx sub. See 1603681 1603695 | October | 2018 | 2019Q2 | 2019 | ZN1600:PA22ABC | ZN5959:PA5K | ZN05959/00005K | SYDNEY | UG | Not Veg | 2018-10-18 | N | 10 | N | 26 | Y | Y | 1.1101 | 39.4971 | 248.462
[7 empty] | 5839 | 5822 | 1603322 | 2018-10-18 11:15 | 2018-10-18 13:05 | 110 | 11kV | 2515 | 26 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 188449 Fdr isolated to repaire broken pin insulator at pole CG-10195. Excluded OMS No. 1603322 | October | 2018 | 2019Q2 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2018-10-18 | N | 96.7308 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1837.8878
[7 empty] | 6569 | 14034 | 1603198 | 2018-10-17 21:36 | 2018-10-18 13:45 | 969 | 11kV | 4845 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188438 Single phase DOLF : 20 Amp pole 4H-60010 broken(hit by lightnening) Sub 46241 left isolated at 11kv taps at pole 4H-60002. Excluded oms report no 1603198. | October | 2018 | 2019Q2 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2018-10-17 | N | 969 | N | 11 | N | N | 1.1101 | 39.4971 | 3540.5831
[7 empty] | 6829 | 16684 | 1603390 | 2018-10-18 14:37 | 2018-10-18 16:45 | 128 | 11kV | 184646 | 1472 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12600 Lisarow panel 9 "Wyoming South" tripped, reclosed and locked out on: Relays: OC, EFI and SEF Signals: 11kv trip EFI: Nil Cause not ascertained. Mains to Patrol in daylight See 1604964,5 ex 1603390,404 | October | 2018 | 2019Q2 | 2019 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2018-10-18 | N | 125.4389 | N | 26 | Y | Y | 1.1101 | 39.4971 | 134933.8507
[7 empty] | 6234 | 10315 | 1603537 | 2018-10-18 18:21 | 2018-10-18 19:43 | 82 | 11kV | 246 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 188474 Single phase DOLF : 10 Amp Excluded OMS 1603537 | October | 2018 | 2019Q2 | 2019 | 243:80080 | 243:80080 | ZN00243/080080 | LAKE MACQUARIE | OH | Veg | 2018-10-18 | N | 82 | N | 26 | Y | Y | 1.1101 | 39.4971 | 179.7695
[7 empty] | 5783 | 5444 | 1603543 | 2018-10-18 18:25 | 2018-10-18 20:20 | 115 | 11kV | 805 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 188475 3 phase DOLF : 10 Amp Excluded OMS 1603543 | October | 2018 | 2019Q2 | 2019 | 243:80080 | 243:80080 | ZN00243/080080 | LAKE MACQUARIE | OH | Veg | 2018-10-18 | N | 115 | N | 26 | Y | Y | 1.1101 | 39.4971 | 588.2703
[7 empty] | 6887 | 17416 | 1603547 | 2018-10-18 18:30 | 2018-10-18 20:44 | 134 | 11kV | 9532 | 89 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188469 2 fault operations 3 phase Intellirupter, Overcurrent Fault Current Aph: 628A, Bph: 831A, Cph: 718A Excluded OMS No. 1603547 | October | 2018 | 2019Q2 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | OH | Veg | 2018-10-18 | N | 107.1011 | N | 26 | Y | Y | 1.1101 | 39.4971 | 6965.7045
[7 empty] | 6959 | 18098 | 1603546 | 2018-10-18 18:30 | 2018-10-18 20:50 | 140 | 11kV | 2660 | 19 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188476 Phases B and C, Fuse Size 63 Amp Line DOLF Feeder Patrol requested 63A B & Cph LF 6905 replaced. Supply restored at 2050hrs by EMSO | October | 2018 | 2019Q2 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2018-10-18 | N | 140 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1943.8495
[7 empty] | 5786 | 5453 | 1603514 | 2018-10-18 17:40 | 2018-10-18 21:50 | 250 | 11kV | 250 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 188470 Single phase DOLF : 10 Amp Excluded OMS 1603514 | October | 2018 | 2019Q2 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2018-10-18 | N | 250 | N | 26 | Y | Y | 1.1101 | 39.4971 | 182.6926
[7 empty] | 5531 | 2483 | 1603600 | 2018-10-18 21:04 | 2018-10-18 22:09 | 65 | 11kV | 130 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 188478 C Phase DOLF : 10 Amp Excluded OMS 1603600 | October | 2018 | 2019Q2 | 2019 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2018-10-18 | N | 65 | N | 26 | Y | Y | 1.1101 | 39.4971 | 95.0002
[7 empty] | 5716 | 4896 | 1603441 | 2018-10-18 15:52 | 2018-10-18 22:10 | 378 | 11kV | 129873 | 414 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Wind Storm | N | Zn12630 Peats Ridge Panel 3 "NMangrove Mountain" tripped, reclosed and locked out on: Relays: C PHase OC and EF, Lockout and TIming Signals: 11kv trip EFI: nil Cause: lighting/surge arrestor blown on UGOH below S12355 BMI BUshels No.4 See 1604832,9,41 ex 1603441 | October | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2018-10-18 | N | 313.7029 | N | 26 | Y | Y | 1.1101 | 39.4971 | 94907.3578
[7 empty] | 6623 | 14579 | 1603536 | 2018-10-18 18:20 | 2018-10-18 22:15 | 235 | 11kV | 2115 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 188480 B & C Phase DOLF : 10 Amp Excluded OMS 1603536 & 1603544 | October | 2018 | 2019Q2 | 2019 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2018-10-18 | N | 235 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1545.5796
[7 empty] | 6761 | 15695 | 1603480 | 2018-10-18 16:36 | 2018-10-18 22:18 | 342 | 11kV | 363426 | 1501 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | N | Zn12610 Long Jetty Panel 20 "Matcham St"fdr CB tripped, reclosed and tripped on: Relays: Earth Fault, Earth Fault Check, Overcurrent, B Phase SEL, EFI, Earth Fault Check Tx2 & Tx3 Signals: 11kv trip Abnormal: AB44165 closed, USL42318 Open (dma) Cause: storm, 11kV bond off at AB44165 See 1604995,8 ex 1603480 | October | 2018 | 2019Q2 | 2019 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Not Veg | 2018-10-18 | N | 242.1226 | N | 26 | Y | Y | 1.1101 | 39.4971 | 265581.0015
[7 empty] | 5907 | 6445 | 1603576 | 2018-10-18 19:35 | 2018-10-18 22:20 | 165 | 11kV | 310 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188481 Single phase DOLF : 2 Amp 2A LF 40414 replaced at 2200hrs. 10A Sub DOLF 54310 Farley sub replaced at 2220hrs. Excluded OMS No. 1603576 + 1603589 | October | 2018 | 2019Q2 | 2019 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2018-10-18 | N | 155 | N | 26 | Y | Y | 1.1101 | 39.4971 | 226.5389
[7 empty] | 5964 | 7041 | 1603523 | 2018-10-18 17:47 | 2018-10-18 22:38 | 291 | 11kV | 2619 | 9 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 188471 Feeder isolated to repair 11kV OHM damage at Pole 5G-10008 | October | 2018 | 2019Q2 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2018-10-18 | N | 291 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1913.888
[7 empty] | 6428 | 12430 | 1603579 | 2018-10-18 19:38 | 2018-10-18 23:55 | 257 | 11kV | 3084 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188482 A Phase 10 Amp Fuse Substation DOLF | October | 2018 | 2019Q2 | 2019 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2018-10-18 | N | 257 | N | 26 | Y | Y | 1.1101 | 39.4971 | 2253.6962
[7 empty] | 5494 | 1910 | 1603534 | 2018-10-18 18:17 | 2018-10-19 01:15 | 418 | 11kV | 11286 | 27 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188485 ABC Phase, 20 Amp Fuse Line DOLF L/F 40534 replaced and also downstream L/F 40521 (10A) | October | 2018 | 2019Q2 | 2019 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2018-10-18 | N | 418 | N | 26 | Y | Y | 1.1101 | 39.4971 | 8247.4759
[7 empty] | 6499 | 13275 | 1603651 | 2018-10-19 07:43 | 2018-10-19 08:38 | 55 | 11kV | 1375 | 25 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.6 tripped on: A, B & C phase O/C Front line UG cable fault from Pnl.6 to S8168 to S47663 | October | 2018 | 2019Q2 | 2019 | ZN2568:PA6 | ZN2568:PA6 | ZN02568/000006 | SYDNEY | UG | Not Veg | 2018-10-19 | N | 55 | N | 10 | N | N | 1.1101 | 39.4971 | 1004.8094
[7 empty] | 6269 | 10584 | 1603625 | 2018-10-19 05:07 | 2018-10-19 09:10 | 243 | 11kV | 486 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 188491 3 Phase DOLF : 10 Amp Excluded OMS 1603625 | October | 2018 | 2019Q2 | 2019 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2018-10-19 | N | 243 | N | 10 | N | N | 1.1101 | 39.4971 | 355.1545
[7 empty] | 5891 | 6332 | 1603646 | 2018-10-19 07:42 | 2018-10-19 09:50 | 128 | 11kV | 177119 | 1962 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | At Zn15014 Mona Vale panel 19 tripped on Relays: SEF, EF, Fault Check and EFI Cause: Suspect defective PT @ 15281 Bungan Head Rd - Caused feeder to trip See OMS 1604716 1604715 1604714 1603687/685/659/647/646 | October | 2018 | 2019Q2 | 2019 | ZN15014:PA19 | ZN15014:PA19 | ZN15014/000019 | NORTHERN BEACHES | OH | Not Veg | 2018-10-19 | N | 90.2747 | N | 10 | N | N | 1.1101 | 39.4971 | 129433.3411
[7 empty] | 6319 | 11113 | 1603597 | 2018-10-18 20:44 | 2018-10-19 09:55 | 791 | 11kV | 3164 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn14891 Wyong section of Panel 14R "WSC Hely" fdr PT14722 Mardi McPherson 0.4 A phase 10 amp 11kv drop out fuse cause: storm See 1605052 ex 1603597 | October | 2018 | 2019Q2 | 2019 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | OH | Veg | 2018-10-18 | N | 791 | N | 26 | Y | Y | 1.1101 | 39.4971 | 2312.1579
[7 empty] | 6625 | 14596 | 1603531 | 2018-10-18 18:12 | 2018-10-19 10:15 | 963 | 11kV | 4735 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 188486 Phases A,B,C 10 Amp fuse, Line DOLF Power on 1015am, HV arrestors and HV fuses replaced by P Holland. PD two blown lightning arrestors. high voltage fuses also blown. On call has run out of hours. depot staff please attend and repair 1st am Friday | October | 2018 | 2019Q2 | 2019 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2018-10-18 | N | 947 | N | 26 | Y | Y | 1.1101 | 39.4971 | 3460.1983
[7 empty] | 5756 | 5202 | 1603608 | 2018-10-18 22:13 | 2018-10-19 10:45 | 752 | 11kV | 1504 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 188490 C Phase DOLF : 10 Amp Blown L/A Excluded OMS 1603608 | October | 2018 | 2019Q2 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | OH | Not Veg | 2018-10-18 | N | 752 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1099.0788
[7 empty] | 6837 | 16791 | 1603703 | 2018-10-19 10:34 | 2018-10-19 12:15 | 101 | 11kV | 101 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 188496 B & C Phase DOLF : 10 Amp Excluded OMS 1603703 | October | 2018 | 2019Q2 | 2019 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2018-10-19 | N | 101 | N | 10 | N | N | 1.1101 | 39.4971 | 73.8078
[7 empty] | 5444 | 1342 | 1603624 | 2018-10-19 04:33 | 2018-10-19 12:20 | 467 | 11kV | 1401 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Panel 13 "Peats Ridge Aux No.1" PT13885 Lutana Wise Ferry A & B phase amp HDO's operated Cause: storm See 1605057 ex 1603624,48 | October | 2018 | 2019Q2 | 2019 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2018-10-19 | N | 467 | N | 10 | N | N | 1.1101 | 39.4971 | 1023.8095
[7 empty] | 6910 | 17673 | 1603516 | 2018-10-18 17:53 | 2018-10-19 15:05 | 1272 | 11kV | 229324 | 1619 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | Lightning | N | Zn13000 Lake Munmorah Panel 11 "Lake Munmorah Aux No.2" opened by AOp after report of 11kv on the ground. OH DOwn CCT on the ground near PT18591 Rutleys Pacific 1.3 See 1605037,40,2 ex 1603517,22,98 | October | 2018 | 2019Q2 | 2019 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2018-10-18 | N | 141.6455 | N | 26 | Y | Y | 1.1101 | 39.4971 | 167583.2153
[7 empty] | 6770 | 15786 | 1603729 | 2018-10-19 12:11 | 2018-10-19 15:20 | 189 | 11kV | 57883 | 999 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.25 tripped, reclosed & tripped on: 51T (ABC pahse) Field EFIs: All to S10762 Abnormal: S10320 Sw/B open (defective cable beyond) LB30088 closed Cable to UGOH failed See 1604789 1604790 1604792 1604793 1604794 1604795 | October | 2018 | 2019Q2 | 2019 | ZN10999:PA25 | ZN10999:PA25 | ZN10999/000025 | GEORGES RIVER | UG | Not Veg | 2018-10-19 | N | 57.9409 | N | 10 | N | N | 1.1101 | 39.4971 | 42299.1891
[7 empty] | 6849 | 16875 | 1603744 | 2018-10-19 13:08 | 2018-10-19 15:26 | 138 | 11kV | 138 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn2835 Burwood section of Pa41 S4100 Beresford Covenant Tx F/Sw has tripped Nuisance trip see DMA 8th time See 1605085 ex 1603744 | October | 2018 | 2019Q2 | 2019 | ZN2835:PA41 | ZN2835:PA41 | ZN02835/000041 | STRATHFIELD | OH | Veg | 2018-10-19 | N | 138 | N | 10 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 6231 | 10284 | 1603440 | 2018-10-18 15:45 | 2018-10-19 15:30 | 1425 | 11kV | 15219 | 373 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Wind Storm | N | Ex Zn102630 Peats Ridge Panel 8 "Kulnura" IR61340 George Vloodtree 0.2 tripped, reclosed and locked out on: Relays: OC trip, SEF trip EFI: nil Cause: Lightning/Surge Arrestor PT11566 George Downs spring 0.1 lightning strike on PT. PT was on ifre. PT left isolated and interrupted See 1604827,9,30,1 ex 1603440,4,7,709 | October | 2018 | 2019Q2 | 2019 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2018-10-18 | N | 40.8016 | N | 26 | Y | Y | 1.1101 | 39.4971 | 11121.5963
[7 empty] | 5989 | 7380 | 1603706 | 2018-10-19 11:05 | 2018-10-19 15:30 | 265 | 11kV | 1325 | 5 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of Panel 24 "LB49474" LB44745 opened due to fallen 11kv pole Cause: pole defective/failure | October | 2018 | 2019Q2 | 2019 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2018-10-19 | N | 265 | N | 10 | N | N | 1.1101 | 39.4971 | 968.2709
[7 empty] | 5828 | 5729 | 1603819 | 2018-10-19 17:03 | 2018-10-19 18:06 | 63 | 11kV | 1071 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 188500 C Phase DOLF : 31 Amp Excluded OMS 1603819 | October | 2018 | 2019Q2 | 2019 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Veg | 2018-10-19 | N | 63 | N | 10 | N | N | 1.1101 | 39.4971 | 782.6552
[7 empty] | 6153 | 9441 | 1603571 | 2018-10-18 19:08 | 2018-10-19 18:10 | 1382 | 11kV | 395202 | 1491 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Lightning | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap Rd" fdr Cause:OH down. Came into contact with LV Interruption time unknown at the time = zone in SCADA fail used DNMS load trends after restoration See 1604930,2,3 ex 1603562,71,617 | October | 2018 | 2019Q2 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2018-10-18 | N | 265.0584 | N | 26 | Y | Y | 1.1101 | 39.4971 | 288801.9651
[7 empty] | 6003 | 7637 | 1603835 | 2018-10-19 18:08 | 2018-10-19 21:20 | 192 | 11kV | 384 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 188501 A phase 10 Amp Fuse Substation DOLF Replaced Faulty Lightning Arrestor | October | 2018 | 2019Q2 | 2019 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2018-10-19 | N | 192 | N | 10 | N | N | 1.1101 | 39.4971 | 280.6159
[7 empty] | 6942 | 17922 | 1603845 | 2018-10-20 00:53 | 2018-10-20 01:41 | 48 | 11kV | 1824 | 38 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | Y | LID 188503 Cross Arm 11kV Tap open cct at pole AF-50031 Note: customer reported Low Volts earlier in evening | October | 2018 | 2019Q2 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2018-10-20 | N | 48 | N | 9 | N | N | 1.1101 | 39.4971 | 1332.9254
[7 empty] | 6347 | 11409 | 1603873 | 2018-10-20 06:16 | 2018-10-20 07:53 | 97 | 11kV | 439 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 188504/01 DOLF : 16 Amp Note Sub 52017 and 50654 had both blown DOL'F's. | October | 2018 | 2019Q2 | 2019 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2018-10-20 | Y | 87.8 | N | 9 | N | Y | 1.1101 | 39.4971 | 320.8083
[7 empty] | 5697 | 4639 | 1603893 | 2018-10-20 09:10 | 2018-10-20 12:12 | 182 | 11kV | 1254 | 7 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | Section of 11kV feeder (ex Wyong Pnl.1) from LB49777 to LB44637 interupted to remove large tree branch from 11kV mains. See 1603898 1603983 | October | 2018 | 2019Q2 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2018-10-20 | Y | 179.1429 | N | 9 | N | Y | 1.1101 | 39.4971 | 916.3862
[7 empty] | 6048 | 8113 | 1603910 | 2018-10-20 13:00 | 2018-10-20 13:35 | 35 | 11kV | 1085 | 31 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | At S2117 Lakeside Rd 400A fuse blown on A B and C phase of distributor 2. Cause: distributor 2 interrupted by DOp to remove crane off LV network See OMS 1603921 1603911 1603910 | October | 2018 | 2019Q2 | 2019 | ZN4545:PA44 | ZN4545:PA44 | ZN04545/000044 | RYDE | OH | Not Veg | 2018-10-20 | N | 35 | N | 9 | N | N | 1.1101 | 39.4971 | 792.886
[7 empty] | 6664 | 14947 | 1603984 | 2018-10-20 17:45 | 2018-10-20 19:00 | 75 | 11kV | 24072 | 324 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At Zn3154 St Ives Panel 23 tripped and locked out on Relays: IOC and Timed A phase EFI Abnormal Switching: AB2081 Open and defective - LB64168 Closed Cause: Storm at the time of interruption - Suspect lightning strike See OMS 1604779 1604780 1603984 | October | 2018 | 2019Q2 | 2019 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Not Veg | 2018-10-20 | N | 74.2963 | N | 9 | N | N | 1.1101 | 39.4971 | 17591.1076
[7 empty] | 6008 | 7725 | 1603976 | 2018-10-20 17:32 | 2018-10-20 19:26 | 114 | 11kV | 116280 | 1020 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | At Zn965 Pennant Hills Panel 43 tripped and reclosed to lockout on Relays: OC and EFI Cause: Feeder patrolled after storm - Supply restored and no cause found. See OMS 1603977 1603976 | October | 2018 | 2019Q2 | 2019 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Veg | 2018-10-20 | Y | 114 | N | 9 | N | Y | 1.1101 | 39.4971 | 84973.9943
[7 empty] | 6370 | 11705 | 1603975 | 2018-10-20 17:32 | 2018-10-20 19:27 | 115 | 11kV | 148810 | 1294 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | At Zn965 Pennant Hill panel 33 tripped and reclosed to lockout on Relays: Overcurrent, Timing and lockout Cause: feeder patrolled - Cause not ascertained CC1: 11-"Despatch to re-issue" | October | 2018 | 2019Q2 | 2019 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Veg | 2018-10-20 | Y | 115 | N | 9 | N | Y | 1.1101 | 39.4971 | 108745.9588
[7 empty] | 6206 | 10049 | 1603997 | 2018-10-20 17:50 | 2018-10-20 19:33 | 103 | 11kV | 112682 | 1094 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn9550 Gwawley Bay - Pnl.43 tripped on: ABC phase O/C Field EIFIs: S48722 S9073 S49698 Lightning | October | 2018 | 2019Q2 | 2019 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Not Veg | 2018-10-20 | N | 103 | N | 9 | N | N | 1.1101 | 39.4971 | 82344.682
[7 empty] | 6186 | 9922 | 1603981 | 2018-10-20 17:43 | 2018-10-20 19:35 | 112 | 11kV | 82995 | 862 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | Y | Zn9245 Engadine - Pnl.19 tripped on: ABC IOC, SEL Field EFIs: NIL Abnormal : Open bonds at :LB35051 Lightning strike has damaged roadside arrestor at PT47661. restored via LV // 1159 & 758 See 1604893 1604894 | October | 2018 | 2019Q2 | 2019 | ZN9245:PA19 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | OH | Not Veg | 2018-10-20 | N | 96.2819 | N | 9 | N | N | 1.1101 | 39.4971 | 60650.2981
[7 empty] | 5955 | 6974 | 1604126 | 2018-10-20 18:54 | 2018-10-20 19:55 | 61 | 11kV | 122 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 188536 3 phase DOLF : 10 Amp Excluded OMS 1604126 | October | 2018 | 2019Q2 | 2019 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2018-10-20 | Y | 61 | N | 9 | N | Y | 1.1101 | 39.4971 | 89.154
[7 empty] | 6895 | 17509 | 1604094 | 2018-10-20 18:38 | 2018-10-20 20:05 | 87 | 11kV | 164118 | 2106 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zb12610 long Jetty - Pnl.13 tripped on: A & B phase O/C Cause not ascertained. Storm See 1605004 1605005 | October | 2018 | 2019Q2 | 2019 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Veg | 2018-10-20 | Y | 77.9288 | N | 9 | N | Y | 1.1101 | 39.4971 | 119932.5937
[7 empty] | 6227 | 10228 | 1603952 | 2018-10-20 14:58 | 2018-10-20 20:13 | 315 | 11kV | 123606 | 564 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | Y | LID 188508 3 fault operations 3 phase Intellirupter; Overcurrent Broken 11kV x arm at pole OS-30032. Excluded OMS 1603952 | October | 2018 | 2019Q2 | 2019 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2018-10-20 | N | 219.1596 | N | 9 | N | N | 1.1101 | 39.4971 | 90327.619
[7 empty] | 7071 | 19346 | 1604010 | 2018-10-20 18:02 | 2018-10-20 20:55 | 173 | 11kV | 244276 | 1412 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | Y | Zn10998 Rockdale Pnl.32 tripped, reclosed & tripped on: ABC IOC, ABC OC Cause not ascertained. Likely lightning | October | 2018 | 2019Q2 | 2019 | ZN10998:PA32 | ZN10998:PA32 | ZN10998/000032 | BAYSIDE | OH | Veg | 2018-10-20 | Y | 173 | N | 9 | N | Y | 1.1101 | 39.4971 | 178509.6959
[7 empty] | 6751 | 15597 | 1604036 | 2018-10-20 18:14 | 2018-10-20 21:12 | 178 | 11kV | 143723 | 1079 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At Zn15002 Narrabeen Panel 8 tripped, reclosed, tripped and locked out on Relays: timed B phase O/C, earth Fault,frame leakage and SEL Abnormal Switching: CP25723 Open and Defective, S16686 Closed Cause: Storm at the time of interruption - feeder patrolled suspect lightning strike See OMS 1604805 1604807 1604808 1604036 | October | 2018 | 2019Q2 | 2019 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | OH | Not Veg | 2018-10-20 | N | 133.2002 | N | 9 | N | N | 1.1101 | 39.4971 | 105028.5293
[7 empty] | 6952 | 18056 | 1604253 | 2018-10-20 20:17 | 2018-10-20 21:35 | 78 | 11kV | 234 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 188548 DOLF : 10 Amp Excluded OMS 1604253 | October | 2018 | 2019Q2 | 2019 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2018-10-20 | N | 78 | N | 9 | N | N | 1.1101 | 39.4971 | 171.0003
[7 empty] | 6035 | 7971 | 1603999 | 2018-10-20 17:55 | 2018-10-20 21:37 | 222 | 11kV | 498334 | 2253 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn10999 Kogarah - Pnll.22 tripped on: A & C IOC, EFI Lightning. See 1604858 1604860 | October | 2018 | 2019Q2 | 2019 | ZN10999:PA22 | ZN10999:PA22 | ZN10999/000022 | BAYSIDE | OH | Not Veg | 2018-10-20 | Y | 221.1869 | N | 9 | N | Y | 1.1101 | 39.4971 | 364167.7888
[7 empty] | 5911 | 6475 | 1603982 | 2018-10-20 17:33 | 2018-10-20 22:33 | 300 | 11kV | 16045 | 69 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 188515 2 Fault operations Phases A, C, Overcurrent FDR Patrolled, nothing found, power restored PROT A ph 554 amps, C Ph 536 Amps | October | 2018 | 2019Q2 | 2019 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2018-10-20 | N | 232.5362 | N | 9 | N | N | 1.1101 | 39.4971 | 11725.2128
[7 empty] | 5913 | 6498 | 1604125 | 2018-10-20 18:54 | 2018-10-20 22:40 | 226 | 11kV | 3212 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 188547 B & C Phase DOLF : 31 Amp 3 xdolfs replaced sub 50208 3.15 amp, 1 x a ph dolf sub 50258 Excluded OMS 1604125 | October | 2018 | 2019Q2 | 2019 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2018-10-20 | Y | 188.9412 | N | 9 | N | Y | 1.1101 | 39.4971 | 2347.2349
[7 empty] | 6169 | 9608 | 1604059 | 2018-10-20 18:25 | 2018-10-20 22:42 | 257 | 11kV | 257311 | 1491 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | Y | REC44936 Bentley Rd tripped, reclosed, tripped & loaced out on: IOC trip. REC44937 Alan St open a few minutes later on no protection operation Lightning strike damaged REC44937 See 1605027 1605030 1605031 1605032 1605032 1605036 1506038 1605041 1605043 | October | 2018 | 2019Q2 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2018-10-20 | Y | 172.5761 | N | 9 | N | Y | 1.1101 | 39.4971 | 188035.2894
[7 empty] | 5580 | 3308 | 1604189 | 2018-10-20 19:29 | 2018-10-20 22:55 | 206 | 11kV | 3090 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | PT12722 Colongra Kamilaroo - Centre phase HDO operated (16A) Cause not ascertained | October | 2018 | 2019Q2 | 2019 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Veg | 2018-10-20 | Y | 206 | N | 9 | N | Y | 1.1101 | 39.4971 | 2258.0809
[7 empty] | 6027 | 7903 | 1603994 | 2018-10-20 17:52 | 2018-10-20 23:20 | 328 | 11kV | 707950 | 2836 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | Y | Zn10999 Kogarah - Pnl.17 tripped on: B & C phase O/C Field EFIs: S64891 S10144 S48982 UGOH to S10789 appears to have a blown arrestor See 1604816 1604817 1604818 1604818 1604820 | October | 2018 | 2019Q2 | 2019 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | OH | Not Veg | 2018-10-20 | Y | 249.6298 | N | 9 | N | Y | 1.1101 | 39.4971 | 517348.979
[7 empty] | 6724 | 15335 | 1604948 | 2018-10-20 19:30 | 2018-10-20 23:22 | 232 | 11kV | 5568 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 188550 B Phase DOLF : 40 Amp LINE FUSE FOUND BLOWN AFTER ATTENDING JOB AT SUB 46321 | October | 2018 | 2019Q2 | 2019 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2018-10-20 | Y | 232 | N | 9 | N | Y | 1.1101 | 39.4971 | 4068.9302
[7 empty] | 7149 | 19988 | 1604194 | 2018-10-20 19:33 | 2018-10-20 23:27 | 234 | 11kV | 3978 | 17 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 188549 A Phase DOLF sub isolated to replace LA Excluded oms 1604194 | October | 2018 | 2019Q2 | 2019 | 509:33397 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2018-10-20 | Y | 234 | N | 9 | N | Y | 1.1101 | 39.4971 | 2907.0051
[7 empty] | 5624 | 3739 | 1604008 | 2018-10-20 17:55 | 2018-10-20 23:29 | 334 | 11kV | 260220 | 880 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn10998 Rockdale - Pnl.2 tripped on: A & B Phase IOC Field EFIs S10109 Lightning See 1604733 1604734 1604735 | October | 2018 | 2019Q2 | 2019 | ZN10998:PA2 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Not Veg | 2018-10-20 | Y | 295.7045 | N | 9 | N | Y | 1.1101 | 39.4971 | 190161.1008
[7 empty] | 6733 | 15382 | 1604095 | 2018-10-20 18:41 | 2018-10-21 00:45 | 364 | 11kV | 22204 | 61 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 188551 Phases A and B, 16 Amp fuse Line DOLF also refer to OMS 1604095 | October | 2018 | 2019Q2 | 2019 | 526:34641 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Veg | 2018-10-20 | Y | 364 | N | 9 | N | Y | 1.1101 | 39.4971 | 16226.0283
[7 empty] | 5373 | 452 | 1604121 | 2018-10-20 18:51 | 2018-10-21 00:54 | 362.6833 | 11kV | 9792.45 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 188552 A,B,C Phases, 10 Amp fuse, Line DOLF | October | 2018 | 2019Q2 | 2019 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Veg | 2018-10-20 | Y | 362.6833 | N | 9 | N | Y | 1.1101 | 39.4971 | 7156.0336
[7 empty] | 6137 | 9272 | 1604289 | 2018-10-20 21:19 | 2018-10-21 01:20 | 241 | 11kV | 142148 | 1412 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Lightning | Y | Zn10998 Rockdale - Pnl.32 tripped on: IOC ABC phase Field EFIs: S10658 S10259 UGOH on tee to S10723 Mutch Tancred failed due to lightning. Restored via LV // See 1604753 1604754 1604759 | October | 2018 | 2019Q2 | 2019 | ZN10998:PA32 | ZN10998:PA32 | ZN10998/000032 | BAYSIDE | OH | Not Veg | 2018-10-20 | Y | 100.6714 | N | 9 | N | Y | 1.1101 | 39.4971 | 103877.5657
[7 empty] | 6925 | 17821 | 1604090 | 2018-10-20 18:37 | 2018-10-21 03:00 | 503 | 11kV | 74671 | 474 | HV | Lightning Strike | Adverse Weather/Environment | Insulator | Unplanned | Lightning | Y | Zn14891 Wyong - Pnl.14 tripped, reclosed & tripped on: A & B phase O/C Field EFIs: S14799 S14630 Lightning caused insulator to fail. See 1604977 1604979 | October | 2018 | 2019Q2 | 2019 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | OH | Not Veg | 2018-10-20 | Y | 157.5338 | N | 9 | N | Y | 1.1101 | 39.4971 | 54567.3644
[7 empty] | 5832 | 5750 | 1603974 | 2018-10-20 17:31 | 2018-10-21 03:25 | 594.2 | 11kV | 11289.8 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 188553 A & C phase DOLF : 20 Amp Feeder needs patrol in daylight, 1 st fuse blew 2nd try held in. | October | 2018 | 2019Q2 | 2019 | 507:80914 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Veg | 2018-10-20 | Y | 594.2 | N | 9 | N | Y | 1.1101 | 39.4971 | 8250.2528
[7 empty] | 6512 | 13438 | 1604361 | 2018-10-21 03:53 | 2018-10-21 05:40 | 107 | 11kV | 118877 | 1111 | HV | Animal Possum | Animal | UGOH | Unplanned | Previous Storm | N | Zn10994 Mortdale - Pnl.10 tripped, reclosed & tripped on: B & C phase O/C Field EFIs: NIL Possum on UGOH to Sw/A @ S10123 and HV bond burnt off at LK30289 (footpath phase) | October | 2018 | 2019Q2 | 2019 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Not Veg | 2018-10-21 | N | 107 | N | 10 | N | N | 1.1101 | 39.4971 | 86871.8053
[7 empty] | 6750 | 15588 | 1604383 | 2018-10-21 06:28 | 2018-10-21 07:52 | 84 | 11kV | 45190 | 662 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | Zn9037 Miranda - Pnl.7 tripped on: C phase IOC Field EFIs :S9938 UG cable fault between S9938 to S9235 tee PT9639 See 1604886 1604887 1604888 | October | 2018 | 2019Q2 | 2019 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | UG | Not Veg | 2018-10-21 | N | 68.2628 | N | 10 | N | N | 1.1101 | 39.4971 | 33023.5191
[7 empty] | 5762 | 5292 | 1604381 | 2018-10-21 07:30 | 2018-10-21 08:40 | 70 | 11kV | 140 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Rain Wind Storm | N | LID 188563 C phase, Substatin DOLF Broken Life lIne lead | October | 2018 | 2019Q2 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2018-10-21 | N | 70 | N | 10 | N | N | 1.1101 | 39.4971 | 102.3079
[7 empty] | 6448 | 12660 | 1604392 | 2018-10-21 06:51 | 2018-10-21 08:55 | 124 | 11kV | 1116 | 9 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Previous Storm | N | Ex Zn12650 West Gosford section of Pa1 PT12166 Glen Boorawa 0.2 11kv 16A footpath HDO blown After Previous Storm C Phase Surge Arrestor & HDO found blown. (Upstream REC.44936 Bentley Rd tripped previous evening for Blown Surge Arrestor @ REC.44937 Alan St - See previous Feeder Interuption 18:25 22:42 20/10/18). PT.13231 Glen Alan - Fuses Ok (Suspect G.I.S. Issue). See 1605075 ex 1604392,426 | October | 2018 | 2019Q2 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2018-10-21 | N | 124 | N | 10 | N | N | 1.1101 | 39.4971 | 815.5399
[7 empty] | 6357 | 11544 | 1604205 | 2018-10-20 19:42 | 2018-10-21 09:55 | 853 | 11kV | 4265 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 188555 A phase Fuse 10 Amp Substation DOLF Volts = 239, 241, 240 Ampt = 8,2,20 Note: first NS call received was 20/10/18 19:42, see related jobs | October | 2018 | 2019Q2 | 2019 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2018-10-20 | Y | 853 | N | 9 | N | Y | 1.1101 | 39.4971 | 3116.7362
[7 empty] | 5850 | 5902 | 1604470 | 2018-10-21 09:49 | 2018-10-21 12:06 | 137 | 11kV | 411 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 188556 A Phase DOLF : 10 Amp Excluded OMS 1604470 | October | 2018 | 2019Q2 | 2019 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2018-10-21 | N | 137 | N | 10 | N | N | 1.1101 | 39.4971 | 300.3467
[7 empty] | 6870 | 17158 | 1604384 | 2018-10-21 11:00 | 2018-10-21 12:10 | 70 | 11kV | 420 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188557 C Phase, 16 Amp fuse, substation DOLF Note: customer reports lov volts and flickering lights prior - refer to related job | October | 2018 | 2019Q2 | 2019 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2018-10-21 | N | 70 | N | 10 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 7163 | 20151 | 1604493 | 2018-10-21 10:32 | 2018-10-21 12:25 | 113 | 11kV | 113 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188558 B and C Phase, 10 Amp fuse, substation DOLF | October | 2018 | 2019Q2 | 2019 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2018-10-21 | N | 113 | N | 10 | N | N | 1.1101 | 39.4971 | 82.5771
[7 empty] | 5488 | 1815 | 1604455 | 2018-10-21 11:45 | 2018-10-21 13:05 | 80 | 11kV | 80 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188560 C Phase, 10 Amp fuse Substation DOLF | October | 2018 | 2019Q2 | 2019 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2018-10-21 | N | 80 | N | 10 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 6568 | 14031 | 1603996 | 2018-10-20 17:52 | 2018-10-21 14:37 | 1245 | 11kV | 670437 | 750 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 188518 1 fault operation Overcurrent tree on mains sub 54213 section isolated for repair. Excluded oms 1603996 | October | 2018 | 2019Q2 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2018-10-20 | Y | 893.916 | N | 9 | N | Y | 1.1101 | 39.4971 | 489935.5851
[7 empty] | 5355 | 200 | 1604023 | 2018-10-20 18:07 | 2018-10-21 15:00 | 1253 | 11kV | 51671 | 99 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC44995 Kulnura - tripped on: IOC trip Tree brought down mains on George Downes Rd See 1605050 1605051 | October | 2018 | 2019Q2 | 2019 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2018-10-20 | Y | 521.9293 | N | 9 | N | Y | 1.1101 | 39.4971 | 37759.6428
[7 empty] | 6372 | 11736 | 1603979 | 2018-10-20 17:38 | 2018-10-21 18:17 | 1479 | 11kV | 125367 | 244 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | Y | recloser CP420 Reynolds Crosslands tripped and locked out on Relays: IOC trip and OC trip Cause: Fault in section of 11kV feeder from LB129 to recloser CP705 Blown Lightning arrestor @ PT1868 NOTE: CP421 tripped @ 02:19, 11:09, 14:34 while attempting to restore section between CP129 and LB702 See OMS 1605026 1605029 1605033 1605035 1605039 1604517 1604369 1604347 1604197 1604114 1603995 1603979 | October | 2018 | 2019Q2 | 2019 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2018-10-20 | Y | 513.7992 | N | 9 | N | Y | 1.1101 | 39.4971 | 91614.5059
[7 empty] | 6848 | 16859 | 1603973 | 2018-10-20 17:27 | 2018-10-21 19:20 | 1553 | 11kV | 198691 | 966 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | Y | At Zn847 Hornsby Panel 18 tripped reclosed tripped and locked out on Relays: Earth fault, EFI and Fault Check Cause: Surge arrestor to S413 failed. See OMS 1604973 1604987 1604980 1604981 16036973 1604210 | October | 2018 | 2019Q2 | 2019 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Not Veg | 2018-10-20 | Y | 205.6843 | N | 9 | N | Y | 1.1101 | 39.4971 | 145197.5224
[7 empty] | 6527 | 13646 | 1604584 | 2018-10-21 22:30 | 2018-10-21 23:35 | 65 | 11kV | 2730 | 42 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 188569 11kV section isolated to repair 33kV pin insulator pole JT-10011 Excluded 1604584 | October | 2018 | 2019Q2 | 2019 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2018-10-21 | N | 65 | N | 10 | N | N | 1.1101 | 39.4971 | 1995.0035
[7 empty] | 5996 | 7535 | 1604183 | 2018-10-21 19:24 | 2018-10-21 23:59 | 275 | 11kV | 26125 | 95 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | At PT733 Somerville Hillview - 63A footpath fuse blown Cause not ascertained - Suspect lightning See OMS 1604896 1604183 | October | 2018 | 2019Q2 | 2019 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Not Veg | 2018-10-21 | N | 275 | N | 10 | N | N | 1.1101 | 39.4971 | 19091.3794
[7 empty] | 6257 | 10478 | 1604629 | 2018-10-22 00:22 | 2018-10-22 02:05 | 103 | 11kV | 515 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 188570 B Phase DOLF : 10 Amp Excluded OMS 1604629 | October | 2018 | 2019Q2 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2018-10-22 | N | 103 | N | 6 | N | N | 1.1101 | 39.4971 | 376.3468
[7 empty] | 6818 | 16580 | 1604587 | 2018-10-21 18:09 | 2018-10-22 10:15 | 966 | 11kV | 966 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 188567 Substaion DOLF Blown arrester replaced | October | 2018 | 2019Q2 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2018-10-21 | N | 966 | Y | 10 | N | Y | 1.1101 | 39.4971 | 705.9243
[7 empty] | 6584 | 14286 | 1604645 | 2018-10-22 06:36 | 2018-10-22 13:40 | 424 | 11kV | 7249 | 171 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 188578 pole fire at transfomer, caused transformer to be faulty Excluded oms 1604648,1604649,1604645 | October | 2018 | 2019Q2 | 2019 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Not Veg | 2018-10-22 | N | 42.3918 | N | 6 | N | N | 1.1101 | 39.4971 | 5297.3554
[7 empty] | 6224 | 10203 | 1604783 | 2018-10-22 10:15 | 2018-10-22 14:07 | 232 | 11kV | 32712 | 141 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 188571 Tree on over head mains between subs 59003 & 59004 Fdr interrupted to remove tree contacting OHM. Excluded OMS 1604783 | October | 2018 | 2019Q2 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2018-10-22 | N | 232 | N | 6 | N | N | 1.1101 | 39.4971 | 23904.9648
[7 empty] | 6376 | 11757 | 1604836 | 2018-10-22 11:05 | 2018-10-22 14:30 | 205 | 11kV | 2655 | 33 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188574 B Phase Bph 11kV OHM broken away from pole MD-90690 on ground. Excluded OMS No. 1604836 + 1604907 | October | 2018 | 2019Q2 | 2019 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2018-10-22 | N | 80.4545 | N | 6 | N | N | 1.1101 | 39.4971 | 1940.1957
[7 empty] | 7097 | 19557 | 1605144 | 2018-10-22 17:39 | 2018-10-22 18:46 | 67 | 11kV | 64611 | 983 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn36100 Rose Bay - Pnl.23 tripped on: Earth Fault Field EFIs: S3361 Contractor hit 11Kv Feeder between S.3361 Chaleyer St Sw/B and S.2423 Liverpoool Old Sw/A JOINT ENTERPRISE AUSTRALIA - ABU BLOWING AIR INTO CONJUTE UNDERGROUND - LOOKING FOR THE CONJUTE WITH A BAR - STRUCK UNDERGROUND CABLE. ABU ALMAALIKI See 1605213 1605214 | October | 2018 | 2019Q2 | 2019 | ZN36100:PA23 | ZN36100:PA23 | ZN36100/000023 | WAVERLEY | UG | Not Veg | 2018-10-22 | N | 65.7284 | N | 6 | N | N | 1.1101 | 39.4971 | 47215.8131
[7 empty] | 5968 | 7080 | 1605150 | 2018-10-22 18:30 | 2018-10-22 20:45 | 135 | 11kV | 135 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188580 DOLF : 10 Amp Excluded OMS 1605150 | October | 2018 | 2019Q2 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2018-10-22 | N | 135 | N | 6 | N | N | 1.1101 | 39.4971 | 98.654
[7 empty] | 5875 | 6131 | 1605173 | 2018-10-23 05:37 | 2018-10-23 07:30 | 113 | 11kV | 3955 | 35 | HV | Equipment Failed in Service | Equipment Failure | Enclosed Load Break Switch | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale section of PT12798 Geoffrey Wyong 0.1 20amps Centre phase HVDO caught fir. Replaced by DOp See 1605679 ex 1605174,9 | October | 2018 | 2019Q2 | 2019 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2018-10-23 | N | 113 | N | 7 | N | N | 1.1101 | 39.4971 | 2890.1973
[7 empty] | 6272 | 10602 | 1605176 | 2018-10-23 06:22 | 2018-10-23 10:00 | 218 | 11kV | 4808 | 35 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188583 3 fault operations Overcurrent Mine reports stolen private OHM beyond Ashton Coal Borehole Pump RAGCB. Broken roller at pole CN-50303. Excluded OMS No. 1605176 | October | 2018 | 2019Q2 | 2019 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Not Veg | 2018-10-23 | N | 137.3714 | N | 7 | N | N | 1.1101 | 39.4971 | 3513.5446
[7 empty] | 6838 | 16793 | 1605267 | 2018-10-23 12:32 | 2018-10-23 13:59 | 87 | 11kV | 1827 | 66 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 188597 4 fault operations Overcurrent Crossarm failure at pole AM-40069. Sw 49180 T/R/T/R/Lo at 1232hrs. Target: OC Sw 49175 T/Lo at 1245hrs. Target: OC Excluded OMS No. 1605274, 1605267, 1605284 | October | 2018 | 2019Q2 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2018-10-23 | N | 27.6818 | N | 7 | N | N | 1.1101 | 39.4971 | 1335.1177
[7 empty] | 5688 | 4535 | 1605319 | 2018-10-23 15:32 | 2018-10-23 16:55 | 83 | 11kV | 166 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 188601 C Phase DOLF : 10 Amp Excluded OMS 1605319 | October | 2018 | 2019Q2 | 2019 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2018-10-23 | N | 83 | N | 7 | N | N | 1.1101 | 39.4971 | 121.3079
[7 empty] | 6597 | 14348 | 1605270 | 2018-10-23 12:40 | 2018-10-23 18:30 | 350 | 11kV | 700 | 2 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188599 Tree on Sub 78074 Excluded OMS 1605270 | October | 2018 | 2019Q2 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2018-10-23 | N | 350 | N | 7 | N | N | 1.1101 | 39.4971 | 511.5394
[7 empty] | 6574 | 14123 | 1605364 | 2018-10-23 17:36 | 2018-10-23 19:00 | 84 | 11kV | 168 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188603 A Phase DOLF : 10 Amp Excluded OMS 1605364 | October | 2018 | 2019Q2 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2018-10-23 | N | 84 | N | 7 | N | N | 1.1101 | 39.4971 | 122.7694
[7 empty] | 6679 | 15073 | 1605280 | 2018-10-23 13:02 | 2018-10-23 19:17 | 375 | 11kV | 750 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 188604 Single phase DOLF : 10 Amp Excluded OMS 1605280 | October | 2018 | 2019Q2 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2018-10-23 | N | 375 | N | 7 | N | N | 1.1101 | 39.4971 | 548.0779
[7 empty] | 6616 | 14521 | 1605388 | 2018-10-24 02:47 | 2018-10-24 04:01 | 74 | 11kV | 104188 | 1611 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Zn12580 Erina Pa10 "Erina High Ernest" fdr tripped on Singals: 11kv trip Relays: C Ph IOC EFI: nil Cause: not ascertained See 1605711,2 ex 1605388 | October | 2018 | 2019Q2 | 2019 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Veg | 2018-10-24 | N | 64.6729 | N | 4 | N | N | 1.1101 | 39.4971 | 76137.5174
[7 empty] | 6220 | 10172 | 1605392 | 2018-10-24 03:09 | 2018-10-24 05:41 | 152 | 11kV | 310483 | 2118 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn10999 Kogarah- Pnl.22 tripped, reclosed, tripped & locked out. Field EFIs: S50796 Tree branch on OH mains outside 41 Willison Rd See 1605726 1605727 | October | 2018 | 2019Q2 | 2019 | ZN10999:PA22 | ZN10999:PA22 | ZN10999/000022 | BAYSIDE | OH | Veg | 2018-10-24 | N | 146.5925 | N | 4 | N | N | 1.1101 | 39.4971 | 226891.8187
[7 empty] | 6995 | 18489 | 1605389 | 2018-10-24 02:34 | 2018-10-24 16:00 | 806 | 11kV | 12318 | 57 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa1 RE44604 Dog Trap Rd tripped and reclosed and tripped on Relays: OC trip, Lockout Cause: tree branch brought down OH near LK41631. High into low. Checked by EMSO See 1605682,3,5 ex 1605389,406,15 | October | 2018 | 2019Q2 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2018-10-24 | N | 216.1053 | N | 4 | N | N | 1.1101 | 39.4971 | 9001.6311
[7 empty] | 5830 | 5745 | 1605581 | 2018-10-24 16:50 | 2018-10-24 17:35 | 45 | 11kV | 900 | 20 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188615 Short interruption to make area safe following the theft of several spans of 11kV OH mains. A Mills reported Mains stolen between poles JS-30949 and pole JS-67002 along Masonite Rd. | October | 2018 | 2019Q2 | 2019 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2018-10-24 | N | 45 | N | 4 | N | N | 1.1101 | 39.4971 | 657.6935
[7 empty] | 6093 | 8682 | 1605628 | 2018-10-25 02:58 | 2018-10-25 04:20 | 82 | 11kV | 47154 | 881 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | REC63273 Sutherland Mitchell - tripped, reclosed & locked out Lightning arrestor at REC 63273 footpath phase failed. PT9559 restored via LV // 516, 515, 956 See 1605737 1605739 | October | 2018 | 2019Q2 | 2019 | ZN9252:PA24 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Not Veg | 2018-10-25 | N | 53.5233 | N | 3 | N | N | 1.1101 | 39.4971 | 34458.7524
[7 empty] | 6614 | 14496 | 1605653 | 2018-10-25 08:12 | 2018-10-25 09:15 | 63 | 11kV | 80103 | 1273 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12650 West Gosford Panel 6 "SCC Racecourse" fdr tripped and reclosed and tripped on Relays: O/C & E/F, lockout, timing, E/F check Tx11 Signals: 11kv trip EFI:S11794 Cause: Contractor error caused failure Crane Operator in Beane St W near Racecourse Rd brought crane into contact with 11kv OH mains. OH mains to repair damage See 1605914,5 ex 1605653 | October | 2018 | 2019Q2 | 2019 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Not Veg | 2018-10-25 | N | 62.9246 | N | 3 | N | N | 1.1101 | 39.4971 | 58536.9098
[7 empty] | 6874 | 17185 | 1605752 | 2018-10-25 12:05 | 2018-10-26 10:10 | 1325 | 11kV | 10173 | 72 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2400 Berowra Panel 13 tripped on Relays: Earth Fault and Fault Check. Signals: 11kV trip with EFI Cause: UG cable fault between S35942 - S6731 - S7477 -S65705 See OMS 1606666 1606668 1606669 1605752 | October | 2018 | 2019Q2 | 2019 | ZN2400:PA13 | ZN2400:PA13 | ZN02400/000013 | HORNSBY | UG | Not Veg | 2018-10-25 | N | 141.2917 | N | 3 | N | N | 1.1101 | 39.4971 | 7434.1283
[7 empty] | 6867 | 17112 | 1605879 | 2018-10-26 09:21 | 2018-10-26 10:27 | 66 | 11kV | 3762 | 57 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188628 C Phase section isolated for emerg repair to stranded conductor pole EO-30270 Excluded oms 1605879 | October | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-10-26 | N | 66 | N | 2 | N | N | 1.1101 | 39.4971 | 2749.1586
[7 empty] | 6937 | 17906 | 1605960 | 2018-10-26 14:54 | 2018-10-26 20:30 | 336 | 11kV | 65472 | 880 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14143 Somersby Panel 17 "Somersby Falls" fdr tripped on Relays: A&B phase OC, EF, EFI Signals: 11kv trip EFI: Reset S18569 S18639 Abnormal: S14023SwB closed S18084SwA Open Cause: tree/branch brought down OH in vitasalo rd See 1606348,50 ex 1605960,6,71,7,84 | October | 2018 | 2019Q2 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2018-10-26 | N | 74.4 | N | 2 | N | N | 1.1101 | 39.4971 | 47845.0065
[7 empty] | 6806 | 16412 | 1606049 | 2018-10-27 04:12 | 2018-10-27 08:28 | 256 | 11kV | 17664 | 69 | HV | Vandalism | 3rd Party Impact | Air Break Switch | Unplanned | No Weather Impact | N | At Zn35370 Galston Panel 8 CP275 found open with a padlock missing Abnorrmal switching: CP2063 Closed LB3342 Open Cause; AB275 Found open with padlock missing See oms 1606457 1606049 | October | 2018 | 2019Q2 | 2019 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2018-10-27 | N | 256 | N | 3 | N | N | 1.1101 | 39.4971 | 12908.3302
[7 empty] | 6779 | 15993 | 1606112 | 2018-10-27 16:53 | 2018-10-27 17:53 | 60 | 11kV | 6320 | 115 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3288 City South - 45/46B tripped on: 46B Earth Fault UG cable fault on 46B leg See 1606258 1606112 1606259 | October | 2018 | 2019Q2 | 2019 | ZN3288:PA45 46ABC | ZN3288:PA45 46ABC | ZN03288/45 46ABC | SYDNEY | UG | Not Veg | 2018-10-27 | N | 54.9565 | N | 3 | N | N | 1.1101 | 39.4971 | 4618.4696
[7 empty] | 6302 | 10930 | 1606132 | 2018-10-27 23:45 | 2018-10-28 01:08 | 83 | 11kV | 10209 | 123 | HV | Animal Flying Fox | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | At Recloser CP21350 Booralie Kaggoa Tripped on Overcurrent Cause: Bat found on ground near PT16215 | October | 2018 | 2019Q2 | 2019 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Not Veg | 2018-10-27 | N | 83 | N | 3 | N | N | 1.1101 | 39.4971 | 7460.4361
[7 empty] | 6629 | 14619 | 1606138 | 2018-10-28 04:42 | 2018-10-28 06:28 | 106 | 11kV | 7314 | 69 | HV | Vandalism | 3rd Party Impact | Air Break Switch | Unplanned | No Weather Impact | N | AB275 Found Open with padlock missing - AB275 found open with padlock missing - second night in a row. abnormal switching: AB2063 Closed, LB3342 Open. See OMS 160459 1606138 | October | 2018 | 2019Q2 | 2019 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2018-10-28 | N | 106 | N | 3 | N | N | 1.1101 | 39.4971 | 5344.8555
[7 empty] | 6520 | 13601 | 1606165 | 2018-10-28 10:44 | 2018-10-28 12:56 | 132 | 11kV | 135172 | 1039 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S3154 Panel 17 tripped, reclosed tripped and locked out on Relays: C phase Overcurrent Reclose timer and lockout Abnormal Switching: LB64168 Closed, AB2081 Open Cause: DOp found tree branch on 11kV mainss outside 40 Waterhouse rd. Feeder failed on restoration. See OMS 1606635 1606636 1606167 1606165 | October | 2018 | 2019Q2 | 2019 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Veg | 2018-10-28 | N | 130.0982 | N | 3 | N | N | 1.1101 | 39.4971 | 98779.7107
[7 empty] | 7001 | 18559 | 1606213 | 2018-10-29 00:30 | 2018-10-29 07:32 | 422 | 11kV | 14184 | 69 | HV | Vandalism | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | AB275 found open with padlock cut. Feeder patrol by DOps fouund PT2243 Bloodwood linch Nursery cut down by chainsaw.Dop and linworker broke bonds to PT2243 Abnormal Switching: AB2063 Closed, CP3342 Open. Cause: Phantom Operator - attempted copper theft See OMS 1606550 1606551 1606213 1606214 | October | 2018 | 2019Q2 | 2019 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2018-10-29 | N | 205.5652 | N | 3 | N | N | 1.1101 | 39.4971 | 10365.2488
[7 empty] | 5869 | 6082 | 1606210 | 2018-10-28 22:48 | 2018-10-29 10:11 | 683 | 11kV | 11617 | 41 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188644 A & C phase Overcurrent OHM wrapped together pole 9N-20173 Excluded OMS 1606210. | October | 2018 | 2019Q2 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2018-10-28 | N | 283.3415 | N | 3 | N | N | 1.1101 | 39.4971 | 8489.361
[7 empty] | 5418 | 1071 | 1606468 | 2018-10-29 17:46 | 2018-10-29 20:35 | 169.1333 | 11kV | 10462.75 | 62 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT1207 David Baydon 31.5Aroadside HDO blown and broken Cause: Fuse fatigue. Supply restore via LV parallel | October | 2018 | 2019Q2 | 2019 | ZN965:PA13 | ZN965:PA13 | ZN00965/000013 | HORNSBY | OH | Not Veg | 2018-10-29 | N | 168.754 | N | 3 | N | N | 1.1101 | 39.4971 | 7645.8691
[7 empty] | 6396 | 11955 | 1606509 | 2018-10-29 20:40 | 2018-10-29 23:20 | 160 | 11kV | 79768 | 1285 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn9118 Cronulla - Pnl.8 tripped on: Earth Fault Cause not ascertained. PT9578 Boomerang Av - A phase HDO found blown, no damage present. Replaced OK See 1606509 | October | 2018 | 2019Q2 | 2019 | ZN9118:PA8 | ZN9118:PA8 | ZN09118/000008 | SUTHERLAND | OH | Veg | 2018-10-29 | N | 62.0763 | N | 3 | N | N | 1.1101 | 39.4971 | 58292.1016
[7 empty] | 6194 | 9960 | 1606523 | 2018-10-30 02:47 | 2018-10-30 05:07 | 140 | 11kV | 163630 | 1512 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn9245 Engadine - pnl.15 tripped on : A & B phase IOC Abnormal: LB35873 Closed with LB35951 open (defective UGOH to S9642 Sw/A) Cause not ascertained See 1607242 1607243 | October | 2018 | 2019Q2 | 2019 | ZN9245:PA15 | ZN9245:PA15 | ZN09245/000015 | SUTHERLAND | OH | Veg | 2018-10-30 | N | 108.2209 | N | 5 | N | N | 1.1101 | 39.4971 | 119575.9777
[7 empty] | 5452 | 1434 | 1606568 | 2018-10-30 07:57 | 2018-10-30 10:15 | 138 | 11kV | 1656 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 188654 A & B phase DOLF : 10 Amp Outage time based on protection event at Hebden Sectionaliser at 0757. Excluded OMS 1606568 & 1606571. | October | 2018 | 2019Q2 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2018-10-30 | N | 138 | N | 5 | N | N | 1.1101 | 39.4971 | 1210.156
[7 empty] | 5601 | 3566 | 1606578 | 2018-10-30 09:31 | 2018-10-30 11:35 | 124 | 11kV | 6820 | 55 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188656 C Phase DOLF : 31 Amp Excluded OMS 1606578 & 1606589. | October | 2018 | 2019Q2 | 2019 | 513:48056 | 513:83493 | ZN00513/083493 | SINGLETON | OH | Veg | 2018-10-30 | N | 124 | N | 5 | N | N | 1.1101 | 39.4971 | 4983.8548
[7 empty] | 5437 | 1273 | 1606598 | 2018-10-30 10:33 | 2018-10-30 14:52 | 259 | 11kV | 19653 | 166 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188661 2 fault operations A & B Phase Overcurrent Magpie burnt mains down line side of 11kV Link 41287. Excluded OMS 1606598 | October | 2018 | 2019Q2 | 2019 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2018-10-30 | N | 118.3916 | N | 5 | N | N | 1.1101 | 39.4971 | 14361.8327
[7 empty] | 6609 | 14433 | 1606704 | 2018-10-30 16:13 | 2018-10-30 17:45 | 92 | 11kV | 66020 | 880 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay - Pnl.1 tripped on: Earth Fault Field EFIs: All down to S9176 UG cable fault between S9176 (Sw/B) and S9114 (Sw/A) teee PT9363 Bimbadeen Ave See 1607244 1607245 1607246 | October | 2018 | 2019Q2 | 2019 | ZN9550:PA1 | ZN9550:PA1 | ZN09550/000001 | SUTHERLAND | UG | Not Veg | 2018-10-30 | N | 75.0227 | N | 5 | N | N | 1.1101 | 39.4971 | 48245.4687
[7 empty] | 6859 | 17015 | 1606898 | 2018-10-31 15:12 | 2018-10-31 17:00 | 108 | 11kV | 107418 | 1306 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn80 Chatswood Panel 37R tripped on Relays: 37R Leg E/F, Fault Check A phase fault and EFI Signals: 11kV trip, Group Earth , TX13 and Zone Earth Cause: 11kV Cable fault from S5011 to S4696 to S2600 - See OMS 1607042 1607044 1607046 1607106 1607107 1607041 1606925 1606901 1606898 | October | 2018 | 2019Q2 | 2019 | ZN80:PA37 | ZN80:PA37 | ZN00080/000037 | LANE COVE | UG | Not Veg | 2018-10-31 | N | 82.2496 | N | 4 | N | N | 1.1101 | 39.4971 | 78497.9061
[7 empty] | 6371 | 11706 | 1606932 | 2018-10-31 16:52 | 2018-10-31 17:44 | 52 | 11kV | 49608 | 954 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills panel 35 tripped on Relays: B and Cphase O/C Signals: 11kV trip Field EFI's NIL. Cause: Tree branch on OH mains in Gully | October | 2018 | 2019Q2 | 2019 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | HORNSBY | OH | Veg | 2018-10-31 | N | 52 | N | 4 | N | N | 1.1101 | 39.4971 | 36252.0632
[7 empty] | 7007 | 18581 | 1606957 | 2018-10-31 19:02 | 2018-10-31 21:45 | 163.4833 | 11kV | 17819.6833 | 109 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex Zn12620 Noraville section of Panel 13 "Wallarah Point" PT13145 Main Cross 0.5 centre phase surge arrestor and 31.5amp HDO operated Cause: lightning/surge arrestor See 1606957 ex 1606959 | October | 2018 | 2019Q2 | 2019 | ZN12620:PA13 | ZN12620:PA13 | ZN12620/000013 | CENTRAL COAST | OH | Not Veg | 2018-10-31 | N | 163.4833 | N | 4 | N | N | 1.1101 | 39.4971 | 13022.099
[7 empty] | 5616 | 3681 | 1606966 | 2018-10-31 20:05 | 2018-10-31 23:10 | 185 | 11kV | 1110 | 6 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 188673 Emerg pole replacement IR-13610 | October | 2018 | 2019Q2 | 2019 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2018-10-31 | N | 185 | N | 4 | N | N | 1.1101 | 39.4971 | 811.1553
[7 empty] | 7002 | 18565 | 1606993 | 2018-11-01 01:09 | 2018-11-01 02:10 | 61 | 11kV | 128335 | 2115 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Primary Equip | Unplanned | No Weather Impact | N | Zn12580 Erina 11kV BS "1-2" CB tripped Signals: 11kv trip, 11kV BB BUOC trip Relays: Group 2 Panel - Multi trip, 11kV fdr BUOC A and C Phases No.2 Tx Panel - No.1 Multi trip, tripping relay, overlay prohibition Abnormal: Zn12580 Erina Tx2 OOS from IS3213 to 11kV Tx2 CB tee S14064 & FIU #2 Protection Malfunction. Appears transient fault on 824 fdr from Gosford to Erina, Avoca and Wamberal has caused current to flow thorugh the Tx2 sprouts earths via BBP CT's causing a loss of the No.2 Group Busbar @ Erina Zone. See outage on 828 fdr at Gosoford STS in conjunction See 1607087,8,9 ex 1606993,7000,8 | November | 2018 | 2019Q2 | 2019 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | Exclude | Not Veg | 2018-11-01 | N | 60.6785 | N | 3 | N | N | 1.1101 | 39.4971 | 93783.4328
[7 empty] | 6215 | 10135 | 1607011 | 2018-11-01 03:30 | 2018-11-01 04:11 | 41 | 11kV | 3813 | 93 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9037 Miranda - Pnl.7 tripped on: C phase IOC Abnormal : S9938 (Sw/B) open to S9235 (Sw/A) tee PT9639 OOS Defective Burnt Possum haning from UGOH near AB39346. Lineworkers to remove AM Friday | November | 2018 | 2019Q2 | 2019 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Not Veg | 2018-11-01 | N | 41 | N | 3 | N | N | 1.1101 | 39.4971 | 2786.4279
[7 empty] | 6047 | 8111 | 1607017 | 2018-11-01 07:31 | 2018-11-01 10:20 | 169 | 11kV | 80341 | 801 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1673 Mosman Panel 2 Feeder has tripped on Signals: 11kV trip CB2, open, tx2 group earth C phase IOC Cause: UG cable fault from CP373 Bogan to AB3019 tee PT1917 Comenara Stainsby See OMS 1607295 1607297 1607296 | November | 2018 | 2019Q2 | 2019 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | UG | Not Veg | 2018-11-01 | N | 100.3009 | N | 3 | N | N | 1.1101 | 39.4971 | 58710.8331
[7 empty] | 6720 | 15295 | 1607217 | 2018-11-02 02:51 | 2018-11-02 04:06 | 75 | 11kV | 114495 | 1565 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 Matraville - Pnl.17 tripped on Earth fault Suspected UG cable fault between S768 (Sw/b) and S6061 (Sw/A) See 1607271 1607272 | November | 2018 | 2019Q2 | 2019 | ZN1788:PA17 | ZN1788:PA17 | ZN01788/000017 | BAYSIDE | UG | Not Veg | 2018-11-02 | N | 73.1597 | N | 8 | N | N | 1.1101 | 39.4971 | 83669.569
[7 empty] | 6930 | 17871 | 1607306 | 2018-11-02 10:16 | 2018-11-02 12:45 | 149 | 11kV | 25479 | 171 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S4637 Reynolds Station TX HV switch tripped due to grading issues with LV fuses DOp required to change HV fuses Cause:P Tree branch on OH mains O/S 40 Reynolds St Cause: Based on customer calls suspect S4365#3 was in parallel woth S4637 See OMS1607965 1607967 1607971 1607325 1607308 1607307 | November | 2018 | 2019Q2 | 2019 | ZN3154:PA18 | ZN3154:PA18 | ZN03154/000018 | KU-RING-GAI | OH | Veg | 2018-11-02 | N | 149 | N | 8 | N | N | 1.1101 | 39.4971 | 18619.3017
[7 empty] | 5810 | 5620 | 1607375 | 2018-11-02 13:34 | 2018-11-02 15:48 | 134 | 11kV | 49547 | 372 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn35370 Galston Panel 2 tripped on Relays: Basler 51 A and Cphase OC. Signals: 11kV trip Cause: tree branch on OH mains - Various Branches cleared off OH See OMS 1607940 1607941 1607375 | November | 2018 | 2019Q2 | 2019 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2018-11-02 | N | 133.1909 | N | 8 | N | N | 1.1101 | 39.4971 | 36207.4862
[7 empty] | 6009 | 7735 | 1607448 | 2018-11-02 18:07 | 2018-11-02 19:37 | 90 | 11kV | 180 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188689 B & C phase DOLF : 10 Amp Excluded OMS 1607448 | November | 2018 | 2019Q2 | 2019 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2018-11-02 | N | 90 | N | 8 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 5974 | 7166 | 1607482 | 2018-11-02 19:40 | 2018-11-02 21:22 | 102 | 11kV | 217464 | 2132 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn10994 Mortdale - Pnl.21L tripped, reclosed & locked out on: A, B & C phase IOC Abnormal: LB30093 Closed with S10123 (Sw/A) open 11kV 3 to 1 cable connection at S10364 (Sw/A) failed explosively | November | 2018 | 2019Q2 | 2019 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | UG | Not Veg | 2018-11-02 | N | 102 | N | 8 | N | N | 1.1101 | 39.4971 | 158916.2771
[7 empty] | 6763 | 15746 | 1607377 | 2018-11-02 13:50 | 2018-11-02 23:59 | 609 | 11kV | 28392 | 82 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Hot >35C | N | At S6616 James Ridge 75A HV fuse blew twice under load. Cause: HV B phase fuse failed twice under load. (Transformer failure)OO distributor 1 is aq 1200A direct distributor - MG is being aranged See OMS 1607992 1607995 1607377 | November | 2018 | 2019Q2 | 2019 | ZN187:PA4 | ZN187:PA4 | ZN00187/000004 | NORTH SYDNEY | UG | Not Veg | 2018-11-02 | N | 346.2439 | N | 8 | N | N | 1.1101 | 39.4971 | 20748.0362
[7 empty] | 5402 | 861 | 1607549 | 2018-11-02 22:19 | 2018-11-03 00:07 | 108 | 11kV | 93636 | 867 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn965 Pennant Hills panel 20 tripped on Relays: Earth fault, EFI Signals: 11kV trip, No3 group earth Cause: UG cable fault in front line section | November | 2018 | 2019Q2 | 2019 | ZN965:PA20 | ZN965:PA20 | ZN00965/000020 | HORNSBY | UG | Not Veg | 2018-11-02 | N | 108 | N | 8 | N | N | 1.1101 | 39.4971 | 68426.427
[7 empty] | 6752 | 15600 | 1607533 | 2018-11-02 22:10 | 2018-11-03 00:30 | 140 | 11kV | 181703 | 1492 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn12650 West Gosford section of Panel 1 "Dog Trap Rd" RE44936 Bentley Rd tripped DOp unable to control or operate locally Abnormal: No COMMS available from Reclose due to telstra outage or information from REC DMA @ RE44937 Allan St Bypass closed Cause: storm. no cause found. Next available linesman See 1608045,6,7,8 ex 1607533,45,54 | November | 2018 | 2019Q2 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2018-11-02 | N | 121.7849 | N | 8 | N | N | 1.1101 | 39.4971 | 132783.1931
[7 empty] | 5940 | 6840 | 1607583 | 2018-11-03 04:41 | 2018-11-03 06:17 | 96 | 11kV | 200984 | 2124 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | ZS STS Primary Equip | Unplanned | No Weather Impact | N | Zn12580 Erina 1-2 Bus Section CB Pa6 tripped Protection Relays: Multi trip, overload prohibition, BU O/C and multi trip A & C phases Sngals: 11kv trip Abnormal: Erina Tx2 OOS per NAR 3039666 & 11kv Tx2 CB's open. 1-2 BS CB closed Due to earthing of Tx2 @ n12580 Erina. Busbar protection CT's are not open or shorted as there is no current. DOp or CRA which requires the busbar CT's left open and shorted when earthing of Tx's or feeders. DOp reset all protection and closed the 11kV 1-2 CB to restore the section 2 bus bar See 1608055,6,7 ex 1607583 | November | 2018 | 2019Q2 | 2019 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | Exclude | Not Veg | 2018-11-03 | N | 94.6252 | N | 3 | N | N | 1.1101 | 39.4971 | 146873.1792
[7 empty] | 6179 | 9802 | 1607712 | 2018-11-03 18:51 | 2018-11-03 20:38 | 107 | 11kV | 66175 | 770 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay - Pnl.36 tripped on : B phase IOC UGOH failed in section from Pnl.36 to LB47770 tee PT9463 See 1608371 1608372 | November | 2018 | 2019Q2 | 2019 | ZN9550:PA36 | ZN9550:PA36 | ZN09550/000036 | SUTHERLAND | Unknown | Unknown | 2018-11-03 | N | 85.9416 | N | 3 | N | N | 1.1101 | 39.4971 | 48358.7382
[7 empty] | 6213 | 10101 | 1607719 | 2018-11-03 19:28 | 2018-11-03 20:58 | 90 | 11kV | 3852 | 56 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Circuit Breaker | Unplanned | No Weather Impact | N | LID 188697 3 fault operations Protection relay not flagging Excluded OMS 1607720 | November | 2018 | 2019Q2 | 2019 | 224:80328 | 214:8672 | ZN00214/008672 | LAKE MACQUARIE | Unknown | Unknown | 2018-11-03 | N | 68.7857 | N | 3 | N | N | 1.1101 | 39.4971 | 2814.928
[7 empty] | 6248 | 10410 | 1607747 | 2018-11-04 06:28 | 2018-11-04 09:45 | 197 | 11kV | 20850 | 734 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 188702 1 fault operation A & B phase Overcurrent Broken pin at pole SI-60503 Excluded OMS 1607747 | November | 2018 | 2019Q2 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2018-11-04 | N | 28.406 | N | 5 | N | N | 1.1101 | 39.4971 | 15236.565
[7 empty] | 7128 | 19771 | 1607767 | 2018-11-04 09:20 | 2018-11-04 10:24 | 64 | 11kV | 63100 | 1149 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S187 Crows Nest Panel 21 tripped on Earth Fault,EFI, Fault Check Cause: 11kV feeder fault in section of feeder from S4886 SW/B to S2739 to S4848. See OMS 1608195 1608196 1607767 | November | 2018 | 2019Q2 | 2019 | ZN187:PA21 | ZN187:PA21 | ZN00187/000021 | NORTH SYDNEY | UG | Not Veg | 2018-11-04 | N | 54.9173 | N | 5 | N | N | 1.1101 | 39.4971 | 46111.6189
[7 empty] | 5849 | 5872 | 1607741 | 2018-11-04 02:59 | 2018-11-04 10:40 | 461 | 11kV | 142699 | 729 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188701 2 fault operations Overcurrent OHM Down pole NR-67003 Excluded OMS 1607741 | November | 2018 | 2019Q2 | 2019 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2018-11-04 | N | 195.7462 | N | 5 | N | N | 1.1101 | 39.4971 | 104280.2203
[7 empty] | 6667 | 14958 | 1607840 | 2018-11-04 21:39 | 2018-11-04 22:24 | 45 | 11kV | 94823 | 2394 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.32 tripped on: Earth Fault UG cable fault between S1690 (Sw/B) and S49727 (Sw/A) and S4883 (Sw/A) See 1608347 1608348 | November | 2018 | 2019Q2 | 2019 | ZN2568:PA32 | ZN2568:PA32 | ZN02568/000032 | SYDNEY | UG | Not Veg | 2018-11-04 | N | 39.6086 | N | 5 | N | N | 1.1101 | 39.4971 | 69293.8516
[7 empty] | 5363 | 309 | 1607828 | 2018-11-04 19:16 | 2018-11-05 08:10 | 774 | 11kV | 1548 | 2 | HV | Animal Bird | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 188707 B Phase DOLF : 10 Amp Bird Excluded OMS 1607828 | November | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-11-04 | N | 774 | N | 5 | N | N | 1.1101 | 39.4971 | 1131.2327
[7 empty] | 6482 | 13102 | 1608065 | 2018-11-05 18:46 | 2018-11-05 19:29 | 43 | 11kV | 56244 | 1308 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn187 Crows Nest panel 17 tripped on Relays: Earthy Fault, EFI Signals:11kV trip, TX11 Group Earth Cause: 11kV Ug fault (Front Line) | November | 2018 | 2019Q2 | 2019 | ZN187:PA17 | ZN187:PA17 | ZN00187/000017 | NORTH SYDNEY | UG | Not Veg | 2018-11-05 | N | 43 | N | 1 | N | N | 1.1101 | 39.4971 | 41101.4563
[7 empty] | 6240 | 10352 | 1608093 | 2018-11-06 02:18 | 2018-11-06 03:45 | 87 | 11kV | 13357 | 183 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Zn3472 Sefton Zn Panel 15 "Carlingford" tripped on A phase IOC, Fault Check , EFI, Lockout, Reclose Time Delay EFI's S5741 Cause: Lightning Surge Arrestor Lightning Arestor UGOH @ Clapham Rd East in section of 11kv fdr from S5741swB to S8241swA to AB888 tee S6040 See 1608620,1,2,3 ex 1608093 | November | 2018 | 2019Q2 | 2019 | ZN3472:PA15 | ZN3472:PA15 | ZN03472/000015 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-11-06 | N | 72.9891 | N | 5 | N | N | 1.1101 | 39.4971 | 9760.9016
[7 empty] | 5925 | 6677 | 1608142 | 2018-11-06 09:57 | 2018-11-06 13:30 | 213 | 11kV | 213 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 188723 Repair Live Line Clamp | November | 2018 | 2019Q2 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2018-11-06 | N | 213 | N | 5 | N | N | 1.1101 | 39.4971 | 155.6541
[7 empty] | 6075 | 8343 | 1608216 | 2018-11-06 15:38 | 2018-11-06 22:15 | 397 | 11kV | 337758 | 2952 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3555 Croydon Pa13 tripped on IOC, Earth Fault EFI's S1512 S36204 S6805 S4040 S1517 11kV UG fault between S4040 to S1913 to S1517 to S2654 S2522 Denman Dalhousie Dist 1 ABC phase fuse blown due to DC in LV// during feeder trip S1907 in LV// during feeder trip (from prior defective 11kV UG fault) See 1608378,9,80,2,3 ex 1608216,37,66 | November | 2018 | 2019Q2 | 2019 | ZN35555:PA13 | ZN35555:PA13 | ZN35555/000013 | INNER WEST | UG | Not Veg | 2018-11-06 | N | 114.4167 | N | 5 | N | N | 1.1101 | 39.4971 | 246823.5842
[7 empty] | 6493 | 13219 | 1608257 | 2018-11-06 19:37 | 2018-11-06 23:01 | 204 | 11kV | 198704 | 3164 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 8 tripped on \Relays: Earth Fault and EFI Signals: 11kV trip, Zone Earth and No1 Group Earth. Field EFI's Cause: 11kV UG intermittent fauult between S6115 and S5598. Note: Defective EFI's @ S5583 and S5345 Abornal Switching: Panel 20 Front Line Defective - S5582 SW/B Closed See OMS 1608416/415/414/416/417/421 1608422 See excluded 1608258 1608257 | November | 2018 | 2019Q2 | 2019 | ZN965:PA8 | ZN965:PA8 | ZN00965/000008 | HORNSBY | UG | Not Veg | 2018-11-06 | N | 62.8015 | N | 5 | N | N | 1.1101 | 39.4971 | 145207.0224
[7 empty] | 5878 | 6173 | 1608332 | 2018-11-07 09:26 | 2018-11-07 10:35 | 69 | 11kV | 71691 | 1039 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Rain Heavy | N | Zn9245 Engadine Zn Panel 4 "S77269 Wilson Princes #2" tripped on Earth Fault, EFI UG cable damaged by contractor between Zn9245 Panel 4 to S77269 sw/A. See OMS 1608350 See 1608332 ex 1608350 | November | 2018 | 2019Q2 | 2019 | ZN9245:PA4 | ZN9245:PA4 | ZN09245/000004 | SUTHERLAND | UG | Not Veg | 2018-11-07 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 52389.6683
[7 empty] | 6305 | 10947 | 1608281 | 2018-11-06 23:56 | 2018-11-07 12:08 | 732 | 11kV | 71736 | 98 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | Ex Zn2400 Berowra section of Pa18 RE3227 Berowra Creek tripped and locked out on: Relays: E/F trip, IOC trip Possum found on AB2013 | November | 2018 | 2019Q2 | 2019 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2018-11-06 | N | 732 | N | 5 | N | N | 1.1101 | 39.4971 | 52422.5529
[7 empty] | 5972 | 7142 | 1608477 | 2018-11-07 16:09 | 2018-11-07 17:10 | 61 | 11kV | 61 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Operators only attended - notiification # 1700144336 per A.Chapman.NFA. Ex Zn12620 Noraville section of Panel 11 "Norah Head" fdr RE45050 Magenta tripped on Earth Fault Abnoraml: S14654 SwA Closed, S18595 SwB Open During restoration of PT18408 on completion of NAR 30701 11kv Surge Arrestors failed on energising. DOp linesman cut away and restored PT | November | 2018 | 2019Q2 | 2019 | ZN12620:PA11 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2018-11-07 | N | 61 | N | 3 | N | N | 1.1101 | 39.4971 | 44.577
[7 empty] | 5406 | 902 | 1608510 | 2018-11-07 20:48 | 2018-11-07 22:40 | 112 | 11kV | 336 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn9700 Kirrawee Zn Ex Panel 20 RE35006 National Park tripped/reclosed/tripped & locked out Relays: OC trip, Lockout Tree/Branch on OH mains. DOp removed tree branch off 11kv mains 2 bays sth of RE35006 | November | 2018 | 2019Q2 | 2019 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Veg | 2018-11-07 | N | 112 | N | 3 | N | N | 1.1101 | 39.4971 | 245.5389
[7 empty] | 6734 | 15392 | 1608527 | 2018-11-08 04:27 | 2018-11-08 07:15 | 168 | 11kV | 31584 | 188 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 188738 A Phase DOLF : 40 Amp Sub 10964 A phase 40A DOLF no cause found Supply off 0427hrs back on 0715hrs Excluded OMS 1608527 | November | 2018 | 2019Q2 | 2019 | 206:34441 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Veg | 2018-11-08 | N | 168 | N | 5 | N | N | 1.1101 | 39.4971 | 23080.6556
[7 empty] | 6173 | 9752 | 1608529 | 2018-11-08 06:07 | 2018-11-08 09:00 | 173 | 11kV | 519 | 3 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188739 Single phase DOLF : 10 Amp tree branch on tx bushings. Excluded OMS 1608529 | November | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2018-11-08 | N | 173 | N | 5 | N | N | 1.1101 | 39.4971 | 379.2699
[7 empty] | 5360 | 254 | 1608569 | 2018-11-08 08:46 | 2018-11-08 10:05 | 79 | 11kV | 237 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188742 B Phase DOLF : 10 Amp birds nest on LA. Excluded OMS 1608569. | November | 2018 | 2019Q2 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2018-11-08 | N | 79 | N | 5 | N | N | 1.1101 | 39.4971 | 173.1926
[7 empty] | 5674 | 4354 | 1608633 | 2018-11-08 11:49 | 2018-11-08 13:50 | 121 | 11kV | 121 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188744 A & B Phase DOLF : 10 Amp Sub reported wrongly as Percefield 71841 Excluded OMS 1608633. | November | 2018 | 2019Q2 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2018-11-08 | N | 121 | N | 5 | N | N | 1.1101 | 39.4971 | 88.4232
[7 empty] | 6324 | 11175 | 1608722 | 2018-11-08 17:35 | 2018-11-08 21:20 | 225 | 11kV | 6338 | 50 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 188479 2 fault operations B Phase Earth Fault Burnt off tapping at pole 9M 10115 and mains twisted between pole 9M-10117 & 9M-10120, section isolated for repairs Excluded OMS 1608722 | November | 2018 | 2019Q2 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2018-11-08 | N | 126.76 | N | 5 | N | N | 1.1101 | 39.4971 | 4631.6235
[7 empty] | 5931 | 6762 | 1608759 | 2018-11-09 02:11 | 2018-11-09 02:58 | 47 | 11kV | 54567 | 1161 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.9 tripped on: Earth fault UG cable fault in front line section from Pnl.9 to S1484 (Sw/A) | November | 2018 | 2019Q2 | 2019 | ZN2568:PA9 | ZN2568:PA9 | ZN02568/000009 | INNER WEST | UG | Not Veg | 2018-11-09 | N | 47 | N | 4 | N | N | 1.1101 | 39.4971 | 39875.9541
[7 empty] | 6649 | 14811 | 1608781 | 2018-11-09 08:26 | 2018-11-09 09:46 | 80 | 11kV | 50510 | 703 | HV | Staff Other | Utility Process Issue | U/G Cable | Unplanned | No Weather Impact | N | Zn630 Mascot - Pnl.26 tripped on Earth fault Abnormal: S35004 (Sw/A) closed with (Sw/B) open for D/R436352 Staff error: Jointer has cut cable between S2848 and S48676 and S35004 See 1609924 1609926 | November | 2018 | 2019Q2 | 2019 | ZN630:PA26 | ZN8100:PA31 | ZN08100/000031 | BAYSIDE | UG | Not Veg | 2018-11-09 | N | 71.8492 | N | 4 | N | N | 1.1101 | 39.4971 | 36911.2182
[7 empty] | 6116 | 9059 | 1608814 | 2018-11-09 10:36 | 2018-11-09 16:05 | 329 | 11kV | 42770 | 130 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn9700 Kirrawee Panel 23 HV bond found burnt off Pole SU13456 on tee near AB35547 Abnormal: AB35007 open Cause: bond. HV bond burnt off at pole SU13456 on tee near AAB35547 See 1609846 ex 1608814,1609021 | November | 2018 | 2019Q2 | 2019 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | OH | Not Veg | 2018-11-09 | N | 329 | N | 4 | N | N | 1.1101 | 39.4971 | 31255.0545
[7 empty] | 5835 | 5775 | 1608914 | 2018-11-09 20:56 | 2018-11-09 21:38 | 42 | 11kV | 53928 | 1284 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay Panel 4 fdr tripped on Relays: EF, EFI Signals: 11kv trip EFI's: S9831 S9456 Abnormal: Panel 36 OOS to LB47770 with LB47897 closed. S9365 Box Belgrave Dist 1 "Belgrave Esp" in LV// with Panel 36 See 1609855,6 ex 1608914,5,24,6,7 | November | 2018 | 2019Q2 | 2019 | ZN9550:PA36 | ZN9550:PA36 | ZN09550/000036 | SUTHERLAND | Unknown | Unknown | 2018-11-09 | N | 42 | N | 4 | N | N | 1.1101 | 39.4971 | 39408.9918
[7 empty] | 6896 | 17552 | 1608934 | 2018-11-10 00:17 | 2018-11-10 01:28 | 71 | 11kV | 61699 | 869 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant hills Panel 20 tripped on B phase timed OC Earth Fault EFI UG cable fault Section of 11kV feeder from S965 Pennant Hills Pa20 to S48292 to S5370 See OMS 1609537 1608937 | November | 2018 | 2019Q2 | 2019 | ZN965:PA20 | ZN965:PA20 | ZN00965/000020 | HORNSBY | UG | Not Veg | 2018-11-10 | N | 71 | N | 3 | N | N | 1.1101 | 39.4971 | 45087.8094
[7 empty] | 6309 | 11003 | 1608959 | 2018-11-10 09:20 | 2018-11-10 10:10 | 50 | 11kV | 100 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188760 C Phase DOLF : 16 Amp Dead Magpie at sub. Tx Volts: 236V Excluded OMS No. 1608959 | November | 2018 | 2019Q2 | 2019 |  |  |  |  | OH | Not Veg | 2018-11-10 | N | 50 | N | 3 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 6211 | 10091 | 1608963 | 2018-11-10 09:52 | 2018-11-10 11:39 | 107 | 11kV | 5228 | 115 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn630 mascot - Pnl.32 tripped on Earth Fault Field EFIs: S35870 S64823 (S64825 did not operate) UG cable fault due to Westconnex excavation works between S64825 (sw/B) and S62083 (Sw/A) Pnl.33 tripped on restoration due to EFI not flagging at S64825 See 16909932 1609933 1609934 1609935 | November | 2018 | 2019Q2 | 2019 | ZN630:PA32 | ZN630:PA32 | ZN00630/000032 | SYDNEY | UG | Not Veg | 2018-11-10 | N | 45.4609 | N | 3 | N | N | 1.1101 | 39.4971 | 3820.4682
[7 empty] | 6816 | 16550 | 1609188 | 2018-11-11 23:00 | 2018-11-12 00:10 | 70 | 11kV | 149590 | 2137 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S2635 Epping Panel 58 tripped on Signals 11kV trip Relays: 50TC OC c phase, 150TN OC EF, 51 AB phase fault a and B Cause: Bat Outside 16 Keats St 4 Bays of 11kV twisted together. | November | 2018 | 2019Q2 | 2019 | ZN2635:PA58 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | OH | Not Veg | 2018-11-11 | N | 70 | N | 1 | N | N | 1.1101 | 39.4971 | 109315.9598
[7 empty] | 6199 | 10016 | 1609330 | 2018-11-12 13:46 | 2018-11-12 15:00 | 74 | 11kV | 94202 | 1273 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12650 West Gosford Panel 6 "S11794 SCC Racecourse" tripped, reclosed and locked out: Relays: Earth Fault, EFI, Fault check, timing and lock out Tx11 Fault CHeck Signals: Tx11 Group Earth, 11KV Trip EFI's: S11794 Crane Hit 11kV outside 17 Beane St West Gosford See 1609330 ex 1609341 | November | 2018 | 2019Q2 | 2019 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Not Veg | 2018-11-12 | N | 74 | N | 2 | N | N | 1.1101 | 39.4971 | 68840.0431
[7 empty] | 5846 | 5852 | 1609434 | 2018-11-12 22:10 | 2018-11-12 23:55 | 105 | 11kV | 5670 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 188778 1 fault operation Sensitive Earth Fault No fault found. | November | 2018 | 2019Q2 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2018-11-12 | N | 105 | N | 2 | N | N | 1.1101 | 39.4971 | 4143.4688
[7 empty] | 7018 | 18685 | 1609510 | 2018-11-13 10:47 | 2018-11-13 12:11 | 84 | 11kV | 14727 | 180 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Lightning | N | LID 188782 Isolated for safety to repair pin off cross arm, at 4J-20023 | November | 2018 | 2019Q2 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2018-11-13 | N | 81.8167 | N | 1 | N | N | 1.1101 | 39.4971 | 10762.0572
[7 empty] | 6956 | 18082 | 1609632 | 2018-11-14 04:52 | 2018-11-14 05:54 | 62 | 11kV | 57472 | 950 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn12660 Woy Woy Panel 16 "St Huberts" fdr tripped and locked out on: Relays: E/F and EFI Signals: 11kv trip EFI: S18242 Cause: Possum removed by DOp off UGOH located between S18242 & S18156 See 1609655,7 ex 1609632 | November | 2018 | 2019Q2 | 2019 | ZN12660:PA16 | ZN12660:PA16 | ZN12660/000016 | CENTRAL COAST | OH | Not Veg | 2018-11-14 | N | 60.4968 | N | 5 | N | N | 1.1101 | 39.4971 | 41998.8425
[7 empty] | 5415 | 1018 | 1609631 | 2018-11-14 04:48 | 2018-11-14 06:03 | 75 | 11kV | 86775 | 1157 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188798 1 Fault Operations Possum at pole JU-63225 | November | 2018 | 2019Q2 | 2019 | 202:34250 | 202:34250 | ZN00202/034250 | NEWCASTLE | OH | Not Veg | 2018-11-14 | N | 75 | N | 5 | N | N | 1.1101 | 39.4971 | 63412.6106
[7 empty] | 6932 | 17877 | 1609636 | 2018-11-14 06:13 | 2018-11-14 10:40 | 267 | 11kV | 20422 | 145 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188800 3 Fault operations, A and B Phases, Overcurrent, Earth Fault Magpie into OHM @ Pole AJ-60164 | November | 2018 | 2019Q2 | 2019 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2018-11-14 | N | 140.8414 | N | 5 | N | N | 1.1101 | 39.4971 | 14923.7953
[7 empty] | 6905 | 17643 | 1609695 | 2018-11-14 10:46 | 2018-11-14 11:19 | 33 | 11kV | 42537 | 1289 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | Ex Zn15008 Harbord Panel 5 "Queenscliffe" tripped O/C & Earth Fault, IOC, reclose time delay, Lockout, EFI EFI's down to S65764 Truck hit pole pole causing HV to clash corner lodge & seddon near 17 lodge See 1609695 ex 1609696,9 | November | 2018 | 2019Q2 | 2019 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | OH | Not Veg | 2018-11-14 | N | 33 | N | 5 | N | N | 1.1101 | 39.4971 | 31084.785
[7 empty] | 6686 | 15115 | 1609794 | 2018-11-14 20:51 | 2018-11-14 22:40 | 109 | 11kV | 298582 | 4108 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn10995 Riverwood Panel 1 "Meadowland Rd" fdr tripped, reclosed and locked out Relays: OC C phase, timed and sintantaneous, timer, Lock out, EFI Signals: 11kv trip, Group Earth, Zone Earth EFI's: S10758 Abnormal: S10720 SwA closed, AB31172 open and defective Cause: possum has damaged UGOH between AB30068 and SwA S10987 tee PT10828 See 1609873,4,5 ex 1609794,5,6,7,99,800 | November | 2018 | 2019Q2 | 2019 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | Unknown | Unknown | 2018-11-14 | N | 72.6831 | N | 5 | N | N | 1.1101 | 39.4971 | 218194.9189
[7 empty] | 6678 | 15064 | 1609891 | 2018-11-15 11:31 | 2018-11-15 11:47 | 16 | 11kV | 992 | 62 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 188813 Single phase Blown Dolfs at sub 54105. (previous storm) Seems to be no customer present at installation. Shed only. When DOLF replaced it tripped RAGCB. L/A replaced at sub 54105 under access. Sub restored at 1329 hrs Excluded OMS 1609891 | November | 2018 | 2019Q2 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2018-11-15 | N | 16 | N | 2 | N | N | 1.1101 | 39.4971 | 724.9243
[7 empty] | 6060 | 8233 | 1609970 | 2018-11-15 16:10 | 2018-11-15 22:07 | 357 | 11kV | 27807 | 190 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188823 1 fault operation Sensitive Earth Fault Earth wire touching Fdr at pole HV-37019 made safe by Dop repairs required. Sw 82131 SEF trip 1610hrs supply back on 2207hrs Excluded OMS 1609970 | November | 2018 | 2019Q2 | 2019 | 239:82131 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Not Veg | 2018-11-15 | N | 146.3526 | N | 2 | N | N | 1.1101 | 39.4971 | 20320.5354
[7 empty] | 7152 | 20022 | 1610066 | 2018-11-16 08:54 | 2018-11-16 11:05 | 131 | 11kV | 131 | 1 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188830 B Phase DOLF : 10 Amp Possum Excluded OMS 1610066 | November | 2018 | 2019Q2 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2018-11-16 | N | 131 | N | 5 | N | N | 1.1101 | 39.4971 | 95.7309
[7 empty] | 5856 | 5952 | 1610417 | 2018-11-16 12:45 | 2018-11-16 15:25 | 160 | 11kV | 1120 | 7 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 188840 3 phase emergency outage required to replace leaking Tx 1163 queen st sub. dq | November | 2018 | 2019Q2 | 2019 | 216:10722 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Not Veg | 2018-11-16 | N | 160 | N | 5 | N | N | 1.1101 | 39.4971 | 818.463
[7 empty] | 5759 | 5248 | 1610146 | 2018-11-16 15:40 | 2018-11-16 16:25 | 45 | 11kV | 45 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Fuse Assembly | Unplanned | No Weather Impact | N | LID 188841 A Phase Fuse fuse fell out. fixed Excluded OMS 1610146 | November | 2018 | 2019Q2 | 2019 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2018-11-16 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 6670 | 15013 | 1610135 | 2018-11-16 16:00 | 2018-11-16 17:10 | 70 | 11kV | 1050 | 15 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 188839 ohm on xarm at 3H-10013 Excluded OMS 1610135 | November | 2018 | 2019Q2 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2018-11-16 | N | 70 | N | 5 | N | N | 1.1101 | 39.4971 | 767.309
[7 empty] | 6653 | 14834 | 1610182 | 2018-11-16 19:46 | 2018-11-16 20:41 | 55 | 11kV | 12650 | 230 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn931 Darlinghurst - Pnl.26 tripped on: EFI flag only. Field EFIs: All on Pnl.26 UG cable fault from S7519 to S6144 to S8017 to S6675 | November | 2018 | 2019Q2 | 2019 | ZN931:PA26 | ZN931:PA26 | ZN00931/000026 | SYDNEY | UG | Not Veg | 2018-11-16 | N | 55 | N | 5 | N | N | 1.1101 | 39.4971 | 9244.2469
[7 empty] | 6452 | 12689 | 1610251 | 2018-11-17 12:54 | 2018-11-17 15:00 | 126 | 11kV | 126 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 188847 B & C Phase DOLF : 10 Amp Excluded OMS 1610251 | November | 2018 | 2019Q2 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2018-11-17 | N | 126 | N | 2 | N | N | 1.1101 | 39.4971 | 92.0771
[7 empty] | 6451 | 12679 | 1610311 | 2018-11-17 20:04 | 2018-11-18 02:00 | 356 | 11kV | 19221 | 386 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyon section of Pa12 Yarramalong' IR50630 Yarramalong Chandlers 0.1 tripped & reclosed 3 times and locked out on overcurrent Wyong relays EFI Signals: Tx2 Group Earth Cause: OH down. one phase of 11kv down beyond USL42775 See 1610958,60 ex 1610311,2,3 | November | 2018 | 2019Q2 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2018-11-17 | N | 49.7953 | N | 2 | N | N | 1.1101 | 39.4971 | 14046.1399
[7 empty] | 5603 | 3580 | 1610373 | 2018-11-18 17:57 | 2018-11-18 21:55 | 238 | 11kV | 952 | 4 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 188852 A Phase Live Line lead burnt off. Excluded oms 1610373. | November | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-11-18 | N | 238 | N | 2 | N | N | 1.1101 | 39.4971 | 695.6935
[7 empty] | 5808 | 5613 | 1610386 | 2018-11-18 21:06 | 2018-11-18 22:01 | 55 | 11kV | 29920 | 544 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn14891 Wyong Panel 20 'Warnervale West Railway' tripped, reclosed, tripped & locked out Relays: O/C & EF, EFI Signals: 11kv trip, Tx2 GE Note: SEF Operation @ LB40915 Cause: UGOH fault short circuit between Panel 20 to USL44801 | November | 2018 | 2019Q2 | 2019 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | Unknown | Unknown | 2018-11-18 | N | 55 | N | 2 | N | N | 1.1101 | 39.4971 | 21864.6535
[7 empty] | 5505 | 2019 | 1610412 | 2018-11-19 08:26 | 2018-11-19 13:25 | 299 | 11kV | 1196 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT 2066 Bay End tripped Cause fuse fatigue | November | 2018 | 2019Q2 | 2019 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2018-11-19 | N | 299 | N | 2 | N | N | 1.1101 | 39.4971 | 874.0015
[7 empty] | 6258 | 10481 | 1610503 | 2018-11-19 14:10 | 2018-11-19 14:33 | 23 | 11kV | 552 | 24 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188856 C Phase stranded mains on c phase adj pole FM-90030, section isolated for repairs | November | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-11-19 | N | 23 | N | 2 | N | N | 1.1101 | 39.4971 | 403.3853
[7 empty] | 5942 | 6863 | 1610579 | 2018-11-20 01:20 | 2018-11-20 03:21 | 121 | 11kV | 128890 | 1250 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12620 Noraville Panel 8 "Manoa Av" tripped Relays: B Phase IOC, Earth Fault, EFI, Lockout Signals: 11k vtrip, CB8 Open EFI's S18799 Cause: Underground fault from Panel 8 to S18799/SwA See 1610971,3 ex 1610579 | November | 2018 | 2019Q2 | 2019 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | UG | Not Veg | 2018-11-20 | N | 103.112 | N | 3 | N | N | 1.1101 | 39.4971 | 94189.0104
[7 empty] | 5817 | 5660 | 1610771 | 2018-11-20 16:41 | 2018-11-20 17:25 | 44 | 11kV | 7344 | 1047 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Secondary Equip | Unplanned | No Weather Impact | N | Zn3288 City South - 45/46 "A" feeder tripped on: A phase timed O/C Abnormal: 45/46B Out of service, 45/46C in process of being switched out for organised outage. S6075 in LV //. S3310 with 46B & C isolated. 45C feeder opened at CP1279 Park Pitt. Shortly after 45C feeder was opened at CP1279, 45/46A feeder tripped. 45A O/C relay pick up set at 270A instead of 320A per diagram and RTI. See 1610874 1610875 1610871 1610870 1610869 1610771 | November | 2018 | 2019Q2 | 2019 | ZN3288:PA45 46ABC | ZN3288:PA45 46ABC | ZN03288/45 46ABC | SYDNEY | Exclude | Not Veg | 2018-11-20 | N | 7.0143 | N | 3 | N | N | 1.1101 | 39.4971 | 5366.7786
[7 empty] | 6038 | 8038 | 1610826 | 2018-11-21 03:55 | 2018-11-21 04:57 | 62 | 11kV | 19344 | 312 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde Panel 34 tripped on Relays: 51N, Invers timed OC, EF, EFI, Fault Check, UF Cause: Possum caused flash over on UGOH beyond PT1061 Ryde Bus depot | November | 2018 | 2019Q2 | 2019 | ZN35500:PA34 | ZN35500:PA34 | ZN35500/000034 | RYDE | OH | Veg | 2018-11-21 | N | 62 | N | 3 | N | N | 1.1101 | 39.4971 | 14136.0246
[7 empty] | 6409 | 12162 | 1610818 | 2018-11-21 01:00 | 2018-11-21 09:28 | 508 | 11kV | 67592 | 422 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 188872 3 fault operation Single phase Earth Fault HV reported down Excluded OMS 1610818 | November | 2018 | 2019Q2 | 2019 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2018-11-21 | N | 160.1706 | N | 3 | N | N | 1.1101 | 39.4971 | 49394.24
[7 empty] | 6514 | 13500 | 1610816 | 2018-11-20 23:06 | 2018-11-21 14:20 | 914 | 11kV | 3055 | 70 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Lightning | N | Ex Zn12630 Peats Ridge section of Panel 3 "Mangrove Mountain" IR49206 Mangrove Mountain West tripped and reclosed Relays: OC trip PT11681 HDO opertaed PT11292 HDO operated Cause: lightning Lightning storm in area at time. HDO operated at PT11681 and PT11292. Tx @ PT11681 appears damaged. subs required to investigate See 1613218,9,20 ex 1610816 | November | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2018-11-20 | N | 43.6429 | N | 3 | N | N | 1.1101 | 39.4971 | 2232.5039
[7 empty] | 6563 | 13929 | 1611013 | 2018-11-21 17:51 | 2018-11-21 19:00 | 69 | 11kV | 69 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 188879 10 Amp fuse No Cause found, not storm conditions | November | 2018 | 2019Q2 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2018-11-21 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 50.4232
[7 empty] | 5873 | 6119 | 1611213 | 2018-11-22 13:22 | 2018-11-22 13:26 | 4 | 11kV | 4948 | 1237 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 188888 3 phase Interupted by AOP Quail to allow emergency removal of car cover pulling OHM phase to phase. DQ | November | 2018 | 2019Q2 | 2019 | 270:83587 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | OH | Veg | 2018-11-22 | N | 4 | N | 17 | N | N | 1.1101 | 39.4971 | 3615.8525
[7 empty] | 6449 | 12665 | 1611248 | 2018-11-22 14:06 | 2018-11-22 15:29 | 83 | 11kV | 35524 | 428 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Ex Zn12610 Long Jetty section of Panel 25 "Long Jetty Aux" Low Volts beyond LB45022 Cause: footpath phase bon burnt and lightning arrestor blown at UGOH between LB45022 & S18655 tee to PT11559 See 16131212 ex 1611248,58,68 | November | 2018 | 2019Q2 | 2019 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2018-11-22 | N | 83 | N | 17 | N | N | 1.1101 | 39.4971 | 25959.8914
[7 empty] | 6477 | 13061 | 1611251 | 2018-11-22 14:07 | 2018-11-22 16:40 | 153 | 11kV | 459 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 188891 LL Clamp fell loose and had to be reattached. Excluded OMS 1611251 | November | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-11-22 | N | 153 | N | 17 | N | N | 1.1101 | 39.4971 | 335.4237
[7 empty] | 6296 | 10832 | 1611373 | 2018-11-22 16:22 | 2018-11-22 17:13 | 51 | 11kV | 62373 | 1223 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1673 Turramurra panel 18 tripped reclosed tripped and locked out on Signals: 11kV trip, Relays: B+C phase OC and lockout Cause: AB3019 Open and LB2209 Closed Cause: Tree branch on OG mains O/S 8 Eurong St Wahroonga See OMS 1613061 1611373 1611381 1611382 1611391 | November | 2018 | 2019Q2 | 2019 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Not Veg | 2018-11-22 | N | 51 | N | 17 | N | N | 1.1101 | 39.4971 | 45580.3487
[7 empty] | 6939 | 17912 | 1611207 | 2018-11-22 13:14 | 2018-11-22 17:50 | 276.4 | 11kV | 4975.2 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Ex Zn14891 Wyong section of Panel 12 "Yarramalong" fdr Autolink 44778 tripped (2 by 16amp HDO's) Cause not asertained. Patrolled and okay, suspect wind CC1: 22-"Refer to SOp" | November | 2018 | 2019Q2 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2018-11-22 | N | 276.4 | N | 17 | N | N | 1.1101 | 39.4971 | 3635.7294
[7 empty] | 5877 | 6163 | 1611187 | 2018-11-22 12:52 | 2018-11-22 18:15 | 323 | 11kV | 86311 | 393 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 188892 2 fault operations Overcurrent; Earth Fault Mains down ET-90084 - ET-91401 Excluded OMS 1611187 | November | 2018 | 2019Q2 | 2019 | 509:33397 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2018-11-22 | N | 219.6209 | N | 17 | N | N | 1.1101 | 39.4971 | 63073.5331
[7 empty] | 7175 | 20382 | 1611335 | 2018-11-22 15:50 | 2018-11-22 18:40 | 170 | 11kV | 340 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 188894 Broken LLC lead., no protection operated. Excluded OMS 1611335 | November | 2018 | 2019Q2 | 2019 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2018-11-22 | N | 170 | N | 17 | N | N | 1.1101 | 39.4971 | 248.462
[7 empty] | 6841 | 16830 | 1611194 | 2018-11-22 12:51 | 2018-11-22 18:50 | 359 | 11kV | 13799 | 106 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn12650 West Gosford section of Panel 1 RE44602 Ourimbah Ck Rd tripped on SEF Tree branch brought down OH 11kv mains down beyond autolink 42941 at PT12419 Lineowrker repaired and okay See 1613215,6 ex 1611194,297 | November | 2018 | 2019Q2 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2018-11-22 | N | 130.1792 | N | 17 | N | N | 1.1101 | 39.4971 | 10083.9022
[7 empty] | 6852 | 16919 | 1611416 | 2018-11-22 17:08 | 2018-11-22 18:55 | 107 | 11kV | 148649 | 1467 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Zn12600 Lisarow Panel 9 "Wyoming South" fdr tripped Relays: A Phase overcurrent Signals: 11kv trip EFI's: Nil Cause: weather related. Patrolled and okay See 1613213,4 ex 1611416 | November | 2018 | 2019Q2 | 2019 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2018-11-22 | N | 101.3286 | N | 17 | N | N | 1.1101 | 39.4971 | 108628.3048
[7 empty] | 6551 | 13828 | 1611470 | 2018-11-22 18:38 | 2018-11-22 19:40 | 62 | 11kV | 2666 | 43 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 188900 A Phase broken live line lead Excluded OMS 1611470 | November | 2018 | 2019Q2 | 2019 | 507:80931 | 507:80931 | ZN00507/080931 | CESSNOCK | OH | Not Veg | 2018-11-22 | N | 62 | N | 17 | N | N | 1.1101 | 39.4971 | 1948.2342
[7 empty] | 5708 | 4768 | 1611119 | 2018-11-22 10:29 | 2018-11-22 19:48 | 559 | 11kV | 3913 | 7 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 188893 Live Line lead broken at top of DOLF assembly Excluded OMS 1611403 & 1611119 | November | 2018 | 2019Q2 | 2019 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2018-11-22 | N | 559 | N | 17 | N | N | 1.1101 | 39.4971 | 2859.505
[7 empty] | 6338 | 11277 | 1611287 | 2018-11-22 14:39 | 2018-11-22 20:45 | 366.35 | 11kV | 7327 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn12630 Peats RIdge section of Pa3 "Mangrove Mtn" fdr No device operation. DOp isolated at CP46938 11kv mains down vicinity PT13362 Abnormal: Autlink bypass was closed at CP46938 Tree branch brought down OH. Lineworker repaired CC1: 22-"Refer to SOp" | November | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2018-11-22 | N | 366.35 | N | 17 | N | N | 1.1101 | 39.4971 | 5354.3555
[7 empty] | 6788 | 16187 | 1611280 | 2018-11-22 14:27 | 2018-11-22 21:30 | 423 | 11kV | 28122 | 179 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 188904 2 fault operations Tree on mains at sub 50449 Excluded OMS 1611280 | November | 2018 | 2019Q2 | 2019 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2018-11-22 | N | 157.1061 | N | 17 | N | N | 1.1101 | 39.4971 | 20550.7281
[7 empty] | 5689 | 4547 | 1611377 | 2018-11-22 16:26 | 2018-11-22 23:32 | 426 | 11kV | 118601 | 677 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 188901 A Phase Earth Fault Tree on mains LS-20353 Excluded OMS 161377. | November | 2018 | 2019Q2 | 2019 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Veg | 2018-11-22 | N | 175.1861 | N | 17 | N | N | 1.1101 | 39.4971 | 86670.1127
[7 empty] | 6375 | 11742 | 1611519 | 2018-11-22 21:12 | 2018-11-23 00:28 | 196 | 11kV | 9256 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 188905 3 Phase Sensitive Earth Fault Excluded OMS 1611519 | November | 2018 | 2019Q2 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2018-11-22 | N | 171.4074 | N | 17 | N | N | 1.1101 | 39.4971 | 6764.0118
[7 empty] | 6489 | 13168 | 1611557 | 2018-11-23 07:01 | 2018-11-23 08:05 | 64 | 11kV | 93184 | 1456 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 188913 2 fault operations A Phase Overcurrent small branch on 11kV OHM. dq | November | 2018 | 2019Q2 | 2019 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2018-11-23 | N | 64 | N | 32 | Y | Y | 1.1101 | 39.4971 | 68096.1187
[7 empty] | 5610 | 3620 | 1611550 | 2018-11-23 06:37 | 2018-11-23 12:10 | 333 | 11kV | 333 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 188919 Broken Live Line Lead Excluded OMS 1611550 | November | 2018 | 2019Q2 | 2019 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2018-11-23 | N | 333 | N | 32 | Y | Y | 1.1101 | 39.4971 | 243.3466
[7 empty] | 5939 | 6836 | 1611415 | 2018-11-22 17:11 | 2018-11-23 12:20 | 1149 | 11kV | 1149 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Wind Strong | N | LID 188908 No protection operations. DOp found volts on neutral. Suspect faulty txf. TX REPLACED Excluded OMS 1611415 | November | 2018 | 2019Q2 | 2019 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2018-11-22 | N | 1149 | N | 17 | N | N | 1.1101 | 39.4971 | 839.6553
[7 empty] | 6708 | 15237 | 1611695 | 2018-11-23 11:11 | 2018-11-23 12:47 | 96 | 11kV | 72646 | 993 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 188917 2 fault operations A Phase Earth Fault Excluded OMS 1611695 | November | 2018 | 2019Q2 | 2019 | 257:81985 | 257:81985 | ZN00257/081985 | NEWCASTLE | OH | Veg | 2018-11-23 | N | 73.1581 | N | 32 | Y | Y | 1.1101 | 39.4971 | 53087.5541
[7 empty] | 6663 | 14946 | 1611713 | 2018-11-23 11:21 | 2018-11-23 12:54 | 93 | 11kV | 30039 | 323 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S3154 St Ive Panel 23 tripped on C phase IOC Abnormal Switching: CP2081 Open and Defective Tree branch on OH mains see OMS 1615147 1611713 | November | 2018 | 2019Q2 | 2019 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Veg | 2018-11-23 | N | 93 | N | 32 | Y | Y | 1.1101 | 39.4971 | 21951.6152
[7 empty] | 5754 | 5195 | 1611167 | 2018-11-23 13:03 | 2018-11-23 13:18 | 15 | 11kV | 3300 | 220 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 188922 3 phase FDR DE-ENERGISED TO REMOVE TREE FROM MAINS Excluded OMS 1611165 | November | 2018 | 2019Q2 | 2019 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2018-11-23 | N | 15 | N | 32 | Y | Y | 1.1101 | 39.4971 | 2411.5427
[7 empty] | 5900 | 6395 | 1611745 | 2018-11-23 11:49 | 2018-11-23 13:20 | 91 | 11kV | 728 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 188921 A Phase tapping burnt off to dolf from OHM. dq Excluded oms 1611745 | November | 2018 | 2019Q2 | 2019 | 240:34846 | 240:34846 | ZN00240/034846 | NEWCASTLE | OH | Not Veg | 2018-11-23 | N | 91 | N | 32 | Y | Y | 1.1101 | 39.4971 | 532.0009
[7 empty] | 5386 | 604 | 1611865 | 2018-11-23 13:09 | 2018-11-23 14:07 | 58 | 11kV | 55738 | 961 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn2400 Berowra Panel 26 tripped on Signals: 11KV trip, Battery defect, Tap changer no volts Relays: A and Cphase OC, Reclose Lockout Cause: Tree on OH mains O/S 79 Yallambee Rd Berowra See OMS 1611865 1611873 | November | 2018 | 2019Q2 | 2019 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Veg | 2018-11-23 | N | 58 | N | 32 | Y | Y | 1.1101 | 39.4971 | 40731.6864
[7 empty] | 5638 | 3925 | 1611797 | 2018-11-23 12:27 | 2018-11-23 15:09 | 161.8667 | 11kV | 109421.8667 | 676 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | EX S2400 Berowra panel 11 Recloser CP1772 Syemours Creeks Relays: OC trip, Lockout Carse: Tree branch on HV adjacent to recloser CP1238 found on ground with burn marks | November | 2018 | 2019Q2 | 2019 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2018-11-23 | N | 161.8667 | N | 32 | Y | Y | 1.1101 | 39.4971 | 79962.2728
[7 empty] | 5606 | 3596 | 1611997 | 2018-11-23 14:37 | 2018-11-23 15:14 | 37 | 11kV | 19314 | 522 | HV | Equipment Failed in Service | Equipment Failure | Tap Changer | Unplanned | Wind Strong | N | LID 188925 C Phase Cph Keiza Reg 61194 found at -16tap. Brought to neutral tap - volts OK Excluded OMS 1611997,1612007,1612019 | November | 2018 | 2019Q2 | 2019 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | Unknown | Not Veg | 2018-11-23 | N | 37 | N | 32 | Y | Y | 1.1101 | 39.4971 | 14114.1015
[7 empty] | 5515 | 2215 | 1611921 | 2018-11-23 13:46 | 2018-11-23 15:28 | 102 | 11kV | 158610 | 1555 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Zn1287 Revesby - Pnl.3 tripped on : C phase IOC Cause not ascertained | November | 2018 | 2019Q2 | 2019 | ZN1287:PA3 | ZN1287:PA3 | ZN01287/000003 | CANTERBURY-BANKSTOWN | OH | Veg | 2018-11-23 | N | 102 | N | 32 | Y | Y | 1.1101 | 39.4971 | 115907.5098
[7 empty] | 5923 | 6665 | 1612037 | 2018-11-23 14:53 | 2018-11-23 16:07 | 74 | 11kV | 67082 | 913 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn14891 Wyong Pa1 "Minnesota" fdr has tripped Signals: 11kv trip Relays: SEL Cause: tree/branch on OH mains Brnach near AB43240 removed by DOp SEL @ RE49433 Pacific Minnesota failed to operate (5Amps load per phase?) PE please investigate See 1613223,5 ex 1612037 | November | 2018 | 2019Q2 | 2019 | ZN14891:PA1 | ZN14891:PA1 | ZN14891/000001 | CENTRAL COAST | OH | Veg | 2018-11-23 | N | 73.4743 | N | 32 | Y | Y | 1.1101 | 39.4971 | 49021.547
[7 empty] | 6044 | 8100 | 1612059 | 2018-11-23 14:44 | 2018-11-23 16:10 | 86 | 11kV | 418 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn12690 Berkeley Vale section of Panel 24L "Berkeley Rd" fdr RE45117 Glenning Valley has tripped and reclosed Relays: IOC, trip, OC trip PT12499 Brush Anderson 0.5 footpath phase blown 10Amp Cause: tree/branch on OH mains See 1613226,7 ex 1612059 | November | 2018 | 2019Q2 | 2019 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2018-11-23 | N | 5.359 | N | 32 | Y | Y | 1.1101 | 39.4971 | 305.4621
[7 empty] | 5901 | 6398 | 1611740 | 2018-11-23 11:44 | 2018-11-23 18:05 | 381 | 11kV | 96640 | 804 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 188918 2 fault operations Overcurrent; Earth Fault 11kV OHM down at pole IS-17742 Excluded OMS 1611740, 1612004, 1611785 | November | 2018 | 2019Q2 | 2019 | 238:34137 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Not Veg | 2018-11-23 | N | 120.199 | N | 32 | Y | Y | 1.1101 | 39.4971 | 70621.6616
[7 empty] | 7118 | 19689 | 1611922 | 2018-11-23 13:48 | 2018-11-23 18:50 | 302 | 11kV | 10600 | 95 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn12630 Peats Ridge section of Panel 13L Peats Ridge Aux" fdr has tripped Signals: 11kV trip Relays: A & B Phase OC, SEL, REEC, LO EFI's: Nil Cause: tree branch brought down OH. tree on 11kV after LB47980 See 1613228,9,30 ex 1611922,65,81,2436 | November | 2018 | 2019Q2 | 2019 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2018-11-23 | N | 111.5789 | N | 32 | Y | Y | 1.1101 | 39.4971 | 7746.1674
[7 empty] | 6890 | 17445 | 1612434 | 2018-11-23 18:44 | 2018-11-23 18:59 | 15 | 11kV | 1530 | 102 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | Wind Strong | N | At Zn15013 Terrey Hills AOP interrupted panel 8 after reports of AB25115 was arcing with additional numerous earth fault alarms from zone Cause: AB25115 was arcing badly. See OMS 1613459 1613460 1612457 1612434 1612435 | November | 2018 | 2019Q2 | 2019 | ZN15013:PA8 | ZN15013:PA8 | ZN15013/000008 | NORTHERN BEACHES | OH | Not Veg | 2018-11-23 | N | 15 | N | 32 | Y | Y | 1.1101 | 39.4971 | 1118.0789
[7 empty] | 6900 | 17594 | 1612211 | 2018-11-23 17:50 | 2018-11-23 19:16 | 86 | 11kV | 5590 | 65 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 188931 Fdr isolated to remove large tree branch near sub 51607. Excluded OMS No. 1612211 | November | 2018 | 2019Q2 | 2019 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2018-11-23 | N | 86 | N | 32 | Y | Y | 1.1101 | 39.4971 | 4085.0071
[7 empty] | 5941 | 6859 | 1611937 | 2018-11-23 13:52 | 2018-11-23 19:50 | 358 | 11kV | 11980 | 90 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At Zn35370 Galston panel 8 Recloser CP559 Cobah RD relays: SEF trip Cause: OH brought down @ PT2247 Nollands End Cause: 1615100 1615101 1611937 1611955 | November | 2018 | 2019Q2 | 2019 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2018-11-23 | N | 133.1111 | N | 32 | Y | Y | 1.1101 | 39.4971 | 8754.6306
[7 empty] | 7102 | 19578 | 1612064 | 2018-11-23 15:07 | 2018-11-23 20:20 | 313 | 11kV | 313 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 188930 C Phase Cph LL Lead broken at DOLF end. Excluded OMS No. 1612064 | November | 2018 | 2019Q2 | 2019 | 532:83293 | 532:83293 | ZN00532/083293 | MAITLAND | OH | Not Veg | 2018-11-23 | N | 313 | N | 32 | Y | Y | 1.1101 | 39.4971 | 228.7312
[7 empty] | 5584 | 3406 | 1612513 | 2018-11-23 20:23 | 2018-11-23 20:57 | 34 | 11kV | 31178 | 917 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | At S15013 Terrey Hills Panel 4 tripped on Relays: Sef, Lockout Cause: Tripped while trying to locate 11kV bond failure See OMS 1615145 1612513 | November | 2018 | 2019Q2 | 2019 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Not Veg | 2018-11-23 | N | 34 | N | 32 | Y | Y | 1.1101 | 39.4971 | 22783.9628
[7 empty] | 6517 | 13575 | 1611718 | 2018-11-23 11:25 | 2018-11-23 21:00 | 575 | 11kV | 172672 | 968 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S847 Hornsby Panerl 18 tripped, reclosed tripped and locked out on Relays: C phase IOC Signals: 11kV Trip EFI's Nil Cause: Large tree on OH mains adjacent to LB 700 See OMS 1613447 1613448 1611718 1612369 | November | 2018 | 2019Q2 | 2019 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Not Veg | 2018-11-23 | N | 178.3802 | N | 32 | Y | Y | 1.1101 | 39.4971 | 126183.6046
[7 empty] | 7125 | 19723 | 1612057 | 2018-11-23 15:02 | 2018-11-23 21:20 | 378 | 11kV | 21080 | 150 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mountain" RE46935 Ironbark Kirks 0.8 has tripped Relays: SEL Cause: tree/branch brought down OH Tree into 11kv, 11kv into 415. See 161323,2 ex 1612057 | November | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2018-11-23 | N | 140.5333 | N | 32 | Y | Y | 1.1101 | 39.4971 | 15404.6422
[7 empty] | 5917 | 6542 | 1611757 | 2018-11-23 11:40 | 2018-11-23 21:56 | 616 | 11kV | 251328 | 408 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Zn14143 Somersby Zone section of Panel 17 From LB46789 bond off between tee off to PT46532 and tee off to PT18504 See 1614896 ex 1611727,57,877,908,2296,512,549 | November | 2018 | 2019Q2 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2018-11-23 | N | 616 | N | 32 | Y | Y | 1.1101 | 39.4971 | 183663.0895
[7 empty] | 6144 | 9345 | 1612161 | 2018-11-23 15:54 | 2018-11-23 23:00 | 426 | 11kV | 16004 | 54 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn14891 Wyong section of Panel 12 "Yarramlaong" RE45015 Brush Creek has tripped Relays: IOC trip, EF Trip and LO Cause: tree branch brought down OH between AB44137 and AB40827 See 1614865,6 ex 1612161,76,381 | November | 2018 | 2019Q2 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2018-11-23 | N | 296.3704 | N | 32 | Y | Y | 1.1101 | 39.4971 | 11695.2512
[7 empty] | 5661 | 4281 | 1611967 | 2018-11-23 14:16 | 2018-11-23 23:15 | 539 | 11kV | 46354 | 86 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP231 MT Ida St tripped and locked out Section of 11kV feeder Cause: Tree damaged mains - Repairs carried out - HV into LV mains See OMS 1613474 1613475 1611967 | November | 2018 | 2019Q2 | 2019 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | OH | Veg | 2018-11-23 | N | 539 | N | 32 | Y | Y | 1.1101 | 39.4971 | 33874.136
[7 empty] | 6854 | 16962 | 1611619 | 2018-11-23 09:25 | 2018-11-23 23:35 | 850 | 11kV | 83072 | 372 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S35370 Galston Panel 2 feeder tripped, reclosed tripped and locked out on Relays: A+C phase OC and Lockout Signals: 11kV trip Cause: Branch on OH mains adjacent to PT808 - After feeder tripped tree came down adjacent to CP58 See OMS 1613463 1613464 1611619 1612244 1611693 1611732 1611738 | November | 2018 | 2019Q2 | 2019 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2018-11-23 | N | 223.3118 | N | 32 | Y | Y | 1.1101 | 39.4971 | 60706.5674
[7 empty] | 6583 | 14276 | 1612563 | 2018-11-24 01:52 | 2018-11-24 02:45 | 53 | 11kV | 4081 | 77 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188934 A & B Phase DOLF : 40 Amp Stick on HV bushing at sub. Readings as left 90A, 70A, 80A Excluded OMS 1612563 | November | 2018 | 2019Q2 | 2019 | 221:11900 | 221:11900 | ZN00221/011900 | LAKE MACQUARIE | OH | Veg | 2018-11-24 | N | 53 | N | 6 | N | N | 1.1101 | 39.4971 | 2982.2744
[7 empty] | 5871 | 6097 | 1611253 | 2018-11-22 14:15 | 2018-11-24 08:40 | 2545 | 11kV | 126076 | 196 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn12630 Peats Ridge section of Panel 1 "Gunderman" fdr 11kv RE45013 Gunderman tripped on overcurrent Cause: tree/brnach brought down OH Bushfire and 11kv mains down between AB43179 and LK42686 tee PT14580 and PT13624 See 1614950,1,2 ex 1611253,499,500 | November | 2018 | 2019Q2 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2018-11-22 | N | 643.2449 | N | 17 | N | N | 1.1101 | 39.4971 | 92132.6222
[7 empty] | 6236 | 10319 | 1612528 | 2018-11-23 19:34 | 2018-11-24 10:08 | 874 | 11kV | 102539 | 122 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Endeavour Energy loss of supply to 11kv settlers rd interconnector due to fault Loss of supply between LK42686 and LB45074 Abnormal: Tree into 11kV between AB43179 and AB42686 with 2 PT's interrupted LB45074 closed DOp patrolled and okay See 1614988,90,1 Ex 1612528,625 | November | 2018 | 2019Q2 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2018-11-23 | N | 840.4836 | N | 32 | Y | Y | 1.1101 | 39.4971 | 74932.4768
[7 empty] | 6497 | 13268 | 1612592 | 2018-11-24 07:57 | 2018-11-24 12:40 | 283 | 11kV | 4811 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Ex Zn14143 Somersby section of Panel 17 PT13348 Calga Pacific B Phase HDO blown Cause: not ascertained. removed foil balloon from PT and okay See 1614933 ex 1612592 | November | 2018 | 2019Q2 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2018-11-24 | N | 283 | N | 6 | N | N | 1.1101 | 39.4971 | 3515.7369
[7 empty] | 6675 | 15055 | 1611715 | 2018-11-23 11:25 | 2018-11-24 14:35 | 1630 | 11kV | 40750 | 25 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Ex Zn12650 West Gosford section of Panel 1 "Dog Trap" 11kV Bond burnt beyond LK42816 and LV Fuse broken at PT48497 See 1615047ex 1611715 1612564 1612761 | November | 2018 | 2019Q2 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2018-11-23 | N | 1630 | N | 32 | Y | Y | 1.1101 | 39.4971 | 29778.8981
[7 empty] | 6348 | 11411 | 1612743 | 2018-11-24 13:59 | 2018-11-24 15:15 | 76 | 11kV | 76 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 188936 B Phase DOLF : 10 Amp Replaced 10 amp HV fuse, B phase, restored at 1515pm, cause was bird on HV arrester. Excluded OMS 1612743 | November | 2018 | 2019Q2 | 2019 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2018-11-24 | N | 76 | N | 6 | N | N | 1.1101 | 39.4971 | 55.5386
[7 empty] | 6432 | 12512 | 1612192 | 2018-11-23 16:11 | 2018-11-24 16:40 | 1469 | 11kV | 119997 | 209 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Recloser 1126 Mona Vale Rd Tripped and Locked out Cause: Tree on HV mains between Link21880 tee PT15550 See OMS 1615134 1615135 1615136 1615138 1615139 Abnormal Switching: CP77332 Open, CP20518 Closed Note: recloser 1126 tripped 3 times on restoration | November | 2018 | 2019Q2 | 2019 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2018-11-23 | N | 574.1483 | N | 32 | Y | Y | 1.1101 | 39.4971 | 87690.2683
[7 empty] | 6385 | 11841 | 1615048 | 2018-11-24 15:22 | 2018-11-24 17:50 | 148 | 11kV | 15688 | 106 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Panel 1 RE44602 Ourmibah Ck Rd was interrupted to allow lineowrkers to repair the 11kv CCT cable which has come off the pin insulator adjacent RE44602 ourimbah Ck Rd | November | 2018 | 2019Q2 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2018-11-24 | N | 148 | N | 6 | N | N | 1.1101 | 39.4971 | 11464.3277
[7 empty] | 5701 | 4664 | 1615079 | 2018-11-24 04:10 | 2018-11-24 19:00 | 890 | 11kV | 1780 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S4613 MWS&DB Victoria Leo - supply manually interrupted due to broken stay wire om OH section of Panel 33 @ pennant Hills | November | 2018 | 2019Q2 | 2019 |  |  |  |  | OH | Not Veg | 2018-11-24 | N | 890 | N | 6 | N | N | 1.1101 | 39.4971 | 1300.7715
[7 empty] | 5663 | 4300 | 1614920 | 2018-11-23 22:01 | 2018-11-24 19:34 | 1293 | 11kV | 610575 | 665 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Ex Zn14143 Somersby section of Panel 17 IR61921 Somersby Falls Viitasalo tripped and locked out on: OC trip Cause: bond IR61921 is in scan fail and so was not aware that it had tripped 11kv bond was found burnt off adjacent to LB46789 various branches also found on feeder See 1614920,1,2,3,4,5 ex 1612592 | November | 2018 | 2019Q2 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2018-11-23 | N | 918.1579 | N | 32 | Y | Y | 1.1101 | 39.4971 | 446190.2011
[7 empty] | 5981 | 7270 | 1612255 | 2018-11-23 16:35 | 2018-11-24 21:15 | 1720 | 11kV | 220576 | 1626 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn12580 Erina section of Panel 4l"springfield" RE49612 Barinya Wells has tripped Signals: 11kv trip Relays: OC trip Cause: tree has hit and destroyed PT12320 and LV mains are down 11kv section from RE49612 to S18344 to PT12320 See 1614825,6 ex 1612255,72,91,1612473 | November | 2018 | 2019Q2 | 2019 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2018-11-23 | N | 135.6556 | N | 32 | Y | Y | 1.1101 | 39.4971 | 161190.4349
[7 empty] | 5935 | 6813 | 1612806 | 2018-11-24 21:04 | 2018-11-24 22:08 | 64.2167 | 11kV | 6742.75 | 105 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188939 A & B phase DOLF : 50 Amp Possum at sub pole. 50A fuses replaced with 40A. Please arrange correct size fuses to be installed. Excluded OMS 1612809 | November | 2018 | 2019Q2 | 2019 | 202:34253 | 202:34253 | ZN00202/034253 | NEWCASTLE | OH | Not Veg | 2018-11-24 | N | 64.2167 | N | 6 | N | N | 1.1101 | 39.4971 | 4927.4028
[7 empty] | 6557 | 13875 | 1612838 | 2018-11-25 09:20 | 2018-11-25 11:45 | 145 | 11kV | 145 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 188943 LLc connection fell off had to be replaced. ExcludedOMS 1612838 | November | 2018 | 2019Q2 | 2019 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2018-11-25 | N | 145 | N | 1 | N | N | 1.1101 | 39.4971 | 105.9617
[7 empty] | 6660 | 14927 | 1612003 | 2018-11-23 14:39 | 2018-11-25 14:00 | 2841 | 11kV | 8812 | 40 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Wind Strong | N | 11kV recloser 24722 Forest Croziers tripped to lockout Section of 11kV feeder panel 10 Relays: IOC trip, OC trip Cause: Broken cross arm at PT15160 Oxford Falls North HV mains twisted together See OMS 1615096 1615098 1615099 1612003 1612309 | November | 2018 | 2019Q2 | 2019 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Not Veg | 2018-11-23 | N | 220.3 | N | 32 | Y | Y | 1.1101 | 39.4971 | 6439.5497
[7 empty] | 6898 | 17569 | 1612259 | 2018-11-23 16:40 | 2018-11-25 16:50 | 2890 | 11kV | 106060 | 37 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | EX ZN2400 Berowra 11kV feeder interrupted for safety reasons between LB290 LB62158 Cause: Tree on HV/LV mains - Suspect cause of recloser 3281 tripping earlier. See OMS 1615089 1615091 1615092 1615093 1612277 | November | 2018 | 2019Q2 | 2019 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2018-11-23 | N | 2866.4865 | N | 32 | Y | Y | 1.1101 | 39.4971 | 77505.5198
[7 empty] | 5848 | 5859 | 1612930 | 2018-11-26 03:12 | 2018-11-26 05:30 | 138 | 11kV | 138 | 1 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn116 Leichhardt - Pnl.7 tripped on: O/C UG cable fault from Pnl.7 to CP64632 to S3824 to S50016 to S557 | November | 2018 | 2019Q2 | 2019 |  |  |  | INNER WEST | UG | Not Veg | 2018-11-26 | N | 138 | N | 4 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 6633 | 14662 | 1612932 | 2018-11-26 05:48 | 2018-11-26 08:35 | 167 | 11kV | 334 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188944 B Phase DOLF : 10 Amp Excluded OMS 1612932 | November | 2018 | 2019Q2 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2018-11-26 | N | 167 | N | 4 | N | N | 1.1101 | 39.4971 | 244.0773
[7 empty] | 5652 | 4129 | 1613170 | 2018-11-26 18:22 | 2018-11-26 19:15 | 53 | 11kV | 4081 | 77 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188951 B & C Phase DOLF : 40 Amp 245V Aph = 80A, B = 60A, C = 50A Excluded oms 1613170 | November | 2018 | 2019Q2 | 2019 | 214:8665 | 214:8665 | ZN00214/008665 | LAKE MACQUARIE | OH | Veg | 2018-11-26 | N | 53 | N | 4 | N | N | 1.1101 | 39.4971 | 2982.2744
[7 empty] | 6692 | 15152 | 1613169 | 2018-11-26 18:30 | 2018-11-26 19:30 | 60 | 11kV | 2400 | 40 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 188953 A Phase section isolated to repair stranded mains between poles DT-73967 & DT-73969 | November | 2018 | 2019Q2 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2018-11-26 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 1753.8492
[7 empty] | 5686 | 4507 | 1613355 | 2018-11-27 12:24 | 2018-11-27 14:20 | 116 | 11kV | 348 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 188960 B Phase DOLF : 10 Amp Magpie Excluded OMS 1613355 | November | 2018 | 2019Q2 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2018-11-27 | N | 116 | N | 2 | N | N | 1.1101 | 39.4971 | 254.3081
[7 empty] | 7060 | 19256 | 1613506 | 2018-11-27 22:32 | 2018-11-28 00:35 | 123 | 11kV | 124112 | 1229 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Wind Strong | N | Zn129 Hunters Hill - Pnl.38 tripped on: A & C phase IOC UGOH below PT327 is damaged See 1614980 1614981 1614985 | November | 2018 | 2019Q2 | 2019 | ZN129:PA38 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | Unknown | Unknown | 2018-11-27 | N | 100.9862 | N | 2 | N | N | 1.1101 | 39.4971 | 90697.3889
[7 empty] | 6488 | 13165 | 1613556 | 2018-11-28 06:40 | 2018-11-28 08:52 | 132 | 11kV | 184800 | 1709 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Lightning | N | Zn14892 Charmhaven Panel 6 fdr tripped on: Singals: Relays: Fault CHeck, Reclose, Timing, Basler BE1-851-50TEC, Minor Alarm, 1.2.1, EFI EFI's S14980 S 14987 S18059 S18082 S14818(Not Down?) S18267(Not Down? S14807 S14740 Cause: suspect lightning. DOp found middle phase of HV UGOH (BU-00955) to/from S14859 SwA smoking when on load See 1613556,649,69,75 | November | 2018 | 2019Q2 | 2019 | ZN14892:PA6 | ZN14892:PA6 | ZN14892/000006 | CENTRAL COAST | OH | Not Veg | 2018-11-28 | N | 108.1334 | N | 34 | Y | Y | 1.1101 | 39.4971 | 135046.3893
[7 empty] | 6414 | 12207 | 1613521 | 2018-11-28 05:16 | 2018-11-28 11:10 | 354 | 11kV | 844999 | 3503 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Wind Strong | N | Zn35500 Top Ryde - Pnl.28 tripped on: A & B IOC Field EFIs: S8724 S5334 S46858 @ PT597 - Footpath and Centre phase HDOs blown Blown arrestors at: UGOH between LB280 to S7089 tee PT124 UGOH between S49473 and S8328 OH section between S5334, LB737 and S61827 See 1614958 1614959 1614960 1614967 1614968 1614969 1614965 1614963 | November | 2018 | 2019Q2 | 2019 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2018-11-28 | N | 241.2215 | N | 34 | Y | Y | 1.1101 | 39.4971 | 617500.3459
[7 empty] | 7040 | 18974 | 1613773 | 2018-11-28 10:05 | 2018-11-28 11:40 | 95 | 11kV | 112980 | 1617 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Wind Storm | N | Zn2196 Milperra - Pnl.5 tripped on: A & C phase IOC Car hit pole on cnr Henry Lawson Dr and Maxwell. Between AB1565 and LB133 to AB2362 tee PT1527 See 1614900 1614901 GIS 1613793 | November | 2018 | 2019Q2 | 2019 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-11-28 | N | 69.8701 | N | 34 | Y | Y | 1.1101 | 39.4971 | 82562.4517
[7 empty] | 5682 | 4440 | 1613704 | 2018-11-28 09:13 | 2018-11-28 11:40 | 147 | 11kV | 147 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188977 B and C Phase 10 Amp fuses Substation DOLF 3 x arrestors replaced | November | 2018 | 2019Q2 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2018-11-28 | N | 147 | N | 34 | Y | Y | 1.1101 | 39.4971 | 107.4233
[7 empty] | 6525 | 13631 | 1613929 | 2018-11-28 11:57 | 2018-11-28 12:54 | 57 | 11kV | 55177 | 1090 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn12600 Lisarow section of Panel 9 RE47607 Toomeys Rd has tripped on: Relays: Earth Fault Cause: tree/branch on OH mains. Large 3 metre tree branch found on OH (HV Pole GO-00690) mains adj tee to LB43462 See 1615056,7 ex 1613929,45 | November | 2018 | 2019Q2 | 2019 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2018-11-28 | N | 50.6211 | N | 34 | Y | Y | 1.1101 | 39.4971 | 40321.7242
[7 empty] | 6433 | 12522 | 1613532 | 2018-11-28 05:34 | 2018-11-28 13:00 | 446 | 11kV | 188107 | 664 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN3154 St Ives Panel 5 tripped on B phase timed overcurrent and Earth fault, C phase IOC Timed OC and EFI Single span of HV into LV due to branch laying across mains. Neutral burnt off from termination arm at PT996. Large tree has recently been cut down from the front yard of 20 Awatea Rd. A large cut branch was left resting across the HV mains which would See OMS 1615105 1615106 1615107 1615108 (note st ives tripped on restoration 1OMS 1615107) 1613532 1613765 Abnroaml Switching: SW/A closed @ S35365 Open @ AB2647 | November | 2018 | 2019Q2 | 2019 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | OH | Veg | 2018-11-28 | N | 283.2937 | N | 34 | Y | Y | 1.1101 | 39.4971 | 137463.0474
[7 empty] | 5523 | 2343 | 1613910 | 2018-11-28 11:48 | 2018-11-28 13:00 | 72 | 11kV | 504 | 7 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 188978 B and C Phase 31 Amp fuse, LINE DOLF Trees fell over due to storm | November | 2018 | 2019Q2 | 2019 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2018-11-28 | N | 72 | N | 34 | Y | Y | 1.1101 | 39.4971 | 368.3083
[7 empty] | 5615 | 3680 | 1613708 | 2018-11-28 07:09 | 2018-11-28 13:08 | 359 | 11kV | 3590 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188988 A Phase DOLF : 16 Amp Excluded OMS 1613705 | November | 2018 | 2019Q2 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2018-11-28 | N | 359 | N | 34 | Y | Y | 1.1101 | 39.4971 | 2623.4661
[7 empty] | 6311 | 11018 | 1613845 | 2018-11-28 09:42 | 2018-11-28 13:27 | 225 | 11kV | 186333 | 1036 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | zN35370 Galston - Pnl.4 tripped on: O/C B & C phase Abnormal: AB954 open defective with LB2895 closed. AB3252 Open defective with ELB62159 Closed Tree branch on mains near PT2214 See 1614938 1614940 1614941 1614943 1614945 1614946 1614947 | November | 2018 | 2019Q2 | 2019 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2018-11-28 | N | 179.8581 | N | 34 | Y | Y | 1.1101 | 39.4971 | 136166.6605
[7 empty] | 6273 | 10612 | 1613876 | 2018-11-28 11:08 | 2018-11-28 15:05 | 237 | 11kV | 85746 | 1038 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At ZN.14144 WAMBERAL Panel #7L 'AB 44978' Feeder has Tripped & Reclosed on: Signals: 11kV Trip. Relays: 51AB (A+B Phase TIMED O/C). FIELD EFI'S: Nil. Section of 11kV Feeder 7L ex. ZN.14144 WAMBERAL - 11kV Wires subsequently found down between AB.44381 & Teeoff to PT.14298 CRYSTAL ENTRANCE. 11kV PA.7 Interrupted for Safety @ 11:54. PT.14299 Interrupted to effect repairs 1300. Dist #2 @ PT.62350 LAVINIA NOORONG Interrupted - Tree brought down ABC. Dop restored fuses 1445, Lineworker's to reconnect ~6 customer's (off due to missing bays of mains). See 1615071,4,5,6,7,8 ex 1613876,80,952,4256,7 | November | 2018 | 2019Q2 | 2019 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Veg | 2018-11-28 | N | 82.6069 | N | 34 | Y | Y | 1.1101 | 39.4971 | 62660.6477
[7 empty] | 6984 | 18362 | 1614160 | 2018-11-28 15:06 | 2018-11-28 15:30 | 24 | 11kV | 24 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 188992 A Phase DOLF : 10 Amp Excluded OMS 1614160 | November | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-11-28 | N | 24 | N | 34 | Y | Y | 1.1101 | 39.4971 | 17.5385
[7 empty] | 5495 | 1928 | 1613870 | 2018-11-28 11:22 | 2018-11-28 15:50 | 268 | 11kV | 107636 | 1412 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188986 C Phase Overcurrent tree on 11kV at S 46965 Excluded OMS 1613878 | November | 2018 | 2019Q2 | 2019 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Veg | 2018-11-28 | N | 76.2295 | N | 34 | Y | Y | 1.1101 | 39.4971 | 78657.2141
[7 empty] | 5924 | 6672 | 1614154 | 2018-11-28 15:01 | 2018-11-28 17:00 | 119 | 11kV | 1071 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 188997 3 Phase DOLF : 20 Amp Excluded OMS 1614154 | November | 2018 | 2019Q2 | 2019 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2018-11-28 | N | 119 | N | 34 | Y | Y | 1.1101 | 39.4971 | 782.6552
[7 empty] | 6586 | 14288 | 1614249 | 2018-11-28 16:02 | 2018-11-28 17:20 | 78 | 11kV | 1170 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | LID 189005 A Phase 16 Amp fuse, Line DOLF Electrical Storm | November | 2018 | 2019Q2 | 2019 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2018-11-28 | N | 78 | N | 34 | Y | Y | 1.1101 | 39.4971 | 855.0015
[7 empty] | 6247 | 10402 | 1613682 | 2018-11-28 08:55 | 2018-11-28 17:38 | 523.0333 | 11kV | 32428.0667 | 62 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Wind Storm | N | At Zn180 Mosman ex panel 32 CP2835 Parriwi Spit Switch C HV fuse tripped. (centre phase) | November | 2018 | 2019Q2 | 2019 | ZN180:PA32 | ZN180:PA32 | ZN00180/000032 | MOSMAN | OH | Not Veg | 2018-11-28 | N | 523.0333 | N | 34 | Y | Y | 1.1101 | 39.4971 | 23697.4747
[7 empty] | 6773 | 15865 | 1614113 | 2018-11-28 14:46 | 2018-11-28 17:40 | 174 | 11kV | 2262 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189001 A and C Phase 20 Amp, Line DOLF patrol requested | November | 2018 | 2019Q2 | 2019 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2018-11-28 | N | 174 | N | 34 | Y | Y | 1.1101 | 39.4971 | 1653.0029
[7 empty] | 5497 | 1940 | 1614324 | 2018-11-28 16:45 | 2018-11-28 18:20 | 95 | 11kV | 23132 | 244 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At ZN847 Hornsby Panel 45 Recloser421 triopped on OC and Lockout Cause: Tree branch near recloser 421 near LB720 See OMS 1615113 1615114 1614324 | November | 2018 | 2019Q2 | 2019 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2018-11-28 | N | 94.8033 | N | 34 | Y | Y | 1.1101 | 39.4971 | 16904.1833
[7 empty] | 5862 | 6014 | 1614406 | 2018-11-28 17:52 | 2018-11-28 19:00 | 68 | 11kV | 68 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189003 A & B Phase Excluded OMS 1614406 | November | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-11-28 | N | 68 | N | 34 | Y | Y | 1.1101 | 39.4971 | 49.6924
[7 empty] | 5677 | 4383 | 1614027 | 2018-11-28 13:23 | 2018-11-28 19:33 | 370 | 11kV | 4008 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn12650 West Gosford section of Panel 1 "Dog Trap Rd" RE45010 palm Grove has tripped, reclosed, tripped on: Relays: Earth Fault, Lockout Cause: tree/branch brought down OH. after LK43412 See 1615030,1,2 ex 1614027 | November | 2018 | 2019Q2 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2018-11-28 | N | 222.6667 | N | 34 | Y | Y | 1.1101 | 39.4971 | 2928.9282
[7 empty] | 6479 | 13073 | 1613997 | 2018-11-28 12:50 | 2018-11-28 19:45 | 415 | 11kV | 415 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | LID 189008 A phase substation DOLF Blown arrestors | November | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-11-28 | N | 415 | N | 34 | Y | Y | 1.1101 | 39.4971 | 303.2698
[7 empty] | 7106 | 19624 | 1613628 | 2018-11-28 07:45 | 2018-11-28 20:15 | 750 | 11kV | 750 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Wind Storm | N | Ex Zn12690 Berkeley Vale section of Panel 12 S12359 Corella on line dists -2x60A ECM 11kv HRC fuses operated for No.2 11kv/415V Tx (#2 RMI) Suspect Tx2 failure. operating agreement from cust elec 1000. Work permit to T/Con 1025. Dist 1 fed straight from Tx to customer MSB See 1615051 ex 1613628 | November | 2018 | 2019Q2 | 2019 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | UG | Not Veg | 2018-11-28 | N | 750 | N | 34 | Y | Y | 1.1101 | 39.4971 | 548.0779
[7 empty] | 5586 | 3413 | 1614203 | 2018-11-28 15:33 | 2018-11-28 20:30 | 297 | 11kV | 2376 | 8 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 189010 DOLF : 10 Amp Replace faulty Tx. Excluded oms 1614261,1614203 | November | 2018 | 2019Q2 | 2019 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2018-11-28 | N | 297 | N | 34 | Y | Y | 1.1101 | 39.4971 | 1736.3107
[7 empty] | 7148 | 19973 | 1614479 | 2018-11-28 18:55 | 2018-11-28 21:15 | 140 | 11kV | 280 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189012 B phase 16 Amp fuse | November | 2018 | 2019Q2 | 2019 | 238:34148 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Veg | 2018-11-28 | N | 140 | N | 34 | Y | Y | 1.1101 | 39.4971 | 204.6157
[7 empty] | 5455 | 1462 | 1614299 | 2018-11-28 17:18 | 2018-11-28 21:44 | 266 | 11kV | 12236 | 46 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 189014 Pole Fire - 11kV half way down pole. Pole needs to be replaced Excluded OMS 1614299 | November | 2018 | 2019Q2 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2018-11-28 | N | 266 | N | 34 | Y | Y | 1.1101 | 39.4971 | 8941.7079
[7 empty] | 6087 | 8589 | 1614398 | 2018-11-28 19:28 | 2018-11-28 22:50 | 202.3667 | 11kV | 4047.3333 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Rain Wind Storm | N | Ex Zn12580 Erina section of Panel 12 PT13311 Erina Valley Ports was interrutped to allow staff to remove large tree from the OH Large gum tree was found on the HV CT and LV Dist oustide 14-16 Erina Valley Red, Erina | November | 2018 | 2019Q2 | 2019 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Veg | 2018-11-28 | N | 202.3667 | N | 34 | Y | Y | 1.1101 | 39.4971 | 2957.6718
[7 empty] | 6262 | 10491 | 1614255 | 2018-11-28 16:06 | 2018-11-28 23:20 | 434 | 11kV | 1736 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 189016 11kV bushing burnt on Tx. Excluded OMS 1614255 | November | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-11-28 | N | 434 | N | 34 | Y | Y | 1.1101 | 39.4971 | 1268.6176
[7 empty] | 6377 | 11758 | 1614556 | 2018-11-28 20:14 | 2018-11-28 23:42 | 208 | 11kV | 238924 | 1162 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn965 Pennant Hills - Pnl.11 tripped, relcosed and loced out on: C phase IOC Fallen tree damaged mains , HV off pin insulator and twisted together See 1615006 1615008 | November | 2018 | 2019Q2 | 2019 | ZN965:PA11 | ZN965:PA17 | ZN00965/000017 | HORNSBY | OH | Veg | 2018-11-28 | N | 205.6145 | N | 34 | Y | Y | 1.1101 | 39.4971 | 174598.6121
[7 empty] | 5818 | 5662 | 1613580 | 2018-11-28 06:33 | 2018-11-28 23:50 | 1037 | 11kV | 363651 | 1593 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Rain Heavy | N | Zn4990 City Central - 51/52 A, B & C feeders tripped on Bz trip S776 Wynyard & George flooded during heavy rain See1614802 1614803 1614804 1614805 | November | 2018 | 2019Q2 | 2019 | ZN4990:PA51 52ABC | ZN4990:PA51 52ABC | ZN04990/51 52ABC | SYDNEY | UG | Not Veg | 2018-11-28 | N | 228.2806 | N | 34 | Y | Y | 1.1101 | 39.4971 | 265745.4249
[7 empty] | 6138 | 9287 | 1614577 | 2018-11-28 20:59 | 2018-11-29 00:56 | 237 | 11kV | 167200 | 710 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | Zn14891 Wyong tripped, reclosed and locked out on: Siglas: 11kv trip, Tx2 Group Earth Relays: Lockout Timing Relay, Fault Check, 51N EF, EFI EFI's: Nil Cause: UG Fault Frontline feeder fault in section of 11kv from ZN14891 Wyong Panel 12 to S47609 SwA See 1614884,6 ex 1614577,83 | November | 2018 | 2019Q2 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | UG | Not Veg | 2018-11-28 | N | 235.493 | N | 34 | Y | Y | 1.1101 | 39.4971 | 122184.8284
[7 empty] | 5764 | 5308 | 1614502 | 2018-11-28 19:15 | 2018-11-29 01:45 | 390 | 11kV | 82685 | 501 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | Rain Heavy | N | At ZN2635 Epping Panel 45 has tripped Signals 11kV trip Relays: A B and C phase IOC, recloser + Lockout EFI Cause: AV and LV on the ground huge tree has smashed cross arms in 11kV between 77695 and LB3046 See OMS 1615157 1615158 1615160 1614607 1614502 1614606 1614515 | November | 2018 | 2019Q2 | 2019 | ZN2635:PA46 | ZN2635:PA46 | ZN02635/000046 | RYDE | OH | Veg | 2018-11-28 | N | 165.0399 | N | 34 | Y | Y | 1.1101 | 39.4971 | 60423.7592
[7 empty] | 6063 | 8286 | 1614604 | 2018-11-28 22:51 | 2018-11-29 03:10 | 259 | 11kV | 11626 | 98 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex Zn12600 Lisarow section of Panel 2 RE411066 Macdonalds Rd tripped, reclosed and locked out on OC trip 11kv down between PT11120 and PT11121. isolated at S62787 swB See 1615061,3 ex 1614604,18 | November | 2018 | 2019Q2 | 2019 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2018-11-28 | N | 118.6327 | N | 34 | Y | Y | 1.1101 | 39.4971 | 8495.9379
[7 empty] | 6988 | 18405 | 1614676 | 2018-11-29 08:31 | 2018-11-29 09:10 | 39 | 11kV | 36444 | 1008 | HV | Excavation Ausgrid Staff | Utility Process Issue | U/G Cable | Unplanned | Rain Wind Storm | N | At S3425 Castle Cove Panel 35 tripped on Relays: Fault Check, Earth Fault, EFI Signals: CB 35 open, TX3 Group Earth 11kV trip Cause: UG cable damaged by staff S2494-S5766-S3581 | November | 2018 | 2019Q2 | 2019 | ZN3425:PA35 | ZN3425:PA35 | ZN03425/000035 | WILLOUGHBY | UG | Not Veg | 2018-11-29 | N | 36.1548 | N | 8 | N | N | 1.1101 | 39.4971 | 26632.2003
[7 empty] | 5717 | 4924 | 1614764 | 2018-11-29 10:12 | 2018-11-29 10:22 | 10 | 11kV | 30 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex Zn12630 Peats Ridge Zone section of Panel 8 section of 11kv fdr interrupted for safety to clear large tree branch 11kV fdr between LK41348 to LB44166 tee LK61945 PT's interrupted (due to non LV//ing) PT47007 & PT49835 DOps found large tree branch on HV OH line side of HV LK61945 while patrolling after trip & restore @ RE49506 See peats ridge 16:14 28/11/18 | November | 2018 | 2019Q2 | 2019 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2018-11-29 | N | 10 | N | 8 | N | N | 1.1101 | 39.4971 | 21.9231
[7 empty] | 6341 | 11337 | 1613762 | 2018-11-28 10:01 | 2018-11-29 11:05 | 1504 | 11kV | 34799 | 26 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Rain Heavy | N | S1006 Geroge & Bond Sts flooded - T/Con used 'pull-off' gear to interrupt sub Dist #4 has no services connected and was left out of service to be decommissioned See1615202 1615203 1615204 | November | 2018 | 2019Q2 | 2019 | ZN8700:PA63 64ABC | ZN8700:PA65 66GHJ | ZN08700/65 66GHJ | SYDNEY | UG | Not Veg | 2018-11-28 | N | 1338.4231 | N | 34 | Y | Y | 1.1101 | 39.4971 | 25430.0828
[7 empty] | 7124 | 19719 | 1613843 | 2018-11-28 11:02 | 2018-11-29 13:56 | 1613.9167 | 11kV | 176118.75 | 1334 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 188982 2 fault operations Overcurrent; Earth Fault Blown UGOH & LA to sub 23907 Rosewood Dr. Excluded OMS 1613843 & 1613849 | November | 2018 | 2019Q2 | 2019 | 233:82815 | 233:82815 | ZN00233/082815 | PORT STEPHENS | Unknown | Unknown | 2018-11-28 | N | 132.0231 | N | 34 | Y | Y | 1.1101 | 39.4971 | 128702.3879
[7 empty] | 7098 | 19561 | 1614831 | 2018-11-29 09:51 | 2018-11-29 15:20 | 329 | 11kV | 1974 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex Zn12630 Peats RIdge section of Panel 10 DOp found a bay of HV OH down between LK43383 & PT11131 Lineworker notified control room, 1 bay of 11kv wires down/low on Hallards rd near George Downes drive, Central mangrove. DOp's interrupted section of 11kV OH @ 11:40. permits issued at 11:55 See 1614831 ex 1614856 | November | 2018 | 2019Q2 | 2019 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2018-11-29 | N | 329 | N | 8 | N | N | 1.1101 | 39.4971 | 1442.541
[7 empty] | 6485 | 13128 | 1613972 | 2018-11-29 12:33 | 2018-11-29 16:10 | 217 | 11kV | 1302 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT11211 Quarry Rd HVDO Operated - Cause not ascertained for outage See OMS 1615725 1613972 1614298 | November | 2018 | 2019Q2 | 2019 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2018-11-29 | N | 217 | N | 8 | N | N | 1.1101 | 39.4971 | 951.4632
[7 empty] | 5518 | 2286 | 1614809 | 2018-11-29 11:42 | 2018-11-29 18:20 | 398.3333 | 11kV | 1195 | 3 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 189026 A & B Phase DOLF : 10 Amp 2 broken crossarms | November | 2018 | 2019Q2 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2018-11-29 | N | 398.3333 | N | 8 | N | N | 1.1101 | 39.4971 | 873.2708
[7 empty] | 7008 | 18599 | 1614798 | 2018-11-29 15:00 | 2018-11-29 18:55 | 235 | 11kV | 470 | 2 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex Zn14891 Wyong section of Panel 12 "Cedar Northcott" Beyond USL 44875 Abnoraml: RE45080 closed, S47409 SwB Open, S47609 SwA Open, AB41839 closed Cause: tree branch brought down OH. As above near PT18152 | November | 2018 | 2019Q2 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2018-11-29 | N | 235 | N | 8 | N | N | 1.1101 | 39.4971 | 343.4621
[7 empty] | 5737 | 5093 | 1614530 | 2018-11-28 19:45 | 2018-11-29 19:00 | 1395 | 11kV | 2790 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 189029 2 dolfs blown at sub, replaced faulty tx Excluded oms 1614530 | November | 2018 | 2019Q2 | 2019 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2018-11-28 | N | 1395 | N | 34 | Y | Y | 1.1101 | 39.4971 | 2038.8497
[7 empty] | 6728 | 15363 | 1615178 | 2018-11-29 22:47 | 2018-11-30 00:41 | 114 | 11kV | 158340 | 1681 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.28 tripped on: Earth Fault Field EFIs: S8256 S5911 S43336 S65785 UG cable fault between S76769 Sw/B and S64529 Sw/A See 1615215 1615216 1615217 1615218 | November | 2018 | 2019Q2 | 2019 | ZN690:PA28 | ZN690:PA28 | ZN00690/000028 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-11-29 | N | 94.1939 | N | 8 | N | N | 1.1101 | 39.4971 | 115710.2018
[7 empty] | 6127 | 9192 | 1615184 | 2018-11-29 23:45 | 2018-11-30 00:59 | 74 | 11kV | 222 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 189033 B Phase DOLF : 10 Amp Excluded OMS 1615184 | November | 2018 | 2019Q2 | 2019 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2018-11-29 | N | 74 | N | 8 | N | N | 1.1101 | 39.4971 | 162.2311
[7 empty] | 5905 | 6426 | 1615297 | 2018-11-30 11:46 | 2018-11-30 13:31 | 105 | 11kV | 114114 | 1114 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn1648 Enfield Panel 15 fdr tripped on Relays: A phase instantaneous, over current, EFI Signals: Tx3 ZGroup E, Zone E, 11kv trip EFI's S2013 (Electronic, did not operate) S3134 S3622 Cause: Private Contractor accidentally drilled through what looks like 700mm electricity with a grundy. Cables dug out and live/exposed. Loud Buzzing electricity souns, arcing and sparking. UG fault from S3622 to S8988 to S3971 | November | 2018 | 2019Q2 | 2019 | ZN1648:PA15 | ZN4853:PA4 | ZN04853/000004 | BURWOOD | UG | Not Veg | 2018-11-30 | N | 102.4363 | N | 4 | N | N | 1.1101 | 39.4971 | 83391.1454
[7 empty] | 6691 | 15143 | 1615337 | 2018-11-30 14:03 | 2018-11-30 17:20 | 197 | 11kV | 197 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 189044 B Phase DOLF : 10 Amp also 100 amp lv fuse was blown on A phase. D norton report private LV ohm dont have a spreader and is possiblt clashing. Excluded oms 1615337 | November | 2018 | 2019Q2 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | MUSWELLBROOK | OH | Veg | 2018-11-30 | N | 197 | N | 4 | N | N | 1.1101 | 39.4971 | 143.9618
[7 empty] | 6807 | 16413 | 1615407 | 2018-11-30 19:30 | 2018-11-30 20:00 | 30 | 11kV | 6720 | 224 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Ex Zn1287 Revesby section of Panel 4 fdr from AB974 was de-energised Air break switch 3134 one of the moving contacts has broken and was in contact with the cross arm. Interrupted to open bonds to the AB See 1616221 ex 1615407 | November | 2018 | 2019Q2 | 2019 | ZN1287:PA4 | ZN1287:PA4 | ZN01287/000004 | SUTHERLAND | OH | Not Veg | 2018-11-30 | N | 30 | N | 4 | N | N | 1.1101 | 39.4971 | 4910.7778
[7 empty] | 5951 | 6949 | 1615302 | 2018-11-30 12:36 | 2018-12-01 00:11 | 695.8 | 11kV | 146118 | 210 | HV | Overload LV Parallel | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn1648 Enfield Panel 15 fdr tripped on Relays: A phase instantaneous, over current, EFI Signals: Tx3 ZGroup E, Zone E, 11kv trip EFI's S2013 (Electronic, did not operate) S3134 S3622 Cause: UG fault from S3622 to S8988 to S3971 See 1616215,7 ex 1615297 | November | 2018 | 2019Q2 | 2019 | ZN690:PA25 | ZN690:PA25 | ZN00690/000025 | BURWOOD | Unknown | Not Veg | 2018-11-30 | N | 695.8 | N | 4 | N | N | 1.1101 | 39.4971 | 106778.7246
[7 empty] | 7085 | 19481 | 1615439 | 2018-12-01 08:11 | 2018-12-01 10:00 | 109 | 11kV | 1308 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 189046 A & B Phase DOLF : 10 Amp fdr patrolled no fault found | December | 2018 | 2019Q2 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2018-12-01 | N | 109 | N | 2 | N | N | 1.1101 | 39.4971 | 955.8478
[7 empty] | 6392 | 11933 | 1615509 | 2018-12-01 15:45 | 2018-12-01 17:55 | 130 | 11kV | 130087 | 1480 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 35 Tripped On Relays: SEL - EFI Signals: 11kV Trip, Zone Earth - Group 3 Earth Abormal switching: SW/A closed @ S967 LB48967 Open Cause: Treansformer tail defective at S967 1616766 1616771 1616770 1616769 1616769 1616773 1610773 1615509 1615510 1615520 1615521 | December | 2018 | 2019Q2 | 2019 | ZN4545:PA35 | ZN4545:PA35 | ZN04545/000035 | RYDE | Unknown | Not Veg | 2018-12-01 | N | 87.8966 | N | 2 | N | N | 1.1101 | 39.4971 | 95063.7427
[7 empty] | 5566 | 3130 | 1615599 | 2018-12-02 09:04 | 2018-12-02 11:21 | 137 | 11kV | 282395 | 2131 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S187 Crows Nest Panel 20 tripped on OC/EF relay - trip, E/F, EFI and EF check relay. Cause: UG cable fault between S63963 and S963 See OMS 1616781 1616782 1615599 | December | 2018 | 2019Q2 | 2019 | ZN187:PA20 | ZN187:PA20 | ZN00187/000020 | NORTH SYDNEY | UG | Not Veg | 2018-12-02 | N | 132.5176 | N | 17 | N | N | 1.1101 | 39.4971 | 206365.9368
[7 empty] | 6267 | 10570 | 1615639 | 2018-12-02 12:47 | 2018-12-02 13:52 | 65 | 11kV | 29831 | 487 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 198052 tree branch fallen into mains at 16 Bolwarra Park Drv, branch removed by DOP power restored Excluded oms 1615642 | December | 2018 | 2019Q2 | 2019 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2018-12-02 | N | 61.2546 | N | 17 | N | N | 1.1101 | 39.4971 | 21799.6149
[7 empty] | 5999 | 7572 | 1615629 | 2018-12-02 12:29 | 2018-12-02 14:45 | 136 | 11kV | 129472 | 952 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S965 Pennant Hills panel 35 tripped on B and C phase overcurrent Cause: Tree branch on OH mains fallen clear See OMS 1615629 1615630 1615633 | December | 2018 | 2019Q2 | 2019 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | HORNSBY | OH | Veg | 2018-12-02 | N | 136 | N | 17 | N | N | 1.1101 | 39.4971 | 94614.3188
[7 empty] | 6000 | 7581 | 1615711 | 2018-12-02 14:42 | 2018-12-02 15:45 | 63 | 11kV | 63 | 1 | HV | Animal Other | Animal | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 189056 Single phase DOLF : 10 Amp goanna removed from sub 10 amp hvf replaced, power restored 1545 | December | 2018 | 2019Q2 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2018-12-02 | N | 63 | N | 17 | N | N | 1.1101 | 39.4971 | 46.0385
[7 empty] | 6388 | 11902 | 1615679 | 2018-12-02 14:04 | 2018-12-02 16:10 | 126 | 11kV | 92500 | 926 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Ex Kogarah Zn Pnl.17 - USL30762 had a Bond burn off causing low volts beyong Abnormal: Rockdale Pnl.3 closed with S10143 Sw/A open See 1615831 1617018 1617019 | December | 2018 | 2019Q2 | 2019 | ZN10999:PA17 | ZN10998:PA3 | ZN10998/000003 | BAYSIDE | OH | Not Veg | 2018-12-02 | N | 99.892 | N | 17 | N | N | 1.1101 | 39.4971 | 67596.2717
[7 empty] | 7135 | 19839 | 1615678 | 2018-12-02 14:00 | 2018-12-02 16:24 | 144 | 11kV | 12992 | 96 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | Recloser CP20852 tripped and locked out Cause not ascertained - extremem wind See OMS 1616340 1616341 1615678 | December | 2018 | 2019Q2 | 2019 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2018-12-02 | N | 135.3333 | N | 17 | N | N | 1.1101 | 39.4971 | 9494.1704
[7 empty] | 6099 | 8765 | 1615771 | 2018-12-02 16:13 | 2018-12-02 17:30 | 77 | 11kV | 4312 | 56 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 189061 wire had fallen out of fuse, repaced and power restored | December | 2018 | 2019Q2 | 2019 | 513:48056 | 513:83493 | ZN00513/083493 | SINGLETON | OH | Not Veg | 2018-12-02 | N | 77 | N | 17 | N | N | 1.1101 | 39.4971 | 3151.0824
[7 empty] | 6576 | 14162 | 1615764 | 2018-12-02 15:57 | 2018-12-02 18:01 | 124 | 11kV | 8432 | 68 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Ex Zn12690 Berkeley Vale section of Panel 6 PT13191 Greffrey Answell 16Amp roadside phase HDO blown Cause: not ascertained. patrolled and okay See 1616268 ex 1615764 1615819 | December | 2018 | 2019Q2 | 2019 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Veg | 2018-12-02 | N | 124 | N | 17 | N | N | 1.1101 | 39.4971 | 6161.8569
[7 empty] | 5393 | 723 | 1615814 | 2018-12-02 14:34 | 2018-12-02 18:30 | 236 | 11kV | 236 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 189062 B Phase DOLF : 10 Amp Galah on ground Excluded OMS 1615814 | December | 2018 | 2019Q2 | 2019 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2018-12-02 | N | 236 | N | 17 | N | N | 1.1101 | 39.4971 | 172.4618
[7 empty] | 7074 | 19370 | 1615705 | 2018-12-02 14:34 | 2018-12-02 20:35 | 361 | 11kV | 1083 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 189064 Broken Live Line Lead Excluded OMS 1615705 | December | 2018 | 2019Q2 | 2019 | 508:82576 | 508:82576 | ZN00508/082576 | PORT STEPHENS | OH | Not Veg | 2018-12-02 | N | 361 | N | 17 | N | N | 1.1101 | 39.4971 | 791.4245
[7 empty] | 5430 | 1174 | 1615910 | 2018-12-02 16:11 | 2018-12-02 21:16 | 305 | 11kV | 7438 | 62 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn12630 Peats RIdge section of panel 3 "mangrove mtn" RE45035 Mangrove Mountain tripped on earth fault Cause: OH DOwn. 2 spans 11kv down vicinity PT13137 See 1616284,6,7 ex 1615910 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2018-12-02 | N | 119.9677 | N | 17 | N | N | 1.1101 | 39.4971 | 5435.471
[7 empty] | 5574 | 3256 | 1615918 | 2018-12-02 21:16 | 2018-12-02 22:48 | 92 | 11kV | 57732 | 643 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | At S15009 Manly Panel 9 Tripped on Relays: Earth Fault, EFI Frame leakage Fault Check Cause: 11kV feeder fault from S16259 Manly Pacific Hotel to S16643 Henrietta Sydney See OMS 1616338 1616339 1615046 | December | 2018 | 2019Q2 | 2019 | ZN15009:PA9 | ZN15009:PA9 | ZN15009/000009 | NORTHERN BEACHES | UG | Not Veg | 2018-12-02 | N | 89.7854 | N | 17 | N | N | 1.1101 | 39.4971 | 42188.8428
[7 empty] | 6620 | 14545 | 1615745 | 2018-12-02 15:37 | 2018-12-02 23:00 | 443 | 11kV | 23482 | 150 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn12630 Peats Ridge section of Panel 3 "Mangrove Mtn" fdr RE46935 Ironbarks Kirks 0.8 tripped on earth fault and IOC Cause: OH Down. 1 span 11kv down vicinity PT13362 Ironbark Kirks 1.7 See 1616258,9,60 ex 1615745,76,826,39 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2018-12-02 | N | 156.5467 | N | 17 | N | N | 1.1101 | 39.4971 | 17159.953
[7 empty] | 6106 | 8884 | 1615788 | 2018-12-02 16:47 | 2018-12-02 23:10 | 383 | 11kV | 3447 | 9 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 189065 Blown tapping at DP-10012 phase down 1647hrs LF40751 opened 2240hrs supply back on 2310hrs Excluded OMS 1615788 | December | 2018 | 2019Q2 | 2019 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2018-12-02 | N | 383 | N | 17 | N | N | 1.1101 | 39.4971 | 2518.9659
[7 empty] | 5831 | 5749 | 1615806 | 2018-12-02 17:21 | 2018-12-03 02:30 | 548.6667 | 11kV | 51026 | 93 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 189066 Tree on Fdr near sub 47597 11kV OHM down Fdr did not trip 1737hrs no supply jobs 1823hrs open ABS 48378 0230hrs all supply back on CC1: 22-"Refer to SOp" | December | 2018 | 2019Q2 | 2019 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2018-12-02 | N | 548.6667 | N | 17 | N | N | 1.1101 | 39.4971 | 37288.2958
[7 empty] | 6331 | 11235 | 1615881 | 2018-12-02 18:54 | 2018-12-03 04:00 | 546 | 11kV | 73164 | 134 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 189067 1 fault operation | December | 2018 | 2019Q2 | 2019 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2018-12-02 | N | 546 | N | 17 | N | N | 1.1101 | 39.4971 | 53466.0932
[7 empty] | 5726 | 5000 | 1616005 | 2018-12-03 08:30 | 2018-12-03 10:59 | 149 | 11kV | 149 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 189069 Single phase DOLF : 10 Amp Excluded OMS 1616005 | December | 2018 | 2019Q2 | 2019 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2018-12-03 | N | 149 | N | 6 | N | N | 1.1101 | 39.4971 | 108.8848
[7 empty] | 6103 | 8831 | 1616233 | 2018-12-03 15:19 | 2018-12-03 17:02 | 103 | 11kV | 103 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | At S8103 Derby Suttor No3 11kv RMBC tripped on- Relays-B phase Tx over current Appears to be a grading issue with customers installation. Has previously tripped off on overcurrent and customer has recently installed some new equipment. They will chase up with Ausgrid. See 1616962 ex 1616233 | December | 2018 | 2019Q2 | 2019 | ZN167:PA17 | ZN167:PA17 | ZN00167/000017 | PARRAMATTA | Unknown | Not Veg | 2018-12-03 | N | 103 | N | 6 | N | N | 1.1101 | 39.4971 | 75.2694
[7 empty] | 5781 | 5423 | 1616237 | 2018-12-03 15:25 | 2018-12-03 18:15 | 170 | 11kV | 170 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | Ex Zn2835 Burwood signals Zone Eart, Tx 3 Group E S4100 Beresford Coventry HV fuses Siba 90A, B pahse (known grading issue, see DMA) Known grading issue, see DMA. Region to follow up See 1616964 ex 1616237 | December | 2018 | 2019Q2 | 2019 | ZN2835:PA41 | ZN2835:PA41 | ZN02835/000041 | STRATHFIELD | Unknown | Not Veg | 2018-12-03 | N | 170 | N | 6 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 6299 | 10877 | 1616203 | 2018-12-03 14:14 | 2018-12-03 19:20 | 306 | 11kV | 154344 | 1654 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 189074 2 fault operations 3 phase Overcurrent; Earth Fault Foil insulation blown onto HV & LV mains at pole IU-82053. Fault caused tapping failure pole IU-80418 - HV in LV. Excluded OMS 1616203 | December | 2018 | 2019Q2 | 2019 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2018-12-03 | N | 93.3156 | N | 6 | N | N | 1.1101 | 39.4971 | 112790.0428
[7 empty] | 5857 | 5972 | 1616332 | 2018-12-03 20:54 | 2018-12-03 21:24 | 30 | 11kV | 30630 | 1021 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn2635 Epping Panel 38 tripped, reclosed tripped and locked out on Relays: A and C phase IOC, Recloser + Lockout Cause: 216 Malton Rd tree on OH mains See OMS 1616332 1616335 1616336 1616337 1616342 1616343 | December | 2018 | 2019Q2 | 2019 | ZN2635:PA38 | ZN2635:PA38 | ZN02635/000038 | HORNSBY | OH | Veg | 2018-12-03 | N | 30 | N | 6 | N | N | 1.1101 | 39.4971 | 22383.5006
[7 empty] | 6365 | 11643 | 1616346 | 2018-12-03 21:52 | 2018-12-03 23:14 | 82 | 11kV | 70098 | 888 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9900 Menai - Pnl.3 tripped on: Earth Fault UG cable fault from Pnl.3 to S9141 and S9327 See 1617006 GIS 1616347 | December | 2018 | 2019Q2 | 2019 | ZN9900:PA3 | ZN9900:PA3 | ZN09900/000003 | SUTHERLAND | UG | Not Veg | 2018-12-03 | N | 78.9392 | N | 6 | N | N | 1.1101 | 39.4971 | 51225.5509
[7 empty] | 7053 | 19141 | 1615853 | 2018-12-02 18:26 | 2018-12-03 23:45 | 1759 | 11kV | 97770 | 531 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn14891 Wyong section of Panel 8 "Betty Anne Green" RE45078 Mardi McPherson tripped on voercurrent Abnormal: S47409:SwB Cp45080 closed Cause: tree/branch brought down OH. Vicinity 413/235/262 Yarramalong Road See 1616926,8 ex 1615853,64,88,96,934,5,6 | December | 2018 | 2019Q2 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2018-12-02 | N | 184.1243 | N | 17 | N | N | 1.1101 | 39.4971 | 71447.4323
[7 empty] | 6381 | 11787 | 1616378 | 2018-12-04 08:12 | 2018-12-04 09:15 | 63 | 11kV | 63 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 189077 C Phase DOLF : 31 Amp Burning DOLF replaced by LL crew. Excluded OMS 1616378. | December | 2018 | 2019Q2 | 2019 | 206:34441 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2018-12-04 | N | 63 | N | 2 | N | N | 1.1101 | 39.4971 | 46.0385
[7 empty] | 6990 | 18416 | 1616466 | 2018-12-04 12:41 | 2018-12-04 13:56 | 75 | 11kV | 88167 | 1239 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn3425 Castle Cove 11kV VCB panel 12 tripped on Relays: MiCom Relay IE-1A A phase, Tie , T1A phase, Lockout, Recloser, Timing and Rault Check UG cable damaged by contractor - excavator hit cable @ 4 Warrane Place see OMS 1616639 1616640 1616466 | December | 2018 | 2019Q2 | 2019 | ZN3425:PA12 | ZN3425:PA12 | ZN03425/000012 | KU-RING-GAI | UG | Not Veg | 2018-12-04 | N | 71.1598 | N | 2 | N | N | 1.1101 | 39.4971 | 64429.8431
[7 empty] | 6943 | 17926 | 1616572 | 2018-12-05 00:02 | 2018-12-05 06:07 | 365 | 11kV | 188031 | 1901 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn116 leichardt 11kv fdr Panel 12 "Balmain Derby" fdr tripped on: Relays: A & B phase O/C EFI's Nil 11kv oh mains on ground and on customers vehicle Rego DVE 62D in Moodie St Rozelle See seperate interruption for dist 2 @ S1563 @ 4:06 Note SEL on feeder failed to operate TPE to investigate See 1616972,4,5,6 LV// 1616591 ex 1616572,7,81 | December | 2018 | 2019Q2 | 2019 | ZN116:PA12 | ZN116:PA12 | ZN00116/000012 | INNER WEST | OH | Not Veg | 2018-12-05 | N | 98.9116 | N | 2 | N | N | 1.1101 | 39.4971 | 137407.5088
[7 empty] | 6535 | 13685 | 1616831 | 2018-12-05 21:11 | 2018-12-05 22:20 | 69 | 11kV | 4830 | 70 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 189091 B Phase DOLF : 40 Amp Possum on Transformer Excluded OMS 1616831 | December | 2018 | 2019Q2 | 2019 | 227:13016 | 227:13016 | ZN00227/013016 | LAKE MACQUARIE | OH | Not Veg | 2018-12-05 | N | 69 | N | 2 | N | N | 1.1101 | 39.4971 | 3529.6215
[7 empty] | 5596 | 3533 | 1616891 | 2018-12-06 09:22 | 2018-12-06 10:30 | 68 | 11kV | 68 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 189092 A Phase DOLF : 10 Amp No Cause Found Excluded OMS 1616891 | December | 2018 | 2019Q2 | 2019 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2018-12-06 | N | 68 | N | 4 | N | N | 1.1101 | 39.4971 | 49.6924
[7 empty] | 5748 | 5147 | 1617103 | 2018-12-06 19:27 | 2018-12-06 19:41 | 13.55 | 11kV | 257.45 | 19 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Panel 3 "Mangrove Mountain" AB40560 to LB61343 de-energized for safety. Interrupted to remove parachute/rope tangled on 11kv oh mains | December | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2018-12-06 | N | 13.55 | N | 4 | N | N | 1.1101 | 39.4971 | 188.1369
[7 empty] | 6246 | 10397 | 1617081 | 2018-12-06 17:41 | 2018-12-06 20:20 | 159 | 11kV | 137749 | 1147 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S180 Mosman Panel 20 tripped on C phase timed IOC, Fault Check and EFI At S180 Mosman Panel 32 tripped on A phase protection- time dOC and Earth Fault, B protn - IOC timed and OC EFI. Cause: UG cable fault between S5522 and S5016 See OMS 1617199 16917195 1617192 1612191 1617081 | December | 2018 | 2019Q2 | 2019 | ZN180:PA20 | ZN180:PA20 | ZN00180/000020 | NORTH SYDNEY | UG | Not Veg | 2018-12-06 | N | 120.095 | N | 4 | N | N | 1.1101 | 39.4971 | 100662.9063
[7 empty] | 6105 | 8862 | 1617125 | 2018-12-06 23:07 | 2018-12-07 02:30 | 203 | 11kV | 192599 | 2368 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.36 tripped on: B & C phase IOC UG cable fault between S10894 Sw/B and S10667 Sw/A tee S1544 See 1617193 161794 161796 | December | 2018 | 2019Q2 | 2019 | ZN10999:PA36 | ZN10999:PA36 | ZN10999/000036 | GEORGES RIVER | UG | Not Veg | 2018-12-06 | N | 81.334 | N | 4 | N | N | 1.1101 | 39.4971 | 140745.6685
[7 empty] | 6088 | 8592 | 1617285 | 2018-12-07 16:28 | 2018-12-07 18:19 | 111 | 11kV | 4107 | 37 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 189117 Broken strands DV-91787 to DV-91788 | December | 2018 | 2019Q2 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2018-12-07 | N | 111 | N | 1 | N | N | 1.1101 | 39.4971 | 3001.2745
[7 empty] | 6390 | 11913 | 1617423 | 2018-12-08 12:53 | 2018-12-08 15:16 | 143 | 11kV | 114111 | 908 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12640 Umina Panel 8 "Woolworths Bullion" fdr tripped, reclosed and locked out and on: Relays: B Phase IOC, EFI, Timing and lockout relays EFI's S78285 UG Fault from S18321 to S13010 See seperate interruption report for Panel 14 EFI's did not work @ S13010 and S46539 See 1617821,2,3,4 ex 1617423 | December | 2018 | 2019Q2 | 2019 | ZN12640:PA8 | ZN12640:PA8 | ZN12640/000008 | CENTRAL COAST | UG | Not Veg | 2018-12-08 | N | 125.6729 | N | 3 | N | N | 1.1101 | 39.4971 | 83388.9531
[7 empty] | 5914 | 6499 | 1617412 | 2018-12-08 12:03 | 2018-12-08 16:20 | 257 | 11kV | 3352 | 56 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 189124 B Phase DOLF : 10 Amp Blown LA A phase at PT72572. Sub dolf did not grade with L/F 61176. Excluded OMS 1617412 | December | 2018 | 2019Q2 | 2019 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2018-12-08 | N | 59.8571 | N | 3 | N | N | 1.1101 | 39.4971 | 2449.5427
[7 empty] | 6851 | 16901 | 1617467 | 2018-12-08 17:40 | 2018-12-08 19:25 | 105 | 11kV | 105 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 189125 Blown LV surge arrestor touching tank fel loose appeared to be cause of DOLF blowing, arrestor replaced. Excluded OMS 1617467. | December | 2018 | 2019Q2 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2018-12-08 | N | 105 | N | 3 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 6022 | 7850 | 1617497 | 2018-12-09 03:35 | 2018-12-09 03:58 | 23 | 11kV | 28273 | 1421 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN7900 Campbell St 11kv VCB panel 6 "S8528" feeder tripped on: Relays: EFI, E/F, O/C + E/F pickup, fault check Field EFIs: nil Signals: 11kv trip Abnormal: Sw/A opened at S1358, Sw/A closed @ S7242 Remarks: UG fault. Zn7900 Campbell St panel 6 to S8528 Sw/D Bourke Hill to S7263 Sw/A Foley Langley | December | 2018 | 2019Q2 | 2019 | ZN7900:PA6 | ZN7900:PA6 | ZN07900/000006 | SYDNEY | UG | Not Veg | 2018-12-09 | N | 19.8966 | N | 1 | N | N | 1.1101 | 39.4971 | 20661.0745
[7 empty] | 5464 | 1542 | 1617562 | 2018-12-10 02:18 | 2018-12-10 02:34 | 16 | 11kV | 8288 | 518 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | LID 189131 2 fault operations possum on UGOH HX-50448 a 1484A b 1599A c 1448A excluded OMS 1617563, | December | 2018 | 2019Q2 | 2019 | 243:80080 | 243:80080 | ZN00243/080080 | LAKE MACQUARIE | OH | Not Veg | 2018-12-10 | N | 16 | N | 4 | N | N | 1.1101 | 39.4971 | 6056.6259
[7 empty] | 6281 | 10725 | 1617566 | 2018-12-10 03:24 | 2018-12-10 04:57 | 93 | 11kV | 20553 | 221 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 189132 2 fault operations Overcurrent; Earth Fault faulty L/A's at ELB 61265 ELB 61233 = A B C o/c & e/f Sw 11460 = A o/c & e/f Excluded oms 1617566 | December | 2018 | 2019Q2 | 2019 | 232:11460 | 232:11460 | ZN00232/011460 | PORT STEPHENS | OH | Not Veg | 2018-12-10 | N | 93 | N | 4 | N | N | 1.1101 | 39.4971 | 15019.5262
[7 empty] | 5928 | 6711 | 1617729 | 2018-12-10 13:42 | 2018-12-10 14:42 | 60 | 11kV | 71100 | 1185 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca Panel 34 "Terrigal Feeder" tripped on: Relays: A+B+C Phase IOC Signals: 11kv trip EFI's Nil Abnormal: S12181 Sw2721 Closed & SwD Open, AB40076 closed, AB44334 open, AB44314 closed, AB44119 open & defective Cause: tree/branch on oh mains. Tree branch on 11kv mains adjacent AB43862. Removed by DOp See 1618097 ex 1617729,32,6,51 | December | 2018 | 2019Q2 | 2019 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2018-12-10 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 51957.7829
[7 empty] | 5395 | 741 | 1617832 | 2018-12-10 18:40 | 2018-12-10 19:30 | 50 | 11kV | 50 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 189142 A Phase DOLF : 10 Amp Excluded OMS 1617832 | December | 2018 | 2019Q2 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2018-12-10 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 6284 | 10745 | 1618022 | 2018-12-11 05:03 | 2018-12-11 05:52 | 49 | 11kV | 48363 | 987 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15006 Dee Why West PAnel 8 tripped and Locked out on B and C phase IOC B and C phase IOC Reclose and Lockout cause metalic balloon At PT15828 flashover/arcing Cause: 1618191 1618193 1618024 1618023 1618022 | December | 2018 | 2019Q2 | 2019 | ZN15006:PA8 | ZN15006:PA8 | ZN15006/000008 | NORTHERN BEACHES | OH | Veg | 2018-12-11 | N | 49 | N | 4 | N | N | 1.1101 | 39.4971 | 35342.2539
[7 empty] | 7039 | 18970 | 1618034 | 2018-12-11 07:20 | 2018-12-11 13:20 | 360 | 11kV | 360 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 189146 A & B Phase DOLF : 40 Amp FAULTY ARRESTOR Excluded OMS 1618034. | December | 2018 | 2019Q2 | 2019 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2018-12-11 | N | 360 | N | 4 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 6682 | 15098 | 1618150 | 2018-12-11 14:16 | 2018-12-11 15:12 | 56 | 11kV | 39760 | 710 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14891 Wyong panel 12 "Yarramlong" fdr tripped, reclosed and locked out on: Relays: C phase timed o/c, lockout, timing relay, fault check, EFI Signals: 11kv trip, Tx2 Group Earth EFI: nil Cause: UG frontline fault from Zn14891 Wyong Panel 12 to S47609 | December | 2018 | 2019Q2 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | UG | Not Veg | 2018-12-11 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 29055.4353
[7 empty] | 6351 | 11446 | 1618178 | 2018-12-11 15:52 | 2018-12-11 16:58 | 66 | 11kV | 57894 | 900 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN1068 Lidcombe, 11kv Panel 17 'Queen Louisa' feeder tripped Relays: A and B phase OC EFI Signals: 11kv trip ZE TX3 GE Field EFI's: S3367/S65863/S77291 Remarks: UG fault. Section of 11kv feeder from S77291 Auburn Beatrice #2 Sw B to S8126 Harrow Queen Sw A to S6136 Harrow Bea #2 | December | 2018 | 2019Q2 | 2019 | ZN1068:PA17 | ZN1068:PA17 | ZN01068/000017 | CUMBERLAND | UG | Not Veg | 2018-12-11 | N | 64.3267 | N | 4 | N | N | 1.1101 | 39.4971 | 42307.2276
[7 empty] | 6742 | 15495 | 1618405 | 2018-12-12 18:39 | 2018-12-12 23:00 | 261 | 11kV | 5552 | 230 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Pole | Unplanned | No Weather Impact | N | LID 189162 Fire in head of pole. Top pole and lower crossarm. Further repairs maybe required later. Opened feeder at Sw 65808 to allow operator to ope ABS 40797. SCADA not working at upstream recloser from ABS. | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-12-12 | N | 24.1391 | N | 1 | N | N | 1.1101 | 39.4971 | 4057.2378
[7 empty] | 6523 | 13616 | 1618611 | 2018-12-13 17:22 | 2018-12-13 19:15 | 113 | 11kV | 1808 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 189245 A Phase DOLF : 20 Amp | December | 2018 | 2019Q2 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2018-12-13 | N | 113 | N | 19 | N | N | 1.1101 | 39.4971 | 1321.2331
[7 empty] | 6624 | 14584 | 1618620 | 2018-12-13 17:58 | 2018-12-13 19:50 | 112.1 | 11kV | 2242 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 189246 Singler phase DOLF X 2 : 20 Amp | December | 2018 | 2019Q2 | 2019 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2018-12-13 | N | 112.1 | N | 19 | N | N | 1.1101 | 39.4971 | 1638.3875
[7 empty] | 6768 | 15763 | 1618626 | 2018-12-13 18:20 | 2018-12-13 20:40 | 140 | 11kV | 700 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 189296 A Phase DOLF : 16 Amp Excluded OMS 1618626 & 1618635 | December | 2018 | 2019Q2 | 2019 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2018-12-13 | N | 140 | N | 19 | N | N | 1.1101 | 39.4971 | 511.5394
[7 empty] | 6198 | 10011 | 1618649 | 2018-12-13 19:23 | 2018-12-13 20:40 | 77 | 11kV | 54131 | 703 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | At S3472 Sefton 11kv CB Pa.34 CB "English Electric etc. "tripped on Signals: 11kv trip Relays: IOC, earth fault check Abnormal: S6081 Sw/A closed, S36126 Sw/A open for planned work Remarks: lightning. Customer reported lightning outside 27 Munro St, Sefton. Dop patrolled, no damage seen | December | 2018 | 2019Q2 | 2019 | ZN3472:PA34 | ZN3472:PA34 | ZN03472/000034 | CUMBERLAND | OH | Not Veg | 2018-12-13 | N | 77 | N | 19 | N | N | 1.1101 | 39.4971 | 39557.3382
[7 empty] | 6032 | 7915 | 1618675 | 2018-12-13 19:47 | 2018-12-13 21:51 | 124 | 11kV | 115388 | 1021 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | Zn10994 Mortdale Panel 19 tripped reclosed and locke dout on Signals: 11kV trip Relays: A phase IOC, B and C phase OC, reclose lockout and EFI. Cause: Tree on 11kV OH on old forest RD Near Elm St See OMS 1619135 1916136 1618675 | December | 2018 | 2019Q2 | 2019 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Veg | 2018-12-13 | N | 113.0147 | N | 19 | N | N | 1.1101 | 39.4971 | 84322.147
[7 empty] | 6049 | 8139 | 1618663 | 2018-12-13 19:36 | 2018-12-13 21:52 | 136 | 11kV | 201552 | 1482 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | At S35800 Bankstown - 11kv CB No.16 "Canterbury Fair" tripped on: Relays: A,B & C Phase IOC, EFI Signals: 11kv trip EFI's: Nil Remarks: cause not ascertained. Probabale lightning strike | December | 2018 | 2019Q2 | 2019 | ZN35800:PA16 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-12-13 | N | 136 | N | 19 | N | N | 1.1101 | 39.4971 | 147288.2568
[7 empty] | 5466 | 1555 | 1621181 | 2018-12-13 19:26 | 2018-12-13 22:00 | 154 | 11kV | 616 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189181 C Phase DOLF : 10 Amp FAULTY ARRESTOR SUB 51386. SEE UPOR 189179/OMS 1621179 | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-12-13 | N | 154 | N | 19 | N | N | 1.1101 | 39.4971 | 450.1546
[7 empty] | 6994 | 18481 | 1618664 | 2018-12-13 19:36 | 2018-12-13 22:04 | 148 | 11kV | 152588 | 1031 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | At S35800 Bankstown - 11kv CB No.7 "short Fair No.1" tripped on: Relays: C phase IOC, EFI Signals: 11kv trip Abnormal: closed at LB2110 and open at AB2462 Remarks: cause not ascertained. Presumed lightning strike | December | 2018 | 2019Q2 | 2019 | ZN35800:PA7 | ZN35800:PA7 | ZN35800/000007 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-12-13 | N | 148 | N | 19 | N | N | 1.1101 | 39.4971 | 111506.8098
[7 empty] | 7123 | 19715 | 1618678 | 2018-12-13 19:23 | 2018-12-13 22:10 | 167 | 11kV | 286442 | 1750 | HV | Burnt Contacts | Equipment Failure | Air Break Switch | Unplanned | Lightning | N | At S1850 Bass Hill, 11kv CB Pa.32 CB "Cantrell St etc" tripped on Signals: 11kv trip Relays: A, B & C phase overcurrent EFIs: nil Abnormal: S47485 Sw/B closed and S5081 Sw/A closed (Defective feeder) Remarks: lightning struck AB.127 and burnt off 2 bonds | December | 2018 | 2019Q2 | 2019 | ZN1850:PA40 | ZN1850:PA40 | ZN01850/000040 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-12-13 | N | 163.6811 | N | 19 | N | N | 1.1101 | 39.4971 | 209323.365
[7 empty] | 5767 | 5329 | 1618653 | 2018-12-13 19:29 | 2018-12-13 22:15 | 166 | 11kV | 332 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 189292 Single phase DOLF : 10 Amp Excluded OMS 1618653 | December | 2018 | 2019Q2 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2018-12-13 | N | 166 | N | 19 | N | N | 1.1101 | 39.4971 | 242.6158
[7 empty] | 6978 | 18303 | 1618699 | 2018-12-13 20:02 | 2018-12-13 22:19 | 137 | 11kV | 103967 | 883 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | At S10998 Rockale Panel 2 tripped, reclosed tripped and locked out on Signals: 11kV trip, Relays: A protection panel: trip A B C phase fault Abnromal Switching: SWB closed at S10402 Airport Tunnel - AB30559 Open Cause not ascertained. See OMS 1619126 1619128 1619129 1618766 1618725 1618699 | December | 2018 | 2019Q2 | 2019 | ZN10998:PA2 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Veg | 2018-12-13 | N | 117.7429 | N | 19 | N | N | 1.1101 | 39.4971 | 75976.0171
[7 empty] | 6672 | 15033 | 1618644 | 2018-12-13 19:11 | 2018-12-13 22:50 | 219 | 11kV | 2056 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189291 Single phase DOLF : 20 Amp No Switching for this. I have entered for Scott Carson. Supply was off from spur fuse 41575. This was restored at 2158hrs. Power restored to sub 54217 at 2250hrs. LVF size 100. DOLF 10A Excluded OMS 1618777 & 1618644 & 1618694 | December | 2018 | 2019Q2 | 2019 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2018-12-13 | N | 171.3333 | N | 19 | N | N | 1.1101 | 39.4971 | 1502.4642
[7 empty] | 5860 | 6010 | 1618650 | 2018-12-13 19:26 | 2018-12-13 23:10 | 224 | 11kV | 224 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 189179 Single phase DOLF : 10 Amp Faulty arrestor Excluded OMS 1618650 | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-12-13 | N | 224 | N | 19 | N | N | 1.1101 | 39.4971 | 163.6926
[7 empty] | 5636 | 3862 | 1618657 | 2018-12-13 19:24 | 2018-12-13 23:50 | 266 | 11kV | 154657 | 1518 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 189178 2 fault operations C Phase Overcurrent, Earth Fault TREE ON MAINS AT POLE IV-60756 Andrew Rd. possible HV into LV checked by MSO . OK. targets T -OC & E/F C PHASE. Excluded OMS 1618665, 1618659, 1618658. | December | 2018 | 2019Q2 | 2019 | 206:34434 | 206:34434 | ZN00206/034434 | LAKE MACQUARIE | OH | Veg | 2018-12-13 | N | 101.8821 | N | 19 | N | N | 1.1101 | 39.4971 | 113018.774
[7 empty] | 7130 | 19778 | 1618821 | 2018-12-13 21:14 | 2018-12-14 02:30 | 316 | 11kV | 632 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 189188 C Phase DOLF : 10 Amp FAULTY ARRESTORS.REPLACED ALSO DOLF CARRIERS. Excluded OMS REPORT NO 1618821 | December | 2018 | 2019Q2 | 2019 | 238:34148 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2018-12-13 | N | 316 | N | 19 | N | N | 1.1101 | 39.4971 | 461.847
[7 empty] | 5648 | 4100 | 1618681 | 2018-12-13 19:55 | 2018-12-14 03:15 | 440 | 11kV | 735020 | 2781 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Lightning | N | The 11kv SwA and SwB CB's at S10925 Forest Water Board werer found to have tripped on: EF At ZN10999 Kogarah Panel 24L tripped when attempting restoration from S10725 Bristol Croydon Panel 24L: Signals : 11kv trip, Relays: B&C phase OC, EFI, fault check, SEF Panel 7: EFI Remarks: An burnt off 11kv wire located at the UGOH above S10725 Bristol Croydon on Panel 24L. More info available upon request | December | 2018 | 2019Q2 | 2019 | ZN10999:PA24 | ZN10999:PA24 | ZN10999/000024 | GEORGES RIVER | UG | Not Veg | 2018-12-13 | N | 264.3006 | N | 19 | N | N | 1.1101 | 39.4971 | 537130.9366
[7 empty] | 5491 | 1848 | 1619013 | 2018-12-13 21:17 | 2018-12-14 09:30 | 733 | 11kV | 2932 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 189201 Single phase DOLF : 10 Amp OMS 1618825 & 1619013 Replaced L/A | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-12-13 | N | 733 | N | 19 | N | N | 1.1101 | 39.4971 | 2142.6191
[7 empty] | 5778 | 5396 | 1618926 | 2018-12-14 06:21 | 2018-12-14 10:55 | 274 | 11kV | 850 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 189215 C Phase oil filled Fuse : 80 Amp 0621hrs Sub 15089 11kV Switch Fuse Tripped C phase 80A fuse blown. 0725hrs LVF 15093 interconnected. 1055hrs All supply back on. Transformer tested ok. Excluded OMS 1618926 | December | 2018 | 2019Q2 | 2019 | 257:81997 | 257:81997 | ZN00257/081997 | NEWCASTLE | UG | Not Veg | 2018-12-14 | N | 85 | N | 25 | Y | Y | 1.1101 | 39.4971 | 621.1549
[7 empty] | 5619 | 3706 | 1619006 | 2018-12-14 09:13 | 2018-12-14 10:57 | 104 | 11kV | 520 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189214 DOLF : 20 Amp Excluded OMS 1619006 | December | 2018 | 2019Q2 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2018-12-14 | N | 104 | N | 25 | Y | Y | 1.1101 | 39.4971 | 380.0007
[7 empty] | 6669 | 15006 | 1618828 | 2018-12-13 21:21 | 2018-12-14 11:30 | 849 | 11kV | 2547 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 189217 Single phase DOLF : 10 Amp Replace Transformer Excluded oms 1618828. | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-12-13 | N | 849 | N | 19 | N | N | 1.1101 | 39.4971 | 1861.2725
[7 empty] | 6209 | 10071 | 1618677 | 2018-12-13 19:14 | 2018-12-14 11:50 | 996 | 11kV | 6972 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 189225 A Phase DOLF : 10 Amp Excluded OMS 1618677 | December | 2018 | 2019Q2 | 2019 | 238:34148 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2018-12-13 | N | 996 | N | 19 | N | N | 1.1101 | 39.4971 | 5094.932
[7 empty] | 6929 | 17840 | 1618690 | 2018-12-14 04:16 | 2018-12-14 11:50 | 454 | 11kV | 3632 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 189231 A Phase DOLF : 16 Amp Excluded oms 1618690,1618917,1618921 | December | 2018 | 2019Q2 | 2019 | 512:83732 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2018-12-14 | N | 454 | N | 25 | Y | Y | 1.1101 | 39.4971 | 2654.1585
[7 empty] | 5380 | 520 | 1619214 | 2018-12-14 14:03 | 2018-12-14 14:51 | 48 | 11kV | 7584 | 158 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189247 B & C phase Overcurrent reclose was off for another fault on the system at the time. | December | 2018 | 2019Q2 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2018-12-14 | N | 48 | N | 25 | Y | Y | 1.1101 | 39.4971 | 5542.1635
[7 empty] | 5472 | 1644 | 1619127 | 2018-12-14 12:26 | 2018-12-14 15:35 | 189 | 11kV | 189 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 189251 A Phase Blown Arrestor Excluded OMS 1619127 | December | 2018 | 2019Q2 | 2019 | 238:34148 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2018-12-14 | N | 189 | N | 25 | Y | Y | 1.1101 | 39.4971 | 138.1156
[7 empty] | 6596 | 14343 | 1619232 | 2018-12-14 15:32 | 2018-12-14 16:30 | 58 | 11kV | 116 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189253 Single phase 10 Amp fuse, substation DOLF | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-12-14 | N | 58 | N | 25 | Y | Y | 1.1101 | 39.4971 | 84.7694
[7 empty] | 6114 | 9030 | 1619299 | 2018-12-14 15:44 | 2018-12-14 17:05 | 81 | 11kV | 53196 | 696 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Wind Storm | N | ZN15014 MONA VALE 11kV CB PA18 'Whitney Samuel" tripped on O/C EFI Fault Check EFI's S16489 only Cause: lightning surge arrestor UGOH to S16057 struck by lightning all arrestors failed section fo 11kv OH from USL 24463 to AB25751 tee PT16057 isolated See 1619254,66,99,24100,2 | December | 2018 | 2019Q2 | 2019 | ZN15014:PA18 | ZN15014:PA18 | ZN15014/000018 | NORTHERN BEACHES | OH | Not Veg | 2018-12-14 | N | 76.431 | N | 25 | Y | Y | 1.1101 | 39.4971 | 38874.0678
[7 empty] | 5458 | 1467 | 1619230 | 2018-12-14 15:31 | 2018-12-14 17:10 | 99 | 11kV | 198 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 189257 A Phase DOLF : 10 Amp Excluded OMS 1619230 | December | 2018 | 2019Q2 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Veg | 2018-12-14 | N | 99 | N | 25 | Y | Y | 1.1101 | 39.4971 | 144.6926
[7 empty] | 5409 | 935 | 1619301 | 2018-12-14 16:46 | 2018-12-14 18:05 | 79 | 11kV | 1896 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189259 B & C phase DOLF : 40 Amp | December | 2018 | 2019Q2 | 2019 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2018-12-14 | N | 79 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1385.5409
[7 empty] | 6506 | 13351 | 1619308 | 2018-12-14 16:59 | 2018-12-14 19:30 | 151 | 11kV | 1208 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | 11 Debenham Kowara C Phase fuse 13Amp was found blown Tree on LV@ PT18613 see other jobs at same time See 1622056 ex 1619308 | December | 2018 | 2019Q2 | 2019 | ZN14143:PA10 | ZN14143:PA10 | ZN14143/000010 | CENTRAL COAST | OH | Veg | 2018-12-14 | N | 151 | N | 25 | Y | Y | 1.1101 | 39.4971 | 882.7708
[7 empty] | 6706 | 15215 | 1619218 | 2018-12-14 14:42 | 2018-12-14 19:45 | 303 | 11kV | 136250 | 490 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189266 2 fault operations Earth Fault Excluded OMS 1619218 | December | 2018 | 2019Q2 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2018-12-14 | N | 278.0612 | N | 25 | Y | Y | 1.1101 | 39.4971 | 99567.4813
[7 empty] | 6337 | 11257 | 1619320 | 2018-12-14 17:21 | 2018-12-14 20:50 | 209 | 11kV | 4939 | 55 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 189273 OHM on crossarm at Pole FP-50482 found enroute to sub job 10A ABC ph sub DOLFs blown 100A C ph LVF blown | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-12-14 | N | 89.8 | N | 25 | Y | Y | 1.1101 | 39.4971 | 3609.2755
[7 empty] | 5699 | 4649 | 1619169 | 2018-12-14 13:20 | 2018-12-14 20:56 | 456 | 11kV | 32865 | 165 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 189279 5 Fault operations, A Phase Overcurrent Intellirupter Replaced LA at Wyong Road RAGCB 74460 and sub 75439 Replaced 1Ph 20A LF 42430 and 1ph 10A sub DOLF 75439 | December | 2018 | 2019Q2 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2018-12-14 | N | 199.1818 | N | 25 | Y | Y | 1.1101 | 39.4971 | 24016.7726
[7 empty] | 6163 | 9540 | 1619313 | 2018-12-14 17:10 | 2018-12-14 21:25 | 255 | 11kV | 765 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189275 Single phase Fuse 10 Amp substation DOLF | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-12-14 | N | 255 | N | 25 | Y | Y | 1.1101 | 39.4971 | 559.0394
[7 empty] | 5998 | 7551 | 1619338 | 2018-12-14 17:47 | 2018-12-14 21:35 | 228 | 11kV | 456 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 189274 Single phase DOLF : 10 Amp Excluded OMS 1619338 | December | 2018 | 2019Q2 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2018-12-14 | N | 228 | N | 25 | Y | Y | 1.1101 | 39.4971 | 333.2314
[7 empty] | 6128 | 9209 | 1619269 | 2018-12-14 16:11 | 2018-12-14 21:35 | 324 | 11kV | 648 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 189263 Single phase DOLF : 10 Amp Blown LA's Excluded OMS 1619269 | December | 2018 | 2019Q2 | 2019 | 522:83123 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2018-12-14 | N | 324 | N | 25 | Y | Y | 1.1101 | 39.4971 | 473.5393
[7 empty] | 7164 | 20165 | 1619323 | 2018-12-14 17:26 | 2018-12-14 21:55 | 269 | 11kV | 1345 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 189276 A Phase DOLF : 10 Amp Excluded OMS 1619323 | December | 2018 | 2019Q2 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2018-12-14 | N | 269 | N | 25 | Y | Y | 1.1101 | 39.4971 | 982.8863
[7 empty] | 6089 | 8606 | 1619209 | 2018-12-14 14:27 | 2018-12-14 23:15 | 528 | 11kV | 1584 | 3 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 189280 ABC 3 phase 10 Amp fuse substation DOLF Replaced damaged Tx | December | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-12-14 | N | 528 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1157.5405
[7 empty] | 5591 | 3486 | 1619336 | 2018-12-14 17:45 | 2018-12-14 23:45 | 360 | 11kV | 1440 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189282 C phase, 10 Amp fuse, substation DOLF | December | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2018-12-14 | N | 360 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1052.3095
[7 empty] | 6562 | 13916 | 1619248 | 2018-12-14 15:39 | 2018-12-15 | 501 | 11kV | 2015 | 131 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 189278 1 Fault operations, A Phase fuse 10 Amp Overcurrent substation DOLF 10A, Aph Sub DOLF and LA replaced at sub 50838 | December | 2018 | 2019Q2 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2018-12-14 | N | 15.3817 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1472.5026
[7 empty] | 5760 | 5249 | 1619393 | 2018-12-15 00:24 | 2018-12-15 00:31 | 7 | 11kV | 77 | 11 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 189283 33kV Fdr TM2 open on CB, 11kV swithched with Sub 78455 interrupted to clear branch of 33kV OHM at pole OR-84014 Excluded oms 1619393 | December | 2018 | 2019Q2 | 2019 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2018-12-15 | N | 7 | N | 10 | N | N | 1.1101 | 39.4971 | 56.2693
[7 empty] | 5628 | 3780 | 1619389 | 2018-12-14 19:19 | 2018-12-15 01:22 | 363 | 11kV | 303920 | 1430 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189277 2 fault operations Overcurrent; Earth Fault 11kV down pole OR-90025 & UG CABLE FAULT AT SUB 24029 Excluded oms 1619389 | December | 2018 | 2019Q2 | 2019 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Veg | 2018-12-14 | N | 212.5315 | N | 25 | Y | Y | 1.1101 | 39.4971 | 222095.7719
[7 empty] | 6366 | 11676 | 1621455 | 2018-12-14 22:40 | 2018-12-15 03:05 | 265 | 11kV | 231302 | 2141 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | LID 189284 1 fault operation Overcurrent; Earth Fault After isolation of know fault area 1887/57654 and closing ELB 18241 Sw 33413 triped on another unknow fault at sub 24029 UG CABLE FAULT AT SUB 24029 See 189277 Excluded oms 1619389 | December | 2018 | 2019Q2 | 2019 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | UG | Not Veg | 2018-12-14 | N | 108.0346 | N | 25 | Y | Y | 1.1101 | 39.4971 | 169028.6793
[7 empty] | 6924 | 17802 | 1619452 | 2018-12-15 05:07 | 2018-12-15 08:26 | 199 | 11kV | 41903 | 254 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | At Zn12630 peats Ridge, Ex Panel #3, Recloser 45071 Central Mangrove has tripped & locked out: Rec 45071 Central Mangrove Relays: OC trip, lockout Abnormal: LB61343 Closed, LB47448 Closed, REC46935 Open, LB61085 Open Remarks: cause not ascertained. Dop to patrol | December | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2018-12-15 | Y | 164.9724 | N | 10 | N | Y | 1.1101 | 39.4971 | 30621.4765
[7 empty] | 7109 | 19639 | 1625168 | 2018-12-15 09:14 | 2018-12-15 09:35 | 21 | 11kV | 658 | 253 | HV | Overload | Utility Process Issue | Recloser / Sectionaliser | Unplanned | No Weather Impact | Y | At Zn12630 peats Ridge, Ex Panel #3, Recloser 45071 Central Mangrove has tripped & locked out: Rec 45071 Central Mangrove Relays: OC trip, lockout Abnormal: LB61343 Closed, LB47448 Closed, REC46935 Open, LB61085 Open Remarks: overload. Quarry came online causing overload | December | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2018-12-15 | Y | 2.6008 | N | 10 | N | Y | 1.1101 | 39.4971 | 480.847
[7 empty] | 6157 | 9464 | 1619465 | 2018-12-15 05:38 | 2018-12-15 10:06 | 268 | 11kV | 2412 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189301 C Phase, Pole Mounted RAGCB, Earth Fault No OMS Number, sw 2389 tripped several hours after Sw 42035 (OMS 1619424) Wanted to keep separate, other events on this feeder include faulty lightning arrestor at S66061, and tree brought down 11kV at pole 8U-60023 see LID 189281 | December | 2018 | 2019Q2 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2018-12-15 | Y | 268 | N | 10 | N | Y | 1.1101 | 39.4971 | 1762.6185
[7 empty] | 6193 | 9959 | 1619222 | 2018-12-14 14:58 | 2018-12-15 11:00 | 1202 | 11kV | 106172 | 323 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn12630 Peats Ridge - Pnl.10 tripped on OC Storm See 1624714 1624715 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2018-12-14 | N | 328.7059 | N | 25 | Y | Y | 1.1101 | 39.4971 | 77587.3661
[7 empty] | 5446 | 1361 | 1619300 | 2018-12-14 14:57 | 2018-12-15 11:50 | 1253 | 11kV | 241499 | 416 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Electrical Storm | N | At Zn12630 Peats Ridge Panel 3 'Mangrove Moutain' feeder has tripped Signals: 11kv trip Relays: IOC, Rec, EFI, LO, A and N trip Field EFI's @ Sub Remarks: storm | December | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2018-12-14 | N | 580.5264 | N | 25 | Y | Y | 1.1101 | 39.4971 | 176480.3462
[7 empty] | 5853 | 5929 | 1623485 | 2018-12-15 16:38 | 2018-12-15 16:49 | 11 | 11kV | 3619 | 329 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Ex Zn15014 Mona Vale section of Panel 14 "Walana Mona & etc" RE22381 Lane Cove Walter tripped and reclosed on: Relays: OC & IOC Signals: Nil EFI's Nil Cause: Lightning | December | 2018 | 2019Q2 | 2019 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2018-12-15 | N | 11 | N | 10 | N | N | 1.1101 | 39.4971 | 2644.6585
[7 empty] | 6996 | 18504 | 1619594 | 2018-12-15 16:22 | 2018-12-15 17:00 | 38 | 11kV | 570 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189318 B phase, 16 Amp fuse, substation DOLF | December | 2018 | 2019Q2 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2018-12-15 | Y | 38 | N | 10 | N | Y | 1.1101 | 39.4971 | 416.5392
[7 empty] | 5590 | 3472 | 1619588 | 2018-12-15 16:18 | 2018-12-15 17:35 | 77 | 11kV | 118272 | 1536 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | S1285 Greenacre Park Panel 24L "Banksia Stacey" fdr tripped, reclosed, tripped and locked out Relays: A,B,C IOC, reclose timer, lockout Signals: 11kv trip Remarks: Helium ballons in mains | December | 2018 | 2019Q2 | 2019 | ZN1285:PA24 | ZN37100:PA11 | ZN37100/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-12-15 | Y | 77 | N | 10 | N | Y | 1.1101 | 39.4971 | 86429.6892
[7 empty] | 7174 | 20381 | 1619587 | 2018-12-15 16:06 | 2018-12-15 18:35 | 149 | 11kV | 143338 | 962 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn2400 Berowra - Pnl.26 tripped on: O/C Lightning - bond burnt off OH section between P26, S50340 tee S2939 See 1624207 1624208 | December | 2018 | 2019Q2 | 2019 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Not Veg | 2018-12-15 | Y | 149 | N | 10 | N | Y | 1.1101 | 39.4971 | 104747.1826
[7 empty] | 5374 | 456 | 1619643 | 2018-12-15 16:15 | 2018-12-15 18:45 | 150 | 11kV | 194100 | 1294 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn3154 St IVes 1kV Panel 11 "Ellalong Rd" tripped on: Relays: A&C phase IOC, EFI Singals: Zone Earth, Group Earth, 11kv trip EFI's: Nil Abnormals: S35365 SwA Closed, LB2647 Open Suspected lightning strike See 1621522 ex 1619643 | December | 2018 | 2019Q2 | 2019 | ZN3154:PA11 | ZN3154:PA11 | ZN03154/000011 | KU-RING-GAI | OH | Not Veg | 2018-12-15 | N | 150 | N | 10 | N | N | 1.1101 | 39.4971 | 141842.555
[7 empty] | 6335 | 11248 | 1619659 | 2018-12-15 16:40 | 2018-12-15 19:00 | 140 | 11kV | 840 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189327 B and C 10 Amp fuse, substation DOLF Start time amended to reflect the first NS call received see OMS 1619659 | December | 2018 | 2019Q2 | 2019 | 512:83732 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2018-12-15 | Y | 140 | N | 10 | N | Y | 1.1101 | 39.4971 | 613.8472
[7 empty] | 6467 | 12948 | 1619577 | 2018-12-15 15:28 | 2018-12-15 19:02 | 214 | 11kV | 37541 | 225 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 189307 1 Fault operations, ABC Phases, Earth Fault, Sensitive Earth Fault 11kV Mains tangled in trees on the ground, beyond Pole FE-70077 | December | 2018 | 2019Q2 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2018-12-15 | N | 166.8489 | N | 10 | N | N | 1.1101 | 39.4971 | 27433.8555
[7 empty] | 6809 | 16471 | 1619753 | 2018-12-15 17:25 | 2018-12-15 20:10 | 165 | 11kV | 155833 | 1657 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | S1287 Revesby Panel 21 "Vega Mars" tripped, reclosed, tripped and locked out Relays: A phase overcurrent, A phase IOC, reclose timer, lockout Signals: 11kv trip Remarks: cause not ascertained. during storm | December | 2018 | 2019Q2 | 2019 | ZN1287:PA21 | ZN1287:PA21 | ZN01287/000021 | CANTERBURY-BANKSTOWN | OH | Veg | 2018-12-15 | Y | 94.0453 | N | 10 | N | Y | 1.1101 | 39.4971 | 113878.1601
[7 empty] | 6160 | 9490 | 1620029 | 2018-12-15 19:44 | 2018-12-15 20:40 | 56 | 11kV | 11008 | 378 | HV | Staff Operation | Utility Process Issue | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Section of 11kv beyond LB183 interrupted by Dop. Ex Panel 3 "Beaconsfield Horlsey" fdr Remarks: interrupted by Dop after tree resting on 11kv mains started to catch alight | December | 2018 | 2019Q2 | 2019 | ZN2196:PA3 | ZN1287:PA19 | ZN01287/000019 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2018-12-15 | Y | 29.1217 | N | 10 | N | Y | 1.1101 | 39.4971 | 8044.3217
[7 empty] | 6259 | 10484 | 1619576 | 2018-12-15 15:27 | 2018-12-15 20:49 | 322 | 11kV | 15420 | 88 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189305 2 Fault operations ABC Phases, overcurrent instantaneous Overcurrent, Electrical Storm at the time, no cause found | December | 2018 | 2019Q2 | 2019 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2018-12-15 | Y | 175.2273 | N | 10 | N | Y | 1.1101 | 39.4971 | 11268.4812
[7 empty] | 6980 | 18310 | 1619424 | 2018-12-14 22:16 | 2018-12-15 21:05 | 1369 | 11kV | 114631 | 140 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 189281 2 Fault operations, B and C Phases Pole Mounted RAGCB, Overcurrent Tree brought down 11kV at Pole 8U-60023 | December | 2018 | 2019Q2 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2018-12-14 | N | 818.7929 | N | 25 | Y | Y | 1.1101 | 39.4971 | 83768.9538
[7 empty] | 7117 | 19684 | 1619978 | 2018-12-15 19:18 | 2018-12-15 21:10 | 112 | 11kV | 2800 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | LID 189325 A Phase 10 Amp DOLF Weather or Electrical Storm | December | 2018 | 2019Q2 | 2019 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2018-12-15 | N | 112 | N | 10 | N | N | 1.1101 | 39.4971 | 2046.1574
[7 empty] | 6539 | 13726 | 1619856 | 2018-12-15 18:01 | 2018-12-15 21:20 | 199 | 11kV | 157766 | 914 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 189326 4 fault operations 3 phase Overcurrent LA cut away at sub 43598, replacement required Excluded oms 1619856 | December | 2018 | 2019Q2 | 2019 | 532:83293 | 532:83314 | ZN00532/083314 | MAITLAND | OH | Not Veg | 2018-12-15 | N | 172.6105 | N | 10 | N | N | 1.1101 | 39.4971 | 115290.7395
[7 empty] | 5394 | 739 | 1620004 | 2018-12-15 19:36 | 2018-12-15 21:25 | 109 | 11kV | 63889 | 615 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn2400 Berowra Ex 11kv fdr Panel 11 "Berowra Tollgates" RE1239 Brooklyn tripped on: Relays: OC/IOC lock out Abnormal: beyond LB2423 defective Remarks: cause not ascertained. Mains to patrol in daylight | December | 2018 | 2019Q2 | 2019 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2018-12-15 | Y | 103.8846 | N | 10 | N | Y | 1.1101 | 39.4971 | 46688.1968
[7 empty] | 6834 | 16774 | 1619960 | 2018-12-15 19:03 | 2018-12-15 21:25 | 142 | 11kV | 9446 | 73 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189322 1 fault operation 3 phase Overcurrent; Earth Fault tree cleared near sub 61668 Excluded oms 1619960 | December | 2018 | 2019Q2 | 2019 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2018-12-15 | N | 129.3973 | N | 10 | N | N | 1.1101 | 39.4971 | 6902.8582
[7 empty] | 6320 | 11114 | 1618820 | 2018-12-15 21:13 | 2018-12-15 23:30 | 137 | 11kV | 274 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | Y | LID 189297 Substation DOLF No restore time or fuse size provided. Restore time is estimate ONLY from Incomplete time in OMS Customer reported he saw - storm- lightning hit pole. cylinder on top has sparks flying intermittent. Glowing red | December | 2018 | 2019Q2 | 2019 | 507:80923 | 507:80923 | ZN00507/080923 | CESSNOCK | OH | Not Veg | 2018-12-15 | N | 137 | N | 10 | N | N | 1.1101 | 39.4971 | 200.2311
[7 empty] | 5391 | 686 | 1619995 | 2018-12-15 19:30 | 2018-12-15 23:33 | 243 | 11kV | 310068 | 1276 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn12640 Umina Panel 12 "Oscar West" fdr tripped Relays: A&C Phase IOC, L/O, timing, efi Signals:trip EFI's SS18447 S18127 S18129 Weather related. Patrolled by DOp | December | 2018 | 2019Q2 | 2019 | ZN12640:PA12 | ZN12640:PA12 | ZN12640/000012 | CENTRAL COAST | OH | Veg | 2018-12-15 | Y | 243 | N | 10 | N | Y | 1.1101 | 39.4971 | 226588.5489
[7 empty] | 6217 | 10144 | 1619581 | 2018-12-15 15:56 | 2018-12-15 23:34 | 458 | 11kV | 11394 | 41 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 189309 2 Fault operations ABC 3 phase, Earth Fault Wire on the ground near Pole 9M-90031 | December | 2018 | 2019Q2 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2018-12-15 | N | 277.9024 | N | 10 | N | N | 1.1101 | 39.4971 | 8326.3991
[7 empty] | 6492 | 13207 | 1619603 | 2018-12-15 16:22 | 2018-12-15 23:52 | 450 | 11kV | 450 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Wind Storm | Y | 132KV Feeder'251' from BS18015 Sydney North to Zn965 Pennant Hills including TX1, TX2 and TX3 Tripped 132kV Feeder '253' From S965 Pennant Hills to S847 Hornsby including TX3 Tripped 11kV Panel 48 Opened by Area Operator - due to wide spread damage Contact System Control for Protection Details Cause: Major Rain Wind Storm 132kV Feeder 251 had 2 trees on OH mains 66-70 Victoria Rd | December | 2018 | 2019Q2 | 2019 |  |  |  |  | OH | Veg | 2018-12-15 | Y | 450 | N | 10 | N | Y | 1.1101 | 39.4971 | 328.8467
[7 empty] | 6713 | 15259 | 1619994 | 2018-12-15 19:30 | 2018-12-16 01:05 | 335 | 11kV | 525531 | 1705 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Wind Storm | Y | ZN12640 UMINA 11kV CB PA7 'Berith west' fdr tripped Relays: IOC, L/O, timing SEL, EFI Signals: trip EFI's S18126 S18128 S18136 Cause: weather related. roadisde 31.5 HDO was blown but did not drop. Arrestor cut away at PT11150 See 1619994,24050,1,2,3 | December | 2018 | 2019Q2 | 2019 | ZN12640:PA7 | ZN12640:PA7 | ZN12640/000007 | CENTRAL COAST | OH | Not Veg | 2018-12-15 | Y | 308.2293 | N | 10 | N | Y | 1.1101 | 39.4971 | 384042.5543
[7 empty] | 6913 | 17691 | 1620078 | 2018-12-15 20:09 | 2018-12-16 01:30 | 321 | 11kV | 193532 | 1287 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | S9252 Jannali Panel 30 "Vesta Glenelg" fdr tripped, reclosed, tripped and locked out Relays: A phase IOC, EFI Signals: 11kv trip Remarks: tree brought down 11kv nr PT9540 Jefferson Cres | December | 2018 | 2019Q2 | 2019 | ZN9252:PA30 | ZN9252:PA30 | ZN09252/000030 | SUTHERLAND | OH | Veg | 2018-12-15 | N | 150.3745 | N | 10 | N | N | 1.1101 | 39.4971 | 141427.4774
[7 empty] | 5557 | 2981 | 1620106 | 2018-12-15 20:07 | 2018-12-16 09:35 | 808 | 11kV | 175098 | 1020 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | S10994 Mortdale Panel 21 "Balmoral barris" fdr tripped, reclosed, tripped and locked out. Relays: Earth fault, EFI, lockout Signals: 11kv trip EFI's: S10364 Remarks: tree/branch on OH mains. Large tree branch on 11kv adjacent PT10513 Boronia Woodlands | December | 2018 | 2019Q2 | 2019 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Veg | 2018-12-15 | Y | 171.6647 | N | 10 | N | Y | 1.1101 | 39.4971 | 127956.4539
[7 empty] | 6666 | 14955 | 1619652 | 2018-12-15 16:32 | 2018-12-16 10:20 | 1068 | 11kV | 11228 | 71 | HV | Vegetation Blow/Fall In | Vegetation | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | Y | LB49206 Mangrove Mtn West tripped Abnormal: LB61343 closed, LB61085 open Relays: OC trip, L/O Section of 11kv Panel 3 'Mangrove Mtn' feeder at Zn12630 Peats Ridge Remarks: weather related. Two faults. 1) tree on 11kv between AB43968 and LK 41734 (ref 3E6) 2) 11kv down between LK 41696 and PT11656 Waratah Kelynack No.2 (ref 3E1) | December | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2018-12-15 | Y | 158.1408 | N | 10 | N | Y | 1.1101 | 39.4971 | 8205.0912
[7 empty] | 6745 | 15506 | 1619675 | 2018-12-15 16:47 | 2018-12-16 10:30 | 1063 | 11kV | 136830 | 1486 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | Y | LID 189315 2 fault operation 3 Phase Earth fault Hv crossarm IU-61909 broken HV into Lv into ground. repaired under AP Excluded OMS 1619675 | December | 2018 | 2019Q2 | 2019 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Not Veg | 2018-12-15 | Y | 92.0794 | N | 10 | N | Y | 1.1101 | 39.4971 | 99991.3282
[7 empty] | 5961 | 7033 | 1619986 | 2018-12-15 19:24 | 2018-12-16 11:00 | 936 | 11kV | 615158 | 664 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Somersby Pnl.17 REC48437 Peats Ridge Cooks 1.35 tripped on: O/C Storm See 1624757 1624758 1624759 | December | 2018 | 2019Q2 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2018-12-15 | Y | 926.4428 | N | 10 | N | Y | 1.1101 | 39.4971 | 449539.3223
[7 empty] | 6195 | 9972 | 1620363 | 2018-12-16 04:39 | 2018-12-16 11:05 | 386 | 11kV | 772 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189340 A phase 10 Amp fuse, Substation DOLF | December | 2018 | 2019Q2 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2018-12-16 | Y | 386 | N | 7 | N | Y | 1.1101 | 39.4971 | 564.1548
[7 empty] | 6876 | 17224 | 1619997 | 2018-12-15 19:33 | 2018-12-16 14:00 | 1107 | 11kV | 663925 | 1325 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn14143 Somersby 11kV Panel 12 'Phillips Gindurra' tripped Relays: E/F Signals: trip EFI's: S44663 S65717 S18442 S18171 S18495 S18469 S14646 S12851 S12633 S12909 Cause: weather related. patrolled by DOps See 1619997,20368,3401,6,9 | December | 2018 | 2019Q2 | 2019 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Veg | 2018-12-15 | Y | 501.0755 | N | 10 | N | Y | 1.1101 | 39.4971 | 485176.8075
[7 empty] | 6632 | 14641 | 1620666 | 2018-12-16 13:36 | 2018-12-16 15:26 | 110 | 11kV | 174460 | 1586 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | At ZN35555 Croydon Panel #16 "Feeder has tripped on: Signals: 11kv trip, Relays: 50TN (Definite Time Earth Fault), EFI Remarks: UG fault. 11kv UG feeder fault (Ex.PA16 Zn35555 Croydon) between S7997 Liverpool Frederucj (Sw/A) & S1879 Benalla Elizabeth (Sw/B) | December | 2018 | 2019Q2 | 2019 | ZN35555:PA16 | ZN35555:PA16 | ZN35555/000016 | INNER WEST | UG | Not Veg | 2018-12-16 | Y | 110 | N | 7 | N | Y | 1.1101 | 39.4971 | 127490.2223
[7 empty] | 5401 | 827 | 1620741 | 2018-12-16 15:25 | 2018-12-16 16:01 | 36 | 11kV | 2484 | 69 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | LID 189349 Pole Mounted RAGCB, Note: Reclose was off for other emergency work at the time | December | 2018 | 2019Q2 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2018-12-16 | N | 36 | N | 7 | N | N | 1.1101 | 39.4971 | 1815.2339
[7 empty] | 6412 | 12186 | 1620689 | 2018-12-16 14:03 | 2018-12-16 16:13 | 130 | 11kV | 281673 | 2270 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Previous Storm | Y | At Zn3922 Drummoyne Panel #29 'S8351 Wise Ln Norman' feeder has tripped on: Signals: Zone earth, Tx2 Group Earth, 11kv trip Remarks: UG fault. Section of 11kv Pa29 Ex Zn3922 Drummoyne -11kv UG fault between S5774 Grafton Street East (Sw/B) to S5672 Caronline Lane (Sw/B) to S5576 Cooper Darling (Sw/A) | December | 2018 | 2019Q2 | 2019 | ZN3922:PA29 | ZN3922:PA29 | ZN03922/000029 | INNER WEST | UG | Not Veg | 2018-12-16 | Y | 124.085 | N | 7 | N | Y | 1.1101 | 39.4971 | 205838.3205
[7 empty] | 6940 | 17920 | 1620607 | 2018-12-16 12:01 | 2018-12-16 16:25 | 264 | 11kV | 3432 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | LID 189351 B and C phase substation DOLF | December | 2018 | 2019Q2 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2018-12-16 | N | 264 | N | 7 | N | N | 1.1101 | 39.4971 | 2508.0044
[7 empty] | 6781 | 16090 | 1620747 | 2018-12-16 15:34 | 2018-12-16 16:58 | 84 | 11kV | 29104 | 412 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Wind Storm | Y | LID 189353 Customer reported DW ARCING and CROSS ARM HAS BROKEN CNR RANGE RD & New England H'Way Whittingham | December | 2018 | 2019Q2 | 2019 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2018-12-16 | Y | 70.6408 | N | 7 | N | Y | 1.1101 | 39.4971 | 21268.3448
[7 empty] | 6059 | 8227 | 1620769 | 2018-12-16 15:54 | 2018-12-16 18:00 | 126 | 11kV | 159958 | 1418 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | Ex ZN13000 LAKE MUNMORAH section of 11kV CB PA7 "Summerland Point' fdr RE45061 Chain Valley Bay Mulloway tripped on L/O, O/C trip Cause: tree bronch on 11kV, isolated from LB45069 to LB61695 to AB43527 to AB43528 SW/Tag at LB61695 See 1620769,99,801,4059,61,2,3 | December | 2018 | 2019Q2 | 2019 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2018-12-16 | Y | 112.8054 | N | 7 | N | Y | 1.1101 | 39.4971 | 116892.5884
[7 empty] | 5747 | 5138 | 1620847 | 2018-12-16 16:48 | 2018-12-16 18:55 | 127 | 11kV | 8382 | 66 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 189393 HV Reported Down DW 11kV down. 4-5 spans Edderton Road between Muswellbrook and Denman. Denman end. | December | 2018 | 2019Q2 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2018-12-16 | N | 127 | N | 7 | N | N | 1.1101 | 39.4971 | 6125.3184
[7 empty] | 6637 | 14720 | 1620610 | 2018-12-16 12:34 | 2018-12-16 19:25 | 411 | 11kV | 67781 | 516 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | Y | ZN12620 NORAVILLE 11kV CB PA2 'Budgewoi' tripped, reclosed and locked out on: 11kV OH brought down OH between LK41777 and PT13763 See 1620633,714,4066,7,8,9 | December | 2018 | 2019Q2 | 2019 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Veg | 2018-12-16 | Y | 131.3585 | N | 7 | N | Y | 1.1101 | 39.4971 | 49532.3556
[7 empty] | 6417 | 12271 | 1620803 | 2018-12-16 16:15 | 2018-12-16 19:45 | 210 | 11kV | 222810 | 1061 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 189358 Feeder tripped initially at 1615 hours due to faulty pin insulator Pole OS-20186. Feeder partially restored isolation beyond ABS 19254 and feeder reclose non auto due to switching, at 1859hrs Sw 33413 tripepd again. Secondary event: Following a full feeder patrol a large branch was found on the ground on load side of ABS 46112. Feeder was tried back in section as per switching and supply fully resored at 1945 hours. PD | December | 2018 | 2019Q2 | 2019 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2018-12-16 | Y | 210 | N | 7 | N | Y | 1.1101 | 39.4971 | 162822.9762
[7 empty] | 7150 | 19992 | 1620896 | 2018-12-16 17:54 | 2018-12-16 20:10 | 136 | 11kV | 1224 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189368 10 Amp c phase substation DOLF | December | 2018 | 2019Q2 | 2019 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2018-12-16 | N | 136 | N | 7 | N | N | 1.1101 | 39.4971 | 894.4631
[7 empty] | 6555 | 13856 | 1619982 | 2018-12-15 19:21 | 2018-12-16 20:15 | 1494 | 11kV | 584884 | 1241 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN12660 WOY WOY 11kV CB PA14 'South Woy Woy' fdr tripped Relays: SEF, Timing, L/O Signals: trip Cause: weather related. 11kv down at Pole WW3958. 11kv into LV. 11kV AB40639 to LB43375 tee PT's x4 isolated See 1619982,20332,4070,2,3,7339,41,4 | December | 2018 | 2019Q2 | 2019 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2018-12-15 | Y | 471.3006 | N | 10 | N | Y | 1.1101 | 39.4971 | 427415.976
[7 empty] | 6086 | 8532 | 1620775 | 2018-12-16 16:02 | 2018-12-16 21:30 | 328 | 11kV | 216676 | 1707 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | ZN14892 CHARMHAVEN 11kV CB PA6 "Parkside Pacific" tripped Relays: 'B & C' Phase O/C, SEL, timing, L/O, F/C Signals: 11kv trip EFI's: Cause: OH Down 11kV and LV down. EMSO will be required 11kV isolated from AB44040to LK42002 tee PT14053 Sw/Tage left at LK42002 See 1620775,93,1023,3974,5,6 | December | 2018 | 2019Q2 | 2019 | ZN14892:PA6 | ZN14892:PA6 | ZN14892/000006 | CENTRAL COAST | OH | Not Veg | 2018-12-16 | Y | 126.9338 | N | 7 | N | Y | 1.1101 | 39.4971 | 158340.4299
[7 empty] | 5397 | 755 | 1619554 | 2018-12-15 16:30 | 2018-12-16 21:45 | 1755 | 11kV | 385659 | 738 | HV | Lightning Strike | Adverse Weather/Environment | Insulator | Unplanned | Electrical Storm | Y | LID 189374 Pole Mounted RAGCB, Sensitive Earth Fault Replaced B Ph Insulator 47482 plus DOLf SUB 26646 | December | 2018 | 2019Q2 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2018-12-15 | Y | 522.5732 | N | 10 | N | Y | 1.1101 | 39.4971 | 281828.2222
[7 empty] | 5635 | 3847 | 1620844 | 2018-12-16 16:46 | 2018-12-16 22:40 | 354 | 11kV | 1062 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189375 single phase 10 Amp fuse substation dolf | December | 2018 | 2019Q2 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2018-12-16 | N | 354 | N | 7 | N | N | 1.1101 | 39.4971 | 776.0783
[7 empty] | 6440 | 12597 | 1620809 | 2018-12-16 16:25 | 2018-12-16 23:25 | 420 | 11kV | 85680 | 362 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | Y | At ZN10994 Mortdale Panel #8L 'Blackshaw Ave" feeder has tripped & locked out on: Signals: 11kv trip Relays: Earth fault, EFI, lockout Field EFI's: nil Remarks: insulator failed. Strain insulator failed @ HV pole on the corner of Blackshaw Ave & Oates causing HV to sag into LV mains & LV mid span pole | December | 2018 | 2019Q2 | 2019 | ZN10994:PA8 | ZN10994:PA8 | ZN10994/000008 | GEORGES RIVER | OH | Not Veg | 2018-12-16 | N | 236.6851 | N | 7 | N | N | 1.1101 | 39.4971 | 62612.4169
[7 empty] | 5801 | 5559 | 1620997 | 2018-12-16 20:07 | 2018-12-16 23:40 | 213 | 11kV | 639 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 189380 10 amp fuse, substation DOLF Blown Lightning arrestor | December | 2018 | 2019Q2 | 2019 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2018-12-16 | N | 213 | N | 7 | N | N | 1.1101 | 39.4971 | 466.9624
[7 empty] | 5725 | 4996 | 1621093 | 2018-12-16 22:50 | 2018-12-16 23:50 | 60 | 11kV | 1140 | 19 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | Y | LID 189379 Broken Live Line Lead from OHM at sub 25148 No OMS job call from Hunter Water | December | 2018 | 2019Q2 | 2019 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2018-12-16 | Y | 60 | N | 7 | N | Y | 1.1101 | 39.4971 | 833.0784
[7 empty] | 6553 | 13847 | 1621033 | 2018-12-16 21:03 | 2018-12-17 02:50 | 347 | 11kV | 214093 | 689 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 189373 Tree on 11kV at Pole NR-60508 at this site. Mains damaged and need repair before energization. Delayed restoration due to: This outage was not visible to the Control Room due to a Communication Failure to the Lemon Tree Passage Intellirupter since 8/2/18. Can someone please investigate repairing the comm's fault as the lack of Comm's delayed Ausgrid's response. Also note there has been a comm's failure to Sw 82285 Kenneth Parade IR since Novenbver 2018. Both comm's failures and failure to to repair delayed the identification of the 1kv outage and then delayed the restoration of the outage. | December | 2018 | 2019Q2 | 2019 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2018-12-16 | Y | 310.73 | N | 7 | N | Y | 1.1101 | 39.4971 | 156452.8497
[7 empty] | 6196 | 9991 | 1619653 | 2018-12-15 16:31 | 2018-12-17 03:00 | 2069 | 11kV | 15066 | 67 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Peats Ridge Pnl.8 REC44994 mangrove Creek tripped on: O/C Tree brought down 11kV after LK44006 See 1624413 1624414 1624415 1624416 1624417 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2018-12-15 | Y | 224.8657 | N | 10 | N | Y | 1.1101 | 39.4971 | 11009.7884
[7 empty] | 6617 | 14530 | 1620859 | 2018-12-16 17:01 | 2018-12-17 03:35 | 634 | 11kV | 2536 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | Ex Zn12630 Peats Ridge section of Panel 1 PT12262 Peats Ridge Brieses 11kv 16Amp HDO operated Cause: not ascertained See 1623273 ex 1620859 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2018-12-16 | Y | 634 | N | 7 | N | Y | 1.1101 | 39.4971 | 1853.234
[7 empty] | 5614 | 3677 | 1619606 | 2018-12-15 16:17 | 2018-12-17 03:54 | 2137 | 11kV | 794964 | 372 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn35370 Galston - Pnl.2 tripped, reclosed, tripped & locked out. Lightning | December | 2018 | 2019Q2 | 2019 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2018-12-15 | Y | 2137 | Y | 10 | N | Y | 1.1101 | 39.4971 | 580936.2437
[7 empty] | 6564 | 13935 | 1621146 | 2018-12-17 05:32 | 2018-12-17 08:15 | 163 | 11kV | 163 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 189388 C phase 10 Amp fuse, substatin DOLF Distribution Transformer | December | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-12-17 | N | 163 | N | 11 | N | N | 1.1101 | 39.4971 | 119.1156
[7 empty] | 6100 | 8786 | 1621206 | 2018-12-17 08:35 | 2018-12-17 09:06 | 31 | 11kV | 3175 | 121 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 189384 - job 3 A phase ABS 26171 on fire, also refer T&R 1623120 and 1623121 | December | 2018 | 2019Q2 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2018-12-17 | N | 26.2397 | N | 11 | N | N | 1.1101 | 39.4971 | 2320.1964
[7 empty] | 5581 | 3325 | 1621170 | 2018-12-17 07:57 | 2018-12-17 09:10 | 73 | 11kV | 13155 | 285 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | LID 189383 Hazemeyer blown up in kiosk 24385 Ghilgai Ave | December | 2018 | 2019Q2 | 2019 | 502:48004 | 502:48004 | ZN00502/048004 | MAITLAND | UG | Not Veg | 2018-12-17 | N | 46.1579 | N | 11 | N | N | 1.1101 | 39.4971 | 9613.286
[7 empty] | 5539 | 2621 | 1621202 | 2018-12-17 07:57 | 2018-12-17 09:20 | 83 | 11kV | 166 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 189391 C Phase 10 Amp fuse substation DOLF | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-12-17 | N | 83 | N | 11 | N | N | 1.1101 | 39.4971 | 121.3079
[7 empty] | 6416 | 12249 | 1621153 | 2018-12-17 06:08 | 2018-12-17 09:35 | 207 | 11kV | 414 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 189385 10 Amp fuse, substation DOLF Note: checked DC all calls began on the 17th | December | 2018 | 2019Q2 | 2019 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2018-12-17 | N | 207 | N | 11 | N | N | 1.1101 | 39.4971 | 302.539
[7 empty] | 6005 | 7688 | 1619595 | 2018-12-15 16:24 | 2018-12-17 10:25 | 2521 | 11kV | 1134450 | 450 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn35370 Galston - Pnl.8 tripped, reclosed, tripped & locked out on: C phase O/C Abnormal: AB35252 open with LB62159 Closed Lightning and Branches | December | 2018 | 2019Q2 | 2019 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2018-12-15 | Y | 2521 | Y | 10 | N | Y | 1.1101 | 39.4971 | 829022.5994
[7 empty] | 6256 | 10475 | 1620120 | 2018-12-15 20:17 | 2018-12-17 11:00 | 2323 | 11kV | 6958 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At ZN9700 Kirrawee ex Panel 20 "Cook Glencoe Nth" fdr Rec 35006 National Park tripped, reclosed, tripped and locked out on OC trip, lockout Remarks: OH down. Section of Pa20 Kirrawee: 11kv feeder isolated from Rec35006 to 35970 tee PT9008 Farnell Ave due to 11kv wires down. Full feeder beyond rec35006 National park still to be patrolled | December | 2018 | 2019Q2 | 2019 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2018-12-15 | Y | 2319.3333 | N | 10 | N | Y | 1.1101 | 39.4971 | 5084.7012
[7 empty] | 5753 | 5178 | 1619681 | 2018-12-15 16:48 | 2018-12-17 11:43 | 2575 | 11kV | 291652 | 117 | HV | Vegetation Blow/Fall In | Vegetation | Pole | Unplanned | Rain Wind Storm | Y | Ex Peats Ridge P1 - iR61097 Wise Ferry Lavender 10.2 tripped @ 16:48 (15/12) -AB44155 interrupted by DOp @ 1:26 (16/12) -REC45189 Cooks Peats Ridge 0.5 tripped @ 1:30 (16/12) Storm - Pole damaged between AB44155 and USL43316 tee PT13487 plus other weather related activity along feeder, Reports of trees bringing down wires See 1624367 1624368 1624369 1624370 1624372 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2018-12-15 | Y | 2492.7521 | N | 10 | N | Y | 1.1101 | 39.4971 | 213130.6793
[7 empty] | 6055 | 8199 | 1620686 | 2018-12-16 01:30 | 2018-12-17 11:54 | 2064 | 11kV | 216720 | 105 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Peats Ridge P1 -REC45189 Cooks Peats Ridge 0.5 tripped @ 1:30 (16/12) - iR61097 Wise Ferry Lavender 10.2 tripped @ 16:48 (15/12) -AB44155 interrupted by DOp @ 1:26 (16/12) Storm - Pole damaged between AB44155 and USL43316 tee PT13487 plus other weather related activity along feeder See 1624367 1624368 1624369 1624370 1624372 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2018-12-16 | Y | 2064 | N | 7 | N | Y | 1.1101 | 39.4971 | 158372.5838
[7 empty] | 6200 | 10019 | 1620060 | 2018-12-15 23:00 | 2018-12-17 12:25 | 2245 | 11kV | 17960 | 8 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | PT12730 Greta Hunts 0.3 isolated from LK43080 Mains down - restored with PT12098 See 1624419 1624420 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2018-12-15 | Y | 2245 | N | 10 | N | Y | 1.1101 | 39.4971 | 13124.6383
[7 empty] | 6947 | 17996 | 1621070 | 2018-12-16 21:47 | 2018-12-17 12:30 | 883 | 11kV | 7947 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | SYS OP DESK 2. BLOWN 10A 'C' PHASE DOLF AT PT SUB 5195. FUSE REPLACED. SUPPLY RESTORED AT 1230HRS 17/12/18. VOLTS AFTER RESTORATION - 242V, 242V, 243V (ABC). CURRENT AFTER RESTORATION - 32A, 22A, 8A (ABC). VISITED CUSTOMER'S PREMISES AFTER RESTORATION AND CUSTOMER STATED ALL WAS NOW OK. Note: no LID report raised | December | 2018 | 2019Q2 | 2019 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2018-12-16 | Y | 883 | Y | 7 | N | Y | 1.1101 | 39.4971 | 5807.4332
[7 empty] | 5719 | 4965 | 1621447 | 2018-12-17 12:24 | 2018-12-17 14:20 | 116 | 11kV | 43359 | 386 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zb187 Crows Nest - Pnl.23 tripped on: O/C trip A Phase Field EFIs; S6876 UG cable fault between S6876 Sw/A and S3173 Sw/B See 1624003 1624004 | December | 2018 | 2019Q2 | 2019 | ZN187:PA23 | ZN187:PA23 | ZN00187/000023 | LANE COVE | UG | Not Veg | 2018-12-17 | N | 112.329 | N | 11 | N | N | 1.1101 | 39.4971 | 31685.4783
[7 empty] | 6066 | 8304 | 1621488 | 2018-12-17 14:01 | 2018-12-17 15:15 | 74 | 11kV | 8444 | 115 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 189396 section isolated to remove tree branch from OHM COREY URBAN TREE SOLUTIONS ARBORIST COREY URBAN TREE SOLUTONS BRANCH HAS HIT HV POWERLINES BRANCH FELL NEED AUSGRID TO ISOLATE POWER CLOSE TO LV CORDED OFF AREA TRUCK AND TOOLS UNDER AFFECTED WIRES. NO18 STILL HAS SUPPLY NO INJURIES | December | 2018 | 2019Q2 | 2019 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Veg | 2018-12-17 | N | 73.4261 | N | 11 | N | N | 1.1101 | 39.4971 | 6170.6261
[7 empty] | 7096 | 19548 | 1624370 | 2018-12-17 16:15 | 2018-12-17 16:20 | 5 | 11kV | 1470 | 294 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Peats Ridge P1 Storm - Pole damaged between AB44155 and USL43316 tee PT13487 plus other weather related activity along feeder See 1624367 1624368 1624369 1624370 1624372 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2018-12-17 | N | 5 | N | 11 | N | N | 1.1101 | 39.4971 | 1074.2326
[7 empty] | 6608 | 14422 | 1620679 | 2018-12-16 01:26 | 2018-12-17 16:30 | 2344 | 11kV | 410395 | 196 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Peats Ridge P1 -AB44155 interrupted by DOp @ 1:26 (16/12) -REC45189 Cooks Peats Ridge 0.5 tripped @ 1:30 (16/12) Storm - Pole damaged between AB44155 and USL43316 tee PT13487 plus other weather related activity along feeder Also see previous job OMS 1624368- iR61097 Wise Ferry Lavender 10.2 tripped @ 16:48 (15/12) See 1624367 1624368 1624369 1624370 1624372 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2018-12-16 | Y | 2093.852 | N | 7 | N | Y | 1.1101 | 39.4971 | 299904.5614
[7 empty] | 7138 | 19855 | 1621617 | 2018-12-17 16:15 | 2018-12-17 17:00 | 45 | 11kV | 225 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189400 C Phase 10 Amp fuse, substation DOLF | December | 2018 | 2019Q2 | 2019 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2018-12-17 | N | 45 | N | 11 | N | N | 1.1101 | 39.4971 | 164.4234
[7 empty] | 5356 | 202 | 1621513 | 2018-12-17 13:54 | 2018-12-17 18:01 | 247 | 11kV | 135694 | 901 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 189397 3 Fault operations, pole mounted RAGCB Tree on OHM, pole VP-30138 | December | 2018 | 2019Q2 | 2019 | 243:80081 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | OH | Veg | 2018-12-17 | N | 150.6038 | N | 11 | N | N | 1.1101 | 39.4971 | 99161.1729
[7 empty] | 6239 | 10337 | 1620664 | 2018-12-16 12:15 | 2018-12-17 18:30 | 1815 | 11kV | 85305 | 47 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | All details based on customer calls - See OMS 1628259 1620664 1620968 132KV Feeder'251' from BS18015 Sydney North to Zn965 Pennant Hills including TX1, TX2 and TX3 Tripped 132kV Feeder '253' From S965 Pennant Hills to S847 Hornsby including TX3 Tripped 11kV Panel 42 Opened by Area Operator - due to wide spread damage Contact System Control for Protection Details Cause: Major Rain Wind Storm 132kV Feeder 251 had 2 trees on OH mains 66-70 Victoria Rd | December | 2018 | 2019Q2 | 2019 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | OH | Not Veg | 2018-12-16 | Y | 1815 | N | 7 | N | Y | 1.1101 | 39.4971 | 62338.3779
[7 empty] | 5392 | 698 | 1621639 | 2018-12-16 09:00 | 2018-12-17 18:30 | 2010 | 11kV | 10050 | 5 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Previous Storm | Y | LID 189404 C Phase 10 Amp Previous lightning damage | December | 2018 | 2019Q2 | 2019 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2018-12-16 | Y | 2010 | N | 7 | N | Y | 1.1101 | 39.4971 | 7344.2436
[7 empty] | 6222 | 10191 | 1619669 | 2018-12-15 16:22 | 2018-12-17 20:20 | 3118 | 11kV | 2286753 | 1297 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | 132KV Feeder'251' from BS18015 Sydney North to Zn965 Pennant Hills including TX1, TX2 and TX3 Tripped 132kV Feeder '253' From S965 Pennant Hills to S847 Hornsby including TX3 Tripped 11kV Panel 42 Opened by Area Operator - due to wide spread damage Contact System Control for Protection Details Cause: Major Rain Wind Storm 132kV Feeder 251 had 2 trees on OH mains 66-70 Victoria Rd | December | 2018 | 2019Q2 | 2019 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Not Veg | 2018-12-15 | Y | 1763.1095 | Y | 10 | N | Y | 1.1101 | 39.4971 | 1671091.6446
[7 empty] | 5678 | 4384 | 1621729 | 2018-12-17 19:21 | 2018-12-18 01:50 | 389 | 11kV | 15303 | 115 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Panel 2 "Holgate" fdr 11kV RE41020 WAttle tree Rd North tripped Relays: O/C trip, E/F, L/O Cause: Tree/branch borught down OH. HV into LV. Section of 11kv fdr from LB45816 to LB45815 See 1622103,4 ex 162172932,6,47,58,85,6 | December | 2018 | 2019Q2 | 2019 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2018-12-17 | N | 133.0696 | N | 11 | N | N | 1.1101 | 39.4971 | 11182.981
[7 empty] | 5702 | 4676 | 1619706 | 2018-12-15 17:04 | 2018-12-18 02:25 | 3441 | 11kV | 203019 | 59 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | All details based on customer calls | December | 2018 | 2019Q2 | 2019 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | PARRAMATTA | OH | Veg | 2018-12-15 | Y | 3441 | N | 10 | N | Y | 1.1101 | 39.4971 | 148360.2972
[7 empty] | 6619 | 14544 | 1620807 | 2018-12-16 16:18 | 2018-12-18 03:10 | 2092 | 11kV | 53451 | 212 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | 11kv Rec45035 Mangrove Mtn tripped Relays: E/F trip, L/O Section of 11kv Panel 3 "Mangrove Mtn" at Zn12630 Peats Ridge Abnormal: R.46935 is open, LB47448 Closed, LB61085 Open, LB61343 closed Remarks: OH down. 11kv down across rd beyond Auto links 46938 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2018-12-16 | Y | 252.1274 | N | 7 | N | Y | 1.1101 | 39.4971 | 39060.4143
[7 empty] | 6760 | 15690 | 1621872 | 2018-12-18 08:26 | 2018-12-18 10:21 | 115 | 11kV | 345 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 189415 single phase 10 Amp substation DOLF | December | 2018 | 2019Q2 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2018-12-18 | N | 115 | N | 9 | N | N | 1.1101 | 39.4971 | 252.1158
[7 empty] | 6744 | 15502 | 1621842 | 2018-12-18 07:57 | 2018-12-18 10:30 | 153 | 11kV | 66227 | 2342 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 189411 1 Fault operations Phase B Earth Fault Permits were left and emergency switching on Desk 2. Section of UG cable failed at 11kv UGOH on pole OR-67262.UGOH REQUIRES REPAIRS and will be left isolated. Note SI 31172 was being performed and feeder abnormal with Sw 36472 closed and ABS 7399 open. | December | 2018 | 2019Q2 | 2019 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | Unknown | Unknown | 2018-12-18 | N | 28.278 | N | 9 | N | N | 1.1101 | 39.4971 | 48396.7382
[7 empty] | 6042 | 8064 | 1620175 | 2018-12-15 16:13 | 2018-12-18 13:05 | 4132 | 11kV | 2880801 | 1037 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn35370 Galston - Pnl.4 tripped, reclosed, tripped & locked out on: B & C phase IOC Abnormal: AB3252 Open with LB62159 Closed Lightning Strike. PT627 Tree on Mains See1624143 1624144 1624147 1624148 1624149 1624150 1624150 1624151 1624152 1624153 16241554 | December | 2018 | 2019Q2 | 2019 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2018-12-15 | Y | 2778.0145 | Y | 10 | N | Y | 1.1101 | 39.4971 | 2105204.4016
[7 empty] | 6374 | 11740 | 1621900 | 2018-12-18 10:11 | 2018-12-18 13:06 | 175 | 11kV | 46200 | 264 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN15013 TERREY HILLS section of 11kV CB PA10 'Terrey Hills' Fdr From RE1126 Mona Vale Rd to defective AB20129 has been interrupted to remove a fallen tree resting on 11kv jsut after AB26207 Abnormal: AB20129 open defective with IS21573 closed AB26207 open and defective with AB25114 closed, LB20518 closed (won't open) defective with LB77332 open Cause: tree/branch on OH mains. Interrutped to remove a fallen tree resting on 11kV just after AB26207 | December | 2018 | 2019Q2 | 2019 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2018-12-18 | N | 175 | N | 9 | N | N | 1.1101 | 39.4971 | 33761.5973
[7 empty] | 5757 | 5213 | 1622027 | 2018-12-18 11:44 | 2018-12-18 14:15 | 151 | 11kV | 453 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Previous Storm | N | LID 189424 Repair burnt of Live Line lead at Merrindal Park sub, 73061 | December | 2018 | 2019Q2 | 2019 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2018-12-18 | N | 151 | N | 9 | N | N | 1.1101 | 39.4971 | 331.039
[7 empty] | 5408 | 924 | 1621944 | 2018-12-18 10:00 | 2018-12-18 14:19 | 259 | 11kV | 518 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Previous Storm | N | LID 189423 Replaced blown L/A at sub 52291 | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2018-12-18 | N | 259 | N | 9 | N | N | 1.1101 | 39.4971 | 378.5391
[7 empty] | 7070 | 19344 | 1621903 | 2018-12-18 09:04 | 2018-12-18 14:40 | 336 | 11kV | 672 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 189426 A Phase Broken Live Live Lead at top of DOLF. Repaired with heatshrink applied to all three leads. | December | 2018 | 2019Q2 | 2019 | 512:83732 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2018-12-18 | N | 336 | N | 9 | N | N | 1.1101 | 39.4971 | 491.0778
[7 empty] | 6630 | 14625 | 1620647 | 2018-12-15 17:11 | 2018-12-18 15:50 | 4239 | 11kV | 372062 | 488 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn847 Hornsby - Pnl.45 tripped on: ABC O/C Field EFIs: S8760 3 bays of mains down between S8760 and LB63746 tee PT2086 See 1624233 1624234 1624235 1624236 | December | 2018 | 2019Q2 | 2019 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2018-12-15 | Y | 762.4221 | Y | 10 | N | Y | 1.1101 | 39.4971 | 271891.9356
[7 empty] | 6518 | 13583 | 1619983 | 2018-12-15 19:13 | 2018-12-18 17:00 | 4187 | 11kV | 356093 | 323 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12630 Peats Ridge - Pnl.10 tripped on: A & B phase IOC 4 bays on 11kV OH mains down (HV into LV) between LB64355 to LB44187 11kV down beyond LB44814 11kV down beyond LB49809 See 1624727 1624730 1624731 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2018-12-15 | Y | 1102.4551 | N | 10 | N | Y | 1.1101 | 39.4971 | 260222.2614
[7 empty] | 5561 | 3038 | 1620886 | 2018-12-16 16:19 | 2018-12-18 17:15 | 2936 | 11kV | 1244285 | 698 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | Y | REC3282 Alberta Avenue - tripped, reclosed & locked out on: O/C **REC1239 Brooklyn tripped numerous times when trying back CP46854 UGOH fault - storm damage See 1624213 1624216 1624217 1624219 | December | 2018 | 2019Q2 | 2019 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | Unknown | Unknown | 2018-12-16 | Y | 1782.6433 | N | 7 | N | Y | 1.1101 | 39.4971 | 909286.7778
[7 empty] | 5710 | 4783 | 1622178 | 2018-12-18 16:58 | 2018-12-18 19:10 | 132 | 11kV | 132 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 189432 B Phase 10 Amp fuse substation DOLF No Cause Found, not storm conditions | December | 2018 | 2019Q2 | 2019 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2018-12-18 | N | 132 | N | 9 | N | N | 1.1101 | 39.4971 | 96.4617
[7 empty] | 7013 | 18637 | 1622199 | 2018-12-18 18:30 | 2018-12-18 19:45 | 75 | 11kV | 75 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 189434 C Phase 10 Amp fuse Substation DOLF no cause found not storm conditions | December | 2018 | 2019Q2 | 2019 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2018-12-18 | N | 75 | N | 9 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 5476 | 1653 | 1624374 | 2018-12-16 15:24 | 2018-12-18 19:50 | 3146 | 11kV | 77192 | 52 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Pnl.1 Peats Ridge REC44945 Lower Mangrove tripped Tree branch brought down OH mains See 1624374 1624375 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2018-12-16 | Y | 1484.4615 | N | 7 | N | Y | 1.1101 | 39.4971 | 56409.6368
[7 empty] | 7129 | 19776 | 1622208 | 2018-12-18 19:15 | 2018-12-18 20:34 | 79 | 11kV | 92721 | 1215 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN2466 Flemington Panel 41 'Parramatta Alban' tripped Relays: IOC on C phase, EFI Signals: 11kv trip Remarks: UG fault. Front line feeder fault from Zn2466 Flemington Panel 41 to S7703 Parramatta Alban to S7238 Adderley Day to S4799 Olypic Stadium | December | 2018 | 2019Q2 | 2019 | ZN2466:PA41 | ZN36000:PA24 | ZN36000/000024 | CUMBERLAND | UG | Not Veg | 2018-12-18 | N | 76.3136 | N | 9 | N | N | 1.1101 | 39.4971 | 67757.772
[7 empty] | 6753 | 15608 | 1622239 | 2018-12-19 00:40 | 2018-12-19 02:10 | 90 | 11kV | 48498 | 683 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | ZN15001 BROOKVALE 11kV CB PA8 'Windbourne Rd' fdr tripped on: Relays: Earth Fault with overcurrent and fault check Signals: 11kv trip EFI's Panel 8 to S16821 Cause: animals/birds. possum at UGOH between LB25282 and S15581 See 1622239,4103,4,5,6 | December | 2018 | 2019Q2 | 2019 | ZN15001:PA8 | ZN15001:PA8 | ZN15001/000008 | NORTHERN BEACHES | OH | Not Veg | 2018-12-19 | N | 71.0073 | N | 13 | N | N | 1.1101 | 39.4971 | 35440.908
[7 empty] | 5611 | 3644 | 1622247 | 2018-12-19 06:28 | 2018-12-19 08:05 | 97 | 11kV | 2813 | 29 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 189461 no further details provided | December | 2018 | 2019Q2 | 2019 | 512:83732 | 512:83736 | ZN00512/083736 | CESSNOCK | OH | Veg | 2018-12-19 | N | 97 | N | 13 | N | N | 1.1101 | 39.4971 | 2055.6574
[7 empty] | 5526 | 2436 | 1622385 | 2018-12-19 11:03 | 2018-12-19 13:41 | 158 | 11kV | 158 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 189448 C Phase 20 Amp substation DOLF | December | 2018 | 2019Q2 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2018-12-19 | N | 158 | N | 13 | N | N | 1.1101 | 39.4971 | 115.4617
[7 empty] | 6443 | 12607 | 1622355 | 2018-12-19 10:12 | 2018-12-19 13:45 | 213 | 11kV | 426 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 189449 B and C phase 5 Amp fuse | December | 2018 | 2019Q2 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2018-12-19 | N | 213 | N | 13 | N | N | 1.1101 | 39.4971 | 311.3082
[7 empty] | 7126 | 19725 | 1619974 | 2018-12-15 19:13 | 2018-12-19 19:30 | 5777 | 11kV | 46216 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | At ZN12630 peats Ridge Panel 3 "Manrove Mountain' Feeder has tripped Signals: 11kv trip Relays: 'A' & 'B' phase IOC Abnormal: LK44115 open (suspect it might be LB61085 instead), LB61343 closed Remarks: weather related. See AP at LB44889 Note: Due to Network faults, these customers are at the very end of what is now a radial feed. Volts are low. Region advises the fault on Panel 3 will be ready late afternoon Tuesday. | December | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2018-12-15 | Y | 5777 | N | 10 | N | Y | 1.1101 | 39.4971 | 33773.2897
[7 empty] | 5456 | 1463 | 1622599 | 2018-12-19 19:05 | 2018-12-19 20:05 | 60 | 11kV | 6600 | 110 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189457 B and C phase 31 Amp fuse Line DOLF | December | 2018 | 2019Q2 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2018-12-19 | N | 60 | N | 13 | N | N | 1.1101 | 39.4971 | 4823.0853
[7 empty] | 5407 | 903 | 1622572 | 2018-12-19 17:49 | 2018-12-19 21:10 | 201 | 11kV | 402 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189458 10 Amp Fuse substation DOLF | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-12-19 | N | 201 | N | 13 | N | N | 1.1101 | 39.4971 | 293.7697
[7 empty] | 6955 | 18074 | 1622601 | 2018-12-19 19:05 | 2018-12-19 21:29 | 144 | 11kV | 112552 | 1023 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At Zn965 Pennant Hills Panel 43 tripped on Relays: OC, EF and EFI Signals: 11kV Trip, Zone Earth TX2 Group Earth. UG cable fault S3205 Silver Akoonah to S5296 to S6712 See OMS 1625130 1625131 1622601 | December | 2018 | 2019Q2 | 2019 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | UG | Not Veg | 2018-12-19 | N | 110.0215 | N | 13 | N | N | 1.1101 | 39.4971 | 82249.6819
[7 empty] | 5841 | 5830 | 1619599 | 2018-12-15 16:17 | 2018-12-19 21:30 | 6073 | 11kV | 1413146 | 506 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn35370 Galston - Pnl.10 tripped, reclosed, tripped and locked out on: A & B phase IOC Lightning strike beyond LB62156 See1624165 1624166 1624168 1624169 1624170 1624171 1624173 1624174 1624175 | December | 2018 | 2019Q2 | 2019 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2018-12-15 | Y | 2792.7787 | Y | 10 | N | Y | 1.1101 | 39.4971 | 1032685.416
[7 empty] | 5812 | 5629 | 1622650 | 2018-12-19 20:06 | 2018-12-19 22:55 | 169 | 11kV | 338 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189465 B Phase 10 Amp fuse, substation DOLF | December | 2018 | 2019Q2 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2018-12-19 | N | 169 | N | 13 | N | N | 1.1101 | 39.4971 | 247.0004
[7 empty] | 6886 | 17410 | 1622616 | 2018-12-19 19:36 | 2018-12-20 00:38 | 301.9833 | 11kV | 80664.85 | 268 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Wind Storm | N | iR50015 Quarry Old Northern - tripped on: O/C REC3280 Hunt Ave - tripped on O/C Abnormal: LB62157 (feeder in a ring) Lightning arrestor failed at PT2175 - 2 x 16A HDOs blown See 1622658 1622618 | December | 2018 | 2019Q2 | 2019 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2018-12-19 | N | 300.9882 | N | 13 | N | N | 1.1101 | 39.4971 | 58947.4932
[7 empty] | 6757 | 15651 | 1623099 | 2018-12-19 20:20 | 2018-12-20 00:50 | 270 | 11kV | 1890 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189470 ABC, 20 Amp fuses Line DOLF No oms job, linesman found blown on way to another job | December | 2018 | 2019Q2 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2018-12-19 | N | 270 | N | 13 | N | N | 1.1101 | 39.4971 | 1381.1563
[7 empty] | 7057 | 19184 | 1622585 | 2018-12-19 18:16 | 2018-12-20 01:32 | 436 | 11kV | 12546 | 46 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 189463 SW 60976 - 3 Fault operations, A phase, Overcurrent, Vegetation on OHM SW 75099 - 6 Fault operations, Earth Fault, Pole Mounted RAGCB, HV reported down, near ABS 49106 LID 189471 B Phase 100 Amp Substation - DOLF 70832:LV 19/12/2018 19:02:00 to 19/12/2018 21:00:00 Isolated fallen private LV mains and replaced LVF, supply returned when SW60976 restored | December | 2018 | 2019Q2 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2018-12-19 | N | 272.7391 | N | 13 | N | N | 1.1101 | 39.4971 | 9168.2468
[7 empty] | 6774 | 15869 | 1622596 | 2018-12-19 19:18 | 2018-12-20 02:22 | 424 | 11kV | 39516 | 109 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 189472 4 Fault operations, Earth Fault pole Mounted RAGCB HV Reported down Repaired main on ground at pole CI-90184 | December | 2018 | 2019Q2 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2018-12-19 | N | 362.5321 | N | 13 | N | N | 1.1101 | 39.4971 | 28877.1273
[7 empty] | 6397 | 11973 | 1622717 | 2018-12-20 02:01 | 2018-12-20 03:32 | 91 | 11kV | 161092 | 2001 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | ZN14892 CHARMHAVEN 11kV CB PA16 "Charmhaven San Remo" tripped and reclosed and tripped on: Signals: 11kv trip, Zone Earth, Tx2 Group Earth Relays: 51N, E/F, timing, lockout, fault check Tx2 B Prot Earth Fault Check EFI: Pa16 S12884 S46911 Cause: Ug Fault between S12884, S14548 & S46911 See 1622717,3989,91 | December | 2018 | 2019Q2 | 2019 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | UG | Not Veg | 2018-12-20 | Y | 80.5057 | N | 8 | N | Y | 1.1101 | 39.4971 | 117721.2822
[7 empty] | 6739 | 15473 | 1622813 | 2018-12-20 08:11 | 2018-12-20 09:54 | 103 | 11kV | 73935 | 903 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | Zn9700 Campbell St - Pnl.15 tripped on: O/C and E/F Abnormal: S3722 Sw/B closed with S1358 Open UG cable fault in front line section of feeder See 1623118 1623931 | December | 2018 | 2019Q2 | 2019 | ZN7900:PA7 | ZN7900:PA7 | ZN07900/000007 | SYDNEY | UG | Not Veg | 2018-12-20 | N | 81.8771 | N | 8 | N | N | 1.1101 | 39.4971 | 54029.5173
[7 empty] | 5631 | 3811 | 1622859 | 2018-12-20 09:30 | 2018-12-20 10:30 | 60 | 11kV | 1140 | 19 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | Y | LID 189493 Conductor on X-arm pole 3H-80074 Excluded OMS 1622807 | December | 2018 | 2019Q2 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2018-12-20 | Y | 60 | N | 8 | N | Y | 1.1101 | 39.4971 | 833.0784
[7 empty] | 6109 | 8950 | 1622793 | 2018-12-20 07:31 | 2018-12-20 10:30 | 179 | 11kV | 179 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 189505 Single phase DOLF : 10 Amp Excluded OMS 1622793 | December | 2018 | 2019Q2 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2018-12-20 | Y | 179 | N | 8 | N | Y | 1.1101 | 39.4971 | 130.8079
[7 empty] | 7132 | 19788 | 1622852 | 2018-12-20 09:22 | 2018-12-20 11:40 | 138 | 11kV | 138 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 189497 A Phase DOLF : 10 Amp Excluded OMS 1622852 | December | 2018 | 2019Q2 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2018-12-20 | Y | 138 | N | 8 | N | Y | 1.1101 | 39.4971 | 100.8463
[7 empty] | 7077 | 19399 | 1626510 | 2018-12-19 17:55 | 2018-12-20 11:49 | 1074 | 11kV | 60144 | 56 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 189504 4 fault operations mains on xarm at 4I-10003, 4H-70068, 4I-10005, 4h-70058. Branch on mains 4H-40037 Excluded OMS 1622575, 1622589, 1622702, 1622699 | December | 2018 | 2019Q2 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2018-12-19 | N | 1074 | Y | 13 | N | Y | 1.1101 | 39.4971 | 43951.4613
[7 empty] | 6828 | 16674 | 1622754 | 2018-12-20 11:38 | 2018-12-20 12:00 | 22 | 11kV | 5808 | 264 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | Y | Ex ZN15013 TERREY HILLS section of 11kV CB PA10 RE1126 Mona Vale Rd tripped and reclsoed Relays: OC trip, IOC trip @PT15031 HDO operated 16amp roadside Abnormal: At time of fialure DOp was trying back HDO @ PT15031 Failed attempt to tryback HDO @ PT15031 Bahi Templ, PT was placed in LV// via LK19697, region to follow up defective Tx or Las See 1622754,4133 | December | 2018 | 2019Q2 | 2019 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | UG | Not Veg | 2018-12-20 | N | 22 | N | 8 | N | N | 1.1101 | 39.4971 | 4244.3151
[7 empty] | 6439 | 12576 | 1622708 | 2018-12-19 22:39 | 2018-12-20 12:00 | 801 | 11kV | 2403 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 189498 Replace arrestors DOLF : 10 Amp Excluded OMS 1622708 | December | 2018 | 2019Q2 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2018-12-19 | N | 801 | Y | 13 | N | Y | 1.1101 | 39.4971 | 1756.0415
[7 empty] | 6154 | 9446 | 1622696 | 2018-12-19 22:03 | 2018-12-20 13:24 | 921 | 11kV | 1842 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 189494 C Phase DOLF 20/12/18 13:29 t44403: Supply back on 1324. 20/12/18 11:01 t44403: Cindy Wilks arranging staff 20/12/18 10:36 CASS: Blown C phase DOLF at Sub 64636. Blown C phase HV arrestor. Open Remove & DT LVF's 64636. Open Remove & DT DOLF's 64636. Please have O/H crew attend to replace blown HV arrestor and re-energise Sub 64636. Traffic Control required 100km/h zone. Excluded OMS 1622696 | December | 2018 | 2019Q2 | 2019 | 238:34148 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2018-12-19 | N | 921 | Y | 13 | N | Y | 1.1101 | 39.4971 | 1346.0793
[7 empty] | 7136 | 19841 | 1622881 | 2018-12-20 09:54 | 2018-12-20 13:50 | 236 | 11kV | 472 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 189506 A Phase DOLF : 10 Amp Excluded OMS 1622881 | December | 2018 | 2019Q2 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2018-12-20 | N | 236 | N | 8 | N | N | 1.1101 | 39.4971 | 344.9237
[7 empty] | 6856 | 16979 | 1622934 | 2018-12-20 11:11 | 2018-12-20 15:30 | 259 | 11kV | 259 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 189509 DOLF : 10 Amp Replace arrestors Excluded OMS 1622934 | December | 2018 | 2019Q2 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2018-12-20 | Y | 259 | N | 8 | N | Y | 1.1101 | 39.4971 | 189.2696
[7 empty] | 6334 | 11245 | 1622828 | 2018-12-20 08:36 | 2018-12-20 17:20 | 524.05 | 11kV | 4192.4 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Somersby Pnl.17 11kV mains down beyond USL41266 tree brought down mains | December | 2018 | 2019Q2 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2018-12-20 | Y | 524.05 | N | 8 | N | Y | 1.1101 | 39.4971 | 3063.6823
[7 empty] | 6070 | 8332 | 1622647 | 2018-12-19 20:02 | 2018-12-20 18:15 | 1333 | 11kV | 2666 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Previous Storm | N | Ex ZN12630 PEATS RIDGE section of 11kV CB PA1 "Gunderman" fdr PT11669 16Amp footpath phase HVDO operated Cause: Possible Fuse Fatigue See 1622647,3956 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2018-12-19 | N | 1333 | N | 13 | N | N | 1.1101 | 39.4971 | 1948.2342
[7 empty] | 6480 | 13083 | 1623179 | 2018-12-20 17:25 | 2018-12-20 19:08 | 103 | 11kV | 11021 | 107 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12690 BERKELEY VALE section of 11kV CB PA16 'S14716' fdr RE45026 Fountaindale tripped on O/C Cause: tree on 11kV Adj PT13163. isolated by DOp and removed by linesman | December | 2018 | 2019Q2 | 2019 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2018-12-20 | Y | 103 | N | 8 | N | Y | 1.1101 | 39.4971 | 8053.8217
[7 empty] | 6918 | 17735 | 1622935 | 2018-12-20 18:23 | 2018-12-20 19:35 | 72 | 11kV | 110774 | 1993 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN12610 LONG JETTY 11kV CB PA10 'Wamberal' fdr interrupted by AOp for safety. EMSO reported 11kv down vicinity PT13171 Forresters Beach Entrance. See 1622935,4158,60,1,2,4 | December | 2018 | 2019Q2 | 2019 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Not Veg | 2018-12-20 | Y | 55.5815 | N | 8 | N | Y | 1.1101 | 39.4971 | 80950.3719
[7 empty] | 5642 | 4043 | 1623153 | 2018-12-20 16:52 | 2018-12-20 19:50 | 178 | 11kV | 118684 | 703 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | Y | Zn847 Hornsby - pnl.47 tripped on: Earth fault Abnormal: AB80 Open & Defective with AB1262 Closed Lightning arrestor failed near S4843 See 1624239 1624241 | December | 2018 | 2019Q2 | 2019 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Not Veg | 2018-12-20 | N | 168.825 | N | 8 | N | N | 1.1101 | 39.4971 | 86730.7666
[7 empty] | 6958 | 18094 | 1623198 | 2018-12-20 17:42 | 2018-12-20 20:25 | 163 | 11kV | 198534 | 1218 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | Y | Section of Pnl.17 Kogarah Zone - AB31256 bond burnt off during lightning storm. Abnormal: S10143 (Sw/A) open, S10879 (Sw/B) open with Rockdale Pnl.3 closed. (DMA) | December | 2018 | 2019Q2 | 2019 | ZN10999:PA17 | ZN10998:PA3 | ZN10998/000003 | BAYSIDE | OH | Not Veg | 2018-12-20 | N | 163 | N | 8 | N | N | 1.1101 | 39.4971 | 145082.7914
[7 empty] | 6306 | 10952 | 1623294 | 2018-12-20 18:44 | 2018-12-20 21:02 | 138 | 11kV | 93102 | 770 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189523 Overcurrent Excluded OMS 1623294 | December | 2018 | 2019Q2 | 2019 | 523:33503 | 523:33503 | ZN00523/033503 | SINGLETON | OH | Veg | 2018-12-20 | Y | 120.9117 | N | 8 | N | Y | 1.1101 | 39.4971 | 68036.1956
[7 empty] | 6450 | 12674 | 1623323 | 2018-12-20 18:52 | 2018-12-20 21:10 | 138 | 11kV | 102982 | 899 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN15014 MONA VALE 11kV CB PA22 'Ponderosa Mona Vale fdr tripped on: Relays: A+C phase IOC, EFI, Fault Check Signals: 11kV trip EFI's S16761 S16817 S16695 S16699 Cause: tree branch on mains removed by Dop See 1623323,4094,5 | December | 2018 | 2019Q2 | 2019 | ZN15014:PA22 | ZN15014:PA22 | ZN15014/000022 | NORTHERN BEACHES | OH | Veg | 2018-12-20 | N | 114.5517 | N | 8 | N | N | 1.1101 | 39.4971 | 75256.2081
[7 empty] | 7038 | 18946 | 1623408 | 2018-12-20 18:40 | 2018-12-20 22:36 | 236 | 11kV | 27140 | 115 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 189522 Overcurrent 11kv on ground near pole SM-40106. | December | 2018 | 2019Q2 | 2019 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2018-12-20 | Y | 236 | N | 8 | N | Y | 1.1101 | 39.4971 | 19833.1115
[7 empty] | 6718 | 15288 | 1623381 | 2018-12-20 18:53 | 2018-12-20 23:20 | 267 | 11kV | 41385 | 155 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Electrical Storm | Y | LID 189524 A Phase 11kv link 40907 burnt up had to be left open and back fed via Sw 57446. No protection operation. Excluded OMS 1623381 | December | 2018 | 2019Q2 | 2019 | 513:48056 | 513:83493 | ZN00513/083493 | SINGLETON | OH | Not Veg | 2018-12-20 | Y | 267 | N | 8 | N | Y | 1.1101 | 39.4971 | 30242.9373
[7 empty] | 5646 | 4080 | 1623274 | 2018-12-20 18:38 | 2018-12-20 23:20 | 282 | 11kV | 283476 | 2137 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn2635 Epping - Pnl.58 tripped on: A & C phase OC Tree branch on mains near LB2434. | December | 2018 | 2019Q2 | 2019 | ZN2635:PA58 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | OH | Veg | 2018-12-20 | N | 132.6514 | N | 8 | N | N | 1.1101 | 39.4971 | 207155.8997
[7 empty] | 6732 | 15378 | 1623604 | 2018-12-20 19:49 | 2018-12-20 23:50 | 241 | 11kV | 16066 | 946 | HV | Lightning Strike | Adverse Weather/Environment | Bond | Unplanned | Lightning | Y | Zn9252 Jannali - Pnl.21 tripped & reclosed on: A, B & C phase O/C - PT9362 left withouth supply Burnt bond at pole SU 10825 vicinity LB 35331. PT 9362 in lv parallel. See 1623893 1623894 | December | 2018 | 2019Q2 | 2019 | ZN9252:PA21 | ZN9252:PA21 | ZN09252/000021 | SUTHERLAND | OH | Not Veg | 2018-12-20 | N | 16.9831 | N | 8 | N | N | 1.1101 | 39.4971 | 11740.5589
[7 empty] | 5583 | 3375 | 1623494 | 2018-12-20 19:48 | 2018-12-21 02:15 | 387 | 11kV | 3483 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189535 3 phase DOLF : 40 Amp Excluded OMS 1623494 | December | 2018 | 2019Q2 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2018-12-20 | Y | 387 | N | 8 | N | Y | 1.1101 | 39.4971 | 2545.2737
[7 empty] | 5512 | 2149 | 1623393 | 2018-12-20 18:48 | 2018-12-21 02:35 | 467.4 | 11kV | 9348 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189533 Single phase DOLF : 20 Amp | December | 2018 | 2019Q2 | 2019 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2018-12-20 | Y | 467.4 | N | 8 | N | Y | 1.1101 | 39.4971 | 6831.2427
[7 empty] | 5926 | 6681 | 1623335 | 2018-12-20 18:55 | 2018-12-21 03:30 | 515 | 11kV | 740965 | 1523 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12570 Avoca - Pnl.37 tripped on: SEF Weather - Bond off and tree across mains See 1624342 1624343 | December | 2018 | 2019Q2 | 2019 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2018-12-20 | Y | 486.5167 | N | 8 | N | Y | 1.1101 | 39.4971 | 541475.3672
[7 empty] | 5525 | 2424 | 1623239 | 2018-12-20 18:10 | 2018-12-21 03:30 | 560 | 11kV | 8889 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Insulator | Unplanned | Electrical Storm | Y | LID 189517 Overcurrent Replaced 11kV tie pole 3H-50050 & link 75084 Excluded OMS 1623239. | December | 2018 | 2019Q2 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2018-12-20 | Y | 467.8421 | N | 8 | N | Y | 1.1101 | 39.4971 | 6495.819
[7 empty] | 5451 | 1431 | 1623240 | 2018-12-20 18:14 | 2018-12-21 04:50 | 636.0833 | 11kV | 10177.3333 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189540 A & C Phase DOLF : 20 Amp | December | 2018 | 2019Q2 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2018-12-20 | Y | 636.0833 | N | 8 | N | Y | 1.1101 | 39.4971 | 7437.295
[7 empty] | 5743 | 5126 | 1623762 | 2018-12-21 05:11 | 2018-12-21 06:30 | 79.1167 | 11kV | 79.1167 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 189541 Single phase DOLF : 5 Amp Excluded OMS 1623767 | December | 2018 | 2019Q2 | 2019 | 512:83732 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2018-12-21 | N | 79.1167 | N | 19 | N | N | 1.1101 | 39.4971 | 57.8161
[7 empty] | 5493 | 1899 | 1623741 | 2018-12-21 02:54 | 2018-12-21 08:03 | 308.8 | 11kV | 6176 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189545 B Phase DOLF : 40 Amp | December | 2018 | 2019Q2 | 2019 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2018-12-21 | N | 308.8 | N | 19 | N | N | 1.1101 | 39.4971 | 4513.2386
[7 empty] | 6184 | 9891 | 1623524 | 2018-12-20 19:56 | 2018-12-21 08:25 | 749 | 11kV | 64988 | 397 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189521 2 fault operations A & B phases Earth Fault; Overcurrent Tree removed from OHM at pole JQ-77169. Excluded OMS 1623524 | December | 2018 | 2019Q2 | 2019 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2018-12-20 | Y | 163.6977 | N | 8 | N | Y | 1.1101 | 39.4971 | 47491.3136
[7 empty] | 5498 | 1955 | 1623776 | 2018-12-21 06:05 | 2018-12-21 08:30 | 145 | 11kV | 435 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 189546 Single phase DOLF : 10 Amp Excluded OMS 1623776 | December | 2018 | 2019Q2 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2018-12-21 | N | 145 | N | 19 | N | N | 1.1101 | 39.4971 | 317.8852
[7 empty] | 5696 | 4626 | 1623610 | 2018-12-20 20:49 | 2018-12-21 08:30 | 701 | 11kV | 701 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 189547 C Phase DOLF : 10 Amp Excluded OMS 1623610 | December | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2018-12-20 | Y | 701 | N | 8 | N | Y | 1.1101 | 39.4971 | 512.2701
[7 empty] | 5986 | 7297 | 1623805 | 2018-12-21 07:57 | 2018-12-21 08:55 | 58 | 11kV | 232 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 189557 C Phase DOLF : 10 Amp Excluded OMS 1623805 | December | 2018 | 2019Q2 | 2019 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2018-12-21 | N | 58 | N | 19 | N | N | 1.1101 | 39.4971 | 169.5388
[7 empty] | 6031 | 7913 | 1623788 | 2018-12-21 06:32 | 2018-12-21 09:10 | 158 | 11kV | 158 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 189589 Blown Live Line Lead Excluded OMS 1623788 | December | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-12-21 | N | 158 | N | 19 | N | N | 1.1101 | 39.4971 | 115.4617
[7 empty] | 6866 | 17107 | 1623613 | 2018-12-20 20:50 | 2018-12-21 09:40 | 770 | 11kV | 3080 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 189590 B Phase DOLF : 10 Amp Excluded OMS 1623613 | December | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2018-12-20 | Y | 770 | N | 8 | N | Y | 1.1101 | 39.4971 | 2250.7732
[7 empty] | 7082 | 19449 | 1623889 | 2018-12-21 09:47 | 2018-12-21 10:25 | 38 | 11kV | 152 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189591 Single phase DOLF : 5 Amp Excluded OMS 1623889 | December | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2018-12-21 | N | 38 | N | 19 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 6132 | 9227 | 1623840 | 2018-12-21 08:20 | 2018-12-21 10:55 | 155 | 11kV | 1085 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 189596 A & B Phase DOLF : 20 Amp Excluded OMS 1623840 | December | 2018 | 2019Q2 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2018-12-21 | N | 155 | N | 19 | N | N | 1.1101 | 39.4971 | 792.886
[7 empty] | 6572 | 14088 | 1623823 | 2018-12-21 07:58 | 2018-12-21 11:50 | 232 | 11kV | 464 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 189594 3 phase DOLF : 10 Amp Excluded OMS 1623823 | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-12-21 | N | 232 | N | 19 | N | N | 1.1101 | 39.4971 | 339.0775
[7 empty] | 6579 | 14213 | 1623759 | 2018-12-20 21:15 | 2018-12-21 12:00 | 885 | 11kV | 23010 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | LID 189621 Single phase Overcurrent Excluded OMS 1623759 | December | 2018 | 2019Q2 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2018-12-20 | Y | 885 | N | 8 | N | Y | 1.1101 | 39.4971 | 16815.0293
[7 empty] | 7031 | 18817 | 1623796 | 2018-12-21 11:27 | 2018-12-21 12:25 | 58 | 11kV | 2436 | 42 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 189611 Web entry Wire on ground Excluded OMS 1623796 | December | 2018 | 2019Q2 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2018-12-21 | N | 58 | N | 19 | N | N | 1.1101 | 39.4971 | 1780.157
[7 empty] | 5715 | 4855 | 1623926 | 2018-12-21 10:45 | 2018-12-21 12:35 | 110 | 11kV | 2530 | 23 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189587 Tree in mains | December | 2018 | 2019Q2 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2018-12-21 | N | 110 | N | 19 | N | N | 1.1101 | 39.4971 | 1848.8494
[7 empty] | 5991 | 7417 | 1623481 | 2018-12-20 19:45 | 2018-12-21 12:35 | 1010 | 11kV | 2020 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 189586 DOLF : 10 Amp Excluded oms 1623486 & 16223481 | December | 2018 | 2019Q2 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2018-12-20 | Y | 1010 | N | 8 | N | Y | 1.1101 | 39.4971 | 1476.1564
[7 empty] | 5567 | 3145 | 1623904 | 2018-12-21 10:11 | 2018-12-21 12:50 | 159 | 11kV | 318 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 189610 Single phase DOLF : 10 Amp Excluded OMS 1623904 | December | 2018 | 2019Q2 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2018-12-21 | N | 159 | N | 19 | N | N | 1.1101 | 39.4971 | 232.385
[7 empty] | 6698 | 15188 | 1623731 | 2018-12-20 18:33 | 2018-12-21 13:30 | 1137 | 11kV | 67816 | 196 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | Rain Wind Storm | Y | REC420 Reynolds Crosslands tripped & reclosed on O/C Fault in CCT between CP420 to LB2239 to USL163 See 1624245 1624246 | December | 2018 | 2019Q2 | 2019 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2018-12-20 | Y | 346 | N | 8 | N | Y | 1.1101 | 39.4971 | 49557.9326
[7 empty] | 6808 | 16446 | 1623526 | 2018-12-20 20:02 | 2018-12-21 13:40 | 1058 | 11kV | 4232 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189531 Single phase DOLF : 10 Amp Excluded OMS 1623526 | December | 2018 | 2019Q2 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2018-12-20 | Y | 1058 | N | 8 | N | Y | 1.1101 | 39.4971 | 3092.6208
[7 empty] | 6941 | 17921 | 1623352 | 2018-12-20 18:52 | 2018-12-21 13:55 | 1143 | 11kV | 76116 | 114 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 189537 3 fault operations Mains on ground pole FN-20057 & broken xarms Excluded oms 1623352, 1623747, 1623489 | December | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-12-20 | Y | 667.6842 | N | 8 | N | Y | 1.1101 | 39.4971 | 55623.3278
[7 empty] | 6039 | 8042 | 1623691 | 2018-12-20 22:19 | 2018-12-21 14:00 | 941 | 11kV | 3764 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 189608 Single phase DOLF : 10 Amp Excluded oms 1623691, 1623704 | December | 2018 | 2019Q2 | 2019 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2018-12-20 | Y | 941 | N | 8 | N | Y | 1.1101 | 39.4971 | 2750.6202
[7 empty] | 5693 | 4596 | 1623300 | 2018-12-20 18:37 | 2018-12-21 15:00 | 1223 | 11kV | 43626 | 91 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 189538 3 fault operations Earth Fault L/A replaced at Sub 51235 Excluded OMS 1623300 & 1623754 | December | 2018 | 2019Q2 | 2019 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2018-12-20 | Y | 479.4066 | N | 8 | N | Y | 1.1101 | 39.4971 | 31880.5941
[7 empty] | 5934 | 6804 | 1623330 | 2018-12-20 18:50 | 2018-12-21 15:10 | 1220 | 11kV | 678998 | 1781 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn12570 Avoca - Pnl.24 tripped on: A Phase IOC Storm See 1624339 1624338 | December | 2018 | 2019Q2 | 2019 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2018-12-20 | Y | 381.2454 | N | 8 | N | Y | 1.1101 | 39.4971 | 496191.7113
[7 empty] | 5504 | 2014 | 1623291 | 2018-12-20 18:40 | 2018-12-21 16:03 | 1283 | 11kV | 325525 | 291 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189602 Mains down at pole SM-40157 Defective Lightning arrestors at 74147 RAGCB Excluded OMS 1623291 | December | 2018 | 2019Q2 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2018-12-20 | Y | 1118.6426 | N | 8 | N | Y | 1.1101 | 39.4971 | 237884.0686
[7 empty] | 6766 | 15758 | 1623325 | 2018-12-20 18:45 | 2018-12-21 16:35 | 1310 | 11kV | 71736 | 176 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 189520 11kV mains down beyond pole EO-50173 Excluded OMS 1623325 | December | 2018 | 2019Q2 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2018-12-20 | Y | 407.5909 | N | 8 | N | Y | 1.1101 | 39.4971 | 52422.5529
[7 empty] | 5709 | 4773 | 1624071 | 2018-12-21 16:35 | 2018-12-21 17:00 | 25 | 11kV | 225 | 9 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 189599 Restored 11kv main to insulator pole AJ50785 . Broken stay is private | December | 2018 | 2019Q2 | 2019 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2018-12-21 | N | 25 | N | 19 | N | N | 1.1101 | 39.4971 | 164.4234
[7 empty] | 6697 | 15177 | 1624118 | 2018-12-21 16:29 | 2018-12-21 17:20 | 50.7833 | 11kV | 558.6167 | 11 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | Ex Pnl.17 Lisarow - LK44957 interrupted to allow safe removal of tree branch from OH mains | December | 2018 | 2019Q2 | 2019 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2018-12-21 | N | 50.7833 | N | 19 | N | N | 1.1101 | 39.4971 | 408.2206
[7 empty] | 7105 | 19603 | 1623322 | 2018-12-20 18:44 | 2018-12-21 17:45 | 1381 | 11kV | 250339 | 240 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12630 Peats Ridge Pnl.11 tripped on: B & C phase O/C Storm - 1: 11kV from LK44005 to PT18875 2: Tree on 11kV between AB41410 to LB46841 See 1624390 1624391 1624392 1624393 1624394 1624395 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2018-12-20 | Y | 1043.0792 | N | 8 | N | Y | 1.1101 | 39.4971 | 182940.3574
[7 empty] | 6618 | 14537 | 1623854 | 2018-12-21 08:45 | 2018-12-21 17:55 | 550 | 11kV | 3850 | 7 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 189570 A Phase DOLF : 10 Amp replaced faulty LAs Excluded oms 1623854 | December | 2018 | 2019Q2 | 2019 | 243:80080 | 243:80080 | ZN00243/080080 | LAKE MACQUARIE | OH | Not Veg | 2018-12-21 | N | 550 | N | 19 | N | N | 1.1101 | 39.4971 | 2813.4664
[7 empty] | 7177 | 20398 | 1623237 | 2018-12-20 18:19 | 2018-12-21 18:15 | 1436 | 11kV | 43948 | 99 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 189527 3 fault operations Earth Fault Replaced fuse carrier sub 1937. Repaired wired down P 9T90031 Excluded OMS 1623237 1623723 1623267 | December | 2018 | 2019Q2 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2018-12-20 | Y | 443.9192 | N | 8 | N | Y | 1.1101 | 39.4971 | 32115.9022
[7 empty] | 6600 | 14364 | 1624172 | 2018-12-21 17:25 | 2018-12-21 19:15 | 110 | 11kV | 440 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189601 wire off pin CG-70012 Excluded OMS 1624172 | December | 2018 | 2019Q2 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2018-12-21 | N | 110 | N | 19 | N | N | 1.1101 | 39.4971 | 321.539
[7 empty] | 5351 | 149 | 1623597 | 2018-12-20 20:40 | 2018-12-21 19:45 | 1385 | 11kV | 5540 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 189603 Replaced arrestor Excluded OMS 1623597 | December | 2018 | 2019Q2 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2018-12-20 | Y | 1385 | N | 8 | N | Y | 1.1101 | 39.4971 | 4048.4686
[7 empty] | 6476 | 13060 | 1624209 | 2018-12-21 19:11 | 2018-12-21 20:25 | 74 | 11kV | 444 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 189605 A Phase DOLF : 10 Amp Excluded OMS 1624209 | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-12-21 | N | 74 | N | 19 | N | N | 1.1101 | 39.4971 | 324.4621
[7 empty] | 6715 | 15267 | 1623734 | 2018-12-21 20:15 | 2018-12-21 21:25 | 70 | 11kV | 910 | 13 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 189616 Single phase No protection ops. Section isolated to replace txf 71408 under AP Excluded OMS 1623734 | December | 2018 | 2019Q2 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2018-12-21 | N | 70 | N | 19 | N | N | 1.1101 | 39.4971 | 665.0012
[7 empty] | 6656 | 14888 | 1623333 | 2018-12-20 18:41 | 2018-12-22 08:30 | 2269 | 11kV | 16153 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex peats Ridge Pnl.6 REC61084 Bushells Peats 0.2 tripped, reclosed and locked out Trees brought down OH mains between AB40570 & LK42078 PT12168 Bushells Peats Ridg 0.1 - Dist #1 - Interrupted for clearances to re-string 11kV See 1624397 1624398 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA6 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2018-12-20 | Y | 1615.3 | N | 8 | N | Y | 1.1101 | 39.4971 | 11804.136
[7 empty] | 5376 | 472 | 1623277 | 2018-12-20 18:33 | 2018-12-22 09:48 | 2355 | 11kV | 287008 | 184 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | Y | LID 189519 Broken crossarm on pole MN-53932 | December | 2018 | 2019Q2 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2018-12-20 | Y | 1559.8261 | N | 8 | N | Y | 1.1101 | 39.4971 | 209736.9811
[7 empty] | 6447 | 12644 | 1624314 | 2018-12-22 08:30 | 2018-12-22 10:16 | 106 | 11kV | 106 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 189619 B Phase DOLF : 16 Amp Excluded OMS 1624314 | December | 2018 | 2019Q2 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2018-12-22 | N | 106 | N | 10 | N | N | 1.1101 | 39.4971 | 77.4617
[7 empty] | 5744 | 5127 | 1624249 | 2018-12-21 20:12 | 2018-12-22 11:45 | 933 | 11kV | 2799 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 189622 A & C Phase DOLFs : 10 Amp Excluded OMS 1624249 | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-12-21 | N | 933 | N | 19 | N | N | 1.1101 | 39.4971 | 2045.4266
[7 empty] | 6252 | 10438 | 1624334 | 2018-12-22 08:30 | 2018-12-22 12:10 | 220 | 11kV | 2860 | 13 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex Peats Ridge Pnl.13 Tree on branch beyond LB61387 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2018-12-22 | N | 220 | N | 10 | N | N | 1.1101 | 39.4971 | 2090.0036
[7 empty] | 6916 | 17713 | 1623383 | 2018-12-20 18:59 | 2018-12-22 13:00 | 2521 | 11kV | 320413 | 149 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Peats Ridge Pnl.3 REC46935 Ironbark Kirks 0.8 tripped on O/C Multiple branches on Mains beyond Autolink 46938 See 1624431 1624430 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2018-12-20 | Y | 2150.4228 | N | 8 | N | Y | 1.1101 | 39.4971 | 234148.3698
[7 empty] | 6136 | 9261 | 1623329 | 2018-12-20 18:42 | 2018-12-22 14:02 | 2600 | 11kV | 516540 | 323 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12630 peats Ridge - Pnl.10 tripped on: A & C phase O/C Tree on branch between LK40537 and LB40906 tee PT13824 See 1624738 1624739 1624740 1624741 1624742 1624744 1624745 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2018-12-20 | Y | 1599.195 | N | 8 | N | Y | 1.1101 | 39.4971 | 377472.1966
[7 empty] | 7127 | 19737 | 1623309 | 2018-12-20 18:34 | 2018-12-22 15:30 | 2696 | 11kV | 171546 | 99 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | Ex Zn12630 Peats Ridge 11kv VCB pnl 8 "Kulnurra" feeder Rec 44995 Kulnurra tripped on SEF Remarks: tree/branch on OH mains | December | 2018 | 2019Q2 | 2019 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2018-12-20 | Y | 1732.7879 | N | 8 | N | Y | 1.1101 | 39.4971 | 125360.757
[7 empty] | 5950 | 6939 | 1623334 | 2018-12-20 18:50 | 2018-12-22 15:45 | 2695 | 11kV | 602750 | 1599 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Insulated | Unplanned | Rain Wind Storm | Y | Zn12570 Avoca - Pnl.22 tripped on: A & B Phase O/C OH mains isolated between AB43330 and AB40388 tee PT12521 PT13822 - tree in LV mains PT13862 - tree in LV mains See 1625234 1625238 1625239 | December | 2018 | 2019Q2 | 2019 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2018-12-20 | Y | 376.9543 | N | 8 | N | Y | 1.1101 | 39.4971 | 440471.9219
[7 empty] | 5952 | 6956 | 1624455 | 2018-12-22 14:55 | 2018-12-22 15:55 | 60 | 11kV | 44924 | 749 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S2196 Milperra Panel 2 "Bullecourt Horsley UWS No.2" fdr tripped Relays: B phase overcurrent, EFI, fault check Signals: 11kv trip, zone earth, Tx 3 group earth Remarks: UG fault. 11kv feeder fault from S4534 Bulletcourt Horsley UWS No.2 to S6612 Bulletcourt Dernan to S1729 Ashford Bul | December | 2018 | 2019Q2 | 2019 | ZN2196:PA2 | ZN2196:PA2 | ZN02196/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-12-22 | N | 59.9786 | N | 10 | N | N | 1.1101 | 39.4971 | 32829.1342
[7 empty] | 5412 | 987 | 1624364 | 2018-12-22 11:07 | 2018-12-22 16:05 | 298 | 11kV | 298 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 189623 B Phase DOLF : 10 Amp Excluded OMS 1624364 | December | 2018 | 2019Q2 | 2019 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2018-12-22 | N | 298 | N | 10 | N | N | 1.1101 | 39.4971 | 217.7696
[7 empty] | 6056 | 8200 | 1624382 | 2018-12-22 11:40 | 2018-12-22 16:05 | 265 | 11kV | 84270 | 318 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Previous Storm | N | Zn12630 Peats Ridge Panel 1 Section of 11kv from Rec61375 Wise Ferry Biara 1.30 Nil protection operation Remarks: interrupted for safety reasons. Remove large tree off CCT beyond Rec 61375 Wise Ferry Biara 1.30 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2018-12-22 | N | 265 | N | 10 | N | N | 1.1101 | 39.4971 | 61582.0305
[7 empty] | 5521 | 2330 | 1623770 | 2018-12-20 18:50 | 2018-12-22 16:20 | 2730 | 11kV | 43929 | 78 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 189534 4 fault operations Earth Fault Cut faulty 11kV LA away sub 17956 requires replacing. Excluded OMS 1623337 | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-12-20 | Y | 563.1923 | N | 8 | N | Y | 1.1101 | 39.4971 | 32102.0175
[7 empty] | 5724 | 4989 | 1624418 | 2018-12-22 13:10 | 2018-12-22 16:20 | 190 | 11kV | 1140 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 189625 C Phase DOLF : 10 Amp Excluded OMS 1624418 | December | 2018 | 2019Q2 | 2019 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2018-12-22 | N | 190 | N | 10 | N | N | 1.1101 | 39.4971 | 833.0784
[7 empty] | 5413 | 1006 | 1624471 | 2018-12-22 15:34 | 2018-12-22 16:50 | 76 | 11kV | 152 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 189627 A Phase DOLF : 10 Amp Excluded OMS 1624471 | December | 2018 | 2019Q2 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2018-12-22 | N | 76 | N | 10 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 5375 | 462 | 1624492 | 2018-12-22 17:23 | 2018-12-22 18:14 | 51 | 11kV | 6732 | 132 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 189629 11kv Isolated for safety clearance for LV ABC work. | December | 2018 | 2019Q2 | 2019 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2018-12-22 | N | 51 | N | 10 | N | N | 1.1101 | 39.4971 | 4919.547
[7 empty] | 7103 | 19579 | 1623647 | 2018-12-20 18:37 | 2018-12-22 19:37 | 2940 | 11kV | 179412 | 83 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Peats Ridge Pnl.3 @18:36 (20/12) - REC49206 Mangrove Mountain tripped @18:37 (20/12) - REC45071 Central Mangrove tripped @18:50 (20/12) - REC46992 Goolara Holy Cross tripped & reclosed Multiple sections of OH mains down due to storm See 1625205 1625206 1625207 1625208 1625209 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2018-12-20 | Y | 2161.5904 | N | 8 | N | Y | 1.1101 | 39.4971 | 131108.9978
[7 empty] | 5484 | 1713 | 1624523 | 2018-12-22 20:33 | 2018-12-22 21:21 | 48 | 11kV | 55680 | 1160 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn129 Hunters Hill - Pnl.40 tripped on A & C phase IOC Bat flew into OH mains in Beach St, Tennyson Point | December | 2018 | 2019Q2 | 2019 | ZN129:PA40 | ZN129:PA40 | ZN00129/000040 | RYDE | OH | Not Veg | 2018-12-22 | N | 48 | N | 10 | N | N | 1.1101 | 39.4971 | 40689.3017
[7 empty] | 6494 | 13227 | 1624519 | 2018-12-22 19:45 | 2018-12-22 21:35 | 110 | 11kV | 110 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 189631 A Phase DOLF Excluded OMS 1624519 | December | 2018 | 2019Q2 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2018-12-22 | N | 110 | N | 10 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 5969 | 7093 | 1624036 | 2018-12-21 13:49 | 2018-12-23 07:10 | 2481 | 11kV | 4962 | 2 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | PT12237 Palmdale Pacific 0.3 - 2 x 11kV HDO operated Storm | December | 2018 | 2019Q2 | 2019 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2018-12-21 | N | 2481 | N | 19 | N | N | 1.1101 | 39.4971 | 3626.0832
[7 empty] | 7134 | 19816 | 1623279 | 2018-12-20 18:37 | 2018-12-23 13:50 | 4033 | 11kV | 1468205 | 861 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | @18:37 (20/12) REC45012 Bar Point tripped @18:38 (20/12) REC45202 tripped @15:07 (21/12) Pnl.17 tripped on SEF @19:458 (21/12) Pnl.17 tripped on SEF Storm damage a multiple locations along feeder. Multiple mains down with REC and Pnl tripping multiple times. See 1624782 1624784 1624785 1624787 1624781 1624788 1624789 1624791 1624792 1624793 1624794 1624795 1624796 1624798 1624801 1624802 1624803 | December | 2018 | 2019Q2 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2018-12-20 | Y | 1705.2323 | N | 8 | N | Y | 1.1101 | 39.4971 | 1072920.9093
[7 empty] | 5872 | 6108 | 1623324 | 2018-12-20 18:36 | 2018-12-23 15:45 | 4149 | 11kV | 253854 | 71 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Peats Ridge Pnl.3 @18:36 (20/12) - REC49206 Mangrove Mountain tripped @18:37 (20/12) - REC45071 Central Mangrove tripped @18:50 (20/12) - REC46992 Goolara Holy Cross tripped & reclosed Multiple sections of OH mains down due to storm See 1625205 1625206 1625207 1625208 1625209 | December | 2018 | 2019Q2 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2018-12-20 | Y | 3575.4085 | N | 8 | N | Y | 1.1101 | 39.4971 | 185509.0158
[7 empty] | 6121 | 9103 | 1623164 | 2018-12-20 17:14 | 2018-12-23 15:58 | 4243.8333 | 11kV | 369213.5 | 87 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn12640 Umina Pnl.13L REC47745 Patonga Meroo tripped on O/C Storm | December | 2018 | 2019Q2 | 2019 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2018-12-20 | Y | 4243.8333 | N | 8 | N | Y | 1.1101 | 39.4971 | 269810.3358
[7 empty] | 6919 | 17766 | 1624620 | 2018-12-23 16:35 | 2018-12-24 00:43 | 488 | 11kV | 136755 | 1269 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn2400 Berowra - Pnl.22 tripped on B phase O/C Tree branch on mains near PT2160 See 1624705 1624706 1624707 | December | 2018 | 2019Q2 | 2019 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Veg | 2018-12-23 | N | 107.766 | N | 1 | N | N | 1.1101 | 39.4971 | 99936.5204
[7 empty] | 5953 | 6959 | 1624671 | 2018-12-24 06:46 | 2018-12-24 08:47 | 121 | 11kV | 196635 | 1839 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S3922 Drummoyne the 11kv Panel 7 "Hampden Coralie" feeder tripped on: Relays: Panel 7 EF, FC, EFI Relays: Panel 19 EF, FC, EFI Signals: Tx1 Group earth, Tx2 Group earth, 11kv trip, Zone earth Remarks: UG fault. Panel 19 @ Drummoyne tripped on attempted restoration from S4510 due to defective EFIs at S8313 and S3213 (first trip). Defective EFI also noted at S3049 | December | 2018 | 2019Q2 | 2019 | ZN3922:PA7 | ZN3922:PA7 | ZN03922/000007 | CANADA BAY | UG | Not Veg | 2018-12-24 | N | 106.925 | N | 3 | N | N | 1.1101 | 39.4971 | 143695.0582
[7 empty] | 5634 | 3840 | 1624712 | 2018-12-24 08:57 | 2018-12-24 11:17 | 140 | 11kV | 420 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 189638 C Phase DOLF : 10 Amp Excluded OMS 1624712 | December | 2018 | 2019Q2 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2018-12-24 | N | 140 | N | 3 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 5821 | 5684 | 1624657 | 2018-12-23 21:04 | 2018-12-24 11:37 | 873 | 11kV | 3313 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP26228 Valley Rd tripped, reclosed, tripped and locked out on O/C and EF Cause: tree branch brought down OH See OMS 1625103 1625104 16245657 1624746 | December | 2018 | 2019Q2 | 2019 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2018-12-23 | N | 828.25 | Y | 1 | N | Y | 1.1101 | 39.4971 | 2421.0427
[7 empty] | 6427 | 12403 | 1624908 | 2018-12-24 21:14 | 2018-12-24 22:35 | 81 | 11kV | 53604 | 1163 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 189643 2 fault operations Overcurrent possum on ELB Sw 61914. LV// before repairs complete Excluded oms ## 1624908 | December | 2018 | 2019Q2 | 2019 | 206:34432 | 206:34432 | ZN00206/034432 | LAKE MACQUARIE | OH | Not Veg | 2018-12-24 | N | 46.0911 | N | 3 | N | N | 1.1101 | 39.4971 | 39172.2221
[7 empty] | 6935 | 17902 | 1624950 | 2018-12-25 14:23 | 2018-12-25 17:25 | 182 | 11kV | 364 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 189646 3 phase DOLF : 10 Amp fault pg clamp on neutral ohm at sub. 3 dolfs replaced too. Excluded oms 1624950 | December | 2018 | 2019Q2 | 2019 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2018-12-25 | N | 182 | N | 1 | N | N | 1.1101 | 39.4971 | 266.0005
[7 empty] | 5946 | 6912 | 1625002 | 2018-12-26 07:53 | 2018-12-26 09:08 | 75 | 11kV | 57525 | 767 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.38 tripped on Earth fault (IOC and Timed) UG cable fault in front line section of feeder. See UG cable fault on Pnl.39 at the same time | December | 2018 | 2019Q2 | 2019 | ZN2568:PA38 | ZN2568:PA38 | ZN02568/000038 | INNER WEST | UG | Not Veg | 2018-12-26 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 42037.5733
[7 empty] | 7049 | 19080 | 1625003 | 2018-12-26 07:53 | 2018-12-26 09:50 | 117 | 11kV | 92644 | 866 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.39 tripped on: A Phase IOC Field EFIs: S3171 UG cable fault in frontline section of feeder See Pnl.38 front line UG cable fault at the same time | December | 2018 | 2019Q2 | 2019 | ZN2568:PA39 | ZN2568:PA39 | ZN02568/000039 | INNER WEST | UG | Not Veg | 2018-12-26 | N | 106.9792 | N | 4 | N | N | 1.1101 | 39.4971 | 67701.5027
[7 empty] | 6999 | 18525 | 1625045 | 2018-12-26 15:51 | 2018-12-26 18:10 | 139 | 11kV | 139 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S2447 Marigold Bea - 11kv RMI fuse operated Remarks: cause not ascertained. Replaced with 3 x 80A SIBA No 75 OEFMA fuses available | December | 2018 | 2019Q2 | 2019 | ZN2196:PA9 | ZN2196:PA9 | ZN02196/000009 | CANTERBURY-BANKSTOWN | OH | Veg | 2018-12-26 | N | 139 | N | 4 | N | N | 1.1101 | 39.4971 | 101.5771
[7 empty] | 6784 | 16107 | 1625071 | 2018-12-26 21:31 | 2018-12-26 23:26 | 115 | 11kV | 690 | 6 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | @ZN2196 Milperra exiting 11kv Panel 12 labelled "S7760 Carrington Mar No.3" @S4570 Carrington Fitz No.1 Transformer Panel - Buchholz/Oil Surge trip indicator, Main Tx Remarks: Buchholz trip. Buccholz Operation to the 11kv/415v Tx1 @ S4570 Carrington Fitz (// T/coil operated Tx) | December | 2018 | 2019Q2 | 2019 | ZN2196:PA12 | ZN2196:PA12 | ZN02196/000012 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-12-26 | N | 115 | N | 4 | N | N | 1.1101 | 39.4971 | 504.2316
[7 empty] | 5906 | 6433 | 1625317 | 2018-12-28 02:56 | 2018-12-28 04:00 | 64 | 11kV | 3008 | 47 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 189661 A Phase DOLF : 31 Amp Supply off 0256hrs cause Possum sub 42958 A phase 31A DOLF supply back on 0400hrs SUB 42958. 'A' PHASE DOLF BLOWN DUE TO POSSUM ACROSS DOLFS. REPLACED 'A' PHASE DOLF CARRIER AND FITTED NEW 31A FUSE ELEMENT. SUPPLY RESTORED AT 0355HRS 28/12/18. VOLTS - 244V/245V/245V (ABC). CURRENT LH LVF - 23A/15A/16A (ABC). CURRENT RH LVF - 25A/6A/4A (ABC). CONTACTED CALLER AND CALLER STATED THAT THERE WERE NO WIRES DOWN, JUST AN EXPLOSION AT PT SUB. Note: No LID raised | December | 2018 | 2019Q2 | 2019 | 205:12210 | 205:12210 | ZN00205/012210 | NEWCASTLE | OH | Not Veg | 2018-12-28 | N | 64 | N | 10 | N | N | 1.1101 | 39.4971 | 2198.1577
[7 empty] | 6434 | 12528 | 1625469 | 2018-12-28 14:50 | 2018-12-28 16:06 | 76 | 11kV | 32892 | 581 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN1285 Greenacre Park 11kv VCB Panel 22 "S5443" feeder tripped on: Relays: O/C B phase, Timmed O/C, EFI, Fault check Signals: 11kv trip, Tx3 group earth Reamarks: UG fault. 11kv feeder fault between S6494 Rickard Appin No.2 Sw/B to S7015 Bankstown Square No.3 Sw/A to S65975 Rickard Jacobs No.1 | December | 2018 | 2019Q2 | 2019 | ZN1285:PA22 | ZN1285:PA22 | ZN01285/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-12-28 | N | 56.6127 | N | 10 | N | N | 1.1101 | 39.4971 | 24036.5035
[7 empty] | 5908 | 6447 | 1625466 | 2018-12-28 14:40 | 2018-12-28 17:30 | 170 | 11kV | 170 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 189671 DOLF : 16 Amp Excluded OMS 1625466 | December | 2018 | 2019Q2 | 2019 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Veg | 2018-12-28 | N | 170 | N | 10 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 7107 | 19627 | 1625495 | 2018-12-28 16:01 | 2018-12-28 17:30 | 89 | 11kV | 22663 | 324 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | LID 189670 1 fault operation Earth Fault UGOH fault at FS 93212, tapping off FS-93202. pole fire at FS-93202. feeder closed and tappings open cct. no targets only EF Flags SCADA IEF and IOC faults recorded on SCADA/ Excluded oms 1625498,496, 495, 504, 505, 512, 514,523 | December | 2018 | 2019Q2 | 2019 | 522:83121 | 522:83121 | ZN00522/083121 | CESSNOCK | Unknown | Unknown | 2018-12-28 | N | 69.9475 | N | 10 | N | N | 1.1101 | 39.4971 | 16561.452
[7 empty] | 5984 | 7287 | 1625147 | 2018-12-27 09:53 | 2018-12-28 18:20 | 1947 | 11kV | 18667 | 203 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S2466 Flemington the 11kv Panel 26 "edwin Flack Uhrig, etc" feeder tripped on: Relays: EF, EFI, FC Signals: 11kv trip, Tx3 Group earth, Zone earth Remarks: UG cable damaged by contractor. 11mv UG mains(both sides of S35058) dug up by builders at 5 Uhrig rd. Cables pulled out of endbox at S35058 Sw/A damaging RMI. LV cable also in hole (dist 2 @ S48512) | December | 2018 | 2019Q2 | 2019 | ZN2466:PA26 | ZN2466:PA18 | ZN02466/000018 | PARRAMATTA | UG | Not Veg | 2018-12-27 | N | 91.9557 | N | 2 | N | N | 1.1101 | 39.4971 | 13641.293
[7 empty] | 6115 | 9042 | 1625306 | 2018-12-27 22:40 | 2018-12-28 18:30 | 1190 | 11kV | 175420 | 166 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN14143 SOMERSBY section of 11kV CB PA17 "Somersby Falls" RE45012 Bar Point tripped on Earth Fault Cause not ascertained. Water Crossing, day shift to patrol See 1625306,6538,9 | December | 2018 | 2019Q2 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2018-12-27 | N | 1056.747 | N | 2 | N | N | 1.1101 | 39.4971 | 128191.762
[7 empty] | 5836 | 5789 | 1625520 | 2018-12-28 17:02 | 2018-12-28 18:57 | 115 | 11kV | 197965 | 1867 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 20 tripped on Relays: Earth Fault, EFI Signals: 11kV trip Abnormal Switching: SW/B Closed at S5582, SW/A At S4255 Opened. Cause: UG fault between S4496 an d S7985 See OMS 1626978 1626980 1625531 1625524 1625521 1625520 | December | 2018 | 2019Q2 | 2019 | ZN965:PA8 | ZN965:PA8 | ZN00965/000008 | HORNSBY | UG | Not Veg | 2018-12-28 | N | 106.0337 | N | 10 | N | N | 1.1101 | 39.4971 | 144666.983
[7 empty] | 6111 | 8973 | 1625440 | 2018-12-28 12:27 | 2018-12-28 19:40 | 433 | 11kV | 118129 | 1224 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S35800 Bankstown 11kv Panel No7 "S2703 Short fair No1" feeder tripped on Relays: 50T IOC B & C phase< 50TN earth fault, EFI Signals: 11kv trip, Tx11 group earth Remarks: UGOH fault short circuit. At S35800 Bankstown ex panel No7, HV UGOH has failed between S7432 Canterbury Gow No1 to S47192 Canterbury Stacy to AB2576 (Bonds broken away) | December | 2018 | 2019Q2 | 2019 | ZN35800:PA7 | ZN35800:PA7 | ZN35800/000007 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2018-12-28 | N | 96.5106 | N | 10 | N | N | 1.1101 | 39.4971 | 86325.189
[7 empty] | 5954 | 6961 | 1625522 | 2018-12-28 17:05 | 2018-12-28 20:30 | 205 | 11kV | 205 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At S5235 Ryde Eastwood Leagues Ex S4545 Meadowbank Panel 6 "Rhodes mellor" the 11kv Tx80A SIBA B phase fuses blew Remarks: fuse replaced and held | December | 2018 | 2019Q2 | 2019 | ZN4545:PA6 | ZN4545:PA6 | ZN04545/000006 | RYDE | OH | Not Veg | 2018-12-28 | N | 205 | N | 10 | N | N | 1.1101 | 39.4971 | 149.808
[7 empty] | 5771 | 5354 | 1625544 | 2018-12-28 18:58 | 2018-12-28 20:30 | 92 | 11kV | 100163 | 1188 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN9245 Engadine 11kv VCB panel 3 'S9279' feeder tripped and locked out on- Relays: E/F, reclose, lockout, EFI Field EFI's: S9279 Signals: 11kv trip Remarks: UG fault. 11kv feeder fault between S9279 Numantia Copeland Sw/B to S9445 Wilson Princess Sw/A tee to PT9691 Copeland Rd | December | 2018 | 2019Q2 | 2019 | ZN9245:PA3 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | UG | Not Veg | 2018-12-28 | N | 84.3123 | N | 10 | N | N | 1.1101 | 39.4971 | 73196.1661
[7 empty] | 6830 | 16722 | 1625548 | 2018-12-28 19:36 | 2018-12-29 00:35 | 299 | 11kV | 96952 | 1087 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S1673 Turramurra the 11kv Panel 6 "AB3326, etc" feeder tripped, reclosed, tripped and locked out on: Relays: Earth fault, EFI, reclose, timing and lockout Signals: 11kv trip, Tx2 group earth Remarks: tree brought down 11kv OH into LV on comenarra pkwy | December | 2018 | 2019Q2 | 2019 | ZN1673:PA6 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Veg | 2018-12-28 | N | 89.1923 | N | 10 | N | N | 1.1101 | 39.4971 | 70849.662
[7 empty] | 7139 | 19880 | 1625598 | 2018-12-29 05:16 | 2018-12-29 07:04 | 108 | 11kV | 50004 | 463 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN9900 MENAI 11kv Panel 5 lablled S9912 Gould Windle triiped on: Relays: B phase overcurrent with earth fault check Signals: 11kv trip, Tx1 group and zone earth Field EFI's: nil Remarks: UG fault. ZN9900 Menai (Pnl5) to S9912 Gould Windle | December | 2018 | 2019Q2 | 2019 | ZN9900:PA5 | ZN9900:PA5 | ZN09900/000005 | SUTHERLAND | UG | Not Veg | 2018-12-29 | N | 108 | N | 4 | N | N | 1.1101 | 39.4971 | 36541.4483
[7 empty] | 6387 | 11892 | 1625642 | 2018-12-29 12:01 | 2018-12-29 12:40 | 39 | 11kV | 78 | 2 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn690 Campsie 11kv Pnl 18 "Canterbury Hosp, etc" feeder tripped on: Relays: C phase overcurrent with efi and fault check Signals: 11kv trip Remarks: UG fault. 11kv cable from S35039 Cleary Lakemba to S35562 Lakemba St Clair | December | 2018 | 2019Q2 | 2019 | ZN690:PA18 | ZN690:PA18 | ZN00690/000018 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2018-12-29 | N | 39 | N | 4 | N | N | 1.1101 | 39.4971 | 57.0001
[7 empty] | 6912 | 17684 | 1625676 | 2018-12-29 15:58 | 2018-12-29 18:05 | 127 | 11kV | 19186 | 166 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex ZN14144 WAMBERAL section of 11kV CB PA10 "Wamberal Aux No.2" RE46525 Coachwood Rd North tripped, reclosed x2 and locked out Cause: Suspect Faulty Surge Arrestor 1 Bay from USL40237 See 1625676,6657,8,61,2 | December | 2018 | 2019Q2 | 2019 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2018-12-29 | N | 115.5783 | N | 4 | N | N | 1.1101 | 39.4971 | 14020.5629
[7 empty] | 6415 | 12240 | 1625748 | 2018-12-30 06:05 | 2018-12-30 08:30 | 145 | 11kV | 202399 | 2070 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN15012 KILLARNEY 11kV CB PA4 "Forestville West" fdr tripped on: Relays: E/F, SEF, fault check, EFI, Reclose, Lockout Signals: 11kv trip, Zone Earth EFI's: S16795 S46590 Abnormal: DMA AB21109 to SwA S16789 tee PT15211. LB22077 closed Cause: UG fault UG fault in section of 11kv fdr from SwB@S46590 to SwB@S16583 tee SwA@17139 Note: region to follow up DOp found EFI @ S17034 but EFI CT not fitted to feeder See 1625748,9,6521,6,7,8,30,2 | December | 2018 | 2019Q2 | 2019 | ZN15012:PA4 | ZN15012:PA4 | ZN15012/000004 | NORTHERN BEACHES | UG | Not Veg | 2018-12-30 | N | 97.7773 | N | 3 | N | N | 1.1101 | 39.4971 | 147907.2194
[7 empty] | 6927 | 17824 | 1625698 | 2018-12-29 18:30 | 2018-12-30 08:45 | 855 | 11kV | 51320 | 150 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Hot >35C | N | LID 189680 2 fault operations B & C Phases Overcurrent Car hit pole KS40075. LV and HV down. Emso checked services OK. Excluded OMS 1625698## | December | 2018 | 2019Q2 | 2019 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2018-12-29 | N | 342.1333 | N | 4 | N | N | 1.1101 | 39.4971 | 37503.1423
[7 empty] | 6948 | 17998 | 1625760 | 2018-12-30 08:11 | 2018-12-30 11:15 | 184 | 11kV | 102938 | 707 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Panel 63 tripped on: Relays: A-N phase Overcurrent, Earth Fault, EFI DMA 1: Section of 11kV feeder from S5233 Mars Woodcock, to S2773 Rose Burns to S46610 Currawong Eloora DMA 2: At S46610 Currawong Access Permits issued for TCON to test local TX See OMS 1626920 1626922 1626923 1625760 1625811 | December | 2018 | 2019Q2 | 2019 | ZN129:PA63 | ZN129:PA63 | ZN00129/000063 | LANE COVE | UG | Not Veg | 2018-12-30 | N | 145.5983 | N | 3 | N | N | 1.1101 | 39.4971 | 75224.0542
[7 empty] | 6188 | 9937 | 1625824 | 2018-12-30 14:09 | 2018-12-30 15:20 | 70.7667 | 11kV | 849.2 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 189689 Single phase DOLF : 20 Amp | December | 2018 | 2019Q2 | 2019 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2018-12-30 | N | 70.7667 | N | 3 | N | N | 1.1101 | 39.4971 | 620.5703
[7 empty] | 6869 | 17124 | 1625576 | 2018-12-28 21:08 | 2018-12-30 16:41 | 2613 | 11kV | 2613 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At S5235 Ryde Eastwood Leagues Ex ZN4545 Meadowbank Panel 6 "Rhodes Mellor" the 11kv Tx 80A SIBA B phase fuse blew after previous replacement At ZN4545 Meadowbank: Panel 6 EFI fault check Signals: Tx1 group earth and zone earth Remarks: At S5235 Ryde Eastwood Leagues the 11kv/415v Transformer has failed. Ex ZN4545 Meadowbank Panel 6 "Rhodes Mellor" Transformer was replaced however failed upon energisation. HV Tx tails were found to be faulty. | December | 2018 | 2019Q2 | 2019 | ZN4545:PA6 | ZN4545:PA6 | ZN04545/000006 | RYDE | UG | Not Veg | 2018-12-28 | N | 2613 | N | 10 | N | N | 1.1101 | 39.4971 | 1909.5033
[7 empty] | 6985 | 18363 | 1625885 | 2018-12-31 02:50 | 2018-12-31 04:04 | 74 | 11kV | 86314 | 1217 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 189690 C Phase tapping burnt off UGOH pole JU-52947. Excluded OMS 1625885## | December | 2018 | 2019Q2 | 2019 | 205:12205 | 205:12205 | ZN00205/012205 | NEWCASTLE | OH | Not Veg | 2018-12-31 | N | 70.9236 | N | 17 | N | N | 1.1101 | 39.4971 | 63075.7254
[7 empty] | 6373 | 11738 | 1626053 | 2018-12-31 16:17 | 2018-12-31 16:46 | 29 | 11kV | 21547 | 743 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At CP46113 Fiddens Wharf Coronga tripped reclosed and locked out on Relays: IOC EFI's NIl Cause: Tree branch on OH mains outside 20 Bradfield Rd Lindfield. See OMS 1626053 1626053 1626056 | December | 2018 | 2019Q2 | 2019 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2018-12-31 | N | 29 | N | 17 | N | N | 1.1101 | 39.4971 | 15745.9121
[7 empty] | 6981 | 18315 | 1626045 | 2018-12-31 15:35 | 2018-12-31 16:58 | 83 | 11kV | 106377 | 1399 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN7481 Darling Harbour 11kv feeder Panel No: 14 "Harris John etc" feeder tripped on: Relays: C phase O/C, E/F, EFI Remarks: UG fault in section of 11kv feeder from S8986 Harris John (Sw/B) to S7946 Point John (Sw/A) | December | 2018 | 2019Q2 | 2019 | ZN7481:PA14 | ZN7481:PA14 | ZN07481/000014 | SYDNEY | UG | Not Veg | 2018-12-31 | N | 76.0379 | N | 17 | N | N | 1.1101 | 39.4971 | 77737.174
[7 empty] | 6216 | 10137 | 1626065 | 2018-12-31 17:06 | 2018-12-31 18:52 | 106 | 11kV | 37300 | 513 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Lightning | N | ZN14892 CHARMHAVEN 11kV CB PA17'S14750 Plane Tree Apple Gum' fdr has tripped, reclosed, tripped & locked out on: Signals: 11kv trip, Tx2 Group Earth Relays: A+C phase timed o/c, earth fault check, EFI, Reclose Timer, Lockout Relay, Tx2 Earth Fualt Check, Frame Leakage Prohibition EFI'S S14750 S18241 S18096 S14836 S18155 See 1626065,7213,4,5 | December | 2018 | 2019Q2 | 2019 | ZN14892:PA17 | ZN14892:PA17 | ZN14892/000017 | CENTRAL COAST | UG | Not Veg | 2018-12-31 | N | 72.7096 | N | 17 | N | N | 1.1101 | 39.4971 | 27257.7398
[7 empty] | 6861 | 17027 | 1626026 | 2018-12-31 19:38 | 2018-12-31 20:49 | 71 | 11kV | 74195 | 1045 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | ZN12690 BERKELEY VALE 11kV CB PA12 'Craftsman Av' fdr tripped, reclosed, tripped & locked out: Signals: 11kv trip Relays: A+B phase IOC, Reclose Timing, Lockout EFIs: Nil Cause: tree/branch on OH mains Surge Arrestors looked suspect on first HV UGOH Out bewteen S.14941 & AB.42921, but proved ok. (Forwarded to Depot to inspect business hours). Tree branch came against CCT in Herford St nr, Corella Cl, Berkeley Vale (HV Pole BV-195). Feeder interrupted for safety @ 20:48 to Close AB.42921 (Not suitable to pickup load + Access Issues). See 1626098 ex 1626026 | December | 2018 | 2019Q2 | 2019 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Veg | 2018-12-31 | N | 71 | N | 17 | N | N | 1.1101 | 39.4971 | 54219.5176
[7 empty] | 6964 | 18163 | 1626146 | 2018-12-31 20:53 | 2018-12-31 23:42 | 169 | 11kV | 9126 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189701 Overcurrent | December | 2018 | 2019Q2 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2018-12-31 | N | 169 | N | 17 | N | N | 1.1101 | 39.4971 | 6669.0116
[7 empty] | 5949 | 6926 | 1626164 | 2018-12-31 21:36 | 2018-12-31 23:59 | 142.6667 | 11kV | 15122.6667 | 106 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 199704 C Phase DOLF : 40 Amp Multiple hazards on LV to address but Supply restored to Tx LVF. Phil Leeman is checking all hazards reported. Excluded OMS 1626164, 1626168, 1626174 ,1626190, 1626175, | December | 2018 | 2019Q2 | 2019 | 238:34150 | 238:34150 | ZN00238/034150 | NEWCASTLE | OH | Veg | 2018-12-31 | N | 142.6667 | N | 17 | N | N | 1.1101 | 39.4971 | 11051.1988
[7 empty] | 5684 | 4463 | 1626158 | 2018-12-31 21:18 | 2019-01-01 00:20 | 182 | 11kV | 3458 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 199713 A Phase DOLF 63 Amp OMS 1626166, 1626158 | December | 2018 | 2019Q2 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2018-12-31 | N | 182 | N | 17 | N | N | 1.1101 | 39.4971 | 2527.0044
[7 empty] | 7021 | 18716 | 1626179 | 2018-12-31 21:50 | 2019-01-01 00:23 | 153 | 11kV | 6273 | 41 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189699 2 fault operations Overcurrent | December | 2018 | 2019Q2 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2018-12-31 | N | 153 | N | 17 | N | N | 1.1101 | 39.4971 | 4584.1234
[7 empty] | 6845 | 16848 | 1626118 | 2018-12-31 19:59 | 2019-01-01 01:08 | 309 | 11kV | 27711 | 91 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 199706 3 fault operations Sensitive Earth Fault TARETS SEF. FEEDER SECTIONALISED & PATROLLED.NO FAULT FOUND.PLEASE PATROL IN DAYLIGHT. Excluded OMS 1626118. | December | 2018 | 2019Q2 | 2019 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2018-12-31 | N | 304.5165 | N | 17 | N | N | 1.1101 | 39.4971 | 20250.3815
[7 empty] | 6636 | 14715 | 1626171 | 2018-12-31 21:44 | 2019-01-01 01:30 | 226 | 11kV | 1808 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 199707 Single phase DOLF : 20 Amp Excluded OMS 1626171 | December | 2018 | 2019Q2 | 2019 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2018-12-31 | N | 226 | N | 17 | N | N | 1.1101 | 39.4971 | 1321.2331
[7 empty] | 6187 | 9936 | 1626142 | 2018-12-31 20:49 | 2019-01-01 02:15 | 325.55 | 11kV | 3906.6 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 199708 Single phase DOLF : 20 Amp REPLACED 2 X LINE FUSES | December | 2018 | 2019Q2 | 2019 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2018-12-31 | N | 325.55 | N | 17 | N | N | 1.1101 | 39.4971 | 2854.8281
[7 empty] | 6085 | 8486 | 1626144 | 2018-12-31 20:58 | 2019-01-01 02:50 | 352 | 11kV | 352 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 199709 Single phase DOLF : 10 Amp FAULTY ARRESTOR Excluded OMS 1626144. | December | 2018 | 2019Q2 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2018-12-31 | N | 352 | N | 17 | N | N | 1.1101 | 39.4971 | 257.2312
[7 empty] | 6755 | 15623 | 1626145 | 2018-12-31 20:31 | 2019-01-01 05:39 | 548 | 11kV | 18747 | 76 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 199705 tree on mains at pole EQ-30174 Excluded OMS 1626145 | December | 2018 | 2019Q2 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2018-12-31 | N | 246.6711 | N | 17 | N | N | 1.1101 | 39.4971 | 13699.7547
[7 empty] | 7067 | 19318 | 1626154 | 2018-12-31 21:14 | 2019-01-01 06:20 | 545.8167 | 11kV | 6003.9833 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 199712 B & C Phase DOLF : 20 Amp | December | 2018 | 2019Q2 | 2019 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2018-12-31 | N | 545.8167 | N | 17 | N | N | 1.1101 | 39.4971 | 4387.5339
[7 empty] | 6064 | 8292 | 1626228 | 2019-01-01 05:54 | 2019-01-01 07:15 | 81 | 11kV | 81 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 199720 Single phase DOLF : 10 Amp v=242 load= 4/1/1 Excluded OMS 1626228 | January | 2019 | 2019Q3 | 2019 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2019-01-01 | N | 81 | N | 19 | N | N | 1.1101 | 39.4971 | 59.1924
[7 empty] | 7167 | 20274 | 1626227 | 2019-01-01 03:03 | 2019-01-01 08:01 | 298 | 11kV | 181290 | 1191 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 42 tripped on Relays: Timed O/C, Earth Fault, EFI At HVC129 HDO operated. Cause: Flashover caused by possum at UGOH to HV129 - found feeder to be supplied by unknown parallel 1926965 1626969 1626970 1626978 1626227 | January | 2019 | 2019Q3 | 2019 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | OH | Not Veg | 2019-01-01 | N | 152.2166 | N | 19 | N | N | 1.1101 | 39.4971 | 132481.3849
[7 empty] | 6673 | 15034 | 1626191 | 2019-01-01 08:05 | 2019-01-01 08:28 | 23 | 11kV | 46 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199723 Single phase DOLF : 10 Amp Excluded OMS 1626258 | January | 2019 | 2019Q3 | 2019 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2019-01-01 | N | 23 | N | 19 | N | N | 1.1101 | 39.4971 | 33.6154
[7 empty] | 6785 | 16113 | 1626099 | 2018-12-31 19:48 | 2019-01-01 10:45 | 897 | 11kV | 2691 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 199734 C Phase DOLF : 10 Amp Excluded OMS 1626099 | December | 2018 | 2019Q2 | 2019 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2018-12-31 | N | 897 | N | 17 | N | N | 1.1101 | 39.4971 | 1966.5034
[7 empty] | 5666 | 4315 | 1626242 | 2019-01-01 07:31 | 2019-01-01 12:18 | 287 | 11kV | 574 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 199740 B & C Phase DOLF : 16 Amp Excluded OMS 1626242 | January | 2019 | 2019Q3 | 2019 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Veg | 2019-01-01 | N | 287 | N | 19 | N | N | 1.1101 | 39.4971 | 419.4623
[7 empty] | 5713 | 4806 | 1626235 | 2019-01-01 06:49 | 2019-01-01 12:25 | 336 | 11kV | 2352 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199743 C Phase DOLF : 10 Amp Excluded OMS 1626235 | January | 2019 | 2019Q3 | 2019 | 511:29876 | 511:29876 | ZN00511/029876 | MAITLAND | OH | Veg | 2019-01-01 | N | 336 | N | 19 | N | N | 1.1101 | 39.4971 | 1718.7722
[7 empty] | 6528 | 13648 | 1626268 | 2019-01-01 09:49 | 2019-01-01 12:25 | 156 | 11kV | 156 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199741 Single phase DOLF : 10 Amp Excluded OMS 1626268 | January | 2019 | 2019Q3 | 2019 | 526:34635 | 526:34635 | ZN00526/034635 | CESSNOCK | OH | Veg | 2019-01-01 | N | 156 | N | 19 | N | N | 1.1101 | 39.4971 | 114.0002
[7 empty] | 5605 | 3595 | 1626245 | 2019-01-01 07:47 | 2019-01-01 13:55 | 368 | 11kV | 1104 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199747 B Phase DOLF : 10 Amp Excluded OMS 1626245 | January | 2019 | 2019Q3 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2019-01-01 | N | 368 | N | 19 | N | N | 1.1101 | 39.4971 | 806.7706
[7 empty] | 5432 | 1195 | 1626307 | 2019-01-01 12:51 | 2019-01-01 14:00 | 69 | 11kV | 69 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199748 B Phase DOLF : 10 Amp Excluded OMS 1626307 | January | 2019 | 2019Q3 | 2019 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2019-01-01 | N | 69 | N | 19 | N | N | 1.1101 | 39.4971 | 50.4232
[7 empty] | 6588 | 14295 | 1626231 | 2019-01-01 06:26 | 2019-01-01 14:30 | 484 | 11kV | 968 | 2 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199755 # Phase DOLF : 10 Amp B & C LVF 100 Amp DOLF & LA's damaged by lightening at PT 18873. Extended area to include feeder with other sub in LV// | January | 2019 | 2019Q3 | 2019 | 238:34150 | 238:34150 | ZN00238/034150 | NEWCASTLE | OH | Not Veg | 2019-01-01 | N | 484 | N | 19 | N | N | 1.1101 | 39.4971 | 707.3858
[7 empty] | 5439 | 1288 | 1626246 | 2019-01-01 11:24 | 2019-01-01 15:40 | 256.2 | 11kV | 256.2 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 199763 B Phase DOLF : 10 Amp SURGE ARRESTOR FAILED SOON AFTER TX RESTORED TO SERVICE, | January | 2019 | 2019Q3 | 2019 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2019-01-01 | N | 256.2 | N | 19 | N | N | 1.1101 | 39.4971 | 187.2234
[7 empty] | 6879 | 17344 | 1626300 | 2019-01-01 12:06 | 2019-01-01 16:00 | 234 | 11kV | 234 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 199772 A Phase DOLF : 10 Amp Exxcluded OMS 1626300 | January | 2019 | 2019Q3 | 2019 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2019-01-01 | N | 234 | N | 19 | N | N | 1.1101 | 39.4971 | 171.0003
[7 empty] | 6135 | 9260 | 1626331 | 2019-01-01 15:22 | 2019-01-01 16:20 | 58 | 11kV | 116 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 199777 B Phase DOLF : 10 Amp Excluded OMS 1626331 | January | 2019 | 2019Q3 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2019-01-01 | N | 58 | N | 19 | N | N | 1.1101 | 39.4971 | 84.7694
[7 empty] | 6847 | 16857 | 1626351 | 2019-01-01 16:26 | 2019-01-01 18:40 | 134 | 11kV | 134 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 199786 Single phase DOLF : 10 Amp Excluded OMS 1626351 | January | 2019 | 2019Q3 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2019-01-01 | N | 134 | N | 19 | N | N | 1.1101 | 39.4971 | 97.9232
[7 empty] | 6474 | 13022 | 1626369 | 2019-01-01 18:24 | 2019-01-01 20:30 | 126 | 11kV | 252 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199787 A & C Phase : 10 Amp Excluded OMS 1626379 Tx Volts: 242V Tx load: 9A | January | 2019 | 2019Q3 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2019-01-01 | N | 126 | N | 19 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 5791 | 5489 | 1626382 | 2019-01-01 19:52 | 2019-01-01 21:34 | 102 | 11kV | 145318 | 1557 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN9252 Jannali 11kv Panel 22 'Jannali Aux No1" feeder tripped, reclosed & tripped Relays: 'C' phase IOC, L/O, efi Signals: trip Field efis: S63052, S9840 Remarks: UG fault. 11kv fault from S9840 Robertson Adelong to S78816 Woronora Cemetery | January | 2019 | 2019Q3 | 2019 | ZN9252:PA22 | ZN9252:PA22 | ZN09252/000022 | SUTHERLAND | UG | Not Veg | 2019-01-01 | N | 93.332 | N | 19 | N | N | 1.1101 | 39.4971 | 106194.1082
[7 empty] | 6843 | 16838 | 1626141 | 2018-12-31 20:43 | 2019-01-01 21:50 | 1507 | 11kV | 76045 | 457 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 189697 1 fault operation Sub 50022 & 50926 possibly faulty and require testing & replacement. Excluded OMS 1626141 & 1626215 | December | 2018 | 2019Q2 | 2019 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2018-12-31 | N | 166.4004 | N | 17 | N | N | 1.1101 | 39.4971 | 55571.4431
[7 empty] | 5381 | 521 | 1626376 | 2019-01-01 19:04 | 2019-01-01 22:30 | 206 | 11kV | 128971 | 1513 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Hot >35C | N | LID 199792 2 fault operations 3 phase Overcurrent 11kV Hazemeyer Switchgear on fire. Excluded OMS No. 1626376+1626379 | January | 2019 | 2019Q3 | 2019 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2019-01-01 | N | 85.2419 | N | 19 | N | N | 1.1101 | 39.4971 | 94248.2028
[7 empty] | 5695 | 4618 | 1626388 | 2019-01-01 20:26 | 2019-01-02 00:25 | 239 | 11kV | 478 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 199791 Single Phase OHM down at pole 8H-50061. | January | 2019 | 2019Q3 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-01-01 | N | 239 | N | 19 | N | N | 1.1101 | 39.4971 | 349.3083
[7 empty] | 7054 | 19146 | 1626405 | 2019-01-01 22:52 | 2019-01-02 02:10 | 198 | 11kV | 1202 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 199793 3 fault operations no fault found please patrol in daylight. Excluded oms report no 1626405. | January | 2019 | 2019Q3 | 2019 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Veg | 2019-01-01 | N | 171.7143 | N | 19 | N | N | 1.1101 | 39.4971 | 878.3861
[7 empty] | 6255 | 10474 | 1626273 | 2019-01-01 07:44 | 2019-01-02 10:44 | 1620 | 11kV | 1620 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 199744 B Phase : 10 Amp On try back TX vented oil and again blew B phase dolf. D Davies advised depot staff to replace Tx on 2 Jan 2019. TX replaced Excluded OMS 1626273. | January | 2019 | 2019Q3 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2019-01-01 | N | 1620 | N | 19 | N | N | 1.1101 | 39.4971 | 1183.8482
[7 empty] | 5683 | 4441 | 1626448 | 2019-01-02 08:52 | 2019-01-02 11:25 | 153 | 11kV | 153 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199799 B & C Phase DOLF : 10 Amp Excluded OMS 1626448 | January | 2019 | 2019Q3 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2019-01-02 | N | 153 | N | 8 | N | N | 1.1101 | 39.4971 | 111.8079
[7 empty] | 5855 | 5948 | 1626582 | 2019-01-02 13:24 | 2019-01-02 14:45 | 81 | 11kV | 162 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199806 Single phase DOLF : 10 Amp Excluded OMS 1626582 | January | 2019 | 2019Q3 | 2019 | 526:34635 | 526:34635 | ZN00526/034635 | CESSNOCK | OH | Veg | 2019-01-02 | N | 81 | N | 8 | N | N | 1.1101 | 39.4971 | 118.3848
[7 empty] | 6817 | 16563 | 1626508 | 2019-01-02 11:45 | 2019-01-02 15:34 | 229 | 11kV | 2189 | 113 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 199807 3 phase section isolated to repair fallen 11kv mains to Gibson sub 54425. b phase 16 amp dolf was replaced at sub 54425 Excluded oms 1626546 | January | 2019 | 2019Q3 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2019-01-02 | N | 19.3717 | N | 8 | N | N | 1.1101 | 39.4971 | 1599.6566
[7 empty] | 6762 | 15729 | 1626626 | 2019-01-02 15:18 | 2019-01-02 17:05 | 107 | 11kV | 107 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199809 Single phase DOLF : 10 Amp Excluded OMS 1626626 | January | 2019 | 2019Q3 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2019-01-02 | N | 107 | N | 8 | N | N | 1.1101 | 39.4971 | 78.1924
[7 empty] | 6441 | 12600 | 1626638 | 2019-01-02 15:53 | 2019-01-02 17:35 | 102 | 11kV | 306 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199810 Single phase DOLF : 10 Amp Excluded OMS 1626638 | January | 2019 | 2019Q3 | 2019 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2019-01-02 | N | 102 | N | 8 | N | N | 1.1101 | 39.4971 | 223.6158
[7 empty] | 6521 | 13603 | 1626637 | 2019-01-02 15:51 | 2019-01-02 19:22 | 211 | 11kV | 51362 | 782 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN3154 ST IVES 11kV CB PA19'Durham Memorial' fdr tripped Relays: A&B phase overcurrent Signals: nil Tree/Branch on OH mains. Large tree resting on 11kV and 415V mains adj PT1127 See 1626637,55,7385,6,7 | January | 2019 | 2019Q3 | 2019 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | OH | Veg | 2019-01-02 | N | 65.6803 | N | 8 | N | N | 1.1101 | 39.4971 | 37533.8347
[7 empty] | 6244 | 10385 | 1626681 | 2019-01-02 19:43 | 2019-01-02 21:00 | 77 | 11kV | 4774 | 62 | HV | Arcing | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | Ex ZN12570 AVOCA section of 11kV CB PA22 PT18482 MUNDOORA DAVISTOWN HVDO Carrier middle phase fixed line side contact found melted & gone HR/Open Abnormal: S.65223 Avoca Davistown replaced recently after MVA. Network was still abnormal. All links found open in LV Pillar WW-10253 (#37516), adj S.65223, with LV// #19934 Closed. Meaning all of Dist #2 @ S.65223 fed off PT.18482. Cause: HVDO Carrier Middle Phase Fixed Line Side Contact found melted, PT restored via LV//. See 1627372 ex 1626681 | January | 2019 | 2019Q3 | 2019 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2019-01-02 | N | 77 | N | 8 | N | N | 1.1101 | 39.4971 | 3488.6984
[7 empty] | 5568 | 3156 | 1626687 | 2019-01-02 21:30 | 2019-01-02 22:50 | 80 | 11kV | 80 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 199811 interrupt to replace noisey L/A Excluded oms 1626687 | January | 2019 | 2019Q3 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2019-01-02 | N | 80 | N | 8 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 5705 | 4714 | 1626724 | 2019-01-03 06:02 | 2019-01-03 08:10 | 128 | 11kV | 256 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199813 C Phase DOLF : 16 Amp Excluded OMS 1626724 | January | 2019 | 2019Q3 | 2019 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2019-01-03 | N | 128 | N | 10 | N | N | 1.1101 | 39.4971 | 187.0772
[7 empty] | 6181 | 9827 | 1626823 | 2019-01-03 10:11 | 2019-01-03 11:40 | 89 | 11kV | 267 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199817 B Phase DOLF : 16 Amp Excluded OMS 1626823 | January | 2019 | 2019Q3 | 2019 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Veg | 2019-01-03 | N | 89 | N | 10 | N | N | 1.1101 | 39.4971 | 195.1157
[7 empty] | 5384 | 590 | 1626840 | 2019-01-03 10:50 | 2019-01-03 13:20 | 150 | 11kV | 150 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199820 Single phase DOLF : 10 Amp 10 amp hvf replaced power restored 1320 Excluded OMS 1626840 | January | 2019 | 2019Q3 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2019-01-03 | N | 150 | N | 10 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 5357 | 211 | 1626875 | 2019-01-03 12:27 | 2019-01-03 15:35 | 188 | 11kV | 1316 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 199823 A & B Phase DOLF : 20 Amp Excluded OMS 1626875 | January | 2019 | 2019Q3 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2019-01-03 | N | 188 | N | 10 | N | N | 1.1101 | 39.4971 | 961.694
[7 empty] | 6069 | 8331 | 1626942 | 2019-01-03 15:15 | 2019-01-03 15:35 | 20 | 11kV | 3200 | 160 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Ex ZN12630 PEATS RIDGE section of 11kV CB PA1 AB 43179 OPENED FOR SWITCHING AT 1515 hrs LB 45074 CLOSED AT 1535 WITH 11 KV FEEDER FROM USL 43921 TO AB for SRR job 33636 Cause: INTERUPTED TO TAKE SUPPLY FROM ENDEAVOUR ENERGY FOR EMERGENCY POLE REPLACEMENT See 1627378 ex 1626942 | January | 2019 | 2019Q3 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2019-01-03 | N | 20 | N | 10 | N | N | 1.1101 | 39.4971 | 2338.4656
[7 empty] | 6802 | 16392 | 1626987 | 2019-01-03 18:04 | 2019-01-03 19:14 | 70 | 11kV | 66854 | 1059 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S342 Paddington ZN P16 tripped on 16R leg B phase OC/EF (kcg relay) no efi's Remarks: UG Fault. S342 Paddington P16 to S619 Oatley Rennie to S7836 Bayswater East | January | 2019 | 2019Q3 | 2019 | ZN342:PA16 | ZN342:PA16 | ZN00342/000016 | SYDNEY | UG | Not Veg | 2019-01-03 | N | 63.1294 | N | 10 | N | N | 1.1101 | 39.4971 | 48854.9313
[7 empty] | 5990 | 7385 | 1627003 | 2019-01-03 19:34 | 2019-01-03 20:11 | 37 | 11kV | 31709 | 857 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN12600 LISAROW 11kV CB PA13 'Tuggerah Mcdonalds' fdr tripped on: A&B phase overcurrent lockout reclose time delay Tree/branch on oh mains. in section o f feeder from USL 41021 to SwA @ S14131 near 11kv UGOH See 1627003 ex 1627005 | January | 2019 | 2019Q3 | 2019 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2019-01-03 | N | 37 | N | 10 | N | N | 1.1101 | 39.4971 | 23172.0019
[7 empty] | 6068 | 8329 | 1626977 | 2019-01-03 17:17 | 2019-01-03 21:12 | 235 | 11kV | 3764 | 173 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Ex ZN12630 PEATS RIDGE section of 11kV CB PA1 Abnormal:LB 45074 CLOSED AB 43179 OPEN Cause: emergency pole replacement INTERUPTED TO CARRYOUT SWITCHING ACROSS ENDEAVOUR ENERGY SYSTEM 45074 OPENED @ 21:08pm AB43179 CLOSED @ 21:12pm See 1626977,95,7382,3 | January | 2019 | 2019Q3 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2019-01-03 | N | 21.7572 | N | 10 | N | N | 1.1101 | 39.4971 | 2750.6202
[7 empty] | 7162 | 20132 | 1627017 | 2019-01-03 20:52 | 2019-01-04 01:09 | 257 | 11kV | 79893 | 558 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | @ZN1287 Revesby 11kv Panel 24 labelled "S61162 Revesby Workers Club No.2" tripped: Relays: A phase timmed Signals: 11kv CB.24 open, 11kv trip, Field EFI's: S61162, 4581 Remarks: burnt bond on UGOH to PT1533 English St. Repaired by L/men | January | 2019 | 2019Q3 | 2019 | ZN1287:PA24 | ZN1287:PA24 | ZN01287/000024 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-01-03 | N | 143.1774 | N | 10 | N | N | 1.1101 | 39.4971 | 58383.448
[7 empty] | 6298 | 10870 | 1627085 | 2019-01-03 23:42 | 2019-01-04 02:08 | 146 | 11kV | 112029 | 1030 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S1673 Turramurra Panel 7 tripped on A and B phase OC EFI, Fault Check and TX2 Group Earth Cause not ascertained: Section Isolated between S4709 to S4710 tee PT1751 See OMS 1628205 1628207 1628208 1627085 | January | 2019 | 2019Q3 | 2019 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Veg | 2019-01-03 | N | 108.766 | N | 10 | N | N | 1.1101 | 39.4971 | 81867.4889
[7 empty] | 5562 | 3092 | 1627099 | 2019-01-04 01:55 | 2019-01-04 03:32 | 97 | 11kV | 293328 | 3024 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn4545 Meadowbank Panel 31 tripped on Relays: A B and C phase OC and Earth Fault, EFI and Fault Check Signals: 11kV trip Cause not ascertained for outage see OMS 1627099 1627101 | January | 2019 | 2019Q3 | 2019 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Veg | 2019-01-04 | N | 97 | N | 5 | N | N | 1.1101 | 39.4971 | 214355.4507
[7 empty] | 6156 | 9459 | 1627121 | 2019-01-04 07:25 | 2019-01-04 08:33 | 68 | 11kV | 2788 | 41 | HV | Animal Other | Animal | Stay Wire | Unplanned | No Weather Impact | N | LID 199831 1 Fault operations, overcurrent bulls rubbing on stay wire, 2nd span past Sw 63470 CC1: 06-"Urgent - O.H Mains - No others" | January | 2019 | 2019Q3 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2019-01-04 | N | 68 | N | 5 | N | N | 1.1101 | 39.4971 | 2037.3882
[7 empty] | 5794 | 5506 | 1627210 | 2019-01-04 10:57 | 2019-01-04 12:15 | 78 | 11kV | 78 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 199836 10 Amp Substation DOLF Known as 898 Gundy rd Arrowfield Stud theres a huge sign. Wires have snapped at Pole 61038 located come into front gate than go to office to be taken to pole. 04/01/19 10:58: No arcing or sparking and has lost supply. | January | 2019 | 2019Q3 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2019-01-04 | N | 78 | N | 5 | N | N | 1.1101 | 39.4971 | 57.0001
[7 empty] | 5609 | 3619 | 1627306 | 2019-01-04 14:50 | 2019-01-04 15:35 | 45 | 11kV | 720 | 16 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | LID 199841 B Phase DOLF : 20 Amp Faigued sub DOLF arcing & sparking. Excluded OMS No. 1627306, 1627311, 1627313, 1627318 | January | 2019 | 2019Q3 | 2019 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2019-01-04 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 6345 | 11401 | 1627410 | 2019-01-04 19:15 | 2019-01-05 01:45 | 390.3333 | 11kV | 13271.3333 | 34 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 199842 Single phase 10 Amp Line DOLF section isolated to repair HV mains | January | 2019 | 2019Q3 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2019-01-04 | N | 390.3333 | N | 5 | N | N | 1.1101 | 39.4971 | 9698.299
[7 empty] | 6677 | 15063 | 1627414 | 2019-01-05 10:20 | 2019-01-05 11:35 | 75 | 11kV | 825 | 11 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | LID 199846 A phase Inadequate design or construction, Low 11kV OHM on 1 ph, reported from Electrical Contractor Found pole stated on job but could not find any issues. Spoke to electrician who was adament wire hanging low. Oncall to investage further tomorrow during daylight hours. Difficult access area. | January | 2019 | 2019Q3 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-01-05 | N | 75 | N | 11 | N | N | 1.1101 | 39.4971 | 602.8857
[7 empty] | 6977 | 18294 | 1627468 | 2019-01-05 09:50 | 2019-01-05 12:15 | 145 | 11kV | 83390 | 699 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | Y | ZN12650 WEST GOSFORD 11kV CB PA10 'Donnison st' fdr tripped on Relays: E/F A PHase EFI Signals: 11kv trip EFI: S18475 S18400 S78315 S78328 S14924 S14925 S18165 Cause: UG fault. EFI's indications at S18165 did not indicate the first trip @0950 CP79707 no EFI's 11kv fdr fault from S18165 to S13511 to S12306 See 1628728,9,30 ex 1627468 | January | 2019 | 2019Q3 | 2019 | ZN12650:PA10 | ZN12650:PA10 | ZN12650/000010 | CENTRAL COAST | UG | Not Veg | 2019-01-05 | Y | 119.299 | N | 11 | N | Y | 1.1101 | 39.4971 | 60938.9524
[7 empty] | 6638 | 14731 | 1627461 | 2019-01-05 09:13 | 2019-01-05 12:53 | 220 | 11kV | 111466 | 1025 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | At Zn15014 Mona Vla ePanel 7 Cabbage Tree Annam Recloser CP20397 Pittwater Cabbage Tree tripped and Locked out on OC trip, IOC trip Lockout Cause: Tree branch brought down OH See OMS 1629323 1629324 | January | 2019 | 2019Q3 | 2019 | ZN15014:PA7 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2019-01-05 | N | 108.7473 | N | 11 | N | N | 1.1101 | 39.4971 | 81456.0651
[7 empty] | 6233 | 10311 | 1627479 | 2019-01-05 04:51 | 2019-01-05 14:10 | 559 | 11kV | 10644 | 1158 | HV | Animal Bird | Animal | DC-PT Transformer | Unplanned | Hot >35C | Y | Ex ZN13000 LAKE MUNMORAH section of 11kV CB PA5R 'Bay Vista Pinnaroo' RE45140 Pinaroo Colledina tripped & reclosed Relays: Earth Fault PT14328 Parraweena Kanangra HDO Road side phase 50A HDO Cause: Animals/Birds DO patrolled main feeder line this morning See 1628636,7 ex 1627479 | January | 2019 | 2019Q3 | 2019 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Not Veg | 2019-01-05 | Y | 9.1917 | N | 11 | N | Y | 1.1101 | 39.4971 | 7778.3213
[7 empty] | 6340 | 11323 | 1627475 | 2019-01-05 10:22 | 2019-01-05 15:45 | 323 | 11kV | 78068 | 781 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Hot >35C | Y | LID 199847 2 fault operations A & B phase Overcurrent; Earth Fault Faulty arrestor on 11kv UGOH pole SW-80122. Excluded oms report no 1627475. | January | 2019 | 2019Q3 | 2019 | 222:33601 | 222:33601 | ZN00222/033601 | LAKE MACQUARIE | OH | Not Veg | 2019-01-05 | N | 99.959 | N | 11 | N | N | 1.1101 | 39.4971 | 57049.7918
[7 empty] | 6265 | 10550 | 1627535 | 2019-01-05 15:05 | 2019-01-05 16:15 | 70 | 11kV | 910 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | Y | LID 199850 B phase 16 Amp fuse, substation DOLF | January | 2019 | 2019Q3 | 2019 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2019-01-05 | N | 70 | N | 11 | N | N | 1.1101 | 39.4971 | 665.0012
[7 empty] | 6510 | 13428 | 1627488 | 2019-01-05 10:54 | 2019-01-05 16:30 | 336 | 11kV | 8847 | 120 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | Y | LID 199848 2 Fault operations, Overcurrent 11kV main down between poles JT-10725 and JT-10728 | January | 2019 | 2019Q3 | 2019 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2019-01-05 | N | 73.725 | N | 11 | N | N | 1.1101 | 39.4971 | 6465.1267
[7 empty] | 5595 | 3521 | 1627539 | 2019-01-05 15:18 | 2019-01-05 16:32 | 74 | 11kV | 148 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Hot >35C | Y | LID 199851 A phase, 10 Amp fuse substation DOLF | January | 2019 | 2019Q3 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2019-01-05 | N | 74 | N | 11 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 6589 | 14301 | 1627544 | 2019-01-05 15:26 | 2019-01-05 16:47 | 81 | 11kV | 140913 | 1750 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | Y | At ZN1850 Bass Hill 11kv Panel '32', labelled 'S35437 Carnarvon Heron', tripped on: Relays: A Protection: ABC OC, B protection: AB & N OC and EFI Signals: 11kv trip Abnormal: Sw/B closed at S47485 Bambil Rex with Sw/A Open at S5081 Bellevue Birdword Remarks: Suspected lightning strike outside 10 whitmore Ave (See note on soft copy) | January | 2019 | 2019Q3 | 2019 | ZN1850:PA40 | ZN1850:PA40 | ZN01850/000040 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-01-05 | Y | 80.5217 | N | 11 | N | Y | 1.1101 | 39.4971 | 102975.0642
[7 empty] | 6552 | 13844 | 1627557 | 2019-01-05 15:43 | 2019-01-05 17:45 | 122 | 11kV | 39668 | 352 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Lightning | Y | Section of Panel 22 Hornsby Hunter Bridge West Recloser CP2935 Somerville Pike Tripped on SEF 400KVA PT 634 Somerville Camri struck by lightning 42 63Amp fuses blwon See OMS 1629340 1629342 1629345 1629344 1627557 | January | 2019 | 2019Q3 | 2019 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Not Veg | 2019-01-05 | N | 112.6932 | N | 11 | N | N | 1.1101 | 39.4971 | 28988.2044
[7 empty] | 6746 | 15514 | 1627570 | 2019-01-05 16:04 | 2019-01-05 17:54 | 110 | 11kV | 119240 | 1084 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | Ex ZN12650 WEST GOSFORD section of 11kV CB PA6 IR50531 Showground Maliwa 0.35 tripped and locked out on OC Cause not ascertained. lightning storm. mains to patrol | January | 2019 | 2019Q3 | 2019 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Veg | 2019-01-05 | Y | 110 | N | 11 | N | Y | 1.1101 | 39.4971 | 87137.075
[7 empty] | 6422 | 12305 | 1627688 | 2019-01-05 18:03 | 2019-01-05 19:19 | 76 | 11kV | 79420 | 1045 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | At ZN3472 Sefton 11kv Panel '22' labelled 'S.1279 Virgil Ave' tripped on: Relays: IOC A&C phase, earth fault, EFI and fault check Signals: 11kv trip Abnormal: S5964 Helen Virgil is OOS and in LV// with Panel 22 Remarks: Blown HDO found PT1658 Kembla Waldron, suspect multiple lightning strikes on same feeder. S.5964 Helen Virgil is OOS and in LV// with Panel 22 see OMS 1627692. | January | 2019 | 2019Q3 | 2019 | ZN3472:PA22 | ZN3472:PA22 | ZN03472/000022 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-01-05 | Y | 76 | N | 11 | N | Y | 1.1101 | 39.4971 | 58037.7935
[7 empty] | 5859 | 5995 | 1627643 | 2019-01-05 17:17 | 2019-01-05 19:35 | 138 | 11kV | 29646 | 234 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | Y | At S9534 Kurnell Sth; Panel 11 tripped, closed, tripped and locked out on: "cook captain fdr" Basler relay 51N Field EFI's: CP35952 Remarks: lightning. Surge arrestors at PT9602 hit by lightning | January | 2019 | 2019Q3 | 2019 | ZN9534:PA11 | ZN9534:PA11 | ZN09534/000011 | SUTHERLAND | OH | Not Veg | 2019-01-05 | N | 126.6923 | N | 11 | N | N | 1.1101 | 39.4971 | 21664.4224
[7 empty] | 5761 | 5269 | 1627724 | 2019-01-05 18:34 | 2019-01-05 20:37 | 123 | 11kV | 103080 | 1001 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | Y | At Zn3152 St Ives Panel 16 tripped on B and C phase overcurent Signals: 11kV Trip with EFI Cause: DOp patrolled and cause not ascertained See OMS 1629352 1629353 1627724 | January | 2019 | 2019Q3 | 2019 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Veg | 2019-01-05 | N | 102.977 | N | 11 | N | N | 1.1101 | 39.4971 | 75327.8237
[7 empty] | 6062 | 8263 | 1627787 | 2019-01-05 19:27 | 2019-01-05 22:57 | 210 | 11kV | 171289 | 939 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | Y | Zn12610 Long Jetty Panel 20 "Matcham St" fdr tripped on Relays: B&C phase IOC and EF Singals: 11kv trip Cause: not ascertained. lightning storm See 1628659,61,2,3 ex 1627787 | January | 2019 | 2019Q3 | 2019 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Veg | 2019-01-05 | Y | 182.4164 | N | 11 | N | Y | 1.1101 | 39.4971 | 125172.949
[7 empty] | 6598 | 14355 | 1627808 | 2019-01-05 19:47 | 2019-01-05 23:17 | 210 | 11kV | 56490 | 269 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | LID 199854 Pole Mounted RAGCB Tree branch removed from OHM adjacent pole KR-960067 | January | 2019 | 2019Q3 | 2019 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2019-01-05 | N | 210 | N | 11 | N | N | 1.1101 | 39.4971 | 41281.2258
[7 empty] | 5625 | 3745 | 1627824 | 2019-01-05 19:58 | 2019-01-06 00:05 | 247 | 11kV | 16907 | 71 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | Y | Ex ZN12630 PEATS RIDGE section of 11kV CB PA3 'Mangrove Mountain' IR49206 Mangrove Mtn West tripped on OC PT65652 Waratah Borrisbrook has a defective surge arrestor See 1628598,600 ex 1627824 | January | 2019 | 2019Q3 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2019-01-05 | Y | 238.1268 | N | 11 | N | Y | 1.1101 | 39.4971 | 12355.1369
[7 empty] | 6868 | 17118 | 1627700 | 2019-01-05 18:16 | 2019-01-06 00:50 | 394 | 11kV | 508944 | 2443 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | Y | At ZN35500 Top Ryde Panel 24 Tripped on A B and C phase overcurrent Abnormal Switching: SW/B closed at S7493 and SW/Opened at S8328 Cause: Lightning arrestor blown at UGOH vicinity to S7493 to AB3785 to S46331 See OMS 1629361 1629363 1629364 1627700 1627723 1627745 | January | 2019 | 2019Q3 | 2019 | ZN35500:PA24 | ZN35500:PA24 | ZN35500/000024 | RYDE | OH | Not Veg | 2019-01-05 | N | 208.3275 | N | 11 | N | N | 1.1101 | 39.4971 | 371921.2639
[7 empty] | 6012 | 7763 | 1627926 | 2019-01-05 23:15 | 2019-01-06 03:00 | 225 | 11kV | 156990 | 1298 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | ZN12660 WOY WOY 11kV CB PA8 North Burge Rd" Relays: A phase IOC, Earth Fault, EFI Signals: 11kv trip Cause: lightning. burnt wire down adjacent LB45205 See 1627926,30,1,5,8609,10,1 | January | 2019 | 2019Q3 | 2019 | ZN12660:PA8 | ZN12660:PA8 | ZN12660/000008 | CENTRAL COAST | OH | Not Veg | 2019-01-05 | Y | 120.9476 | N | 11 | N | Y | 1.1101 | 39.4971 | 114723.6616
[7 empty] | 6134 | 9238 | 1627901 | 2019-01-05 22:23 | 2019-01-06 06:12 | 469 | 11kV | 228214 | 1573 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | At ZN2310 Punchbowl Panel 23 'Roseview Ave,LB893' tripped Relays: 'A' Prot, IOC 'A&B' phase, 'B' Prot IOC, L/O Signals: 11kv trip Remarks: OH down. 11kv down in Acacia St | January | 2019 | 2019Q3 | 2019 | ZN2310:PA23 | ZN2310:PA30 | ZN02310/000030 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-01-05 | Y | 145.082 | N | 11 | N | Y | 1.1101 | 39.4971 | 166772.06
[7 empty] | 5680 | 4410 | 1627761 | 2019-01-05 19:14 | 2019-01-06 07:40 | 746 | 11kV | 1659923 | 3528 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn12650 West Gosford Panel 1 'Dog Trap Rd' tripped on Relays: B&C phase OC, Earth Fault, EFI, Reclose and lock out Signals: 11kv trip EFI: N/A Abnormal: AB42057 is closed LB41071 is open Lightning burnt down 11kv wire below RE44937 See 1628744,5 ex 1627761,946 | January | 2019 | 2019Q3 | 2019 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2019-01-05 | Y | 470.4997 | N | 11 | N | Y | 1.1101 | 39.4971 | 1213022.769
[7 empty] | 6283 | 10736 | 1627906 | 2019-01-05 21:56 | 2019-01-06 09:00 | 664 | 11kV | 7304 | 11 | HV | Vegetation Blow/Fall In | Vegetation | Lightning Arrestor | Unplanned | Lightning | Y | Ex ZN14144 WAMBERAL section of 11kV CB PA2 PT11285 OAK COACHWOOD 0.5 HDO's operated road and middle pahse 10 Amp NGK Tree branch on OH mains. DOp cleared paper bark off the HDO's and surge arrestors See 1628606 ex 1627906,80 | January | 2019 | 2019Q3 | 2019 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2019-01-05 | Y | 664 | N | 11 | N | Y | 1.1101 | 39.4971 | 5337.5478
[7 empty] | 6122 | 9119 | 1627984 | 2019-01-06 07:30 | 2019-01-06 09:20 | 110 | 11kV | 110 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 199863 10 Amp fuse | January | 2019 | 2019Q3 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2019-01-06 | N | 110 | N | 7 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 7113 | 19663 | 1627962 | 2019-01-06 08:00 | 2019-01-06 10:40 | 160 | 11kV | 11360 | 71 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 199861 HV reported down, subs interrupted due to car accident FIRE RESCUE - IAN CAR HAS HIT POWER POLE - POLE# OP30171 INCIDENT# 3828 06/01/19 07:02: POLE# ON WEB GIS IS DP30171 | January | 2019 | 2019Q3 | 2019 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2019-01-06 | N | 160 | N | 7 | N | N | 1.1101 | 39.4971 | 8301.5529
[7 empty] | 7050 | 19091 | 1628003 | 2019-01-06 08:38 | 2019-01-06 11:20 | 162 | 11kV | 324 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 1628817 Single phase DOLF : 10 Amp Excluded OMS 1628003 | January | 2019 | 2019Q3 | 2019 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2019-01-06 | N | 162 | N | 7 | N | N | 1.1101 | 39.4971 | 236.7696
[7 empty] | 7143 | 19918 | 1627917 | 2019-01-06 08:18 | 2019-01-06 11:30 | 192 | 11kV | 1344 | 7 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 199868 C ph live line lead broken off top of DOLF on Sub 27518. Open removed and DT LVF's 27518. Open removed and DT DOLF's 27518. Interruption 0835hrs. O/H crew required to carry out repairs. | January | 2019 | 2019Q3 | 2019 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2019-01-06 | N | 192 | N | 7 | N | N | 1.1101 | 39.4971 | 982.1556
[7 empty] | 5626 | 3756 | 1627865 | 2019-01-05 21:00 | 2019-01-06 11:45 | 885 | 11kV | 2655 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | LID 199866 16 Amp fuse, Line DOLF | January | 2019 | 2019Q3 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2019-01-05 | Y | 885 | N | 11 | N | Y | 1.1101 | 39.4971 | 1940.1957
[7 empty] | 6237 | 10320 | 1627888 | 2019-01-05 22:11 | 2019-01-06 14:52 | 1001 | 11kV | 217660 | 318 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Lightning | Y | Ex ZN12630 PEATS RIDGE section of 11kV CB PA1 'Gunderman' RE61375 'Wisferry Biara 1.3 tripped and locked out Cause: OH down. 11kv overhead wire down between 11kv usl 43962 and RE45013 Gunderman See interruption for non phasing BSP change over See 1627888,8028,30,2,65,622,4,6,7 | January | 2019 | 2019Q3 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2019-01-05 | Y | 684.4654 | N | 11 | N | Y | 1.1101 | 39.4971 | 159059.5081
[7 empty] | 6982 | 18323 | 1628086 | 2019-01-06 14:15 | 2019-01-06 17:50 | 215 | 11kV | 101695 | 473 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV CB PA12 LB48839Z interrupted for safety reasons due to 11kV mains on corss arm untied from pins See 1635293 ex 1628086 | January | 2019 | 2019Q3 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2019-01-06 | N | 215 | N | 7 | N | N | 1.1101 | 39.4971 | 74315.7065
[7 empty] | 6530 | 13661 | 1628147 | 2019-01-06 20:34 | 2019-01-06 21:00 | 26 | 11kV | 4082 | 157 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 199870 tapping came off at abs 63808 during emergency switching t0006, sub 64985 only sub interrupted. Excluded oms # 1628147 | January | 2019 | 2019Q3 | 2019 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2019-01-06 | N | 26 | N | 7 | N | N | 1.1101 | 39.4971 | 2983.0052
[7 empty] | 6053 | 8171 | 1628156 | 2019-01-06 21:40 | 2019-01-07 02:15 | 274.7833 | 11kV | 28572.6833 | 104 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 199871 11KV section isolated to replace xarm at pole IU-61741, subs 48527 & 77242 interrupted as they would not hold up on LV // Excluded oms # 1628147 | January | 2019 | 2019Q3 | 2019 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2019-01-06 | N | 274.7373 | N | 7 | N | N | 1.1101 | 39.4971 | 20880.0742
[7 empty] | 7114 | 19665 | 1628175 | 2019-01-07 05:07 | 2019-01-07 06:54 | 107 | 11kV | 281107 | 2985 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S2310 Punchbowl Zn Panel #4 labelled Pentland Payten tripped on Relays: A & B phase IOC, Earth fault, EFI Remarks: UG fault. 11kv UG cable fault from S4761 Wangee Yangoora to S6246 Boorea Merrick | January | 2019 | 2019Q3 | 2019 | ZN2310:PA4 | ZN2310:PA4 | ZN02310/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-01-07 | N | 94.1732 | N | 5 | N | N | 1.1101 | 39.4971 | 205424.7043
[7 empty] | 6546 | 13786 | 1628203 | 2019-01-07 08:05 | 2019-01-07 12:35 | 270 | 11kV | 2160 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 199874 No protection operation, Chris Pengelly opened Sw 74200 upon finding mains down. Tree on mains brought mains down between Stoney Ck RAGCB and sub 70214. Section isolated and repairs completed | January | 2019 | 2019Q3 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2019-01-07 | N | 270 | N | 5 | N | N | 1.1101 | 39.4971 | 1578.4643
[7 empty] | 5947 | 6922 | 1628566 | 2019-01-07 13:02 | 2019-01-07 15:30 | 148 | 11kV | 16381 | 236 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At ZN2466 Flemington 11kv Panel No27 "S2566 Carter King" feeder tripped on Relays: E/F, EFI, Fault check Signals: 11kv trip, Zone e, Tx3 group E Remarks: UG cable damaged by contractor. Suspect 11kv cable strike from Excavator by contractor o/s #7 Carter Street, Lidcombe. Section of 11kv ex ZN2466 Flemington Panel 27. 11kv feeder from S77660 Carter Birnie No.1 (Sw/B) to CP1006 Carter St (Sw/A) to S7860 Carter Uhrig No.3 (Sw/A) tee S4537 Carter Record Co | January | 2019 | 2019Q3 | 2019 | ZN2466:PA27 | ZN2466:PA1 | ZN02466/000001 | PARRAMATTA | UG | Not Veg | 2019-01-07 | N | 69.411 | N | 5 | N | N | 1.1101 | 39.4971 | 11970.7516
[7 empty] | 6853 | 16961 | 1628733 | 2019-01-07 16:49 | 2019-01-07 19:15 | 146 | 11kV | 5218 | 97 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S8000 Macquarie Park Panel 387 tripped on timed overcurrent amd earth fault. Cause: 11kV Feeder fault between S7225 and S5887 tee S3763 See OMS 1629886 1629888 1629887 1629889 1628733 | January | 2019 | 2019Q3 | 2019 | ZN8000:PA38 | ZN8000:PA38 | ZN08000/000038 | RYDE | UG | Not Veg | 2019-01-07 | N | 53.7938 | N | 5 | N | N | 1.1101 | 39.4971 | 3813.1605
[7 empty] | 5865 | 6053 | 1628768 | 2019-01-07 19:35 | 2019-01-07 20:35 | 60 | 11kV | 4320 | 72 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZN36200 EMPIRE BAY section of 11kV CB PA8 PT12217 WARDS HILL STEWART 11kv 20amp HV Drop out fuse (roadside phase) blown Cause: pole fire. 11kV HV HDO failed to operate See 1628768,9,900 | January | 2019 | 2019Q3 | 2019 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2019-01-07 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 3156.9286
[7 empty] | 6170 | 9614 | 1628949 | 2019-01-08 13:16 | 2019-01-08 13:20 | 4 | 11kV | 304 | 76 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN12650 WEST GOSFORD section of 11kV CB PA1 AB43611 interrupted to remove branch Cause: Tree/Branch on oh mains AB43611 | January | 2019 | 2019Q3 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2019-01-08 | N | 4 | N | 6 | N | N | 1.1101 | 39.4971 | 222.1542
[7 empty] | 6378 | 11767 | 1628845 | 2019-01-08 09:24 | 2019-01-08 15:45 | 381 | 11kV | 153118 | 1325 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn14143 Somersby Panel 12 tripped on B phase IOC Cause: CP42602 to CP45416 to CP64564 tee PT11662 PT11777 PT14433 broken cross arm curringah near arunta at karion See 1629175,6 ex 1628845,98 | January | 2019 | 2019Q3 | 2019 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Not Veg | 2019-01-08 | N | 115.5608 | N | 6 | N | N | 1.1101 | 39.4971 | 111894.1182
[7 empty] | 6957 | 18091 | 1629073 | 2019-01-08 20:16 | 2019-01-08 21:13 | 57 | 11kV | 25330 | 502 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S36100 Rose Bay Zone 11kv Panel 13 "S7837 Newcastle New South" feeder tripped on: Relays: B & C Phase IOC, EFI, Fault check Signals: Tx1 Group earth, 11kv trip Remarks: UG Fault. Section of 11kv feeder defective from S7837 Newcastle New South to S36119 Rawson new South Head to S47001 Vickery Ave | January | 2019 | 2019Q3 | 2019 | ZN36100:PA13 | ZN36100:PA13 | ZN36100/000013 | WOOLLAHRA | UG | Not Veg | 2019-01-08 | N | 50.4582 | N | 6 | N | N | 1.1101 | 39.4971 | 18510.4169
[7 empty] | 6149 | 9419 | 1629078 | 2019-01-08 21:16 | 2019-01-08 22:15 | 59 | 11kV | 60062 | 1450 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 199896 2 fault operations C Phase Earth Fault Car hit UGOH pole KT-40011 & damaged cable. Isolated faulty section of cable & left permit for repairs. Excluded OMS 1629078 | January | 2019 | 2019Q3 | 2019 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2019-01-08 | N | 41.4221 | N | 6 | N | N | 1.1101 | 39.4971 | 43891.5381
[7 empty] | 5809 | 5614 | 1629089 | 2019-01-08 21:53 | 2019-01-08 23:40 | 107 | 11kV | 169897 | 2071 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At6 Zn2635 Epping 11kV VCB Panel 31 tripped on Relays: 50TX 150TN Minor Alarm and trip Lamp. Cause: Possible fault between S5283 to S4630 tee PT1108 See OMS 1629891 1629893 1629894 1629089 | January | 2019 | 2019Q3 | 2019 | ZN2635:PA31 | ZN2635:PA31 | ZN02635/000031 | PARRAMATTA | UG | Not Veg | 2019-01-08 | N | 82.0362 | N | 6 | N | N | 1.1101 | 39.4971 | 124155.7165
[7 empty] | 6846 | 16854 | 1629102 | 2019-01-08 22:18 | 2019-01-08 23:40 | 82 | 11kV | 90446 | 1103 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | CP49995 Hennry Kendall tripped, relosed tripped and locked out on Overcurrent Cause: Possum found at base of pole LB62052 Abnormal Switching: CP62053 Closed, Panel 33 Open See OMS 1629896 1629102 1629103 1629104 1629112 | January | 2019 | 2019Q3 | 2019 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | OH | Not Veg | 2019-01-08 | N | 82 | N | 6 | N | N | 1.1101 | 39.4971 | 66095.2691
[7 empty] | 6812 | 16517 | 1629126 | 2019-01-09 06:55 | 2019-01-09 08:20 | 85 | 11kV | 116094 | 1454 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S9118 Cronulla, 11kv Panel 22 "S9786 Franklin King" tripped on Relays: A ph IOC, C ph IOC+OC, earth fault, EFI, reclose and lockout Signals: 11kv trip Remarks: UG fault. 11kv feeder fault between S9305 Gannons Denman Sw/B and S9406 Wallumatta Denman Sw/A | January | 2019 | 2019Q3 | 2019 | ZN9118:PA22 | ZN9118:PA22 | ZN09118/000022 | SUTHERLAND | UG | Not Veg | 2019-01-09 | N | 79.8446 | N | 14 | N | N | 1.1101 | 39.4971 | 84838.071
[7 empty] | 6803 | 16400 | 1629222 | 2019-01-09 11:49 | 2019-01-09 14:30 | 161 | 11kV | 322 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199903 A Phase DOLF : 10 Amp Excluded OMS 1629222 | January | 2019 | 2019Q3 | 2019 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2019-01-09 | N | 161 | N | 14 | N | N | 1.1101 | 39.4971 | 235.3081
[7 empty] | 6018 | 7812 | 1629337 | 2019-01-09 17:24 | 2019-01-09 18:40 | 76 | 11kV | 228 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 199910 A Phase DOLF : 10 Amp Excluded OMS 1629337 | January | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-01-09 | N | 76 | N | 14 | N | N | 1.1101 | 39.4971 | 166.6157
[7 empty] | 6534 | 13683 | 1629349 | 2019-01-09 17:52 | 2019-01-09 19:00 | 68 | 11kV | 136 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 199911 B Phase DOLF : 10 AMP Excluded OMS 1629349 | January | 2019 | 2019Q3 | 2019 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2019-01-09 | N | 68 | N | 14 | N | N | 1.1101 | 39.4971 | 99.3848
[7 empty] | 5508 | 2050 | 1629351 | 2019-01-09 17:54 | 2019-01-09 19:47 | 113 | 11kV | 1718 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 199914 2 fault operations B & C Phase Overcurrent Excluded OMS 1629351 | January | 2019 | 2019Q3 | 2019 | 813:89058 | 813:89058 | ZN00813/089058 | UPPER HUNTER | OH | Veg | 2019-01-09 | N | 101.0588 | N | 14 | N | N | 1.1101 | 39.4971 | 1255.4637
[7 empty] | 6591 | 14307 | 1629321 | 2019-01-09 17:06 | 2019-01-09 21:05 | 239 | 11kV | 3585 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 199913 3 phase DOLF : 20 Amp Excluded OMS 1629321, 1629325, 1629334, 1629354, 1629373 | January | 2019 | 2019Q3 | 2019 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2019-01-09 | N | 239 | N | 14 | N | N | 1.1101 | 39.4971 | 2619.8123
[7 empty] | 6092 | 8627 | 1629380 | 2019-01-09 20:03 | 2019-01-09 21:09 | 66 | 11kV | 198 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 199916 B & C Phase DOLF : 16 Amp Excluded OMS 1629380 | January | 2019 | 2019Q3 | 2019 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2019-01-09 | N | 66 | N | 14 | N | N | 1.1101 | 39.4971 | 144.6926
[7 empty] | 6590 | 14302 | 1629313 | 2019-01-09 16:46 | 2019-01-09 21:25 | 278.75 | 11kV | 24808.75 | 89 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 199915 C Phase DOLF : 31 Amp Replace faulty Tx. Excluded OMS 1629335, 1629346 | January | 2019 | 2019Q3 | 2019 | 512:83733 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Not Veg | 2019-01-09 | N | 278.75 | N | 14 | N | N | 1.1101 | 39.4971 | 18129.5028
[7 empty] | 5731 | 5082 | 1629327 | 2019-01-09 17:25 | 2019-01-09 21:37 | 252 | 11kV | 94157 | 377 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 199912 C Phase Mains down between poles IQ-42102 & IQ-42101, SECTION ISOLATED FOR REPAIRS Excluded OMS 1629327 | January | 2019 | 2019Q3 | 2019 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2019-01-09 | N | 249.7533 | N | 14 | N | N | 1.1101 | 39.4971 | 68807.1584
[7 empty] | 5653 | 4131 | 1629368 | 2019-01-09 18:39 | 2019-01-09 22:10 | 211 | 11kV | 844 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 199933 C Phase DOLF : 10 Amp Excluded OMS 1629368 | January | 2019 | 2019Q3 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2019-01-09 | N | 211 | N | 14 | N | N | 1.1101 | 39.4971 | 616.7703
[7 empty] | 6571 | 14087 | 1629396 | 2019-01-09 22:40 | 2019-01-09 23:50 | 70 | 11kV | 280 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 199936 A Phase DOLF : 10 Amp Excluded OMS 1629396 | January | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-01-09 | N | 70 | N | 14 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 5920 | 6613 | 1629392 | 2019-01-09 23:10 | 2019-01-10 02:12 | 182 | 11kV | 36888 | 1298 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | ZN12660 WOY WOY 11kV CB PA8 'North Burge Rd' tripped & reclosed on: Relays: Timmed O/C, EFI EFI: S18313 Cause: lightning 11kv down @ Adj PT18861 11kv fdr Alive and Down on arrival by DOp 11kV Panel 8 de-energised for safety reasons at 23:10PM See 1629690 2nd 1629691,2 ex 1629392,3,9 | January | 2019 | 2019Q3 | 2019 | ZN12660:PA8 | ZN12660:PA8 | ZN12660/000008 | CENTRAL COAST | OH | Not Veg | 2019-01-09 | N | 28.4191 | N | 14 | N | N | 1.1101 | 39.4971 | 26956.6624
[7 empty] | 6295 | 10830 | 1629412 | 2019-01-10 03:09 | 2019-01-10 05:02 | 113 | 11kV | 116164 | 1028 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S1673 Turramurra Panel 7 tripped on Relays: 50TC IOC, Earth Fault, Check EFI Cause: Possum found at the base of pole on UGOH on Cnr of Eastern and Boundary Rds DOP inable to remove possum - Region to Remove | January | 2019 | 2019Q3 | 2019 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Veg | 2019-01-10 | N | 113 | N | 7 | N | N | 1.1101 | 39.4971 | 84889.2249
[7 empty] | 6178 | 9797 | 1620852 | 2018-12-16 16:49 | 2019-01-10 10:00 | 35591 | 11kV | 44191 | 21 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 189377 1 Fault operations, Overvoltage 11kV fell wrapping around pole EM-30158 (sub 53256) 16/12/18 23:55 t40158: See LID 189317 power on to all but customers pole sub 53256. Note: Sub re-energised on 10.1.19 @10am | December | 2018 | 2019Q2 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2018-12-16 | Y | 2104.3333 | N | 7 | N | Y | 1.1101 | 39.4971 | 32293.4794
[7 empty] | 6420 | 12298 | 1629445 | 2019-01-10 08:11 | 2019-01-10 10:20 | 129 | 11kV | 903 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 199940 B & C Phase DOLF : 20 Amp Excluded OMS 1629445 & 1629460 Covered both jobs. | January | 2019 | 2019Q3 | 2019 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2019-01-10 | N | 129 | N | 7 | N | N | 1.1101 | 39.4971 | 659.8858
[7 empty] | 6249 | 10419 | 1629374 | 2019-01-09 19:14 | 2019-01-10 16:26 | 1272.35 | 11kV | 729056.55 | 573 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN15001 BROOKVALE 11kV CB PA8 'Winbourne rd' fdr tripped on ABC phase IOC, EFI Abnormal: AB25282 open, S15581SwA Open, S16245SwA Opened , S46569SwA Closed, S15691 in LV// Ug Fault 11kv fdr from S16821SwA to LB25282 to S17050 Harbord rd 170 See 1629687 ex 1629374 | January | 2019 | 2019Q3 | 2019 | ZN15001:PA8 | ZN15001:PA8 | ZN15001/000008 | NORTHERN BEACHES | UG | Not Veg | 2019-01-09 | N | 1272.35 | N | 14 | N | N | 1.1101 | 39.4971 | 532773.0232
[7 empty] | 5698 | 4648 | 1629684 | 2019-01-10 16:20 | 2019-01-10 17:40 | 80 | 11kV | 80 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 199948 B Phase DOLF : 10 Amp Excluded OMS 1629684 | January | 2019 | 2019Q3 | 2019 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2019-01-10 | N | 80 | N | 7 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 5426 | 1165 | 1629471 | 2019-01-10 09:30 | 2019-01-10 17:55 | 505 | 11kV | 2763 | 51 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 199939/01 RAGCB Tripped blown sub 52944 | January | 2019 | 2019Q3 | 2019 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2019-01-10 | N | 54.1765 | N | 7 | N | N | 1.1101 | 39.4971 | 2019.1189
[7 empty] | 5553 | 2886 | 1629705 | 2019-01-10 17:18 | 2019-01-10 19:00 | 102 | 11kV | 306 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 199949 A Phase DOLF : 10 Amp Excluded OMS 1629705 | January | 2019 | 2019Q3 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2019-01-10 | N | 102 | N | 7 | N | N | 1.1101 | 39.4971 | 223.6158
[7 empty] | 5618 | 3690 | 1629720 | 2019-01-10 18:35 | 2019-01-10 19:25 | 50 | 11kV | 750 | 15 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 199950 Isolated to repair Low mains adj PT 70401 Excluded OMS 1629720 | January | 2019 | 2019Q3 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2019-01-10 | N | 50 | N | 7 | N | N | 1.1101 | 39.4971 | 548.0779
[7 empty] | 7044 | 19006 | 1629719 | 2019-01-10 18:47 | 2019-01-11 00:45 | 357.5833 | 11kV | 715.1667 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 199956 A Phase DOLF : 3 Amp faulty LF 40414 replaced Live Line | January | 2019 | 2019Q3 | 2019 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2019-01-10 | N | 357.5833 | N | 7 | N | N | 1.1101 | 39.4971 | 522.6227
[7 empty] | 6975 | 18266 | 1629940 | 2019-01-11 17:20 | 2019-01-11 20:15 | 175 | 11kV | 175 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 199985 Single phase DOLF : 10 Amp Excluded OMS 1629940 | January | 2019 | 2019Q3 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2019-01-11 | N | 175 | N | 4 | N | N | 1.1101 | 39.4971 | 127.8848
[7 empty] | 5532 | 2486 | 1629985 | 2019-01-11 21:57 | 2019-01-11 23:35 | 98 | 11kV | 98 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 199995 A & B Phase DOLF : 10 Amp Excluded OMS 1629985 | January | 2019 | 2019Q3 | 2019 | 243:80075 | 243:80075 | ZN00243/080075 | CENTRAL COAST | OH | Veg | 2019-01-11 | N | 98 | N | 4 | N | N | 1.1101 | 39.4971 | 71.6155
[7 empty] | 6882 | 17384 | 1629997 | 2019-01-12 01:15 | 2019-01-12 01:29 | 14 | 11kV | 4116 | 348 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Air Break Switch | Unplanned | No Weather Impact | N | At S12660 Woy Woy Panel 8 CP41181 was opened and therefore denergised a section of 11kV feeder thus allowing AB41979 to be opened as it was arcing and had a high resistance. See OMS 1630864 1630861 1630001 1629998 1629997 | January | 2019 | 2019Q3 | 2019 | ZN12660:PA8 | ZN12660:PA8 | ZN12660/000008 | CENTRAL COAST | OH | Not Veg | 2019-01-12 | N | 11.8276 | N | 10 | N | N | 1.1101 | 39.4971 | 3007.8514
[7 empty] | 6289 | 10772 | 1629993 | 2019-01-11 23:10 | 2019-01-12 01:37 | 147 | 11kV | 151115 | 1085 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 191002 2 fault operations A & B Phase Overcurrent Branch on HV mains pole HR-51110 Green st . Excluded oms report no 1629993 & 1629996. | January | 2019 | 2019Q3 | 2019 | 502:48008 | 502:48008 | ZN00502/048008 | MAITLAND | OH | Veg | 2019-01-11 | N | 139.2765 | N | 4 | N | N | 1.1101 | 39.4971 | 110430.3849
[7 empty] | 7036 | 18901 | 1630005 | 2019-01-12 05:29 | 2019-01-12 07:25 | 116 | 11kV | 3016 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 191005 A Phase DOLF : 10 Amp | January | 2019 | 2019Q3 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2019-01-12 | N | 116 | N | 10 | N | N | 1.1101 | 39.4971 | 2204.0038
[7 empty] | 5765 | 5313 | 1630032 | 2019-01-12 08:49 | 2019-01-12 09:40 | 51 | 11kV | 102 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191006 C Phase DOLF : 16 Amp | January | 2019 | 2019Q3 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Veg | 2019-01-12 | N | 51 | N | 10 | N | N | 1.1101 | 39.4971 | 74.5386
[7 empty] | 7059 | 19223 | 1630037 | 2019-01-12 09:27 | 2019-01-12 11:29 | 122 | 11kV | 244 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191013 Single phase DOLF : 10 Amp Excluded OMS 1630037 | January | 2019 | 2019Q3 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2019-01-12 | N | 122 | N | 10 | N | N | 1.1101 | 39.4971 | 178.308
[7 empty] | 5560 | 3004 | 1630035 | 2019-01-12 09:07 | 2019-01-12 12:10 | 183 | 11kV | 183 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191014 Single phase DOLF : 10 Amp Excluded OMS 1630035 | January | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-01-12 | N | 183 | N | 10 | N | N | 1.1101 | 39.4971 | 133.731
[7 empty] | 7017 | 18680 | 1629962 | 2019-01-11 19:09 | 2019-01-12 13:38 | 1109 | 11kV | 13308 | 12 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 199981 2 fault operations A & B phases Overcurrent; Intellirupter HV OHM down on either sied of pole 4M-80050. | January | 2019 | 2019Q3 | 2019 | 802:82225 | 802:82225 | ZN00802/082225 | MID-WESTERN REGIONAL | OH | Not Veg | 2019-01-11 | N | 1109 | N | 4 | N | N | 1.1101 | 39.4971 | 9725.0939
[7 empty] | 6969 | 18194 | 1630087 | 2019-01-12 13:25 | 2019-01-12 14:15 | 50 | 11kV | 200 | 4 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191016 No protection operation Small grass fire at base of pole Section isolated to make repairs, wrong information on pole stating fdr 33612 actually fdr 33605. See report 191021 Excluded OMS 1630087 | January | 2019 | 2019Q3 | 2019 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Not Veg | 2019-01-12 | N | 50 | N | 10 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 5435 | 1216 | 1630080 | 2019-01-12 13:05 | 2019-01-12 15:00 | 115 | 11kV | 230 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191003 Single phase DOLF : 10 Amp Excluded OMS 1630080 | January | 2019 | 2019Q3 | 2019 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2019-01-12 | N | 115 | N | 10 | N | N | 1.1101 | 39.4971 | 168.0772
[7 empty] | 5551 | 2871 | 1630092 | 2019-01-12 14:09 | 2019-01-12 17:58 | 229 | 11kV | 7557 | 33 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Hot >35C | N | LID 191022 1 fault operation Earth Fault Broken insulator at pole CQ-50165 caused OHM to contact fence. Approx. 300sqm grassfire started. | January | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2019-01-12 | N | 229 | N | 10 | N | N | 1.1101 | 39.4971 | 5522.4327
[7 empty] | 5736 | 5092 | 1630110 | 2019-01-12 15:43 | 2019-01-12 18:40 | 177 | 11kV | 354 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Hot >35C | N | LID 191023 Single phase DOLF : 10 Amp Replace L/A's Excluded OMS 1630110 | January | 2019 | 2019Q3 | 2019 | 512:83733 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Not Veg | 2019-01-12 | N | 177 | N | 10 | N | N | 1.1101 | 39.4971 | 258.6928
[7 empty] | 5621 | 3713 | 1630177 | 2019-01-12 23:01 | 2019-01-13 06:45 | 464 | 11kV | 90664 | 248 | HV | 3rd Party Vehicle | 3rd Party Impact | Insulator | Unplanned | No Weather Impact | N | LID 191026 2X11KV MAINS ON CROSSARM & 1 HANGING NEAR LV. NO FEEDER OPERATION. Excluded OMS REPORT NO 1630177 & 1630179. | January | 2019 | 2019Q3 | 2019 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Not Veg | 2019-01-12 | N | 365.5806 | N | 10 | N | N | 1.1101 | 39.4971 | 66254.5771
[7 empty] | 5555 | 2913 | 1630189 | 2019-01-13 03:22 | 2019-01-13 07:30 | 248 | 11kV | 744 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191027 Single phase DOLF : 10 Amp Excluded OMS 1630189 | January | 2019 | 2019Q3 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2019-01-13 | N | 248 | N | 3 | N | N | 1.1101 | 39.4971 | 543.6933
[7 empty] | 6174 | 9755 | 1630235 | 2019-01-13 10:57 | 2019-01-13 12:25 | 88 | 11kV | 88 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191029 Single phase DOLF : 10 Amp Excluded OMS No. 1630235 | January | 2019 | 2019Q3 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2019-01-13 | N | 88 | N | 3 | N | N | 1.1101 | 39.4971 | 64.3078
[7 empty] | 5361 | 285 | 1630210 | 2019-01-13 09:30 | 2019-01-13 14:20 | 290.2167 | 11kV | 5804.3333 | 20 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 191028 Lead off C Phase Line Fuse 47027 Excluded OMS 1630219 | January | 2019 | 2019Q3 | 2019 | 507:80914 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Not Veg | 2019-01-13 | N | 290.2167 | N | 3 | N | N | 1.1101 | 39.4971 | 4241.6356
[7 empty] | 6383 | 11809 | 1630331 | 2019-01-14 07:56 | 2019-01-14 10:15 | 139 | 11kV | 41209 | 335 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale Panel 16 fdr tripped/reclsoed/tripped & locked out on: Signals: 11kv trip, Tx13 Group Earth Relays: A+C phase O/C, A phase Autoclose Timing Relay, Lockout EFI's: S14716 S50376 S14898 (EFI Defective), S14763 (EFI Disconnected, sitting on top of RMI) Cause: 11kv frontline fdr fault from Zn12690 Berkley Vale Panel 16 to SwA @S14716, tee S12691 Also Protection Operation Suspect, Protection to investigate See 1631371,3,4 ex 1630331,80,3,5,6 | January | 2019 | 2019Q3 | 2019 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | UG | Not Veg | 2019-01-14 | N | 123.0119 | N | 5 | N | N | 1.1101 | 39.4971 | 30114.3217
[7 empty] | 5904 | 6424 | 1630367 | 2019-01-14 09:25 | 2019-01-14 11:03 | 98 | 11kV | 99839 | 1028 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S1673 Turramurra Panel 7 tripped on Earth fault and EFI. Cause: Dead possum and crow at UGOH to LB 203 UGOH is now defective See OMS 1630806 1630809 1630367 1630402 | January | 2019 | 2019Q3 | 2019 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | Unknown | Unknown | 2019-01-14 | N | 97.1196 | N | 5 | N | N | 1.1101 | 39.4971 | 72959.3964
[7 empty] | 5667 | 4316 | 1630338 | 2019-01-14 08:27 | 2019-01-14 11:35 | 188 | 11kV | 752 | 4 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191037 A Phase DOLF : 10 Amp Safety reasons Excluded OMS 1630338 | January | 2019 | 2019Q3 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2019-01-14 | N | 188 | N | 5 | N | N | 1.1101 | 39.4971 | 549.5394
[7 empty] | 6954 | 18066 | 1630478 | 2019-01-14 12:03 | 2019-01-14 13:15 | 72 | 11kV | 72 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191046 A Phase DOLF : 10 Amp Bird contacted mains. Excluded OMS 1630478 | January | 2019 | 2019Q3 | 2019 | 238:34148 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2019-01-14 | N | 72 | N | 5 | N | N | 1.1101 | 39.4971 | 52.6155
[7 empty] | 5886 | 6277 | 1630611 | 2019-01-14 23:45 | 2019-01-15 04:41 | 296 | 11kV | 42270 | 196 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191052 1 fault operation Sensitive Earth fault Please check protection suspected grading issue SEF fault within army base tripped feeder breaker Excluded OMS 1630611 | January | 2019 | 2019Q3 | 2019 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2019-01-14 | N | 215.6633 | N | 5 | N | N | 1.1101 | 39.4971 | 30889.6692
[7 empty] | 6810 | 16488 | 1630628 | 2019-01-15 04:42 | 2019-01-15 06:52 | 130 | 11kV | 5290 | 178 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN3425 CASTLE COVE 11kV CB PA27 Relays: No relay operations EFI and Fault check only Signals: 11kv trip, Tx1 Group Earth Cause: UG Fault. Arc ing sounds heard at S5885. fault in section of 11kv fdr from Panel 27 to S5093 sw/B to S5885 tee Tx1 See 1631635,6 ex 1630628 | January | 2019 | 2019Q3 | 2019 | ZN3425:PA27 | ZN3425:PA27 | ZN03425/000027 | WILLOUGHBY | UG | Not Veg | 2019-01-15 | N | 29.7191 | N | 8 | N | N | 1.1101 | 39.4971 | 3865.776
[7 empty] | 7064 | 19308 | 1630658 | 2019-01-15 08:18 | 2019-01-15 09:50 | 92 | 11kV | 184 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191058 Single phase DOLF : 10 Amp Excluded OMS 1630658 | January | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-01-15 | N | 92 | N | 8 | N | N | 1.1101 | 39.4971 | 134.4618
[7 empty] | 6648 | 14802 | 1630692 | 2019-01-15 09:36 | 2019-01-15 10:50 | 74 | 11kV | 154012 | 2462 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | @ZN1788 Matraville 11kv Panel 17 labelled "S4631 Barwon Gwydir" tripped: Relays: B phase Earth fault, C phase overload, EFI Abnormal: closed sw/b @ S2437 Flack St, Open sw/A @ S2702 Australia Mur Remarks: end box fault. 11kv "Sw.A" @ S6801 Beauchamp Rhodes | January | 2019 | 2019Q3 | 2019 | ZN1788:PA17 | ZN1788:PA17 | ZN01788/000017 | BAYSIDE | UG | Not Veg | 2019-01-15 | N | 62.5556 | N | 8 | N | N | 1.1101 | 39.4971 | 112547.427
[7 empty] | 6516 | 13569 | 1630623 | 2019-01-15 04:32 | 2019-01-15 14:50 | 618 | 11kV | 463525.4 | 3518 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | At S9252 Jannali 11kv Panel 28 "The Grand Pde etc' tripped on: Relays: A/B and C phase IOC Alarms: 11kv trip with efi Abnormal: LB32653 closed, Sw/A open at S.78816 Sw/A closed at S9240, Sw/A open at S9237. NB: DMA S9840 to S78816 and also PT9514 in LV// Remarks: Possum on HV UGOH above LB35653 - UGOH damaged. 11kv feeder from S49937 to LB35273 to LB35653 tee to PT65273 Third National | January | 2019 | 2019Q3 | 2019 | ZN9252:PA28 | ZN9252:PA28 | ZN09252/000028 | SUTHERLAND | OH | Not Veg | 2019-01-15 | N | 131.7582 | N | 8 | N | N | 1.1101 | 39.4971 | 338730.6906
[7 empty] | 6946 | 17989 | 1629536 | 2019-01-09 22:18 | 2019-01-15 14:51 | 8193 | 11kV | 8193 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Electrical Storm | N | LID 199932 1 fault operation A Phase Overcurrent Mac Gen advised. Trip Current Aph 867A. Customer driven outage. Restored on OK from customer after their network repaired. | January | 2019 | 2019Q3 | 2019 |  |  |  | SINGLETON | Unknown | Not Veg | 2019-01-09 | N | 8193 | N | 14 | N | N | 1.1101 | 39.4971 | 5987.2027
[7 empty] | 5993 | 7467 | 1630761 | 2019-01-15 13:50 | 2019-01-15 15:22 | 92 | 11kV | 38361 | 486 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Sub 1285 Greenacre Park Panel #35 labelled Heath St tripped on IT receive translay and F/C @Sub 2420 Bankstown Square #1 11kv CB A tripped and #1 Tx415v acb tripped on IT send Translay Remarks: UG fault section of 11kv feeder from S1285 Greenacre Park panel #35 to S4315 Heath St Sw/A | January | 2019 | 2019Q3 | 2019 | ZN1285:PA35 | ZN1285:PA35 | ZN01285/000035 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-01-15 | N | 78.9321 | N | 8 | N | N | 1.1101 | 39.4971 | 28033.0873
[7 empty] | 5802 | 5565 | 1630765 | 2019-01-15 14:25 | 2019-01-15 15:50 | 85 | 11kV | 58093 | 772 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN340 Botany 11kv Panel 45 labelled "S1420 Edgehill Av" tripped: Relays: "A" prot & "B" prot, B phase, neutral, EF, EFI, fault flag, O/C trip Signals: 11kv Cb45 Sw/84105 open, CB45 volt detector supply fail, RTU prot trip, prot trip latch Remarks: UG fault. 11kv feeder fault from "SW/A" @ S6804 Hale Underwood yo "Sw/D" @ S6548 Byrnes Erith | January | 2019 | 2019Q3 | 2019 | ZN340:PA45 | ZN340:PA45 | ZN00340/000045 | BAYSIDE | UG | Not Veg | 2019-01-15 | N | 75.25 | N | 8 | N | N | 1.1101 | 39.4971 | 42452.6509
[7 empty] | 5734 | 5087 | 1630867 | 2019-01-15 18:46 | 2019-01-15 21:11 | 145 | 11kV | 8033 | 73 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 191069 2 fault operations Tree pulled of mains beyond ABS 65736. Recloser did not record fault flag all it provided was lock out flag. Excluded OMS 1630867 | January | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-01-15 | N | 110.0411 | N | 8 | N | N | 1.1101 | 39.4971 | 5870.2795
[7 empty] | 5796 | 5508 | 1630875 | 2019-01-15 18:02 | 2019-01-15 23:00 | 298 | 11kV | 41720 | 140 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 191068 2 fault operations Sensitive Earth Fault Trees on mains between sub 59003 and sub 59004. | January | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-01-15 | N | 298 | N | 8 | N | N | 1.1101 | 39.4971 | 30487.7455
[7 empty] | 5782 | 5430 | 1630908 | 2019-01-16 05:11 | 2019-01-16 06:53 | 102 | 11kV | 124518 | 1261 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN35600 Kingsford 11kv Panel 6 labelled "S.36621 Kingsford Zone Aux No.1 & S.48093 Barker Anzac No.2 HVC "tripped: Relays: Earth fault, EFI, left feeder frame leakage fault check relay Remarks: 11kv feeder fault from Sw/B @ S36221 Kingsford Zone Aux No.1 to Sw/A @ S.3332 Arden Coo tee to Sw/A @ S.5806 Avoca Jellicoe | January | 2019 | 2019Q3 | 2019 | ZN35600:PA6 | ZN35600:PA6 | ZN35600/000006 | RANDWICK | UG | Not Veg | 2019-01-16 | N | 98.7454 | N | 5 | N | N | 1.1101 | 39.4971 | 90994.0817
[7 empty] | 5514 | 2204 | 1630918 | 2019-01-16 06:53 | 2019-01-16 08:50 | 117 | 11kV | 234 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191074 B Phase DOLF : 16 Amp Magpie Excluded OMS 1630918 | January | 2019 | 2019Q3 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2019-01-16 | N | 117 | N | 5 | N | N | 1.1101 | 39.4971 | 171.0003
[7 empty] | 6719 | 15293 | 1631133 | 2019-01-16 15:27 | 2019-01-16 16:57 | 90 | 11kV | 80400 | 1004 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn4800 Homebush Bay 11kv VCB panel 29 S-63482 feeder tripped on: Remarks; UG fault. 11kv UG feeder fault from ZN1610 Homebush to S63482 Hill Half no.3 Sw/A to S4800 Olympic Stadium NE | January | 2019 | 2019Q3 | 2019 | ZN1610:PA29 | ZN1610:PA29 | ZN01610/000029 | PARRAMATTA | UG | Not Veg | 2019-01-16 | N | 80.0797 | N | 5 | N | N | 1.1101 | 39.4971 | 58753.9486
[7 empty] | 6966 | 18189 | 1631196 | 2019-01-16 17:30 | 2019-01-16 18:45 | 75 | 11kV | 6450 | 86 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 191081 A Phase DOLF : 40 Amp Excluded OMS 1631196 | January | 2019 | 2019Q3 | 2019 | 513:48058 | 513:83504 | ZN00513/083504 | SINGLETON | OH | Veg | 2019-01-16 | N | 75 | N | 5 | N | N | 1.1101 | 39.4971 | 4713.4698
[7 empty] | 6548 | 13789 | 1631199 | 2019-01-16 17:30 | 2019-01-16 19:10 | 100 | 11kV | 300 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 191083 Single phase DOLF : 10 Amp Excluded OMS 1631199 | January | 2019 | 2019Q3 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2019-01-16 | N | 100 | N | 5 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 7055 | 19157 | 1631254 | 2019-01-17 05:31 | 2019-01-17 06:45 | 74 | 11kV | 152214 | 2171 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN12620 NORAVILLE 11kV CB PA7 "Fravent st" tripped on: Relays - 51N, EFI EFI's S14590 S14589 S48014 S14588 S14587 S14391 S14694 S14693 EFI did not operate S14695 Signals: 11kv trip Cause: UG fault Underground cable fault from S14693:SwA to S14692:SwB See 1632457,8 Ex 1631254 | January | 2019 | 2019Q3 | 2019 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | UG | Not Veg | 2019-01-17 | N | 70.1124 | N | 7 | N | N | 1.1101 | 39.4971 | 111233.5016
[7 empty] | 7027 | 18789 | 1631343 | 2019-01-17 12:09 | 2019-01-17 13:08 | 59 | 11kV | 6549 | 111 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191089 A Phase DOLF : 40 Amp Excluded OMS 1631343 | January | 2019 | 2019Q3 | 2019 | 205:12203 | 205:12203 | ZN00205/012203 | NEWCASTLE | OH | Veg | 2019-01-17 | N | 59 | N | 7 | N | N | 1.1101 | 39.4971 | 4785.816
[7 empty] | 7147 | 19970 | 1631295 | 2019-01-17 09:50 | 2019-01-17 13:50 | 240 | 11kV | 720 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 191091 A & B Phase DOLF : 10 Amp Excluded OMS 1631295 | January | 2019 | 2019Q3 | 2019 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2019-01-17 | N | 240 | N | 7 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 6016 | 7801 | 1631382 | 2019-01-17 13:18 | 2019-01-17 14:48 | 90 | 11kV | 12510 | 139 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | S2466 Flemington Panel 2 "Day Derby No2" fdr tripped Relays: Earth fault, EFI, fault check Signals: 11kv trip, Zone earth EFI's: nil Remarks: UG fault. front line feeder fault from Flemington Panel 2 to Sw/B S.6019 Day Derby No.2 | January | 2019 | 2019Q3 | 2019 | ZN2466:PA2 | ZN2466:PA2 | ZN02466/000002 | PARRAMATTA | UG | Not Veg | 2019-01-17 | N | 90 | N | 7 | N | N | 1.1101 | 39.4971 | 9141.939
[7 empty] | 5970 | 7099 | 1631349 | 2019-01-17 12:25 | 2019-01-17 15:16 | 171 | 11kV | 263980 | 1545 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN35370 GALSTON 11kV CB PA10 Galston Aux 2' tripped, reclosed, tripped on Relays: OC/EF, EFI Signals: 50T B and C phase intantaneous, Reclose and lockout, 11kv trip Abnormal: LB62157 closed, LB408 open, S6680SwB Closed, S6048SwA Open Cause: tree branch contact - other. Branch found on mains near PT2410 See 1632740,1,2 ex 1631349,50,63 | January | 2019 | 2019Q3 | 2019 | ZN965:PA24 | ZN965:PA24 | ZN00965/000024 | HORNSBY | OH | Veg | 2019-01-17 | N | 170.8608 | N | 7 | N | N | 1.1101 | 39.4971 | 192908.7979
[7 empty] | 5679 | 4387 | 1631469 | 2019-01-17 17:50 | 2019-01-18 01:20 | 450 | 11kV | 450 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | Ex ZN14892 CHARMHAVEN section of 11kV CB PA1 "S18361" S14239 HIAWATHA S.T.W. D2 HV fuses operated Cause: Possibel transformer failure DOp also noticed marks around endbox and may indicate Tx tails have failed. Permits issued for jointer/t/con PM oncall to talk to customer abour arranging MG See 1632473 ex 1631469 | January | 2019 | 2019Q3 | 2019 | ZN14892:PA1 | ZN14892:PA1 | ZN14892/000001 | CENTRAL COAST | UG | Not Veg | 2019-01-17 | N | 450 | N | 7 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 6453 | 12702 | 1631494 | 2019-01-17 20:55 | 2019-01-18 15:00 | 1085 | 11kV | 1085 | 1 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Ex ZN14143 SOMERSBY section of 11kV CB PA12 Section of 11kv fdr from S65717:B to S18171:A tee S18442 interrupted for safety due to incoming and outgiong feeders to to S18442 found unearthed covers taken off and conduits tied back to stakes on building site. See 1632609 ex 1631494 | January | 2019 | 2019Q3 | 2019 | ZN14143:PA12 | ZN14143:PA12 | ZN14143/000012 | CENTRAL COAST | UG | Not Veg | 2019-01-17 | N | 1085 | N | 7 | N | N | 1.1101 | 39.4971 | 792.886
[7 empty] | 5637 | 3911 | 1631792 | 2019-01-18 20:49 | 2019-01-18 21:40 | 51 | 11kV | 51 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 191112 C Phase DOLF : 10 Amp Excluded OMS 1631792 | January | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-01-18 | N | 51 | N | 2 | N | N | 1.1101 | 39.4971 | 37.2693
[7 empty] | 6621 | 14548 | 1631824 | 2019-01-19 04:21 | 2019-01-19 05:45 | 84 | 11kV | 528 | 7 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN1610 Homebush Bay 11kv Panel 5 "Superdome #1" tripped on: Relays: earth fault and C phase overcurrent. Signals: 11kv trip Field EFI's: S5324 Remarks: cable fault between S5324 Superdome #1 to S5117 RAS Plaza park north | January | 2019 | 2019Q3 | 2019 | ZN1610:PA5 | ZN1610:PA5 | ZN01610/000005 | PARRAMATTA | UG | Not Veg | 2019-01-19 | N | 75.4286 | N | 10 | N | N | 1.1101 | 39.4971 | 385.8468
[7 empty] | 6394 | 11945 | 1631846 | 2019-01-19 09:20 | 2019-01-19 11:30 | 130 | 11kV | 29510 | 227 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | LID 191117 Section interrupted to test faulty transformer 24280 supply off at 0920hrs back on 1130hrs | January | 2019 | 2019Q3 | 2019 | 240:34846 | 240:34846 | ZN00240/034846 | NEWCASTLE | UG | Not Veg | 2019-01-19 | N | 130 | N | 10 | N | N | 1.1101 | 39.4971 | 21565.0376
[7 empty] | 6826 | 16655 | 1631880 | 2019-01-19 11:21 | 2019-01-19 12:24 | 63 | 11kV | 86940 | 1380 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | ZN36200 EMPIRE BAY 11kV CB PA8S49860' fdr has tripped reclsoed and locked out Signals: 11kv trip, lock out Relays: A & B pahse O/C EFI EFI's S49860 Cause: tree branch on OH mains at 39 Maitland Bay Dr Killcare See 1631880 ex 1631888 | January | 2019 | 2019Q3 | 2019 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2019-01-19 | N | 63 | N | 10 | N | N | 1.1101 | 39.4971 | 63533.1877
[7 empty] | 5807 | 5598 | 1631901 | 2019-01-19 12:33 | 2019-01-19 13:17 | 43.4667 | 11kV | 36772.8 | 846 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | ZN12570 AVOCA 11kV CB PA34 'Terrigal' fdr has tripped, reclosed and locke dout Singals: 11kv trip, lock out Relays: B,C phase instantaneous, lock out, EFI Cause: Branch on mains outside 3 francis road north avoca See 1631901 Ex 1631902,4,8 | January | 2019 | 2019Q3 | 2019 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2019-01-19 | N | 43.4667 | N | 10 | N | N | 1.1101 | 39.4971 | 26872.4776
[7 empty] | 6271 | 10598 | 1631844 | 2019-01-18 23:39 | 2019-01-19 13:35 | 836 | 11kV | 30096 | 36 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Ex ZN35370 GALSTON section of 11kV CB PA2 11kv bond off on radial leg to PT2110 near tee off to PT808 Interrupted from AB443 to PT808 7 PT2110 to repair bond Cause: bond. | January | 2019 | 2019Q3 | 2019 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2019-01-18 | N | 836 | N | 2 | N | N | 1.1101 | 39.4971 | 21993.2691
[7 empty] | 7146 | 19954 | 1631928 | 2019-01-19 13:42 | 2019-01-19 15:19 | 97 | 11kV | 96070 | 1046 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.19 tripped on: Earth Fault UG cable fault from S7243 (Sw/F) to S49909 (Sw/A) See 1632582 1632581 | January | 2019 | 2019Q3 | 2019 | ZN2568:PA19 | ZN2568:PA19 | ZN02568/000019 | INNER WEST | UG | Not Veg | 2019-01-19 | N | 91.8451 | N | 10 | N | N | 1.1101 | 39.4971 | 70205.1224
[7 empty] | 5670 | 4328 | 1631958 | 2019-01-19 17:17 | 2019-01-19 20:11 | 174.85 | 11kV | 36674.75 | 227 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | LID 191123 Isolate 11kV UGM to replace faulty Tx sub 24280 Bakeri Circuit sub | January | 2019 | 2019Q3 | 2019 | 240:34846 | 240:34846 | ZN00240/034846 | NEWCASTLE | UG | Not Veg | 2019-01-19 | N | 161.5628 | N | 10 | N | N | 1.1101 | 39.4971 | 26800.8256
[7 empty] | 6622 | 14559 | 1631980 | 2019-01-19 20:08 | 2019-01-19 21:08 | 60 | 11kV | 96897 | 1631 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN15015 NORTH HEAD 11kV CB PA5 'Manly Hospital/FIU' fdr tripped Relays: B Phase OC EFI Signals: 11kv trip EFI's S16194 S16136 S16721 S15820 S16194 Manly Hosp No.1 11kV SwB tripped Relays: B Phase OC Cause: Ug fault from S15820 Addison Rd 146 to S50491 Bower Shelly See 1632705,6,7 ex 1631980 | January | 2019 | 2019Q3 | 2019 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | UG | Not Veg | 2019-01-19 | N | 59.4096 | N | 10 | N | N | 1.1101 | 39.4971 | 70809.4696
[7 empty] | 6147 | 9397 | 1632006 | 2019-01-19 22:42 | 2019-01-20 00:35 | 113 | 11kV | 169313 | 1665 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN129 HUNTERS HILL 11kV CB PA57 "Eltham Gerrish" fdr tripped on: Relays: B & C phase overcurrent Signals: 11kv trip EFI: nil Cause: not ascertained. patrolled and okay. NB S46610 defective and in LV// and fed into fault, lineworker to inspect See 1633018,21 LV// 1633037 ex 1632006,9 | January | 2019 | 2019Q3 | 2019 | ZN129:PA57 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Veg | 2019-01-19 | N | 101.6895 | N | 10 | N | N | 1.1101 | 39.4971 | 123728.9465
[7 empty] | 6426 | 12399 | 1631996 | 2019-01-19 21:35 | 2019-01-20 03:50 | 375 | 11kV | 96092 | 650 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | LID 191124 3 fault operations B & C Phase Overcurrent Blown UGOH pole HS-42235 Protection 50T BC Excluded oms 1631996 | January | 2019 | 2019Q3 | 2019 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | Unknown | Unknown | 2019-01-19 | N | 147.8338 | N | 10 | N | N | 1.1101 | 39.4971 | 70221.1994
[7 empty] | 6504 | 13333 | 1631998 | 2019-01-19 21:20 | 2019-01-20 14:45 | 1045 | 11kV | 23705 | 60 | HV | Vandalism | 3rd Party Impact | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV CB PA5 RE45083 the Durren Recloser tripped and reclosed and locked out on OC IOC and EF Standoff insulator broken abov PT14855 and earths stolen at PT18455 and PT14598 See 1632620,2,3 Ex 1631998,2020 | January | 2019 | 2019Q3 | 2019 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | Unknown | Not Veg | 2019-01-19 | N | 395.0833 | N | 10 | N | N | 1.1101 | 39.4971 | 17322.9148
[7 empty] | 7160 | 20101 | 1632133 | 2019-01-20 21:46 | 2019-01-20 22:35 | 49 | 11kV | 2646 | 54 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 191130 A Phase DOLF : 31 Amp Fatigued Fuse Excluded OMS 1632133 CC1: 22-"Refer to SOp" | January | 2019 | 2019Q3 | 2019 | 239:82136 | 239:82136 | ZN00239/082136 | LAKE MACQUARIE | OH | Not Veg | 2019-01-20 | N | 49 | N | 1 | N | N | 1.1101 | 39.4971 | 1933.6188
[7 empty] | 6681 | 15083 | 1632144 | 2019-01-21 01:31 | 2019-01-21 02:17 | 46 | 11kV | 30268 | 658 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN12570 AVOCA section of 11kV CB PA33 CP50407 The scenic bounty tripped, reclosed & locked out: Relays: OC Signals: 11kv trip Cause: Tree/branch on OH amins near PT11718 | January | 2019 | 2019Q3 | 2019 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2019-01-21 | N | 46 | N | 20 | Y | Y | 1.1101 | 39.4971 | 22118.9616
[7 empty] | 6312 | 11022 | 1632158 | 2019-01-21 03:46 | 2019-01-21 05:24 | 98 | 11kV | 44198 | 451 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN35370 GALSTON 11kV CB PA8 fdr tripped, reclosed, tripped and locked out Relays: B & C phase overcurrent Signals: 11kv trip Abnormal: AB3252 open, LB62159 closed Cause: Lightning. DOp patrolled but didn't find a cause See 1633071 ex 1632158,67 | January | 2019 | 2019Q3 | 2019 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2019-01-21 | N | 98 | N | 20 | Y | Y | 1.1101 | 39.4971 | 32298.5948
[7 empty] | 5540 | 2636 | 1632163 | 2019-01-21 04:18 | 2019-01-21 06:42 | 144 | 11kV | 39168 | 272 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Ex ZN12620 NORAVILLE section of 11kV CB PA1 "Noraville Aux" fdr RE47817 Buff Pt Elouera tripped and locked out on overcurrent Cause: lightning, during storm | January | 2019 | 2019Q3 | 2019 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2019-01-21 | N | 144 | N | 20 | Y | Y | 1.1101 | 39.4971 | 28622.8191
[7 empty] | 6737 | 15448 | 1632150 | 2019-01-21 03:16 | 2019-01-21 07:27 | 251 | 11kV | 78526 | 343 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN12690 BERKELEY VALE 11kV CB PA16 "Catamaran Sailcraft" tripped, reclosed & locked out Relays: OC A + B Phase, Earth Fault, EFI, Reclose and Timer Signals: 11kv trip EFI: S14716 S50376 S14898 S14763 S49651 S14347 Cause: not ascertained. Mains to Patrol See 1633131,2 ex 1632150 | January | 2019 | 2019Q3 | 2019 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2019-01-21 | N | 228.9388 | N | 20 | Y | Y | 1.1101 | 39.4971 | 57384.4847
[7 empty] | 5776 | 5386 | 1632179 | 2019-01-21 06:24 | 2019-01-21 07:30 | 65.8833 | 11kV | 1449.4333 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 191137 A & C Phase DOLF : 20 Amp | January | 2019 | 2019Q3 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2019-01-21 | N | 65.8833 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1059.2031
[7 empty] | 6791 | 16219 | 1632157 | 2019-01-21 03:45 | 2019-01-21 07:55 | 250 | 11kV | 244750 | 979 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | Ex ZN12620 NORAVILLE section of 11kV CB PA1 RE47818 Wilfred Barrett Terilbah tripped and locked out Cause: lightning 11kV Surge arrestor has failed at the UGOH between RE47818 and S14653:SwB refer also to T and Reclose OMS 1633134 @ 21/01/2019 03:44 | January | 2019 | 2019Q3 | 2019 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2019-01-21 | N | 250 | N | 20 | Y | Y | 1.1101 | 39.4971 | 178856.0811
[7 empty] | 6804 | 16401 | 1632214 | 2019-01-21 07:57 | 2019-01-21 09:45 | 108 | 11kV | 216 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191138 C Phase DOLF : 10 Amp Excluded OMS 1632214 | January | 2019 | 2019Q3 | 2019 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2019-01-21 | N | 108 | N | 20 | Y | Y | 1.1101 | 39.4971 | 157.8464
[7 empty] | 5718 | 4952 | 1632149 | 2019-01-21 03:13 | 2019-01-21 10:50 | 457 | 11kV | 1828 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | Ex ZN12630 PEATS RIDGE section of 11kV CB PA10 "Peats Ridge" PT11880 NARDOO EULOO 0.4 11kV HDO road side phase 10Amp fuse blown due to lightning See 1633123 ex 1632149 | January | 2019 | 2019Q3 | 2019 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2019-01-21 | N | 457 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1335.8485
[7 empty] | 5793 | 5493 | 1632276 | 2019-01-21 09:47 | 2019-01-21 11:25 | 98 | 11kV | 98 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191144 A Phase DOLF : 10 Amp Excluded OMS 1632276 | January | 2019 | 2019Q3 | 2019 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Veg | 2019-01-21 | N | 98 | N | 20 | Y | Y | 1.1101 | 39.4971 | 71.6155
[7 empty] | 6832 | 16766 | 1632236 | 2019-01-21 08:50 | 2019-01-21 11:37 | 167 | 11kV | 1336 | 8 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Lightning | N | PT2061 HUNT COTSWOLD 11kv HDO B Phase blown Cause: lightning Lightning hit PT2061 causing B phase HDO to blow replaced and returned to service See 1633082 ex 1632236,98 | January | 2019 | 2019Q3 | 2019 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2019-01-21 | N | 167 | N | 20 | Y | Y | 1.1101 | 39.4971 | 976.3094
[7 empty] | 5489 | 1844 | 1632578 | 2019-01-21 11:07 | 2019-01-21 12:00 | 53 | 11kV | 2120 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 191148 1 fault operation | January | 2019 | 2019Q3 | 2019 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2019-01-21 | N | 53 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1549.2335
[7 empty] | 6928 | 17827 | 1632359 | 2019-01-21 12:16 | 2019-01-21 12:57 | 41 | 11kV | 34645 | 845 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC62226 Connells Terry tripped & locked Tree branch on OH mains | January | 2019 | 2019Q3 | 2019 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Veg | 2019-01-21 | N | 41 | N | 20 | Y | Y | 1.1101 | 39.4971 | 25317.5441
[7 empty] | 6963 | 18134 | 1632147 | 2019-01-21 02:56 | 2019-01-21 13:00 | 604 | 11kV | 17018 | 95 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Lightning | N | ZN12630 PEATS RIDGE 11kV CB PA13'Peats Ridge Aux No.1' tripped, reclosed & locked out Relays: A,B & C phas timed OC, SEF Signals: 11kv gtrip EFI's: Cause: OH Earth Wire Down Stay wire from Fdr 720 has fallen tripping Panel 13 Peats Ridge and Fdr720 See 1633107,9,10 ex 1632147 | January | 2019 | 2019Q3 | 2019 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2019-01-21 | N | 179.1368 | N | 20 | Y | Y | 1.1101 | 39.4971 | 12436.2525
[7 empty] | 7155 | 20034 | 1632322 | 2019-01-21 10:57 | 2019-01-21 13:18 | 141 | 11kV | 564 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Lightning | N | Ex ZN14891 WYONG section of 11kV CB PA12 PT13290 RAVENSDALE BRUSH 0.7 11kv HDO B phase 10A fuse blown cause: lightning See 1633144 ex 1632322 | January | 2019 | 2019Q3 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2019-01-21 | N | 141 | N | 20 | Y | Y | 1.1101 | 39.4971 | 412.1546
[7 empty] | 6974 | 18251 | 1632181 | 2019-01-21 06:35 | 2019-01-21 18:00 | 685 | 11kV | 2740 | 4 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Lightning | N | Ex ZN12630 PEATS RIDGE section of 11kV CB PA1 PT12262 PEATS RIDGE BRIESES 0.8 11kv HDO c phase 16A fuse blown Cause: lightning PT12262 Peats Ridge Brieses 0.8 has had an internal failure and a new transformer is required See 1633143 ex1632181 | January | 2019 | 2019Q3 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2019-01-21 | N | 685 | N | 20 | Y | Y | 1.1101 | 39.4971 | 2002.3112