## Coverpage
2023-11-30
Ausgrid’s 2024-29 Revised Proposal
Attachment 5.5.3: Climate Resilience Model 3 - LV Spreader Bars
Empowering communities for a resilient, affordable and net-zero future.

## Summary
Climate Resilience Program - Low Voltage Spreader Bars
Purpose
This is a top-down model used to determine the effectiveness of investment in spreader bars in mitigating wind related risk on the low voltage network.
Summary of outputs
This is the model outputs as used in the business case. It is from tab - 'Model(as used)'
| Option A | Option B | Option C
| Base Case | Consider LV Risk in Isolation of Event Response | Consider LV Risk integrated with event response
Number of spreaders | 0 | 3257 | 4750
5y project cost | 0 | 4245043.0245 | 6091000
5y project benefit | 0 | 5610301.8561 | 8183286.9852
NPV | 0 | 1365258.8316 | 2092286.9852
BCR | 0 | 1.3216 | 1.3435
About the options
| Option A | Option B | Option C
| Base Case | Consider LV Risk in Isolation of Event Response | Consider LV Risk integrated with event response
Description | This is Business as usual case with no additional spreader bars, but considers context of other replacement programs. | The current baseline risk to the Low Voltage Network is grown at the rate of climate growth, adjusting for benefits that might be delivered by other programs. We seek to maintain current risk (ie only adjust for the growth in risk). | We consider both the LV climate risk growth and the impact that the LV Network has on Ausgrid’s major event response process. We are staging HV network investments across our whole network over twenty years, and therefore won’t have initially invested everywhere there is increasing climate risk for customers. With targeted deployment of additional spreader bars through a one off (one period only) investment on the LV network, Ausgrid can manage outage response time for customers. This will maintain safety for customers at the onset of a major event, bring forward HV repair, and reduce the impact of crew fatigue management constraints as the event progresses. This option seeks to maintain outcomes overall for customers.
To create new scenario, enter a spreader bar number in cell B93 in the tab 'Model'

## Model
Climate Resilience Program - Low Voltage Spreader Bars
Step 1 - Gather Network Data
Assumptions | Value |  | Source or Reasoning
LV component of climate risk | 21190164 |  | LV VoEUSE calculated from sum of event CMIs from climate event days
Bare spreader length (BF) | 1943.7123 | (km) | From LV_MAINS_SUMMARY tab
Bare spreader spans (BF) | 44789 | (span count) | From LV_MAINS_SUMMARY tab
Bare spreader length (non BF) | 7098.4209 | (km) | From LV_MAINS_SUMMARY tab
Bare spreader spans (non BF) | 217969 | (span count) | From LV_MAINS_SUMMARY tab
Bare spreader penetration (BF) | 98% |  | Significant work has been put into ensuring high penetration of spreader bars in bushfire areas.
Bare spreader penetration (non BF) | 5% |  | Upper limit of estimate - Non-bushfire areas have significantly lower spreader penetration.
Average span length | 0.034412
Replacement Program (Bare to ABC) km per annum | 284 |  | Total LV spans and number of spreaders will decrease each year as mains are reactively replaced by Aerial Bundled Cable (ABC) that no longer requires spreaders.
Replacement spans per annum | 1650.5679 |  | Forecast information
Effectiveness of spreader for wind | 90% |  | Spreader bars reduce the risk of interruptions due to wind
Effectiveness of spreader for veg | 50% |  | Spreader bars reduce the risk of interruptions due to vegetation
Cost to install per spreader | 412 |  | Based on Reactive Actual Rate
Efficiency of installing multiple spreader | 60% | 247.2 | Reduced unit rate based on efficiency of bundling work.
Spreaders per span | 1 |  | Most LV spans only require one spreader bar
WACC | 3.44% |  | As per rest of the submission
Cost to plan and identify missing spans | 220000 |  | 1/5 FTE x 5 years
Planning Costs (1/5 of an FTE per annum) | 44000 |  | Calculated
Risk Growth Rate | 1% |  | Based on climate data in End-to-End model
Determine the Baseline risk
Percentage of LV Component
21190164
Wind risk component
21% | 4449772.1876
Veg risk component
30.76% | 6518490.3423
Total Risk
10968262.5299
Risk Effectiveness
Wind effectiveness | 90%
Wind component | 21%
Veg Effectiveness | 50%
Veg component | 30.76%
Weighted risk effectiveness | 66.23%
Annual total risk on all spans | 10968262.5299
Total number of spans | 262758
Total number of spans that do not have spreaders | 207966.33
Spreader penetration | 20.85%
Baseline risk (assuming no spreaders) | 12725703.6975
Step 2 - Adjust the low voltage network risk for other programs
Baseline (assuming existing spreaders and replacement program)
Year |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Program Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Annual span replacement with ABC |  | FY25: 1650.5679; FY26: 1650.5679; FY27: 1650.5679; FY28: 1650.5679; FY29: 1650.5679
Annual span replacement with ABC that have spreaders |  | FY25: 344.185; FY26: 344.185; FY27: 344.185; FY28: 344.185; FY29: 344.185
Number of spans of OH bare mains | 262758 | 261107.4321 | 259456.8643 | 257806.2964 | 256155.7286 | 254505.1607 | 254505.1607 | 254505.1607 | 254505.1607 | 254505.1607 | 254505.1607 | 254505.1607 | 254505.1607 | 254505.1607 | 254505.1607 | 254505.1607
Number of spans with no spreaders | 207966.33 | 207622.145 | 207277.9599 | 206933.7749 | 206589.5899 | 206245.4049 | 206245.4049 | 206245.4049 | 206245.4049 | 206245.4049 | 206245.4049 | 206245.4049 | 206245.4049 | 206245.4049 | 206245.4049 | 206245.4049
Number of spans with spreaders | 54791.67 | 54447.485 | 54103.2999 | 53759.1149 | 53414.9299 | 53070.7449 | 53070.7449 | 53070.7449 | 53070.7449 | 53070.7449 | 53070.7449 | 53070.7449 | 53070.7449 | 53070.7449 | 53070.7449 | 53070.7449
Baseline spreader penetration | 20.85% | 20.85% | 20.85% | 20.85% | 20.85% | 20.85% | 20.85% | 20.85% | 20.85% | 20.85% | 20.85% | 20.85% | 20.85% | 20.85% | 20.85% | 20.85%
Step 3 - Calculate the risk, and apply climate change risk growth
Year |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Baseline Risk (assuming existing spreaders) | 10968262.5299 | 11077945.1552 | 11188724.6067 | 11300611.8528 | 11413617.9713 | 11527754.151 | 11643031.6925 | 11759462.0095 | 11877056.6296 | 11995827.1958 | 12115785.4678 | 12236943.3225 | 12359312.7557 | 12482905.8833 | 12607734.9421 | 12733812.2915
Cumulative change in Risk |  | 109682.6253 | 110779.4516 | 111887.2461 | 113006.1185 | 114136.1797 | 115277.5415 | 116430.3169 | 117594.6201 | 118770.5663 | 119958.272 | 121157.8547 | 122369.4332 | 123593.1276 | 124829.0588 | 126077.3494
NPV Risk reduction | -1352815.5618
Step 4 - Input Options Data - User can test the impact of adding spreader bars to the low voltage network
| Spreader Bars/Year | FY25: Total for the Reg Period
Enter the number of spreader bars to invest in | 4750 | FY25: 23750
Step 5 - Calculate Cost and Benefits - This is calculated for the number of spreader bars added in step 4
Risk Reduction by adding spreader bars is calculated
Year |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Annual span replacement with ABC |  | FY25: 1650.5679; FY26: 1650.5679; FY27: 1650.5679; FY28: 1650.5679; FY29: 1650.5679
Annual span replacement with ABC that have spreaders |  | FY25: 344.185; FY26: 374.2117; FY27: 404.4295; FY28: 434.8407; FY29: 465.4478
Annual span with no spreader reduction |  | FY25: 4750; FY26: 4750; FY27: 4750; FY28: 4750; FY29: 4750
Number of spans with spreaders | 54791.67 | 59197.485 | 63573.2732 | 67918.8438 | 72234.0031 | 76518.5553 | 76518.5553 | 76518.5553 | 76518.5553 | 76518.5553 | 76518.5553 | 76518.5553 | 76518.5553 | 76518.5553 | 76518.5553 | 76518.5553
Spreader penetration | 20.85% | 22.67% | 24.5% | 26.34% | 28.2% | 30.07% | 30.07% | 30.07% | 30.07% | 30.07% | 30.07% | 30.07% | 30.07% | 30.07% | 30.07% | 30.07%
Remaining Risk (after new spreaders) | 10968262.5299 | 10923092.75 | 10874927.7839 | 10823689.4275 | 10769297.6042 | 10711670.316 | 10818787.0191 | 10926974.8893 | 11036244.6382 | 11146607.0846 | 11258073.1555 | 11370653.887 | 11484360.4259 | 11599204.0301 | 11715196.0704 | 11832348.0311
Cumulative change in Risk |  | -154852.4051 | -313796.8228 | -476922.4252 | -644320.3671 | -816083.835 | -824244.6734 | -832487.1201 | -840811.9913 | -849220.1112 | -857712.3124 | -866289.4355 | -874952.3298 | -883701.8531 | -892538.8717 | -901464.2604
NPV Risk reduction | 8183286.9852
Summary for the FY25-29 Regulatory Period
Annual spreader cost | 1174200
Annual planning cost | 44000
Annual total cost | 1218200
5y project cost | 6091000
5y project benefit | 8183286.9852
NPV | 2092286.9852
BCR | 1.3435
To create new scenario, enter a spreader bar number in cell B93.

## MED LV Rel_data
Percent of Total Events by Asset and Trigger
LV EVENTS for MEDs only
Percent of Total Events by Asset and Trigger | 1.1677 | 19.4678 | 0.019142 | 0.40199 | 13.2848 | 3.5988 | 17.1516 | 0.038285 | 0.019142 | 3.7711 | 41.0796 | Percent of Total Events by Trigger
event_trigger_super_group | 3rd Party Impact | Adverse Weather/Environment | Animal | Customer Installation | Equipment Failure | OTHER - REFER COMMENTS | Self Clearing Trigger | UNKNOWN | Unknown (CASS) | Utility Process Issue | Vegetation
event_asset_at_fault
3rd Party Asset | 0.038285 | 0.07657 | 0 | 0.28714 | 0.038285 | 0 | 0 | 0.038285 | 0 | 0 | 0.057427 |  | 0.53599
Air Break Switch | 0 | 0 | 0 | 0 | 0.019142 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.019142
BOND OR HIGH RESISTANCE | 0 | 0.019142 | 0 | 0 | 0 | 0 | 0.134 | 0 | 0 | 0 | 0 |  | 0.15314
BUSBAR PROTECTION RELAY | 0 | 0 | 0 | 0 | 0 | 0 | 0.019142 | 0 | 0 | 0 | 0 |  | 0.019142
Bond | 0 | 0.038285 | 0 | 0 | 0.84227 | 0.019142 | 0 | 0 | 0 | 0.057427 | 0.057427 |  | 1.0145
Busbar | 0 | 0 | 0 | 0 | 0.019142 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.019142
CABLE CONNECTION | 0 | 0 | 0 | 0 | 0 | 0 | 0.038285 | 0 | 0 | 0 | 0 |  | 0.038285
CROSS-ARM | 0 | 0 | 0 | 0 | 0.019142 | 0 | 0.15314 | 0 | 0 | 0 | 0.019142 |  | 0.19142
Circuit Breaker | 0 | 0 | 0 | 0 | 0.019142 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.019142
Cross arm | 0 | 0.15314 | 0 | 0 | 0.57427 | 0 | 0.019142 | 0 | 0 | 0 | 0.32542 |  | 1.072
DC Not Transformer | 0.019142 | 0 | 0 | 0 | 0.17228 | 0.07657 | 0.019142 | 0 | 0 | 0.07657 | 0 |  | 0.36371
DC Transformer | 0 | 0 | 0 | 0 | 0.038285 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.038285
DC-PT Not Transformer | 0 | 0.019142 | 0 | 0 | 0.038285 | 0 | 0.038285 | 0 | 0 | 0 | 0.019142 |  | 0.11485
DC-PT Transformer | 0 | 0 | 0 | 0 | 0.038285 | 0 | 0 | 0 | 0 | 0 | 0.038285 |  | 0.07657
DISTRIBUTION PILLAR | 0 | 0 | 0 | 0 | 0 | 0 | 0.019142 | 0 | 0 | 0 | 0 |  | 0.019142
Feeder/Distributor O/H | 0.019142 | 0.59342 | 0 | 0 | 0.44028 | 0.15314 | 5.647 | 0 | 0 | 0.134 | 1.7228 |  | 8.7098
Feeder/Distributor U/G | 0 | 0.019142 | 0 | 0.019142 | 0.038285 | 0 | 0.74655 | 0 | 0 | 0 | 0.019142 |  | 0.84227
Fuse | 0 | 0.134 | 0 | 0.019142 | 0.28714 | 0.19142 | 0.095712 | 0 | 0 | 0.17228 | 0.038285 |  | 0.93798
Fuse Assembly | 0 | 0 | 0 | 0 | 0.17228 | 0.019142 | 0 | 0 | 0 | 0 | 0 |  | 0.19142
Insulator | 0 | 0 | 0 | 0 | 0.038285 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.038285
Joint | 0 | 0 | 0 | 0 | 0.038285 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.038285
LV DISTRIBUTION BOARD | 0.019142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.019142
LV DISTRIBUTION CABLE | 0 | 0 | 0 | 0 | 0 | 0.019142 | 0.68913 | 0 | 0 | 0.07657 | 0 |  | 0.78484
LV DISTRIBUTOR CABLE | 0 | 0.07657 | 0 | 0 | 0 | 0.038285 | 0.55513 | 0 | 0 | 0.019142 | 0.38285 |  | 1.072
LV DISTRIBUTOR LINK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019142 | 0 |  | 0.019142
LV FUSE LINK | 0 | 0 | 0.019142 | 0 | 0.038285 | 0 | 0.44028 | 0 | 0 | 0.66998 | 0 |  | 1.1677
O/H Conductor ABC | 0.095712 | 0.99541 | 0 | 0.019142 | 0.26799 | 0.057427 | 0.019142 | 0 | 0 | 0.095712 | 1.9525 |  | 3.5031
O/H Conductor Bare | 0.22971 | 1.8568 | 0 | 0 | 2.2971 | 0.93798 | 0.11485 | 0 | 0.019142 | 0.51685 | 8.2312 |  | 14.2037 | 10.2029
O/H Conductor Insulated | 0.019142 | 1.2443 | 0 | 0 | 0.32542 | 0.07657 | 0 | 0 | 0 | 0 | 0.86141 |  | 2.5268
O/H Conductor Unknown | 0.28714 | 11.9832 | 0 | 0 | 3.6179 | 0.89969 | 0.80398 | 0 | 0 | 0.24885 | 20.8078 |  | 38.6485 | 33.5949
O/H Link | 0 | 0 | 0 | 0 | 0.28714 | 0 | 0 | 0 | 0 | 0.66998 | 0.019142 |  | 0.97626
OH CONDUCTOR | 0.07657 | 1.8951 | 0 | 0 | 0.019142 | 0.17228 | 7.4464 | 0 | 0 | 0.28714 | 5.9724 |  | 15.8691
OTHER - REFER COMMENTS | 0.019142 | 0.134 | 0 | 0 | 0.095712 | 0.72741 | 0 | 0 | 0 | 0.55513 | 0.22971 |  | 1.7611
POLE | 0 | 0 | 0 | 0 | 0 | 0 | 0.057427 | 0 | 0 | 0.019142 | 0.019142 |  | 0.095712
Pillar | 0.019142 | 0 | 0 | 0 | 0.24885 | 0.019142 | 0 | 0 | 0 | 0.019142 | 0.057427 |  | 0.36371
Pole | 0.24885 | 0.21057 | 0 | 0.038285 | 0.51685 | 0.07657 | 0 | 0 | 0 | 0 | 0.21057 |  | 1.3017
SUPPORT INSULATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0.019142 | 0 | 0 | 0 | 0 |  | 0.019142
Streetlighting Hardware | 0 | 0 | 0 | 0 | 0.038285 | 0 | 0 | 0 | 0 | 0 | 0.019142 |  | 0.057427
U/G Cable | 0.07657 | 0 | 0 | 0 | 1.7802 | 0.095712 | 0.057427 | 0 | 0 | 0.057427 | 0.019142 |  | 2.0865
U/G Link | 0 | 0 | 0 | 0 | 0.11485 | 0 | 0 | 0 | 0 | 0.038285 | 0 |  | 0.15314
UGOH | 0 | 0.019142 | 0 | 0.019142 | 0.80398 | 0 | 0 | 0 | 0 | 0.038285 | 0 |  | 0.88055
UNDERGROUND LINKBOX | 0 | 0 | 0 | 0 | 0 | 0.019142 | 0 | 0 | 0 | 0 | 0 |  | 0.019142
ZONE TRANSFORMER | 0 | 0 | 0 | 0 | 0 | 0 | 0.019142 | 0 | 0 | 0 | 0 |  | 0.019142
Outputs
Estimated % of Events for Adverse Weather and Self Clearing | 21%
Estimated % of Events for Veg | 30.76%

## LV_MAINS_SUMMARY
LIFECYCLE_STATUS | COMM
GIS_STATUS | in service
[8 empty] | Length (km) | Number of spans
MODEL_SHORT_NAME_REF | LGA_NAME | CONDUCTOR_TYPE | INSULATION_TYPE | BARE_VS_COVERED | BUSHFIRE_CATEGORY | BUSHFIRE_CATEGORY_2022 | BUSHFIRE_VS_NOT_BUSHFIRE_2022 | Sum of ASSET_LENGTH | Count of ASSET_ID | Average span length (m) | MODEL_SHORT_NAME_REF | BUSHFIRE_VS_NOT_BUSHFIRE_2022 | BARE_VS_COVERED | Sum of Sum of ASSET_LENGTH | Sum of Count of ASSET_ID
Overhead Mains - LV | ASHFIELD | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 6.9148 | 224 | 30.8696 | Overhead Mains - LV | BUSHFIRE | BARE | 1943.7123 | 44789 | 11.53%
Overhead Mains - LV | ASHFIELD | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 83.2072 | 2769 | 30.0496 | Overhead Mains - LV | BUSHFIRE | COVERED | 18.4512 | 571 | 0.147%
Overhead Mains - LV | ASHFIELD | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 12.7965 | 626 | 20.4417 | Overhead Mains - LV | NOT IN BUSHFIRE | BARE | 7098.4209 | 217969 | 56.1%
Overhead Mains - LV | ASHFIELD | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.036098 | 1 | 36.0982 | Overhead Mains - LV | NOT IN BUSHFIRE | COVERED | 3316.4707 | 125198 | 32.22%
Overhead Mains - LV | ASHFIELD | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.49728 | 28 | 17.7601 | Grand Total |  |  | 12377.0551 | 388527 | 100%
Overhead Mains - LV | ASHFIELD | PVC_SINGLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.15761 | 5 | 31.5222
Overhead Mains - LV | ASHFIELD | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 5.4715 | 348 | 15.7227
Overhead Mains - LV | AUBURN | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 23.9409 | 758 | 31.5843 | MODEL_SHORT_NAME_REF | BUSHFIRE_VS_NOT_BUSHFIRE_2022 | INSULATION_TYPE | Sum of Sum of ASSET_LENGTH | Sum of Count of ASSET_ID
Overhead Mains - LV | AUBURN | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 144.1108 | 4963 | 29.037 | Overhead Mains - LV | BUSHFIRE | BARE | 1943.7123 | 44789 | 11.53%
Overhead Mains - LV | AUBURN | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 16.2258 | 705 | 23.0153 | Overhead Mains - LV | BUSHFIRE | PVC | 18.4512 | 571 | 0.147%
Overhead Mains - LV | AUBURN | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.24612 | 7 | 35.16 | Overhead Mains - LV | NOT IN BUSHFIRE | BARE | 7098.4209 | 217969 | 56.1%
Overhead Mains - LV | AUBURN | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.66967 | 36 | 18.6018 | Overhead Mains - LV | NOT IN BUSHFIRE | PVC | 85.2543 | 3564 | 0.9173%
Overhead Mains - LV | AUBURN | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 5.8767 | 287 | 20.4764 | Overhead Mains - LV | NOT IN BUSHFIRE | XLPE | 3231.2164 | 121634 | 31.31%
Overhead Mains - LV | BANKSTOWN | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 7.0808 | 217 | 32.6303 | Grand Total |  |  | 12377.0551 | 388527 | 100%
Overhead Mains - LV | BANKSTOWN | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.16334 | 4 | 40.8358
Overhead Mains - LV | BANKSTOWN | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 143.3639 | 4449 | 32.2239
Overhead Mains - LV | BANKSTOWN | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.040019 | 1 | 40.0193 | MODEL_SHORT_NAME_REF | BUSHFIRE_VS_NOT_BUSHFIRE_2022 | Sum of Sum of ASSET_LENGTH | Sum of Count of ASSET_ID
Overhead Mains - LV | BANKSTOWN | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 11.3436 | 342 | 33.1683 | Overhead Mains - LV | BUSHFIRE | 1962.1635 | 45360 |  | 11.67%
Overhead Mains - LV | BANKSTOWN | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.19775 | 4 | 49.4379 | Overhead Mains - LV | NOT IN BUSHFIRE | 10414.8916 | 343167 |  | 88.33%
Overhead Mains - LV | BANKSTOWN | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 368.3679 | 12096 | 30.4537 | Grand Total |  | 12377.0551 | 388527 |  | 100%
Overhead Mains - LV | BANKSTOWN | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.45471 | 13 | 34.9774
Overhead Mains - LV | BANKSTOWN | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 126.5817 | 5670 | 22.3248
Overhead Mains - LV | BANKSTOWN | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.01675 | 1 | 16.7504 | CONDUCTOR_TYPE | INSULATION_TYPE | BARE_VS_COVERED | Sum of Sum of ASSET_LENGTH | Sum of Count of ASSET_ID
Overhead Mains - LV | BANKSTOWN | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.35607 | 13 | 27.3897 | ACSR | BARE | BARE | 87.8592 | 1134 | 0.2919%
Overhead Mains - LV | BANKSTOWN | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 2.845 | 136 | 20.9188 | ALUMINIUM | BARE | BARE | 3335.2999 | 86908 | 22.37%
Overhead Mains - LV | BANKSTOWN | TWIN_TWIST | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.09428 | 3 | 31.4268 | CONSAC | XLPE | COVERED | 0.074648 | 6 | 0.001544%
Overhead Mains - LV | BANKSTOWN | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 35.5293 | 2112 | 16.8226 | COPPER | BARE | BARE | 5523.5359 | 172208 | 44.32%
Overhead Mains - LV | BOTANY BAY | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 13.4542 | 431 | 31.2163 | LV_ABC | XLPE | COVERED | 2829.1629 | 99839 | 25.7%
Overhead Mains - LV | BOTANY BAY | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 68.4599 | 2427 | 28.2076 | PVC | PVC | COVERED | 4.5147 | 191 | 0.04916%
Overhead Mains - LV | BOTANY BAY | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 32.4088 | 1477 | 21.9423 | PVC_BUNDLE | PVC | COVERED | 97.6619 | 3893 | 1.002%
Overhead Mains - LV | BOTANY BAY | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.13796 | 9 | 15.3286 | PVC_SINGLE | PVC | COVERED | 1.5289 | 51 | 0.01313%
Overhead Mains - LV | BOTANY BAY | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.45749 | 23 | 19.8909 | TWIN_TWIST | BARE | BARE | 95.4382 | 2508 | 0.6455%
Overhead Mains - LV | BOTANY BAY | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.91983 | 51 | 18.0358 | XLPE | XLPE | COVERED | 399.838 | 21680 | 5.58%
Overhead Mains - LV | BURWOOD | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 12.797 | 412 | 31.0607 | XLPE_CONC_N | XLPE | COVERED | 2.1056 | 107 | 0.02754%
Overhead Mains - LV | BURWOOD | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 61.4331 | 2021 | 30.3974 | XLPE_SAC | XLPE | COVERED | 0.03523 | 2 | 0.0005148%
Overhead Mains - LV | BURWOOD | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 10.3212 | 481 | 21.4577 | Grand Total |  |  | 12377.0551 | 388527 | 100%
Overhead Mains - LV | BURWOOD | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.33716 | 17 | 19.8331
Overhead Mains - LV | BURWOOD | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 4.1542 | 261 | 15.9164
Overhead Mains - LV | CANADA BAY | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 24.323 | 754 | 32.2586 | MODEL_SHORT_NAME_REF | CONDUCTOR_TYPE | BUSHFIRE_VS_NOT_BUSHFIRE_2022 | BARE_VS_COVERED | Sum of Sum of ASSET_LENGTH | Sum of Count of ASSET_ID
Overhead Mains - LV | CANADA BAY | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 141.1148 | 4455 | 31.6756 | Overhead Mains - LV | LV_ABC | NOT IN BUSHFIRE | COVERED | 2829.1629 | 99839
Overhead Mains - LV | CANADA BAY | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 23.069 | 999 | 23.0921 | Grand Total |  |  |  | 2829.1629 | 99839
Overhead Mains - LV | CANADA BAY | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.016865 | 1 | 16.8648
Overhead Mains - LV | CANADA BAY | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.94582 | 42 | 22.5196
Overhead Mains - LV | CANADA BAY | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 10.4789 | 639 | 16.3989
Overhead Mains - LV | CANTERBURY | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 43.2558 | 1387 | 31.1866
Overhead Mains - LV | CANTERBURY | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 263.8006 | 8378 | 31.4873
Overhead Mains - LV | CANTERBURY | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 54.3722 | 2534 | 21.4571
Overhead Mains - LV | CANTERBURY | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.02696 | 1 | 26.9601
Overhead Mains - LV | CANTERBURY | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.3108 | 62 | 21.1413
Overhead Mains - LV | CANTERBURY | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 27.9926 | 1696 | 16.5051
Overhead Mains - LV | CESSNOCK | ACSR | BARE | BARE | buffer | buffer | BUSHFIRE | 0.85986 | 14 | 61.4185
Overhead Mains - LV | CESSNOCK | ACSR | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.15556 | 2 | 77.7779
Overhead Mains - LV | CESSNOCK | ACSR | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 0.33157 | 4 | 82.8937
Overhead Mains - LV | CESSNOCK | ACSR | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.91444 | 14 | 65.3171
Overhead Mains - LV | CESSNOCK | ACSR | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 2.5193 | 27 | 93.3078
Overhead Mains - LV | CESSNOCK | ACSR | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.89608 | 10 | 89.6077
Overhead Mains - LV | CESSNOCK | ACSR | BARE | BARE | vegetation category 3 | vegetation category 3 | BUSHFIRE | 10.687 | 144 | 74.2155
Overhead Mains - LV | CESSNOCK | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 43.6011 | 953 | 45.7514
Overhead Mains - LV | CESSNOCK | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.3944 | 11 | 35.8545
Overhead Mains - LV | CESSNOCK | ALUMINIUM | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.24536 | 5 | 49.0718
Overhead Mains - LV | CESSNOCK | ALUMINIUM | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 3.7691 | 72 | 52.3482
Overhead Mains - LV | CESSNOCK | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.28373 | 4 | 70.9324
Overhead Mains - LV | CESSNOCK | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 118.1194 | 2802 | 42.1554
Overhead Mains - LV | CESSNOCK | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 8.5875 | 134 | 64.0859
Overhead Mains - LV | CESSNOCK | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 2.7468 | 38 | 72.2832
Overhead Mains - LV | CESSNOCK | ALUMINIUM | BARE | BARE | vegetation category 3 | vegetation category 1 | BUSHFIRE | 0.23005 | 3 | 76.6847
Overhead Mains - LV | CESSNOCK | ALUMINIUM | BARE | BARE | vegetation category 3 | vegetation category 3 | BUSHFIRE | 30.8381 | 455 | 67.776
Overhead Mains - LV | CESSNOCK | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 12.3783 | 303 | 40.8524
Overhead Mains - LV | CESSNOCK | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.2559 | 5 | 51.1802
Overhead Mains - LV | CESSNOCK | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.073963 | 2 | 36.9813
Overhead Mains - LV | CESSNOCK | COPPER | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 0.74105 | 19 | 39.0025
Overhead Mains - LV | CESSNOCK | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.11544 | 2 | 57.7177
Overhead Mains - LV | CESSNOCK | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 32.1485 | 898 | 35.8002
Overhead Mains - LV | CESSNOCK | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 3.1039 | 57 | 54.4544
Overhead Mains - LV | CESSNOCK | COPPER | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 1.0343 | 20 | 51.7145
Overhead Mains - LV | CESSNOCK | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.057869 | 1 | 57.8687
Overhead Mains - LV | CESSNOCK | COPPER | BARE | BARE | vegetation category 3 | vegetation category 3 | BUSHFIRE | 13.9437 | 273 | 51.0759
Overhead Mains - LV | CESSNOCK | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 142.5466 | 4147 | 34.3734
Overhead Mains - LV | CESSNOCK | PVC | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.24314 | 4 | 60.7845
Overhead Mains - LV | CESSNOCK | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.99588 | 35 | 28.4537
Overhead Mains - LV | CESSNOCK | PVC_BUNDLE | PVC | COVERED | buffer | vegetation category 1 | BUSHFIRE | 0.032144 | 1 | 32.1435
Overhead Mains - LV | CESSNOCK | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 3.5261 | 136 | 25.9272
Overhead Mains - LV | CESSNOCK | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.07817 | 1 | 78.1698
Overhead Mains - LV | CESSNOCK | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.11208 | 2 | 56.0407
Overhead Mains - LV | CESSNOCK | PVC_BUNDLE | PVC | COVERED | vegetation category 3 | vegetation category 3 | BUSHFIRE | 1.1953 | 27 | 44.2687
Overhead Mains - LV | CESSNOCK | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.79172 | 20 | 39.5859
Overhead Mains - LV | DUNGOG | ACSR | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.080614 | 1 | 80.6143
Overhead Mains - LV | DUNGOG | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.099464 | 1 | 99.4637
Overhead Mains - LV | DUNGOG | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.15564 | 2 | 77.8202
Overhead Mains - LV | DUNGOG | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.098209 | 2 | 49.1045
Overhead Mains - LV | DUNGOG | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.016203 | 1 | 16.2033
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 112.207 | 2973 | 37.742
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 35.2773 | 1027 | 34.3498
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 2.9168 | 55 | 53.0336
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.075276 | 2 | 37.6378
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 0.18614 | 3 | 62.0483
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 5.3811 | 139 | 38.7133
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 136.3081 | 3958 | 34.4386
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 1 | BUSHFIRE | 0.12984 | 4 | 32.461
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 2 | BUSHFIRE | 0.057501 | 1 | 57.5011
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 0.06221 | 1 | 62.2097
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 24.9268 | 607 | 41.0656
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | vegetation category 1 | not in bushfire | NOT IN BUSHFIRE | 5.0151 | 111 | 45.1812
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 15.101 | 294 | 51.3639
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 2 | BUSHFIRE | 1.5699 | 30 | 52.3291
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.57773 | 8 | 72.2156
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 3.4352 | 72 | 47.7113
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | vegetation category 2 | not in bushfire | NOT IN BUSHFIRE | 1.9674 | 43 | 45.7527
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 1 | BUSHFIRE | 1.0243 | 21 | 48.7748
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.08632 | 1 | 86.3196
Overhead Mains - LV | GOSFORD | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.18605 | 3 | 62.0167
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 63.7637 | 1665 | 38.2965
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 16.7911 | 510 | 32.9238
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 3.1643 | 56 | 56.5049
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.051451 | 3 | 17.1502
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 0.58874 | 8 | 73.5929
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 2.2157 | 61 | 36.3225
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 86.2732 | 2840 | 30.3779
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | not in bushfire | vegetation category 1 | BUSHFIRE | 0.064247 | 1 | 64.2468
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 0.045114 | 1 | 45.114
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 20.3482 | 450 | 45.2183
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | vegetation category 1 | not in bushfire | NOT IN BUSHFIRE | 4.1726 | 100 | 41.7256
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 18.9829 | 379 | 50.0869
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | vegetation category 1 | vegetation category 2 | BUSHFIRE | 0.43446 | 11 | 39.4962
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.37675 | 6 | 62.792
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 5.6169 | 110 | 51.0627
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | vegetation category 2 | not in bushfire | NOT IN BUSHFIRE | 1.1699 | 27 | 43.3301
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | vegetation category 2 | vegetation category 1 | BUSHFIRE | 1.813 | 35 | 51.801
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.16564 | 4 | 41.4092
Overhead Mains - LV | GOSFORD | COPPER | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.089651 | 2 | 44.8256
Overhead Mains - LV | GOSFORD | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 294.6604 | 9348 | 31.5212
Overhead Mains - LV | GOSFORD | PVC | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.048332 | 1 | 48.332
Overhead Mains - LV | GOSFORD | PVC | PVC | COVERED | buffer | not in bushfire | NOT IN BUSHFIRE | 0.04904 | 2 | 24.5202
Overhead Mains - LV | GOSFORD | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.030911 | 1 | 30.9106
Overhead Mains - LV | GOSFORD | PVC | PVC | COVERED | vegetation category 1 | buffer | BUSHFIRE | 0.01773 | 1 | 17.7302
Overhead Mains - LV | GOSFORD | PVC | PVC | COVERED | vegetation category 1 | not in bushfire | NOT IN BUSHFIRE | 0.042581 | 1 | 42.5809
Overhead Mains - LV | GOSFORD | PVC | PVC | COVERED | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.035267 | 1 | 35.2668
Overhead Mains - LV | GOSFORD | PVC | PVC | COVERED | vegetation category 2 | buffer | BUSHFIRE | 0.019645 | 1 | 19.6452
Overhead Mains - LV | GOSFORD | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 1.0338 | 47 | 21.9961
Overhead Mains - LV | GOSFORD | PVC_BUNDLE | PVC | COVERED | buffer | not in bushfire | NOT IN BUSHFIRE | 0.30469 | 14 | 21.7637
Overhead Mains - LV | GOSFORD | PVC_BUNDLE | PVC | COVERED | buffer | vegetation category 1 | BUSHFIRE | 0.0185 | 1 | 18.4999
Overhead Mains - LV | GOSFORD | PVC_BUNDLE | PVC | COVERED | not in bushfire | buffer | BUSHFIRE | 0.020268 | 1 | 20.2685
Overhead Mains - LV | GOSFORD | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 2.3393 | 123 | 19.0183
Overhead Mains - LV | GOSFORD | PVC_BUNDLE | PVC | COVERED | not in bushfire | vegetation category 2 | BUSHFIRE | 0.021133 | 1 | 21.1334
Overhead Mains - LV | GOSFORD | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | buffer | BUSHFIRE | 0.78042 | 24 | 32.5176
Overhead Mains - LV | GOSFORD | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | not in bushfire | NOT IN BUSHFIRE | 0.022039 | 1 | 22.039
Overhead Mains - LV | GOSFORD | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.12977 | 6 | 21.6291
Overhead Mains - LV | GOSFORD | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | vegetation category 2 | BUSHFIRE | 0.040448 | 1 | 40.4479
Overhead Mains - LV | GOSFORD | PVC_BUNDLE | PVC | COVERED | vegetation category 2 | buffer | BUSHFIRE | 0.019929 | 1 | 19.929
Overhead Mains - LV | GOSFORD | PVC_BUNDLE | PVC | COVERED | vegetation category 2 | not in bushfire | NOT IN BUSHFIRE | 0.059641 | 2 | 29.8206
Overhead Mains - LV | GOSFORD | PVC_SINGLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.025657 | 1 | 25.657
Overhead Mains - LV | GOSFORD | PVC_SINGLE | PVC | COVERED | buffer | not in bushfire | NOT IN BUSHFIRE | 0.015234 | 1 | 15.2339
Overhead Mains - LV | GOSFORD | PVC_SINGLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.055366 | 3 | 18.4554
Overhead Mains - LV | GOSFORD | PVC_SINGLE | PVC | COVERED | vegetation category 1 | buffer | BUSHFIRE | 0.052024 | 2 | 26.0121
Overhead Mains - LV | GOSFORD | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 15.7747 | 609 | 25.9027
Overhead Mains - LV | GOSFORD | XLPE_CONC_N | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.017679 | 1 | 17.6788
Overhead Mains - LV | GOSFORD | XLPE_SAC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.03523 | 2 | 17.6152
Overhead Mains - LV | HAWKESBURY | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.015951 | 1 | 15.9509
Overhead Mains - LV | HAWKESBURY | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.037349 | 1 | 37.3492
Overhead Mains - LV | HORNSBY | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 60.7006 | 1742 | 34.8454
Overhead Mains - LV | HORNSBY | ALUMINIUM | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 3.2083 | 98 | 32.738
Overhead Mains - LV | HORNSBY | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 2.3255 | 51 | 45.5975
Overhead Mains - LV | HORNSBY | ALUMINIUM | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.28502 | 7 | 40.7169
Overhead Mains - LV | HORNSBY | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 4.7451 | 134 | 35.4112
Overhead Mains - LV | HORNSBY | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 58.2596 | 1688 | 34.514
Overhead Mains - LV | HORNSBY | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 2 | BUSHFIRE | 0.15679 | 4 | 39.1976
Overhead Mains - LV | HORNSBY | ALUMINIUM | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.09071 | 3 | 30.2366
Overhead Mains - LV | HORNSBY | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.066785 | 2 | 33.3926
Overhead Mains - LV | HORNSBY | ALUMINIUM | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.045362 | 1 | 45.3615
Overhead Mains - LV | HORNSBY | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 80.1237 | 2448 | 32.7303
Overhead Mains - LV | HORNSBY | COPPER | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 6.3685 | 188 | 33.8751
Overhead Mains - LV | HORNSBY | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 3.3883 | 92 | 36.8288
Overhead Mains - LV | HORNSBY | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 1.0394 | 25 | 41.5755
Overhead Mains - LV | HORNSBY | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 8.3852 | 230 | 36.4576
Overhead Mains - LV | HORNSBY | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 199.2937 | 6099 | 32.6765
Overhead Mains - LV | HORNSBY | COPPER | BARE | BARE | not in bushfire | vegetation category 1 | BUSHFIRE | 0.013386 | 1 | 13.3863
Overhead Mains - LV | HORNSBY | COPPER | BARE | BARE | not in bushfire | vegetation category 2 | BUSHFIRE | 0.081376 | 3 | 27.1254
Overhead Mains - LV | HORNSBY | COPPER | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.31541 | 7 | 45.0581
Overhead Mains - LV | HORNSBY | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.44578 | 13 | 34.2905
Overhead Mains - LV | HORNSBY | COPPER | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.06328 | 2 | 31.6401
Overhead Mains - LV | HORNSBY | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.020094 | 1 | 20.0943
Overhead Mains - LV | HORNSBY | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 107.1134 | 3586 | 29.8699
Overhead Mains - LV | HORNSBY | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.013905 | 1 | 13.9053
Overhead Mains - LV | HORNSBY | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.41464 | 17 | 24.3908
Overhead Mains - LV | HORNSBY | PVC_BUNDLE | PVC | COVERED | buffer | not in bushfire | NOT IN BUSHFIRE | 0.14168 | 7 | 20.2398
Overhead Mains - LV | HORNSBY | PVC_BUNDLE | PVC | COVERED | not in bushfire | buffer | BUSHFIRE | 0.071251 | 4 | 17.8128
Overhead Mains - LV | HORNSBY | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.6158 | 78 | 20.7152
Overhead Mains - LV | HORNSBY | PVC_SINGLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.1023 | 4 | 25.5746
Overhead Mains - LV | HORNSBY | PVC_SINGLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.027515 | 1 | 27.5146
Overhead Mains - LV | HORNSBY | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 33.7337 | 1830 | 18.4337
Overhead Mains - LV | HORNSBY | XLPE_CONC_N | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.015433 | 1 | 15.4329
Overhead Mains - LV | HUNTERS HILL | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 0.32924 | 11 | 29.9308
Overhead Mains - LV | HUNTERS HILL | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.8387 | 62 | 29.6566
Overhead Mains - LV | HUNTERS HILL | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 2.7228 | 82 | 33.2054
Overhead Mains - LV | HUNTERS HILL | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 30.6256 | 1005 | 30.4733
Overhead Mains - LV | HUNTERS HILL | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.077799 | 2 | 38.8997
Overhead Mains - LV | HUNTERS HILL | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 10.2161 | 393 | 25.9952
Overhead Mains - LV | HUNTERS HILL | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.069134 | 2 | 34.5671
Overhead Mains - LV | HUNTERS HILL | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 3.6672 | 214 | 17.1364
Overhead Mains - LV | HURSTVILLE | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 5.1111 | 162 | 31.5497
Overhead Mains - LV | HURSTVILLE | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.24939 | 7 | 35.6273
Overhead Mains - LV | HURSTVILLE | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 67.7527 | 2069 | 32.7466
Overhead Mains - LV | HURSTVILLE | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 2.8735 | 100 | 28.735
Overhead Mains - LV | HURSTVILLE | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.17877 | 10 | 17.8765
Overhead Mains - LV | HURSTVILLE | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 115.5315 | 4063 | 28.435
Overhead Mains - LV | HURSTVILLE | COPPER | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.05565 | 1 | 55.6499
Overhead Mains - LV | HURSTVILLE | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 45.465 | 1691 | 26.8864
Overhead Mains - LV | HURSTVILLE | PVC | PVC | COVERED | not in bushfire | buffer | BUSHFIRE | 0.013233 | 1 | 13.2329
Overhead Mains - LV | HURSTVILLE | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.042033 | 2 | 21.0165
Overhead Mains - LV | HURSTVILLE | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.24783 | 9 | 27.5369
Overhead Mains - LV | HURSTVILLE | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 4.9917 | 200 | 24.9585
Overhead Mains - LV | HURSTVILLE | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | buffer | BUSHFIRE | 0.038024 | 1 | 38.0239
Overhead Mains - LV | HURSTVILLE | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 6.2978 | 324 | 19.4378
Overhead Mains - LV | KOGARAH | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.52665 | 14 | 37.6177
Overhead Mains - LV | KOGARAH | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 51.435 | 1570 | 32.7611
Overhead Mains - LV | KOGARAH | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 1.4569 | 47 | 30.998
Overhead Mains - LV | KOGARAH | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 80.4964 | 2732 | 29.4643
Overhead Mains - LV | KOGARAH | COPPER | BARE | BARE | not in bushfire | vegetation category 2 | BUSHFIRE | 0.10006 | 4 | 25.0144
Overhead Mains - LV | KOGARAH | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 27.6525 | 1006 | 27.4876
Overhead Mains - LV | KOGARAH | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.030014 | 2 | 15.0069
Overhead Mains - LV | KOGARAH | PVC_BUNDLE | PVC | COVERED | not in bushfire | buffer | BUSHFIRE | 0.065183 | 3 | 21.7276
Overhead Mains - LV | KOGARAH | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 2.8884 | 109 | 26.4994
Overhead Mains - LV | KOGARAH | PVC_BUNDLE | PVC | COVERED | not in bushfire | vegetation category 2 | BUSHFIRE | 0.058172 | 2 | 29.086
Overhead Mains - LV | KOGARAH | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 4.4542 | 244 | 18.255
Overhead Mains - LV | KU-RING-GAI | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 20.8124 | 598 | 34.8034
Overhead Mains - LV | KU-RING-GAI | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.19528 | 5 | 39.0554
Overhead Mains - LV | KU-RING-GAI | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 30.2433 | 878 | 34.4457
Overhead Mains - LV | KU-RING-GAI | ALUMINIUM | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.05043 | 2 | 25.2148
Overhead Mains - LV | KU-RING-GAI | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.32212 | 7 | 46.017
Overhead Mains - LV | KU-RING-GAI | ALUMINIUM | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.10704 | 3 | 35.6784
Overhead Mains - LV | KU-RING-GAI | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.20907 | 5 | 41.8143
Overhead Mains - LV | KU-RING-GAI | CONSAC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.074648 | 6 | 12.4413
Overhead Mains - LV | KU-RING-GAI | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 85.0603 | 2440 | 34.8608
Overhead Mains - LV | KU-RING-GAI | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.55468 | 16 | 34.6674
Overhead Mains - LV | KU-RING-GAI | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.14392 | 4 | 35.9806
Overhead Mains - LV | KU-RING-GAI | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 275.5157 | 8076 | 34.1154
Overhead Mains - LV | KU-RING-GAI | COPPER | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.41058 | 11 | 37.3254
Overhead Mains - LV | KU-RING-GAI | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 1.5019 | 34 | 44.173
Overhead Mains - LV | KU-RING-GAI | COPPER | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.54834 | 11 | 49.8488
Overhead Mains - LV | KU-RING-GAI | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.29283 | 8 | 36.6032
Overhead Mains - LV | KU-RING-GAI | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 82.3337 | 3176 | 25.9237
Overhead Mains - LV | KU-RING-GAI | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.018527 | 1 | 18.5268
Overhead Mains - LV | KU-RING-GAI | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.30602 | 12 | 25.5016
Overhead Mains - LV | KU-RING-GAI | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.8406 | 46 | 18.2739
Overhead Mains - LV | KU-RING-GAI | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | buffer | BUSHFIRE | 0.078398 | 2 | 39.1988
Overhead Mains - LV | KU-RING-GAI | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.078332 | 3 | 26.1107
Overhead Mains - LV | KU-RING-GAI | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 36.408 | 2031 | 17.9261
Overhead Mains - LV | LAKE MACQUARIE | ACSR | BARE | BARE | buffer | buffer | BUSHFIRE | 0.78222 | 12 | 65.1851
Overhead Mains - LV | LAKE MACQUARIE | ACSR | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.13431 | 2 | 67.1539
Overhead Mains - LV | LAKE MACQUARIE | ACSR | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.28793 | 4 | 71.9832
Overhead Mains - LV | LAKE MACQUARIE | ACSR | BARE | BARE | vegetation category 3 | vegetation category 3 | BUSHFIRE | 0.081101 | 1 | 81.1014
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 159.0166 | 3435 | 46.293
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.089952 | 1 | 89.9519
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.10479 | 1 | 104.7937
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 0.15703 | 2 | 78.5174
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 290.9253 | 7022 | 41.4306
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 1.3185 | 18 | 73.2491
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 4.9188 | 81 | 60.7265
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.65743 | 10 | 65.7434
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.28421 | 5 | 56.841
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 2.5722 | 46 | 55.9184
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.60007 | 7 | 85.7244
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | vegetation category 3 | buffer | BUSHFIRE | 0.3972 | 7 | 56.7432
Overhead Mains - LV | LAKE MACQUARIE | ALUMINIUM | BARE | BARE | vegetation category 3 | vegetation category 3 | BUSHFIRE | 4.4761 | 61 | 73.3784
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 83.7527 | 2004 | 41.7928
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.16034 | 2 | 80.1704
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.065431 | 1 | 65.4306
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 192.7047 | 5332 | 36.1412
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 1.0201 | 15 | 68.0097
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 7.7658 | 128 | 60.6705
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | vegetation category 1 | vegetation category 2 | BUSHFIRE | 0.42405 | 6 | 70.6749
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.73148 | 8 | 91.4348
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.23872 | 4 | 59.6793
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 2.6636 | 50 | 53.2725
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.33672 | 5 | 67.345
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | vegetation category 3 | buffer | BUSHFIRE | 0.60377 | 10 | 60.3765
Overhead Mains - LV | LAKE MACQUARIE | COPPER | BARE | BARE | vegetation category 3 | vegetation category 3 | BUSHFIRE | 5.1325 | 80 | 64.1565
Overhead Mains - LV | LAKE MACQUARIE | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 204.1322 | 6339 | 32.2026
Overhead Mains - LV | LAKE MACQUARIE | PVC | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.04489 | 1 | 44.8903
Overhead Mains - LV | LAKE MACQUARIE | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 2.4083 | 60 | 40.1386
Overhead Mains - LV | LAKE MACQUARIE | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 2.5929 | 75 | 34.5716
Overhead Mains - LV | LAKE MACQUARIE | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.049206 | 1 | 49.2059
Overhead Mains - LV | LAKE MACQUARIE | PVC_BUNDLE | PVC | COVERED | vegetation category 2 | buffer | BUSHFIRE | 0.021539 | 1 | 21.5394
Overhead Mains - LV | LAKE MACQUARIE | PVC_BUNDLE | PVC | COVERED | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.22324 | 3 | 74.4128
Overhead Mains - LV | LAKE MACQUARIE | PVC_BUNDLE | PVC | COVERED | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.031623 | 1 | 31.623
Overhead Mains - LV | LAKE MACQUARIE | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.2908 | 35 | 36.8808
Overhead Mains - LV | LANE COVE | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 1.8382 | 54 | 34.041
Overhead Mains - LV | LANE COVE | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 11.0807 | 338 | 32.7833
Overhead Mains - LV | LANE COVE | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 5.9669 | 182 | 32.7853
Overhead Mains - LV | LANE COVE | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.19054 | 5 | 38.1079
Overhead Mains - LV | LANE COVE | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 61.2909 | 1914 | 32.0224
Overhead Mains - LV | LANE COVE | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.022921 | 2 | 11.4605
Overhead Mains - LV | LANE COVE | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.080661 | 3 | 26.8871
Overhead Mains - LV | LANE COVE | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 17.2897 | 659 | 26.2363
Overhead Mains - LV | LANE COVE | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.21529 | 6 | 35.8822
Overhead Mains - LV | LANE COVE | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.7778 | 31 | 25.0903
Overhead Mains - LV | LANE COVE | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 9.4183 | 539 | 17.4736
Overhead Mains - LV | LEICHHARDT | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 16.3727 | 569 | 28.7746
Overhead Mains - LV | LEICHHARDT | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 88.92 | 3226 | 27.5635
Overhead Mains - LV | LEICHHARDT | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 27.0557 | 1409 | 19.2021
Overhead Mains - LV | LEICHHARDT | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.073188 | 3 | 24.3961
Overhead Mains - LV | LEICHHARDT | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.5496 | 60 | 25.8268
Overhead Mains - LV | LEICHHARDT | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 6.1345 | 364 | 16.8531
Overhead Mains - LV | MAITLAND | ACSR | BARE | BARE | buffer | buffer | BUSHFIRE | 0.050373 | 1 | 50.3732
Overhead Mains - LV | MAITLAND | ACSR | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 0.023341 | 1 | 23.3409
Overhead Mains - LV | MAITLAND | ACSR | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 1.0715 | 14 | 76.5356
Overhead Mains - LV | MAITLAND | ACSR | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.56781 | 6 | 94.6357
Overhead Mains - LV | MAITLAND | ACSR | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.0663 | 18 | 59.2392
Overhead Mains - LV | MAITLAND | ACSR | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 3.621 | 44 | 82.2951
Overhead Mains - LV | MAITLAND | ACSR | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.13215 | 2 | 66.0738
Overhead Mains - LV | MAITLAND | ACSR | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.058013 | 1 | 58.0131
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 2.2117 | 39 | 56.7107
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 2.2484 | 40 | 56.2094
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.18353 | 2 | 91.7667
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.2363 | 3 | 78.7664
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 3.1722 | 48 | 66.0871
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 6.3516 | 118 | 53.8275
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 93.07 | 2165 | 42.9885
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 25.9515 | 368 | 70.5203
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.12489 | 2 | 62.4437
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | vegetation category 1 | not in bushfire | NOT IN BUSHFIRE | 0.50936 | 9 | 56.5961
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.41605 | 7 | 59.4355
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.082326 | 1 | 82.3258
Overhead Mains - LV | MAITLAND | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.10577 | 1 | 105.7659
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 0.45609 | 12 | 38.0077
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 0.33611 | 10 | 33.6109
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.036188 | 1 | 36.1885
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 1.2022 | 20 | 60.1104
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 3.034 | 72 | 42.1394
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 41.9942 | 1202 | 34.9369
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | not in bushfire | vegetation category 2 | BUSHFIRE | 0.046852 | 2 | 23.4258
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 25.6475 | 402 | 63.7998
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.037984 | 1 | 37.9839
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.047714 | 3 | 15.9045
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | vegetation category 1 | vegetation category 2 | BUSHFIRE | 0.030741 | 1 | 30.7406
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.17006 | 3 | 56.6865
Overhead Mains - LV | MAITLAND | COPPER | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.0479 | 1 | 47.8995
Overhead Mains - LV | MAITLAND | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 99.9122 | 2620 | 38.1344
Overhead Mains - LV | MAITLAND | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.017626 | 1 | 17.6263
Overhead Mains - LV | MAITLAND | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.24759 | 6 | 41.2642
Overhead Mains - LV | MAITLAND | PVC_BUNDLE | PVC | COVERED | not in bushfire | buffer | BUSHFIRE | 0.31525 | 13 | 24.2499
Overhead Mains - LV | MAITLAND | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 6.3191 | 284 | 22.2503
Overhead Mains - LV | MAITLAND | PVC_BUNDLE | PVC | COVERED | not in bushfire | vegetation category 3 | BUSHFIRE | 0.40979 | 18 | 22.7661
Overhead Mains - LV | MAITLAND | PVC_SINGLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.13266 | 5 | 26.5328
Overhead Mains - LV | MAITLAND | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.5167 | 43 | 35.2712
Overhead Mains - LV | MANLY | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 2.3243 | 68 | 34.1809
Overhead Mains - LV | MANLY | ALUMINIUM | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 0.28532 | 7 | 40.7598
Overhead Mains - LV | MANLY | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.043351 | 3 | 14.4502
Overhead Mains - LV | MANLY | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 18.5378 | 550 | 33.705
Overhead Mains - LV | MANLY | ALUMINIUM | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.041416 | 1 | 41.416
Overhead Mains - LV | MANLY | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.028358 | 1 | 28.3581
Overhead Mains - LV | MANLY | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 5.9362 | 170 | 34.9186
Overhead Mains - LV | MANLY | COPPER | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 0.74215 | 22 | 33.7339
Overhead Mains - LV | MANLY | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.11949 | 4 | 29.8727
Overhead Mains - LV | MANLY | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.088265 | 3 | 29.4217
Overhead Mains - LV | MANLY | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.2424 | 8 | 30.3001
Overhead Mains - LV | MANLY | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 50.0284 | 1531 | 32.677
Overhead Mains - LV | MANLY | COPPER | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.2948 | 7 | 42.1138
Overhead Mains - LV | MANLY | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.13806 | 3 | 46.0204
Overhead Mains - LV | MANLY | COPPER | BARE | BARE | vegetation category 1 | vegetation category 2 | BUSHFIRE | 0.067423 | 2 | 33.7117
Overhead Mains - LV | MANLY | COPPER | BARE | BARE | vegetation category 2 | vegetation category 1 | BUSHFIRE | 0.31488 | 10 | 31.4884
Overhead Mains - LV | MANLY | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.038405 | 1 | 38.4046
Overhead Mains - LV | MANLY | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 25.2332 | 999 | 25.2585
Overhead Mains - LV | MANLY | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.079163 | 3 | 26.3875
Overhead Mains - LV | MANLY | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.4558 | 22 | 20.7182
Overhead Mains - LV | MANLY | TWIN_TWIST | BARE | BARE | buffer | buffer | BUSHFIRE | 1.38 | 39 | 35.3855
Overhead Mains - LV | MANLY | TWIN_TWIST | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 0.18388 | 6 | 30.6459
Overhead Mains - LV | MANLY | TWIN_TWIST | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.040615 | 1 | 40.6149
Overhead Mains - LV | MANLY | TWIN_TWIST | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.081729 | 2 | 40.8643
Overhead Mains - LV | MANLY | TWIN_TWIST | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 4.6612 | 137 | 34.0236
Overhead Mains - LV | MANLY | TWIN_TWIST | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.044071 | 1 | 44.0713
Overhead Mains - LV | MANLY | TWIN_TWIST | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.077081 | 2 | 38.5406
Overhead Mains - LV | MANLY | TWIN_TWIST | BARE | BARE | vegetation category 2 | vegetation category 1 | BUSHFIRE | 0.03574 | 1 | 35.7402
Overhead Mains - LV | MANLY | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 10.8588 | 620 | 17.5141
Overhead Mains - LV | MARRICKVILLE | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 19.3052 | 699 | 27.6184
Overhead Mains - LV | MARRICKVILLE | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 151.0573 | 5722 | 26.3994
Overhead Mains - LV | MARRICKVILLE | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 41.8132 | 2111 | 19.8073
Overhead Mains - LV | MARRICKVILLE | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.085652 | 4 | 21.413
Overhead Mains - LV | MARRICKVILLE | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 2.6226 | 116 | 22.6083
Overhead Mains - LV | MARRICKVILLE | PVC_SINGLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.013012 | 1 | 13.0115
Overhead Mains - LV | MARRICKVILLE | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 3.4899 | 167 | 20.8978
Overhead Mains - LV | MID-WESTERN REGIONAL | ACSR | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.049675 | 1 | 49.6747
Overhead Mains - LV | MOSMAN | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 0.33804 | 10 | 33.8041
Overhead Mains - LV | MOSMAN | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 6.12 | 194 | 31.5466
Overhead Mains - LV | MOSMAN | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 6.8491 | 207 | 33.0875
Overhead Mains - LV | MOSMAN | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.28764 | 8 | 35.9547
Overhead Mains - LV | MOSMAN | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 39.9677 | 1299 | 30.768
Overhead Mains - LV | MOSMAN | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.012428 | 1 | 12.4284
Overhead Mains - LV | MOSMAN | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.41086 | 13 | 31.6045
Overhead Mains - LV | MOSMAN | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 11.9582 | 439 | 27.2396
Overhead Mains - LV | MOSMAN | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.012967 | 1 | 12.9671
Overhead Mains - LV | MOSMAN | PVC_BUNDLE | PVC | COVERED | buffer | vegetation category 1 | BUSHFIRE | 0.016942 | 1 | 16.9418
Overhead Mains - LV | MOSMAN | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.13209 | 9 | 14.6763
Overhead Mains - LV | MOSMAN | PVC_BUNDLE | PVC | COVERED | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.080305 | 4 | 20.0763
Overhead Mains - LV | MOSMAN | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 7.7666 | 480 | 16.1804
Overhead Mains - LV | MUSWELLBROOK | ACSR | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 0.50402 | 6 | 84.0029
Overhead Mains - LV | MUSWELLBROOK | ACSR | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.13302 | 2 | 66.5106
Overhead Mains - LV | MUSWELLBROOK | ACSR | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.43586 | 13 | 33.5274
Overhead Mains - LV | MUSWELLBROOK | ACSR | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 2.5525 | 34 | 75.0733
Overhead Mains - LV | MUSWELLBROOK | ACSR | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.10366 | 1 | 103.6551
Overhead Mains - LV | MUSWELLBROOK | ACSR | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.31049 | 5 | 62.0982
Overhead Mains - LV | MUSWELLBROOK | ACSR | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.10683 | 2 | 53.4146
Overhead Mains - LV | MUSWELLBROOK | ALUMINIUM | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 1.2044 | 17 | 70.8476
Overhead Mains - LV | MUSWELLBROOK | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 1.2532 | 26 | 48.2016
Overhead Mains - LV | MUSWELLBROOK | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 11.654 | 270 | 43.1631
Overhead Mains - LV | MUSWELLBROOK | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 5.5773 | 94 | 59.3331
Overhead Mains - LV | MUSWELLBROOK | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.29964 | 5 | 59.9277
Overhead Mains - LV | MUSWELLBROOK | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 1.0453 | 16 | 65.3282
Overhead Mains - LV | MUSWELLBROOK | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 0.11005 | 2 | 55.027
Overhead Mains - LV | MUSWELLBROOK | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.07554 | 1 | 75.5396
Overhead Mains - LV | MUSWELLBROOK | COPPER | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 0.79378 | 22 | 36.0809
Overhead Mains - LV | MUSWELLBROOK | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 2.1956 | 62 | 35.4126
Overhead Mains - LV | MUSWELLBROOK | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 10.2178 | 342 | 29.8765
Overhead Mains - LV | MUSWELLBROOK | COPPER | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 6.3665 | 114 | 55.8466
Overhead Mains - LV | MUSWELLBROOK | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.13433 | 3 | 44.777
Overhead Mains - LV | MUSWELLBROOK | COPPER | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.80379 | 16 | 50.2371
Overhead Mains - LV | MUSWELLBROOK | COPPER | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.18869 | 4 | 47.1734
Overhead Mains - LV | MUSWELLBROOK | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 41.1096 | 1048 | 39.2267
Overhead Mains - LV | MUSWELLBROOK | PVC | PVC | COVERED | not in bushfire | vegetation category 3 | BUSHFIRE | 0.036837 | 1 | 36.8367
Overhead Mains - LV | MUSWELLBROOK | PVC_BUNDLE | PVC | COVERED | buffer | vegetation category 3 | BUSHFIRE | 0.078636 | 1 | 78.6358
Overhead Mains - LV | MUSWELLBROOK | PVC_BUNDLE | PVC | COVERED | not in bushfire | buffer | BUSHFIRE | 0.0308 | 1 | 30.8
Overhead Mains - LV | MUSWELLBROOK | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.5583 | 44 | 35.4164
Overhead Mains - LV | MUSWELLBROOK | PVC_BUNDLE | PVC | COVERED | not in bushfire | vegetation category 3 | BUSHFIRE | 0.3816 | 9 | 42.4
Overhead Mains - LV | MUSWELLBROOK | PVC_SINGLE | PVC | COVERED | not in bushfire | buffer | BUSHFIRE | 0.015632 | 1 | 15.632
Overhead Mains - LV | MUSWELLBROOK | PVC_SINGLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.10034 | 3 | 33.4461
Overhead Mains - LV | MUSWELLBROOK | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.25362 | 7 | 36.2311
Overhead Mains - LV | NEWCASTLE | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 28.884 | 702 | 41.1453
Overhead Mains - LV | NEWCASTLE | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.39469 | 8 | 49.3368
Overhead Mains - LV | NEWCASTLE | ALUMINIUM | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.14862 | 2 | 74.3113
Overhead Mains - LV | NEWCASTLE | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 239.9157 | 6286 | 38.1667
Overhead Mains - LV | NEWCASTLE | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.05274 | 2 | 26.3699
Overhead Mains - LV | NEWCASTLE | ALUMINIUM | BARE | BARE | vegetation category 3 | buffer | BUSHFIRE | 0.09625 | 1 | 96.2501
Overhead Mains - LV | NEWCASTLE | ALUMINIUM | BARE | BARE | vegetation category 3 | vegetation category 3 | BUSHFIRE | 0.58419 | 9 | 64.9099
Overhead Mains - LV | NEWCASTLE | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 25.1893 | 672 | 37.484
Overhead Mains - LV | NEWCASTLE | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.42472 | 12 | 35.3934
Overhead Mains - LV | NEWCASTLE | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.11784 | 4 | 29.4609
Overhead Mains - LV | NEWCASTLE | COPPER | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 0.30037 | 3 | 100.1238
Overhead Mains - LV | NEWCASTLE | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 230.7256 | 6644 | 34.7269
Overhead Mains - LV | NEWCASTLE | COPPER | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.016285 | 1 | 16.2854
Overhead Mains - LV | NEWCASTLE | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.46192 | 8 | 57.7398
Overhead Mains - LV | NEWCASTLE | COPPER | BARE | BARE | vegetation category 3 | vegetation category 3 | BUSHFIRE | 0.62838 | 8 | 78.5477
Overhead Mains - LV | NEWCASTLE | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 165.2497 | 5921 | 27.9091
Overhead Mains - LV | NEWCASTLE | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.4326 | 12 | 36.05
Overhead Mains - LV | NEWCASTLE | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.59966 | 18 | 33.3142
Overhead Mains - LV | NEWCASTLE | PVC_BUNDLE | PVC | COVERED | buffer | vegetation category 1 | BUSHFIRE | 0.052697 | 1 | 52.6965
Overhead Mains - LV | NEWCASTLE | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 3.8225 | 122 | 31.3316
Overhead Mains - LV | NEWCASTLE | PVC_SINGLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.23247 | 5 | 46.4946
Overhead Mains - LV | NEWCASTLE | PVC_SINGLE | PVC | COVERED | buffer | vegetation category 1 | BUSHFIRE | 0.052167 | 1 | 52.1668
Overhead Mains - LV | NEWCASTLE | PVC_SINGLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.33167 | 11 | 30.152
Overhead Mains - LV | NEWCASTLE | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 3.8377 | 92 | 41.714
Overhead Mains - LV | NORTH SYDNEY | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 0.37047 | 11 | 33.6793
Overhead Mains - LV | NORTH SYDNEY | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 11.687 | 388 | 30.1211
Overhead Mains - LV | NORTH SYDNEY | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 0.69359 | 25 | 27.7435
Overhead Mains - LV | NORTH SYDNEY | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 66.619 | 2296 | 29.0152
Overhead Mains - LV | NORTH SYDNEY | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.40806 | 8 | 51.008
Overhead Mains - LV | NORTH SYDNEY | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.28382 | 9 | 31.5356
Overhead Mains - LV | NORTH SYDNEY | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 30.6123 | 1171 | 26.142
Overhead Mains - LV | NORTH SYDNEY | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.018732 | 1 | 18.7321
Overhead Mains - LV | NORTH SYDNEY | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.81509 | 38 | 21.4496
Overhead Mains - LV | NORTH SYDNEY | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 10.2169 | 572 | 17.8618
Overhead Mains - LV | PARRAMATTA | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.20939 | 8 | 26.1731
Overhead Mains - LV | PARRAMATTA | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 2.8119 | 82 | 34.2913
Overhead Mains - LV | PARRAMATTA | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.0584 | 42 | 25.199
Overhead Mains - LV | PARRAMATTA | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.0527 | 3 | 17.5666
Overhead Mains - LV | PARRAMATTA | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.2184 | 14 | 15.6002
Overhead Mains - LV | PITTWATER | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 21.8831 | 500 | 43.7663
Overhead Mains - LV | PITTWATER | ALUMINIUM | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 2.8028 | 72 | 38.9278
Overhead Mains - LV | PITTWATER | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.16922 | 3 | 56.4057
Overhead Mains - LV | PITTWATER | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.13559 | 4 | 33.8981
Overhead Mains - LV | PITTWATER | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 65.3553 | 1666 | 39.2289
Overhead Mains - LV | PITTWATER | ALUMINIUM | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.34613 | 8 | 43.2668
Overhead Mains - LV | PITTWATER | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.27215 | 6 | 45.3578
Overhead Mains - LV | PITTWATER | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 15.6412 | 413 | 37.8722
Overhead Mains - LV | PITTWATER | COPPER | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 2.0978 | 64 | 32.7785
Overhead Mains - LV | PITTWATER | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.36922 | 6 | 61.5367
Overhead Mains - LV | PITTWATER | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.089196 | 3 | 29.7322
Overhead Mains - LV | PITTWATER | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.1529 | 3 | 50.9657
Overhead Mains - LV | PITTWATER | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 50.8512 | 1477 | 34.4287
Overhead Mains - LV | PITTWATER | COPPER | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.093585 | 1 | 93.5851
Overhead Mains - LV | PITTWATER | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 1.796 | 51 | 35.2153
Overhead Mains - LV | PITTWATER | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 64.4086 | 1945 | 33.115
Overhead Mains - LV | PITTWATER | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.060007 | 2 | 30.0037
Overhead Mains - LV | PITTWATER | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.29625 | 9 | 32.9167
Overhead Mains - LV | PITTWATER | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.45684 | 16 | 28.5522
Overhead Mains - LV | PITTWATER | TWIN_TWIST | BARE | BARE | buffer | buffer | BUSHFIRE | 4.2922 | 113 | 37.9841
Overhead Mains - LV | PITTWATER | TWIN_TWIST | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 1.3806 | 35 | 39.4447
Overhead Mains - LV | PITTWATER | TWIN_TWIST | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.035879 | 1 | 35.8795
Overhead Mains - LV | PITTWATER | TWIN_TWIST | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.068419 | 2 | 34.2097
Overhead Mains - LV | PITTWATER | TWIN_TWIST | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.03574 | 1 | 35.74
Overhead Mains - LV | PITTWATER | TWIN_TWIST | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 27.4375 | 695 | 39.4784
Overhead Mains - LV | PITTWATER | TWIN_TWIST | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.034053 | 1 | 34.0531
Overhead Mains - LV | PITTWATER | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 19.5872 | 986 | 19.8653
Overhead Mains - LV | PORT STEPHENS | ACSR | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 0.040352 | 1 | 40.3519
Overhead Mains - LV | PORT STEPHENS | ACSR | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.098876 | 2 | 49.4381
Overhead Mains - LV | PORT STEPHENS | ACSR | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 2.0725 | 35 | 59.2147
Overhead Mains - LV | PORT STEPHENS | ACSR | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.032077 | 1 | 32.0769
Overhead Mains - LV | PORT STEPHENS | ACSR | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.04469 | 1 | 44.6901
Overhead Mains - LV | PORT STEPHENS | ACSR | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 0.96301 | 14 | 68.7866
Overhead Mains - LV | PORT STEPHENS | ACSR | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.10084 | 1 | 100.8397
Overhead Mains - LV | PORT STEPHENS | ACSR | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.29433 | 3 | 98.1109
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 38.2871 | 848 | 45.1499
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 26.8248 | 588 | 45.6204
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 6.9986 | 111 | 63.0501
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.91654 | 16 | 57.2835
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 55.7361 | 883 | 63.1213
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 3.328 | 71 | 46.8726
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 60.8211 | 1430 | 42.5322
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 1 | BUSHFIRE | 0.31793 | 5 | 63.5858
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 2 | BUSHFIRE | 0.45119 | 9 | 50.1324
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 37.5377 | 611 | 61.4365
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 2.1327 | 38 | 56.1245
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | vegetation category 1 | not in bushfire | NOT IN BUSHFIRE | 0.33788 | 10 | 33.7883
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 3.6467 | 55 | 66.3042
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 2 | BUSHFIRE | 0.070725 | 1 | 70.7253
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 3.9795 | 66 | 60.2959
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.015114 | 1 | 15.1141
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | vegetation category 2 | not in bushfire | NOT IN BUSHFIRE | 0.063181 | 2 | 31.5905
Overhead Mains - LV | PORT STEPHENS | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.11406 | 2 | 57.0287
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 7.9915 | 208 | 38.4207
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 9.0592 | 241 | 37.59
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.97729 | 15 | 65.1529
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.17409 | 4 | 43.5215
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 11.9669 | 224 | 53.4237
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 1.8338 | 43 | 42.6462
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 33.3067 | 914 | 36.4406
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 13.899 | 270 | 51.4777
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.3921 | 9 | 43.5666
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | vegetation category 1 | not in bushfire | NOT IN BUSHFIRE | 0.18636 | 5 | 37.2716
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.55094 | 15 | 36.7293
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | vegetation category 1 | vegetation category 2 | BUSHFIRE | 0.33142 | 7 | 47.3454
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.49445 | 7 | 70.6362
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.12034 | 2 | 60.1723
Overhead Mains - LV | PORT STEPHENS | COPPER | BARE | BARE | vegetation category 2 | not in bushfire | NOT IN BUSHFIRE | 0.030075 | 1 | 30.0753
Overhead Mains - LV | PORT STEPHENS | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 101.6327 | 2515 | 40.4106
Overhead Mains - LV | PORT STEPHENS | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.34263 | 10 | 34.2634
Overhead Mains - LV | PORT STEPHENS | PVC_BUNDLE | PVC | COVERED | buffer | not in bushfire | NOT IN BUSHFIRE | 0.23599 | 6 | 39.3312
Overhead Mains - LV | PORT STEPHENS | PVC_BUNDLE | PVC | COVERED | buffer | vegetation category 3 | BUSHFIRE | 0.74335 | 20 | 37.1673
Overhead Mains - LV | PORT STEPHENS | PVC_BUNDLE | PVC | COVERED | not in bushfire | buffer | BUSHFIRE | 0.067936 | 2 | 33.9679
Overhead Mains - LV | PORT STEPHENS | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.4635 | 16 | 28.9688
Overhead Mains - LV | PORT STEPHENS | PVC_BUNDLE | PVC | COVERED | not in bushfire | vegetation category 3 | BUSHFIRE | 0.36643 | 11 | 33.3118
Overhead Mains - LV | PORT STEPHENS | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | buffer | BUSHFIRE | 0.027589 | 1 | 27.5895
Overhead Mains - LV | PORT STEPHENS | PVC_SINGLE | PVC | COVERED | buffer | not in bushfire | NOT IN BUSHFIRE | 0.079127 | 2 | 39.5634
Overhead Mains - LV | PORT STEPHENS | PVC_SINGLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.030009 | 1 | 30.009
Overhead Mains - LV | PORT STEPHENS | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.7766 | 51 | 34.8351
Overhead Mains - LV | RANDWICK | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 28.4717 | 955 | 29.8133
Overhead Mains - LV | RANDWICK | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 224.7872 | 8121 | 27.6797
Overhead Mains - LV | RANDWICK | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 73.5655 | 3196 | 23.018
Overhead Mains - LV | RANDWICK | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.30462 | 16 | 19.0388
Overhead Mains - LV | RANDWICK | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 2.559 | 112 | 22.8481
Overhead Mains - LV | RANDWICK | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 2.684 | 123 | 21.8209
Overhead Mains - LV | ROCKDALE | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 69.5953 | 2173 | 32.0273
Overhead Mains - LV | ROCKDALE | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 143.4639 | 4849 | 29.5863
Overhead Mains - LV | ROCKDALE | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 50.3591 | 1949 | 25.8384
Overhead Mains - LV | ROCKDALE | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.050182 | 2 | 25.0908
Overhead Mains - LV | ROCKDALE | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 8.0471 | 279 | 28.8425
Overhead Mains - LV | ROCKDALE | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 5.2659 | 267 | 19.7224
Overhead Mains - LV | RYDE | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 3.1342 | 94 | 33.342
Overhead Mains - LV | RYDE | ALUMINIUM | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.081449 | 2 | 40.7246
Overhead Mains - LV | RYDE | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 27.5009 | 849 | 32.3922
Overhead Mains - LV | RYDE | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.58698 | 15 | 39.1317
Overhead Mains - LV | RYDE | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 2 | BUSHFIRE | 0.059033 | 1 | 59.0335
Overhead Mains - LV | RYDE | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 10.7854 | 331 | 32.5843
Overhead Mains - LV | RYDE | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.023879 | 1 | 23.8793
Overhead Mains - LV | RYDE | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.10507 | 3 | 35.0233
Overhead Mains - LV | RYDE | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 225.8131 | 7081 | 31.89
Overhead Mains - LV | RYDE | COPPER | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.01942 | 1 | 19.4203
Overhead Mains - LV | RYDE | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 1.7974 | 49 | 36.6809
Overhead Mains - LV | RYDE | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.19062 | 3 | 63.5415
Overhead Mains - LV | RYDE | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 55.9514 | 2087 | 26.8095
Overhead Mains - LV | RYDE | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.17708 | 11 | 16.0981
Overhead Mains - LV | RYDE | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.56365 | 29 | 19.4362
Overhead Mains - LV | RYDE | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.053753 | 2 | 26.8765
Overhead Mains - LV | RYDE | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | vegetation category 2 | BUSHFIRE | 0.03127 | 1 | 31.2698
Overhead Mains - LV | RYDE | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 27.5697 | 1595 | 17.2851
Overhead Mains - LV | SINGLETON | ACSR | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 1.1755 | 18 | 65.3045
Overhead Mains - LV | SINGLETON | ACSR | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 2.1113 | 22 | 95.9667
Overhead Mains - LV | SINGLETON | ACSR | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 3.9561 | 44 | 89.9119
Overhead Mains - LV | SINGLETON | ACSR | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 7.7776 | 116 | 67.0485
Overhead Mains - LV | SINGLETON | ACSR | BARE | BARE | not in bushfire | vegetation category 1 | BUSHFIRE | 14.4052 | 162 | 88.9209
Overhead Mains - LV | SINGLETON | ACSR | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 6.6226 | 73 | 90.7201
Overhead Mains - LV | SINGLETON | ACSR | BARE | BARE | vegetation category 1 | not in bushfire | NOT IN BUSHFIRE | 0.065456 | 1 | 65.4558
Overhead Mains - LV | SINGLETON | ACSR | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.63012 | 6 | 105.0193
Overhead Mains - LV | SINGLETON | ACSR | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 1.7993 | 18 | 99.959
Overhead Mains - LV | SINGLETON | ACSR | BARE | BARE | vegetation category 2 | vegetation category 1 | BUSHFIRE | 1.0363 | 13 | 79.7177
Overhead Mains - LV | SINGLETON | ACSR | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 1.8515 | 19 | 97.4478
Overhead Mains - LV | SINGLETON | ALUMINIUM | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 1.7677 | 28 | 63.1334
Overhead Mains - LV | SINGLETON | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 2.1703 | 26 | 83.4714
Overhead Mains - LV | SINGLETON | ALUMINIUM | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 0.62243 | 9 | 69.1589
Overhead Mains - LV | SINGLETON | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 24.4482 | 529 | 46.2158
Overhead Mains - LV | SINGLETON | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 1 | BUSHFIRE | 11.001 | 141 | 78.0215
Overhead Mains - LV | SINGLETON | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 4.0427 | 59 | 68.5212
Overhead Mains - LV | SINGLETON | ALUMINIUM | BARE | BARE | vegetation category 1 | not in bushfire | NOT IN BUSHFIRE | 0.10358 | 1 | 103.5821
Overhead Mains - LV | SINGLETON | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.61046 | 8 | 76.3077
Overhead Mains - LV | SINGLETON | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.47719 | 7 | 68.1693
Overhead Mains - LV | SINGLETON | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 1 | BUSHFIRE | 0.34542 | 4 | 86.356
Overhead Mains - LV | SINGLETON | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.12807 | 2 | 64.0348
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 0.97778 | 20 | 48.8889
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 2.8926 | 54 | 53.5665
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 1.3575 | 19 | 71.4475
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 24.282 | 627 | 38.7272
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | not in bushfire | vegetation category 1 | BUSHFIRE | 17.5009 | 287 | 60.9787
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 2.3718 | 41 | 57.8486
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | vegetation category 1 | not in bushfire | NOT IN BUSHFIRE | 0.092178 | 2 | 46.089
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.52364 | 12 | 43.6367
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | vegetation category 1 | vegetation category 3 | BUSHFIRE | 0.6138 | 10 | 61.3796
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | vegetation category 2 | not in bushfire | NOT IN BUSHFIRE | 0.52534 | 4 | 131.3343
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | vegetation category 2 | vegetation category 1 | BUSHFIRE | 0.51631 | 7 | 73.7582
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.32981 | 5 | 65.9618
Overhead Mains - LV | SINGLETON | COPPER | BARE | BARE | vegetation category 3 | vegetation category 1 | BUSHFIRE | 0.079264 | 2 | 39.6321
Overhead Mains - LV | SINGLETON | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 91.2526 | 1969 | 46.3447
Overhead Mains - LV | SINGLETON | PVC | PVC | COVERED | buffer | vegetation category 1 | BUSHFIRE | 0.03344 | 1 | 33.4403
Overhead Mains - LV | SINGLETON | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.041691 | 1 | 41.6908
Overhead Mains - LV | SINGLETON | PVC_BUNDLE | PVC | COVERED | buffer | vegetation category 1 | BUSHFIRE | 0.088574 | 2 | 44.2869
Overhead Mains - LV | SINGLETON | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.51168 | 20 | 25.584
Overhead Mains - LV | SINGLETON | PVC_BUNDLE | PVC | COVERED | not in bushfire | vegetation category 1 | BUSHFIRE | 0.14387 | 5 | 28.7736
Overhead Mains - LV | SINGLETON | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.082773 | 2 | 41.3865
Overhead Mains - LV | SINGLETON | PVC_SINGLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.074614 | 2 | 37.3069
Overhead Mains - LV | SINGLETON | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.28457 | 10 | 28.4574
Overhead Mains - LV | STRATHFIELD | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 13.561 | 430 | 31.5372
Overhead Mains - LV | STRATHFIELD | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 77.416 | 2477 | 31.254
Overhead Mains - LV | STRATHFIELD | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 17.239 | 726 | 23.7451
Overhead Mains - LV | STRATHFIELD | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.94083 | 35 | 26.881
Overhead Mains - LV | STRATHFIELD | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 4.8931 | 291 | 16.8149
Overhead Mains - LV | SUTHERLAND | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 39.2228 | 1205 | 32.55
Overhead Mains - LV | SUTHERLAND | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.024861 | 1 | 24.8605
Overhead Mains - LV | SUTHERLAND | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.79992 | 23 | 34.779
Overhead Mains - LV | SUTHERLAND | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 129.2522 | 3956 | 32.6724
Overhead Mains - LV | SUTHERLAND | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 1.7378 | 33 | 52.6611
Overhead Mains - LV | SUTHERLAND | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 32.7491 | 1031 | 31.7644
Overhead Mains - LV | SUTHERLAND | COPPER | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 0.26359 | 7 | 37.6553
Overhead Mains - LV | SUTHERLAND | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.14979 | 3 | 49.9307
Overhead Mains - LV | SUTHERLAND | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.91467 | 32 | 28.5833
Overhead Mains - LV | SUTHERLAND | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 319.5398 | 10459 | 30.5517
Overhead Mains - LV | SUTHERLAND | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 2.0703 | 39 | 53.085
Overhead Mains - LV | SUTHERLAND | COPPER | BARE | BARE | vegetation category 2 | not in bushfire | NOT IN BUSHFIRE | 0.045629 | 1 | 45.6291
Overhead Mains - LV | SUTHERLAND | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.05665 | 2 | 28.3252
Overhead Mains - LV | SUTHERLAND | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 132.0572 | 4868 | 27.1276
Overhead Mains - LV | SUTHERLAND | PVC | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.17189 | 2 | 85.9464
Overhead Mains - LV | SUTHERLAND | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.03449 | 1 | 34.4901
Overhead Mains - LV | SUTHERLAND | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 1.471 | 44 | 33.4309
Overhead Mains - LV | SUTHERLAND | PVC_BUNDLE | PVC | COVERED | buffer | not in bushfire | NOT IN BUSHFIRE | 0.045705 | 2 | 22.8523
Overhead Mains - LV | SUTHERLAND | PVC_BUNDLE | PVC | COVERED | buffer | vegetation category 1 | BUSHFIRE | 0.039849 | 1 | 39.8494
Overhead Mains - LV | SUTHERLAND | PVC_BUNDLE | PVC | COVERED | buffer | vegetation category 2 | BUSHFIRE | 0.023177 | 1 | 23.1771
Overhead Mains - LV | SUTHERLAND | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 5.536 | 194 | 28.5363
Overhead Mains - LV | SUTHERLAND | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 29.065 | 1484 | 19.5856
Overhead Mains - LV | SYDNEY | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 13.3618 | 496 | 26.9391
Overhead Mains - LV | SYDNEY | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 87.6203 | 3391 | 25.8391
Overhead Mains - LV | SYDNEY | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 111.8995 | 5513 | 20.2974
Overhead Mains - LV | SYDNEY | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.070703 | 4 | 17.6758
Overhead Mains - LV | SYDNEY | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 7.1002 | 371 | 19.1381
Overhead Mains - LV | SYDNEY | PVC_SINGLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.012439 | 1 | 12.4389
Overhead Mains - LV | SYDNEY | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 3.4703 | 170 | 20.4137
Overhead Mains - LV | THE HILLS SHIRE | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 0.15304 | 4 | 38.2594
Overhead Mains - LV | THE HILLS SHIRE | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.62152 | 21 | 29.5961
Overhead Mains - LV | THE HILLS SHIRE | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 0.067711 | 1 | 67.7108
Overhead Mains - LV | THE HILLS SHIRE | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.018973 | 1 | 18.9727
Overhead Mains - LV | THE HILLS SHIRE | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.16916 | 8 | 21.1447
Overhead Mains - LV | THE HILLS SHIRE | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.39414 | 18 | 21.8969
Overhead Mains - LV | THE HILLS SHIRE | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.15751 | 6 | 26.2518
Overhead Mains - LV | THE HILLS SHIRE | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.88827 | 43 | 20.6575
Overhead Mains - LV | UPPER HUNTER | ACSR | BARE | BARE | buffer | buffer | BUSHFIRE | 0.15767 | 2 | 78.8344
Overhead Mains - LV | UPPER HUNTER | ACSR | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 3.6749 | 67 | 54.8495
Overhead Mains - LV | UPPER HUNTER | ACSR | BARE | BARE | vegetation category 3 | buffer | BUSHFIRE | 0.15422 | 1 | 154.2242
Overhead Mains - LV | UPPER HUNTER | ACSR | BARE | BARE | vegetation category 3 | vegetation category 3 | BUSHFIRE | 10.2783 | 128 | 80.2989
Overhead Mains - LV | UPPER HUNTER | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 2.3748 | 44 | 53.9729
Overhead Mains - LV | UPPER HUNTER | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 23.7189 | 533 | 44.5007
Overhead Mains - LV | UPPER HUNTER | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.0692 | 1 | 69.1999
Overhead Mains - LV | UPPER HUNTER | ALUMINIUM | BARE | BARE | vegetation category 3 | buffer | BUSHFIRE | 0.17733 | 3 | 59.1102
Overhead Mains - LV | UPPER HUNTER | ALUMINIUM | BARE | BARE | vegetation category 3 | vegetation category 3 | BUSHFIRE | 11.44 | 179 | 63.9107
Overhead Mains - LV | UPPER HUNTER | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 0.72881 | 14 | 52.058
Overhead Mains - LV | UPPER HUNTER | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 14.8186 | 445 | 33.3002
Overhead Mains - LV | UPPER HUNTER | COPPER | BARE | BARE | vegetation category 3 | buffer | BUSHFIRE | 0.12453 | 3 | 41.5101
Overhead Mains - LV | UPPER HUNTER | COPPER | BARE | BARE | vegetation category 3 | vegetation category 3 | BUSHFIRE | 11.9088 | 208 | 57.2538
Overhead Mains - LV | UPPER HUNTER | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 48.2289 | 1219 | 39.5643
Overhead Mains - LV | UPPER HUNTER | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 2.1953 | 73 | 30.0724
Overhead Mains - LV | UPPER HUNTER | PVC_BUNDLE | PVC | COVERED | vegetation category 3 | vegetation category 3 | BUSHFIRE | 0.42908 | 7 | 61.2967
Overhead Mains - LV | UPPER HUNTER | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.061094 | 2 | 30.5469
Overhead Mains - LV | WARRINGAH | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 43.8662 | 1098 | 39.951
Overhead Mains - LV | WARRINGAH | ALUMINIUM | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 0.037235 | 1 | 37.2349
Overhead Mains - LV | WARRINGAH | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.076007 | 2 | 38.0033
Overhead Mains - LV | WARRINGAH | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 116.559 | 3110 | 37.4788
Overhead Mains - LV | WARRINGAH | ALUMINIUM | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.093694 | 2 | 46.8471
Overhead Mains - LV | WARRINGAH | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 1.8801 | 35 | 53.7176
Overhead Mains - LV | WARRINGAH | ALUMINIUM | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.16869 | 4 | 42.1726
Overhead Mains - LV | WARRINGAH | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.51136 | 11 | 46.4871
Overhead Mains - LV | WARRINGAH | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 25.9983 | 695 | 37.4076
Overhead Mains - LV | WARRINGAH | COPPER | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 0.057217 | 2 | 28.6086
Overhead Mains - LV | WARRINGAH | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.10681 | 2 | 53.4055
Overhead Mains - LV | WARRINGAH | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.065715 | 2 | 32.8577
Overhead Mains - LV | WARRINGAH | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 124.0437 | 3590 | 34.5526
Overhead Mains - LV | WARRINGAH | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 1.3609 | 34 | 40.0254
Overhead Mains - LV | WARRINGAH | COPPER | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.061889 | 2 | 30.9443
Overhead Mains - LV | WARRINGAH | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.41549 | 6 | 69.2475
Overhead Mains - LV | WARRINGAH | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 109.8755 | 3697 | 29.7202
Overhead Mains - LV | WARRINGAH | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.2728 | 14 | 19.4856
Overhead Mains - LV | WARRINGAH | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.0149 | 37 | 27.4287
Overhead Mains - LV | WARRINGAH | PVC_SINGLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.019045 | 1 | 19.0446
Overhead Mains - LV | WARRINGAH | TWIN_TWIST | BARE | BARE | buffer | buffer | BUSHFIRE | 6.5619 | 163 | 40.2571
Overhead Mains - LV | WARRINGAH | TWIN_TWIST | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 0.053103 | 1 | 53.1033
Overhead Mains - LV | WARRINGAH | TWIN_TWIST | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 48.8671 | 1302 | 37.5323
Overhead Mains - LV | WARRINGAH | TWIN_TWIST | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.07316 | 2 | 36.5798
Overhead Mains - LV | WARRINGAH | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 28.9188 | 1546 | 18.7055
Overhead Mains - LV | WAVERLEY | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 6.8652 | 248 | 27.6821
Overhead Mains - LV | WAVERLEY | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 66.7717 | 2518 | 26.5177
Overhead Mains - LV | WAVERLEY | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 24.3584 | 1153 | 21.1261
Overhead Mains - LV | WAVERLEY | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.54377 | 34 | 15.9932
Overhead Mains - LV | WAVERLEY | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.80539 | 47 | 17.1361
Overhead Mains - LV | WAVERLEY | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.74043 | 46 | 16.0962
Overhead Mains - LV | WILLOUGHBY | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 2.5499 | 77 | 33.1161
Overhead Mains - LV | WILLOUGHBY | ALUMINIUM | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.033722 | 1 | 33.7222
Overhead Mains - LV | WILLOUGHBY | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 17.8097 | 574 | 31.0274
Overhead Mains - LV | WILLOUGHBY | ALUMINIUM | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.097609 | 2 | 48.8045
Overhead Mains - LV | WILLOUGHBY | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.061581 | 2 | 30.7904
Overhead Mains - LV | WILLOUGHBY | ALUMINIUM | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.087888 | 2 | 43.944
Overhead Mains - LV | WILLOUGHBY | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.10147 | 3 | 33.8226
Overhead Mains - LV | WILLOUGHBY | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 17.2257 | 507 | 33.9758
Overhead Mains - LV | WILLOUGHBY | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 0.080989 | 2 | 40.4943
Overhead Mains - LV | WILLOUGHBY | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.20293 | 7 | 28.9904
Overhead Mains - LV | WILLOUGHBY | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 127.4703 | 4096 | 31.1207
Overhead Mains - LV | WILLOUGHBY | COPPER | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 0.11951 | 4 | 29.8777
Overhead Mains - LV | WILLOUGHBY | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.025133 | 1 | 25.1327
Overhead Mains - LV | WILLOUGHBY | COPPER | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 0.072433 | 2 | 36.2165
Overhead Mains - LV | WILLOUGHBY | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.24785 | 4 | 61.9623
Overhead Mains - LV | WILLOUGHBY | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 42.7987 | 1687 | 25.3697
Overhead Mains - LV | WILLOUGHBY | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.23302 | 7 | 33.2879
Overhead Mains - LV | WILLOUGHBY | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.032254 | 2 | 16.127
Overhead Mains - LV | WILLOUGHBY | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.3826 | 66 | 20.9487
Overhead Mains - LV | WILLOUGHBY | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 16.6475 | 999 | 16.6641
Overhead Mains - LV | WOOLLAHRA | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 5.2614 | 191 | 27.5466
Overhead Mains - LV | WOOLLAHRA | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 65.9334 | 2484 | 26.5432
Overhead Mains - LV | WOOLLAHRA | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 34.4085 | 1568 | 21.9442
Overhead Mains - LV | WOOLLAHRA | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.096994 | 10 | 9.6994
Overhead Mains - LV | WOOLLAHRA | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 2.018 | 102 | 19.7848
Overhead Mains - LV | WOOLLAHRA | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.3701 | 76 | 18.028
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | buffer | buffer | BUSHFIRE | 76.1034 | 1861 | 40.8938
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 12.034 | 318 | 37.8427
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 3.9216 | 66 | 59.4186
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.8817 | 16 | 55.1065
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 0.96359 | 14 | 68.8281
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 13.6078 | 366 | 37.1798
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 160.6229 | 4502 | 35.6781
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 2 | BUSHFIRE | 0.075595 | 1 | 75.5952
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | not in bushfire | vegetation category 3 | BUSHFIRE | 0.079563 | 2 | 39.7815
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 1.4262 | 26 | 54.8534
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | vegetation category 1 | not in bushfire | NOT IN BUSHFIRE | 0.072524 | 1 | 72.5244
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 1.7613 | 33 | 53.3721
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 2.4815 | 46 | 53.9458
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | vegetation category 2 | not in bushfire | NOT IN BUSHFIRE | 0.20497 | 4 | 51.2434
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 1 | BUSHFIRE | 0.74269 | 14 | 53.0494
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 0.2085 | 4 | 52.124
Overhead Mains - LV | WYONG | ALUMINIUM | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.26541 | 5 | 53.0818
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | buffer | buffer | BUSHFIRE | 66.4722 | 1488 | 44.6722
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | buffer | not in bushfire | NOT IN BUSHFIRE | 8.76 | 232 | 37.7584
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | buffer | vegetation category 1 | BUSHFIRE | 7.2191 | 145 | 49.7872
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | buffer | vegetation category 2 | BUSHFIRE | 0.80698 | 16 | 50.4364
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | buffer | vegetation category 3 | BUSHFIRE | 0.51554 | 10 | 51.5539
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | not in bushfire | buffer | BUSHFIRE | 8.645 | 205 | 42.1709
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 167.3373 | 5182 | 32.292
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | not in bushfire | vegetation category 1 | BUSHFIRE | 0.23865 | 3 | 79.5506
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | not in bushfire | vegetation category 2 | BUSHFIRE | 0.10063 | 2 | 50.3157
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | vegetation category 1 | buffer | BUSHFIRE | 1.5158 | 30 | 50.5281
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | vegetation category 1 | not in bushfire | NOT IN BUSHFIRE | 0.20337 | 3 | 67.7906
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | vegetation category 1 | vegetation category 1 | BUSHFIRE | 2.0542 | 42 | 48.9094
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | vegetation category 1 | vegetation category 2 | BUSHFIRE | 0.14863 | 3 | 49.5448
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | vegetation category 2 | buffer | BUSHFIRE | 4.1123 | 69 | 59.5979
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | vegetation category 2 | not in bushfire | NOT IN BUSHFIRE | 0.57401 | 13 | 44.155
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | vegetation category 2 | vegetation category 1 | BUSHFIRE | 1.0992 | 18 | 61.065
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | vegetation category 2 | vegetation category 2 | BUSHFIRE | 1.5847 | 22 | 72.034
Overhead Mains - LV | WYONG | COPPER | BARE | BARE | vegetation category 2 | vegetation category 3 | BUSHFIRE | 0.022684 | 1 | 22.6842
Overhead Mains - LV | WYONG | LV_ABC | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 219.4103 | 7129 | 30.7771
Overhead Mains - LV | WYONG | PVC | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.19553 | 6 | 32.5888
Overhead Mains - LV | WYONG | PVC | PVC | COVERED | buffer | not in bushfire | NOT IN BUSHFIRE | 0.088182 | 3 | 29.394
Overhead Mains - LV | WYONG | PVC | PVC | COVERED | buffer | vegetation category 1 | BUSHFIRE | 0.027341 | 1 | 27.3412
Overhead Mains - LV | WYONG | PVC | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 0.63423 | 34 | 18.6539
Overhead Mains - LV | WYONG | PVC | PVC | COVERED | vegetation category 1 | vegetation category 1 | BUSHFIRE | 0.041843 | 1 | 41.843
Overhead Mains - LV | WYONG | PVC_BUNDLE | PVC | COVERED | buffer | buffer | BUSHFIRE | 0.37191 | 14 | 26.5651
Overhead Mains - LV | WYONG | PVC_BUNDLE | PVC | COVERED | buffer | not in bushfire | NOT IN BUSHFIRE | 0.17124 | 7 | 24.4628
Overhead Mains - LV | WYONG | PVC_BUNDLE | PVC | COVERED | buffer | vegetation category 1 | BUSHFIRE | 0.11329 | 3 | 37.7631
Overhead Mains - LV | WYONG | PVC_BUNDLE | PVC | COVERED | not in bushfire | buffer | BUSHFIRE | 0.19566 | 6 | 32.6103
Overhead Mains - LV | WYONG | PVC_BUNDLE | PVC | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 1.8541 | 74 | 25.055
Overhead Mains - LV | WYONG | PVC_BUNDLE | PVC | COVERED | not in bushfire | vegetation category 2 | BUSHFIRE | 0.053355 | 2 | 26.6773
Overhead Mains - LV | WYONG | PVC_BUNDLE | PVC | COVERED | vegetation category 1 | buffer | BUSHFIRE | 0.10032 | 2 | 50.1616
Overhead Mains - LV | WYONG | PVC_BUNDLE | PVC | COVERED | vegetation category 2 | buffer | BUSHFIRE | 0.14723 | 4 | 36.8083
Overhead Mains - LV | WYONG | XLPE | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 10.0629 | 392 | 25.6707
Overhead Mains - LV | WYONG | XLPE_CONC_N | XLPE | COVERED | not in bushfire | not in bushfire | NOT IN BUSHFIRE | 2.0725 | 105 | 19.7377

## Bare Length (km)
BARE_VS_COVERED | BARE
LGA_NAME | BUSHFIRE_VS_NOT_BUSHFIRE_2022 | Sum of Count of ASSET_ID | Sum of Sum of ASSET_LENGTH | Average span length (m)
ASHFIELD | NOT IN BUSHFIRE | 2993 | 90.122 | 30.1109
ASHFIELD Total |  | 2993 | 90.122 | 30.1109
AUBURN | NOT IN BUSHFIRE | 5721 | 168.0517 | 29.3745
AUBURN Total |  | 5721 | 168.0517 | 29.3745
BANKSTOWN | BUSHFIRE | 581 | 19.2802 | 33.1845
| NOT IN BUSHFIRE | 16548 | 511.8261 | 30.9298
BANKSTOWN Total |  | 17129 | 531.1063 | 31.0063
BOTANY BAY | NOT IN BUSHFIRE | 2858 | 81.9141 | 28.6613
BOTANY BAY Total |  | 2858 | 81.9141 | 28.6613
BURWOOD | NOT IN BUSHFIRE | 2433 | 74.2301 | 30.5097
BURWOOD Total |  | 2433 | 74.2301 | 30.5097
CANADA BAY | NOT IN BUSHFIRE | 5209 | 165.4377 | 31.76
CANADA BAY Total |  | 5209 | 165.4377 | 31.76
CANTERBURY | NOT IN BUSHFIRE | 9765 | 307.0563 | 31.4446
CANTERBURY Total |  | 9765 | 307.0563 | 31.4446
CESSNOCK | BUSHFIRE | 2558 | 137.8499 | 53.8897
| NOT IN BUSHFIRE | 3714 | 151.1824 | 40.7061
CESSNOCK Total |  | 6272 | 289.0322 | 46.0829
DUNGOG | BUSHFIRE | 2 | 0.15564 | 77.8202
| NOT IN BUSHFIRE | 2 | 0.18008 | 90.039
DUNGOG Total |  | 4 | 0.33572 | 83.9296
GOSFORD | BUSHFIRE | 7006 | 285.6441 | 40.7714
| NOT IN BUSHFIRE | 8616 | 286.9746 | 33.3072
GOSFORD Total |  | 15622 | 572.6187 | 36.6546
HAWKESBURY | BUSHFIRE | 1 | 0.015951 | 15.9509
HAWKESBURY Total |  | 1 | 0.015951 | 15.9509
HORNSBY | BUSHFIRE | 4766 | 162.2918 | 34.052
| NOT IN BUSHFIRE | 8073 | 267.1301 | 33.0893
HORNSBY Total |  | 12839 | 429.4219 | 33.4467
HUNTERS HILL | BUSHFIRE | 95 | 3.1299 | 32.9461
| NOT IN BUSHFIRE | 1067 | 32.4644 | 30.4258
HUNTERS HILL Total |  | 1162 | 35.5942 | 30.6319
HURSTVILLE | BUSHFIRE | 280 | 8.4684 | 30.2441
| NOT IN BUSHFIRE | 6132 | 183.2843 | 29.8898
HURSTVILLE Total |  | 6412 | 191.7526 | 29.9053
KOGARAH | BUSHFIRE | 65 | 2.0836 | 32.0556
| NOT IN BUSHFIRE | 4302 | 131.9314 | 30.6675
KOGARAH Total |  | 4367 | 134.015 | 30.6881
KU-RING-GAI | BUSHFIRE | 3144 | 110.2089 | 35.0537
| NOT IN BUSHFIRE | 8954 | 305.759 | 34.1478
KU-RING-GAI Total |  | 12098 | 415.968 | 34.3832
LAKE MACQUARIE | BUSHFIRE | 6004 | 278.6395 | 46.409
| NOT IN BUSHFIRE | 12356 | 483.7643 | 39.1522
LAKE MACQUARIE Total |  | 18360 | 762.4038 | 41.5253
LANE COVE | BUSHFIRE | 246 | 8.0993 | 32.9238
| NOT IN BUSHFIRE | 2252 | 72.3716 | 32.1366
LANE COVE Total |  | 2498 | 80.4709 | 32.2141
LEICHHARDT | NOT IN BUSHFIRE | 3795 | 105.2927 | 27.7451
LEICHHARDT Total |  | 3795 | 105.2927 | 27.7451
MAITLAND | BUSHFIRE | 1175 | 75.094 | 63.9098
| NOT IN BUSHFIRE | 3445 | 139.2477 | 40.4202
MAITLAND Total |  | 4620 | 214.3417 | 46.3943
MANLY | BUSHFIRE | 327 | 11.3366 | 34.6685
| NOT IN BUSHFIRE | 2253 | 74.4388 | 33.0398
MANLY Total |  | 2580 | 85.7754 | 33.2463
MARRICKVILLE | NOT IN BUSHFIRE | 6421 | 170.3625 | 26.5321
MARRICKVILLE Total |  | 6421 | 170.3625 | 26.5321
MID-WESTERN REGIONAL | BUSHFIRE | 1 | 0.049675 | 49.6747
MID-WESTERN REGIONAL Total |  | 1 | 0.049675 | 49.6747
MOSMAN | BUSHFIRE | 239 | 7.8981 | 33.0464
| NOT IN BUSHFIRE | 1493 | 46.0877 | 30.8692
MOSMAN Total |  | 1732 | 53.9858 | 31.1696
MUSWELLBROOK | BUSHFIRE | 432 | 23.7586 | 54.9969
| NOT IN BUSHFIRE | 625 | 22.3077 | 35.6922
MUSWELLBROOK Total |  | 1057 | 46.0663 | 43.5821
NEWCASTLE | BUSHFIRE | 1432 | 57.2993 | 40.0135
| NOT IN BUSHFIRE | 12930 | 470.6412 | 36.3992
NEWCASTLE Total |  | 14362 | 527.9406 | 36.7595
NORTH SYDNEY | BUSHFIRE | 53 | 1.7559 | 33.131
| NOT IN BUSHFIRE | 2684 | 78.306 | 29.1751
NORTH SYDNEY Total |  | 2737 | 80.0619 | 29.2517
PARRAMATTA | NOT IN BUSHFIRE | 90 | 3.0213 | 33.5697
PARRAMATTA Total |  | 90 | 3.0213 | 33.5697
PITTWATER | BUSHFIRE | 1116 | 45.4146 | 40.6941
| NOT IN BUSHFIRE | 4009 | 149.9252 | 37.3972
PITTWATER Total |  | 5125 | 195.3398 | 38.1151
PORT STEPHENS | BUSHFIRE | 3577 | 195.8255 | 54.7457
| NOT IN BUSHFIRE | 3193 | 130.7143 | 40.9378
PORT STEPHENS Total |  | 6770 | 326.5398 | 48.2334
RANDWICK | NOT IN BUSHFIRE | 9076 | 253.2588 | 27.9042
RANDWICK Total |  | 9076 | 253.2588 | 27.9042
ROCKDALE | NOT IN BUSHFIRE | 7022 | 213.0592 | 30.3417
ROCKDALE Total |  | 7022 | 213.0592 | 30.3417
RYDE | BUSHFIRE | 500 | 16.7834 | 33.5668
| NOT IN BUSHFIRE | 7930 | 253.314 | 31.9438
RYDE Total |  | 8430 | 270.0974 | 32.04
SINGLETON | BUSHFIRE | 1050 | 77.9955 | 74.2815
| NOT IN BUSHFIRE | 1346 | 61.2153 | 45.4794
SINGLETON Total |  | 2396 | 139.2109 | 58.1014
STRATHFIELD | NOT IN BUSHFIRE | 2907 | 90.977 | 31.2958
STRATHFIELD Total |  | 2907 | 90.977 | 31.2958
SUTHERLAND | BUSHFIRE | 2369 | 77.7259 | 32.8096
| NOT IN BUSHFIRE | 14423 | 449.1012 | 31.1378
SUTHERLAND Total |  | 16792 | 526.8271 | 31.3737
SYDNEY | NOT IN BUSHFIRE | 3887 | 100.9821 | 25.9794
SYDNEY Total |  | 3887 | 100.9821 | 25.9794
THE HILLS SHIRE | BUSHFIRE | 6 | 0.23972 | 39.9535
| NOT IN BUSHFIRE | 29 | 0.79068 | 27.2647
THE HILLS SHIRE Total |  | 35 | 1.0304 | 29.4399
UPPER HUNTER | BUSHFIRE | 583 | 37.4136 | 64.1743
| NOT IN BUSHFIRE | 1045 | 42.2124 | 40.3946
UPPER HUNTER Total |  | 1628 | 79.626 | 48.9103
WARRINGAH | BUSHFIRE | 2059 | 81.2933 | 39.4819
| NOT IN BUSHFIRE | 8005 | 289.5642 | 36.1729
WARRINGAH Total |  | 10064 | 370.8574 | 36.8499
WAVERLEY | NOT IN BUSHFIRE | 2766 | 73.6368 | 26.6221
WAVERLEY Total |  | 2766 | 73.6368 | 26.6221
WILLOUGHBY | BUSHFIRE | 614 | 20.9068 | 34.0502
| NOT IN BUSHFIRE | 4670 | 145.2801 | 31.1092
WILLOUGHBY Total |  | 5284 | 166.1869 | 31.451
WOOLLAHRA | NOT IN BUSHFIRE | 2675 | 71.1948 | 26.6149
WOOLLAHRA Total |  | 2675 | 71.1948 | 26.6149
WYONG | BUSHFIRE | 4508 | 197.0546 | 43.7122
| NOT IN BUSHFIRE | 10255 | 349.809 | 34.1111
WYONG Total |  | 14763 | 546.8636 | 37.0428
Grand Total |  | 262758 | 9042.1332 | 34.4124

## Table 1
BARE_VS_COVERED | (All) |  |  | BARE_VS_COVERED | BARE
Sum of Sum of ASSET_LENGTH | BUSHFIRE_VS_NOT_BUSHFIRE_2022 |  |  | Sum of Count of ASSET_ID | BUSHFIRE_VS_NOT_BUSHFIRE_2022
LGA_NAME | BUSHFIRE | NOT IN BUSHFIRE | Grand Total | LGA_NAME | BUSHFIRE | NOT IN BUSHFIRE | Grand Total
ASHFIELD |  | 109.081 | 109.081 | ASHFIELD |  | 2993 | 2993
AUBURN |  | 191.07 | 191.07 | AUBURN |  | 5721 | 5721
BANKSTOWN | 19.6362 | 676.7988 | 696.435 | BANKSTOWN | 581 | 16548 | 17129
BOTANY BAY |  | 115.8382 | 115.8382 | BOTANY BAY |  | 2858 | 2858
BURWOOD |  | 89.0427 | 89.0427 | BURWOOD |  | 2433 | 2433
CANADA BAY |  | 199.9484 | 199.9484 | CANADA BAY |  | 5209 | 5209
CANTERBURY |  | 390.7589 | 390.7589 | CANTERBURY |  | 9765 | 9765
CESSNOCK | 140.5065 | 298.0468 | 438.5533 | CESSNOCK | 2558 | 3714 | 6272
DUNGOG | 0.17184 | 0.27829 | 0.45013 | DUNGOG | 2 | 2 | 4
GOSFORD | 287.907 | 600.3815 | 888.2885 | GOSFORD | 7006 | 8616 | 15622
HAWKESBURY | 0.015951 | 0.037349 | 0.0533 | HAWKESBURY | 1 |  | 1
HORNSBY | 162.88 | 409.7915 | 572.6715 | HORNSBY | 4766 | 8073 | 12839
HUNTERS HILL | 3.1299 | 46.4168 | 49.5466 | HUNTERS HILL | 95 | 1067 | 1162
HURSTVILLE | 8.7674 | 240.0808 | 248.8483 | HURSTVILLE | 280 | 6132 | 6412
KOGARAH | 2.207 | 166.9566 | 169.1636 | KOGARAH | 65 | 4302 | 4367
KU-RING-GAI | 110.6717 | 425.4345 | 536.1062 | KU-RING-GAI | 3144 | 8954 | 12098
LAKE MACQUARIE | 281.4184 | 691.7802 | 973.1986 | LAKE MACQUARIE | 6004 | 12356 | 18360
LANE COVE | 8.3145 | 99.8575 | 108.172 | LANE COVE | 246 | 2252 | 2498
LEICHHARDT |  | 140.1057 | 140.1057 | LEICHHARDT |  | 3795 | 3795
MAITLAND | 76.0666 | 247.1459 | 323.2125 | MAITLAND | 1175 | 3445 | 4620
MANLY | 11.3366 | 111.0657 | 122.4023 | MANLY | 327 | 2253 | 2580
MARRICKVILLE |  | 218.3869 | 218.3869 | MARRICKVILLE |  | 6421 | 6421
MID-WESTERN REGIONAL | 0.049675 |  | 0.049675 | MID-WESTERN REGIONAL | 1 |  | 1
MOSMAN | 7.9953 | 65.9576 | 73.9529 | MOSMAN | 239 | 1493 | 1732
MUSWELLBROOK | 24.3021 | 65.3296 | 89.6317 | MUSWELLBROOK | 432 | 625 | 1057
NEWCASTLE | 58.2363 | 644.3153 | 702.5516 | NEWCASTLE | 1432 | 12930 | 14362
NORTH SYDNEY | 1.7559 | 119.9691 | 121.725 | NORTH SYDNEY | 53 | 2684 | 2737
PARRAMATTA |  | 4.3507 | 4.3507 | PARRAMATTA |  | 90 | 90
PITTWATER | 45.7109 | 234.4378 | 280.1487 | PITTWATER | 1116 | 4009 | 5125
PORT STEPHENS | 197.3735 | 234.9323 | 432.3057 | PORT STEPHENS | 3577 | 3193 | 6770
RANDWICK |  | 332.372 | 332.372 | RANDWICK |  | 9076 | 9076
ROCKDALE |  | 276.7814 | 276.7814 | ROCKDALE |  | 7022 | 7022
RYDE | 17.0455 | 337.3988 | 354.4443 | RYDE | 500 | 7930 | 8430
SINGLETON | 78.3442 | 153.3805 | 231.7247 | SINGLETON | 1050 | 1346 | 2396
STRATHFIELD |  | 114.0499 | 114.0499 | STRATHFIELD |  | 2907 | 2907
SUTHERLAND | 79.4318 | 615.8396 | 695.2713 | SUTHERLAND | 2369 | 14423 | 16792
SYDNEY |  | 223.5353 | 223.5353 | SYDNEY |  | 3887 | 3887
THE HILLS SHIRE | 0.23972 | 2.2306 | 2.4703 | THE HILLS SHIRE | 6 | 29 | 35
UPPER HUNTER | 37.8427 | 92.6976 | 130.5403 | UPPER HUNTER | 583 | 1045 | 1628
WARRINGAH | 81.5661 | 429.3923 | 510.9584 | WARRINGAH | 2059 | 8005 | 10064
WAVERLEY |  | 100.0848 | 100.0848 | WAVERLEY |  | 2766 | 2766
WILLOUGHBY | 20.9391 | 206.3419 | 227.2809 | WILLOUGHBY | 614 | 4670 | 5284
WOOLLAHRA |  | 109.0885 | 109.0885 | WOOLLAHRA |  | 2675 | 2675
WYONG | 198.3011 | 584.1023 | 782.4034 | WYONG | 4508 | 10255 | 14763
Grand Total | 1962.1635 | 10414.8916 | 12377.0551 | Grand Total | 44789 | 217969 | 262758

## Table 2
MODEL_SHORT_NAME_REF | LGA_NAME | BARE_VS_COVERED | BUSHFIRE_VS_NOT_BUSHFIRE_2022 | Sum of ASSET_LENGTH | Count of ASSET_ID | LGA | Bushfire | Not Bushfire | Bushfire Zone (%) | Total length (km) | Region | SAIDI for climate MEDs (mins/yr) | Region | Sum of SAIDI for climate MEDs (mins/yr)
Overhead Mains - LV | ASHFIELD | BARE | NOT IN BUSHFIRE | 6.9148 | 224 | ASHFIELD |  | 109.081 | 0 | 109.081 | Mid |  | Coastal | 738.4261
Overhead Mains - LV | ASHFIELD | BARE | NOT IN BUSHFIRE | 83.2072 | 2769 | AUBURN |  | 191.07 | 0 | 191.07 | Mid | 2.9526 | Inland | 372.5782
Overhead Mains - LV | ASHFIELD | COVERED | NOT IN BUSHFIRE | 12.7965 | 626 | BANKSTOWN | 19.6362 | 676.7988 | 2.8195 | 696.435 | Inland |  | Mid | 625.4262
Overhead Mains - LV | ASHFIELD | COVERED | NOT IN BUSHFIRE | 0.036098 | 1 | BOTANY BAY |  | 115.8382 | 0 | 115.8382 | Coastal | 16.7964 | Grand Total | 1736.4305
Overhead Mains - LV | ASHFIELD | COVERED | NOT IN BUSHFIRE | 0.49728 | 28 | BURWOOD |  | 89.0427 | 0 | 89.0427 | Mid | 1.8949
Overhead Mains - LV | ASHFIELD | COVERED | NOT IN BUSHFIRE | 0.15761 | 5 | CANADA BAY |  | 199.9484 | 0 | 199.9484 | Mid | 0.41916
Overhead Mains - LV | ASHFIELD | COVERED | NOT IN BUSHFIRE | 5.4715 | 348 | CANTERBURY |  | 390.7589 | 0 | 390.7589 | Mid | 11.2734
Overhead Mains - LV | AUBURN | BARE | NOT IN BUSHFIRE | 23.9409 | 758 | CESSNOCK | 140.5065 | 298.0468 | 32.0386 | 438.5533 | Inland | 139.3241
Overhead Mains - LV | AUBURN | BARE | NOT IN BUSHFIRE | 144.1108 | 4963 | DUNGOG | 0.17184 | 0.27829 | 38.1764 | 0.45013 | Inland
Overhead Mains - LV | AUBURN | COVERED | NOT IN BUSHFIRE | 16.2258 | 705 | GOSFORD | 287.907 | 600.3815 | 32.4114 | 888.2885 | Mid | 194.5377
Overhead Mains - LV | AUBURN | COVERED | NOT IN BUSHFIRE | 0.24612 | 7 | HAWKESBURY | 0.015951 | 0.037349 | 29.9266 | 0.0533 | Inland
Overhead Mains - LV | AUBURN | COVERED | NOT IN BUSHFIRE | 0.66967 | 36 | HORNSBY | 162.88 | 409.7915 | 28.4421 | 572.6715 | Mid | 139.4604
Overhead Mains - LV | AUBURN | COVERED | NOT IN BUSHFIRE | 5.8767 | 287 | HUNTERS HILL | 3.1299 | 46.4168 | 6.317 | 49.5466 | Mid | 16.7964
Overhead Mains - LV | BANKSTOWN | BARE | BUSHFIRE | 7.0808 | 217 | HURSTVILLE | 8.7674 | 240.0808 | 3.5232 | 248.8483 | Mid
Overhead Mains - LV | BANKSTOWN | BARE | BUSHFIRE | 0.16334 | 4 | KOGARAH | 2.207 | 166.9566 | 1.3046 | 169.1636 | Coastal
Overhead Mains - LV | BANKSTOWN | BARE | NOT IN BUSHFIRE | 143.3639 | 4449 | KU-RING-GAI | 110.6717 | 425.4345 | 20.6436 | 536.1062 | Mid | 85.9204
Overhead Mains - LV | BANKSTOWN | BARE | BUSHFIRE | 0.040019 | 1 | LAKE MACQUARIE | 281.4184 | 691.7802 | 28.9168 | 973.1986 | Coastal | 194.5377
Overhead Mains - LV | BANKSTOWN | BARE | BUSHFIRE | 11.3436 | 342 | LANE COVE | 8.3145 | 99.8575 | 7.6864 | 108.172 | Mid | 7.2124
Overhead Mains - LV | BANKSTOWN | BARE | BUSHFIRE | 0.19775 | 4 | LEICHHARDT |  | 140.1057 | 0 | 140.1057 | Mid
Overhead Mains - LV | BANKSTOWN | BARE | NOT IN BUSHFIRE | 368.3679 | 12096 | MAITLAND | 76.0666 | 247.1459 | 23.5345 | 323.2125 | Inland | 146.4889
Overhead Mains - LV | BANKSTOWN | BARE | BUSHFIRE | 0.45471 | 13 | MANLY | 11.3366 | 111.0657 | 9.2617 | 122.4023 | Coastal | 59.611
Overhead Mains - LV | BANKSTOWN | COVERED | NOT IN BUSHFIRE | 126.5817 | 5670 | MARRICKVILLE |  | 218.3869 | 0 | 218.3869 | Mid | 2.3087
Overhead Mains - LV | BANKSTOWN | COVERED | NOT IN BUSHFIRE | 0.01675 | 1 | MID-WESTERN REGIONAL | 0.049675 |  | 100 | 0.049675 | inland
Overhead Mains - LV | BANKSTOWN | COVERED | BUSHFIRE | 0.35607 | 13 | MOSMAN | 7.9953 | 65.9576 | 10.8114 | 73.9529 | coastal | 0.41916
Overhead Mains - LV | BANKSTOWN | COVERED | NOT IN BUSHFIRE | 2.845 | 136 | MUSWELLBROOK | 24.3021 | 65.3296 | 27.1133 | 89.6317 | inland | 38.579
Overhead Mains - LV | BANKSTOWN | BARE | NOT IN BUSHFIRE | 0.09428 | 3 | NEWCASTLE | 58.2363 | 644.3153 | 8.2893 | 702.5516 | Coastal | 128.8456
Overhead Mains - LV | BANKSTOWN | COVERED | NOT IN BUSHFIRE | 35.5293 | 2112 | NORTH SYDNEY | 1.7559 | 119.9691 | 1.4425 | 121.725 | Coastal | 0.41916
Overhead Mains - LV | BOTANY BAY | BARE | NOT IN BUSHFIRE | 13.4542 | 431 | PARRAMATTA |  | 4.3507 | 0 | 4.3507 | Mid | 21.1476
Overhead Mains - LV | BOTANY BAY | BARE | NOT IN BUSHFIRE | 68.4599 | 2427 | PITTWATER | 45.7109 | 234.4378 | 16.3166 | 280.1487 | Coastal
Overhead Mains - LV | BOTANY BAY | COVERED | NOT IN BUSHFIRE | 32.4088 | 1477 | PORT STEPHENS | 197.3735 | 234.9323 | 45.656 | 432.3057 | Coastal | 336.5396
Overhead Mains - LV | BOTANY BAY | COVERED | NOT IN BUSHFIRE | 0.13796 | 9 | RANDWICK |  | 332.372 | 0 | 332.372 | Coastal | 0.41916
Overhead Mains - LV | BOTANY BAY | COVERED | NOT IN BUSHFIRE | 0.45749 | 23 | ROCKDALE |  | 276.7814 | 0 | 276.7814 | Coastal
Overhead Mains - LV | BOTANY BAY | COVERED | NOT IN BUSHFIRE | 0.91983 | 51 | RYDE | 17.0455 | 337.3988 | 4.8091 | 354.4443 | Mid | 17.0139
Overhead Mains - LV | BURWOOD | BARE | NOT IN BUSHFIRE | 12.797 | 412 | SINGLETON | 78.3442 | 153.3805 | 33.8092 | 231.7247 | Mid | 82.5908
Overhead Mains - LV | BURWOOD | BARE | NOT IN BUSHFIRE | 61.4331 | 2021 | STRATHFIELD |  | 114.0499 | 0 | 114.0499 | Mid | 7.2124
Overhead Mains - LV | BURWOOD | COVERED | NOT IN BUSHFIRE | 10.3212 | 481 | SUTHERLAND | 79.4318 | 615.8396 | 11.4246 | 695.2713 | Mid | 11.2734
Overhead Mains - LV | BURWOOD | COVERED | NOT IN BUSHFIRE | 0.33716 | 17 | SYDNEY |  | 223.5353 | 0 | 223.5353 | Coastal | 0.41916
Overhead Mains - LV | BURWOOD | COVERED | NOT IN BUSHFIRE | 4.1542 | 261 | THE HILLS SHIRE | 0.23972 | 2.2306 | 9.704 | 2.4703 | Inland
Overhead Mains - LV | CANADA BAY | BARE | NOT IN BUSHFIRE | 24.323 | 754 | UPPER HUNTER | 37.8427 | 92.6976 | 28.9893 | 130.5403 | Inland | 48.1862
Overhead Mains - LV | CANADA BAY | BARE | NOT IN BUSHFIRE | 141.1148 | 4455 | WARRINGAH | 81.5661 | 429.3923 | 15.9634 | 510.9584 | Mid
Overhead Mains - LV | CANADA BAY | COVERED | NOT IN BUSHFIRE | 23.069 | 999 | WAVERLEY |  | 100.0848 | 0 | 100.0848 | Coastal
Overhead Mains - LV | CANADA BAY | COVERED | NOT IN BUSHFIRE | 0.016865 | 1 | WILLOUGHBY | 20.9391 | 206.3419 | 9.2129 | 227.2809 | Mid | 23.4119
Overhead Mains - LV | CANADA BAY | COVERED | NOT IN BUSHFIRE | 0.94582 | 42 | WOOLLAHRA |  | 109.0885 | 0 | 109.0885 | Coastal | 0.41916
Overhead Mains - LV | CANADA BAY | COVERED | NOT IN BUSHFIRE | 10.4789 | 639 | WYONG | 198.3011 | 584.1023 | 25.3451 | 782.4034 | Coastal
Overhead Mains - LV | CANTERBURY | BARE | NOT IN BUSHFIRE | 43.2558 | 1387
Overhead Mains - LV | CANTERBURY | BARE | NOT IN BUSHFIRE | 263.8006 | 8378
Overhead Mains - LV | CANTERBURY | COVERED | NOT IN BUSHFIRE | 54.3722 | 2534
Overhead Mains - LV | CANTERBURY | COVERED | NOT IN BUSHFIRE | 0.02696 | 1
Overhead Mains - LV | CANTERBURY | COVERED | NOT IN BUSHFIRE | 1.3108 | 62
Overhead Mains - LV | CANTERBURY | COVERED | NOT IN BUSHFIRE | 27.9926 | 1696
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.85986 | 14
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.15556 | 2
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.33157 | 4
Overhead Mains - LV | CESSNOCK | BARE | NOT IN BUSHFIRE | 0.91444 | 14
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 2.5193 | 27
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.89608 | 10
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 10.687 | 144
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 43.6011 | 953
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.3944 | 11
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.24536 | 5
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 3.7691 | 72
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.28373 | 4
Overhead Mains - LV | CESSNOCK | BARE | NOT IN BUSHFIRE | 118.1194 | 2802
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 8.5875 | 134
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 2.7468 | 38
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.23005 | 3
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 30.8381 | 455
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 12.3783 | 303
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.2559 | 5
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.073963 | 2
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.74105 | 19
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.11544 | 2
Overhead Mains - LV | CESSNOCK | BARE | NOT IN BUSHFIRE | 32.1485 | 898
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 3.1039 | 57
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 1.0343 | 20
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 0.057869 | 1
Overhead Mains - LV | CESSNOCK | BARE | BUSHFIRE | 13.9437 | 273
Overhead Mains - LV | CESSNOCK | COVERED | NOT IN BUSHFIRE | 142.5466 | 4147
Overhead Mains - LV | CESSNOCK | COVERED | BUSHFIRE | 0.24314 | 4
Overhead Mains - LV | CESSNOCK | COVERED | BUSHFIRE | 0.99588 | 35
Overhead Mains - LV | CESSNOCK | COVERED | BUSHFIRE | 0.032144 | 1
Overhead Mains - LV | CESSNOCK | COVERED | NOT IN BUSHFIRE | 3.5261 | 136
Overhead Mains - LV | CESSNOCK | COVERED | BUSHFIRE | 0.07817 | 1
Overhead Mains - LV | CESSNOCK | COVERED | BUSHFIRE | 0.11208 | 2
Overhead Mains - LV | CESSNOCK | COVERED | BUSHFIRE | 1.1953 | 27
Overhead Mains - LV | CESSNOCK | COVERED | NOT IN BUSHFIRE | 0.79172 | 20
Overhead Mains - LV | DUNGOG | BARE | NOT IN BUSHFIRE | 0.080614 | 1
Overhead Mains - LV | DUNGOG | BARE | NOT IN BUSHFIRE | 0.099464 | 1
Overhead Mains - LV | DUNGOG | BARE | BUSHFIRE | 0.15564 | 2
Overhead Mains - LV | DUNGOG | COVERED | NOT IN BUSHFIRE | 0.098209 | 2
Overhead Mains - LV | DUNGOG | COVERED | BUSHFIRE | 0.016203 | 1
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 112.207 | 2973
Overhead Mains - LV | GOSFORD | BARE | NOT IN BUSHFIRE | 35.2773 | 1027
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 2.9168 | 55
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.075276 | 2
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.18614 | 3
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 5.3811 | 139
Overhead Mains - LV | GOSFORD | BARE | NOT IN BUSHFIRE | 136.3081 | 3958
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.12984 | 4
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.057501 | 1
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.06221 | 1
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 24.9268 | 607
Overhead Mains - LV | GOSFORD | BARE | NOT IN BUSHFIRE | 5.0151 | 111
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 15.101 | 294
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 1.5699 | 30
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.57773 | 8
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 3.4352 | 72
Overhead Mains - LV | GOSFORD | BARE | NOT IN BUSHFIRE | 1.9674 | 43
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 1.0243 | 21
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.08632 | 1
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.18605 | 3
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 63.7637 | 1665
Overhead Mains - LV | GOSFORD | BARE | NOT IN BUSHFIRE | 16.7911 | 510
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 3.1643 | 56
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.051451 | 3
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.58874 | 8
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 2.2157 | 61
Overhead Mains - LV | GOSFORD | BARE | NOT IN BUSHFIRE | 86.2732 | 2840
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.064247 | 1
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.045114 | 1
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 20.3482 | 450
Overhead Mains - LV | GOSFORD | BARE | NOT IN BUSHFIRE | 4.1726 | 100
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 18.9829 | 379
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.43446 | 11
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.37675 | 6
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 5.6169 | 110
Overhead Mains - LV | GOSFORD | BARE | NOT IN BUSHFIRE | 1.1699 | 27
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 1.813 | 35
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.16564 | 4
Overhead Mains - LV | GOSFORD | BARE | BUSHFIRE | 0.089651 | 2
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 294.6604 | 9348
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.048332 | 1
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 0.04904 | 2
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 0.030911 | 1
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.01773 | 1
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 0.042581 | 1
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.035267 | 1
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.019645 | 1
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 1.0338 | 47
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 0.30469 | 14
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.0185 | 1
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.020268 | 1
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 2.3393 | 123
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.021133 | 1
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.78042 | 24
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 0.022039 | 1
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.12977 | 6
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.040448 | 1
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.019929 | 1
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 0.059641 | 2
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.025657 | 1
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 0.015234 | 1
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 0.055366 | 3
Overhead Mains - LV | GOSFORD | COVERED | BUSHFIRE | 0.052024 | 2
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 15.7747 | 609
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 0.017679 | 1
Overhead Mains - LV | GOSFORD | COVERED | NOT IN BUSHFIRE | 0.03523 | 2
Overhead Mains - LV | HAWKESBURY | BARE | BUSHFIRE | 0.015951 | 1
Overhead Mains - LV | HAWKESBURY | COVERED | NOT IN BUSHFIRE | 0.037349 | 1
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 60.7006 | 1742
Overhead Mains - LV | HORNSBY | BARE | NOT IN BUSHFIRE | 3.2083 | 98
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 2.3255 | 51
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 0.28502 | 7
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 4.7451 | 134
Overhead Mains - LV | HORNSBY | BARE | NOT IN BUSHFIRE | 58.2596 | 1688
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 0.15679 | 4
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 0.09071 | 3
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 0.066785 | 2
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 0.045362 | 1
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 80.1237 | 2448
Overhead Mains - LV | HORNSBY | BARE | NOT IN BUSHFIRE | 6.3685 | 188
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 3.3883 | 92
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 1.0394 | 25
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 8.3852 | 230
Overhead Mains - LV | HORNSBY | BARE | NOT IN BUSHFIRE | 199.2937 | 6099
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 0.013386 | 1
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 0.081376 | 3
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 0.31541 | 7
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 0.44578 | 13
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 0.06328 | 2
Overhead Mains - LV | HORNSBY | BARE | BUSHFIRE | 0.020094 | 1
Overhead Mains - LV | HORNSBY | COVERED | NOT IN BUSHFIRE | 107.1134 | 3586
Overhead Mains - LV | HORNSBY | COVERED | NOT IN BUSHFIRE | 0.013905 | 1
Overhead Mains - LV | HORNSBY | COVERED | BUSHFIRE | 0.41464 | 17
Overhead Mains - LV | HORNSBY | COVERED | NOT IN BUSHFIRE | 0.14168 | 7
Overhead Mains - LV | HORNSBY | COVERED | BUSHFIRE | 0.071251 | 4
Overhead Mains - LV | HORNSBY | COVERED | NOT IN BUSHFIRE | 1.6158 | 78
Overhead Mains - LV | HORNSBY | COVERED | BUSHFIRE | 0.1023 | 4
Overhead Mains - LV | HORNSBY | COVERED | NOT IN BUSHFIRE | 0.027515 | 1
Overhead Mains - LV | HORNSBY | COVERED | NOT IN BUSHFIRE | 33.7337 | 1830
Overhead Mains - LV | HORNSBY | COVERED | NOT IN BUSHFIRE | 0.015433 | 1
Overhead Mains - LV | HUNTERS HILL | BARE | BUSHFIRE | 0.32924 | 11
Overhead Mains - LV | HUNTERS HILL | BARE | NOT IN BUSHFIRE | 1.8387 | 62
Overhead Mains - LV | HUNTERS HILL | BARE | BUSHFIRE | 2.7228 | 82
Overhead Mains - LV | HUNTERS HILL | BARE | NOT IN BUSHFIRE | 30.6256 | 1005
Overhead Mains - LV | HUNTERS HILL | BARE | BUSHFIRE | 0.077799 | 2
Overhead Mains - LV | HUNTERS HILL | COVERED | NOT IN BUSHFIRE | 10.2161 | 393
Overhead Mains - LV | HUNTERS HILL | COVERED | NOT IN BUSHFIRE | 0.069134 | 2
Overhead Mains - LV | HUNTERS HILL | COVERED | NOT IN BUSHFIRE | 3.6672 | 214
Overhead Mains - LV | HURSTVILLE | BARE | BUSHFIRE | 5.1111 | 162
Overhead Mains - LV | HURSTVILLE | BARE | BUSHFIRE | 0.24939 | 7
Overhead Mains - LV | HURSTVILLE | BARE | NOT IN BUSHFIRE | 67.7527 | 2069
Overhead Mains - LV | HURSTVILLE | BARE | BUSHFIRE | 2.8735 | 100
Overhead Mains - LV | HURSTVILLE | BARE | BUSHFIRE | 0.17877 | 10
Overhead Mains - LV | HURSTVILLE | BARE | NOT IN BUSHFIRE | 115.5315 | 4063
Overhead Mains - LV | HURSTVILLE | BARE | BUSHFIRE | 0.05565 | 1
Overhead Mains - LV | HURSTVILLE | COVERED | NOT IN BUSHFIRE | 45.465 | 1691
Overhead Mains - LV | HURSTVILLE | COVERED | BUSHFIRE | 0.013233 | 1
Overhead Mains - LV | HURSTVILLE | COVERED | NOT IN BUSHFIRE | 0.042033 | 2
Overhead Mains - LV | HURSTVILLE | COVERED | BUSHFIRE | 0.24783 | 9
Overhead Mains - LV | HURSTVILLE | COVERED | NOT IN BUSHFIRE | 4.9917 | 200
Overhead Mains - LV | HURSTVILLE | COVERED | BUSHFIRE | 0.038024 | 1
Overhead Mains - LV | HURSTVILLE | COVERED | NOT IN BUSHFIRE | 6.2978 | 324
Overhead Mains - LV | KOGARAH | BARE | BUSHFIRE | 0.52665 | 14
Overhead Mains - LV | KOGARAH | BARE | NOT IN BUSHFIRE | 51.435 | 1570
Overhead Mains - LV | KOGARAH | BARE | BUSHFIRE | 1.4569 | 47
Overhead Mains - LV | KOGARAH | BARE | NOT IN BUSHFIRE | 80.4964 | 2732
Overhead Mains - LV | KOGARAH | BARE | BUSHFIRE | 0.10006 | 4
Overhead Mains - LV | KOGARAH | COVERED | NOT IN BUSHFIRE | 27.6525 | 1006
Overhead Mains - LV | KOGARAH | COVERED | NOT IN BUSHFIRE | 0.030014 | 2
Overhead Mains - LV | KOGARAH | COVERED | BUSHFIRE | 0.065183 | 3
Overhead Mains - LV | KOGARAH | COVERED | NOT IN BUSHFIRE | 2.8884 | 109
Overhead Mains - LV | KOGARAH | COVERED | BUSHFIRE | 0.058172 | 2
Overhead Mains - LV | KOGARAH | COVERED | NOT IN BUSHFIRE | 4.4542 | 244
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 20.8124 | 598
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 0.19528 | 5
Overhead Mains - LV | KU-RING-GAI | BARE | NOT IN BUSHFIRE | 30.2433 | 878
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 0.05043 | 2
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 0.32212 | 7
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 0.10704 | 3
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 0.20907 | 5
Overhead Mains - LV | KU-RING-GAI | COVERED | NOT IN BUSHFIRE | 0.074648 | 6
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 85.0603 | 2440
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 0.55468 | 16
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 0.14392 | 4
Overhead Mains - LV | KU-RING-GAI | BARE | NOT IN BUSHFIRE | 275.5157 | 8076
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 0.41058 | 11
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 1.5019 | 34
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 0.54834 | 11
Overhead Mains - LV | KU-RING-GAI | BARE | BUSHFIRE | 0.29283 | 8
Overhead Mains - LV | KU-RING-GAI | COVERED | NOT IN BUSHFIRE | 82.3337 | 3176
Overhead Mains - LV | KU-RING-GAI | COVERED | NOT IN BUSHFIRE | 0.018527 | 1
Overhead Mains - LV | KU-RING-GAI | COVERED | BUSHFIRE | 0.30602 | 12
Overhead Mains - LV | KU-RING-GAI | COVERED | NOT IN BUSHFIRE | 0.8406 | 46
Overhead Mains - LV | KU-RING-GAI | COVERED | BUSHFIRE | 0.078398 | 2
Overhead Mains - LV | KU-RING-GAI | COVERED | BUSHFIRE | 0.078332 | 3
Overhead Mains - LV | KU-RING-GAI | COVERED | NOT IN BUSHFIRE | 36.408 | 2031
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.78222 | 12
Overhead Mains - LV | LAKE MACQUARIE | BARE | NOT IN BUSHFIRE | 0.13431 | 2
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.28793 | 4
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.081101 | 1
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 159.0166 | 3435
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.089952 | 1
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.10479 | 1
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.15703 | 2
Overhead Mains - LV | LAKE MACQUARIE | BARE | NOT IN BUSHFIRE | 290.9253 | 7022
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 1.3185 | 18
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 4.9188 | 81
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.65743 | 10
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.28421 | 5
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 2.5722 | 46
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.60007 | 7
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.3972 | 7
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 4.4761 | 61
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 83.7527 | 2004
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.16034 | 2
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.065431 | 1
Overhead Mains - LV | LAKE MACQUARIE | BARE | NOT IN BUSHFIRE | 192.7047 | 5332
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 1.0201 | 15
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 7.7658 | 128
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.42405 | 6
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.73148 | 8
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.23872 | 4
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 2.6636 | 50
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.33672 | 5
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 0.60377 | 10
Overhead Mains - LV | LAKE MACQUARIE | BARE | BUSHFIRE | 5.1325 | 80
Overhead Mains - LV | LAKE MACQUARIE | COVERED | NOT IN BUSHFIRE | 204.1322 | 6339
Overhead Mains - LV | LAKE MACQUARIE | COVERED | BUSHFIRE | 0.04489 | 1
Overhead Mains - LV | LAKE MACQUARIE | COVERED | BUSHFIRE | 2.4083 | 60
Overhead Mains - LV | LAKE MACQUARIE | COVERED | NOT IN BUSHFIRE | 2.5929 | 75
Overhead Mains - LV | LAKE MACQUARIE | COVERED | BUSHFIRE | 0.049206 | 1
Overhead Mains - LV | LAKE MACQUARIE | COVERED | BUSHFIRE | 0.021539 | 1
Overhead Mains - LV | LAKE MACQUARIE | COVERED | BUSHFIRE | 0.22324 | 3
Overhead Mains - LV | LAKE MACQUARIE | COVERED | BUSHFIRE | 0.031623 | 1
Overhead Mains - LV | LAKE MACQUARIE | COVERED | NOT IN BUSHFIRE | 1.2908 | 35
Overhead Mains - LV | LANE COVE | BARE | BUSHFIRE | 1.8382 | 54
Overhead Mains - LV | LANE COVE | BARE | NOT IN BUSHFIRE | 11.0807 | 338
Overhead Mains - LV | LANE COVE | BARE | BUSHFIRE | 5.9669 | 182
Overhead Mains - LV | LANE COVE | BARE | BUSHFIRE | 0.19054 | 5
Overhead Mains - LV | LANE COVE | BARE | NOT IN BUSHFIRE | 61.2909 | 1914
Overhead Mains - LV | LANE COVE | BARE | BUSHFIRE | 0.022921 | 2
Overhead Mains - LV | LANE COVE | BARE | BUSHFIRE | 0.080661 | 3
Overhead Mains - LV | LANE COVE | COVERED | NOT IN BUSHFIRE | 17.2897 | 659
Overhead Mains - LV | LANE COVE | COVERED | BUSHFIRE | 0.21529 | 6
Overhead Mains - LV | LANE COVE | COVERED | NOT IN BUSHFIRE | 0.7778 | 31
Overhead Mains - LV | LANE COVE | COVERED | NOT IN BUSHFIRE | 9.4183 | 539
Overhead Mains - LV | LEICHHARDT | BARE | NOT IN BUSHFIRE | 16.3727 | 569
Overhead Mains - LV | LEICHHARDT | BARE | NOT IN BUSHFIRE | 88.92 | 3226
Overhead Mains - LV | LEICHHARDT | COVERED | NOT IN BUSHFIRE | 27.0557 | 1409
Overhead Mains - LV | LEICHHARDT | COVERED | NOT IN BUSHFIRE | 0.073188 | 3
Overhead Mains - LV | LEICHHARDT | COVERED | NOT IN BUSHFIRE | 1.5496 | 60
Overhead Mains - LV | LEICHHARDT | COVERED | NOT IN BUSHFIRE | 6.1345 | 364
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.050373 | 1
Overhead Mains - LV | MAITLAND | BARE | NOT IN BUSHFIRE | 0.023341 | 1
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 1.0715 | 14
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.56781 | 6
Overhead Mains - LV | MAITLAND | BARE | NOT IN BUSHFIRE | 1.0663 | 18
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 3.621 | 44
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.13215 | 2
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.058013 | 1
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 2.2117 | 39
Overhead Mains - LV | MAITLAND | BARE | NOT IN BUSHFIRE | 2.2484 | 40
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.18353 | 2
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.2363 | 3
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 3.1722 | 48
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 6.3516 | 118
Overhead Mains - LV | MAITLAND | BARE | NOT IN BUSHFIRE | 93.07 | 2165
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 25.9515 | 368
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.12489 | 2
Overhead Mains - LV | MAITLAND | BARE | NOT IN BUSHFIRE | 0.50936 | 9
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.41605 | 7
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.082326 | 1
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.10577 | 1
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.45609 | 12
Overhead Mains - LV | MAITLAND | BARE | NOT IN BUSHFIRE | 0.33611 | 10
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.036188 | 1
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 1.2022 | 20
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 3.034 | 72
Overhead Mains - LV | MAITLAND | BARE | NOT IN BUSHFIRE | 41.9942 | 1202
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.046852 | 2
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 25.6475 | 402
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.037984 | 1
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.047714 | 3
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.030741 | 1
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.17006 | 3
Overhead Mains - LV | MAITLAND | BARE | BUSHFIRE | 0.0479 | 1
Overhead Mains - LV | MAITLAND | COVERED | NOT IN BUSHFIRE | 99.9122 | 2620
Overhead Mains - LV | MAITLAND | COVERED | NOT IN BUSHFIRE | 0.017626 | 1
Overhead Mains - LV | MAITLAND | COVERED | BUSHFIRE | 0.24759 | 6
Overhead Mains - LV | MAITLAND | COVERED | BUSHFIRE | 0.31525 | 13
Overhead Mains - LV | MAITLAND | COVERED | NOT IN BUSHFIRE | 6.3191 | 284
Overhead Mains - LV | MAITLAND | COVERED | BUSHFIRE | 0.40979 | 18
Overhead Mains - LV | MAITLAND | COVERED | NOT IN BUSHFIRE | 0.13266 | 5
Overhead Mains - LV | MAITLAND | COVERED | NOT IN BUSHFIRE | 1.5167 | 43
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 2.3243 | 68
Overhead Mains - LV | MANLY | BARE | NOT IN BUSHFIRE | 0.28532 | 7
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.043351 | 3
Overhead Mains - LV | MANLY | BARE | NOT IN BUSHFIRE | 18.5378 | 550
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.041416 | 1
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.028358 | 1
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 5.9362 | 170
Overhead Mains - LV | MANLY | BARE | NOT IN BUSHFIRE | 0.74215 | 22
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.11949 | 4
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.088265 | 3
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.2424 | 8
Overhead Mains - LV | MANLY | BARE | NOT IN BUSHFIRE | 50.0284 | 1531
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.2948 | 7
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.13806 | 3
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.067423 | 2
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.31488 | 10
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.038405 | 1
Overhead Mains - LV | MANLY | COVERED | NOT IN BUSHFIRE | 25.2332 | 999
Overhead Mains - LV | MANLY | COVERED | NOT IN BUSHFIRE | 0.079163 | 3
Overhead Mains - LV | MANLY | COVERED | NOT IN BUSHFIRE | 0.4558 | 22
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 1.38 | 39
Overhead Mains - LV | MANLY | BARE | NOT IN BUSHFIRE | 0.18388 | 6
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.040615 | 1
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.081729 | 2
Overhead Mains - LV | MANLY | BARE | NOT IN BUSHFIRE | 4.6612 | 137
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.044071 | 1
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.077081 | 2
Overhead Mains - LV | MANLY | BARE | BUSHFIRE | 0.03574 | 1
Overhead Mains - LV | MANLY | COVERED | NOT IN BUSHFIRE | 10.8588 | 620
Overhead Mains - LV | MARRICKVILLE | BARE | NOT IN BUSHFIRE | 19.3052 | 699
Overhead Mains - LV | MARRICKVILLE | BARE | NOT IN BUSHFIRE | 151.0573 | 5722
Overhead Mains - LV | MARRICKVILLE | COVERED | NOT IN BUSHFIRE | 41.8132 | 2111
Overhead Mains - LV | MARRICKVILLE | COVERED | NOT IN BUSHFIRE | 0.085652 | 4
Overhead Mains - LV | MARRICKVILLE | COVERED | NOT IN BUSHFIRE | 2.6226 | 116
Overhead Mains - LV | MARRICKVILLE | COVERED | NOT IN BUSHFIRE | 0.013012 | 1
Overhead Mains - LV | MARRICKVILLE | COVERED | NOT IN BUSHFIRE | 3.4899 | 167
Overhead Mains - LV | MID-WESTERN REGIONAL | BARE | BUSHFIRE | 0.049675 | 1
Overhead Mains - LV | MOSMAN | BARE | BUSHFIRE | 0.33804 | 10
Overhead Mains - LV | MOSMAN | BARE | NOT IN BUSHFIRE | 6.12 | 194
Overhead Mains - LV | MOSMAN | BARE | BUSHFIRE | 6.8491 | 207
Overhead Mains - LV | MOSMAN | BARE | BUSHFIRE | 0.28764 | 8
Overhead Mains - LV | MOSMAN | BARE | NOT IN BUSHFIRE | 39.9677 | 1299
Overhead Mains - LV | MOSMAN | BARE | BUSHFIRE | 0.012428 | 1
Overhead Mains - LV | MOSMAN | BARE | BUSHFIRE | 0.41086 | 13
Overhead Mains - LV | MOSMAN | COVERED | NOT IN BUSHFIRE | 11.9582 | 439
Overhead Mains - LV | MOSMAN | COVERED | NOT IN BUSHFIRE | 0.012967 | 1
Overhead Mains - LV | MOSMAN | COVERED | BUSHFIRE | 0.016942 | 1
Overhead Mains - LV | MOSMAN | COVERED | NOT IN BUSHFIRE | 0.13209 | 9
Overhead Mains - LV | MOSMAN | COVERED | BUSHFIRE | 0.080305 | 4
Overhead Mains - LV | MOSMAN | COVERED | NOT IN BUSHFIRE | 7.7666 | 480
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 0.50402 | 6
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 0.13302 | 2
Overhead Mains - LV | MUSWELLBROOK | BARE | NOT IN BUSHFIRE | 0.43586 | 13
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 2.5525 | 34
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 0.10366 | 1
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 0.31049 | 5
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 0.10683 | 2
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 1.2044 | 17
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 1.2532 | 26
Overhead Mains - LV | MUSWELLBROOK | BARE | NOT IN BUSHFIRE | 11.654 | 270
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 5.5773 | 94
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 0.29964 | 5
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 1.0453 | 16
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 0.11005 | 2
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 0.07554 | 1
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 0.79378 | 22
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 2.1956 | 62
Overhead Mains - LV | MUSWELLBROOK | BARE | NOT IN BUSHFIRE | 10.2178 | 342
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 6.3665 | 114
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 0.13433 | 3
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 0.80379 | 16
Overhead Mains - LV | MUSWELLBROOK | BARE | BUSHFIRE | 0.18869 | 4
Overhead Mains - LV | MUSWELLBROOK | COVERED | NOT IN BUSHFIRE | 41.1096 | 1048
Overhead Mains - LV | MUSWELLBROOK | COVERED | BUSHFIRE | 0.036837 | 1
Overhead Mains - LV | MUSWELLBROOK | COVERED | BUSHFIRE | 0.078636 | 1
Overhead Mains - LV | MUSWELLBROOK | COVERED | BUSHFIRE | 0.0308 | 1
Overhead Mains - LV | MUSWELLBROOK | COVERED | NOT IN BUSHFIRE | 1.5583 | 44
Overhead Mains - LV | MUSWELLBROOK | COVERED | BUSHFIRE | 0.3816 | 9
Overhead Mains - LV | MUSWELLBROOK | COVERED | BUSHFIRE | 0.015632 | 1
Overhead Mains - LV | MUSWELLBROOK | COVERED | NOT IN BUSHFIRE | 0.10034 | 3
Overhead Mains - LV | MUSWELLBROOK | COVERED | NOT IN BUSHFIRE | 0.25362 | 7
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 28.884 | 702
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 0.39469 | 8
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 0.14862 | 2
Overhead Mains - LV | NEWCASTLE | BARE | NOT IN BUSHFIRE | 239.9157 | 6286
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 0.05274 | 2
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 0.09625 | 1
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 0.58419 | 9
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 25.1893 | 672
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 0.42472 | 12
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 0.11784 | 4
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 0.30037 | 3
Overhead Mains - LV | NEWCASTLE | BARE | NOT IN BUSHFIRE | 230.7256 | 6644
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 0.016285 | 1
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 0.46192 | 8
Overhead Mains - LV | NEWCASTLE | BARE | BUSHFIRE | 0.62838 | 8
Overhead Mains - LV | NEWCASTLE | COVERED | NOT IN BUSHFIRE | 165.2497 | 5921
Overhead Mains - LV | NEWCASTLE | COVERED | NOT IN BUSHFIRE | 0.4326 | 12
Overhead Mains - LV | NEWCASTLE | COVERED | BUSHFIRE | 0.59966 | 18
Overhead Mains - LV | NEWCASTLE | COVERED | BUSHFIRE | 0.052697 | 1
Overhead Mains - LV | NEWCASTLE | COVERED | NOT IN BUSHFIRE | 3.8225 | 122
Overhead Mains - LV | NEWCASTLE | COVERED | BUSHFIRE | 0.23247 | 5
Overhead Mains - LV | NEWCASTLE | COVERED | BUSHFIRE | 0.052167 | 1
Overhead Mains - LV | NEWCASTLE | COVERED | NOT IN BUSHFIRE | 0.33167 | 11
Overhead Mains - LV | NEWCASTLE | COVERED | NOT IN BUSHFIRE | 3.8377 | 92
Overhead Mains - LV | NORTH SYDNEY | BARE | BUSHFIRE | 0.37047 | 11
Overhead Mains - LV | NORTH SYDNEY | BARE | NOT IN BUSHFIRE | 11.687 | 388
Overhead Mains - LV | NORTH SYDNEY | BARE | BUSHFIRE | 0.69359 | 25
Overhead Mains - LV | NORTH SYDNEY | BARE | NOT IN BUSHFIRE | 66.619 | 2296
Overhead Mains - LV | NORTH SYDNEY | BARE | BUSHFIRE | 0.40806 | 8
Overhead Mains - LV | NORTH SYDNEY | BARE | BUSHFIRE | 0.28382 | 9
Overhead Mains - LV | NORTH SYDNEY | COVERED | NOT IN BUSHFIRE | 30.6123 | 1171
Overhead Mains - LV | NORTH SYDNEY | COVERED | NOT IN BUSHFIRE | 0.018732 | 1
Overhead Mains - LV | NORTH SYDNEY | COVERED | NOT IN BUSHFIRE | 0.81509 | 38
Overhead Mains - LV | NORTH SYDNEY | COVERED | NOT IN BUSHFIRE | 10.2169 | 572
Overhead Mains - LV | PARRAMATTA | BARE | NOT IN BUSHFIRE | 0.20939 | 8
Overhead Mains - LV | PARRAMATTA | BARE | NOT IN BUSHFIRE | 2.8119 | 82
Overhead Mains - LV | PARRAMATTA | COVERED | NOT IN BUSHFIRE | 1.0584 | 42
Overhead Mains - LV | PARRAMATTA | COVERED | NOT IN BUSHFIRE | 0.0527 | 3
Overhead Mains - LV | PARRAMATTA | COVERED | NOT IN BUSHFIRE | 0.2184 | 14
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 21.8831 | 500
Overhead Mains - LV | PITTWATER | BARE | NOT IN BUSHFIRE | 2.8028 | 72
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 0.16922 | 3
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 0.13559 | 4
Overhead Mains - LV | PITTWATER | BARE | NOT IN BUSHFIRE | 65.3553 | 1666
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 0.34613 | 8
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 0.27215 | 6
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 15.6412 | 413
Overhead Mains - LV | PITTWATER | BARE | NOT IN BUSHFIRE | 2.0978 | 64
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 0.36922 | 6
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 0.089196 | 3
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 0.1529 | 3
Overhead Mains - LV | PITTWATER | BARE | NOT IN BUSHFIRE | 50.8512 | 1477
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 0.093585 | 1
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 1.796 | 51
Overhead Mains - LV | PITTWATER | COVERED | NOT IN BUSHFIRE | 64.4086 | 1945
Overhead Mains - LV | PITTWATER | COVERED | NOT IN BUSHFIRE | 0.060007 | 2
Overhead Mains - LV | PITTWATER | COVERED | BUSHFIRE | 0.29625 | 9
Overhead Mains - LV | PITTWATER | COVERED | NOT IN BUSHFIRE | 0.45684 | 16
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 4.2922 | 113
Overhead Mains - LV | PITTWATER | BARE | NOT IN BUSHFIRE | 1.3806 | 35
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 0.035879 | 1
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 0.068419 | 2
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 0.03574 | 1
Overhead Mains - LV | PITTWATER | BARE | NOT IN BUSHFIRE | 27.4375 | 695
Overhead Mains - LV | PITTWATER | BARE | BUSHFIRE | 0.034053 | 1
Overhead Mains - LV | PITTWATER | COVERED | NOT IN BUSHFIRE | 19.5872 | 986
Overhead Mains - LV | PORT STEPHENS | BARE | NOT IN BUSHFIRE | 0.040352 | 1
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.098876 | 2
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 2.0725 | 35
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.032077 | 1
Overhead Mains - LV | PORT STEPHENS | BARE | NOT IN BUSHFIRE | 0.04469 | 1
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.96301 | 14
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.10084 | 1
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.29433 | 3
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 38.2871 | 848
Overhead Mains - LV | PORT STEPHENS | BARE | NOT IN BUSHFIRE | 26.8248 | 588
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 6.9986 | 111
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.91654 | 16
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 55.7361 | 883
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 3.328 | 71
Overhead Mains - LV | PORT STEPHENS | BARE | NOT IN BUSHFIRE | 60.8211 | 1430
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.31793 | 5
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.45119 | 9
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 37.5377 | 611
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 2.1327 | 38
Overhead Mains - LV | PORT STEPHENS | BARE | NOT IN BUSHFIRE | 0.33788 | 10
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 3.6467 | 55
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.070725 | 1
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 3.9795 | 66
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.015114 | 1
Overhead Mains - LV | PORT STEPHENS | BARE | NOT IN BUSHFIRE | 0.063181 | 2
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.11406 | 2
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 7.9915 | 208
Overhead Mains - LV | PORT STEPHENS | BARE | NOT IN BUSHFIRE | 9.0592 | 241
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.97729 | 15
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.17409 | 4
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 11.9669 | 224
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 1.8338 | 43
Overhead Mains - LV | PORT STEPHENS | BARE | NOT IN BUSHFIRE | 33.3067 | 914
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 13.899 | 270
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.3921 | 9
Overhead Mains - LV | PORT STEPHENS | BARE | NOT IN BUSHFIRE | 0.18636 | 5
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.55094 | 15
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.33142 | 7
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.49445 | 7
Overhead Mains - LV | PORT STEPHENS | BARE | BUSHFIRE | 0.12034 | 2
Overhead Mains - LV | PORT STEPHENS | BARE | NOT IN BUSHFIRE | 0.030075 | 1
Overhead Mains - LV | PORT STEPHENS | COVERED | NOT IN BUSHFIRE | 101.6327 | 2515
Overhead Mains - LV | PORT STEPHENS | COVERED | BUSHFIRE | 0.34263 | 10
Overhead Mains - LV | PORT STEPHENS | COVERED | NOT IN BUSHFIRE | 0.23599 | 6
Overhead Mains - LV | PORT STEPHENS | COVERED | BUSHFIRE | 0.74335 | 20
Overhead Mains - LV | PORT STEPHENS | COVERED | BUSHFIRE | 0.067936 | 2
Overhead Mains - LV | PORT STEPHENS | COVERED | NOT IN BUSHFIRE | 0.4635 | 16
Overhead Mains - LV | PORT STEPHENS | COVERED | BUSHFIRE | 0.36643 | 11
Overhead Mains - LV | PORT STEPHENS | COVERED | BUSHFIRE | 0.027589 | 1
Overhead Mains - LV | PORT STEPHENS | COVERED | NOT IN BUSHFIRE | 0.079127 | 2
Overhead Mains - LV | PORT STEPHENS | COVERED | NOT IN BUSHFIRE | 0.030009 | 1
Overhead Mains - LV | PORT STEPHENS | COVERED | NOT IN BUSHFIRE | 1.7766 | 51
Overhead Mains - LV | RANDWICK | BARE | NOT IN BUSHFIRE | 28.4717 | 955
Overhead Mains - LV | RANDWICK | BARE | NOT IN BUSHFIRE | 224.7872 | 8121
Overhead Mains - LV | RANDWICK | COVERED | NOT IN BUSHFIRE | 73.5655 | 3196
Overhead Mains - LV | RANDWICK | COVERED | NOT IN BUSHFIRE | 0.30462 | 16
Overhead Mains - LV | RANDWICK | COVERED | NOT IN BUSHFIRE | 2.559 | 112
Overhead Mains - LV | RANDWICK | COVERED | NOT IN BUSHFIRE | 2.684 | 123
Overhead Mains - LV | ROCKDALE | BARE | NOT IN BUSHFIRE | 69.5953 | 2173
Overhead Mains - LV | ROCKDALE | BARE | NOT IN BUSHFIRE | 143.4639 | 4849
Overhead Mains - LV | ROCKDALE | COVERED | NOT IN BUSHFIRE | 50.3591 | 1949
Overhead Mains - LV | ROCKDALE | COVERED | NOT IN BUSHFIRE | 0.050182 | 2
Overhead Mains - LV | ROCKDALE | COVERED | NOT IN BUSHFIRE | 8.0471 | 279
Overhead Mains - LV | ROCKDALE | COVERED | NOT IN BUSHFIRE | 5.2659 | 267
Overhead Mains - LV | RYDE | BARE | BUSHFIRE | 3.1342 | 94
Overhead Mains - LV | RYDE | BARE | BUSHFIRE | 0.081449 | 2
Overhead Mains - LV | RYDE | BARE | NOT IN BUSHFIRE | 27.5009 | 849
Overhead Mains - LV | RYDE | BARE | BUSHFIRE | 0.58698 | 15
Overhead Mains - LV | RYDE | BARE | BUSHFIRE | 0.059033 | 1
Overhead Mains - LV | RYDE | BARE | BUSHFIRE | 10.7854 | 331
Overhead Mains - LV | RYDE | BARE | BUSHFIRE | 0.023879 | 1
Overhead Mains - LV | RYDE | BARE | BUSHFIRE | 0.10507 | 3
Overhead Mains - LV | RYDE | BARE | NOT IN BUSHFIRE | 225.8131 | 7081
Overhead Mains - LV | RYDE | BARE | BUSHFIRE | 0.01942 | 1
Overhead Mains - LV | RYDE | BARE | BUSHFIRE | 1.7974 | 49
Overhead Mains - LV | RYDE | BARE | BUSHFIRE | 0.19062 | 3
Overhead Mains - LV | RYDE | COVERED | NOT IN BUSHFIRE | 55.9514 | 2087
Overhead Mains - LV | RYDE | COVERED | BUSHFIRE | 0.17708 | 11
Overhead Mains - LV | RYDE | COVERED | NOT IN BUSHFIRE | 0.56365 | 29
Overhead Mains - LV | RYDE | COVERED | BUSHFIRE | 0.053753 | 2
Overhead Mains - LV | RYDE | COVERED | BUSHFIRE | 0.03127 | 1
Overhead Mains - LV | RYDE | COVERED | NOT IN BUSHFIRE | 27.5697 | 1595
Overhead Mains - LV | SINGLETON | BARE | NOT IN BUSHFIRE | 1.1755 | 18
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 2.1113 | 22
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 3.9561 | 44
Overhead Mains - LV | SINGLETON | BARE | NOT IN BUSHFIRE | 7.7776 | 116
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 14.4052 | 162
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 6.6226 | 73
Overhead Mains - LV | SINGLETON | BARE | NOT IN BUSHFIRE | 0.065456 | 1
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 0.63012 | 6
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 1.7993 | 18
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 1.0363 | 13
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 1.8515 | 19
Overhead Mains - LV | SINGLETON | BARE | NOT IN BUSHFIRE | 1.7677 | 28
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 2.1703 | 26
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 0.62243 | 9
Overhead Mains - LV | SINGLETON | BARE | NOT IN BUSHFIRE | 24.4482 | 529
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 11.001 | 141
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 4.0427 | 59
Overhead Mains - LV | SINGLETON | BARE | NOT IN BUSHFIRE | 0.10358 | 1
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 0.61046 | 8
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 0.47719 | 7
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 0.34542 | 4
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 0.12807 | 2
Overhead Mains - LV | SINGLETON | BARE | NOT IN BUSHFIRE | 0.97778 | 20
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 2.8926 | 54
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 1.3575 | 19
Overhead Mains - LV | SINGLETON | BARE | NOT IN BUSHFIRE | 24.282 | 627
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 17.5009 | 287
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 2.3718 | 41
Overhead Mains - LV | SINGLETON | BARE | NOT IN BUSHFIRE | 0.092178 | 2
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 0.52364 | 12
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 0.6138 | 10
Overhead Mains - LV | SINGLETON | BARE | NOT IN BUSHFIRE | 0.52534 | 4
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 0.51631 | 7
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 0.32981 | 5
Overhead Mains - LV | SINGLETON | BARE | BUSHFIRE | 0.079264 | 2
Overhead Mains - LV | SINGLETON | COVERED | NOT IN BUSHFIRE | 91.2526 | 1969
Overhead Mains - LV | SINGLETON | COVERED | BUSHFIRE | 0.03344 | 1
Overhead Mains - LV | SINGLETON | COVERED | NOT IN BUSHFIRE | 0.041691 | 1
Overhead Mains - LV | SINGLETON | COVERED | BUSHFIRE | 0.088574 | 2
Overhead Mains - LV | SINGLETON | COVERED | NOT IN BUSHFIRE | 0.51168 | 20
Overhead Mains - LV | SINGLETON | COVERED | BUSHFIRE | 0.14387 | 5
Overhead Mains - LV | SINGLETON | COVERED | BUSHFIRE | 0.082773 | 2
Overhead Mains - LV | SINGLETON | COVERED | NOT IN BUSHFIRE | 0.074614 | 2
Overhead Mains - LV | SINGLETON | COVERED | NOT IN BUSHFIRE | 0.28457 | 10
Overhead Mains - LV | STRATHFIELD | BARE | NOT IN BUSHFIRE | 13.561 | 430
Overhead Mains - LV | STRATHFIELD | BARE | NOT IN BUSHFIRE | 77.416 | 2477
Overhead Mains - LV | STRATHFIELD | COVERED | NOT IN BUSHFIRE | 17.239 | 726
Overhead Mains - LV | STRATHFIELD | COVERED | NOT IN BUSHFIRE | 0.94083 | 35
Overhead Mains - LV | STRATHFIELD | COVERED | NOT IN BUSHFIRE | 4.8931 | 291
Overhead Mains - LV | SUTHERLAND | BARE | BUSHFIRE | 39.2228 | 1205
Overhead Mains - LV | SUTHERLAND | BARE | BUSHFIRE | 0.024861 | 1
Overhead Mains - LV | SUTHERLAND | BARE | BUSHFIRE | 0.79992 | 23
Overhead Mains - LV | SUTHERLAND | BARE | NOT IN BUSHFIRE | 129.2522 | 3956
Overhead Mains - LV | SUTHERLAND | BARE | BUSHFIRE | 1.7378 | 33
Overhead Mains - LV | SUTHERLAND | BARE | BUSHFIRE | 32.7491 | 1031
Overhead Mains - LV | SUTHERLAND | BARE | NOT IN BUSHFIRE | 0.26359 | 7
Overhead Mains - LV | SUTHERLAND | BARE | BUSHFIRE | 0.14979 | 3
Overhead Mains - LV | SUTHERLAND | BARE | BUSHFIRE | 0.91467 | 32
Overhead Mains - LV | SUTHERLAND | BARE | NOT IN BUSHFIRE | 319.5398 | 10459
Overhead Mains - LV | SUTHERLAND | BARE | BUSHFIRE | 2.0703 | 39
Overhead Mains - LV | SUTHERLAND | BARE | NOT IN BUSHFIRE | 0.045629 | 1
Overhead Mains - LV | SUTHERLAND | BARE | BUSHFIRE | 0.05665 | 2
Overhead Mains - LV | SUTHERLAND | COVERED | NOT IN BUSHFIRE | 132.0572 | 4868
Overhead Mains - LV | SUTHERLAND | COVERED | BUSHFIRE | 0.17189 | 2
Overhead Mains - LV | SUTHERLAND | COVERED | NOT IN BUSHFIRE | 0.03449 | 1
Overhead Mains - LV | SUTHERLAND | COVERED | BUSHFIRE | 1.471 | 44
Overhead Mains - LV | SUTHERLAND | COVERED | NOT IN BUSHFIRE | 0.045705 | 2
Overhead Mains - LV | SUTHERLAND | COVERED | BUSHFIRE | 0.039849 | 1
Overhead Mains - LV | SUTHERLAND | COVERED | BUSHFIRE | 0.023177 | 1
Overhead Mains - LV | SUTHERLAND | COVERED | NOT IN BUSHFIRE | 5.536 | 194
Overhead Mains - LV | SUTHERLAND | COVERED | NOT IN BUSHFIRE | 29.065 | 1484
Overhead Mains - LV | SYDNEY | BARE | NOT IN BUSHFIRE | 13.3618 | 496
Overhead Mains - LV | SYDNEY | BARE | NOT IN BUSHFIRE | 87.6203 | 3391
Overhead Mains - LV | SYDNEY | COVERED | NOT IN BUSHFIRE | 111.8995 | 5513
Overhead Mains - LV | SYDNEY | COVERED | NOT IN BUSHFIRE | 0.070703 | 4
Overhead Mains - LV | SYDNEY | COVERED | NOT IN BUSHFIRE | 7.1002 | 371
Overhead Mains - LV | SYDNEY | COVERED | NOT IN BUSHFIRE | 0.012439 | 1
Overhead Mains - LV | SYDNEY | COVERED | NOT IN BUSHFIRE | 3.4703 | 170
Overhead Mains - LV | THE HILLS SHIRE | BARE | BUSHFIRE | 0.15304 | 4
Overhead Mains - LV | THE HILLS SHIRE | BARE | NOT IN BUSHFIRE | 0.62152 | 21
Overhead Mains - LV | THE HILLS SHIRE | BARE | BUSHFIRE | 0.067711 | 1
Overhead Mains - LV | THE HILLS SHIRE | BARE | BUSHFIRE | 0.018973 | 1
Overhead Mains - LV | THE HILLS SHIRE | BARE | NOT IN BUSHFIRE | 0.16916 | 8
Overhead Mains - LV | THE HILLS SHIRE | COVERED | NOT IN BUSHFIRE | 0.39414 | 18
Overhead Mains - LV | THE HILLS SHIRE | COVERED | NOT IN BUSHFIRE | 0.15751 | 6
Overhead Mains - LV | THE HILLS SHIRE | COVERED | NOT IN BUSHFIRE | 0.88827 | 43
Overhead Mains - LV | UPPER HUNTER | BARE | BUSHFIRE | 0.15767 | 2
Overhead Mains - LV | UPPER HUNTER | BARE | NOT IN BUSHFIRE | 3.6749 | 67
Overhead Mains - LV | UPPER HUNTER | BARE | BUSHFIRE | 0.15422 | 1
Overhead Mains - LV | UPPER HUNTER | BARE | BUSHFIRE | 10.2783 | 128
Overhead Mains - LV | UPPER HUNTER | BARE | BUSHFIRE | 2.3748 | 44
Overhead Mains - LV | UPPER HUNTER | BARE | NOT IN BUSHFIRE | 23.7189 | 533
Overhead Mains - LV | UPPER HUNTER | BARE | BUSHFIRE | 0.0692 | 1
Overhead Mains - LV | UPPER HUNTER | BARE | BUSHFIRE | 0.17733 | 3
Overhead Mains - LV | UPPER HUNTER | BARE | BUSHFIRE | 11.44 | 179
Overhead Mains - LV | UPPER HUNTER | BARE | BUSHFIRE | 0.72881 | 14
Overhead Mains - LV | UPPER HUNTER | BARE | NOT IN BUSHFIRE | 14.8186 | 445
Overhead Mains - LV | UPPER HUNTER | BARE | BUSHFIRE | 0.12453 | 3
Overhead Mains - LV | UPPER HUNTER | BARE | BUSHFIRE | 11.9088 | 208
Overhead Mains - LV | UPPER HUNTER | COVERED | NOT IN BUSHFIRE | 48.2289 | 1219
Overhead Mains - LV | UPPER HUNTER | COVERED | NOT IN BUSHFIRE | 2.1953 | 73
Overhead Mains - LV | UPPER HUNTER | COVERED | BUSHFIRE | 0.42908 | 7
Overhead Mains - LV | UPPER HUNTER | COVERED | NOT IN BUSHFIRE | 0.061094 | 2
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 43.8662 | 1098
Overhead Mains - LV | WARRINGAH | BARE | NOT IN BUSHFIRE | 0.037235 | 1
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 0.076007 | 2
Overhead Mains - LV | WARRINGAH | BARE | NOT IN BUSHFIRE | 116.559 | 3110
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 0.093694 | 2
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 1.8801 | 35
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 0.16869 | 4
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 0.51136 | 11
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 25.9983 | 695
Overhead Mains - LV | WARRINGAH | BARE | NOT IN BUSHFIRE | 0.057217 | 2
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 0.10681 | 2
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 0.065715 | 2
Overhead Mains - LV | WARRINGAH | BARE | NOT IN BUSHFIRE | 124.0437 | 3590
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 1.3609 | 34
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 0.061889 | 2
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 0.41549 | 6
Overhead Mains - LV | WARRINGAH | COVERED | NOT IN BUSHFIRE | 109.8755 | 3697
Overhead Mains - LV | WARRINGAH | COVERED | BUSHFIRE | 0.2728 | 14
Overhead Mains - LV | WARRINGAH | COVERED | NOT IN BUSHFIRE | 1.0149 | 37
Overhead Mains - LV | WARRINGAH | COVERED | NOT IN BUSHFIRE | 0.019045 | 1
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 6.5619 | 163
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 0.053103 | 1
Overhead Mains - LV | WARRINGAH | BARE | NOT IN BUSHFIRE | 48.8671 | 1302
Overhead Mains - LV | WARRINGAH | BARE | BUSHFIRE | 0.07316 | 2
Overhead Mains - LV | WARRINGAH | COVERED | NOT IN BUSHFIRE | 28.9188 | 1546
Overhead Mains - LV | WAVERLEY | BARE | NOT IN BUSHFIRE | 6.8652 | 248
Overhead Mains - LV | WAVERLEY | BARE | NOT IN BUSHFIRE | 66.7717 | 2518
Overhead Mains - LV | WAVERLEY | COVERED | NOT IN BUSHFIRE | 24.3584 | 1153
Overhead Mains - LV | WAVERLEY | COVERED | NOT IN BUSHFIRE | 0.54377 | 34
Overhead Mains - LV | WAVERLEY | COVERED | NOT IN BUSHFIRE | 0.80539 | 47
Overhead Mains - LV | WAVERLEY | COVERED | NOT IN BUSHFIRE | 0.74043 | 46
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 2.5499 | 77
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 0.033722 | 1
Overhead Mains - LV | WILLOUGHBY | BARE | NOT IN BUSHFIRE | 17.8097 | 574
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 0.097609 | 2
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 0.061581 | 2
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 0.087888 | 2
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 0.10147 | 3
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 17.2257 | 507
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 0.080989 | 2
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 0.20293 | 7
Overhead Mains - LV | WILLOUGHBY | BARE | NOT IN BUSHFIRE | 127.4703 | 4096
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 0.11951 | 4
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 0.025133 | 1
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 0.072433 | 2
Overhead Mains - LV | WILLOUGHBY | BARE | BUSHFIRE | 0.24785 | 4
Overhead Mains - LV | WILLOUGHBY | COVERED | NOT IN BUSHFIRE | 42.7987 | 1687
Overhead Mains - LV | WILLOUGHBY | COVERED | NOT IN BUSHFIRE | 0.23302 | 7
Overhead Mains - LV | WILLOUGHBY | COVERED | BUSHFIRE | 0.032254 | 2
Overhead Mains - LV | WILLOUGHBY | COVERED | NOT IN BUSHFIRE | 1.3826 | 66
Overhead Mains - LV | WILLOUGHBY | COVERED | NOT IN BUSHFIRE | 16.6475 | 999
Overhead Mains - LV | WOOLLAHRA | BARE | NOT IN BUSHFIRE | 5.2614 | 191
Overhead Mains - LV | WOOLLAHRA | BARE | NOT IN BUSHFIRE | 65.9334 | 2484
Overhead Mains - LV | WOOLLAHRA | COVERED | NOT IN BUSHFIRE | 34.4085 | 1568
Overhead Mains - LV | WOOLLAHRA | COVERED | NOT IN BUSHFIRE | 0.096994 | 10
Overhead Mains - LV | WOOLLAHRA | COVERED | NOT IN BUSHFIRE | 2.018 | 102
Overhead Mains - LV | WOOLLAHRA | COVERED | NOT IN BUSHFIRE | 1.3701 | 76
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 76.1034 | 1861
Overhead Mains - LV | WYONG | BARE | NOT IN BUSHFIRE | 12.034 | 318
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 3.9216 | 66
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.8817 | 16
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.96359 | 14
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 13.6078 | 366
Overhead Mains - LV | WYONG | BARE | NOT IN BUSHFIRE | 160.6229 | 4502
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.075595 | 1
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.079563 | 2
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 1.4262 | 26
Overhead Mains - LV | WYONG | BARE | NOT IN BUSHFIRE | 0.072524 | 1
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 1.7613 | 33
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 2.4815 | 46
Overhead Mains - LV | WYONG | BARE | NOT IN BUSHFIRE | 0.20497 | 4
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.74269 | 14
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.2085 | 4
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.26541 | 5
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 66.4722 | 1488
Overhead Mains - LV | WYONG | BARE | NOT IN BUSHFIRE | 8.76 | 232
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 7.2191 | 145
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.80698 | 16
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.51554 | 10
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 8.645 | 205
Overhead Mains - LV | WYONG | BARE | NOT IN BUSHFIRE | 167.3373 | 5182
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.23865 | 3
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.10063 | 2
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 1.5158 | 30
Overhead Mains - LV | WYONG | BARE | NOT IN BUSHFIRE | 0.20337 | 3
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 2.0542 | 42
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.14863 | 3
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 4.1123 | 69
Overhead Mains - LV | WYONG | BARE | NOT IN BUSHFIRE | 0.57401 | 13
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 1.0992 | 18
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 1.5847 | 22
Overhead Mains - LV | WYONG | BARE | BUSHFIRE | 0.022684 | 1
Overhead Mains - LV | WYONG | COVERED | NOT IN BUSHFIRE | 219.4103 | 7129
Overhead Mains - LV | WYONG | COVERED | BUSHFIRE | 0.19553 | 6
Overhead Mains - LV | WYONG | COVERED | NOT IN BUSHFIRE | 0.088182 | 3
Overhead Mains - LV | WYONG | COVERED | BUSHFIRE | 0.027341 | 1
Overhead Mains - LV | WYONG | COVERED | NOT IN BUSHFIRE | 0.63423 | 34
Overhead Mains - LV | WYONG | COVERED | BUSHFIRE | 0.041843 | 1
Overhead Mains - LV | WYONG | COVERED | BUSHFIRE | 0.37191 | 14
Overhead Mains - LV | WYONG | COVERED | NOT IN BUSHFIRE | 0.17124 | 7
Overhead Mains - LV | WYONG | COVERED | BUSHFIRE | 0.11329 | 3
Overhead Mains - LV | WYONG | COVERED | BUSHFIRE | 0.19566 | 6
Overhead Mains - LV | WYONG | COVERED | NOT IN BUSHFIRE | 1.8541 | 74
Overhead Mains - LV | WYONG | COVERED | BUSHFIRE | 0.053355 | 2
Overhead Mains - LV | WYONG | COVERED | BUSHFIRE | 0.10032 | 2
Overhead Mains - LV | WYONG | COVERED | BUSHFIRE | 0.14723 | 4
Overhead Mains - LV | WYONG | COVERED | NOT IN BUSHFIRE | 10.0629 | 392
Overhead Mains - LV | WYONG | COVERED | NOT IN BUSHFIRE | 2.0725 | 105