## R24 Targets
Transmission service component caps, floors and targets - UPDATED
Parameters | Distribution | Target | Floor | Cap | Weighting
Average circuit outage rate (%)
Transmission line - fault | Pearson5 | 15.9531 | 20.99 | 11.64 | 0.2%
Tranformer - fault | Weibull | 6.2019 | 10.67 | 2.25 | 0.2%
Reactive plant - fault | Uniform | 13.8462 | 27.4 | 1.44 | 0.1%
Transmission line - forced | Pearson5 | 17.8399 | 28.26 | 10.65 | 0.1%
Transformer - forced | Pearson5 | 6.5376 | 14.58 | 2.53 | 0.1%
Reactive plant - forced | Triang | 20 | 29.99 | 6.88 | 0.05%
Loss of supply events
LOS > 0.10 system minutes | Poisson | 4.2 | 8 | 1 | 0.15%
LOS > 1.00 system minutes | Geomet | 0.8 | 3 | 0 | 0.15%
Average outage duration (minutes)
Average outage duration | LogLogistic | 129.5018 | 551.5 | 15.85 | 0.2%
Proper operation of equipment
Failure of protection system | Poisson | 4 | 8 | 1 | 0%
Material failure of SCADA | Geomet | 1 | 4 | 0 | 0%
Incorrect operational isolation | Poisson | 2.4 | 5 | 0 | 0%
Transmission MIC parameter values - UPDATED
Calendar year | Performance count
Target | 1967.8
Cap for unplanned outages | 334.526
Dollar per dispatch interval | 842.8917
Note:
Kolmogorov-Smirnov Goodness-of-Fit Test

## Fault COR
Lines outage rate - Fault
Calendar year | Event rate (%)
2017 | 9.3897
2018 | 15.8879
2019 | 21.6981
2020 | 13.2075
2021 | 13.0841
2022 | 15.8879
Distribution | Target | Floor | Cap
Pearson5 | 15.9531 | 20.99 | 11.64
Transformers outage rate - Fault
Calendar year | Event rate (%)
2017 | 8.2569
2018 | 10
2019 | 8.2569
2020 | 5.5046
2021 | 4.5455
2022 | 2.7027
Distribution | Target | Floor | Cap
Weibull | 6.2019 | 10.67 | 2.25
Reactive plant outage rate - Fault
Calendar year | Event rate (%)
2017 | 33.3333
2018 | 23.0769
2019 | 0
2020 | 23.0769
2021 | 7.6923
2022 | 15.3846
Distribution | Target | Floor | Cap
Uniform | 13.8462 | 27.4 | 1.44

## Forced COR
Lines outage rate - Forced
Calendar year | Event rate (%)
2017 | 7.5117
2018 | 12.1495
2019 | 30.1887
2020 | 14.1509
2021 | 15.8879
2022 | 16.8224
Distribution | Target | Floor | Cap
Pearson5 | 17.8399 | 28.26 | 10.65
Transformers outage rate - Forced
Calendar year | Event rate (%)
2017 | 13.7615
2018 | 7.2727
2019 | 4.5872
2020 | 4.5872
2021 | 2.7273
2022 | 13.5135
Distribution | Target | Floor | Cap
Pearson5 | 6.5376 | 14.58 | 2.53
Reactive plant outage rate - Forced
Calendar year | Event rate (%)
2017 | 8.3333
2018 | 15.3846
2019 | 15.3846
2020 | 15.3846
2021 | 23.0769
2022 | 30.7692
Distribution | Target | Floor | Cap
Triang | 20 | 29.99 | 6.88

## LOS
LOS > 0.1 sys mins
Calendar year | No. of events
2017 | 4
2018 | 2
2019 | 2
2020 | 8
2021 | 2
2022 | 7
Distribution | Target | Floor | Cap
Poisson | 4.2 | 8 | 1
LOS > 1 sys mins
Calendar year | No. of events
2017 | 1
2018 | 0
2019 | 1
2020 | 0
2021 | 0
2022 | 3
Distribution | Target | Floor | Cap
Geomet | 0.8 | 3 | 0

## AOD
AOD
Calendar year | Duration (mins)
2017 | 410.4545
2018 | 45.9091
2019 | 273
2020 | 105
2021 | 19
2022 | 204.6
Distribution | Target | Floor | Cap
LogLogistic | 129.5018 | 551.5 | 15.85

## POE
Failure of protection system
Calendar year | No. of events
2017 | 4
2018 | 1
2019 | 2
2020 | 4
2021 | 5
2022 | 8
Distribution | Target | Floor | Cap
Poisson | 4 | 8 | 1
Material failure of SCADA
Calendar year | No. of events
2017 | 4
2018 | 4
2019 | 0
2020 | 0
2021 | 1
2022 | 0
Distribution | Target | Floor | Cap
Geomet | 1 | 4 | 0
Incorrect operational isolation
Calendar year | No. of events
2017 | 3
2018 | 6
2019 | 1
2020 | 1
2021 | 2
2022 | 2
Distribution | Target | Floor | Cap
Poisson | 2.4 | 5 | 0

## MIC
MIC
Calendar year | Unplanned | Planned | Total (Planned + Unplanned) | Capped Unplanned count | Adjusted performance count (Planned + Capped Unplanned) | Comments
2015 | 87 | 160 | 247 | 87 | 247
2016 | 597 | 2267 | 2864 | 343 | 2610 | 113 WA-BW planned events - Exclusion '9' applied
2017 | 271 | 2431 | 2702 | 271 | 2702
2018 | 224 | 3905 | 4129 | 224 | 4129 | 131 WA-BW planned events - Exclusion '9' applied
2019 | 59 | 1696 | 1755 | 59 | 1755
2020 | 26 | 1368 | 1394 | 26 | 1394
2021 | 151 | 1227 | 1378 | 151 | 1378
2022 | 27 | 1017 | 1044 | 27 | 1044
Min |  |  | 1044
Max |  |  | 4129
Average of 5 median |  | M | 2018.6 | T | 1967.8
Unplanned outage event limit (0.17*T) | 334.526
Nominal Smoothed MAR (2024/25) ($) | 165864232.3632
Dollars per Dispatch Interval ($/DI) | 842.8917
Target | 1967.8