## Insight
Raised Date
· Identifies the date of the incident.
EECL Work Order
· Prefix OT/OS identifies P0 failure.
Asset category
· Identified voltage level and type of failed equipment.
Equip No.
· Identifies equipment number of failed asset.
Comp Code Description
· Identifies discipline.
Object
· Identifies the object that failed.
Cause
· Identifies the cause of the failure.
Damage
· Identifies the damage sustained to the asset.
Insight
Majority of the unassisted failures are related to conductor itself. Bare Steel conductor has the highest number of unassisted failures. The failures have not been normalised with popuplation.

## Ergon Conductor Failures
Raised Date | WORK_ORDER | Asset Category | EQUIP_NO | COMP_CODE_DESCRIPTION | MSSS_OBJECT_DESCRIPTION | MSSS_DAMAGE_DESCRIPTION | MSSS_CAUSE_DESCRIPTION
2023-12-25 | OT212731 | > 11 kV & < = 22 kV ; SWER | 000000949507 | Conductor/Conductive | PG Clamp | Loose Connection | Vibration
2024-05-13 | OT235865 | > 1 kV & < = 11 kV | 000001595158 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2024-05-29 | OT237320 | > 1 kV & < = 11 kV | 000001616303 | Conductor/Conductive | Bare Steel Conductor | Unravelled | Corrosion
2024-01-11 | OT217626 | > 11 kV & < = 22 kV ; SWER | 000001784929 | Conductor/Conductive | Bare Steel Conductor | Deteriorated | Corrosion
2024-02-16 | OT225798 | > 1 kV & < = 11 kV | 000001407927 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2024-04-30 | OT234662 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000911665 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2024-03-24 | OT230635 | > 11 kV & < = 22 kV ; SWER | 000001776569 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Vibration
2024-04-27 | OT234451 | > 11 kV & < = 22 kV ; SWER | 000001912906 | Conductor/Conductive | Connection, Unknown | Loose Connection | Vibration
2024-02-23 | OT226772 | > 1 kV & < = 11 kV | 000001101664 | Conductor/Conductive | Split Bolt Clamp | Burnt Off | Fatigue
2024-03-28 | OT231264 | < = 1 kV | 000001224563 | Conductor/Conductive | PG Clamp | Loose Connection | Corrosion
2024-03-21 | OT230437 | > 1 kV & < = 11 kV | 000001340523 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2024-02-23 | OT226777 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000971262 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Age
2024-05-03 | OT235052 | > 1 kV & < = 11 kV | 000001319732 | Conductor/Conductive | Bare Al. Conductor | Unravelled | Age
2024-04-21 | OT233844 | < = 1 kV | 000000754322 | Conductor/Conductive | Connection, Unknown | Burnt Off | Fatigue
2024-03-12 | OT229317 | < = 1 kV | 000001147122 | Conductor/Conductive | LV ABC | Broken | Age
2024-05-02 | OT234954 | > 1 kV & < = 11 kV | 000001765219 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Age
2024-02-17 | OT225941 | > 11 kV & < = 22 kV ; SWER | 000001938448 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Vibration
2024-01-15 | OT218233 | < = 1 kV | 000001469871 | Conductor/Conductive | PG Clamp | Loose Connection | Vibration
2024-01-17 | OT218740 | > 1 kV & < = 11 kV | 000001443080 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Incorrect Installation
2024-02-14 | OT225503 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001125724 | Conductor/Conductive | Bare Al. Alloy Conductor | Broken | Corrosion
2024-05-19 | OT236398 | > 1 kV & < = 11 kV | 000001322164 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2024-01-27 | OT221592 | < = 1 kV | 000001513966 | Conductor/Conductive | PG Clamp | Burnt Off | Current Overload
2024-01-24 | OT220313 | > 1 kV & < = 11 kV | 000001690797 | Conductor/Conductive | PG Clamp | Burnt Off | Fatigue
2024-04-27 | OT234405 | > 11 kV & < = 22 kV ; SWER | 000001803956 | Conductor/Conductive | Bare Steel Conductor | Broken | Age
2024-02-20 | OT226317 | > 11 kV & < = 22 kV ; SWER | 000001610550 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2024-01-21 | OT219438 | > 11 kV & < = 22 kV ; SWER | 000000998375 | Conductor/Conductive | Connection, Unknown | Broken | Fatigue
2024-01-19 | OT219104 | < = 1 kV | 000001863451 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Incorrect Installation
2024-01-22 | OT219841 | > 1 kV & < = 11 kV | 000001337972 | Conductor/Conductive | PG Clamp | Burnt Off | Current Overload
2024-04-25 | OT234266 | < = 1 kV | 000001097778 | Conductor/Conductive | LV ABC | Burnt Off | Corrosion
2023-10-27 | OT200803 | > 1 kV & < = 11 kV | 000001413740 | Conductor/Conductive | PG Clamp | Burnt Off | Corrosion
2024-06-08 | OT238344 | > 1 kV & < = 11 kV | 000001402633 | Conductor/Conductive | Bare ACSR Conductor | Broken | Age
2024-01-23 | OT219992 | > 1 kV & < = 11 kV | 000001032259 | Conductor/Conductive | Bare ACSR Conductor | Burnt Off | Corrosion
2023-10-08 | OT198270 | < = 1 kV | 000001319982 | Conductor/Conductive | Connection, Unknown | Burnt Off | Corrosion
2024-06-08 | OT238280 | > 1 kV & < = 11 kV | 000000968623 | Conductor/Conductive | Bare Cu Conductor | Broken | Corrosion
2024-06-18 | OT239280 | > 1 kV & < = 11 kV | 000001436248 | Conductor/Conductive | Connection, Unknown | Broken | Vibration
2023-10-09 | OT198367 | > 11 kV & < = 22 kV ; SWER | 000001667517 | Conductor/Conductive | Bare Steel Conductor | Broken | Age
2024-06-25 | OT239993 | < = 1 kV | 000001048368 | Conductor/Conductive | LV ABC | Burnt Off | Incorrect Installation
2023-10-31 | OT201340 | > 11 kV & < = 22 kV ; SWER | 000001178238 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Vibration
2024-06-21 | OT239668 | < = 1 kV | 000001485670 | Conductor/Conductive | LV ABC | Burnt Off | Incorrect Installation
2023-11-01 | OT201518 | > 11 kV & < = 22 kV ; SWER | 000001088385 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2023-11-20 | OT204468 | < = 1 kV | 000000726912 | Conductor/Conductive | LV ABC | Broken | Age
2023-08-29 | OT193710 | > 11 kV & < = 22 kV ; SWER | 000001053508 | Conductor/Conductive | Bare ACSR Conductor | Broken | Vibration
2024-06-24 | OT239917 | > 11 kV & < = 22 kV ; SWER | 000000745511 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2024-03-27 | OT231098 | < = 1 kV | 000001018594 | Conductor/Conductive | Bare Al. Alloy Conductor | Broken | Corrosion
2024-03-18 | OT230010 | < = 1 kV | 000009201699 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Incorrect Installation
2024-04-18 | OT233561 | < = 1 kV | 000001793826 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Age
2024-05-08 | OT235488 | < = 1 kV | 000007999697 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Corrosion
2024-03-11 | OT229120 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001117531 | Conductor/Conductive | Live Line Clamp | High Resistivity | Corrosion
2024-04-21 | OT233829 | > 11 kV & < = 22 kV ; Single-Phase | 000001288447 | Conductor/Conductive | Bare ACSR Conductor | Burnt Off | Age
2023-07-03 | OT187973 | > 11 kV & < = 22 kV ; SWER | 000001158600 | Conductor/Conductive | Attachment Tie, Hand | Burnt Off | Corrosion
2023-08-13 | OT192196 | > 11 kV & < = 22 kV ; SWER | 000001465412 | Conductor/Conductive | Bare Steel Conductor | Broken | Age
2023-12-24 | OT212000 | > 11 kV & < = 22 kV ; SWER | 000001946712 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Vibration
2024-04-24 | OT234211 | < = 1 kV | 000001850329 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2024-01-28 | OT221916 | < = 1 kV | 000001573317 | Conductor/Conductive | LV ABC | Broken | Age
2024-01-11 | OT217818 | > 1 kV & < = 11 kV | 000001444140 | Conductor/Conductive | Bare Cu Conductor | Deteriorated | Corrosion
2024-01-24 | OT220305 | < = 1 kV | 000001459333 | Conductor/Conductive | Connection, Unknown | Burnt Off | Corrosion
2024-01-29 | OT222534 | < = 1 kV | 000001459333 | Conductor/Conductive | Connection, Unknown | Loose Connection | Incorrect Installation
2024-02-24 | OT226869 | < = 1 kV | 000001435401 | Conductor/Conductive | LV ABC | Burnt Off | Incorrect Installation
2024-03-13 | OT229337 | < = 1 kV | 000001451617 | Conductor/Conductive | Split Bolt Clamp | Loose Connection | Fatigue
2024-01-23 | OT219878 | > 11 kV & < = 22 kV ; SWER | 000000943838 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2024-02-28 | OT227384 | > 1 kV & < = 11 kV | 000001847539 | Conductor/Conductive | Attachment Tie, Preformed | Broken | Fatigue
2024-04-15 | OT233284 | > 1 kV & < = 11 kV | 000001462333 | Conductor/Conductive | Bare Steel Conductor | Broken | Hazard on Line
2024-05-09 | OT235607 | > 1 kV & < = 11 kV | 000000804097 | Conductor/Conductive | HV Cable | Broken | Corrosion
2024-05-15 | OT236132 | > 11 kV & < = 22 kV ; SWER | 000007876480 | Conductor/Conductive | Live Line Clamp | Broken | Vibration
2024-01-09 | OT217305 | > 22 kV & < = 66 kV | 000001948855 | Conductor/Conductive | Bare ACSR Conductor | Burnt Off | Vibration
2024-02-29 | OT227438 | > 1 kV & < = 11 kV | 000001516181 | Conductor/Conductive | Bare ACSR Conductor | Broken | Age
2024-03-24 | OT230705 | > 1 kV & < = 11 kV | 000001523692 | Conductor/Conductive | Bare Steel Conductor | Broken | Age
2024-01-17 | OT218714 | > 1 kV & < = 11 kV | 000001600183 | Conductor/Conductive | Bare Al. Alloy Conductor | Broken | Vibration
2024-02-08 | OT224694 | > 1 kV & < = 11 kV | 000001719459 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2024-02-24 | OT226876 | > 1 kV & < = 11 kV | 000001603236 | Conductor/Conductive | Bare ACSR Conductor | Broken | Corrosion
2024-03-13 | OT229326 | > 1 kV & < = 11 kV | 000001791775 | Conductor/Conductive | McIntyre Sleeve | Broken | Corrosion
2024-05-28 | OT237314 | > 1 kV & < = 11 kV | 000001446150 | Conductor/Conductive | PG Clamp | High Resistivity | Corrosion
2023-09-05 | OT194495 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000728939 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Age
2023-12-22 | OT211597 | > 1 kV & < = 11 kV | 000001343255 | Conductor/Conductive | Live Line Clamp | Broken | Vibration
2023-10-19 | OT199680 | > 1 kV & < = 11 kV | 000001422242 | Conductor/Conductive | Bare Steel Conductor | Broken | Incorrect Installation
2023-12-12 | OT208734 | < = 1 kV | 000001706853 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Age
2023-09-29 | OT197231 | > 1 kV & < = 11 kV | 000005267761 | Conductor/Conductive | Bare Cu Conductor | Broken | Vibration
2023-10-10 | OT198560 | < = 1 kV | 000007026373 | Conductor/Conductive | LV ABC | Burnt Off | Age
2023-10-18 | OT199450 | > 1 kV & < = 11 kV | 000001439414 | Conductor/Conductive | Live Line Clamp | Broken | Fatigue
2023-10-25 | OT200406 | > 1 kV & < = 11 kV | 000007538240 | Conductor/Conductive | Bare Steel Conductor | Lack of Ground Clearance | Corrosion
2023-09-13 | OT195462 | > 1 kV & < = 11 kV | 000001459121 | Conductor/Conductive | Connection, Unknown | Broken | Fatigue
2023-09-12 | OT195408 | > 11 kV & < = 22 kV ; SWER | 000001952264 | Conductor/Conductive | Bare ACSR Conductor | Broken | Vibration
2024-06-04 | OT237935 | < = 1 kV | 000001108380 | Conductor/Conductive | LV ABC | Burnt Off | Age
2023-10-07 | OT198193 | > 1 kV & < = 11 kV | 000001642544 | Conductor/Conductive | Bare ACSR Conductor | Broken | Incorrect Installation
2023-12-02 | OT206701 | < = 1 kV | 000001214121 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2023-11-13 | OT203328 | < = 1 kV | 000001394061 | Conductor/Conductive | LV ABC | Broken | Age
2024-03-22 | OT230447 | > 22 kV & < = 66 kV | 000001841796 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Age
2024-06-10 | OT238474 | < = 1 kV | 000001236677 | Conductor/Conductive | LV ABC | Burnt Off | Age
2023-09-15 | OT195777 | > 1 kV & < = 11 kV | 000001386157 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2024-03-11 | OT229191 | > 1 kV & < = 11 kV | 000001101665 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Age
2024-03-14 | OT229464 | > 1 kV & < = 11 kV | 000000967106 | Conductor/Conductive | Bare Al. Conductor | Broken | Incorrect Installation
2024-04-04 | OT231991 | > 1 kV & < = 11 kV | 000001373108 | Conductor/Conductive | PG Clamp | High Resistivity | Corrosion
2024-05-10 | OT235670 | > 1 kV & < = 11 kV | 000001378056 | Conductor/Conductive | Bare Steel Conductor | Broken | Age
2023-09-21 | OT196373 | > 1 kV & < = 11 kV | 000000722572 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2023-07-04 | OT188076 | < = 1 kV | 000001427928 | Conductor/Conductive | LV ABC | Short Circuit | Age
2023-08-21 | OT192892 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000909266 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2023-07-03 | OT188065 | Other | 000001736227 | Conductor/Conductive | Bare Al. Alloy Conductor | Broken | Corrosion
2023-07-10 | OT188721 | > 1 kV & < = 11 kV | 000001812917 | Conductor/Conductive | Bare Steel Conductor | Broken | Age
2023-08-07 | OT191494 | > 1 kV & < = 11 kV | 000001821272 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Age
2023-08-30 | OT193851 | > 1 kV & < = 11 kV | 000000931451 | Conductor/Conductive | Bare Cu Conductor | Broken | Corrosion
2024-06-04 | OT237945 | > 1 kV & < = 11 kV | 000001042147 | Conductor/Conductive | Bare Steel Conductor | Broken | Vibration
2024-04-08 | OT232382 | > 1 kV & < = 11 kV | 000001502129 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Age
2024-01-22 | OT219843 | < = 1 kV | 000001577749 | Conductor/Conductive | Connection, Unknown | Broken | Corrosion
2024-02-25 | OT226944 | < = 1 kV | 000001673989 | Conductor/Conductive | LV ABC | Burnt Off | Age
2024-01-16 | OT218547 | > 1 kV & < = 11 kV | 000001701304 | Conductor/Conductive | Attachment Tie, Hand | Broken | Vibration
2024-02-20 | OT226261 | > 11 kV & < = 22 kV ; SWER | 000001692233 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2024-01-28 | OT222050 | > 1 kV & < = 11 kV | 000008781624 | Conductor/Conductive | Connection, Unknown | Broken | Corrosion
2024-01-26 | OT221188 | < = 1 kV | 000001671303 | Conductor/Conductive | LV ABC | Insulation Deteriorated | Age
2024-02-02 | OT223784 | > 1 kV & < = 11 kV | 000001624911 | Conductor/Conductive | Connection, Unknown | Burnt Off | Fatigue
2024-03-25 | OT230817 | < = 1 kV | 000001060382 | Conductor/Conductive | LV ABC | Burnt Off | Corrosion
2023-07-16 | OT189372 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000901431 | Conductor/Conductive | Bare Al. Alloy Conductor | Burnt Off | Age
2023-11-16 | OT203923 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001366918 | Conductor/Conductive | Bare Al. Alloy Conductor | Burnt Off | Corrosion
2024-01-22 | OT219710 | > 11 kV & < = 22 kV ; SWER | 000001038522 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2023-08-22 | OT193106 | > 11 kV & < = 22 kV ; SWER | 000000892349 | Conductor/Conductive | PG Clamp | Loose Connection | Vibration
2024-03-28 | OT231267 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000897472 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Age
2024-03-28 | OT231291 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000897498 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Age
2023-07-04 | OT188184 | < = 1 kV | 000001579008 | Conductor/Conductive | Connection, Unknown | Loose Connection | Incorrect Installation
2023-09-04 | OT194458 | < = 1 kV | 000001720706 | Conductor/Conductive | LV ABC | Burnt Off | Age
2023-09-06 | OT194599 | > 1 kV & < = 11 kV | 000001689350 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Age
2023-10-20 | OT199683 | > 1 kV & < = 11 kV | 000000930199 | Conductor/Conductive | Bare Steel Conductor | Broken | Vibration
2023-11-30 | OT206367 | < = 1 kV | 000001336286 | Conductor/Conductive | Connection, Unknown | Loose Connection | Incorrect Installation
2023-11-30 | OT206385 | > 11 kV & < = 22 kV ; SWER | 000001572408 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2023-12-10 | OT208284 | > 1 kV & < = 11 kV | 000000823088 | Conductor/Conductive | Live Line Clamp | Broken | Vibration
2024-03-10 | OT229025 | < = 1 kV | 000001280831 | Conductor/Conductive | Bare Al. Alloy Conductor | Burnt Off | Corrosion
2023-12-01 | OT206596 | > 1 kV & < = 11 kV | 000001406053 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2023-12-22 | OT211775 | > 1 kV & < = 11 kV | 000001371886 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2024-01-13 | OT217993 | > 1 kV & < = 11 kV | 000001371418 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2023-08-16 | OT192499 | > 1 kV & < = 11 kV | 000001721237 | Conductor/Conductive | Hexagonal Crimp Connection | Burnt Off | Vibration
2023-08-20 | OT192797 | > 1 kV & < = 11 kV | 000001749005 | Conductor/Conductive | McIntyre Sleeve | Broken | Incorrect Installation
2023-09-03 | OT194280 | > 1 kV & < = 11 kV | 000001583043 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2023-09-13 | OT195431 | > 1 kV & < = 11 kV | 000001765219 | Conductor/Conductive | Bare Steel Conductor | Broken | Age
2023-10-16 | OT199229 | > 1 kV & < = 11 kV | 000000925468 | Conductor/Conductive | Bare Steel Conductor | Deteriorated | Corrosion
2023-09-10 | OT195175 | > 1 kV & < = 11 kV | 000001435664 | Conductor/Conductive | Bare Steel Conductor | Broken | Incorrect Installation
2023-12-19 | OT210655 | > 1 kV & < = 11 kV | 000001435004 | Conductor/Conductive | Connection, Unknown | High Resistivity | Corrosion
2024-01-01 | OT215500 | > 1 kV & < = 11 kV | 000000808499 | Conductor/Conductive | Bare Steel Conductor | Lack of Ground Clearance | Hazard on Line
2023-09-21 | OT196277 | > 1 kV & < = 11 kV | 000001415561 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Age
2024-01-30 | OT222661 | > 1 kV & < = 11 kV | 000001398682 | Conductor/Conductive | PG Clamp | Burnt Off | Incorrect Installation
2023-09-01 | OT194208 | > 1 kV & < = 11 kV | 000001346542 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2023-12-05 | OT207510 | < = 1 kV | 000001521862 | Conductor/Conductive | Bare ACSR Conductor | Broken | Age
2024-01-10 | OT217584 | > 1 kV & < = 11 kV | 000001791375 | Conductor/Conductive | Helical Preformed Splice | Burnt Off | Corrosion
2024-06-19 | OT239468 | < = 1 kV | 000001643315 | Conductor/Conductive | Bare Al. Conductor | Broken | Corrosion
2023-12-25 | OT212594 | < = 1 kV | 000001316559 | Conductor/Conductive | LV ABC | Burnt Off | Age
2023-07-20 | OT189756 | > 1 kV & < = 11 kV | 000007363364 | Conductor/Conductive | Live Line Clamp | Broken | Fatigue
2024-02-08 | OT224764 | > 1 kV & < = 11 kV | 000001547996 | Conductor/Conductive | Bare Al. Conductor | Clashing | Hazard on Line
2024-04-17 | OT233485 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001282114 | Conductor/Conductive | D-Loop Clamp | Burnt Off | Corrosion
2024-02-06 | OT224436 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001237973 | Conductor/Conductive | Bare Al. Conductor | Broken | Age
2024-04-09 | OT232625 | < = 1 kV | 000001262693 | Conductor/Conductive | Bare Al. Conductor | Deteriorated | Age
2024-04-24 | OT234159 | < = 1 kV | 000006388264 | Conductor/Conductive | LV ABC | Burnt Off | Corrosion
2024-05-09 | OT235514 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000839469 | Conductor/Conductive | Attachment Tie, Hand | Broken | Vibration
2024-02-15 | OT225736 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000827122 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Age
2024-02-16 | OT225912 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000925107 | Conductor/Conductive | Helical Dead-End | Broken | Corrosion
2023-07-19 | OT189711 | > 11 kV & < = 22 kV ; SWER | 000001196405 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2023-09-11 | OT195244 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001196405 | Conductor/Conductive | Bare ACSR Conductor | Unravelled | Corrosion
2024-03-25 | OT230871 | > 1 kV & < = 11 kV | 000001429528 | Conductor/Conductive | Bare Steel Conductor | Broken | Incorrect Installation
2024-02-02 | OT223664 | < = 1 kV | 000001001859 | Conductor/Conductive | Split Bolt Clamp | Broken | Fatigue
2024-02-12 | OT225299 | > 1 kV & < = 11 kV | 000001445463 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2024-02-28 | OT227378 | > 1 kV & < = 11 kV | 000001849812 | Conductor/Conductive | PG Clamp | Burnt Off | Corrosion
2024-01-01 | OT215644 | > 1 kV & < = 11 kV | 000001694667 | Conductor/Conductive | Bare Al. Alloy Conductor | Broken | Hazard on Line
2024-05-14 | OT235949 | < = 1 kV | 000000926664 | Conductor/Conductive | Connection, Unknown | High Resistivity | Corrosion
2024-01-26 | OT221276 | > 11 kV & < = 22 kV ; SWER | 000001952836 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2024-06-04 | OT237905 | < = 1 kV | 000001707371 | Conductor/Conductive | Bare Al. Conductor | Short Circuit | Hazard on Line
2024-06-26 | OT240133 | > 11 kV & < = 22 kV ; SWER | 000001539881 | Conductor/Conductive | Bare Steel Conductor | Unravelled | Vibration
2024-03-22 | OT230547 | > 11 kV & < = 22 kV ; SWER | 000008734251 | Conductor/Conductive | Bare Steel Conductor | Broken | Vibration
2023-08-04 | OT191222 | > 1 kV & < = 11 kV | 000001674626 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2023-07-17 | OT189422 | > 11 kV & < = 22 kV ; SWER | 000001658104 | Conductor/Conductive | Live Line Clamp | Burnt Off | Fatigue
2024-04-02 | OT231754 | < = 1 kV | 000000908608 | Conductor/Conductive | Split Bolt Clamp | Burnt Off | Fatigue
2024-05-30 | OT237466 | > 11 kV & < = 22 kV ; SWER | 000001044923 | Conductor/Conductive | Split Bolt Clamp | Broken | Fatigue
2023-09-06 | OT194702 | > 1 kV & < = 11 kV | 000001541195 | Conductor/Conductive | Bare ACSR Conductor | Burnt Off | Age
2023-10-03 | OT197738 | > 1 kV & < = 11 kV | 000001495916 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2023-11-05 | OT202036 | < = 1 kV | 000000885118 | Conductor/Conductive | Split Bolt Clamp | Burnt Off | Fatigue
2024-06-04 | OT237946 | > 1 kV & < = 11 kV | 000006376949 | Conductor/Conductive | HV Cable | Broken | Vibration
2024-05-08 | OT235501 | > 11 kV & < = 22 kV ; SWER | 000000819555 | Conductor/Conductive | Live Line Clamp | Broken | Vibration
2024-05-19 | OT236416 | > 11 kV & < = 22 kV ; SWER | 000000819555 | Conductor/Conductive | Bare ACSR Conductor | Deteriorated | Corrosion
2023-10-03 | OT197693 | > 1 kV & < = 11 kV | 000001924931 | Conductor/Conductive | Bare Al. Alloy Conductor | Burnt Off | Incorrect Installation
2024-03-15 | OT229728 | > 1 kV & < = 11 kV | 000001842317 | Conductor/Conductive | Bare ACSR Conductor | Burnt Off | Corrosion
2024-05-30 | OT237468 | > 1 kV & < = 11 kV | 000001771793 | Conductor/Conductive | Bare Steel Conductor | Deteriorated | Corrosion
2023-11-08 | OT202740 | < = 1 kV | 000001831057 | Conductor/Conductive | LV ABC | Burnt Off | Corrosion
2023-09-04 | OT194435 | > 1 kV & < = 11 kV | 000000839951 | Conductor/Conductive | Live Line Clamp | Burnt Off | Fatigue
2024-01-24 | OT220240 | > 1 kV & < = 11 kV | 000001596101 | Conductor/Conductive | HV ABC | Burnt Off | Corrosion
2023-08-05 | OT191355 | < = 1 kV | 000001302359 | Conductor/Conductive | LV ABC | Burnt Off | Incorrect Installation
2023-08-09 | OT191815 | > 11 kV & < = 22 kV ; Single-Phase | 000001165950 | Conductor/Conductive | Helical Preformed Splice | High Resistivity | Corrosion
2023-11-23 | OT205091 | < = 1 kV | 000001143602 | Conductor/Conductive | Connection, Unknown | Broken | Fatigue
2023-12-14 | OT209088 | < = 1 kV | 000001138980 | Conductor/Conductive | Bare Al. Conductor | Lack of Ground Clearance | Hazard on Line
2023-07-07 | OT188497 | > 11 kV & < = 22 kV ; SWER | 000001285698 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2023-08-22 | OT193082 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001286479 | Conductor/Conductive | Live Line Clamp | Burnt Off | Corrosion
2023-12-27 | OT213609 | > 1 kV & < = 11 kV | 000001308008 | Conductor/Conductive | Bare ACSR Conductor | Broken | Hazard on Line
2023-12-01 | OT206676 | > 1 kV & < = 11 kV | 000000959145 | Conductor/Conductive | PG Clamp | High Resistivity | Corrosion
2023-12-18 | OT210492 | > 11 kV & < = 22 kV ; SWER | 000001753171 | Conductor/Conductive | PG Clamp | Burnt Off | Corrosion
2023-12-30 | OT214853 | > 11 kV & < = 22 kV ; Single-Phase | 000000947230 | Conductor/Conductive | Bare Cu Conductor | Broken | Vibration
2023-07-28 | OT190624 | > 1 kV & < = 11 kV | 000001863344 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2023-08-03 | OT191135 | > 1 kV & < = 11 kV | 000001465168 | Conductor/Conductive | Split Bolt Clamp | Broken | Corrosion
2023-10-15 | OT199050 | > 1 kV & < = 11 kV | 000001846855 | Conductor/Conductive | Connection, Unknown | Broken | Fatigue
2023-12-27 | OT213442 | > 1 kV & < = 11 kV | 000001089458 | Conductor/Conductive | PG Clamp | Broken | Corrosion
2024-02-28 | OT227286 | > 1 kV & < = 11 kV | 000001478626 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2023-08-17 | OT192528 | < = 1 kV | 000001366859 | Conductor/Conductive | Bare Al. Conductor | Deteriorated | Age
2023-08-24 | OT193229 | > 11 kV & < = 22 kV ; SWER | 000008865777 | Conductor/Conductive | Attachment Tie, Hand | Broken | Vibration
2023-09-23 | OT196571 | > 11 kV & < = 22 kV ; SWER | 000001546023 | Conductor/Conductive | Bare Steel Conductor | Clashing | Vibration
2023-09-29 | OT197260 | < = 1 kV | 000000802468 | Conductor/Conductive | LV ABC | Insulation Deteriorated | Corrosion
2023-12-02 | OT206808 | > 11 kV & < = 22 kV ; SWER | 000001776953 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2023-07-14 | OT189202 | < = 1 kV | 000001646868 | Conductor/Conductive | Bare Cu Conductor | Deteriorated | Age
2024-04-02 | OT231750 | < = 1 kV | 000001530604 | Conductor/Conductive | PG Clamp | High Resistivity | Fatigue
2023-07-11 | OT188940 | > 1 kV & < = 11 kV | 000000884396 | Conductor/Conductive | Live Line Clamp | Loose Connection | Incorrect Installation
2023-08-08 | OT191701 | > 1 kV & < = 11 kV | 000008814233 | Conductor/Conductive | Live Line Clamp | Broken | Vibration
2023-09-19 | OT196072 | > 1 kV & < = 11 kV | 000001649376 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2023-09-28 | OT197188 | < = 1 kV | 000001478887 | Conductor/Conductive | Bare Cu Conductor | Deteriorated | Age
2023-11-11 | OT203156 | > 1 kV & < = 11 kV | 000000997849 | Conductor/Conductive | Live Line Clamp | High Resistivity | Incorrect Installation
2023-11-12 | OT203285 | < = 1 kV | 000001475779 | Conductor/Conductive | LV ABC | Burnt Off | Age
2023-11-27 | OT205569 | > 1 kV & < = 11 kV | 000001056130 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2023-12-14 | OT209145 | < = 1 kV | 000000816884 | Conductor/Conductive | Connection, Unknown | Loose Connection | Vibration
2023-12-18 | OT210543 | < = 1 kV | 000000765203 | Conductor/Conductive | LV ABC | Burnt Off | Corrosion
2023-12-18 | OT210550 | < = 1 kV | 000000765203 | Conductor/Conductive | LV ABC | Burnt Off | Corrosion
2024-06-18 | OT239323 | > 1 kV & < = 11 kV | 000001461909 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2023-07-11 | OT188839 | > 22 kV & < = 66 kV | 000001888094 | Conductor/Conductive | Bare ACSR Conductor | Burnt Off | Corrosion
2023-08-15 | OT192349 | > 1 kV & < = 11 kV | 000000981731 | Conductor/Conductive | Live Line Clamp | Loose Connection | Incorrect Installation
2024-02-02 | OT223797 | > 11 kV & < = 22 kV ; SWER | 000001620686 | Conductor/Conductive | Split Bolt Clamp | Loose Connection | Fatigue
2023-11-16 | OT203771 | > 1 kV & < = 11 kV | 000001515622 | Conductor/Conductive | Bare Steel Conductor | Unravelled | Age
2023-12-25 | OT212623 | > 1 kV & < = 11 kV | 000001500341 | Conductor/Conductive | Bare Cu Conductor | Broken | Vibration
2023-10-02 | OT197572 | < = 1 kV | 000001122248 | Conductor/Conductive | LV ABC | Burnt Off | Age
2023-12-08 | OT208167 | < = 1 kV | 000001117451 | Conductor/Conductive | LV ABC | Burnt Off | Incorrect Installation
2024-06-25 | OT239999 | > 11 kV & < = 22 kV ; SWER | 000001079423 | Conductor/Conductive | Connection, Unknown | Loose Connection | Vibration
2023-09-04 | OT194448 | > 11 kV & < = 22 kV ; SWER | 000001599674 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2024-02-05 | OT224096 | > 1 kV & < = 11 kV | 000001651778 | Conductor/Conductive | Hexagonal Crimp Connection | Broken | Fatigue
2023-11-12 | OT203300 | < = 1 kV | 000001130971 | Conductor/Conductive | LV ABC | Burnt Off | Age
2023-12-29 | OT214168 | > 11 kV & < = 22 kV ; SWER | 000001822044 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Corrosion
2023-07-26 | OT190329 | > 1 kV & < = 11 kV | 000001757657 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2023-09-05 | OT194571 | > 1 kV & < = 11 kV | 000000841575 | Conductor/Conductive | Bare Steel Conductor | Broken | Incorrect Installation
2023-08-22 | OT193124 | > 11 kV & < = 22 kV ; SWER | 000001681204 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2023-12-04 | OT207106 | > 11 kV & < = 22 kV ; SWER | 000000932123 | Conductor/Conductive | Live Line Clamp | Broken | Vibration
2023-11-04 | OT201960 | > 11 kV & < = 22 kV ; SWER | 000001592283 | Conductor/Conductive | Attachment Tie, Hand | Broken | Corrosion
2023-10-25 | OT200339 | < = 1 kV | 000008657296 | Conductor/Conductive | Bare Cu Conductor | Clashing | Unknown
2023-08-28 | OT193642 | > 1 kV & < = 11 kV | 000001490040 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2024-04-10 | OT232777 | > 1 kV & < = 11 kV | 000001444598 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2024-05-19 | OT236464 | > 1 kV & < = 11 kV | 000001476452 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2024-06-17 | OT239248 | > 1 kV & < = 11 kV | 000001445206 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2023-10-22 | OT199884 | > 11 kV & < = 22 kV ; SWER | 000001844053 | Conductor/Conductive | Bare Steel Conductor | Broken | Vibration
2024-05-22 | OT236691 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001157313 | Conductor/Conductive | Attachment Tie, Hand | Broken | Vibration
2024-06-17 | OT239246 | > 11 kV & < = 22 kV ; Multiple-Phase | 000006990196 | Conductor/Conductive | Bare ACSR Conductor | Burnt Off | Corrosion
2024-06-24 | OT239884 | > 11 kV & < = 22 kV ; SWER | 000001114977 | Conductor/Conductive | Bare Steel Conductor | Broken | Age
2024-05-11 | OT235770 | > 1 kV & < = 11 kV | 000001141850 | Conductor/Conductive | Helical Dead-End | Broken | Corrosion
2023-08-04 | OT191239 | < = 1 kV | 000001336543 | Conductor/Conductive | LV ABC | Insulation Deteriorated | Age
2023-10-12 | OT198733 | < = 1 kV | 000007387999 | Conductor/Conductive | Split Bolt Clamp | Burnt Off | Fatigue
2023-11-13 | OT203312 | > 1 kV & < = 11 kV | 000001177314 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2024-03-20 | OT230307 | > 1 kV & < = 11 kV | 000000769178 | Conductor/Conductive | Bare Al. Alloy Conductor | Burnt Off | Age
2024-03-27 | OT231190 | > 1 kV & < = 11 kV | 000001351651 | Conductor/Conductive | Connection, Unknown | Broken | Fatigue
2024-04-20 | OT233736 | < = 1 kV | 000001340592 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2023-11-02 | OT201653 | > 1 kV & < = 11 kV | 000001318596 | Conductor/Conductive | PG Clamp | Burnt Off | Fatigue
2024-05-02 | OT234965 | < = 1 kV | 000001315186 | Conductor/Conductive | Bare Al. Conductor | Deteriorated | Corrosion
2024-01-05 | OT216623 | > 11 kV & < = 22 kV ; SWER | 000001639156 | Conductor/Conductive | Live Line Clamp | Broken | Fatigue
2023-07-10 | OT188740 | > 1 kV & < = 11 kV | 000001233489 | Conductor/Conductive | Bare Steel Conductor | Unravelled | Vibration
2023-08-21 | OT192970 | < = 1 kV | 000001449656 | Conductor/Conductive | LV ABC | Burnt Off | Corrosion
2023-09-20 | OT196162 | > 1 kV & < = 11 kV | 000001434176 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2023-09-02 | OT194243 | > 11 kV & < = 22 kV ; SWER | 000001219809 | Conductor/Conductive | Bare ACSR Conductor | Broken | Vibration
2023-08-20 | OT192796 | > 11 kV & < = 22 kV ; SWER | 000001821673 | Conductor/Conductive | Bare Al. Alloy Conductor | Broken | Corrosion
2024-03-29 | OT231403 | > 11 kV & < = 22 kV ; SWER | 000000837684 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Age
2023-11-11 | OT203170 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001223450 | Conductor/Conductive | Attachment Tie, Hand | Broken | Fatigue
2023-07-23 | OT190027 | > 1 kV & < = 11 kV | 000001349632 | Conductor/Conductive | PG Clamp | Loose Connection | Vibration
2023-12-06 | OT207714 | < = 1 kV | 000000773373 | Conductor/Conductive | Split Bolt Clamp | High Resistivity | Corrosion
2024-01-22 | OT219717 | < = 1 kV | 000000791154 | Conductor/Conductive | LV ABC | Burnt Off | Corrosion
2023-07-20 | OT189739 | > 1 kV & < = 11 kV | 000001320634 | Conductor/Conductive | Bare Al. Conductor | Deteriorated | Age
2023-08-06 | OT191465 | > 1 kV & < = 11 kV | 000001335062 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2023-09-01 | OT194201 | > 1 kV & < = 11 kV | 000001337820 | Conductor/Conductive | Bare Cu Conductor | Deteriorated | Age
2023-10-30 | OT201228 | < = 1 kV | 000001616524 | Conductor/Conductive | LV ABC | Burnt Off | Incorrect Installation
2023-12-19 | OT210623 | < = 1 kV | 000001000252 | Conductor/Conductive | Bare Al. Conductor | Broken | Vibration
2023-07-02 | OT187853 | > 1 kV & < = 11 kV | 000001854101 | Conductor/Conductive | Attachment Tie, Hand | Broken | Fatigue
2023-07-26 | OT190464 | > 1 kV & < = 11 kV | 000001296299 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2024-04-03 | OT231853 | > 1 kV & < = 11 kV | 000001152272 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2024-04-17 | OT233434 | > 1 kV & < = 11 kV | 000008819481 | Conductor/Conductive | Bare ACSR Conductor | Unravelled | Hazard on Line
2023-10-24 | OT200272 | > 11 kV & < = 22 kV ; SWER | 000000809894 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2023-09-04 | OT194398 | > 1 kV & < = 11 kV | 000000942514 | Conductor/Conductive | Helical Dead-End | Broken | Vibration
2024-05-14 | OT235956 | > 11 kV & < = 22 kV ; SWER | 000000821177 | Conductor/Conductive | Bare Steel Conductor | Deteriorated | Corrosion
2024-05-20 | OT236541 | > 1 kV & < = 11 kV | 000000802499 | Conductor/Conductive | Bare Al. Alloy Conductor | Over Tensioned | Incorrect Installation
2023-07-25 | OT190177 | > 1 kV & < = 11 kV | 000001124544 | Conductor/Conductive | PG Clamp | Burnt Off | Corrosion
2023-09-11 | OT195295 | > 1 kV & < = 11 kV | 000000727598 | Conductor/Conductive | Connection, Unknown | Broken | Corrosion
2023-10-13 | OT198915 | < = 1 kV | 000001452415 | Conductor/Conductive | PG Clamp | High Resistivity | Corrosion
2023-10-25 | OT200415 | < = 1 kV | 000001450305 | Conductor/Conductive | Bare Al. Conductor | Broken | Age
2023-10-27 | OT200823 | < = 1 kV | 000001857280 | Conductor/Conductive | Helical Dead-End | Broken | Corrosion
2023-11-20 | OT204474 | > 1 kV & < = 11 kV | 000001509715 | Conductor/Conductive | Connection, Unknown | Broken | Fatigue
2024-01-06 | OT216877 | > 1 kV & < = 11 kV | 000001442145 | Conductor/Conductive | PG Clamp | High Resistivity | Fatigue
2024-03-06 | OT228484 | < = 1 kV | 000001514403 | Conductor/Conductive | PG Clamp | Burnt Off | Fatigue
2024-04-03 | OT231891 | < = 1 kV | 000001446924 | Conductor/Conductive | Split Bolt Clamp | Burnt Off | Corrosion
2024-04-08 | OT232506 | < = 1 kV | 000001772203 | Conductor/Conductive | LV ABC | Burnt Off | Vibration
2024-05-29 | OT237414 | > 1 kV & < = 11 kV | 000001446982 | Conductor/Conductive | Connection, Unknown | Broken | Vibration
2024-06-05 | OT238049 | > 1 kV & < = 11 kV | 000001850268 | Conductor/Conductive | Bare Cu Conductor | Unravelled | Age
2024-06-14 | OT239007 | > 1 kV & < = 11 kV | 000001443698 | Conductor/Conductive | PG Clamp | Loose Connection | Fatigue
2023-07-28 | OT190642 | < = 1 kV | 000000807125 | Conductor/Conductive | Live Line Clamp | Broken | Fatigue
2023-08-20 | OT192836 | > 1 kV & < = 11 kV | 000001647881 | Conductor/Conductive | Connection, Unknown | Broken | Vibration
2023-10-05 | OT198031 | > 1 kV & < = 11 kV | 000007350473 | Conductor/Conductive | PG Clamp | High Resistivity | Incorrect Installation
2023-10-22 | OT199952 | < = 1 kV | 000001023940 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Incorrect Installation
2023-10-23 | OT200086 | < = 1 kV | 000001020115 | Conductor/Conductive | LV ABC | Burnt Off | Incorrect Installation
2023-11-09 | OT202971 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000933001 | Conductor/Conductive | HV ABC | Short Circuit | Age
2023-11-19 | OT204252 | < = 1 kV | 000001355334 | Conductor/Conductive | Bare Cu Conductor | Short Circuit | Age
2023-11-23 | OT205087 | < = 1 kV | 000001541573 | Conductor/Conductive | PG Clamp | Burnt Off | Fatigue
2024-06-13 | OT238810 | > 1 kV & < = 11 kV | 000001519949 | Conductor/Conductive | Live Line Clamp | Broken | Fatigue
2023-09-16 | OT195836 | > 1 kV & < = 11 kV | 000000834329 | Conductor/Conductive | Connection, Unknown | Broken | Vibration
2024-03-15 | OT229671 | > 1 kV & < = 11 kV | 000001847520 | Conductor/Conductive | Connection, Unknown | Burnt Off | Corrosion
2024-04-03 | OT231833 | > 1 kV & < = 11 kV | 000001861755 | Conductor/Conductive | Helical Dead-End | Burnt Off | Fatigue
2024-04-15 | OT233251 | < = 1 kV | 000001849909 | Conductor/Conductive | LV ABC | Deteriorated | Incorrect Installation
2024-04-11 | OT232791 | > 11 kV & < = 22 kV ; SWER | 000001532715 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Vibration
2024-03-13 | OT229353 | > 1 kV & < = 11 kV | 000001469192 | Conductor/Conductive | Split Bolt Clamp | Burnt Off | Vibration
2024-05-24 | OT236937 | > 11 kV & < = 22 kV ; SWER | 000001944193 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2024-05-29 | OT237378 | > 1 kV & < = 11 kV | 000001465030 | Conductor/Conductive | Connection, Unknown | Burnt Off | Fatigue
2023-08-22 | OT193028 | > 11 kV & < = 22 kV ; SWER | 000001971894 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2023-11-17 | OT203934 | > 11 kV & < = 22 kV ; SWER | 000000818725 | Conductor/Conductive | D-Loop Clamp | Loose Connection | Vibration
2024-05-28 | OT237304 | > 11 kV & < = 22 kV ; SWER | 000006180286 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Incorrect Installation
2023-09-17 | OT195902 | > 1 kV & < = 11 kV | 000001664048 | Conductor/Conductive | Live Line Clamp | Burnt Off | Vibration
2023-09-19 | OT196071 | > 1 kV & < = 11 kV | 000001649376 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2023-09-28 | OT197156 | > 1 kV & < = 11 kV | 000001511038 | Conductor/Conductive | Bare Steel Conductor | Unravelled | Age
2023-10-20 | OT199777 | > 1 kV & < = 11 kV | 000001517564 | Conductor/Conductive | Live Line Clamp | Burnt Off | Current Overload
2023-11-10 | OT203033 | < = 1 kV | 000001016377 | Conductor/Conductive | Bare Al. Conductor | Lack of Ground Clearance | Incorrect Installation
2023-11-10 | OT203058 | < = 1 kV | 000001551181 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Corrosion
2024-04-06 | OT232215 | < = 1 kV | 000001037653 | Conductor/Conductive | Bare Al. Conductor | Broken | Vibration
2024-06-03 | OT237822 | > 1 kV & < = 11 kV | 000001485975 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Incorrect Installation
2024-06-11 | OT238620 | > 1 kV & < = 11 kV | 000001687160 | Conductor/Conductive | Live Line Clamp | Broken | Fatigue
2024-06-13 | OT238871 | > 1 kV & < = 11 kV | 000001652221 | Conductor/Conductive | Bare ACSR Conductor | Burnt Off | Age
2024-06-18 | OT239337 | > 1 kV & < = 11 kV | 000001652221 | Conductor/Conductive | Live Line Clamp | Loose Connection | Incorrect Installation
2024-03-15 | OT229687 | > 1 kV & < = 11 kV | 000001690320 | Conductor/Conductive | PG Clamp | High Resistivity | Corrosion
2024-03-28 | OT231380 | > 1 kV & < = 11 kV | 000001869231 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2024-06-07 | OT238270 | > 1 kV & < = 11 kV | 000001705532 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2024-06-23 | OT239830 | > 22 kV & < = 66 kV | 000007593269 | Conductor/Conductive | Connection, Unknown | Broken | Vibration
2023-09-08 | OT195011 | > 1 kV & < = 11 kV | 000001830366 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2023-10-08 | OT198260 | < = 1 kV | 000001824777 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Vibration
2023-11-05 | OT202071 | < = 1 kV | 000001804531 | Conductor/Conductive | Bare Cu Conductor | Broken | Corrosion
2024-03-13 | OT229343 | > 1 kV & < = 11 kV | 000001710655 | Conductor/Conductive | Bare ACSR Conductor | Broken | Corrosion
2024-03-16 | OT229823 | > 1 kV & < = 11 kV | 000001571651 | Conductor/Conductive | Bare Steel Conductor | Deteriorated | Age
2024-04-17 | OT233520 | > 1 kV & < = 11 kV | 000001710655 | Conductor/Conductive | Bare ACSR Conductor | Broken | Age
2024-04-25 | OT234276 | > 1 kV & < = 11 kV | 000001804497 | Conductor/Conductive | Bare Steel Conductor | Broken | Age
2024-05-06 | OT235263 | > 1 kV & < = 11 kV | 000001819550 | Conductor/Conductive | Bare Steel Conductor | Broken | Age
2024-05-24 | OT236946 | > 1 kV & < = 11 kV | 000001830546 | Conductor/Conductive | Attachment Tie, Hand | Broken | Fatigue
2024-06-01 | OT237610 | > 1 kV & < = 11 kV | 000001815202 | Conductor/Conductive | PG Clamp | High Resistivity | Incorrect Installation
2024-06-02 | OT237711 | < = 1 kV | 000001708473 | Conductor/Conductive | Bare ACSR Conductor | Burnt Off | Age
2024-06-20 | OT239624 | > 1 kV & < = 11 kV | 000001874753 | Conductor/Conductive | Helical Dead-End | Broken | Fatigue
2023-08-12 | OT192069 | > 1 kV & < = 11 kV | 000001485860 | Conductor/Conductive | Bare Al. Alloy Conductor | Broken | Corrosion
2023-10-10 | OT198431 | > 22 kV & < = 66 kV | 000000831131 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2023-10-29 | OT201037 | < = 1 kV | 000001624403 | Conductor/Conductive | Split Bolt Clamp | High Resistivity | Fatigue
2023-11-04 | OT201855 | < = 1 kV | 000001923926 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Age
2024-05-02 | OT234933 | < = 1 kV | 000001649039 | Conductor/Conductive | Connection, Unknown | Loose Connection | Vibration
2024-05-26 | OT237078 | > 1 kV & < = 11 kV | 000001741444 | Conductor/Conductive | D-Loop Clamp | Loose Connection | Corrosion
2024-06-01 | OT237593 | > 1 kV & < = 11 kV | 000001768553 | Conductor/Conductive | Helical Dead-End | Broken | Corrosion
2023-08-28 | OT193591 | > 11 kV & < = 22 kV ; SWER | 000001135478 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Corrosion
2024-04-08 | OT232496 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001271036 | Conductor/Conductive | Connection, Unknown | Broken | Fatigue
2024-05-22 | OT236734 | < = 1 kV | 000001098261 | Conductor/Conductive | PG Clamp | High Resistivity | Fatigue
2023-07-16 | OT189339 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001237973 | Conductor/Conductive | Bare Al. Alloy Conductor | Burnt Off | Corrosion
2023-08-02 | OT191009 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001253308 | Conductor/Conductive | Live Line Clamp | Burnt Off | Fatigue
2023-09-27 | OT197073 | < = 1 kV | 000001252813 | Conductor/Conductive | Bare Al. Conductor | Deteriorated | Age
2023-10-09 | OT198292 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001298242 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Corrosion
2023-12-14 | OT209068 | < = 1 kV | 000001294142 | Conductor/Conductive | LV ABC | Lack of Ground Clearance | Hazard on Line
2024-03-26 | OT230984 | < = 1 kV | 000001080751 | Conductor/Conductive | Bare Al. Conductor | Broken | Vibration
2024-04-06 | OT232269 | < = 1 kV | 000001263930 | Conductor/Conductive | PG Clamp | Burnt Off | Fatigue
2024-04-12 | OT232989 | < = 1 kV | 000001263590 | Conductor/Conductive | Bare Al. Conductor | Deteriorated | Age
2024-04-13 | OT233065 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001280871 | Conductor/Conductive | Bare Al. Conductor | Broken | Age
2024-04-16 | OT233291 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001277968 | Conductor/Conductive | Bare Al. Alloy Conductor | Lack of Ground Clearance | Age
2023-09-02 | OT194269 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000939248 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Vibration
2023-07-26 | OT190463 | < = 1 kV | 000001153063 | Conductor/Conductive | PG Clamp | Burnt Off | Corrosion
2024-04-15 | OT233210 | > 11 kV & < = 22 kV ; Multiple-Phase | 000005297881 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Corrosion
2024-05-02 | OT234902 | < = 1 kV | 000001153063 | Conductor/Conductive | PG Clamp | Burnt Off | Vibration
2024-06-21 | OT239699 | < = 1 kV | 000000996273 | Conductor/Conductive | LV ABC | Deteriorated | Age
2023-08-28 | OT193571 | > 11 kV & < = 22 kV ; SWER | 000001284746 | Conductor/Conductive | Bare Steel Conductor | Broken | Age
2024-04-01 | OT231665 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001124973 | Conductor/Conductive | PG Clamp | Burnt Off | Fatigue
2024-04-11 | OT232868 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001157232 | Conductor/Conductive | Bare Al. Conductor | Broken | Corrosion
2024-04-15 | OT233183 | > 11 kV & < = 22 kV ; SWER | 000001292144 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2024-02-19 | OT226120 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000971262 | Conductor/Conductive | PG Clamp | Burnt Off | Fatigue
2023-12-04 | OT207310 | < = 1 kV | 000000952864 | Conductor/Conductive | Attachment Tie, Hand | Broken | Corrosion
2024-02-13 | OT225319 | > 11 kV & < = 22 kV ; Multiple-Phase | 000009153178 | Conductor/Conductive | Helical Preformed Splice | Burnt Off | Current Overload
2024-04-23 | OT234079 | > 1 kV & < = 11 kV | 000001474009 | Conductor/Conductive | Bare Cu Conductor | Unravelled | Incorrect Installation
2024-02-27 | OT227148 | > 1 kV & < = 11 kV | 000001828117 | Conductor/Conductive | Bare Cu Conductor | Unravelled | Age
2023-12-07 | OT207943 | > 1 kV & < = 11 kV | 000000973299 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2024-02-03 | OT223834 | > 1 kV & < = 11 kV | 000001438137 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2024-02-26 | OT227094 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001140075 | Conductor/Conductive | Bare Al. Conductor | Unravelled | Vibration
2023-11-25 | OT205353 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000952892 | Conductor/Conductive | Bare Al. Conductor | High Resistivity | Loose Connection
2023-11-22 | OT204880 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001234611 | Conductor/Conductive | Bare Al. Conductor | Broken | Deterioration
2024-05-28 | OT237295 | > 1 kV & < = 11 kV | 000001169269 | Conductor/Conductive | Bare Al. Conductor | Broken | Corrosion
2023-11-12 | OT203277 | > 1 kV & < = 11 kV | 000001712279 | Conductor/Conductive | Bare Al. Alloy Conductor | Burnt Off | Incorrect Installation
2023-10-07 | OT198217 | > 1 kV & < = 11 kV | 000005298209 | Conductor/Conductive | Live Line Clamp | Broken | Corrosion
2023-11-10 | OT203103 | < = 1 kV | 000001925551 | Conductor/Conductive | LV ABC | Burnt Off | Corrosion
2023-09-20 | OT196198 | < = 1 kV | 000001283737 | Conductor/Conductive | Bare Al. Conductor | Over Tensioned | Hazard on Line
2023-11-05 | OT202158 | > 11 kV & < = 22 kV ; SWER | 000001280589 | Conductor/Conductive | Bare ACSR Conductor | Broken | Corrosion
2023-11-14 | OT203457 | > 11 kV & < = 22 kV ; SWER | 000001282118 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Vibration
2023-12-13 | OT208846 | > 11 kV & < = 22 kV ; SWER | 000001280001 | Conductor/Conductive | Bare ACSR Conductor | Broken | Corrosion
2023-12-14 | OT209384 | > 11 kV & < = 22 kV ; SWER | 000001280565 | Conductor/Conductive | Bare Steel Conductor | Deteriorated | Age
2023-12-28 | OT213930 | < = 1 kV | 000000764276 | Conductor/Conductive | PG Clamp | High Resistivity | Fatigue
2023-10-02 | OT197579 | > 11 kV & < = 22 kV ; Single-Phase | 000000839614 | Conductor/Conductive | D-Loop Clamp | Broken | Fatigue
2023-12-04 | OT207256 | < = 1 kV | 000000892910 | Conductor/Conductive | LV ABC | Burnt Off | Incorrect Installation
2023-09-09 | OT195114 | < = 1 kV | 000001084218 | Conductor/Conductive | LV ABC | Burnt Off | Corrosion
2024-02-29 | OT227585 | < = 1 kV | 000001012831 | Conductor/Conductive | Bare Al. Conductor | Broken | Vibration
2023-07-27 | OT190559 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000938321 | Conductor/Conductive | Bare Al. Alloy Conductor | Burnt Off | Corrosion
2023-08-16 | OT192466 | > 11 kV & < = 22 kV ; SWER | 000001283348 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2023-08-19 | OT192739 | > 11 kV & < = 22 kV ; Single-Phase | 000001166410 | Conductor/Conductive | Bare Al. Alloy Conductor | Broken | Corrosion
2023-12-18 | OT210537 | > 11 kV & < = 22 kV ; SWER | 000001139175 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2024-02-28 | OT227428 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000882819 | Conductor/Conductive | Bare Cu Conductor | Burnt Off | Incorrect Installation
2024-05-15 | OT236134 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001118960 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Age
2024-02-05 | OT224176 | < = 1 kV | 000001562609 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Age
2024-03-31 | OT231590 | > 1 kV & < = 11 kV | 000000978630 | Conductor/Conductive | Bare Al. Conductor | Broken | Age
2024-03-04 | OT227978 | > 1 kV & < = 11 kV | 000001734421 | Conductor/Conductive | Bare Cu Conductor | Broken | Age
2024-02-22 | OT226631 | > 11 kV & < = 22 kV ; SWER | 000001285254 | Conductor/Conductive | Bare Steel Conductor | Broken | Corrosion
2023-12-18 | OT210292 | < = 1 kV | 000001835180 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Hazard on Line
2023-12-25 | OT212673 | < = 1 kV | 000001226974 | Conductor/Conductive | LV ABC | Burnt Off | Incorrect Installation
2023-09-19 | OT196080 | > 11 kV & < = 22 kV ; SWER | 000000960381 | Conductor/Conductive | Bare ACSR Conductor | Broken | Vibration
2023-10-19 | OT199569 | > 11 kV & < = 22 kV ; SWER | 000001581712 | Conductor/Conductive | Live Line Clamp | Loose Connection | Vibration
2023-12-31 | OT215226 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001828704 | Conductor/Conductive | PG Clamp | Burnt Off | Fatigue
2024-01-09 | OT217261 | < = 1 kV | 000001565811 | Conductor/Conductive | Split Bolt Clamp | High Resistivity | Corrosion
2024-02-01 | OT223370 | > 11 kV & < = 22 kV ; Multiple-Phase | 000001578854 | Conductor/Conductive | LV ABC | Burnt Off | Age
2023-10-10 | OT198482 | < = 1 kV | 000000944115 | Conductor/Conductive | PG Clamp | High Resistivity | Fatigue
2023-10-10 | OT198483 | < = 1 kV | 000000944115 | Conductor/Conductive | PG Clamp | High Resistivity | Fatigue
2024-04-01 | OT231619 | > 22 kV & < = 66 kV | 000001871832 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Corrosion
2023-08-20 | OT192801 | > 1 kV & < = 11 kV | 000001441757 | Conductor/Conductive | Connection, Unknown | Burnt Off | Fatigue
2023-08-24 | OT193298 | > 1 kV & < = 11 kV | 000001443699 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2023-08-30 | OT193801 | > 1 kV & < = 11 kV | 000001445863 | Conductor/Conductive | Bare Steel Conductor | Broken | Age
2023-09-18 | OT195922 | > 22 kV & < = 66 kV | 000001857291 | Conductor/Conductive | Bare Steel Conductor | Deteriorated | Corrosion
2023-10-01 | OT197446 | > 1 kV & < = 11 kV | 000001443200 | Conductor/Conductive | Bare ACSR Conductor | Burnt Off | Incorrect Installation
2023-10-04 | OT197788 | > 1 kV & < = 11 kV | 000001443792 | Conductor/Conductive | PG Clamp | Loose Connection | Fatigue
2023-11-30 | OT206199 | < = 1 kV | 000001464563 | Conductor/Conductive | PG Clamp | Burnt Off | Corrosion
2023-12-01 | OT206620 | < = 1 kV | 000008916253 | Conductor/Conductive | Connection, Unknown | Burnt Off | Fatigue
2023-12-02 | OT206905 | > 1 kV & < = 11 kV | 000001500541 | Conductor/Conductive | PG Clamp | Broken | Corrosion
2024-01-03 | OT216058 | > 1 kV & < = 11 kV | 000001442211 | Conductor/Conductive | Bare Steel Conductor | Deteriorated | Age
2024-01-08 | OT217090 | < = 1 kV | 000001434741 | Conductor/Conductive | PG Clamp | Burnt Off | Fatigue
2024-01-11 | OT217612 | < = 1 kV | 000001310555 | Conductor/Conductive | LV ABC | Burnt Off | Age
2024-01-11 | OT217812 | > 1 kV & < = 11 kV | 000001444140 | Conductor/Conductive | Bare Steel Conductor | Deteriorated | Corrosion
2024-06-15 | OT239069 | < = 1 kV | 000001834993 | Conductor/Conductive | PG Clamp | Burnt Off | Incorrect Installation
2024-02-27 | OT227218 | > 1 kV & < = 11 kV | 000001572072 | Conductor/Conductive | Attachment Tie, Hand | Broken | Vibration
2023-08-30 | OT193857 | > 1 kV & < = 11 kV | 000001706710 | Conductor/Conductive | Connection, Unknown | Broken | Corrosion
2024-02-15 | OT225702 | > 11 kV & < = 22 kV ; SWER |  | Conductor/Conductive | Bare Steel Conductor | Disconnected | Vibration
2024-01-11 | OT217759 | > 1 kV & < = 11 kV |  | Conductor/Conductive | Connection, Unknown | Broken | Unknown
2024-01-24 | OT220182 | > 1 kV & < = 11 kV | 000007877368 | Conductor/Conductive | Bare Al. Conductor | Broken Strands | Unknown
2024-02-09 | OT224867 | > 1 kV & < = 11 kV | 000000261236 | Conductor/Conductive | HV Covered Conductor | Cracked | <null>
2024-04-30 | OT234763 | > 22 kV & < = 66 kV | 000000019678 | Conductor/Conductive | Bare Steel Conductor | Broken | Unknown
2024-03-15 | OT229670 | < = 1 kV | 000002703434 | Conductor/Conductive | Bare Al. Conductor | Unknown | Unknown
2024-04-12 | OT232978 | Other | 000000000065 | Conductor/Conductive | Bare Steel Conductor | Broken | Incorrect Installation
2024-01-30 | OT222936 | > 11 kV & < = 22 kV ; Single-Phase | 000002223012 | Conductor/Conductive | Armour Rod | Broken | Corrosion
2024-06-19 | OT239410 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000044424 | Conductor/Conductive | Feeder | Fault Clearance | Vibration
2024-04-24 | OT234149 | < = 1 kV | 000002063719 | Conductor/Conductive | LV ABC | Lack of Ground Clearance | Age
2024-01-19 | OT219112 | > 22 kV & < = 66 kV | 000002133179 | Conductor/Conductive | Bridge | Burnt off | Unknown
2023-09-04 | OT194337 | > 1 kV & < = 11 kV | 000006633593 | Conductor/Conductive | Connection, Unknown | Burnt Off | Defective
2024-06-18 | OT239342 | > 22 kV & < = 66 kV | 000000019795 | Conductor/Conductive | Bridge | Unknown | Unknown
2024-06-11 | OT238578 | > 22 kV & < = 66 kV | 000000031358 | Conductor/Conductive | Connection, Unknown | Broken | Unknown
2024-04-13 | OT233039 | > 1 kV & < = 11 kV | 000002242938 | Conductor/Conductive | Bare Steel Conductor | Broken | Unknown
2024-03-05 | OT228438 | > 11 kV & < = 22 kV ; Multiple-Phase | 000002689153 | Conductor/Conductive | Live Line Clamp | Loose Connection | Corrosion
2024-03-16 | OT229746 | > 22 kV & < = 66 kV | 000002609177 | Conductor/Conductive | PG Clamp | Broken | Vibration
2024-01-31 | OT223184 | > 1 kV & < = 11 kV | 000002059548 | Conductor/Conductive | Bridge | Unknown | Unknown
2023-10-12 | OT198734 | > 1 kV & < = 11 kV | 000002345842 | Conductor/Conductive | Bare Steel Conductor | Deteriorated | Corrosion
2023-10-03 | OT197704 | > 11 kV & < = 22 kV ; SWER | 000007067606 | Conductor/Conductive | Live Line Clamp | Burnt off | Unknown
2023-09-30 | OT197365 | > 22 kV & < = 66 kV | 000000044164 | Conductor/Conductive | Feeder | Fault Clearance | Unknown
2023-09-24 | OT196665 | < = 1 kV | 000007032627 | Conductor/Conductive | LV ABC | Insulation Deteriorated | Age
2023-10-24 | OT200263 | > 1 kV & < = 11 kV | 000002307805 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2023-11-06 | OT202296 | < = 1 kV | 000002663666 | Conductor/Conductive | LV ABC | Burnt Off | Age
2024-05-27 | OT237115 | > 1 kV & < = 11 kV | 000000103515 | Conductor/Conductive | PG Clamp | Corroded | Vibration
2024-04-30 | OT234655 | > 11 kV & < = 22 kV ; Multiple-Phase | 000002163901 | Conductor/Conductive | Live Line Clamp | Loose Connection | Unknown
2024-04-28 | OT234531 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000024727 | Conductor/Conductive | Bare Cu Conductor | Broken | Fatigue
2024-01-13 | OT218027 | > 11 kV & < = 22 kV ; SWER | 000002266390 | Conductor/Conductive | Bridge | Burnt off | Unknown
2024-06-17 | OT239139 | > 11 kV & < = 22 kV ; Multiple-Phase | 000002729023 | Conductor/Conductive | Bridge | Unknown | Unknown
2023-11-21 | OT204703 | > 11 kV & < = 22 kV ; Multiple-Phase | 000006867642 | Conductor/Conductive | Attachment Tie, Hand | Missing | Unknown
2023-12-04 | OT207345 | < = 1 kV | 000005858344 | Conductor/Conductive | LV ABC | Unknown | Unknown
2023-07-26 | OT190334 | > 1 kV & < = 11 kV | 000002392131 | Conductor/Conductive | Bare Steel Conductor | Broken Strands | Unknown
2024-02-16 | OT225822 | < = 1 kV | 000002115020 | Conductor/Conductive | Bare Cu Conductor | Broken | Fatigue
2023-12-01 | OT206621 | < = 1 kV | 000002866324 | Conductor/Conductive | Connection, Unknown | Burnt Off | Fatigue
2023-12-05 | OT207651 | > 11 kV & < = 22 kV ; Multiple-Phase | 000000032100 | Conductor/Conductive | Bare Al. Alloy Conductor | Broken | Age
2024-05-06 | OT235257 | > 11 kV & < = 22 kV ; SWER | 000002184764 | Conductor/Conductive | Bare Steel Conductor | Unknown | Unknown
2024-05-21 | OT236575 | > 1 kV & < = 11 kV | 000002839814 | Conductor/Conductive | Bare Steel Conductor | Deteriorated | Corrosion
2024-03-03 | OT227873 | > 1 kV & < = 11 kV | 000000006384 | Conductor/Conductive | Attachment Tie, Hand | Broken | Fatigue
2023-09-04 | OT194431 | < = 1 kV | 000002554542 | Conductor/Conductive | LV ABC | Burnt Off | Incorrect Installation
2023-09-03 | OT194281 | > 1 kV & < = 11 kV | 000002634008 | Conductor/Conductive | Live Line Clamp | Broken | Corrosion
2023-09-06 | OT194721 | < = 1 kV | 000002690719 | Conductor/Conductive | Bridge | Burnt Off | Age
2023-08-08 | OT191644 | < = 1 kV | 000009252920 | Conductor/Conductive | LV ABC | Deteriorated | Age
2023-12-26 | OT213147 | > 1 kV & < = 11 kV | 000002337230 | Conductor/Conductive | Bridge | <null> | Unknown
2023-10-11 | OT198586 | > 11 kV & < = 22 kV ; SWER | 000002425859 | Conductor/Conductive | Bare Steel Conductor | Broken | Unknown
2024-05-18 | OT236361 | < = 1 kV | 000002364659 | Conductor/Conductive | Bare Al. Alloy Conductor | Over Tensioned | Hazard on Line
2024-03-27 | OT231218 | > 1 kV & < = 11 kV | 000002177526 | Conductor/Conductive | D-Loop Clamp | Loose Nut | Vibration
2023-08-25 | OT193356 | < = 1 kV | 000002301506 | Conductor/Conductive | LV ABC | Burnt Off | Unknown
2023-07-08 | OT188587 | > 11 kV & < = 22 kV ; Single-Phase | 000006026182 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Age
2024-05-14 | OT235991 | > 11 kV & < = 22 kV ; SWER | 000002090049 | Conductor/Conductive | Live Line Clamp | Unknown | Unknown
2024-06-17 | OT239183 | > 11 kV & < = 22 kV ; SWER | 000002272336 | Conductor/Conductive | Bridge | Unknown | Unknown
2024-01-01 | OT215685 | < = 1 kV | 000002066903 | Conductor/Conductive | Bare Al. Conductor | Burnt Off | Corrosion
2023-08-22 | OT193069 | > 1 kV & < = 11 kV | 000002058946 | Conductor/Conductive | Bridge | Damaged | Unknown
2024-06-08 | OT238320 | < = 1 kV | 000002485006 | Conductor/Conductive | LV Covered Conductor | Disconnected | Unknown
2024-03-26 | OT231056 | < = 1 kV | 000002144469 | Conductor/Conductive | PG Clamp | Loose Connection | Corrosion
2023-07-27 | OT190509 | > 11 kV & < = 22 kV ; Single-Phase | 000002498397 | Conductor/Conductive | Bridge | Burnt Partly | Unknown
2024-03-28 | OT231316 | < = 1 kV | 000002108564 | Conductor/Conductive | LV Covered Conductor | Broken | <null>
2023-10-13 | OT198840 | > 1 kV & < = 11 kV | 000002284400 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2023-11-03 | OT201762 | > 11 kV & < = 22 kV ; SWER | 000007091535 | Conductor/Conductive | Bare Steel Conductor | Burnt Off | Corrosion
2024-01-18 | OT218828 | < = 1 kV | 000002148772 | Conductor/Conductive | PG Clamp | Burnt Off | Fatigue
2023-10-26 | OT200628 | > 11 kV & < = 22 kV ; SWER | 000002302030 | Conductor/Conductive | Live Line Clamp | Broken | Vibration
2023-11-14 | OT203536 | < = 1 kV | 000002498409 | Conductor/Conductive | Bare Steel Conductor | Deteriorated | Corrosion
2023-12-31 | OT215033 | < = 1 kV | 000002644921 | Conductor/Conductive | LV ABC | Deteriorated | Vibration
2024-01-31 | OT223211 | < = 1 kV | 000000022361 | Conductor/Conductive | Feeder | Fault Clearance | Current Overload
2024-01-20 | OT219300 | > 1 kV & < = 11 kV | 000002650208 | Conductor/Conductive | Bare ACSR Conductor | Broken | Unknown
2024-03-27 | OT231113 | > 1 kV & < = 11 kV | 000002776801 | Conductor/Conductive | Bare Steel Conductor | Broken | Unknown

## Pivot Table
Asset Category | Count of Asset Category
< = 1 kV | 140
> 1 kV & < = 11 kV | 197
> 11 kV & < = 22 kV ; Multiple-Phase | 48
> 11 kV & < = 22 kV ; Single-Phase | 8
> 11 kV & < = 22 kV ; SWER | 77
> 22 kV & < = 66 kV | 13
Other | 2
Total Result | 485