## Pivot
Distribution Transformers | Count of RIN Category
Ground Outdoor / Indoor Chamber Mounted; < 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 4
Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 2
Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 38
Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 37
Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 39
Grand Total | 120
Row Labels | Count of RIN Category -AER
Current Transformer | 1
Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA | 1
Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA | 1
Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA | 2
Voltage Transformer | 1
Grand Total | 6

## Distriubtion Transformer Data
5-year Window | ASSOCIATED_EQUIP | CLOSED_DT | COMP_CODE | COMP_CODE_DESCRIPTION | COMPLETED_CODE_DESCRIPTION | COMPLETION_COMMENTS | CONSEQUENCE_DESCRIPTION | Date | Date1 | DEPOT_DESCRIPTION | DSTRCT_CODE | EQUIP_CLASS | EQUIP_CLASS_DESCRIPTION | EQUIP_LOCATION | EQUIP_NO | F4 | Financial End Year | FISCAL YEAR | FY Date (End Year) | HV/LV | Month/Year of Raised Date | MSS_MAJOR_EVENT_DAY_EVENT_CODE | MSSS Cause | MSSS_DAMAGE_APPARENT_CAUSE_DESCRIPTION | MSSS_OBJECT_FAILURE_DESCRIPTION | NETWORK_EVENT_TYPE_DESCRIPTION | North/South | OUTAGE TRIGGER DESCRIPTION | OUTAGE_ACTUAL_START_TIMESTAMP | OUTAGE_COMMENTARY | OUTAGE_DATE | OUTAGE_DESCRIPTION | OUTAGE_EVENT_TYPE_DESCRIPTION | OUTAGE_EXEMPTION_DESCRIPTION | OUTAGE_LOG_DETAILS | OUTAGE_MSSS_VALID | OUTAGE_NAME | OUTAGE_PRIMARY_ASSET_DESCRIPTION | OUTAGE_PRIMARY_ASSET_NAME | OUTAGE_PRIMARY_ASSET_NO | OUTAGE_PROTECTION_ASSET_NAME | OUTAGE_STANDARD_REASON_DESCRIPTION | OUTAGE_STATUS_DESCRIPTION | OUTAGE_TYPE_DESCRIPTION | OUTAGE_WEATHER_DESCRIPTION | PLANT_NO | RIN Category | lat | long | RAISED_DATE | REQUEST_ID | SHORT_DESC_1 | SHORT_DESC_2 | SJ_DSTRCT_CODE | STD_JOB_DESC | STD_JOB_NO | SUB_REGION_NAME | VOLTAGE_DESCRIPTION | WO_DESC | WO_JOB_CODEX1 | WO_JOB_CODEX2 | WO_JOB_CODEX3 | WO_JOB_CODEX4 | WO_JOB_CODEX8 | WO_TYPE_DESCRIPTION | WORK_GRP_DESC | WORK_ORDER | WORK_ORDER_EXTENDED_DESCRIPTION | WORK_ORDER_ID | YYYYMM | Aflc | AFLC Population | Circuit Breaker and Recloser Population | Circuit Breakers and Reclosers | Crossarm Population | Distirbution TX Population | Distribution Transformers | Distribution TX Population | Historic Failures | Instrument Transformer Population | Instrument Transformers | Normalised Failure Rate | Number of Records | OH Conductor | OH Conductor Population | OUTAGE_PRIMARY_ASSET_ID | OUTAGE_PROTECTION_ASSET_ID | Pole Top Structure | Poles | Poles Population | RNUM | Service Lines | Services Population | Substation Transformer Population | Substation Transformers | Switches | Switches Population | UG Cable | UG Cable Population
2023-07-03 |  | 2023-07-04 | TDDI | Transformer-Distribution | Closed |  |  | 2023-07-03 | 2023-07-01 | BOWEN | EECL | NS | Network Site | XLHBB | 1700345 |  |  | 23/24 | 2024-01-03 | HV | 2023-07-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | HV-Unassisted failure(Apparent defect) | 2023-07-03 14:38 | F-1664-s MERI-03 - Access required to Replace BNS254 (Clearance isssues between edo arm & 11kV mains) | 2023-07-03 | BOWEN: MOUNT DANGAR RD | Distribution Event | Normal Event | Access required to Replace BNS254 Crew to attend in the morning. 4/7/22 Sending Asset Event to FFA FFA Order Created F-AE23NQ7073-1-0 DfltHost . Sending Asset Event to FFA Time On modified from 23:59 03-Jul to 23:59 04-Jul Sending Asset Event to FFA Crews attending: Peter Short 0427 250 855 bwnfco01. Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA outage increase due to requirement for BNS254 repairs Time On modified from 23:59 04-Jul to 15:00 04-Jul Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ7073-1-0 bwnfco01 Peter Short 0427250855 FFA Order En Route F-AE23NQ7073-1-0 bwnfco01 FFA Order On Site F-AE23NQ7073-1-0 bwnfco01 Time On modified from 15:00 04-Jul to 17:00 04-Jul Sending Asset Event to FFA FFA Order F-AE23NQ7073-1-0 Completed by technician Peter Short in crew bwnfco01(0427250855) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replaced faulty tx with 63kva Site Label : 5202146 Actual Power Restoration for F-AE23NQ7073-1-0: 04-JUL-2023 15:14:00 Time On modified from 17:00 04-Jul to 14:57 04-Jul | Valid | 23NQ7073 | Merinda No.03 11kV FEEDER SECTION | MERI-03 WILLCOX - MT DANGAR | MERI-03 WILLCOX.FC | WILLCOX NO.1 REC | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS5202146 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -20.15068307875760 | 148.125435495098 | 2023-07-03 | 1852816 | MAHOGANY WAY PTY LTD | P - Phase Down (LV) | EECL | Transformers Return to Service | D2002 | North Queensland | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | BOWEN | OT187993 | .HEADING Technician: Peter Short Comments | OT187993 | 202307
2023-07-03 |  | 2023-07-03 | TDDI | Transformer-Distribution | Closed |  |  | 2023-07-03 | 2023-07-01 | BUNDABERG | EECL | NS | Network Site | XLFBB | 1438574 |  |  | 23/24 | 2024-01-03 | HV | 2023-07-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2023-07-03 12:18 | F-712-r 11kV Pole Dist Sub 9671 Crew has advised TX has FIS | 2023-07-03 | BUNDABERG: SAUERS RD | Distribution Event | Normal Event | 11kV Pole Dist Sub 9671 Crew has advised TX has FIS bndcsfr11 Sending Asset Event to FFA FFA Order Created F-AE23WB7191-1-0 DfltHost FFA Order Acknowledged F-AE23WB7191-1-0 bndcsfr11 TrevorJohnson 0407129831 FFA Order En Route F-AE23WB7191-1-0 bndcsfr11 FFA Order On Site F-AE23WB7191-1-0 bndcsfr11 Sending Asset Event to FFA Time On modified from 23:59 03-Jul to 17:01 03-Jul Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23WB7191-1-0 Completed by technician TrevorJohnson in crew bndcsfr11(0407129831) with code A-T-303 - Distribution substation Action Taken : Replaced Tx Site Label : 2101973 Time On modified from 17:01 03-JUL to 17:28 03-JUL | Valid | 23WB7191 |  | Sauers Rd east of Zielke Rd | 9671 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS2101973 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -24.83478355407710 | 152.395645141602 | 2023-07-03 | 1852741 | MS F L GRAHAM | O - Other | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | BUNDABERG CS | OT187953 | Technician: TrevorJohnson Comments | OT187953 | 202307
2023-07-03 | [7 empty] | 2023-07-03 | 2023-07-01 | MORANBAH | EECL | FC | Feeder Section | XCPNO | 7510869 |  |  | 23/24 | 2024-01-03 | HV | 2023-07-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-07-03 22:39 | F-475-t - NEBO 19kV RC854011 Valkyrie ACR CB tripped. SCADA Interface automated outage. | 2023-07-03 | NEBO: VALKYRIE ACCESS RD, DINGO DEVELOPMENT RD VALKYRIE: VALKYRIE RD | Distribution Event | Normal Event | entered from the SCADA Interface Tripped on O/C Poor access currently - crews will get chopper in the morning and patrol - please put on mnboc01 - crews will advise if they need it moved Time On modified from 23:59 03-Jul to 23:59 04-Jul Sending Asset Event to FFA FFA Order Created F-AE23MK4722-1-0 DfltHost FFA Order Acknowledged F-AE23MK4722-1-0 mnboc01 Jesse Boswood 0438515383 FFA Order En Route F-AE23MK4722-1-0 mnboc01 Manual Reclose Checklist Sending Asset Event to FFA FFA Order On Site F-AE23MK4722-1-0 mnboc01 Crew advised Relocated nest from Recloser and attempted a reclose. Not succesful.Currently Isolating at load Links to confirm recloser Sending Asset Event to FFA First reclose was unsuccessful up to SECT SL589725 at 1047. Crew then patrolled back to recloser before secoind attempt. Sending Asset Event to FFA Succesful energisation of Recloser. Load link closed and crews to complete patrol between Recloser and Sectionaliser SL589725. Crew advised about 20% and in crappy areas Sending Asset Event to FFA Patrolled all line up to sectionaliser - no fault found - opened LKS 922 and FLKS 1953 to sectionalise and attempting anothee reclose. Asset selection modified Sending Asset Event to FFA Reclose successful with LKS 922 and FLKS 1953 open. Closed FLKS 1953 and ACR stayed closed. Crews will pull HV fuse at 6408 and close LKS922. Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA ACr tripped upon closing of LKS922 - Links opened again and reclose sucessful Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA All supply restored bar pump at Sub 6408. Crews will try to attend to make repairs by the end of the week. Customer OK with extended outage. AP will be written on fault sheet F-475-t. Mick Crisp 0456 174 588 will update if crews cannot attend by Friday. Ground is wet so may be ongoing access issues Time On modified from 23:59 04-Jul to 13:00 07-Jul Sending Asset Event to FFA Crews attending 14/7/23 to replace TX like for like. Crews will be Ethan Hand or Jesse Boswood Time On modified from 13:00 07-Jul to 13:00 14-Jul Sending Asset Event to FFA FFA Order F-AE23MK4722-1-0 Completed by technician Jesse Boswood in crew mnboc01(0438515383) with code A-T-303 - Distribution substation Action Taken : Problem found at tx6408, t-off to tx has been isolated planned to go rectify fault on Friday 14th if the property dries up Site Label : TX6408 Refer to F-475-t for repairs. Time On modified from 13:00 14-Jul to 14:00 14-Jul Time On modified from 14:00 14-Jul to 13:21 14-Jul auto-completed | Invalid | 23MK4722 | PEAK DOWNS HWY, STRATHFIELD QLD 4742 | Mt Flora SWER | 224.FC | VALKYRIE | Unknown | Completed | Unplanned Outage | Wet / Rain | FC-19-691442 | Ground Outdoor / Indoor Chamber Mounted; < 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2023-07-03 | 1852911 | U Unknown |  | EECL | Forced Regulated | CEFR | Mackay | 19kV | U Unknown | M0209 | M0052 | M9999 |  | H | Operational | MORANBAH | OT188068 |  | OT188068 | 202307
2023-07-04 |  | 2023-07-04 | TDDI | Transformer-Distribution | Closed |  |  | 2023-07-04 | 2023-07-01 | MONTO | EECL | NS | Network Site | XCFZT | 934114 |  |  | 23/24 | 2024-01-04 | HV | 2023-07-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2023-07-04 03:33 | F-1603-q Crew advise 11kV Pole Dist Sub 239736 requires replacement with isolation and earthing from S2509 FFA Order F-AE23CA7969-1-0 Completed by technician Ben Scott in crew moncmfr03(0417991328) with code A-T-303 - Distribution substation Action Taken : blown 25kva 11kv 3 phase TX replaced. Site Label : 4127167 | 2023-07-04 | MUNGUNGO: MONAL RD | Distribution Event | Normal Event | Crew advise 11kV Pole Dist Sub 239736 requires replacement with isolation and earthing from S2509 Extend outage to S2509. Crew advise 0700-1000hrs Fault job F-1603-q created in Pon Sending Asset Event to FFA FFA Order Created F-AE23CA7969-1-0 DfltHost Pad moncmfr03 Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 04-Jul to 10:16 04-Jul Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA7969-1-0 moncmfr03 Ben Scott 0417991328 FFA Order En Route F-AE23CA7969-1-0 moncmfr03 FFA Order On Site F-AE23CA7969-1-0 moncmfr03 FFA Order F-AE23CA7969-1-0 Completed by technician Ben Scott in crew moncmfr03(0417991328) with code A-T-303 - Distribution substation Action Taken : blown 25kva 11kv 3 phase TX replaced. Site Label : 4127167 | Valid | 23CA7969 |  | MT102 MUNGUNGO RECLOSER | MT102X17899 | S2509 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS4127167 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -24.68734741210940 | 151.131164550781 | 2023-07-04 | 1852913 | MR N WILLIAMS | D - Lines Down | EECL | Transformers Return to Service | D2002 | Capricornia | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | MONTO | OT188070 | Technician: Ben Scott Comments | OT188070 | 202307
2023-07-24 |  | 2023-07-28 |  |  | Closed |  |  | 2023-07-24 | 2023-07-01 | JULIA CREEK | EECL | NT | Network Slot | XCHBJ | 2843242 |  |  | 23/24 | 2024-01-24 | HV | 2023-07-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2023-07-24 14:00 | 19.1kV SWER Pole Dist Sub JCS84 - Requires replacement | 2023-07-24 | JULIA CREEK: GAROMNA STATION | Distribution Event | Normal Event | Crew advise defective tx. Crew on site following FC2348765. Time Off modified from 17:12 24-Jul to 14:00 24-Jul Sending Asset Event to FFA FFA Order Created F-AE23NQ9433-1-0 DfltHost Sending Asset Event to FFA Delayed till Wednesday Time On modified from 23:59 24-Jul to 23:59 26-Jul Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ9433-1-0 jckcmcs01 Nathan James-Laneyrie 0473859801 Time On modified from 23:59 26-Jul to 23:59 27-Jul Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 27-Jul to 18:00 27-Jul Sending Asset Event to FFA FFA Order En Route F-AE23NQ9433-1-0 jckcmcs01 FFA Order On Site F-AE23NQ9433-1-0 jckcmcs01 Time On modified from 18:00 27-Jul to 16:19 27-Jul Sending Asset Event to FFA FFA Order En Route F-AE23NQ9433-1-0 jckcmcs01 FFA Order On Site F-AE23NQ9433-1-0 jckcmcs01 FFA Order F-AE23NQ9433-1-0 Completed by technician Nathan James-Laneyrie in crew jckcmcs01(0473859801) with code A-T-303 - Distribution substation Action Taken : replace swer tx Site Label : 5040388 Actual Power Restoration for F-AE23NQ9433-1-0: 27-JUL-2023 17:07:00 auto-completed | Invalid | 23NQ9433 | Sub, Julia Creek No.10 SWER - NELIA | JCS84 | JCS84 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | SP-149652 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | #N/A | #N/A | 2023-07-24 | 1856776 | EFM Equipment Failure or Malfunction |  | EECL | Forced Regulated | NQFR | North Queensland | 19kV | EFM Equipment Failure or Malfunction | M0209 | M0001 | M9999 |  | H | Operational | JULIA CREEK | OT190149 |  | OT190149 | 202307
2023-07-25 |  | 2023-07-27 | TDDI | Transformer-Distribution | Closed |  |  | 2023-07-25 | 2023-07-01 | SARINA | EECL | NS | Network Site | XLFPS | 1858179 |  |  | 23/24 | 2024-01-25 | HV | 2023-07-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-07-25 23:02 | F-1687-q 11kV Pole Dist Sub 3703 lod bangs x 2 multiple calls from sub area. Crew replaced blown 11kV 200amp transformer and replaced 1 x road span of open wire vertical construction. SL 4041822. (S Gregory). | 2023-07-25 | FRESHWATER POINT: MIRAN KHAN DR | Distribution Event | Normal Event | 11kV Pole Dist Sub 3703 lod bangs x 2 multiple calls from thos sub area. Sending Asset Event to FFA FFA Order Created F-AE23MK6184-1-0 DfltHost FFA Order Acknowledged F-AE23MK6184-1-0 saroc01 Troy von snarski 0418196550 FFA Order En Route F-AE23MK6184-1-0 saroc01 FFA Order On Site F-AE23MK6184-1-0 saroc01 Time On modified from 23:59 25-Jul to 01:30 26-Jul Sending Asset Event to FFA Sending Asset Event to FFA Crew have advised Oncall supervisor Ian Rix has postponed jod until 05:00 hrs 26/07/2023. Sending Asset Event to FFA Time On modified from 01:30 26-Jul to 02:30 26-Jul Sending Asset Event to FFA Time On modified from 02:30 26-Jul to 08:00 26-Jul Sending Asset Event to FFA FFA Order Suspended F-AE23MK6184-1-0 by Troy von snarski 0418196550 out of hour. isolated and gear collected for day crew to complete work Undre access to replace Transformer Time On modified from 08:00 26-Jul to 08:30 26-Jul Sending Asset Event to FFA Time On modified from 08:30 26-Jul to 08:45 26-Jul Sending Asset Event to FFA Time On modified from 08:45 26-Jul to 09:30 26-Jul Sending Asset Event to FFA Time On modified from 09:30 26-Jul to 09:50 26-Jul Sending Asset Event to FFA Crews advised a lot of extra work required. Time On modified from 09:50 26-Jul to 12:00 26-Jul Sending Asset Event to FFA Awaiting ACO to sign off Time On modified from 12:00 26-Jul to 14:00 26-Jul Sending Asset Event to FFA Time On modified from 14:00 26-Jul to 15:00 26-Jul Sending Asset Event to FFA Time On modified from 15:00 26-Jul to 13:59 26-Jul Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23MK6184-1-0 saroc01 FFA Order On Site F-AE23MK6184-1-0 saroc01 FFA Order F-AE23MK6184-1-0 Completed by technician ROSS WALL in crew SAROC01(0438144033) with code A-T-303 - Distribution substation Action Taken : Replaced blown 11kv 200 amp transformer and replaced 1 x road span of open wire vertical construction Site Label : 4041822 Time On modified from 13:59 26-JUL to 14:30 26-JUL Updated Reasons tab. Reason for Event changed from HV or LV Fuse blown | Valid | 23MK6184 |  | CAVARAN PARK | 3703 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS4041822 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -21.44536590576170 | 149.284881591797 | 2023-07-25 | 1857075 | MR J COHEN | O - Other | EECL | Transformers Return to Service | D2002 | Mackay | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | SARINA | OT190320 | Technician: ROSS WALL Comments | OT190320 | 202307
2023-07-26 |  | 2023-08-10 | TDDI | Transformer-Distribution | Closed |  |  | 2023-07-26 | 2023-07-01 | ATHERTON | EECL | NS | Network Site | XLTNA | 1283695 |  |  | 23/24 | 2024-01-26 | HV | 2023-07-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-07-26 16:50 | Fault occurred at:26/07/2023 16:49; Damien Small, 0438764428; >DFL --> StartedWithinPastWeek:YES -- LightsDimUnderLoad:NO -- -- NeighboursAffected:UNSURE -- OccursSameTimeEachDay:NO<; Incident Details:flickering power on one phase. All breakers on at s/board. No COVID-19 advises; Warnings[dflSafety, dflTurnOffAppliances]: ADVISED | 2023-07-26 | 1 STONEHOUSE RD;EAST BARRON QLD 4883 | Distribution Event | Normal Event |  | Valid | 23FN10876 |  | GODFREY | SS280 |  | Unknown | Completed | Unplanned Outage | Wet / Rain | NS2127448 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -17.36931800842290 | 145.538772583008 | 2023-07-26 | 1857287 | T/AS D & D LIVESTOCK | O - Other | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | G | Capital | ATHERTON 2 | OT190442 | Technician: Glen Webley Comments quality of supply required before suspect tax changed out | OT190442 | 202307
2023-08-04 |  | 2023-08-05 | TDDI | Transformer-Distribution | Closed |  |  | 2023-08-04 | 2023-08-01 | WINTON | EECL | NS | Network Site | XCPNW | 1798144 |  |  | 23/24 | 2024-02-04 | HV | 2023-08-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | HV-Unassisted failure(Apparent defect) | 2023-08-04 17:45 | F-519-t Transformer Faulty. | 2023-08-04 | WINTON: BENDEMEER STATION | Distribution Event | Normal Event | Transformer Faulty. Sending Asset Event to FFA FFA Order Created F-AE23NQ9804-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ9804-1-0 wntcsfr03 Kirk harrold 0427893349 Time On modified from 23:59 05-Aug to 20:04 05-Aug Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23NQ9804-1-0 wntcsfr03 FFA Order On Site F-AE23NQ9804-1-0 wntcsfr03 FFA Order F-AE23NQ9804-1-0 Completed by technician Kirk harrold in crew wntcsfr03(0427893349) with code A-T-303 - Distribution substation Action Taken : Replaced blown TX, EDO and removed exiting pole circuit breaker and fused service Site Label : 5066184 | Valid | 23NQ9804 | Elderslie SWER No.01 feeder section B | ELDERSLIESWER NO.01-MTCAMPBELL NO.01 ACR | EL-01B |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS5066184 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -21.89541625976560 | 142.416564941406 | 2023-08-04 | 1858991 | J G NICHOLS | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | North Queensland | 19kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | H | Capital | WINTON | OT191320 | Technician: Kirk harrold Comments | OT191320 | 202308
2023-08-13 |  | 2023-08-13 | TDDI | Transformer-Distribution | Closed |  |  | 2023-08-13 | 2023-08-01 | INGHAM | EECL | NS | Network Site | XCHBG | 1618781 |  |  | 23/24 | 2024-02-13 | HV | 2023-08-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-08-13 14:57 | INS231 Failed TX, requires access to replace. John Gallon advised | 2023-08-13 | HALIFAX: MONA RD, VELLA'S RD | Distribution Event | Normal Event | INS231 Failed TX, requires access to replace. John Gallon advised Sending Asset Event to FFA FFA Order Created F-AE23NQ10066-1-0 DfltHost FFA Order Pending F-AE23NQ10066-1-0 Time On modified from 23:59 13-Aug to 20:00 13-Aug Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ10066-1-0 ingcs02 John Gallon 0400892791 FFA Order En Route F-AE23NQ10066-1-0 ingcs02 FFA Order On Site F-AE23NQ10066-1-0 ingcs02 Time On modified from 20:00 13-Aug to 18:37 13-Aug Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23NQ10066-1-0 Completed by technician John Gallon in crew ingcs02(0400892791) with code A-T-303 - Distribution substation Action Taken : Replace TX After Hours Call Site Label : 5077290 Actual Power Restoration for F-AE23NQ10066-1-0: 13-AUG-2023 19:17:00 auto-completed | Valid | 23NQ10066 | Sub, Macknade No.04 11kV feeder | INS231 | INS231 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS5077290 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -18.55942153930660 | 146.281234741211 | 2023-08-13 | 1860463 | SOUTHPEAK PASTORAL CO PTY. LTD | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | North Queensland | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | INGHAM | OT192176 | Technician: John Gallon Comments | OT192176 | 202308
2023-08-15 |  | 2023-08-15 | TDDI | Transformer-Distribution | Closed |  |  | 2023-08-15 | 2023-08-01 | MURGON | EECL | NS | Network Site | XCFBR | 1371315 |  |  | 23/24 | 2024-02-15 | HV | 2023-08-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2023-08-02 12:51 | Crew advised during a re connect after form B, 11kV Pole Dist Sub 3911 EDO's were open, tired reclose and failed. TX requires replacement. EDO's currently open | 2023-08-02 | N/A | Distribution Event | Normal Event | Crew advised during a re connect after form B, 11kV Pole Dist Sub 3911 EDO's were open, tired reclose and failed. TX requires replacement. EDO's currently open Time On modified from 23:59 02-Aug to 12:00 16-Aug Crew advised approx 2 weeks until repairs. Darren Miller emailed with fault details u Time On modified from 12:00 16-Aug to 12:00 14-Aug 23WB11425 ust to install new tx 3911 | Valid | 23WB11364 |  | 3911 | 3911 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS2074629 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -26.03104591369630 | 151.814544677734 | 2023-08-15 | 1860745 | EFM Equipment Failure or Malfunction |  | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | MURGON | OT192305 | Technician: Richie Trunks Comments Transformer failed in service. Has been replaced. | OT192305 | 202308
2023-09-01 |  | 2023-09-01 | TDDI | Transformer-Distribution | Closed |  |  | 2023-09-01 | 2023-09-01 | HERVEY BAY | EECL | NS | Network Site | XLFBH | 1331006 |  |  | 23/24 | 2024-03-01 | HV | 2023-09-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2023-09-01 02:39 | Crew require access to TX after MRC unsuccessful @ 11kV Pole Dist Sub 8166 Crew replaced 11kV 315kVA transformer. SL 3300457. (S Gregory). | 2023-09-01 | PIALBA: BEACH RD, NEWHAVEN ST, OLD MARYBOROUGH RD | Distribution Event | Normal Event | Crew require access to TX after MRC unsuccessful @ 11kV Pole Dist Sub 8166 Sending Asset Event to FFA FFA Order Created F-AE23WB12271-1-0 DfltHost FFA Order Acknowledged F-AE23WB12271-1-0 hboc01 Rhys Murphy 0438186466 FFA Order En Route F-AE23WB12271-1-0 hboc01 FFA Order On Site F-AE23WB12271-1-0 hboc01 crew to replace TX Reason for Event changed from HV or LV Fuse blown Sending Asset Event to FFA Time On modified from 23:59 01-Sep to 08:59 01-Sep Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23WB12271-1-0 Completed by technician Rhys Murphy in crew hboc01(0438186466) with code A-T-303 - Distribution substation Action Taken : Replace Blown 11kV 315kVA Transformer Site Label : 3300457 Time On modified from 08:59 01-SEP to 09:04 01-SEP Added notes to Reasons tab. | Invalid | 23WB12271 |  | OLD MARYBOROUGH RD | 8166 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS3300457 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -25.28344154357910 | 152.831253051758 | 2023-09-01 | 1864096 | MISS D HAMMOND | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | J | Capital | HERVEY BAY 2 | OT194096 | Technician: Rhys Murphy Comments | OT194096 | 202309
2023-09-13 |  | 2023-09-15 | TDDI | Transformer-Distribution | Closed |  |  | 2023-09-13 | 2023-09-01 | ISLAND COMM | EECL | NS | Network Site | XLTNG | 1155067 |  |  | 23/24 | 2024-03-13 | HV | 2023-09-01 |  | Corrosion | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-09-13 09:06 | 22kV Pole Dist Sub SS7239 broken down lead on TX | 2023-09-13 | HAMMOND ISLAND: HAMMOND 1 ST | Distribution Event | Normal Event | 22kV Pole Dist Sub SS7239 broken down lead on TX Crews isolate on HV only, customer has personal gen set. crews will repair on 15/09 F-1932-s Sending Asset Event to FFA FFA Order Created F-AE23FN12596-1-0 DfltHost . Time On modified from 23:59 13-Sep to 23:59 15-Sep Sending Asset Event to FFA . Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN12596-1-0 thics01 Scott 0408672666 FFA Order En Route F-AE23FN12596-1-0 thics01 FFA Order On Site F-AE23FN12596-1-0 thics01 FFA Order Suspended F-AE23FN12596-1-0 by Scott 0408672666 FFA Order En Route F-AE23FN12596-1-0 thics01 FFA Order On Site F-AE23FN12596-1-0 thics01 FFA Order F-AE23FN12596-1-0 Completed by technician Scott in crew thics01(0408672666) with code A-T-303 - Distribution substation Action Taken : Replace HV Down leads @ SS7239. Emergency switching. All ok. Site Label : 5209213 Time On modified from 23:59 15-SEP to 12:30 15-SEP FFA Order F-AE23FN12596-1-0 Completed by technician Scott in crew thics01(0408672666) with code A-T-303 - Distribution substation Action Taken : Replace HV Down leads @ SS7239. Emergency switching. All ok. Site Label : 5209213 Time On modified from 23:59 15-SEP to 12:30 15-SEP Time On modified from 23:59 15-Sep to 12:35 15-Sep | Valid | 23FN12596 |  | AMSA BUNKER | SS7239 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wind | NS5209213 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | #N/A | #N/A | 2023-09-13 | 1866447 | SITE VACANT | U - Unknown / No Power | EECL | Forced Regulated (Isolated Distribution) | DFFR | Far North | 22kV | SITE VACANT | M0209 | M0052 | M0011 |  | G | Operational | THURSDAY ISLAND | OT195463 | Technician: Scott Comments | OT195463 | 202309
2023-09-23 |  | 2023-09-24 | TDDI | Transformer-Distribution | Closed |  |  | 2023-09-23 | 2023-09-01 | INNISFAIL | EECL | NS | Network Site | XLTNI | 1183855 |  |  | 23/24 | 2024-03-23 | HV | 2023-09-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-09-23 18:59 | Replace TX 22kV Pole Dist Sub SS6648 | 2023-09-23 | BELLENDEN KER: BRUCE HWY | Distribution Event | Normal Event | Replace TX 22kV Pole Dist Sub SS6648 Sending Asset Event to FFA FFA Order Created F-AE23FN12942-1-0 DfltHost Sending Asset Event to FFA Time On modified from 23:59 23-Sep to 02:00 24-Sep Sending Asset Event to FFA Time On modified from 02:00 24-Sep to 00:23 24-Sep Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN12942-1-0 insoc01 Dan Colls 0437304684 FFA Order En Route F-AE23FN12942-1-0 insoc01 FFA Order On Site F-AE23FN12942-1-0 insoc01 FFA Order F-AE23FN12942-1-0 Completed by technician Dan Colls in crew INSOC01(0437304684) with code A-T-303 - Distribution substation Action Taken : Replaced faulty 25 kVa transformer. Site Label : 5094200 Actual Power Restoration for F-AE23FN12942-1-0: 24-SEP-2023 00:44:00 auto-completed | Invalid | 23FN12942 |  | LAURIDSEN | SS6648 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS5094200 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -17.291618347168 | 145.925735473633 | 2023-09-23 | 1868537 | MR A M ERWOOD | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | G | Capital | INNISFAIL 1 | OT196596 | Technician: Dan Colls Comments | OT196596 | 202309
2023-09-26 |  | 2023-09-28 |  |  | Closed |  |  | 2023-09-26 | 2023-09-01 | ROCKHAMPTON | EECL | FD | Feeder | XLFPR | 25445 |  |  | 23/24 | 2024-03-26 | HV | 2023-09-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2023-09-26 19:02 | F-28246-g - FREN- FV-S106 Transformer 22626 fault Crew replaced 11kV Pole Dist Sub 22626 and EDOS. SL 4256730. (S Gregory). | 2023-09-26 | KAWANA, NORMAN GARDENS | Distribution Event | Normal Event | entered from the SCADA Interface Depot Co-ord Advised CCOC01 Sending Asset Event to FFA FFA Order Created F-AE23CA13793-1-0 DfltHost OC Trip to lock out. 66kV F6006 Diff Trip and reclose at the same time Sending Asset Event to FFA Sending Asset Event to FFA crew patrolling Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA13793-1-0 ccoc01 crew have finished patrol and no additional damage to 11kV Feeder or 66kV Feeder above. damage to 11kV Pole Dist Sub 22626 only Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 26-Sep to 23:59 27-Sep Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA 11kV Pole Dist Sub 22626 to be replaced 27/09 Sending Asset Event to FFA Contractor enquiry about on-going outage to 8 MACNEVIN ST NORMAN GARDENS tx 22626, mental health facility with 80 persons onsite. Passed onto co-ord, investigating options. Contractor contact info - Phil Benson, ph 0418 156 427. Sending Asset Event to FFA Crew on LLW to Replace HV Fuses, then onto Acces to replace TX Sending Asset Event to FFA Time On modified from 23:59 27-Sep to 11:55 27-Sep Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23CA13793-1-0 ccoc01 FFA Order On Site F-AE23CA13793-1-0 ccoc01 FFA Order F-AE23CA13793-1-0 Completed by technician Reid Shepherd in crew ccoc01(0418380394) with code A-T-303 - Distribution substation Action Taken : replaced TX and EDO’s Site Label : 4256730 Added notes to Reasons tab. | Invalid | 23CA13793 | FREN-RICHARDSON | Richardson Rd | FV106 | FV-S106 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | FD-1428 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | #N/A | #N/A | 2023-09-26 | 1869129 | U Unknown |  | EECL | Forced Regulated | CEFR | Capricornia | 11kV | U Unknown | M0209 | M0001 | M9999 |  | J | Operational | ROCKHAMPTON 3 | OT196948 |  | OT196948 | 202309
2023-09-26 |  | 2023-09-26 | TDDI | Transformer-Distribution | Closed |  |  | 2023-09-26 | 2023-09-01 | SARINA | EECL | NS | Network Site | XLFPS | 1467111 |  |  | 23/24 | 2024-03-26 | HV | 2023-09-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-09-26 01:02 | 12.7kV SWER Pole Dist Sub 4682 - Crews confirmed TX faulty, requires replacement during depot hrs | 2023-09-26 | BLUE MOUNTAIN: BLUE MOUNTAIN RD | Distribution Event | Normal Event | 12.7kV SWER Pole Dist Sub 4682 - Crews confirmed TX faulty, requires replacement during depot hrs F-629-t Steve Gutschlag aware and organising crews Crews sourcing Tx from Mackay before attending to job Sending Asset Event to FFA FFA Order Created F-AE23MK7747-1-0 DfltHost SEAN MC WATERS ON SARFR03 Sending Asset Event to FFA FFA Order Acknowledged F-AE23MK7747-1-0 sarfr03 Sean McWaters 0456941523 FFA Order En Route F-AE23MK7747-1-0 sarfr03 FFA Order On Site F-AE23MK7747-1-0 sarfr03 Time On modified from 23:59 26-Sep to 13:47 26-Sep Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23MK7747-1-0 Completed by technician Sean McWaters in crew sarfr03(0456941523) with code A-T-303 - Distribution substation Action Taken : replaced 10kva 12.7kv swer transformer Site Label : 2035913 Actual Power Restoration for F-AE23MK7747-1-0: 26-SEP-2023 14:07:00 | Valid | 23MK7747 |  | PARRY | 4682 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS2035913 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -21.59092330932620 | 149.038818359375 | 2023-09-26 | 1868886 | MR L PARRY | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Mackay | 12.7kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | I | Capital | SARINA | OT196822 | Technician: Sean McWaters Comments | OT196822 | 202309
2023-09-28 |  | 2023-09-28 | TDDI | Transformer-Distribution | Closed |  |  | 2023-09-28 | 2023-09-01 | CLERMONT | EECL | NS | Network Site | XCPNC | 1609325 |  |  | 23/24 | 2024-03-28 | HV | 2023-09-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2023-09-28 17:22 | F-1880-q - CL204 -22kV Dropout Fuse S8748 have operated as 22kV Pole Dist Sub 338520 requires replacement | 2023-09-28 | CAPELLA: PRIMARY RD | Distribution Event | Normal Event | 22kV Dropout Fuse S8748 have operated as 22kV Pole Dist Sub 338520 requires replacement CLMCS02 Sending Asset Event to FFA FFA Order Created F-AE23CA13916-1-0 DfltHost Primary Asset de-escalated from Gregory Hwy (FC) Sending Asset Event to FFA Time On modified from 23:59 28-Sep to 22:30 28-Sep Sending Asset Event to FFA Time On modified from 22:30 28-Sep to 22:23 28-Sep Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA13916-1-0 clmcs02 MICHAEL CRISP 0456174588 FFA Order En Route F-AE23CA13916-1-0 clmcs02 FFA Order On Site F-AE23CA13916-1-0 clmcs02 Sending Asset Event to FFA FFA Order F-AE23CA13916-1-0 Completed by technician MICHAEL CRISP in crew clmcs02(0456174588) with code A-T-303 - Distribution substation Action Taken : replaced faulty transformer Site Label : 4046187 | Invalid | 23CA13916 |  | S8748 | S8748 | S8748 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS4046187 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -23.08357620239260 | 148.015106201172 | 2023-09-28 | 1869560 | CENTRAL HIGHLANDS REGIONAL COU | O - Other | EECL | Transformers Return to Service | D2002 | Capricornia | 22kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | G | Capital | CLERMONT | OT197183 | Technician: MICHAEL CRISP Comments | OT197183 | 202309
2023-09-30 |  | 2023-10-01 | TDDI | Transformer-Distribution | Closed |  |  | 2023-09-30 | 2023-09-01 | CLERMONT | EECL | NS | Network Site | XCPNC | 1609325 |  |  | 23/24 | 2024-03-30 | HV | 2023-09-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2023-09-30 16:59 | F-948-r - Crew require to replace 22kV Pole Dist Sub 338520 down stream from 22kV Dropout Fuse S8748 | 2023-09-30 | CAPELLA: PRIMARY RD | Distribution Event | Normal Event | Crew require to replace 22kV Pole Dist Sub 338520 down stream from 22kV Dropout Fuse S8748 clmcs02 Sending Asset Event to FFA FFA Order Created F-AE23CA13962-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA13962-1-0 clmcs02 Michael Crisp 0456174588 FFA Order En Route F-AE23CA13962-1-0 clmcs02 FFA Order On Site F-AE23CA13962-1-0 clmcs02 Time On modified from 23:59 01-Oct to 12:00 01-Oct Sending Asset Event to FFA FFA Order F-AE23CA13962-1-0 Completed by technician Michael Crisp in crew clmcs02(0456174588) with code A-T-303 - Distribution substation Action Taken : replaced faulty transformer like for like Site Label : 4046187 auto-completed | Valid | 23CA13962 |  | S8748 | S8748 | S8748 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS4046187 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -23.08357620239260 | 148.015106201172 | 2023-09-30 | 1869848 | CENTRAL HIGHLANDS REGIONAL COU | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | Capricornia | 22kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | G | Capital | CLERMONT | OT197401 | Technician: Michael Crisp Comments | OT197401 | 202309
2023-10-01 |  | 2023-10-01 | TDDI | Transformer-Distribution | Closed |  |  | 2023-10-01 | 2023-10-01 | INNISFAIL | EECL | NS | Network Site | XLTNI | 1179918 |  |  | 23/24 | 2024-04-01 | HV | 2023-10-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-10-01 06:11 | F-646-t - Mick Andrews advised TX SS2816 requires replacement from F/C 2366737 | 2023-10-01 | BABINDA: BRUCE HWY, NELSON RD PALMA SIDING: BABINDA ST, BRUCE HWY, NELSON RD | Distribution Event | Normal Event | Mick Andrews advised TX SS2816 requires replacement from F/C 2366737 Please send to Mick Andrews insoc01 Sending Asset Event to FFA FFA Order Created F-AE23FN13169-1-0 DfltHost Sending Asset Event to FFA Time On modified from 23:59 01-Oct to 10:32 01-Oct Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN13169-1-0 insoc01 Mick Andrews 0419414924 FFA Order En Route F-AE23FN13169-1-0 insoc01 FFA Order On Site F-AE23FN13169-1-0 insoc01 FFA Order F-AE23FN13169-1-0 Completed by technician Mick Andrews in crew insoc01(0419414924) with code A-T-303 - Distribution substation Action Taken : Replace transformer SS2816 Site Label : 5094142 Actual Power Restoration for F-AE23FN13169-1-0: 01-OCT-2023 11:59:00 | Invalid | 23FN13169 |  | PALMA NO 2 | SS2816 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS5094142 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -17.32505729668440 | 145.928348887517 | 2023-10-01 | 1869884 | MISS R BUHAGIAR | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | G | Capital | INNISFAIL 1 | OT197425 | Technician: Mick Andrews Comments | OT197425 | 202310
2023-10-01 |  | 2023-10-01 | TDDI | Transformer-Distribution | Closed |  |  | 2023-10-01 | 2023-10-01 | MILLMERRAN | EECL | NS | Network Site | XCGDI | 1489403 |  |  | 23/24 | 2024-04-01 | HV | 2023-10-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2023-10-01 08:21 | F-2007-s 11kV Pole Dist Sub PE04213 Transformer is faulty and needs to be replaced. | 2023-10-01 | KINCORA: SCHOOL RD | Distribution Event | Normal Event | 11kV Pole Dist Sub PE04213 Transformer is faulty and needs to be replaced. Sending Asset Event to FFA FFA Order Created F-AE23SW17812-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 01-Oct to 16:00 01-Oct Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW17812-1-0 twmoc03 David Balmer 0415309502 FFA Order En Route F-AE23SW17812-1-0 twmoc03 FFA Order On Site F-AE23SW17812-1-0 twmoc03 FFA Order F-AE23SW17812-1-0 Completed by technician David Balmer in crew twmoc03(0415309502) with code A-T-303 - Distribution substation Action Taken : replaced blown transformer Site Label : 6011607 Time On modified from 16:00 01-OCT to 15:17 01-OCT | Valid | 23SW17812 | Mansbridge, Kincora | PE04213 | PE04213 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS6011607 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -27.80955314636230 | 151.568542480469 | 2023-10-01 | 1869900 | MS N MARSHAM | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | South West | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | MILLMERRAN | OT197436 | .HEADING Technician: David Balmer Comments Technician: David Balmer Comments | OT197436 | 202310
2023-10-05 |  | 2023-10-05 | TDDI | Transformer-Distribution | Closed |  |  | 2023-10-05 | 2023-10-01 | CHINCHILLA | EECL | NS | Network Site | XCGDH | 990706 |  |  | 23/24 | 2024-04-05 | HV | 2023-10-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2023-10-05 10:51 | F-1916-q - 33kV Disc Links DL17645 has operated (Fuse) | 2023-10-05 | WARRA: WARRA KOGAN RD | Distribution Event | Normal Event | 33kV Disc Links DL17645 has operated (Fuse) Manual Reclose Checklist DLBCS02 Sending Asset Event to FFA FFA Order Created F-AE23SW17994-1-0 DfltHost FFA Order Acknowledged F-AE23SW17994-1-0 dlbcs02 Mick Markey 0436452828 FFA Order En Route F-AE23SW17994-1-0 dlbcs02 FFA Order On Site F-AE23SW17994-1-0 dlbcs02 FFA Order F-AE23SW17994-1-0 Completed by technician Mick Markey in crew dlbcs02(0436452828) with code A-T-303 - Distribution substation Action Taken : Replaced blown TX. Site Label : 3097255 Time On modified from 23:59 05-Oct to 21:18 05-Oct | Valid | 23SW17994 |  | 17645 | 17645 | 17645 | HV or LV Fuse blown | Completed | Unplanned Outage | Fine | NS3097255 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -26.94596862792970 | 150.878997802734 | 2023-10-05 | 1870752 | PASTORAL PROPERTIES (CROPPING) | P - Phase Down (LV) | EECL | Transformers Return to Service | D2002 | South West | 33kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | F | Capital | DALBY 1 | OT197959 | Technician: Mick Markey Comments | OT197959 | 202310
2023-10-10 |  | 2023-10-11 | TDDI | Transformer-Distribution | Closed |  |  | 2023-10-10 | 2023-10-01 | M'LAND COMM | EECL | NS | Network Site | XLTNG | 9010530 |  |  | 23/24 | 2024-04-10 | HV | 2023-10-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2023-10-10 13:50 | Doomagee Fdr 4 Tripped on O/C after Outage 23FN12933 Crews adv will Isolate some LV's of Subs and Close and try to restore in sections After fault finding crews found 22kV Pole Dist Sub SP861058 had faulty LAs - Asset extracted from this event and transformer will be replaced under 23FN13498. (S Gregory). | 2023-10-10 | DOOMADGEE: BURKE ST, CANTEL ST, DOUGLAS RD, NEW ESTATE RD | Distribution Event | Normal Event | Doomagee Fdr 4 Tripped on O/C after Outage 23FN12933 Crews adv will Isolate some LV's of Subs and Close and try to restore in sections Asset selection modified Asset selection modified Asset selection modified Asset selection modified Asset selection modified Replay sequence/s deleted after 10-OCT-23 16:33:06 Asset selection modified Asset selection modified Asset selection modified Asset selection modified Assets extracted from SP861058 (Off Cantle St) into event 23FN13498 Time On modified from 23:59 10-Oct to 18:37 10-Oct Feeder tripped after planned event 23FN12933, after fault finding crews found SP861058 had faulty LA's, sub extracted from event and crews to return tomorrow to replace TX. Reason for Event changed from Protective Device Operated Updated Reasons tab. Updated Event Trigger from HV-Unassisted failure to Distribution substation. | Valid | 23FN13483 | DOOM-DOOMADGEE 4 | DOOMADGEE NO 4 | 2DO4 | 2DO4 ROBERT ST STEP-UP | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS11755522 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2023-10-10 | 1871818 | PROT Protective Device Operated |  | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | G | Capital | NORMANTON | OT198565 | Technician: Dave Manthey Comments | OT198565 | 202310
2023-10-13 |  | 2023-10-14 |  |  | Closed |  |  | 2023-10-13 | 2023-10-01 | TOWNSVILLE | EECL | NT | Network Slot | XLHBT | 2279321 |  |  | 23/24 | 2024-04-13 | HV | 2023-10-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2023-10-13 20:00 | TVS2047. Crew advised requires replacement Brock Bezanson Found with HV Fuses down. Transformer US | 2023-10-13 | N/A | Distribution Event | Normal Event | TVS2047. Crew advised requires replacement Brock Bezanson Found with HV Fuses down. Transformer US. Please send to Brock Bezanson Sending Asset Event to FFA FFA Order Created F-AE23NQ12291-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ12291-1-0 twvoc01 Brock Bezanson 0455524351 FFA Order En Route F-AE23NQ12291-1-0 twvoc01 FFA Order On Site F-AE23NQ12291-1-0 twvoc01 FFA Order F-AE23NQ12291-1-0 Completed by technician Brock Bezanson in crew twvoc01(0455524351) with code A-T-303 - Distribution substation Action Taken : replace old transformer due to failure in service. like for like. Site Label : TVS 2047 Time On modified from 16:00 14-OCT to 11:44 14-OCT | Invalid | 23NQ12291 | Lot 2 Haberecht Rd | TVS2047 | TVS2047 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | SP-110905 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | #N/A | #N/A | 2023-10-13 | 1872564 | EFM Equipment Failure or Malfunction |  | EECL | Transformers Return to Service | D2002 | North Queensland | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | TOWNSVILLE RR | OT198943 | ToughPad Location: Site Label Entered:TVS 2047 Component: TDDI Component Mod: OC Technician: Brock Bezanson Comments | OT198943 | 202310
2023-10-15 |  | 2023-10-16 |  |  | Closed |  |  | 2023-10-15 | 2023-10-01 | PROSERPINE | EECL | FC | Feeder Section | XLHBP | 5357821 |  |  | 23/24 | 2024-04-15 | HV | 2023-10-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2023-10-15 23:46 | LAGUNA QUAYS 11kV O Connell R ACR CB tripped. SCADA Interface automated outage. | 2023-10-15 | ANDROMACHE, BLOOMSBURY, LETHEBROOK, PROSERPINE, THOOPARA | Distribution Event | Normal Event | entered from the SCADA Interface Time On modified from 23:59 15-Oct to 23:59 16-Oct Luke Read 0436 069 696 Sending Asset Event to FFA FFA Order Created F-AE23MK8180-1-0 DfltHost FFA Order Acknowledged F-AE23MK8180-1-0 prpoc01 FFA Order En Route F-AE23MK8180-1-0 prpoc01 FFA Order On Site F-AE23MK8180-1-0 prpoc01 Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA WGL adv job to happen this arvo. Restore time to be updated once crew are on access. Sending Asset Event to FFA Time On modified from 23:59 16-Oct to 20:22 16-Oct Sending Asset Event to FFA FFA Order F-AE23MK8180-1-0 Completed by technician LUKE READ in crew PRPOC01() with code A-T-303 - Distribution substation Action Taken : replaced 63 KVA SUB Site Label : 3529 auto-completed | Invalid | 23MK8180 | Unknown | OCONNELL RIVER RECLOSER | O'CONNELL RIVER | O'CONNELL RIVER RECLOSER | Unknown | Completed | Unplanned Outage | Fine | FC-11-86813 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | #N/A | #N/A | 2023-10-15 | 1872754 | U Unknown |  | EECL | Transformers Return to Service | D2002 | Mackay | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | PROSERPINE | OT199119 | ToughPad Location: Site Label Entered:3529 Component: TDDI Component Mod: OC Technician: LUKE READ Comments | OT199119 | 202310
2023-10-16 |  | 2023-11-30 |  |  | Closed |  |  | 2023-10-16 | 2023-10-01 | CUNNAMULLA | EECL | NT | Network Slot | XCGDU | 2241355 |  |  | 23/24 | 2024-04-16 | HV | 2023-10-01 |  | Unknown | Damaged | Reactor, Unknown | Outage | South | HV-Unassisted failure(Apparent defect) | 2023-10-16 18:04 | F-1947-q - 19.1kV SWER HV Fuse DL874086 has operated. scorch mark on 19.1kV SWER Reactor Sub PW03349 | 2023-10-16 | CUNNAMULLA: WIDGEEGOARA RD | Distribution Event | Normal Event | 19.1kV SWER HV Fuse DL874086 has operated. scorch mark on 19.1kV SWER Reactor Sub PW03349 cuncmfr03 Time On modified from 23:59 17-Oct to 09:21 17-Oct Sending Asset Event to FFA FFA Order Created F-AE23SW18409-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW18409-1-0 cuncmfr03 Phil Boshoff 0436486711 FFA Order En Route F-AE23SW18409-1-0 cuncmfr03 FFA Order On Site F-AE23SW18409-1-0 cuncmfr03 FFA Order F-AE23SW18409-1-0 Completed by technician Phil Boshoff in crew cuncmfr03(0436486711) with code A-T-315 - Service Asset Fault Action Taken : 19.1kv reactor faulty Site Label : 4162536 | Invalid | 23SW18409 | CAMDEN, SPONSTON, CAMDEN RD, NOORAMA QL | Camden SWER Recloser | CB604381 | DL874086 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Hot | SP-181294 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | #N/A | #N/A | 2023-10-16 | 1873008 | MR B BIGNELL | N - Neighbours Out as Well | EECL | Forced Regulated | SWFR | South West | 19kV | MR B BIGNELL | M0400 | M0052 | M9999 |  | H | Operational | CUNNAMULLA | OT199266 |  | OT199266 | 202310
2023-10-18 |  | 2023-10-18 | TDDI | Transformer-Distribution | Closed |  |  | 2023-10-18 | 2023-10-01 | COOKTOWN | EECL | NS | Network Site | XCTNO | 1123792 |  |  | 23/24 | 2024-04-18 | HV | 2023-10-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2023-10-18 06:21 | Crew replaced failed in service 315kVA 22kV Pole Dist Sub SS764. SL 5169959. (S Gregory). | 2023-10-18 | COOKTOWN: BANKS ST, CHARLOTTE ST, FLINDERS ST, HELEN ST, HILL ST, WEBBER ESP | Distribution Event | Normal Event | Multiple calls in for 22kV Pole Dist Sub SS764 for phase down Crews attending: Steve Johnson 0409 279 877 cktcsfr02. Sending Asset Event to FFA FFA Order Created F-AE23FN13831-1-0 DfltHost FFA Order Acknowledged F-AE23FN13831-1-0 cktcsfr02 Steven Johnson 0409279877 FFA Order En Route F-AE23FN13831-1-0 cktcsfr02 FFA Order On Site F-AE23FN13831-1-0 cktcsfr02 Crews have attended and have found that TX is cactus and requires replacing - Crews require access to the HV EDO's only Sending Asset Event to FFA Time On modified from 23:59 18-Oct to 11:30 18-Oct Sending Asset Event to FFA F-2080-s, Steve Johnson to attend Sending Asset Event to FFA Time On modified from 11:30 18-Oct to 10:42 18-Oct Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23FN13831-1-0 Completed by technician Steven Johnson in crew cktcsfr02(0409279877) with code A-T-303 - Distribution substation Action Taken : Replaced FIS 315kVA transformer - SS764 Site Label : 5169959 Time On modified from 10:42 18-OCT to 10:46 18-OCT Updated Reasons tab. Updated Event Trigger from HV-CCF to Distribution substation. Reason for Event changed from HV or LV Fuse blown | Invalid | 23FN13831 |  | Endeavour Park, Charlotte St | SS764 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS5169959 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -15.46346855163570 | 145.250122070312 | 2023-10-18 | 1873279 | RUSSLEE PTY LTD | P - Phase Down (LV) | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | G | Capital | COOKTOWN | OT199431 | Technician: Steven Johnson Comments | OT199431 | 202310
2023-10-22 |  | 2023-10-22 | RGDI | Regulator-Distribution | Closed |  |  | 2023-10-22 | 2023-10-01 | KILKIVAN | EECL | NS | Network Site | XCFBK | 1011367 |  |  | 23/24 | 2024-04-22 | HV | 2023-10-01 |  | Unknown | Damaged | Regulator, Unknown | Outage | South | HV-Unassisted failure(Apparent defect) | 2023-10-22 19:14 | Bells Bridge Feeder 11kV CB A452 appears to have a burnt off bridge Crew bypassed 11kV Regulator 15290 after finding blown surge arrestor. SL 3051860. (S Gregory). | 2023-10-22 | BELLS BRIDGE, CURRA, LOWER WONGA, WIDGEE | Distribution Event | Normal Event | Bells Bridge Feeder 11kV CB A452 appears to have a burnt off bridge kkvcsfr01 Sending Asset Event to FFA FFA Order Created F-AE23WB13787-1-0 DfltHost FFA Order Acknowledged F-AE23WB13787-1-0 kkvcsfr01 Ty Farrow 0417449186 FFA Order En Route F-AE23WB13787-1-0 kkvcsfr01 FFA Order On Site F-AE23WB13787-1-0 kkvcsfr01 Time On modified from 23:59 22-Oct to 21:32 22-Oct Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23WB13787-1-0 kkvcsfr01 FFA Order On Site F-AE23WB13787-1-0 kkvcsfr01 FFA Order F-AE23WB13787-1-0 Completed by technician Ty Farrow in crew kkvcsfr01(0417449186 ) with code A-T-304 - HV-Conductor Connection Failure Action Taken : bypassed regs15290. found blown surge arrestor on a tank of the regulators. will require Syscon being raised to repair regs Site Label : 3051860 Reason for Event changed from Unknown Updated Reasons tab. Updated Event Trigger from HV-CCF to HV-Unassisted failure. | Valid | 23WB13787 |  | BELLS BRIDGE FEEDER COMP | WL-A-A | 11KV BELLS BRIDGE FDR CB | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS3051860 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -26.08468627929690 | 152.429016113281 | 2023-10-22 | 1874191 | U Unknown |  | EECL | Forced Regulated | WBFR | Wide Bay | 11kV | U Unknown | M0399 | M0052 | M9999 |  | J | Operational | KILKIVAN | OT199956 | Technician: Ty Farrow Comments | OT199956 | 202310
2023-10-23 |  | 2023-10-23 | TDDI | Transformer-Distribution | Closed |  |  | 2023-10-23 | 2023-10-01 | ATHERTON | EECL | NS | Network Site | XLTNA | 1286645 |  |  | 23/24 | 2024-04-23 | HV | 2023-10-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-10-23 11:59 | F-690-t - 22kV Pole Dist Sub SS4077 Crew require isolation to replace ss4077 | 2023-10-23 | UPPER BARRON: ELMS RD | Distribution Event | Normal Event | 22kV Pole Dist Sub SS4077 Crew require isolation to replace ss4077 Sending Asset Event to FFA FFA Order Created F-AE23FN13987-1-0 DfltHost FFA Order Acknowledged F-AE23FN13987-1-0 athfr02 Scott Lanskey 0427148830 Crew switching for access now Time On modified from 23:59 23-Oct to 16:00 23-Oct Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23FN13987-1-0 athfr02 FFA Order On Site F-AE23FN13987-1-0 athfr02 Time On modified from 16:00 23-Oct to 14:28 23-Oct Sending Asset Event to FFA FFA Order F-AE23FN13987-1-0 Completed by technician Scott Lanskey in crew athfr02(0427148830) with code A-T-303 - Distribution substation Action Taken : replaced tx Site Label : 2127408 Actual Power Restoration for F-AE23FN13987-1-0: 23-OCT-2023 15:07:00 | Valid | 23FN13987 |  | WALMSLEY | SS4077 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS2127408 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -17.374532699585 | 145.532562255859 | 2023-10-23 | 1874247 | MR R WALMSLEY | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | G | Capital | ATHERTON 2 | OT200007 | Technician: Scott Lanskey Comments | OT200007 | 202310
2023-10-26 |  | 2023-11-01 | TDDI | Transformer-Distribution | Closed |  |  | 2023-10-26 | 2023-10-01 | MURGON | EECL | NS | Network Site | XCFBR | 1365896 |  |  | 23/24 | 2024-04-26 | HV | 2023-10-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2023-10-26 18:03 | F-1990-q MURGON 11kV Whtlnds ACR S8601 CB tripped. SCADA Interface automated outage. MRGCS01 Crew advised have reclosed blown EDO's at TX 8921 and tripped ACR.. | 2023-10-26 | BARLIL, BYEE, CLOYNA, GLENROCK, MERLWOOD, MURGON, WHEATLANDS, WINDERA | Distribution Event | Normal Event | entered from the SCADA Interface MRGCS01 Crew advised have reclosed blown EDO's at TX 8921 and tripped ACR.. Manual Reclose Checklist Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Created F-AE23WB13909-1-0 DfltHost Crew advised TX will be replaced Fri 27/10. Sending Asset Event to FFA . Time On modified from 23:59 26-Oct to 15:00 27-Oct Sending Asset Event to FFA FFA Order Acknowledged F-AE23WB13909-1-0 mrgcs01 GRANT KOVAC 0411032982 Asset selection modified Sending Asset Event to FFA Crew Require Access to TX8912 to replace and upgrade to 63KVA Sending Asset Event to FFA F-1990-q - TX8921 requires Replacement. Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 15:00 27-Oct to 14:01 27-Oct Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE23WB13909-1-0 mrgcs01 FFA Order On Site F-AE23WB13909-1-0 mrgcs01 FFA Order Suspended F-AE23WB13909-1-0 by GRANT KOVAC 0411032982 FFA Order En Route F-AE23WB13909-1-0 mrgcs01 FFA Order On Site F-AE23WB13909-1-0 mrgcs01 FFA Order F-AE23WB13909-1-0 Completed by technician Grant kovac in crew mrgcs01(0411032982) with code A-T-28 - Overload Action Taken : upon energising Tx8921 , tx was faulty. and tripped fdr instead of local hv fuses. opened hv fuses on tx and advised control of situation . Site Label : 2024167 | Invalid | 23WB13909 | WHEATLANDS LOOP RD FDR COMP | WHEATLANDS LOOP RD FDR COMP | MG-F-E | Wheatlands Loop Rd Recloser | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS2024167 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -26.181188583374 | 151.844757080078 | 2023-10-26 | 1875317 | HETHERINGTON FARMING CO PTY LT | P - Phase Down (LV) | EECL | Forced Regulated | WBFR | Wide Bay | 11kV | HETHERINGTON FARMING CO PTY LT | M0209 | M0052 | M0070 |  | J | Operational | MURGON | OT200622 | Technician: Grant kovac Comments | OT200622 | 202310
2023-10-29 | [7 empty] | 2023-10-29 | 2023-10-01 | MORANBAH | EECL | NT | Network Slot | XCPNO | 2775024 |  |  | 23/24 | 2024-04-29 | HV | 2023-10-01 |  | Internal Fault | Damaged | Padmount Substation | Outage | North | Distribution substation | 2023-10-29 01:13 | 11kV Ground Dist Sub 10152 - Crews require access for fuse replacement | 2023-10-29 | NEBO: WAVERLEY ST | Distribution Event | Normal Event | 11kV Ground Dist Sub 10152 - Crews require access for fuse replacement Sending Asset Event to FFA FFA Order Created F-AE23MK8578-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23MK8578-1-0 mckoc02 Dwayne Casey 0429956658 FFA Order En Route F-AE23MK8578-1-0 mckoc02 FFA Order On Site F-AE23MK8578-1-0 mckoc02 Transformer fuses blew on close. Crew out of hours Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Sub10152 is now on generation, see 23MK8581 Time On modified from 23:59 29-Oct to 23:59 30-Oct Sending Asset Event to FFA Time On modified from 23:59 30-Oct to 23:59 01-Nov Sending Asset Event to FFA Time On modified from 23:59 01-Nov to 15:22 01-Nov Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA End time updated to align to time that supply was restored via Generator - refer 23MK8581. Time On modified from 15:22 01-Nov to 13:11 29-Oct Sending Asset Event to FFA FFA Order cancelled.F-AE23MK8578-1-0 | Invalid | 23MK8578 |  | MARLEY ACCOMMODATION | 10152 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | GT-116504 | Ground Outdoor / Indoor Chamber Mounted; < 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2023-10-29 | 1875852 | CIVEO PTY LTD (NEBO) NMI-30505 | O - Other | EECL | Forced Regulated | CEFR | Mackay | 11kV | CIVEO PTY LTD (NEBO) NMI-30505 | M0269 | M0052 | M0070 |  | J | Operational | MORANBAH | OT201023 |  | OT201023 | 202310
2023-11-01 |  | 2023-11-04 |  |  | Closed |  |  | 2023-11-01 | 2023-11-01 | PROSERPINE | EECL | NT | Network Slot | XLHBP | 2325769 |  |  | 23/24 | 2024-05-01 | HV | 2023-11-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2023-11-01 06:09 | F-2161-s Crews require access to sub - initial fuse replacement failed Crew replaced faulty 11kV Pole Dist Sub 4037. Isolation required at GS796031 to enable replacement. SL 4036738. | 2023-11-01 | PROSERPINE: BRUCE HWY | Distribution Event | Normal Event | Crews require access to sub - initial fuse replacement failed Sending Asset Event to FFA FFA Order Created F-AE23MK8667-1-0 DfltHost FFA Order Acknowledged F-AE23MK8667-1-0 prpcsfr02 Steven spark 0427114514 FFA Order En Route F-AE23MK8667-1-0 prpcsfr02 FFA Order On Site F-AE23MK8667-1-0 prpcsfr02 FFA Order Suspended F-AE23MK8667-1-0 by Steven spark 0427114514 tx requires replacement CRews will upscale outage on saturday and replace Tx and arm on Tx pole. Outage will need to be upscaled to capture all customers downstream of GS796031 Time On modified from 23:59 01-Nov to 16:00 04-Nov Sending Asset Event to FFA to be completed on the 4/11 Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA FFA Order En Route F-AE23MK8667-1-0 prpcsfr02 FFA Order On Site F-AE23MK8667-1-0 prpcsfr02 Asset selection modified Sending Asset Event to FFA FFA Order En Route F-AE23MK8667-1-0 prpcsfr02 FFA Order On Site F-AE23MK8667-1-0 prpcsfr02 Time On modified from 16:00 04-Nov to 13:05 04-Nov Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23MK8667-1-0 Completed by technician Steven spark in crew prpcsfr02(0427114514) with code A-T-303 - Distribution substation Action Taken : replaced faulty TX Site Label : 4036738 Updated Reasons tab. Updated Event Trigger from HV-Unassisted failure to Distribution substation. | Invalid | 23MK8667 | LAQU-QUEENS HILL | QUEENS HILL | 109 | GS796031 | HV or LV Fuse blown | Completed | Unplanned Outage | Hot | SP-155725 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | #N/A | #N/A | 2023-11-01 | 1876498 | MR M VICKERS | H - HV Fuse Down | EECL | Forced Regulated | CEFR | Mackay | 11kV | MR M VICKERS | M0209 | M0001 | M9999 |  | J | Operational | PROSERPINE | OT201386 |  | OT201386 | 202311
2023-11-02 |  | 2023-12-04 | RGDI | Regulator-Distribution | Closed |  | Replace | 2023-11-02 | 2023-11-01 | TULLY | EECL | NS | Network Site | XLHBY | 875047 |  |  | 23/24 | 2024-05-02 | HV | 2023-11-01 |  | Unknown | Damaged | Regulator, Unknown | Outage | North | HV-Unassisted failure(Apparent defect) | 2023-11-02 12:27 | Bingal Bay Fdr trip and Lockout on O/C Crew found surge diverters at REG MB41A& B, black carbon present, fire at base of pole - Bypassed faulty regulators. SL 5099881. (S Gregory). | 2023-11-02 | BINGIL BAY, EL ARISH, GARNERS BEACH, MISSION BEACH | Distribution Event | Normal Event | Bingal Bay Fdr trip and Lockout on O/C Sending Asset Event to FFA FFA Order Created F-AE23FN14293-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN14293-1-0 tlyfr01 Mitchell Todd 0427627604 FFA Order En Route F-AE23FN14293-1-0 tlyfr01 FFA Order On Site F-AE23FN14293-1-0 tlyfr01 Crews found Surge Deverters at REG MB41A&B, black carbon present and fire at base of pole Manual Reclose Checklist Sending Asset Event to FFA Restoration Comments for F-AE23FN14293-1-0 by tlyfr01: isolated fault on regulators mb41A Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 02-Nov to 14:04 02-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23FN14293-1-0 Completed by technician Mitchell Todd in crew tlyfr01(0427627604) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : bypassed faulty regulators Site Label : 5099881 Updated Reasons tab. Updated Event Trigger from HV-CCF to HV-Unassisted failure. Reason for Event changed from Unknown | Valid | 23FN14293 | El Arish 132/22kV Substation | EL ARISH (T171) 132/22KV SUBSTATION | ELAR | 22KV RMU 2 FDR CB | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS5099881 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -17.82262039184570 | 146.043914794922 | 2023-11-02 | 1876887 | U Unknown |  | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0399 | M0052 | M9999 | 7 | G | Capital | TULLY | OT201596 | .HEADING Technician: Mitchell Todd Comments Bypassed faulty Regulators | OT201596 | 202311
2023-11-04 |  | 2023-11-04 | TDDI | Transformer-Distribution | Closed |  |  | 2023-11-04 | 2023-11-01 | BLACKALL | EECL | NS | Network Site | XCPNK | 1614272 |  |  | 23/24 | 2024-05-04 | HV | 2023-11-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | South | HV-Unassisted failure(Apparent defect) | 2023-11-04 08:35 | F-2043-q Woolga solator Fuses blown DO806626 - Blown SWER Isolator to be replaced. Crew replaced blown SWER isolator. SL 4200849. (S Gregory). | 2023-11-04 | TAMBO: LANGLO RD, WARD RD | Distribution Event | Normal Event | on BKLCS01 apears Isolator fuses blowen Sending Asset Event to FFA FFA Order Created F-AE23CA15327-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA15327-1-0 bklcs01 P Hauff 0428241427 FFA Order En Route F-AE23CA15327-1-0 bklcs01 FFA Order On Site F-AE23CA15327-1-0 bklcs01 Blown SWER Isolator to be replaced. Reason for Event changed from Unknown Sending Asset Event to FFA Time On modified from 23:59 04-Nov to 17:00 04-Nov Sending Asset Event to FFA Reverse switching has commenced Sending Asset Event to FFA Time On modified from 17:00 04-Nov to 16:30 04-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23CA15327-1-0 Completed by technician P Hauff in crew bklcs01(0428241427) with code A-T-303 - Distribution substation Action Taken : replaced blown Swer isolator Site Label : 4200849 Actual Power Restoration for F-AE23CA15327-1-0: 04-NOV-2023 16:30:00 Added notes to Reasons tab. | Invalid | 23CA15327 | Woolga SWER | Woolga SWER | SW/432311 | Unknown Number | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS4200849 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | -25.04268074035640 | 145.870635986328 | 2023-11-04 | 1877317 | TARRINA PTY LTD | N - Neighbours Out as Well | EECL | Transformers Return to Service | D2002 | Capricornia | 19kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | H | Capital | BLACKALL | OT201861 | Technician: P Hauff Comments | OT201861 | 202311
2023-11-13 |  | 2023-11-13 | TDDI | Transformer-Distribution | Closed |  |  | 2023-11-13 | 2023-11-01 | HOME HILL | EECL | NS | Network Site | XLHBH | 1709827 |  |  | 23/24 | 2024-05-13 | HV | 2023-11-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-11-13 14:51 | CLSO - CLSDO04 11kV Feeder - Crew require emergency access to replace damaged Transformer. | 2023-11-13 | CLARE: MITCHELL RD | Distribution Event | Normal Event | Crew require emergency access to replace damaged Transformer. Primary Asset de-escalated from Claresouth No.04 (FC) Sending Asset Event to FFA FFA Order Created F-AE23NQ13470-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ13470-1-0 hhlfr01 Erri Vener 0439680072 FFA Order En Route F-AE23NQ13470-1-0 hhlfr01 FFA Order On Site F-AE23NQ13470-1-0 hhlfr01 Time On modified from 23:59 13-Nov to 17:12 13-Nov Sending Asset Event to FFA FFA Order F-AE23NQ13470-1-0 Completed by technician Erri Vener in crew hhlfr01(0439680072) with code A-T-303 - Distribution substation Action Taken : replaced faulty BDS 3010 3 phase 63 KVA tx. like for like. Site Label : 5073519 Actual Power Restoration for F-AE23NQ13470-1-0: 13-NOV-2023 17:18:00 | Valid | 23NQ13470 | Sub, Clare South No.4 11kV feeder | BDS3010 | BDS3010 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wind | NS5073519 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -19.85227966308590 | 147.176727294922 | 2023-11-13 | 1879614 | WILMAR SUGAR PTY LTD | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | North Queensland | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | HOME HILL 2 | OT203409 | .HEADING Technician: Erri Vener Comments | OT203409 | 202311
2023-11-14 |  | 2023-11-14 | TDDI | Transformer-Distribution | Closed |  |  | 2023-11-14 | 2023-11-01 | GLADSTONE | EECL | NS | Network Site | XLFPG | 942192 |  |  | 23/24 | 2024-05-14 | HV | 2023-11-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2023-11-14 13:59 | 11kV Pole Dist Sub 152164 has FIS Crew replaced transformer, EDOs, and overhead conductor. SL 4141867. (S Gregory). | 2023-11-14 | GLADSTONE: MEEGAN RD | Distribution Event | Normal Event | 11kV Pole Dist Sub 152164 has FIS pcoc01 Sending Asset Event to FFA FFA Order Created F-AE23CA15894-1-0 DfltHost FFA Order Acknowledged F-AE23CA15894-1-0 pcoc01 Geoff tomkins 0437331686 FFA Order En Route F-AE23CA15894-1-0 pcoc01 FFA Order On Site F-AE23CA15894-1-0 pcoc01 Asset selection modified Sending Asset Event to FFA outage extended to open Links Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Replay sequence time changed from 14-NOV-23 17:11:07 to 14-Nov-23 17:09:00 Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 14-Nov to 20:00 14-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23CA15894-1-0 Completed by technician Geoff tomkins in crew pcoc01(0437331686) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : replaced trx, egos, overhead conductor Site Label : 4141867 Added notes to Reasons tab. Updated Event Trigger from HV-Unassisted failure to Distribution substation. | Valid | 23CA15894 | CLIN-CLINTON PK | CI104 Clinton Park | CI104 | X1025 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS4141867 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -23.86918830871580 | 151.194015502930 | 2023-11-14 | 1879855 | MR A JENNER | F - Fire - Pole/Structure | EECL | Transformers Return to Service | D2002 | Capricornia | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | GLADSTONE 1 | OT203537 | Technician: Geoff tomkins Comments | OT203537 | 202311
2023-11-17 |  | 2023-11-17 | TDDI | Transformer-Distribution | Closed |  |  | 2023-11-17 | 2023-11-01 | KILKIVAN | EECL | NS | Network Site | XCFBK | 1370637 |  |  | 23/24 | 2024-05-17 | HV | 2023-11-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2023-11-17 05:12 | F-28866-g : 11kV Pole Dist Sub 3716 Full TX Replacement | 2023-11-17 | WOOLOOGA: SMITH RD | Distribution Event | Normal Event | 11kV Pole Dist Sub 3716 Full TX Replacement Sending Asset Event to FFA FFA Order Created F-AE23WB14691-1-0 DfltHost sent to kkvfco01 Sending Asset Event to FFA F-28866-g Switching Sheet Written Switch Sheet Distributed Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23WB14691-1-0 kkvfco01 Ty Farrow 0417449186 FFA Order En Route F-AE23WB14691-1-0 kkvfco01 FFA Order On Site F-AE23WB14691-1-0 kkvfco01 Time On modified from 23:59 17-Nov to 16:24 17-Nov Sending Asset Event to FFA FFA Order F-AE23WB14691-1-0 Completed by technician Ty Farrow in crew kkvfco01(0417449186 ) with code A-T-303 - Distribution substation Action Taken : replaced blown 10kva tx 3716 Site Label : 6057379 Actual Power Restoration for F-AE23WB14691-1-0: 17-NOV-2023 16:14:00 | Valid | 23WB14691 |  | Smiths Rd Woolooga | 3716 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Storm Electrical | NS6057379 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -26.03883171081540 | 152.381347656250 | 2023-11-17 | 1880493 | MR L GEAR | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | KILKIVAN | OT203937 | Technician: Ty Farrow Comments | OT203937 | 202311
2023-11-18 |  | 2023-11-19 | TDDI | Transformer-Distribution | Closed |  |  | 2023-11-18 | 2023-11-01 | HUGHENDEN | EECL | NS | Network Site | XCHBU | 824867 |  |  | 23/24 | 2024-05-18 | HV | 2023-11-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2023-11-18 21:50 | Crew advise tx HUS105 has FIS | 2023-11-18 | HUGHENDEN: ANTRIM STATION | Distribution Event | Normal Event | Crew advise tx HUS105 has FIS Sending Asset Event to FFA FFA Order Created F-AE23NQ13653-1-0 DfltHost Sending Asset Event to FFA Time On modified from 23:59 19-Nov to 16:51 19-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ13653-1-0 huhcdwgl1 BRETT TOWNLEY 0429797319 FFA Order En Route F-AE23NQ13653-1-0 huhcdwgl1 FFA Order On Site F-AE23NQ13653-1-0 huhcdwgl1 FFA Order F-AE23NQ13653-1-0 Completed by technician BRETT TOWNLEY in crew huhcdwgl1(0429797319) with code A-T-303 - Distribution substation Action Taken : replace tx failed in service Site Label : 5019036 Actual Power Restoration for F-AE23NQ13653-1-0: 19-NOV-2023 18:35:00 auto-completed | Valid | 23NQ13653 | Sub, Stamford No.03 Tangorin SWER feeder | HUS105 | HUS105 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Hot | NS5019036 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -21.64121246337890 | 144.278106689453 | 2023-11-18 | 1880897 | FOR A & B HICK FAMILY TRUST | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | North Queensland | 19kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | H | Capital | HUGHENDEN | OT204230 | Technician: BRETT TOWNLEY Comments | OT204230 | 202311
2023-11-20 |  | 2023-11-20 | TDDI | Transformer-Distribution | Closed |  |  | 2023-11-20 | 2023-11-01 | COOKTOWN | EECL | NS | Network Site | XCTNO | 1118040 |  |  | 23/24 | 2024-05-20 | HV | 2023-11-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2023-11-20 13:16 | F-2269-s - Crews require access to 22kV Pole Dist Sub SS4368 utilising HV EDO's as Isolation point. | 2023-11-20 | COOKTOWN: RAILWAY AVE W | Distribution Event | Normal Event | Crews require access to 22kV Pole Dist Sub SS4368 utilising HV EDO's as Isolation point. Crews Attending: Steve Johnson 0409 279 877 Sending Asset Event to FFA FFA Order Created F-AE23FN14898-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN14898-1-0 cktcdwgl1 Steve Johnson 0409279877 FFA Order En Route F-AE23FN14898-1-0 cktcdwgl1 FFA Order On Site F-AE23FN14898-1-0 cktcdwgl1 FFA Order F-AE23FN14898-1-0 Completed by technician Steve Johnson in crew cktcdwgl1(0409279877) with code A-T-303 - Distribution substation Action Taken : Replaced FIS 25kVA Transformer Site Label : 5112134 Time On modified from 23:59 20-NOV to 17:20 20-NOV | Invalid | 23FN14898 |  | Rutherford | SS4368 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS5112134 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -15.43017387390140 | 145.101974487305 | 2023-11-20 | 1881222 | MR P RUTHERFORD | O - Other | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | G | Capital | COOKTOWN | OT204458 | Technician: Steve Johnson Comments | OT204458 | 202311
2023-11-25 |  | 2023-12-14 |  |  | Closed |  |  | 2023-11-25 | 2023-11-01 | EMERALD | EECL | NS | Network Site | XLFPE | 967776 |  |  | 23/24 | 2024-05-25 | HV | 2023-11-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2023-11-25 05:35 | F-1298-r : EMERALD 22kV Foleys Rd RC789775 ACR CB tripped. SCADA Interface automated outage. 22kV Recloser RC789775 tripped to lockout on EF. Manual Reclose attempt unsuccessful. Crew found blown LAs at 22kV Pole Dist Sub 272670, then found the transformer had blown. Transformer to be replaced under 23CA16527, other customers restored. SL 4253818. (S Gregory). | 2023-11-25 | EMERALD: BAUHINIAS RD, FOLEY RD, FRANCIS ACCESS RD, LOCHARBOR RD, LOCHLEES RD, OFF FOLEY RD, OLD LOCHLEES RD, WYUNA RD WYUNA: FOREST HILL RD YAMALA: BAUHINIA RD | Distribution Event | Normal Event | entered from the SCADA Interface 22kV Recloser RC789775 tripped to lockout on EF Unsuccessful reclose attempt. On call co-ordinator advised to contact 1st on call to attend site Sending Asset Event to FFA FFA Order Created F-AE23CA16510-1-0 DfltHost Sending Asset Event to FFA F-1298-r Reason for Event changed from Unknown Sending Asset Event to FFA 15 minute manual reclose attempt unsuccessful. Crews dispatched. Depot Co-ord Advised Sending Asset Event to FFA FFA Order Acknowledged F-AE23CA16510-1-0 emlfr01 Trent Goody 0436432147 FFA Order En Route F-AE23CA16510-1-0 emlfr01 FFA Order On Site F-AE23CA16510-1-0 emlfr01 Site access poor following rain. Sectionalising commenced at S3132. Manual reclose succesful up to S3132 at 0829. Crew continuing aerial line patrol and sectionalising downstream. Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Sectionalising unsuccessful downstream of S3132. Fault lies between S3132 and X020018, S8323 & S8321. Crew continuing with aerial patrol. F-1298-r. Switching Sheet Written Switch Sheet Distributed Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Sending Asset Event to FFA 2nd manual reclose attempt failed. Crew pulling tee-off & individual TX fuses. Site access only via helicopter. ACR RC789775 left OPEN to minimise aerial logistics / flight time in rain. Sending Asset Event to FFA Blown LA found at TX 272670. Supply restored to all remaining customers at 1357. TX 272670 remains offline. Asset selection modified Sending Asset Event to FFA LAs at TX 272670 cut away & reclose attempted. TX faulty and tripped upstream ACR. TX 272670 left OFFLINE and requires full replacement. Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Replay sequence/s deleted after 25-NOV-23 14:09:00 Assets extracted from 272670 (SANDERS NO. 2) into event 23CA16527 New asset event for TX 272670 = 23CA16527 Time On modified from 23:59 25-Nov to 14:13 25-Nov Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE23CA16510-1-0 Completed by technician Trent Goody in crew EMLFR01() with code A-T-303 - Distribution substation Action Taken : Crew identified blown TX at 272670. Crew will replace TX as soon as weather permits. Site Label : 4253818 Actual Power Restoration for F-AE23CA16510-1-0: 25-NOV-2023 14:54:00 Updated Reasons tab. Reason for Event changed from Unknown | Invalid | 23CA16510 | RC789775-FOLEYS RD, EMERALD QLD 4720 | FOLEYS RD | EM244RC789775 | Foleys Rd Recloser | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS4253818 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -23.47813034057620 | 148.356887817383 | 2023-11-25 | 1882564 | U Unknown |  | EECL | Transformers Return to Service | D2002 | Capricornia | 22kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | G | Capital | EMERALD | OT205261 | .HEADING Technician: Trent Goody Comments Crew identified blown TX at 272670. Crew will replace TX as soon as weather permits. ToughPad Location: Site Label Entered:272670 Component: TDDI Component Mod: OC Technician: Luke Freeman Comments | OT205261 | 202311
2023-11-27 |  | 2024-04-19 | RXDI | Reactor-Distribution | Closed |  | Made Safe | 2023-11-27 | 2023-11-01 | RICHMOND | EECL | NS | Network Site | XCHBR | 943323 |  |  | 23/24 | 2024-05-27 | HV | 2023-11-01 |  | Unknown | Broken | Reactor, Unknown | Outage | North | Overload | 2023-11-25 11:19 | F-2313-s RICHMOND 19kV Clutha North No.1 ACR CB tripped. SCADA Interface automated outage. | 2023-11-25 | NELIA: BUNDA BUNDA STATION RICHMOND: SUTHERLAND STATION MAXWELTON: EUTHELLA STATION, GLADEVALE STATION, GLENGALLA STATION, SAXBY DOWNS STATION, ROTHBURY PARK STATION | Distribution Event | Normal Event | entered from the SCADA Interface John Bishop checking on Helicopter availability Still waiting on Helicopter will attempt MRC Manual Reclose Checklist MRC Failed Crew to Patrol Sending Asset Event to FFA FFA Order Created F-AE23NQ13942-1-0 DfltHost Crew to fly 0600 Sunday Sending Asset Event to FFA Time On modified from 23:59 25-Nov to 23:59 26-Nov Sending Asset Event to FFA Sending Asset Event to FFA Aerial Patrol Commenced Sending Asset Event to FFA Patrol complete with no fault found. Close unsuccessful Sending Asset Event to FFA Crew adv Reactor RIS75 is U/S HV Fuse Opened and MRC Successful Time On modified from 23:59 26-Nov to 10:02 26-Nov Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ13942-1-0 rchcs01 John bishop 0429473146 FFA Order En Route F-AE23NQ13942-1-0 rchcs01 FFA Order On Site F-AE23NQ13942-1-0 rchcs01 FFA Order F-AE23NQ13942-1-0 Completed by technician John bishop in crew rchcs01(0429473146) with code A-T-28 - Overload Action Taken : replace reactor at later Site Label : 9999999 auto-completed | Valid | 23NQ13942 | Nonda SWER Feeder Section C | NONDASWER-CLUTHANTH NO.01 ACR | NO-01C | CLUTHA NTH NO.1 RECLOSER | Unknown | Completed | Unplanned Outage | Storm Electrical | NS5068889 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -20.21388244628910 | 142.471313476563 | 2023-11-27 | 1882818 | U Unknown |  | EECL | Forced Regulated | NQFR | North Queensland | 19kV | U Unknown | M0400 | M0001 | M9999 | B | H | Operational | RICHMOND | OT205500 | Technician: Maks Chylewski Comments removed RIS75 reactor from service as it was causing fault on the line. EDO is open | OT205500 | 202311
2023-11-28 |  | 2023-11-29 | TDDI | Transformer-Distribution | Closed |  |  | 2023-11-28 | 2023-11-01 | MACKAY | EECL | NS | Network Site | XLFPK | 1447715 |  |  | 23/24 | 2024-05-28 | HV | 2023-11-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-11-28 02:56 | F-2355-s Multiple calls from 11kV Pole Dist Sub 3868 for dim flickering lights/no supply | 2023-11-28 | BAKERS CREEK: LEMBERGS RD, PRATTS RD | Distribution Event | Normal Event | Multiple calls from 11kV Pole Dist Sub 3868 for dim flickering lights/no supply . Sending Asset Event to FFA FFA Order Created F-AE23MK9388-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23MK9388-1-0 mckoc01 Adam Clark 0429728928 FFA Order En Route F-AE23MK9388-1-0 mckoc01 FFA Order On Site F-AE23MK9388-1-0 mckoc01 Removing Asset Event from FFA FFA Order cancelled.F-AE23MK9388-1-0 Crews have left TX safe with both HV and LV isolated Another crew will be attending during depot hours today 28/11/23 for a TX change and will ring up for dispatch instructions. Time On modified from 23:59 28-Nov to 10:54 28-Nov Sending Asset Event to FFA FFA Order Created F-AE23MK9388-1-1 DfltHost FFA Order Acknowledged F-AE23MK9388-1-1 mcklwgl1 Shanan studt 0467731299 FFA Order En Route F-AE23MK9388-1-1 mcklwgl1 FFA Order On Site F-AE23MK9388-1-1 mcklwgl1 FFA Order F-AE23MK9388-1-1 Completed by technician Shanan studt in crew mcklwgl1(0467731299) with code A-T-303 - Distribution substation Action Taken : replaced tx 3868 Site Label : 4015462 Time On modified from 10:54 28-NOV to 11:03 28-NOV | Valid | 23MK9388 |  | BLACKBURN | 3868 |  | Unknown | Completed | Unplanned Outage | Wet / Rain | NS4015462 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | -21.22205734252930 | 149.140502929688 | 2023-11-28 | 1883115 | MISS S MCDOUGALL | L - Life Threatening | EECL | Transformers Return to Service | D2002 | Mackay | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | MACKAY 2 | OT205679 | Technician: Shanan studt Comments | OT205679 | 202311
2023-11-29 |  | 2023-12-08 |  |  | Closed |  |  | 2023-11-29 | 2023-11-01 | ISLAND COMM | EECL | NT | Network Slot | XLTNG | 2857619 |  |  | 23/24 | 2024-05-29 | HV | 2023-11-01 | M | Corrosion | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-11-29 16:29 | F-785-t - Tomkin Billy advised Kubin Fdr 2 Tripped and has OC alarms on. | 2023-11-29 | KUBIN: AIRPORT RD, MEIMALGAU RD, MEPAU ST, MUALGAU RD, WAGALGAU RD | Distribution Event | Normal Event | Kubin Fdr 2 Tripped and has OC alarms on. Spoken to Kassim Mahamad Oncall who advised Crews will attend 30/11/23 to patrol the line due to O/C Trip. Please assign to thioc01 Sending Asset Event to FFA Delayed until crew can attend in the Morning Sending Asset Event to FFA Time On modified from 23:59 29-Nov to 15:00 30-Nov Sending Asset Event to FFA FFA Order Created F-AE23FN15354-1-0 DfltHost FFA Order Acknowledged F-AE23FN15354-1-0 thioc01 Scott 0408672666 FFA Order En Route F-AE23FN15354-1-0 thioc01 FFA Order On Site F-AE23FN15354-1-0 thioc01 Sending Asset Event to FFA Patrol completed and nothing found. Crew adv may be an issue with the PLC at Power Station. Will attempt an MRC Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Crew adv they just had to replace a part at the power station and will attempt an mRC Sending Asset Event to FFA MRC failed. Crew to patrol again. If nothing is found we will isolate HV cable at AP13 and try an MRC Time On modified from 15:00 30-Nov to 23:59 30-Nov Sending Asset Event to FFA Crew adv looks like a suspeted blown EDO that didn't drop properly at SS7825. Will isolate TX complete the patrol and attempt another MRC Sending Asset Event to FFA MRC completed 1332. Crew suspect LA's at Sub SS7825 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 30-Nov to 16:00 30-Nov Sending Asset Event to FFA Scott advised he has to travel back ti TI to get more gear for repairs to continue tomorrow. Time On modified from 16:00 30-Nov to 16:00 01-Dec Sending Asset Event to FFA FFA Order Suspended F-AE23FN15354-1-0 by Scott 0408672666 Additional equipment required. Crew back on to a permit now. Unsure if TX will come back today. Crew to advise OCCN when they know. Time On modified from 16:00 01-Dec to 23:59 02-Dec Sending Asset Event to FFA Time On modified from 23:59 02-Dec to 23:59 03-Dec Sending Asset Event to FFA Scott Wilkes adv waiting on resources to complete. ETA at this stage Tues Time On modified from 23:59 03-Dec to 23:59 05-Dec Sending Asset Event to FFA extend outage , awaiting mobile plant to lift transformer Time On modified from 23:59 05-Dec to 23:59 08-Dec Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 08-Dec to 15:26 08-Dec Sending Asset Event to FFA FFA Order En Route F-AE23FN15354-1-0 thioc01 FFA Order On Site F-AE23FN15354-1-0 thioc01 FFA Order F-AE23FN15354-1-0 Completed by technician Scott in crew thioc01(0408672666) with code A-T-303 - Distribution substation Action Taken : Replace faulty 100kva Transformer. Site Label : 5163610 Updated Asset Event Type from Sub Transmission to Distribution. | Invalid | 23FN15354 |  | OUTGOING FEEDER BAY | KUBIN NO 2 | 415V KUBIN NO 2 CB | Protective Device Operated | Completed | Unplanned Outage | Fine | SP-105235 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2023-11-29 | 1883692 | PROT Protective Device Operated |  | EECL | Forced Regulated (Isolated Distribution) | DFFR | Far North | 22kV | PROT Protective Device Operated | M0209 | M0052 | M0011 |  | G | Operational | THURSDAY ISLAND | OT206066 |  | OT206066 | 202311
2023-11-30 |  | 2023-11-30 | TDDI | Transformer-Distribution | Closed |  |  | 2023-11-30 | 2023-11-01 | WARWICK | EECL | NS | Network Site | XLGDW | 1605555 |  |  | 23/24 | 2024-05-30 | HV | 2023-11-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2023-11-30 06:32 | F-1359-r - 11kV Recloser CB4412 KILLARNEY 11kV Koreelah CB4412 CB tripped. SCADA Interface automated outage.' Crew replaced blown 11kV Pole Dist Sub PE02470. SL 3214497. (S Gregory). | 2023-11-30 | ACACIA CREEK, ACACIA PLATEAU, CENTRAL KOREELAH, HEWETSONS MILL, NEW KOREELAH, OLD KOREELAH, | Distribution Event | Normal Event | entered from the SCADA Interface Tripped to lockout on SEF F-1359-r waroc02 Crew to conduct feeder patrol 11kV Recloser CB4412 Sending Asset Event to FFA FFA Order Created F-AE23SW21102-1-0 DfltHost Sent to pad but pad was offline at the time, may need to send again its sitting in the pending orders Sending Asset Event to FFA Sent to WAROC02 Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW21102-1-0 waroc02 Luke Brosnan 0418972973 Crew heading to the area Sending Asset Event to FFA FFA Order En Route F-AE23SW21102-1-0 waroc02 FFA Order On Site F-AE23SW21102-1-0 waroc02 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Sectionalising Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 30-Nov to 16:30 30-Nov Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Crew replacing faulty Transformer PE02470 Sending Asset Event to FFA Time On modified from 16:30 30-Nov to 17:00 30-Nov Sending Asset Event to FFA FFA Order F-AE23SW21102-1-0 Completed by technician Luke Brosnan in crew waroc02(0418972973) with code A-T-303 - Distribution substation Action Taken : replaced Blown Tx PE02470 Site Label : 3214497 Time On modified from 17:00 30-Nov to 16:48 30-Nov Reason for Event changed from Lightning / Storm Updated Reasons tab. Updated Event Trigger from SAF to Distribution substation. | Valid | 23SW21102 |  | KOREELAH | 3350 | Koreelah Recloser | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS3214497 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -28.43429183959960 | 152.384887695313 | 2023-11-30 | 1883817 | U Unknown |  | EECL | Transformers Return to Service | D2002 | South West | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | STANTHORPE | OT206188 | Technician: Luke Brosnan Comments Replaced Blown Tx PE02470 | OT206188 | 202311
2023-11-30 | [7 empty] | 2023-11-30 | 2023-11-01 | RICHMOND | EECL | NT | Network Slot | XCHBR | 5998164 |  |  | 23/24 | 2024-05-30 | HV | 2023-11-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2023-11-30 10:32 | F-2377-s RICH - RI80 H652 Fdr: Replace RIS174 Transformer due to Oil Leak. Replacement Tx u/s - another New TX req. RIS174 replaced. (S Gregory). | 2023-11-30 | RICHMOND: FLINDERS HWY | Sub Transmission Event | Normal Event | Replace Transformer due to Oil Leak Sending Asset Event to FFA FFA Order Created F-AE23NQ14201-1-0 DfltHost Sending Asset Event to FFA FFA Order cancelled.F-AE23NQ14201-1-0 Crews have advised they will be doing this job tomorrow 1/12/23 Time On modified from 23:59 30-Nov to 23:59 01-Dec . Crews need to extend outage to replace crossarm Asset selection modified Time On modified from 23:59 01-Dec to 14:00 01-Dec Time On modified from 14:00 01-Dec to 16:00 01-Dec crews reverse switching now Time On modified from 16:00 01-Dec to 16:45 01-Dec Time On modified from 16:45 01-Dec to 17:30 01-Dec Asset selection modified CRews have advised TX RIS174 has been replaced but still have a problem with TX Volts. HV volts are ok. Crews have advised they will be back out tomorrow to investigate Time On modified from 17:30 01-Dec to 17:30 02-Dec John Bishop adv too wet to attempt today. Storms in area. He has spoken to customer and customer is happy to delay to tomorrow Time On modified from 17:30 02-Dec to 17:30 03-Dec switching & repairs commenced Asset selection modified Time On modified from 17:30 03-Dec to 13:30 03-Dec Asset selection modified Time On modified from 13:30 03-Dec to 10:37 03-Dec Updated Reasons tab. Updated Asset Event Type from Transmission to Sub Transmission. | Invalid | 23NQ14201 | TRALEE, FLINDERS HWY, STAMFORD QLD 4821 | HUGHENDEN-RICHMOND NO.10 (Fdr Comp) | HUGH-RICH NO.10 | BARABON QUARRY NO.2 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | SP-447760 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2023-11-30 | 1883902 | GROMAC QUARRIES (NQ) PTY. LTD. | O - Other | EECL | Forced Regulated | NQFR | North Queensland | 33kV | GROMAC QUARRIES (NQ) PTY. LTD. | M0209 | M0001 | M9999 |  | F | Operational | RICHMOND | OT206251 |  | OT206251 | 202311
2023-12-03 |  | 2023-12-03 | TDDI | Transformer-Distribution | Closed |  |  | 2023-12-03 | 2023-12-01 | HOME HILL | EECL | NS | Network Site | XLHBH | 1724188 |  |  | 23/24 | 2024-06-03 | LV | 2023-12-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2023-12-03 16:51 | Crew are replacing U/S transformer BDS312 | 2023-12-03 | HOME HILL: FORDS RD | Distribution Event | Normal Event | Crew are replacing U/S transformer BDS312 hhlfr01. Sending Asset Event to FFA FFA Order Created F-AE23NQ14365-1-0 DfltHost Time On modified from 23:59 03-Dec to 20:46 03-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ14365-1-0 hhlfr01 Adam Mitchell 0437469307 FFA Order En Route F-AE23NQ14365-1-0 hhlfr01 FFA Order On Site F-AE23NQ14365-1-0 hhlfr01 FFA Order F-AE23NQ14365-1-0 Completed by technician Adam Mitchell in crew hhlfr01(0437469307) with code A-T-303 - Distribution substation Action Taken : tx change Site Label : 2025186 Actual Power Restoration for F-AE23NQ14365-1-0: 03-DEC-2023 21:11:00 Updated Asset Event Type from Transmission to Distribution. | Invalid | 23NQ14365 | Sub, HomeHill No.6 11kV feeder | BDS312 | BDS312 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS2025186 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | #N/A | #N/A | 2023-12-03 | 1884873 | W BENNETT FORD & CO | L - Life Threatening | EECL | Transformers Return to Service | D2002 | North Queensland | LV | Transformers Return to Service | M0209 | M0001 | M0070 |  | M | Capital | HOME HILL 2 | OT207045 | .HEADING Technician: Adam Mitchell Comments | OT207045 | 202312
2023-12-09 |  | 2024-01-16 | TDDI | Transformer-Distribution | Closed |  |  | 2023-12-09 | 2023-12-01 | TOOWOOMBA | EECL | NS | Network Site | XLGDT | 1660720 |  |  | 23/24 | 2024-06-09 | HV | 2023-12-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | HV-Unassisted failure(Apparent defect) | 2023-12-09 15:58 | Fault occurred at:09/12/2023 15:55; DAVID COOMBS, 0412547340;>FUSES --> Fuse:LV Blown<;Incident Details:One phase down (this happened yesterday as well);Access Details:Clear access - electric fence is not active. If electric fence falls, please put back up so horses done escape;COVID-19:NO;Warnings[fuseDown]: ADVISED;Dog restraint:YARD;Sensitive Load:N | 2023-12-09 | LINTHORPE PARK;60 BARRON RD;BIDDESTON QLD 4401 | Distribution Event | Normal Event |  | Valid | 23SW21665 | Murphy, Biddeston | PE05813 | PE05813 |  | Unknown | Completed | Unplanned Outage | Cold | NS3105013 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -27.57637596130370 | 151.669235229492 | 2023-12-09 | 1886589 | MR D COOMBS | O - Other | EECL | Transformers Return to Service | D2002 | South West | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | TOOWOOMBA RAPIDS | OT208251 | Technician: Matt Cooper Comments 25kva tx requiring replacement inc downleads and edo arm. UNKNOWN FAULT ON TX, YOUNG FAMILY LIVING IN REMOTE LOCATION. EE ATTENDED 3 times in one week for fuse replacements (3 different crews) no signs of any apparent cause of fault. Tx is 50 plus years old. CUSTOMER ADVISED IF IT IS TO BLOW A FUSE AGAIN CONTACT EE FOR TX REPLACEMENT. | OT208251 | 202312
2023-12-21 |  | 2023-12-22 |  |  | Closed |  |  | 2023-12-21 | 2023-12-01 | CNS CENTRAL | EECL | FD | Feeder | XLTNC | 7295198 |  |  | 23/24 | 2024-06-21 | HV | 2023-12-01 |  | Internal Fault | Broken | Padmount Substation | Outage | North | HV-Unassisted failure(Apparent defect) | 2023-12-21 23:50 | F-906-t CAIRNS NORTH 22kV Manoora Fdr CB FA10Q00 tripped. SCADA Interface automated outage. Crew replaced 3 switch RMU due to failed C phase bushing on SD2. SS8782. (S Gregory). | 2023-12-21 | BRINSMEAD, KANIMBLA, MANOORA, REDLYNCH, WHITFIELD | Distribution Event | Normal Event | entered from the SCADA Interface Time On modified from 23:59 21-Dec to 23:59 22-Dec Dean Bauer 0438 587 099 cnsoc01 Sending Asset Event to FFA FFA Order Created F-AE23FN16624-1-0 DfltHost Tripped on EF Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN16624-1-0 cnsoc01 Dean Bauer 0438587099 Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 22-Dec to 08:00 22-Dec Sending Asset Event to FFA Crew replacing SS8782 after FIS Sending Asset Event to FFA FFA Order En Route F-AE23FN16624-1-0 cnsoc01 FFA Order On Site F-AE23FN16624-1-0 cnsoc01 Time On modified from 08:00 22-Dec to 06:08 22-Dec Sending Asset Event to FFA FFA Order F-AE23FN16624-1-0 Completed by technician Dean Bauer in crew cnsoc01() with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : Replaced 3switch RMU due to failed C phase bushing on SD2. No option in FDC for RMU, had to enter as a distribution sectionaliser Site Label : SS8782 Actual Power Restoration for F-AE23FN16624-1-0: 22-DEC-2023 05:20:00 auto-completed Updated Reasons tab. Reason for Event changed from Unknown | Invalid | 23FN16624 | CANO-MANOORA | Manoora Feeder | 2MNR | FA10Q00 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | FD-2275 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | #N/A | #N/A | 2023-12-21 | 1890773 | U Unknown |  | EECL | Cable Return to Service | D2001 | Far North | 22kV | Cable Return to Service | M0269 | M0001 | M0070 |  | G | Capital | Cairns Fault Response | OT211555 | ToughPad Location: Site Label Entered:SS8782 Component: ENCL Component Mod: OC Technician: Dean Bauer Comments Replaced 3switch RMU due to failed C phase bushing on SD2. | OT211555 | 202312
2023-12-21 |  | 2023-12-22 | TDDI | Transformer-Distribution | Closed |  |  | 2023-12-21 | 2023-12-01 | TOOWOOMBA | EECL | NS | Network Site | XLGDT | 1565519 |  |  | 23/24 | 2024-06-21 | HV | 2023-12-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | South | Severe Weather | 2023-12-21 17:19 | F-1622-r 11kV Pole Dist Sub PE06159. access reqd, blown LA's | 2023-12-21 | DRAYTON: ANZAC AVE | Distribution Event | Normal Event | 11kV Pole Dist Sub PE06159. access reqd, blown LA's Sending Asset Event to FFA FFA Order Created F-AE23SW22595-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW22595-1-0 twmfrsl01 Paul Middleton 0401294792 FFA Order En Route F-AE23SW22595-1-0 twmfrsl01 FFA Order On Site F-AE23SW22595-1-0 twmfrsl01 Reclose of Transf. PE06159 EDOs unsuccessful. Crew to advise if work will continue tonight Sending Asset Event to FFA Crew is trying to sort a LV alternative feed Sending Asset Event to FFA crews to attend tomorrow Time On modified from 23:59 21-Dec to 23:59 22-Dec Sending Asset Event to FFA Time On modified from 23:59 22-Dec to 09:47 22-Dec Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW22595-1-0 twmcm06 Rory Mackenzie 0427704018 FFA Order En Route F-AE23SW22595-1-0 twmcm06 FFA Order On Site F-AE23SW22595-1-0 twmcm06 Sending Asset Event to FFA FFA Order F-AE23SW22595-1-0 Completed by technician Rory Mackenzie in crew twmcm06(0427704018 ) with code A-T-303 - Distribution substation Action Taken : Replaced 63kva Tx Site Label : 3233979 Actual Power Restoration for F-AE23SW22595-1-0: 22-DEC-2023 10:48:00 | Invalid | 23SW22595 | Holborn, Anzac Ave, Drayton | PE06159 | PE06159 |  | Unknown | Completed | Unplanned Outage | Wet / Rain | NS3233979 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -27.59839630126950 | 151.905166625977 | 2023-12-21 | 1890686 | MR G RICKERT | P - Phase Down (LV) | EECL | Transformers Return to Service | D2002 | South West | 11kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | J | Capital | TOOWOOMBA RAPIDS | OT211478 | .HEADING Technician: Paul Middleton Comments Technician: Rory Mackenzie Comments | OT211478 | 202312
2023-12-22 |  | 2023-12-22 | TDDI | Transformer-Distribution | Closed |  |  | 2023-12-22 | 2023-12-01 | KILKIVAN | EECL | NS | Network Site | XCFBK | 1433025 |  |  | 23/24 | 2024-06-22 | HV | 2023-12-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2023-12-22 07:09 | Crew require Access to replace TX 9439 F-1635-r | 2023-12-22 | KILKIVAN: ROSSMORE RD | Distribution Event | Normal Event | Crew require Access to replace TX 9439 Sending Asset Event to FFA FFA Order Created F-AE23WB16207-1-0 DfltHost Time On modified from 23:59 22-Dec to 13:15 22-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23WB16207-1-0 kkvcmfr01 Liam Brauer 0436479936 FFA Order En Route F-AE23WB16207-1-0 kkvcmfr01 FFA Order On Site F-AE23WB16207-1-0 kkvcmfr01 FFA Order F-AE23WB16207-1-0 Completed by technician Liam Brauer in crew kkvcmfr01(0436479936) with code A-T-303 - Distribution substation Action Taken : replaced blown up transformer. Site Label : 2060034 Actual Power Restoration for F-AE23WB16207-1-0: 22-DEC-2023 13:19:00 FFA Order F-AE23WB16207-1-0 Completed by technician Liam Brauer in crew kkvcmfr01(0436479936) with code A-T-303 - Distribution substation Action Taken : replaced blown up transformer. Site Label : 2060034 Actual Power Restoration for F-AE23WB16207-1-0: 22-DEC-2023 13:19:00 | Valid | 23WB16207 |  | Rossmore Rd Kilkivan | 9439 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS2060034 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -26.1636753082275 | 152.279220581055 | 2023-12-22 | 1890813 | FOR HUTCHISON FAMILY TRUST | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | KILKIVAN | OT211593 | Technician: Liam Brauer Comments | OT211593 | 202312
2023-12-23 |  | 2024-03-08 |  |  | Closed |  |  | 2023-12-23 | 2023-12-01 | TOOWOOMBA | EECL | NT | Network Slot | XLGDT | 7670470 |  |  | 23/24 | 2024-06-23 | HV | 2023-12-01 |  | Internal Fault | Broken | Padmount Substation | Outage | South | Distribution substation | 2023-12-23 17:15 | F-1651-r Greenwattle St South 11kV CB604940 Tripped and reclosed during upstream device lockout. Fault call for downstream GE765578 loud bang suspect 2nd fault RMU of GE00335 to be replaced (S Gregory). | 2023-12-23 | GLENVALE, HARRISTOWN, NEWTOWN, TOOWOOMBA | Distribution Event | Normal Event | Greenwattle St South 11kV CB604940 F-1651-r twmoc03 Sending Asset Event to FFA FFA Order Created F-AE23SW22753-1-0 DfltHost Asset selection modified Sending Asset Event to FFA Onsite crew adviseed that there might not be anything wrong with the RMU but will take a permit to check it out Sending Asset Event to FFA Time On modified from 23:59 23-Dec to 22:11 23-Dec Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23SW22753-1-0 twmoc03 Dalton balke 0407644145 FFA Order En Route F-AE23SW22753-1-0 twmoc03 FFA Order On Site F-AE23SW22753-1-0 twmoc03 FFA Order F-AE23SW22753-1-0 Completed by technician Dalton balke in crew TWMOC03(0407644145) with code A-T-303 - Distribution substation Action Taken : RMU TO BE REPLACED Site Label : GE00335 Updated Reasons tab. Reason for Event changed from Unknown | Invalid | 23SW22753 | 80 GLENVALE RD, HARRISTOWN QLD 4350 | GREENWATTLE STREET SOUTH RECLOSER | CB604940 | GREENWATTLE STREET SOUTH RECLOSER | Equipment Failure or Malfunction | Completed | Unplanned Outage | Storm Electrical | RC-1058000 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | #N/A | #N/A | 2023-12-23 | 1891172 | U Unknown |  | EECL | Cable Return to Service | D2001 | South West | 11kV | Cable Return to Service | M0269 | M0001 | M0070 |  | J | Capital | TOOWOOMBA 1 | OT211910 | ToughPad Location: Site Label Entered:GE00335 Component: ENCL Component Mod: OC Technician: Dalton balke Comments RMU to be replaced | OT211910 | 202312
2023-12-23 |  | 2023-12-23 | TDDI | Transformer-Distribution | Closed |  |  | 2023-12-23 | 2023-12-01 | KINGAROY | EECL | NS | Network Site | XCFBY | 792158 |  |  | 23/24 | 2024-06-23 | HV | 2023-12-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2023-12-23 16:45 | F-2476-q - 11kV Pole Dist Sub 6071 Blown, requires replacing | 2023-12-23 | SANDY RIDGES: GENTRY RD | Distribution Event | Normal Event | 11kV Pole Dist Sub 6071 Blown, requires replacing kngcs01 Sending Asset Event to FFA FFA Order Created F-AE23WB16232-1-0 DfltHost FFA Order Acknowledged F-AE23WB16232-1-0 kngcs01 FFA Order En Route F-AE23WB16232-1-0 kngcs01 FFA Order On Site F-AE23WB16232-1-0 kngcs01 FFA Order F-AE23WB16232-1-0 Completed by technician Rob Taylor in crew kngcs01() with code A-T-303 - Distribution substation Action Taken : Replaced blown 11kv TX Site Label : 3348560 Time On modified from 21:00 23-DEC to 22:15 23-DEC | Valid | 23WB16232 |  | 6071 | 6071 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS3348560 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -26.56251335144040 | 152.009582519531 | 2023-12-23 | 1891144 | MR S COLLINS | O - Other | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | KINGAROY 1 | OT211876 | Technician: Rob Taylor Comments | OT211876 | 202312
2023-12-25 |  | 2023-12-25 | TDDI | Transformer-Distribution | Closed |  |  | 2023-12-25 | 2023-12-01 | GORDONVALE | EECL | NS | Network Site | XLTNC | 1003159 |  |  | 23/24 | 2024-06-25 | HV | 2023-12-01 | M | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-12-25 06:58 | Replace 22kV Pole Dist Sub SS2359 | 2023-12-25 | LITTLE MULGRAVE: LITTLE MULGRAVE RD | Distribution Event | Normal Event | Replace 22kV Pole Dist Sub SS2359 Sending Asset Event to FFA FFA Order Created F-AE23FN16772-1-0 DfltHost FFA Order Acknowledged F-AE23FN16772-1-0 cnsoc01 CLIFF JONES 0411720874 FFA Order En Route F-AE23FN16772-1-0 cnsoc01 FFA Order On Site F-AE23FN16772-1-0 cnsoc01 FFA Order F-AE23FN16772-1-0 Completed by technician CLIFF JONES in crew cnsoc01(0411720874) with code A-T-303 - Distribution substation Action Taken : faulty transformer replaced 10kva Site Label : 5016300 Time On modified from 23:59 25-DEC to 11:33 25-DEC | Valid | 23FN16772 |  | PEEVER NO 2 | SS2359 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS5016300 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -17.12475395202640 | 145.695495605469 | 2023-12-25 | 1891852 | MR B BATCH | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | G | Capital | Cairns Fault Response | OT212579 | Technician: CLIFF JONES Comments | OT212579 | 202312
2023-12-27 |  | 2023-12-28 | TDDI | Transformer-Distribution | Closed |  |  | 2023-12-27 | 2023-12-01 | MURGON | EECL | NS | Network Site | XCFBR | 1366955 |  |  | 23/24 | 2024-06-27 | HV | 2023-12-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Overload | 2023-12-27 15:34 | F-2622-q - EE Jack McBlane 0428 071 189 has requested Access from EDO's to replace blown Transformer 11kV Pole Dist Sub 11807. MRGCM01 | 2023-12-27 | MURGON: HOUGHTON ST | Distribution Event | Normal Event | EE Jack McBlane 0428 071 189 has requested Access from EDO's to replace blown Transformer 11kV Pole Dist Sub 11807. MRGCM01 Sending Asset Event to FFA FFA Order Created F-AE23WB16532-1-0 DfltHost Sending Asset Event to FFA Time On modified from 23:59 27-Dec to 18:57 27-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23WB16532-1-0 mrgcm01 Jack McBlane 0428071189 FFA Order En Route F-AE23WB16532-1-0 mrgcm01 FFA Order On Site F-AE23WB16532-1-0 mrgcm01 FFA Order F-AE23WB16532-1-0 Completed by technician Jack McBlane in crew mrgcm01(0428071189) with code A-T-28 - Overload Action Taken : tx was blown and replaced Site Label : 3010711 Actual Power Restoration for F-AE23WB16532-1-0: 28-DEC-2023 07:17:00 | Valid | 23WB16532 |  | 11807 | 11807 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Storm Electrical | NS3010711 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -26.23095321655270 | 151.956405639648 | 2023-12-27 | 1893008 | MRS K DUNN | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | MURGON | OT213702 | Technician: Jack McBlane Comments | OT213702 | 202312
2023-12-27 |  | 2023-12-27 | TDDI | Transformer-Distribution | Closed |  |  | 2023-12-27 | 2023-12-01 | TOWNSVILLE | EECL | NS | Network Site | XLHBT | 1811501 |  |  | 23/24 | 2024-06-27 | HV | 2023-12-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-12-27 08:33 | 11kV Pole Dist Sub TVS135 - Crew advised Tx replacement | 2023-12-27 | GARBUTT: DALRYMPLE RD | Distribution Event | Normal Event | 11kV Pole Dist Sub TVS135 - Crew advised Tx replacement Sending Asset Event to FFA FFA Order Created F-AE23NQ15322-1-0 DfltHost FFA Order Acknowledged F-AE23NQ15322-1-0 twvfr04 Tynan Dugdell 0409137912 FFA Order En Route F-AE23NQ15322-1-0 twvfr04 FFA Order On Site F-AE23NQ15322-1-0 twvfr04 Restoration Comments for F-AE23NQ15322-1-0 by twvfr04: TX change. FFA Order F-AE23NQ15322-1-0 referred with code:R050 description:Insufficient Skills or Equipment by Tynan Dugdell 0409137912 pleas send to Glenn Morris on pad twvoh08 FFA Order cancelled.F-AE23NQ15322-1-0 Sending Asset Event to FFA FFA Order Created F-AE23NQ15322-1-1 DfltHost Updated outage end time Time On modified from 23:59 27-Dec to 16:00 27-Dec Sending Asset Event to FFA Time On modified from 16:00 27-Dec to 15:42 27-Dec Sending Asset Event to FFA FFA Order Acknowledged F-AE23NQ15322-1-1 twvoh08 Glenn Morris 0437017487 FFA Order En Route F-AE23NQ15322-1-1 twvoh08 FFA Order On Site F-AE23NQ15322-1-1 twvoh08 FFA Order F-AE23NQ15322-1-1 Completed by technician Glenn Morris in crew twvoh08(0437017487) with code A-T-303 - Distribution substation Action Taken : REPLACED TX Site Label : 2029986 Actual Power Restoration for F-AE23NQ15322-1-1: 27-DEC-2023 16:28:00 | Invalid | 23NQ15322 | Sub, Garbutt No.03 11kV feeder | TVS135 | TVS135 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS2029986 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -19.27240174239820 | 146.770770804415 | 2023-12-27 | 1892808 | CLARK EQUIPMENT SALES PTY LTD | LV - Low voltage (dim lights) | EECL | Transformers Return to Service | D2002 | North Queensland | 11kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | J | Capital | TOWNSVILLE RR | OT213528 | Technician: Glenn Morris Comments | OT213528 | 202312
2023-12-28 |  | 2023-12-28 | TDDI | Transformer-Distribution | Closed |  |  | 2023-12-28 | 2023-12-01 | INNISFAIL | EECL | NS | Network Site | XLTNI | 932877 |  |  | 23/24 | 2024-06-28 | HV | 2023-12-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-12-28 04:55 | 22kV Pole Dist Sub SS7766 , multiple fault calls | 2023-12-28 | MOURILYAN: NEW HARBOUR LINE RD NEW HARBOURLINE: NEW HARBOURLINE RD | Distribution Event | Normal Event | 22kV Pole Dist Sub SS7766 , multiple fault calls Sending Asset Event to FFA FFA Order Created F-AE23FN16888-1-0 DfltHost FFA Order Acknowledged F-AE23FN16888-1-0 insoc01 Dan Colls 0437304684 FFA Order En Route F-AE23FN16888-1-0 insoc01 FFA Order On Site F-AE23FN16888-1-0 insoc01 Dan advised TX needs replacing. He is heading back to depot to arrange. Sending Asset Event to FFA Time On modified from 23:59 28-Dec to 12:00 28-Dec Sending Asset Event to FFA Time On modified from 12:00 28-Dec to 09:42 28-Dec Sending Asset Event to FFA FFA Order F-AE23FN16888-1-0 Completed by technician Dan Colls in crew INSOC01(0437304684) with code A-T-303 - Distribution substation Action Taken : Replaced faulty 50 kVa Transformer. Site Label : 5035623 Actual Power Restoration for F-AE23FN16888-1-0: 28-DEC-2023 09:51:00 auto-completed | Invalid | 23FN16888 |  | PHILLIPS | SS7766 |  | HV or LV Fuse blown | Completed | Unplanned Outage | Hot | NS5035623 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -17.61419677734380 | 146.059432983398 | 2023-12-28 | 1893096 | MRS A PENNISI | O - Other | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | G | Capital | INNISFAIL 1 | OT213785 | Technician: Dan Colls Comments | OT213785 | 202312
2023-12-28 |  | 2023-12-28 | TDDI | Transformer-Distribution | Closed |  |  | 2023-12-28 | 2023-12-01 | INNISFAIL | EECL | NS | Network Site | XLTNI | 1286377 |  |  | 23/24 | 2024-06-28 | HV | 2023-12-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-12-28 10:19 | Crew advised access required to replace TX | 2023-12-28 | LEVER ESTATE: CUTHILL RD | Distribution Event | Normal Event | Crew advised access required to replace TX F-2804-s Sending Asset Event to FFA FFA Order Created F-AE23FN16904-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 28-Dec to 16:18 28-Dec Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE23FN16904-1-0 inscs03 Dan Colls 043730468 FFA Order En Route F-AE23FN16904-1-0 inscs03 FFA Order On Site F-AE23FN16904-1-0 inscs03 FFA Order F-AE23FN16904-1-0 Completed by technician Dan Colls in crew INSCS03(043730468) with code A-T-303 - Distribution substation Action Taken : Replaced faulty 25 kVa Transformer. Site Label : 5111276 auto-completed | Invalid | 23FN16904 | Unknown | Silkwood Recl FC | T2.386.FC |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Hot | NS5111276 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -17.72446823120120 | 145.982666015625 | 2023-12-28 | 1893176 | MR A JACKSON | O - Other | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | G | Capital | INNISFAIL 1 | OT213860 | Technician: Dan Colls Comments | OT213860 | 202312
2023-12-29 |  | 2023-12-30 | TDDI | Transformer-Distribution | Closed |  |  | 2023-12-29 | 2023-12-01 | TULLY | EECL | NS | Network Site | XLHBY | 1136788 |  |  | 23/24 | 2024-06-29 | HV | 2023-12-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2023-12-29 20:30 | F-2815-s 22kV Pole Dist Sub SS3008 - Crew replaced 200kVA transformer due to a lot of recent outages. SL 5208009. (S Gregory). | 2023-12-29 | TULLY: BLACKMAN ST, BRYANT ST, COOK ST, MURRAY ST, THURLES ST, WEBB ST | Distribution Event | Normal Event | 22kV Pole Dist Sub SS3008 (15 Webb Street), multiple loss of supply calls suggest possible fault at this location. Issued to Shane Waters 0437 713 405, tlyloc01. Sending Asset Event to FFA FFA Order Created F-AE23FN16967-1-0 DfltHost FFA Order Acknowledged F-AE23FN16967-1-0 tlyloc01 Shane Waters 0437713405 FFA Order En Route F-AE23FN16967-1-0 tlyloc01 FFA Order On Site F-AE23FN16967-1-0 tlyloc01 Crews advised replacing TX SS3008 Time On modified from 23:59 29-Dec to 23:30 29-Dec Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:30 29-Dec to 00:30 30-Dec Sending Asset Event to FFA Time On modified from 00:30 30-Dec to 00:07 30-Dec Sending Asset Event to FFA FFA Order F-AE23FN16967-1-0 Completed by technician Shane Waters in crew TLYLOC01(0437713405) with code A-T-303 - Distribution substation Action Taken : Replace 200KvA Tx at SS3008 ,due to many power outages at this location over the last couple of months Site Label : 5208009 Actual Power Restoration for F-AE23FN16967-1-0: 30-DEC-2023 01:22:00 auto-completed Updated Reasons tab. Reason for Event changed from Unknown | Valid | 23FN16967 |  | SUB NO:3008 | SS3008 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Hot | NS5208009 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -17.92772865295410 | 145.926544189453 | 2023-12-29 | 1893699 | U Unknown |  | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | G | Capital | TULLY | OT214309 | Technician: Shane Waters Comments | OT214309 | 202312
2023-12-31 |  | 2024-01-02 |  |  | Closed |  |  | 2023-12-31 | 2023-12-01 | MIDDLEMOUNT | EECL | NT | Network Slot | XCFZD | 2246520 |  |  | 23/24 | 2024-06-30 | HV | 2023-12-01 | M | Internal Fault | Broken | Tx, Tank Body | Outage | South | Severe Weather | 2023-12-31 16:34 | F-2736-q 22kV Pole Dist Sub 359005 - Crew failed transformer after storm damage (S Gregory). | 2023-12-31 | MIDDLEMOUNT: CLARENCE BAKER DR, HINDLE ST, O'ROURKE TCE | Distribution Event | Normal Event | 22kV Pole Dist Sub 359005 to be replaced Sending Asset Event to FFA FFA Order Created F-AE24CA0046-1-0 DfltHost Time On modified from 23:59 01-Jan to 15:20 01-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA0046-1-0 mdmcm02 Ben Russell 0428783428 FFA Order En Route F-AE24CA0046-1-0 mdmcm02 FFA Order On Site F-AE24CA0046-1-0 mdmcm02 FFA Order En Route F-AE24CA0046-1-0 mdmcm02 FFA Order On Site F-AE24CA0046-1-0 mdmcm02 FFA Order F-AE24CA0046-1-0 Completed by technician Ben Russell in crew mdmcm02(0428783428) with code A-T-317 - Severe Weather Action Taken : tx failed after storm damage Site Label : 359005 Time On modified from 15:20 01-JAN to 14:47 01-JAN Added notes to Reasons tab. | Invalid | 24CA0046 | HINDLE ST MDM | HINDLE ST MDM | 359005 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Storm Electrical | SP-161446 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | #N/A | #N/A | 2023-12-31 | 1894566 | MS B COTTERELL | L - Life Threatening | EECL | Forced Regulated | CEFR | Capricornia | 22kV | MS B COTTERELL | M0209 | M0001 | M0070 |  | G | Operational | MIDDLEMOUNT | OT215165 | ToughPad Location: Site Label Entered:359005 Component: TDDI Component Mod: OC Technician: Ben Russell Comments | OT215165 | 202312
2024-01-03 |  | 2024-01-03 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-03 | 2024-01-01 | SARINA | EECL | NS | Network Site | XLFPS | 1460396 |  |  | 23/24 | 2024-07-03 | HV | 2024-01-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2024-01-03 08:37 | F-2873-s SARI - Western Fdr: Crew to replace Sub 1089 | 2024-01-03 | BLUE MOUNTAIN: BORGS RD | Distribution Event | Normal Event | Crew to replace Sub 1089 Sending Asset Event to FFA FFA Order Created F-AE24MK0069-1-0 DfltHost Asset selection modified Sending Asset Event to FFA FFA Order Acknowledged F-AE24MK0069-1-0 saroc01 Ben Richardson 0438791641 FFA Order En Route F-AE24MK0069-1-0 saroc01 FFA Order On Site F-AE24MK0069-1-0 saroc01 Asset selection modified Sending Asset Event to FFA FFA Order Created F-AE24MK0069-1-1 DfltHost Time On modified from 17:00 03-Jan to 15:30 03-Jan Sending Asset Event to FFA FFA Order F-AE24MK0069-1-0 Completed by technician Ben Richardson in crew saroc01(0438791641) with code A-T-303 - Distribution substation Action Taken : Replaced 10kVA Swer TX Site Label : 4213923 FFA Order F-AE24MK0069-1-0 Completed by technician Ben Richardson in crew saroc01(0438791641) with code A-T-303 - Distribution substation Action Taken : Replaced 10kVA Swer TX Site Label : 4213923 FFA Order cancelled.F-AE24MK0069-1-1 FFA Order F-AE24MK0069-1-0 Completed by technician Ben Richardson in crew saroc01(0438791641) with code A-T-303 - Distribution substation Action Taken : Replaced 10kVA Swer TX Site Label : 4213923 | Valid | 24MK0069 | Blue Mountains SWER | Blue Mountains SWER | 226.FC | LKS255 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Hot | NS4213923 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -21.5284271240234 | 149.002334594727 | 2024-01-03 | 1895580 | RACECOURSE PROJECTS PTY LTD | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Mackay | 12.7kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | I | Capital | SARINA | OT216091 | Technician: Ben Richardson Comments | OT216091 | 202401
2024-01-04 |  | 2024-01-04 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-04 | 2024-01-01 | TOWNSVILLE | EECL | NS | Network Site | XLHBT | 1750523 |  |  | 23/24 | 2024-07-04 | HV | 2024-01-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-01-04 18:45 | F-965-t 11kV Pole Dist Sub TVS1584 - multiple fault calls for los beyond sub LV | 2024-01-04 | KELSO: STRAWBERRY RD | Distribution Event | Normal Event | 11kV Pole Dist Sub TVS1584 - multiple fault calls for los beyond sub LV Sending Asset Event to FFA FFA Order Created F-AE24NQ0307-1-0 DfltHost FFA Order Acknowledged F-AE24NQ0307-1-0 twvoc02 Clint Pearce 0408064502 FFA Order En Route F-AE24NQ0307-1-0 twvoc02 FFA Order On Site F-AE24NQ0307-1-0 twvoc02 Sending Asset Event to FFA Crew advise that Conductor has burnt off LV Transformer Bushing. Sheet F-965-t written for access to transformer . Sending Asset Event to FFA FFA Order En Route F-AE24NQ0307-1-0 twvoc02 FFA Order On Site F-AE24NQ0307-1-0 twvoc02 Time On modified from 23:59 04-Jan to 22:37 04-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24NQ0307-1-0 Completed by technician Clint Pearce in crew TWVOC02(0408064502) with code A-T-303 - Distribution substation Action Taken : Obtained HV Access on TVS1584, replaced a burnt up LV bridge on C Phase from LV fuse to LV bushing on transformer. Site Label : 2006378 Actual Power Restoration for F-AE24NQ0307-1-0: 04-JAN-2024 22:46:00 auto-completed | Valid | 24NQ0307 | Sub, Rasmussen No.06 11kV feeder | TVS1584 | TVS1584 |  | Unknown | Completed | Unplanned Outage | Hot | NS2006378 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -19.41001494730930 | 146.717098430752 | 2024-01-04 | 1896071 | MRS S HEMA | U - Unknown / No Power | EECL | Forced Regulated | NQFR | North Queensland | 11kV | MRS S HEMA | M0209 | M0001 | M9999 |  | J | Operational | TOWNSVILLE RR | OT216486 | Technician: Clint Pearce Comments Obtained HV Access on TVS1584, replaced a burnt up LV bridge on C Phase from LV fuse to LV bushing on transformer. | OT216486 | 202401
2024-01-05 |  | 2024-01-06 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-05 | 2024-01-01 | YEPPOON | EECL | NS | Network Site | XLFPY | 1686159 |  |  | 23/24 | 2024-07-05 | HV | 2024-01-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-01-05 19:55 | 11kV Pole Dist Sub 111119 - Crew replaced transformer. SL 4143149. (S Gregory). | 2024-01-05 | BANGALEE: CULGOA ST, KIAMA AVE, MIRRAWENA AVE | Distribution Event | Normal Event | Fault calls indicate possible issue with 11kV Pole Dist Sub 111119 ccoc03 Sending Asset Event to FFA FFA Order Created F-AE24CA0445-1-0 DfltHost FFA Order Acknowledged F-AE24CA0445-1-0 ccoc03 Don Kerr 0418748384 FFA Order En Route F-AE24CA0445-1-0 ccoc03 FFA Order On Site F-AE24CA0445-1-0 ccoc03 crew advise TX FIS C phase 190V crew to replace in the morning Time On modified from 23:59 05-Jan to 14:59 06-Jan Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 14:59 06-Jan to 13:07 06-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24CA0445-1-0 Completed by technician Don Kerr in crew ccoc03(0418748384) with code A-T-303 - Distribution substation Action Taken : tx needs replacing Site Label : 4143149 Updated Reasons tab. Reason for Event changed from Unknown | Valid | 24CA0445 | YEPP-FARNBOROUGH | Farnborough Rd | YP111 | X5710 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Hot | NS4143149 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -23.07536315917970 | 150.762969970703 | 2024-01-05 | 1896372 | DADDO INVESTMENTS PTY LTD | O - Other | EECL | Transformers Return to Service | D2002 | Capricornia | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | YEPPOON | OT216746 | .HEADING Technician: Don Kerr Comments tx requires replacement Technician: Don Kerr Comments | OT216746 | 202401
2024-01-06 |  | 2024-01-06 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-06 | 2024-01-01 | MACKAY | EECL | NS | Network Site | XLFPK | 1502830 |  |  | 23/24 | 2024-07-06 | HV | 2024-01-01 |  | Corrosion | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2024-01-06 14:39 | F-2909-s -11kV Pole Dist Sub 6866 - Crew replaced 200kVA transformer. SL 2087759. (S Gregory). | 2024-01-06 | MACKAY: EVAN ST, WENTFORD ST | Distribution Event | Normal Event | 11kV Pole Dist Sub 6866 , Multiple fcs at this TX , possible blown TX fuse Sending Asset Event to FFA FFA Order Created F-AE24MK0188-1-0 DfltHost FFA Order Acknowledged F-AE24MK0188-1-0 mckoc01 Liam Scott 0409913086 FFA Order En Route F-AE24MK0188-1-0 mckoc01 FFA Order On Site F-AE24MK0188-1-0 mckoc01 Reason for Event changed from HV or LV Fuse blown Sending Asset Event to FFA Switching Sheet Written Switch Sheet Distributed Sending Asset Event to FFA Time On modified from 23:59 06-Jan to 19:00 06-Jan Sending Asset Event to FFA FFA Order En Route F-AE24MK0188-1-0 mckoc01 FFA Order On Site F-AE24MK0188-1-0 mckoc01 Crew still working Time On modified from 19:00 06-Jan to 20:00 06-Jan Sending Asset Event to FFA Time On modified from 20:00 06-Jan to 20:30 06-Jan Sending Asset Event to FFA Time On modified from 20:30 06-Jan to 19:45 06-Jan Sending Asset Event to FFA FFA Order F-AE24MK0188-1-0 Completed by technician Liam Scott in crew mckoc01(0409913086) with code A-T-315 - Service Asset Fault Action Taken : replaced blown 200kva tx Site Label : 2087759 Actual Power Restoration for F-AE24MK0188-1-0: 06-JAN-2024 20:13:00 auto-completed Added notes to Reasons tab. Updated Event Trigger from SAF to Distribution substation. | Valid | 24MK0188 |  | EVAN ST | 6866 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS2087759 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -21.1520328521729 | 149.190383911133 | 2024-01-06 | 1896477 | MR A KEOGH | O - Other | EECL | Transformers Return to Service | D2002 | Mackay | 11kV | Transformers Return to Service | M0209 | M0052 | M0011 |  | J | Capital | MACKAY 2 | OT216835 | Technician: Liam Scott Comments | OT216835 | 202401
2024-01-07 |  | 2024-05-08 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-07 | 2024-01-01 | ISLAND COMM | EECL | NS | Network Site | XLTNG | 6892924 |  |  | 23/24 | 2024-07-07 | HV | 2024-01-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2024-01-07 08:10 | SS585224 appears to have failed in service. F-2913-s - DAIS Fdr 3 tripped on OC LV of SS585224 split between SS11214 and SS6118 to allow time for replacement of SS585224. SS585224 replaced under planned outage 24FN2365. (S Gregory). | 2024-01-07 | DARNLEY ISLAND: ERUB ISLAND RD, MEDIGEE VILLAGE, ROAD NO 7, ROAD NO 8 | Distribution Event | Normal Event | DAIS Fdr 3 tripped on OC. Power station attendant advises attempt to reclose failed, tripped on OC again. Thursday island to be advised. Manual Reclose Checklist Sending Asset Event to FFA FFA Order Created F-AE24FN0215-1-0 DfltHost FFA Order Acknowledged F-AE24FN0215-1-0 thioc01 Rua Tabua 0439490124 FFA Order En Route F-AE24FN0215-1-0 thioc01 Sending Asset Event to FFA FFA Order On Site F-AE24FN0215-1-0 thioc01 crew patrolled fdr - no faults found. Tested fdr exit cable - OK. Fdr tripped when SS585224 EDOs closed. AP issued to inspect sub Asset selection modified Sending Asset Event to FFA Crew removed LA's but Feeder tripped again when EDO's closed. TX will need to be replaced but crew unsure when this will occur, looking at supplying customers from adjacent LV, yet to be comfirmed. Reason for Event changed from Unknown Sending Asset Event to FFA LV of SS585224 has been temporarily split between SS11214 & SS6118 until TX SS585224 can be replaced. Crew require dead changeover on reversal as LV Phasing has not been confirmed. Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Suspended F-AE24FN0215-1-0 by Rua Tabua 0439490124 follow up work required. 22kV 3/315 replacement required Time On modified from 23:59 07-Jan to 23:59 09-Jan Sending Asset Event to FFA FFA Order En Route F-AE24FN0215-1-0 thioc01 FFA Order On Site F-AE24FN0215-1-0 thioc01 FFA Order F-AE24FN0215-1-0 Completed by technician Rua Tabua in crew thioc01(0439490124 ) with code A-T-303 - Distribution substation Action Taken : sub station not serviceable outage area supply restored via tied in follow up work required to replace Tx Site Label : SS585224 Time On modified from 23:59 09-Jan to 23:59 10-Jan Time On modified from 23:59 10-Jan to 23:59 12-Jan Jason Jia advised attempting to arrange equipment and plant to replace the transformer and advised to push out to 12/02/2024 at this stage and he can advised further updates as they become available Time On modified from 23:59 12-Jan to 23:59 12-Feb NFI Time On modified from 23:59 12-Feb to 23:59 19-Feb Time On modified from 23:59 19-Feb to 23:59 23-Feb Asset selection modified Updated customers due to comments above stating LV restored from adjacent subs 7/1/24 Transformer to be replaced on planned outage 24FN2365 25/02/24 Time On modified from 23:59 23-Feb to 15:06 22-Feb Added notes to Reasons tab. | Valid | 24FN0215 | DAIS-DARNLEY 3 | DARNLEY IS NO 3 | 2DA3 | 2DA3 CIRCUIT BREAKER | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS5163467 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2024-01-07 | 1896561 | U Unknown |  | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | G | Capital | THURSDAY ISLAND | OT216907 | Technician: Rua Tabua Comments 22 kV 3/ 315kVA transformer required for replacement | OT216907 | 202401
2024-01-07 |  | 2024-01-13 |  |  | Closed |  |  | 2024-01-07 | 2024-01-01 | EMERALD | EECL | FC | Feeder Section | DUMMY | 131003 |  |  | 23/24 | 2024-07-07 | HV | 2024-01-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-01-07 08:31 | F-2118-r EMERALD 19kV Gordon Rd X783038 ACR CB tripped. SCADA Interface automated outage. Crew replaced 19.1kV SWER Pole Dist Sub 272661. SL 4023385. (S Gregory). | 2024-01-07 | CAPELLA: GLENCOE RD, KILGOUR RD, MAGENTA RD, YAN YAN RD, LILYVALE RD, CUDDERSON RD EMERALD: GORDON RD | Distribution Event | Normal Event | entered from the SCADA Interface Matt Armstrong Adv MRC Attempt No1 Depot Co-ord Advised Sending Asset Event to FFA FFA Order Created F-AE24CA0470-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA0470-1-0 emlcs02 Hannah Carle 0459742691 FFA Order En Route F-AE24CA0470-1-0 emlcs02 F-2118-r Sending Asset Event to FFA Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA 16:25 hrs - Reclose with Reg Load opened failed.. Sending Asset Event to FFA 16:34 hrs - Reclose with Reg line fuse opened failed Sending Asset Event to FFA 16:50 hrs - X783041 Load Link for ACR X783038 is opened to test energise ACR - Successful. Sending Asset Event to FFA 17:25 hrs - MRC success with LLC opened at Pole 4023384. Crew to investigate faulted section. Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA MRC done with TX 272511 & TX 592663 HV fuses opened with Tee-Off to TX 272661 in circuit.Failed. Crew to isolate LLC at tee-Off to TX 272661 and Feeder to be reclosed.. Sending Asset Event to FFA Fault between LLC at Pole 4023387 & TX 272661. Asset selection modified Time On modified from 23:59 07-Jan to 23:59 16-Jan Reason for Event changed from Unknown Sending Asset Event to FFA Time On modified from 23:59 16-Jan to 23:59 13-Jan Sending Asset Event to FFA Sending Asset Event to FFA emlll01 Sending Asset Event to FFA Time On modified from 23:59 13-Jan to 10:17 13-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA0470-1-0 emlll01 Michael 0488703194 FFA Order En Route F-AE24CA0470-1-0 emlll01 FFA Order On Site F-AE24CA0470-1-0 emlll01 FFA Order F-AE24CA0470-1-0 Completed by technician Michael in crew emlll01(0488703194) with code A-T-184 - Transformer Trip - Zone Sub Action Taken : replace transformer 272661 Site Label : 4023385 Added notes to Reasons tab. Updated Event Trigger from Lightnig to Distribution substation. | Invalid | 24CA0470 | X8133/EM256 Gordon Rd SWER | Gordon Rd | EM256X783038 | Gordon Rd | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | FC-19-58229 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2024-01-07 | 1896566 | U Unknown |  | EECL | Forced Regulated | CEFR | Capricornia | 19kV | U Unknown | M0209 | M0001 | M9999 |  | H | Operational | EMERALD | OT216910 |  | OT216910 | 202401
2024-01-10 |  | 2024-01-10 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-10 | 2024-01-01 | HOME HILL | EECL | NS | Network Site | XLHBH | 1720465 |  |  | 23/24 | 2024-07-10 | HV | 2024-01-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2024-01-10 07:53 | F-2942-s - 11kV Pole Dist Sub BDS1041 requires replacement due to failure | 2024-01-10 | AYR: MAIDAVALE RD | Distribution Event | Normal Event | F-2942-s - 11kV Pole Dist Sub BDS1041 requires replacement due to failure Andrew Washbourne Sending Asset Event to FFA FFA Order Created F-AE24NQ0577-1-0 DfltHost Time On modified from 23:59 10-Jan to 14:06 10-Jan Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ0577-1-0 hhloc01 Andrewwashbourne 0408689718 FFA Order En Route F-AE24NQ0577-1-0 hhloc01 FFA Order On Site F-AE24NQ0577-1-0 hhloc01 FFA Order F-AE24NQ0577-1-0 Completed by technician Andrewwashbourne in crew hhloc01(0408689718) with code A-T-303 - Distribution substation Action Taken : REPLACED TX NST - .19 Site Label : 5000808 Actual Power Restoration for F-AE24NQ0577-1-0: 10-JAN-2024 14:27:00 auto-completed | Invalid | 24NQ0577 | Sub, Ayr No.6 11kV feeder | BDS1041 | BDS1041 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS5000808 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -19.6245174407959 | 147.361404418945 | 2024-01-10 | 1897319 | FOR RW PM & RK DOWSON | P - Phase Down (LV) | EECL | Transformers Return to Service | D2002 | North Queensland | 11kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | J | Capital | HOME HILL 2 | OT217446 | .HEADING Technician: Andrewwashbourne Comments REPLACED TX NST - .19 | OT217446 | 202401
2024-01-10 |  | 2024-01-10 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-10 | 2024-01-01 | TOOWOOMBA | EECL | NS | Network Site | XLGDT | 1491674 |  |  | 23/24 | 2024-07-10 | HV | 2024-01-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2024-01-10 07:38 | F-2155-r 11kV Pole Dist Sub PE09972, failed in service, to be replaced | 2024-01-10 | CROWS NEST: PIERCES CREEK RD | Distribution Event | Normal Event | 11kV Pole Dist Sub PE09972, failed in service, to be replaced F-2155-r twmoc01 Sending Asset Event to FFA FFA Order Created F-AE24SW0742-1-0 DfltHost FFA Order Acknowledged F-AE24SW0742-1-0 twmoc01 FFA Order En Route F-AE24SW0742-1-0 twmoc01 Time On modified from 23:59 10-Jan to 18:43 10-Jan Sending Asset Event to FFA FFA Order On Site F-AE24SW0742-1-0 twmoc01 FFA Order F-AE24SW0742-1-0 Completed by technician James Gough in crew twmoc01() with code A-T-303 - Distribution substation Action Taken : Replaced 10 kva TX with 25kva single phase Site Label : 5250878 Actual Power Restoration for F-AE24SW0742-1-0: 10-JAN-2024 20:34:00 | Valid | 24SW0742 | DJ & GP GILLIS. PIERCES CREEK ROAD, CROWS NEST | PE09972 | PE09972 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS5250878 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -27.14816856384280 | 152.019744873047 | 2024-01-10 | 1897318 | MRS J WEBLIN | O - Other | EECL | Transformers Return to Service | D2002 | South West | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | TOOWOOMBA RAPIDS | OT217445 | Technician: James Gough Comments | OT217445 | 202401
2024-01-10 |  | 2024-02-01 | RGDI | Regulator-Distribution | Closed |  |  | 2024-01-10 | 2024-01-01 | NTH BEACHES | EECL | NS | Network Site | XLTNC | 8667964 |  |  | 23/24 | 2024-07-10 | HV | 2024-01-01 |  | Unknown | Broken | Regulator, Unknown | Outage | North | HV-Unassisted failure(Apparent defect) | 2024-01-10 21:22 | F-2948-s - KAMERUNGA 22kV Bluewater Fdr CB F15Q00 tripped. SCADA Interface automated outage. Three tank regulator pole RG792957 shorted out between tanks, no cause found. Requires replacement. SL 11215602. (S Gregory). | 2024-01-10 | SMITHFIELD, TRINITY BEACH, TRINITY PARK | Distribution Event | Normal Event | entered from the SCADA Interface OC Trip to lock out. issued to Liam Duncan 0437 825 412 Crew ID - cnsoc01 second on call crew have been dispatched. Depot Co-ord Advised Sending Asset Event to FFA FFA Order Created F-AE24FN0355-1-0 DfltHost FFA Order Acknowledged F-AE24FN0355-1-0 cnsoc01 Liam Duncan 0437825412 Crews have patrolled sections of lines where reports of lines down were. All wires are in the air but Regs RG792957 have failed in service. Crews are isolation the regs now and placing it into bypass. Manual Reclose Checklist Sending Asset Event to FFA MRC Failed, crews to continue patrolling. Sending Asset Event to FFA Crews are still patrolling. Time On modified from 23:59 10-Jan to 23:59 11-Jan Sending Asset Event to FFA Crews have completed a full line patrol of all the overhead with no fault found. Crews to sectionalise at Sub SS8101 and try another MRC Asset selection modified Sending Asset Event to FFA Crews to open Gas Switch GS816748 and try restore part power. Asset selection modified Sending Asset Event to FFA Crews to try restore power upto Open ACR BE5 Asset selection modified Sending Asset Event to FFA All power restored. Only fault found was the Faulty Reg. unsure why the first MRS failed. Sycon 24FN0360 raised. Time On modified from 23:59 11-Jan to 01:12 11-Jan Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order En Route F-AE24FN0355-1-0 cnsoc01 FFA Order On Site F-AE24FN0355-1-0 cnsoc01 FFA Order F-AE24FN0355-1-0 Completed by technician Liam Duncan in crew cnsoc01(0437825412) with code A-T-315 - Service Asset Fault Action Taken : 3 tank regulator pole RG792957 shorted out between tanks. no cause found, may have been a snake but nothing left. requires replacement. occ has raised a syscon. Site Label : 11215602 auto-completed Added notes to Reasons tab. Updated Event Trigger from SAF to HV-Unassisted failure. | Valid | 24FN0355 | KAME-BLUEWATER | BLUEWATER | 2BLW | F15Q00 22KV BLUEWATER CB | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS11215602 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2024-01-10 | 1897567 | U Unknown |  | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0399 | M0001 | M9999 |  | G | Capital | Cairns Fault Response | OT217600 | .HEADING Technician: Liam Duncan Comments 3 tank regulator pole RG792957 shorted out between tanks. no cause found, may have been a snake but nothing left. requires replacement. occ has raised a syscon. PO has raised WR - 1897580 for the replacement of these Reg tanks. | OT217600 | 202401
2024-01-12 |  | 2024-01-13 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-12 | 2024-01-01 | TOOWOOMBA | EECL | NS | Network Site | XLGDT | 1524814 |  |  | 23/24 | 2024-07-12 | HV | 2024-01-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-01-12 14:06 | F-30480-g 11kV Pole Dist Sub PE08703 blown to be replaced | 2024-01-12 | OAKEY: MCKENZIE RD | Distribution Event | Normal Event | 11kV Pole Dist Sub PE08703 blown to be replaced Sending Asset Event to FFA FFA Order Created F-AE24SW0972-1-0 DfltHost Time On modified from 23:59 12-Jan to 23:59 13-Jan Sending Asset Event to FFA to be replaced Sat Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW0972-1-0 twmoc01 Baden Berger 0451002449 FFA Order En Route F-AE24SW0972-1-0 twmoc01 FFA Order On Site F-AE24SW0972-1-0 twmoc01 Time On modified from 23:59 13-Jan to 11:33 13-Jan Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW0972-1-0 Completed by technician Baden Berger in crew twmoc01(0451002449) with code A-T-303 - Distribution substation Action Taken : replaced TX Site Label : 3090419 Time On modified from 11:33 13-JAN to 13:47 13-JAN | Valid | 24SW0972 | Commens, Oakey | PE08703 | PE08703 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS3090419 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -27.399679183960 | 151.651962280273 | 2024-01-12 | 1898081 | MR B BULLOCK | P - Phase Down (LV) | EECL | Transformers Return to Service | D2002 | South West | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | TOOWOOMBA RAPIDS | OT217928 | Technician: Baden Berger Comments | OT217928 | 202401
2024-01-13 |  | 2024-01-16 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-13 | 2024-01-01 | CLONCURRY | EECL | NS | Network Site | XCHBL | 926878 |  |  | 23/24 | 2024-07-13 | HV | 2024-01-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-01-13 09:22 | F-2972-s - Crew require HV access to replace 19.1kV SWER Pole Dist Sub CLS129 | 2024-01-13 | CLONCURRY: THREE WAYS RD | Distribution Event | Normal Event | Crew require HV access to replace 19.1kV SWER Pole Dist Sub CLS129 issued to Kurt Duncan clccmcs01 Sending Asset Event to FFA FFA Order Created F-AE24NQ0684-1-0 DfltHost Sending Asset Event to FFA Time On modified from 23:59 13-Jan to 14:30 13-Jan Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 14:30 13-Jan to 14:13 13-Jan Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ0684-1-0 clccmcs01 Kurt Duncan 0427701876 FFA Order En Route F-AE24NQ0684-1-0 clccmcs01 FFA Order On Site F-AE24NQ0684-1-0 clccmcs01 FFA Order F-AE24NQ0684-1-0 Completed by technician Kurt Duncan in crew clccmcs01(0427701876) with code A-T-303 - Distribution substation Action Taken : replaced blown transformer at CLS129 Site Label : 5050295 Actual Power Restoration for F-AE24NQ0684-1-0: 13-JAN-2024 13:51:00 auto-completed | Invalid | 24NQ0684 |  | CLS129 | CLS129 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS5050295 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -20.35747718811040 | 140.269973754883 | 2024-01-13 | 1898173 | TELSTRA LIMITED | O - Other | EECL | Transformers Return to Service | D2002 | North Queensland | 19kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | H | Capital | CLONCURRY | OT218001 | .HEADING Technician: Kurt Duncan Comments | OT218001 | 202401
2024-01-15 |  | 2024-01-15 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-15 | 2024-01-01 | YEPPOON | EECL | NS | Network Site | XLFPY | 1790040 |  |  | 23/24 | 2024-07-15 | HV | 2024-01-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2024-01-15 07:06 | F-2877-q - Crew advises 22kV Pole Dist Sub 111319 needs replacing. | 2024-01-15 | BYFIELD: RICHTERS RD | Distribution Event | Normal Event | Crew advises 22kV Pole Dist Sub 111319 needs replacing. yepcm05, crew to advise isolation point on arrival. Sending Asset Event to FFA FFA Order Created F-AE24CA0841-1-0 DfltHost Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 15-Jan to 15:22 15-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA0841-1-0 yepcm05 Tom Simpson 0427554084 FFA Order En Route F-AE24CA0841-1-0 yepcm05 FFA Order On Site F-AE24CA0841-1-0 yepcm05 FFA Order F-AE24CA0841-1-0 Completed by technician Tom Simpson in crew yepcm05(0427554084) with code A-T-303 - Distribution substation Action Taken : Replaced transformer Site Label : 2005491 | Invalid | 24CA0841 | YEPP-WATERPARK | Waterpark | YP207 | X5964 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS2005491 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -22.8346004486084 | 150.660202026367 | 2024-01-15 | 1898438 | MR P RICHTER | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Capricornia | 22kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | G | Capital | YEPPOON | OT218250 | .HEADING Technician: Tom Simpson Comments will replace trx later today Technician: Tom Simpson Comments | OT218250 | 202401
2024-01-16 |  | 2024-01-17 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-16 | 2024-01-01 | CHINCHILLA | EECL | NS | Network Site | XCGDH | 1052502 |  |  | 23/24 | 2024-07-16 | HV | 2024-01-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2024-01-16 20:51 | F-2198-r - MICO - Condamine FDR (Note- Abnormally fed) Crews report 12.7kV SWER Pole Dist Sub PC03466 requires replacement | 2024-01-16 | MILES: WARREGO HWY | Distribution Event | Normal Event | Crews report 12.7kV SWER Pole Dist Sub PC03466 requires replacement Time On modified from 23:59 16-Jan to 23:59 17-Jan Crews advise will return in daylight hours to complete job. Not sent to FFA please send FFFA task to chnfr01 Sending Asset Event to FFA FFA Order Created F-AE24SW1129-1-0 DfltHost FFA Order Acknowledged F-AE24SW1129-1-0 chnfr01 Jeremy koehler 0400201688 FFA Order En Route F-AE24SW1129-1-0 chnfr01 FFA Order On Site F-AE24SW1129-1-0 chnfr01 Sending Asset Event to FFA Time On modified from 23:59 17-Jan to 10:32 17-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24SW1129-1-0 Completed by technician Jeremy koehler in crew chnfr01(0400201688) with code A-T-303 - Distribution substation Action Taken : replace blown tx Site Label : 5244864 Actual Power Restoration for F-AE24SW1129-1-0: 17-JAN-2024 10:42:00 | Valid | 24SW1129 | KILLARNEY | PC03466 | PC03466 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS5244864 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -26.64677810668950 | 150.240707397461 | 2024-01-16 | 1898998 | MRS J OSBORNE | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | South West | 12.7kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | I | Capital | CHINCHILLA | OT218607 | Technician: Jeremy koehler Comments | OT218607 | 202401
2024-01-17 |  | 2024-01-17 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-17 | 2024-01-01 | INGHAM | EECL | NS | Network Site | XCHBG | 1573358 |  |  | 23/24 | 2024-07-17 | HV | 2024-01-01 |  | Corrosion | Broken | Tx, Tank Body | Outage | North | HV-Unassisted failure(Apparent defect) | 2024-01-17 19:06 | David Brodie advised INS460 requires replacement | 2024-01-17 | ABERGOWRIE: ALAMEIN RD, EL ALAMEIN RD, LEE CREEK RD | Distribution Event | Normal Event | David Brodie advised INS460 requires replacement Sending Asset Event to FFA FFA Order Created F-AE24NQ0868-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ0868-1-0 ingcsfr02 DAVID BRODIE 0407657024 FFA Order En Route F-AE24NQ0868-1-0 ingcsfr02 FFA Order On Site F-AE24NQ0868-1-0 ingcsfr02 Time On modified from 23:59 17-Jan to 00:15 18-Jan Sending Asset Event to FFA Time On modified from 00:15 18-Jan to 23:37 17-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24NQ0868-1-0 Completed by technician DAVID BRODIE in crew INGCSFR02(0407657024) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : REPLACE INS460 Site Label : 2142035 Time On modified from 23:37 17-JAN to 23:43 17-JAN | Valid | 24NQ0868 | Sub, Lannercost No.4 11kV feeder | INS460 | INS460 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS2142035 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -18.45849800109860 | 145.924560546875 | 2024-01-17 | 1899239 | MR J CRISAFULLI | O - Other | EECL | Transformers Return to Service | D2002 | North Queensland | 11kV | Transformers Return to Service | M0209 | M0001 | M0011 |  | J | Capital | INGHAM | OT218770 | .HEADING Technician: DAVID BRODIE Comments REPLACE 63KVA TX NEW TX TD94910190 Technician: DAVID BRODIE Comments REPLACE INS460 | OT218770 | 202401
2024-01-17 |  | 2024-01-17 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-17 | 2024-01-01 | CHILDERS | EECL | NS | Network Site | XCFBC | 1437585 |  |  | 23/24 | 2024-07-17 | HV | 2024-01-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-01-17 07:14 | F-2896-q - Crew require Isolation at 11kV Pole Dist Sub 5328 to repair broken X-arm. | 2024-01-17 | CHILDERS: HUXLEY RD | Distribution Event | Normal Event | Crew require LV Isolation at 11kV Pole Dist Sub 5328 to repair broken X-arm. chlcdwgl1 Sending Asset Event to FFA FFA Order Created F-AE24WB0716-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB0716-1-0 chlcdwgl1 Nick Roffey 0427825813 FFA Order En Route F-AE24WB0716-1-0 chlcdwgl1 FFA Order On Site F-AE24WB0716-1-0 chlcdwgl1 Sending Asset Event to FFA Crew require access to replace tx Sending Asset Event to FFA Time On modified from 18:00 17-Jan to 20:00 17-Jan Sending Asset Event to FFA Time On modified from 20:00 17-Jan to 18:09 17-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE24WB0716-1-0 chlcdwgl1 FFA Order On Site F-AE24WB0716-1-0 chlcdwgl1 FFA Order F-AE24WB0716-1-0 Completed by technician Nick Roffey in crew chlcdwgl1(0427825813) with code A-T-303 - Distribution substation Action Taken : replaced Lv strain arm. transformer and all associated Lv bridging and fuses Site Label : 3063985 Time On modified from 18:09 17-JAN to 21:00 17-JAN | Invalid | 24WB0716 |  | Huxley rd | 5328 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS3063985 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -25.218240737915 | 152.260360717773 | 2024-01-17 | 1899013 | MS B BEER | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | J | Capital | CHILDERS | OT218628 | Technician: Nick Roffey Comments | OT218628 | 202401
2024-01-21 |  | 2024-01-24 |  |  | Closed |  |  | 2024-01-21 | 2024-01-01 | BARCALDINE | EECL | NT | Network Slot | XCPNB | 2674769 |  |  | 23/24 | 2024-07-21 | HV | 2024-01-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2024-01-21 20:41 | F-2251-r 22kV Pole Dist Sub 391611 Sparking and leaking oil | 2024-01-21 | BARCALDINE: CAPRICORN HWY | Distribution Event | Normal Event | 22kV Pole Dist Sub 391611 Sparking and leaking oil brccmfr02 Sending Asset Event to FFA FFA Order Created F-AE24CA1166-1-0 DfltHost Sending Asset Event to FFA Time On modified from 23:59 22-Jan to 17:00 23-Jan Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA1166-1-0 brccmfr02 Brad Heumiller 0437739195 FFA Order En Route F-AE24CA1166-1-0 brccmfr02 FFA Order On Site F-AE24CA1166-1-0 brccmfr02 Restoration Comments for F-AE24CA1166-1-0 by brccmfr02: transformer at 391611 Power station Barcaldine burning and leaking oil from Lv bush A phase isolated and earthed made safe will replace this transformer on Tuesday AM have spoken to WGL at power station and he is happen for Tuesday replacement. Read Above Sending Asset Event to FFA Reassigned to BRCCMFR01 - Gary Acton to make repairs. Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 17:00 23-Jan to 16:36 23-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA1166-1-0 brccmfr01 Jason Coveney 0437746018 FFA Order En Route F-AE24CA1166-1-0 brccmfr01 FFA Order On Site F-AE24CA1166-1-0 brccmfr01 FFA Order F-AE24CA1166-1-0 Completed by technician Jason Coveney in crew brccmfr01(0437746018) with code A-T-303 - Distribution substation Action Taken : Replaced faulty 200kva 3 phase TX Site Label : 2004771 Time On modified from 16:36 23-JAN to 17:02 23-JAN | Invalid | 24CA1166 | POWER STATION | Power Station | 391611 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | SP-162884 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2024-01-21 | 1900247 | ERGON ENERGY CORPORATION LIMIT | O - Other | EECL | Forced Regulated | CEFR | Capricornia | 22kV | ERGON ENERGY CORPORATION LIMIT | M0209 | M0052 | M9999 |  | G | Operational | BARCALDINE | OT219559 | .HEADING 9/2/24 rb100570 all costs cleared as requested 31/1/24 rb100570 journal in progress to trf to wo 7687387 | OT219559 | 202401
2024-01-22 |  | 2024-01-22 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-22 | 2024-01-01 | HOME HILL | EECL | NS | Network Site | XLHBH | 1734359 |  |  | 23/24 | 2024-07-22 | HV | 2024-01-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Overload | 2024-01-22 10:01 | Crew require access to replace BDS214 | 2024-01-22 | HOME HILL: BECKE RD | Distribution Event | Normal Event | Crew require access to replace BDS214 Sending Asset Event to FFA FFA Order Created F-AE24NQ1021-1-0 DfltHost FFA Order Acknowledged F-AE24NQ1021-1-0 hhlfr01 Steve O’Shea 0427650719 FFA Order En Route F-AE24NQ1021-1-0 hhlfr01 FFA Order On Site F-AE24NQ1021-1-0 hhlfr01 Time On modified from 23:59 22-Jan to 15:30 22-Jan Sending Asset Event to FFA FFA Order F-AE24NQ1021-1-0 Completed by technician Steve O’Shea in crew hhlfr01(0427650719 ) with code A-T-28 - Overload Action Taken : replace 200kva 3 phase tx. commissioned ok. polarity good. 233v x 3 nit = 0.1 ohms x 3 Site Label : 5211017 Actual Power Restoration for F-AE24NQ1021-1-0: 22-JAN-2024 15:35:00 auto-completed | Valid | 24NQ1021 | Sub, HomeHill No.7 11kV feeder | BDS214 | BDS214 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS5211017 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -19.69911575317380 | 147.403610229492 | 2024-01-22 | 1900358 | OSMENKENS CORP PTY LTD | P - Phase Down (LV) | EECL | Transformers Return to Service | D2002 | North Queensland | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | HOME HILL 2 | OT219638 | .HEADING Technician: Steve O Shea Comments replace 200kva 3 phase tx. commissioned ok. polarity good. 233v x 3 nit = 0.1 ohms x 3 | OT219638 | 202401
2024-01-22 |  | 2024-01-23 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-22 | 2024-01-01 | MONTO | EECL | NS | Network Site | XCFZT | 921601 |  |  | 23/24 | 2024-07-22 | HV | 2024-01-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-01-22 20:42 | F-30731-g Crew request isolation from 11kV Dropout Fuse S7614 to replace tx 239339 | 2024-01-22 | MONTO: GLADSTONE RD | Distribution Event | Normal Event | Crew request isolation from 11kV Dropout Fuse S7614 to replace tx 239339 Alistair, moncmfr02 Sending Asset Event to FFA FFA Order Created F-AE24CA1219-1-0 DfltHost Time On modified from 23:59 22-Jan to 23:59 23-Jan Sending Asset Event to FFA Sending Asset Event to FFA crew will return 23/01 Sending Asset Event to FFA F-30731-g Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 23-Jan to 09:58 23-Jan Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA1219-1-0 moncmfr02 Alistair MacDonald 0438185372 FFA Order En Route F-AE24CA1219-1-0 moncmfr02 Sending Asset Event to FFA FFA Order On Site F-AE24CA1219-1-0 moncmfr02 FFA Order F-AE24CA1219-1-0 Completed by technician Alistair MacDonald in crew moncmfr02(0438185372) with code A-T-303 - Distribution substation Action Taken : Replaced 1 x 10 Iva transformer Site Label : 4144079 | Valid | 24CA1219 |  | S7614 | S7614 | S7614 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Hot | NS4144079 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -24.77424430847170 | 151.210845947266 | 2024-01-22 | 1900661 | MS P GEORGE | F - Fire - Pole/Structure | EECL | Transformers Return to Service | D2002 | Capricornia | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | MONTO | OT219859 | Technician: Alistair MacDonald Comments | OT219859 | 202401
2024-01-22 |  | 2024-01-23 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-22 | 2024-01-01 | DALBY | EECL | NS | Network Site | XLGDD | 1631155 |  |  | 23/24 | 2024-07-22 | HV | 2024-01-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | South | HV-Unassisted failure(Apparent defect) | 2024-01-22 16:05 | Crew require acces to replace Transformer | 2024-01-22 | COORANGA NORTH: GORGE RD | Distribution Event | Normal Event | Crew require acces to replace edo assembly Sending Asset Event to FFA FFA Order Created F-AE24SW1584-1-0 DfltHost Time On modified from 23:59 22-Jan to 23:00 22-Jan Sending Asset Event to FFA Time On modified from 23:00 22-Jan to 01:00 23-Jan Sending Asset Event to FFA Time On modified from 01:00 23-Jan to 00:04 23-Jan Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW1584-1-0 dlbloc01 Rowan Chambers 0429826200 FFA Order En Route F-AE24SW1584-1-0 dlbloc01 FFA Order On Site F-AE24SW1584-1-0 dlbloc01 Sending Asset Event to FFA Crews advised transformer was replaced DSO Sending Asset Event to FFA FFA Order En Route F-AE24SW1584-1-0 dlbloc01 FFA Order On Site F-AE24SW1584-1-0 dlbloc01 FFA Order F-AE24SW1584-1-0 Completed by technician Rowan Chambers in crew dlbloc01(0429826200) with code A-T-303 - Distribution substation Action Taken : crew replaced blown TX Site Label : 4203836 | Invalid | 24SW1584 | 804 CEDARVALE RD, COORANGA QLD 4408 | COORANGA NORTH SWER | 012D |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Hot | NS4203836 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -26.77581787109380 | 151.331085205078 | 2024-01-22 | 1900544 | MRS T A RAMSEY | D - Lines Down | EECL | Transformers Return to Service | D2002 | South West | 12.7kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | I | Capital | DALBY 1 | OT219759 | Technician: Rowan Chambers Comments | OT219759 | 202401
2024-01-28 |  | 2024-01-28 | TDDI | Transformer-Distribution | Closed |  |  | 2024-01-28 | 2024-01-01 | BUNDABERG | EECL | NS | Network Site | XLFBB | 1338198 |  |  | 23/24 | 2024-07-28 | HV | 2024-01-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-01-28 09:15 | 11kV Pole Dist Sub 2753 - replace blown TX | 2024-01-28 | ELLIOTT HEADS: ELLIOTT HEADS RD, HARTS RD | Distribution Event | Normal Event | 11kV Pole Dist Sub 2753 - replace blown TX Sending Asset Event to FFA FFA Order Created F-AE24WB2338-1-0 DfltHost sent to bndoc01 Sending Asset Event to FFA Time On modified from 23:59 28-Jan to 13:23 28-Jan Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB2338-1-0 bndoc01 Peter Marschall 0401944718 FFA Order En Route F-AE24WB2338-1-0 bndoc01 FFA Order On Site F-AE24WB2338-1-0 bndoc01 FFA Order F-AE24WB2338-1-0 Completed by technician Peter Marschall in crew bndoc01(0401944718) with code A-T-303 - Distribution substation Action Taken : replaced faulty overhead 63kva distribution transformer Site Label : 3051089 Actual Power Restoration for F-AE24WB2338-1-0: 28-JAN-2024 14:05:00 auto-completed | Valid | 24WB2338 |  | Elliott Hds Rd opp Prim School | 2753 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS3051089 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -24.90758895874020 | 152.474380493164 | 2024-01-28 | 1902932 | MRS J HENRY | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | BUNDABERG CS | OT221776 | .HEADING Technician: Peter Marschall Comments | OT221776 | 202401
2024-01-29 |  | 2024-01-29 |  |  | Closed |  |  | 2024-01-29 | 2024-01-01 | TOWNSVILLE | EECL | NT | Network Slot | XLHBT | 2058835 |  |  | 23/24 | 2024-07-29 | HV | 2024-01-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2024-01-29 07:15 | F-3192-s HEPA HP-05 TVS192 requires replacement faulty TX | 2024-01-29 | HYDE PARK: BAYSWATER RD, KINGS RD PIMLICO: ALBANY RD, BAYSWATER RD, KINGS RD, KITCHENER RD, SYCAMORE ST | Distribution Event | Normal Event | TVS192, Multiple FC's on sub area, Crews to investigate Please assign to TWVFR07 Sending Asset Event to FFA FFA Order Created F-AE24NQ3527-1-0 DfltHost FFA Order Acknowledged F-AE24NQ3527-1-0 twvfr07 Lawrence Hitchcock 0408776017 Crews advised 1 HV Fuse blown MRC and upstream ar blocked for attempt to close Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Crews attempted Manual Reclose on HV Fuse and tripped upstream Recloser RC883760 Sending Asset Event to FFA Crews then Opened other two HV Fuses and Recloser Closed in Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Sending Asset Event to FFA Reason for Event changed from HV or LV Fuse blown Sending Asset Event to FFA Time On modified from 23:59 29-Jan to 18:00 29-Jan Sending Asset Event to FFA FFA Order En Route F-AE24NQ3527-1-0 twvfr07 FFA Order On Site F-AE24NQ3527-1-0 twvfr07 FFA Order F-AE24NQ3527-1-0 Completed by technician Lawrence Hitchcock in crew twvfr07(0408776017) with code A-T-303 - Distribution substation Action Taken : Replaced Faulty Pole Transformer. 200KVA TVS192. Site Label : TVS192 Power restored at 15.16 Time On modified from 18:00 29-Jan to 15:16 29-Jan | Invalid | 24NQ3527 | Hermit Park No.05 11kV feeder section A | HERMITPARK NO.05 | HP-05A | RC883760 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Storm Electrical | SP-148526 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2024-01-29 | 1903353 | FUSE HV or LV Fuse blown |  | EECL | Transformers Return to Service | D2002 | North Queensland | 11kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | J | Capital | TOWNSVILLE RR | OT222188 | ToughPad Location: Site Label Entered:TVS192 Component: TDDI Component Mod: OC Technician: Lawrence Hitchcock Comments completed | OT222188 | 202401
2024-01-30 |  | 2024-02-29 | TDDI | Transformer-Distribution | Closed |  | Replace | 2024-01-30 | 2024-01-01 | GORDONVALE | EECL | NS | Network Site | XLTNC | 921756 |  |  | 23/24 | 2024-07-30 | HV | 2024-01-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-01-30 20:12 | F-3226 22kV Ground Dist Sub SS8174 - Nultiple FC's from this sub. | 2024-01-30 | GOLDSBOROUGH: COSTAIN ST, INGOT CL, MINESHAFT ST, PANNIKIN ST, STAMP ST LITTLE MULGRAVE: COSTAIN ST | Distribution Event | Normal Event | 22kV Ground Dist Sub SS8174 - Nultiple FC's from this sub. Sending Asset Event to FFA FFA Order Created F-AE24FN2211-1-0 DfltHost FFA Order Acknowledged F-AE24FN2211-1-0 cnsoc01 Jarod Lindsay-Catford 0428665969 FFA Order En Route F-AE24FN2211-1-0 cnsoc01 FFA Order On Site F-AE24FN2211-1-0 cnsoc01 Crew advised Fuses Blown in RMU for TX SS8174 - TX FIS. Crew arranging Generator to feed LV network. Sending Asset Event to FFA Time On modified from 23:59 30-Jan to 01:00 31-Jan Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Supply restored via SS8532. Work to be completed in daylight hours Asset selection modified Time On modified from 01:00 31-Jan to 23:59 31-Jan Sending Asset Event to FFA FFA Order F-AE24FN2211-1-0 Completed by technician Jarod Lindsay-Catford in crew cnsoc01(0428665969 ) with code A-T-303 - Distribution substation Action Taken : 1000kVA tx has failed, crews back switched LV, all customers previously supplied by ss8174 ( failed tx) are now supplied by cables 1 and 2 from SS8532 Site Label : 28784 Actual Power Restoration for F-AE24FN2211-1-0: 30-JAN-2024 23:36:00 Delayed till Transformer replaced Time On modified from 23:59 31-Jan to 23:59 01-Feb Time On modified from 23:59 01-Feb to 23:59 02-Feb Time On modified from 23:59 02-Feb to 23:59 09-Feb Time On modified from 23:59 09-Feb to 23:59 12-Feb NFI Time On modified from 23:59 12-Feb to 23:59 17-Feb Time On modified from 23:59 17-Feb to 23:59 29-Feb Time On modified from 23:59 29-Feb to 13:54 28-Feb auto-completed | Valid | 24FN2211 | GORD-RIVERSTONE | RIVERSTONE ROAD | 2RIR | 8174.RMU.FS1 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS28784-0001 | Ground Outdoor / Indoor Chamber Mounted; < 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -17.15419197082520 | 145.743499755859 | 2024-01-30 | 1904480 | U Unknown |  | EECL | Transformers Return to Service | D2002 | Far North | 22kV | SS8174 - Replace 100KVA TX | M0209 | M0001 | M9999 | 7 | G | Capital | CAIRNS 1 | OT222982 | .HEADING Technician: Jarod Lindsay-Catford Comments 1000kVA tx has failed, | OT222982 | 202401
2024-02-03 |  | 2024-02-04 | TDDI | Transformer-Distribution | Closed |  |  | 2024-02-03 | 2024-02-01 | MACKAY | EECL | NS | Network Site | XLFPK | 1462721 |  |  | 23/24 | 2024-08-03 | HV | 2024-02-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2024-02-03 17:18 | 11kV Pole Dist Sub 6853 - Crew replaced blown 315kVA transformer. SL 4102919. (S Gregory). | 2024-02-03 | MACKAY: BODDINGTON ST, HAMLET ST, JULIET ST, MARGARET ST, ROMEO ST, SHAKESPEARE ST, SYDNEY ST, WOOD ST | Distribution Event | Normal Event | 11kV Pole Dist Sub 6853 - Multiple Fault calls beyond sub. Sending Asset Event to FFA FFA Order Created F-AE24MK1792-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24MK1792-1-0 mckoc01 Wayne Zahra 0419713519 FFA Order En Route F-AE24MK1792-1-0 mckoc01 FFA Order On Site F-AE24MK1792-1-0 mckoc01 Transformer tro be replaced Sending Asset Event to FFA Time On modified from 23:59 03-Feb to 05:00 04-Feb Sending Asset Event to FFA Time On modified from 05:00 04-Feb to 02:08 04-Feb Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Suspended F-AE24MK1792-1-0 by Wayne Zahra 0419713519 job complete- going on break- will do FDC forms etc tomorrow FFA Order En Route F-AE24MK1792-1-0 mckoc01 FFA Order On Site F-AE24MK1792-1-0 mckoc01 FFA Order F-AE24MK1792-1-0 Completed by technician Wayne Zahra in crew mckoc01(0419713519) with code A-T-303 - Distribution substation Action Taken : replaced blown 315 kava dist tx Site Label : 4102919 Actual Power Restoration for F-AE24MK1792-1-0: 04-FEB-2024 03:19:00 auto-completed Updated Reasons tab. Reason for Event changed from Unknown | Valid | 24MK1792 |  | ROMEO ST | 6853 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Hot | NS4102919 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -21.14767265319820 | 149.184463500977 | 2024-02-03 | 1905732 | MR K COOPER | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | Mackay | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | MACKAY 2 | OT223876 | Technician: Wayne Zahra Comments | OT223876 | 202402
2024-02-08 |  | 2024-02-09 | TDDI | Transformer-Distribution | Closed |  |  | 2024-02-08 | 2024-02-01 | MACKAY | EECL | NS | Network Site | XLFPK | 1516537 |  |  | 23/24 | 2024-08-08 | HV | 2024-02-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-02-08 15:30 | F-3326-s 11kV Pole Dist Sub 2899 - Crew replaced faulty 100kVA transformer. SL 4002098. (S Gregory). | 2024-02-08 | ERAKALA: COAKLEY CT, WICKS CT | Distribution Event | Normal Event | Multiple calls for no supply from 11kV Pole Dist Sub 2899 - Crews currently enroute Sending Asset Event to FFA FFA Order Created F-AE24MK1935-1-0 DfltHost FFA Order Acknowledged F-AE24MK1935-1-0 mckoc01 Shane Austin 0418872273 Sending Asset Event to FFA Crews advise that they took access to replace the LA's but the sub needs to be replaced. Time On modified from 23:59 08-Feb to 21:00 08-Feb Sending Asset Event to FFA Time On modified from 21:00 08-Feb to 22:00 08-Feb Sending Asset Event to FFA Time On modified from 22:00 08-Feb to 23:30 08-Feb Sending Asset Event to FFA FFA Order Acknowledged F-AE24MK1935-1-0 mckoc02 Jack Mackenzie 0438483454 FFA Order En Route F-AE24MK1935-1-0 mckoc02 Time On modified from 23:30 08-Feb to 00:05 09-Feb Sending Asset Event to FFA FFA Order On Site F-AE24MK1935-1-0 mckoc02 FFA Order F-AE24MK1935-1-0 Completed by technician Jack Mackenzie in crew mckoc02(0438483454) with code A-T-320 - SUBT-Unassisted failure(Apparent defect) Action Taken : replaced faulty 100kVA transformer Site Label : 4002098 Actual Power Restoration for F-AE24MK1935-1-0: 09-FEB-2024 01:30:00 Updated Reasons tab. Updated Event Trigger from SUBT-Unassisted failure to Distribution substation. Reason for Event changed from HV or LV Fuse blown | Invalid | 24MK1935 |  | COAKLEY CRT | 2899 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS4002098 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -21.12797737121580 | 149.110931396484 | 2024-02-08 | 1907139 | MRS S WEST | N - Neighbours Out as Well | EECL | Transformers Return to Service | D2002 | Mackay | 11kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | J | Capital | MACKAY 2 | OT224809 | Technician: Jack Mackenzie Comments | OT224809 | 202402
2024-02-13 |  | 2024-02-13 | TDDI | Transformer-Distribution | Closed |  |  | 2024-02-13 | 2024-02-01 | CHINCHILLA | EECL | NS | Network Site | XCGDH | 1916145 |  |  | 23/24 | 2024-08-13 | HV | 2024-02-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Fuse Operated - No Trigger Found | 2024-02-13 08:40 | F-2476-r - MILE - Dulacca FDR - 12.7kV SWER Pole Dist Sub PC02468 Crew advised TX FIS requires replacement. Access from LL Clamps. | 2024-02-13 | DRILLHAM: HOMEBUSH RD | Distribution Event | Normal Event | 12.7kV SWER Pole Dist Sub PC02468 Crew advised TX FIS requires replacement. Access from LL Clamps. chncw01 Sending Asset Event to FFA FFA Order Created F-AE24SW4794-1-0 DfltHost FFA Order Acknowledged F-AE24SW4794-1-0 chncw01 Jeremy Koehler 0400201688 FFA Order En Route F-AE24SW4794-1-0 chncw01 Sending Asset Event to FFA FFA Order On Site F-AE24SW4794-1-0 chncw01 Time On modified from 23:59 13-Feb to 12:09 13-Feb Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Created F-AE24SW4794-1-1 DfltHost FFA Order F-AE24SW4794-1-0 Completed by technician Jeremy Koehler in crew chncw01(0400201688) with code A-T-303 - Distribution substation Action Taken : tx blown replace all hardware and stays Site Label : 4225030 Actual Power Restoration for F-AE24SW4794-1-0: 13-FEB-2024 10:23:00 FFA Order cancelled.F-AE24SW4794-1-1 | Valid | 24SW4794 | HOMEBUSH COTTAGE | PC02468 | PC02468 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS4225030 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -26.53514099121090 | 149.879486083984 | 2024-02-13 | 1907929 | FRITH FAMILY FARMS | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | South West | 12.7kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | I | Capital | CHINCHILLA | OT225344 | Technician: Jeremy Koehler Comments tx blown replace all hardware and stays | OT225344 | 202402
2024-02-17 |  | 2024-02-17 |  |  | Closed |  |  | 2024-02-17 | 2024-02-01 | MACKAY | EECL | NT | Network Slot | XLFPK | 6746359 |  |  | 23/24 | 2024-08-17 | LV | 2024-02-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | North | HV-Unassisted failure(Apparent defect) | 2024-02-17 10:23 | 11kV Ground Dist Sub 580899 , Blown HV fuses | 2024-02-17 | MACKAY: MANGROVE RD | Distribution Event | Normal Event | 11kV Ground Dist Sub 580899 , Blown HV fuses Sending Asset Event to FFA FFA Order Created F-AE24MK2132-1-0 DfltHost FFA Order Acknowledged F-AE24MK2132-1-0 mckoc01 Bart Friese 0417389732 FFA Order En Route F-AE24MK2132-1-0 mckoc01 FFA Order On Site F-AE24MK2132-1-0 mckoc01 RMU and TX replaced on F-3381-s Time On modified from 23:59 17-Feb to 17:00 17-Feb Sending Asset Event to FFA FFA Order Suspended F-AE24MK2132-1-0 by Bart Friese 0417389732 all work completed and supply restored but forgot to get the tx data information to complete the tx FDC. FFA Order En Route F-AE24MK2132-1-0 mckoc01 FFA Order On Site F-AE24MK2132-1-0 mckoc01 FFA Order F-AE24MK2132-1-0 Completed by technician Bart Friese in crew mckoc01(0417389732) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : 500 Kva padmount transformer replacement due Tx failed in service. Site Label : 167507 Actual Power Restoration for F-AE24MK2132-1-0: 17-FEB-2024 18:35:00 auto-completed | Invalid | 24MK2132 | CANELAND CENTRAL, 2 MANGROVE RD, MACKAY | BIG W | 580899 |  | HV or LV Fuse blown | Completed | Unplanned Outage | Hot | GT-648323 | Ground Outdoor / Indoor Chamber Mounted; < 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2024-02-17 | 1909064 | WOOLWORTHS GROUP LIMITED | U - Unknown / No Power | EECL | Forced Regulated | CEFR | Mackay | LV | WOOLWORTHS GROUP LIMITED | M0209 | M0001 | M0070 |  | M | Operational | MACKAY 2 | OT225966 |  | OT225966 | 202402
2024-02-19 |  | 2024-02-19 | TDDI | Transformer-Distribution | Closed |  |  | 2024-02-19 | 2024-02-01 | TOWNSVILLE | EECL | NS | Network Site | XLHBT | 1732268 |  |  | 23/24 | 2024-08-19 | HV | 2024-02-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-02-19 07:19 | F-3389-s Crew Req Access to Replace Failed in Service Transformer TVS1115 | 2024-02-19 | ROSENEATH: FLINDERS HWY | Distribution Event | Normal Event | Crew Req Access to Replace Failed in Service Transformer TVS1115 Primary Asset de-escalated from Stuart Drive 19 (FC) Sending Asset Event to FFA FFA Order Created F-AE24NQ4927-1-0 DfltHost FFA Order Acknowledged F-AE24NQ4927-1-0 twvfr06 Kerrie McHugh 0419269209 FFA Order En Route F-AE24NQ4927-1-0 twvfr06 FFA Order On Site F-AE24NQ4927-1-0 twvfr06 Power restored 1515 Time On modified from 23:59 19-Feb to 15:15 19-Feb Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24NQ4927-1-0 Completed by technician Kerrie McHugh in crew twvfr06(0419269209) with code A-T-303 - Distribution substation Action Taken : Replaced 25kVA Tx TVS1115 Site Label : 5201949 Actual Power Restoration for F-AE24NQ4927-1-0: 19-FEB-2024 15:18:00 auto-completed | Valid | 24NQ4927 | Sub, Stuart No.4 11kV feeder | TVS1115 | TVS1115 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS5201949 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -19.370267868042 | 146.848571777344 | 2024-02-19 | 1909240 | GOODSELL EARTHMOVING PTY LTD | P - Phase Down (LV) | EECL | Transformers Return to Service | D2002 | North Queensland | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | TOWNSVILLE RR | OT226115 | Technician: Kerrie McHugh Comments | OT226115 | 202402
2024-02-23 |  | 2024-02-24 | TDDI | Transformer-Distribution | Closed |  |  | 2024-02-23 | 2024-02-01 | HUGHENDEN | EECL | NS | Network Site | XCHBU | 1669341 |  |  | 23/24 | 2024-08-23 | HV | 2024-02-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-02-23 23:28 | F-1296-t HUS 313 requires to be replaced | 2024-02-23 | HUGHENDEN: SODA VALLEY STATION | Distribution Event | Normal Event | HUS 313 requires to be replaced Sending Asset Event to FFA FFA Order Created F-AE24NQ5257-1-0 DfltHost Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 24-Feb to 17:49 24-Feb Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ5257-1-0 huhcmfr02 Michael Steadman 0429969325 FFA Order En Route F-AE24NQ5257-1-0 huhcmfr02 FFA Order On Site F-AE24NQ5257-1-0 huhcmfr02 FFA Order F-AE24NQ5257-1-0 Completed by technician Michael Steadman in crew huhcmfr02(0429969325) with code A-T-303 - Distribution substation Action Taken : replaced 10 kva transformer Site Label : 5168983 auto-completed | Valid | 24NQ5257 | HUGHSS 19.1KV DUTTON RIVER NO.4.FC | DUTTON RIVER NO.4.FC | DUTTON RIVER 4.FC |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS5168983 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -20.63377571105960 | 144.011779785156 | 2024-02-23 | 1910494 | MRS S MCCLYMONT | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | North Queensland | 19kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | H | Capital | HUGHENDEN | OT226794 | Technician: Michael Steadman Comments | OT226794 | 202402
2024-02-25 |  | 2024-02-25 | TDDI | Transformer-Distribution | Closed |  |  | 2024-02-25 | 2024-02-01 | TARA | EECL | NS | Network Site | XCGDA | 1996346 |  |  | 23/24 | 2024-08-25 | HV | 2024-02-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-02-25 07:43 | F-3087-q - 12.7kV SWER Pole Dist Sub PC03130, Crew require access to replace TX, will require isolation from S346 to maintain exclusion zones | 2024-02-25 | MOONIE: COLEMANS RD | Distribution Event | Normal Event | 12.7kV SWER Pole Dist Sub PC03130, Crew require access to replace TX, will require isolation from S346 to maintain exclusion zones DSO requested Bad comms Sending Asset Event to FFA FFA Order Created F-AE24SW5411-1-0 DfltHost Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 25-Feb to 17:48 25-Feb Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW5411-1-0 tarcdwgl1 James KEOGH 0436427380 FFA Order En Route F-AE24SW5411-1-0 tarcdwgl1 FFA Order On Site F-AE24SW5411-1-0 tarcdwgl1 FFA Order F-AE24SW5411-1-0 Completed by technician James KEOGH in crew tarcdwgl1(0436427380) with code A-T-303 - Distribution substation Action Taken : pc 03130 failed replaced tx Site Label : 4127958 | Invalid | 24SW5411 | BULLOCK HEAD RD RECLOSER | WEIR RIVER | 079T | Crowders Creek Rd | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS4127958 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -27.72478866577150 | 150.647644042969 | 2024-02-25 | 1910635 | MR J O'CONNOR | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | South West | 12.7kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | I | Capital | TARA | OT226908 | Technician: James KEOGH Comments | OT226908 | 202402
2024-02-27 |  | 2024-02-28 | TDDI | Transformer-Distribution | Closed |  |  | 2024-02-27 | 2024-02-01 | NORMANTON | EECL | NS | Network Site | XCTNN | 8547713 |  |  | 23/24 | 2024-08-27 | HV | 2024-02-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-02-27 14:09 | Electrician->Fault occurred at:27/02/2024 14:04; Nick Stitt Elect & Air Con, 0400287338;>SHOCK --> WhereFrom:gate<;Incident Details:elect adv 30AC between indap earth & cust rec shock/tingle from gate connected to building. Elect made safe but not sure of Cust as Gov employee not onsite 0400287338;COVID-19:N/A;Warnings[shockOrFatality, shockOrFatality, medicalAttention]: ADVISED;Sensitive Load:N | 2024-02-27 | 5 BURKE DEVELOPMENT RD;NORMANTON QLD 4890 | Distribution Event | Normal Event |  | Valid | 24FN3447 | UNKNOWN RD, NORMANTON QLD 4890 | Gulf Dev Rd | SS775579 |  | Unknown | Completed | Unplanned Outage | Fine | NS11008320 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -17.687837600708 | 141.058135986328 | 2024-02-27 | 1911345 | CARPENTARIA SHIRE COUNCIL | T - Tingle / Shock | EECL | Forced Regulated | FNFR | Far North | 22kV | CARPENTARIA SHIRE COUNCIL | M0209 | M0001 | M9999 |  | G | Operational | NORMANTON | OT227308 | Technician: AllanRobinson Comments replaced on other workorder | OT227308 | 202402
2024-02-27 |  | 2024-02-28 | TDDI | Transformer-Distribution | Closed |  |  | 2024-02-27 | 2024-02-01 | NORMANTON | EECL | NS | Network Site | XCTNN | 8547713 |  |  | 23/24 | 2024-08-27 | HV | 2024-02-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | HV-Unassisted failure(Apparent defect) | 2024-02-27 14:09 | F - 3438-s 22kV Pole Dist Sub SS775579 . LV isolated due to High VOLTS Sw sheet and AP required to replace TX tank | 2024-02-27 | NORMANTON: BURKE DEVELOPMENT RD | Distribution Event | Normal Event | 22kV Pole Dist Sub SS775579 . LV isolated due to High VOLTS Sw sheet and AP required to replace TX tank Reason for Event changed from Unknown Time On modified from 16:00 28-Feb to 22:10 27-Feb closed in error reactivated Time On modified from 22:10 27-Feb to 22:33 27-Feb Time On modified from 22:33 27-Feb to 16:00 28-Feb Time On modified from 16:00 28-Feb to 10:27 28-Feb Sending Asset Event to FFA FFA Order Created F-AE24FN3420-1-0 DfltHost FFA Order Acknowledged F-AE24FN3420-1-0 nrmoc01 AllanRobinson 0409450233 FFA Order En Route F-AE24FN3420-1-0 nrmoc01 FFA Order On Site F-AE24FN3420-1-0 nrmoc01 FFA Order F-AE24FN3420-1-0 Completed by technician AllanRobinson in crew nrmoc01(0409450233) with code A-T-30 - Vibration Action Taken : tx open circuit neutral internally. replace tx Site Label : 11008320 Actual Power Restoration for F-AE24FN3420-1-0: 28-FEB-2024 10:30:00 | Valid | 24FN3420 | UNKNOWN RD, NORMANTON QLD 4890 | Gulf Dev Rd | SS775579 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS11008320 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -17.687837600708 | 141.058135986328 | 2024-02-27 | 1911219 | CARPENTARIA SHIRE COUNCIL | T - Tingle / Shock | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | G | Capital | NORMANTON | OT227224 | Technician: AllanRobinson Comments | OT227224 | 202402
2024-03-01 |  | 2024-03-02 | TDDI | Transformer-Distribution | Closed |  |  | 2024-03-01 | 2024-03-01 | DALBY | EECL | NS | Network Site | XLGDD | 1271820 |  |  | 23/24 | 2024-09-01 | HV | 2024-03-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-03-01 18:57 | F-3107-q - 12.7kV SWER Pole Dist Sub PC00386 - Crew advise TX FIS requires replacement, mobile ok, access from LL Clamps | 2024-03-01 | YAMSION: HUMPHRY'S RD | Distribution Event | Normal Event | 12.7kV SWER Pole Dist Sub PC00386 - Crew advise TX FIS requires replacement, mobile ok, access from LL Clamps Crew to attend tomorrow to replace TX 02.03.24 dlbloc01 Time On modified from 23:59 01-Mar to 12:00 02-Mar Sending Asset Event to FFA FFA Order Created F-AE24SW5629-1-0 DfltHost Sending Asset Event to FFA DSO requested DSO Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW5629-1-0 dlbloc01 Steve Gscheidle 0409186844 FFA Order En Route F-AE24SW5629-1-0 dlbloc01 Time On modified from 12:00 02-Mar to 11:25 02-Mar Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order On Site F-AE24SW5629-1-0 dlbloc01 FFA Order F-AE24SW5629-1-0 Completed by technician Steve Gscheidle in crew dlbloc01(0409186844) with code A-T-303 - Distribution substation Action Taken : replace blown 12.7kv swer tx that failed in service Site Label : 3141025 Time On modified from 11:25 02-MAR to 11:25 02-MAR FFA Order F-AE24SW5629-1-0 Completed by technician Steve Gscheidle in crew dlbloc01(0409186844) with code A-T-303 - Distribution substation Action Taken : replace blown 12.7kv swer tx that failed in service Site Label : 3141025 Time On modified from 11:25 02-MAR to 11:25 02-MAR FFA Order F-AE24SW5629-1-0 Completed by technician Steve Gscheidle in crew dlbloc01(0409186844) with code A-T-303 - Distribution substation Action Taken : replace blown 12.7kv swer tx that failed in service Site Label : 3141025 Time On modified from 11:25 02-MAR to 11:25 02-MAR | Invalid | 24SW5629 | THE VALLEY | PC00386 | PC00386 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Hot | NS3141025 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -27.00628852844240 | 151.550003051758 | 2024-03-01 | 1912126 | MR C HUNTER | O - Other | EECL | Transformers Return to Service | D2002 | South West | 12.7kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | I | Capital | DALBY 1 | OT227698 | Technician: Steve Gscheidle Comments | OT227698 | 202403
2024-03-03 |  | 2024-03-03 | TDDI | Transformer-Distribution | Closed |  |  | 2024-03-03 | 2024-03-01 | MACKAY | EECL | NS | Network Site | XLFPK | 1454803 |  |  | 23/24 | 2024-09-03 | HV | 2024-03-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-03-03 17:06 | NTH MACKAY 11kV Golf Links RC804799 ACR CB tripped. SCADA Interface automated outage. Crew replaced 11kV Pole Dist Sub 6838. SL 4118788. (S Gregory). | 2024-03-03 | BEACONSFIELD, RURAL VIEW | Distribution Event | Normal Event | entered from the SCADA Interface Sending Asset Event to FFA FFA Order Created F-AE24MK2554-1-0 DfltHost On Call Supervisor :Josh Ribaldone 0409 777 969 Depot Co-ord Advised Sending Asset Event to FFA Andy Buffini 0437 174 844 Sending Asset Event to FFA FFA Order Acknowledged F-AE24MK2554-1-0 mckoc02 Andy Buffini 0437174844 FFA Order En Route F-AE24MK2554-1-0 mckoc02 FFA Order On Site F-AE24MK2554-1-0 mckoc02 Asset selection modified Time On modified from 23:59 03-Mar to 23:59 03-Mar Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Crew adv replaced damaged TX 6838. Crew replaced with a 25kVA. Time On modified from 23:59 03-Mar to 21:00 03-Mar Sending Asset Event to FFA Time On modified from 21:00 03-Mar to 20:28 03-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24MK2554-1-0 Completed by technician Andy Buffini in crew mckoc02(0437174844) with code A-T-303 - Distribution substation Action Taken : replaced tx6838 Site Label : 4118788 Reason for Event changed from Unknown Updated Reasons tab. Updated Event Trigger from SAF to Distribution substation. | Valid | 24MK2554 | MACKAY-BUCASIA RD, BEACONSFIELD QLD 4740 | FC GOLF LINKS | RC804799 | GOLF LINKS | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS4118788 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -21.07355690002440 | 149.157043457031 | 2024-03-03 | 1912366 | U Unknown |  | EECL | Forced Regulated | CEFR | Mackay | 11kV | U Unknown | M0209 | M0001 | M9999 |  | J | Operational | MACKAY 2 | OT227908 | Technician: Andy Buffini Comments replaced tx6838 | OT227908 | 202403
2024-03-11 |  | 2024-03-12 |  |  | Closed |  |  | 2024-03-11 | 2024-03-01 | HERVEY BAY | EECL | NT | Network Slot | XLFBH | 2802034 |  |  | 23/24 | 2024-09-11 | HV | 2024-03-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2024-03-11 19:47 | F- 2625-r 11kV Pole Dist Sub 9098, crews require access for repair | 2024-03-11 | URRAWEEN: URRAWEEN RD | Distribution Event | Normal Event | 11kV Pole Dist Sub 9098, crews require access for repair Sending Asset Event to FFA FFA Order Created F-AE24WB3988-1-0 DfltHost F- 2625-r Sending Asset Event to FFA Time On modified from 23:59 11-Mar to 10:17 12-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB3988-1-0 hboc01 Alex howlett 0417539076 FFA Order En Route F-AE24WB3988-1-0 hboc01 FFA Order On Site F-AE24WB3988-1-0 hboc01 FFA Order F-AE24WB3988-1-0 Completed by technician Alex howlett in crew hboc01(0417539076) with code A-T-303 - Distribution substation Action Taken : replaced faulty transformer after testing 320v on A phase, 240v on b phase, 240v on c phase, 0v on neutral. Site Label : 9098 Time On modified from 10:17 12-MAR to 10:33 12-MAR | Invalid | 24WB3988 |  | HBCC PUMPING STATION | 9098 |  | Unknown | Completed | Unplanned Outage | Fine | SP-168064 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2024-03-11 | 1914488 | FRASER COAST REGIONAL COUNCIL | O - Other | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | HERVEY BAY 2 | OT229202 | ToughPad Location: Site Label Entered:9098 Component: TDDI Component Mod: OC Technician: Alex howlett Comments | OT229202 | 202403
2024-03-12 |  | 2024-03-12 | TDDI | Transformer-Distribution | Closed |  |  | 2024-03-12 | 2024-03-01 | ROCKHAMPTON | EECL | NS | Network Site | XLFPR | 1636571 |  |  | 23/24 | 2024-09-12 | HV | 2024-03-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | HV-Unassisted failure(Apparent defect) | 2024-03-12 15:50 | F-2629-r 12.7kV SWER Pole Dist Sub 22226 - blown TX | 2024-03-12 | BAJOOL: GALVIN RD | Distribution Event | Normal Event | 12.7kV SWER Pole Dist Sub 22226 - blown TX Sending Asset Event to FFA FFA Order Created F-AE24CA4387-1-0 DfltHost Asset selection modified Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 12-Mar to 21:06 12-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA4387-1-0 ccoc05 Ben Franks 0473410055 FFA Order En Route F-AE24CA4387-1-0 ccoc05 FFA Order On Site F-AE24CA4387-1-0 ccoc05 FFA Order F-AE24CA4387-1-0 Completed by technician Ben Franks in crew ccoc05(0473410055) with code A-T-303 - Distribution substation Action Taken : Install new 12.7KV 10KVA transformer Site Label : 4039314 | Valid | 24CA4387 | Midgee SWER | Midgee SWER | SW/22075 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS4039314 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -23.60811996459960 | 150.555297851563 | 2024-03-12 | 1914651 | MR J BACCON | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Capricornia | 12.7kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | I | Capital | ROCKHAMPTON 3 | OT229287 | Technician: Ben Franks Comments replaced blown tx | OT229287 | 202403
2024-03-18 |  | 2024-03-19 | TDDI | Transformer-Distribution | Closed |  |  | 2024-03-18 | 2024-03-01 | MAREEBA | EECL | NS | Network Site | XLTNR | 1300177 |  |  | 23/24 | 2024-09-18 | HV | 2024-03-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | North | HV-Unassisted failure(Apparent defect) | 2024-03-18 05:06 | Multiple call from 22kV Recloser Pole MA1A for no supply | 2024-03-18 | MARYFARMS: BUTCHERS CREEK RD, EAST MARY RD, MULLIGAN HWY, PENINSULA DEVELOPMENT RD, WEST MARY RD MOUNT CARBINE: MULLIGAN HWY | Distribution Event | Normal Event | Multiple call from 22kV Recloser Pole MA1A for no supply Sending Asset Event to FFA FFA Order Created F-AE24FN4153-1-0 DfltHost Lenard advised have patrolled line as much as possible, section at the end across a creek and a gated customer with cameras and do not enter signs without our locks was inaccessible.No faults found on the patrolled sections Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA FFA Order Acknowledged F-AE24FN4153-1-0 mbaco01 John musso 0437302916 FFA Order En Route F-AE24FN4153-1-0 mbaco01 FFA Order On Site F-AE24FN4153-1-0 mbaco01 Asset selection modified Time On modified from 23:59 18-Mar to 14:09 18-Mar Sending Asset Event to FFA Time On modified from 14:09 18-Mar to 14:07 18-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE24FN4153-1-0 mbaco01 FFA Order On Site F-AE24FN4153-1-0 mbaco01 FFA Order F-AE24FN4153-1-0 Completed by technician John musso in crew mbaco01(0437302916) with code A-T-303 - Distribution substation Action Taken : replaced Site Label : 5008674 Actual Power Restoration for F-AE24FN4153-1-0: 18-MAR-2024 14:00:00 | Invalid | 24FN4153 | RECLOSER ON POLE | Mary Farms Recl FC | MA1A.2CAB.FC | Mary Farms Recloser | Unknown | Completed | Unplanned Outage | Wet / Rain | NS5008674 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -16.57591438293460 | 145.184967041016 | 2024-03-18 | 1915667 | MS E ROSS | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | G | Capital | MAREEBA 2 | OT229900 | Technician: John musso Comments | OT229900 | 202403
2024-03-24 |  | 2024-03-25 | TDDI | Transformer-Distribution | Closed |  |  | 2024-03-24 | 2024-03-01 | TOOWOOMBA | EECL | NS | Network Site | XLGDT | 1464350 |  |  | 23/24 | 2024-09-24 | HV | 2024-03-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-03-25 07:22 | Crew advise blown HV fuse at 11kV Dropout Fuse DL7145 | 2024-03-25 | ACLAND: ACLAND SABINE RD, COOKE'S RD, O'SHEA'S RD BRYMAROO: ACLAND BRYMAROO RD JONDARYAN: ACLAND-BRYMAROO RD, JONDARYAN NUNGIL RD MALU: BOWENVILLE ACLAND RD | Distribution Event | Normal Event | Crew advise blown HV fuse at 11kV Dropout Fuse DL7145 Sending Asset Event to FFA FFA Order Created F-AE24SW6823-1-0 DfltHost Matt Briggs adv B Ph EDO blown. Patrolled - no fault found. Closed successfully at 1614hrs. Confirming LV supply to other subs to confirm no other faults. Manual Reclose Checklist Sending Asset Event to FFA Time On modified from 23:59 25-Mar to 16:14 25-Mar Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW6823-1-0 twmfrcm01 Matt Briggs 0419256307 FFA Order En Route F-AE24SW6823-1-0 twmfrcm01 FFA Order On Site F-AE24SW6823-1-0 twmfrcm01 FFA Order F-AE24SW6823-1-0 Completed by technician Matt Briggs in crew twmfrcm01(0419256307) with code A-T-303 - Distribution substation Action Taken : replaced faulty 10kva tx Site Label : 2015579 | Valid | 24SW6823 | NUNGIL ROAD | NUNGIL ROAD | 3832 | DO7145 | HV or LV Fuse blown | Completed | Unplanned Outage | Wet / Rain | NS2015579 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -27.28394889831540 | 151.625488281250 | 2024-03-24 | 1917106 | MR K BILTOFT | O - Other | EECL | Transformers Return to Service | D2002 | South West | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | TOOWOOMBA RAPIDS | OT230730 | Technician: Matt Briggs Comments | OT230730 | 202403
2024-03-24 |  | 2024-03-27 | TDDI | Transformer-Distribution | Closed |  |  | 2024-03-24 | 2024-03-01 | CUNNAMULLA | EECL | NS | Network Site | XCGDU | 1252525 |  |  | 23/24 | 2024-09-24 | HV | 2024-03-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-03-24 13:26 | F-2671-r fault calls suggest cb603598 (comms failed) tripped Crew advised 19.1kV SWER Pole Dist Sub PW03447 (0 customers) appears blown and have left offline. SL 6012763. (S Gregory). | 2024-03-24 | CHARLEVILLE: CHARLEVILLE-WYANDRA RD, ROSEVALE RD CUNNAMULLA: MT ALFRED-QUILPIE RD WYANDRA: CHARLEVILLE-WYANDRA RD, MITCHELL HWY, MOUNT ALFRED RD, ROSEVALE RD | Distribution Event | Normal Event | fault calls suggest cb603598 (comms failed) tripped Sending Asset Event to FFA FFA Order Created F-AE24SW6852-1-0 DfltHost Sending Asset Event to FFA Sending Asset Event to FFA DSO Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW6852-1-0 chrcmfr01 Les Toms 0428280025 FFA Order En Route F-AE24SW6852-1-0 chrcmfr01 Time On modified from 23:59 26-Mar to 11:11 26-Mar Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order On Site F-AE24SW6852-1-0 chrcmfr01 FFA Order F-AE24SW6852-1-0 Completed by technician Les Toms in crew CHRCMFR01(0428280025 ) with code A-T-303 - Distribution substation Action Taken : Transformer 03447 appears blown, crew left TX offline Site Label : 6012763 Updated Reasons tab. Updated Event Trigger from SAF to Distribution substation. Reason for Event changed from Unknown | Valid | 24SW6852 | EXISTING RAILWAY CORRIDOR, CUNNAMULLA QL | Wyandra | CB603598 | DO18125 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS6012763 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -27.084264755249 | 145.920318603516 | 2024-03-24 | 1917051 | MR P FISHER | N - Neighbours Out as Well | EECL | Forced Regulated | SWFR | South West | 19kV | MR P FISHER | M0209 | M0001 | M9999 |  | H | Operational | CUNNAMULLA | OT230685 | Technician: Les Toms Comments | OT230685 | 202403
2024-03-25 |  | 2024-03-25 | TDDI | Transformer-Distribution | Closed |  |  | 2024-03-25 | 2024-03-01 | ROCKHAMPTON | EECL | NS | Network Site | XLFPR | 1701254 |  |  | 23/24 | 2024-09-25 | HV | 2024-03-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | HV-Unassisted failure(Apparent defect) | 2024-03-25 12:10 | F-3216-q - ROCK STH 11kV Gracemere Fdr CB S101 tripped. Prot Trip - report of lines down near 20310 | 2024-03-25 | ALLENSTOWN, MIDGEE, PORT CURTIS, ROCKHAMPTON, ROCKHAMPTON CITY | Distribution Event | Normal Event | entered from the SCADA Interface Crew attending Matthew Benson ccoc02 Sending Asset Event to FFA FFA Order Created F-AE24CA4842-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA4842-1-0 ccoc02 Matthew Benson 0437238565 Asset selection modified Sending Asset Event to FFA Lines down, broken xarm at sub 20310. Time On modified from 23:59 25-Mar to 19:00 25-Mar HV Wires Down Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 19:00 25-Mar to 17:42 25-Mar Sending Asset Event to FFA FFA Order En Route F-AE24CA4842-1-0 ccoc02 FFA Order On Site F-AE24CA4842-1-0 ccoc02 FFA Order F-AE24CA4842-1-0 Completed by technician Matthew Benson in crew ccoc02(0437238565) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : HV cross arm broke, causing hv conductor to fall and come in contact with lv mains, breaking transformer on the way down Site Label : 4060131 | Valid | 24CA4842 | ROSO-GRACEMERE | Gracemere | RS101 | RS-S101 | Unknown | Completed | Unplanned Outage | Wet / Rain | NS4060131 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -23.40655226266850 | 150.508478783758 | 2024-03-25 | 1917275 | U Unknown |  | EECL | Transformers Return to Service | D2002 | Capricornia | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | ROCKHAMPTON 3 | OT230812 | .HEADING Technician: Matthew Benson Comments Technician: Matthew Benson Comments | OT230812 | 202403
2024-03-26 |  | 2024-04-02 |  |  | Closed |  |  | 2024-03-26 | 2024-03-01 | COOKTOWN | EECL | NT | Network Slot | XCTNO | 2803074 |  |  | 23/24 | 2024-09-26 | HV | 2024-03-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | HV-Unassisted failure(Apparent defect) | 2024-03-26 21:55 | Crews will require access 22kV Pole Dist Sub SS6427 via EDO's to carry out fault work | 2024-03-26 | LAKELAND: MULLIGAN HWY, PENINSULA DEVELOPMENT RD | Distribution Event | Normal Event | Crews will require access 22kV Pole Dist Sub SS6427 via EDO's to carry out fault work Crews attending: Mick Saunders 0436 418 642. Sending Asset Event to FFA FFA Order Created F-AE24FN4579-1-0 DfltHost FFA Order Acknowledged F-AE24FN4579-1-0 cktcsfr01 Mick Saunders 0436418642 FFA Order En Route F-AE24FN4579-1-0 cktcsfr01 FFA Order On Site F-AE24FN4579-1-0 cktcsfr01 Time On modified from 23:59 26-Mar to 23:59 27-Mar Sending Asset Event to FFA Transformer isolated/earthed, crew to return tomorrow for repairs Sending Asset Event to FFA FFA Order Suspended F-AE24FN4579-1-0 by Mick Saunders 0436418642 FFA Order Pending F-AE24FN4579-1-0 Crew onsite to continue works Sending Asset Event to FFA Time On modified from 23:59 27-Mar to 16:56 27-Mar Sending Asset Event to FFA FFA Order Acknowledged F-AE24FN4579-1-0 cktoc01 Mick saunders 0436418642 FFA Order En Route F-AE24FN4579-1-0 cktoc01 FFA Order On Site F-AE24FN4579-1-0 cktoc01 FFA Order F-AE24FN4579-1-0 Completed by technician Mick saunders in crew cktoc01(0436418642) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : 200kva tx failure, isolated and earthed, replaced tx and power restored Site Label : 515563 Actual Power Restoration for F-AE24FN4579-1-0: 28-MAR-2024 16:28:00 | Invalid | 24FN4579 |  | Elmes | SS6427 |  | Unknown | Completed | Unplanned Outage | Wet / Rain | SP-100029 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2024-03-26 | 1917721 | T/AS LAKELAND ROADHOUSE | U - Unknown / No Power | EECL | Forced Regulated | FNFR | Far North | 22kV | T/AS LAKELAND ROADHOUSE | M0209 | M0001 | M9999 |  | G | Operational | COOKTOWN | OT231066 |  | OT231066 | 202403
2024-03-26 |  | 2024-05-01 |  |  | Closed |  |  | 2024-03-26 | 2024-03-01 | CNS CENTRAL | EECL | FD | Feeder | XLTNC | 24240 |  |  | 23/24 | 2024-09-26 | HV | 2024-03-01 |  | Unknown | Broken | Padmount Substation | Outage | North | HV-Unassisted failure(Apparent defect) | 2024-03-26 22:44 | F-3608-s - EDMONTON 22kV White Rock Fdr CB FA06Q00 tripped. SCADA Interface automated outage. SS596020 SD1 RMU switch found to have flashed over during electrical storm, blown bushing/termination. RMU replaced and returned to service under planned outage 24FN6463. SL 183389. (S Gregory). | 2024-03-26 | EDMONTON, WHITE ROCK | Distribution Event | Normal Event | entered from the SCADA Interface Tripped on Dir O/C and E/F On Call supervisor has been advised - he will organise more crews to head out. I have aske him to let crews know to contact OCCN so we know who will be attending. Storm in Area Crews Attending: Anthony McConville 0409 490 954 Sending Asset Event to FFA FFA Order Created F-AE24FN4582-1-0 DfltHost Time On modified from 23:59 26-Mar to 23:59 27-Mar Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Fault indicators appeared to show that cable between SS8152 & SS8352 had failed. Front end of fdr livened at 0025. Back end attempted to be livened froim Forest Gardens fdr via SS8704 SD2, however Forest Gardens Fdr Cb tripped. Forest Gardens Fdr re-livened once parallel opened. Fault finding continuing beyond SS8352 SD2. Sending Asset Event to FFA FFA Order Acknowledged F-AE24FN4582-1-0 cnsug07 Anthony McConville 0409490954 FFA Order En Route F-AE24FN4582-1-0 cnsug07 FFA Order On Site F-AE24FN4582-1-0 cnsug07 Asset selection modified Sending Asset Event to FFA SS596020 SD1 RMU switch found to have flashed over during electrical storm. Cable isolated between SD1 & Links G1.83. Feeder re-livened at 0145. RMU will require replacement. Syscon 24FN4588 created. Haz Tags applied on site. Sending Asset Event to FFA Time On modified from 23:59 27-Mar to 23:59 30-Mar Sending Asset Event to FFA Time On modified from 23:59 30-Mar to 23:59 02-Apr Sending Asset Event to FFA FFA Order En Route F-AE24FN4582-1-0 cnsug07 FFA Order On Site F-AE24FN4582-1-0 cnsug07 FFA Order F-AE24FN4582-1-0 Completed by technician Anthony McConville in crew cnsug07(0409490954) with code A-T-306 - HV-Unassisted failure(Apparent defect) Action Taken : HV Fault in SS596020. SD1 has blown bushing/termination. HV switching to keep all substations on. RMU requires replacement. Site Label : 183389 RMU Req Time On modified from 23:59 02-Apr to 23:59 12-Apr Delayed for Now Time On modified from 23:59 12-Apr to 23:59 13-Apr Time On modified from 23:59 13-Apr to 23:59 27-Apr Time On modified from 23:59 27-Apr to 23:59 29-Apr Time On modified from 23:59 29-Apr to 23:59 30-Apr Time On modified from 23:59 30-Apr to 10:00 01-May Greg Ritchie adv will ebter New AFW to Replace RMU and this Unplanned Outage to be Delayed till Then Time On modified from 10:00 01-May to 10:00 17-May Time On modified from 10:00 17-May to 10:00 19-May Time On modified from 10:00 19-May to 10:00 26-May NFI Time On modified from 10:00 26-May to 10:00 02-Jun Time On modified from 10:00 02-Jun to 10:00 04-Jun NFI Time On modified from 10:00 04-Jun to 10:00 21-Jun AFW 24FN6463 entered to replace RMU on the 28/06/2024 Time On modified from 10:00 21-Jun to 14:00 28-Jun RMU placed back into service on S-12166-s Time On modified from 14:00 28-Jun to 14:10 28-Jun Updated Reasons tab. Reason for Event changed from Unknown | Invalid | 24FN4582 | EDMO-WHITE ROCK | WHITE ROCK | 2WHR | 22KV WHITE ROCK FDR CB | Equipment Failure or Malfunction | Completed | Unplanned Outage | Storm Electrical | FD-2122 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2024-03-26 | 1917722 | Unknown |  | EECL | Cable Return to Service | D2001 | Far North | 22kV | Cable Return to Service | M0269 | M0001 | M9999 |  | G | Capital | CAIRNS 1 | OT231068 | .HEADING ToughPad Location: Site Label Entered:1183389 Component: ENCL Component Mod: OC Technician: Anthony McConville Comments HV Fault in SS596020. SD1 has blown bushing/termination. HV switching to keep all substations on. RMU requires replacement. 01/05/2024 AC209496 - Closing this OT WO and WR as duplicate and has been progressed on WR1917724. | OT231068 | 202403
2024-03-26 |  | 2024-04-08 |  |  | Closed |  |  | 2024-03-26 | 2024-03-01 | EMERALD | EECL | FC | Feeder Section | XLFPE | 5468496 |  |  | 23/24 | 2024-09-26 | HV | 2024-03-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2024-03-26 16:03 | F-2674-r - EMERALD 22kV Caplla Rd ACR CB X8169 tripped. SCADA Interface automated outage. | 2024-03-26 | CAPELLA, EMERALD | Distribution Event | Normal Event | entered from the SCADA Interface 22kV Recloser X8169 - Tripped on SEF Depot Co-ord Advised Crew advsied on a fault job at TX589485 on reclose attempt of HV fuses it tripped the upstream ACR on SEF X8169. EMLFR01 Sending Asset Event to FFA FFA Order Created F-AE24CA4933-1-0 DfltHost Crew are isolating the TX589485 Then will reclose attempt of the FDR Sending Asset Event to FFA Reason for Event changed from Unknown Sending Asset Event to FFA Crews isolated & earthed TX589485 & Request reclose of FDR Manual Reclose Checklist Sending Asset Event to FFA Reclose succesful at 1646 Asset selection modified Sending Asset Event to FFA Crew advised TX requires Replacement possibly returning Tommorrow the 27th if not the following Day. Time On modified from 23:59 26-Mar to 16:00 27-Mar Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA4933-1-0 emlfr01 Anthony Ewing 0436429818 FFA Order En Route F-AE24CA4933-1-0 emlfr01 FFA Order On Site F-AE24CA4933-1-0 emlfr01 Restoration Comments for F-AE24CA4933-1-0 by emlfr01: TX site isolated waiting for replacement. FFA Order En Route F-AE24CA4933-1-0 emlfr01 FFA Order On Site F-AE24CA4933-1-0 emlfr01 Time On modified from 16:00 27-Mar to 18:00 27-Mar Sending Asset Event to FFA Time On modified from 18:00 27-Mar to 17:20 27-Mar Sending Asset Event to FFA Sending Asset Event to FFA FFA Order En Route F-AE24CA4933-1-0 emlfr01 FFA Order On Site F-AE24CA4933-1-0 emlfr01 FFA Order En Route F-AE24CA4933-1-0 emlfr01 FFA Order On Site F-AE24CA4933-1-0 emlfr01 FFA Order En Route F-AE24CA4933-1-0 emlfr01 FFA Order On Site F-AE24CA4933-1-0 emlfr01 FFA Order F-AE24CA4933-1-0 Completed by technician Anthony Ewing in crew emlfr01(0436429818) with code A-T-303 - Distribution substation Action Taken : Replaced Distribution TX like for like Site Label : 2148169 | Invalid | 24CA4933 | EM256 X8169 CAPELLA RD ACR | EM256 X8169 CAPELLA RD ACR | X8169/EM256 | X8169 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | FC-22-78457 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | #N/A | #N/A | 2024-03-26 | 1917658 | U Unknown |  | EECL | Forced Regulated | CEFR | Capricornia | 22kV | U Unknown | M0209 | M0052 | M9999 |  | G | Operational | EMERALD | OT231025 |  | OT231025 | 202403
2024-04-06 |  | 2024-04-07 | TDDI | Transformer-Distribution | Closed |  |  | 2024-04-06 | 2024-04-01 | ROCKHAMPTON | EECL | NS | Network Site | XLFPR | 1520829 |  |  | 23/24 | 2024-10-06 | HV | 2024-04-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-04-06 19:04 | F-2714-r SEF Trip SEF Detect downstream of RC873398. Comms failed immediately. Sectionalising found blown 11kV Pole Dist Sub 21886 - Replaced. SL 4136053. (S Gregory). | 2024-04-06 | GLENLEE, KAWANA, PARKHURST | Distribution Event | Normal Event | CCOC01 Blake Hayward 0417 917 095 Sending Asset Event to FFA FFA Order Created F-AE24CA5399-1-0 DfltHost FFA Order Acknowledged F-AE24CA5399-1-0 ccoc01 Blake Hayward 0419917095 FFA Order En Route F-AE24CA5399-1-0 ccoc01 SEF Detect downstream of RC873398. Comms failed immediately. Crews to open Gas Switch. OCC to energise the Belmont Rd Side of the feeder. Sending Asset Event to FFA FFA Order On Site F-AE24CA5399-1-0 ccoc01 Sending Asset Event to FFA Primary Asset de-escalated from Parkhurst 66/11kv Substation (ZS) Sending Asset Event to FFA Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA Crews patrolled feeder. Attempting to re-eng from RC873398 Sending Asset Event to FFA Feeder Tripped Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Crews to open RMU LB877446 Sending Asset Event to FFA Energised up to LB877446 Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA 319 Open Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Blown Tx 21886. crews also found X697Y Burning. Isolate from DO877452 to repair Asset selection modified Sending Asset Event to FFA Crews to return in daylight with Bucket Truck to repair Time On modified from 23:59 06-Apr to 23:59 07-Apr Sending Asset Event to FFA Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Time On modified from 23:59 07-Apr to 11:58 07-Apr Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA5399-1-0 yepwgo1 Greg Den Exter 0428747125 FFA Order En Route F-AE24CA5399-1-0 yepwgo1 FFA Order On Site F-AE24CA5399-1-0 yepwgo1 FFA Order F-AE24CA5399-1-0 Completed by technician Greg Den Exter in crew yepwgo1(0428747125) with code A-T-303 - Distribution substation Action Taken : Replaced blown up TX Site Label : 4136053 Updated Reasons tab. Reason for Event changed from Protective Device Operated | Invalid | 24CA5399 | 11KV ALEXANDRA ST FDR | 11KV OUTGOING FDR | ALEXANDRA ST | FB15Q00 11KV ALEXANDRA ST FDR CB | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS4136052 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -23.32777960228090 | 150.491427868660 | 2024-04-06 | 1919584 | PROT Protective Device Operated |  | EECL | Transformers Return to Service | D2002 | Capricornia | 11kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | J | Capital | ROCKHAMPTON 3 | OT232288 | Technician: Greg Den Exter Comments | OT232288 | 202404
2024-04-08 |  | 2024-04-09 | RXDI | Reactor-Distribution | Closed |  |  | 2024-04-08 | 2024-04-01 | BARCALDINE | EECL | NS | Network Site | XCPNB | 734058 |  |  | 23/24 | 2024-10-08 | HV | 2024-04-01 |  | Internal Fault | Damaged | Reactor, Unknown | Outage | South | HV-Unassisted failure(Apparent defect) | 2024-04-08 06:39 | F-2723-r - BARC - Cressbank SWER - Calls indicate issue at 12.7kV SWER Recloser X6871. Regulator on Portwine Rd is in bypass, could be the issue. Calls from TX 391183 and 391668. James advised supply restored at 1758 hrs, Reactor RE162477 (2026783) HV Fuses open as Reactor failed in service and RTS TBA | 2024-04-08 | ALPHA: KILCOOL RD, OFF CAPRICORN HWY, OFF TAMBO RD, PORTWINE RD | Distribution Event | Normal Event | Calls indicate issue at 12.7kV SWER Recloser X6871. Regulator on Portwine Rd is in bypass, could be the issue. Calls from TX 391183 and 391668. Depot to advise. Sending Asset Event to FFA FFA Order Created F-AE24CA5409-1-0 DfltHost Removing Asset Event from FFA FFA Order cancelled.F-AE24CA5409-1-0 DSO Sending Asset Event to FFA FFA Order Created F-AE24CA5409-1-1 DfltHost Sent brccmfr02. Sending Asset Event to FFA WGL adv brccdwgl1. Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA5409-1-1 brccdwgl1 James Hunt 0427698564 FFA Order En Route F-AE24CA5409-1-1 brccdwgl1 James advised supply restored at 1758 hrs, Reactor RE162477 (2026783) HV Fuses open as Reactor failed in service and RTS TBA Time On modified from 23:59 08-Apr to 17:58 08-Apr Reason for Event changed from Unknown Sending Asset Event to FFA Sending Asset Event to FFA FFA Order On Site F-AE24CA5409-1-1 brccdwgl1 FFA Order F-AE24CA5409-1-1 Completed by technician James Hunt in crew brccdwgl1(0427698564) with code A-T-303 - Distribution substation Action Taken : Reactor at site label 2026783 failed in service. Site Label : 2026783 | Invalid | 24CA5409 |  | Cressbank Recloser - Glenmyra SWER | X6871 | Cressbank Recloser - Glenmyra SWER | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS2026783 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -23.73001861572270 | 147.124374389648 | 2024-04-08 | 1919699 | BEAUMONT PASTORAL COMPANY | U - Unknown / No Power | EECL | Forced Regulated | CEFR | Capricornia | 19kV | BEAUMONT PASTORAL COMPANY | M0400 | M0052 | M0070 |  | H | Operational | BARCALDINE | OT232387 | Technician: James Hunt Comments Reactor at site label 2026783 failed in service. | OT232387 | 202404
2024-04-13 |  | 2024-04-14 | TDDI | Transformer-Distribution | Closed |  |  | 2024-04-13 | 2024-04-01 | THEODORE | EECL | NS | Network Site | XCFZB | 919914 |  |  | 23/24 | 2024-10-13 | HV | 2024-04-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-04-13 11:28 | F-2734-r 22kV Dropout Fuse X2631, Crew need access downstream of X2631 to replace TX 79328 | 2024-04-13 | DULULU: DEE RIVER RD, JAMESONS LANE | Distribution Event | Normal Event | 22kV Dropout Fuse X2631, Crew need access downstream of X2631 to replace TX 79328 Sending Asset Event to FFA FFA Order Created F-AE24CA5635-1-0 DfltHost Sending Asset Event to FFA F-2734-r Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 13-Apr to 18:23 13-Apr Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA5635-1-0 bilcm06 Tom Hill 0437516802 FFA Order En Route F-AE24CA5635-1-0 bilcm06 FFA Order On Site F-AE24CA5635-1-0 bilcm06 FFA Order F-AE24CA5635-1-0 Completed by technician Tom Hill in crew bilcm06(0437516802) with code A-T-303 - Distribution substation Action Taken : replaced transformer due to internal fault Site Label : 2008852 Reason for Event changed from Transient Fault of Unknown Origin | Valid | 24CA5635 |  | X2631 | X2631 | X2631 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS2008852 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -23.86734199523930 | 150.253036499023 | 2024-04-13 | 1920953 | TFUO Transient Fault of Unknown Origin |  | EECL | Transformers Return to Service | D2002 | Capricornia | 22kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | G | Capital | BILOELA | OT233081 | Technician: Tom Hill Comments | OT233081 | 202404
2024-04-14 |  | 2024-04-15 | TDDI | Transformer-Distribution | Closed |  |  | 2024-04-14 | 2024-04-01 | MAREEBA | EECL | NS | Network Site | XLTNR | 1216965 |  |  | 23/24 | 2024-10-14 | HV | 2024-04-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-04-14 22:30 | 22kV Pole Dist Sub SS2703 - Crew replaced transformer. SL 5010157. (S Gregory). | 2024-04-14 | MAREEBA: BAILEY ST, FOULIS ST, JAMIESON ST, KENNEALLY RD, LANNOY ST | Distribution Event | Normal Event | Multiple calls of LOS from beyond 22kV Pole Dist Sub SS2703 Sending Asset Event to FFA FFA Order Created F-AE24FN5200-1-0 DfltHost FFA Order Acknowledged F-AE24FN5200-1-0 mbacsfr06 Cameron Jerome 0419932114 FFA Order En Route F-AE24FN5200-1-0 mbacsfr06 Time On modified from 23:59 14-Apr to 23:59 15-Apr Sending Asset Event to FFA Crews advised Sub SS2703 required replacement. crews are switching to replace tx now. Sending Asset Event to FFA Time On modified from 23:59 15-Apr to 07:00 15-Apr Sending Asset Event to FFA Time On modified from 07:00 15-Apr to 03:45 15-Apr Sending Asset Event to FFA FFA Order On Site F-AE24FN5200-1-0 mbacsfr06 FFA Order F-AE24FN5200-1-0 Completed by technician Cameron Jerome in crew mbacsfr06(0419932114 ) with code A-T-320 - SUBT-Unassisted failure(Apparent defect) Action Taken : replaced tx ss2703 Site Label : 5010157 Actual Power Restoration for F-AE24FN5200-1-0: 15-APR-2024 05:11:00 Reason for Event changed from Unknown Added notes to Reasons tab. Updated Event Trigger from SUBT-Unassisted failure to Distribution substation. | Invalid | 24FN5200 |  | Lannoy St | SS2703 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS5010157 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -17.01424789428710 | 145.430969238281 | 2024-04-14 | 1921051 | U Unknown |  | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | G | Capital | MAREEBA 2 | OT233171 | Technician: Cameron Jerome Comments replaced tx ss2703 | OT233171 | 202404
2024-04-18 |  | 2024-04-19 | TDDI | Transformer-Distribution | Closed |  |  | 2024-04-18 | 2024-04-01 | BILOELA | EECL | NS | Network Site | XCFZB | 1001375 |  |  | 23/24 | 2024-10-18 | HV | 2024-04-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-04-18 16:00 | 12.7kV SWER Pole Dist Sub 718150 - Crew advised Transformer is faulty and has had lid blown off TX. | 2024-04-18 | N/A | Distribution Event | Normal Event | 12.7kV SWER Pole Dist Sub 718150 - Crew advised Transformer is faulty and has had lid blown off TX. Crew has advised Customer TX will be replaced tomorrow.019/04. Asset selection reset . Asset selection modified Refer to F-3288-q Sending Asset Event to FFA FFA Order Created F-AE24CA5851-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24CA5851-1-0 bilcm01 Anthony Picton 0427161706 FFA Order En Route F-AE24CA5851-1-0 bilcm01 FFA Order On Site F-AE24CA5851-1-0 bilcm01 Time On modified from 14:00 19-Apr to 09:04 19-Apr Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24CA5851-1-0 Completed by technician Anthony Picton in crew BILCM01(0427161706) with code A-T-303 - Distribution substation Action Taken : replace 12.7 kv transformer Site Label : 4138676 | Valid | 24CA5851 | Dawes North SWER | Dawes North SWER | SW/718115 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS4138676 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -24.62893867492680 | 150.709564208984 | 2024-04-18 | 1921954 | MR M WHITE | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Capricornia | 12.7kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | I | Capital | BILOELA | OT233599 | Technician: Anthony Picton Comments | OT233599 | 202404
2024-04-23 |  | 2024-04-23 |  |  | Closed |  |  | 2024-04-23 | 2024-04-01 | KILKIVAN | EECL | NT | Network Slot | XCFBK | 2652158 |  |  | 23/24 | 2024-10-23 | LV | 2024-04-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-04-23 18:20 | Brownout calls on 11kV Pole Dist Sub 9441 | 2024-04-23 | GLENWOOD: ARBORSEVENTEEN RD, WARDS RD | Distribution Event | Normal Event | Brownout calls on 11kV Pole Dist Sub 9441 kkvcsfr01 Sending Asset Event to FFA . Sending Asset Event to FFA FFA Order Created F-AE24WB5204-1-0 DfltHost FFA Order Acknowledged F-AE24WB5204-1-0 kkvcsfr01 Sam tardent 0436522484 FFA Order En Route F-AE24WB5204-1-0 kkvcsfr01 FFA Order On Site F-AE24WB5204-1-0 kkvcsfr01 FFA Order F-AE24WB5204-1-0 Completed by technician Sam tardent in crew kkvcsfr01(0436522484) with code A-T-303 - Distribution substation Action Taken : test customers switchboard , both said had low volts when power restored after planned outage but once onsite it was back to normal . we tested at switchboards and got 221v and nit test of 0.31 ohms Site Label : 9441 Time On modified from 23:59 23-APR to 21:14 23-APR | Invalid | 24WB5204 |  | Wards Rd/Arborseventeen Rd Glenwood | 9441 |  | Unknown | Completed | Unplanned Outage | Wet / Rain | SP-128676 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | #N/A | #N/A | 2024-04-23 | 1922849 | U Unknown |  | EECL | Forced Regulated | WBFR | Wide Bay | LV | U Unknown | M0209 | M0001 | M9999 |  | M | Operational | KILKIVAN | OT234124 | ToughPad Location: Site Label Entered:9441 Component: TDDI Component Mod: OC Technician: Sam tardent Comments everything seems fine, network possibly overloaded after supply restored after planned outage and had Low volts but now fine | OT234124 | 202404
2024-04-27 |  | 2024-04-27 | TDDI | Transformer-Distribution | Closed |  |  | 2024-04-27 | 2024-04-01 | TOWNSVILLE | EECL | NS | Network Site | XLHBT | 1741802 |  |  | 23/24 | 2024-10-27 | HV | 2024-04-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-04-27 15:30 | 11kV Pole Dist Sub TVS2978, Shane gamble onsite , advise Cphase bush burning and leaking oil badley, uplunned TX change requuired | 2024-04-27 | KIRWAN: BAMFORD LANE, JULIA ST, NELIA ST, PINE ST, TAMARIND ST | Distribution Event | Normal Event | 11kV Pole Dist Sub TVS2978, Shane gamble onsite , advise Cphase bush burning and leaking oil badley, uplunned TX change requuired Sending Asset Event to FFA FFA Order Created F-AE24NQ7906-1-0 DfltHost FFA Order Acknowledged F-AE24NQ7906-1-0 twvoc01 Shane Gamble 0407640444 FFA Order En Route F-AE24NQ7906-1-0 twvoc01 FFA Order On Site F-AE24NQ7906-1-0 twvoc01 Time On modified from 23:59 27-Apr to 18:39 27-Apr Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24NQ7906-1-0 Completed by technician Shane Gamble in crew twvoc01(0407640444) with code A-T-303 - Distribution substation Action Taken : Replaced 200 kVa TX under access due to burning up C phase LV bushing. Burning up bushing also had oil pouring out around bushing casket. TX FDC and commissioning completed. Site Label : 2114774 Time On modified from 18:39 27-APR to 19:15 27-APR | Invalid | 24NQ7906 | Sub, Cranbrook No.7 11kV feeder | TVS2978 | TVS2978 |  | Unknown | Completed | Unplanned Outage | Fine | NS2114774 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -19.30682182312010 | 146.740753173828 | 2024-04-27 | 1923454 | MR S GRIGG | O - Other | EECL | Transformers Return to Service | D2002 | North Queensland | 11kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | J | Capital | TOWNSVILLE RR | OT234442 | Technician: Shane Gamble Comments | OT234442 | 202404
2024-05-01 |  | 2024-05-01 | TDDI | Transformer-Distribution | Closed |  |  | 2024-05-01 | 2024-05-01 | TOOWOOMBA | EECL | NS | Network Site | XLGDT | 1647696 |  |  | 23/24 | 2024-11-01 | HV | 2024-05-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-05-01 13:55 | 11kV Pole Dist Sub PE09563 - Crew advised need access to replace faulty TX. | 2024-05-01 | N/A | Distribution Event | Normal Event | 11kV Pole Dist Sub PE09563 - Crew advised need access to replace faulty TX. twmoc01 Time On modified from 23:59 01-May to 20:35 01-May | Valid | 24SW8363 | Unknown | AUBIGNY | 2098 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS3073326 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -27.49865913391110 | 151.645858764648 | 2024-05-01 | 1924207 | MR W REEN | L - Life Threatening | EECL | Transformers Return to Service | D2002 | South West | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | TOOWOOMBA RAPIDS | OT234846 | .HEADING Technician: Jeff Lewis Comments replaced 63 kva tx and LVCM | OT234846 | 202405
2024-05-09 |  | 2024-05-11 |  |  | Closed |  | Replace | 2024-05-09 | 2024-05-01 | TOOWOOMBA | EECL | NT | Network Slot | XLGDT | 6218906 |  |  | 23/24 | 2024-11-09 | HV | 2024-05-01 |  | Internal Fault | Broken | Padmount Substation | Outage | South | Distribution substation | 2024-05-09 11:16 | 11kV Ring Main Unit FS19883 - blown HV fuse to TX GE01093. After fuse replaced, GE01093 failed. Generator connected to GE01093 to restore customers and repairs made under Forced Outage 24SW8748. (S Gregory). | 2024-05-09 | HIGHFIELDS: CHERRY CL, GEOFFREY WAY, JANELLE CT, PARKWAY DR, PREECE DR | Distribution Event | Normal Event | 11kV Ring Main Unit FS19883 - blown HV fuse to TX GE01093. Crew require access to replace fuse.. Time On modified from 23:59 09-May to 14:30 09-May Time On modified from 14:30 09-May to 15:30 09-May Time On modified from 15:30 09-May to 17:30 09-May Time On modified from 17:30 09-May to 19:30 09-May Fuse replaced transformer has failed. To be replaced under a forced AFW on this sat 11/05/24. Generator placed on GE01093. To be removed on 11/05/204. Time On modified from 19:30 09-May to 17:58 09-May Updated Reasons tab. Updated Event Trigger from T&MR to Distribution substation. Reason for Event changed from HV or LV Fuse blown | Invalid | 24SW8659 |  | to GE01093 | FS19883 | to GE01093 | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NT137931 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2024-05-09 | 1925562 | MRS B DRISCOLL | U - Unknown / No Power | EECL | Forced Regulated | SWFR | South West | 11kV | MRS B DRISCOLL | M0269 | M0001 | M0070 | 7 | J | Operational | TOOWOOMBA RAPIDS | OT235545 |  | OT235545 | 202405
2024-05-09 |  | 2024-05-10 | TDDI | Transformer-Distribution | Closed |  |  | 2024-05-09 | 2024-05-01 | MAREEBA | EECL | NS | Network Site | XLTNR | 1231619 |  |  | 23/24 | 2024-11-09 | HV | 2024-05-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-05-09 19:03 | Fault Job F-3811-s Crew advised that they require access to replace SS2754 | 2024-05-09 | ARRIGA: ARRIGA RD | Distribution Event | Normal Event | Crew advised that they require access to replace SS2754 Fault Job F-3811-s Sending Asset Event to FFA FFA Order Created F-AE24FN6119-1-0 DfltHost Sending Asset Event to FFA Time On modified from 23:59 09-May to 23:59 10-May Sending Asset Event to FFA FFA Order Acknowledged F-AE24FN6119-1-0 mbaco01 Marcus McMahon 0437576228 FFA Order En Route F-AE24FN6119-1-0 mbaco01 FFA Order On Site F-AE24FN6119-1-0 mbaco01 Time On modified from 23:59 10-May to 00:12 10-May Sending Asset Event to FFA FFA Order F-AE24FN6119-1-0 Completed by technician Marcus McMahon in crew mbaco01(0437576228 ) with code A-T-303 - Distribution substation Action Taken : TX Replace due to open circuit on the LV winding Site Label : 5003519 Actual Power Restoration for F-AE24FN6119-1-0: 10-MAY-2024 00:30:00 auto-completed | Invalid | 24FN6119 |  | IWS ARRIGA | SS2754 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Wet / Rain | NS5003519 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -17.07110636378980 | 145.304780458086 | 2024-05-09 | 1925699 | MR R BRAY | O - Other | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0001 | M0070 |  | G | Capital | ATHERTON 2 | OT235609 | Technician: Marcus McMahon Comments | OT235609 | 202405
2024-05-20 |  | 2024-05-20 | TDDI | Transformer-Distribution | Closed |  |  | 2024-05-20 | 2024-05-01 | GIN GIN | EECL | NS | Network Site | XCFBN | 8644699 |  |  | 23/24 | 2024-11-20 | HV | 2024-05-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | Distribution substation | 2024-05-20 09:02 | 11kV Pole Dist Sub SP788536 - Crew advised faulty TX to be replaced. | 2024-05-20 | DUINGAL: MCLENNAN DR | Distribution Event | Normal Event | 11kV Pole Dist Sub SP788536 - Crew advised faulty TX to be replaced. ggfr03 F-2804-r Time On modified from 23:59 20-May to 14:00 20-May Sending Asset Event to FFA FFA Order Created F-AE24WB5812-1-0 DfltHost Sending Asset Event to FFA Time On modified from 14:00 20-May to 12:06 20-May Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB5812-1-0 ggfr03 Nathan Francis 0460435210 FFA Order En Route F-AE24WB5812-1-0 ggfr03 FFA Order On Site F-AE24WB5812-1-0 ggfr03 FFA Order F-AE24WB5812-1-0 Completed by technician Nathan Francis in crew ggfr03(0460435210) with code A-T-303 - Distribution substation Action Taken : replaced faulty transformer Site Label : 11163076 Time On modified from 12:06 20-MAY to 12:17 20-MAY FFA Order F-AE24WB5812-1-0 Completed by technician Nathan Francis in crew ggfr03(0460435210) with code A-T-303 - Distribution substation Action Taken : replaced faulty transformer Site Label : 11163076 Time On modified from 12:06 20-MAY to 12:17 20-MAY FFA Order F-AE24WB5812-1-0 Completed by technician Nathan Francis in crew ggfr03(0460435210) with code A-T-303 - Distribution substation Action Taken : replaced faulty transformer Site Label : 11163076 Time On modified from 12:06 20-MAY to 12:17 20-MAY | Valid | 24WB5812 | 128 - 130 MCLENNAN DVE, DUINGAL QLD 4660 | SP788536 | SP788536 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS11163076 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -25.12949201585060 | 152.013346106492 | 2024-05-20 | 1927370 | GREENSILL FARMS PTY LTD | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | GIN GIN | OT236499 | Technician: Nathan Francis Comments replaced faulty transformer | OT236499 | 202405
2024-05-29 |  | 2024-05-30 | TDDI | Transformer-Distribution | Closed |  |  | 2024-05-29 | 2024-05-01 | MAREEBA | EECL | NS | Network Site | XLTNR | 1240655 |  |  | 23/24 | 2024-11-29 | HV | 2024-05-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2024-05-29 22:19 | 22kV Recloser Pole HEN1 Tripped on EF. C phase Crew replaced 200kVA 22kV Pole Dist Sub SS4719. SL 5040891. (S Gregory). | 2024-05-29 | ARRIGA: MAREEBA DIMBULAH RD, MCBEAN RD GLEN RUSSELL: ANDY SHEPPARD DR PADDYS GREEN: BOWER RD, DIMBULAH RD, IVICEVIC RD, MCBEAN RD, TYRCONNELL RD WEST PADDYS GREEN: BOWER RD, MCBEAN RD | Distribution Event | Normal Event | 22kV Recloser Pole HEN1 Tripped on EF. C phase Time Off modified from 22:24 29-May to 22:19 29-May Brendan Nastasi 0437 537 234 Sending Asset Event to FFA FFA Order Created F-AE24FN6868-1-0 DfltHost Crews to Patrol to find fault Reason for Event changed from Unknown Sending Asset Event to FFA FFA Order Acknowledged F-AE24FN6868-1-0 mbaco01 Brendan nastasi 0437537234 FFA Order En Route F-AE24FN6868-1-0 mbaco01 Time On modified from 23:59 29-May to 23:59 30-May Sending Asset Event to FFA Restored up to KE14, patrol continuing Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Line patroller to HA1, No cause found, HA1 - OPD, KE14 - RDC, Successful.. Sending Asset Event to FFA Line patrolled beyond HA1 no cause found, HA1 - RDC HEN1 ACR tripped on E/F HA1 - OPD. Asset selection modified Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA WGl to arrange for crew to perform detailed patrol during daylight hrs. Sending Asset Event to FFA Crew advised SS4719 has failed and requires replacing Time On modified from 23:59 30-May to 13:00 30-May Sending Asset Event to FFA Time On modified from 13:00 30-May to 12:50 30-May Sending Asset Event to FFA Sending Asset Event to FFA Assign to mba10L1 Sending Asset Event to FFA FFA Order Acknowledged F-AE24FN6868-1-0 mba10l1 Andrew cadorin 0427616093 FFA Order En Route F-AE24FN6868-1-0 mba10l1 FFA Order On Site F-AE24FN6868-1-0 mba10l1 FFA Order F-AE24FN6868-1-0 Completed by technician Andrew cadorin in crew mba10l1(0427616093) with code A-T-303 - Distribution substation Action Taken : replaced 200 kva at ss4719 Site Label : 5040891 Added notes to Reasons tab. Reason for Event changed from Protective Device Operated | Valid | 24FN6868 |  | TABACUM | 2TAB.FC | Tyrconnell Recloser | Protective Device Operated | Completed | Unplanned Outage | Wet / Rain | NS5040891 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -16.91581499933020 | 145.252113998762 | 2024-05-29 | 1929252 | U Unknown |  | EECL | Transformers Return to Service | D2002 | Far North | 22kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | G | Capital | MAREEBA 2 | OT237415 | Technician: Andrew cadorin Comments | OT237415 | 202405
2024-05-31 |  | 2024-06-01 | TDDI | Transformer-Distribution | Closed |  |  | 2024-05-31 | 2024-05-01 | HERVEY BAY | EECL | NS | Network Site | XLFBH | 1325312 |  |  | 23/24 | 2024-11-30 | HV | 2024-05-01 |  | Unknown | Broken | Tx, Tank Body | Outage | South | HV-Unassisted failure(Apparent defect) | 2024-05-31 20:28 | F-3413-q Crew require access to 11kV Pole Dist Sub 12530 due to TX damage | 2024-05-31 | HERVEY BAY: UNMETERED SUPPLY KINGAROY: UNMETERED SUPPLY URANGAN: BUCCANEER DR, JETTY RD | Distribution Event | Normal Event | Crew require access to 11kV Pole Dist Sub 12530 due to TX damage TX replacement, access from EDO hboc01 Sending Asset Event to FFA FFA Order Created F-AE24WB6130-1-0 DfltHost F-3413-q Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 31-May to 23:42 31-May Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB6130-1-0 hboc01 Scott Harling 0447761083 FFA Order En Route F-AE24WB6130-1-0 hboc01 FFA Order On Site F-AE24WB6130-1-0 hboc01 FFA Order F-AE24WB6130-1-0 Completed by technician Scott Harling in crew hboc01(0447761083) with code A-T-303 - Distribution substation Action Taken : Replaced 200kva TX 3 Hv fuses blown and 2 shots on Fdr. Site Label : 3057208 Time On modified from 23:42 31-MAY to 00:19 01-JUN | Valid | 24WB6130 |  | MILLER ST | 12530 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS3057208 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | -25.29440116882320 | 152.908355712891 | 2024-05-31 | 1929711 | HERVEY BAY BOAT CLUB INC | F - Fire - Pole/Structure | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | HERVEY BAY 2 | OT237589 | Technician: Scott Harling Comments | OT237589 | 202405
2024-06-07 |  | 2024-06-07 | RXDI | Reactor-Distribution | Closed |  |  | 2024-06-07 | 2024-06-01 | RICHMOND | EECL | NS | Network Site | XCHBR | 1841805 |  |  | 23/24 | 2024-12-07 | HV | 2024-06-01 |  | Unknown | Broken | Reactor, Unknown | Outage | North | Distribution substation | 2024-06-07 03:56 | F-3952-s - RICHMOND 33kV Barabon Fdr CB H652 tripped. SCADA Interface automated outage. | 2024-06-07 | HUGHENDEN, RICHMOND, | Sub Transmission Event | Normal Event | entered from the SCADA Interface Issued to Maks Chylewski 0428 600 619, rchcs01. F-3952-s. Msg left with O/C Supervisor Justin Vardy 0409 144 002, advising him of feeder fault. Depot Co-ord Advised Sending Asset Event to FFA FFA Order Created F-AE24NQ9519-1-0 DfltHost Maks Chylewski 0428 600 619 advised he will organize a helicopter to conduct line patrol. Sending Asset Event to FFA Asset selection modified Manual Reclose Checklist Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Created Forced outage 24NQ9538 to allow crew to remove bird nest from open point GS795749 Sending Asset Event to FFA J Bishop Advised Cracked insulators at 2034483 & 2034499 Sending Asset Event to FFA Time On modified from 23:59 07-Jun to 16:21 07-Jun Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ9519-1-0 rchcs01 Maks Chylewski 0428600619 FFA Order En Route F-AE24NQ9519-1-0 rchcs01 FFA Order On Site F-AE24NQ9519-1-0 rchcs01 FFA Order F-AE24NQ9519-1-0 Completed by technician Maks Chylewski in crew rchcs01(0428600619) with code A-T-303 - Distribution substation Action Taken : flew line found birds nest at GS795749 removed from line, and check insulators at two poles under access, after another inspection found reactor on HUS123 blown removed from service and reenergised line Site Label : 5216005 auto-completed | Valid | 24NQ9519 | RICH-80 | Barabon Quarry 33kV Feeder | RI-80 | RI-H652 | Unknown | Completed | Unplanned Outage | Fine | NS5216005 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -20.89272117614750 | 143.581756591797 | 2024-06-07 | 1931028 | U Unknown |  | EECL | Forced Regulated | NQFR | North Queensland | 19kV | U Unknown | M0400 | M0001 | M9999 |  | H | Operational | RICHMOND | OT238165 | Technician: Maks Chylewski Comments | OT238165 | 202406
2024-06-09 |  | 2024-06-10 | TDDI | Transformer-Distribution | Closed |  |  | 2024-06-09 | 2024-06-01 | PROSTON | EECL | NS | Network Site | XCFBR | 1416428 |  |  | 23/24 | 2024-12-09 | HV | 2024-06-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2024-06-09 18:18 | F-3456-q - 11kV Recloser 591642 - Fault downstream of recloser Faults indicate blown fuse at 11kV Dropout Fuse 591649, Fuses confirmed in service by crew Crew found fault at hardwired 11kV Pole Dist Sub 3643. SL 2071771. (S Gregory). | 2024-06-09 | DARR CREEK, DURONG, DURONG SOUTH | Distribution Event | Normal Event | Faults indicate blown fuse at 11kV Dropout Fuse 591649 MRGCM01 Sending Asset Event to FFA FFA Order Created F-AE24WB6366-1-0 DfltHost FFA Order Acknowledged F-AE24WB6366-1-0 mrgcm01 Jack McBlane 0428071189 Intermitted comms issue with recloser delaying sectionalising Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Crew adv out of hours, return tomorrow to start pulling hv fuses on Transformers Time On modified from 23:59 09-Jun to 23:59 10-Jun Sending Asset Event to FFA Sending Asset Event to FFA F-3456-q Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Crews on site opening sec S1993 Sending Asset Event to FFA Crews conformer reclose unsuccessful closing S1993 opening S1862. Sending Asset Event to FFA reclose unsuccessful closed s1862 DSO clearance issue to darren steinhardt to investigate transformers will ring back with findings . Sending Asset Event to FFA Crew have found fault at transformer 3643 hardwired transformer Isolating closing open links and then attmepting reclose crews waiting for EWP to install pole step and earth LL lead to gain access to replace . Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB6366-1-0 mrgoc01 DARREN STEINHARDT 0407892168 FFA Order En Route F-AE24WB6366-1-0 mrgoc01 FFA Order On Site F-AE24WB6366-1-0 mrgoc01 FFA Order F-AE24WB6366-1-0 Completed by technician DARREN STEINHARDT in crew mrgoc01(0407892168) with code A-T-303 - Distribution substation Action Taken : hard wired faulty TX at 3643 Site Label : 2071771 Actual Power Restoration for F-AE24WB6366-1-0: 10-JUN-2024 14:18:00 Time On modified from 23:59 10-Jun to 14:20 10-Jun Added notes to Reasons tab. Updated Asset Event Type from Transmission to Distribution. Reason for Event changed from Unknown | Invalid | 24WB6366 | MUNDUBBERA DURONG RD, DURONG QLD 4610 | Woolletts Rd | 591649 | Durong SWER Recloser | Equipment Failure or Malfunction | Completed | Unplanned Outage | Cold | NS2071771 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -26.38228607177730 | 151.239303588867 | 2024-06-09 | 1931459 | T/AS G P & J L CALVERT | O - Other | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | J | Capital | MURGON | OT238421 | Technician: DARREN STEINHARDT Comments | OT238421 | 202406
2024-06-09 |  | 2024-06-09 |  |  | Closed |  |  | 2024-06-09 | 2024-06-01 | COLLINSVILLE | EECL | NT | Network Slot | XLHBB | 2150271 |  |  | 23/24 | 2024-12-09 | HV | 2024-06-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | North | Distribution substation | 2024-06-09 06:09 | Mark advised require access to CVS30 to replace bundle box and LA's | 2024-06-09 | COLLINSVILLE: BIRRALEE STATION | Distribution Event | Normal Event | Mark advised require access to CVS30 to replace bundle box and LA's Mark Chappel . Sending Asset Event to FFA FFA Order Created F-AE24NQ9582-1-0 DfltHost Crews advised TX requires replacement Sending Asset Event to FFA Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 09-Jun to 18:32 09-Jun Sending Asset Event to FFA FFA Order Acknowledged F-AE24NQ9582-1-0 clvoh01 Chappo 0428766675 FFA Order En Route F-AE24NQ9582-1-0 clvoh01 FFA Order On Site F-AE24NQ9582-1-0 clvoh01 FFA Order F-AE24NQ9582-1-0 Completed by technician Chappo in crew clvoh01(0428766675) with code A-T-303 - Distribution substation Action Taken : replaced blown 33kv tx Site Label : Cvs30 Actual Power Restoration for F-AE24NQ9582-1-0: 09-JUN-2024 19:39:00 auto-completed | Invalid | 24NQ9582 | Sub, Collinsville No.2 feeder | CVS30 | CVS30 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | SP-107531 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2024-06-09 | 1931382 | HELEN LITTLE | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | North Queensland | 33kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | F | Capital | BOWEN | OT238357 | ToughPad Location: Site Label Entered:Cvs30 Component: TDDI Component Mod: OC Technician: Chappo Comments | OT238357 | 202406
2024-06-11 |  | 2024-06-12 | TDDI | Transformer-Distribution | Closed |  |  | 2024-06-11 | 2024-06-01 | BIGGENDEN | EECL | NS | Network Site | XCFBI | 1403241 |  |  | 23/24 | 2024-12-11 | HV | 2024-06-01 |  | Corrosion | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2024-06-11 08:54 | F-3472-q 11kV Pole Dist Sub 4168 HV Lead Broken requires Isolation from HV Fuses | 2024-06-11 | DEGILBO: BELAH RD | Distribution Event | Normal Event | 11kV Pole Dist Sub 4168 HV Lead Broken Isolation From HV Fuses bgncdwgl1 Sending Asset Event to FFA FFA Order Created F-AE24WB6436-1-0 DfltHost Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB6436-1-0 bgncdwgl1 Phillip Sharps 0437047448 FFA Order En Route F-AE24WB6436-1-0 bgncdwgl1 FFA Order On Site F-AE24WB6436-1-0 bgncdwgl1 FFA Order F-AE24WB6436-1-0 Completed by technician Phillip Sharps in crew bgncdwgl1(0437047448) with code A-T-303 - Distribution substation Action Taken : Replaced damaged transformer Site Label : 3217449 Time On modified from 23:59 12-JUN to 10:20 12-JUN Time On modified from 10:20 12-Jun to 10:08 12-Jun | Valid | 24WB6436 |  | 4168 | 4168 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS3217449 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -25.446008682251 | 151.983978271484 | 2024-06-11 | 1931827 | MR D COURTICE | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0052 | M0011 |  | J | Capital | BIGGENDEN | OT238587 | Technician: Phillip Sharps Comments | OT238587 | 202406
2024-06-13 |  | 2024-06-13 |  |  | Closed |  |  | 2024-06-13 | 2024-06-01 | MACKAY | EECL | NT | Network Slot | XLFPK | 2329851 |  |  | 23/24 | 2024-12-13 | HV | 2024-06-01 |  | Unknown | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-06-13 03:50 | F-3978-s 11kV Pole Dist Sub 2199 - Crew replaced blown HV fuses, but unsuccessful. Crew replaced transformer. (S Gregory). | 2024-06-13 | NORTH MACKAY: BRADFORD ST, DOLBY CT, KENZEY ST, LAIRD ST, ROSE ST, THE CRESCENT | Distribution Event | Normal Event | Multiple calls for loud bang and loss of supply from 11kV Pole Dist Sub 2199 Sending Asset Event to FFA FFA Order Created F-AE24MK5045-1-0 DfltHost FFA Order Acknowledged F-AE24MK5045-1-0 mckoc02 Matt Toivanen 0477050123 FFA Order En Route F-AE24MK5045-1-0 mckoc02 FFA Order On Site F-AE24MK5045-1-0 mckoc02 F-3978-s Sending Asset Event to FFA Sending Asset Event to FFA Time On modified from 23:59 13-Jun to 12:27 13-Jun Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24MK5045-1-0 Completed by technician Matt Toivanen in crew mckoc02(0477050123) with code A-T-303 - Distribution substation Action Taken : Found HV fuses down at sub 2199. Replaced fuses and attempted to reclose without success. Replaced sub and carried out post energisation testing. Site Label : 2199 Time On modified from 12:27 13-JUN to 12:30 13-JUN Reason for Event changed from HV or LV Fuse blown Updated Reasons tab. Updated Event Trigger from Animal impact to Distribution substation. | Invalid | 24MK5045 |  | KENZEY ST | 2199 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | SP-154229 | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | #N/A | #N/A | 2024-06-13 | 1932375 | MS N SCHOLES | O - Other | EECL | Transformers Return to Service | D2002 | Mackay | 11kV | Transformers Return to Service | M0209 | M0001 | M9999 |  | J | Capital | MACKAY 2 | OT238797 | ToughPad Location: Site Label Entered:2199 Component: TDDI Component Mod: OC Technician: Matt Toivanen Comments | OT238797 | 202406
2024-06-25 |  | 2024-06-25 | TDDI | Transformer-Distribution | Closed |  |  | 2024-06-25 | 2024-06-01 | MARYBOROUGH | EECL | NS | Network Site | XLFBA | 5906070 |  |  | 23/24 | 2024-12-25 | HV | 2024-06-01 |  | Unknown | Damaged | Tx, Tank Body | Outage | South | HV-Unassisted failure(Apparent defect) | 2024-06-25 10:00 | F-32380-g Crew Advised when energising TX after blown HV fuse, transformer was making concerning noises and requires replacement | 2024-06-25 | OWANYILLA: OWANYILLA BOUNDARY RD | Distribution Event | Normal Event | Crew Advised when energising TX after blown HV fuse, transformer was making concerning noises and requires replacement Sending Asset Event to FFA FFA Order Created F-AE24WB6836-1-0 DfltHost Sending Asset Event to FFA F-32380-g Sending Asset Event to FFA Time On modified from 17:00 25-Jun to 14:00 25-Jun Sending Asset Event to FFA Crew Replaced TX Sending Asset Event to FFA FFA Order Acknowledged F-AE24WB6836-1-0 mrbcs08 Jason rehren 0475384191 FFA Order En Route F-AE24WB6836-1-0 mrbcs08 FFA Order On Site F-AE24WB6836-1-0 mrbcs08 FFA Order F-AE24WB6836-1-0 Completed by technician Jason rehren in crew mrbcs08(0475384191 ) with code A-T-303 - Distribution substation Action Taken : replaced transformer, transformer making arcing noises when fuse replaced on initial fault call. Site Label : 3008800 Time On modified from 14:00 25-JUN to 15:48 25-JUN | Valid | 24WB6836 | BLACKMOUNT RD, OWANYILLA QLD 4650 | Blackmount Rd | 649275 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS3008800 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | -25.67291831970210 | 152.586669921875 | 2024-06-25 | 1934697 | MRS M WARRENER | H - HV Fuse Down | EECL | Transformers Return to Service | D2002 | Wide Bay | 11kV | Transformers Return to Service | M0209 | M0052 | M9999 |  | J | Capital | MARYBOROUGH 3 | OT240019 | Technician: Jason rehren Comments | OT240019 | 202406
2024-06-30 |  | 2024-06-30 | TDDI | Transformer-Distribution | Closed |  |  | 2024-06-30 | 2024-06-01 | CHINCHILLA | EECL | NS | Network Site | XCGDH | 1914584 |  |  | 23/24 | 2024-12-30 | HV | 2024-06-01 |  | Internal Fault | Damaged | Tx, Tank Body | Outage | South | Distribution substation | 2024-06-30 11:18 | 12.7kV SWER Pole Dist Sub PC03696 - Blown Tx | 2024-06-30 | MILES: PADDYS CREEK RD | Distribution Event | Normal Event | 12.7kV SWER Pole Dist Sub PC03696 - Blown Tx chnfr01 Sending Asset Event to FFA FFA Order Created F-AE24SW10809-1-0 DfltHost Sending Asset Event to FFA Time On modified from 23:59 30-Jun to 16:21 30-Jun Sending Asset Event to FFA Sending Asset Event to FFA FFA Order Acknowledged F-AE24SW10809-1-0 chnfr01 Nick Wolski 0428776314 FFA Order En Route F-AE24SW10809-1-0 chnfr01 FFA Order On Site F-AE24SW10809-1-0 chnfr01 FFA Order F-AE24SW10809-1-0 Completed by technician Nick Wolski in crew chnfr01(0428776314) with code A-T-303 - Distribution substation Action Taken : blown tx changed Site Label : 2044761 Time On modified from 16:21 30-JUN to 16:26 30-JUN | Invalid | 24SW10809 | LOMANDRA | PC03696 | PC03696 |  | Equipment Failure or Malfunction | Completed | Unplanned Outage | Fine | NS2044761 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -26.62961387634280 | 150.127868652344 | 2024-06-30 | 1935620 | MRS P HOWE | U - Unknown / No Power | EECL | Transformers Return to Service | D2002 | South West | 12.7kV | Transformers Return to Service | M0209 | M0052 | M0070 |  | I | Capital | CHINCHILLA | OT240518 | Technician: Nick Wolski Comments | OT240518 | 202406
2024-06-30 |  | 2024-06-30 | TDDI | Transformer-Distribution | Closed |  |  | 2024-06-30 | 2024-06-01 | MACKAY | EECL | NS | Network Site | XLFPK | 1497294 |  |  | 23/24 | 2024-12-30 | HV | 2024-06-01 |  | Internal Fault | Broken | Tx, Tank Body | Outage | North | Distribution substation | 2024-06-30 12:01 | ETON 11kV Sawn Creek RC862558 ACR CB tripped. SCADA Interface automated outage. | 2024-06-30 | ETON, VICTORIA PLAINS, WALKERSTON | Distribution Event | Normal Event | entered from the SCADA Interface Sending Asset Event to FFA FFA Order Created F-AE24MK5436-1-0 DfltHost Lachlan Minster on MCKOC01 Sending Asset Event to FFA FFA Order Acknowledged F-AE24MK5436-1-0 mckoc01 Lachlan Minster 0437656382 FFA Order En Route F-AE24MK5436-1-0 mckoc01 Depot Co-ord Advised Sending Asset Event to FFA SEF Trip Reports of Pole Fire Caseys Rd Crews Disp Sending Asset Event to FFA Crew confirm Sub 3398 had 2 blown Hv Fuses and are Continuing with Patrol to confirm NO Other Faults Sending Asset Event to FFA Will attempt MRC when Patrol Completed Sending Asset Event to FFA Manual Reclose Checklist Sending Asset Event to FFA Patrol Completed No Other Faults Found Sending Asset Event to FFA Asset selection modified Sending Asset Event to FFA MRC Successful but Sub 3398 has Failed Requires Replacing Sending Asset Event to FFA FFA Order En Route F-AE24MK5436-1-0 mckoc01 FFA Order On Site F-AE24MK5436-1-0 mckoc01 Time On modified from 23:59 30-Jun to 16:47 30-Jun Sending Asset Event to FFA Sending Asset Event to FFA FFA Order F-AE24MK5436-1-0 Completed by technician Lachlan Minster in crew mckoc01(0437656382) with code A-T-303 - Distribution substation Action Taken : TX3398 has internal fault dropping both HV fuses, switched and access to replace 10kva pole TX, replaced service line to house and tested. supply restored Site Label : 2017990 auto-completed | Invalid | 24MK5436 | 589352-PEAK DOWNS HWY, VICTORIA PLAINS Q | Sawn Creek | RC862558 | Sawn Creek Recloser | Unknown | Completed | Unplanned Outage | Wet / Rain | NS2017990 | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | -21.21130561828610 | 149.012893676758 | 2024-06-30 | 1935627 | U Unknown |  | EECL | Forced Regulated | CEFR | Mackay | 11kV | U Unknown | M0209 | M0001 | M0070 |  | J | Operational | MACKAY 2 | OT240520 | Technician: Lachlan Minster Comments | OT240520 | 202406

## Substation and Instrument Tx.
Substation and Instrument Transformers
FeederStat/OMS Number | Work Order | Date | Region | Substation ID | Asset ID | Plant Number | Asset Name | Object Failure | RIN Category -AER
| 9670832 | 2023-10-06 | NQ | HEPASS | TR2 | TC93214479 | Hermit Park T2 | TC (OLTC) | Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA
23NQ13714 | OT204579 | 2023-11-21 | NQ | NESMSS | TR1 | TC93209195 | Neil Smith T1 | TC (OLTC) | Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA
24FN0806 | OT219943 | 2024-01-22 | FN | CRAISS | TR1 | TR92896167 | Craiglie 132/22KV ZONE SUB | Cable Box | Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA
| 10025189 | 2024-04-22 | MK | GLELSS | TR5 | TR93871035 | Glenella 66/33/11KV Substation | TC (OLTC) | Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA
| OT194602 | 2023-09-01 |  | CLERSS |  | CT92016837 | Clermont TR2 CT - C phase | CT | Current Transformer
| OT237618 | 2024-06-01 | CA | MEMOSS |  | VT94430108 | Memooloo PVT TR3 (Station Service) - Phase C | VT | Voltage Transformer