## Numbers
Row Labels | Count of CB2 | Count of ACR2 | Count of RMU2 | Count of Switches
11 | 28 | 4 | 5 | 5
22 | 8 | 4 | 2
33 | 8 | 2
66 | 13 |  |  | 2
132 | 2
220 | 0
Grand Total | 59 | 10 | 7 | 7 |  | 83
0
RIN Data
< = 11 kV ; FUSE
[5 empty] | < = 11 kV ; Switch | 10
[5 empty] | < = 11 kV ; Circuit Breaker | 32
[5 empty] | > 11 kV & < = 22 kV ; Switch | 2
[5 empty] | > 11 kV & < = 22 kV ; Circuit Breaker | 12
[5 empty] | > 22 kV & < = 33 kV ; Switch | 0
[5 empty] | > 22 kV & < = 33 kV ; Circuit Breaker | 10
[5 empty] | > 33 kV & < = 66 kV ; Switch | 2
[5 empty] | > 33 kV & < = 66 kV ; Circuit Breaker | 13
[5 empty] | > 66 kV & < = 132 kV ; Switch | 0
[5 empty] | > 66 kV & < = 132 kV ; Circuit Breaker | 2
[5 empty] | > 132 kV ; Switch | 0
[5 empty] | > 132 kV ; Circuit Breaker | 0

## CB Failures
Column1 | REQUEST_ID | RAISED_DATE | FY | WORK_ORDER | WO_DESC | WO_JOB_CODEX1_1 | ORIG_PRIORITY | ORIG_PRIORITY_DESCRIPTION | WO_STATUS_M | WO_STATUS_M_DESCRIPTION | WO_STATUS_U | WO_STATUS_U_DESCRIPTION | CLOSED_DT | CLOSED_COMMIT_DT | CLOSED_TIME | COMPLETED_CODE | COMPLETED_CODE_DESCRIPTION | CLOSED_STATUS | CLOSED_STATUS_DESCRIPTION | SHUTDOWN_EQUIP | SHUTDOWN_TYPE | SHUTDOWN_TYPE_DESCRIPTION | PARENT_WO | PARENT_WO_DESC | MAINT_TYPE | MAINT_TYPE_DESCRIPTION | MSSS_OBJECT_FAILURE_DESCRIPTION | MSSS_DAMAGE_APPARENT_CAUSE_DESCRIPTION | MSSS_CAUSE_DESCRIPTION | CONSEQUENCE_DESCRIPTION | VOLTAGE_DESCRIPTION | PLAN_PRIORITY | PLAN_PRIORITY_DESCRIPTION | CUST_NO | FAILURE_PART | EQUIP_NO | COMP_CODE | COMP_CODE_DESCRIPTION | COMP_MOD_CODE | COMP_MOD_CODE_DESCRIPTION | REQUEST_ID_2 | SHORT_DESC_1 | SHORT_DESC_2 | LOCATION | ITEM_NAME_1 | ITEM_NAME_2 | EQUIP_STATUS | EQUIP_LOCATION | PLANT_NO | EQUIP_CLASS | EQUIP_CLASS_DESCRIPTION | WORK_ORDER_EXTENDED_DESCRIPTION | REQUEST_ID_3 | WORK_REQUEST_EXTENDED_DESCRIPTION | NAMP_LINE | NAMP_LINE_DESCRIPTION | Voltage | OT | CB | CB FAULT | ACR | Rec Fault | RMU | RMUFault | Switch | Switch Fault | Isol | Isol Fault | CB2 | ACR2 | RMU2 | Switches | Switches Comment2 | RMU Comm2
6310 | 000001934346 | 2024-06-23 | 2024 | OT239846 | MERI CB FB04Q00 Did Not Operate | 1 | 0 | P0 - Forced | A | Authorised | VG | (1) Investigate |  |  | 0.99931 | [9 empty] | MF | Maintenance Forced | [5 empty] | 0 | P0 - Forced |  |  | 200154 |  |  |  |  | 000001934346 | NURGT System Condition - 24NQ10108 |  |  | FB04Q00 11KV MERI-04 FDR CB | MERISS MERI-04 FEEDER CB SLOT | IS | XLHBB | MERISS-FB04-Q00 | ST | Slot - GIS | .HEADING 28/06/2024 - MMorris - Waiting on direction from Protection Group - moved to Sept 24 \r23-Jun-24 11:36 Matt Mansfield Out of Service Merinda No4 Fdr CB FB04Q00 did not operate for wires down at pole 5201711. (Grounded conductor was on de-energised side of break) During reverse switching when Recloser FB04Q00 was closed the Maintenance Required alarm asserted. Recloser was\ropened again & alarm cleared approx 15 minutes later. Load transfer has been left in place. Investigation into maintenance alarm required. Also NOEN have requested the events from the recloser be extracted to assist with the protection report into the operation of the recloser during\rthe fault 23-Jun-24 11:50 Matt Mansfield Update Reverse load transfer written as part of F-4032-s | 000001934346 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
39633 | 000001910347 | 2024-02-23 | 2024 | OT226703 | CALL TX CP-T2 11kV CB CP-S102 | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-24 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Incorrect operation/activity | Technical Assessment | 11kV | 0 | P0 - Forced |  |  | 282801 |  |  |  |  | 000001910347 | URGNT System Condition - 24CA3681 |  |  | CP-T2 66/11KV TRANSF 2 | CALLSS TRANSF 2 SLOT | IS | XLFPG | CALLSS-TX02-T01 | ST | Slot - GIS |  | 000001910347 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
49985 | 000001926968 | 2024-05-17 | 2024 | OT236264 | WEMA FB09Q00 CB Fail on OC trip | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-21 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> | <null> | 11kV | 0 | P0 - Forced |  |  | 224816 |  |  |  |  | 000001926968 | URGNT System Condition - 24MK4393 |  |  | FB09Q00 11KV ROCKLEIGH FDR CB | WEMASS ROCKLEIGH FEEDER CB SLOT | IS | XLFPK | WEMASS-FB09-Q00 | ST | Slot - GIS |  | 000001926968 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
46387 | 000001921084 | 2024-04-15 | 2024 | OT233185 | PIRR CB3710 pitch leaking in spouts | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-10 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Leaking | Leakage |  | 11kV | 0 | P0 - Forced |  |  | 187161 |  |  |  |  | 000001921084 | NURGT System Condition - 24SW7634 |  |  | CB3710 11KV PIRRINUAN FDR CB | PIRRSS PIRRINUAN FEEDER CB SLOT | IS | XLGDD | PIRRSS-FB04-Q00 | ST | Slot - GIS |  | 000001921084 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
39458 | 000001910233 | 2024-02-22 | 2024 | OT226651 | CALL T1 11kV CB CP-S106 Arc sounds cubi | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-09 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Inadequate coating | Repair | 11kV | 0 | P0 - Forced |  |  | 282781 |  |  |  |  | 000001910233 | URGNT System Condition - 24CA3656 |  |  | CP-T1 66/11KV TRANSF 1 | CALLSS TRANSF 1 SLOT | IS | XLFPG | CALLSS-TX01-T01 | ST | Slot - GIS |  | 000001910233 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
12429 | 000001912313 | 2024-03-03 | 2024 | OT227865 | STUA_Unable to Close via Scada or locall | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-03-06 |  | 11:59:00 pm | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> | <null> | 11kV | 0 | P0 - Forced |  |  | 000000164465 |  |  |  |  | 000001912313 | URGNT System Condition - 24NQ5650 |  |  | J252 11KV CLUDEN ST FDR CB | STUASS CLUDEN ST FEEDER CB SLOT | IS | XLHBT | STUASS-FB15-Q00 | ST | Slot - GIS |  | 000001912313 |  |  |  | 11 | 1 | 4 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 4
9084 | 000001906977 | 2024-02-08 | 2024 | OT224726 | EAAY_Cap2 CB V252 won't close. left OOS | 1 | 0 | P0 - Forced | C | Closed | CN | In Construction | 2024-02-16 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Circuit Breaker | Deteriorated | Intermittent Fault |  | 11kV | 0 | P0 - Forced |  |  | 164 |  |  |  |  | 1906977 | NURGT System Condition - 24NQ4424 |  |  | EAST AYR SPILLER ST 66/11KV SUB (EAAY) | EAAYSS 66/11KV ZONE SUB | IS | XLHBH | EAAYSS | SS | Substation Site | .HEADING System Condition - Non Urgent Cap2 CB V252 won't close. left OOS Cap2 CB V252 won't close. left OOS \r14/02/2024 CFielder: Followed up M Green and M Manuel for more info on the actual issue with the CB so a defect and plan of attack can be raised and programmed. There is also issues with two spare CB's on site that need attention to make one good system spare. | 000001906977 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
6284 | 000001902420 | 2024-01-27 | 2024 | OT221297 | Switchgear RTS Friendlys CB | 1 |  |  | C | Closed |  |  | 2024-02-12 |  | 0.97917 | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Damaged | Unknown |  | 11kV | 0 | P0 - Forced |  |  | 6553235 | SW | Switch | OC | Outage Codes | 1902420 | BUNDABERG FRIENDLY SOCIETY MED | P - Phase Down (LV) |  | 86052 | 23 BINGERA ST, BUNDABERG WEST QLD 4670 | IS | XLFBB | NS86052 | NS | Network Site | .HEADING Technician: Dennis Dennien Comments rmu circuit breaker will not close live. requires incoming supply to be de\renergised before CB will stay closed , then re energise the incoming supply. settings in CB need checking/rectifying, or CB is faulty \rCompleted under assett event 24WB2297, RTS created for RMU CB under WR 1902440 JS | 000001902420 |  |  |  | 11 | 1 | 4 | 4 | 0 |  | 4 | 4 | 0 |  | 0 |  | 4 |  | 4 |  |  | 0
6372 | 000001902803 | 2024-01-28 | 2024 | OT221651 | FD-1206_CB J252 possibly miss latching | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-01-31 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 36766 |  |  |  |  | 1902803 | URGNT System Condition - 24NQ3322 |  |  | CLUDEN | STOA ST10 | IS | XLHBT | FD-1206 | FD | Feeder | .HEADING System Condition - URGENT CB J252 possibly miss latching, please investigate CB J252 possibly miss latching, please investigate \r28-Jan-24 03:35 Gary Adams Out of Service CB J252 possibly miss latching, please investigate 28-Jan-24 03:43 Gary Adams Update 28-Jan-24 06:02 Gary Adams Restored Time On modified from 23:59 04-Feb to 04:55 28-Jan\r28-Jan-24 06:02 Gary Adams Completed | 000001902803 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
5508 | 000001902396 | 2024-01-26 | 2024 | OT221268 | EAAY_No.10 Fdr CB J252 Spring Charge Alm | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-01-31 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 7089303 |  |  |  |  | 1902396 | URGNT System Condition - 24NQ3153 |  |  | EASTAYR NO.10 | EAAY 14019 | IS | XLHBH | FD-4019 | FD | Feeder | .HEADING System Condition - URGENT East Ayr No.10 Fdr CB J252 Spring Charge alarm On. . East Ayr No.10 Fdr CB J252\rSpring Charge alarm On. . 26-Jan-24 21:37 Callan Farnill Update Fdr CB to be opened once load transfered | 000001902396 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
3107 | 000001899145 | 2024-01-17 | 2024 | OT218707 | GLFS GF-S105 spring charg mot bear fail | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-01-30 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Fatigue | Repair | 11kV | 0 | P0 - Forced |  |  | 290420 |  |  |  |  | 1899145 | URGNT System Condition - 24CA0967 |  |  | GF-S105 11KV WEST GLADSTONE FDR CB | GLFSSS WEST GLADSTONE FDR CB SLOT | IS | XLFPG | GLFSSS-FB59-Q00 | ST | Slot - GIS | .HEADING 17-Jan-24 13:34 Dale Graff Out of Service West Gladstone Feeder 11kV CB GF-S105 spring charge motor bearing has failed | 000001899145 |  |  |  | 11 | 1 | 4 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
1725 | 000001896911 | 2024-01-08 | 2024 | OT217151 | TORQ CB D452 failed to to close from OCC | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2024-01-08 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Circuit Breaker | Loose Connection | Loose Connection | Repair | 11kV | 0 | P0 - Forced |  |  | 164709 |  |  |  |  | 1896911 | URGNT System Condition - 24WB0317 |  |  | D452 11KV SCARNESS HEIGHTS FDR CB | TORQSS SCARNESS HEIGHTS FEEDER CB SLOT | IS | XLFBH | TORQSS-FB04-Q00 | ST | Slot - GIS | .HEADING 08-Jan-24 14:23 Scott Boswood System Abnormal Scarness Heights Feeder 11kV CB D452 failed to to close from OCC(S). 08-Jan-24 14:24 Scott Boswood Restored\rBruce Houguet attended site and found a loose connection. CB able to be closed/opened from OCC(S). Time On modified from 23:59 15-Jan to 14:24 08-Jan 08-Jan-24 14:24 Scott Boswood Completed | 000001896911 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
11519 | 000001892430 | 2023-12-26 | 2024 | OT213166 | PURR CB 4489 - unable to close | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2023-12-27 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Wiring and Electrical Componen | Out of Specification | Corrosion |  | 11kV | 0 | P0 - Forced |  |  | 190467 |  |  |  |  | 000001892430 | URGNT System Condition - 23SW23452 |  |  | CB4489 11KV ROSSVALE FDR CB | PURRSS ROSSVALE FEEDER CB SLOT | IS | XLGDT | PURRSS-FB55-Q00 | ST | Slot - GIS | .HEADING 26-Dec-23 15:03 Steven Zammit Out of Service Rossvale Feeder 11kV CB 4489 - unable to close 26-Dec-23 15:04 Steven Zammit Update 26-Dec-23 15:17 Steven Zammit Update\r26-Dec-23 17:16 Brendan Atfield Restored Dirty Aux contact for the close coil. Time On modified from 23:59 02-Jan to 17:16 26-Dec 26-Dec-23 17:16 Brendan Atfield Completed | 000001892430 |  |  |  | 11 | 1 | 5 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 4
11163 | 000001891774 | 2023-12-25 | 2024 | OT212507 | SCR0 SOKO CB C452 exploded-fault finding | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-12-27 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Defective component |  | 11kV | 0 | P0 - Forced |  |  | 163173 |  |  |  |  | 000001891774 | SCR0 RTS R0 - High Priority 23WB16325 |  |  | C452 11KV SHARON FDR CB | SOKOSS SHARON FEEDER CB SLOT | IS | XLFBB | SOKOSS-FB52-Q00 | ST | Slot - GIS | .HEADING 25-Dec-23 00:25 David Houghton System Abnormal Sharon Fdr 11kV CB C452 has exploded during fault finding | 000001891774 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
4932 | 000001883497 | 2023-11-29 | 2024 | OT205944 | ALST Cap1 CB Continously tying to close | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2023-12-12 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Circuit Breaker | Repairable Degradation | Fatigue |  | 11kV | 0 | P0 - Forced |  |  | 5290144 |  |  |  |  | 000001883497 | SCR0 RTS R0 - 23MK9446 |  |  | FB0352 CAPACITOR 1 11KV CB | ALSTSS CAP 1 CB SLOT | IS | XLFPK | ALSTSS-MX01-Q00 | ST | Slot - GIS | .HEADING 29-Nov-23 09:15 Callan Farnill System Abnormal 11kV Cap No.1 CB - Continuously trying to close - Goes for a close then goes indeterminant. Seems to be coming in when not require (not enough VARS)\r29-Nov-23 09:22 Callan Farnill Update Could be miss latching, Spoke to test section they will investigate first as to if the relay is working correctly, then pass onto Subs if there is a latching issue 29-Nov-23 09:23 Callan Farnill Update | 000001883497 |  |  |  | 11 | 1 | 1 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 4
3665 | 000001881661 | 2023-11-22 | 2024 | OT204744 | NESM CB A552 burnt out trip coil | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-11-29 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 185207 |  |  |  |  | 000001881661 | URGNT System Condition - 23NQ13761 |  |  | 11kV TRANSF 1 CB | NESM A552 SLOT | IS | XLHBT | NESMSS-TX01-Q00 | ST | Slot - GIS | .HEADING 11kV TRANSF 1 CB A552 at Neil Smith has a burnt out trip coil and needs to be replaced. Happened during unplanned event 23NQ13714 | 000001881661 |  |  |  | 11 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
2640 | 000001880470 | 2023-11-16 | 2024 | OT203917 | TUAN D452 CB not closing | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-11-23 |  | 0.91667 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Circuit Breaker | No Damage | Unknown | Repair | 11kV | 0 | P0 - Forced |  |  | 23788 |  |  |  |  | 000001880470 | TFUO Transient Fault of Unknown 23WB1464 |  |  | MBOROUGH - MBOROUGH CITY T/TUAN | MBOROUGH - MBOROUGH CITY 66KV T/TUAN | IS | XLFBA | FD-6219 | FD | Feeder | .HEADING Transient Fault of Unknown Origin Transient Fault of Unknown Origin on MARYBOROUGH 66kV Mary City Fdr CB G352 entered from the SCADA Interface\r 16-Nov-23 20:25 SCADA Interface (Sth) New entered from the SCADA Interface 16-Nov-23 20:36 Samuel Elliott Re-Activate 16-Nov-23 20:37 Samuel Elliott Update\rTUAN Tuan Asset selection modified 16-Nov-23 20:39 Samuel Elliott Update Asset selection modified\rTime On modified from 20:23 16-Nov to 20:45 16-Nov 16-Nov-23 20:40 Samuel Elliott Update 66kV Fdr trip on current Diff, Line A/R. Tuan was then energised and once clearance was recieved via sawmill all power was restored.\r16-Nov-23 20:48 Samuel Elliott Update C452 CB will close remotely, crew being dispatched F-1224-r. Time On modified from 20:45 16-Nov to 22:00 16-Nov 16-Nov-23 20:53 Luke Roberts Update\r16-Nov-23 22:07 Darren Wieden Update Time On modified from 22:00 16-Nov to 23:59 16-Nov 16-Nov-23 22:07 Darren Wieden Update F-1224-r Switching Sheet Written\r17-Nov-23 00:08 Paul Jacobs Update . M.Jinks advises faulty close coil on CB C452. Switching in progress to transfer Poona fdr to MACI & use Poona CB in Sawmill cubicle. Time On modified from 23:59 16-Nov to 23:59 17-Nov\r17-Nov-23 01:42 Paul Jacobs Update 0118 - Sawmillk supply restored via Poona CB in Sawmill cubicle, Poona via Pocket Fdr (MACI). 23/11/23 - MJ Sawmill CB has been repaired and placed into\rservice in the Poona feeder bay. | 000001880470 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
2087 | 000001879627 | 2023-11-13 | 2024 | OT203414 | PROT_11kV CB A452 Intermitant & Alm Acti | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-11-20 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Defective component |  | 11kV | 0 | P0 - Forced |  |  | 145397 |  |  |  |  | 000001879627 | URGNT System Condition - 23WB14486 |  |  | A452 11KV PROSTON FDR CB | PROTSS PROSTON FEEDER CB SLOT | IS | XCFBR | PROTSS-FB52-Q00 | ST | Slot - GIS | .HEADING System Condition - URGENT Proston Feeder 11kV CB A452 showing indeterminant and main required alarm active \rProston Feeder 11kV CB A452 showing indeterminant and main required alarm active 13-Nov-23 19:36 Brodie Millan Update during switching it was found reclose A452 indicates\rcorrectly when open but not when closed. | 000001879627 |  |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
4193 | 1875927 | 2023-10-29 | 2024 | OT201090 | ROSO_11KV Bus CB RS-S107 will not close | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-11-15 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Not Working | Inadequate coating |  | 11kV | 0 | P0 - Forced |  |  | 4316 |  |  |  |  | 1875927 | URGNT System Condition - 23CA15044 |  |  | RSSS ROCKHAMPTON SOUTH 66/11KV SUB | ROSOSS 66/11KV ZONE SUB | IS | XLFPR | ROSOSS | SS | Substation Site | .HEADING System Condition - URGENT 11KV Bus CB RS-S107 will not close. Forced outage 23CA15043 F-28613-g for investigation and repair. 11KV Bus CB RS-S107 will not close. Forced outage 23CA15043\rF-28613-g for investigation and repair. | 000001875927 | System Condition - URGENT 11KV Bus CB RS-S107 will not close. Forced outage 23CA15043 F-28613-g for investigation and repair. 11KV Bus CB RS-S107 will not close. Forced outage 23CA15043 F-28613-g for investigation and repair. |  |  | 11 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
412 | 1870285 | 2023-10-03 | 2024 | OT197724 | AITK B252 Replace Bushing Dampener | 1 | 0 | P0 - Forced | C | Closed | CN | In Construction | 2023-10-30 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 6771704 |  |  |  |  | 1870285 | URGNT System Condition - 23NQ11939 |  |  | B252 11KV AV02 FDR CB | AITKSS AV02 FEEDER CB SLOT | IS | XLHBT | AITKSS-FB61-Q00 | ST | Slot - GIS | .HEADING B252 requires replacement bushing on the close mechanism, parts will be ordered today and arrive in approx 1 month's time. CB can be used but will require local attence to reset mechanism to close. F.Nobile and P.Scuito have further info. | 000001870285 | .HEADING System Condition - URGENT B252 requires replacement bushing on the close mechanism, parts will be ordered today and arrive in approx 1 month's time. CB can be used but will require local attence to\rreset mechanism to close. F.Nobile and P.Scuito have further info. B252 requires replacement bushing on the close mechanism, parts will be ordered today and arrive in approx 1 month's time. CB can be used but will require local attence to\rreset mechanism to close. F.Nobile and P.Scuito have further info. |  |  | 11 | 1 | 12 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
3440 | 1874881 | 2023-10-25 | 2024 | OT200358 | MACI CB C452 damaged | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-10-25 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Defective component |  | 11kV | 0 | P0 - Forced |  |  | 157001 |  |  |  |  | 1874881 | URGNT System Condition - 23WB13873 |  |  | C452 11KV TINANA CREEK FDR CB | MACISS TINANA CREEK FEEDER CB SLOT | IS | XLFBA | MACISS-FB55-Q00 | ST | Slot - GIS | .HEADING w/o created to fix N.A | 000001874881 | .HEADING System Condition - URGENT Tinana Creek Feeder 11kV CB C452 damaged Tinana Creek Feeder 11kV CB C452 damaged |  |  | 11 | 1 | 9 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
580 | 1870604 | 2023-10-04 | 2024 | OT197878 | DAGL 11kV CB H252 requires maintenance | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2023-10-19 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 161714 |  |  |  |  | 1870604 | URGNT System Condition -23NQ11966 |  |  | H252 11KV DG08 FDR CB | DAGLSS DG08 FEEDER CB SLOT | IS | XLHBT | DAGLSS-FB56-Q00 | ST | Slot - GIS | .HEADING 04-Oct-23 16:44 Leon Metcalfe System Abnormal 11kV CB H252 requires maintenance. During switching on S- 4856-t, CB would not close by SCADA or locally. Kyle McCarthy adv exercised mechanism but requires further\rmaintenance. 04-Oct-23 16:50 Leon Metcalfe Update Asset selection reset 04-Oct-23 16:50 Leon Metcalfe Update\rAsset selection modified 04-Oct-23 17:35 Leon Metcalfe Update 05-Oct-23 09:28 Ian Farnill Restored work has been completed returned back into service Time On modified from 23:59 11-Oct to 09:28 05-Oct\r05-Oct-23 09:28 Ian Farnill Completed | 000001870604 | .HEADING System Condition - URGENT 11kV CB H252 requires maintenance. During switching on S-4856-t, CB would not close by SCADA or locally. 11kV CB H252 requires maintenance. During switching on\rS-4856-t, CB would not close by SCADA or locally. Kyle McCarthy adv exercised mechanism but requires further maintenance. |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
865 | 1871115 | 2023-10-06 | 2024 | OT198156 | OAKE FB0852 Bus Sect 1-2 CB Spring disch | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-10-11 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Defective component |  | 11kV | 0 | P0 - Forced |  |  | 248825 |  |  |  |  | 1871115 | URGNT System Condition - 23SW18050 |  |  | FB0852 11KV BUS TIE CB | OAKESS 11KV BUS CB SLOT | IS | XLGDT | OAKESS-FB08-Q00 | ST | Slot - GIS | .HEADING System Condition - URGENT 11kV Bus Tie CB FB0852 Bus Sect 1-2 CB Spring discharged. Will need to be investigated and reset. \r11kV Bus Tie CB FB0852 Bus Sect 1-2 CB Spring discharged. Will need to be investigated and reset. S Garske advised the housing for the spring charge has shattered and is unserviceable. FB0852 left OOS. NOE's\radvised. | 000001871115 | .HEADING System Condition - URGENT 11kV Bus Tie CB FB0852 Bus Sect 1-2 CB Spring discharged. Will need to be investigated and reset. \r11kV Bus Tie CB FB0852 Bus Sect 1-2 CB Spring discharged. Will need to be investigated and reset. |  |  | 11 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
68840 | 000001861279 | 2023-08-17 | 2024 | OT192578 | CANN FB0352 bent location lock slide pin | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-12 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Corrosion |  | 11kV | 0 | P0 - Forced |  |  | 241885 |  |  |  |  | 000001861279 | NURGT System Condition - 23MK6763 |  |  | FB0352 11KV TFR1 CB | CANNSS TRANSF 1 CB SLOT | IS | XLHBP | CANNSS-TX01-Q10 | ST | Slot - GIS | .HEADING Luke Read 0436 069 696 reported FB0352 is hard to rack up and breaker location lock slide pin is bent. Please investigate/repair. \r----------------------------------------------------------- 12/9/23 AMCD Crew investigated and found worm drive on cb needed to be lubricated. All operating correctly. | 000001861279 | .HEADING System Condition - Non Urgent Luke Read 0436 069 696 reported FB0352 is hard to rack up and breaker location lock slide pin is bent. Please investigate/repair.\rLuke Read 0436 069 696 reported FB0352 is difficult to rack up and breaker location lock slide pin is bent. Please investigate/repair. |  |  | 11 | 1 | 4 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
69495 | 000001861962 | 2023-08-21 | 2024 | OT192998 | PURR CB 4488 wont close locally/remotely | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-01 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Defective component |  | 11kV | 0 | P0 - Forced |  |  | 213802 |  |  |  |  | 000001861962 | URGNT System Condition - 23SW16297 |  |  | CB4488 11KV TRANSF 1 CB | PURRSS TRANSF 1 CB SLOT | IS | XLGDT | PURRSS-TX01-Q00 | ST | Slot - GIS | .HEADING System Condition - URGENT CB 4488 will not close locally or remotely. Planned Switching will run tomorrow to investigate via S-9063-q 23SW16220.\r CB 4488 will not close locally or remotely. Planned Switching will run tomorrow to investigate via S-9063-q 23SW16220. | 000001861962 | .HEADING System Condition - URGENT CB 4488 will not close locally or remotely. Planned Switching will run tomorrow to investigate via S-9063-q 23SW16220.\r CB 4488 will not close locally or remotely. Planned Switching will run tomorrow to investigate via S-9063-q 23SW16220. |  |  | 11 | 1 | 1 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 4
66696 | 000001856875 | 2023-07-25 | 2024 | OT190213 | ROSO Tx1 CB RS-S104 Bus Shuts wont close | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-29 |  | 0.375 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Incorrect operation/activity |  | 11kV | 0 | P0 - Forced |  |  | 307407 |  |  |  |  | 000001856875 | URGNT System Condition -23CA11433 |  |  | RS-S104 11KV TRANSF 1 CB | ROSOSS TRANSF 1 CB SLOT | IS | XLFPR | ROSOSS-TX51-Q10 | ST | Slot - GIS | .HEADING System Condition - URGENT 11KV TRANSF 1 CB RS-S104 - Bus Shutters will Not close. Please Investigate 11KV TRANSF 1 CB RS-S104 - Bus Shutters will Not close.\rPlease Investigate | 000001856875 | System Condition - URGENT 11KV TRANSF 1 CB RS-S104 - Bus Shutters will Not close. Please Investigate 11KV TRANSF 1 CB RS-S104 - Bus Shutters will Not close. Please Investigate |  |  | 11 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
105520 | 000001856429 | 2023-07-21 | 2024 | OT189943 | FREN FV-T3 11kV CB FV-S110 fail to close | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-07 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 289576 |  |  |  |  | 000001856429 | URGNT System Condition - 23CA11353 |  |  | FV-S110 11KV NORMAN RD FDR CB | FRENSS NORMAN RD FEEDER CB SLOT | IS | XLFPR | FRENSS-FB10-Q00 | ST | Slot - GIS | .HEADING System Condition - URGENT Norman Road Feeder / Transformer FV-T3 11kV CB FV-S110 failed to close due to fault with closing contactor. Norman Road Feeder / Transformer FV-T3 11kV CB FV-S110\rfailed to close due to fault with closing contactor. Crew attended site and found sticky componenets on contactor. repairs made and CB returned to service Time Off modified from 21:38 21-Jul to 19:30 21-Jul\rTime On modified from 23:59 28-Jul to 22:02 21-Jul | 000001856429 | System Condition - URGENT Norman Road Feeder / Transformer FV-T3 11kV CB FV-S110 failed to close due to fault with closing contactor. Norman Road Feeder / Transformer FV-T3 11kV CB FV-S110 failed to close due to fault with closing contactor. |  |  | 11 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
70359 | 000001856353 | 2023-07-21 | 2024 | OT189891 | WETO TX 3 11kV CB3982. CB will not close | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-07-28 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Defective component |  | 11kV | 0 | P0 - Forced |  |  | 204203 |  |  |  |  | 000001856353 | URGNT System Condition - 23SW9744 |  |  | CB3982 11KV TRANSF 3 CB | WETOSS TRANSF 3 CB SLOT | IS | XLGDT | WETOSS-TX55-Q10 | ST | Slot - GIS | .HEADING System Condition - URGENT Transformer No.3 11kV CB3982. CB will not close. Operating mechanism has a broken arm, requires rebuild. Transformer No.3 11kV CB3982. CB will not close. Operating\rmechanism has a broken arm, requires rebuild. | 000001856353 | System Condition - URGENT Transformer No.3 11kV CB3982. CB will not close. Operating mechanism has a broken arm, requires rebuild. Transformer No.3 11kV CB3982. CB will not close. Operating mechanism has a broken arm, requires rebuild. |  |  | 11 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
1904 | 000001927300 | 2024-05-19 | 2024 | OT236441 | ATHE 2/RMU 2 FDR CB Spring Not Charging | 1 | 0 | P0 - Forced | C | Closed | CN | In Construction | 2024-06-21 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Incorrect operation/activity |  | 22kV | 0 | P0 - Forced |  |  | 133547 |  |  |  |  | 000001927300 | URGNT System Condition - 24FN6466 |  |  | FA12Q00 22KV ATHERTON 2/RMU 2 FDR CB | ATHESS ATHERTON 2 FEEDER CB SLOT | IS | XLTNA | ATHESS-FA12-Q00 | ST | Slot - GIS | .HEADING 21.05.2024 SS202376 : System Condition - URGENT\r22kV CB Atherton No.2 - FA12Q00 - spring does not charge 22/05/24 jsmith - outage entered for 29th May, Rang OCC to extend RBD to 31/05 \r24/05/24 jsmith - contacted by controll, unable to write sheets in time, extended to mid/end june | 000001927300 |  |  |  | 22 | 1 | 5 | 4 | 0 |  | 1 | 4 | 0 |  | 0 |  | 4 |  | 4 |  |  | 0
2710 | 000001928561 | 2024-05-26 | 2024 | OT237084 | BARC Tx BB-T6 22kV CB BB-S207 Serv Mech | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-06-05 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Contamination | Pollution |  | 22kV | 0 | P0 - Forced |  |  | 267787 |  |  |  |  | 000001928561 | URGNT System Condition - 24CA7410 |  |  | BB-S207 22KV TRANSF 6 CB | BARCSS TRANSF 6 CB SLOT | IS | XCPNB | BARCSS-TX06-Q00 | ST | Slot - GIS | .HEADING System Condition - URGENT 66/22kV Transformer BB-T6 22kV CB BB-S207, During 23CA18117 (S-8206-r), Trent advised the CB was difficult to wind into position due to the worm drive being covered in\rold grease. Crew to service mechanism. 66/22kV Transformer BB-T6 22kV CB BB-S207, During 23CA18117 (S-8206-r), Trent advised the CB was difficult to wind into position due to the worm drive being covered in old grease. Crew to service mechanism. | 000001928561 |  |  |  | 22 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
47200 | 000001922419 | 2024-04-22 | 2024 | OT233909 | MOSS TX1 22kV Fail To Close | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-07 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Pollution |  | 22kV | 0 | P0 - Forced |  |  | 71 |  |  |  |  | 000001922419 | URGNT System Condition - 24FN5533 |  |  | MOSSMAN 66/22KV SUB (MOSSMAN) | MOSSSS 66/22KV ZONE SUB | AR | XCTNS | MOSSSS | SS | Substation Site |  | 000001922419 |  |  |  | 22 | 1 | 4 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
17920 | 000001920870 | 2024-04-12 | 2024 | OT233010 | SCR0 RTS CB RL-S203 Work Clear to Off | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-04-30 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Comms | 0 | P0 - Forced |  |  | 306513 |  |  |  |  | 1920870 | SCR0 RTS R0 - High Priority 24CA5623 |  |  | RL-S203 22KV BAJOOL FDR CB | RAGLSS BAJOOL FEEDER CB SLOT | IS | XLFPR | RAGLSS-FA51-Q00 | ST | Slot - GIS |  | 000001920870 |  |  |  | 22 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
10477 | 000001909112 | 2024-02-17 | 2024 | OT226007 | GEOR_T3 22kV CB wont close_mislatching | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-02-28 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Pollution |  | 22kV | 0 | P0 - Forced |  |  | 78 |  |  |  |  | 1909112 | URGNT System Condition - 24FN2969 |  |  | GEORGETOWN 132/66/22/6.6KV SUB (GEOR) | GEORSS 132/66/22/6.6KV ZONE SUB | AR | XCTNG | GEORSS | SS | Substation Site | .HEADING System Condition - URGENT T3 22kV CB wont close, appears to be mislatching T3 22kV CB wont close, appears to be mislatching \rcrews attended site, and rectified. attendees d.sweeper close spring dampner stricted by old grease | 000001909112 |  |  |  | 22 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
5580 | 000001901950 | 2024-01-26 | 2024 | OT220816 | PAND EFM CB PD-S207 not latch after clos | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2024-02-01 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Suspect Operation | Incorrect operation/activity |  | 22kV | 0 | P0 - Forced |  |  | 302413 |  |  |  |  | 1901950 | EFM Equip Failure or Malfunct 24CA1968 |  |  | PD-S207 22KV GLENDALE ROAD CB | PANDSS GLENDALE ROAD FEEDER CB SLOT | IS | XLFPR | PANDSS-FA07-Q00 | ST | Slot - GIS | .HEADING 25-Jan-24 23:56 David Houghton To be dispatched Glendale Road Feeder 22kV CB PD-S207 not latching after close operation 26-Jan-24 05:17 David Houghton Update\r26-Jan-24 06:18 Nathan Judd Update 26-Jan-24 06:19 Cameron Marshall Dispatched 26-Jan-24 06:19 David Houghton Work Commenced 26-Jan-24 07:22 Cameron Marshall Update Crew found CB truck interlock not aligned\r26-Jan-24 08:36 Cameron Marshall Update CB tripping, cause unknown. Sub Ops investigating, Dist crew dispatched to patrol feeder. 26-Jan-24 11:22 Cameron Marshall Update Crew confirmed Olive Rec. RC772061 has been operating this\rmorning - OC 1+, modem reset and now visible from NOS 26-Jan-24 11:38 Cameron Marshall Update Crew have found a tree near the lines, line patrol ongoing 26-Jan-24 14:38 Luke Richmond Update Asset selection modified\r26-Jan-24 14:53 Luke Richmond Update Asset selection modified 26-Jan-24 16:47 Luke Richmond Update Asset selection modified 26-Jan-24 16:47 Luke Richmond Update\rAsset selection modified 26-Jan-24 16:52 Luke Richmond Update Asset selection modified 26-Jan-24 16:56 Luke Richmond Update Asset selection modified\r26-Jan-24 17:08 Sam Herde Update 26-Jan-24 17:12 Steven Zammit Update Asset selection modified 26-Jan-24 17:13 Steven Zammit Update Olive Recloser tripped on load\r26-Jan-24 17:14 Steven Zammit Update Asset selection modified 26-Jan-24 17:15 Steven Zammit Update Asset selection modified 26-Jan-24 17:16 Steven Zammit Update\rGlendale CB replaced with Bus Coupler CB - CB closed OK 26-Jan-24 18:21 Luke Richmond Update Asset selection modified 26-Jan-24 18:22 Luke Richmond Update Asset selection modified\r26-Jan-24 18:22 Luke Richmond Update Asset selection modified 26-Jan-24 18:22 Luke Richmond Update Asset selection modified 26-Jan-24 18:22 Luke Richmond Update\rAsset selection modified 26-Jan-24 18:25 Luke Richmond Restored Glendale Road Feeder 22kV CB PD-S207 replaced by 22KV Bus Tie CB PD-S206. repairs to be done on CB before return to service. Syscon 24CA1994 created for repairs. OOS docs added\rin PoN to both CBs for information Time On modified from 23:59 26-Jan to 17:44 26-Jan 26-Jan-24 18:27 Luke Richmond Completed | 000001901950 |  |  |  | 22 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
10250 | 000001890755 | 2023-12-21 | 2024 | OT211547 | TIER FA03Q00 CB slow to op during storm | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-01-09 |  | 0.41667 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Inadequate coating |  | 22kV | 0 | P0 - Forced |  |  | 309386 |  |  |  |  | 000001890755 | NURGT System Condition -23CA18072 |  |  | FA03Q00 22KV CARAVAN PARK FDR CB | TIERSS CARAVAN PARK FEEDER CB SLOT | IS | XCFZD | TIERSS-FA03-Q00 | ST | Slot - GIS | .HEADING 21-Dec-23 21:44 Michael Parker System Abnormal 22KV CARAVAN PARK FDR CB FA03Q00 - CB slow to operate during storm causing CB Fail operation. Please investigate/ maintain.\r21-Dec-23 21:44 Michael Parker Update Asset selection reset 21-Dec-23 21:44 Michael Parker Update Asset selection modified 21-Dec-23 21:49 Michael Parker Update | 000001890755 |  |  |  | 22 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
64273 | 000001859925 | 2023-08-09 | 2024 | OT191846 | CANO FA07Q00 Will not close | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2023-08-11 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Incorrect operation/activity |  | 22kV | 0 | P0 - Forced |  |  | 5790122 |  |  |  |  | 000001859925 | URGNT System Condition - 23FN11375 |  |  | FA07Q00 22KV TRANSF 1 CB | CANOSS TRANSF 1 CB SLOT | IS | XLTNC | CANOSS-TX01-Q00 | ST | Slot - GIS | .HEADING 09-Aug-23 20:46 Callan Farnill System Abnormal 22kV Transformer No.1 FA07Q00 Will not close . 09-Aug-23 20:50 Callan Farnill Restored\rCrews took out a NAW on CB, Cleaned contacts and CB is working correctly. CB retuned to service Time Off modified from 20:40 09-Aug to 19:30 09-Aug Time On modified from 23:59 16-Aug to 20:47 09-Aug 09-Aug-23 20:52 Callan Farnill Completed | 000001859925 | System Condition - URGENT 22kV Transformer No.1 FA07Q00 Will not close . 22kV Transformer No.1 FA07Q00 Will not close . |  |  | 22 | 1 | 4 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
5450 | 000001933401 | 2024-06-18 | 2024 | OT239365 | MILE_Wandoan Feeder 33kV CB3715 slow | 1 | 0 | P0 - Forced | C | Closed |  |  | 2024-06-20 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Defective component |  | 33kV | 0 | P0 - Forced |  |  | 186754 |  |  |  |  | 000001933401 | URGNT System Condition - 24SW10325 |  |  | CB3715 33KV WANDOAN FDR CB | MILESS WANDOAN FEEDER CB SLOT | IS | XCGDH | MILESS-EB03-Q00 | ST | Slot - GIS | .HEADING System Condition - URGENT Wandoan Feeder 33kV CB3715 very slow to close Conor advises he can attend next week Wandoan Feeder 33kV CB3715 very slow to close | 000001933401 |  |  |  | 33 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
5066 | 000001932644 | 2024-06-14 | 2024 | OT238946 | MILE_Bus 1-3 33kV CB CB3714 Trips | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-06-14 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> | <null> | Not Applicable | 0 | P0 - Forced |  |  | 197212 |  |  |  |  | 000001932644 | URGNT System Condition - 24SW10152 |  |  | CB3714 33KV BUS 1-3 CB | MILESS 33KV BUS CB SLOT | IS | XCGDH | MILESS-EB07-Q | ST | Slot - GIS | .HEADING System Condition - URGENT Bus 1-3 33kV CB CB3714 Trips when closed remotely. Miles 11kv load shifted to CHIN via Rywung CB3726. When reversing load shift the CB3714 Tripped when Close command\rsent. Bus 1-3 33kV CB CB3714 Trips when closed remotely. Miles 11kv load shifted to CHIN via Rywung CB3726. When reversing load shift the CB3714 Tripped when Close command sent. | 000001932644 |  |  |  | 33 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
1977 | 000001927334 | 2024-05-20 | 2024 | OT236473 | MILE_CB3715 Delay when Close Command Iss | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-06-03 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Wiring and Electrical Componen | Out of Specification | Incorrect operation/activity |  | 33kV | 0 | P0 - Forced |  |  | 7685 |  |  |  |  | 000001927334 | NURGT System Condition - 24SW9035 |  |  | MILES 33/11KV SUB (MC008) | MILESS 33/11KV ZONE SUB | IS | XCGDH | MILESS | SS | Substation Site | .HEADING Investigation was completed under 24SW8286 (29/05/2024). Crew could not find fault (even after simulating auto reclose). EFS aware. SysCon Closed\r Jason Zimmerle 03/06/2024 ----------------------------------------------------------- System Condition - Non Urgent\rCB3715 had an approx 15-20sec delay between when a close command from SCADA was issued to when the CB closed, ie, A crew on site verified that they heard the close command received at the CB (clicking noise like a relay operating) then the approx 15-20sec delay & then CB closed.\rCB3715 had an approx 15-20sec delay between when a close command from SCADA was issued to when the CB closed, ie, A crew on site verified that they heard the close command received at the CB (clicking noise like a relay operating) then the approx 15-20sec delay & then CB closed. | 000001927334 |  |  |  | 33 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
29148 | 000001895508 | 2024-01-02 | 2024 | OT216046 | NOCL Cloncurry SWER ACR trip Fdr CB B252 | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-29 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | OHEW | 0 | P0 - Forced |  |  | 6402688 |  |  |  |  | 000001895508 | URGNT System Condition - 24NQ0126 |  |  | CLS262 CLONCURRY SWER ACR | CLS262-FLINDERS HWY, CLONCURRY QLD 4824 | IS | XCHBL | RC-492164 | NT | Network Slot |  | 000001895508 |  |  |  | 33 | 1 | 1 | 4 | 1 | 4 | 0 |  | 0 |  | 0 |  | 4 | 0
75383 | 000001852575 | 2023-07-02 | 2024 | OT187844 | JUCR J652 failed to close via SCADA | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-01 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | ACR, Body | Suspect Operation | Defective component |  | 33kV | 0 | P0 - Forced |  |  | 160577 |  |  |  |  | 000001852575 | URGNT System Condition - 23NQ7014 |  |  | J652 19.1KV JC10 CB | JUCRSS JC10 FEEDER CB SLOT | IS | XCHBJ | JUCRSS-EB56-Q00 | ST | Slot - GIS | .HEADING Julia Creek No.10 / Nelia Feeder 19.1kV CB J652 failed to close via SCADA or Local control onsite after O/C trip on SWER Feeder. Crews investigated with Test section and Mick O'Keeffe and\rfound recloser not opening fully, Crews operated manual trip lever to get Recloser in correct position to operate via SCADA. Mick advises Capacitor will need to be replaced. | 000001852575 | .HEADING 010823 SS 81239 - M O'KEEFFE advises manual trip lever stuck between operations. Known issue, rectified on site. System Condition - URGENT\rJulia Creek No.10 / Nelia Feeder 19.1kV CB J652 failed to close via SCADA or Local control onsite after O/C trip on SWER Feeder. Crews investigated with Test section and Mick O'Keeffe and found recloser not opening fully, Crews operated manual\rtrip lever to get Recloser in correct position to operate via SCADA. Mick advises Capacitor will need to be replaced. Julia Creek No.10 / Nelia Feeder 19.1kV CB J652 failed to\rclose via SCADA or Local control onsite after O/C trip on SWER Feeder. Crews investigated with Test section and Mick O'Keeffe and found recloser not opening fully, Crews operated manual trip lever to get Recloser in correct position to operate\rvia SCADA. Mick advises Capacitor will need to be replaced. |  |  | 33 | 1 | 12 | 4 | 12 |  | 0 |  | 0 |  | 0 |  | 4
63121 | 000001856475 | 2023-07-22 | 2024 | OT189983 | SARI 33kV TX 2 CB EB08 failed to operate | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2023-07-27 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Corroded | Fatigue |  | 33kV | 0 | P0 - Forced |  |  | 237647 |  |  |  |  | 000001856475 | URGNT System Condition - 23MK6128 |  |  | 2T CB 11KV TRANSF 2 CB | SARISS TRANSF 2 CB SLOT | IS | XLFPS | SARISS-TX02-Q10 | ST | Slot - GIS | .HEADING 22-Jul-23 14:41 Clayton O'Neill Out of Service 33kV TRANSF 2 CB EB08 failed to operate and clear T2 fault 22-Jul-23 14:42 Clayton O'Neill Update 23-Jul-23 14:22 Clayton O'Neill Restored\rFailure of the 33kV TF CB to trip has been put down to a faulty auxiliary contact (52a) which has also now been cleaned and proven. Time On modified from 23:59 29-Jul to 14:22 23-Jul 23-Jul-23 14:22 Clayton O'Neill Completed\r 27/7/23 AMCD 33KV TX2 EB08 Failed to operate under fault conditions. Crew found high resistance on negative of trip coil circuit, Cleaned contcts and tested. | 000001856475 | .HEADING System Condition - URGENT 33kV TRANSF 2 CB EB08 failed to operate and clear T2 fault 33kV TRANSF 2 CB EB08 failed to operate and clear T2 fault |  |  | 33 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
19775 | 000001852876 | 2023-07-03 | 2024 | OT188025 | YARA-33kV ABB RMAG CB EB07Q00-NAR Applie | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-07-17 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Incorrect operation/activity |  | 33kV | 0 | P0 - Forced |  |  | 8750071 |  |  |  |  | 000001852876 | SYNAR System Condition - 23SW9074 | Restriction Applies |  | EB07Q00 33KV MARYRRGH FDR CB | YARASS MARYROROUGH SOLAR FDR CB SLOT | AR | XCGDI | YARASS-EB07-Q00 | ST | Slot - GIS | .HEADING System Condition - Network Access Restriction Applies YARA 33kV ABB RMAG CB EB07Q00 is failing PD testing. NAR666 has been placed and recommend a 5m RMHZ exclusion zone from CB\rYARA 33kV ABB RMAG CB EB07Q00 is failing PD testing. NAR666 has been placed and recommend a 5m RMHZ exclusion zone from CB | 000001852876 | .HEADING System Condition - Network Access Restriction Applies YARA 33kV ABB RMAG CB EB07Q00 is failing PD testing. NAR666 has been placed and recommend a 5m RMHZ exclusion zone from CB\rYARA 33kV ABB RMAG CB EB07Q00 is failing PD testing. NAR666 has been placed and recommend a 5m RMHZ exclusion zone from CB |  |  | 33 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
75423 | 000001853442 | 2023-07-06 | 2024 | OT188371 | OAKE Tx3 Fdr CB Spring EB1152 toggl | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-07-07 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Defective component |  | 33kV | 0 | P0 - Forced |  |  | 248006 |  |  |  |  | 000001853442 | NURGT System Condition - 23SW9171 |  |  | EB1152 33KV TFR3 CB | OAKESS TFR3 CB SLOT | IS | XLGDT | OAKESS-EB11-Q00 | ST | Slot - GIS | .HEADING CB was under access at the time while we performed some work. Syscon created in error. Shane Macdonald 07/07/23\r System Condition - Non Urgent 33kV Tranf 3 Fdr CB Spring EB1152 toggling. Please investigate. 33kV Tranf 3 Fdr CB Spring EB1152 toggling. Please\rinvestigate. | 000001853442 | System Condition - Non Urgent 33kV Tranf 3 Fdr CB Spring EB1152 toggling. Please investigate. 33kV Tranf 3 Fdr CB Spring EB1152 toggling. Please investigate. |  |  | 33 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
4718 | 000001932075 | 2024-06-12 | 2024 | OT238698 | GEOR T1 CB Bearing Fail_Spring Chrg Mech | 1 | 0 | P0 - Forced | C | Closed | CN | In Construction | 2024-06-21 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Incorrect operation/activity |  | 66kV | 0 | P0 - Forced |  |  | 143015 |  |  |  |  | 000001932075 | URGNT System Condition - URGENT 24FN7331 |  |  | T1 66KV TRANSF 1 CB | GEORSS TRANSF 1 CB SLOT | IS | XCTNG | GEORSS-TX51-Q10 | ST | Slot - GIS | .HEADING System Condition - URGENT Transformer No.1 66kV CB - Crew adv failed bearing on\rspring charge mech jsmith - bearing replaced | 000001932075 |  |  |  | 66 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
51142 | 000001929008 | 2024-05-28 | 2024 | OT237300 | HOHI T1 CB A452 NOT OPENING FULLY | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-05-31 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Broken | Fatigue |  | 66kV | 0 | P0 - Forced |  |  | 177843 |  |  |  |  | 000001929008 | URGNT System Condition - 24NQ9146 |  |  | A452 66KV TRANSF 1 CB | HOHISS TRANSF 1 CB SLOT | IS | XLHBH | HOHISS-TX01-Q00 | ST | Slot - GIS |  | 000001929008 |  |  |  | 66 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
9292 | 000001907351 | 2024-02-09 | 2024 | OT224941 | POCU EA0352 EA0652 Dif trip CB fail | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2024-02-21 |  | 0.45972 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 5192779 |  |  |  |  | 1907351 | HESS Human Error - Second Sys 24CA2757 |  |  | EA0652 66KV 6111 GLADSTONE NTH CB | POCUSS 6111 GLADSTONE NORTH CB SLOT | IS | XLFPG | POCUSS-EA06-Q00 | ST | Slot - GIS | .HEADING 24CA2757 ** S.Boyd 21/02/2024 05-Feb-24 10:20 Jeffrey Barron To be dispatched\r66KV 6110 CLINTON INDUSTRIAL CB EA0352 & 66KV 6111 GLADSTONE NORTH CB EA0652, Diff trip CB fail 05-Feb-24 10:20 Jeffrey Barron Update Asset selection reset 05-Feb-24 10:20 Jeffrey Barron Update\rport off on 24ca0619. Asset selection modified 05-Feb-24 10:38 Jeffrey Barron Update F-2433-r 05-Feb-24 11:05 Jeffrey Barron Restored\rTime On modified from 23:59 05-Feb to 11:02 05-Feb 05-Feb-24 11:06 Jeffrey Barron Completed ** | 000001907351 |  |  |  | 66 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
1316 | 000001896499 | 2024-01-06 | 2024 | OT216858 | WEBU CB A1224, Gas Locked Oper A1124 | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2024-01-15 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Leaking | Defective component |  | 66kV | 0 | P0 - Forced |  |  | 8744992 |  |  |  |  | 1896499 | URGNT System Condition - 24WB0264 |  |  | A1124 66KV BUS SECTION CB | WEBUSS 66KV BUS SECTION CB SLOT | IS | XLFBB | WEBUSS-EA55-Q00 | ST | Slot - GIS | .HEADING 06-Jan-24 17:46 Cameron Marshall System Abnormal 11kV Bus CB A1224, Gas Locked Oper A1124, please investigate 06-Jan-24 17:48 Cameron Marshall Update Primary Asset de-escalated from West Bundaberg 66/11kv\rSubstation (ZS) 06-Jan-24 18:06 Cameron Marshall Update F-2817-q 06-Jan-24 19:59 Michael Parker Restored Sticky contact on densimeter rectified. Gas all OK, alarms\rcleared. Time On modified from 23:59 13-Jan to 19:59 06-Jan 06-Jan-24 19:59 Michael Parker Completed | 000001896499 |  |  |  | 66 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
4632 | 000001883117 | 2023-11-28 | 2024 | OT205686 | MURG Sus burntout close coil on CB B352 | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-12-04 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Attachment Tie | Loose Nut | Wind |  | 66kV | 0 | P0 - Forced |  |  | 158152 |  |  |  |  | 000001883117 | URGNT System Condition -23WB14979 |  |  | 66KV KINGAROY FDR CB | MURG B352 SLOT | IS | XCFBR | MURGSS-EA53-Q00 | ST | Slot - GIS | .HEADING System Condition - URGENT Suspect Burnt out Close Coil on 66KV KINGAROY FDR CB B352. Crew onsite report smoke in the CB cabinet after Close attempts failed\rSuspect Burnt out Close Coil on 66KV KINGAROY FDR CB B352. Crew onsite report smoke in the CB cabinet after Close attempts failed Spoke to James Redmond who will organise a crew to attend .\rDarren Steinhardt is currently onsite. PON tag applied | 000001883117 |  |  |  | 66 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
1894 | 000001879227 | 2023-11-11 | 2024 | OT203151 | EMER EM-T2 CB EM-S608 C ph Oil Loss | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-11-13 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Leakage |  | 66kV | 0 | P0 - Forced |  |  | 367068 |  |  |  |  | 000001879227 | URGNT System Condition - 23CA15754 |  |  | DELLE 66KV OCB | EMERSS 66KV TRANSF 2 CB EM-S608 | IS | XLFPE | CB91641941 | CB | Circuit Breaker | .HEADING LS 80409 13/11/2023 - Dates already in current month. System Condition - URGENT Transformer EM-T2 66kV CB EM-S608, crews advise 1 leg of\rCB has lost alot of oil overnight, no oil is visible in sight glass. Transformer EM-T2 66kV CB EM-S608, crews advise 1 leg of CB has lost alot of oil overnight, no oil is visible in sight glass.\r-------------------------------------------------------- 13/11/23 B.Arthur - Chris Walters and John Pratchett attended site. Email below - \"John and myself attended Emerald on Saturday due to reported oil loss on the T2 66kv Delle CB EM-S608. We found\rthe oil had dropped below the site glass on C phases and quiet a fresh fast leak coming from underneath C Phase. Townsville subs and test were onsite for project work and had reported it, and they said the leak has suddenly appeared.\r On Saturday afternoon/night, we drained the pole, removed it from the stand and replaced all 3 O-Rings under neath associated with the clamping rods and the damper. We gave it a good degrease and reinstalled the pole, filled and\rfiltered. We returned the next morning and it didn't appear to be leaking. The final oil level is approx. just above halfway in the site glass.\r We timed the CB and ran a breakdown test on the oil pre and post repair, and an IR post repair. All results were within specification. \rTiming Spread Pre: \" Close - 0.85ms \" Trip - 0.9ms\r Post: \" Close - 1.5ms \" Trip 1 - 0.3ms \" Trip 2 - 0.8ms\r Oil Breakdown Pre: 36kv Post: 57.4kv\r IR Post: \" 250Gohm to earth\r\" 300Gohm across gap\" Completed | 000001879227 |  |  |  | 66 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
551 | 000001865183 | 2023-09-06 | 2024 | OT194719 | LITT CB LM-S613 Wont Close after Outage | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-20 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Deteriorated | Loose/missing component | Repair | 66kV | 0 | P0 - Forced |  |  | 294788 |  |  |  |  | 000001865183 | URGNT System Condition - 23CA13121 |  |  | LM-S613 66KV 6030 MONTO FDR CB | LITTSS 6030 MONTO FEEDER CB SLOT | IS | XCFZV | LITTSS-EA52-Q00 | ST | Slot - GIS | .HEADING System Condition - URGENT 6030 Monto Feeder 66kV CB LM-S613 Wont Close after Outage 6030 Monto Feeder 66kV CB LM-S613 Wont Close after Outage \rLimits out of allignment. Sub Ops reset everything. Returned to service successfully Time On modified from 23:59 13-Sep to 18:06 06-Sep | 000001865183 | .HEADING System Condition - URGENT 6030 Monto Feeder 66kV CB LM-S613 Wont Close after Outage 6030 Monto Feeder 66kV CB LM-S613 Wont Close after Outage |  |  | 66 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
68835 | 000001857850 | 2023-07-30 | 2024 | OT190752 | ROSO CB RS-S101 Service switch maint | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-12 |  | 0.5 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | High Coolant Temperature | Incorrect operation/activity |  | DC | 0 | P0 - Forced |  |  | 307335 |  |  |  |  | 000001857850 | NURGT System Condition - 23CA11617 |  |  | RS-S101 11KV GRACEMERE CB | ROSOSS GRACEMERE FEEDER CB SLOT | IS | XLFPR | ROSOSS-FB56-Q00 | ST | Slot - GIS | .HEADING System Condition - Non Urgent Gracemere Feeder 11kV CB RS-S101 - Tyson Richter advises suspect maintenance/ off/ service switch. Please arrange replacement.\rGracemere Feeder 11kV CB RS-S101 - Tyson Richter advises suspect maintenance/ off/ service switch. Please arrange replacement. | 000001857850 | .HEADING System Condition - Non Urgent Gracemere Feeder 11kV CB RS-S101 - Tyson Richter advises suspect maintenance/ off/ service switch. Please arrange replacement.\rGracemere Feeder 11kV CB RS-S101 - Tyson Richter advises suspect maintenance/ off/ service switch. Please arrange replacement. |  |  | 66 | 1 | 0 |  | 0 |  | 0 |  | 13 | 4 | 0 |  | 4 |  |  |  | CB
62752 | 000001863401 | 2023-08-29 | 2024 | OT193736 | ROSO CB RS-S603 Motor Limit Switc faulty | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-08 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Wiring and Electrical Componen | Out of Specification | Vibration |  | DC | 0 | P0 - Forced |  |  | 307739 |  |  |  |  | 000001863401 | URGNT System Condition - 23CA12714 |  |  | RS-S603 66KV TRANSF 1 CB | ROSOSS TRANSF 1 CB SLOT | IS | XLFPR | ROSOSS-TX51-Q00 | ST | Slot - GIS | .HEADING System Condition - URGENT 66KV TRANSF 1 CB RS-S603 - Motor Limit Switch is Faulty. CB was difficult to close 66KV TRANSF 1 CB RS-S603 - Motor Limit Switch is Faulty.\rCB was difficult to close | 000001863401 | System Condition - URGENT 66KV TRANSF 1 CB RS-S603 - Motor Limit Switch is Faulty. CB was difficult to close 66KV TRANSF 1 CB RS-S603 - Motor Limit Switch is Faulty. CB was difficult to close |  |  | 66 | 1 | 1 | 4 | 0 |  | 0 |  | 12 |  | 0 |  | 4
70370 | 000001855180 | 2023-07-14 | 2024 | OT189268 | LACR CB LC-S610 not staying closed | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-30 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 371282 |  |  |  |  | 000001855180 | URGNT System Condition - 23CA8613 |  |  | ASEA 66KV OCB | LACRSS LC-S610 66KV 6096 EGANS HILL FDR | IS | XLFPR | CB92283579 | CB | Circuit Breaker | .HEADING System Condition - URGENT 6096 Egans Hill Feeder 66kV CB LC-S610 not staying closed. Latch catch playing up. 6096 Egans Hill Feeder 66kV CB LC-S610 not staying closed.\rLatch catch playing up. Lubricated and function tested under NAWN, returned to service. Time On modified from 23:59 21-Jul to 17:10 14-Jul | 000001855180 | System Condition - URGENT 6096 Egans Hill Feeder 66kV CB LC-S610 not staying closed. Latch catch playing up. 6096 Egans Hill Feeder 66kV CB LC-S610 not staying closed. Latch catch playing up. |  |  | 66 | 1 | 13 | 4 | 1 | 0 | 0 |  | 0 |  | 0 |  | 4
20342 | 000001859786 | 2023-08-09 | 2024 | OT191775 | WEBU CB G452 bearing spring char slippin | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-15 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Armour Rod | Leaning | Cement Growth |  | 66kV | 0 | P0 - Forced |  |  | 165667 |  |  |  |  | 000001859786 | URGNT System Condition - 23WB11552 |  |  | G452 11KV OAKWOOD CB | WEBUSS OAKWOOD FEEDER CB SLOT | IS | XLFBB | WEBUSS-FB57-Q00 | ST | Slot - GIS | .HEADING System Condition - URGENT Cam Thomas advises that while working on Oakwood Feeder 11kV CB G452 he has found that the bearing on the spring charge motor is slipping and requires replacement.\rCB spring will be left charged but Auto Reclose left disabled. When the Syscon gets rectified please also remove the Info note on the CB in PowerOn. Cam Thomas advises that while working on Oakwood Feeder\r11kV CB G452 he has found that the bearing on the spring charge motor is slipping and requires replacement. CB spring will be left charged but Auto Reclose left disabled. When the Syscon gets rectified please also remove the Info\rnote on the CB in PowerOn. Asset selection modified Asset selection reset Asset selection modified\r W/O CREATED | 000001859786 | System Condition - URGENT Cam Thomas advises that while working on Oakwood Feeder 11kV CB G452 he has found that the bearing on the spring charge motor is slipping and requires replacement. CB spring will be left charged but Auto Reclose left\rdisabled. When the Syscon gets rectified please also remove the Info note on the CB in PowerOn. Cam Thomas advises that while working on Oakwood Feeder 11kV CB G452 he has found that the bearing on the spring\rcharge motor is slipping and requires replacement. CB spring will be left charged but Auto Reclose left disabled. When the Syscon gets rectified please also remove the Info note on the CB in PowerOn. |  |  | 66 | 1 | 13 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
18481 | 000001859549 | 2023-08-08 | 2024 | OT191672 | MORA EA10T03 Low oil C phase sight glass | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-15 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Tank, Head & Secondary Term Bo | Leaking | Seal | Repair | 66kV | 0 | P0 - Forced |  |  | 256111 |  |  |  |  | 000001859549 | URGNT System Condition - 23MK6498 |  |  | EA10T03 66KV UTAH 1 FDR CT | MORASS UTAH 1 FEEDER CT SLOT | IS | XCPNO | MORASS-EA10-T03 | ST | Slot - GIS | .HEADING 66KV UTAH 1 FDR CB EA10Q00 - Low oil C phase sight glass of CTs EA10T03 08-Aug-23 12:47 Ryan Smith System Abnormal .\r08-Aug-23 12:57 Ryan Smith Update 08-Aug-23 18:50 Ryan Landa Update Crews have topped up CT, Crews have advised to leave sycon out until tomorrow 9/8/23 for test to do online PD scan. | 000001859549 | System Condition - URGENT 66KV UTAH 1 FDR CB EA10Q00 - Low oil C phase sight glass of CTs EA10T03 66KV UTAH 1 FDR CB EA10Q00 - Low oil C phase sight glass of CTs EA10T03 |  |  | 66 | 1 | 12 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
75415 | 000001858924 | 2023-08-04 | 2024 | OT191286 | WEBU CB J452 bearing slippin charg motor | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-08-09 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Defective component |  | 66kV | 0 | P0 - Forced |  |  | 165457 |  |  |  |  | 000001858924 | NURGT System Condition - 23WB11424 |  |  | J452 11KV AVOCA STREET CB | WEBUSS AVOCA ST FEEDER CB SLOT | IS | XLFBB | WEBUSS-FB52-Q00 | ST | Slot - GIS | .HEADING System Condition - Non Urgent Tim Vagias advises that while working under 23WB7382 on Avoca Street Feeder 11kV CB J452 he has found that the bearing on the spring charge motor is slipping and requires\rreplacement. Tim Vagias advises that while working under 23WB7382 on Avoca Street Feeder 11kV CB J452 he has found that the bearing on the spring charge motor is slipping and requires replacement.\r CB spring will be left charged but Auto Reclose left disabled. When the Syscon gets rectified please also remove the Info note on the CB in PowerOn.\r w/o created | 000001858924 | .HEADING System Condition - Non Urgent Tim Vagias advises that while working under 23WB7382 on Avoca Street Feeder 11kV CB J452 he has found that the bearing on the spring charge motor is slipping and requires\rreplacement. Tim Vagias advises that while working under 23WB7382 on Avoca Street Feeder 11kV CB J452 he has found that the bearing on the spring charge motor is slipping and requires replacement. |  |  | 66 | 1 | 1 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4
3517 | 000001929981 | 2024-06-03 | 2024 | OT237778 | MICB 132kV CB 7B190 contact alignment | 1 | 0 | P0 - Forced | A | Authorised | SC | (4)With Scheduler |  |  | 0.99931 | [9 empty] | MF | Maintenance Forced | Switch, Control Box | No Damage | Fatigue |  | 220kV | 0 | P0 - Forced |  |  | 7445686 |  |  |  |  | 000001929981 | NURGT System Condition - 24NQ9351 |  |  | 7B190 132KV GEN B1 GCB | MICBSS GEN B1 FEEDER GCB SLOT | IS | XCHBI | MICBSS-DA03-Q00 | ST | Slot - GIS | .HEADING 03-Jun-24 12:35 Jamie Sorbello System Abnormal MICA CK B 132kV Gen B1 CB 7B190 showing indeterminate when CB is open. CB is indicating correctly when the CB is close. Possible contact alignment issue when the CB is open.\rPlease Investigate. 03-Jun-24 12:39 Jamie Sorbello Update Time On modified from 23:59 10-Jun to 23:59 10-Dec 18/06/2024 CFielder: Aligned with next routine outage to\rinvestigate open indication | 000001929981 |  |  |  | 132 | 1 | 5 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 4
4717 | 000001932054 | 2024-06-12 | 2024 | OT238696 | GEOR T1 CB4412 Bearing Fail_Spring Mech | 1 | 0 | P0 - Forced | C | Closed | CN | In Construction | 2024-06-21 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Incorrect operation/activity |  | 132kV | 0 | P0 - Forced |  |  | 143032 |  |  |  |  | 000001932054 | URGNT System Condition - URGENT 24FN7330 |  |  | 4412 TRANSF 1 132KV CB 4412 | GEORSS TRANSF 1 CB SLOT | IS | XCTNG | GEORSS-TX51-Q00 | ST | Slot - GIS | .HEADING 12-Jun-24 08:44 Ben Retallick Out of Service 132kV Transformer No.1 CB 4412. Crew adv failed bearing on\rthe spring charge mech. 12-Jun-24 08:48 Ben Retallick Update 12-Jun-24 08:55 Ben Retallick Update Time On modified from 23:59 19-Jun to 12:00 14-Jun \rjsmith - bearing changed | 000001932054 |  |  |  | 132 | 1 | 5 | 4 | 0 |  | 0 |  | 0 |  | 0 |  | 4

## ACR failures
Column1 | REQUEST_ID | RAISED_DATE | FY | WORK_ORDER | WO_DESC | WO_JOB_CODEX1_1 | ORIG_PRIORITY | ORIG_PRIORITY_DESCRIPTION | WO_STATUS_M | WO_STATUS_M_DESCRIPTION | WO_STATUS_U | WO_STATUS_U_DESCRIPTION | CLOSED_DT | CLOSED_COMMIT_DT | CLOSED_TIME | COMPLETED_CODE | COMPLETED_CODE_DESCRIPTION | CLOSED_STATUS | CLOSED_STATUS_DESCRIPTION | SHUTDOWN_EQUIP | SHUTDOWN_TYPE | SHUTDOWN_TYPE_DESCRIPTION | PARENT_WO | PARENT_WO_DESC | MAINT_TYPE | MAINT_TYPE_DESCRIPTION | MSSS_OBJECT_FAILURE_DESCRIPTION | MSSS_DAMAGE_APPARENT_CAUSE_DESCRIPTION | MSSS_CAUSE_DESCRIPTION | CONSEQUENCE_DESCRIPTION | VOLTAGE_DESCRIPTION | PLAN_PRIORITY | PLAN_PRIORITY_DESCRIPTION | CUST_NO | FAILURE_PART | EQUIP_NO | COMP_CODE | COMP_CODE_DESCRIPTION | COMP_MOD_CODE | COMP_MOD_CODE_DESCRIPTION | REQUEST_ID_2 | SHORT_DESC_1 | SHORT_DESC_2 | LOCATION | ITEM_NAME_1 | ITEM_NAME_2 | EQUIP_STATUS | EQUIP_LOCATION | PLANT_NO | EQUIP_CLASS | EQUIP_CLASS_DESCRIPTION | WORK_ORDER_EXTENDED_DESCRIPTION | REQUEST_ID_3 | WORK_REQUEST_EXTENDED_DESCRIPTION | NAMP_LINE | NAMP_LINE_DESCRIPTION | Voltage | OT | CB | CB FAULT | ACR | Rec Fault | RMU | RMUFault | Switch | Switch Fault | Isol | Isol Fault | CB2 | ACR2 | RMU2 | Switches | Switches Comment2 | RMU Comm2
50047 | 000001927188 | 2024-05-18 | 2024 | OT236357 | SCR0 RTS R0 - High Prior BYPASS RECLOSER | 1 | 0 | P0 - Forced | C | Closed |  |  | 2024-05-20 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> | <null> | Not Applicable | 0 | P0 - Forced |  |  | 2270298 |  |  |  |  | 000001927188 | DD RTS R1 CB16374 PECHEY TO NOJA |  |  | Pechey Recloser | Pechey Recloser | IS | XLGDT | RC-66409 | NT | Network Slot |  | 000001927188 |  |  |  | 11 | 1 | 0 |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4
47239 | 000001922339 | 2024-04-22 | 2024 | OT233859 | SCR0 RTS R0 - Hawes Lane Recloser | 1 | 0 | P0 - Forced | C | Closed |  |  | 2024-05-14 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Pole Possum Guard | Missing | Unknown | Replace | 11kV | 0 | P0 - Forced |  |  | 8223826 |  |  |  |  | 000001922339 | SCR0 RTS R0 - High Priority |  |  | Hawes Lane Recloser |  | IS | XLFBA | RC-1355360 | NT | Network Slot |  | 000001922339 |  |  |  | 11 | 1 | 0 |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4
7534 | 000001887142 | 2023-12-12 | 2024 | OT208673 | SCR0 RTS R0 - High Priority-SugarloafACR | 1 | 0 | P0 - Forced | C | Closed |  |  | 2023-12-19 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 2366492 |  |  |  |  | 000001887142 | SCR0 RTS R0 - High Priority |  |  | SUGARLOAF RECLOSER | SUGARLOAF-1405 SHUTE HARBOUR RD, CANNON | IS | XLHBP | RC-57147 | NT | Network Slot |  | 000001887142 |  |  |  | 11 | 1 | 0 |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4
5361 | 000001884213 | 2023-12-01 | 2024 | OT206458 | Switchgear Return to Service | 1 |  |  | C | Closed |  |  | 2023-12-01 |  | 0.66667 | CL | Closed | C | Completed | [5 empty] | CN | Construction | ACR, Body | Damaged | Corrosion |  | 11kV | 0 | P0 - Forced |  |  | 1442176 | RECL | Recloser | OC | Outage Codes | 000001884213 | U Unknown |  |  | 4090494 | 388 | IS | XLFPK | NS4090494 | NS | Network Site | Technician: Ezekiel Barba \nComments put Markeys Rd recloser in bypass , future works required to replace recloser. as there are holes in top of recloser tank | 000001884213 |  |  |  | 11 | 1 | 0 |  | 4 | 4 | 0 |  | 0 |  | 0 |  |  | 4
14521 | 000001915607 | 2024-03-17 | 2024 | OT229855 | SCR2 RTS R2 - PH-58 ACR Bypassed | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2024-03-20 |  | 11:59:00 pm | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 000005929895 |  |  |  |  | 000001915607 | SCR2 RTS R2 - Low Priority 24FN4147 |  |  | Brooks Rd SWER Recloser | 84 CAMPBELL RD, MUNGALLI QLD 4886 | IS | XCTNR | RC-362322 | NT | Network Slot |  | 000001915607 |  |  |  | 22 | 1 | 0 |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4
14515 | 000001915579 | 2024-03-17 | 2024 | OT229831 | U Unknown | 1 | 0 | P0 - Forced | C | Closed |  |  | 2024-03-18 |  | 11:59:00 pm | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Surge Diverter Body, Unknown | Short Circuit | Unknown |  | 12.7kV | 0 | P0 - Forced |  |  | 000001137716 | SURG | Surge Diverters | OC | Outage Codes | 000001915579 | U Unknown |  |  | WA4 | Watson Rd | IS | XCTNR | NS5208932 | NS | Network Site |  | 000001915579 |  |  |  | 22 | 1 | 0 |  | 4 | 4 | 0 |  | 0 |  | 0 |  |  | 4
3451 | 000001881436 | 2023-11-21 | 2024 | OT204597 | SCR2 RTS R2 - 22kV Recloser RC885338 | 1 | 0 | P0 - Forced | C | Closed |  |  | 2023-11-28 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 22kV | 0 | P0 - Forced |  |  | 9232802 |  |  |  |  | 000001881436 | SCR2 RTS R2 - Low Priority |  |  | Harvey Rd | 211 HARVEY RD, REDLYNCH QLD 4870 | IS | XLTNC | RC-885338 | NT | Network Slot |  | 000001881436 |  |  |  | 22 | 1 | 0 |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4
546 | 000001864311 | 2023-09-01 | 2024 | OT194207 | 607088 Hollands rd swer ACR VT volts | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-29 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | SWER HV Elec Recloser 12.7kV | Out of Specification | Unknown | Repair | 12.7kV | 0 | P0 - Forced |  |  | 7762155 |  |  |  |  | 000001864311 | SCR2 RTS R2 - Low Priority 23WB12303 |  |  | Hollands Rd SWER Recloser | MERCERS RD, MEADOWVALE QLD 4670 | IS | XLFBB | RC-1103285 | NT | Network Slot | .HEADING RTS R2 - Low Priority 11kV Recloser 607088 - VT not reading correctly o Identifier Name & Number -&gt; Brady Mayne :\r0429615407 o Recorder Name & Number -&gt; WITHERS, Mitchell : 409618728 o Time & Date equipment was identified as no longer in service -&gt; 01/09/2023\ro Equipment Operational Number, Type & Model - &gt; 11kV Recloser 607088 - VT not reading correctly o High Level Scope e.g. Further Investigation required or Replace plant - &gt; \r- DETAILS: 23WB12303; TEN MILE RD; Hollands Rd SWER Recloser; 607088. POLE MOUNTED RECLOSER, Required to be INVESTIGATE. VT only reading 5.8kV on recloser - CURRENT STATUS : POLE MOUNTED RECLOSER\r- PRIORITY : Priority R2 (9 MONTHS) - ASSET AREA : Bundaberg Burnett; Bundaberg(4) - CONTACT : ; BUNDABERG OH1 11kV Recloser 607088 - VT not reading correctly | 000001864311 | .HEADING RTS R2 - Low Priority 11kV Recloser 607088 - VT not reading correctly o Identifier Name & Number -&gt; Brady Mayne :\r0429615407 o Recorder Name & Number -&gt; WITHERS, Mitchell : 409618728 o Time & Date equipment was identified as no longer in service -&gt; 01/09/2023\ro Equipment Operational Number, Type & Model - &gt; 11kV Recloser 607088 - VT not reading correctly o High Level Scope e.g. Further Investigation required or Replace plant - &gt; \r- DETAILS: 23WB12303; TEN MILE RD; Hollands Rd SWER Recloser; 607088. POLE MOUNTED RECLOSER, Required to be INVESTIGATE. VT only reading 5.8kV on recloser - CURRENT STATUS : POLE MOUNTED RECLOSER\r- PRIORITY : Priority R2 (9 MONTHS) - ASSET AREA : Bundaberg Burnett; Bundaberg(4) - CONTACT : ; BUNDABERG OH1 11kV Recloser 607088 - VT not reading correctly |  |  | 22 | 1 | 0 |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4
10247 | 000001890453 | 2023-12-21 | 2024 | OT211296 | MOSS System Condition -URGENT RC-868498 | 1 | 0 | P0 - Forced | C | Closed |  |  | 2024-01-05 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 9080982 |  |  |  |  | 000001890453 | URGNT System Condition - URGENT |  |  | RC868498 | 59 STEWART CREEK RD, DAINTREE QLD 4873 | IS | XCTNS | RC-868498 | NT | Network Slot | .HEADING 21-Dec-23 10:33 Tony Lenz System Abnormal Cody Goodale advised Control Box at Gas Switch RC868498 has been completely submerged and requires inspection/replacement\r22-Dec-23 11:49 Tony Lenz Update Correction to above is entire Recloser has been submenrged. Sticks are on top of Rcloser 22-Dec-23 11:49 Tony Lenz Update Time On modified from 23:59 28-Dec to 23:59 22-Dec\r22-Dec-23 11:52 Tony Lenz Update Reason for Event changed from System Condition - URGENT 22-Dec-23 11:53 Tony Lenz Update Time On modified from 23:59 22-Dec to 23:59 26-Apr 22-Dec-23 12:03 Tony Lenz Update\r22-Dec-23 12:05 Tony Lenz Update Reassigned to RPMN Far North as per RTS process 05-Jan-24 09:40 EAI Interface Update 000001890453 completed by SUTTON,TRISTAN (0000213395).----WR #:000001890453----\rSystem Condition - URGENT Cody Goodale advised Control Box at Gas Switch RC868498 has been completely submerged and requires\rinspection/replacement Cody Goodale advised Control Box at Gas Switch RC868498 has been completely submerged and requires\rinspection/replacement ---- WO:OT211296---- No completion comments. \r05-Jan-24 14:57 Mal Quantrill Update Box still requires replacement | 000001890453 |  |  |  | 33 | 1 | 0 |  | 4 | 4 | 0 |  | 4 |  | 0 |  |  | 4
8563 | 000001888782 | 2023-12-16 | 2024 | OT209883 | NEBO - 19kV Landsborough West ACR failed | 1 | 0 | P0 - Forced | C | Closed | CP | (9) Complete | 2023-12-29 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | Not Applicable | 0 | P0 - Forced |  |  | 9147713 |  |  |  |  | 000001888782 | NURGT System Condition - Non Urgent |  |  | RC875520 | STRATHFIELD RD, STRATHFIELD QLD 4742 | IS | XCPNO | RC-875520 | NT | Network Slot |  | 000001888782 |  |  |  | 33 | 1 |  |  | 1 | 4 | 0 |  | 0 |  | 0 |  |  | 4

## RMU Failures
Column1 | REQUEST_ID | RAISED_DATE | FY | WORK_ORDER | WO_DESC | WO_JOB_CODEX1_1 | ORIG_PRIORITY | ORIG_PRIORITY_DESCRIPTION | WO_STATUS_M | WO_STATUS_M_DESCRIPTION | WO_STATUS_U | WO_STATUS_U_DESCRIPTION | CLOSED_DT | CLOSED_COMMIT_DT | CLOSED_TIME | COMPLETED_CODE | COMPLETED_CODE_DESCRIPTION | CLOSED_STATUS | CLOSED_STATUS_DESCRIPTION | SHUTDOWN_EQUIP | SHUTDOWN_TYPE | SHUTDOWN_TYPE_DESCRIPTION | PARENT_WO | PARENT_WO_DESC | MAINT_TYPE | MAINT_TYPE_DESCRIPTION | MSSS_OBJECT_FAILURE_DESCRIPTION | MSSS_DAMAGE_APPARENT_CAUSE_DESCRIPTION | MSSS_CAUSE_DESCRIPTION | CONSEQUENCE_DESCRIPTION | VOLTAGE_DESCRIPTION | PLAN_PRIORITY | PLAN_PRIORITY_DESCRIPTION | CUST_NO | FAILURE_PART | EQUIP_NO | COMP_CODE | COMP_CODE_DESCRIPTION | COMP_MOD_CODE | COMP_MOD_CODE_DESCRIPTION | REQUEST_ID_2 | SHORT_DESC_1 | SHORT_DESC_2 | LOCATION | ITEM_NAME_1 | ITEM_NAME_2 | EQUIP_STATUS | EQUIP_LOCATION | PLANT_NO | EQUIP_CLASS | EQUIP_CLASS_DESCRIPTION | WORK_ORDER_EXTENDED_DESCRIPTION | REQUEST_ID_3 | WORK_REQUEST_EXTENDED_DESCRIPTION | NAMP_LINE | NAMP_LINE_DESCRIPTION | Voltage | OT | CB | CB FAULT | ACR | Rec Fault | RMU | RMUFault | Switch | Switch Fault | Isol | Isol Fault | CB2 | ACR2 | RMU2 | Switches | Switches Comment2 | RMU Comm2 | Make | Model | YoM | Column2
6654 | 000001935034 | 2024-06-26 | 2024 | OT240182 | RTS R2 - COMMUNITY CENTRE RMU NO GAS | 1 | 0 | P0 - Forced | A | Authorised |  |  |  |  | 0.64583 | [9 empty] | MF | Maintenance Forced |  |  |  |  | 22kV | 0 | P0 - Forced |  |  | 2401965 |  |  |  |  | 000001935034 | PN RTS R1 BARNFIELD DR COMMUNITY CTR_RMU | LO RBD 26/07 |  | 1684S | 86 CELEBER DVE, ANDERGROVE QLD 4740 | IS | XLFPK | LB-77633 | NT | Network Slot |  | 000001935034 |  |  |  | 11 | 1 | 0 |  | 0 |  | 1 | 4 | 0 |  | 0 |  |  |  | 4 |  |  | 0 | ABB | Safelink | 1993
18023 | 000001921040 | 2024-04-14 | 2024 | OT233156 | Switchgear Return to Service | 1 |  |  | C | Closed |  |  | 2024-04-14 |  |  | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Alignment Incorrect | Internal Fault |  | 11kV | 0 | P0 - Forced |  |  | 2403741 |  |  |  |  | 1921040 | THURINGOWA STATE HIGH SCHOOL | O - Other |  | TVS3886 | THURINGOWA STATE HIGH SCHOOL, SOUTH VIC | IS | XLHBT | GT-184170 | NT | Network Slot |  | 000001921040 |  |  |  | 11 | 1 | 0 |  | 0 |  | 4 | 4 | 4 | 4 | 0 |  |  |  | 4 | 4 | 0 | 0 | ABB | Safelink | 2006
9552 | 000001907670 | 2024-02-12 | 2024 | OT225200 | SCR0 RTS R0 - High Priority | 1 | 0 | P0 - Forced | C | Closed |  |  | 2024-02-13 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 8254690 |  |  |  |  | 1907670 | BB_RTS R2_RMU 615693 BAKERFINCH DR BARG |  |  | Baker-Finch Dve | BAKER-FINCH DVE, BARGARA QLD 4670 | IS | XLFBB | GT-1184961 | NT | Network Slot | .HEADING RTS R0 - High Priority RMU 615693 HAS LOW GAS RMU 615693 HAS LOW GAS | 000001907670 |  |  |  | 11 | 1 | 0 |  | 0 |  | 4 | 4 | 0 |  | 0 |  |  |  | 4 |  |  | 0 | Schneider | FBX | 2015
6284 | 000001902420 | 2024-01-27 | 2024 | OT221297 | Switchgear RTS Friendlys CB | 1 |  |  | C | Closed |  |  | 2024-02-12 |  | 0.97917 | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Damaged | Unknown |  | 11kV | 0 | P0 - Forced |  |  | 6553235 | SW | Switch | OC | Outage Codes | 1902420 | BUNDABERG FRIENDLY SOCIETY MED | P - Phase Down (LV) |  | 86052 | 23 BINGERA ST, BUNDABERG WEST QLD 4670 | IS | XLFBB | NS86052 | NS | Network Site | .HEADING Technician: Dennis Dennien Comments rmu circuit breaker will not close live. requires incoming supply to be de\renergised before CB will stay closed , then re energise the incoming supply. settings in CB need checking/rectifying, or CB is faulty \rCompleted under assett event 24WB2297, RTS created for RMU CB under WR 1902440 JS | 000001902420 |  |  |  | 11 | 1 | 4 | 4 | 0 |  | 4 | 4 | 0 |  | 0 |  | 4 |  | 4 |  |  | 0 | ABB | SAFERING | 2008
10470 | 000001891160 | 2023-12-23 | 2024 | OT211905 | Switchgear Return to Service | 1 |  |  | C | Closed |  |  | 2024-01-04 |  | 0.64601 | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Damaged | Internal Fault |  | 11kV | 0 | P0 - Forced |  |  | 8169052 |  |  |  |  | 000001891160 | U Unknown |  |  | GLENVALE EAST | 11KV GLENVALE EAST FDR (14088) | IS | XLGDT | FD-4088 | FD | Feeder | .HEADING ToughPad Location: \nSite Label Entered:GE00335\nComponent: SW\nComponent Mod: OC\nTechnician: Dalton balke\nComments RMU to be replaced ToughPad Location: \nSite Label Entered:GE00335\nComponent:\rSW\nComponent Mod: OC\nTechnician: Stewart Cameron \nComments replace padmount GE00335 | 000001891160 |  |  |  | 11 | 1 | 0 |  | 0 |  | 4 | 4 | 0 |  | 0 |  |  |  | 4 |  |  | 0 | ABB | SDAF 3 SERIES 3 | 1994
1904 | 000001927300 | 2024-05-19 | 2024 | OT236441 | ATHE 2/RMU 2 FDR CB Spring Not Charging | 1 | 0 | P0 - Forced | C | Closed | CN | In Construction | 2024-06-21 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | CB Body | Damaged | Incorrect operation/activity |  | 22kV | 0 | P0 - Forced |  |  | 133547 |  |  |  |  | 000001927300 | URGNT System Condition - 24FN6466 |  |  | FA12Q00 22KV ATHERTON 2/RMU 2 FDR CB | ATHESS ATHERTON 2 FEEDER CB SLOT | IS | XLTNA | ATHESS-FA12-Q00 | ST | Slot - GIS | .HEADING 21.05.2024 SS202376 : System Condition - URGENT\r22kV CB Atherton No.2 - FA12Q00 - spring does not charge 22/05/24 jsmith - outage entered for 29th May, Rang OCC to extend RBD to 31/05 \r24/05/24 jsmith - contacted by controll, unable to write sheets in time, extended to mid/end june | 000001927300 |  |  |  | 22 | 1 | 5 | 4 | 0 |  | 1 | 4 | 0 |  | 0 |  | 4 |  | 4 |  |  | 0 | GEC | AV24 | 1985
43970 | 000001917722 | 2024-03-26 | 2024 | OT231068 | Cable Return to Service | 1 |  |  | C | Closed |  |  | 2024-05-01 |  | 0.66667 | CL | Closed | C | Completed | [5 empty] | CN | Construction | Padmount Substation | Broken | Unknown |  | 22kV | 0 | P0 - Forced |  |  | 24240 |  |  |  |  | 000001917722 | Unknown |  |  | WHITE ROCK |  | IS | XLTNC | FD-2122 | FD | Feeder |  | 000001917722 |  |  |  | 22 | 1 | 0 |  | 0 |  | 4 | 4 | 0 |  | 0 |  |  |  | 4 |  |  | 0 | ORMAZABAL | GA3K1TS-C | 2011

## Switch Failures
Column1 | REQUEST_ID | RAISED_DATE | FY | WORK_ORDER | WO_DESC | WO_JOB_CODEX1_1 | ORIG_PRIORITY | ORIG_PRIORITY_DESCRIPTION | WO_STATUS_M | WO_STATUS_M_DESCRIPTION | WO_STATUS_U | WO_STATUS_U_DESCRIPTION | CLOSED_DT | CLOSED_COMMIT_DT | CLOSED_TIME | COMPLETED_CODE | COMPLETED_CODE_DESCRIPTION | CLOSED_STATUS | CLOSED_STATUS_DESCRIPTION | SHUTDOWN_EQUIP | SHUTDOWN_TYPE | SHUTDOWN_TYPE_DESCRIPTION | PARENT_WO | PARENT_WO_DESC | MAINT_TYPE | MAINT_TYPE_DESCRIPTION | MSSS_OBJECT_FAILURE_DESCRIPTION | MSSS_DAMAGE_APPARENT_CAUSE_DESCRIPTION | MSSS_CAUSE_DESCRIPTION | CONSEQUENCE_DESCRIPTION | VOLTAGE_DESCRIPTION | PLAN_PRIORITY | PLAN_PRIORITY_DESCRIPTION | CUST_NO | FAILURE_PART | EQUIP_NO | COMP_CODE | COMP_CODE_DESCRIPTION | COMP_MOD_CODE | COMP_MOD_CODE_DESCRIPTION | REQUEST_ID_2 | SHORT_DESC_1 | SHORT_DESC_2 | LOCATION | ITEM_NAME_1 | ITEM_NAME_2 | EQUIP_STATUS | EQUIP_LOCATION | PLANT_NO | EQUIP_CLASS | EQUIP_CLASS_DESCRIPTION | WORK_ORDER_EXTENDED_DESCRIPTION | REQUEST_ID_3 | WORK_REQUEST_EXTENDED_DESCRIPTION | NAMP_LINE | NAMP_LINE_DESCRIPTION | Voltage | OT | CB | CB FAULT | ACR | Rec Fault | RMU | RMUFault | Switch | Switch Fault | Isol | Isol Fault | CB2 | ACR2 | RMU2 | Switches | Switches Comment2 | RMU Comm2 | Make | Model | YoM
18023 | 000001921040 | 2024-04-14 | 2024 | OT233156 | Switchgear Return to Service | 1 |  |  | C | Closed |  |  | 2024-04-14 |  |  | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Alignment Incorrect | Internal Fault |  | 11kV | 0 | P0 - Forced |  |  | 2403741 |  |  |  |  | 1921040 | THURINGOWA STATE HIGH SCHOOL | O - Other |  | TVS3886 | THURINGOWA STATE HIGH SCHOOL, SOUTH VIC | IS | XLHBT | GT-184170 | NT | Network Slot |  | 000001921040 |  |  |  | 11 | 1 | 0 |  | 0 |  | 4 | 4 | 4 | 4 | 0 |  |  |  | 4 | 4 | 0 | 0 | ABB | Safelink | 2006
13078 | 000001913462 | 2024-03-06 | 2024 | OT228590 | CAFE_11kV Bus Tie Gas Switch A829_FIS | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2024-03-15 |  | 11:59:00 pm | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | Switch Oil/Gas Insulation | Gas Leakage | Fatigue | Replace | 11kV | 0 | P0 - Forced |  |  | 000000170205 |  |  |  |  | 000001913462 | URGNT System Condition - 24NQ5832 |  |  | A829 11KV BUS ISOL | CAFESS BUS ISOL SLOT | IS | XLHBT | CAFESS-FB51-Q01 | ST | Slot - GIS |  | 000001913462 |  |  |  | 11 | 1 | 0 |  | 0 |  | 0 |  | 5 | 4 | 0 |  |  |  |  | 4 | 0 |  | Scneider | RL27 | N/A
8522 | 000001888652 | 2023-12-16 | 2024 | OT209763 | Switchgear Return to Service | 1 |  |  | C | Closed |  |  | 2023-12-16 |  |  | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Damaged | Unknown |  | 11kV | 0 | P0 - Forced |  |  | 1864849 | SW | Switch | OC | Outage Codes | 000001888652 | MRS D M JANSEN | S - Sparking Lines/Pole |  | 3312297 | 28693 BRUCE HWY, CHILDERS QLD 4660 | IS | XCFBC | NS3312297 | NS | Network Site | Technician: Clayton Hughes \nComments replaced burnt hv link | 000001888652 |  |  |  | 11 | 1 | 0 |  | 0 |  | 0 |  | 4 | 4 | 0 |  |  |  |  | 4 | 0 |  | HV link | N/A | N/A
2814 | 1873838 | 2023-10-20 | 2024 | OT199703 | Switchgear Return to Service | 1 |  |  | C | Closed |  |  | 2023-11-15 |  | 0.64583 | CL | Closed | C | Completed | [5 empty] | CN | Construction | Switch, Unknown | Damaged | Unknown | Replace | 11kV | 0 | P0 - Forced |  |  | 1522735 | SW | Switch | OC | Outage Codes | 1873838 | DD RTS R1 TMBA CEC PLNS RD DL7157 RPLC |  |  | 3248105 | F3145 | IS | XCGDI | NS3248105 | NS | Network Site | Technician: Pat lunney\nComments Replaced DL 7157 \n\nContractors carried this work out on 23SW17647 | 000001873838 | .HEADING RTS R1 - Medium Priority 11kV Disc Links DL7157 B Phase has nearly pulled through crossarm and require replacing. Unable to be Operated. 11kV Disc Links DL7157 B Phase has nearly pulled through\rcrossarm and require replacing. Unable to be Operated. ============================================================ COMMENTS: \r02/11/23 201384 KJ: Issued to XCGDL via Opex. |  |  | 11 | 1 | 0 |  | 0 |  | 0 |  | 12 | 4 | 0 |  |  |  |  | 4 | 0 |  | HV Link | N/A | N/A
75391 | 000001858784 | 2023-08-04 | 2024 | OT191216 | BOWE D257 Earth Switch faulty - 23NQ9768 | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-05 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | <null> | <null> | <null> |  | 11kV | 0 | P0 - Forced |  |  | 168725 |  |  |  |  | 000001858784 | URGNT System Condition - 23NQ9768 |  |  | D257 11KV BN04 FDR ES | BOWESS BN04 FEEDER ES SLOT | IS | XLHBB | BOWESS-FB52-Q05 | ST | Slot - GIS | .HEADING System Condition - URGENT D257 Earth Switch faulty. Earth Switch contacts not moving when handle operated. Also contacts appear to be not fully opened\rD257 Earth Switch faulty. Earth Switch contacts not moving when handle operated. Also contacts appear to be not fully opened. | 000001858784 | .HEADING System Condition - URGENT D257 Earth Switch faulty. Earth Switch contacts not moving when handle operated. Also contacts appear to be not fully opened\rD257 Earth Switch faulty. Earth Switch contacts not moving when handle operated. Also contacts appear to be not fully opened. |  |  | 11 | 1 | 0 |  | 0 |  | 0 |  | 13 | 4 | 0 |  |  |  |  | 4 | 0 |  | Mitsubishi | 10-PVR | 1981
2139 | 1872996 | 2023-10-16 | 2024 | OT199253 | ATHE 66kV Earth Switch EA05Q05 | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-10-30 |  | 0.99931 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | HV Isolators Fuses & Earth Swi | Loose Connection | Wear and Tear |  | DC | 0 | P0 - Forced |  |  | 101 |  |  |  |  | 1872996 | URGNT System Condition - 23FN13778 |  |  | ATHERTON 66/22KV SUB (ATHE) | ATHESS 66/22KV ZONE SUB | IS | XLTNA | ATHESS | SS | Substation Site | .HEADING System Condition - URGENT Atherton No.1 Fdr - 66kV Earth Switch EA05Q05 - indicating closed. Limit switch needs to be adjusted. Atherton No.1 Fdr - 66kV Earth Switch EA05Q05 - indicating\rclosed. Limit switch needs to be adjusted. | 000001872996 | System Condition - URGENT Atherton No.1 Fdr - 66kV Earth Switch EA05Q05 - indicating closed. Limit switch needs to be adjusted. Atherton No.1 Fdr - 66kV Earth Switch EA05Q05 - indicating closed. Limit switch needs to be adjusted. |  |  | 66 | 1 | 0 |  | 0 |  | 0 |  | 13 | 4 | 0 |  |  |  |  | 4 | 0 |  | ACELEC TAPLIN | 66RD-1 | 2004
69497 | 000001859551 | 2023-08-08 | 2024 | OT191675 | CANN EA0229 contacts sticking on switch | 1 | 0 | P0 - Forced | C | Closed | SC | (4)With Scheduler | 2023-09-01 |  | 0.625 | CL | Closed | C | Completed | [5 empty] | MF | Maintenance Forced | HV Isolators Fuses & Earth Swi | Deteriorated | Incorrect operation/activity |  | 66kV | 0 | P0 - Forced |  |  | 243767 |  |  |  |  | 000001859551 | URGNT System Condition - 23MK6500 |  |  | EA0229 66KV TFR1-TFR2 TIE ISOL | CANNSS 66KV BUS ISOL SLOT | IS | XLHBP | CANNSS-EA02-Q02 | ST | Slot - GIS | .HEADING [CANN] 66kV TFR1-TFR2 TIE ISOL EA0229 - contacts sticking on switch, still possible to operate. 31/9/23 AMCD Contacted OCC and advised this is a\rconsistent issue with switch. Crew completed visual inspection and looks ok. | 000001859551 | System Condition - URGENT [CANN] 66kV TFR1-TFR2 TIE ISOL EA0229 - contacts sticking on switch [CANN] 66kV TFR1-TFR2 TIE ISOL EA0229 - Sticky contacts on switch |  |  | 66 | 1 | 0 |  | 0 |  | 0 |  | 13 | 4 | 12 | 4 |  |  |  | 4 | 0 |  | HAYCOLEC | 930 | 1999

## Version Info
This workbook is created as a cut down version of the full data set only showing the failures. The information is copy and past of filtered data from Ergon WO 23_24_RIN_Revised V2.xlsx