## Summary
Analysis Summary
| Data Source | From Grid Planning and Optimisation Team
| VCR Used | 53.47 | $/kWh
Asset : Poles
| Financial Year | 2021/22 | 2022/23 | 2023/24
| Reliability Cost (Failures) | 11294251.9664 | 20706764.7868 | 19548899.6555
Asset : Pole Tops
| Financial Year | 2021/22 | 2022/23 | 2023/24
| Reliability Cost (Failures) | 13223025.0298 | 11635255.5548 | 3000398.1868
Methodology
Grid Planning and Optimisation team gathers the Consumption Days and Total feeder consumption from the retailer.
Using Consumption Days and Total Energy Consumption, kWh per min is calculated for each feeder.
Eg, In Rolleston Feeder
Consumption Days |  |  | = | 443173
Minutes per Day |  |  | = | 1440
Total Energy Consumption (kWh) |  |  | = | 17623823
Therefore,
Feeder kWh per min |  |  | = | 0.027616
The outage caused by pole failure during 21CA10056 outage,
Total Customer Minutes Lost (min) |  |  | = | 1526.9667
Therefore,
Energy not delivered during the failure (kWh) |  |  | = | 42.1691

## Energy not Delivered
[14 empty] | VCR Used ($/kWh) |  | 53.47
EVENT_YEAR | REGULATOR | OUTAGE_TYPE_GROUP | OUTAGE_NAME | FEEDER_ID | FEEDER_NO | FEEDER_DESCRIPTION | FEEDER_CATEGORY | ZONE_SUB_ID | ZONE_SUB_ASSET_NO | ZONE_SUB_ASSET_NAME | CUSTOMER_MINUTES | CUSTOMERS_INTERRUPTED | KWH_PER_MIN | Energy Not Supplied kWh | Asset | Reliability Cost
2021_2022 | AER | UNPLANNED | 21CA10056 | 40001009 | EM246 | Rolleston | LR | 40017951 | EMER | EMERALD 66/22KV SUB (EMSS) | 1526.9667 | 19 | 0.027616 | 42.1691 | Pole | 2254.7794
2021_2022 | AER | UNPLANNED | 21CA10434 | 40001038 | BW220 | Duaringa | LR | 40000019 | BLAC | BLACKWATER BWBS 132/66/22KV SUB (T032) | 8901.55 | 247 | 0.04454 | 396.4728 | Pole Top | 21199.402
2021_2022 | AER | UNPLANNED | 21CA11133 | 40001207 | LM104 | LM104 Boynedale | SR | 40018005 | LITT | LITTLEMORE 66/11KV SUB (LMSS) | 216 | 2 | 0.014629 | 3.1599 | Pole Top | 168.9597
2021_2022 | AER | UNPLANNED | 21CA11450 | 40001038 | BW220 | Duaringa | LR | 40000019 | BLAC | BLACKWATER BWBS 132/66/22KV SUB (T032) | 27784 | 404 | 0.04454 | 1237.4925 | Pole | 66168.7218
2021_2022 | AER | UNPLANNED | 21CA11893 | 40001038 | BW220 | Duaringa | LR | 40000019 | BLAC | BLACKWATER BWBS 132/66/22KV SUB (T032) | 673.3 | 1 | 0.04454 | 29.9886 | Pole Top | 1603.4912
2021_2022 | AER | UNPLANNED | 21CA13074 | 40001011 | EM244 | Foley Road | LR | 40017951 | EMER | EMERALD 66/22KV SUB (EMSS) | 76251.85 | 57 | 0.066682 | 5084.6025 | Pole | 271873.6977
2021_2022 | AER | UNPLANNED | 21CA13075 | 40223073 | ROLE-FA0752 | ORION | LR | 40222084 | ROLE | Rolleston 132/66/22kV Substation | 78093.25 | 71 | 0.030643 | 2392.9971 | Pole | 127953.5558
2021_2022 | AER | UNPLANNED | 21CA13096 | 82563612 | EM256 | Rubyvale-Capella | LR | 40017951 | EMER | EMERALD 66/22KV SUB (EMSS) | 169896.95 | 1787 | 0.030462 | 5175.463 | Pole | 276732.0084
2021_2022 | AER | UNPLANNED | 21CA13256 | 40001060 | BB204 | Barcaldine | SR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 9873.5333 | 29 | 0.031121 | 307.2762 | Pole | 16430.0593
2021_2022 | AER | UNPLANNED | 21CA14545 | 40216323 | BK206 | Tambo | LR | 40018027 | BLAK | BLACKALL 66/22KV SUB (BKSS) | 31746.45 | 67 | 0.025858 | 820.8843 | Pole | 43892.6815
2021_2022 | AER | UNPLANNED | 21CA15243 | 40001063 | BB211 | Blackall Old | LR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 9935.1167 | 77 | 0.014225 | 141.3306 | Pole Top | 7556.9464
2021_2022 | AER | UNPLANNED | 21CA15671 | 40001038 | BW220 | Duaringa | LR | 40000019 | BLAC | BLACKWATER BWBS 132/66/22KV SUB (T032) | 11664.4 | 52 | 0.04454 | 519.5295 | Pole | 27779.2412
2021_2022 | AER | UNPLANNED | 21CA16026 | 40000984 | MT109 | Moonford | SR | 40017931 | MTSS | Monto 66/11kV Substation | 17699.2667 | 14 | 0.03687 | 652.5725 | Pole Top | 34893.0538
2021_2022 | AER | UNPLANNED | 21CA16416 | 40001030 | BF203 | Cooroorah (Oaky Ck Pumps) | SR | 40017971 | BEWE | BEDFORD WEIR 66/22KV SUB (BFSS) | 4089.6 | 16 | 0.47017 | 1922.7906 | Pole Top | 102811.6159
2021_2022 | AER | UNPLANNED | 21CA17199 | 40001060 | BB204 | Barcaldine | SR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 2465 | 29 | 0.031121 | 76.7138 | Pole Top | 4101.8848
2021_2022 | AER | UNPLANNED | 21CA17499 | 40216323 | BK206 | Tambo | LR | 40018027 | BLAK | BLACKALL 66/22KV SUB (BKSS) | 20154 | 44 | 0.025858 | 521.1323 | Pole | 27864.9456
2021_2022 | AER | UNPLANNED | 21FN10114 | 10020655 | 2KAT | KAIRI-TINAROO | SR | 10030331 | ATHE | Atherton 66/22kV Sub (ATHE) | 29822.2 | 108 | 0.04036 | 1203.623 | Pole Top | 64357.7225
2021_2022 | AER | UNPLANNED | 21FN10315 | 83031320 | CHILLAGOE | CHILLAGOE | SR | 83029417 | CHIA | CHILLAGOE 66/22KV SUBSTATION | 12710 | 155 | 0.032561 | 413.8505 | Pole Top | 22128.5846
2021_2022 | AER | UNPLANNED | 21FN10535 | 10020850 | 2BAR | BARRINE | SR | 10030331 | ATHE | Atherton 66/22kV Sub (ATHE) | 95778 | 782 | 0.016585 | 1588.4738 | Pole Top | 84935.6926
2021_2022 | AER | UNPLANNED | 21FN11793 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 12224.9333 | 8 | 0.07076 | 865.036 | Pole | 46253.4768
2021_2022 | AER | UNPLANNED | 21FN11978 | 10020767 | 2TT3 | TULLY TOWN NO3 | SR | 10030282 | TULL | TULLY 132/22KV SUBSTATION (TULL) | 20226.3333 | 173 | 0.032272 | 652.7524 | Pole Top | 34902.6692
2021_2022 | AER | UNPLANNED | 21FN12003 | 10020689 | 2TUM | TUMOULIN | SR | 10030280 | EVEL | Evelyn 66/22kV Substation | 12716 | 176 | 0.023861 | 303.4128 | Pole Top | 16223.4804
2021_2022 | AER | UNPLANNED | 21FN12058 | 10020670 | 2GIR | GILBERT RIVER | LR | 10030300 | GEOR | GEORGETOWN 132/66/22/6.6KV SUB (GEOR) | 14281.2 | 48 | 0.029301 | 418.4599 | Pole | 22375.051
2021_2022 | AER | UNPLANNED | 21FN12059 | 10020804 | 2KDA | KURANDA RANGE | SR | 10030288 | KAMERUNGA | Kamerunga 132/22kV Substation | 22023 | 178 | 0.017509 | 385.5953 | Pole Top | 20617.7789
2021_2022 | AER | UNPLANNED | 21FN13177 | 10020659 | 2HOP | HOPEVALE | LR | 10030297 | COOK | Cooktown 66/22kV Substation | 4838.55 | 42 | 0.024948 | 120.7101 | Pole Top | 6454.3674
2021_2022 | AER | UNPLANNED | 21FN13373 | 10020755 | 2SMC | SMITHS CREEK | LR | 10030281 | MOGA | MT GARNET 66/22kV SUBSTATION | 344.0167 | 1 | 0.033197 | 11.4202 | Pole | 610.6378
2021_2022 | AER | UNPLANNED | 21FN13589 | 10020836 | 2ATR | ATHERTON ROAD | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 162 | 2 | 0.030523 | 4.9448 | Pole | 264.398
2021_2022 | AER | UNPLANNED | 21FN13663 | 81669225 | 2ROS | ROSSVILLE | SR | 10030293 | BLOO | BLOOMFIELD 22KV SWITCHING STATION | 4903.4667 | 10 | 0.013735 | 67.3469 | Pole Top | 3601.0364
2021_2022 | AER | UNPLANNED | 21FN13810 | 10132687 | 2KIP | KINGS PLAINS | SR | 10132681 | LAKE | Lakeland 132/66/22kV Substation | 9578.25 | 35 | 0.11097 | 1062.8564 | Pole Top | 56830.9322
2021_2022 | AER | UNPLANNED | 21FN14074 | 10020832 | 2CO3 | COOK NO 3 | UR | 10030288 | KAMERUNGA | Kamerunga 132/22kV Substation | 131817 | 595 | 0.032911 | 4338.1901 | Pole Top | 231963.027
2021_2022 | AER | UNPLANNED | 21FN14170 | 10020771 | 2CW2 | CARDWELL NO 2 | LR | 10030282 | TULL | TULLY 132/22KV SUBSTATION (TULL) | 650.25 | 5 | 0.045854 | 29.8165 | Pole Top | 1594.2909
2021_2022 | AER | UNPLANNED | 21FN14254 | 10020836 | 2ATR | ATHERTON ROAD | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 48100 | 325 | 0.030523 | 1468.1757 | Pole Top | 78503.3563
2021_2022 | AER | UNPLANNED | 21FN7259 | 10020837 | 2TAB | TABACUM | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 678.0667 | 4 | 0.051318 | 34.7971 | Pole Top | 1860.5983
2021_2022 | AER | UNPLANNED | 21FN7391 | 10020771 | 2CW2 | CARDWELL NO 2 | LR | 10030282 | TULL | TULLY 132/22KV SUBSTATION (TULL) | 7304 | 83 | 0.045854 | 334.9174 | Pole Top | 17908.036
2021_2022 | AER | UNPLANNED | 21FN8242 | 10020670 | 2GIR | GILBERT RIVER | LR | 10030300 | GEOR | GEORGETOWN 132/66/22/6.6KV SUB (GEOR) | 3860.8333 | 21 | 0.029301 | 113.128 | Pole | 6048.9555
2021_2022 | AER | UNPLANNED | 21FN8350 | 10020670 | 2GIR | GILBERT RIVER | LR | 10030300 | GEOR | GEORGETOWN 132/66/22/6.6KV SUB (GEOR) | 39678 | 34 | 0.029301 | 1162.623 | Pole | 62165.4534
2021_2022 | AER | UNPLANNED | 21FN8527 | 10020659 | 2HOP | HOPEVALE | LR | 10030297 | COOK | Cooktown 66/22kV Substation | 75672 | 792 | 0.024948 | 1887.8326 | Pole | 100942.4076
2021_2022 | AER | UNPLANNED | 21FN8614 | 10020846 | 2MOS | MOSSMAN | SR | 10030292 | MOSSMAN | Mossman 66/22kV Substation | 3706 | 34 | 0.035161 | 130.3078 | Pole Top | 6967.5568
2021_2022 | AER | UNPLANNED | 21FN8797 | 10020770 | 2TMI | TULLY MILL | SR | 10030282 | TULL | TULLY 132/22KV SUBSTATION (TULL) | 4503 | 1 | 0.16106 | 725.257 | Pole Top | 38779.4936
2021_2022 | AER | UNPLANNED | 21FN9258 | 10020836 | 2ATR | ATHERTON ROAD | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 981 | 9 | 0.030523 | 29.9435 | Pole Top | 1601.0768
2021_2022 | AER | UNPLANNED | 21FN9417 | 10020659 | 2HOP | HOPEVALE | LR | 10030297 | COOK | Cooktown 66/22kV Substation | 66467.7 | 342 | 0.024948 | 1658.2076 | Pole Top | 88664.3629
2021_2022 | AER | UNPLANNED | 21FN9553 | 10020847 | 2DAI | DAINTREE | SR | 10030292 | MOSSMAN | Mossman 66/22kV Substation | 16598 | 86 | 0.018716 | 310.6546 | Pole Top | 16610.7005
2021_2022 | AER | UNPLANNED | 21FN9602 | 10020774 | 2IN1 | INNISFAIL NO1 | SR | 10030283 | INNI | Innisfail 132/22kV Substation | 151717.8 | 1818 | 0.02416 | 3665.5085 | Pole Top | 195994.7384
2021_2022 | AER | UNPLANNED | 21FN9625 | 10020771 | 2CW2 | CARDWELL NO 2 | LR | 10030282 | TULL | TULLY 132/22KV SUBSTATION (TULL) | 35016.8 | 204 | 0.045854 | 1605.6595 | Pole Top | 85854.6161
2021_2022 | AER | UNPLANNED | 21FN9695 | 10020673 | 2NOR | NORMANTON | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 6524 | 14 | 0.044308 | 289.0641 | Pole | 15456.2597
2021_2022 | AER | UNPLANNED | 21MK4321 | 30053752 | 109 | QUEENS HILL | LR | 30064303 | LAQU | Laguna Quays 66/11kV Substation | 2940 | 42 | 0.01551 | 45.5988 | Pole Top | 2438.1704
2021_2022 | AER | UNPLANNED | 21MK5662 | 30053845 | 335 | ETON | SR | 30064338 | ETON | Eton 33/11kV Substation | 368 | 4 | 0.022826 | 8.4 | Pole Top | 449.1473
2021_2022 | AER | UNPLANNED | 21MK6854 | 30053747 | 104 | Kelsey Creek | SR | 83922970 | KECE | KELSEY CREEK EAST 66/11KV SUBSTATION | 7180.8 | 24 | 0.027603 | 198.2084 | Pole Top | 10598.2055
2021_2022 | AER | UNPLANNED | 21MK6956 | 83946269 | 4001 | WALKERSTON | SR | 30064316 | PLEY | Pleystowe 33/11kV Substation | 26934.15 | 111 | 0.017703 | 476.8211 | Pole Top | 25495.6267
2021_2022 | AER | UNPLANNED | 21MK7134 | 30053822 | 312 | RACECOURSE | SR | 30064327 | WEMA | West Mackay 33/11kV Substation | 58 | 2 | 0.031415 | 1.8221 | Pole Top | 97.4263
2021_2022 | AER | UNPLANNED | 21MK7692 | 30053848 | 338 | Mount Alice | SR | 30064299 | BALB | Balberra 33/11kV Substation | 26588.75 | 155 | 0.026828 | 713.3295 | Pole Top | 38141.7297
2021_2022 | AER | UNPLANNED | 21MK7962 | 30053745 | 102 | Strathdickie | SR | 83922970 | KECE | KELSEY CREEK EAST 66/11KV SUBSTATION | 3771 | 24 | 0.022141 | 83.4944 | Pole Top | 4464.448
2021_2022 | AER | UNPLANNED | 21MK8066 | 30053747 | 104 | Kelsey Creek | SR | 83922970 | KECE | KELSEY CREEK EAST 66/11KV SUBSTATION | 2446.95 | 9 | 0.027603 | 67.5421 | Pole Top | 3611.4749
2021_2022 | AER | UNPLANNED | 21NQ10176 | 20011545 | RL-01 | Rangelands SWER No.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 24582.15 | 33 | 0.043637 | 1072.6969 | Pole | 57357.101
2021_2022 | AER | UNPLANNED | 21NQ10306 | 20001859 | BA-01 | Bambaroo No.01 | SR | 20001858 | BAMB | BAMBAROO 66/11KV SUBSTATION | 3650.5333 | 88 | 0.02207 | 80.568 | Pole Top | 4307.9693
2021_2022 | AER | UNPLANNED | 21NQ10306 | 20005787 | FX-01 | MOUNTFOX NO.1 | SR | 20005786 | MOFO | Mt Fox 66/11kV Substation | 46176.7167 | 47 | 0.010759 | 496.814 | Pole Top | 26564.6458
2021_2022 | AER | UNPLANNED | 21NQ10306 | 20006383 | GR-02 | GREENVALE NO.02 | LR | 20006382 | GREN | GREENVALE 66/11KV SUB (GR) | 79059.8333 | 175 | 0.025381 | 2006.6152 | Pole Top | 107293.7166
2021_2022 | AER | UNPLANNED | 21NQ10306 | 20010961 | MU-01 | MUTARNEE NO.01 | SR | 20010960 | MUTA | MUTARNEE 66/11KV SUB (MU) | 8587.05 | 207 | 0.019152 | 164.458 | Pole Top | 8793.57
2021_2022 | AER | UNPLANNED | 21NQ10306 | 84653782 | BA-02 | BAMBAROO NO 2 | SR | 20001858 | BAMB | BAMBAROO 66/11KV SUBSTATION | 2323.0667 | 56 | 0.022861 | 53.1072 | Pole Top | 2839.6437
2021_2022 | AER | UNPLANNED | 21NQ10570 | 82962940 | CLSO-05 | CLARESOUTH NO.05 | SR | 82961890 | CLSO | CLARESOUTH T193 132/66/11KV SUBSTATION | 1520 | 10 | 0.15141 | 230.1473 | Pole | 12305.9777
2021_2022 | AER | UNPLANNED | 21NQ11016 | 20001649 | AY-04 | AYR NO.04 | SR | 20001223 | AYRZ | Ayr 66/11kV Sub (AYRZ) | 1319 | 15 | 0.040354 | 53.2274 | Pole Top | 2846.0675
2021_2022 | AER | UNPLANNED | 21NQ11242 | 20005133 | DR-12 | DUCHESSRD NO.12 | LR | 20005132 | DURO | DUCHESS RD 132/11KV SUBSTATION | 5075.7 | 6 | 0.027968 | 141.959 | Pole | 7590.5492
2021_2022 | AER | UNPLANNED | 21NQ11338 | 20008686 | JC-11 | JULIACREEK NO.11 ORINDI | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 14066.6667 | 50 | 0.037237 | 523.7952 | Pole | 28007.3277
2021_2022 | AER | UNPLANNED | 21NQ11470 | 20013273 | 1213 | WOSO-01 | SR | 84555017 | WOSO | WOODSTOCK SOUTH 66/11KV SUB (WOSO) | 12730 | 67 | 0.020524 | 261.2717 | Pole | 13970.2004
2021_2022 | AER | UNPLANNED | 21NQ11966 | 20003294 | CB-03 | CRANBROOK NO.03 | UR | 20003280 | CRAN | CRANBROOK 66/11KV SUB (CB) | 23808 | 93 | 0.020795 | 495.0864 | Pole | 26472.2688
2021_2022 | AER | UNPLANNED | 21NQ12115 | 20007716 | HU-30 | TOWN | SR | 20007579 | HUGH | HUGHENDEN 66/33/6.6KV SUBSTATION | 9487 | 53 | 0.033881 | 321.4313 | Pole | 17186.9337
2021_2022 | AER | UNPLANNED | 21NQ12606 | 20006350 | GL-01 | GUTHALUNGRA NO.01 | SR | 20006349 | GUTH | GUTHALUNGRA 66/11KV SUB (GUTH) | 16917.7333 | 248 | 0.013536 | 229.0069 | Pole Top | 12244.9973
2021_2022 | AER | UNPLANNED | 21NQ12606 | 20006478 | GU-01 | GUMLU NO.01 | SR | 20006477 | GUML | GUMLU 66/11KV SUBSTATION | 3615.4833 | 53 | 0.068526 | 247.7562 | Pole Top | 13247.5253
2021_2022 | AER | UNPLANNED | 21NQ12606 | 20006518 | GU-02 | GUMLU NO.02 | SR | 20006477 | GUML | GUMLU 66/11KV SUBSTATION | 12006.1333 | 176 | 0.035006 | 420.2862 | Pole Top | 22472.7038
2021_2022 | AER | UNPLANNED | 21NQ12954 | 82564200 | MILC-11 | MILLCHESTER NO.11 | SR | 20010917 | MILC | Millchester 132/66/11kV Substation | 6426 | 102 | 0.021481 | 138.0352 | Pole Top | 7380.7416
2021_2022 | AER | UNPLANNED | 21NQ13475 | 25273362 | ALSH-04 | ALANSHERRIFF NO.04 | SR | 25268187 | ALSH | Alan Sherriff 132/11kV Substation | 288414.4 | 918 | 0.022719 | 6552.5382 | Pole Top | 350364.2184
2021_2022 | AER | UNPLANNED | 21NQ13538 | 20007634 | HU-20 | TORRENS CK | LR | 20007579 | HUGH | HUGHENDEN 66/33/6.6KV SUBSTATION | 203065.5 | 186 | 0.024974 | 5071.4392 | Pole | 271169.8558
2021_2022 | AER | UNPLANNED | 21NQ13615 | 25280514 | BN-08 | BOWEN NO.08 | SR | 20002433 | BOWE | BOWEN 66/11KV SUBSTATION | 3066 | 42 | 0.021745 | 66.6703 | Pole Top | 3564.8592
2021_2022 | AER | UNPLANNED | 21NQ14060 | 25268413 | JC-01 | JULIACREEK NO.01 TRIPLEX | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 10806.95 | 9 | 0.029115 | 314.6438 | Pole | 16824.004
2021_2022 | AER | UNPLANNED | 21NQ14273 | 20006518 | GU-02 | GUMLU NO.02 | SR | 20006477 | GUML | GUMLU 66/11KV SUBSTATION | 2831 | 19 | 0.035006 | 99.1019 | Pole Top | 5298.977
2021_2022 | AER | UNPLANNED | 21NQ14692 | 25276003 | RI-80 | Barabon Quarry 33kV Feeder | LR | 20011486 | RI | Richmond 66/33/19.1kV Substation | 16097 | 13 | 0.032953 | 530.4376 | Pole | 28362.4971
2021_2022 | AER | UNPLANNED | 21NQ14705 | 82962852 | CLSO-02 | CLARESOUTH NO.02 | SR | 82961890 | CLSO | CLARESOUTH T193 132/66/11KV SUBSTATION | 41736.5333 | 146 | 0.092952 | 3879.4793 | Pole Top | 207435.7586
2021_2022 | AER | UNPLANNED | 21NQ14855 | 20013230 | WI-01 | TOWN NO.01 | SR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 13953 | 348 | 0.030201 | 421.3943 | Pole Top | 22531.9508
2021_2022 | AER | UNPLANNED | 21NQ14968 | 20003949 | CR-01 | CAPERIVER NO.01 | LR | 20003948 | CARI | Cape River C 66/11kV Substation | 47586.7 | 42 | 0.019197 | 913.5246 | Pole Top | 48846.1595
2021_2022 | AER | UNPLANNED | 21NQ15530 | 84041077 | LANN-02 | LANNERCOST NO.02 | SR | 20009097 | LANN | Lannercost 66/11kV Substation | 21002.6667 | 172 | 0.016812 | 353.093 | Pole Top | 18879.8838
2021_2022 | AER | UNPLANNED | 21NQ15630 | 20007634 | HU-20 | TORRENS CK | LR | 20007579 | HUGH | HUGHENDEN 66/33/6.6KV SUBSTATION | 14740 | 110 | 0.024974 | 368.1227 | Pole | 19683.5192
2021_2022 | AER | UNPLANNED | 21NQ15838 | 20012587 | ST05 | SERENE VALLEY | SR | 20012369 | STUA | Stuart 66/11kV Substation | 26289 | 207 | 0.017887 | 470.2294 | Pole Top | 25143.1665
2021_2022 | AER | UNPLANNED | 21NQ15894 | 25280514 | BN-08 | BOWEN NO.08 | SR | 20002433 | BOWE | BOWEN 66/11KV SUBSTATION | 4252.75 | 15 | 0.021745 | 92.4762 | Pole | 4944.7015
2021_2022 | AER | UNPLANNED | 21NQ15901 | 25268413 | JC-01 | JULIACREEK NO.01 TRIPLEX | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 28017.0833 | 19 | 0.029115 | 815.716 | Pole | 43616.3323
2021_2022 | AER | UNPLANNED | 21NQ15911 | 25273297 | GE-01 | CORFIELD SWER | LR | 25267919 | GLEE | GLENELG 66/19.1KV SUB (GLEE) | 10743.5167 | 11 | 0.033779 | 362.9098 | Pole | 19404.7891
2021_2022 | AER | UNPLANNED | 21NQ15921 | 20011545 | RL-01 | Rangelands SWER No.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 5368.3333 | 5 | 0.043637 | 234.2592 | Pole | 12525.8383
2021_2022 | AER | UNPLANNED | 21NQ15925 | 20011824 | RN-01 | Richmond Nth SWER No.01 | LR | 20011486 | RI | Richmond 66/33/19.1kV Substation | 26792.7333 | 31 | 0.029793 | 798.2362 | Pole | 42681.6877
2021_2022 | AER | UNPLANNED | 21NQ16355 | 25267897 | AS-01 | Apsley SWER No.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 45033.9 | 43 | 0.027515 | 1239.0978 | Pole | 66254.5583
2021_2022 | AER | UNPLANNED | 21NQ8645 | 20009035 | KE-02 | KIRKNIE NO.02 | SR | 20009031 | KIRK | KIRKNIE 66/11KV SUBSTATION | 286 | 2 | 0.1187 | 33.9487 | Pole Top | 1815.2348
2021_2022 | AER | UNPLANNED | 21NQ8983 | 82843815 | AV-02 | AITKENVALE NO.02 | UR | 20001079 | AITK | AITKENVALE 66/11KV SUBSTATION (AITK) | 20580 | 173 | 0.029017 | 597.1631 | Pole | 31930.3107
2021_2022 | AER | UNPLANNED | 21NQ9121 | 20004307 | CT-03 | YORK ST | LR | 20004053 | CHTO | CHARTERSTOWERS 66/11KV SUBSTATION | 1308.4 | 15 | 0.072396 | 94.7224 | Pole Top | 5064.8075
2021_2022 | AER | UNPLANNED | 21NQ9994 | 20011598 | RASM-04 | RASMUSSEN NO.04 | SR | 20011587 | RASM | Rasmussen 66/11kV Substation | 27993 | 147 | 0.021727 | 608.2148 | Pole Top | 32521.2433
2021_2022 | AER | UNPLANNED | 21SW10055 | 84668557 | 14069 | SWAN CREEK | SR | 84536204 | WAEA | WARWICK EAST 33/11KV SUB | 47297.85 | 549 | 0.0167 | 789.8906 | Pole | 42235.4521
2021_2022 | AER | UNPLANNED | 21SW10084 | 60026844 | F4645 | WILLOWBURN | SR | 60007227 | ME020 | North Street 33/11kV Substation | 6732.6 | 98 | 0.015868 | 106.8312 | Pole Top | 5712.2661
2021_2022 | AER | UNPLANNED | 21SW10165 | 60026815 | F4035 | ROCKY CREEK | SR | 60007244 | MILM | MILLMERRAN 33/11KV SUB | 7946 | 14 | 0.035091 | 278.8309 | Pole Top | 14909.0875
2021_2022 | AER | UNPLANNED | 21SW10735 | 60026735 | F2685 | DALVEEN | SR | 60007243 | ME117 | Pozieres 33/11kV Substation |  |  | 0.022834 |  | Pole Top | 0
2021_2022 | AER | UNPLANNED | 21SW10735 | 60026802 | F3890 | PASSCHENDAELE | SR | 60007243 | ME117 | Pozieres 33/11kV Substation |  |  | 0.06612 |  | Pole Top | 0
2021_2022 | AER | UNPLANNED | 21SW10735 | 60026830 | F4370 | THULIMBAH | SR | 60007243 | ME117 | Pozieres 33/11kV Substation |  |  | 0.04368 |  | Pole Top | 0
2021_2022 | AER | UNPLANNED | 21SW11181 | 60026697 | F200C | PARTRIDGE STREET | SR | 60007255 | CHAR | CHARLEVILLE 66/22/11KV SUB | 636 | 6 | 0.038887 | 24.7324 | Pole | 1322.4431
2021_2022 | AER | UNPLANNED | 21SW11599 | 60026712 | F2295 | BRINGALILY | LR | 60007244 | MILM | MILLMERRAN 33/11KV SUB | 492 | 4 | 0.033537 | 16.5004 | Pole Top | 882.2789
2021_2022 | AER | UNPLANNED | 21SW12686 | 60026675 | F077S | MAIN CAMP | LR | 60007215 | SAGE | ST GEORGE (MC052) 66/33KV SUB (SAGE) | 87136 | 392 | 0.037521 | 3269.4556 | Pole | 174817.7916
2021_2022 | AER | UNPLANNED | 21SW12695 | 60026758 | F3085 | HENDON | SR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 444 | 3 | 0.028604 | 12.7001 | Pole Top | 679.072
2021_2022 | AER | UNPLANNED | 21SW12764 | 60026675 | F077S | MAIN CAMP | LR | 60007215 | SAGE | ST GEORGE (MC052) 66/33KV SUB (SAGE) | 73889.1667 | 392 | 0.037521 | 2772.4173 | Pole | 148241.1511
2021_2022 | AER | UNPLANNED | 21SW13719 | 82907503 | F2787 | ECHO VALLEY | SR | 60331401 | KESP | KEARNEYS SPRINGS 110/11KV SUB (KESP) | 18645.5333 | 113 | 0.018933 | 353.0243 | Pole Top | 18876.2115
2021_2022 | AER | UNPLANNED | 21SW14035 | 84667056 | 14066 | HIGH ST | SR | 60007241 | EATO | EAST TOOWOOMBA 33/11KV SUB | 23328 | 96 | 0.011639 | 271.5083 | Pole | 14517.5462
2021_2022 | AER | UNPLANNED | 21SW14421 | 60026686 | F112R | TIMBURY HILLS | SR | 60007250 | MW002 | Roma East 33/11kV Substation | 6688 | 19 | 0.038789 | 259.4213 | Pole | 13871.2579
2021_2022 | AER | UNPLANNED | 21SW15812 | 60026786 | F3505 | MERINGANDAN | SR | 60007235 | MERN | MERINGANDAN 33/11KV SUB (ME062) | 7303 | 67 | 0.019792 | 144.54 | Pole Top | 7728.556
2021_2022 | AER | UNPLANNED | 21SW15871 | 60322052 | F086S | ALFRED STREET EAST | SR | 60007216 | SAGT | SAINT GEORGE TOWN 33/11KV SUB | 4762.7 | 97 | 0.024974 | 118.9442 | Pole Top | 6359.948
2021_2022 | AER | UNPLANNED | 21SW15962 | 60026703 | F2085 | APPLETHORPE | SR | 60007222 | STTO | STANTHORPE TOWN 33/11KV SUB | 11588.4 | 87 | 0.025439 | 294.7924 | Pole Top | 15762.5473
2021_2022 | AER | UNPLANNED | 21SW16189 | 60026743 | F2880 | FORMARTIN | SR | 60007238 | NORW | NORWIN 33/11KV SUB (ME074) | 430.2833 | 1 | 0.048235 | 20.7546 | Pole Top | 1109.7459
2021_2022 | AER | UNPLANNED | 21SW16311 | 60026816 | F4090 | ROSSVALE | LR | 60007248 | PURR | PURRAWUNDA 33/11KV SUB | 43383.6667 | 272 | 0.019674 | 853.5248 | Pole | 45637.9701
2021_2022 | AER | UNPLANNED | 21SW16592 | 60026766 | F315C | EULO | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 19014.95 | 19 | 0.018798 | 357.4376 | Pole | 19112.19
2021_2022 | AER | UNPLANNED | 21SW16738 | 60026666 | F049R | ROMA NORTH | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 5830.4667 | 19 | 0.025151 | 146.6404 | Pole | 7840.8619
2021_2022 | AER | UNPLANNED | 21SW16817 | 60026824 | F4185 | SOUTHBROOK | SR | 60007233 | BROX | BROXBURN 33/11KV SUB (ME057) | 23759.2 | 74 | 0.019622 | 466.2014 | Pole Top | 24927.7885
2021_2022 | AER | UNPLANNED | 21SW17031 | 83850831 | GRANADA | GRANADA | SR | 82709366 | SKIB | SKID B 33/11kV SUBSTATION | 10306.2333 | 38 | 0.021253 | 219.0389 | Pole Top | 11712.0074
2021_2022 | AER | UNPLANNED | 21SW17543 | 60026712 | F2295 | BRINGALILY | LR | 60007244 | MILM | MILLMERRAN 33/11KV SUB | 25417.4 | 154 | 0.033537 | 852.4359 | Pole Top | 45579.747
2021_2022 | AER | UNPLANNED | 21SW17698 | 60026747 | F2980 | GOOMBURRA | LR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 29425.2667 | 118 | 0.01983 | 583.5175 | Pole Top | 31200.6829
2021_2022 | AER | UNPLANNED | 21SW17857 | 60026666 | F049R | ROMA NORTH | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 285475.0333 | 549 | 0.025151 | 7179.9007 | Pole | 383909.289
2021_2022 | AER | UNPLANNED | 21SW17857 | 60026693 | F181R | DUBLIN STREET | SR | 60007254 | MITC | MITCHELL 33/11KV SUB | 165487.3 | 253 | 0.023839 | 3945.0631 | Pole | 210942.5262
2021_2022 | AER | UNPLANNED | 21SW17857 | 60026694 | F175R | MITCHELL HOSPITAL | SR | 60007254 | MITC | MITCHELL 33/11KV SUB | 218469.4 | 334 | 0.019063 | 4164.7525 | Pole | 222689.3148
2021_2022 | AER | UNPLANNED | 21SW17857 | 60026695 | F184R | MITCHELL RURAL | SR | 60007254 | MITC | MITCHELL 33/11KV SUB | 13082 | 20 | 0.10249 | 1340.7291 | Pole | 71688.7823
2021_2022 | AER | UNPLANNED | 21SW17857 | 60026696 | F187R | MUNGALLALA | LR | 60007254 | MITC | MITCHELL 33/11KV SUB | 120354.4 | 184 | 0.025295 | 3044.3848 | Pole | 162783.2536
2021_2022 | AER | UNPLANNED | 21SW18126 | 60026725 | F2530 | CLIFTON WEST | SR | 60007249 | CLIF | CLIFTON 33/11KV SUB (ME399) | 2265 | 15 | 0.023728 | 53.7447 | Pole Top | 2873.7285
2021_2022 | AER | UNPLANNED | 21SW18419 | 60026807 | F3930 | PILTON | SR | 60007249 | CLIF | CLIFTON 33/11KV SUB (ME399) | 42 | 1 | 0.02747 | 1.1537 | Pole Top | 61.6904
2021_2022 | AER | UNPLANNED | 21SW18430 | 60026794 | F3765 | NOBBY | LR | 60007240 | MOSI | MOUNT SIBLEY 33/11KV SUB | 8896.4 | 104 | 0.03051 | 271.4253 | Pole Top | 14513.1093
2021_2022 | AER | UNPLANNED | 21SW18925 | 60026733 | F2660 | CROWS NEST TOWN | LR | 60007231 | CRNE | CROWS NEST 33/11KV SUB (ME032) | 13246 | 74 | 0.017507 | 231.9042 | Pole | 12399.9156
2021_2022 | AER | UNPLANNED | 21SW19217 | 60026724 | F2525 | CLIFTON TOWN | SR | 60007249 | CLIF | CLIFTON 33/11KV SUB (ME399) | 7140 | 102 | 0.030867 | 220.3893 | Pole Top | 11784.2181
2021_2022 | AER | UNPLANNED | 21SW19220 | 111735271 | F3097 | HIGHFIELDS PUMP STATION | SR | 60007228 | HIGH | HIGHFIELDS 33/11KV SUB | 91 | 1 | 6.9444e-06 | 0.00063194 | Pole Top | 0.03379
2021_2022 | AER | UNPLANNED | 21SW19311 | 85206371 | 14114 | WILLI ST | SR | 60007247 | WEWA | WEST WARWICK 33/11KV SUB (WEWA) | 2160 | 12 | 0.015565 | 33.6202 | Pole Top | 1797.6706
2021_2022 | AER | UNPLANNED | 21SW19355 | 60026787 | F351C | CUNNAMULLA NORTH | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 137233.7333 | 146 | 0.01915 | 2628.0241 | Pole | 140520.4507
2021_2022 | AER | UNPLANNED | 21SW19546 | 60026824 | F4185 | SOUTHBROOK | SR | 60007233 | BROX | BROXBURN 33/11KV SUB (ME057) | 31034.05 | 189 | 0.019622 | 608.948 | Pole Top | 32560.4496
2021_2022 | AER | UNPLANNED | 21SW19682 | 60026888 | F058W | TAROOM | LR | 60007208 | WAND | WANDOAN 33/22KV SUB | 275449.1667 | 485 | 0.030357 | 8361.7767 | Pole | 447104.2013
2021_2022 | AER | UNPLANNED | 21SW19693 | 60026766 | F315C | EULO | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 165704.6833 | 49 | 0.018798 | 3114.8696 | Pole | 166552.0756
2021_2022 | AER | UNPLANNED | 21SW19725 | 60026718 | F2415 | CABARLAH | SR | 60007235 | MERN | MERINGANDAN 33/11KV SUB (ME062) | 2959.2333 | 13 | 0.026522 | 78.4861 | Pole Top | 4196.6511
2021_2022 | AER | UNPLANNED | 21SW19783 | 60026755 | F3060 | HARRIS STREET | LR | 60007222 | STTO | STANTHORPE TOWN 33/11KV SUB | 245217.05 | 1787 | 0.018894 | 4633.0313 | Pole Top | 247728.1836
2021_2022 | AER | UNPLANNED | 21SW19833 | 60026650 | F022R | BRUCEDALE | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 174431.5 | 584 | 0.026405 | 4605.9201 | Pole | 246278.5495
2021_2022 | AER | UNPLANNED | 21SW20091 | 60026718 | F2415 | CABARLAH | SR | 60007235 | MERN | MERINGANDAN 33/11KV SUB (ME062) | 87475.2 | 544 | 0.026522 | 2320.0557 | Pole Top | 124053.3793
2021_2022 | AER | UNPLANNED | 21SW20167 | 60026734 | F2661 | CROWS NEST INDUSTRIAL ROAD | LR | 60007231 | CRNE | CROWS NEST 33/11KV SUB (ME032) | 4691.05 | 7 | 0.018439 | 86.4981 | Pole Top | 4625.0526
2021_2022 | AER | UNPLANNED | 21SW20189 | 60026790 | F3535 | MILLMERRAN TOWN | SR | 60007244 | MILM | MILLMERRAN 33/11KV SUB | 4681.6667 | 53 | 0.020076 | 93.9887 | Pole | 5025.5748
2021_2022 | AER | UNPLANNED | 21SW9522 | 60026729 | F2620 | COPPS HILL | SR | 60007233 | BROX | BROXBURN 33/11KV SUB (ME057) | 574.2 | 3 | 0.06461 | 37.0988 | Pole Top | 1983.672
2021_2022 | AER | UNPLANNED | 21SW9571 | 60026742 | F2860 | EVERGREEN | SR | 60007239 | PERA | PERANGA 33/11KV SUB (ME075) | 32952.7 | 114 | 0.014348 | 472.7967 | Pole Top | 25280.4405
2021_2022 | AER | UNPLANNED | 21WB10500 | 50000127 | MG-E | REDGATE | LR | 50000121 | MURG | Murgon 66/11kV Substation | 4133 | 128 | 0.022065 | 91.1948 | Pole Top | 4876.1856
2021_2022 | AER | UNPLANNED | 21WB10944 | 50000168 | RS-H | BADDOW | SR | 50000162 | ROST | ROCKY STREET 66/11KV SUB (RS) | 152355.4833 | 349 | 0.062185 | 9474.2079 | Pole Top | 506585.8991
2021_2022 | AER | UNPLANNED | 21WB10961 | 84375978 | CH-D | ISIS | SR | 50000019 | CHIL | Childers 66/11kV Substation | 4324 | 46 | 0.025142 | 108.7135 | Pole Top | 5812.9106
2021_2022 | AER | UNPLANNED | 21WB11614 | 50000065 | GY-B | WETHERON | LR | 50000064 | GAYN | Gayndah 66/11kV Substation | 5081.0833 | 5 | 0.02095 | 106.4495 | Pole Top | 5691.8534
2021_2022 | AER | UNPLANNED | 21WB11781 | 50000129 | MG-G | GOOMERI | SR | 50000121 | MURG | Murgon 66/11kV Substation | 166 | 2 | 0.013898 | 2.3071 | Pole Top | 123.3597
2021_2022 | AER | UNPLANNED | 21WB11792 | 50000184 | SK-B | SOUTH BINGERA | SR | 50000181 | SOKO | SOUTH KOLAN 66/11KV SUB | 1092 | 14 | 0.020283 | 22.1488 | Pole Top | 1184.2943
2021_2022 | AER | UNPLANNED | 21WB11988 | 50000233 | WV-C | MORGANVILLE | SR | 50000231 | WALL | WALLAVILLE 66/11KV SUB | 226.5667 | 1 | 0.015196 | 3.4428 | Pole Top | 184.0865
2021_2022 | AER | UNPLANNED | 21WB12669 | 50000168 | RS-H | BADDOW | SR | 50000162 | ROST | ROCKY STREET 66/11KV SUB (RS) | 1758.1667 | 7 | 0.062185 | 109.3314 | Pole Top | 5845.9494
2021_2022 | AER | UNPLANNED | 21WB12900 | 50000020 | CH-C | STOCKYARD | SR | 50000019 | CHIL | Childers 66/11kV Substation | 12179.8667 | 101 | 0.016422 | 200.0136 | Pole Top | 10694.7261
2021_2022 | AER | UNPLANNED | 21WB12987 | 50000232 | WV-B | GIN GIN | SR | 50000231 | WALL | WALLAVILLE 66/11KV SUB | 4838.9333 | 16 | 0.02029 | 98.1827 | Pole Top | 5249.8303
2021_2022 | AER | UNPLANNED | 21WB13115 | 50000205 | WB-D | GEORGE ST | UR | 50000199 | WEBU | West Bundaberg 66/11kV Substation | 9873.5 | 62 | 0.039612 | 391.1054 | Pole Top | 20912.4038
2021_2022 | AER | UNPLANNED | 21WB13128 | 50000065 | GY-B | WETHERON | LR | 50000064 | GAYN | Gayndah 66/11kV Substation | 2709.5 | 5 | 0.02095 | 56.7644 | Pole Top | 3035.1946
2021_2022 | AER | UNPLANNED | 21WB13197 | 50000068 | GY-D | BINJOUR | SR | 50000064 | GAYN | Gayndah 66/11kV Substation | 3380.5333 | 14 | 0.018309 | 61.8957 | Pole | 3309.5634
2021_2022 | AER | UNPLANNED | 21WB13301 | 50000065 | GY-B | WETHERON | LR | 50000064 | GAYN | Gayndah 66/11kV Substation | 1476 | 9 | 0.02095 | 30.9224 | Pole Top | 1653.4221
2021_2022 | AER | UNPLANNED | 21WB13743 | 50000208 | WB-G | OAKWOOD | SR | 50000199 | WEBU | West Bundaberg 66/11kV Substation | 152.15 | 1 | 0.020296 | 3.088 | Pole | 165.1169
2021_2022 | AER | UNPLANNED | 21WB13799 | 50000167 | RS-G | NEPTUNE STREET | SR | 50000162 | ROST | ROCKY STREET 66/11KV SUB (RS) | 479.3667 | 1 | 0.029282 | 14.037 | Pole Top | 750.5603
2021_2022 | AER | UNPLANNED | 21WB13850 | 50000150 | OY-D | QWRC | SR | 50000147 | OWAN | OWANYILLA 66/11KV SUB | 68945.5 | 758 | 0.017423 | 1201.2573 | Pole Top | 64231.2296
2021_2022 | AER | UNPLANNED | 21WB13922 | 50000129 | MG-G | GOOMERI | SR | 50000121 | MURG | Murgon 66/11kV Substation |  |  | 0.013898 |  | Pole Top | 0
2021_2022 | AER | UNPLANNED | 21WB14133 | 50000011 | BD-D | MONOGIRILBY | SR | 50000010 | BODA | BOONDOOMBA DAM 66/11KV SUB | 897 | 13 | 0.016274 | 14.5982 | Pole Top | 780.5661
2021_2022 | AER | UNPLANNED | 21WB14265 | 50080259 | TN-D | POONA | SR | 50080257 | TUAN | TUAN 66/11KV SUB | 10117.8 | 54 | 0.023334 | 236.0875 | Pole Top | 12623.5961
2021_2022 | AER | UNPLANNED | 21WB14280 | 50000184 | SK-B | SOUTH BINGERA | SR | 50000181 | SOKO | SOUTH KOLAN 66/11KV SUB | 3006.3 | 16 | 0.020283 | 60.976 | Pole Top | 3260.3882
2021_2022 | AER | UNPLANNED | 21WB14359 | 50000050 | FF-E | KOWBI | SR | 50000045 | FF | Farnsfield 66/11kV Substation | 1128 | 12 | 0.02329 | 26.2709 | Pole Top | 1404.7053
2021_2022 | AER | UNPLANNED | 21WB6921 | 50000044 | EV-C | EIDSVOLD | LR | 50000042 | EIDS | EIDSVOLD 66/11KV SUB (EV) | 48686.2 | 101 | 0.018203 | 886.228 | Pole Top | 47386.6087
2021_2022 | AER | UNPLANNED | 21WB7560 | 50000129 | MG-G | GOOMERI | SR | 50000121 | MURG | Murgon 66/11kV Substation | 30633.0667 | 112 | 0.013898 | 425.741 | Pole Top | 22764.3731
2021_2022 | AER | UNPLANNED | 21WB8869 | 50000094 | KR-E | KUMBIA | LR | 50000087 | KING | Kingaroy 66/11kV Substation | 203.1 | 1 | 0.018099 | 3.6759 | Pole Top | 196.5482
2021_2022 | AER | UNPLANNED | 21WB9023 | 50000073 | HD-C | TAKURA | SR | 50000071 | HOWA | HOWARD 66/11KV SUB | 2059.5667 | 41 | 0.015022 | 30.9391 | Pole Top | 1654.3117
2021_2022 | AER | UNPLANNED | 21WB9046 | 50000129 | MG-G | GOOMERI | SR | 50000121 | MURG | Murgon 66/11kV Substation | 7045.4167 | 25 | 0.013898 | 97.9178 | Pole Top | 5235.6656
2021_2022 | AER | UNPLANNED | 21WB9133 | 84375978 | CH-D | ISIS | SR | 50000019 | CHIL | Childers 66/11kV Substation | 40853.2167 | 251 | 0.025142 | 1027.1267 | Pole Top | 54920.4666
2021_2022 | AER | UNPLANNED | 21WB9467 | 50000065 | GY-B | WETHERON | LR | 50000064 | GAYN | Gayndah 66/11kV Substation | 23320 | 265 | 0.02095 | 488.5576 | Pole Top | 26123.1733
2021_2022 | AER | UNPLANNED | 22CA0242 | 40001010 | CL204 | Capella | LR | 40000023 | CLER | CLERMONT 132/66/22/11KV SUB (T071) CLBS | 38163.7 | 46 | 0.030403 | 1160.2766 | Pole | 62039.9919
2021_2022 | AER | UNPLANNED | 22CA0266 | 82563612 | EM256 | Rubyvale-Capella | LR | 40017951 | EMER | EMERALD 66/22KV SUB (EMSS) | 48509.6 | 104 | 0.030462 | 1477.7172 | Pole | 79013.5375
2021_2022 | AER | UNPLANNED | 22CA0658 | 40001208 | MV202 | Bororen | LR | 40018016 | MIVA | MIRIAM VALE MVSS 66/22KV SUB | 47765.75 | 693 | 0.012525 | 598.2563 | Pole Top | 31988.7658
2021_2022 | AER | UNPLANNED | 22CA0849 | 40001066 | LR204 | Morella | LR | 40017977 | LONG | LONGREACH 66/22KV SUB (LRSS) | 13396.4667 | 37 | 0.026454 | 354.3838 | Pole | 18948.9007
2022_2023 | AER | UNPLANNED | 22CA10793 | 40000973 | THEO-FA10 | Theodore Feeder | LR | 40017933 | THEO | Theodore 66/22kV Substation | 7041.5 | 15 | 0.028186 | 198.471 | Pole | 10612.2435
2022_2023 | AER | UNPLANNED | 22CA10891 | 40001090 | CN110 | Agnes St | UR | 40017970 | CNSS | Canning Street 66/11kV Substation | 2120 | 40 | 0.038212 | 81.0102 | Pole Top | 4331.6144
2022_2023 | AER | UNPLANNED | 22CA11833 | 84064137 | FB11 | SIMPSON ST | UR | 82566965 | BERS | BERSERKER 66/11KV SUBSTATION | 34959 | 271 | 0.019584 | 684.643 | Pole Top | 36607.8628
2022_2023 | AER | UNPLANNED | 22CA11885 | 40001111 | MA111 | Stanwell | LR | 40017988 | MALC | MALCHI MASS 66/11KV SUB | 684 | 6 | 0.022508 | 15.3958 | Pole Top | 823.2118
2022_2023 | AER | UNPLANNED | 22CA12490 | 40001063 | BB211 | Blackall Old | LR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 512 | 4 | 0.017703 | 9.0637 | Pole Top | 484.6382
2022_2023 | AER | UNPLANNED | 22CA12626 | 83877341 | FB15 | CLIFTON ST FDR | UR | 82566965 | BERS | BERSERKER 66/11KV SUBSTATION | 110940.6 | 1164 | 0.021439 | 2378.4439 | Pole Top | 127175.3929
2022_2023 | AER | UNPLANNED | 22CA12626 | 84064137 | FB11 | SIMPSON ST | UR | 82566965 | BERS | BERSERKER 66/11KV SUBSTATION | 2706.0833 | 35 | 0.019584 | 52.9964 | Pole Top | 2833.7174
2022_2023 | AER | UNPLANNED | 22CA12730 | 40001032 | BF208 | Yarrabee | SR | 40017971 | BEWE | BEDFORD WEIR 66/22KV SUB (BFSS) | 10860.1833 | 11 | 1.0637 | 11552.2439 | Pole | 617698.4815
2022_2023 | AER | UNPLANNED | 22CA12810 | 40000985 | MT103 | Selene | LR | 40017931 | MTSS | Monto 66/11kV Substation | 127753 | 644 | 0.021394 | 2733.0968 | Pole Top | 146138.6875
2021_2022 | AER | UNPLANNED | 22CA1286 | 40001003 | YP207 | Waterpark | SR | 40017948 | YPSS | Yeppoon 66/22/11kV Substation | 12021.6 | 97 | 0.025571 | 307.4046 | Pole Top | 16436.9227
2022_2023 | AER | UNPLANNED | 22CA12956 | 40001062 | BB210 | Alpha | LR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 651.8667 | 1 | 0.029454 | 19.2004 | Pole Top | 1026.645
2022_2023 | AER | UNPLANNED | 22CA13060 | 40001194 | GF111 | HOSPITAL TIE | UR | 40017981 | GFSS | Friend Street 66/11kV Substation | 16698 | 121 | 0.026622 | 444.537 | Pole Top | 23769.3957
2022_2023 | AER | UNPLANNED | 22CA13188 | 40216323 | BK206 | Tambo | LR | 40018027 | BLAK | BLACKALL 66/22KV SUB (BKSS) | 31307.6 | 24 | 0.024256 | 759.3906 | Pole | 40604.6154
2021_2022 | AER | UNPLANNED | 22CA1324 | 40000975 | THEO-FA06 | Cracow Town Feeder | LR | 40017933 | THEO | Theodore 66/22kV Substation | 28597.2 | 114 | 0.21604 | 6178.0603 | Pole Top | 330340.8828
2022_2023 | AER | UNPLANNED | 22CA13567 | 40001110 | MA108 | Gracemere Rural | SR | 40017988 | MALC | MALCHI MASS 66/11KV SUB | 5570.4 | 24 | 0.021652 | 120.608 | Pole Top | 6448.9078
2022_2023 | AER | UNPLANNED | 22CA13723 | 40216323 | BK206 | Tambo | LR | 40018027 | BLAK | BLACKALL 66/22KV SUB (BKSS) | 3341.4667 | 19 | 0.024256 | 81.0499 | Pole | 4333.7391
2022_2023 | AER | UNPLANNED | 22CA13822 | 40001061 | BB208 | Aramac | LR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 40531.4 | 34 | 0.021067 | 853.8841 | Pole | 45657.1822
2022_2023 | AER | UNPLANNED | 22CA13954 | 40001010 | CL204 | Capella | LR | 40000023 | CLER | CLERMONT 132/66/22/11KV SUB (T071) CLBS | 12852.5833 | 31 | 0.030197 | 388.1134 | Pole | 20752.4256
2022_2023 | AER | UNPLANNED | 22CA14419 | 40001176 | BR108 | Benaraby | SR | 40017973 | BRSS | Boyne Residential 66/11kV Substation | 57966.4667 | 170 | 0.025075 | 1453.4994 | Pole Top | 77718.6124
2021_2022 | AER | UNPLANNED | 22CA1522 | 40001177 | CI104 | CI104 Clinton Park | SR | 40017975 | CISS | Clinton 66/11kV Substation | 13264 | 120 | 0.018052 | 239.4438 | Pole Top | 12803.0626
2022_2023 | AER | UNPLANNED | 22CA15317 | 40001066 | LR204 | Morella | LR | 40017977 | LONG | LONGREACH 66/22KV SUB (LRSS) | 16222.15 | 17 | 0.027694 | 449.2637 | Pole | 24022.1309
2022_2023 | AER | UNPLANNED | 22CA15606 | 40223076 | ROLE-FA0652 | CRESCENT | LR | 40222084 | ROLE | Rolleston 132/66/22kV Substation | 100133.8 | 76 | 0.033717 | 3376.1709 | Pole | 180523.856
2022_2023 | AER | UNPLANNED | 22CA15641 | 40001009 | EM246 | Rolleston | LR | 40017951 | EMER | EMERALD 66/22KV SUB (EMSS) | 37145.1833 | 49 | 0.031041 | 1153.0083 | Pole | 61651.3564
2022_2023 | AER | UNPLANNED | 22CA15814 | 40000979 | WN213 | Gogango | LR | 40017934 | WOWA | WOWAN 66/22KV SUB (WNSS) | 122.95 | 1 | 0.022115 | 2.719 | Pole Top | 145.3856
2022_2023 | AER | UNPLANNED | 22CA15857 | 40001066 | LR204 | Morella | LR | 40017977 | LONG | LONGREACH 66/22KV SUB (LRSS) | 13045.25 | 29 | 0.027694 | 361.2812 | Pole | 19317.7047
2022_2023 | AER | UNPLANNED | 22CA15874 | 40001059 | BB203 | WESTERN HIGHWAY | SR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 6101.2 | 56 | 0.020688 | 126.2189 | Pole | 6748.9242
2022_2023 | AER | UNPLANNED | 22CA15994 | 40223073 | ROLE-FA0752 | ORION | LR | 40222084 | ROLE | Rolleston 132/66/22kV Substation | 38345.5 | 69 | 0.02683 | 1028.8143 | Pole | 55010.7016
2022_2023 | AER | UNPLANNED | 22CA16477 | 40001010 | CL204 | Capella | LR | 40000023 | CLER | CLERMONT 132/66/22/11KV SUB (T071) CLBS | 90952.75 | 385 | 0.030197 | 2746.5284 | Pole Top | 146856.8713
2022_2023 | AER | UNPLANNED | 22CA16529 | 40001246 | BL103 | Biloela North | SR | 40000001 | BILO | BILOELA 132/66/11KV SUB (BLBS) | 9272.8 | 140 | 0.15368 | 1425.0354 | Pole Top | 76196.6447
2021_2022 | AER | UNPLANNED | 22CA1858 | 40000999 | CL208 | Copperfield | SR | 40000023 | CLER | CLERMONT 132/66/22/11KV SUB (T071) CLBS | 16712.8 | 52 | 0.045401 | 758.7822 | Pole Top | 40572.0867
2021_2022 | AER | UNPLANNED | 22CA2389 | 40001118 | PD209 | ALTON DOWNS | LR | 40017986 | PAND | PANDOIN 66/22KV SUB (PDBS) | 11842 | 62 | 0.019594 | 232.0304 | Pole Top | 12406.6648
2021_2022 | AER | UNPLANNED | 22CA2648 | 82563612 | EM256 | Rubyvale-Capella | LR | 40017951 | EMER | EMERALD 66/22KV SUB (EMSS) | 43826.35 | 261 | 0.030462 | 1335.0543 | Pole Top | 71385.3536
2021_2022 | AER | UNPLANNED | 22CA2902 | 40216323 | BK206 | Tambo | LR | 40018027 | BLAK | BLACKALL 66/22KV SUB (BKSS) | 9907.6 | 67 | 0.025858 | 256.1859 | Pole | 13698.2602
2021_2022 | AER | UNPLANNED | 22CA3650 | 40000963 | CO203 | Lawgi | LR | 40017994 | COOM | COOMINGLAH 66/22KV SUB (COSS) | 0 | 0 | 0.012317 | 0 | Pole Top | 0
2021_2022 | AER | UNPLANNED | 22CA3652 | 82561111 | MA123 | GRACEMERE NORTH | SR | 40017988 | MALC | MALCHI MASS 66/11KV SUB | 250.2833 | 1 | 0.015713 | 3.9328 | Pole Top | 210.2875
2021_2022 | AER | UNPLANNED | 22CA4222 | 40000973 | THEO-FA10 | Theodore Feeder | LR | 40017933 | THEO | Theodore 66/22kV Substation | 137302 | 60 | 0.16966 | 23295.1919 | Pole | 1245593.9102
2021_2022 | AER | UNPLANNED | 22CA4467 | 40001066 | LR204 | Morella | LR | 40017977 | LONG | LONGREACH 66/22KV SUB (LRSS) | 34175.75 | 37 | 0.026454 | 904.0691 | Pole | 48340.5744
2021_2022 | AER | UNPLANNED | 22CA4470 | 40001066 | LR204 | Morella | LR | 40017977 | LONG | LONGREACH 66/22KV SUB (LRSS) | 17123.8167 | 13 | 0.026454 | 452.9853 | Pole | 24221.1256
2021_2022 | AER | UNPLANNED | 22CA4526 | 40000977 | WN211 | Jambin | LR | 40017934 | WOWA | WOWAN 66/22KV SUB (WNSS) | 9162.4333 | 34 | 0.017824 | 163.3121 | Pole Top | 8732.2958
2021_2022 | AER | UNPLANNED | 22CA4546 | 40001132 | RG111 | Knight St | UR | 40000002 | RGBS | Rockhampton Glenmore 132/66/11kV | 13690.6 | 66 | 0.022904 | 313.573 | Pole Top | 16766.7479
2021_2022 | AER | UNPLANNED | 22CA4725 | 40001118 | PD209 | ALTON DOWNS | LR | 40017986 | PAND | PANDOIN 66/22KV SUB (PDBS) | 15050.1 | 117 | 0.019594 | 294.8894 | Pole Top | 15767.7373
2021_2022 | AER | UNPLANNED | 22CA4782 | 40001034 | BW209 | QEC Coal Plant | SR | 40000019 | BLAC | BLACKWATER BWBS 132/66/22KV SUB (T032) | 9516.15 | 63 | 0.12658 | 1204.5968 | Pole Top | 64409.7889
2021_2022 | AER | UNPLANNED | 22CA5011 | 40001068 | LR210 | Isisford | LR | 40017977 | LONG | LONGREACH 66/22KV SUB (LRSS) | 18541.2 | 16 | 0.024394 | 452.2966 | Pole | 24184.2998
2021_2022 | AER | UNPLANNED | 22CA5087 | 40216323 | BK206 | Tambo | LR | 40018027 | BLAK | BLACKALL 66/22KV SUB (BKSS) | 43487.25 | 45 | 0.025858 | 1124.4722 | Pole | 60125.5262
2021_2022 | AER | UNPLANNED | 22CA5634 | 40001010 | CL204 | Capella | LR | 40000023 | CLER | CLERMONT 132/66/22/11KV SUB (T071) CLBS | 147396.45 | 244 | 0.030403 | 4481.2389 | Pole Top | 239611.8448
2021_2022 | AER | UNPLANNED | 22CA5929 | 40001046 | TI204 | Caravan Park | SR | 40017984 | TIER | TIERI 66/22KV SUBSTATION | 254.15 | 1 | 0.045207 | 11.4894 | Pole Top | 614.3376
2021_2022 | AER | UNPLANNED | 22CA6140 | 85221946 | TB223 | KINKA | SR | 40018029 | TANB | Tanby 66/22kV Substation | 44874 | 277 | 0.017026 | 764.0351 | Pole Top | 40852.9575
2021_2022 | AER | UNPLANNED | 22CA6174 | 40001061 | BB208 | Aramac | LR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 125809.5 | 510 | 0.021761 | 2737.7149 | Pole | 146385.6158
2021_2022 | AER | UNPLANNED | 22CA6191 | 40001215 | YP109 | Arthur St | UR | 40017948 | YPSS | Yeppoon 66/22/11kV Substation | 60576.3333 | 863 | 0.038965 | 2360.3865 | Pole Top | 126209.867
2021_2022 | AER | UNPLANNED | 22CA6401 | 40001014 | YP208 | Tanby | SR | 40017948 | YPSS | Yeppoon 66/22/11kV Substation | 15318.6667 | 66 | 0.015866 | 243.0397 | Pole Top | 12995.3336
2021_2022 | AER | UNPLANNED | 22CA6494 | 40000965 | MR201 | Moura Urban | SR | 40000028 | MOUR | MOURA MRBS 132/66/11KV SUB (T027) | 21804 | 158 | 0.13503 | 2944.2784 | Pole Top | 157430.5649
2021_2022 | AER | UNPLANNED | 22CA6890 | 40001139 | RL203 | Bajool | LR | 40017929 | RLSS | Raglan 66/22kV Substation | 720 | 12 | 0.040646 | 29.2652 | Pole Top | 1564.8097
2021_2022 | AER | UNPLANNED | 22CA6899 | 40001009 | EM246 | Rolleston | LR | 40017951 | EMER | EMERALD 66/22KV SUB (EMSS) | 499638.5 | 1416 | 0.027616 | 13798.1296 | Pole | 737785.9909
2021_2022 | AER | UNPLANNED | 22CA7855 | 85018902 | 14100 | PHILIP STREET | UR | 40000021 | GLSO | GLADSTONE SOUTH 132/66/11KV SUB (T019 ) | 2880 | 45 | 0.03193 | 91.9581 | Pole Top | 4916.9981
2021_2022 | AER | UNPLANNED | 22CA7895 | 40001111 | MA111 | Stanwell | LR | 40017988 | MALC | MALCHI MASS 66/11KV SUB | 12692 | 76 | 0.021247 | 269.6613 | Pole Top | 14418.7907
2021_2022 | AER | UNPLANNED | 22CA8397 | 40223076 | ROLE-FA0652 | CRESCENT | LR | 40222084 | ROLE | Rolleston 132/66/22kV Substation | 36432.6667 | 232 | 0.034885 | 1270.9373 | Pole | 67957.015
2021_2022 | AER | UNPLANNED | 22CA8515 | 40001208 | MV202 | Bororen | LR | 40018016 | MIVA | MIRIAM VALE MVSS 66/22KV SUB | 416 | 3 | 0.012525 | 5.2103 | Pole Top | 278.5956
2022_2023 | AER | UNPLANNED | 22CA9555 | 40223076 | ROLE-FA0652 | CRESCENT | LR | 40222084 | ROLE | Rolleston 132/66/22kV Substation | 18017.3 | 7 | 0.033717 | 607.482 | Pole | 32482.0637
2022_2023 | AER | UNPLANNED | 22CA9618 | 40000973 | THEO-FA10 | Theodore Feeder | LR | 40017933 | THEO | Theodore 66/22kV Substation | 5610 | 15 | 0.028186 | 158.1229 | Pole Top | 8454.8301
2022_2023 | AER | UNPLANNED | 22CA9905 | 40001208 | MV202 | Bororen | LR | 40018016 | MIVA | MIRIAM VALE MVSS 66/22KV SUB | 213472.2 | 499 | 0.015954 | 3405.7509 | Pole Top | 182105.5014
2021_2022 | AER | UNPLANNED | 22FN0157 | 10020771 | 2CW2 | CARDWELL NO 2 | LR | 10030282 | TULL | TULLY 132/22KV SUBSTATION (TULL) | 259.8167 | 1 | 0.045854 | 11.9136 | Pole Top | 637.0217
2021_2022 | AER | UNPLANNED | 22FN0158 | 10020673 | 2NOR | NORMANTON | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 15547.8 | 28 | 0.044308 | 688.8889 | Pole | 36834.8919
2021_2022 | AER | UNPLANNED | 22FN0222 | 10020771 | 2CW2 | CARDWELL NO 2 | LR | 10030282 | TULL | TULLY 132/22KV SUBSTATION (TULL) | 4830.7333 | 83 | 0.045854 | 221.5083 | Pole Top | 11844.0507
2021_2022 | AER | UNPLANNED | 22FN0373 | 84659987 | 2ART | ARTHUR ST FDR | SR | 82618594 | CANO | CAIRNS NORTH (T093) 132/22KV SUBSTATION | 9087.0667 | 68 | 0.041787 | 379.7249 | Pole Top | 20303.8907
2021_2022 | AER | UNPLANNED | 22FN0386 | 10020659 | 2HOP | HOPEVALE | LR | 10030297 | COOK | Cooktown 66/22kV Substation | 5124 | 28 | 0.024948 | 127.8314 | Pole Top | 6835.1424
2021_2022 | AER | UNPLANNED | 22FN0458 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 65978.85 | 63 | 0.07076 | 4668.6621 | Pole | 249633.3619
2022_2023 | AER | UNPLANNED | 22FN10117 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 61678 | 63 | 0.076656 | 4727.981 | Pole | 252805.1461
2022_2023 | AER | UNPLANNED | 22FN10377 | 10020827 | 2FRE | FRESHWATER | SR | 10030288 | KAMERUNGA | Kamerunga 132/22kV Substation | 250516.5167 | 1349 | 0.031714 | 7944.9842 | Pole Top | 424818.3058
2022_2023 | AER | UNPLANNED | 22FN10863 | 10020778 | 2BA2 | BABINDA NO2 | SR | 10030283 | INNI | Innisfail 132/22kV Substation | 20993 | 653 | 0.024165 | 507.2915 | Pole Top | 27124.8772
2022_2023 | AER | UNPLANNED | 22FN10903 | 10128810 | 2CHL | CHILVERTON | SR | 10128809 | RAVENSHOE | Ravenshoe 66/22kV Substation | 63619.6667 | 120 | 0.017796 | 1132.162 | Pole Top | 60536.7013
2022_2023 | AER | UNPLANNED | 22FN11054 | 10020771 | 2CW2 | CARDWELL NO 2 | LR | 10030282 | TULL | TULLY 132/22KV SUBSTATION (TULL) | 2829 | 23 | 0.040386 | 114.2506 | Pole Top | 6108.9806
2022_2023 | AER | UNPLANNED | 22FN11273 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 125648.1333 | 68 | 0.076656 | 9631.6676 | Pole | 515005.2645
2022_2023 | AER | UNPLANNED | 22FN11646 | 10020842 | 2KUR | KURANDA | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 898.3333 | 5 | 0.026931 | 24.1931 | Pole Top | 1293.6055
2022_2023 | AER | UNPLANNED | 22FN11730 | 83031323 | ALMADEN | ALMADEN | SR | 83029417 | CHIA | CHILLAGOE 66/22KV SUBSTATION | 14586.2167 | 13 | 1.4882 | 21706.6583 | Pole | 1160655.0206
2022_2023 | AER | UNPLANNED | 22FN12089 | 10020670 | 2GIR | GILBERT RIVER | LR | 10030300 | GEOR | GEORGETOWN 132/66/22/6.6KV SUB (GEOR) | 6913.4 | 16 | 0.088941 | 614.8839 | Pole | 32877.8405
2022_2023 | AER | UNPLANNED | 22FN12364 | 10020773 | 2BA1 | BABINDA NO1 | SR | 10030283 | INNI | Innisfail 132/22kV Substation | 1862 | 19 | 0.025954 | 48.3266 | Pole Top | 2584.0208
2022_2023 | AER | UNPLANNED | 22FN12825 | 10020773 | 2BA1 | BABINDA NO1 | SR | 10030283 | INNI | Innisfail 132/22kV Substation | 2079 | 21 | 0.025954 | 53.9586 | Pole Top | 2885.1661
2022_2023 | AER | UNPLANNED | 22FN12938 | 10020670 | 2GIR | GILBERT RIVER | LR | 10030300 | GEOR | GEORGETOWN 132/66/22/6.6KV SUB (GEOR) | 61284.3333 | 47 | 0.088941 | 5450.6824 | Pole | 291447.9904
2022_2023 | AER | UNPLANNED | 22FN13006 | 10020669 | 2EIN | EINASLEIGH | LR | 10030300 | GEOR | GEORGETOWN 132/66/22/6.6KV SUB (GEOR) | 1639 | 11 | 0.034351 | 56.3009 | Pole Top | 3010.4072
2021_2022 | AER | UNPLANNED | 22FN1301 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 3960.1333 | 8 | 0.07076 | 280.219 | Pole | 14983.3075
2022_2023 | AER | UNPLANNED | 22FN13076 | 10020806 | 2PEE | PEERAMON | LR | 10030331 | ATHE | Atherton 66/22kV Sub (ATHE) | 73012.0333 | 1690 | 0.018729 | 1367.4687 | Pole Top | 73118.5508
2022_2023 | AER | UNPLANNED | 22FN13187 | 10020767 | 2TT3 | TULLY TOWN NO3 | SR | 10030282 | TULL | TULLY 132/22KV SUBSTATION (TULL) | 800 | 10 | 0.032589 | 26.0713 | Pole Top | 1394.0339
2022_2023 | AER | UNPLANNED | 22FN13232 | 10020777 | 2IN2 | INNISFAIL NO2 | SR | 10030283 | INNI | Innisfail 132/22kV Substation | 33782.95 | 333 | 0.037889 | 1279.9967 | Pole Top | 68441.4215
2022_2023 | AER | UNPLANNED | 22FN13967 | 83864041 | 2KUB | KURRIMINE BEACH 22KV FDR | SR | 81642836 | ELAR | EL ARISH (T171) 132/22KV SUBSTATION | 4070.4 | 72 | 0.028885 | 117.5727 | Pole Top | 6286.6129
2021_2022 | AER | UNPLANNED | 22FN1878 | 10020671 | 2CRT | CROYDON TOWN | LR | 10030301 | CROYDON | Croydon 66/22kV Substation | 5937 | 8 | 0.03773 | 224.006 | Pole | 11977.5997
2021_2022 | AER | UNPLANNED | 22FN1977 | 10020659 | 2HOP | HOPEVALE | LR | 10030297 | COOK | Cooktown 66/22kV Substation | 117 | 1 | 0.024948 | 2.9189 | Pole | 156.0718
2021_2022 | AER | UNPLANNED | 22FN2033 | 10020765 | 2ELA | EL ARISH | SR | 10030282 | TULL | TULLY 132/22KV SUBSTATION (TULL) | 8792 | 70 | 0.017529 | 154.1172 | Pole Top | 8240.645
2021_2022 | AER | UNPLANNED | 22FN3360 | 10020755 | 2SMC | SMITHS CREEK | LR | 10030281 | MOGA | MT GARNET 66/22kV SUBSTATION | 1872 | 208 | 0.033197 | 62.1441 | Pole | 3322.8448
2021_2022 | AER | UNPLANNED | 22FN3667 | 10020850 | 2BAR | BARRINE | SR | 10030331 | ATHE | Atherton 66/22kV Sub (ATHE) | 42 | 1 | 0.016585 | 0.69657 | Pole Top | 37.2455
2021_2022 | AER | UNPLANNED | 22FN4029 | 10020803 | 2HS2 | HARTLEY ST NO 2 | UR | 10030286 | CACI | CAIRNS CITY 132/22KV SUB (CAIRNS CITY) | 23326 | 398 | 0.066903 | 1560.5744 | Pole Top | 83443.9153
2021_2022 | AER | UNPLANNED | 22FN5014 | 10020857 | 2WOL | WOLFRAM | SR | 10030295 | DIMB | Dimbulah 66/22kV Substation | 9315.7667 | 29 | 0.046995 | 437.7942 | Pole Top | 23408.8555
2021_2022 | AER | UNPLANNED | 22FN5158 | 10020775 | 2MAL | MALANDA | SR | 10030331 | ATHE | Atherton 66/22kV Sub (ATHE) | 76233.9667 | 478 | 0.032841 | 2503.5991 | Pole | 133867.4454
2021_2022 | AER | UNPLANNED | 22FN6216 | 10020836 | 2ATR | ATHERTON ROAD | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 7860 | 131 | 0.030523 | 239.914 | Pole Top | 12828.1992
2021_2022 | AER | UNPLANNED | 22FN7273 | 10020679 | 2BIL | BILYANA | SR | 10030303 | CARD | Cardwell 132/22kV Substation | 1474 | 22 | 0.019604 | 28.8957 | Pole Top | 1545.0553
2022_2023 | AER | UNPLANNED | 22FN8329 | 10020775 | 2MAL | MALANDA | SR | 10030331 | ATHE | Atherton 66/22kV Sub (ATHE) | 312 | 8 | 0.044769 | 13.9678 | Pole Top | 746.8591
2022_2023 | AER | UNPLANNED | 22FN9614 | 10020817 | 2CAR | CARBEEN | SR | 10030331 | ATHE | Atherton 66/22kV Sub (ATHE) | 817.2333 | 2 | 0.04134 | 33.7846 | Pole Top | 1806.4623
2022_2023 | AER | UNPLANNED | 22FN9634 | 10020841 | 2BIB | BIBOOHRA | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 73602 | 522 | 0.033016 | 2430.0791 | Pole Top | 129936.3287
2022_2023 | AER | UNPLANNED | 22FN9812 | 10020826 | 2BLW | BLUEWATER | SR | 10030288 | KAMERUNGA | Kamerunga 132/22kV Substation | 8335.65 | 61 | 0.023852 | 198.8196 | Pole Top | 10630.8823
2022_2023 | AER | UNPLANNED | 22FN9975 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 356 | 1 | 0.076656 | 27.2895 | Pole Top | 1459.1691
2021_2022 | AER | UNPLANNED | 22MK0022 | 30053771 | 203 | Southern (Sarina) | SR | 30064323 | SARI | Sarina 33/11kV Substation | 2596 | 22 | 0.031527 | 81.8429 | Pole Top | 4376.1396
2021_2022 | AER | UNPLANNED | 22MK0027 | 85068151 | 14102 | FOXDALE | SR | 83922970 | KECE | KELSEY CREEK EAST 66/11KV SUBSTATION | 74221.3333 | 196 | 0.020004 | 1484.7154 | Pole Top | 79387.7308
2021_2022 | AER | UNPLANNED | 22MK0241 | 30053837 | 327 | Farleigh | SR | 30064340 | FARL | Farleigh 33/11kV Substation | 5158.8 | 27 | 0.021059 | 108.6376 | Pole Top | 5808.855
2021_2022 | AER | UNPLANNED | 22MK0269 | 85068151 | 14102 | FOXDALE | SR | 83922970 | KECE | KELSEY CREEK EAST 66/11KV SUBSTATION | 14700 | 150 | 0.020004 | 294.0572 | Pole Top | 15723.2374
2021_2022 | AER | UNPLANNED | 22MK0399 | 30053745 | 102 | Strathdickie | SR | 83922970 | KECE | KELSEY CREEK EAST 66/11KV SUBSTATION | 74908 | 829 | 0.022141 | 1658.5526 | Pole Top | 88682.8086
2021_2022 | AER | UNPLANNED | 22MK0530 | 30053841 | 331 | Western (Pleystowe) | SR | 30064316 | PLEY | Pleystowe 33/11kV Substation | 37696.75 | 320 | 0.021295 | 802.7482 | Pole Top | 42922.9455
2021_2022 | AER | UNPLANNED | 22MK0900 | 85161016 | 14108 | NABILLA | SR | 84908972 | MASO | MARIAN SOUTH 66/11KV SUB (MASO) | 201669.7333 | 1156 | 0.019032 | 3838.1716 | Pole Top | 205227.0367
2021_2022 | AER | UNPLANNED | 22MK1237 | 30053864 | 354 | Finchhatton | SR | 30064314 | PINN | Pinnacle 66/11kV Substation | 4523.85 | 27 | 0.014468 | 65.4522 | Pole Top | 3499.7312
2021_2022 | AER | UNPLANNED | 22MK1250 | 30053837 | 327 | Farleigh | SR | 30064340 | FARL | Farleigh 33/11kV Substation | 3405.2 | 8 | 0.021059 | 71.7091 | Pole Top | 3834.2857
2021_2022 | AER | UNPLANNED | 22MK1332 | 85161016 | 14108 | NABILLA | SR | 84908972 | MASO | MARIAN SOUTH 66/11KV SUB (MASO) | 3996 | 36 | 0.019032 | 76.0517 | Pole Top | 4066.4865
2021_2022 | AER | UNPLANNED | 22MK1830 | 30053769 | 201 | Northern | SR | 30064323 | SARI | Sarina 33/11kV Substation | 312.9 | 3 | 0.018467 | 5.7783 | Pole Top | 308.9676
2021_2022 | AER | UNPLANNED | 22MK2211 | 30053865 | 355 | Mirani | SR | 30064307 | MIRA | Mirani 66/11kV Substation | 3720 | 20 | 0.02291 | 85.2265 | Pole Top | 4557.0626
2021_2022 | AER | UNPLANNED | 22MK2320 | 30053837 | 327 | Farleigh | SR | 30064340 | FARL | Farleigh 33/11kV Substation | 7380 | 41 | 0.021059 | 155.4132 | Pole Top | 8309.946
2021_2022 | AER | UNPLANNED | 22MK2430 | 30053822 | 312 | RACECOURSE | SR | 30064327 | WEMA | West Mackay 33/11kV Substation | 33817 | 522 | 0.031415 | 1062.3629 | Pole Top | 56804.5459
2021_2022 | AER | UNPLANNED | 22MK3584 | 30053820 | 310 | KEMMIS | UR | 30064327 | WEMA | West Mackay 33/11kV Substation | 265.95 | 1 | 0.023979 | 6.3771 | Pole Top | 340.986
2022_2023 | AER | UNPLANNED | 22MK5302 | 30053744 | 101 | Crystalbrook | SR | 83922970 | KECE | KELSEY CREEK EAST 66/11KV SUBSTATION | 3314.7333 | 14 | 0.018584 | 61.602 | Pole Top | 3293.8604
2022_2023 | AER | UNPLANNED | 22MK5995 | 30053862 | 352 | Gargett | SR | 30064314 | PINN | Pinnacle 66/11kV Substation | 25000.2333 | 133 | 0.014821 | 370.5191 | Pole | 19811.6572
2022_2023 | AER | UNPLANNED | 22MK6342 | 85068151 | 14102 | FOXDALE | SR | 83922970 | KECE | KELSEY CREEK EAST 66/11KV SUBSTATION | 2940 | 35 | 0.022137 | 65.0819 | Pole Top | 3479.9293
2022_2023 | AER | UNPLANNED | 22MK6522 | 30053837 | 327 | Farleigh | SR | 30064340 | FARL | Farleigh 33/11kV Substation | 2293.8 | 12 | 0.024614 | 56.4595 | Pole Top | 3018.8881
2022_2023 | AER | UNPLANNED | 22MK6847 | 30053822 | 312 | RACECOURSE | SR | 30064327 | WEMA | West Mackay 33/11kV Substation | 8067.25 | 35 | 0.033915 | 273.597 | Pole Top | 14629.2339
2022_2023 | AER | UNPLANNED | 22MK7664 | 30053745 | 102 | Strathdickie | SR | 83922970 | KECE | KELSEY CREEK EAST 66/11KV SUBSTATION | 144883.8667 | 692 | 0.025831 | 3742.5001 | Pole Top | 200111.4789
2022_2023 | AER | UNPLANNED | 22MK8555 | 30053774 | 206 | Louisa Creek | SR | 82837593 | LOCR | LOUISA CRK (T176) 132/33/11KV S'STN | 41478 | 388 | 0.025855 | 1072.3979 | Pole Top | 57341.116
2022_2023 | AER | UNPLANNED | 22MK8704 | 30053773 | 205 | Munbura | SR | 30064299 | BALB | Balberra 33/11kV Substation | 34713 | 133 | 0.018617 | 646.2481 | Pole Top | 34554.8863
2022_2023 | AER | UNPLANNED | 22MK9162 | 30053839 | 329 | Nebia | SR | 30064316 | PLEY | Pleystowe 33/11kV Substation | 2925 | 25 | 0.020817 | 60.8893 | Pole Top | 3255.75
2022_2023 | AER | UNPLANNED | 22MK9318 | 30053847 | 337 | BARRIE LANE | SR | 30064338 | ETON | Eton 33/11kV Substation | 186394.5833 | 399 | 0.023287 | 4340.5836 | Pole Top | 232091.0058
2021_2022 | AER | UNPLANNED | 22NQ0039 | 25268413 | JC-01 | JULIACREEK NO.01 TRIPLEX | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 33530 | 26 | 0.029115 | 976.2242 | Pole | 52198.7105
2021_2022 | AER | UNPLANNED | 22NQ0113 | 20011096 | MX-01 | MAXWELTON NTH SWER NO.01 19.1kV FDR | SR | 20011486 | RI | Richmond 66/33/19.1kV Substation | 22840.8 | 18 | 0.025202 | 575.6358 | Pole | 30779.2478
2021_2022 | AER | UNPLANNED | 22NQ0187 | 82914282 | BLRI-11 | BLACKRIVER NO.11 | SR | 20020706 | BLRI | BLACKRIVER 66/11KV SUBSTATION | 451.45 | 3 | 0.020726 | 9.3566 | Pole Top | 500.297
2021_2022 | AER | UNPLANNED | 22NQ0194 | 20008686 | JC-11 | JULIACREEK NO.11 ORINDI | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 63417.5 | 50 | 0.037237 | 2361.4536 | Pole | 126266.9222
2021_2022 | AER | UNPLANNED | 22NQ0212 | 20005412 | DR-10 | DUCHESSRD NO.10 | UR | 20005132 | DURO | DUCHESS RD 132/11KV SUBSTATION | 9663.1 | 71 | 0.020135 | 194.5681 | Pole Top | 10403.5563
2021_2022 | AER | UNPLANNED | 22NQ0387 | 20010480 | ML-02 | MILLAROO | SR | 20010443 | MILL | MILLAROO 66/11KV SUB (ML) | 1736.1833 | 1 | 0.1008 | 175.001 | Pole | 9357.3042
2021_2022 | AER | UNPLANNED | 22NQ0484 | 25273274 | GE-02 | VELLUM DOWNS | SR | 25267919 | GLEE | GLENELG 66/19.1KV SUB (GLEE) | 25742.85 | 21 | 0.029847 | 768.3465 | Pole | 41083.4849
2021_2022 | AER | UNPLANNED | 22NQ0540 | 20007736 | HU-40 | RICHMOND | LR | 20007579 | HUGH | HUGHENDEN 66/33/6.6KV SUBSTATION | 95116.4167 | 85 | 0.035272 | 3354.9032 | Pole Top | 179386.6749
2021_2022 | AER | UNPLANNED | 22NQ0543 | 25268413 | JC-01 | JULIACREEK NO.01 TRIPLEX | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 20729.7167 | 19 | 0.029115 | 603.5446 | Pole | 32271.5323
2021_2022 | AER | UNPLANNED | 22NQ0746 | 20020666 | SV-01 | Suvla SWER No.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 35507.0833 | 31 | 0.020778 | 737.774 | Pole | 39448.7778
2021_2022 | AER | UNPLANNED | 22NQ0749 | 20005133 | DR-12 | DUCHESSRD NO.12 | LR | 20005132 | DURO | DUCHESS RD 132/11KV SUBSTATION | 95384.1 | 78 | 0.027968 | 2667.7373 | Pole | 142643.9116
2021_2022 | AER | UNPLANNED | 22NQ0753 | 20008745 | JC-13 | JULIACREEK NO.13 TALDOORA | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 32248.2 | 36 | 0.056274 | 1814.7207 | Pole | 97033.1173
2022_2023 | AER | UNPLANNED | 22NQ10069 | 20009493 | LP-01 | MOUNTLEYSHONPUMP NO.01 | SR | 20009492 | MOLP | MOUNT LEYSHON PUMP 66/11KV SUB | 5116.5833 | 13 | 0.023258 | 119.0035 | Pole Top | 6363.1175
2022_2023 | AER | UNPLANNED | 22NQ10160 | 20004937 | NC-02 | NORTHCLONCURRY NO.02 | LR | 20004930 | NOCL | North Cloncurry 66/11kV Substation | 31206.25 | 55 | 0.035045 | 1093.6155 | Pole | 58475.6182
2022_2023 | AER | UNPLANNED | 22NQ10417 | 20001859 | BA-01 | Bambaroo No.01 | SR | 20001858 | BAMB | BAMBAROO 66/11KV SUBSTATION | 1183 | 91 | 0.020074 | 23.7481 | Pole Top | 1269.8094
2022_2023 | AER | UNPLANNED | 22NQ10417 | 20005787 | FX-01 | MOUNTFOX NO.1 | SR | 20005786 | MOFO | Mt Fox 66/11kV Substation | 12054 | 49 | 0.014238 | 171.6257 | Pole Top | 9176.8256
2022_2023 | AER | UNPLANNED | 22NQ10417 | 20006383 | GR-02 | GREENVALE NO.02 | LR | 20006382 | GREN | GREENVALE 66/11KV SUB (GR) | 47232 | 192 | 0.02723 | 1286.1455 | Pole Top | 68770.1995
2022_2023 | AER | UNPLANNED | 22NQ10417 | 20010961 | MU-01 | MUTARNEE NO.01 | SR | 20010960 | MUTA | MUTARNEE 66/11KV SUB (MU) | 2704 | 208 | 0.019875 | 53.7418 | Pole Top | 2873.5747
2022_2023 | AER | UNPLANNED | 22NQ10417 | 84653782 | BA-02 | BAMBAROO NO 2 | SR | 20001858 | BAMB | BAMBAROO 66/11KV SUBSTATION | 728 | 56 | 0.024143 | 17.5764 | Pole Top | 939.8085
2022_2023 | AER | UNPLANNED | 22NQ10427 | 20001263 | AY-06 | AYR NO.06 | SR | 20001223 | AYRZ | Ayr 66/11kV Sub (AYRZ) | 1472.0333 | 79 | 0.03277 | 48.2387 | Pole | 2579.3209
2022_2023 | AER | UNPLANNED | 22NQ10432 | 20013230 | WI-01 | TOWN NO.01 | SR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 3686.6667 | 5 | 0.030808 | 113.5791 | Pole | 6073.0745
2022_2023 | AER | UNPLANNED | 22NQ11019 | 25267901 | EL-01 | ELDERSLIESWER NO.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 40642.2 | 27 | 0.035429 | 1439.9281 | Pole | 76992.9576
2022_2023 | AER | UNPLANNED | 22NQ11093 | 25273362 | ALSH-04 | ALANSHERRIFF NO.04 | SR | 25268187 | ALSH | Alan Sherriff 132/11kV Substation | 121900.6167 | 927 | 0.026915 | 3280.8955 | Pole | 175429.4808
2022_2023 | AER | UNPLANNED | 22NQ11281 | 82561856 | MILC-09 | MILLCHESTER NO.09 | LR | 20010917 | MILC | Millchester 132/66/11kV Substation | 10730.4 | 9 | 0.028427 | 305.0309 | Pole | 16309.9998
2022_2023 | AER | UNPLANNED | 22NQ11409 | 20008686 | JC-11 | JULIACREEK NO.11 ORINDI | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 26871.5333 | 22 | 0.036913 | 991.8963 | Pole | 53036.694
2022_2023 | AER | UNPLANNED | 22NQ11410 | 20004937 | NC-02 | NORTHCLONCURRY NO.02 | LR | 20004930 | NOCL | North Cloncurry 66/11kV Substation | 22931.1 | 18 | 0.035045 | 803.6148 | Pole | 42969.2849
2022_2023 | AER | UNPLANNED | 22NQ11809 | 20010480 | ML-02 | MILLAROO | SR | 20010443 | MILL | MILLAROO 66/11KV SUB (ML) | 6500 | 50 | 0.072285 | 469.8553 | Pole Top | 25123.1609
2022_2023 | AER | UNPLANNED | 22NQ11870 | 20003792 | CO-01 | COLLINSVILLE NO.01 | SR | 20003791 | COLL | COLLINSVILLE SUBSTATION | 2552 | 44 | 0.024446 | 62.3853 | Pole Top | 3335.7402
2022_2023 | AER | UNPLANNED | 22NQ12222 | 20004937 | NC-02 | NORTHCLONCURRY NO.02 | LR | 20004930 | NOCL | North Cloncurry 66/11kV Substation | 3616.0333 | 14 | 0.035045 | 126.723 | Pole | 6775.8793
2021_2022 | AER | UNPLANNED | 22NQ1233 | 20003435 | CC-01 | CLONCURRY NO.01 | LR | 20003434 | CLON | CLONCURRY 66/11KV SUB (CC) | 36468.9 | 351 | 0.038494 | 1403.8407 | Pole Top | 75063.361
2022_2023 | AER | UNPLANNED | 22NQ12698 | 25273297 | GE-01 | CORFIELD SWER | LR | 25267919 | GLEE | GLENELG 66/19.1KV SUB (GLEE) | 8921.6 | 8 | 0.036849 | 328.755 | Pole | 17578.5279
2022_2023 | AER | UNPLANNED | 22NQ12730 | 25276003 | RI-80 | Barabon Quarry 33kV Feeder | LR | 20011486 | RI | Richmond 66/33/19.1kV Substation | 1621.25 | 5 | 0.032251 | 52.2863 | Pole | 2795.7501
2022_2023 | AER | UNPLANNED | 22NQ12854 | 20010961 | MU-01 | MUTARNEE NO.01 | SR | 20010960 | MUTA | MUTARNEE 66/11KV SUB (MU) | 3825 | 17 | 0.019875 | 76.0216 | Pole Top | 4064.8755
2022_2023 | AER | UNPLANNED | 22NQ12969 | 20008686 | JC-11 | JULIACREEK NO.11 ORINDI | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 51707 | 50 | 0.036913 | 1908.6362 | Pole | 102054.7768
2022_2023 | AER | UNPLANNED | 22NQ13389 | 20002652 | BN-06 | BOWEN NO.06 | SR | 20002433 | BOWE | BOWEN 66/11KV SUBSTATION | 2212 | 50 | 0.037873 | 83.7758 | Pole Top | 4479.4937
2022_2023 | AER | UNPLANNED | 22NQ13503 | 25268413 | JC-01 | JULIACREEK NO.01 TRIPLEX | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 15800.4 | 19 | 0.030315 | 478.9898 | Pole | 25611.5862
2022_2023 | AER | UNPLANNED | 22NQ13539 | 25268413 | JC-01 | JULIACREEK NO.01 TRIPLEX | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 3608.5 | 3 | 0.030315 | 109.3918 | Pole | 5849.1816
2021_2022 | AER | UNPLANNED | 22NQ1364 | 20010480 | ML-02 | MILLAROO | SR | 20010443 | MILL | MILLAROO 66/11KV SUB (ML) | 56 | 1 | 0.1008 | 5.6446 | Pole Top | 301.8166
2022_2023 | AER | UNPLANNED | 22NQ13771 | 20004307 | CT-03 | YORK ST | LR | 20004053 | CHTO | CHARTERSTOWERS 66/11KV SUBSTATION | 2021 | 8 | 0.064095 | 129.5351 | Pole Top | 6926.2404
2022_2023 | AER | UNPLANNED | 22NQ14115 | 25267901 | EL-01 | ELDERSLIESWER NO.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 16477.2333 | 11 | 0.035429 | 583.7782 | Pole | 31214.6224
2022_2023 | AER | UNPLANNED | 22NQ14126 | 20008784 | JC-08 | JULIACREEK NO.08 CANOBIE | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 8988.35 | 9 | 0.085077 | 764.6981 | Pole | 40888.4062
2022_2023 | AER | UNPLANNED | 22NQ14128 | 20008686 | JC-11 | JULIACREEK NO.11 ORINDI | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 63647.5 | 50 | 0.036913 | 2349.3902 | Pole | 125621.8966
2022_2023 | AER | UNPLANNED | 22NQ14172 | 20006383 | GR-02 | GREENVALE NO.02 | LR | 20006382 | GREN | GREENVALE 66/11KV SUB (GR) | 12210 | 74 | 0.02723 | 332.483 | Pole Top | 17777.8653
2022_2023 | AER | UNPLANNED | 22NQ14309 | 84653808 | 3220 | BELYANDO 19.1KV 3220 FDR | SR | 84484529 | WIRR | WIRRALIE 66/33KV SUB (WIRR) | 23714.4 | 18 | 0.067882 | 1609.7913 | Pole | 86075.5383
2022_2023 | AER | UNPLANNED | 22NQ14309 | 84653811 | 3221 | SCARTWATER 19.1KV 3221 FDR | SR | 84484529 | WIRR | WIRRALIE 66/33KV SUB (WIRR) | 11156.8333 | 10 | 0.036454 | 406.7075 | Pole | 21746.648
2022_2023 | AER | UNPLANNED | 22NQ14309 | 84653816 | 3222 | MT COOLOON 19.1KV 3222 FDR | SR | 84484529 | WIRR | WIRRALIE 66/33KV SUB (WIRR) | 29007.7667 | 26 | 0.039828 | 1155.311 | Pole | 61774.4789
2022_2023 | AER | UNPLANNED | 22NQ14391 | 82912329 | OONN-10 | OONOONBA NO.10 | SR | 82866131 | OONN | OONOONBA 66/11KV SUBSTATION | 21175 | 121 | 0.026522 | 561.6103 | Pole Top | 30029.3045
2022_2023 | AER | UNPLANNED | 22NQ14445 | 20003547 | CF-01 | CAPE FERGUSON NO.01 | UR | 20003546 | CAFE | CAPE FERGUSON 66/11KV SUB (CAFE) | 341.05 | 1 | 12.6068 | 4299.5454 | Pole Top | 229896.6952
2022_2023 | AER | UNPLANNED | 22NQ14445 | 20003550 | CF-02 | CAPE FERGUSON NO.02 | SR | 20003546 | CAFE | CAPE FERGUSON 66/11KV SUB (CAFE) | 118344.35 | 347 | 0.014611 | 1729.1873 | Pole Top | 92459.645
2022_2023 | AER | UNPLANNED | 22NQ14627 | 25267735 | IN-06 | Ingham No.06 | SR | 20007838 | INGH | INGHAM 132/66/11KV SUBSTATION | 34631.5 | 396 | 0.023253 | 805.296 | Pole Top | 43059.1792
2022_2023 | AER | UNPLANNED | 22NQ15349 | 20013453 | 1214 | WOSO-02 | SR | 84555017 | WOSO | WOODSTOCK SOUTH 66/11KV SUB (WOSO) | 65221.0833 | 70 | 0.025001 | 1630.57 | Pole Top | 87186.5806
2022_2023 | AER | UNPLANNED | 22NQ15747 | 20011824 | RN-01 | Richmond Nth SWER No.01 | LR | 20011486 | RI | Richmond 66/33/19.1kV Substation | 19776 | 16 | 0.034698 | 686.1918 | Pole | 36690.675
2021_2022 | AER | UNPLANNED | 22NQ1575 | 20009306 | LANN-05 | LANNERCOST NO.05 | SR | 20009097 | LANN | Lannercost 66/11kV Substation | 4183 | 37 | 0.025971 | 108.6352 | Pole Top | 5808.7262
2022_2023 | AER | UNPLANNED | 22NQ16159 | 20011487 | RI-10 | Richmond No.10 | SR | 20011486 | RI | Richmond 66/33/19.1kV Substation | 329.4167 | 1 | 0.033193 | 10.9345 | Pole | 584.6654
2022_2023 | AER | UNPLANNED | 22NQ16208 | 20004937 | NC-02 | NORTHCLONCURRY NO.02 | LR | 20004930 | NOCL | North Cloncurry 66/11kV Substation | 37727.55 | 27 | 0.035045 | 1322.1528 | Pole | 70695.5116
2022_2023 | AER | UNPLANNED | 22NQ16552 | 20001649 | AY-04 | AYR NO.04 | SR | 20001223 | AYRZ | Ayr 66/11kV Sub (AYRZ) | 1976 | 26 | 0.033385 | 65.9688 | Pole Top | 3527.3494
2021_2022 | AER | UNPLANNED | 22NQ1751 | 20005265 | DR-05 | DUCHESSRD NO.05 | SR | 20005132 | DURO | DUCHESS RD 132/11KV SUBSTATION | 10148.4 | 72 | 0.02643 | 268.2184 | Pole Top | 14341.6374
2021_2022 | AER | UNPLANNED | 22NQ1925 | 20005133 | DR-12 | DUCHESSRD NO.12 | LR | 20005132 | DURO | DUCHESS RD 132/11KV SUBSTATION | 1947.8667 | 14 | 0.027968 | 54.4786 | Pole Top | 2912.9731
2021_2022 | AER | UNPLANNED | 22NQ2101 | 82914276 | BLRI-08 | BLACKRIVER NO.08 | SR | 20020706 | BLRI | BLACKRIVER 66/11KV SUBSTATION | 394 | 1 | 0.021094 | 8.3112 | Pole Top | 444.3992
2021_2022 | AER | UNPLANNED | 22NQ2260 | 20001859 | BA-01 | Bambaroo No.01 | SR | 20001858 | BAMB | BAMBAROO 66/11KV SUBSTATION | 3039 | 90 | 0.02207 | 67.0713 | Pole Top | 3586.303
2021_2022 | AER | UNPLANNED | 22NQ2260 | 20005787 | FX-01 | MOUNTFOX NO.1 | SR | 20005786 | MOFO | Mt Fox 66/11kV Substation | 50388.8 | 48 | 0.010759 | 542.1317 | Pole Top | 28987.7826
2021_2022 | AER | UNPLANNED | 22NQ2260 | 20006383 | GR-02 | GREENVALE NO.02 | LR | 20006382 | GREN | GREENVALE 66/11KV SUB (GR) | 193157.0667 | 184 | 0.025381 | 4902.5137 | Pole Top | 262137.4053
2021_2022 | AER | UNPLANNED | 22NQ2260 | 20010961 | MU-01 | MUTARNEE NO.01 | SR | 20010960 | MUTA | MUTARNEE 66/11KV SUB (MU) | 6989.7 | 207 | 0.019152 | 133.8658 | Pole Top | 7157.8035
2021_2022 | AER | UNPLANNED | 22NQ2260 | 84653782 | BA-02 | BAMBAROO NO 2 | SR | 20001858 | BAMB | BAMBAROO 66/11KV SUBSTATION | 1823.4 | 54 | 0.022861 | 41.6844 | Pole Top | 2228.8669
2021_2022 | AER | UNPLANNED | 22NQ2287 | 20003792 | CO-01 | COLLINSVILLE NO.01 | SR | 20003791 | COLL | COLLINSVILLE SUBSTATION | 358 | 1 | 0.028455 | 10.187 | Pole | 544.6981
2021_2022 | AER | UNPLANNED | 22NQ2706 | 25267901 | EL-01 | ELDERSLIESWER NO.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 33168.8 | 28 | 0.03302 | 1095.2218 | Pole | 58561.5104
2021_2022 | AER | UNPLANNED | 22NQ2753 | 82561856 | MILC-09 | MILLCHESTER NO.09 | LR | 20010917 | MILC | Millchester 132/66/11kV Substation | 6060 | 54 | 0.026254 | 159.0984 | Pole Top | 8506.9919
2021_2022 | AER | UNPLANNED | 22NQ2869 | 25273297 | GE-01 | CORFIELD SWER | LR | 25267919 | GLEE | GLENELG 66/19.1KV SUB (GLEE) | 11289.5667 | 11 | 0.033779 | 381.3551 | Pole | 20391.0569
2021_2022 | AER | UNPLANNED | 22NQ3024 | 20007111 | HH-07 | HOMEHILL NO.07 | SR | 20006664 | HOHI | HOMEHILL 66/11KV SUBSTATION | 43353 | 37 | 0.056579 | 2452.863 | Pole Top | 131154.5842
2021_2022 | AER | UNPLANNED | 22NQ3057 | 20003294 | CB-03 | CRANBROOK NO.03 | UR | 20003280 | CRAN | CRANBROOK 66/11KV SUB (CB) | 2990.7667 | 83 | 0.020795 | 62.1929 | Pole Top | 3325.4528
2021_2022 | AER | UNPLANNED | 22NQ3162 | 20003435 | CC-01 | CLONCURRY NO.01 | LR | 20003434 | CLON | CLONCURRY 66/11KV SUB (CC) | 24198.6 | 18 | 0.038494 | 931.5054 | Pole | 49807.5963
2021_2022 | AER | UNPLANNED | 22NQ3198 | 20004307 | CT-03 | YORK ST | LR | 20004053 | CHTO | CHARTERSTOWERS 66/11KV SUBSTATION | 33033 | 273 | 0.072396 | 2391.4441 | Pole Top | 127870.5186
2021_2022 | AER | UNPLANNED | 22NQ3291 | 20009483 | LE-02 | MOUNTLEYSHON NO.02 | SR | 20009480 | MOLE | MOUNT LEYSHON 66/11KV SUB (LE) | 287.1 | 1 | 0.22414 | 64.3504 | Pole Top | 3440.815
2021_2022 | AER | UNPLANNED | 22NQ3291 | 20009493 | LP-01 | MOUNTLEYSHONPUMP NO.01 | SR | 20009492 | MOLP | MOUNT LEYSHON PUMP 66/11KV SUB | 5454.9 | 19 | 0.016962 | 92.5283 | Pole Top | 4947.4871
2021_2022 | AER | UNPLANNED | 22NQ3291 | 20011334 | PJ-01 | PAJINGO MINE NO.01 | SR | 20011333 | PAJI | PAJINGO 66/11KV SUB (PJ) | 287.1 | 1 | 111.7411 | 32080.8779 | Pole Top | 1715364.5393
2021_2022 | AER | UNPLANNED | 22NQ3310 | 82564200 | MILC-11 | MILLCHESTER NO.11 | SR | 20010917 | MILC | Millchester 132/66/11kV Substation | 118.9833 | 1 | 0.021481 | 2.5558 | Pole Top | 136.6613
2021_2022 | AER | UNPLANNED | 22NQ3323 | 20002985 | BO-06 | BOHLE NO.06 | UR | 20002743 | BOHL | BOHLE 66/11KV SUBSTATION | 22790 | 48 | 0.23472 | 5349.2942 | Pole Top | 286026.7626
2021_2022 | AER | UNPLANNED | 22NQ3871 | 20009306 | LANN-05 | LANNERCOST NO.05 | SR | 20009097 | LANN | Lannercost 66/11kV Substation | 13769.3 | 38 | 0.025971 | 357.5977 | Pole Top | 19120.7492
2021_2022 | AER | UNPLANNED | 22NQ3927 | 20004307 | CT-03 | YORK ST | LR | 20004053 | CHTO | CHARTERSTOWERS 66/11KV SUBSTATION | 8804 | 124 | 0.072396 | 637.3709 | Pole Top | 34080.2242
2021_2022 | AER | UNPLANNED | 22NQ4177 | 20012587 | ST05 | SERENE VALLEY | SR | 20012369 | STUA | Stuart 66/11kV Substation | 120497.85 | 363 | 0.017887 | 2155.3362 | Pole Top | 115245.8256
2021_2022 | AER | UNPLANNED | 22NQ4301 | 25267901 | EL-01 | ELDERSLIESWER NO.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 52366.1167 | 43 | 0.03302 | 1729.1103 | Pole | 92455.527
2021_2022 | AER | UNPLANNED | 22NQ4578 | 20003547 | CF-01 | CAPE FERGUSON NO.01 | UR | 20003546 | CAFE | CAPE FERGUSON 66/11KV SUB (CAFE) | 293.2167 | 1 | 12.8556 | 3769.4766 | Pole Top | 201553.9164
2021_2022 | AER | UNPLANNED | 22NQ4578 | 20003550 | CF-02 | CAPE FERGUSON NO.02 | SR | 20003546 | CAFE | CAPE FERGUSON 66/11KV SUB (CAFE) | 101746.1833 | 347 | 0.012313 | 1252.7898 | Pole Top | 66986.6715
2021_2022 | AER | UNPLANNED | 22NQ4714 | 20002267 | BL-01 | BLUEWATER NO.01 | SR | 20002266 | BLUE | BLUEWATER 66/11KV SUBSTATION (BLUE) | 5055.7 | 3 | 0.022457 | 113.5375 | Pole Top | 6070.8513
2021_2022 | AER | UNPLANNED | 22NQ5101 | 20004955 | NC-03 | NORTHCLONCURRY NO.03 | SR | 20004930 | NOCL | North Cloncurry 66/11kV Substation | 124 | 2 | 0.056864 | 7.0511 | Pole Top | 377.0239
2021_2022 | AER | UNPLANNED | 22NQ5429 | 82561856 | MILC-09 | MILLCHESTER NO.09 | LR | 20010917 | MILC | Millchester 132/66/11kV Substation | 9324.3333 | 10 | 0.026254 | 244.7998 | Pole | 13089.4436
2021_2022 | AER | UNPLANNED | 22NQ5468 | 20006518 | GU-02 | GUMLU NO.02 | SR | 20006477 | GUML | GUMLU 66/11KV SUBSTATION | 57048 | 4 | 0.035006 | 1997.02 | Pole Top | 106780.657
2021_2022 | AER | UNPLANNED | 22NQ5627 | 20004081 | CT-02 | WATERWORKS | SR | 20004053 | CHTO | CHARTERSTOWERS 66/11KV SUBSTATION | 275.85 | 1 | 0.020667 | 5.7009 | Pole Top | 304.8272
2021_2022 | AER | UNPLANNED | 22NQ6039 | 20005265 | DR-05 | DUCHESSRD NO.05 | SR | 20005132 | DURO | DUCHESS RD 132/11KV SUBSTATION | 186 | 2 | 0.02643 | 4.9159 | Pole Top | 262.8537
2021_2022 | AER | UNPLANNED | 22NQ6057 | 20007716 | HU-30 | TOWN | SR | 20007579 | HUGH | HUGHENDEN 66/33/6.6KV SUBSTATION | 72778.0167 | 743 | 0.033881 | 2465.8096 | Pole | 131846.8379
2021_2022 | AER | UNPLANNED | 22NQ6202 | 20004307 | CT-03 | YORK ST | LR | 20004053 | CHTO | CHARTERSTOWERS 66/11KV SUBSTATION | 40278 | 300 | 0.072396 | 2915.9503 | Pole Top | 155915.8643
2021_2022 | AER | UNPLANNED | 22NQ6315 | 20012178 | SD-01 | Saunders No.01 | SR | 20012177 | SAUN | SAUNDERS 66/11KV SUB (SAUN) | 7455 | 71 | 0.031493 | 234.7775 | Pole Top | 12553.5549
2021_2022 | AER | UNPLANNED | 22NQ6408 | 82564200 | MILC-11 | MILLCHESTER NO.11 | SR | 20010917 | MILC | Millchester 132/66/11kV Substation | 32560 | 370 | 0.021481 | 699.4127 | Pole Top | 37397.595
2021_2022 | AER | UNPLANNED | 22NQ6572 | 20013273 | 1213 | WOSO-01 | SR | 84555017 | WOSO | WOODSTOCK SOUTH 66/11KV SUB (WOSO) | 12622 | 66 | 0.020524 | 259.0551 | Pole Top | 13851.6787
2021_2022 | AER | UNPLANNED | 22NQ7026 | 20001649 | AY-04 | AYR NO.04 | SR | 20001223 | AYRZ | Ayr 66/11kV Sub (AYRZ) | 2047 | 23 | 0.040354 | 82.6053 | Pole Top | 4416.9069
2021_2022 | AER | UNPLANNED | 22NQ7161 | 83897505 | RASM-02 | RASMUSSEN NO.02 | SR | 20011587 | RASM | Rasmussen 66/11kV Substation | 26350 | 310 | 0.022206 | 585.137 | Pole Top | 31287.2752
2021_2022 | AER | UNPLANNED | 22NQ7439 | 20004081 | CT-02 | WATERWORKS | SR | 20004053 | CHTO | CHARTERSTOWERS 66/11KV SUBSTATION | 90748.6667 | 520 | 0.020667 | 1875.4726 | Pole Top | 100281.5208
2021_2022 | AER | UNPLANNED | 22NQ7612 | 20005412 | DR-10 | DUCHESSRD NO.10 | UR | 20005132 | DURO | DUCHESS RD 132/11KV SUBSTATION | 13360.3667 | 113 | 0.020135 | 269.0132 | Pole Top | 14384.1342
2021_2022 | AER | UNPLANNED | 22NQ7711 | 20005265 | DR-05 | DUCHESSRD NO.05 | SR | 20005132 | DURO | DUCHESS RD 132/11KV SUBSTATION | 46735 | 474 | 0.02643 | 1235.1885 | Pole | 66045.5267
2022_2023 | AER | UNPLANNED | 22NQ8265 | 84023546 | MERI-11 | MERINDA NO.11 | SR | 20009877 | MERI | Merinda 66/11kV Substation | 64837.3 | 66 | 0.039612 | 2568.3359 | Pole Top | 137328.9199
2022_2023 | AER | UNPLANNED | 22NQ8277 | 20011824 | RN-01 | Richmond Nth SWER No.01 | LR | 20011486 | RI | Richmond 66/33/19.1kV Substation | 49852.6667 | 16 | 0.034698 | 1729.7983 | Pole | 92492.3135
2022_2023 | AER | UNPLANNED | 22NQ8609 | 25273020 | DR-02 | DUCHESSRD NO.02 | UR | 20005132 | DURO | DUCHESS RD 132/11KV SUBSTATION | 8639.5667 | 59 | 0.025177 | 217.519 | Pole Top | 11630.7431
2022_2023 | AER | UNPLANNED | 22NQ8721 | 20007111 | HH-07 | HOMEHILL NO.07 | SR | 20006664 | HOHI | HOMEHILL 66/11KV SUBSTATION | 176.8833 | 1 | 0.056272 | 9.9535 | Pole Top | 532.2143
2022_2023 | AER | UNPLANNED | 22NQ9781 | 20010779 | MP-06 | MONAPARK NO.06 | SR | 20010630 | MOPA | MONA PARK 66/11KV SUB | 1368 | 18 | 0.051975 | 71.1022 | Pole Top | 3801.8349
2021_2022 | AER | UNPLANNED | 22SW0020 | 60026747 | F2980 | GOOMBURRA | LR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 2274.4 | 8 | 0.01983 | 45.1025 | Pole Top | 2411.6292
2021_2022 | AER | UNPLANNED | 22SW0059 | 60026747 | F2980 | GOOMBURRA | LR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 244.4667 | 1 | 0.01983 | 4.8479 | Pole Top | 259.2169
2021_2022 | AER | UNPLANNED | 22SW0198 | 60026757 | F306C | SOUTH EAST RURAL | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 26072.5 | 38 | 0.026538 | 691.9192 | Pole | 36996.9201
2021_2022 | AER | UNPLANNED | 22SW0240 | 60026676 | F079S | ST GEORGE MEATWORKS | LR | 60007215 | SAGE | ST GEORGE (MC052) 66/33KV SUB (SAGE) | 8707.35 | 9 | 0.080053 | 697.0494 | Pole | 37271.2322
2021_2022 | AER | UNPLANNED | 22SW0277 | 60026650 | F022R | BRUCEDALE | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 232880.8333 | 485 | 0.026405 | 6149.2937 | Pole | 328802.7325
2021_2022 | AER | UNPLANNED | 22SW0303 | 60026675 | F077S | MAIN CAMP | LR | 60007215 | SAGE | ST GEORGE (MC052) 66/33KV SUB (SAGE) | 150183.2 | 222 | 0.037521 | 5635.0682 | Pole | 301307.0988
2021_2022 | AER | UNPLANNED | 22SW0602 | 60026783 | F3475 | McGLEW STREET | LR | 60007222 | STTO | STANTHORPE TOWN 33/11KV SUB | 384 | 3 | 0.017026 | 6.5379 | Pole Top | 349.5812
2021_2022 | AER | UNPLANNED | 22SW0724 | 60026766 | F315C | EULO | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 3230.3333 | 20 | 0.018798 | 60.7229 | Pole | 3246.8528
2022_2023 | AER | UNPLANNED | 22SW10037 | 60026667 | F060T | TARA | LR | 60007206 | KOGA | KOGAN REGULATOR (MC13) | 6146.2 | 1167 | 0.028525 | 175.3178 | Pole Top | 9374.2414
2022_2023 | AER | UNPLANNED | 22SW10037 | 60026671 | F070T | FRY STREET | SR | 60007207 | TARA | TARA 33/11KV SUB | 1469.4 | 279 | 0.026585 | 39.0635 | Pole Top | 2088.7242
2022_2023 | AER | UNPLANNED | 22SW10037 | 60026672 | F071T | BILTON STREET | SR | 60007207 | TARA | TARA 33/11KV SUB | 1142.8667 | 217 | 0.020852 | 23.8312 | Pole Top | 1274.2562
2022_2023 | AER | UNPLANNED | 22SW10037 | 84000793 | 3178 | WILKIE CREEK | SR | 82674826 | DAAN | DAANDINE (T188) 110/33KV SUBSTATION | 478.7667 | 106 | 0.099348 | 47.5646 | Pole Top | 2543.2773
2022_2023 | AER | UNPLANNED | 22SW10074 | 60026773 | F3317 | KILLARNEY SOUTH | SR | 60007236 | KILL | KILLARNEY 33/11KV SUB (ME063) | 670.3667 | 2 | 0.018023 | 12.082 | Pole Top | 646.0266
2022_2023 | AER | UNPLANNED | 22SW10306 | 60026703 | F2085 | APPLETHORPE | SR | 60007222 | STTO | STANTHORPE TOWN 33/11KV SUB | 2106 | 39 | 0.030263 | 63.733 | Pole Top | 3407.8021
2022_2023 | AER | UNPLANNED | 22SW10350 | 60026718 | F2415 | CABARLAH | SR | 60007235 | MERN | MERINGANDAN 33/11KV SUB (ME062) | 5433 | 29 | 0.032443 | 176.2638 | Pole Top | 9424.8265
2022_2023 | AER | UNPLANNED | 22SW10510 | 60026716 | F233C | MORVEN | LR | 60007255 | CHAR | CHARLEVILLE 66/22/11KV SUB | 53355 | 225 | 0.031882 | 1701.0393 | Pole Top | 90954.5705
2021_2022 | AER | UNPLANNED | 22SW1065 | 60300323 | F081S | NOONDOO | LR | 60007215 | SAGE | ST GEORGE (MC052) 66/33KV SUB (SAGE) | 15694.0667 | 11 | 0.066472 | 1043.2089 | Pole | 55780.3792
2022_2023 | AER | UNPLANNED | 22SW10736 | 60026773 | F3317 | KILLARNEY SOUTH | SR | 60007236 | KILL | KILLARNEY 33/11KV SUB (ME063) | 1605.2833 | 13 | 0.018023 | 28.9321 | Pole Top | 1546.9978
2022_2023 | AER | UNPLANNED | 22SW10836 | 60026764 | F3145 | HORRANE | SR | 60007242 | CEPL | CECIL PLAINS 33/11KV SUB | 4780 | 36 | 0.047905 | 228.9856 | Pole Top | 12243.8626
2021_2022 | AER | UNPLANNED | 22SW1086 | 60026675 | F077S | MAIN CAMP | LR | 60007215 | SAGE | ST GEORGE (MC052) 66/33KV SUB (SAGE) | 71905.6667 | 110 | 0.037521 | 2697.9938 | Pole Top | 144261.7271
2022_2023 | AER | UNPLANNED | 22SW10871 | 60026778 | F3400 | LINTHORPE | SR | 60007233 | BROX | BROXBURN 33/11KV SUB (ME057) | 66273 | 102 | 0.027408 | 1816.4144 | Pole | 97123.6776
2022_2023 | AER | UNPLANNED | 22SW10875 | 60026821 | F4135 | SHORT STREET | LR | 60007222 | STTO | STANTHORPE TOWN 33/11KV SUB | 2288 | 26 | 0.022225 | 50.85 | Pole Top | 2718.9474
2022_2023 | AER | UNPLANNED | 22SW10898 | 60330584 | F3522 | MILITARY BASE | UR | 60330485 | OAKE | Oakey 33/11kV Substation | 180.75 | 1 | 0.4248 | 76.7831 | Pole Top | 4105.5944
2022_2023 | AER | UNPLANNED | 22SW10903 | 60026809 | F3950 | PITTSWORTH | SR | 60007233 | BROX | BROXBURN 33/11KV SUB (ME057) | 2779 | 35 | 0.025673 | 71.3465 | Pole Top | 3814.8967
2022_2023 | AER | UNPLANNED | 22SW11049 | 60026767 | F3160 | HURSLEY ROAD | UR | 60007224 | WETO | WEST TOOWOOMBA 33/11KV SUB | 5304 | 39 | 0.030814 | 163.4381 | Pole Top | 8739.0344
2022_2023 | AER | UNPLANNED | 22SW11440 | 60026783 | F3475 | McGLEW STREET | LR | 60007222 | STTO | STANTHORPE TOWN 33/11KV SUB | 10800 | 60 | 0.02115 | 228.4157 | Pole Top | 12213.3861
2022_2023 | AER | UNPLANNED | 22SW11498 | 60026889 | F061W | GULUGUBA | LR | 60007208 | WAND | WANDOAN 33/22KV SUB | 308.3 | 1 | 0.035246 | 10.8663 | Pole | 581.0219
2022_2023 | AER | UNPLANNED | 22SW11797 | 60026747 | F2980 | GOOMBURRA | LR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 4275 | 45 | 0.025409 | 108.6254 | Pole Top | 5808.2019
2022_2023 | AER | UNPLANNED | 22SW11916 | 84670339 | 14067 | MURRAY'S BRIDGE | SR | 84536204 | WAEA | WARWICK EAST 33/11KV SUB | 12825 | 121 | 0.025709 | 329.7201 | Pole Top | 17630.1321
2022_2023 | AER | UNPLANNED | 22SW12051 | 84670339 | 14067 | MURRAY'S BRIDGE | SR | 84536204 | WAEA | WARWICK EAST 33/11KV SUB | 105.9167 | 1 | 0.025709 | 2.723 | Pole Top | 145.6004
2022_2023 | AER | UNPLANNED | 22SW12406 | 60026725 | F2530 | CLIFTON WEST | SR | 60007249 | CLIF | CLIFTON 33/11KV SUB (ME399) | 644.9333 | 2 | 0.031095 | 20.054 | Pole Top | 1072.2858
2022_2023 | AER | UNPLANNED | 22SW12407 | 60026713 | F2320 | BROOKSTEAD | SR | 60007226 | YASO | YARRANLEA SOUTH 33/11KV SUB | 232 | 2 | 0.024718 | 5.7346 | Pole Top | 306.6273
2022_2023 | AER | UNPLANNED | 22SW12531 | 60026650 | F022R | BRUCEDALE | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 429 | 1 | 0.028126 | 12.0661 | Pole Top | 645.172
2022_2023 | AER | UNPLANNED | 22SW13060 | 60026766 | F315C | EULO | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 3840 | 30 | 0.021724 | 83.4196 | Pole Top | 4460.4461
2022_2023 | AER | UNPLANNED | 22SW13089 | 112330157 | 14169 | CAMBOOYA | SR | 60331401 | KESP | KEARNEYS SPRINGS 110/11KV SUB (KESP) | 150234 | 686 | 0.025801 | 3876.1692 | Pole Top | 207258.7682
2022_2023 | AER | UNPLANNED | 22SW13323 | 60026742 | F2860 | EVERGREEN | SR | 60007239 | PERA | PERANGA 33/11KV SUB (ME075) | 105793.2667 | 176 | 0.019152 | 2026.1137 | Pole Top | 108336.2995
2022_2023 | AER | UNPLANNED | 22SW13333 | 60026666 | F049R | ROMA NORTH | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 25203.7833 | 41 | 0.027915 | 703.5696 | Pole | 37619.8657
2022_2023 | AER | UNPLANNED | 22SW13503 | 60026656 | F028D | NANDI - GRASSDALE | SR | 60007198 | NAND | NANDI 33/11KV SUBSTATION | 15396.8667 | 28 | 0.045647 | 702.8144 | Pole | 37579.4878
2022_2023 | AER | UNPLANNED | 22SW13628 | 60026676 | F079S | ST GEORGE MEATWORKS | LR | 60007215 | SAGE | ST GEORGE (MC052) 66/33KV SUB (SAGE) | 34732.5333 | 43 | 0.068076 | 2364.4538 | Pole | 126427.3454
2021_2022 | AER | UNPLANNED | 22SW1368 | 60026816 | F4090 | ROSSVALE | LR | 60007248 | PURR | PURRAWUNDA 33/11KV SUB | 7995 | 41 | 0.019674 | 157.2926 | Pole Top | 8410.4364
2021_2022 | AER | UNPLANNED | 22SW1381 | 82987762 | F3743 | NELSON ST | SR | 60331401 | KESP | KEARNEYS SPRINGS 110/11KV SUB (KESP) | 1007 | 10 | 0.017904 | 18.0296 | Pole Top | 964.0419
2022_2023 | AER | UNPLANNED | 22SW14008 | 84668557 | 14069 | SWAN CREEK | SR | 84536204 | WAEA | WARWICK EAST 33/11KV SUB | 60324.3333 | 550 | 0.020733 | 1250.6974 | Pole Top | 66874.7905
2022_2023 | AER | UNPLANNED | 22SW14010 | 60026676 | F079S | ST GEORGE MEATWORKS | LR | 60007215 | SAGE | ST GEORGE (MC052) 66/33KV SUB (SAGE) | 5183.2 | 33 | 0.068076 | 352.8518 | Pole Top | 18866.9859
2022_2023 | AER | UNPLANNED | 22SW14010 | 60327170 | F078S | BEARDMORE DAM | LR | 60327166 | BURG | BURGORAH 33KV REGULATOR | 22974.6 | 99 | 0.042928 | 986.2448 | Pole Top | 52734.5068
2022_2023 | AER | UNPLANNED | 22SW14344 | 60026747 | F2980 | GOOMBURRA | LR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 62023.7833 | 61 | 0.025409 | 1575.9907 | Pole | 84268.2242
2022_2023 | AER | UNPLANNED | 22SW14449 | 60026775 | F3375 | LEGUME | SR | 60007236 | KILL | KILLARNEY 33/11KV SUB (ME063) | 21845 | 230 | 0.015715 | 343.2991 | Pole Top | 18356.2039
2022_2023 | AER | UNPLANNED | 22SW14481 | 60026819 | F4115 | SANDY CREEK | LR | 60007247 | WEWA | WEST WARWICK 33/11KV SUB (WEWA) | 44890.3 | 167 | 0.025338 | 1137.4475 | Pole Top | 60819.3187
2022_2023 | AER | UNPLANNED | 22SW14754 | 60026801 | F3875 | PARROT STREET | SR | 60007227 | ME020 | North Street 33/11kV Substation | 9316.65 | 63 | 0.03042 | 283.4168 | Pole Top | 15154.2965
2022_2023 | AER | UNPLANNED | 22SW15587 | 60026735 | F2685 | DALVEEN | LR | 60007243 | ME117 | Pozieres 33/11kV Substation | 1162 | 14 | 0.028423 | 33.027 | Pole Top | 1765.9526
2022_2023 | AER | UNPLANNED | 22SW15619 | 40000974 | THEO-FA08 | Taroom Feeder | LR | 40017933 | THEO | Theodore 66/22kV Substation | 28747.4 | 669 | 0.025243 | 725.6687 | Pole Top | 38801.5074
2021_2022 | AER | UNPLANNED | 22SW1565 | 60026731 | F2645 | CREEK STREET | SR | 60007231 | CRNE | CROWS NEST 33/11KV SUB (ME032) | 191550.8 | 174 | 0.016755 | 3209.3783 | Pole Top | 171605.4562
2021_2022 | AER | UNPLANNED | 22SW1600 | 60026666 | F049R | ROMA NORTH | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 17259.8 | 44 | 0.025151 | 434.0963 | Pole | 23211.128
2022_2023 | AER | UNPLANNED | 22SW16785 | 60027002 | F097D | JANDOWAE | LR | 60007197 | WEDA | WEST DALBY 33/11KV SUB | 24875.55 | 23 | 0.046648 | 1160.3969 | Pole | 62046.4232
2022_2023 | AER | UNPLANNED | 22SW16790 | 60026682 | F095D | KAIMKILLENBUN | LR | 82867225 | DAEA | DALBY EAST 110/33KV SUBSTATION | 155559.5667 | 143 | 0.033878 | 5270.0367 | Pole | 281788.8619
2022_2023 | AER | UNPLANNED | 22SW16790 | 60026995 | F087D | MT MOWBULLAN | SR | 60007212 | MC020 | Mt. Mowbullan 33/11kV Substation | 248160.8 | 184 | 0.039497 | 9801.6463 | Pole | 524094.0292
2022_2023 | AER | UNPLANNED | 22SW16790 | 60026997 | F090D | SQUARETOP | LR | 60007199 | MC004 | Kaimkillenbun 33/11kV Substation | 609612.4 | 452 | 0.020246 | 12342.1389 | Pole | 659934.1645
2022_2023 | AER | UNPLANNED | 22SW16847 | 60026702 | F2075 | ANCHORFIELD | SR | 60007229 | PAMP | PAMPAS 33/11KV SUB | 11742.6667 | 34 | 0.096996 | 1138.9922 | Pole Top | 60901.9108
2022_2023 | AER | UNPLANNED | 22SW17013 | 60026816 | F4090 | ROSSVALE | LR | 60007248 | PURR | PURRAWUNDA 33/11KV SUB | 388.9667 | 1 | 0.025922 | 10.0826 | Pole Top | 539.1174
2022_2023 | AER | UNPLANNED | 22SW17326 | 60026825 | F4205 | SPRINGSIDE | SR | 60007233 | BROX | BROXBURN 33/11KV SUB (ME057) | 1695.2667 | 4 | 0.023849 | 40.4303 | Pole Top | 2161.8097
2022_2023 | AER | UNPLANNED | 22SW17411 | 60026703 | F2085 | APPLETHORPE | SR | 60007222 | STTO | STANTHORPE TOWN 33/11KV SUB | 314.4 | 2 | 0.030263 | 9.5146 | Pole Top | 508.7431
2022_2023 | AER | UNPLANNED | 22SW17454 | 60026742 | F2860 | EVERGREEN | SR | 60007239 | PERA | PERANGA 33/11KV SUB (ME075) | 40482 | 114 | 0.019152 | 775.2964 | Pole Top | 41455.0965
2022_2023 | AER | UNPLANNED | 22SW17616 | 60026891 | F074C | MILES - CONDAMINE | LR | 60007202 | MILE | MILES 33/11kV SUBSTATION | 45042.4167 | 39 | 0.043686 | 1967.7395 | Pole | 105215.0336
2022_2023 | AER | UNPLANNED | 22SW17621 | 60026657 | F029C | CONDAMINE | SR | 60007203 | MICO | MILES-CONDAMINE 33/22KV SUB (MC009) | 152204 | 120 | 0.030088 | 4579.5285 | Pole | 244867.3877
2022_2023 | AER | UNPLANNED | 22SW17640 | 60026722 | F2465 | CECIL PLAINS TOWN | SR | 60007242 | CEPL | CECIL PLAINS 33/11KV SUB | 114613.3333 | 140 | 0.023401 | 2682.0902 | Pole | 143411.3612
2022_2023 | AER | UNPLANNED | 22SW17640 | 60026756 | F3065 | HASLEMERE | SR | 60007242 | CEPL | CECIL PLAINS 33/11KV SUB | 27016 | 33 | 0.059263 | 1601.0548 | Pole | 85608.3984
2022_2023 | AER | UNPLANNED | 22SW17640 | 60026764 | F3145 | HORRANE | SR | 60007242 | CEPL | CECIL PLAINS 33/11KV SUB | 11173.3333 | 80 | 0.047905 | 535.2579 | Pole | 28620.2424
2022_2023 | AER | UNPLANNED | 22SW17640 | 60026831 | F4380 | TIPTON | SR | 60007242 | CEPL | CECIL PLAINS 33/11KV SUB | 8799 | 63 | 0.027143 | 238.8318 | Pole | 12770.3359
2022_2023 | AER | UNPLANNED | 22SW17640 | 60026839 | F4550 | WATSON STREET | SR | 60007242 | CEPL | CECIL PLAINS 33/11KV SUB | 32746.6667 | 40 | 0.40835 | 13372.238 | Pole | 715013.568
2022_2023 | AER | UNPLANNED | 22SW17944 | 60026787 | F351C | CUNNAMULLA NORTH | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 78074 | 30 | 0.021015 | 1640.7319 | Pole | 87729.9349
2022_2023 | AER | UNPLANNED | 22SW18036 | 60026701 | F206C | AUGATHELLA | LR | 60007255 | CHAR | CHARLEVILLE 66/22/11KV SUB | 55878.5 | 30 | 0.06044 | 3377.3227 | Pole | 180585.4424
2022_2023 | AER | UNPLANNED | 22SW18508 | 84668557 | 14069 | SWAN CREEK | SR | 84536204 | WAEA | WARWICK EAST 33/11KV SUB | 1530 | 30 | 0.020733 | 31.7213 | Pole Top | 1696.1386
2021_2022 | AER | UNPLANNED | 22SW1952 | 60026712 | F2295 | BRINGALILY | LR | 60007244 | MILM | MILLMERRAN 33/11KV SUB | 83720 | 364 | 0.033537 | 2807.759 | Pole Top | 150130.8718
2021_2022 | AER | UNPLANNED | 22SW1952 | 60026790 | F3535 | MILLMERRAN TOWN | SR | 60007244 | MILM | MILLMERRAN 33/11KV SUB | 172960 | 752 | 0.020076 | 3472.328 | Pole Top | 185665.3777
2021_2022 | AER | UNPLANNED | 22SW1952 | 60026815 | F4035 | ROCKY CREEK | SR | 60007244 | MILM | MILLMERRAN 33/11KV SUB | 20240 | 88 | 0.035091 | 710.2362 | Pole Top | 37976.3317
2021_2022 | AER | UNPLANNED | 22SW2142 | 60026712 | F2295 | BRINGALILY | LR | 60007244 | MILM | MILLMERRAN 33/11KV SUB | 237 | 1 | 0.033537 | 7.9484 | Pole Top | 425.0002
2021_2022 | AER | UNPLANNED | 22SW2435 | 60026771 | F3280 | JONDARYAN | LR | 60330485 | OAKE | Oakey 33/11kV Substation | 18648 | 56 | 0.053897 | 1005.0792 | Pole Top | 53741.5863
2021_2022 | AER | UNPLANNED | 22SW2545 | 60026774 | F3365 | LANEWOOD | SR | 60330485 | OAKE | Oakey 33/11kV Substation | 3953 | 59 | 0.016407 | 64.857 | Pole Top | 3467.9015
2021_2022 | AER | UNPLANNED | 22SW3015 | 60026734 | F2661 | CROWS NEST INDUSTRIAL ROAD | LR | 60007231 | CRNE | CROWS NEST 33/11KV SUB (ME032) | 52921.5333 | 268 | 0.018439 | 975.8181 | Pole Top | 52176.9914
2021_2022 | AER | UNPLANNED | 22SW3123 | 60026701 | F206C | AUGATHELLA | LR | 60007255 | CHAR | CHARLEVILLE 66/22/11KV SUB | 2516.1333 | 8 | 0.054842 | 137.991 | Pole | 7378.3798
2021_2022 | AER | UNPLANNED | 22SW3135 | 60026644 | F004Q | QUILPIE RURAL | LR | 60007257 | QUIL | QUILPIE 66/11KV SUB | 15129.3333 | 16 | 0.025503 | 385.8389 | Pole | 20630.8054
2021_2022 | AER | UNPLANNED | 22SW3136 | 60026766 | F315C | EULO | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 43943.5333 | 19 | 0.018798 | 826.0381 | Pole | 44168.2549
2021_2022 | AER | UNPLANNED | 22SW3393 | 84965669 | 14088 | GLENVALE EAST | SR | 60025703 | TORR | TORRINGTON 110/33/11KV SUB (T116) | 16749.6 | 72 | 0.019723 | 330.3568 | Pole Top | 17664.178
2021_2022 | AER | UNPLANNED | 22SW3490 | 60026747 | F2980 | GOOMBURRA | LR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 5534 | 20 | 0.01983 | 109.7419 | Pole | 5867.9019
2021_2022 | AER | UNPLANNED | 22SW3505 | 60026675 | F077S | MAIN CAMP | LR | 60007215 | SAGE | ST GEORGE (MC052) 66/33KV SUB (SAGE) | 160563.5 | 390 | 0.037521 | 6024.5505 | Pole Top | 322132.7176
2021_2022 | AER | UNPLANNED | 22SW3581 | 60026892 | F076C | DULACCA | LR | 60007202 | MILE | MILES 33/11kV SUBSTATION | 177007.9667 | 374 | 0.016779 | 2970.069 | Pole | 158809.5891
2021_2022 | AER | UNPLANNED | 22SW3643 | 83850831 | GRANADA | GRANADA | SR | 82709366 | SKIB | SKID B 33/11kV SUBSTATION | 2516.55 | 19 | 0.021253 | 53.4844 | Pole Top | 2859.8083
2021_2022 | AER | UNPLANNED | 22SW3912 | 60026816 | F4090 | ROSSVALE | LR | 60007248 | PURR | PURRAWUNDA 33/11KV SUB | 6 | 1 | 0.019674 | 0.11804 | Pole Top | 6.3118
2021_2022 | AER | UNPLANNED | 22SW4116 | 60026745 | F2960 | GLENGALLAN | SR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 78175.2667 | 358 | 0.016488 | 1288.9423 | Pole | 68919.7473
2021_2022 | AER | UNPLANNED | 22SW4116 | 60026747 | F2980 | GOOMBURRA | LR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 141501.6 | 648 | 0.01983 | 2806.0465 | Pole | 150039.3049
2021_2022 | AER | UNPLANNED | 22SW4116 | 60026758 | F3085 | HENDON | SR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 82324.2333 | 377 | 0.028604 | 2354.7803 | Pole | 125910.1009
2021_2022 | AER | UNPLANNED | 22SW4116 | 60026833 | F4425 | TOOWOOMBA ROAD | SR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 135387.3333 | 620 | 0.023299 | 3154.4076 | Pole | 168666.1741
2021_2022 | AER | UNPLANNED | 22SW4307 | 60026729 | F2620 | COPPS HILL | SR | 60007233 | BROX | BROXBURN 33/11KV SUB (ME057) | 52528.5833 | 119 | 0.06461 | 3393.8464 | Pole Top | 181468.9685
2021_2022 | AER | UNPLANNED | 22SW4322 | 60026650 | F022R | BRUCEDALE | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 39909.1167 | 43 | 0.026405 | 1053.8131 | Pole | 56347.3877
2021_2022 | AER | UNPLANNED | 22SW4488 | 84965685 | 14089 | TROYS RD | SR | 60025703 | TORR | TORRINGTON 110/33/11KV SUB (T116) | 204046.7833 | 1073 | 0.020582 | 4199.7216 | Pole | 224559.1148
2021_2022 | AER | UNPLANNED | 22SW4947 | 60026786 | F3505 | MERINGANDAN | SR | 60007235 | MERN | MERINGANDAN 33/11KV SUB (ME062) | 5538 | 39 | 0.019792 | 109.6074 | Pole Top | 5860.707
2021_2022 | AER | UNPLANNED | 22SW5553 | 60026815 | F4035 | ROCKY CREEK | SR | 60007244 | MILM | MILLMERRAN 33/11KV SUB | 3120 | 39 | 0.035091 | 109.4831 | Pole Top | 5854.059
2021_2022 | AER | UNPLANNED | 22SW5688 | 60026729 | F2620 | COPPS HILL | SR | 60007233 | BROX | BROXBURN 33/11KV SUB (ME057) | 18993.8 | 92 | 0.06461 | 1227.1803 | Pole Top | 65617.3282
2021_2022 | AER | UNPLANNED | 22SW5692 | 60026703 | F2085 | APPLETHORPE | SR | 60007222 | STTO | STANTHORPE TOWN 33/11KV SUB | 6000 | 43 | 0.025439 | 152.6314 | Pole Top | 8161.2029
2021_2022 | AER | UNPLANNED | 22SW5970 | 60026705 | F2140 | BALD HILLS | SR | 60007238 | NORW | NORWIN 33/11KV SUB (ME074) | 16330 | 71 | 0.027873 | 455.1703 | Pole Top | 24337.9579
2021_2022 | AER | UNPLANNED | 22SW6456 | 60026786 | F3505 | MERINGANDAN | SR | 60007235 | MERN | MERINGANDAN 33/11KV SUB (ME062) | 21226.8 | 72 | 0.019792 | 420.1181 | Pole Top | 22463.7152
2021_2022 | AER | UNPLANNED | 22SW6878 | 60026699 | F203C | PARRY STREET | SR | 60007255 | CHAR | CHARLEVILLE 66/22/11KV SUB | 2006 | 59 | 0.022676 | 45.4881 | Pole Top | 2432.2489
2021_2022 | AER | UNPLANNED | 22SW6895 | 60026693 | F181R | DUBLIN STREET | SR | 60007254 | MITC | MITCHELL 33/11KV SUB | 1980 | 44 | 0.023839 | 47.2014 | Pole Top | 2523.8565
2021_2022 | AER | UNPLANNED | 22SW6981 | 60026644 | F004Q | QUILPIE RURAL | LR | 60007257 | QUIL | QUILPIE 66/11KV SUB | 40141.6667 | 81 | 0.025503 | 1023.721 | Pole | 54738.3613
2021_2022 | AER | UNPLANNED | 22SW7427 | 60026774 | F3365 | LANEWOOD | SR | 60330485 | OAKE | Oakey 33/11kV Substation | 434214.9 | 1528 | 0.016407 | 7124.1734 | Pole Top | 380929.5527
2021_2022 | AER | UNPLANNED | 22SW7459 | 60026888 | F058W | TAROOM | LR | 60007208 | WAND | WANDOAN 33/22KV SUB | 146636 | 492 | 0.030357 | 4451.4111 | Pole Top | 238016.9541
2021_2022 | AER | UNPLANNED | 22SW7459 | 60026889 | F061W | GULUGUBA | LR | 60007208 | WAND | WANDOAN 33/22KV SUB | 75992 | 184 | 0.037334 | 2837.0519 | Pole Top | 151697.1641
2021_2022 | AER | UNPLANNED | 22SW7459 | 60026890 | F063W | WANDOAN TOWN | SR | 60007208 | WAND | WANDOAN 33/22KV SUB | 140833 | 341 | 0.019583 | 2757.9452 | Pole Top | 147467.3305
2021_2022 | AER | UNPLANNED | 22SW7459 | 60026893 | F077C | WANDOAN | SR | 60007202 | MILE | MILES 33/11kV SUBSTATION | 28910 | 70 | 0.089845 | 2597.415 | Pole Top | 138883.7817
2021_2022 | AER | UNPLANNED | 22SW7498 | 60026734 | F2661 | CROWS NEST INDUSTRIAL ROAD | LR | 60007231 | CRNE | CROWS NEST 33/11KV SUB (ME032) | 2092.8833 | 7 | 0.018439 | 38.5906 | Pole | 2063.439
2021_2022 | AER | UNPLANNED | 22SW7577 | 60026836 | F4480 | VIEW STREET | UR | 60007241 | EATO | EAST TOOWOOMBA 33/11KV SUB | 167336.5333 | 947 | 0.014596 | 2442.4324 | Pole Top | 130596.8579
2021_2022 | AER | UNPLANNED | 22SW7737 | 82980894 | F2687 | DARLING HEIGHTS | SR | 60331401 | KESP | KEARNEYS SPRINGS 110/11KV SUB (KESP) | 395 | 5 | 0.020954 | 8.2768 | Pole Top | 442.5579
2021_2022 | AER | UNPLANNED | 22SW7738 | 60026725 | F2530 | CLIFTON WEST | SR | 60007249 | CLIF | CLIFTON 33/11KV SUB (ME399) | 244 | 4 | 0.023728 | 5.7897 | Pole Top | 309.576
2021_2022 | AER | UNPLANNED | 22SW7766 | 60026725 | F2530 | CLIFTON WEST | SR | 60007249 | CLIF | CLIFTON 33/11KV SUB (ME399) | 53927.5 | 30 | 0.023728 | 1279.61 | Pole Top | 68420.7466
2021_2022 | AER | UNPLANNED | 22SW7773 | 60026820 | F4130 | SHIEL STREET | UR | 60007241 | EATO | EAST TOOWOOMBA 33/11KV SUB | 7820.4 | 76 | 0.013552 | 105.9821 | Pole Top | 5666.8603
2021_2022 | AER | UNPLANNED | 22SW7827 | 60026794 | F3765 | NOBBY | LR | 60007240 | MOSI | MOUNT SIBLEY 33/11KV SUB | 41310 | 243 | 0.03051 | 1260.35 | Pole Top | 67390.9162
2021_2022 | AER | UNPLANNED | 22SW8000 | 60026816 | F4090 | ROSSVALE | LR | 60007248 | PURR | PURRAWUNDA 33/11KV SUB | 3496 | 23 | 0.019674 | 68.7799 | Pole Top | 3677.6593
2021_2022 | AER | UNPLANNED | 22SW8214 | 83850831 | GRANADA | GRANADA | SR | 82709366 | SKIB | SKID B 33/11kV SUBSTATION | 7881 | 37 | 0.021253 | 167.4953 | Pole Top | 8955.9713
2021_2022 | AER | UNPLANNED | 22SW8468 | 60026792 | F3705 | MYWYBILLA | SR | 60007238 | NORW | NORWIN 33/11KV SUB (ME074) | 25378.6833 | 31 | 0.043135 | 1094.7166 | Pole Top | 58534.4942
2021_2022 | AER | UNPLANNED | 22SW8520 | 60026838 | F4545 | WARWICK INDUSTRIAL | SR | 84536204 | WAEA | WARWICK EAST 33/11KV SUB | 2400 | 16 | 0.092238 | 221.3709 | Pole Top | 11836.7024
2021_2022 | AER | UNPLANNED | 22WB0123 | 50000073 | HD-C | TAKURA | SR | 50000071 | HOWA | HOWARD 66/11KV SUB | 129 | 1 | 0.015022 | 1.9379 | Pole Top | 103.617
2021_2022 | AER | UNPLANNED | 22WB0315 | 50000127 | MG-E | REDGATE | LR | 50000121 | MURG | Murgon 66/11kV Substation | 49912.0333 | 74 | 0.022065 | 1101.3108 | Pole Top | 58887.0891
2021_2022 | AER | UNPLANNED | 22WB0399 | 50000130 | MG-H | TANSEY | LR | 50000121 | MURG | Murgon 66/11kV Substation | 35561 | 158 | 0.028457 | 1011.9667 | Pole Top | 54109.8583
2021_2022 | AER | UNPLANNED | 22WB0905 | 50000145 | NN-F | BROOKLANDS | LR | 50000141 | NANA | NANANGO 66/11KV SUB (NANA) | 561.8 | 4 | 0.19167 | 107.6796 | Pole Top | 5757.6291
2021_2022 | AER | UNPLANNED | 22WB0986 | 50000137 | MV-B | MOORLANDS | SR | 50000136 | MEAD | MEADOWVALE 66/11KV SUB (MEAD) | 9744 | 168 | 0.046643 | 454.4846 | Pole Top | 24301.2911
2022_2023 | AER | UNPLANNED | 22WB10402 | 50000125 | MG-C | MEATWORKS | LR | 50000121 | MURG | Murgon 66/11kV Substation | 5659.8667 | 22 | 0.022846 | 129.306 | Pole Top | 6913.9898
2022_2023 | AER | UNPLANNED | 22WB10503 | 50000020 | CH-C | STOCKYARD | SR | 50000019 | CHIL | Childers 66/11kV Substation | 2060 | 20 | 0.021884 | 45.0808 | Pole Top | 2410.4728
2022_2023 | AER | UNPLANNED | 22WB10782 | 50000025 | DG-C | TOWN | LR | 50000024 | DEGI | DEGILBO 66/11KV SUB (DG) | 2925 | 39 | 0.021726 | 63.5489 | Pole Top | 3397.9602
2022_2023 | AER | UNPLANNED | 22WB11266 | 50000068 | GY-D | BINJOUR | SR | 50000064 | GAYN | Gayndah 66/11kV Substation | 10584 | 147 | 0.021866 | 231.4334 | Pole Top | 12374.7451
2022_2023 | AER | UNPLANNED | 22WB11502 | 50000027 | DG-A | MT GOONANEMAN | SR | 50000024 | DEGI | DEGILBO 66/11KV SUB (DG) | 936 | 4 | 0.039664 | 37.1252 | Pole | 1985.0857
2022_2023 | AER | UNPLANNED | 22WB11712 | 50000067 | GY-C | HUMPHREY | SR | 50000064 | GAYN | Gayndah 66/11kV Substation | 2145.2667 | 2 | 0.046894 | 100.5995 | Pole Top | 5379.0536
2022_2023 | AER | UNPLANNED | 22WB11998 | 50000151 | OY-F | RIVER ROAD | SR | 50000147 | OWAN | OWANYILLA 66/11KV SUB | 824.75 | 5 | 0.025828 | 21.3019 | Pole Top | 1139.0143
2022_2023 | AER | UNPLANNED | 22WB12020 | 50000049 | FF-D | NORTH GREGORY | SR | 50000045 | FF | Farnsfield 66/11kV Substation | 8424 | 81 | 0.054793 | 461.5725 | Pole Top | 24680.2839
2022_2023 | AER | UNPLANNED | 22WB12386 | 50000065 | GY-B | WETHERON | LR | 50000064 | GAYN | Gayndah 66/11kV Substation | 890 | 5 | 0.023303 | 20.74 | Pole Top | 1108.9691
2022_2023 | AER | UNPLANNED | 22WB12468 | 50000116 | MD-A | O'BIL BIL FDR | SR | 82738151 | MUTO | MUNDUBBERA TOWN 66/11KV SUBSTATION | 17848.6667 | 74 | 0.020061 | 358.0567 | Pole | 19145.2931
2022_2023 | AER | UNPLANNED | 22WB12907 | 50000020 | CH-C | STOCKYARD | SR | 50000019 | CHIL | Childers 66/11kV Substation | 8656.5333 | 37 | 0.021884 | 189.4388 | Pole Top | 10129.2904
2022_2023 | AER | UNPLANNED | 22WB12948 | 50000118 | MD-C | BOYNE FDR | LR | 82738151 | MUTO | MUNDUBBERA TOWN 66/11KV SUBSTATION | 18421.8167 | 79 | 0.048112 | 886.3048 | Pole Top | 47390.7199
2022_2023 | AER | UNPLANNED | 22WB13042 | 50000229 | WL-A | BELLS BRIDGE | LR | 50000228 | WOOL | Woolooga 66/11kV Substation | 3354 | 26 | 0.018724 | 62.7989 | Pole Top | 3357.8584
2022_2023 | AER | UNPLANNED | 22WB13062 | 50000233 | WV-C | MORGANVILLE | SR | 50000231 | WALL | WALLAVILLE 66/11KV SUB | 180 | 1 | 0.016583 | 2.985 | Pole Top | 159.6082
2022_2023 | AER | UNPLANNED | 22WB13162 | 50000057 | GC-A | GUNALDA | LR | 50000056 | GOOT | GOOTCHIE 66/11KV SUB | 35582.2667 | 49 | 0.019069 | 678.5217 | Pole Top | 36280.5554
2021_2022 | AER | UNPLANNED | 22WB1335 | 50000068 | GY-D | BINJOUR | SR | 50000064 | GAYN | Gayndah 66/11kV Substation | 56585 | 114 | 0.018309 | 1036.0402 | Pole Top | 55397.0718
2021_2022 | AER | UNPLANNED | 22WB1336 | 50000160 | PT-B | DURONG | LR | 50000158 | PROT | PROSTON 66/11KV SUB | 48093.9667 | 106 | 0.017906 | 861.1678 | Pole Top | 46046.6423
2022_2023 | AER | UNPLANNED | 22WB13912 | 50000150 | OY-D | QWRC | SR | 50000147 | OWAN | OWANYILLA 66/11KV SUB | 85239.4333 | 766 | 0.018512 | 1577.9201 | Pole Top | 84371.3854
2021_2022 | AER | UNPLANNED | 22WB1519 | 50000058 | GC-B | NETHERBY | SR | 50000056 | GOOT | GOOTCHIE 66/11KV SUB | 9100.8333 | 25 | 0.030778 | 280.1069 | Pole Top | 14977.3163
2021_2022 | AER | UNPLANNED | 22WB1696 | 50000044 | EV-C | EIDSVOLD | LR | 50000042 | EIDS | EIDSVOLD 66/11KV SUB (EV) | 214 | 2 | 0.018203 | 3.8954 | Pole Top | 208.2877
2021_2022 | AER | UNPLANNED | 22WB1991 | 50000073 | HD-C | TAKURA | SR | 50000071 | HOWA | HOWARD 66/11KV SUB | 187725.6 | 1644 | 0.015022 | 2820.037 | Pole Top | 150787.3772
2021_2022 | AER | UNPLANNED | 22WB2344 | 50000025 | DG-C | TOWN | LR | 50000024 | DEGI | DEGILBO 66/11KV SUB (DG) | 707697.7 | 823 | 0.013644 | 9656.1103 | Pole | 516312.2168
2021_2022 | AER | UNPLANNED | 22WB2344 | 50000026 | DG-D | MINES | SR | 50000024 | DEGI | DEGILBO 66/11KV SUB (DG) | 58473.2 | 68 | 0.016347 | 955.8527 | Pole | 51109.4419
2021_2022 | AER | UNPLANNED | 22WB2344 | 50000027 | DG-A | MT GOONANEMAN | SR | 50000024 | DEGI | DEGILBO 66/11KV SUB (DG) | 130704.8 | 152 | 0.052742 | 6893.6915 | Pole | 368605.6835
2021_2022 | AER | UNPLANNED | 22WB2344 | 50000028 | DG-B | CORINGA | SR | 50000024 | DEGI | DEGILBO 66/11KV SUB (DG) | 89429.6 | 104 | 0.011384 | 1018.057 | Pole | 54435.5066
2021_2022 | AER | UNPLANNED | 22WB3187 | 50000130 | MG-H | TANSEY | LR | 50000121 | MURG | Murgon 66/11kV Substation | 45811 | 157 | 0.028457 | 1303.653 | Pole | 69706.3277
2021_2022 | AER | UNPLANNED | 22WB3959 | 50000068 | GY-D | BINJOUR | SR | 50000064 | GAYN | Gayndah 66/11kV Substation | 31188.95 | 159 | 0.018309 | 571.0525 | Pole Top | 30534.1787
2021_2022 | AER | UNPLANNED | 22WB3983 | 50000125 | MG-C | MEATWORKS | LR | 50000121 | MURG | Murgon 66/11kV Substation | 295 | 5 | 0.017075 | 5.0373 | Pole Top | 269.342
2021_2022 | AER | UNPLANNED | 22WB4045 | 50000065 | GY-B | WETHERON | LR | 50000064 | GAYN | Gayndah 66/11kV Substation | 136 | 2 | 0.02095 | 2.8492 | Pole | 152.3478
2021_2022 | AER | UNPLANNED | 22WB4256 | 50000235 | WV-E | WALLAVILLE | SR | 50000231 | WALL | WALLAVILLE 66/11KV SUB | 79 | 1 | 0.024784 | 1.9579 | Pole Top | 104.6891
2021_2022 | AER | UNPLANNED | 22WB5049 | 50000160 | PT-B | DURONG | LR | 50000158 | PROT | PROSTON 66/11KV SUB | 198302.2 | 282 | 0.017906 | 3550.7878 | Pole Top | 189860.6231
2021_2022 | AER | UNPLANNED | 22WB5508 | 50000050 | FF-E | KOWBI | SR | 50000045 | FF | Farnsfield 66/11kV Substation | 1428 | 14 | 0.02329 | 33.2578 | Pole Top | 1778.2971
2021_2022 | AER | UNPLANNED | 22WB5540 | 50000168 | RS-H | BADDOW | SR | 50000162 | ROST | ROCKY STREET 66/11KV SUB (RS) | 1493.9167 | 13 | 0.062185 | 92.899 | Pole Top | 4967.3113
2021_2022 | AER | UNPLANNED | 22WB5564 | 50000160 | PT-B | DURONG | LR | 50000158 | PROT | PROSTON 66/11KV SUB | 234316.2 | 282 | 0.017906 | 4195.6524 | Pole Top | 224341.5339
2021_2022 | AER | UNPLANNED | 22WB6050 | 50000021 | CH-E | REDRIDGE | SR | 50000019 | CHIL | Childers 66/11kV Substation | 9108.9 | 54 | 0.019071 | 173.7201 | Pole Top | 9288.8145
2021_2022 | AER | UNPLANNED | 22WB6061 | 50000150 | OY-D | QWRC | SR | 50000147 | OWAN | OWANYILLA 66/11KV SUB | 1255 | 5 | 0.017423 | 21.8662 | Pole Top | 1169.1872
2021_2022 | AER | UNPLANNED | 22WB6152 | 50000241 | YR-F | COOYAR | LR | 50000237 | YARR | YARRAMAN 66/11KV SUB | 6652 | 4 | 0.011203 | 74.5216 | Pole Top | 3984.6699
2021_2022 | AER | UNPLANNED | 22WB6679 | 50000174 | SB-D | DR MAYS | SR | 50000172 | SOBU | SOUTH BUNDABERG 66/11KV SUB (SB) | 180 | 1 | 0.024467 | 4.404 | Pole Top | 235.4818
2021_2022 | AER | UNPLANNED | 22WB6697 | 50000129 | MG-G | GOOMERI | SR | 50000121 | MURG | Murgon 66/11kV Substation | 23868.3333 | 50 | 0.013898 | 331.7242 | Pole Top | 17737.2919
2022_2023 | AER | UNPLANNED | 22WB7727 | 50000229 | WL-A | BELLS BRIDGE | LR | 50000228 | WOOL | Woolooga 66/11kV Substation | 326 | 2 | 0.018724 | 6.1039 | Pole Top | 326.375
2022_2023 | AER | UNPLANNED | 22WB7739 | 50000160 | PT-B | DURONG | LR | 50000158 | PROT | PROSTON 66/11KV SUB | 1541.7333 | 4 | 0.016978 | 26.1748 | Pole Top | 1399.5664
2022_2023 | AER | UNPLANNED | 22WB8110 | 50000160 | PT-B | DURONG | LR | 50000158 | PROT | PROSTON 66/11KV SUB | 65159.2167 | 281 | 0.016978 | 1106.2414 | Pole Top | 59150.7276
2022_2023 | AER | UNPLANNED | 22WB8337 | 50000061 | GV-D | ELLIOTT RIVER | SR | 50000060 | GIVE | GIVELDA 66/11KV SUB | 24648 | 88 | 0.031475 | 775.791 | Pole Top | 41481.5468
2022_2023 | AER | UNPLANNED | 22WB8498 | 50000241 | YR-F | COOYAR | LR | 50000237 | YARR | YARRAMAN 66/11KV SUB | 8372.7 | 27 | 0.014098 | 118.0391 | Pole Top | 6311.549
2022_2023 | AER | UNPLANNED | 22WB8552 | 50000094 | KR-E | KUMBIA | LR | 50000087 | KING | Kingaroy 66/11kV Substation | 4054.6 | 12 | 0.021611 | 87.6231 | Pole Top | 4685.2057
2022_2023 | AER | UNPLANNED | 22WB8640 | 50000154 | PB-C | DOOLONG SOUTH | SR | 50000152 | PIAL | PIALBA 66/11kV SUBSTATION | 420 | 4 | 0.024644 | 10.3507 | Pole Top | 553.4507
2022_2023 | AER | UNPLANNED | 22WB8644 | 50000116 | MD-A | O'BIL BIL FDR | SR | 82738151 | MUTO | MUNDUBBERA TOWN 66/11KV SUBSTATION | 1862 | 7 | 0.020061 | 37.353 | Pole Top | 1997.266
2022_2023 | AER | UNPLANNED | 22WB8972 | 50000084 | KL-B | OAKVIEW | SR | 50000083 | KITO | KILKIVAN TOWN 66/11kV SUBSTATION | 300 | 2 | 0.02032 | 6.0959 | Pole Top | 325.9462
2022_2023 | AER | UNPLANNED | 22WB9061 | 50000065 | GY-B | WETHERON | LR | 50000064 | GAYN | Gayndah 66/11kV Substation | 7200 | 1 | 0.023303 | 167.7845 | Pole Top | 8971.4353
2022_2023 | AER | UNPLANNED | 22WB9171 | 50000185 | SK-C | SHARON | SR | 50000181 | SOKO | SOUTH KOLAN 66/11KV SUB | 35504 | 229 | 0.026513 | 941.3005 | Pole Top | 50331.3361
2022_2023 | AER | UNPLANNED | 22WB9376 | 50000118 | MD-C | BOYNE FDR | LR | 82738151 | MUTO | MUNDUBBERA TOWN 66/11KV SUBSTATION | 276.1 | 1 | 0.048112 | 13.2836 | Pole Top | 710.2762
2022_2023 | AER | UNPLANNED | 22WB9421 | 50000145 | NN-F | BROOKLANDS | LR | 50000141 | NANA | NANANGO 66/11KV SUB (NANA) | 97413.6 | 126 | 0.19124 | 18629.145 | Pole | 996100.3838
2022_2023 | AER | UNPLANNED | 22WB9497 | 50000084 | KL-B | OAKVIEW | SR | 50000083 | KITO | KILKIVAN TOWN 66/11kV SUBSTATION | 2145 | 15 | 0.02032 | 43.5855 | Pole Top | 2330.5153
2022_2023 | AER | UNPLANNED | 23CA0221 | 83022292 | FA0452 | FINGERBOARD | LR | 82613011 | AGWA | AGNES WATER 66/22KV SUBSTATION | 60 | 1 | 0.016958 | 1.0175 | Pole Top | 54.4035
2022_2023 | AER | UNPLANNED | 23CA0252 | 40001033 | BG207 | BINGEGANG RURAL CIRCUIT | LR | 40017963 | BING | BINGEGANG 66/22KV SUB (BGSS) | 51308.4 | 99 | 0.028826 | 1479.0323 | Pole Top | 79083.8549
2022_2023 | AER | UNPLANNED | 23CA0252 | 40001052 | BG208 | Pumping Station | LR | 40017963 | BING | BINGEGANG 66/22KV SUB (BGSS) | 25913.3333 | 50 | 0.28395 | 7358.197 | Pole Top | 393442.7917
2022_2023 | AER | UNPLANNED | 23CA0460 | 40000998 | CL203 | Clermont Town | SR | 40000023 | CLER | CLERMONT 132/66/22/11KV SUB (T071) CLBS | 18224.2667 | 91 | 0.02692 | 490.5964 | Pole Top | 26232.187
2022_2023 | AER | UNPLANNED | 23CA0917 | 40001061 | BB208 | Aramac | LR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 60905.6 | 8 | 0.021067 | 1283.1119 | Pole | 68607.9947
2022_2023 | AER | UNPLANNED | 23CA1178 | 40001117 | PD207 | Glendale Road | SR | 40017986 | PAND | PANDOIN 66/22KV SUB (PDBS) | 69829.4667 | 301 | 0.041711 | 2912.6802 | Pole Top | 155741.0077
2022_2023 | AER | UNPLANNED | 23CA1305 | 40001072 | LR209 | Ilfracombe | LR | 40017977 | LONG | LONGREACH 66/22KV SUB (LRSS) | 9381 | 59 | 0.023042 | 216.1553 | Pole Top | 11557.8218
2023_2024 | AER | UNPLANNED | 23CA13126 | 82563612 | EM256 | Rubyvale-Capella | LR | 40017951 | EMER | EMERALD 66/22KV SUB (EMSS) | 906318.6333 | 1778 | 0.035155 | 31861.5018 | Pole | 1703634.5001
2022_2023 | AER | UNPLANNED | 23CA1413 | 40001010 | CL204 | Capella | LR | 40000023 | CLER | CLERMONT 132/66/22/11KV SUB (T071) CLBS | 14275.6667 | 10 | 0.030197 | 431.0867 | Pole | 23050.2073
2022_2023 | AER | UNPLANNED | 23CA1505 | 40200483 | SB202 | ROLLESTON NORTH | LR | 40017982 | SOBL | SOUTH BLACKWATER 66/22KV SUB (SBSS) | 9270 | 90 | 0.028185 | 261.2766 | Pole Top | 13970.4597
2023_2024 | AER | UNPLANNED | 23CA15342 | 40001010 | CL204 | Capella | LR | 40000023 | CLER | CLERMONT 132/66/22/11KV SUB (T071) CLBS | 50131.2 | 42 | 0.027284 | 1367.7862 | Pole | 73135.5256
2023_2024 | AER | UNPLANNED | 23CA16557 | 40001061 | BB208 | Aramac | LR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 22016.3333 | 20 | 0.025096 | 552.5221 | Pole | 29543.3577
2023_2024 | AER | UNPLANNED | 23CA16684 | 40001204 | YP108 | Braithwaite St | SR | 40017948 | YPSS | Yeppoon 66/22/11kV Substation | 52878.4 | 664 | 0.017952 | 949.2482 | Pole | 50756.3012
2023_2024 | AER | UNPLANNED | 23CA16938 | 40001010 | CL204 | Capella | LR | 40000023 | CLER | CLERMONT 132/66/22/11KV SUB (T071) CLBS | 14490 | 10 | 0.027284 | 395.347 | Pole | 21139.206
2022_2023 | AER | UNPLANNED | 23CA1704 | 40001138 | RL201 | Port Alma | SR | 40017929 | RLSS | Raglan 66/22kV Substation | 1054.9333 | 46 | 0.20271 | 213.8447 | Pole Top | 11434.2747
2022_2023 | AER | UNPLANNED | 23CA1704 | 40001185 | EQ101 | QCL Quarry | SR | 40017972 | EAEQ | EAST END QUARRY 66/11KV SUB (EQSS) | 20.9333 | 1 | 7.4431 | 155.8097 | Pole Top | 8331.1448
2022_2023 | AER | UNPLANNED | 23CA1704 | 40001210 | RL202 | Mt Larcom | LR | 40017929 | RLSS | Raglan 66/22kV Substation | 13232.5333 | 577 | 0.02164 | 286.3568 | Pole Top | 15311.499
2023_2024 | AER | UNPLANNED | 23CA17678 | 40000985 | MT103 | Selene | LR | 40017931 | MTSS | Monto 66/11kV Substation | 8247.0333 | 31 | 0.022573 | 186.1572 | Pole | 9953.827
2023_2024 | AER | UNPLANNED | 23CA17964 | 40001061 | BB208 | Aramac | LR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 7620.9 | 3 | 0.025096 | 191.2542 | Pole | 10226.3611
2023_2024 | AER | UNPLANNED | 23CA18028 | 40001061 | BB208 | Aramac | LR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 33100 | 28 | 0.025096 | 830.6779 | Pole | 44416.3487
2023_2024 | AER | UNPLANNED | 23CA18467 | 40001061 | BB208 | Aramac | LR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 4744.3333 | 20 | 0.025096 | 119.0638 | Pole | 6366.3433
2022_2023 | AER | UNPLANNED | 23CA1869 | 40001175 | BR107 | BR107 Tarcoola | UR | 40017973 | BRSS | Boyne Residential 66/11kV Substation | 12688 | 61 | 0.01982 | 251.4722 | Pole Top | 13446.2181
2023_2024 | AER | UNPLANNED | 23CA18939 | 82563612 | EM256 | Rubyvale-Capella | LR | 40017951 | EMER | EMERALD 66/22KV SUB (EMSS) | 370908.4167 | 1775 | 0.035155 | 13039.2323 | Pole | 697207.7499
2022_2023 | AER | UNPLANNED | 23CA2232 | 40000966 | MR202 | Moura Rural | LR | 40000028 | MOUR | MOURA MRBS 132/66/11KV SUB (T027) | 1765.2 | 1 | 0.049952 | 88.1749 | Pole | 4714.7116
2022_2023 | AER | UNPLANNED | 23CA2293 | 40001068 | LR210 | Isisford | LR | 40017977 | LONG | LONGREACH 66/22KV SUB (LRSS) | 16926 | 93 | 0.02518 | 426.1985 | Pole Top | 22788.8339
2022_2023 | AER | UNPLANNED | 23CA2359 | 40001119 | PH102 | Alexandra St | SR | 40017939 | PHSS | Parkhurst 66/11kV Substation | 33299.8167 | 269 | 0.029906 | 995.8527 | Pole Top | 53248.2445
2022_2023 | AER | UNPLANNED | 23CA2978 | 40000965 | MR201 | Moura Urban | LR | 40000028 | MOUR | MOURA MRBS 132/66/11KV SUB (T027) | 594.5 | 2 | 0.12257 | 72.8674 | Pole Top | 3896.2215
2022_2023 | AER | UNPLANNED | 23CA3238 | 40000977 | WN211 | Jambin | LR | 40017934 | WOWA | WOWAN 66/22KV SUB (WNSS) | 8084.3333 | 20 | 0.02231 | 180.3579 | Pole Top | 9643.738
2022_2023 | AER | UNPLANNED | 23CA3439 | 40000998 | CL203 | Clermont Town | SR | 40000023 | CLER | CLERMONT 132/66/22/11KV SUB (T071) CLBS | 126530.5 | 170 | 0.02692 | 3406.1948 | Pole Top | 182129.2343
2022_2023 | AER | UNPLANNED | 23CA3471 | 40001038 | BW220 | Duaringa | LR | 40000019 | BLAC | BLACKWATER BWBS 132/66/22KV SUB (T032) | 11318 | 36 | 0.04901 | 554.6904 | Pole Top | 29659.297
2022_2023 | AER | UNPLANNED | 23CA3525 | 40001139 | RL203 | Bajool | LR | 40017929 | RLSS | Raglan 66/22kV Substation | 12761.4 | 36 | 0.04085 | 521.2978 | Pole Top | 27873.7923
2022_2023 | AER | UNPLANNED | 23CA3649 | 40001105 | LC107 | Rockonia Rd | UR | 40017944 | LCSS | Lakes Creek 66/11kV Substation | 5220 | 58 | 0.016131 | 84.2044 | Pole Top | 4502.4067
2022_2023 | AER | UNPLANNED | 23CA4611 | 40001006 | EM226 | Emerald North | SR | 40017951 | EMER | EMERALD 66/22KV SUB (EMSS) | 11844.75 | 15 | 0.03543 | 419.6605 | Pole | 22439.2445
2022_2023 | AER | UNPLANNED | 23CA4671 | 40001111 | MA111 | Stanwell | LR | 40017988 | MALC | MALCHI MASS 66/11KV SUB | 19125 | 129 | 0.022508 | 430.4738 | Pole Top | 23017.4351
2022_2023 | AER | UNPLANNED | 23CA4907 | 40001039 | CM201 | Comet | SR | 40017961 | COME | COMET 66/22KV SUB (CMSS) | 5986.6667 | 100 | 0.056073 | 335.6895 | Pole Top | 17949.3188
2022_2023 | AER | UNPLANNED | 23CA4907 | 40200482 | CM202 | COMET RURALS | SR | 40017961 | COME | COMET 66/22KV SUB (CMSS) | 1796 | 30 | 0.22615 | 406.1674 | Pole Top | 21717.7707
2022_2023 | AER | UNPLANNED | 23CA4907 | 111705159 | 2322 | LURLINE | SR | 40017961 | COME | COMET 66/22KV SUB (CMSS) | 299.3333 | 5 | 0.24296 | 72.7265 | Pole Top | 3888.6839
2022_2023 | AER | UNPLANNED | 23CA4988 | 40216323 | BK206 | Tambo | LR | 40018027 | BLAK | BLACKALL 66/22KV SUB (BKSS) | 3774 | 37 | 0.024256 | 91.5414 | Pole Top | 4894.7163
2022_2023 | AER | UNPLANNED | 23CA6000 | 40001177 | CI104 | CI104 Clinton Park | SR | 40017975 | CISS | Clinton 66/11kV Substation | 8910 | 54 | 0.021482 | 191.4002 | Pole Top | 10234.1706
2022_2023 | AER | UNPLANNED | 23CA6655 | 40001139 | RL203 | Bajool | LR | 40017929 | RLSS | Raglan 66/22kV Substation | 30869.1 | 243 | 0.04085 | 1260.9896 | Pole Top | 67425.1164
2022_2023 | AER | UNPLANNED | 23CA6774 | 40200483 | SB202 | ROLLESTON NORTH | LR | 40017982 | SOBL | SOUTH BLACKWATER 66/22KV SUB (SBSS) | 1805.4667 | 88 | 0.028185 | 50.8874 | Pole Top | 2720.9492
2023_2024 | AER | UNPLANNED | 23CA8180 | 40001184 | CP105 | Calliope | SR | 40017974 | CALL | CALLIOPE 66/11KV SUB (CPSS) | 9393.0167 | 23 | 0.024932 | 234.1909 | Pole | 12522.1877
2022_2023 | AER | UNPLANNED | 23FN0214 | 10020844 | 2CAB | CARBINE | SR | 10030291 | MOMO | MT MOLLOY 66/22KV SUBSTATION | 118495.2667 | 661 | 0.029129 | 3451.6259 | Pole Top | 184558.4352
2022_2023 | AER | UNPLANNED | 23FN0214 | 10020845 | 2CAS | CASSOWARY | SR | 10030292 | MOSSMAN | Mossman 66/22kV Substation | 607.8667 | 97 | 0.019553 | 11.8855 | Pole Top | 635.5187
2022_2023 | AER | UNPLANNED | 23FN0214 | 10020846 | 2MOS | MOSSMAN | SR | 10030292 | MOSSMAN | Mossman 66/22kV Substation | 7482.4 | 1194 | 0.036067 | 269.865 | Pole Top | 14429.6819
2022_2023 | AER | UNPLANNED | 23FN0214 | 10020847 | 2DAI | DAINTREE | SR | 10030292 | MOSSMAN | Mossman 66/22kV Substation | 11981.8667 | 1912 | 0.020991 | 251.5128 | Pole Top | 13448.3907
2022_2023 | AER | UNPLANNED | 23FN0214 | 10020848 | 2SCK | STEWART CREEK | SR | 10030292 | MOSSMAN | Mossman 66/22kV Substation | 651.7333 | 104 | 0.027904 | 18.1862 | Pole Top | 972.4174
2022_2023 | AER | UNPLANNED | 23FN0214 | 10135223 | 2YAL | YALKULA | SR | 10030291 | MOMO | MT MOLLOY 66/22KV SUBSTATION | 1971.9333 | 11 | 0.018305 | 36.0954 | Pole Top | 1930.0209
2022_2023 | AER | UNPLANNED | 23FN0605 | 10020670 | 2GIR | GILBERT RIVER | LR | 10030300 | GEOR | GEORGETOWN 132/66/22/6.6KV SUB (GEOR) | 15432.0667 | 47 | 0.088941 | 1372.5416 | Pole | 73389.7976
2022_2023 | AER | UNPLANNED | 23FN0753 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 8857.8 | 7 | 0.076656 | 679.0024 | Pole | 36306.2587
2022_2023 | AER | UNPLANNED | 23FN0854 | 10020828 | 2TAR | TARZALI | LR | 10030331 | ATHE | Atherton 66/22kV Sub (ATHE) | 1696 | 16 | 0.018511 | 31.3952 | Pole Top | 1678.7036
2022_2023 | AER | UNPLANNED | 23FN1048 | 10020855 | 2MUT | MUTCHILBA | SR | 10030295 | DIMB | Dimbulah 66/22kV Substation | 402958.25 | 655 | 0.041043 | 16538.5362 | Pole | 884315.5285
2022_2023 | AER | UNPLANNED | 23FN1048 | 10020856 | 2PET | PETFORD | SR | 10030295 | DIMB | Dimbulah 66/22kV Substation | 145173.6 | 144 | 0.03421 | 4966.4335 | Pole | 265555.1973
2022_2023 | AER | UNPLANNED | 23FN1048 | 10020857 | 2WOL | WOLFRAM | SR | 10030295 | DIMB | Dimbulah 66/22kV Substation | 214522.95 | 213 | 0.052193 | 11196.5862 | Pole | 598681.466
2022_2023 | AER | UNPLANNED | 23FN1048 | 83031320 | CHILLAGOE | CHILLAGOE | SR | 83029417 | CHIA | CHILLAGOE 66/22KV SUBSTATION | 191060.45 | 163 | 0.03577 | 6834.2853 | Pole | 365429.2351
2022_2023 | AER | UNPLANNED | 23FN1048 | 83031323 | ALMADEN | ALMADEN | SR | 83029417 | CHIA | CHILLAGOE 66/22KV SUBSTATION | 48058.15 | 41 | 1.4882 | 71518.329 | Pole | 3824085.0492
2022_2023 | AER | UNPLANNED | 23FN1086 | 10020670 | 2GIR | GILBERT RIVER | LR | 10030300 | GEOR | GEORGETOWN 132/66/22/6.6KV SUB (GEOR) | 85 | 1 | 0.088941 | 7.56 | Pole Top | 404.2318
2022_2023 | AER | UNPLANNED | 23FN1329 | 10020806 | 2PEE | PEERAMON | LR | 10030331 | ATHE | Atherton 66/22kV Sub (ATHE) | 155.4667 | 1 | 0.018729 | 2.9118 | Pole | 155.6935
2023_2024 | AER | UNPLANNED | 23FN13857 | 10020670 | 2GIR | GILBERT RIVER | LR | 10030300 | GEOR | GEORGETOWN 132/66/22/6.6KV SUB (GEOR) | 18885.8167 | 17 | 0.065037 | 1228.2717 | Pole | 65675.6897
2023_2024 | AER | UNPLANNED | 23FN14249 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 8855.7 | 7 | 0.079143 | 700.869 | Pole | 37475.4658
2023_2024 | AER | UNPLANNED | 23FN14668 | 10020675 | 2KAR | KARUMBA | SR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 104120 | 380 | 0.043894 | 4570.2793 | Pole | 244372.8361
2023_2024 | AER | UNPLANNED | 23FN15148 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 220731.8333 | 65 | 0.079143 | 17469.4379 | Pole | 934090.8425
2023_2024 | AER | UNPLANNED | 23FN16641 | 10020844 | 2CAB | CARBINE | SR | 10030291 | MOMO | MT MOLLOY 66/22KV SUBSTATION | 210842.45 | 653 | 0.030946 | 6524.6915 | Pole | 348875.2548
2023_2024 | AER | UNPLANNED | 23FN16800 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 70793 | 60 | 0.079143 | 5602.7891 | Pole | 299581.1343
2023_2024 | AER | UNPLANNED | 23FN16982 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 7811.8667 | 7 | 0.079143 | 618.2566 | Pole | 33058.182
2022_2023 | AER | UNPLANNED | 23FN2651 | 10020850 | 2BAR | BARRINE | SR | 10030331 | ATHE | Atherton 66/22kV Sub (ATHE) | 154050 | 1555 | 0.018072 | 2783.9372 | Pole Top | 148857.1196
2022_2023 | AER | UNPLANNED | 23FN3000 | 10020771 | 2CW2 | CARDWELL NO 2 | LR | 10030282 | TULL | TULLY 132/22KV SUBSTATION (TULL) | 38548 | 202 | 0.040386 | 1556.7808 | Pole Top | 83241.0686
2022_2023 | AER | UNPLANNED | 23FN3625 | 82889011 | 2EME | EMERALD CREEK | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 1171.8 | 6 | 0.029344 | 34.3857 | Pole Top | 1838.6016
2022_2023 | AER | UNPLANNED | 23FN3628 | 10128810 | 2CHL | CHILVERTON | SR | 10128809 | RAVENSHOE | Ravenshoe 66/22kV Substation | 63 | 1 | 0.017796 | 1.1211 | Pole Top | 59.9471
2022_2023 | AER | UNPLANNED | 23FN3796 | 10131881 | 0KCS | KIDSTON CONTINGENCY SUPPLY 6.6KV FEEDER | SR | 10030299 | KIDS | KIDSTON 132/6.6kV SUBSTATION | 19023 | 17 | 2.0149 | 38330.024 | Pole | 2049506.3811
2022_2023 | AER | UNPLANNED | 23FN4039 | 10020837 | 2TAB | TABACUM | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 1894.6333 | 503 | 0.049832 | 94.4137 | Pole | 5048.3017
2022_2023 | AER | UNPLANNED | 23FN4039 | 10020844 | 2CAB | CARBINE | SR | 10030291 | MOMO | MT MOLLOY 66/22KV SUBSTATION | 148328.7 | 657 | 0.029129 | 4320.6382 | Pole | 231024.5256
2022_2023 | AER | UNPLANNED | 23FN4039 | 10135223 | 2YAL | YALKULA | SR | 10030291 | MOMO | MT MOLLOY 66/22KV SUBSTATION | 2483.4333 | 11 | 0.018305 | 45.4582 | Pole | 2430.6492
2022_2023 | AER | UNPLANNED | 23FN4205 | 10020772 | 2SI2 | SILKWOOD NO2 | LR | 10030283 | INNI | Innisfail 132/22kV Substation | 1687 | 7 | 0.02896 | 48.8562 | Pole Top | 2612.3395
2022_2023 | AER | UNPLANNED | 23FN4560 | 10020659 | 2HOP | HOPEVALE | LR | 10030297 | COOK | Cooktown 66/22kV Substation | 4694 | 17 | 0.028613 | 134.3091 | Pole Top | 7181.5054
2022_2023 | AER | UNPLANNED | 23FN4692 | 10020841 | 2BIB | BIBOOHRA | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 296 | 2 | 0.033016 | 9.7729 | Pole Top | 522.5558
2022_2023 | AER | UNPLANNED | 23FN4911 | 10020832 | 2CO3 | COOK NO 3 | UR | 10030288 | KAMERUNGA | Kamerunga 132/22kV Substation | 9541.5833 | 55 | 0.035787 | 341.4629 | Pole Top | 18258.0219
2022_2023 | AER | UNPLANNED | 23FN5238 | 10020842 | 2KUR | KURANDA | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 687.25 | 5 | 0.026931 | 18.5084 | Pole Top | 989.6442
2022_2023 | AER | UNPLANNED | 23FN5613 | 10020817 | 2CAR | CARBEEN | SR | 10030331 | ATHE | Atherton 66/22kV Sub (ATHE) | 328620.0833 | 1688 | 0.04134 | 13585.2225 | Pole Top | 726401.8464
2022_2023 | AER | UNPLANNED | 23FN6232 | 10132684 | 2LA1 | LAURA 1 | LR | 10132681 | LAKE | Lakeland 132/66/22kV Substation | 41717.9667 | 181 | 0.055076 | 2297.6734 | Pole Top | 122856.5975
2022_2023 | AER | UNPLANNED | 23FN6491 | 82889011 | 2EME | EMERALD CREEK | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 238 | 6 | 0.029344 | 6.9839 | Pole Top | 373.4316
2022_2023 | AER | UNPLANNED | 23FN7258 | 10020787 | 2HER | HERBERTON | SR | 10030331 | ATHE | Atherton 66/22kV Sub (ATHE) | 1144 | 13 | 0.016516 | 18.8945 | Pole Top | 1010.2873
2022_2023 | AER | UNPLANNED | 23FN7716 | 10020659 | 2HOP | HOPEVALE | LR | 10030297 | COOK | Cooktown 66/22kV Substation | 78085 | 805 | 0.028613 | 2234.2401 | Pole Top | 119464.8167
2022_2023 | AER | UNPLANNED | 23MK0560 | 30053840 | 330 | Eastern | SR | 30064316 | PLEY | Pleystowe 33/11kV Substation | 3072 | 24 | 0.032345 | 99.3628 | Pole Top | 5312.9311
2022_2023 | AER | UNPLANNED | 23MK0718 | 30053862 | 352 | Gargett | SR | 30064314 | PINN | Pinnacle 66/11kV Substation | 5848.25 | 15 | 0.014821 | 86.6747 | Pole Top | 4634.4977
2023_2024 | AER | UNPLANNED | 23MK10249 | 30053845 | 335 | ETON | SR | 30064338 | ETON | Eton 33/11kV Substation | 90957.9 | 99 | 0.019879 | 1808.1954 | Pole | 96684.2065
2022_2023 | AER | UNPLANNED | 23MK1145 | 30053864 | 354 | Finchhatton | SR | 30064314 | PINN | Pinnacle 66/11kV Substation | 14800 | 50 | 0.016669 | 246.6971 | Pole Top | 13190.8926
2022_2023 | AER | UNPLANNED | 23MK1225 | 30053840 | 330 | Eastern | SR | 30064316 | PLEY | Pleystowe 33/11kV Substation | 1551 | 11 | 0.032345 | 50.1666 | Pole Top | 2682.4076
2022_2023 | AER | UNPLANNED | 23MK1276 | 30053745 | 102 | Strathdickie | SR | 83922970 | KECE | KELSEY CREEK EAST 66/11KV SUBSTATION | 5986.85 | 24 | 0.025831 | 154.6465 | Pole Top | 8268.9497
2022_2023 | AER | UNPLANNED | 23MK2015 | 83832366 | 424 | SARINA BEACH | SR | 30064323 | SARI | Sarina 33/11kV Substation | 11303.9833 | 43 | 0.021152 | 239.0969 | Pole Top | 12784.5138
2022_2023 | AER | UNPLANNED | 23MK2819 | 30053862 | 352 | Gargett | SR | 30064314 | PINN | Pinnacle 66/11kV Substation | 3306 | 29 | 0.014821 | 48.997 | Pole Top | 2619.8691
2022_2023 | AER | UNPLANNED | 23MK2859 | 30053848 | 338 | Mount Alice | SR | 30064299 | BALB | Balberra 33/11kV Substation | 20680.7 | 109 | 0.027107 | 560.5936 | Pole Top | 29974.9415
2022_2023 | AER | UNPLANNED | 23MK2934 | 30053779 | 211 | Braeside | LR | 30064332 | NEBO | NEBO 275/132/11KV SUB (H11) | 370.4333 | 1 | 0.11294 | 41.8365 | Pole Top | 2236.9954
2022_2023 | AER | UNPLANNED | 23MK3262 | 30053822 | 312 | RACECOURSE | SR | 30064327 | WEMA | West Mackay 33/11kV Substation | 2844 | 18 | 0.033915 | 96.4529 | Pole Top | 5157.3388
2022_2023 | AER | UNPLANNED | 23MK3405 | 30053862 | 352 | Gargett | SR | 30064314 | PINN | Pinnacle 66/11kV Substation | 9578 | 63 | 0.014821 | 141.952 | Pole Top | 7590.1713
2022_2023 | AER | UNPLANNED | 23MK3517 | 82563108 | 403 | GEORGE ST FDR 11KV | UR | 82550255 | ALST | ALFRED STREET 33/11KV SUBSTATION | 3584 | 64 | 0.018335 | 65.7122 | Pole Top | 3513.6325
2022_2023 | AER | UNPLANNED | 23MK3979 | 30053744 | 101 | Crystalbrook | SR | 83922970 | KECE | KELSEY CREEK EAST 66/11KV SUBSTATION | 3135 | 33 | 0.018584 | 58.2618 | Pole Top | 3115.2589
2022_2023 | AER | UNPLANNED | 23MK4177 | 30053785 | 218 | Coppabella Hybrid SWER | SR | 30064308 | MORA | Moranbah T034 132/66/11kV Substation | 10256 | 52 | 0.05332 | 546.8501 | Pole Top | 29240.0741
2022_2023 | AER | UNPLANNED | 23MK4266 | 30053778 | 210 | Nebo | LR | 30064332 | NEBO | NEBO 275/132/11KV SUB (H11) | 23131.1667 | 121 | 0.03425 | 792.2413 | Pole Top | 42361.1422
2022_2023 | AER | UNPLANNED | 23MK4304 | 30053807 | 241 | Koumala | SR | 30064335 | KOUM | Koumala 33/11kV Substation | 4935.2333 | 28 | 0.015885 | 78.3955 | Pole | 4191.8091
2022_2023 | AER | UNPLANNED | 23MK4521 | 30053864 | 354 | Finchhatton | SR | 30064314 | PINN | Pinnacle 66/11kV Substation | 6878.0833 | 28 | 0.016669 | 114.6489 | Pole | 6130.2742
2022_2023 | AER | UNPLANNED | 23MK4615 | 30053864 | 354 | Finchhatton | SR | 30064314 | PINN | Pinnacle 66/11kV Substation | 246 | 1 | 0.016669 | 4.1005 | Pole Top | 219.254
2022_2023 | AER | UNPLANNED | 23NQ0148 | 20012178 | SD-01 | Saunders No.01 | SR | 20012177 | SAUN | SAUNDERS 66/11KV SUB (SAUN) | 85358 | 419 | 0.035305 | 3013.5249 | Pole Top | 161133.1766
2022_2023 | AER | UNPLANNED | 23NQ0508 | 20008892 | KA-02 | KALAMIA NO.02 | SR | 20008888 | KALA | KALAMIA 66/11KV SUBSTATION | 9825.75 | 45 | 0.054614 | 536.62 | Pole Top | 28693.0715
2022_2023 | AER | UNPLANNED | 23NQ0576 | 20001859 | BA-01 | Bambaroo No.01 | SR | 20001858 | BAMB | BAMBAROO 66/11KV SUBSTATION | 6660 | 90 | 0.020074 | 133.6958 | Pole Top | 7148.7155
2022_2023 | AER | UNPLANNED | 23NQ0576 | 20005787 | FX-01 | MOUNTFOX NO.1 | SR | 20005786 | MOFO | Mt Fox 66/11kV Substation | 10350 | 50 | 0.014238 | 147.364 | Pole Top | 7879.5541
2022_2023 | AER | UNPLANNED | 23NQ0576 | 20006383 | GR-02 | GREENVALE NO.02 | LR | 20006382 | GREN | GREENVALE 66/11KV SUB (GR) | 16353 | 79 | 0.02723 | 445.2985 | Pole Top | 23810.1091
2022_2023 | AER | UNPLANNED | 23NQ0576 | 20010961 | MU-01 | MUTARNEE NO.01 | SR | 20010960 | MUTA | MUTARNEE 66/11KV SUB (MU) | 15540 | 210 | 0.019875 | 308.8564 | Pole Top | 16514.5529
2022_2023 | AER | UNPLANNED | 23NQ0576 | 84653782 | BA-02 | BAMBAROO NO 2 | SR | 20001858 | BAMB | BAMBAROO 66/11KV SUBSTATION | 4218 | 57 | 0.024143 | 101.8367 | Pole Top | 5445.2089
2022_2023 | AER | UNPLANNED | 23NQ0752 | 20005412 | DR-10 | DUCHESSRD NO.10 | UR | 20005132 | DURO | DUCHESS RD 132/11KV SUBSTATION | 5992 | 56 | 0.021689 | 129.9633 | Pole Top | 6949.1391
2022_2023 | AER | UNPLANNED | 23NQ0938 | 20006799 | HH-05 | HOMEHILL NO.05 | SR | 20006664 | HOHI | HOMEHILL 66/11KV SUBSTATION | 1024 | 8 | 0.046426 | 47.5404 | Pole Top | 2541.9876
2022_2023 | AER | UNPLANNED | 23NQ1157 | 20011515 | RI-50 | Richmond No.50 | SR | 20011486 | RI | Richmond 66/33/19.1kV Substation | 9044.8 | 12 | 0.028303 | 255.9918 | Pole Top | 13687.8792
2022_2023 | AER | UNPLANNED | 23NQ1227 | 20009035 | KE-02 | KIRKNIE NO.02 | SR | 20009031 | KIRK | KIRKNIE 66/11KV SUBSTATION | 3996 | 36 | 0.12986 | 518.9162 | Pole Top | 27746.4502
2023_2024 | AER | UNPLANNED | 23NQ12755 | 20007634 | HU-20 | TORRENS CK | LR | 20007579 | HUGH | HUGHENDEN 66/33/6.6KV SUBSTATION | 2906.3333 | 5 | 0.029503 | 85.7466 | Pole | 4584.8692
2023_2024 | AER | UNPLANNED | 23NQ13636 | 20007634 | HU-20 | TORRENS CK | LR | 20007579 | HUGH | HUGHENDEN 66/33/6.6KV SUBSTATION | 62992 | 34 | 0.029503 | 1858.4751 | Pole | 99372.6629
2023_2024 | AER | UNPLANNED | 23NQ14096 | 20007634 | HU-20 | TORRENS CK | LR | 20007579 | HUGH | HUGHENDEN 66/33/6.6KV SUBSTATION | 7571.4167 | 13 | 0.029503 | 223.3822 | Pole | 11944.2443
2023_2024 | AER | UNPLANNED | 23NQ14399 | 20010102 | MERI-03 | MERINDA NO.03 | SR | 20009877 | MERI | Merinda 66/11kV Substation | 1399.2667 | 4 | 0.06747 | 94.4089 | Pole | 5048.0425
2023_2024 | AER | UNPLANNED | 23NQ14866 | 20004937 | NC-02 | NORTHCLONCURRY NO.02 | LR | 20004930 | NOCL | North Cloncurry 66/11kV Substation | 17330.7 | 18 | 0.03199 | 554.4096 | Pole | 29644.2812
2023_2024 | AER | UNPLANNED | 23NQ14971 | 20007716 | HU-30 | TOWN | SR | 20007579 | HUGH | HUGHENDEN 66/33/6.6KV SUBSTATION | 917.9833 | 1 | 0.030942 | 28.4047 | Pole | 1518.7979
2023_2024 | AER | UNPLANNED | 23NQ15005 | 20008686 | JC-11 | JULIACREEK NO.11 ORINDI | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 25554.55 | 21 | 0.033779 | 863.1971 | Pole | 46155.1474
2023_2024 | AER | UNPLANNED | 23NQ15081 | 25267897 | AS-01 | Apsley SWER No.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 58196.3333 | 44 | 0.033417 | 1944.7275 | Pole | 103984.5779
2023_2024 | AER | UNPLANNED | 23NQ15158 | 25267901 | EL-01 | ELDERSLIESWER NO.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 48676.8 | 42 | 0.032542 | 1584.0601 | Pole | 84699.6952
2023_2024 | AER | UNPLANNED | 23NQ15193 | 25273297 | GE-01 | CORFIELD SWER | LR | 25267919 | GLEE | GLENELG 66/19.1KV SUB (GLEE) | 82704 | 24 | 0.035862 | 2965.9693 | Pole | 158590.3779
2023_2024 | AER | UNPLANNED | 23NQ15203 | 20011545 | RL-01 | Rangelands SWER No.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 26569.85 | 33 | 0.038003 | 1009.7379 | Pole | 53990.6832
2023_2024 | AER | UNPLANNED | 23NQ15232 | 25273297 | GE-01 | CORFIELD SWER | LR | 25267919 | GLEE | GLENELG 66/19.1KV SUB (GLEE) | 47086 | 20 | 0.035862 | 1688.62 | Pole | 90290.5123
2022_2023 | AER | UNPLANNED | 23NQ1866 | 20005039 | DI-01 | DISRAELI NO.01 | SR | 20005038 | DISR | DISRAELI 66/11KV SUBSTATION | 2314.3333 | 2 | 0.16972 | 392.7804 | Pole Top | 21001.9682
2022_2023 | AER | UNPLANNED | 23NQ1866 | 20006599 | HB-01 | HILLSBOROUGH NO.01 | SR | 20006598 | HB | HILLSBOROUGH 66/11KV SUSBTATION | 142.1667 | 1 | 0.065468 | 9.3073 | Pole Top | 497.663
2022_2023 | AER | UNPLANNED | 23NQ1866 | 20011420 | RD-01 | Ravenswood No.1 SWER | SR | 20011419 | RAVN | Ravenswood 66/11kV Substation | 6255.3333 | 44 | 0.021997 | 137.5971 | Pole Top | 7357.3175
2022_2023 | AER | UNPLANNED | 23NQ1866 | 20011458 | RD-02 | Ravenswood No.2 | SR | 20011419 | RAVN | Ravenswood 66/11kV Substation | 568.6667 | 4 | 0.50439 | 286.8273 | Pole Top | 15336.6545
2022_2023 | AER | UNPLANNED | 23NQ1866 | 20011464 | RD-03 | Ravenswood No.3 | SR | 20011419 | RAVN | Ravenswood 66/11kV Substation | 13079.3333 | 92 | 0.050185 | 656.3804 | Pole Top | 35096.6591
2022_2023 | AER | UNPLANNED | 23NQ1866 | 20013575 | WS-01 | WOODHOUSE STN NO.1 | SR | 20013574 | WOOD | WOODHOUSE 66/11kV SUBSTATION | 710.8333 | 5 | 0.059948 | 42.6128 | Pole Top | 2278.5066
2022_2023 | AER | UNPLANNED | 23NQ2080 | 20006799 | HH-05 | HOMEHILL NO.05 | SR | 20006664 | HOHI | HOMEHILL 66/11KV SUBSTATION | 114756.9 | 369 | 0.046426 | 5327.7286 | Pole | 284873.6479
2022_2023 | AER | UNPLANNED | 23NQ2083 | 20003792 | CO-01 | COLLINSVILLE NO.01 | SR | 20003791 | COLL | COLLINSVILLE SUBSTATION | 4327 | 37 | 0.024446 | 105.7763 | Pole Top | 5655.8573
2022_2023 | AER | UNPLANNED | 23NQ2172 | 20006478 | GU-01 | GUMLU NO.01 | SR | 20006477 | GUML | GUMLU 66/11KV SUBSTATION | 4116 | 49 | 0.0802 | 330.1017 | Pole Top | 17650.5361
2022_2023 | AER | UNPLANNED | 23NQ2452 | 82962855 | CLSO-04 | CLARESOUTH NO.04 | SR | 82961890 | CLSO | CLARESOUTH T193 132/66/11KV SUBSTATION | 6141 | 69 | 0.057998 | 356.168 | Pole Top | 19044.3052
2022_2023 | AER | UNPLANNED | 23NQ2467 | 20010102 | MERI-03 | MERINDA NO.03 | SR | 20009877 | MERI | Merinda 66/11kV Substation | 18542.1333 | 31 | 0.05922 | 1098.0674 | Pole Top | 58713.6648
2022_2023 | AER | UNPLANNED | 23NQ2792 | 84023546 | MERI-11 | MERINDA NO.11 | SR | 20009877 | MERI | Merinda 66/11kV Substation | 71617 | 335 | 0.039612 | 2836.8934 | Pole Top | 151688.6925
2022_2023 | AER | UNPLANNED | 23NQ2894 | 25267901 | EL-01 | ELDERSLIESWER NO.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 42984 | 42 | 0.035429 | 1522.8967 | Pole | 81429.2851
2022_2023 | AER | UNPLANNED | 23NQ2908 | 25276003 | RI-80 | Barabon Quarry 33kV Feeder | LR | 20011486 | RI | Richmond 66/33/19.1kV Substation | 44894.6167 | 18 | 0.032251 | 1447.8796 | Pole | 77418.1224
2022_2023 | AER | UNPLANNED | 23NQ3131 | 20010444 | ML-01 | DALBEG | SR | 20010443 | MILL | MILLAROO 66/11KV SUB (ML) | 7947.9333 | 43 | 0.087105 | 692.3018 | Pole Top | 37017.3756
2022_2023 | AER | UNPLANNED | 23NQ3181 | 20003547 | CF-01 | CAPE FERGUSON NO.01 | UR | 20003546 | CAFE | CAPE FERGUSON 66/11KV SUB (CAFE) | 1542.85 | 1 | 12.6068 | 19450.3847 | Pole Top | 1040012.0691
2022_2023 | AER | UNPLANNED | 23NQ3181 | 20003550 | CF-02 | CAPE FERGUSON NO.02 | SR | 20003546 | CAFE | CAPE FERGUSON 66/11KV SUB (CAFE) | 155446.15 | 349 | 0.014611 | 2271.2999 | Pole Top | 121446.4048
2022_2023 | AER | UNPLANNED | 23NQ3585 | 20003294 | CB-03 | CRANBROOK NO.03 | UR | 20003280 | CRAN | CRANBROOK 66/11KV SUB (CB) | 44406.1667 | 74 | 0.022606 | 1003.8599 | Pole Top | 53676.3866
2022_2023 | AER | UNPLANNED | 23NQ3649 | 20009306 | LANN-05 | LANNERCOST NO.05 | SR | 20009097 | LANN | Lannercost 66/11kV Substation | 23104.8333 | 226 | 0.026547 | 613.3573 | Pole Top | 32796.2151
2022_2023 | AER | UNPLANNED | 23NQ3899 | 20012370 | ST01 | STUART DRIVE | SR | 20012369 | STUA | Stuart 66/11kV Substation | 179039.5 | 930 | 0.024208 | 4334.1608 | Pole | 231747.5793
2022_2023 | AER | UNPLANNED | 23NQ4093 | 20011700 | RASM-06 | RASMUSSEN NO.06 | SR | 20011587 | RASM | Rasmussen 66/11kV Substation | 80168 | 519 | 0.032318 | 2590.8692 | Pole Top | 138533.7737
2022_2023 | AER | UNPLANNED | 23NQ4197 | 20002143 | BD-02 | BURDEKIN DAM NO.02 | SR | 20002139 | BUDA | BURDEKIN DAM 33/11KV SUBSTATION | 164 | 1 | 9.058e-06 | 0.0014855 | Pole Top | 0.07943
2022_2023 | AER | UNPLANNED | 23NQ4197 | 20002149 | BD-03 | BURDEKIN DAM NO.03 | SR | 20002139 | BUDA | BURDEKIN DAM 33/11KV SUBSTATION | 274 | 2 | 0.019665 | 5.3882 | Pole Top | 288.106
2022_2023 | AER | UNPLANNED | 23NQ4241 | 20003949 | CR-01 | CAPERIVER NO.01 | LR | 20003948 | CARI | Cape River C 66/11kV Substation | 3744 | 48 | 0.019657 | 73.5951 | Pole Top | 3935.13
2022_2023 | AER | UNPLANNED | 23NQ4365 | 20003949 | CR-01 | CAPERIVER NO.01 | LR | 20003948 | CARI | Cape River C 66/11kV Substation | 424 | 4 | 0.019657 | 8.3345 | Pole Top | 445.6451
2022_2023 | AER | UNPLANNED | 23NQ4472 | 20006697 | HH-04 | HOMEHILL NO.04 | SR | 20006664 | HOHI | HOMEHILL 66/11KV SUBSTATION | 4585 | 35 | 0.079128 | 362.8023 | Pole Top | 19399.0383
2022_2023 | AER | UNPLANNED | 23NQ4495 | 20012587 | ST05 | SERENE VALLEY | SR | 20012369 | STUA | Stuart 66/11kV Substation | 111935 | 367 | 0.021481 | 2404.4494 | Pole Top | 128565.9079
2022_2023 | AER | UNPLANNED | 23NQ4636 | 20011701 | RASM-07 | RASMUSSEN NO.07 | SR | 20011587 | RASM | Rasmussen 66/11kV Substation | 988 | 4 | 0.10498 | 103.7189 | Pole Top | 5545.8472
2022_2023 | AER | UNPLANNED | 23NQ5403 | 82561865 | MILC-10 | MILLCHESTER NO.10 | SR | 20010917 | MILC | Millchester 132/66/11kV Substation | 3074.2833 | 13 | 0.024694 | 75.916 | Pole Top | 4059.2301
2022_2023 | AER | UNPLANNED | 23NQ5669 | 82912317 | OONN-04 | OONOONBA NO.04 | UR | 82866131 | OONN | OONOONBA 66/11KV SUBSTATION | 29148 | 260 | 0.017586 | 512.5912 | Pole Top | 27408.2515
2022_2023 | AER | UNPLANNED | 23NQ6134 | 20006212 | GI-02 | GIRU NO.02 | SR | 20006135 | GIRU | GIRU 66/11KV SUBSTATION (GIRU) | 1425 | 19 | 0.030027 | 42.789 | Pole Top | 2287.9294
2022_2023 | AER | UNPLANNED | 23NQ6160 | 20010437 | MK-01 | MARYKATHLEEN NO.01 | SR | 20010436 | MAKA | Mary Kathleen 66/11kV Substation | 8592 | 6 | 0.017341 | 148.9975 | Pole Top | 7966.8955
2022_2023 | AER | UNPLANNED | 23NQ6195 | 82564200 | MILC-11 | MILLCHESTER NO.11 | SR | 20010917 | MILC | Millchester 132/66/11kV Substation | 962 | 13 | 0.021231 | 20.4245 | Pole Top | 1092.0994
2022_2023 | AER | UNPLANNED | 23NQ6671 | 20010631 | MP-03 | MONAPARK NO.03 | SR | 20010630 | MOPA | MONA PARK 66/11KV SUB | 5858 | 82 | 0.1182 | 692.429 | Pole Top | 37024.1766
2022_2023 | AER | UNPLANNED | 23SW0181 | 60026823 | F4175 | SOUTH STREET | UR | 60025699 | SOTO | SOUTH TOOWOOMBA 110/33/11KV SUB (T043) | 4450 | 50 | 0.019815 | 88.1773 | Pole Top | 4714.8419
2022_2023 | AER | UNPLANNED | 23SW0676 | 60026747 | F2980 | GOOMBURRA | LR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 5130 | 45 | 0.025409 | 130.3505 | Pole Top | 6969.8423
2022_2023 | AER | UNPLANNED | 23SW1415 | 60026675 | F077S | MAIN CAMP | LR | 60007215 | SAGE | ST GEORGE (MC052) 66/33KV SUB (SAGE) | 798 | 7 | 0.035582 | 28.3943 | Pole | 1518.2442
2022_2023 | AER | UNPLANNED | 23SW1438 | 60026755 | F3060 | HARRIS STREET | LR | 60007222 | STTO | STANTHORPE TOWN 33/11KV SUB | 40401.3333 | 215 | 0.021956 | 887.0424 | Pole Top | 47430.1567
2022_2023 | AER | UNPLANNED | 23SW1453 | 60026747 | F2980 | GOOMBURRA | LR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 25394.1333 | 44 | 0.025409 | 645.2512 | Pole Top | 34501.58
2022_2023 | AER | UNPLANNED | 23SW1567 | 60026702 | F2075 | ANCHORFIELD | SR | 60007229 | PAMP | PAMPAS 33/11KV SUB | 120 | 1 | 0.096996 | 11.6395 | Pole Top | 622.3654
2023_2024 | AER | UNPLANNED | 23SW16258 | 60026889 | F061W | GULUGUBA | LR | 60007208 | WAND | WANDOAN 33/22KV SUB | 4560 | 16 | 0.039519 | 180.2065 | Pole | 9635.6407
2022_2023 | AER | UNPLANNED | 23SW1669 | 60026725 | F2530 | CLIFTON WEST | SR | 60007249 | CLIF | CLIFTON 33/11KV SUB (ME399) | 987 | 7 | 0.031095 | 30.6904 | Pole Top | 1641.0163
2022_2023 | AER | UNPLANNED | 23SW1700 | 60026747 | F2980 | GOOMBURRA | LR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 11806 | 61 | 0.025409 | 299.9841 | Pole | 16040.1479
2022_2023 | AER | UNPLANNED | 23SW1701 | 60026747 | F2980 | GOOMBURRA | LR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 50658.3 | 119 | 0.025409 | 1287.2 | Pole | 68826.5816
2022_2023 | AER | UNPLANNED | 23SW1760 | 60026733 | F2660 | CROWS NEST TOWN | LR | 60007231 | CRNE | CROWS NEST 33/11KV SUB (ME032) | 2442 | 22 | 0.02048 | 50.0113 | Pole Top | 2674.1049
2022_2023 | AER | UNPLANNED | 23SW1774 | 60026725 | F2530 | CLIFTON WEST | SR | 60007249 | CLIF | CLIFTON 33/11KV SUB (ME399) | 1395 | 7 | 0.031095 | 43.377 | Pole Top | 2319.3696
2023_2024 | AER | UNPLANNED | 23SW18638 | 60026697 | F200C | PARTRIDGE STREET | SR | 60007255 | CHAR | CHARLEVILLE 66/22/11KV SUB | 91014 | 197 | 0.029888 | 2720.1859 | Pole | 145448.3388
2023_2024 | AER | UNPLANNED | 23SW19594 | 60026650 | F022R | BRUCEDALE | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 47280.7833 | 53 | 0.026637 | 1259.4331 | Pole | 67341.8897
2023_2024 | AER | UNPLANNED | 23SW20617 | 60026787 | F351C | CUNNAMULLA NORTH | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 18160.7167 | 61 | 0.019525 | 354.5926 | Pole | 18960.0637
2023_2024 | AER | UNPLANNED | 23SW20887 | 60026644 | F004Q | QUILPIE RURAL | LR | 60007257 | QUIL | QUILPIE 66/11KV SUB | 23013 | 30 | 0.028449 | 654.701 | Pole | 35006.8611
2023_2024 | AER | UNPLANNED | 23SW21011 | 60026670 | F069C | BRIGALOW | LR | 60025697 | CHIN | CHINCHILLA 132/110/33KV SUB (T013) | 12864.3333 | 70 | 0.020114 | 258.7535 | Pole | 13835.5475
2023_2024 | AER | UNPLANNED | 23SW21062 | 60026888 | F058W | TAROOM | LR | 60007208 | WAND | WANDOAN 33/22KV SUB | 13792.9 | 11 | 0.023859 | 329.0802 | Pole | 17595.9172
2023_2024 | AER | UNPLANNED | 23SW21254 | 60026666 | F049R | ROMA NORTH | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 71103.3667 | 43 | 0.026217 | 1864.0936 | Pole | 99673.0851
2023_2024 | AER | UNPLANNED | 23SW21666 | 60026696 | F187R | MUNGALLALA | LR | 60007254 | MITC | MITCHELL 33/11KV SUB | 79865.0833 | 185 | 0.027973 | 2234.1053 | Pole | 119457.6114
2023_2024 | AER | UNPLANNED | 23SW22874 | 60026847 | F4715 | YANDILLA | LR | 60007229 | PAMP | PAMPAS 33/11KV SUB | 48523.3 | 39 | 0.023672 | 1148.6562 | Pole | 61418.6471
2023_2024 | AER | UNPLANNED | 23SW23189 | 60026791 | F3645 | MT LOFTY | UR | 60007227 | ME020 | North Street 33/11kV Substation | 1733.1333 | 1 | 0.01919 | 33.2589 | Pole | 1778.3525
2022_2023 | AER | UNPLANNED | 23SW2332 | 60026722 | F2465 | CECIL PLAINS TOWN | SR | 60007242 | CEPL | CECIL PLAINS 33/11KV SUB | 112249.2 | 138 | 0.023401 | 2626.7666 | Pole | 140453.21
2022_2023 | AER | UNPLANNED | 23SW2332 | 60026756 | F3065 | HASLEMERE | SR | 60007242 | CEPL | CECIL PLAINS 33/11KV SUB | 30095.8 | 37 | 0.059263 | 1783.5736 | Pole | 95367.6797
2022_2023 | AER | UNPLANNED | 23SW2332 | 60026764 | F3145 | HORRANE | SR | 60007242 | CEPL | CECIL PLAINS 33/11KV SUB | 65072 | 80 | 0.047905 | 3117.2707 | Pole | 166680.4663
2022_2023 | AER | UNPLANNED | 23SW2332 | 60026831 | F4380 | TIPTON | SR | 60007242 | CEPL | CECIL PLAINS 33/11KV SUB | 52057.6 | 64 | 0.027143 | 1413.0026 | Pole | 75553.2489
2022_2023 | AER | UNPLANNED | 23SW2332 | 60026839 | F4550 | WATSON STREET | SR | 60007242 | CEPL | CECIL PLAINS 33/11KV SUB | 32536 | 40 | 0.40835 | 13286.2114 | Pole | 710413.725
2022_2023 | AER | UNPLANNED | 23SW2362 | 60026705 | F2140 | BALD HILLS | SR | 60007238 | NORW | NORWIN 33/11KV SUB (ME074) | 78686 | 72 | 0.042102 | 3312.8356 | Pole | 177137.3216
2023_2024 | AER | UNPLANNED | 23SW24114 | 60026650 | F022R | BRUCEDALE | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 35338 | 38 | 0.026637 | 941.3094 | Pole | 50331.8163
2023_2024 | AER | UNPLANNED | 23SW24121 | 60026676 | F079S | ST GEORGE MEATWORKS | LR | 60007215 | SAGE | ST GEORGE (MC052) 66/33KV SUB (SAGE) | 327619.95 | 381 | 0.07765 | 25439.5888 | Pole | 1360254.8117
2023_2024 | AER | UNPLANNED | 23SW24121 | 60026680 | F090S | SURAT ROAD | SR | 60007217 | ROWO | ROO WORKS 33/11KV SUB | 65425.7833 | 151 | 0.037491 | 2452.8517 | Pole | 131153.9792
2023_2024 | AER | UNPLANNED | 23SW24121 | 60327170 | F078S | BEARDMORE DAM | LR | 60327166 | BURG | BURGORAH 33KV REGULATOR | 43328.3333 | 100 | 0.050156 | 2173.1761 | Pole | 116199.7242
2022_2023 | AER | UNPLANNED | 23SW2661 | 60026715 | F2330 | BRYMAROO | SR | 60007239 | PERA | PERANGA 33/11KV SUB (ME075) | 1755.25 | 15 | 0.047117 | 82.7014 | Pole Top | 4422.043
2022_2023 | AER | UNPLANNED | 23SW2911 | 60026824 | F4185 | SOUTHBROOK | SR | 60007233 | BROX | BROXBURN 33/11KV SUB (ME057) | 1938 | 19 | 0.024928 | 48.31 | Pole Top | 2583.1373
2022_2023 | AER | UNPLANNED | 23SW3500 | 60026729 | F2620 | COPPS HILL | SR | 60007233 | BROX | BROXBURN 33/11KV SUB (ME057) | 1232 | 16 | 0.064576 | 79.5578 | Pole Top | 4253.9537
2022_2023 | AER | UNPLANNED | 23SW3655 | 60331113 | F2452 | COTSWOLD HILLS | SR | 60025703 | TORR | TORRINGTON 110/33/11KV SUB (T116) | 185699 | 1159 | 0.023797 | 4419.1349 | Pole Top | 236291.1408
2022_2023 | AER | UNPLANNED | 23SW3665 | 60026667 | F060T | TARA | LR | 60007206 | KOGA | KOGAN REGULATOR (MC13) | 78599.55 | 333 | 0.028525 | 2242.0192 | Pole Top | 119880.765
2022_2023 | AER | UNPLANNED | 23SW3670 | 60026788 | F3525 | MILL HILL | SR | 84536204 | WAEA | WARWICK EAST 33/11KV SUB | 60 | 1 | 0.03564 | 2.1384 | Pole Top | 114.3412
2022_2023 | AER | UNPLANNED | 23SW3799 | 83850808 | CAWDOR | CAWDOR | SR | 82709366 | SKIB | SKID B 33/11kV SUBSTATION | 89446.7667 | 292 | 0.023834 | 2131.9003 | Pole Top | 113992.7108
2022_2023 | AER | UNPLANNED | 23SW3865 | 60026747 | F2980 | GOOMBURRA | LR | 60007232 | ALLO | Allora 33/11kV Sub (ME037) | 8377 | 28 | 0.025409 | 212.855 | Pole Top | 11381.3585
2022_2023 | AER | UNPLANNED | 23SW3980 | 82991938 | F3352 | KRATZKE ROAD FDR | UR | 60007228 | HIGH | HIGHFIELDS 33/11KV SUB | 288502 | 645 | 0.045251 | 13055.1278 | Pole | 698057.6856
2022_2023 | AER | UNPLANNED | 23SW4177 | 82912886 | F4468 | DRAYTON | SR | 60331401 | KESP | KEARNEYS SPRINGS 110/11KV SUB (KESP) | 2300 | 20 | 0.034819 | 80.0844 | Pole Top | 4282.1112
2022_2023 | AER | UNPLANNED | 23SW4561 | 60026816 | F4090 | ROSSVALE | LR | 60007248 | PURR | PURRAWUNDA 33/11KV SUB | 56453.75 | 87 | 0.025922 | 1463.3681 | Pole | 78246.2931
2022_2023 | AER | UNPLANNED | 23SW4846 | 60026778 | F3400 | LINTHORPE | SR | 60007233 | BROX | BROXBURN 33/11KV SUB (ME057) | 452.4167 | 1 | 0.027408 | 12.3999 | Pole Top | 663.0207
2022_2023 | AER | UNPLANNED | 23SW4872 | 60026734 | F2661 | CROWS NEST INDUSTRIAL ROAD | LR | 60007231 | CRNE | CROWS NEST 33/11KV SUB (ME032) | 5844.7167 | 19 | 0.022701 | 132.6812 | Pole Top | 7094.4634
2022_2023 | AER | UNPLANNED | 23SW4956 | 60026786 | F3505 | MERINGANDAN | SR | 60007235 | MERN | MERINGANDAN 33/11KV SUB (ME062) | 7824.8333 | 28 | 0.026128 | 204.4465 | Pole Top | 10931.7561
2022_2023 | AER | UNPLANNED | 23SW5114 | 60026644 | F004Q | QUILPIE RURAL | LR | 60007257 | QUIL | QUILPIE 66/11KV SUB | 13103.6833 | 29 | 0.029021 | 380.2872 | Pole Top | 20333.9545
2022_2023 | AER | UNPLANNED | 23SW5380 | 60026718 | F2415 | CABARLAH | SR | 60007235 | MERN | MERINGANDAN 33/11KV SUB (ME062) | 485.2833 | 1 | 0.032443 | 15.7441 | Pole Top | 841.839
2022_2023 | AER | UNPLANNED | 23SW5585 | 60026734 | F2661 | CROWS NEST INDUSTRIAL ROAD | LR | 60007231 | CRNE | CROWS NEST 33/11KV SUB (ME032) | 2233 | 11 | 0.022701 | 50.6914 | Pole Top | 2710.4713
2022_2023 | AER | UNPLANNED | 23SW5592 | 60026650 | F022R | BRUCEDALE | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 13051.2833 | 53 | 0.028126 | 367.0804 | Pole | 19627.7908
2022_2023 | AER | UNPLANNED | 23SW6217 | 60026716 | F233C | MORVEN | LR | 60007255 | CHAR | CHARLEVILLE 66/22/11KV SUB | 41346.0833 | 355 | 0.031882 | 1318.1766 | Pole Top | 70482.9023
2022_2023 | AER | UNPLANNED | 23SW6326 | 60026667 | F060T | TARA | LR | 60007206 | KOGA | KOGAN REGULATOR (MC13) | 34769.4 | 46 | 0.028525 | 991.7825 | Pole | 53030.6124
2022_2023 | AER | UNPLANNED | 23SW6339 | 60026711 | F2260 | BORDER ROAD | SR | 60007236 | KILL | KILLARNEY 33/11KV SUB (ME063) | 760 | 8 | 0.023099 | 17.5553 | Pole Top | 938.6844
2022_2023 | AER | UNPLANNED | 23SW6928 | 60026742 | F2860 | EVERGREEN | SR | 60007239 | PERA | PERANGA 33/11KV SUB (ME075) | 2646 | 7 | 0.019152 | 50.6752 | Pole Top | 2709.6039
2022_2023 | AER | UNPLANNED | 23SW7046 | 60026847 | F4715 | YANDILLA | LR | 60007229 | PAMP | PAMPAS 33/11KV SUB | 3419.4 | 18 | 0.026152 | 89.4234 | Pole Top | 4781.4678
2022_2023 | AER | UNPLANNED | 23SW7220 | 60026844 | F4645 | WILLOWBURN | SR | 60007227 | ME020 | North Street 33/11kV Substation | 3808 | 136 | 0.019017 | 72.4181 | Pole Top | 3872.1954
2022_2023 | AER | UNPLANNED | 23SW7428 | 60026771 | F3280 | JONDARYAN | LR | 60330485 | OAKE | Oakey 33/11kV Substation | 1168.3833 | 1 | 0.054034 | 63.133 | Pole Top | 3375.7205
2022_2023 | AER | UNPLANNED | 23SW7661 | 60027003 | F099D | WARRA | LR | 60007197 | WEDA | WEST DALBY 33/11KV SUB | 198 | 2 | 0.078688 | 15.5803 | Pole Top | 833.0795
2022_2023 | AER | UNPLANNED | 23SW7988 | 60026816 | F4090 | ROSSVALE | LR | 60007248 | PURR | PURRAWUNDA 33/11KV SUB | 2088 | 24 | 0.025922 | 54.1242 | Pole Top | 2894.0196
2022_2023 | AER | UNPLANNED | 23SW8009 | 60026783 | F3475 | McGLEW STREET | LR | 60007222 | STTO | STANTHORPE TOWN 33/11KV SUB | 2394 | 18 | 0.02115 | 50.6321 | Pole Top | 2707.3006
2022_2023 | AER | UNPLANNED | 23SW8716 | 84982802 | 14092 | MORGAN PARK | SR | 84536204 | WAEA | WARWICK EAST 33/11KV SUB | 270 | 5 | 0.069366 | 18.7289 | Pole Top | 1001.4323
2022_2023 | AER | UNPLANNED | 23SW8817 | 60026766 | F315C | EULO | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 20849.4 | 18 | 0.021724 | 452.9293 | Pole | 24218.1317
2023_2024 | AER | UNPLANNED | 23SW9086 | 60026644 | F004Q | QUILPIE RURAL | LR | 60007257 | QUIL | QUILPIE 66/11KV SUB | 3540.75 | 9 | 0.028449 | 100.7314 | Pole | 5386.1097
2023_2024 | AER | UNPLANNED | 23SW9699 | 60026766 | F315C | EULO | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 31686.5 | 127 | 0.019293 | 611.3338 | Pole | 32688.0196
2022_2023 | AER | UNPLANNED | 23WB0626 | 82556066 | BG-B | RIVERVIEW 1773 | SR | 81518239 | BARG | Bargara Substation 66/11kV | 287249.2333 | 1961 | 0.017901 | 5142.1501 | Pole Top | 274950.7642
2022_2023 | AER | UNPLANNED | 23WB0821 | 50000130 | MG-H | TANSEY | LR | 50000121 | MURG | Murgon 66/11kV Substation | 201.6 | 3 | 0.030776 | 6.2045 | Pole Top | 331.7564
2022_2023 | AER | UNPLANNED | 23WB0921 | 50000144 | NN-E | SOUTH NANANGO | SR | 50000141 | NANA | NANANGO 66/11KV SUB (NANA) | 187.3667 | 1 | 0.015576 | 2.9184 | Pole Top | 156.0443
2022_2023 | AER | UNPLANNED | 23WB1082 | 50000061 | GV-D | ELLIOTT RIVER | SR | 50000060 | GIVE | GIVELDA 66/11KV SUB | 38693.6667 | 206 | 0.031475 | 1217.8757 | Pole Top | 65119.8128
2022_2023 | AER | UNPLANNED | 23WB1082 | 50000062 | GV-E | QWRC | UR | 50000060 | GIVE | GIVELDA 66/11KV SUB | 187.8333 | 1 | 12.3994 | 2329.0149 | Pole Top | 124532.426
2022_2023 | AER | UNPLANNED | 23WB1082 | 50000063 | GV-F | THE CEDARS | SR | 50000060 | GIVE | GIVELDA 66/11KV SUB | 9767.3333 | 52 | 0.041362 | 403.9946 | Pole Top | 21601.5931
2022_2023 | AER | UNPLANNED | 23WB1191 | 82888836 | TQ-K | DAYMAN ST | UR | 50000191 | TORQ | Torquay 66/11kV Substation | 9021 | 97 | 0.023021 | 207.6709 | Pole Top | 11104.1621
2022_2023 | AER | UNPLANNED | 23WB1291 | 50000053 | GB-C | INVICTA | LR | 50000051 | GOOB | GOOBURRUM 66/11KV SUB (GB) | 90063.8667 | 358 | 0.021849 | 1967.8085 | Pole Top | 105218.7228
2023_2024 | AER | UNPLANNED | 23WB13094 | 50000015 | BY-A | BUCCA | SR | 50000014 | BULL | BULLYARD 66/11KV SUB | 465.4167 | 1 | 0.033397 | 15.5434 | Pole | 831.1071
2022_2023 | AER | UNPLANNED | 23WB1332 | 50000139 | MV-D | GOOBURRUM | SR | 50000136 | MEAD | MEADOWVALE 66/11KV SUB (MEAD) | 4888.5 | 30 | 0.026848 | 131.2461 | Pole Top | 7017.7276
2022_2023 | AER | UNPLANNED | 23WB2372 | 50000142 | NN-C | NANANGO TOWN | SR | 50000141 | NANA | NANANGO 66/11KV SUB (NANA) | 4200 | 35 | 0.020758 | 87.1832 | Pole Top | 4661.6874
2022_2023 | AER | UNPLANNED | 23WB2400 | 50000108 | MC-C | TINANA CK | SR | 50000105 | MACI | MARYBOROUGH CITY 66/11KV SUB | 152 | 2 | 0.028513 | 4.334 | Pole Top | 231.7411
2022_2023 | AER | UNPLANNED | 23WB2444 | 50000154 | PB-C | DOOLONG SOUTH | SR | 50000152 | PIAL | PIALBA 66/11kV SUBSTATION | 194361.1333 | 647 | 0.024644 | 4789.927 | Pole Top | 256117.3989
2022_2023 | AER | UNPLANNED | 23WB2579 | 50000061 | GV-D | ELLIOTT RIVER | SR | 50000060 | GIVE | GIVELDA 66/11KV SUB | 1517.75 | 5 | 0.031475 | 47.7709 | Pole Top | 2554.3094
2022_2023 | AER | UNPLANNED | 23WB3019 | 50000049 | FF-D | NORTH GREGORY | SR | 50000045 | FF | Farnsfield 66/11kV Substation | 30754 | 108 | 0.054793 | 1685.0905 | Pole Top | 90101.7867
2022_2023 | AER | UNPLANNED | 23WB3316 | 50000159 | PT-A | PROSTON | LR | 50000158 | PROT | PROSTON 66/11KV SUB | 1403 | 23 | 0.01511 | 21.1997 | Pole Top | 1133.5484
2022_2023 | AER | UNPLANNED | 23WB3645 | 50000148 | OY-A | ANTIGUA | SR | 50000147 | OWAN | OWANYILLA 66/11KV SUB | 248 | 4 | 0.031202 | 7.7382 | Pole Top | 413.7602
2022_2023 | AER | UNPLANNED | 23WB3947 | 50000177 | SB-F | ALLOWAY | SR | 50000172 | SOBU | SOUTH BUNDABERG 66/11KV SUB (SB) | 33244.1667 | 79 | 0.086686 | 2881.8114 | Pole | 154090.4538
2022_2023 | AER | UNPLANNED | 23WB4285 | 50000229 | WL-A | BELLS BRIDGE | LR | 50000228 | WOOL | Woolooga 66/11kV Substation | 362 | 2 | 0.018724 | 6.7779 | Pole Top | 362.4164
2022_2023 | AER | UNPLANNED | 23WB4795 | 50000117 | MD-B | RIVERLEIGH FDR | LR | 82738151 | MUTO | MUNDUBBERA TOWN 66/11KV SUBSTATION | 847 | 7 | 0.046842 | 39.6752 | Pole | 2121.4337
2022_2023 | AER | UNPLANNED | 23WB5101 | 50000232 | WV-B | GIN GIN | SR | 50000231 | WALL | WALLAVILLE 66/11KV SUB | 8640 | 64 | 0.023473 | 202.8093 | Pole Top | 10844.2118
2022_2023 | AER | UNPLANNED | 23WB5506 | 50000050 | FF-E | KOWBI | SR | 50000045 | FF | Farnsfield 66/11kV Substation | 2400 | 10 | 0.027913 | 66.9923 | Pole Top | 3582.0781
2022_2023 | AER | UNPLANNED | 23WB6092 | 50000095 | KR-F | WOOROOLIN | LR | 50000087 | KING | Kingaroy 66/11kV Substation | 359.05 | 1 | 0.020598 | 7.3959 | Pole Top | 395.4568
2022_2023 | AER | UNPLANNED | 23WB6918 | 50000043 | EV-A | MALMOE | SR | 50000042 | EIDS | EIDSVOLD 66/11KV SUB (EV) | 13000.35 | 99 | 0.033242 | 432.1564 | Pole Top | 23107.4009
2022_2023 | AER | UNPLANNED | 23WB6918 | 50000044 | EV-C | EIDSVOLD | LR | 50000042 | EIDS | EIDSVOLD 66/11KV SUB (EV) | 67890.7167 | 517 | 0.01932 | 1311.6342 | Pole Top | 70133.0798
2022_2023 | AER | UNPLANNED | 23WB6918 | 50000116 | MD-A | O'BIL BIL FDR | SR | 82738151 | MUTO | MUNDUBBERA TOWN 66/11KV SUBSTATION | 28627.0333 | 218 | 0.020061 | 574.2783 | Pole Top | 30706.6602
2022_2023 | AER | UNPLANNED | 23WB6918 | 50000117 | MD-B | RIVERLEIGH FDR | LR | 82738151 | MUTO | MUNDUBBERA TOWN 66/11KV SUBSTATION | 35192.8667 | 268 | 0.046842 | 1648.5059 | Pole Top | 88145.6103
2022_2023 | AER | UNPLANNED | 23WB6918 | 50000118 | MD-C | BOYNE FDR | LR | 82738151 | MUTO | MUNDUBBERA TOWN 66/11KV SUBSTATION | 54365.1 | 414 | 0.048112 | 2615.5972 | Pole Top | 139855.9803
2022_2023 | AER | UNPLANNED | 23WB6918 | 50000120 | MD-E | MUNDUBBERA FDR | SR | 82738151 | MUTO | MUNDUBBERA TOWN 66/11KV SUBSTATION | 66183.6 | 504 | 0.028333 | 1875.1494 | Pole Top | 100264.2401
2022_2023 | AER | UNPLANNED | 23WB6918 | 83922716 | 1997 | PHILPOT FDR | SR | 82738151 | MUTO | MUNDUBBERA TOWN 66/11KV SUBSTATION | 19172.2333 | 146 | 0.011346 | 217.5254 | Pole Top | 11631.0831
2022_2023 | AER | UNPLANNED | 23WB7133 | 50000229 | WL-A | BELLS BRIDGE | LR | 50000228 | WOOL | Woolooga 66/11kV Substation | 5835.6667 | 28 | 0.018724 | 109.2646 | Pole Top | 5842.3799
2023_2024 | AER | UNPLANNED | 24CA0719 | 40216323 | BK206 | Tambo | LR | 40018027 | BLAK | BLACKALL 66/22KV SUB (BKSS) | 42558.75 | 49 | 0.027816 | 1183.8317 | Pole Top | 63299.4821
2023_2024 | AER | UNPLANNED | 24CA1098 | 40216323 | BK206 | Tambo | LR | 40018027 | BLAK | BLACKALL 66/22KV SUB (BKSS) | 13440.7167 | 11 | 0.027816 | 373.8725 | Pole | 19990.9632
2023_2024 | AER | UNPLANNED | 24CA2656 | 40001062 | BB210 | Alpha | LR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 7226.2167 | 23 | 0.026769 | 193.4374 | Pole | 10343.0978
2023_2024 | AER | UNPLANNED | 24CA3006 | 40001062 | BB210 | Alpha | LR | 40000024 | BARC | BARCALDINE 132/66/22KV SUB (BBBS) | 305 | 1 | 0.026769 | 8.1645 | Pole | 436.5555
2023_2024 | AER | UNPLANNED | 24CA3884 | 40001010 | CL204 | Capella | LR | 40000023 | CLER | CLERMONT 132/66/22/11KV SUB (T071) CLBS | 8480.75 | 21 | 0.027284 | 231.3899 | Pole | 12372.417
2023_2024 | AER | UNPLANNED | 24CA4493 | 40000962 | BL109 | Meissner | LR | 40000001 | BILO | BILOELA 132/66/11KV SUB (BLBS) | 13577.6167 | 17 | 0.035466 | 481.5388 | Pole | 25747.8818
2023_2024 | AER | UNPLANNED | 24FN0149 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 23559.4667 | 18 | 0.079143 | 1864.5731 | Pole Top | 99698.7237
2023_2024 | AER | UNPLANNED | 24FN2066 | 10020674 | 2BUR | BURKETOWN | LR | 10030302 | NORM | NORMANTON 66/22KV SUB (NORM) | 1578.5 | 6 | 0.079143 | 124.9276 | Pole | 6679.8811
2023_2024 | AER | UNPLANNED | 24FN3593 | 10020842 | 2KUR | KURANDA | SR | 10030290 | MARE | MAREEBA 66/22kV SUBSTATION | 173083.8 | 1066 | 0.021041 | 3641.7809 | Pole | 194726.0243
2023_2024 | AER | UNPLANNED | 24MK0493 | 30053747 | 104 | Kelsey Creek | SR | 83922970 | KECE | KELSEY CREEK EAST 66/11KV SUBSTATION | 351.1167 | 1 | 0.024986 | 8.7731 | Pole | 469.0978
2023_2024 | AER | UNPLANNED | 24NQ0051 | 82561856 | MILC-09 | MILLCHESTER NO.09 | LR | 20010917 | MILC | Millchester 132/66/11kV Substation | 8354.5 | 6 | 0.023241 | 194.1636 | Pole | 10381.9268
2023_2024 | AER | UNPLANNED | 24NQ0058 | 25273274 | GE-02 | VELLUM DOWNS | SR | 25267919 | GLEE | GLENELG 66/19.1KV SUB (GLEE) | 26716.1 | 21 | 0.038675 | 1033.2372 | Pole Top | 55247.1913
2023_2024 | AER | UNPLANNED | 24NQ0099 | 25268413 | JC-01 | JULIACREEK NO.01 TRIPLEX | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 12550.8 | 9 | 0.032439 | 407.1344 | Pole Top | 21769.475
2023_2024 | AER | UNPLANNED | 24NQ0110 | 20004937 | NC-02 | NORTHCLONCURRY NO.02 | LR | 20004930 | NOCL | North Cloncurry 66/11kV Substation | 295513.7 | 326 | 0.03199 | 9453.4919 | Pole | 505478.2101
2023_2024 | AER | UNPLANNED | 24NQ0260 | 20003435 | CC-01 | CLONCURRY NO.01 | LR | 20003434 | CLON | CLONCURRY 66/11KV SUB (CC) | 11756.8 | 33 | 0.03749 | 440.7632 | Pole Top | 23567.6099
2023_2024 | AER | UNPLANNED | 24NQ0427 | 20003866 | CO-02 | COLLINSVILLE NO.02 | LR | 20003791 | COLL | COLLINSVILLE SUBSTATION | 36097.5 | 5 | 1.3658 | 49302.3389 | Pole Top | 2636196.059
2023_2024 | AER | UNPLANNED | 24NQ0620 | 20007634 | HU-20 | TORRENS CK | LR | 20007579 | HUGH | HUGHENDEN 66/33/6.6KV SUBSTATION | 33297.3333 | 65 | 0.029503 | 982.3829 | Pole | 52528.0144
2023_2024 | AER | UNPLANNED | 24NQ2880 | 20008686 | JC-11 | JULIACREEK NO.11 ORINDI | LR | 20008541 | JUCR | JULIA CREEK 66/33/19.1KV SUB (JC) | 12951.8 | 48 | 0.033779 | 437.4937 | Pole | 23392.7906
2023_2024 | AER | UNPLANNED | 24NQ2889 | 20012410 | ST02 | BRUCE HIGHWAY | SR | 20012369 | STUA | Stuart 66/11kV Substation | 3180232.7667 | 576 | 0.027381 | 87077.7401 | Pole | 4656046.7607
2023_2024 | AER | UNPLANNED | 24NQ4121 | 20020666 | SV-01 | Suvla SWER No.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 24660.8 | 16 | 0.02118 | 522.3123 | Pole | 27928.0363
2023_2024 | AER | UNPLANNED | 24NQ4404 | 20004937 | NC-02 | NORTHCLONCURRY NO.02 | LR | 20004930 | NOCL | North Cloncurry 66/11kV Substation | 32760 | 36 | 0.03199 | 1047.9934 | Pole | 56036.2046
2023_2024 | AER | UNPLANNED | 24NQ4667 | 20020666 | SV-01 | Suvla SWER No.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 10463.2 | 16 | 0.02118 | 221.6091 | Pole | 11849.4384
2023_2024 | AER | UNPLANNED | 24NQ5069 | 25267897 | AS-01 | Apsley SWER No.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 56901.5333 | 44 | 0.033417 | 1901.4596 | Pole | 101671.0433
2023_2024 | AER | UNPLANNED | 24NQ5071 | 25267901 | EL-01 | ELDERSLIESWER NO.01 | LR | 20013229 | WINT | WINTON 66/11/33KV SUB (WINT) | 59541.15 | 42 | 0.032542 | 1937.6122 | Pole | 103604.1247
2023_2024 | AER | UNPLANNED | 24NQ5073 | 20005133 | DR-12 | DUCHESSRD NO.12 | LR | 20005132 | DURO | DUCHESS RD 132/11KV SUBSTATION | 16489.5 | 75 | 0.025672 | 423.3202 | Pole | 22634.9309
2023_2024 | AER | UNPLANNED | 24NQ5511 | 20009483 | LE-02 | MOUNTLEYSHON NO.02 | SR | 20009480 | MOLE | MOUNT LEYSHON 66/11KV SUB (LE) | 935.0833 | 1 | 0.30051 | 280.9982 | Pole | 15024.9729
2023_2024 | AER | UNPLANNED | 24NQ5511 | 20009493 | LP-01 | MOUNTLEYSHONPUMP NO.01 | SR | 20009492 | MOLP | MOUNT LEYSHON PUMP 66/11KV SUB | 18701.6667 | 20 | 0.018036 | 337.3108 | Pole | 18036.0075
2023_2024 | AER | UNPLANNED | 24NQ5511 | 20011334 | PJ-01 | PAJINGO MINE NO.01 | SR | 20011333 | PAJI | PAJINGO 66/11KV SUB (PJ) | 935.0833 | 1 | 102.1364 | 95506.0222 | Pole | 5106707.0072
2023_2024 | AER | UNPLANNED | 24NQ6868 | 20004937 | NC-02 | NORTHCLONCURRY NO.02 | LR | 20004930 | NOCL | North Cloncurry 66/11kV Substation | 19899.7333 | 53 | 0.03199 | 636.593 | Pole | 34038.6303
2023_2024 | AER | UNPLANNED | 24SW0281 | 60026644 | F004Q | QUILPIE RURAL | LR | 60007257 | QUIL | QUILPIE 66/11KV SUB | 8382.9 | 6 | 0.028449 | 238.4866 | Pole | 12751.8801
2023_2024 | AER | UNPLANNED | 24SW0434 | 60026788 | F3525 | MILL HILL | SR | 84536204 | WAEA | WARWICK EAST 33/11KV SUB | 56119.6667 | 800 | 0.028833 | 1618.0751 | Pole Top | 86518.478
2023_2024 | AER | UNPLANNED | 24SW0455 | 60026641 | F001R | YULEBA | LR | 60025702 | ROMA | ROMA 132/66/33KV SUB (T083) | 20271.7667 | 49 | 0.024528 | 497.2267 | Pole | 26586.7128
2023_2024 | AER | UNPLANNED | 24SW0760 | 60026766 | F315C | EULO | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 510913.8 | 513 | 0.019293 | 9857.1596 | Pole | 527062.3233
2023_2024 | AER | UNPLANNED | 24SW0823 | 60026766 | F315C | EULO | LR | 60007256 | CUNN | CUNNAMULLA 66/22/11KV SUB | 22842.6 | 18 | 0.019293 | 440.7067 | Pole | 23564.5892
2023_2024 | AER | UNPLANNED | 24SW0981 | 60026774 | F3365 | LANEWOOD | SR | 60330485 | OAKE | Oakey 33/11kV Substation | 13293.5 | 55 | 0.019838 | 263.7211 | Pole Top | 14101.1678
2023_2024 | AER | UNPLANNED | 24SW1418 | 60026743 | F2880 | FORMARTIN | SR | 60007238 | NORW | NORWIN 33/11KV SUB (ME074) | 32705 | 31 | 0.06379 | 2086.2566 | Pole | 111552.1406
2023_2024 | AER | UNPLANNED | 24SW3781 | 60026892 | F076C | DULACCA | LR | 60007202 | MILE | MILES 33/11kV SUBSTATION | 126987.85 | 373 | 0.01731 | 2198.1245 | Pole | 117533.7152
2023_2024 | AER | UNPLANNED | 24SW4860 | 60026644 | F004Q | QUILPIE RURAL | LR | 60007257 | QUIL | QUILPIE 66/11KV SUB | 9091.5 | 9 | 0.028449 | 258.6457 | Pole | 13829.7865
2023_2024 | AER | UNPLANNED | 24SW5082 | 60026687 | F118R | CORFE ROAD | SR | 60007250 | MW002 | Roma East 33/11kV Substation | 4140 | 36 | 0.01907 | 78.951 | Pole | 4221.5106
2023_2024 | AER | UNPLANNED | 24WB3848 | 50000035 | EB-G | KEPNOCK | SR | 50000029 | EABU | East Bundaberg 66/11kV Substation | 152 | 1 | 0.016764 | 2.5481 | Pole | 136.2453

## Pole & Pole Top Failures 21-24
OUTAGE_NAME
Outage Name | Asset
21SW9522 | Pole Top
21SW9571 | Pole Top
21WB6921 | Pole Top
21NQ8645 | Pole Top
21FN7259 | Pole Top
21FN7391 | Pole Top
21SW10084 | Pole Top
21SW10165 | Pole Top
21NQ9121 | Pole Top
21WB7560 | Pole Top
21SW10735 | Pole Top
21MK4321 | Pole Top
21NQ9994 | Pole Top
21FN8614 | Pole Top
21FN8797 | Pole Top
21SW11599 | Pole Top
21CA10434 | Pole Top
21NQ10306 | Pole Top
21FN9090 | Pole Top
21FN9160 | Pole Top
21FN9179 | Pole Top
21WB8869 | Pole Top
21FN9258 | Pole Top
21FN9417 | Pole Top
21WB9023 | Pole Top
21CA11133 | Pole Top
21WB9046 | Pole Top
21FN9553 | Pole Top
21FN9602 | Pole Top
21WB9133 | Pole Top
21FN9625 | Pole Top
21NQ11016 | Pole Top
21SW12695 | Pole Top
21WB9467 | Pole Top
21FN10114 | Pole Top
21FN10144 | Pole Top
21CA11893 | Pole Top
21FN10351 | Pole Top
21FN10315 | Pole Top
21SW13719 | Pole Top
21MK5662 | Pole Top
21FN10535 | Pole Top
21WB10260 | Pole Top
21WB10500 | Pole Top
21NQ12606 | Pole Top
21WB10845 | Pole Top
21WB10944 | Pole Top
21WB10961 | Pole Top
21NQ12954 | Pole Top
21WB11614 | Pole Top
21SW15812 | Pole Top
21NQ13475 | Pole Top
21WB11781 | Pole Top
21SW15871 | Pole Top
21WB11792 | Pole Top
21NQ13615 | Pole Top
21SW15962 | Pole Top
21WB11988 | Pole Top
21FN11978 | Pole Top
21SW16189 | Pole Top
21FN12003 | Pole Top
21FN12059 | Pole Top
21MK6854 | Pole Top
21MK6956 | Pole Top
21SW16817 | Pole Top
21NQ14273 | Pole Top
21SW17031 | Pole Top
21CA15243 | Pole Top
21MK7134 | Pole Top
21WB12669 | Pole Top
21NQ14705 | Pole Top
21SW17543 | Pole Top
21NQ14855 | Pole Top
21SW17698 | Pole Top
21WB12900 | Pole Top
21WB12987 | Pole Top
21NQ14968 | Pole Top
21FN13177 | Pole Top
21WB13115 | Pole Top
21CA16026 | Pole Top
21WB13128 | Pole Top
21WB13124 | Pole Top
21SW18126 | Pole Top
21WB13301 | Pole Top
21SW18419 | Pole Top
21SW18430 | Pole Top
21CA16416 | Pole Top
21FN13663 | Pole Top
21NQ15530 | Pole Top
21MK7692 | Pole Top
21NQ15678 | Pole Top
21FN13810 | Pole Top
21WB13799 | Pole Top
21NQ15838 | Pole Top
21WB13850 | Pole Top
21WB13922 | Pole Top
21SW19217 | Pole Top
21SW19220 | Pole Top
21FN14074 | Pole Top
21SW19311 | Pole Top
21SW19546 | Pole Top
21MK7962 | Pole Top
21CA17199 | Pole Top
21SW19725 | Pole Top
21WB14133 | Pole Top
21FN14170 | Pole Top
21SW19783 | Pole Top
21WB14265 | Pole Top
21WB14280 | Pole Top
21FN14254 | Pole Top
21MK8066 | Pole Top
21SW20091 | Pole Top
21WB14359 | Pole Top
21SW20167 | Pole Top
22SW0020 | Pole Top
22MK0027 | Pole Top
22MK0022 | Pole Top
22NQ0212 | Pole Top
22SW0059 | Pole Top
22NQ0187 | Pole Top
22FN0157 | Pole Top
22WB0123 | Pole Top
22FN0222 | Pole Top
22MK0241 | Pole Top
22FN0373 | Pole Top
22MK0269 | Pole Top
22WB0315 | Pole Top
22NQ0540 | Pole Top
22FN0386 | Pole Top
22WB0399 | Pole Top
22CA0658 | Pole Top
22SW0602 | Pole Top
22MK0399 | Pole Top
22SW1086 | Pole Top
22NQ0984 | Pole Top
22MK0530 | Pole Top
22CA1286 | Pole Top
22CA1285 | Pole Top
22NQ1178 | Pole Top
22NQ1233 | Pole Top
22CA1324 | Pole Top
22SW1381 | Pole Top
22SW1368 | Pole Top
22NQ1364 | Pole Top
22WB0905 | Pole Top
22SW1565 | Pole Top
22WB0986 | Pole Top
22CA1522 | Pole Top
22NQ1575 | Pole Top
22NQ1751 | Pole Top
22SW1952 | Pole Top
22CA1858 | Pole Top
22WB1336 | Pole Top
22WB1335 | Pole Top
22NQ1857 | Pole Top
22MK0900 | Pole Top
22NQ1925 | Pole Top
22WB1519 | Pole Top
22SW2142 | Pole Top
22NQ2101 | Pole Top
22NQ2260 | Pole Top
22WB1696 | Pole Top
22SW2435 | Pole Top
22CA2389 | Pole Top
22SW2545 | Pole Top
22FN2033 | Pole Top
22WB1991 | Pole Top
22CA2648 | Pole Top
22MK1237 | Pole Top
22SW3015 | Pole Top
22NQ2753 | Pole Top
22MK1250 | Pole Top
22NQ2859 | Pole Top
22MK1332 | Pole Top
22SW3393 | Pole Top
22NQ3024 | Pole Top
22SW3505 | Pole Top
22NQ3057 | Pole Top
22SW3643 | Pole Top
22NQ3198 | Pole Top
22NQ3291 | Pole Top
22NQ3310 | Pole Top
22SW3912 | Pole Top
22NQ3323 | Pole Top
22CA3652 | Pole Top
22CA3650 | Pole Top
22MK1830 | Pole Top
22SW4307 | Pole Top
22WB3657 | Pole Top
22SW4463 | Pole Top
22CA4457 | Pole Top
22WB3959 | Pole Top
22CA4526 | Pole Top
22WB3983 | Pole Top
22MK2211 | Pole Top
22CA4546 | Pole Top
22NQ3871 | Pole Top
22NQ3927 | Pole Top
22CA4725 | Pole Top
22SW4930 | Pole Top
22MK2320 | Pole Top
22CA4782 | Pole Top
22FN3667 | Pole Top
22SW4947 | Pole Top
22WB4256 | Pole Top
22MK2430 | Pole Top
22NQ4177 | Pole Top
22FN4029 | Pole Top
22SW5553 | Pole Top
22SW5692 | Pole Top
22SW5688 | Pole Top
22NQ4578 | Pole Top
22NQ4714 | Pole Top
22CA5533 | Pole Top
22SW5970 | Pole Top
22CA5634 | Pole Top
22FN4610 | Pole Top
22WB5049 | Pole Top
22NQ5101 | Pole Top
22CA5929 | Pole Top
22NQ5243 | Pole Top
22SW6456 | Pole Top
22CA6140 | Pole Top
22CA6155 | Pole Top
22FN5014 | Pole Top
22NQ5468 | Pole Top
22CA6191 | Pole Top
22FN5087 | Pole Top
22NQ5627 | Pole Top
22WB5508 | Pole Top
22CA6309 | Pole Top
22WB5540 | Pole Top
22WB5564 | Pole Top
22CA6401 | Pole Top
22SW6878 | Pole Top
22CA6494 | Pole Top
22SW6895 | Pole Top
22MK3584 | Pole Top
22NQ6039 | Pole Top
22NQ6202 | Pole Top
22WB6050 | Pole Top
22CA6890 | Pole Top
22WB6061 | Pole Top
22SW7427 | Pole Top
22CA6907 | Pole Top
22NQ6315 | Pole Top
22SW7459 | Pole Top
22CA6935 | Pole Top
22WB6152 | Pole Top
22NQ6408 | Pole Top
22WB6175 | Pole Top
22SW7577 | Pole Top
22SW7738 | Pole Top
22SW7737 | Pole Top
22SW7766 | Pole Top
22SW7773 | Pole Top
22NQ6572 | Pole Top
22FN6216 | Pole Top
22SW7827 | Pole Top
22SW8000 | Pole Top
22WB6484 | Pole Top
22SW8214 | Pole Top
22NQ7026 | Pole Top
22WB6679 | Pole Top
22NQ7161 | Pole Top
22WB6697 | Pole Top
22SW8468 | Pole Top
22SW8520 | Pole Top
22NQ7439 | Pole Top
22CA7855 | Pole Top
22CA7895 | Pole Top
22NQ7612 | Pole Top
22FN7273 | Pole Top
22CA8515 | Pole Top
22SW10037 | Pole Top
22NQ8265 | Pole Top
22WB7727 | Pole Top
22WB7739 | Pole Top
22SW10074 | Pole Top
22SW10306 | Pole Top
22FN7939 | Pole Top
22SW10350 | Pole Top
22CA9483 | Pole Top
22NQ8609 | Pole Top
22WB8110 | Pole Top
22SW10510 | Pole Top
22CA9618 | Pole Top
22NQ8721 | Pole Top
22WB8337 | Pole Top
22MK5302 | Pole Top
22SW10736 | Pole Top
22SW10836 | Pole Top
22SW10875 | Pole Top
22FN8329 | Pole Top
22SW10903 | Pole Top
22SW10898 | Pole Top
22WB8498 | Pole Top
FC2275357 | Pole Top
22WB8552 | Pole Top
22CA9905 | Pole Top
22SW11049 | Pole Top
22SW11039 | Pole Top
22WB8640 | Pole Top
22WB8644 | Pole Top
22SW11191 | Pole Top
22SW11440 | Pole Top
22WB9061 | Pole Top
22WB8972 | Pole Top
22FN8960 | Pole Top
22SW11797 | Pole Top
22WB9171 | Pole Top
22NQ9781 | Pole Top
22SW11916 | Pole Top
22WB9304 | Pole Top
22SW12051 | Pole Top
22WB9376 | Pole Top
22SW12262 | Pole Top
22NQ10069 | Pole Top
22CA10766 | Pole Top
22WB9497 | Pole Top
22SW12406 | Pole Top
22SW12407 | Pole Top
22WB9632 | Pole Top
22SW12531 | Pole Top
22CA10891 | Pole Top
22NQ10417 | Pole Top
22FN9614 | Pole Top
22FN9634 | Pole Top
22MK6342 | Pole Top
22FN9812 | Pole Top
22SW13060 | Pole Top
22SW13089 | Pole Top
22SW13173 | Pole Top
22FN9975 | Pole Top
22SW13323 | Pole Top
22MK6522 | Pole Top
22FN10123 | Pole Top
22NQ11215 | Pole Top
22WB10402 | Pole Top
22FN10377 | Pole Top
22CA11682 | Pole Top
22CA11833 | Pole Top
22MK6847 | Pole Top
22WB10503 | Pole Top
22CA11885 | Pole Top
22SW14010 | Pole Top
22SW14008 | Pole Top
22WB10782 | Pole Top
22NQ11809 | Pole Top
22NQ11870 | Pole Top
22FN10793 | Pole Top
22FN10863 | Pole Top
22FN10903 | Pole Top
22FN10907 | Pole Top
22SW14449 | Pole Top
22SW14481 | Pole Top
22CA12490 | Pole Top
22FN11054 | Pole Top
22CA12626 | Pole Top
22FN11146 | Pole Top
22CA12810 | Pole Top
22SW14754 | Pole Top
22CA12956 | Pole Top
22WB11266 | Pole Top
22CA13031 | Pole Top
22NQ12854 | Pole Top
22CA13060 | Pole Top
22SW15587 | Pole Top
22CA13567 | Pole Top
22SW15619 | Pole Top
22FN11646 | Pole Top
22WB11712 | Pole Top
22MK7664 | Pole Top
22NQ13389 | Pole Top
22SW15833 | Pole Top
22WB11998 | Pole Top
22WB12020 | Pole Top
22NQ13771 | Pole Top
22FN12077 | Pole Top
22CA14419 | Pole Top
22NQ14172 | Pole Top
22FN12364 | Pole Top
22WB12386 | Pole Top
22NQ14391 | Pole Top
22NQ14445 | Pole Top
22SW16847 | Pole Top
22NQ14627 | Pole Top
22NQ14658 | Pole Top
22FN12825 | Pole Top
22SW17013 | Pole Top
22FN13006 | Pole Top
22FN13076 | Pole Top
22MK8555 | Pole Top
22SW17326 | Pole Top
22WB12907 | Pole Top
22FN13187 | Pole Top
22SW17411 | Pole Top
22SW17454 | Pole Top
22NQ15349 | Pole Top
22FN13232 | Pole Top
22WB12948 | Pole Top
22WB13062 | Pole Top
22MK8704 | Pole Top
22WB13042 | Pole Top
22WB13162 | Pole Top
22CA15844 | Pole Top
22CA15814 | Pole Top
22MK9162 | Pole Top
22CA16371 | Pole Top
22SW18508 | Pole Top
22FN13967 | Pole Top
22CA16477 | Pole Top
22CA16529 | Pole Top
22WB13912 | Pole Top
22MK9318 | Pole Top
22NQ16552 | Pole Top
23SW0040 | Pole Top
23SW0181 | Pole Top
23CA0191 | Pole Top
23CA0221 | Pole Top
23NQ0148 | Pole Top
23FN0214 | Pole Top
23CA0252 | Pole Top
23SW0372 | Pole Top
23CA0460 | Pole Top
23MK0328 | Pole Top
23WB0626 | Pole Top
23NQ0508 | Pole Top
23SW0676 | Pole Top
23NQ0576 | Pole Top
23WB0821 | Pole Top
23NQ0752 | Pole Top
23MK0560 | Pole Top
23WB0921 | Pole Top
23FN0854 | Pole Top
23CA0971 | Pole Top
23NQ0938 | Pole Top
23MK0718 | Pole Top
23SW1438 | Pole Top
23SW1453 | Pole Top
23SW1431 | Pole Top
23CA1178 | Pole Top
23NQ1157 | Pole Top
23WB1082 | Pole Top
23SW1529 | Pole Top
23NQ1227 | Pole Top
23SW1567 | Pole Top
23CA1263 | Pole Top
23FN1086 | Pole Top
23CA1305 | Pole Top
23WB1191 | Pole Top
23WB1332 | Pole Top
23SW1669 | Pole Top
23WB1291 | Pole Top
23WB1394 | Pole Top
23SW1760 | Pole Top
23SW1774 | Pole Top
23CA1505 | Pole Top
23CA1704 | Pole Top
23MK1145 | Pole Top
23CA1869 | Pole Top
23NQ1866 | Pole Top
23MK1225 | Pole Top
23MK1276 | Pole Top
23SW2466 | Pole Top
23NQ2083 | Pole Top
23SW2661 | Pole Top
23CA2293 | Pole Top
23NQ2172 | Pole Top
23CA2359 | Pole Top
23SW2911 | Pole Top
23WB2372 | Pole Top
23FN2280 | Pole Top
23WB2400 | Pole Top
23NQ2452 | Pole Top
23WB2444 | Pole Top
23NQ2467 | Pole Top
23WB2579 | Pole Top
23FN2651 | Pole Top
23CA2978 | Pole Top
23NQ2792 | Pole Top
23NQ2818 | Pole Top
23SW3500 | Pole Top
23CA3190 | Pole Top
23CA3238 | Pole Top
23SW3655 | Pole Top
23MK2015 | Pole Top
23SW3665 | Pole Top
23NQ3040 | Pole Top
23SW3670 | Pole Top
23WB2962 | Pole Top
23WB3019 | Pole Top
23SW3799 | Pole Top
23FN3000 | Pole Top
23CA3439 | Pole Top
23CA3471 | Pole Top
23NQ3131 | Pole Top
23SW3865 | Pole Top
23CA3525 | Pole Top
23NQ3181 | Pole Top
23WB3316 | Pole Top
23CA3649 | Pole Top
23SW4157 | Pole Top
23SW4177 | Pole Top
23WB3645 | Pole Top
23NQ3585 | Pole Top
23FN3625 | Pole Top
23FN3628 | Pole Top
23SW4846 | Pole Top
23NQ3649 | Pole Top
23CA4089 | Pole Top
23SW4872 | Pole Top
23SW4956 | Pole Top
23SW5113 | Pole Top
23SW5114 | Pole Top
23CA4325 | Pole Top
23SW5380 | Pole Top
23FN4205 | Pole Top
23SW5589 | Pole Top
23SW5585 | Pole Top
23NQ4093 | Pole Top
23MK2819 | Pole Top
23CA4671 | Pole Top
23WB4285 | Pole Top
23MK2859 | Pole Top
23NQ4197 | Pole Top
23MK2934 | Pole Top
23NQ4241 | Pole Top
23FN4560 | Pole Top
23CA4907 | Pole Top
23NQ4365 | Pole Top
23CA4988 | Pole Top
23FN4692 | Pole Top
23NQ4472 | Pole Top
23NQ4495 | Pole Top
23SW6217 | Pole Top
23FN4911 | Pole Top
23MK3262 | Pole Top
23NQ4636 | Pole Top
23SW6339 | Pole Top
23NQ4694 | Pole Top
23NQ4692 | Pole Top
23MK3405 | Pole Top
23WB4927 | Pole Top
23FN5238 | Pole Top
23FN5370 | Pole Top
23WB5101 | Pole Top
23MK3517 | Pole Top
23WB5138 | Pole Top
23SW6928 | Pole Top
23FN5613 | Pole Top
23SW7046 | Pole Top
23WB5506 | Pole Top
23CA6000 | Pole Top
23SW7220 | Pole Top
23NQ5403 | Pole Top
23SW7428 | Pole Top
23NQ5669 | Pole Top
23FN6232 | Pole Top
23FN6247 | Pole Top
23MK3979 | Pole Top
23SW7661 | Pole Top
23WB6092 | Pole Top
23WB6089 | Pole Top
23CA6655 | Pole Top
23FN6491 | Pole Top
23CA6694 | Pole Top
23MK4177 | Pole Top
23SW8009 | Pole Top
23WB6373 | Pole Top
23NQ6134 | Pole Top
23NQ6160 | Pole Top
23NQ6195 | Pole Top
23MK4266 | Pole Top
23WB6664 | Pole Top
23SW7956 | Pole Top
23SW7988 | Pole Top
23CA6774 | Pole Top
23SW8716 | Pole Top
23WB6918 | Pole Top
23WB7133 | Pole Top
23FN7258 | Pole Top
23MK4511 | Pole Top
23NQ6671 | Pole Top
23FN7716 | Pole Top
23MK4615 | Pole Top
23CA2659 | Pole Top
21NQ8983 | Pole
21SW10055 | Pole
21SW11181 | Pole
21FN8350 | Pole
21FN8527 | Pole
21CA10056 | Pole
21FN8242 | Pole
21NQ10176 | Pole
21NQ10570 | Pole
21NQ11470 | Pole
21NQ11338 | Pole
21FN9695 | Pole
21NQ11242 | Pole
21CA11450 | Pole
21SW12686 | Pole
21SW12764 | Pole
21SW14035 | Pole
21CA13256 | Pole
21SW14421 | Pole
21NQ11966 | Pole
21CA13075 | Pole
21CA13096 | Pole
21CA13074 | Pole
21NQ12115 | Pole
21SW16311 | Pole
21SW16738 | Pole
21NQ14060 | Pole
21FN12058 | Pole
21NQ13538 | Pole
21FN11793 | Pole
21SW16592 | Pole
21CA15671 | Pole
21CA14545 | Pole
21SW17857 | Pole
21NQ14692 | Pole
21SW20189 | Pole
21FN13589 | Pole
21SW18925 | Pole
21WB13743 | Pole
21WB13197 | Pole
21CA17499 | Pole
21NQ16355 | Pole
21SW19693 | Pole
21NQ15925 | Pole
21NQ15921 | Pole
21NQ15901 | Pole
21NQ15894 | Pole
21NQ15911 | Pole
21SW19355 | Pole
21FN13373 | Pole
21SW19682 | Pole
21SW19833 | Pole
21NQ16476 | Pole
21NQ15630 | Pole
22NQ0387 | Pole
22SW1600 | Pole
22SW1065 | Pole
22CA0849 | Pole
22SW0724 | Pole
22NQ0749 | Pole
22NQ0753 | Pole
22NQ0746 | Pole
22NQ0543 | Pole
22NQ0484 | Pole
22SW0240 | Pole
22SW0198 | Pole
22CA0242 | Pole
22NQ0113 | Pole
22NQ0039 | Pole
22FN0158 | Pole
22FN1301 | Pole
22FN0458 | Pole
22NQ0194 | Pole
22CA0266 | Pole
22SW0303 | Pole
22SW0277 | Pole
22SW0317 | Pole
22FN1977 | Pole
22SW3490 | Pole
22SW3136 | Pole
22SW3123 | Pole
22NQ2869 | Pole
22NQ2706 | Pole
22FN1878 | Pole
22NQ2287 | Pole
22SW3135 | Pole
22CA2902 | Pole
22SW3581 | Pole
22WB2344 | Pole
22WB4045 | Pole
22FN3360 | Pole
22SW4488 | Pole
22WB3187 | Pole
22SW4116 | Pole
22CA4395 | Pole
22CA5087 | Pole
22NQ4301 | Pole
22CA4470 | Pole
22CA4467 | Pole
22SW4390 | Pole
22SW4322 | Pole
22NQ3162 | Pole
22CA5011 | Pole
22CA4222 | Pole
22NQ5429 | Pole
22CA6174 | Pole
22SW5783 | Pole
22FN5158 | Pole
22SW7498 | Pole
22SW6981 | Pole
22CA6899 | Pole
22NQ6057 | Pole
22NQ7711 | Pole
22CA8397 | Pole
22NQ8277 | Pole
22CA9555 | Pole
22SW10871 | Pole
22SW11498 | Pole
22MK5995 | Pole
22WB9421 | Pole
22NQ10160 | Pole
22CA10793 | Pole
22NQ10427 | Pole
22NQ10432 | Pole
22NQ11019 | Pole
22SW13333 | Pole
22NQ11093 | Pole
22SW13541 | Pole
22NQ11130 | Pole
22FN10117 | Pole
22SW13503 | Pole
22SW13628 | Pole
22NQ11281 | Pole
22NQ11410 | Pole
22NQ11409 | Pole
22SW14344 | Pole
22NQ12222 | Pole
22CA12730 | Pole
22NQ12698 | Pole
22NQ12730 | Pole
22FN11273 | Pole
22CA13188 | Pole
22WB11502 | Pole
22NQ12969 | Pole
22WB11755 | Pole
22CA13723 | Pole
22FN11730 | Pole
22FN11753 | Pole
22CA13822 | Pole
22NQ13539 | Pole
22NQ13503 | Pole
22CA13954 | Pole
22FN12089 | Pole
22NQ14115 | Pole
22NQ14126 | Pole
22NQ14128 | Pole
22NQ14309 | Pole
22WB12468 | Pole
22SW16785 | Pole
22SW16790 | Pole
22FN12938 | Pole
22CA15317 | Pole
22SW17616 | Pole
22SW17621 | Pole
22SW17640 | Pole
22CA15606 | Pole
22CA15641 | Pole
22CA15857 | Pole
22SW17944 | Pole
22CA15874 | Pole
22SW18036 | Pole
22NQ15747 | Pole
22CA15994 | Pole
22NQ16159 | Pole
22NQ16208 | Pole
23FN0605 | Pole
23FN0753 | Pole
23CA0917 | Pole
23SW1415 | Pole
23FN1048 | Pole
23CA1413 | Pole
23SW1700 | Pole
23SW1701 | Pole
23FN1329 | Pole
23SW2332 | Pole
23SW2362 | Pole
23NQ2080 | Pole
23CA2232 | Pole
23NQ2908 | Pole
23SW4561 | Pole
23SW3980 | Pole
23WB3947 | Pole
23CA3713 | Pole
23NQ2894 | Pole
23FN3796 | Pole
23NQ3899 | Pole
23FN4039 | Pole
23SW5592 | Pole
23CA4611 | Pole
23FN4353 | Pole
23WB4795 | Pole
23SW6326 | Pole
23MK4304 | Pole
23MK4521 | Pole
23SW8817 | Pole
23SW9699 | Pole
23CA8180 | Pole
23SW9086 | Pole
23SW16258 | Pole
23CA13126 | Pole
23WB13094 | Pole
23FN13857 | Pole
23SW18638 | Pole
23NQ12755 | Pole
23FN14249 | Pole
23CA15342 | Pole
23SW19594 | Pole
23FN14668 | Pole
23NQ13636 | Pole
23SW20617 | Pole
23FN15148 | Pole
23CA16557 | Pole
23NQ14096 | Pole
23SW20887 | Pole
23SW21062 | Pole
23SW21011 | Pole
23CA16684 | Pole
23SW21254 | Pole
23CA16938 | Pole
23SW21666 | Pole
23NQ14866 | Pole
23NQ14971 | Pole
23NQ15081 | Pole
23CA18028 | Pole
23NQ15315 | Pole
23FN16982 | Pole
23WB17030 | Pole
23MK10249 | Pole
23NQ14359 | Pole
23NQ14399 | Pole
23CA17678 | Pole
23NQ15005 | Pole
23CA17964 | Pole
23FN16641 | Pole
23SW23189 | Pole
23SW22874 | Pole
23NQ15158 | Pole
23NQ15193 | Pole
23NQ15203 | Pole
23NQ15232 | Pole
23CA18467 | Pole
23FN16800 | Pole
23CA18939 | Pole
23SW24121 | Pole
23SW24114 | Pole
24NQ0051 | Pole
24NQ0058 | Pole
24NQ0099 | Pole
24NQ0110 | Pole
24SW0281 | Pole
24NQ0260 | Pole
24FN0149 | Pole
24SW0434 | Pole
24SW0455 | Pole
24NQ0427 | Pole
24SW0760 | Pole
24NQ0620 | Pole
24SW0823 | Pole
24CA0719 | Pole
24SW0981 | Pole
24MK0493 | Pole
24CA1098 | Pole
24SW1418 | Pole
24CA1231 | Pole
24NQ2880 | Pole
24FN2066 | Pole
24NQ2889 | Pole
24SW3781 | Pole
24CA2656 | Pole
24NQ4121 | Pole
24NQ4404 | Pole
24CA3006 | Pole
24SW4860 | Pole
24NQ4667 | Pole
24SW5360 | Pole
24SW5082 | Pole
24NQ5069 | Pole
24NQ5071 | Pole
24NQ5073 | Pole
24NQ5511 | Pole
24CA3884 | Pole
24FN3593 | Pole
24CA4493 | Pole
24SW6576 | Pole
24NQ6868 | Pole
24WB3848 | Pole