## Cover
United Energy
Regulatory proposal 2026-31
Lower Mornington Peninsula supply area
| Model number: | 3.01
2025-01-31
17

## Summary
United Energy
Lower Mornington Peninsula supply area
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Construct HGS-RBD sub-transmission line |  | -19.1037 | 22.118 | 3.0142
| Option 3 | Construct HGS-RBD sub-transmission line and new Shoreham zone substation |  | -31.5976 | 37.5885 | 5.9909
| Option 4 | Expanded non-network solution capability |  | -5.7138 | -2.0185 | -7.7323
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 3 | Construct HGS-RBD sub-transmission line and new Shoreham zone substation |  | 5.9909
PREFERRED OPTION
Preferred Option
Option 3
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 0 | 0 | 0 | 31.6016 | 31.6016 |  | 63.2032
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 3.0142 | 5.9909 | -7.7323 |  |  | Option 3
| Capex 10% higher |  | 0 | 1.1039 | 2.8312 | -7.7323 |  |  | Option 3
| Capex 10% lower |  | 0 | 4.9246 | 9.1507 | -7.7323 |  |  | Option 3
| Total benefits 10% higher |  | 0 | 5.226 | 9.7498 | -7.9342 |  |  | Option 3
| Total benefits 10% lower |  | 0 | 0.80245 | 2.2321 | -7.5305 |  |  | Option 3
| Capex 10% higher & Total benefits 10% lower |  | 0 | -1.1079 | -0.92769 | -7.5305 |  |  | Option 1 (base case)
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
United Energy
Lower Mornington Peninsula supply area
Project
|  | Business: | United Energy
|  | Descripton: | Lower Mornington Peninsula supply area
|  | Date of cost inputs: | December |  | 2023
|  | Option | Description
|  | Option 1 (base case) | No change to existing practices
|  | Option 2 | Construct HGS-RBD sub-transmission line
|  | Option 3 | Construct HGS-RBD sub-transmission line and new Shoreham zone substation
|  | Option 4 | Expanded non-network solution capability
Option 5
|  | Compliance project | No
|  | Expenditure starts | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  | 3.5% | [real_disc]
|  | VCR date |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  | 20 | [years]\
|  | Output dollars |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | RBD |  | Rosebud | 35928.5557 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  | 1
|  | Harm to property from bushfire |  |  | 1
|  | Harm to environment |  |  | 1
|  | Safety - Public trespass |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  | 3
|  | Safety from bushfire in HBRA |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  | 10
^ Public or employee
|  | Incident type |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  | 20%
Other benefits
| ENVIRONMENTAL | [7 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  | Value
|  | Reliability in worst-served areas |  |  | 0 | 2023-12-31 | per MWh
|  | Network resilience |  |  | 38562.334 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  | 862.6028 | 2023-12-31 | per MWh
|  | Aesthetics |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  | 0.34751 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  | 0.34751 | 2023-12-31 | per customer minute
|  | Communication |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[5 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  | 10% | -10%

## Option1 (base case)
United Energy
Lower Mornington Peninsula supply area
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  |  |  | 2.9113 | 4.222 | 5.7763 | 7.0445 | 8.6906 | 11.4907 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996
| Energy not Supplied - MEDs |  |  |  |  | 45.9185 | 46.5613 | 47.2132 | 47.8742 | 48.5444 | 49.224 | 49.9132 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612
| Energy not Supplied - Non MEDs |  |  |  |  | 21.535 | 21.8365 | 22.1422 | 22.4522 | 22.7666 | 23.0853 | 23.4085 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362
| Total energy at risk |  |  | MWh |  | 70.3648 | 72.6198 | 75.1317 | 77.3709 | 80.0015 | 83.8 | 89.5213 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478 | 90.5478
| Energy at risk value | $/MWh | 35928.5557 | 2023-12-31 |  | 2528107.3866 | 2609125.4513 | 2699375.1954 | 2779825.5147 | 2874340.1324 | 3010812.5254 | 3216370.3218 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985 | 3253251.0985
| Bushfire risk |  |  | 2023-12-31 |  | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5
| Customer value of network resilience |  |  | 2023-12-31 |  | 60246.3901 | 61089.8395 | 61945.0973 | 62812.3286 | 63691.7012 | 64583.3851 | 65487.5525 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782
| Cost of events (GSLs, call costs, claims) |  |  | 2023-12-31 |  | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
| Total risk cost |  |  |  |  | 2643095.2767 | 2724956.7908 | 2816061.7927 | 2897379.3434 | 2992773.3337 | 3130137.4105 | 3336599.3743 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767 | 3374396.9767
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38562.334 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex saving |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
United Energy
Lower Mornington Peninsula supply area
OPTION 2 | Construct HGS-RBD sub-transmission line
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| New 66kV Line |  | 50 | 2023-12-31 | 0 | 0 | 0 | 17167718.5 | 17167718.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 17167718.5 | 17167718.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating saving |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  |  | 2.9113 | 4.222 | 5.7763 | 7.0445 | 8.6906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy not Supplied - MEDs |  |  |  | 45.9185 | 46.5613 | 47.2132 | 47.8742 | 48.5444 | 49.224 | 49.9132 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612
| Energy not Supplied - Non MEDs |  |  |  | 21.535 | 21.8365 | 22.1422 | 22.4522 | 22.7666 | 23.0853 | 23.4085 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362
| Total energy at risk |  |  | MWh | 70.3648 | 72.6198 | 75.1317 | 77.3709 | 80.0015 | 72.3093 | 73.3217 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482 | 74.3482
| Energy at risk value | $/MWh | 35928.5557 | 2023-12-31 | 2528107.3866 | 2609125.4513 | 2699375.1954 | 2779825.5147 | 2874340.1324 | 2597969.6201 | 2634341.1948 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715 | 2671221.9715
| Bushfire risk |  |  | 2023-12-31 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5
| Customer value of network resilience |  |  | 2023-12-31 | 60246.3901 | 61089.8395 | 61945.0973 | 62812.3286 | 63691.7012 | 64583.3851 | 65487.5525 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782
| Cost of events (GSLs, call costs, claims) |  |  | 2023-12-31 | 50000 | 50000 | 50000 | 50000 | 50000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 2643095.2767 | 2724956.7908 | 2816061.7927 | 2897379.3434 | 2992773.3337 | 2667294.5052 | 2704570.2473 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497 | 2742367.8497
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38562.334 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex saving |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 900000 | 900000 | 900000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 900000 | 900000 | 900000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000
-1
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 462842.9053 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127
Capital expenditure
| New 66kV Line |  |  | 2023-12-31 | 0 | 0 | 0 | -17167718.5 | -17167718.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| New 66kV Line |  |  | 2023-12-31 | 0 | 0 | 0 | -17167718.5 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - New 66kV Line |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -731923.5244 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -731923.5244 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -731923.5244 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 462842.9053 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127 | 632029.127
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 900000 | 900000 | 900000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 168076.4756 | -101004.1436 | 68182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781
| First capex year |  |  | 4
| First year |  |  | 4
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 0 | 0 | 0 | 168076.4756 | -101004.1436 | 68182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | -731923.5244 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 900000 | 1362842.9053 | 1532029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127 | 1732029.127
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 0 | 0 | 0 | 94884.1231 | -247388.8485 | -78202.6268 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732 | 121797.3732
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 0 | 0 | 0 | 241268.828 | 45380.5613 | 214566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783 | 414566.783
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 0 | 0 | 0 | 258076.4756 | 35280.1469 | 221384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908 | 441384.9908
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 0 | 0 | 0 | 78076.4756 | -237288.4342 | -85020.8346 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654 | 94979.1654
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 0 | 0 | 0 | 4884.1231 | -383673.139 | -231405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395 | -51405.5395
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | 0 | 168076.4756 | -101004.1436 | 68182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | 0 | 168076.4756 | -101004.1436 | 68182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | 0 | 0 | 168076.4756 | -101004.1436 | 68182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781 | 268182.0781

## Option3
United Energy
Lower Mornington Peninsula supply area
OPTION 3 | Construct HGS-RBD sub-transmission line and new Shoreham zone substation
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| New 66kV Line |  | 50 | 2023-12-31 | 0 | 0 | 0 | 17167718.5 | 17167718.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New Shoreham ZSS |  | 50 | 2023-12-31 | 0 | 0 | 0 | 11227698.5 | 11227698.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 28395417 | 28395417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  |  | 2.9113 | 4.222 | 5.7763 | 7.0445 | 8.6906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy not Supplied - MEDs |  |  |  | 45.9185 | 46.5613 | 47.2132 | 47.8742 | 48.5444 | 27.0732 | 27.4522 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366
| Energy not Supplied - Non MEDs |  |  |  | 21.535 | 21.8365 | 22.1422 | 22.4522 | 22.7666 | 12.6969 | 12.8747 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549
| Total energy at risk |  |  | MWh | 70.3648 | 72.6198 | 75.1317 | 77.3709 | 80.0015 | 39.7701 | 40.3269 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915 | 40.8915
| Energy at risk value | $/MWh | 35928.5557 | 2023-12-31 | 2528107.3866 | 2609125.4513 | 2699375.1954 | 2779825.5147 | 2874340.1324 | 1428883.2911 | 1448887.6571 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843 | 1469172.0843
| Bushfire risk |  |  | 2023-12-31 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825
| Customer value of network resilience |  |  | 2023-12-31 | 60246.3901 | 61089.8395 | 61945.0973 | 62812.3286 | 63691.7012 | 35520.8618 | 36018.1539 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408
| Cost of events (GSLs, call costs, claims) |  |  | 2023-12-31 | 50000 | 50000 | 50000 | 50000 | 50000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 2643095.2767 | 2724956.7908 | 2816061.7927 | 2897379.3434 | 2992773.3337 | 1467011.9779 | 1487513.636 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173 | 1508302.3173
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38562.334 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex saving |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 900000 | 900000 | 900000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 900000 | 900000 | 900000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 1663125.4326 | 1849085.7383 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594
Capital expenditure
| New 66kV Line |  |  | 2023-12-31 | 0 | 0 | 0 | -17167718.5 | -17167718.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New Shoreham ZSS |  |  | 2023-12-31 | 0 | 0 | 0 | -11227698.5 | -11227698.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| New 66kV Line |  |  | 2023-12-31 | 0 | 0 | 0 | -17167718.5 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437 | -34335437
| New Shoreham ZSS |  |  | 2023-12-31 | 0 | 0 | 0 | -11227698.5 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397 | -22455397
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - New 66kV Line |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -731923.5244 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489 | -1463847.0489
| Annualised capex - New Shoreham ZSS |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -478678.4369 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739 | -957356.8739
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -1210601.9614 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -1210601.9614 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 1663125.4326 | 1849085.7383 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594 | 1866094.6594
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 900000 | 900000 | 900000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000 | 1100000
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | -310601.9614 | 141921.5098 | 327881.8155 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366
| First capex year |  |  | 4
| First year |  |  | 4
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 0 | 0 | 0 | -310601.9614 | 141921.5098 | 327881.8155 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | -1210601.9614 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228 | -2421203.9228
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 900000 | 2563125.4326 | 2749085.7383 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594 | 2966094.6594
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 0 | 0 | 0 | -431662.1575 | -100198.8825 | 85761.4232 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443 | 302770.3443
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 0 | 0 | 0 | -189541.7653 | 384041.9021 | 570002.2078 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289 | 787011.1289
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | 0 | 0 | 0 | -220601.9614 | 398234.0531 | 602790.3893 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025 | 841500.2025
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | 0 | 0 | 0 | -400601.9614 | -114391.0335 | 52973.2417 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707 | 248281.2707
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | 0 | 0 | 0 | -521662.1575 | -356511.4257 | -189147.1506 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784 | 6160.8784
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | -310601.9614 | 141921.5098 | 327881.8155 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | -310601.9614 | 141921.5098 | 327881.8155 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 0 | 0 | -310601.9614 | 141921.5098 | 327881.8155 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366 | 544890.7366

## Option4
United Energy
Lower Mornington Peninsula supply area
OPTION 4 | Expanded non-network solution capability
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| None |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 100000 | 100000 | 200000 | 200000 | 300000 | 300000 | 400000 | 400000 | 500000 | 500000 | 600000 | 600000 | 700000 | 700000 | 800000 | 800000 | 900000 | 900000 | 1000000 | 1000000
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  |  | 2.9113 | 4.222 | 5.7763 | 7.0445 | 8.6906 | 11.4907 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996
| Energy not Supplied - MEDs |  |  |  | 45.9185 | 46.5613 | 47.2132 | 47.8742 | 48.5444 | 49.224 | 49.9132 | 50.612 | 51.3205 | 52.039 | 52.7676 | 53.5063 | 54.2554 | 55.015 | 55.7852 | 56.5662 | 57.3581 | 58.1611 | 58.9754 | 59.801 | 60.6382 | 61.4872 | 62.348 | 63.2209 | 64.106
| Energy not Supplied - Non MEDs |  |  |  | 21.535 | 21.8365 | 22.1422 | 22.4522 | 22.7666 | 23.0853 | 23.4085 | 23.7362 | 24.0685 | 24.4055 | 24.7471 | 25.0936 | 25.4449 | 25.8011 | 26.1624 | 26.5286 | 26.9 | 27.2766 | 27.6585 | 28.0457 | 28.4384 | 28.8365 | 29.2402 | 29.6496 | 30.0647
| Total energy at risk |  |  | MWh | 70.3648 | 72.6198 | 75.1317 | 77.3709 | 80.0015 | 83.8 | 89.5213 | 90.5478 | 91.5887 | 92.6441 | 93.7143 | 94.7995 | 95.8999 | 97.0157 | 98.1472 | 99.2944 | 100.4578 | 101.6374 | 102.8335 | 104.0464 | 105.2762 | 106.5233 | 107.7878 | 109.0701 | 110.3703
| Energy at risk value | $/MWh | 35928.5557 | 2023-12-31 | 2528107.3866 | 2609125.4513 | 2699375.1954 | 2779825.5147 | 2874340.1324 | 3010812.5254 | 3216370.3218 | 3253251.0985 | 3290648.2061 | 3328568.8733 | 3367020.4297 | 3406010.3079 | 3445546.0445 | 3485635.2813 | 3526285.7675 | 3567505.3604 | 3609302.0277 | 3651683.8483 | 3694659.0144 | 3738235.8328 | 3782422.7267 | 3827228.2371 | 3872661.0247 | 3918729.8712 | 3965443.6816
| Bushfire risk |  |  | 2023-12-31 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5
| Customer value of network resilience |  |  | 2023-12-31 | 60246.3901 | 61089.8395 | 61945.0973 | 62812.3286 | 63691.7012 | 64583.3851 | 65487.5525 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782
| Cost of events (GSLs, call costs, claims) |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 2593095.2767 | 2674956.7908 | 2766061.7927 | 2847379.3434 | 2942773.3337 | 3080137.4105 | 3286599.3743 | 3324396.9767 | 3361794.0843 | 3399714.7514 | 3438166.3079 | 3477156.1861 | 3516691.9227 | 3556781.1595 | 3597431.6457 | 3638651.2386 | 3680447.9059 | 3722829.7265 | 3765804.8926 | 3809381.711 | 3853568.6049 | 3898374.1153 | 3943806.9029 | 3989875.7494 | 4036589.5598
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38562.334 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex saving |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 12602.8924 | -25317.7747 | -63769.3312 | -102759.2094 | -142294.9459 | -182384.1828 | -223034.6689 | -264254.2619 | -306050.9292 | -348432.7498 | -391407.9159 | -434984.7343 | -479171.6282 | -523977.1386 | -569409.9261 | -615478.7727 | -662192.5831
Capital expenditure
| None |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| None |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - None |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -100000 | -100000 | -200000 | -200000 | -300000 | -300000 | -400000 | -400000 | -500000 | -500000 | -600000 | -600000 | -700000 | -700000 | -800000 | -800000 | -900000 | -900000 | -1000000 | -1000000
| Risk mitigated |  |  | 2023-12-31 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 12602.8924 | -25317.7747 | -63769.3312 | -102759.2094 | -142294.9459 | -182384.1828 | -223034.6689 | -264254.2619 | -306050.9292 | -348432.7498 | -391407.9159 | -434984.7343 | -479171.6282 | -523977.1386 | -569409.9261 | -615478.7727 | -662192.5831
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 50000 | 50000 | 50000 | 50000 | 50000 | -50000 | -50000 | -150000 | -187397.1076 | -325317.7747 | -363769.3312 | -502759.2094 | -542294.9459 | -682384.1828 | -723034.6689 | -864254.2619 | -906050.9292 | -1048432.7498 | -1091407.9159 | -1234984.7343 | -1279171.6282 | -1423977.1386 | -1469409.9261 | -1615478.7727 | -1662192.5831
| First capex year |  |  | 0
First year
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 50000 | 50000 | 50000 | 50000 | 50000 | -50000 | -50000 | -150000 | -187397.1076 | -325317.7747 | -363769.3312 | -502759.2094 | -542294.9459 | -682384.1828 | -723034.6689 | -864254.2619 | -906050.9292 | -1048432.7498 | -1091407.9159 | -1234984.7343 | -1279171.6282 | -1423977.1386 | -1469409.9261 | -1615478.7727 | -1662192.5831
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 12602.8924 | -25317.7747 | -63769.3312 | -102759.2094 | -142294.9459 | -182384.1828 | -223034.6689 | -264254.2619 | -306050.9292 | -348432.7498 | -391407.9159 | -434984.7343 | -479171.6282 | -523977.1386 | -569409.9261 | -615478.7727 | -662192.5831
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 50000 | 50000 | 50000 | 50000 | 50000 | -50000 | -50000 | -150000 | -187397.1076 | -325317.7747 | -363769.3312 | -502759.2094 | -542294.9459 | -682384.1828 | -723034.6689 | -864254.2619 | -906050.9292 | -1048432.7498 | -1091407.9159 | -1234984.7343 | -1279171.6282 | -1423977.1386 | -1469409.9261 | -1615478.7727 | -1662192.5831
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 50000 | 50000 | 50000 | 50000 | 50000 | -50000 | -50000 | -150000 | -187397.1076 | -325317.7747 | -363769.3312 | -502759.2094 | -542294.9459 | -682384.1828 | -723034.6689 | -864254.2619 | -906050.9292 | -1048432.7498 | -1091407.9159 | -1234984.7343 | -1279171.6282 | -1423977.1386 | -1469409.9261 | -1615478.7727 | -1662192.5831
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 55000 | 55000 | 55000 | 55000 | 55000 | -45000 | -45000 | -145000 | -186136.8184 | -327849.5522 | -370146.2643 | -513035.1303 | -556524.4405 | -700622.601 | -745338.1358 | -890679.6881 | -936656.0221 | -1083276.0248 | -1130548.7075 | -1278483.2077 | -1327088.791 | -1476374.8524 | -1526350.9187 | -1677026.65 | -1728411.8414
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 45000 | 45000 | 45000 | 45000 | 45000 | -55000 | -55000 | -155000 | -188657.3968 | -322785.9972 | -357392.398 | -492483.2885 | -528065.4513 | -664145.7645 | -700731.202 | -837828.8357 | -875445.8362 | -1013589.4748 | -1052267.1243 | -1191486.2609 | -1231254.4654 | -1371579.4247 | -1412468.9335 | -1553930.8954 | -1595973.3248
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 45000 | 45000 | 45000 | 45000 | 45000 | -55000 | -55000 | -155000 | -188657.3968 | -322785.9972 | -357392.398 | -492483.2885 | -528065.4513 | -664145.7645 | -700731.202 | -837828.8357 | -875445.8362 | -1013589.4748 | -1052267.1243 | -1191486.2609 | -1231254.4654 | -1371579.4247 | -1412468.9335 | -1553930.8954 | -1595973.3248
sens | 0 | 0% | 0% | Option 4sens | 50000 | 50000 | 50000 | 50000 | 50000 | -50000 | -50000 | -150000 | -187397.1076 | -325317.7747 | -363769.3312 | -502759.2094 | -542294.9459 | -682384.1828 | -723034.6689 | -864254.2619 | -906050.9292 | -1048432.7498 | -1091407.9159 | -1234984.7343 | -1279171.6282 | -1423977.1386 | -1469409.9261 | -1615478.7727 | -1662192.5831
sens | 0 | 0% | 0% | Option 4sens | 50000 | 50000 | 50000 | 50000 | 50000 | -50000 | -50000 | -150000 | -187397.1076 | -325317.7747 | -363769.3312 | -502759.2094 | -542294.9459 | -682384.1828 | -723034.6689 | -864254.2619 | -906050.9292 | -1048432.7498 | -1091407.9159 | -1234984.7343 | -1279171.6282 | -1423977.1386 | -1469409.9261 | -1615478.7727 | -1662192.5831
sens | 0 | 0% | 0% | Option 4sens | 50000 | 50000 | 50000 | 50000 | 50000 | -50000 | -50000 | -150000 | -187397.1076 | -325317.7747 | -363769.3312 | -502759.2094 | -542294.9459 | -682384.1828 | -723034.6689 | -864254.2619 | -906050.9292 | -1048432.7498 | -1091407.9159 | -1234984.7343 | -1279171.6282 | -1423977.1386 | -1469409.9261 | -1615478.7727 | -1662192.5831

## Option5
United Energy
Lower Mornington Peninsula supply area
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy at risk (weighted)
Energy not Supplied - MEDs
Energy not Supplied - Non MEDs
| Total energy at risk |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 35928.5557 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental network resilience value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bushfire risk |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of network resilience |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38562.334 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
United Energy
Lower Mornington Peninsula supply area
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 57583875.3998 | 2026-06-30 |  | 2813562.682 | 2903728.7108 | 3004168.7924 | 3093702.9702 | 3198889.4835 | 3350771.3355 | 3579539.2067 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895 | 3620584.2895
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 56529110.8918 | 2026-06-30 |  | 2941534.1591 | 3032638.8734 | 3134030.7821 | 3224530.1127 | 3330695.2909 | 3483569.5091 | 3713343.6397 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694 | 3755409.0694
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 49853979.37 | 2026-06-30 |  | 2813562.682 | 2903728.7108 | 3004168.7924 | 3093702.9702 | 3198889.4835 | 2891313.2452 | 2931791.6307 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135 | 2972836.7135
Option 2 | Capital expenditure | Option 2Capital expenditure | -33304774.7318 | 2026-06-30 |  | 0 | 0 | 0 | -19106171.0288 | -19106171.0288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 48737984.0906 | 2026-06-30 |  | 2941534.1591 | 3032638.8734 | 3134030.7821 | 3224530.1127 | 3330695.2909 | 2968465.7865 | 3009950.4313 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 3052015.8611 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -19103746.9257 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -814566.9466 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | -1629133.8931 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 7791126.8012 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 515103.7226 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 703393.2084 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 14326867.2829 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 1001621.3818 | 1001621.3818 | 1001621.3818 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 187054.4352 | -112408.7888 | 75880.697 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 0 | 0
Option 2 | NPV | Option 2NPV | 3014247.1584 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -19103746.9257 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 22117994.0841 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 33612919.4259 | 2026-06-30 |  | 2813562.682 | 2903728.7108 | 3004168.7924 | 3093702.9702 | 3198889.4835 | 1590222.2849 | 1612485.3969 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924 | 1635060.1924
Option 3 | Capital expenditure | Option 3Capital expenditure | -55086117.972 | 2026-06-30 |  | 0 | 0 | 0 | -31601618.6796 | -31601618.6796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 33267441.1622 | 2026-06-30 |  | 2941534.1591 | 3032638.8734 | 3134030.7821 | 3224530.1127 | 3330695.2909 | 1632656.1826 | 1655472.7372 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 1678608.7236 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -31597609.2116 | 2026-06-30 |  | 0 | 0 | 0 | 0 | -1347294.2326 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | -2694588.4652 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 23261669.7297 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 1850913.3265 | 2057870.9024 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 2076800.3458 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 14326867.2829 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 1001621.3818 | 1001621.3818 | 1001621.3818 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 1224203.9111 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | -345672.8508 | 157946.2431 | 364903.819 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 0 | 0
Option 3 | NPV | Option 3NPV | 5990927.8009 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -31597609.2116 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 37588537.0126 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 61157867.4845 | 2026-06-30 |  | 2813562.682 | 2903728.7108 | 3004168.7924 | 3093702.9702 | 3198889.4835 | 3350771.3355 | 3579539.2067 | 3620584.2895 | 3662204.0035 | 3704406.3935 | 3747199.617 | 3790591.9455 | 3834591.7667 | 3879207.5854 | 3924448.0255 | 3970321.8318 | 4016837.8714 | 4064005.1355 | 4111832.7413 | 4160329.9337 | 4209506.0867 | 4259370.7058 | 4309933.4296 | 4361204.0316 | 4413192.422
Option 4 | Capital expenditure | Option 4Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 58547619.2778 | 2026-06-30 |  | 2885888.5268 | 2976993.2411 | 3078385.1498 | 3168884.4804 | 3275049.6586 | 3427923.8768 | 3657698.0073 | 3699763.4371 | 3741383.1511 | 3783585.5411 | 3826378.7645 | 3869771.0931 | 3913770.9143 | 3958386.733 | 4003627.1731 | 4049500.9794 | 4096017.019 | 4143184.2831 | 4191011.8889 | 4239509.0812 | 4288685.2342 | 4338549.8534 | 4389112.5772 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | -5713819.4147 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | -111291.2646 | -111291.2646 | -222582.5293 | -222582.5293 | -333873.7939 | -333873.7939 | -445165.0586 | -445165.0586 | -556456.3232 | -556456.3232 | -667747.5878 | -667747.5878 | -779038.8525 | -779038.8525 | -890330.1171 | -890330.1171 | -1001621.3818 | -1001621.3818 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | -2018508.3859 | 2026-06-30 |  | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 14025.9183 | -28176.4717 | -70969.6951 | -114362.0237 | -158361.8448 | -202977.6635 | -248218.1036 | -294091.9099 | -340607.9495 | -387775.2137 | -435602.8195 | -484100.0118 | -533276.1648 | -583140.784 | -633703.5078 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | -55645.6323 | -55645.6323 | -166936.897 | -208556.611 | -362050.2656 | -404843.489 | -559527.0822 | -603526.9034 | -759433.9867 | -804674.4269 | -961839.4978 | -1008355.5374 | -1166814.0661 | -1214641.672 | -1374430.1289 | -1423606.2819 | -1584762.1657 | -1635324.8895 | 0 | 0
Option 4 | NPV | Option 4NPV | -7732327.8006 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | -5713819.4147 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | -2018508.3859 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 3 | Annualised capex | -1 |  |  | Option 3 annualised capex | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 2.6946 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 2.9415 | 3.0326 | 3.134 | 3.2245 | 3.3307 | 3.4836 | 3.7133 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554 | 3.7554
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 16.1996 |  |  | Energy at risk energy at risk (weighted) | 2.9113 | 4.222 | 5.7763 | 7.0445 | 8.6906 | 11.4907 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996
Option 1 (base case) | Energy at risk value | 3.2533 |  |  | Option 1 (base case) risk cost | 2.5281 | 2.6091 | 2.6994 | 2.7798 | 2.8743 | 3.0108 | 3.2164 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533 | 3.2533

## Sensitivity_calcs
United Energy
Lower Mornington Peninsula supply area
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 3014247.1584 |  | 0 | 0 | 0 | 0 | 0 | 187054.4352 | -112408.7888 | 75880.697 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 1103872.4658 |  | 0 | 0 | 0 | 0 | 0 | 105597.7405 | -275322.1781 | -87032.6923 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 135549.837 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 4924621.851 |  | 0 | 0 | 0 | 0 | 0 | 268511.1299 | 50504.6005 | 238794.0863 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 461376.6156 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 5226046.5668 |  | 0 | 0 | 0 | 0 | 0 | 287216.5734 | 39263.7216 | 246382.156 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 491222.9382 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 802447.75 |  | 0 | 0 | 0 | 0 | 0 | 86892.297 | -264081.2992 | -94620.762 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 105703.5143 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | -1107926.9426 |  | 0 | 0 | 0 | 0 | 0 | 5435.6024 | -426994.6885 | -257534.1513 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | -57209.875 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 3014247.1584 |  | 0 | 0 | 0 | 0 | 0 | 187054.4352 | -112408.7888 | 75880.697 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 3014247.1584 |  | 0 | 0 | 0 | 0 | 0 | 187054.4352 | -112408.7888 | 75880.697 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 3014247.1584 |  | 0 | 0 | 0 | 0 | 0 | 187054.4352 | -112408.7888 | 75880.697 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 298463.2263 | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | -345672.8508 | 157946.2431 | 364903.819 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 5990927.8009 |  | 0 | 0 | 0 | 0 | 0 | -345672.8508 | 157946.2431 | 364903.819 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 2831166.8798 |  | 0 | 0 | 0 | 0 | 0 | -480402.2741 | -111512.6035 | 95444.9725 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 336956.9451 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 9150688.7221 |  | 0 | 0 | 0 | 0 | 0 | -210943.4276 | 427405.0896 | 634362.6655 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 875874.6382 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 9749781.5022 |  | 0 | 0 | 0 | 0 | 0 | -245510.7127 | 443199.7139 | 670853.0474 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 936516.2174 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 2232074.0997 |  | 0 | 0 | 0 | 0 | 0 | -445834.989 | -127307.2278 | 58954.5906 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 276315.366 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | -927686.8215 |  | 0 | 0 | 0 | 0 | 0 | -580564.4123 | -396766.0743 | -210504.256 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 6856.5195 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 5990927.8009 |  | 0 | 0 | 0 | 0 | 0 | -345672.8508 | 157946.2431 | 364903.819 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 5990927.8009 |  | 0 | 0 | 0 | 0 | 0 | -345672.8508 | 157946.2431 | 364903.819 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 5990927.8009 |  | 0 | 0 | 0 | 0 | 0 | -345672.8508 | 157946.2431 | 364903.819 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 606415.7917 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | -7732327.8006 |  | 0 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | -55645.6323 | -55645.6323 | -166936.897 | -208556.611 | -362050.2656 | -404843.489 | -559527.0822 | -603526.9034 | -759433.9867 | -804674.4269 | -961839.4978 | -1008355.5374 | -1166814.0661 | -1214641.672 | -1374430.1289 | -1423606.2819 | -1584762.1657 | -1635324.8895 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | -7732327.8006 |  | 0 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | -55645.6323 | -55645.6323 | -166936.897 | -208556.611 | -362050.2656 | -404843.489 | -559527.0822 | -603526.9034 | -759433.9867 | -804674.4269 | -961839.4978 | -1008355.5374 | -1166814.0661 | -1214641.672 | -1374430.1289 | -1423606.2819 | -1584762.1657 | -1635324.8895 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | -7732327.8006 |  | 0 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | -55645.6323 | -55645.6323 | -166936.897 | -208556.611 | -362050.2656 | -404843.489 | -559527.0822 | -603526.9034 | -759433.9867 | -804674.4269 | -961839.4978 | -1008355.5374 | -1166814.0661 | -1214641.672 | -1374430.1289 | -1423606.2819 | -1584762.1657 | -1635324.8895 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | -7934178.6392 |  | 0 | 61210.1956 | 61210.1956 | 61210.1956 | 61210.1956 | 61210.1956 | -50081.0691 | -50081.0691 | -161372.3337 | -207154.0191 | -364867.9127 | -411940.4585 | -570963.2846 | -619363.0879 | -779731.7531 | -829496.2372 | -991248.6888 | -1042416.3323 | -1205591.5875 | -1258201.9539 | -1422840.1301 | -1476933.8984 | -1643076.2441 | -1698695.2403 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | -7530476.962 |  | 0 | 50081.0691 | 50081.0691 | 50081.0691 | 50081.0691 | 50081.0691 | -61210.1956 | -61210.1956 | -172501.4602 | -209959.2028 | -359232.6184 | -397746.5195 | -548090.8799 | -587690.7189 | -739136.2204 | -779852.6165 | -932430.3068 | -974294.7424 | -1128036.5448 | -1171081.39 | -1326020.1278 | -1370278.6655 | -1526448.0873 | -1571954.5388 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | -7530476.962 |  | 0 | 50081.0691 | 50081.0691 | 50081.0691 | 50081.0691 | 50081.0691 | -61210.1956 | -61210.1956 | -172501.4602 | -209959.2028 | -359232.6184 | -397746.5195 | -548090.8799 | -587690.7189 | -739136.2204 | -779852.6165 | -932430.3068 | -974294.7424 | -1128036.5448 | -1171081.39 | -1326020.1278 | -1370278.6655 | -1526448.0873 | -1571954.5388 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -7732327.8006 |  | 0 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | -55645.6323 | -55645.6323 | -166936.897 | -208556.611 | -362050.2656 | -404843.489 | -559527.0822 | -603526.9034 | -759433.9867 | -804674.4269 | -961839.4978 | -1008355.5374 | -1166814.0661 | -1214641.672 | -1374430.1289 | -1423606.2819 | -1584762.1657 | -1635324.8895 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -7732327.8006 |  | 0 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | -55645.6323 | -55645.6323 | -166936.897 | -208556.611 | -362050.2656 | -404843.489 | -559527.0822 | -603526.9034 | -759433.9867 | -804674.4269 | -961839.4978 | -1008355.5374 | -1166814.0661 | -1214641.672 | -1374430.1289 | -1423606.2819 | -1584762.1657 | -1635324.8895 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | -7732327.8006 |  | 0 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | -55645.6323 | -55645.6323 | -166936.897 | -208556.611 | -362050.2656 | -404843.489 | -559527.0822 | -603526.9034 | -759433.9867 | -804674.4269 | -961839.4978 | -1008355.5374 | -1166814.0661 | -1214641.672 | -1374430.1289 | -1423606.2819 | -1584762.1657 | -1635324.8895 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 0 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 3.0142 | 5.9909 | -7.7323 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens1 | Capex 10% higher | 0 | 1.1039 | 2.8312 | -7.7323 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens2 | Capex 10% lower | 0 | 4.9246 | 9.1507 | -7.7323 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens3 | Total benefits 10% higher | 0 | 5.226 | 9.7498 | -7.9342 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens4 | Total benefits 10% lower | 0 | 0.80245 | 2.2321 | -7.5305 |  |  | 2026-27: #NAME?; 2028-29: Option 3
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | -1.1079 | -0.92769 | -7.5305 |  |  | 2026-27: #NAME?; 2028-29: Option 1 (base case)
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Risks_Shoreham
United Energy
Lower Mornington Peninsula supply area
RISKS - SHOREHAM
SUMMARY | [8 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
|  | Energy not Supplied - MEDs |  |  |  |  | MWh |  | 45.9185 | 46.5613 | 47.2132 | 47.8742 | 48.5444 | 49.224 | 49.9132 | 50.612 | 51.3205 | 52.039 | 52.7676 | 53.5063 | 54.2554 | 55.015 | 55.7852 | 56.5662 | 57.3581 | 58.1611 | 58.9754 | 59.801 | 60.6382 | 61.4872 | 62.348 | 63.2209 | 64.106
|  | Energy not Supplied - Non MEDs |  |  |  |  | MWh |  | 21.535 | 21.8365 | 22.1422 | 22.4522 | 22.7666 | 23.0853 | 23.4085 | 23.7362 | 24.0685 | 24.4055 | 24.7471 | 25.0936 | 25.4449 | 25.8011 | 26.1624 | 26.5286 | 26.9 | 27.2766 | 27.6585 | 28.0457 | 28.4384 | 28.8365 | 29.2402 | 29.6496 | 30.0647
|  | Bushfire risk | (after DF) |  |  |  | 2023-12-31 |  | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5
|  | Customer value of network resilience | $/MWh | 35928.5557 |  |  | 2023-12-31 |  | 60246.3901 | 61089.8395 | 61945.0973 | 62812.3286 | 63691.7012 | 64583.3851 | 65487.5525 | 66404.3782 | 67334.0395 | 68276.716 | 69232.5901 | 70201.8463 | 71184.6722 | 72181.2576 | 73191.7952 | 74216.4803 | 75255.511 | 76309.0882 | 77377.4154 | 78460.6993 | 79559.149 | 80672.9771 | 81802.3988 | 82947.6324 | 84108.8992
Option 1 (base case)
Flat from FY34
|  | Energy not Supplied - MEDs |  | Option 1 (base case)Energy not Supplied - MEDs |  |  | MWh |  | 45.9185 | 46.5613 | 47.2132 | 47.8742 | 48.5444 | 49.224 | 49.9132 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612
|  | Energy not Supplied - Non MEDs |  | Option 1 (base case)Energy not Supplied - Non MEDs |  |  | MWh |  | 21.535 | 21.8365 | 22.1422 | 22.4522 | 22.7666 | 23.0853 | 23.4085 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362
Option 1 (base case)
|  | Bushfire risk |  | Option 1 (base case)Bushfire risk |  |  | 2023-12-31 |  | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5
|  | Customer value of network resilience |  | Option 1 (base case)Customer value of network resilience |  |  | 2023-12-31 |  | 60246.3901 | 61089.8395 | 61945.0973 | 62812.3286 | 63691.7012 | 64583.3851 | 65487.5525 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782
Option 2
|  | % of base case | [6 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | Energy not Supplied - MEDs |  | Option 2Energy not Supplied - MEDs |  |  | MWh |  | 45.9185 | 46.5613 | 47.2132 | 47.8742 | 48.5444 | 49.224 | 49.9132 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612 | 50.612
|  | Energy not Supplied - Non MEDs |  | Option 2Energy not Supplied - Non MEDs |  |  | MWh |  | 21.535 | 21.8365 | 22.1422 | 22.4522 | 22.7666 | 23.0853 | 23.4085 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362 | 23.7362
Option 2
|  | Bushfire risk |  | Option 2Bushfire risk |  |  | 2023-12-31 |  | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5
|  | Customer value of network resilience |  | Option 2Customer value of network resilience |  |  | 2023-12-31 |  | 60246.3901 | 61089.8395 | 61945.0973 | 62812.3286 | 63691.7012 | 64583.3851 | 65487.5525 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782
Option 3
|  | % of base case | [6 empty] | 100% | 100% | 100% | 100% | 100% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55% | 55%
|  | Energy not Supplied - MEDs |  | Option 3Energy not Supplied - MEDs |  |  | MWh |  | 45.9185 | 46.5613 | 47.2132 | 47.8742 | 48.5444 | 27.0732 | 27.4522 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366 | 27.8366
|  | Energy not Supplied - Non MEDs |  | Option 3Energy not Supplied - Non MEDs |  |  | MWh |  | 21.535 | 21.8365 | 22.1422 | 22.4522 | 22.7666 | 12.6969 | 12.8747 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549 | 13.0549
Option 3
|  | Bushfire risk |  | Option 3Bushfire risk |  |  | 2023-12-31 |  | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825 | 2607.825
|  | Customer value of network resilience |  | Option 3Customer value of network resilience |  |  | 2023-12-31 |  | 60246.3901 | 61089.8395 | 61945.0973 | 62812.3286 | 63691.7012 | 35520.8618 | 36018.1539 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408 | 36522.408
Option 4
|  | Energy not Supplied - MEDs |  | Option 4Energy not Supplied - MEDs |  |  | MWh |  | 45.9185 | 46.5613 | 47.2132 | 47.8742 | 48.5444 | 49.224 | 49.9132 | 50.612 | 51.3205 | 52.039 | 52.7676 | 53.5063 | 54.2554 | 55.015 | 55.7852 | 56.5662 | 57.3581 | 58.1611 | 58.9754 | 59.801 | 60.6382 | 61.4872 | 62.348 | 63.2209 | 64.106
|  | Energy not Supplied - Non MEDs |  | Option 4Energy not Supplied - Non MEDs |  |  | MWh |  | 21.535 | 21.8365 | 22.1422 | 22.4522 | 22.7666 | 23.0853 | 23.4085 | 23.7362 | 24.0685 | 24.4055 | 24.7471 | 25.0936 | 25.4449 | 25.8011 | 26.1624 | 26.5286 | 26.9 | 27.2766 | 27.6585 | 28.0457 | 28.4384 | 28.8365 | 29.2402 | 29.6496 | 30.0647
Option 4
|  | Bushfire risk |  | Option 4Bushfire risk |  |  | 2023-12-31 |  | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5
|  | Customer value of network resilience |  | Option 4Customer value of network resilience |  |  | 2023-12-31 |  | 60246.3901 | 61089.8395 | 61945.0973 | 62812.3286 | 63691.7012 | 64583.3851 | 65487.5525 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782 | 66404.3782
average
WORKINGS | [6 empty] | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Inputs and assumptions
|  | Customer no. |  |  | 709122
|  | Growth Rate |  |  | 1.4%
|  | Percentage of LV and services outages |  |  | 75%
|  | Improvement in HV outages |  |  | 0%
|  | Reduction in fire starts due to REFCL |  |  | 100%
|  | CPI |  |  | 2.5%
[6 empty] | DMA15 | 2015: DMA23; 2016: MTN32; 2017: RBD21
|  | Consumption by zone sub |  |  | 2022 | 119345.4558 | 2015: 112566.8762; 2016: 220770.1494; 2017: 136260.4812
|  | Customers at zone substation (as per RIN) |  |  | 2022 | 17086 | 2015: 17086; 2016: 24561; 2017: 19923
|  | Customers on DMA23 (as per RIN) |  |  | 2022 | 1066 | 2015: 1838; 2016: 2872; 2017: 2135
|  | Consumption on DMA23 |  |  | 2022 | 7445.9941 | 2015: 12109.2075; 2016: 25815.3931; 2017: 14602.0242
|  | Consumption per customer on DMA23 pa |  |  | 2022 | 6.985 | 2015: 6.5883; 2016: 8.9886; 2017: 6.8394
|  | Consumption per customer on DMA23 per hour |  |  | 2022 | 0.00079737 | 2015: 0.00075208; 2016: 0.0010261; 2017: 0.00078075
Reliability
DMA15
DMA15 |  | Feeder CMOS |  |  |  |  | average 2025: 285525.8623
DMA15
DMA15 | [6 empty] | 2022: 0.00079737
DMA15 |  | Energy at risk |  |  |  |  | MWh | [6 empty] | 3.7945 | 3.8476 | 3.9015 | 3.9561 | 4.0115 | 4.0677 | 4.1246 | 4.1824 | 4.2409 | 4.3003 | 4.3605 | 4.4215 | 4.4834 | 4.5462 | 4.6099 | 4.6744 | 4.7398 | 4.8062 | 4.8735 | 4.9417 | 5.0109 | 5.081 | 5.1522 | 5.2243 | 5.2974 | 5.3716 | 5.4468 | 5.5231 | 5.6004 | 5.6788 | 5.7583
DMA23
DMA23 |  | Feeder CMOS |  |  |  |  | average 2025: 535316.2657
DMA23
DMA23 |  | Consumption per customer on DMA23 per hour |  |  |  |  | 2022: 0.00075208
DMA23 |  | DMA Energy at risk |  |  |  |  | MWh | [6 empty] | 6.71 | 6.804 | 6.8992 | 6.9958 | 7.0938 | 7.1931 | 7.2938 | 7.3959 | 7.4994 | 7.6044 | 7.7109 | 7.8188 | 7.9283 | 8.0393 | 8.1519 | 8.266 | 8.3817 | 8.4991 | 8.618 | 8.7387 | 8.861 | 8.9851 | 9.1109 | 9.2384 | 9.3678 | 9.4989 | 9.6319 | 9.7668 | 9.9035 | 10.0421 | 10.1827
MTN32
MTN32 |  | Feeder CMOS |  |  |  |  | average 2025: 431473.9181
MTN32
MTN32 |  | Consumption per customer on MTN32 per hour |  |  |  |  | 2022: 0.0010261
MTN32 |  | MTN Energy at risk | [11 empty] | 7.3789 | 7.4822 | 7.587 | 7.6932 | 7.8009 | 7.9101 | 8.0209 | 8.1332 | 8.247 | 8.3625 | 8.4796 | 8.5983 | 8.7186 | 8.8407 | 8.9645 | 9.09 | 9.2172 | 9.3463 | 9.4771 | 9.6098 | 9.7443 | 9.8808 | 10.0191 | 10.1594 | 10.3016 | 10.4458 | 10.5921 | 10.7403 | 10.8907 | 11.0432 | 11.1978
RBD21
RBD21 |  | Feeder CMOS |  |  |  |  | average 2025: 180214.8544
RBD21
RBD21 |  | Consumption per customer on RBD21 per hour |  |  |  |  | 2022: 0.00078075
RBD21 |  | RBD Energy at risk | [11 empty] | 2.345 | 2.3779 | 2.4112 | 2.4449 | 2.4791 | 2.5139 | 2.549 | 2.5847 | 2.6209 | 2.6576 | 2.6948 | 2.7325 | 2.7708 | 2.8096 | 2.8489 | 2.8888 | 2.9293 | 2.9703 | 3.0119 | 3.054 | 3.0968 | 3.1401 | 3.1841 | 3.2287 | 3.2739 | 3.3197 | 3.3662 | 3.4133 | 3.4611 | 3.5095 | 3.5587
TOTAL
|  | Energy at risk | [14 empty] | 21.0901 | 21.3853 | 21.6847 | 21.9883 | 22.2962 | 22.6083 | 22.9248 | 23.2458 | 23.5712 | 23.9012 | 24.2358 | 24.5751 | 24.9192 | 25.268 | 25.6218 | 25.9805 | 26.3442 | 26.713 | 27.087 | 27.4662 | 27.8508 | 28.2407 | 28.636 | 29.037 | 29.4435 | 29.8557 | 30.2737 | 30.6975
Improvement in HV outages | bar: average 2025 to average 2052
|  | Total Energy at Risk | [14 empty] | 21.0901 | 21.3853 | 21.6847 | 21.9883 | 22.2962 | 22.6083 | 22.9248 | 23.2458 | 23.5712 | 23.9012 | 24.2358 | 24.5751 | 24.9192 | 25.268 | 25.6218 | 25.9805 | 26.3442 | 26.713 | 27.087 | 27.4662 | 27.8508 | 28.2407 | 28.636 | 29.037 | 29.4435 | 29.8557 | 30.2737 | 30.6975
Reliability MED impact less than 12hrs (less resilience) (HV Only)
DMA15
DMA15 |  | Minutes below 12 hours CMOS |  |  |  |  | 2015: 495.58; 2016: 0; 2017: 0; 2018: 288216.9; 2019: 0; 2020: 0; 2021: 6208024.89; 2022: 0; 2023: 0; average 2025: 721859.7078
DMA15
DMA15 |  | Consumption per customer on DMA15 per hour |  |  |  |  | 2022: 0.00079737
DMA15 |  | DMA Energy at risk | [11 empty] | 9.5932 | 9.7275 | 9.8637 | 10.0018 | 10.1418 | 10.2838 | 10.4278 | 10.5737 | 10.7218 | 10.8719 | 11.0241 | 11.1784 | 11.3349 | 11.4936 | 11.6545 | 11.8177 | 11.9831 | 12.1509 | 12.321 | 12.4935 | 12.6684 | 12.8458 | 13.0256 | 13.208 | 13.3929 | 13.5804 | 13.7705 | 13.9633 | 14.1588 | 14.357 | 14.558
DMA23
DMA23 |  | Minutes below 12 hours CMOS |  |  |  |  | 2015: 0; 2016: 0; 2017: 0; 2018: 2846; 2019: 0; 2020: 0; 2021: 4824779.43; 2022: 0; 2023: 0; average 2025: 536402.8256
DMA23
DMA23 |  | Consumption per customer on DMA23 per hour |  |  |  |  | 2022: 0.00075208
DMA23 |  | DMA Energy at risk | [11 empty] | 6.7237 | 6.8178 | 6.9132 | 7.01 | 7.1082 | 7.2077 | 7.3086 | 7.4109 | 7.5147 | 7.6199 | 7.7265 | 7.8347 | 7.9444 | 8.0556 | 8.1684 | 8.2828 | 8.3987 | 8.5163 | 8.6355 | 8.7564 | 8.879 | 9.0033 | 9.1294 | 9.2572 | 9.3868 | 9.5182 | 9.6515 | 9.7866 | 9.9236 | 10.0625 | 10.2034
MTN32
MTN32 |  | Minutes below 12 hours CMOS |  |  |  |  | 2015: 592233.86; 2016: 0; 2017: 0; 2018: 0; 2019: 0; 2020: 471432.52; 2021: 11925018.5; 2022: 0; 2023: 0; average 2025: 1443187.2089
MTN32
MTN32 |  | Consumption per customer on MTN32 per hour |  |  |  |  | 2022: 0.0010261
MTN32 |  | MTN Energy at risk | [11 empty] | 24.6809 | 25.0265 | 25.3768 | 25.7321 | 26.0924 | 26.4577 | 26.8281 | 27.2037 | 27.5845 | 27.9707 | 28.3623 | 28.7594 | 29.162 | 29.5703 | 29.9842 | 30.404 | 30.8297 | 31.2613 | 31.6989 | 32.1427 | 32.5927 | 33.049 | 33.5117 | 33.9809 | 34.4566 | 34.939 | 35.4281 | 35.9241 | 36.4271 | 36.9371 | 37.4542
RBD21
RBD21 |  | Minutes below 12 hours CMOS |  |  |  |  | 2015: 0; 2016: 0; 2017: 0; 2018: 0; 2019: 0; 2021: 476422.85; 2022: 0; 2023: 0; average 2025: 59552.8562
RBD21
RBD21 |  | Consumption per customer on RBD21 per hour |  |  |  |  | 2022: 0.00078075
RBD21 |  | RBD Energy at risk | [11 empty] | 0.77493 | 0.78578 | 0.79678 | 0.80793 | 0.81925 | 0.83072 | 0.84235 | 0.85414 | 0.8661 | 0.87822 | 0.89052 | 0.90298 | 0.91563 | 0.92844 | 0.94144 | 0.95462 | 0.96799 | 0.98154 | 0.99528 | 1.0092 | 1.0233 | 1.0377 | 1.0522 | 1.0669 | 1.0819 | 1.097 | 1.1124 | 1.1279 | 1.1437 | 1.1597 | 1.176
TOTAL
|  | Energy at risk | [14 empty] | 43.5518 | 44.1616 | 44.7798 | 45.4068 | 46.0424 | 46.687 | 47.3407 | 48.0034 | 48.6755 | 49.3569 | 50.0479 | 50.7486 | 51.4591 | 52.1795 | 52.91 | 53.6508 | 54.4019 | 55.1635 | 55.9358 | 56.7189 | 57.513 | 58.3181 | 59.1346 | 59.9625 | 60.8019 | 61.6532 | 62.5163 | 63.3915
Improvement in HV outages | bar: average 2025 to average 2052
|  | Total Energy at Risk | [14 empty] | 43.5518 | 44.1616 | 44.7798 | 45.4068 | 46.0424 | 46.687 | 47.3407 | 48.0034 | 48.6755 | 49.3569 | 50.0479 | 50.7486 | 51.4591 | 52.1795 | 52.91 | 53.6508 | 54.4019 | 55.1635 | 55.9358 | 56.7189 | 57.513 | 58.3181 | 59.1346 | 59.9625 | 60.8019 | 61.6532 | 62.5163 | 63.3915
Resilience greater than 12hrs (incremental)
DMA15
DMA15 |  | Minutes above 12 hours CMOS |  |  |  |  | 2015: 457.5667; 2016: 1509.85; 2017: 37; 2018: 2080.6333; 2019: 142369.4; 2021: 32416.1667; 2022: 35591.35; 2023: 0; average 2025: 26807.7458
DMA15
DMA15 |  | Consumption per customer on DMA15 per hour |  |  |  |  | 2022: 0.00079737
DMA15 |  | DMA Energy at risk | [11 empty] | 0.35626 | 0.36125 | 0.36631 | 0.37144 | 0.37664 | 0.38191 | 0.38726 | 0.39268 | 0.39818 | 0.40375 | 0.4094 | 0.41513 | 0.42095 | 0.42684 | 0.43281 | 0.43887 | 0.44502 | 0.45125 | 0.45757 | 0.46397 | 0.47047 | 0.47705 | 0.48373 | 0.4905 | 0.49737 | 0.50434 | 0.5114 | 0.51856 | 0.52582 | 0.53318 | 0.54064
DMA23
DMA23 |  | Minutes above 12 hours CMOS |  |  |  |  | 2015: 0; 2016: 2048.2667; 2017: 0; 2018: 15064.7667; 2019: 68622.85; 2021: 21332.95; 2022: 383.3; 2023: 0; average 2025: 15350.3048
DMA23
DMA23 |  | Consumption per customer on DMA23 per hour |  |  |  |  | 2022: 0.00075208
DMA23 |  | DMA Energy at risk | [11 empty] | 0.19241 | 0.19511 | 0.19784 | 0.20061 | 0.20342 | 0.20626 | 0.20915 | 0.21208 | 0.21505 | 0.21806 | 0.22111 | 0.22421 | 0.22735 | 0.23053 | 0.23376 | 0.23703 | 0.24035 | 0.24371 | 0.24712 | 0.25058 | 0.25409 | 0.25765 | 0.26126 | 0.26491 | 0.26862 | 0.27238 | 0.2762 | 0.28006 | 0.28398 | 0.28796 | 0.29199
MTN32
MTN32 |  | Minutes above 12 hours CMOS |  |  |  |  | 2015: 6326.95; 2016: 2643.9167; 2017: 0; 2018: 85359.0833; 2019: 2340; 2021: 7841.3333; 2022: 102.6167; 2023: 959.6; average 2025: 14944.8429
MTN32
MTN32 |  | Consumption per customer on MTN32 per hour |  |  |  |  | 2022: 0.0010261
MTN32 |  | MTN Energy at risk | [11 empty] | 0.25558 | 0.25916 | 0.26279 | 0.26647 | 0.2702 | 0.27398 | 0.27782 | 0.28171 | 0.28565 | 0.28965 | 0.2937 | 0.29782 | 0.30199 | 0.30621 | 0.3105 | 0.31485 | 0.31925 | 0.32372 | 0.32826 | 0.33285 | 0.33751 | 0.34224 | 0.34703 | 0.35189 | 0.35681 | 0.36181 | 0.36687 | 0.37201 | 0.37722 | 0.3825 | 0.38785
RBD21
RBD21 |  | Minutes above 12 hours CMOS |  |  |  |  | 2015: 10241.9333; 2016: 1460.75; 2017: 0; 2018: 4185.3; 2019: 0; 2021: 12593.1833; 2022: 1869.0333; 2023: 0; average 2025: 4335.7429
RBD21
RBD21 |  | Consumption per customer on RBD21 per hour |  |  |  |  | 2022: 0.00078075
RBD21 |  | RBD Energy at risk | [11 empty] | 0.056419 | 0.057209 | 0.05801 | 0.058822 | 0.059645 | 0.06048 | 0.061327 | 0.062185 | 0.063056 | 0.063939 | 0.064834 | 0.065742 | 0.066662 | 0.067595 | 0.068542 | 0.069501 | 0.070474 | 0.071461 | 0.072461 | 0.073476 | 0.074504 | 0.075548 | 0.076605 | 0.077678 | 0.078765 | 0.079868 | 0.080986 | 0.08212 | 0.08327 | 0.084435 | 0.085617
TOTAL
|  | Energy at risk | [14 empty] | 0.89733 | 0.90989 | 0.92263 | 0.93555 | 0.94865 | 0.96193 | 0.9754 | 0.98905 | 1.0029 | 1.0169 | 1.0312 | 1.0456 | 1.0603 | 1.0751 | 1.0901 | 1.1054 | 1.1209 | 1.1366 | 1.1525 | 1.1686 | 1.185 | 1.2016 | 1.2184 | 1.2355 | 1.2527 | 1.2703 | 1.2881 | 1.3061
|  | Percentage of LV and services outages | [14 empty] | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75%
Improvement in HV outages | bar: average 2025 to average 2052
|  | Total Energy at Risk | [14 empty] | 0.22433 | 0.22747 | 0.23066 | 0.23389 | 0.23716 | 0.24048 | 0.24385 | 0.24726 | 0.25072 | 0.25423 | 0.25779 | 0.2614 | 0.26506 | 0.26877 | 0.27254 | 0.27635 | 0.28022 | 0.28414 | 0.28812 | 0.29216 | 0.29625 | 0.30039 | 0.3046 | 0.30886 | 0.31319 | 0.31757 | 0.32202 | 0.32653
Resilience MED impact less than 12hrs
DMA15
DMA15 |  | Minutes below 12 hours CMOS |  |  |  |  | 2015: 720; 2016: 2160; 2017: 720; 2018: 738720; 2019: 90720; 2021: 8640; 2022: 105840; 2023: 0; average 2025: 118440
DMA15
DMA15 |  | Consumption per customer on DMA15 per hour |  |  |  |  | 2022: 0.00079737
DMA15 |  | DMA Energy at risk | [11 empty] | 1.574 | 1.596 | 1.6184 | 1.6411 | 1.664 | 1.6873 | 1.7109 | 1.7349 | 1.7592 | 1.7838 | 1.8088 | 1.8341 | 1.8598 | 1.8858 | 1.9122 | 1.939 | 1.9661 | 1.9937 | 2.0216 | 2.0499 | 2.0786 | 2.1077 | 2.1372 | 2.1671 | 2.1975 | 2.2282 | 2.2594 | 2.291 | 2.3231 | 2.3556 | 2.3886
DMA23
DMA23 |  | Minutes below 12 hours CMOS |  |  |  |  | 2015: 0; 2016: 26640; 2017: 0; 2018: 1357200; 2019: 42480; 2021: 8640; 2022: 4320; 2023: 0; average 2025: 205611.4286
DMA23
DMA23 |  | Consumption per customer on DMA23 per hour |  |  |  |  | 2022: 0.00075208
DMA23 |  | DMA Energy at risk | [11 empty] | 2.5773 | 2.6134 | 2.65 | 2.6871 | 2.7247 | 2.7628 | 2.8015 | 2.8407 | 2.8805 | 2.9208 | 2.9617 | 3.0032 | 3.0452 | 3.0878 | 3.1311 | 3.1749 | 3.2194 | 3.2644 | 3.3101 | 3.3565 | 3.4035 | 3.4511 | 3.4994 | 3.5484 | 3.5981 | 3.6485 | 3.6996 | 3.7513 | 3.8039 | 3.8571 | 3.9111
MTN32
MTN32 |  | Minutes below 12 hours CMOS |  |  |  |  | 2015: 12960; 2016: 6480; 2017: 0; 2018: 434880; 2019: 14400; 2021: 8640; 2022: 720; 2023: 1440; average 2025: 68297.1429
MTN32
MTN32 |  | Consumption per customer on MTN32 per hour |  |  |  |  | 2022: 0.0010261
MTN32 |  | MTN Energy at risk | [11 empty] | 1.168 | 1.1843 | 1.2009 | 1.2177 | 1.2348 | 1.2521 | 1.2696 | 1.2874 | 1.3054 | 1.3237 | 1.3422 | 1.361 | 1.3801 | 1.3994 | 1.419 | 1.4388 | 1.459 | 1.4794 | 1.5001 | 1.5211 | 1.5424 | 1.564 | 1.5859 | 1.6081 | 1.6306 | 1.6534 | 1.6766 | 1.7001 | 1.7239 | 1.748 | 1.7725
RBD21
RBD21 |  | Minutes below 12 hours CMOS |  |  |  |  | 2015: 12240; 2016: 23760; 2017: 0; 2018: 0; 2019: 0; 2021: 25200; 2022: 3600; 2023: 0; average 2025: 9257.1429
RBD21
RBD21 |  | Consumption per customer on RBD21 per hour |  |  |  |  | 2022: 0.00078075
RBD21 |  | RBD Energy at risk | [11 empty] | 0.12046 | 0.12214 | 0.12385 | 0.12559 | 0.12735 | 0.12913 | 0.13094 | 0.13277 | 0.13463 | 0.13651 | 0.13843 | 0.14036 | 0.14233 | 0.14432 | 0.14634 | 0.14839 | 0.15047 | 0.15257 | 0.15471 | 0.15688 | 0.15907 | 0.1613 | 0.16356 | 0.16585 | 0.16817 | 0.17052 | 0.17291 | 0.17533 | 0.17779 | 0.18028 | 0.1828
TOTAL
|  | Energy at risk | [14 empty] | 5.6714 | 5.7508 | 5.8313 | 5.913 | 5.9958 | 6.0797 | 6.1648 | 6.2511 | 6.3386 | 6.4274 | 6.5174 | 6.6086 | 6.7011 | 6.795 | 6.8901 | 6.9865 | 7.0844 | 7.1835 | 7.2841 | 7.3861 | 7.4895 | 7.5943 | 7.7007 | 7.8085 | 7.9178 | 8.0286 | 8.141 | 8.255
|  | Percentage of LV and services outages | [14 empty] | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75%
Improvement in HV outages | bar: average 2025 to average 2052
|  | Total Energy at Risk | [14 empty] | 1.4179 | 1.4377 | 1.4578 | 1.4782 | 1.4989 | 1.5199 | 1.5412 | 1.5628 | 1.5847 | 1.6068 | 1.6293 | 1.6522 | 1.6753 | 1.6987 | 1.7225 | 1.7466 | 1.7711 | 1.7959 | 1.821 | 1.8465 | 1.8724 | 1.8986 | 1.9252 | 1.9521 | 1.9794 | 2.0072 | 2.0353 | 2.0638
Fire risk reduction due to additional coverage of REFCL
RBD21
Actual Performance |  | IRUs |  |  |  |  | 2016: 0.2; 2017: 0.2; 2018: 0; 2019: 0; 2020: 0.38; 2021: 0.48; 2022: 0.2; 2023: 1.0688; average 2025: 0.3161
|  | Reduction in fire starts due to REFCL | [14 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | Forecast IRU improvement | [14 empty] | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161 | 0.3161
|  | Forecast IRU Value | [13 empty] | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000
|  | Forecast IRU benefit ($) | [14 empty] | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5 | 4741.5

## Risks_LMP
United Energy
Lower Mornington Peninsula supply area
RISKS - LMP
ZSS/TS/Line | No Tx/Line
LMP | 1
| N Rating | N-1 Rating | Load Tan Phi (actual) | Load Tan Phi (forecast) | 10%/50% POE | Cap Bank (actual) | Cap Bank (forecast) | 2024 MVAR | Interval | 15m
S | 123 | 123 | -0.011461 | -0.011461 | 1.1361 |  | 0 | -1.4033 | Exposure | 0.094%
W | 123 | 123 | -0.025255 | -0.025255 | 1.0694 |  | 0 | -2.1133
| Neutral 50 POE | Actual | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast | Forecast
Option 1 (base case) - 50% PoE Load Forecast |  | FY24 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
LMP | S (MW) | 122.44 | 123.67 | 123.65 | 124.82 | 126.39 | 127.89 | 128.94 | 130.15 | 132.01 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47 | 134.47
| W (MW) | 83.68 | 84.215 | 85.07 | 85.995 | 87.39 | 88.725 | 89.825 | 91.045 | 92.34 | 93.775 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58
Transfers | S (MW) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| W (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
After TFs | S (MW) | 113.44 | 114.67 | 114.65 | 115.82 | 117.39 | 118.89 | 119.94 | 121.15 | 123.01 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47
| W (MW) | 83.68 | 84.215 | 85.07 | 85.995 | 87.39 | 88.725 | 89.825 | 91.045 | 92.34 | 93.775 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58
Option 2 - 50% PoE Load Forecast
LMP | S (MW) | 113.44 | 114.67 | 114.65 | 115.82 | 117.39 | 118.89 | 119.94 | 121.15 | 123.01 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47
| W (MW) | 83.68 | 84.215 | 85.07 | 85.995 | 87.39 | 88.725 | 89.825 | 91.045 | 92.34 | 93.775 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58
Transfers | S (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| W (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
After TFs | S (MW) | 113.44 | 114.67 | 114.65 | 115.82 | 117.39 | 118.89 | 119.94 | 121.15 | 123.01 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47
| W (MW) | 83.68 | 84.215 | 85.07 | 85.995 | 87.39 | 88.725 | 89.825 | 91.045 | 92.34 | 93.775 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58
Option 2 - Augmentation Details |  | FY27: 2027 works completed
N Rating | S (MVA) | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
N-1 Rating | S (MVA) | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
N Rating | W (MVA) | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
N-1 Rating | W (MVA) | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
No. Transformers/Lines | bar: FY24 to FY51
Option 1 (base case) |  | FY24: ACTUAL
LMP |  | FY24 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
50% PoE Summer Maximum Demand (MVA) |  | 113.4475 | 114.6775 | 114.6575 | 115.8276 | 117.3977 | 118.8978 | 119.9479 | 121.158 | 123.0181 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782
50% PoE Summer Load at Risk (MVA) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018079 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782
50% PoE Winter Maximum Demand (MVA) |  | 83.7067 | 84.2419 | 85.0971 | 86.0224 | 87.4179 | 88.7533 | 89.8536 | 91.074 | 92.3694 | 93.8049 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102
50% PoE Winter Load at Risk (MVA) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE N energy at risk (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0046129 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376
50% PoE N-1 energy at risk (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% PoE N energy at risk (MWh) |  | 4.6545 | 7.0565 | 7.0136 | 9.7045 | 14.0732 | 19.2544 | 23.4817 | 28.9686 | 38.2914 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433
10% PoE N-1 energy at risk (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE N expected unserved energy (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0046129 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376
50% PoE N - 1 expected unserved energy (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% PoE N expected unserved energy (MWh) |  | 4.6545 | 7.0565 | 7.0136 | 9.7045 | 14.0732 | 19.2544 | 23.4817 | 28.9686 | 38.2914 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433
10% PoE N - 1 expected unserved energy (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE hours at risk (hrs) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
10% energy at risk (MWh) | 30% | 4.6545 | 7.0565 | 7.0136 | 9.7045 | 14.0732 | 19.2544 | 23.4817 | 28.9686 | 38.2914 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433
50% energy at risk (MWh) | 70% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0046129 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376
10% expected unserved energy (MWh) |  | 4.6545 | 7.0565 | 7.0136 | 9.7045 | 14.0732 | 19.2544 | 23.4817 | 28.9686 | 38.2914 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433
50% expected unserved energy (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0046129 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376
Weighted energy at risk |  | 1.3964 | 2.1169 | 2.1041 | 2.9113 | 4.222 | 5.7763 | 7.0445 | 8.6906 | 11.4907 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996 | 16.1996
Option 2 |  | ACTUAL FY24: ACTUAL
LMP |  | FY24 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
50% PoE Summer Maximum Demand (MVA) |  | 113.4475 | 114.6775 | 114.6575 | 115.8276 | 117.3977 | 118.8978 | 119.9479 | 121.158 | 123.0181 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 0
50% PoE Summer Load at Risk (MVA) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE Winter Maximum Demand (MVA) |  | 83.7067 | 84.2419 | 85.0971 | 86.0224 | 87.4179 | 88.7533 | 89.8536 | 91.074 | 92.3694 | 93.8049 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 0
50% PoE Winter Load at Risk (MVA) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE N energy at risk (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE N-1 energy at risk (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% PoE N energy at risk (MWh) |  | 4.6545 | 7.0565 | 7.0136 | 9.7045 | 14.0732 | 19.2544 | 23.4817 | 28.9686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% PoE N-1 energy at risk (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE N expected unserved energy (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE N - 1 expected unserved energy (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% PoE N expected unserved energy (MWh) |  | 4.6545 | 7.0565 | 7.0136 | 9.7045 | 14.0732 | 19.2544 | 23.4817 | 28.9686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% PoE N - 1 expected unserved energy (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE hours at risk (hrs) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% energy at risk (MWh) |  | 4.6545 | 7.0565 | 7.0136 | 9.7045 | 14.0732 | 19.2544 | 23.4817 | 28.9686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% energy at risk (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% expected unserved energy (MWh) |  | 4.6545 | 7.0565 | 7.0136 | 9.7045 | 14.0732 | 19.2544 | 23.4817 | 28.9686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% expected unserved energy (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted energy at risk |  | 1.3964 | 2.1169 | 2.1041 | 2.9113 | 4.222 | 5.7763 | 7.0445 | 8.6906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option1_EaR
United Energy
Lower Mornington Peninsula supply area
ENERGY AT RISK: OPTION 1 (base case)
Summary |  |  |  | FY24 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
50% PoE | N |  | Total Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
50% PoE | N-1 |  | Total Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Total Hours at Risk | 1.5 | 1.75 | 1.75 | 2 | 2.5 | 3.25 | 3.75 | 4.25 | 4.75 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25 | 5.25
10% LAR | N-1 |  | Total Hours at Risk | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
50% PoE | N |  | Total EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0046129 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376
50% PoE | N-1 |  | Total EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Total EatR, MWhrs | 4.6545 | 7.0565 | 7.0136 | 9.7045 | 14.0732 | 19.2544 | 23.4817 | 28.9686 | 38.2914 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433
10% LAR | N-1 |  | Total EatR, MWhrs | 0.00030571 | 0.00046347 | 0.00046065 | 0.00063739 | 0.00092432 | 0.0012646 | 0.0015423 | 0.0019026 | 0.002515 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405 | 0.003405
50% PoE | N |  | Total EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0046129 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376 | 0.92376
50% PoE | N-1 |  | Total EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Total EEatR, MWhrs | 4.6545 | 7.0565 | 7.0136 | 9.7045 | 14.0732 | 19.2544 | 23.4817 | 28.9686 | 38.2914 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433 | 51.8433
10% LAR | N-1 |  | Total EEatR, MWhrs | 2.8736e-07 | 4.3566e-07 | 4.3301e-07 | 5.9914e-07 | 8.6887e-07 | 1.1887e-06 | 1.4497e-06 | 1.7885e-06 | 2.3641e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06 | 3.2007e-06
Summer hrs above 95% |  | 1.75 | hrs above 95% MD
Winter hrs above 95% |  | 2.5 | hrs above 95% MD
0.094%
Transfers | ON
LMP | 50% PoE | 0.9205% | MW | 113.44 | 114.67 | 114.65 | 115.82 | 117.39 | 118.89 | 119.94 | 121.15 | 123.01 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47
Summer |  | load pf | MVAr | -1.3002 | -1.3143 | -1.314 | -1.3275 | -1.3455 | -1.3626 | -1.3747 | -1.3885 | -1.4099 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381
|  | 0.99993 | MVA | 113.4475 | 114.6775 | 114.6575 | 115.8276 | 117.3977 | 118.8978 | 119.9479 | 121.158 | 123.0181 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782
|  |  | MVA | 113.4475 | 114.6775 | 114.6575 | 115.8276 | 117.3977 | 118.8978 | 119.9479 | 121.158 | 123.0181 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782
50% PoE | N | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123
50% PoE | N-1 | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123
50% LAR | N |  | Ratio Rating/Load | 1.0842 | 1.0726 | 1.0728 | 1.0619 | 1.0477 | 1.0345 | 1.0254 | 1.0152 | 0.99985 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024
50% LAR | N-1 |  | Ratio Rating/Load | 1.0842 | 1.0726 | 1.0728 | 1.0619 | 1.0477 | 1.0345 | 1.0254 | 1.0152 | 0.99985 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024 | 0.98024
Load tan Phi | -0.011461 |  |  | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461
Cap | 0 |  | MVAr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% PoE | 10%/50% | 1.1361 | MVA | 128.8931 | 130.2907 | 130.268 | 131.5973 | 133.3812 | 135.0855 | 136.2786 | 137.6534 | 139.7668 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619
10% PoE | N | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123
10% PoE | N-1 | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123
10% LAR | N |  | Ratio Rating/Load | 0.95427 | 0.94404 | 0.9442 | 0.93466 | 0.92216 | 0.91053 | 0.90256 | 0.89354 | 0.88003 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278
10% LAR | N-1 |  | Ratio Rating/Load | 0.95427 | 0.94404 | 0.9442 | 0.93466 | 0.92216 | 0.91053 | 0.90256 | 0.89354 | 0.88003 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278 | 0.86278
50% PoE | N |  | EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018451 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951
50% PoE | N-1 |  | EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | EatR, MWhrs | 18.618 | 28.226 | 28.0543 | 38.8179 | 56.2929 | 77.0176 | 93.9269 | 115.8744 | 153.1658 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732
10% LAR | N-1 |  | EatR, MWhrs | 0.0012228 | 0.0018539 | 0.0018426 | 0.0025495 | 0.0036973 | 0.0050585 | 0.0061691 | 0.0076106 | 0.01006 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362 | 0.01362
No of Tx | bar: FY24 to FY51
50% PoE | N | 1 | EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018451 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951 | 3.6951
50% PoE | N-1 |  | EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N | 1 | EEatR, MWhrs | 18.618 | 28.226 | 28.0543 | 38.8179 | 56.2929 | 77.0176 | 93.9269 | 115.8744 | 153.1658 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732 | 207.3732
10% LAR | N-1 | 0.094% | EEatR, MWhrs | 1.1495e-06 | 1.7426e-06 | 1.732e-06 | 2.3966e-06 | 3.4755e-06 | 4.755e-06 | 5.7989e-06 | 7.154e-06 | 9.4563e-06 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05 | 1.2803e-05
50% PoE | N |  | Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
50% PoE | N-1 |  | Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Hours at Risk | 6 | 7 | 7 | 8 | 10 | 13 | 15 | 17 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
10% LAR | N-1 |  | Hours at Risk | bar: FY24 to FY51
50% PoE | N |  | Load at Risk, MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018079 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782
50% PoE | N-1 |  | Load at Risk, MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018079 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782 | 2.4782
10% LAR | N |  | Load at Risk, MVA | 5.8931 | 7.2907 | 7.268 | 8.5973 | 10.3812 | 12.0855 | 13.2786 | 14.6534 | 16.7668 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619
10% LAR | N-1 |  | Load at Risk, MVA | 5.8931 | 7.2907 | 7.268 | 8.5973 | 10.3812 | 12.0855 | 13.2786 | 14.6534 | 16.7668 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619 | 19.5619
50% PoE |  |  | Load/N-1 | 92.23% | 93.23% | 93.22% | 94.17% | 95.45% | 96.66% | 97.52% | 98.5% | 100% | 102% | 102% | 102% | 102% | 102% | 102% | 102% | 102% | 102% | 102% | 102% | 102% | 102% | 102% | 102% | 102% | 102% | 102% | 102%
LMP | 50% PoE | 1.119% | MW | 83.68 | 84.215 | 85.07 | 85.995 | 87.39 | 88.725 | 89.825 | 91.045 | 92.34 | 93.775 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58
Winter |  | load pf | MVAr | -2.1133 | -2.1268 | -2.1484 | -2.1718 | -2.207 | -2.2407 | -2.2685 | -2.2993 | -2.332 | -2.3683 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886
|  | 0.99968 | MVA | 83.7067 | 84.2419 | 85.0971 | 86.0224 | 87.4179 | 88.7533 | 89.8536 | 91.074 | 92.3694 | 93.8049 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102
|  |  | MVA | 83.7067 | 84.2419 | 85.0971 | 86.0224 | 87.4179 | 88.7533 | 89.8536 | 91.074 | 92.3694 | 93.8049 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102
50% PoE | N | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123
50% PoE | N-1 | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123
50% LAR | N |  | Ratio Rating/Load | 1.4694 | 1.4601 | 1.4454 | 1.4299 | 1.407 | 1.3859 | 1.3689 | 1.3505 | 1.3316 | 1.3112 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001
50% LAR | N-1 |  | Ratio Rating/Load | 1.4694 | 1.4601 | 1.4454 | 1.4299 | 1.407 | 1.3859 | 1.3689 | 1.3505 | 1.3316 | 1.3112 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001 | 1.3001
Load tan Phi | -0.025255 | 0.99968 | MVA | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255
Cap | 0 |  | MVAr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% PoE | 10%/50% | 1.0694 | MVA | 89.5185 | 90.0909 | 91.0055 | 91.9951 | 93.4874 | 94.9155 | 96.0923 | 97.3974 | 98.7828 | 100.3179 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791
10% PoE | N | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123
10% PoE | N-1 | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123
10% LAR | N |  | Ratio Rating/Load | 1.374 | 1.3653 | 1.3516 | 1.337 | 1.3157 | 1.2959 | 1.28 | 1.2629 | 1.2451 | 1.2261 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157
10% LAR | N-1 |  | Ratio Rating/Load | 1.374 | 1.3653 | 1.3516 | 1.337 | 1.3157 | 1.2959 | 1.28 | 1.2629 | 1.2451 | 1.2261 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157 | 1.2157
50% PoE | N |  | EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 |  | EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No of Tx | bar: FY24 to FY51
50% PoE | N | 1 | EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 | 0.094% | EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N | 1 | EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 | 0.094% | EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N |  | Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 |  | Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N |  | Load at Risk, MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | Load at Risk, MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Load at Risk, MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 |  | Load at Risk, MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE |  |  | Load/N-1 | 68.05% | 68.49% | 69.18% | 69.94% | 71.07% | 72.16% | 73.05% | 74.04% | 75.1% | 76.26% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92% | 76.92%
Total Energy based on average LDC
Summer MWh |  | 1308.9666 |  | 148489.1766 | 150099.2056 | 150073.0263 | 151604.5172 | 153659.5949 | 155623.0449 | 156997.4598 | 158581.3095 | 161015.9875 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454
Wintr MWh |  | 2043.1376 |  | 170969.7549 | 172062.8336 | 173809.7162 | 175699.6185 | 178549.7955 | 181277.3842 | 183524.8355 | 186017.4634 | 188663.3266 | 191595.2291 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549
Total year MWh |  |  |  | 319458.9316 | 322162.0392 | 323882.7425 | 327304.1358 | 332209.3904 | 336900.429 | 340522.2954 | 344598.7729 | 349679.3141 | 355831.2745 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003

## Option2_EaR
United Energy
Lower Mornington Peninsula supply area
ENERGY AT RISK: OPTION 2
Option 2 |  |  |  | FY24 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50
50% PoE | N |  | Total Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | Total Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Total Hours at Risk | 1.5 | 1.75 | 1.75 | 2 | 2.5 | 3.25 | 3.75 | 4.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 |  | Total Hours at Risk | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N |  | Total EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | Total EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Total EatR, MWhrs | 4.6545 | 7.0565 | 7.0136 | 9.7045 | 14.0732 | 19.2544 | 23.4817 | 28.9686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 |  | Total EatR, MWhrs | 0.00030571 | 0.00046347 | 0.00046065 | 0.00063739 | 0.00092432 | 0.0012646 | 0.0015423 | 0.0019026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N |  | Total EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | Total EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Total EEatR, MWhrs | 4.6545 | 7.0565 | 7.0136 | 9.7045 | 14.0732 | 19.2544 | 23.4817 | 28.9686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 |  | Total EEatR, MWhrs | 2.8736e-07 | 4.3566e-07 | 4.3301e-07 | 5.9914e-07 | 8.6887e-07 | 1.1887e-06 | 1.4497e-06 | 1.7885e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer hrs above 95% |  | 1.75 | hrs above 95% MD
Winter hrs above 95% |  | 2.5 | hrs above 95% MD
0.094%
Transfers | ON
LMP | 50% PoE | 0.9205% | MW | 113.44 | 114.67 | 114.65 | 115.82 | 117.39 | 118.89 | 119.94 | 121.15 | 123.01 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47 | 125.47
Summer |  | load pf | MVAr | -1.3002 | -1.3143 | -1.314 | -1.3275 | -1.3455 | -1.3626 | -1.3747 | -1.3885 | -1.4099 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381 | -1.4381
|  | 0.99993 | MVA | 113.4475 | 114.6775 | 114.6575 | 115.8276 | 117.3977 | 118.8978 | 119.9479 | 121.158 | 123.0181 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782
|  |  | MVA | 113.4475 | 114.6775 | 114.6575 | 115.8276 | 117.3977 | 118.8978 | 119.9479 | 121.158 | 123.0181 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782 | 125.4782
50% PoE | N | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
50% PoE | N-1 | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
50% LAR | N |  | Ratio Rating/Load | 1.0842 | 1.0726 | 1.0728 | 1.0619 | 1.0477 | 1.0345 | 1.0254 | 1.0152 | 1.2681 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432
50% LAR | N-1 |  | Ratio Rating/Load | 1.0842 | 1.0726 | 1.0728 | 1.0619 | 1.0477 | 1.0345 | 1.0254 | 1.0152 | 1.2681 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432 | 1.2432
Load tan Phi | -0.011461 |  |  | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461 | -0.011461
Cap | 0 |  | MVAr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% PoE | 10%/50% | 1.1361 | MVA | 128.8931 | 130.2907 | 130.268 | 131.5973 | 133.3812 | 135.0855 | 136.2786 | 137.6534 | 139.7668 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619 | 142.5619
10% PoE | N | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
10% PoE | N-1 | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
10% LAR | N |  | Ratio Rating/Load | 0.95427 | 0.94404 | 0.9442 | 0.93466 | 0.92216 | 0.91053 | 0.90256 | 0.89354 | 1.1161 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943
10% LAR | N-1 |  | Ratio Rating/Load | 0.95427 | 0.94404 | 0.9442 | 0.93466 | 0.92216 | 0.91053 | 0.90256 | 0.89354 | 1.1161 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 1.0943
50% PoE | N |  | EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | EatR, MWhrs | 18.618 | 28.226 | 28.0543 | 38.8179 | 56.2929 | 77.0176 | 93.9269 | 115.8744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 |  | EatR, MWhrs | 0.0012228 | 0.0018539 | 0.0018426 | 0.0025495 | 0.0036973 | 0.0050585 | 0.0061691 | 0.0076106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No of Tx | bar: FY24 to FY50
50% PoE | N | 1 | EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N | 1 | EEatR, MWhrs | 18.618 | 28.226 | 28.0543 | 38.8179 | 56.2929 | 77.0176 | 93.9269 | 115.8744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 | 0.094% | EEatR, MWhrs | 1.1495e-06 | 1.7426e-06 | 1.732e-06 | 2.3966e-06 | 3.4755e-06 | 4.755e-06 | 5.7989e-06 | 7.154e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N |  | Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Hours at Risk | 6 | 7 | 7 | 8 | 10 | 13 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 |  | Hours at Risk | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N |  | Load at Risk, MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | Load at Risk, MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Load at Risk, MVA | 5.8931 | 7.2907 | 7.268 | 8.5973 | 10.3812 | 12.0855 | 13.2786 | 14.6534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 |  | Load at Risk, MVA | 5.8931 | 7.2907 | 7.268 | 8.5973 | 10.3812 | 12.0855 | 13.2786 | 14.6534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE |  |  | Load/N-1 | 92.23% | 93.23% | 93.22% | 94.17% | 95.45% | 96.66% | 97.52% | 98.5% | 78.86% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43% | 80.43%
LMP | 50% PoE | 1.119% | MW | 83.68 | 84.215 | 85.07 | 85.995 | 87.39 | 88.725 | 89.825 | 91.045 | 92.34 | 93.775 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58 | 94.58
Winter |  | load pf | MVAr | -2.1133 | -2.1268 | -2.1484 | -2.1718 | -2.207 | -2.2407 | -2.2685 | -2.2993 | -2.332 | -2.3683 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886 | -2.3886
|  | 0.99968 | MVA | 83.7067 | 84.2419 | 85.0971 | 86.0224 | 87.4179 | 88.7533 | 89.8536 | 91.074 | 92.3694 | 93.8049 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102
|  |  | MVA | 83.7067 | 84.2419 | 85.0971 | 86.0224 | 87.4179 | 88.7533 | 89.8536 | 91.074 | 92.3694 | 93.8049 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102 | 94.6102
50% PoE | N | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
50% PoE | N-1 | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
50% LAR | N |  | Ratio Rating/Load | 1.4694 | 1.4601 | 1.4454 | 1.4299 | 1.407 | 1.3859 | 1.3689 | 1.3505 | 1.6889 | 1.663 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489
50% LAR | N-1 |  | Ratio Rating/Load | 1.4694 | 1.4601 | 1.4454 | 1.4299 | 1.407 | 1.3859 | 1.3689 | 1.3505 | 1.6889 | 1.663 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489 | 1.6489
Load tan Phi | -0.025255 | 0.99968 | MVA | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255 | -0.025255
Cap | 0 |  | MVAr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% PoE | 10%/50% | 1.0694 | MVA | 89.5185 | 90.0909 | 91.0055 | 91.9951 | 93.4874 | 94.9155 | 96.0923 | 97.3974 | 98.7828 | 100.3179 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791 | 101.1791
10% PoE | N | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
10% PoE | N-1 | CR | MVA | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156
10% LAR | N |  | Ratio Rating/Load | 1.374 | 1.3653 | 1.3516 | 1.337 | 1.3157 | 1.2959 | 1.28 | 1.2629 | 1.5792 | 1.5551 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418
10% LAR | N-1 |  | Ratio Rating/Load | 1.374 | 1.3653 | 1.3516 | 1.337 | 1.3157 | 1.2959 | 1.28 | 1.2629 | 1.5792 | 1.5551 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418 | 1.5418
50% PoE | N |  | EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 |  | EatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No of Tx | bar: FY24 to FY50
50% PoE | N | 1 | EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 | 0.094% | EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N | 1 | EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 | 0.094% | EEatR, MWhrs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N |  | Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 |  | Hours at Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N |  | Load at Risk, MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE | N-1 |  | Load at Risk, MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N |  | Load at Risk, MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% LAR | N-1 |  | Load at Risk, MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50% PoE |  |  | Load/N-1 | 68.05% | 68.49% | 69.18% | 69.94% | 71.07% | 72.16% | 73.05% | 74.04% | 59.21% | 60.13% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65% | 60.65%
Total Energy based on average LDC
Summer MWh |  | 1308.9666 |  | 148489.1766 | 150099.2056 | 150073.0263 | 151604.5172 | 153659.5949 | 155623.0449 | 156997.4598 | 158581.3095 | 161015.9875 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454 | 164236.0454
Wintr MWh |  | 2043.1376 |  | 170969.7549 | 172062.8336 | 173809.7162 | 175699.6185 | 178549.7955 | 181277.3842 | 183524.8355 | 186017.4634 | 188663.3266 | 191595.2291 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549 | 193239.9549
Total year MWh |  |  |  | 319458.9316 | 322162.0392 | 323882.7425 | 327304.1358 | 332209.3904 | 336900.429 | 340522.2954 | 344598.7729 | 349679.3141 | 355831.2745 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003 | 357476.0003

## AVG LDC
United Energy
Lower Mornington Peninsula supply area
AVERAGE LDC
Data:
Summer April 2019 - Sept 2019
Winter Oct 2018 - March 2019
Summer (Oct to Mar) |  | Winter (Apr to Sep)
MW pu | MVA pu | MW pu | MVA pu
1 | 1 | 1 | 1
0.98741 | 0.98742 | 0.99475 | 0.99465
0.98276 | 0.98276 | 0.98938 | 0.98906
0.97114 | 0.97123 | 0.98414 | 0.98431
0.96595 | 0.96671 | 0.97964 | 0.97987
0.96168 | 0.96259 | 0.9736 | 0.9738
0.95541 | 0.95598 | 0.96499 | 0.96533
0.94463 | 0.94562 | 0.96158 | 0.96182
0.93796 | 0.93838 | 0.9556 | 0.95623
0.93204 | 0.93193 | 0.95028 | 0.95121
0.92686 | 0.92681 | 0.94648 | 0.94776
0.92149 | 0.92183 | 0.94364 | 0.94459
0.9187 | 0.91976 | 0.94017 | 0.94054
0.91157 | 0.91254 | 0.93619 | 0.93709
0.90902 | 0.90965 | 0.93283 | 0.93403
0.90362 | 0.90357 | 0.92991 | 0.93155
0.89915 | 0.89965 | 0.92734 | 0.92877
0.89618 | 0.89618 | 0.92464 | 0.92574
0.88793 | 0.88956 | 0.92323 | 0.9243
0.88305 | 0.88426 | 0.9204 | 0.92108
0.87336 | 0.87515 | 0.91644 | 0.91762
0.86598 | 0.86741 | 0.91476 | 0.91658
0.86115 | 0.86193 | 0.91252 | 0.91376
0.85292 | 0.85407 | 0.91084 | 0.9119
0.84701 | 0.84858 | 0.90783 | 0.90934
0.84108 | 0.84228 | 0.90546 | 0.9064
0.83693 | 0.83815 | 0.90225 | 0.90396
0.83529 | 0.83633 | 0.9004 | 0.90183
0.82926 | 0.83188 | 0.8989 | 0.90054
0.82574 | 0.82646 | 0.89668 | 0.89802
0.82397 | 0.82451 | 0.8958 | 0.89699
0.81951 | 0.82052 | 0.89439 | 0.89557
0.81534 | 0.81651 | 0.89166 | 0.89328
0.81143 | 0.81245 | 0.89043 | 0.89149
0.80881 | 0.81022 | 0.8889 | 0.88981
0.8057 | 0.80704 | 0.88692 | 0.88838
0.80383 | 0.80614 | 0.8856 | 0.88752
0.79965 | 0.80284 | 0.88435 | 0.88602
0.79845 | 0.80108 | 0.8835 | 0.8848
0.7966 | 0.79863 | 0.88167 | 0.88327
0.79368 | 0.79626 | 0.87994 | 0.88116
0.79055 | 0.79257 | 0.87896 | 0.88017
0.78736 | 0.78983 | 0.87768 | 0.87967
0.78584 | 0.78772 | 0.8758 | 0.87787
0.78387 | 0.78535 | 0.87447 | 0.87619
0.78092 | 0.78243 | 0.8737 | 0.87513
0.7779 | 0.78035 | 0.87276 | 0.87454
0.77486 | 0.77611 | 0.87177 | 0.87332
0.7701 | 0.77183 | 0.87063 | 0.87222
0.76754 | 0.7699 | 0.86934 | 0.87078
0.76382 | 0.76609 | 0.86814 | 0.86968
0.76105 | 0.763 | 0.86677 | 0.86813
0.75788 | 0.76051 | 0.8655 | 0.86703
0.75492 | 0.75791 | 0.86438 | 0.86615
0.75388 | 0.75594 | 0.86332 | 0.86531
0.75169 | 0.75369 | 0.86199 | 0.86429
0.74931 | 0.75196 | 0.86139 | 0.8636
0.74777 | 0.74931 | 0.86066 | 0.86266
0.74545 | 0.74734 | 0.85954 | 0.86119
0.74297 | 0.74507 | 0.85857 | 0.86051
0.73949 | 0.74319 | 0.85738 | 0.85932
0.73667 | 0.73988 | 0.85677 | 0.85856
0.73477 | 0.73665 | 0.8561 | 0.85779
0.7322 | 0.73453 | 0.85505 | 0.85687
0.73064 | 0.73318 | 0.85412 | 0.85601
0.72855 | 0.73152 | 0.85343 | 0.85538
0.72573 | 0.72989 | 0.85246 | 0.85438
0.72401 | 0.72771 | 0.85176 | 0.85367
0.72255 | 0.72553 | 0.85097 | 0.85305
0.72039 | 0.72311 | 0.85044 | 0.85209
0.71832 | 0.72092 | 0.84966 | 0.85132
0.71526 | 0.71847 | 0.84897 | 0.8507
0.71389 | 0.71663 | 0.84817 | 0.84978
0.71216 | 0.71475 | 0.84752 | 0.84895
0.7109 | 0.71378 | 0.84693 | 0.84853
0.70984 | 0.71213 | 0.84617 | 0.84788
0.70804 | 0.71127 | 0.84526 | 0.84708
0.70622 | 0.70844 | 0.84454 | 0.84657
0.70462 | 0.70721 | 0.84377 | 0.84608
0.70349 | 0.70622 | 0.84293 | 0.84512
0.70261 | 0.70536 | 0.84194 | 0.84413
0.70146 | 0.70412 | 0.84138 | 0.84359
0.69952 | 0.70266 | 0.84087 | 0.84277
0.69823 | 0.70142 | 0.84004 | 0.84197
0.69658 | 0.69968 | 0.83955 | 0.84151
0.69405 | 0.69751 | 0.83908 | 0.84107
0.69255 | 0.69584 | 0.83828 | 0.84003
0.69084 | 0.69419 | 0.83772 | 0.83971
0.68971 | 0.69292 | 0.83683 | 0.83916
0.68808 | 0.69147 | 0.83609 | 0.8386
0.68622 | 0.68953 | 0.83564 | 0.83794
0.68438 | 0.68819 | 0.83491 | 0.83694
0.68305 | 0.68687 | 0.83434 | 0.83631
0.68182 | 0.68522 | 0.83372 | 0.83571
0.68081 | 0.68412 | 0.83309 | 0.83526
0.67941 | 0.68286 | 0.83237 | 0.83474
0.67853 | 0.68205 | 0.83173 | 0.83395
0.67664 | 0.68022 | 0.83125 | 0.83342
0.67521 | 0.67828 | 0.83088 | 0.83292
0.67372 | 0.67698 | 0.83043 | 0.83244
0.67194 | 0.67583 | 0.83003 | 0.83218
0.67074 | 0.67432 | 0.82917 | 0.8315
0.66838 | 0.67218 | 0.82823 | 0.83087
0.66709 | 0.67076 | 0.82762 | 0.83033
0.66612 | 0.66925 | 0.82713 | 0.82973
0.66553 | 0.66851 | 0.82663 | 0.82915
0.66438 | 0.66684 | 0.82612 | 0.82853
0.66139 | 0.66474 | 0.82568 | 0.82793
0.66028 | 0.66356 | 0.82498 | 0.82762
0.65927 | 0.66317 | 0.8245 | 0.8272
0.65851 | 0.66213 | 0.82401 | 0.82665
0.6572 | 0.66073 | 0.82344 | 0.82566
0.65607 | 0.65978 | 0.82255 | 0.82497
0.6552 | 0.6593 | 0.82206 | 0.82446
0.65454 | 0.6583 | 0.82138 | 0.82401
0.65354 | 0.65737 | 0.8211 | 0.82347
0.65285 | 0.65665 | 0.82029 | 0.8231
0.65177 | 0.65559 | 0.81972 | 0.82249
0.65086 | 0.65474 | 0.81923 | 0.82219
0.65016 | 0.65383 | 0.81897 | 0.82165
0.64965 | 0.65287 | 0.81846 | 0.82121
0.64774 | 0.65197 | 0.81817 | 0.82078
0.64707 | 0.65109 | 0.81768 | 0.82038
0.64623 | 0.65035 | 0.81716 | 0.81993
0.64544 | 0.64966 | 0.81666 | 0.81946
0.64485 | 0.64858 | 0.81621 | 0.81901
0.64389 | 0.64757 | 0.8159 | 0.81868
0.64312 | 0.64667 | 0.81548 | 0.81808
0.64225 | 0.64595 | 0.81508 | 0.81775
0.64099 | 0.64515 | 0.81464 | 0.81737
0.63981 | 0.64359 | 0.81434 | 0.81702
0.63854 | 0.64244 | 0.81399 | 0.81662
0.63779 | 0.64192 | 0.81366 | 0.81628
0.63694 | 0.64145 | 0.81319 | 0.81577
0.63558 | 0.6403 | 0.81277 | 0.81548
0.63446 | 0.63919 | 0.81228 | 0.81497
0.63361 | 0.63773 | 0.81182 | 0.81453
0.63239 | 0.63644 | 0.81127 | 0.81425
0.63153 | 0.63553 | 0.81082 | 0.81379
0.63074 | 0.63502 | 0.81035 | 0.81333
0.62929 | 0.63409 | 0.81003 | 0.8131
0.62841 | 0.63304 | 0.80972 | 0.81285
0.62786 | 0.6325 | 0.8092 | 0.81254
0.62742 | 0.63221 | 0.80891 | 0.81214
0.62693 | 0.6317 | 0.80856 | 0.8117
0.62645 | 0.63117 | 0.80818 | 0.81116
0.62589 | 0.63057 | 0.80772 | 0.81062
0.62482 | 0.62961 | 0.8072 | 0.8103
0.6242 | 0.62913 | 0.80631 | 0.80948
0.62369 | 0.62832 | 0.80584 | 0.80905
0.62323 | 0.62764 | 0.80555 | 0.80864
0.62261 | 0.62713 | 0.80522 | 0.8083
0.62205 | 0.6267 | 0.80492 | 0.80782
0.62077 | 0.6259 | 0.80461 | 0.8074
0.62014 | 0.62519 | 0.80401 | 0.80694
0.61936 | 0.62461 | 0.80368 | 0.80663
0.61872 | 0.62365 | 0.80335 | 0.80631
0.61791 | 0.62242 | 0.8029 | 0.80595
0.6167 | 0.62136 | 0.80238 | 0.80566
0.61597 | 0.62049 | 0.80214 | 0.80544
0.61512 | 0.61959 | 0.80169 | 0.80499
0.61404 | 0.61897 | 0.80139 | 0.80455
0.61283 | 0.61832 | 0.80101 | 0.80421
0.61209 | 0.61754 | 0.80079 | 0.80394
0.61147 | 0.61656 | 0.80036 | 0.80378
0.61089 | 0.61609 | 0.80016 | 0.80342
0.61023 | 0.61493 | 0.79995 | 0.80316
0.60932 | 0.61387 | 0.79973 | 0.80292
0.60834 | 0.61338 | 0.79935 | 0.8025
0.60778 | 0.61259 | 0.7991 | 0.80215
0.60732 | 0.61173 | 0.7987 | 0.80197
0.60674 | 0.61088 | 0.79836 | 0.8016
0.60611 | 0.61028 | 0.79813 | 0.80129
0.60512 | 0.60971 | 0.79788 | 0.80092
0.60433 | 0.60901 | 0.79769 | 0.80061
0.60321 | 0.60828 | 0.79739 | 0.80042
0.6026 | 0.60786 | 0.79705 | 0.80012
0.60165 | 0.60694 | 0.7968 | 0.79989
0.60097 | 0.60646 | 0.79651 | 0.79939
0.60039 | 0.60587 | 0.79621 | 0.7991
0.59977 | 0.60553 | 0.79585 | 0.79879
0.59932 | 0.60498 | 0.79554 | 0.79862
0.59906 | 0.60459 | 0.79513 | 0.79821
0.5985 | 0.60413 | 0.79486 | 0.79779
0.59782 | 0.60348 | 0.79454 | 0.79744
0.59677 | 0.60223 | 0.79412 | 0.79723
0.59627 | 0.60154 | 0.79388 | 0.79699
0.59578 | 0.60098 | 0.79339 | 0.79672
0.59507 | 0.6001 | 0.79278 | 0.79633
0.59418 | 0.59939 | 0.79265 | 0.79605
0.59385 | 0.59864 | 0.79245 | 0.79579
0.59291 | 0.59801 | 0.79222 | 0.79528
0.59249 | 0.59745 | 0.79202 | 0.79508
0.59196 | 0.59682 | 0.79177 | 0.79485
0.59125 | 0.59654 | 0.79163 | 0.79468
0.59077 | 0.59631 | 0.79128 | 0.79435
0.58997 | 0.59581 | 0.791 | 0.79398
0.5894 | 0.59533 | 0.79067 | 0.79366
0.58872 | 0.5948 | 0.79037 | 0.79355
0.58837 | 0.5943 | 0.78988 | 0.79329
0.58767 | 0.59347 | 0.78969 | 0.79309
0.5872 | 0.59264 | 0.78946 | 0.79288
0.58651 | 0.59218 | 0.78931 | 0.79262
0.58578 | 0.59182 | 0.78897 | 0.79239
0.58546 | 0.59088 | 0.7887 | 0.79217
0.58491 | 0.59052 | 0.78839 | 0.79194
0.58414 | 0.58991 | 0.78819 | 0.79139
0.58364 | 0.58925 | 0.78802 | 0.7912
0.58326 | 0.58882 | 0.78773 | 0.79079
0.58272 | 0.58839 | 0.78751 | 0.79065
0.58235 | 0.58798 | 0.78709 | 0.79043
0.58195 | 0.58758 | 0.78682 | 0.79021
0.58167 | 0.5871 | 0.78669 | 0.78997
0.58113 | 0.58656 | 0.78635 | 0.78987
0.5806 | 0.58587 | 0.78615 | 0.78962
0.57959 | 0.58524 | 0.78573 | 0.78945
0.5789 | 0.58458 | 0.78559 | 0.7892
0.57817 | 0.58414 | 0.78538 | 0.78884
0.57771 | 0.58356 | 0.785 | 0.7886
0.57743 | 0.58315 | 0.78479 | 0.7883
0.57684 | 0.58258 | 0.78454 | 0.7879
0.57631 | 0.58192 | 0.7842 | 0.78773
0.5756 | 0.58108 | 0.7839 | 0.78746
0.57492 | 0.58068 | 0.78362 | 0.78725
0.57407 | 0.57976 | 0.7835 | 0.78708
0.57368 | 0.57923 | 0.78332 | 0.78673
0.57325 | 0.57876 | 0.78305 | 0.78646
0.57268 | 0.57833 | 0.78282 | 0.7862
0.57206 | 0.57788 | 0.78263 | 0.78598
0.57118 | 0.57751 | 0.7823 | 0.78578
0.57073 | 0.57694 | 0.78208 | 0.78547
0.57038 | 0.57663 | 0.78183 | 0.78526
0.56982 | 0.57584 | 0.78159 | 0.78488
0.56921 | 0.5752 | 0.78126 | 0.7846
0.56853 | 0.5744 | 0.7809 | 0.78434
0.56779 | 0.57396 | 0.78054 | 0.78408
0.56709 | 0.57354 | 0.78037 | 0.78381
0.56662 | 0.57309 | 0.78002 | 0.78362
0.56594 | 0.57267 | 0.7798 | 0.78334
0.56559 | 0.57213 | 0.77967 | 0.7831
0.56514 | 0.57154 | 0.77932 | 0.78283
0.56476 | 0.57099 | 0.77895 | 0.7826
0.56408 | 0.5704 | 0.77864 | 0.78231
0.56322 | 0.56986 | 0.77843 | 0.78203
0.5628 | 0.56948 | 0.77804 | 0.78169
0.56249 | 0.56881 | 0.7778 | 0.78135
0.56224 | 0.56834 | 0.77768 | 0.78109
0.56183 | 0.56782 | 0.7775 | 0.78094
0.5615 | 0.56744 | 0.77727 | 0.78064
0.56112 | 0.56719 | 0.77699 | 0.78043
0.56066 | 0.56676 | 0.77678 | 0.78031
0.55991 | 0.56632 | 0.77664 | 0.77997
0.55932 | 0.56589 | 0.77639 | 0.77973
0.5586 | 0.56541 | 0.7762 | 0.77955
0.55826 | 0.56515 | 0.77607 | 0.77935
0.5576 | 0.56442 | 0.77583 | 0.77917
0.55723 | 0.56372 | 0.77558 | 0.77902
0.55687 | 0.56316 | 0.77544 | 0.77878
0.55652 | 0.56261 | 0.77529 | 0.77856
0.55613 | 0.56193 | 0.77505 | 0.7781
0.55552 | 0.56163 | 0.7748 | 0.77795
0.55483 | 0.56119 | 0.77451 | 0.77767
0.55449 | 0.56091 | 0.77411 | 0.77736
0.55428 | 0.56059 | 0.77375 | 0.77707
0.5537 | 0.5599 | 0.77349 | 0.77689
0.55309 | 0.55946 | 0.7732 | 0.77672
0.55266 | 0.55911 | 0.77295 | 0.77654
0.5521 | 0.55884 | 0.77277 | 0.77626
0.55173 | 0.55817 | 0.77259 | 0.77609
0.55117 | 0.55777 | 0.77246 | 0.77599
0.55078 | 0.55726 | 0.77205 | 0.77582
0.55032 | 0.55656 | 0.77181 | 0.7757
0.54996 | 0.55613 | 0.77164 | 0.77542
0.54977 | 0.55569 | 0.77148 | 0.77525
0.54953 | 0.55543 | 0.7712 | 0.77512
0.54914 | 0.55517 | 0.7711 | 0.77483
0.5486 | 0.55474 | 0.77096 | 0.77465
0.5481 | 0.55405 | 0.77071 | 0.7743
0.54784 | 0.55365 | 0.77051 | 0.77415
0.5473 | 0.5531 | 0.77032 | 0.77389
0.54682 | 0.55289 | 0.77016 | 0.77366
0.54622 | 0.55263 | 0.77001 | 0.77351
0.54572 | 0.55208 | 0.76985 | 0.77331
0.54525 | 0.55162 | 0.76962 | 0.77316
0.545 | 0.55138 | 0.76939 | 0.77296
0.54453 | 0.55098 | 0.76914 | 0.77275
0.54411 | 0.55054 | 0.76887 | 0.7725
0.54367 | 0.55025 | 0.76872 | 0.77235
0.54327 | 0.54979 | 0.76858 | 0.77224
0.54276 | 0.54916 | 0.76831 | 0.77206
0.54232 | 0.54881 | 0.76814 | 0.77191
0.54187 | 0.54844 | 0.768 | 0.77167
0.54149 | 0.54772 | 0.76778 | 0.77152
0.5409 | 0.54751 | 0.76761 | 0.77119
0.54046 | 0.5471 | 0.76734 | 0.77096
0.54008 | 0.54658 | 0.76721 | 0.77074
0.53967 | 0.546 | 0.76704 | 0.77061
0.53919 | 0.54545 | 0.76683 | 0.77042
0.53889 | 0.5452 | 0.76668 | 0.77032
0.53863 | 0.54495 | 0.76661 | 0.77016
0.53809 | 0.54469 | 0.76651 | 0.77002
0.53764 | 0.54435 | 0.76622 | 0.76978
0.53721 | 0.54399 | 0.76612 | 0.76962
0.53678 | 0.54352 | 0.76596 | 0.76951
0.53643 | 0.54322 | 0.76574 | 0.7693
0.53599 | 0.54278 | 0.76561 | 0.76919
0.53567 | 0.54248 | 0.76545 | 0.769
0.535 | 0.54216 | 0.76527 | 0.76872
0.53471 | 0.54185 | 0.765 | 0.76855
0.53418 | 0.54161 | 0.76478 | 0.76837
0.53367 | 0.54123 | 0.76458 | 0.76825
0.53339 | 0.54089 | 0.76442 | 0.7681
0.5329 | 0.54048 | 0.76419 | 0.76781
0.53254 | 0.54003 | 0.76394 | 0.76768
0.53232 | 0.53955 | 0.76368 | 0.76748
0.53188 | 0.53935 | 0.7634 | 0.76724
0.5316 | 0.53919 | 0.76314 | 0.76702
0.53135 | 0.53883 | 0.76291 | 0.76674
0.53119 | 0.5386 | 0.7626 | 0.76655
0.53067 | 0.53815 | 0.76237 | 0.76629
0.53045 | 0.53767 | 0.76218 | 0.76606
0.53 | 0.53741 | 0.76193 | 0.76585
0.52978 | 0.53717 | 0.7618 | 0.76566
0.52955 | 0.53685 | 0.76165 | 0.76553
0.52913 | 0.53645 | 0.76148 | 0.76542
0.52887 | 0.53621 | 0.76131 | 0.76527
0.52866 | 0.53593 | 0.76107 | 0.76509
0.52847 | 0.53571 | 0.76089 | 0.76491
0.52827 | 0.53543 | 0.76073 | 0.76472
0.52796 | 0.53508 | 0.76063 | 0.76452
0.52756 | 0.53475 | 0.76035 | 0.7643
0.52731 | 0.53461 | 0.76018 | 0.76412
0.52698 | 0.53426 | 0.76006 | 0.76398
0.52671 | 0.53382 | 0.7598 | 0.76379
0.52639 | 0.5335 | 0.75962 | 0.76357
0.52619 | 0.53311 | 0.75949 | 0.76335
0.52599 | 0.53287 | 0.75925 | 0.76311
0.5258 | 0.53267 | 0.75913 | 0.763
0.52554 | 0.53242 | 0.75896 | 0.76279
0.52526 | 0.53209 | 0.7588 | 0.76265
0.52479 | 0.53169 | 0.7586 | 0.76243
0.52417 | 0.53138 | 0.75851 | 0.76232
0.52392 | 0.5311 | 0.75838 | 0.76215
0.5236 | 0.53089 | 0.75815 | 0.762
0.52324 | 0.53064 | 0.75798 | 0.76183
0.523 | 0.53045 | 0.75785 | 0.76175
0.52269 | 0.53017 | 0.75767 | 0.76163
0.52249 | 0.52999 | 0.75743 | 0.76149
0.52225 | 0.5297 | 0.75725 | 0.76133
0.52193 | 0.52933 | 0.75709 | 0.76122
0.52166 | 0.52908 | 0.7569 | 0.761
0.52137 | 0.52872 | 0.75675 | 0.76088
0.52109 | 0.52835 | 0.7566 | 0.76072
0.52078 | 0.52813 | 0.75638 | 0.7605
0.52056 | 0.52789 | 0.75627 | 0.76028
0.52035 | 0.5276 | 0.75614 | 0.76014
0.52001 | 0.52732 | 0.75599 | 0.75999
0.51975 | 0.52707 | 0.7559 | 0.75985
0.5196 | 0.5268 | 0.75572 | 0.75972
0.51921 | 0.52654 | 0.75553 | 0.75958
0.51892 | 0.52624 | 0.75523 | 0.75932
0.51854 | 0.52588 | 0.75505 | 0.75918
0.51827 | 0.52539 | 0.75485 | 0.75902
0.51808 | 0.52507 | 0.75471 | 0.75887
0.51761 | 0.52487 | 0.75459 | 0.75877
0.51741 | 0.52473 | 0.75439 | 0.75863
0.5171 | 0.52454 | 0.75418 | 0.7584
0.51684 | 0.52422 | 0.75407 | 0.75827
0.51666 | 0.52403 | 0.75398 | 0.75808
0.5164 | 0.52368 | 0.75383 | 0.75791
0.51602 | 0.52345 | 0.75369 | 0.75777
0.51576 | 0.52305 | 0.75353 | 0.75766
0.51553 | 0.52287 | 0.75343 | 0.75754
0.51535 | 0.5228 | 0.75327 | 0.75738
0.51502 | 0.52266 | 0.75311 | 0.75725
0.51465 | 0.52246 | 0.75291 | 0.75711
0.51424 | 0.52216 | 0.75275 | 0.75693
0.51407 | 0.5216 | 0.7526 | 0.75675
0.51381 | 0.52125 | 0.75245 | 0.75652
0.51364 | 0.52105 | 0.75222 | 0.75637
0.51334 | 0.52083 | 0.75207 | 0.75626
0.51318 | 0.52065 | 0.75191 | 0.75607
0.51303 | 0.52041 | 0.7517 | 0.75584
0.51279 | 0.52006 | 0.75158 | 0.75571
0.5124 | 0.51989 | 0.75147 | 0.75556
0.51215 | 0.51953 | 0.75132 | 0.75543
0.51196 | 0.51901 | 0.75112 | 0.75532
0.51157 | 0.51873 | 0.75095 | 0.75511
0.51132 | 0.51836 | 0.75082 | 0.75495
0.51111 | 0.51811 | 0.75072 | 0.75486
0.51063 | 0.5178 | 0.75065 | 0.75463
0.51042 | 0.51758 | 0.75043 | 0.75449
0.51017 | 0.51743 | 0.75019 | 0.75436
0.50985 | 0.51712 | 0.74981 | 0.75415
0.50959 | 0.51692 | 0.7497 | 0.75405
0.50942 | 0.51673 | 0.74951 | 0.75384
0.50928 | 0.51645 | 0.74932 | 0.75362
0.50884 | 0.51618 | 0.74918 | 0.75341
0.50868 | 0.51596 | 0.74898 | 0.75328
0.50837 | 0.51574 | 0.74887 | 0.75313
0.50818 | 0.51558 | 0.74872 | 0.75295
0.50802 | 0.51543 | 0.7486 | 0.75282
0.50767 | 0.51524 | 0.74843 | 0.75265
0.50742 | 0.51496 | 0.74829 | 0.75247
0.50717 | 0.51481 | 0.74813 | 0.75236
0.50705 | 0.51462 | 0.74794 | 0.75219
0.50685 | 0.5145 | 0.7478 | 0.75204
0.5065 | 0.51422 | 0.74757 | 0.75191
0.50632 | 0.5141 | 0.74734 | 0.7518
0.50616 | 0.51353 | 0.74716 | 0.75166
0.50585 | 0.51336 | 0.74699 | 0.75152
0.50559 | 0.5132 | 0.74681 | 0.75135
0.50532 | 0.51308 | 0.74669 | 0.75115
0.50518 | 0.51289 | 0.74655 | 0.75102
0.50493 | 0.51262 | 0.74642 | 0.7508
0.50481 | 0.51249 | 0.74623 | 0.75059
0.50466 | 0.51224 | 0.74607 | 0.75044
0.50441 | 0.51199 | 0.74591 | 0.75022
0.50415 | 0.51172 | 0.7458 | 0.75006
0.50399 | 0.51143 | 0.74569 | 0.74993
0.50366 | 0.51122 | 0.74544 | 0.74981
0.50351 | 0.51095 | 0.74526 | 0.74962
0.5033 | 0.51089 | 0.74509 | 0.74947
0.50308 | 0.51077 | 0.74493 | 0.74933
0.50291 | 0.51054 | 0.74471 | 0.74921
0.50274 | 0.51031 | 0.74453 | 0.74907
0.50248 | 0.51013 | 0.74437 | 0.74894
0.50222 | 0.50996 | 0.74426 | 0.74882
0.50191 | 0.50979 | 0.74409 | 0.7487
0.50173 | 0.5094 | 0.74397 | 0.74856
0.50154 | 0.50905 | 0.74386 | 0.74846
0.50142 | 0.50889 | 0.74376 | 0.7483
0.50125 | 0.50873 | 0.74354 | 0.74821
0.50101 | 0.50854 | 0.74347 | 0.74805
0.50081 | 0.50839 | 0.74338 | 0.74789
0.50058 | 0.50809 | 0.74326 | 0.74778
0.50039 | 0.50789 | 0.74316 | 0.74766
0.50008 | 0.50774 | 0.743 | 0.74757
0.49988 | 0.50758 | 0.74285 | 0.74743
0.49958 | 0.50748 | 0.74266 | 0.74731
0.49926 | 0.50728 | 0.74254 | 0.74707
0.49905 | 0.50709 | 0.74245 | 0.74685
0.49884 | 0.50679 | 0.7423 | 0.74669
0.49862 | 0.50656 | 0.74216 | 0.74655
0.49847 | 0.5061 | 0.742 | 0.74645
0.49826 | 0.50593 | 0.74189 | 0.74626
0.49808 | 0.50579 | 0.74179 | 0.74615
0.49784 | 0.50555 | 0.74165 | 0.74601
0.49755 | 0.50543 | 0.74148 | 0.74588
0.49737 | 0.50535 | 0.74137 | 0.74574
0.49714 | 0.50518 | 0.74119 | 0.74564
0.49704 | 0.50485 | 0.74096 | 0.74551
0.49688 | 0.50471 | 0.7408 | 0.74531
0.49673 | 0.50451 | 0.74067 | 0.74513
0.49656 | 0.5042 | 0.74053 | 0.74496
0.49626 | 0.50411 | 0.74035 | 0.74486
0.49607 | 0.50393 | 0.74027 | 0.74475
0.49584 | 0.50378 | 0.74012 | 0.74456
0.49565 | 0.50351 | 0.73998 | 0.74437
0.49547 | 0.5034 | 0.73986 | 0.74427
0.49533 | 0.50315 | 0.73972 | 0.74408
0.49519 | 0.50298 | 0.73959 | 0.74397
0.49492 | 0.50278 | 0.73944 | 0.74381
0.49472 | 0.50258 | 0.73927 | 0.74362
0.49456 | 0.50236 | 0.73912 | 0.74351
0.49442 | 0.50223 | 0.73899 | 0.7433
0.49419 | 0.5019 | 0.73881 | 0.7431
0.4939 | 0.50165 | 0.73863 | 0.74296
0.49375 | 0.50151 | 0.7386 | 0.74285
0.49349 | 0.5013 | 0.73847 | 0.74278
0.49326 | 0.50105 | 0.73839 | 0.74262
0.493 | 0.50087 | 0.73826 | 0.74251
0.49278 | 0.50065 | 0.73809 | 0.74237
0.49257 | 0.50045 | 0.73788 | 0.74229
0.49237 | 0.50028 | 0.73775 | 0.74208
0.49219 | 0.50009 | 0.7376 | 0.74196
0.49197 | 0.50001 | 0.73744 | 0.74186
0.4918 | 0.49983 | 0.73733 | 0.74172
0.49162 | 0.49968 | 0.73719 | 0.74162
0.4914 | 0.49942 | 0.73703 | 0.74145
0.49122 | 0.49923 | 0.73688 | 0.74132
0.49089 | 0.49905 | 0.73677 | 0.7412
0.49073 | 0.49895 | 0.73658 | 0.74104
0.49057 | 0.49874 | 0.73636 | 0.74084
0.49041 | 0.49852 | 0.73625 | 0.74076
0.49028 | 0.49837 | 0.73612 | 0.74062
0.49013 | 0.4982 | 0.73598 | 0.74054
0.49004 | 0.49801 | 0.73587 | 0.74038
0.48993 | 0.49786 | 0.7357 | 0.74025
0.48983 | 0.49763 | 0.73563 | 0.74017
0.48963 | 0.49745 | 0.73547 | 0.74
0.48945 | 0.49729 | 0.73534 | 0.73991
0.48928 | 0.49707 | 0.73521 | 0.73976
0.48913 | 0.49686 | 0.73509 | 0.73965
0.48889 | 0.49668 | 0.73499 | 0.73957
0.48868 | 0.49652 | 0.73487 | 0.73945
0.48858 | 0.49637 | 0.73472 | 0.73934
0.48842 | 0.49623 | 0.73456 | 0.73923
0.48832 | 0.49608 | 0.73443 | 0.73904
0.48814 | 0.49591 | 0.73433 | 0.73887
0.48795 | 0.49577 | 0.73418 | 0.73879
0.48774 | 0.49557 | 0.73408 | 0.73865
0.48752 | 0.49543 | 0.73395 | 0.73854
0.48739 | 0.49528 | 0.73377 | 0.73837
0.48727 | 0.49509 | 0.73365 | 0.73825
0.48714 | 0.49483 | 0.73351 | 0.73811
0.48686 | 0.49471 | 0.73344 | 0.738
0.48674 | 0.49452 | 0.73331 | 0.73788
0.4866 | 0.49432 | 0.73322 | 0.73778
0.4865 | 0.49418 | 0.73305 | 0.73764
0.48642 | 0.49404 | 0.73287 | 0.73746
0.4863 | 0.49389 | 0.73278 | 0.73731
0.48608 | 0.49364 | 0.73267 | 0.73718
0.48592 | 0.49352 | 0.73256 | 0.73706
0.48572 | 0.49334 | 0.73243 | 0.73694
0.48557 | 0.49321 | 0.73228 | 0.73684
0.4854 | 0.49293 | 0.73217 | 0.73674
0.48521 | 0.49259 | 0.73205 | 0.73654
0.48507 | 0.49245 | 0.73189 | 0.73648
0.48486 | 0.49233 | 0.73171 | 0.73636
0.48474 | 0.49219 | 0.73155 | 0.73623
0.48458 | 0.49207 | 0.73141 | 0.73616
0.48444 | 0.49197 | 0.73123 | 0.73603
0.48429 | 0.49183 | 0.73115 | 0.73594
0.48414 | 0.49169 | 0.731 | 0.73584
0.48402 | 0.49151 | 0.73088 | 0.73571
0.48391 | 0.49133 | 0.73074 | 0.73559
0.48368 | 0.49121 | 0.73066 | 0.73551
0.48347 | 0.49108 | 0.73056 | 0.73529
0.48317 | 0.49097 | 0.73043 | 0.7352
0.48299 | 0.4909 | 0.73032 | 0.73505
0.48281 | 0.49077 | 0.73014 | 0.73494
0.48269 | 0.49065 | 0.73 | 0.73486
0.48259 | 0.4905 | 0.72988 | 0.73472
0.48249 | 0.49036 | 0.72972 | 0.73453
0.48234 | 0.4903 | 0.72958 | 0.73441
0.48218 | 0.49018 | 0.72942 | 0.7343
0.48205 | 0.49004 | 0.72936 | 0.73417
0.48193 | 0.48997 | 0.72927 | 0.73403
0.48173 | 0.48986 | 0.72915 | 0.73396
0.48147 | 0.48968 | 0.72899 | 0.73385
0.48132 | 0.4895 | 0.72882 | 0.73374
0.48123 | 0.48936 | 0.72869 | 0.73362
0.48109 | 0.48926 | 0.72852 | 0.73349
0.48077 | 0.48908 | 0.72833 | 0.73336
0.48068 | 0.48896 | 0.72824 | 0.73321
0.48049 | 0.48879 | 0.72814 | 0.73305
0.48035 | 0.48855 | 0.72795 | 0.73288
0.48016 | 0.48844 | 0.72782 | 0.7327
0.48002 | 0.48838 | 0.72768 | 0.73261
0.47986 | 0.48815 | 0.72753 | 0.73249
0.47977 | 0.48793 | 0.72746 | 0.73236
0.47957 | 0.4878 | 0.72734 | 0.73226
0.47938 | 0.48768 | 0.72723 | 0.73211
0.47928 | 0.48752 | 0.72707 | 0.73198
0.4792 | 0.48729 | 0.72698 | 0.73186
0.4791 | 0.48719 | 0.72687 | 0.73167
0.47886 | 0.48702 | 0.72667 | 0.73158
0.47869 | 0.48688 | 0.72657 | 0.73146
0.4786 | 0.48678 | 0.7264 | 0.73137
0.47836 | 0.4866 | 0.72629 | 0.73121
0.47812 | 0.4865 | 0.72606 | 0.73104
0.47796 | 0.48632 | 0.72597 | 0.73088
0.47784 | 0.4862 | 0.72591 | 0.73074
0.47771 | 0.48599 | 0.72579 | 0.73066
0.47753 | 0.48576 | 0.72567 | 0.73039
0.47737 | 0.48567 | 0.72554 | 0.73027
0.47723 | 0.48548 | 0.72542 | 0.73017
0.47692 | 0.48533 | 0.72523 | 0.73008
0.47678 | 0.48515 | 0.72503 | 0.72997
0.47661 | 0.48502 | 0.72489 | 0.72971
0.4764 | 0.48488 | 0.72469 | 0.72957
0.47629 | 0.48475 | 0.72461 | 0.72944
0.47612 | 0.48467 | 0.72452 | 0.72934
0.47606 | 0.48447 | 0.72434 | 0.72924
0.47594 | 0.48432 | 0.72423 | 0.72911
0.47569 | 0.4842 | 0.72406 | 0.72892
0.47559 | 0.48403 | 0.72389 | 0.7288
0.47549 | 0.48389 | 0.72374 | 0.72868
0.47536 | 0.48375 | 0.7236 | 0.72861
0.47528 | 0.4836 | 0.7235 | 0.72847
0.4751 | 0.48349 | 0.72342 | 0.72837
0.47497 | 0.48331 | 0.72331 | 0.72824
0.47488 | 0.4832 | 0.72321 | 0.72817
0.47469 | 0.48308 | 0.72307 | 0.72801
0.47452 | 0.48286 | 0.72296 | 0.72788
0.47442 | 0.48272 | 0.72282 | 0.72781
0.47434 | 0.48254 | 0.72268 | 0.72765
0.47417 | 0.48238 | 0.72259 | 0.72749
0.47406 | 0.48229 | 0.72246 | 0.72739
0.47395 | 0.48215 | 0.72232 | 0.72726
0.47376 | 0.48205 | 0.72226 | 0.72716
0.47358 | 0.48193 | 0.72214 | 0.72706
0.47336 | 0.48179 | 0.72199 | 0.72693
0.47322 | 0.48169 | 0.72181 | 0.72681
0.473 | 0.48156 | 0.72163 | 0.72667
0.4729 | 0.48138 | 0.72149 | 0.72658
0.47277 | 0.48121 | 0.72134 | 0.72648
0.47266 | 0.48098 | 0.72128 | 0.72642
0.4725 | 0.48093 | 0.72117 | 0.7263
0.47233 | 0.48081 | 0.72106 | 0.72616
0.47225 | 0.4806 | 0.72097 | 0.72606
0.47204 | 0.48051 | 0.72087 | 0.72594
0.47193 | 0.48029 | 0.72077 | 0.72585
0.47181 | 0.48012 | 0.72064 | 0.72572
0.47169 | 0.48002 | 0.72048 | 0.72561
0.47157 | 0.47991 | 0.72038 | 0.72549
0.4715 | 0.47971 | 0.72027 | 0.72537
0.47131 | 0.4796 | 0.72016 | 0.72529
0.47116 | 0.47943 | 0.72006 | 0.72517
0.47095 | 0.47933 | 0.71987 | 0.72504
0.47072 | 0.47928 | 0.71977 | 0.72493
0.47058 | 0.47913 | 0.71959 | 0.72482
0.47041 | 0.47889 | 0.71948 | 0.72467
0.47023 | 0.47876 | 0.71938 | 0.72457
0.46995 | 0.47865 | 0.7192 | 0.72441
0.46984 | 0.47852 | 0.71908 | 0.72427
0.46973 | 0.47841 | 0.71892 | 0.72415
0.46962 | 0.4782 | 0.71882 | 0.72404
0.46953 | 0.47791 | 0.71863 | 0.72391
0.46944 | 0.4777 | 0.71855 | 0.72382
0.46938 | 0.47763 | 0.71843 | 0.72372
0.46921 | 0.47755 | 0.71833 | 0.72365
0.46907 | 0.47739 | 0.7182 | 0.72355
0.46888 | 0.47724 | 0.71814 | 0.72345
0.46877 | 0.47714 | 0.71807 | 0.72334
0.46866 | 0.47704 | 0.71796 | 0.7232
0.46852 | 0.47689 | 0.71783 | 0.72311
0.46844 | 0.47669 | 0.71775 | 0.72301
0.46831 | 0.4766 | 0.71764 | 0.72283
0.4682 | 0.47645 | 0.71753 | 0.72275
0.46803 | 0.4763 | 0.71737 | 0.72264
0.46793 | 0.47618 | 0.71728 | 0.72248
0.46777 | 0.4761 | 0.71712 | 0.72232
0.46762 | 0.47596 | 0.71701 | 0.72223
0.46752 | 0.47584 | 0.71694 | 0.72217
0.46741 | 0.4757 | 0.7168 | 0.72202
0.46723 | 0.47559 | 0.71671 | 0.72196
0.46705 | 0.47549 | 0.71664 | 0.72186
0.46692 | 0.47536 | 0.71652 | 0.72178
0.46678 | 0.47522 | 0.71639 | 0.72164
0.46665 | 0.47507 | 0.71623 | 0.72152
0.4666 | 0.4749 | 0.71615 | 0.72141
0.4665 | 0.47481 | 0.71602 | 0.72128
0.46635 | 0.47475 | 0.71593 | 0.72118
0.46617 | 0.4746 | 0.71583 | 0.72107
0.46606 | 0.47447 | 0.71572 | 0.72096
0.46599 | 0.47435 | 0.71562 | 0.72084
0.46584 | 0.47417 | 0.71554 | 0.72075
0.46564 | 0.47406 | 0.71544 | 0.72069
0.46555 | 0.47392 | 0.71529 | 0.7206
0.46544 | 0.47377 | 0.71514 | 0.72042
0.46526 | 0.47367 | 0.71496 | 0.72025
0.4651 | 0.47357 | 0.71483 | 0.72013
0.46502 | 0.47349 | 0.71473 | 0.71997
0.46492 | 0.47334 | 0.71465 | 0.71984
0.46485 | 0.47319 | 0.71453 | 0.71973
0.4646 | 0.47301 | 0.71441 | 0.71962
0.46437 | 0.47288 | 0.71431 | 0.71949
0.46422 | 0.47274 | 0.71419 | 0.7194
0.46416 | 0.47265 | 0.71409 | 0.71932
0.46402 | 0.47255 | 0.71402 | 0.71923
0.46393 | 0.47248 | 0.7139 | 0.71913
0.46381 | 0.47239 | 0.71376 | 0.71903
0.46373 | 0.47232 | 0.71365 | 0.71896
0.46359 | 0.47224 | 0.71353 | 0.71884
0.4635 | 0.47207 | 0.7134 | 0.71873
0.46343 | 0.47191 | 0.71326 | 0.71864
0.46336 | 0.47184 | 0.71319 | 0.71851
0.46311 | 0.47173 | 0.71304 | 0.71843
0.46301 | 0.47161 | 0.71292 | 0.71834
0.46293 | 0.47147 | 0.71285 | 0.71824
0.4628 | 0.47135 | 0.71274 | 0.71808
0.46272 | 0.47118 | 0.71263 | 0.71797
0.46266 | 0.47099 | 0.71254 | 0.71781
0.46253 | 0.47088 | 0.7124 | 0.71772
0.46244 | 0.47074 | 0.71225 | 0.71761
0.46236 | 0.47061 | 0.71215 | 0.71752
0.4622 | 0.47045 | 0.71208 | 0.71741
0.4621 | 0.47033 | 0.71193 | 0.71735
0.46197 | 0.47023 | 0.71182 | 0.71729
0.46181 | 0.47016 | 0.71171 | 0.71718
0.46158 | 0.46998 | 0.71163 | 0.71713
0.46149 | 0.46983 | 0.71153 | 0.71702
0.46138 | 0.46978 | 0.71143 | 0.71695
0.46113 | 0.46972 | 0.71132 | 0.71682
0.46105 | 0.46961 | 0.71125 | 0.71668
0.46096 | 0.4695 | 0.71118 | 0.71662
0.46076 | 0.46938 | 0.7111 | 0.7165
0.46066 | 0.46929 | 0.71102 | 0.71641
0.46056 | 0.46919 | 0.71095 | 0.71627
0.46046 | 0.46912 | 0.71079 | 0.7162
0.46039 | 0.46898 | 0.71069 | 0.71614
0.46027 | 0.46888 | 0.71056 | 0.71605
0.46012 | 0.46872 | 0.71045 | 0.71591
0.45996 | 0.46851 | 0.71035 | 0.71582
0.45977 | 0.46835 | 0.71024 | 0.71563
0.45962 | 0.46824 | 0.71015 | 0.71558
0.45949 | 0.46814 | 0.71006 | 0.7155
0.45941 | 0.46793 | 0.70996 | 0.71542
0.45932 | 0.46786 | 0.70984 | 0.7153
0.45924 | 0.46778 | 0.70969 | 0.71511
0.45911 | 0.46757 | 0.70963 | 0.71499
0.45895 | 0.4675 | 0.70948 | 0.71488
0.45879 | 0.46739 | 0.70933 | 0.71474
0.4587 | 0.4673 | 0.70925 | 0.7146
0.45861 | 0.46719 | 0.70915 | 0.71452
0.45853 | 0.4671 | 0.70899 | 0.71446
0.45838 | 0.46702 | 0.70887 | 0.71436
0.4583 | 0.46693 | 0.70872 | 0.71428
0.45822 | 0.46682 | 0.70862 | 0.71419
0.45813 | 0.46673 | 0.70852 | 0.7141
0.45799 | 0.46663 | 0.7084 | 0.71398
0.45789 | 0.46652 | 0.70827 | 0.71386
0.4578 | 0.4664 | 0.70813 | 0.71375
0.45764 | 0.46625 | 0.70794 | 0.71368
0.4575 | 0.46611 | 0.70783 | 0.71357
0.45738 | 0.46596 | 0.70769 | 0.71348
0.45727 | 0.46588 | 0.70758 | 0.71335
0.45712 | 0.46579 | 0.70747 | 0.71317
0.45696 | 0.46567 | 0.70739 | 0.71309
0.45686 | 0.46557 | 0.70733 | 0.713
0.45676 | 0.46547 | 0.70719 | 0.71291
0.45666 | 0.46537 | 0.70705 | 0.7128
0.45653 | 0.46526 | 0.70694 | 0.71271
0.45635 | 0.46511 | 0.70688 | 0.71263
0.45622 | 0.46493 | 0.70679 | 0.71252
0.45614 | 0.46485 | 0.70669 | 0.71241
0.45596 | 0.46477 | 0.70658 | 0.71231
0.45589 | 0.46465 | 0.70639 | 0.71224
0.45575 | 0.4645 | 0.70627 | 0.71213
0.45567 | 0.4644 | 0.70614 | 0.71203
0.45557 | 0.46434 | 0.70597 | 0.71191
0.45545 | 0.46427 | 0.70582 | 0.71185
0.45531 | 0.46419 | 0.70573 | 0.71172
0.45514 | 0.46411 | 0.70567 | 0.71155
0.45502 | 0.46405 | 0.70558 | 0.71141
0.4549 | 0.46398 | 0.70552 | 0.71128
0.45482 | 0.4639 | 0.70539 | 0.71116
0.45468 | 0.46382 | 0.70531 | 0.71101
0.45458 | 0.46369 | 0.70517 | 0.71093
0.45441 | 0.46357 | 0.70509 | 0.71087
0.45436 | 0.46338 | 0.70493 | 0.71076
0.45429 | 0.46325 | 0.70484 | 0.71066
0.45421 | 0.46316 | 0.70478 | 0.71058
0.45408 | 0.46307 | 0.70471 | 0.71047
0.45392 | 0.46296 | 0.70464 | 0.71033
0.45382 | 0.46287 | 0.7045 | 0.71027
0.4537 | 0.4628 | 0.7044 | 0.71015
0.45357 | 0.4627 | 0.7043 | 0.71003
0.45353 | 0.46261 | 0.70423 | 0.70995
0.45342 | 0.46257 | 0.70405 | 0.70988
0.4533 | 0.4625 | 0.70399 | 0.70979
0.45321 | 0.46239 | 0.70391 | 0.70968
0.45309 | 0.46229 | 0.70379 | 0.70963
0.45304 | 0.46218 | 0.70368 | 0.70955
0.45292 | 0.46204 | 0.70359 | 0.70947
0.45278 | 0.46196 | 0.7035 | 0.7093
0.45272 | 0.46188 | 0.70338 | 0.70918
0.45262 | 0.46181 | 0.70332 | 0.70908
0.45251 | 0.46169 | 0.70327 | 0.70899
0.45243 | 0.4616 | 0.70316 | 0.70892
0.45236 | 0.46152 | 0.7031 | 0.70883
0.45222 | 0.46138 | 0.70302 | 0.70873
0.45214 | 0.46123 | 0.70294 | 0.7086
0.45205 | 0.46106 | 0.70284 | 0.70848
0.45194 | 0.46097 | 0.70274 | 0.70836
0.45183 | 0.46089 | 0.7026 | 0.70827
0.45172 | 0.46077 | 0.70249 | 0.70817
0.45162 | 0.46058 | 0.70244 | 0.70809
0.45151 | 0.46045 | 0.70226 | 0.70795
0.45131 | 0.46038 | 0.70217 | 0.70787
0.45115 | 0.46017 | 0.70207 | 0.7078
0.45107 | 0.46005 | 0.70195 | 0.70771
0.45101 | 0.45999 | 0.70185 | 0.70764
0.45095 | 0.45993 | 0.70178 | 0.70752
0.45083 | 0.45985 | 0.70165 | 0.70741
0.45072 | 0.45976 | 0.70157 | 0.70727
0.45064 | 0.45962 | 0.70152 | 0.70721
0.45051 | 0.45953 | 0.70141 | 0.70709
0.45042 | 0.45944 | 0.70131 | 0.707
0.45036 | 0.45936 | 0.70127 | 0.70693
0.45024 | 0.45927 | 0.70118 | 0.70685
0.45012 | 0.45922 | 0.70109 | 0.70677
0.45003 | 0.45912 | 0.70102 | 0.7067
0.44994 | 0.45905 | 0.70094 | 0.70658
0.44985 | 0.45895 | 0.70081 | 0.7065
0.44975 | 0.45889 | 0.70072 | 0.70644
0.44961 | 0.45877 | 0.70065 | 0.70637
0.44947 | 0.45872 | 0.70056 | 0.70627
0.44941 | 0.45856 | 0.70042 | 0.70616
0.44932 | 0.45847 | 0.70031 | 0.70607
0.44925 | 0.45841 | 0.70017 | 0.70598
0.44917 | 0.45834 | 0.70008 | 0.70589
0.44905 | 0.45827 | 0.69996 | 0.70578
0.44896 | 0.45818 | 0.69987 | 0.70569
0.44887 | 0.45807 | 0.69973 | 0.70557
0.44872 | 0.45796 | 0.69966 | 0.70548
0.4486 | 0.45791 | 0.69959 | 0.70537
0.44851 | 0.45785 | 0.6995 | 0.70526
0.44845 | 0.4577 | 0.6994 | 0.70515
0.44834 | 0.45763 | 0.69929 | 0.70501
0.44827 | 0.45755 | 0.69916 | 0.70493
0.4482 | 0.45748 | 0.69907 | 0.70484
0.44806 | 0.45736 | 0.69899 | 0.70477
0.44796 | 0.45725 | 0.69895 | 0.70466
0.44788 | 0.45718 | 0.69884 | 0.70455
0.44775 | 0.45706 | 0.69878 | 0.70449
0.44769 | 0.45698 | 0.69869 | 0.70438
0.44763 | 0.45685 | 0.69857 | 0.70431
0.44747 | 0.45672 | 0.69847 | 0.70423
0.44734 | 0.45661 | 0.69835 | 0.70416
0.44726 | 0.45654 | 0.69825 | 0.7041
0.44715 | 0.45645 | 0.69816 | 0.70402
0.44703 | 0.45636 | 0.69808 | 0.70395
0.44697 | 0.4563 | 0.69794 | 0.70388
0.44689 | 0.45621 | 0.6979 | 0.70376
0.44684 | 0.45606 | 0.69779 | 0.70369
0.44674 | 0.4559 | 0.69774 | 0.7036
0.44668 | 0.45579 | 0.69766 | 0.7035
0.44662 | 0.45572 | 0.69755 | 0.7034
0.44656 | 0.45566 | 0.69747 | 0.70331
0.44651 | 0.45551 | 0.69737 | 0.7032
0.44643 | 0.45544 | 0.69728 | 0.70311
0.44633 | 0.45539 | 0.69719 | 0.70305
0.44623 | 0.4553 | 0.69706 | 0.70293
0.44617 | 0.4552 | 0.69696 | 0.70279
0.44607 | 0.45513 | 0.69685 | 0.7027
0.446 | 0.45506 | 0.6968 | 0.70259
0.4459 | 0.45501 | 0.69673 | 0.70249
0.4458 | 0.45492 | 0.69662 | 0.70242
0.44572 | 0.45481 | 0.69653 | 0.70229
0.44564 | 0.45473 | 0.69641 | 0.70219
0.44551 | 0.45464 | 0.69632 | 0.70209
0.44544 | 0.45447 | 0.69625 | 0.70197
0.4453 | 0.45435 | 0.69613 | 0.70189
0.44525 | 0.45424 | 0.69602 | 0.70182
0.44515 | 0.45415 | 0.69592 | 0.70173
0.44499 | 0.45405 | 0.69586 | 0.70164
0.44489 | 0.45393 | 0.69576 | 0.70158
0.44484 | 0.45384 | 0.69571 | 0.7015
0.44478 | 0.45374 | 0.69564 | 0.70143
0.44466 | 0.45368 | 0.69554 | 0.70136
0.44457 | 0.45358 | 0.69547 | 0.70125
0.44452 | 0.45353 | 0.6953 | 0.70115
0.44444 | 0.4534 | 0.69515 | 0.70109
0.44438 | 0.45329 | 0.69507 | 0.70096
0.44428 | 0.45325 | 0.695 | 0.70088
0.44418 | 0.45316 | 0.69487 | 0.70073
0.44408 | 0.45312 | 0.69479 | 0.70066
0.44399 | 0.45306 | 0.69471 | 0.70057
0.44387 | 0.45295 | 0.69463 | 0.70049
0.44378 | 0.4529 | 0.69454 | 0.70038
0.44369 | 0.45284 | 0.6945 | 0.70031
0.44351 | 0.45279 | 0.69443 | 0.70024
0.44334 | 0.45271 | 0.69434 | 0.70018
0.44323 | 0.45263 | 0.69422 | 0.70012
0.44315 | 0.45255 | 0.6941 | 0.70004
0.44307 | 0.45245 | 0.69402 | 0.69995
0.44295 | 0.45235 | 0.69392 | 0.69988
0.44287 | 0.45225 | 0.69383 | 0.69981
0.44274 | 0.45217 | 0.69371 | 0.69972
0.44265 | 0.45206 | 0.69362 | 0.69962
0.4426 | 0.45197 | 0.6935 | 0.69952
0.44252 | 0.45189 | 0.6934 | 0.69944
0.44243 | 0.4518 | 0.6933 | 0.69936
0.44236 | 0.45172 | 0.69324 | 0.6993
0.44223 | 0.45164 | 0.69317 | 0.69921
0.44218 | 0.45152 | 0.69307 | 0.69907
0.44208 | 0.45143 | 0.69297 | 0.69897
0.44202 | 0.45134 | 0.69286 | 0.69892
0.44198 | 0.45129 | 0.69277 | 0.69884
0.44194 | 0.45117 | 0.69269 | 0.69872
0.44184 | 0.45109 | 0.69259 | 0.69867
0.44171 | 0.45103 | 0.69251 | 0.69859
0.44164 | 0.45094 | 0.69244 | 0.69852
0.44158 | 0.4508 | 0.69236 | 0.69845
0.44148 | 0.45072 | 0.6923 | 0.69833
0.44144 | 0.45064 | 0.69223 | 0.69827
0.44134 | 0.45058 | 0.69214 | 0.6982
0.44127 | 0.45053 | 0.69205 | 0.69813
0.44118 | 0.45049 | 0.69197 | 0.69805
0.44109 | 0.45043 | 0.69189 | 0.698
0.44101 | 0.45035 | 0.6918 | 0.6979
0.44096 | 0.45028 | 0.69174 | 0.69783
0.4409 | 0.45022 | 0.69164 | 0.69775
0.44083 | 0.45016 | 0.69155 | 0.69765
0.44075 | 0.45009 | 0.69146 | 0.69754
0.44067 | 0.45001 | 0.69139 | 0.69744
0.44059 | 0.44992 | 0.69132 | 0.69737
0.44054 | 0.44983 | 0.69121 | 0.6973
0.44043 | 0.44979 | 0.69113 | 0.69722
0.44036 | 0.44968 | 0.69105 | 0.69716
0.44026 | 0.44963 | 0.69096 | 0.69711
0.44019 | 0.44958 | 0.69089 | 0.69698
0.44012 | 0.4495 | 0.69079 | 0.69693
0.44008 | 0.44938 | 0.69065 | 0.69686
0.43998 | 0.44934 | 0.69058 | 0.69678
0.43988 | 0.44929 | 0.69043 | 0.69668
0.43977 | 0.44919 | 0.69035 | 0.69661
0.43972 | 0.44914 | 0.69025 | 0.69655
0.43965 | 0.44901 | 0.69016 | 0.69643
0.43951 | 0.44895 | 0.69008 | 0.69636
0.43942 | 0.44884 | 0.68998 | 0.69626
0.43935 | 0.44875 | 0.68984 | 0.69617
0.4393 | 0.4487 | 0.68974 | 0.69612
0.43922 | 0.44865 | 0.68966 | 0.69605
0.43917 | 0.44854 | 0.6896 | 0.69599
0.43911 | 0.44849 | 0.68953 | 0.69587
0.43906 | 0.44838 | 0.68942 | 0.69574
0.43899 | 0.44829 | 0.68932 | 0.69565
0.43894 | 0.44816 | 0.68926 | 0.69553
0.43888 | 0.44809 | 0.68918 | 0.69544
0.43879 | 0.44801 | 0.68906 | 0.69538
0.43871 | 0.44792 | 0.68898 | 0.69529
0.43863 | 0.44784 | 0.68882 | 0.6952
0.43859 | 0.4478 | 0.68877 | 0.69512
0.43852 | 0.4477 | 0.68872 | 0.69505
0.43844 | 0.44766 | 0.68865 | 0.69495
0.43839 | 0.44762 | 0.68857 | 0.69488
0.43829 | 0.44755 | 0.68849 | 0.69479
0.43822 | 0.44747 | 0.6884 | 0.69471
0.43815 | 0.44743 | 0.68835 | 0.69465
0.43805 | 0.44738 | 0.68825 | 0.69457
0.43798 | 0.44726 | 0.68813 | 0.6945
0.43792 | 0.44718 | 0.68807 | 0.69439
0.43785 | 0.44708 | 0.68796 | 0.69432
0.43773 | 0.44701 | 0.68789 | 0.69425
0.43768 | 0.44689 | 0.68784 | 0.6942
0.43753 | 0.44685 | 0.68779 | 0.69416
0.43744 | 0.44676 | 0.6877 | 0.69408
0.43737 | 0.44672 | 0.68761 | 0.694
0.43729 | 0.44668 | 0.68755 | 0.69391
0.43721 | 0.44663 | 0.68747 | 0.6938
0.43715 | 0.44658 | 0.68736 | 0.69367
0.43702 | 0.44649 | 0.68729 | 0.69359
0.43696 | 0.4464 | 0.68723 | 0.69348
0.43691 | 0.44635 | 0.68714 | 0.69342
0.43683 | 0.44627 | 0.68704 | 0.69332
0.43678 | 0.4462 | 0.68696 | 0.69323
0.43671 | 0.44614 | 0.68686 | 0.69315
0.43664 | 0.44609 | 0.68674 | 0.69307
0.43653 | 0.44603 | 0.68668 | 0.693
0.43648 | 0.44596 | 0.68659 | 0.69294
0.43643 | 0.44591 | 0.68649 | 0.69287
0.43636 | 0.44583 | 0.68637 | 0.69279
0.4363 | 0.44574 | 0.68626 | 0.69273
0.43626 | 0.44562 | 0.68619 | 0.69265
0.43621 | 0.44558 | 0.6861 | 0.69256
0.43615 | 0.44548 | 0.68605 | 0.69243
0.43607 | 0.44542 | 0.68599 | 0.69233
0.43602 | 0.44532 | 0.68593 | 0.69226
0.43597 | 0.44527 | 0.68586 | 0.69216
0.43588 | 0.44522 | 0.6858 | 0.69204
0.43582 | 0.44514 | 0.68568 | 0.69194
0.43576 | 0.44504 | 0.68563 | 0.69187
0.4357 | 0.445 | 0.68555 | 0.69181
0.43561 | 0.44492 | 0.68544 | 0.69175
0.43554 | 0.44484 | 0.68538 | 0.69166
0.4355 | 0.44477 | 0.68532 | 0.69161
0.43542 | 0.44468 | 0.68525 | 0.69154
0.43531 | 0.44464 | 0.68516 | 0.69146
0.43526 | 0.44457 | 0.68504 | 0.69141
0.4352 | 0.44451 | 0.68496 | 0.69134
0.43514 | 0.44444 | 0.68491 | 0.69129
0.4351 | 0.44438 | 0.68482 | 0.69122
0.43504 | 0.44431 | 0.68472 | 0.69114
0.43501 | 0.44424 | 0.68464 | 0.69106
0.43491 | 0.44413 | 0.68457 | 0.69099
0.4348 | 0.44407 | 0.68447 | 0.69093
0.43473 | 0.44403 | 0.68438 | 0.69086
0.43468 | 0.44391 | 0.68434 | 0.69078
0.43459 | 0.44386 | 0.68425 | 0.69073
0.43453 | 0.44372 | 0.68419 | 0.69064
0.43448 | 0.44364 | 0.6841 | 0.69053
0.43441 | 0.44354 | 0.684 | 0.69044
0.43435 | 0.4435 | 0.68389 | 0.69039
0.43429 | 0.44347 | 0.6838 | 0.69031
0.43423 | 0.44338 | 0.68371 | 0.69027
0.43419 | 0.44333 | 0.68367 | 0.69021
0.43411 | 0.44327 | 0.68362 | 0.69011
0.43398 | 0.44322 | 0.68348 | 0.69006
0.4339 | 0.44317 | 0.68342 | 0.69
0.43382 | 0.44309 | 0.68336 | 0.68991
0.43375 | 0.44304 | 0.68329 | 0.6898
0.43369 | 0.443 | 0.6832 | 0.6897
0.43363 | 0.44294 | 0.6831 | 0.6896
0.43358 | 0.44287 | 0.68301 | 0.68954
0.43355 | 0.44275 | 0.68294 | 0.68947
0.43349 | 0.4427 | 0.68291 | 0.68938
0.43343 | 0.44261 | 0.68283 | 0.6893
0.43333 | 0.44256 | 0.68272 | 0.68917
0.43327 | 0.44252 | 0.68259 | 0.68904
0.43321 | 0.44244 | 0.6825 | 0.68898
0.43312 | 0.44236 | 0.68242 | 0.68889
0.43305 | 0.44229 | 0.68232 | 0.68876
0.43293 | 0.44218 | 0.68225 | 0.68868
0.43282 | 0.44212 | 0.68216 | 0.68861
0.43273 | 0.44204 | 0.68207 | 0.68855
0.43268 | 0.44192 | 0.68198 | 0.68846
0.43256 | 0.44184 | 0.68188 | 0.68834
0.43248 | 0.44178 | 0.68177 | 0.68826
0.43242 | 0.44171 | 0.68168 | 0.68818
0.43235 | 0.44166 | 0.68161 | 0.68805
0.4323 | 0.44161 | 0.68152 | 0.68799
0.43226 | 0.44157 | 0.68143 | 0.68789
0.4322 | 0.4415 | 0.68134 | 0.68781
0.43213 | 0.44138 | 0.68125 | 0.68775
0.43208 | 0.44134 | 0.68117 | 0.68764
0.43198 | 0.44127 | 0.68108 | 0.68754
0.43194 | 0.44122 | 0.68103 | 0.6875
0.43185 | 0.44115 | 0.68098 | 0.68742
0.43175 | 0.44109 | 0.68087 | 0.68736
0.43171 | 0.44102 | 0.68078 | 0.68728
0.43164 | 0.44096 | 0.6807 | 0.68716
0.43158 | 0.4409 | 0.68062 | 0.68707
0.43148 | 0.4408 | 0.68056 | 0.687
0.43138 | 0.44072 | 0.68047 | 0.68692
0.4313 | 0.44065 | 0.6804 | 0.68684
0.43119 | 0.44058 | 0.68036 | 0.68675
0.43116 | 0.44052 | 0.68029 | 0.6867
0.43109 | 0.44046 | 0.68023 | 0.68664
0.43102 | 0.4404 | 0.68017 | 0.68656
0.43097 | 0.44034 | 0.68012 | 0.68649
0.43089 | 0.44026 | 0.68006 | 0.68645
0.43083 | 0.44019 | 0.67996 | 0.68637
0.43077 | 0.44011 | 0.6799 | 0.68631
0.43071 | 0.44006 | 0.67986 | 0.68624
0.43068 | 0.43997 | 0.6798 | 0.68618
0.43062 | 0.43989 | 0.67974 | 0.68611
0.43057 | 0.43983 | 0.67967 | 0.68603
0.43047 | 0.43979 | 0.67957 | 0.68598
0.4304 | 0.43972 | 0.67952 | 0.68593
0.43034 | 0.43965 | 0.67941 | 0.68587
0.43027 | 0.43958 | 0.6793 | 0.68581
0.43021 | 0.43954 | 0.67924 | 0.68573
0.43013 | 0.43946 | 0.67915 | 0.68569
0.43008 | 0.4394 | 0.6791 | 0.68563
0.42998 | 0.4393 | 0.67904 | 0.68555
0.42993 | 0.43925 | 0.67896 | 0.68547
0.42986 | 0.43917 | 0.67885 | 0.68541
0.4298 | 0.43911 | 0.67874 | 0.68533
0.42976 | 0.43904 | 0.67867 | 0.68528
0.4297 | 0.43897 | 0.67862 | 0.68522
0.42962 | 0.43889 | 0.67853 | 0.68511
0.42956 | 0.43885 | 0.67843 | 0.68506
0.42947 | 0.43877 | 0.67836 | 0.68502
0.42941 | 0.43871 | 0.67829 | 0.68496
0.42935 | 0.43865 | 0.67822 | 0.68491
0.42927 | 0.43861 | 0.67815 | 0.68481
0.42922 | 0.43857 | 0.67805 | 0.68475
0.42912 | 0.43851 | 0.67796 | 0.6847
0.42905 | 0.43843 | 0.67787 | 0.68461
0.42896 | 0.43836 | 0.67779 | 0.68453
0.4289 | 0.43827 | 0.67774 | 0.68444
0.42884 | 0.4382 | 0.67767 | 0.68435
0.42874 | 0.43813 | 0.67761 | 0.68425
0.42866 | 0.43806 | 0.6775 | 0.68421
0.42862 | 0.438 | 0.67744 | 0.68415
0.42859 | 0.43789 | 0.67738 | 0.68408
0.42855 | 0.43785 | 0.6773 | 0.68401
0.42848 | 0.43779 | 0.6772 | 0.68391
0.42842 | 0.43774 | 0.67708 | 0.68385
0.4283 | 0.43767 | 0.677 | 0.68378
0.42824 | 0.43761 | 0.67695 | 0.68373
0.42815 | 0.43757 | 0.6769 | 0.68368
0.42811 | 0.4375 | 0.67681 | 0.68361
0.42802 | 0.43741 | 0.67673 | 0.68351
0.42796 | 0.43733 | 0.67666 | 0.68342
0.42792 | 0.43722 | 0.67656 | 0.68328
0.42785 | 0.43718 | 0.67644 | 0.6832
0.42776 | 0.43714 | 0.67633 | 0.68314
0.42773 | 0.43704 | 0.67624 | 0.68307
0.42765 | 0.43695 | 0.67613 | 0.683
0.4276 | 0.43688 | 0.67605 | 0.68294
0.42755 | 0.43684 | 0.67597 | 0.68289
0.42748 | 0.43678 | 0.6759 | 0.68282
0.42741 | 0.43669 | 0.67585 | 0.68274
0.42736 | 0.43661 | 0.67577 | 0.68267
0.42728 | 0.43654 | 0.67569 | 0.6826
0.42721 | 0.43647 | 0.67562 | 0.68256
0.42712 | 0.43639 | 0.67552 | 0.68249
0.42705 | 0.43633 | 0.67547 | 0.68243
0.42699 | 0.43626 | 0.67539 | 0.68236
0.42692 | 0.43619 | 0.67534 | 0.68228
0.42688 | 0.43616 | 0.67524 | 0.68222
0.42681 | 0.43607 | 0.67516 | 0.68216
0.42672 | 0.43602 | 0.67507 | 0.6821
0.42666 | 0.43596 | 0.675 | 0.68204
0.42652 | 0.4359 | 0.6749 | 0.68199
0.42646 | 0.43585 | 0.67485 | 0.68192
0.42631 | 0.4358 | 0.67475 | 0.68187
0.42626 | 0.43572 | 0.67471 | 0.6818
0.42621 | 0.43568 | 0.67463 | 0.68169
0.42619 | 0.43561 | 0.67453 | 0.6816
0.42611 | 0.43553 | 0.67449 | 0.68151
0.42605 | 0.43548 | 0.67441 | 0.68142
0.42597 | 0.43541 | 0.67431 | 0.68135
0.42588 | 0.43534 | 0.67422 | 0.68128
0.4258 | 0.43527 | 0.67414 | 0.68121
0.42576 | 0.43519 | 0.67408 | 0.68113
0.42569 | 0.43512 | 0.67402 | 0.68101
0.42562 | 0.43508 | 0.67396 | 0.68089
0.42557 | 0.43497 | 0.67389 | 0.68084
0.4255 | 0.43488 | 0.67382 | 0.68078
0.42545 | 0.43482 | 0.67377 | 0.68068
0.42537 | 0.43472 | 0.6737 | 0.68064
0.42531 | 0.43469 | 0.67363 | 0.68055
0.42526 | 0.43465 | 0.67353 | 0.68049
0.42519 | 0.43461 | 0.67348 | 0.68043
0.42512 | 0.43454 | 0.6734 | 0.68032
0.42507 | 0.43448 | 0.67328 | 0.68022
0.425 | 0.43441 | 0.67321 | 0.6802
0.42495 | 0.43434 | 0.67309 | 0.68007
0.42487 | 0.43432 | 0.67299 | 0.67998
0.42479 | 0.43424 | 0.67294 | 0.67987
0.42472 | 0.43419 | 0.67286 | 0.67978
0.42467 | 0.43416 | 0.6728 | 0.67975
0.42461 | 0.43409 | 0.6727 | 0.6797
0.42457 | 0.43402 | 0.67263 | 0.67962
0.42452 | 0.43394 | 0.67252 | 0.67957
0.42449 | 0.43387 | 0.67248 | 0.67949
0.42445 | 0.4338 | 0.67239 | 0.67944
0.4244 | 0.43375 | 0.67234 | 0.67942
0.42433 | 0.4337 | 0.67227 | 0.67936
0.42429 | 0.43363 | 0.6722 | 0.67928
0.42422 | 0.43355 | 0.67211 | 0.67921
0.42418 | 0.43348 | 0.67204 | 0.67913
0.42412 | 0.43344 | 0.67199 | 0.67905
0.42406 | 0.43336 | 0.67189 | 0.67897
0.42398 | 0.43331 | 0.6718 | 0.67889
0.42394 | 0.43326 | 0.67174 | 0.67878
0.42384 | 0.43322 | 0.67165 | 0.67873
0.4238 | 0.43317 | 0.67156 | 0.67866
0.42373 | 0.43311 | 0.67151 | 0.67857
0.42368 | 0.43302 | 0.67143 | 0.67847
0.42359 | 0.43293 | 0.67137 | 0.67839
0.42351 | 0.4329 | 0.67127 | 0.67831
0.42343 | 0.43281 | 0.67121 | 0.67824
0.42338 | 0.43274 | 0.67114 | 0.67817
0.42335 | 0.43267 | 0.67109 | 0.67807
0.42328 | 0.43261 | 0.67103 | 0.67798
0.42322 | 0.43257 | 0.67094 | 0.67792
0.42316 | 0.4325 | 0.67089 | 0.67783
0.42306 | 0.43246 | 0.67083 | 0.67775
0.42299 | 0.43241 | 0.67079 | 0.67772
0.42294 | 0.43231 | 0.67073 | 0.67761
0.42289 | 0.43227 | 0.67066 | 0.67751
0.42286 | 0.43219 | 0.6706 | 0.67746
0.42276 | 0.43215 | 0.67052 | 0.67738
0.42268 | 0.43209 | 0.67044 | 0.67734
0.42263 | 0.43202 | 0.67041 | 0.67728
0.42254 | 0.43196 | 0.67036 | 0.67721
0.42245 | 0.4319 | 0.67029 | 0.67714
0.42238 | 0.43187 | 0.67023 | 0.67706
0.42233 | 0.43181 | 0.67019 | 0.67696
0.42224 | 0.43177 | 0.67012 | 0.67693
0.42219 | 0.43173 | 0.67003 | 0.67686
0.42215 | 0.43165 | 0.66998 | 0.6768
0.42204 | 0.43159 | 0.66989 | 0.67671
0.42194 | 0.43153 | 0.66983 | 0.67668
0.42189 | 0.43148 | 0.66975 | 0.67659
0.4218 | 0.43138 | 0.6697 | 0.67653
0.42172 | 0.43132 | 0.66965 | 0.67647
0.42166 | 0.43127 | 0.66959 | 0.67642
0.42159 | 0.43121 | 0.66954 | 0.67636
0.4215 | 0.43117 | 0.66942 | 0.67631
0.42142 | 0.43112 | 0.66936 | 0.67625
0.42135 | 0.43104 | 0.6693 | 0.67619
0.42131 | 0.43097 | 0.66924 | 0.67613
0.42126 | 0.43092 | 0.66915 | 0.67606
0.42123 | 0.43085 | 0.66909 | 0.676
0.42119 | 0.43078 | 0.66902 | 0.67593
0.42114 | 0.43072 | 0.66897 | 0.67588
0.42109 | 0.43062 | 0.66888 | 0.67584
0.42103 | 0.43057 | 0.66884 | 0.67578
0.42097 | 0.43048 | 0.6688 | 0.67569
0.42092 | 0.43044 | 0.66875 | 0.6756
0.42088 | 0.43036 | 0.66866 | 0.67553
0.4208 | 0.43029 | 0.66861 | 0.67549
0.42074 | 0.43021 | 0.66852 | 0.67544
0.42068 | 0.43015 | 0.66843 | 0.67533
0.42062 | 0.4301 | 0.66837 | 0.67529
0.42056 | 0.43003 | 0.66831 | 0.67524
0.42053 | 0.42995 | 0.66826 | 0.67518
0.42048 | 0.4299 | 0.66816 | 0.67513
0.42041 | 0.42986 | 0.66811 | 0.67508
0.42035 | 0.42979 | 0.66799 | 0.67503
0.42031 | 0.42972 | 0.66796 | 0.67497
0.42026 | 0.42966 | 0.66788 | 0.67488
0.42015 | 0.42961 | 0.66781 | 0.67482
0.4201 | 0.42954 | 0.66775 | 0.67478
0.42004 | 0.4295 | 0.66769 | 0.6747
0.41999 | 0.42944 | 0.66762 | 0.67464
0.41997 | 0.42939 | 0.66753 | 0.67459
0.41989 | 0.42936 | 0.66746 | 0.67455
0.41984 | 0.42929 | 0.66741 | 0.6745
0.41976 | 0.42922 | 0.66734 | 0.67441
0.41963 | 0.42915 | 0.66725 | 0.67435
0.41958 | 0.42908 | 0.66717 | 0.67426
0.41953 | 0.42898 | 0.66711 | 0.6742
0.41945 | 0.42891 | 0.66708 | 0.67414
0.41942 | 0.42885 | 0.66697 | 0.67407
0.41935 | 0.42879 | 0.6669 | 0.67402
0.41932 | 0.42872 | 0.66685 | 0.67397
0.41928 | 0.42865 | 0.66677 | 0.67392
0.41923 | 0.42856 | 0.66669 | 0.67383
0.41918 | 0.42846 | 0.66663 | 0.67373
0.41912 | 0.42841 | 0.66657 | 0.67367
0.41906 | 0.42838 | 0.66647 | 0.67363
0.41903 | 0.4283 | 0.66639 | 0.67356
0.41899 | 0.42827 | 0.66634 | 0.67353
0.41892 | 0.42822 | 0.66625 | 0.67346
0.41888 | 0.42816 | 0.66621 | 0.67338
0.41884 | 0.42809 | 0.66614 | 0.67335
0.41876 | 0.42804 | 0.66609 | 0.67328
0.41871 | 0.42799 | 0.66601 | 0.67319
0.41866 | 0.42795 | 0.66595 | 0.67313
0.41861 | 0.42786 | 0.66589 | 0.67306
0.41856 | 0.4278 | 0.66582 | 0.67298
0.41853 | 0.42777 | 0.66574 | 0.67293
0.4185 | 0.42772 | 0.66568 | 0.67285
0.41842 | 0.42762 | 0.66562 | 0.67277
0.41838 | 0.42758 | 0.66554 | 0.67269
0.41834 | 0.4275 | 0.66551 | 0.67263
0.41826 | 0.42745 | 0.66543 | 0.67257
0.41819 | 0.42739 | 0.66536 | 0.67251
0.41814 | 0.42733 | 0.6653 | 0.67243
0.41808 | 0.42726 | 0.66525 | 0.67235
0.418 | 0.42718 | 0.66519 | 0.67227
0.41795 | 0.42712 | 0.66512 | 0.67223
0.41792 | 0.42708 | 0.66507 | 0.67218
0.41785 | 0.42702 | 0.66501 | 0.67212
0.41779 | 0.42697 | 0.66494 | 0.67206
0.41775 | 0.4269 | 0.66486 | 0.67197
0.41771 | 0.42684 | 0.66483 | 0.67194
0.41765 | 0.42678 | 0.66477 | 0.67188
0.4176 | 0.42674 | 0.66472 | 0.67183
0.41752 | 0.42669 | 0.66465 | 0.67179
0.41747 | 0.42664 | 0.66459 | 0.67171
0.41744 | 0.42658 | 0.66453 | 0.67167
0.41737 | 0.4265 | 0.66448 | 0.67162
0.41734 | 0.42646 | 0.66442 | 0.67159
0.41728 | 0.42639 | 0.66433 | 0.67155
0.41721 | 0.42635 | 0.66428 | 0.67149
0.41713 | 0.42629 | 0.66421 | 0.67144
0.41708 | 0.42626 | 0.66415 | 0.67139
0.41702 | 0.42622 | 0.66406 | 0.67135
0.41695 | 0.42616 | 0.664 | 0.6713
0.4169 | 0.42609 | 0.66393 | 0.67124
0.41685 | 0.42599 | 0.66388 | 0.67119
0.4168 | 0.42596 | 0.66382 | 0.67116
0.41675 | 0.42591 | 0.66376 | 0.67108
0.41671 | 0.42585 | 0.66373 | 0.67102
0.4166 | 0.42581 | 0.66367 | 0.67094
0.41653 | 0.42577 | 0.66361 | 0.67089
0.41649 | 0.42571 | 0.66356 | 0.67083
0.4164 | 0.42566 | 0.6635 | 0.67075
0.41633 | 0.4256 | 0.66345 | 0.67066
0.41626 | 0.42554 | 0.66339 | 0.6706
0.4162 | 0.42551 | 0.66336 | 0.67056
0.41614 | 0.42548 | 0.66329 | 0.6705
0.41609 | 0.42543 | 0.66324 | 0.67043
0.41604 | 0.42539 | 0.66318 | 0.67039
0.41601 | 0.42534 | 0.66313 | 0.67032
0.41596 | 0.42526 | 0.66308 | 0.67028
0.41591 | 0.42521 | 0.66304 | 0.6702
0.41587 | 0.42516 | 0.66296 | 0.67015
0.41585 | 0.42512 | 0.6629 | 0.67008
0.41582 | 0.42507 | 0.66285 | 0.67
0.41577 | 0.42503 | 0.66282 | 0.66991
0.41572 | 0.42496 | 0.66274 | 0.66987
0.41568 | 0.42492 | 0.66265 | 0.66982
0.41562 | 0.42487 | 0.66261 | 0.66977
0.41555 | 0.42484 | 0.66252 | 0.66973
0.41551 | 0.42481 | 0.66245 | 0.66967
0.41547 | 0.42477 | 0.66241 | 0.66961
0.41539 | 0.42472 | 0.66234 | 0.66957
0.41533 | 0.42465 | 0.66228 | 0.66951
0.41524 | 0.4246 | 0.66223 | 0.66946
0.41518 | 0.42455 | 0.66218 | 0.6694
0.41514 | 0.42449 | 0.66212 | 0.66929
0.41509 | 0.42445 | 0.66205 | 0.66923
0.41502 | 0.42438 | 0.66195 | 0.66917
0.41497 | 0.42431 | 0.66189 | 0.66908
0.41491 | 0.42426 | 0.66184 | 0.66902
0.41487 | 0.42424 | 0.66179 | 0.66897
0.41481 | 0.42417 | 0.66172 | 0.66889
0.41475 | 0.42411 | 0.66166 | 0.66883
0.41471 | 0.42407 | 0.66156 | 0.66876
0.41465 | 0.424 | 0.66149 | 0.66872
0.41461 | 0.42397 | 0.66141 | 0.66865
0.41453 | 0.42393 | 0.66133 | 0.66862
0.4145 | 0.42387 | 0.66128 | 0.66855
0.41442 | 0.4238 | 0.66124 | 0.66853
0.41435 | 0.42377 | 0.66116 | 0.66849
0.41427 | 0.42374 | 0.66111 | 0.6684
0.41421 | 0.4237 | 0.66105 | 0.66834
0.41413 | 0.42366 | 0.66101 | 0.66829
0.4141 | 0.42361 | 0.66095 | 0.66822
0.41406 | 0.42355 | 0.6609 | 0.66815
0.41403 | 0.4235 | 0.6608 | 0.66809
0.41395 | 0.42341 | 0.66074 | 0.66802
0.4139 | 0.42336 | 0.66071 | 0.66796
0.41383 | 0.42331 | 0.66062 | 0.66787
0.41377 | 0.42328 | 0.66055 | 0.66782
0.41372 | 0.42323 | 0.66049 | 0.66777
0.41365 | 0.42317 | 0.66043 | 0.66771
0.41361 | 0.42311 | 0.66035 | 0.66764
0.41352 | 0.42306 | 0.66029 | 0.66759
0.41344 | 0.42302 | 0.6602 | 0.66753
0.41337 | 0.423 | 0.66015 | 0.66751
0.41329 | 0.42297 | 0.66006 | 0.66747
0.41326 | 0.42291 | 0.65997 | 0.66742
0.41319 | 0.42285 | 0.65989 | 0.66734
0.41312 | 0.4228 | 0.65986 | 0.66725
0.41306 | 0.42274 | 0.65981 | 0.66717
0.413 | 0.42269 | 0.65976 | 0.66712
0.41293 | 0.42264 | 0.65971 | 0.66704
0.41289 | 0.42258 | 0.65967 | 0.66696
0.41281 | 0.42252 | 0.65963 | 0.66691
0.41278 | 0.42247 | 0.65958 | 0.66686
0.41272 | 0.42242 | 0.65953 | 0.66679
0.41267 | 0.42232 | 0.65944 | 0.66674
0.41261 | 0.42229 | 0.65936 | 0.66667
0.41255 | 0.42224 | 0.65935 | 0.66663
0.41249 | 0.42219 | 0.6593 | 0.66657
0.41246 | 0.42214 | 0.65925 | 0.66648
0.41243 | 0.42211 | 0.65921 | 0.66643
0.4124 | 0.42206 | 0.65915 | 0.66639
0.41238 | 0.422 | 0.6591 | 0.66637
0.41233 | 0.42195 | 0.659 | 0.66631
0.41231 | 0.42186 | 0.65894 | 0.66623
0.41226 | 0.42182 | 0.65889 | 0.66614
0.41215 | 0.42178 | 0.65884 | 0.66611
0.41207 | 0.42172 | 0.65881 | 0.66603
0.41202 | 0.42165 | 0.65877 | 0.66593
0.41196 | 0.42157 | 0.65869 | 0.66586
0.41191 | 0.4215 | 0.65859 | 0.66578
0.41183 | 0.42145 | 0.65853 | 0.66572
0.41177 | 0.42143 | 0.65846 | 0.66567
0.41174 | 0.42136 | 0.65843 | 0.66563
0.4117 | 0.42127 | 0.65838 | 0.66558
0.41165 | 0.42122 | 0.65832 | 0.66552
0.41159 | 0.42117 | 0.65826 | 0.66544
0.41154 | 0.42112 | 0.65819 | 0.66541
0.41152 | 0.42107 | 0.65811 | 0.66539
0.4115 | 0.42103 | 0.65806 | 0.66531
0.41146 | 0.42099 | 0.658 | 0.66524
0.4114 | 0.42096 | 0.65794 | 0.66519
0.41137 | 0.42091 | 0.65787 | 0.66514
0.41135 | 0.42086 | 0.65782 | 0.66508
0.4113 | 0.42081 | 0.65779 | 0.66504
0.41126 | 0.42076 | 0.65774 | 0.66498
0.4112 | 0.4207 | 0.65766 | 0.66488
0.41114 | 0.42068 | 0.65758 | 0.66479
0.41108 | 0.42064 | 0.65749 | 0.66473
0.41102 | 0.42058 | 0.65741 | 0.66465
0.41098 | 0.42055 | 0.65737 | 0.66456
0.41091 | 0.42052 | 0.6573 | 0.6645
0.41088 | 0.42048 | 0.65723 | 0.66446
0.41084 | 0.42043 | 0.65719 | 0.66443
0.41078 | 0.42038 | 0.65714 | 0.66437
0.41075 | 0.42032 | 0.65704 | 0.66433
0.41069 | 0.42027 | 0.65697 | 0.66427
0.41064 | 0.42024 | 0.65691 | 0.66422
0.41058 | 0.42019 | 0.65687 | 0.66419
0.41055 | 0.42009 | 0.65679 | 0.66411
0.41051 | 0.42006 | 0.65671 | 0.66404
0.41045 | 0.42001 | 0.65667 | 0.664
0.41041 | 0.41997 | 0.65663 | 0.66393
0.41036 | 0.41992 | 0.65657 | 0.66388
0.41033 | 0.41988 | 0.65648 | 0.66384
0.41025 | 0.41986 | 0.65643 | 0.66379
0.41021 | 0.41983 | 0.65633 | 0.66375
0.41014 | 0.41979 | 0.65627 | 0.66369
0.4101 | 0.41974 | 0.65623 | 0.66365
0.41003 | 0.41969 | 0.65615 | 0.66357
0.40999 | 0.41965 | 0.65609 | 0.66349
0.40994 | 0.41961 | 0.65603 | 0.66343
0.40989 | 0.41954 | 0.65596 | 0.66337
0.40985 | 0.4195 | 0.65585 | 0.6633
0.40975 | 0.41941 | 0.65579 | 0.66327
0.40969 | 0.41936 | 0.65571 | 0.66324
0.40964 | 0.4193 | 0.65568 | 0.66319
0.4096 | 0.41924 | 0.65562 | 0.66312
0.40956 | 0.41921 | 0.65554 | 0.66306
0.40951 | 0.41913 | 0.65551 | 0.66301
0.40947 | 0.41909 | 0.65546 | 0.66298
0.40942 | 0.41905 | 0.65541 | 0.66293
0.40939 | 0.41899 | 0.65538 | 0.66286
0.40932 | 0.41894 | 0.6553 | 0.66282
0.40924 | 0.4189 | 0.65527 | 0.66278
0.40921 | 0.41886 | 0.65522 | 0.66274
0.40916 | 0.41879 | 0.65516 | 0.6627
0.4091 | 0.4187 | 0.65513 | 0.66264
0.409 | 0.41864 | 0.65508 | 0.66259
0.40897 | 0.41857 | 0.65502 | 0.66252
0.40891 | 0.4185 | 0.65495 | 0.66247
0.40887 | 0.41848 | 0.65492 | 0.66242
0.40883 | 0.41844 | 0.65486 | 0.66237
0.40877 | 0.4184 | 0.65482 | 0.6623
0.40874 | 0.41834 | 0.65479 | 0.6622
0.40869 | 0.41828 | 0.65475 | 0.66214
0.40863 | 0.41825 | 0.65469 | 0.66211
0.40858 | 0.41821 | 0.65463 | 0.66205
0.40855 | 0.41817 | 0.65459 | 0.66201
0.40854 | 0.41813 | 0.65453 | 0.66197
0.40848 | 0.41809 | 0.65446 | 0.66194
0.40846 | 0.41803 | 0.65442 | 0.66189
0.40842 | 0.418 | 0.65437 | 0.66184
0.40835 | 0.41796 | 0.6543 | 0.66181
0.40831 | 0.41793 | 0.65424 | 0.66176
0.40826 | 0.41789 | 0.6542 | 0.66172
0.40816 | 0.41782 | 0.65416 | 0.66168
0.40808 | 0.41776 | 0.65412 | 0.66162
0.40802 | 0.4177 | 0.65409 | 0.66155
0.40798 | 0.41765 | 0.65405 | 0.6615
0.40795 | 0.41757 | 0.65397 | 0.66144
0.40789 | 0.41753 | 0.6539 | 0.66139
0.40782 | 0.41751 | 0.65381 | 0.66134
0.40779 | 0.41746 | 0.65377 | 0.66128
0.40773 | 0.4174 | 0.65372 | 0.66122
0.40769 | 0.41733 | 0.65366 | 0.66119
0.40764 | 0.41729 | 0.65357 | 0.66115
0.40759 | 0.41724 | 0.65347 | 0.6611
0.40754 | 0.41719 | 0.65343 | 0.66103
0.40749 | 0.41714 | 0.65339 | 0.66096
0.40744 | 0.4171 | 0.65333 | 0.66088
0.4074 | 0.41703 | 0.65329 | 0.66084
0.40738 | 0.41699 | 0.65325 | 0.66078
0.40735 | 0.41694 | 0.6532 | 0.66073
0.40732 | 0.41687 | 0.65314 | 0.66066
0.4073 | 0.41681 | 0.65312 | 0.66061
0.40723 | 0.41677 | 0.65303 | 0.66054
0.4072 | 0.41671 | 0.65294 | 0.66051
0.40715 | 0.41665 | 0.65288 | 0.66047
0.40712 | 0.4166 | 0.65284 | 0.66043
0.40706 | 0.41655 | 0.6528 | 0.66037
0.40703 | 0.4165 | 0.65275 | 0.66032
0.40701 | 0.41645 | 0.65268 | 0.66028
0.40698 | 0.41639 | 0.65263 | 0.66023
0.40694 | 0.41634 | 0.65259 | 0.66018
0.4069 | 0.41629 | 0.65256 | 0.66015
0.40684 | 0.41624 | 0.6525 | 0.66006
0.40679 | 0.41617 | 0.65245 | 0.66002
0.40674 | 0.41614 | 0.6524 | 0.65996
0.4067 | 0.41609 | 0.65233 | 0.65989
0.40666 | 0.41608 | 0.65229 | 0.65982
0.40661 | 0.41602 | 0.65224 | 0.65978
0.40657 | 0.41598 | 0.65218 | 0.6597
0.4065 | 0.41595 | 0.65214 | 0.65963
0.40645 | 0.41589 | 0.6521 | 0.65957
0.4064 | 0.41583 | 0.65201 | 0.65952
0.40637 | 0.41579 | 0.65192 | 0.65946
0.40634 | 0.41575 | 0.65188 | 0.65938
0.4063 | 0.41572 | 0.65183 | 0.65929
0.40627 | 0.41569 | 0.65177 | 0.65922
0.40624 | 0.41563 | 0.65171 | 0.65918
0.40621 | 0.4156 | 0.65166 | 0.65914
0.40615 | 0.41558 | 0.65163 | 0.65909
0.40608 | 0.41556 | 0.65159 | 0.65904
0.40604 | 0.41553 | 0.65152 | 0.65899
0.40601 | 0.41549 | 0.6515 | 0.65894
0.40597 | 0.41545 | 0.65144 | 0.65891
0.4059 | 0.41538 | 0.65139 | 0.65883
0.40586 | 0.41535 | 0.65135 | 0.65878
0.4058 | 0.41531 | 0.65131 | 0.65874
0.40577 | 0.41527 | 0.65124 | 0.65866
0.40573 | 0.41522 | 0.65119 | 0.65863
0.40567 | 0.41514 | 0.65114 | 0.65856
0.40562 | 0.41512 | 0.65107 | 0.65852
0.40559 | 0.41509 | 0.65103 | 0.65846
0.40555 | 0.41506 | 0.65098 | 0.65842
0.40553 | 0.41501 | 0.65092 | 0.65837
0.40548 | 0.41497 | 0.65082 | 0.65832
0.40544 | 0.41492 | 0.65079 | 0.65828
0.4054 | 0.41488 | 0.65075 | 0.65825
0.40536 | 0.41483 | 0.65069 | 0.65819
0.40526 | 0.41478 | 0.65066 | 0.65812
0.40522 | 0.41473 | 0.65062 | 0.65804
0.40516 | 0.41471 | 0.65058 | 0.65799
0.4051 | 0.41466 | 0.65054 | 0.65793
0.40506 | 0.41464 | 0.65049 | 0.65789
0.405 | 0.4146 | 0.6504 | 0.65783
0.40495 | 0.41457 | 0.65033 | 0.65776
0.40493 | 0.41452 | 0.65027 | 0.65771
0.4049 | 0.41448 | 0.65022 | 0.65767
0.40486 | 0.41442 | 0.65015 | 0.65762
0.4048 | 0.4144 | 0.65011 | 0.6576
0.40476 | 0.41436 | 0.65006 | 0.65754
0.4047 | 0.41433 | 0.65002 | 0.65749
0.40463 | 0.41429 | 0.64998 | 0.65743
0.40459 | 0.41427 | 0.64992 | 0.65739
0.40456 | 0.41424 | 0.64988 | 0.65735
0.40451 | 0.4142 | 0.64982 | 0.6573
0.40442 | 0.41417 | 0.64977 | 0.65724
0.40434 | 0.41414 | 0.64969 | 0.65719
0.40429 | 0.41408 | 0.64963 | 0.65712
0.40425 | 0.41402 | 0.64956 | 0.65707
0.40419 | 0.41398 | 0.6495 | 0.65702
0.40416 | 0.4139 | 0.64943 | 0.65696
0.40409 | 0.41385 | 0.64937 | 0.65693
0.40405 | 0.41381 | 0.6493 | 0.65689
0.40403 | 0.41379 | 0.64924 | 0.65684
0.40398 | 0.41373 | 0.64918 | 0.6568
0.40396 | 0.4137 | 0.6491 | 0.65671
0.40389 | 0.41366 | 0.64905 | 0.65669
0.40384 | 0.41363 | 0.64894 | 0.65666
0.4038 | 0.41357 | 0.64887 | 0.65663
0.40374 | 0.41353 | 0.64881 | 0.6566
0.40368 | 0.41348 | 0.64875 | 0.65653
0.40365 | 0.41343 | 0.64871 | 0.65647
0.40361 | 0.4134 | 0.64866 | 0.65641
0.40357 | 0.41337 | 0.64861 | 0.65636
0.40352 | 0.41332 | 0.64855 | 0.65631
0.40348 | 0.41326 | 0.64852 | 0.65626
0.40343 | 0.41324 | 0.64848 | 0.65617
0.40338 | 0.41321 | 0.64844 | 0.65613
0.40333 | 0.41318 | 0.64841 | 0.65607
0.40328 | 0.41313 | 0.64834 | 0.65602
0.40325 | 0.41309 | 0.64827 | 0.65593
0.40319 | 0.41305 | 0.64818 | 0.65589
0.40316 | 0.413 | 0.64815 | 0.65584
0.40312 | 0.41296 | 0.64809 | 0.65578
0.40309 | 0.41292 | 0.64805 | 0.65574
0.40304 | 0.41287 | 0.648 | 0.65567
0.40296 | 0.41277 | 0.64795 | 0.65562
0.40292 | 0.41272 | 0.64789 | 0.65556
0.40291 | 0.4127 | 0.64779 | 0.6555
0.40286 | 0.41266 | 0.64771 | 0.65545
0.4028 | 0.41261 | 0.64764 | 0.65539
0.40277 | 0.41257 | 0.6476 | 0.65536
0.40272 | 0.41252 | 0.64755 | 0.65531
0.40267 | 0.41249 | 0.6475 | 0.65525
0.40264 | 0.41245 | 0.64745 | 0.65522
0.40259 | 0.41242 | 0.64739 | 0.65515
0.40256 | 0.41236 | 0.64733 | 0.65509
0.40251 | 0.41234 | 0.6473 | 0.65503
0.40248 | 0.41229 | 0.64723 | 0.655
0.40246 | 0.41225 | 0.64719 | 0.65493
0.40244 | 0.41221 | 0.64713 | 0.65489
0.40239 | 0.41216 | 0.64709 | 0.65486
0.40234 | 0.41211 | 0.64706 | 0.65479
0.40231 | 0.41207 | 0.64697 | 0.65475
0.40227 | 0.412 | 0.64694 | 0.65469
0.40222 | 0.41196 | 0.64687 | 0.65465
0.40215 | 0.41193 | 0.64681 | 0.65458
0.40205 | 0.41188 | 0.64675 | 0.65454
0.402 | 0.41185 | 0.6467 | 0.65447
0.40196 | 0.41179 | 0.64665 | 0.65443
0.40191 | 0.41177 | 0.6466 | 0.65439
0.40187 | 0.41173 | 0.6465 | 0.65432
0.40182 | 0.4117 | 0.64644 | 0.65425
0.40179 | 0.41162 | 0.64638 | 0.65417
0.40174 | 0.41155 | 0.64633 | 0.65411
0.40169 | 0.41151 | 0.64627 | 0.65406
0.40168 | 0.41148 | 0.64622 | 0.65401
0.40163 | 0.41142 | 0.6462 | 0.65395
0.40156 | 0.41137 | 0.64616 | 0.6539
0.40153 | 0.41133 | 0.64607 | 0.65383
0.40148 | 0.41129 | 0.64603 | 0.65376
0.40145 | 0.41125 | 0.646 | 0.65369
0.40142 | 0.41123 | 0.64593 | 0.65363
0.40136 | 0.41118 | 0.64589 | 0.65359
0.40132 | 0.41113 | 0.64587 | 0.65355
0.40127 | 0.4111 | 0.64583 | 0.65348
0.40123 | 0.41106 | 0.64577 | 0.65346
0.40119 | 0.41103 | 0.64572 | 0.6534
0.40115 | 0.41098 | 0.64568 | 0.65335
0.40111 | 0.41092 | 0.64562 | 0.65331
0.40108 | 0.41089 | 0.64556 | 0.65327
0.40099 | 0.41083 | 0.64551 | 0.6532
0.40094 | 0.41079 | 0.64547 | 0.65314
0.4009 | 0.41075 | 0.6454 | 0.65308
0.40085 | 0.41071 | 0.64534 | 0.65303
0.40082 | 0.41067 | 0.64531 | 0.65299
0.4008 | 0.4106 | 0.64525 | 0.65293
0.40075 | 0.41056 | 0.64519 | 0.65288
0.40068 | 0.41052 | 0.64512 | 0.65283
0.40061 | 0.41049 | 0.64507 | 0.65278
0.40057 | 0.41045 | 0.64503 | 0.6527
0.40052 | 0.41039 | 0.64499 | 0.65262
0.4005 | 0.41035 | 0.64494 | 0.65257
0.40046 | 0.4103 | 0.64489 | 0.65252
0.40044 | 0.41026 | 0.64483 | 0.65247
0.4004 | 0.41024 | 0.64475 | 0.65242
0.40036 | 0.4102 | 0.64468 | 0.65238
0.40032 | 0.41016 | 0.64464 | 0.65231
0.4003 | 0.41013 | 0.64458 | 0.65227
0.40027 | 0.4101 | 0.64455 | 0.65223
0.40022 | 0.41005 | 0.6445 | 0.65221
0.40018 | 0.40998 | 0.64445 | 0.65218
0.40014 | 0.40992 | 0.64439 | 0.65215
0.40009 | 0.40986 | 0.64429 | 0.65209
0.40004 | 0.40982 | 0.64423 | 0.65202
0.4 | 0.40978 | 0.64418 | 0.65195
0.39997 | 0.40973 | 0.64414 | 0.65188
0.39996 | 0.40969 | 0.64408 | 0.65185
0.39991 | 0.40963 | 0.64403 | 0.65179
0.39986 | 0.40959 | 0.64399 | 0.65176
0.39982 | 0.40954 | 0.64393 | 0.65169
0.39978 | 0.40949 | 0.64387 | 0.65162
0.39974 | 0.40945 | 0.6438 | 0.65157
0.3997 | 0.4094 | 0.64377 | 0.65152
0.39966 | 0.40937 | 0.64371 | 0.65148
0.39962 | 0.40932 | 0.64366 | 0.65145
0.39957 | 0.40929 | 0.64359 | 0.65141
0.39953 | 0.40925 | 0.64354 | 0.65137
0.3995 | 0.40922 | 0.6435 | 0.6513
0.39946 | 0.40918 | 0.64345 | 0.65125
0.39943 | 0.40913 | 0.64338 | 0.65122
0.39939 | 0.4091 | 0.64333 | 0.65118
0.39935 | 0.40905 | 0.64328 | 0.65112
0.39933 | 0.40901 | 0.64321 | 0.65109
0.3993 | 0.40897 | 0.64317 | 0.65104
0.39924 | 0.40893 | 0.64314 | 0.651
0.3992 | 0.4089 | 0.6431 | 0.65097
0.39918 | 0.40885 | 0.64305 | 0.65093
0.39913 | 0.40881 | 0.64301 | 0.65086
0.39908 | 0.40877 | 0.64295 | 0.65083
0.39904 | 0.40874 | 0.64289 | 0.65082
0.39898 | 0.40869 | 0.64283 | 0.65077
0.39892 | 0.40865 | 0.64276 | 0.65073
0.39887 | 0.40862 | 0.6427 | 0.65066
0.39883 | 0.40857 | 0.64263 | 0.65063
0.39877 | 0.40852 | 0.64259 | 0.65059
0.39871 | 0.40849 | 0.64253 | 0.65054
0.39866 | 0.40845 | 0.64248 | 0.65048
0.39859 | 0.40839 | 0.64241 | 0.65041
0.39854 | 0.40833 | 0.64236 | 0.65035
0.39851 | 0.40829 | 0.64228 | 0.6503
0.39847 | 0.40826 | 0.64224 | 0.6502
0.39839 | 0.40822 | 0.6422 | 0.65015
0.39836 | 0.40818 | 0.64216 | 0.6501
0.39832 | 0.40815 | 0.64211 | 0.65005
0.39829 | 0.40812 | 0.64201 | 0.65
0.39825 | 0.40809 | 0.64193 | 0.64995
0.39821 | 0.40805 | 0.64185 | 0.64992
0.39819 | 0.40801 | 0.64173 | 0.64986
0.39816 | 0.40799 | 0.6417 | 0.6498
0.39814 | 0.40795 | 0.64166 | 0.64972
0.3981 | 0.40792 | 0.64164 | 0.64965
0.39806 | 0.40787 | 0.6416 | 0.6496
0.39802 | 0.40784 | 0.64153 | 0.64952
0.39799 | 0.4078 | 0.64149 | 0.64946
0.39792 | 0.40776 | 0.64146 | 0.64939
0.39787 | 0.40773 | 0.64141 | 0.64932
0.39783 | 0.40768 | 0.64138 | 0.64927
0.39777 | 0.40765 | 0.6413 | 0.64922
0.39774 | 0.40758 | 0.64124 | 0.64917
0.39771 | 0.40753 | 0.6412 | 0.64912
0.39766 | 0.40748 | 0.6411 | 0.64907
0.39763 | 0.40744 | 0.64106 | 0.64902
0.39761 | 0.40739 | 0.64101 | 0.64895
0.39757 | 0.40738 | 0.64095 | 0.64889
0.39753 | 0.40734 | 0.64088 | 0.64884
0.39748 | 0.4073 | 0.64083 | 0.6488
0.39745 | 0.40726 | 0.6408 | 0.64876
0.3974 | 0.40721 | 0.64075 | 0.64873
0.39737 | 0.40716 | 0.64069 | 0.64867
0.39734 | 0.40711 | 0.64066 | 0.64859
0.39729 | 0.40707 | 0.64063 | 0.64853
0.39725 | 0.40703 | 0.64056 | 0.64847
0.39721 | 0.40698 | 0.6405 | 0.64841
0.39715 | 0.40693 | 0.64045 | 0.64835
0.3971 | 0.40688 | 0.64042 | 0.64829
0.39706 | 0.40685 | 0.64036 | 0.64821
0.397 | 0.40681 | 0.6403 | 0.64816
0.39696 | 0.40678 | 0.64025 | 0.6481
0.39692 | 0.40671 | 0.64023 | 0.64805
0.39688 | 0.40668 | 0.64017 | 0.64801
0.39684 | 0.4066 | 0.64013 | 0.64797
0.3968 | 0.40654 | 0.64009 | 0.64791
0.39674 | 0.40651 | 0.64004 | 0.64784
0.3967 | 0.40644 | 0.63998 | 0.64781
0.39664 | 0.4064 | 0.6399 | 0.64774
0.39661 | 0.40636 | 0.63985 | 0.64767
0.39659 | 0.40632 | 0.63977 | 0.64763
0.39655 | 0.40629 | 0.63968 | 0.64758
0.39649 | 0.40626 | 0.63963 | 0.6475
0.39644 | 0.40621 | 0.63956 | 0.64743
0.3964 | 0.40618 | 0.63951 | 0.64739
0.39636 | 0.40614 | 0.63946 | 0.64733
0.39634 | 0.4061 | 0.63942 | 0.64727
0.39629 | 0.40605 | 0.63937 | 0.64724
0.39625 | 0.40601 | 0.63936 | 0.64719
0.39618 | 0.40597 | 0.63933 | 0.64707
0.39615 | 0.40593 | 0.63928 | 0.64703
0.39609 | 0.40587 | 0.63922 | 0.64699
0.39606 | 0.40584 | 0.63914 | 0.64694
0.39601 | 0.4058 | 0.63911 | 0.64687
0.39597 | 0.40577 | 0.63905 | 0.64683
0.39593 | 0.4057 | 0.63899 | 0.64679
0.3959 | 0.40566 | 0.63892 | 0.64673
0.39586 | 0.40562 | 0.63886 | 0.64667
0.39582 | 0.40557 | 0.6388 | 0.64662
0.39578 | 0.40554 | 0.63875 | 0.64658
0.39576 | 0.40547 | 0.63872 | 0.64655
0.39574 | 0.40543 | 0.63865 | 0.64651
0.39569 | 0.4054 | 0.63861 | 0.64646
0.39564 | 0.40537 | 0.63857 | 0.64641
0.3956 | 0.40535 | 0.6385 | 0.64638
0.39554 | 0.40532 | 0.63844 | 0.64634
0.39548 | 0.40528 | 0.6384 | 0.64631
0.39544 | 0.40523 | 0.63834 | 0.64624
0.39538 | 0.4052 | 0.63827 | 0.64618
0.39534 | 0.40515 | 0.63821 | 0.64615
0.39531 | 0.4051 | 0.63812 | 0.64609
0.39527 | 0.40507 | 0.6381 | 0.64603
0.39519 | 0.40505 | 0.63805 | 0.646
0.39515 | 0.40502 | 0.63799 | 0.64595
0.39512 | 0.40496 | 0.63794 | 0.64592
0.39507 | 0.40492 | 0.63791 | 0.64589
0.39503 | 0.4049 | 0.63785 | 0.64584
0.39498 | 0.40486 | 0.63777 | 0.6458
0.39494 | 0.40483 | 0.63771 | 0.64577
0.39491 | 0.4048 | 0.63764 | 0.64574
0.39488 | 0.40477 | 0.6376 | 0.64568
0.39483 | 0.40472 | 0.63755 | 0.64565
0.39478 | 0.40467 | 0.63751 | 0.6456
0.39475 | 0.40464 | 0.63748 | 0.64555
0.39472 | 0.40461 | 0.63742 | 0.64552
0.39471 | 0.40457 | 0.63737 | 0.64544
0.39465 | 0.40452 | 0.63731 | 0.6454
0.39461 | 0.40451 | 0.63725 | 0.64532
0.39457 | 0.40446 | 0.6372 | 0.64528
0.39454 | 0.40444 | 0.63715 | 0.64525
0.39451 | 0.40438 | 0.63711 | 0.64518
0.39446 | 0.40433 | 0.63705 | 0.64515
0.39441 | 0.40428 | 0.63699 | 0.64511
0.39438 | 0.40425 | 0.63695 | 0.64506
0.39433 | 0.40421 | 0.63689 | 0.64501
0.3943 | 0.40418 | 0.63685 | 0.64497
0.39426 | 0.40413 | 0.63679 | 0.64493
0.39422 | 0.40406 | 0.63674 | 0.64487
0.39417 | 0.40403 | 0.63671 | 0.6448
0.3941 | 0.40401 | 0.63667 | 0.64473
0.39408 | 0.40397 | 0.63659 | 0.6447
0.39404 | 0.40393 | 0.63653 | 0.64466
0.39401 | 0.40392 | 0.63648 | 0.64461
0.39396 | 0.40389 | 0.63642 | 0.64457
0.39393 | 0.40385 | 0.63636 | 0.64452
0.3939 | 0.40381 | 0.6363 | 0.64449
0.39385 | 0.40378 | 0.63624 | 0.64446
0.3938 | 0.40375 | 0.63617 | 0.64442
0.39377 | 0.40372 | 0.63612 | 0.64435
0.39372 | 0.40369 | 0.63607 | 0.64429
0.39368 | 0.40366 | 0.63602 | 0.64425
0.39366 | 0.40361 | 0.63594 | 0.64418
0.39361 | 0.40357 | 0.6359 | 0.64409
0.39358 | 0.40354 | 0.63587 | 0.64402
0.39354 | 0.40351 | 0.63582 | 0.64399
0.3935 | 0.40345 | 0.63577 | 0.64396
0.39347 | 0.40341 | 0.63571 | 0.64391
0.39343 | 0.40337 | 0.63563 | 0.64385
0.3934 | 0.40334 | 0.63558 | 0.6438
0.39337 | 0.40328 | 0.63555 | 0.64374
0.39331 | 0.40326 | 0.63551 | 0.64371
0.39328 | 0.40323 | 0.63547 | 0.64368
0.39324 | 0.4032 | 0.63542 | 0.64364
0.3932 | 0.40315 | 0.63535 | 0.64359
0.39317 | 0.40312 | 0.6353 | 0.64353
0.39313 | 0.40307 | 0.63526 | 0.64347
0.3931 | 0.40303 | 0.63518 | 0.64344
0.39304 | 0.40298 | 0.63515 | 0.64339
0.393 | 0.40293 | 0.6351 | 0.64335
0.39295 | 0.40291 | 0.63503 | 0.64332
0.39292 | 0.40285 | 0.63498 | 0.64327
0.3929 | 0.40282 | 0.63494 | 0.64321
0.39285 | 0.40278 | 0.63489 | 0.64316
0.39281 | 0.40275 | 0.63485 | 0.64312
0.39279 | 0.40273 | 0.63482 | 0.64308
0.39274 | 0.40269 | 0.63479 | 0.64304
0.39271 | 0.40264 | 0.63474 | 0.64297
0.39267 | 0.40261 | 0.63467 | 0.64293
0.39265 | 0.40258 | 0.63462 | 0.64289
0.39262 | 0.40256 | 0.63458 | 0.64283
0.39258 | 0.40253 | 0.63454 | 0.64279
0.39255 | 0.4025 | 0.6345 | 0.64273
0.39251 | 0.40246 | 0.63446 | 0.64269
0.39248 | 0.40242 | 0.63442 | 0.64264
0.39244 | 0.40239 | 0.63438 | 0.64261
0.39242 | 0.40237 | 0.63432 | 0.64256
0.39238 | 0.40233 | 0.63428 | 0.64253
0.39235 | 0.4023 | 0.63419 | 0.64249
0.3923 | 0.40224 | 0.63415 | 0.64242
0.39227 | 0.40221 | 0.63411 | 0.64238
0.39224 | 0.40217 | 0.63406 | 0.64234
0.39221 | 0.40214 | 0.634 | 0.64231
0.39218 | 0.40211 | 0.63396 | 0.64226
0.39216 | 0.40208 | 0.63392 | 0.64223
0.39213 | 0.40204 | 0.63387 | 0.6422
0.3921 | 0.40201 | 0.63384 | 0.64215
0.39207 | 0.40198 | 0.63375 | 0.64204
0.39204 | 0.40194 | 0.63371 | 0.64199
0.392 | 0.40188 | 0.63367 | 0.64195
0.39198 | 0.40186 | 0.63363 | 0.6419
0.39194 | 0.40184 | 0.63357 | 0.64186
0.39191 | 0.4018 | 0.63351 | 0.64182
0.39187 | 0.40178 | 0.63347 | 0.64178
0.39184 | 0.40174 | 0.63341 | 0.64172
0.39181 | 0.40171 | 0.63338 | 0.64167
0.39179 | 0.40165 | 0.63332 | 0.64157
0.39173 | 0.40163 | 0.63327 | 0.64154
0.3917 | 0.40161 | 0.63324 | 0.6415
0.39167 | 0.40156 | 0.63318 | 0.64147
0.39164 | 0.40153 | 0.63313 | 0.6414
0.39158 | 0.40148 | 0.63308 | 0.64134
0.39154 | 0.40145 | 0.63303 | 0.64128
0.39152 | 0.40142 | 0.63298 | 0.64123
0.3915 | 0.40139 | 0.63294 | 0.64118
0.39146 | 0.40136 | 0.63287 | 0.64113
0.3914 | 0.40131 | 0.63283 | 0.64109
0.39136 | 0.40127 | 0.63279 | 0.64103
0.39131 | 0.40123 | 0.63273 | 0.641
0.39129 | 0.40121 | 0.63268 | 0.64097
0.39126 | 0.40117 | 0.63262 | 0.64091
0.39125 | 0.40113 | 0.63258 | 0.64087
0.39122 | 0.40109 | 0.63252 | 0.64083
0.39119 | 0.40105 | 0.63245 | 0.64077
0.39117 | 0.401 | 0.63241 | 0.64073
0.39113 | 0.40095 | 0.63237 | 0.64068
0.3911 | 0.40091 | 0.63232 | 0.64062
0.39106 | 0.40089 | 0.63228 | 0.64056
0.39102 | 0.40084 | 0.63221 | 0.64053
0.39098 | 0.40082 | 0.63216 | 0.64046
0.39096 | 0.40078 | 0.63212 | 0.6404
0.3909 | 0.40074 | 0.63207 | 0.64036
0.39085 | 0.40072 | 0.63199 | 0.64031
0.3908 | 0.4007 | 0.63192 | 0.64027
0.39075 | 0.40066 | 0.6319 | 0.64021
0.39071 | 0.40061 | 0.63185 | 0.64014
0.39067 | 0.40058 | 0.6318 | 0.6401
0.39062 | 0.40053 | 0.63175 | 0.64005
0.39059 | 0.40048 | 0.63169 | 0.64002
0.39056 | 0.40046 | 0.63162 | 0.63996
0.39053 | 0.40042 | 0.63157 | 0.6399
0.39049 | 0.40036 | 0.63153 | 0.63985
0.39046 | 0.40033 | 0.63148 | 0.63981
0.39042 | 0.40027 | 0.63139 | 0.63973
0.39038 | 0.40025 | 0.63133 | 0.63969
0.39034 | 0.40023 | 0.63128 | 0.63965
0.39028 | 0.4002 | 0.63123 | 0.6396
0.39025 | 0.40015 | 0.63119 | 0.63956
0.39017 | 0.4001 | 0.63111 | 0.63952
0.39014 | 0.40007 | 0.63107 | 0.6395
0.39011 | 0.40003 | 0.63104 | 0.63946
0.39007 | 0.39996 | 0.631 | 0.63941
0.39004 | 0.39994 | 0.63097 | 0.63933
0.39 | 0.39985 | 0.63093 | 0.63929
0.38996 | 0.39982 | 0.6309 | 0.63926
0.38992 | 0.3998 | 0.63086 | 0.63921
0.3899 | 0.39977 | 0.63081 | 0.63917
0.38986 | 0.39972 | 0.63077 | 0.63916
0.38982 | 0.39969 | 0.63072 | 0.63911
0.38976 | 0.39966 | 0.63068 | 0.63904
0.38973 | 0.39963 | 0.63064 | 0.63897
0.38969 | 0.3996 | 0.63059 | 0.63892
0.38967 | 0.39957 | 0.63054 | 0.63886
0.38965 | 0.39953 | 0.6305 | 0.63881
0.38962 | 0.39948 | 0.63047 | 0.63878
0.38959 | 0.39945 | 0.63042 | 0.63874
0.38955 | 0.3994 | 0.63036 | 0.63869
0.38951 | 0.39937 | 0.6303 | 0.63865
0.3895 | 0.39935 | 0.63026 | 0.63861
0.38947 | 0.39932 | 0.63021 | 0.63858
0.38943 | 0.39929 | 0.63015 | 0.63851
0.38937 | 0.39926 | 0.63011 | 0.63846
0.38934 | 0.39924 | 0.63006 | 0.63842
0.38928 | 0.3992 | 0.63001 | 0.63838
0.38925 | 0.39916 | 0.62995 | 0.63829
0.3892 | 0.3991 | 0.62989 | 0.63825
0.38918 | 0.39908 | 0.62983 | 0.63821
0.38913 | 0.39905 | 0.6298 | 0.63815
0.3891 | 0.39901 | 0.62976 | 0.63809
0.38907 | 0.39897 | 0.62971 | 0.63804
0.38904 | 0.39894 | 0.62965 | 0.638
0.389 | 0.39891 | 0.62959 | 0.63796
0.38895 | 0.39888 | 0.62957 | 0.63793
0.38891 | 0.39886 | 0.62951 | 0.63789
0.38888 | 0.39882 | 0.62947 | 0.63784
0.38883 | 0.3988 | 0.62938 | 0.6378
0.3888 | 0.39877 | 0.62931 | 0.63776
0.38876 | 0.39873 | 0.62928 | 0.63769
0.38874 | 0.39869 | 0.62922 | 0.63763
0.38872 | 0.39866 | 0.62916 | 0.63758
0.38868 | 0.39863 | 0.62912 | 0.63755
0.38865 | 0.3986 | 0.62907 | 0.63749
0.38858 | 0.39857 | 0.629 | 0.63746
0.38856 | 0.39853 | 0.62895 | 0.63742
0.38854 | 0.3985 | 0.62889 | 0.63736
0.38851 | 0.39848 | 0.62883 | 0.63732
0.38848 | 0.39843 | 0.62879 | 0.63728
0.38845 | 0.39839 | 0.62874 | 0.63725
0.38841 | 0.39837 | 0.6287 | 0.63722
0.38839 | 0.39833 | 0.62868 | 0.63717
0.38836 | 0.3983 | 0.62861 | 0.63712
0.38833 | 0.39827 | 0.62857 | 0.63709
0.3883 | 0.39824 | 0.62852 | 0.63704
0.38826 | 0.39821 | 0.62847 | 0.63698
0.38823 | 0.39817 | 0.62838 | 0.63694
0.38819 | 0.39814 | 0.62834 | 0.6369
0.38818 | 0.39808 | 0.62828 | 0.63685
0.38814 | 0.39805 | 0.62825 | 0.63678
0.3881 | 0.39802 | 0.62823 | 0.63671
0.38805 | 0.39797 | 0.6282 | 0.63666
0.388 | 0.39796 | 0.62817 | 0.63663
0.38795 | 0.39793 | 0.6281 | 0.63658
0.3879 | 0.3979 | 0.62806 | 0.63653
0.38787 | 0.39787 | 0.62799 | 0.6365
0.38784 | 0.39784 | 0.62793 | 0.63645
0.3878 | 0.39781 | 0.62788 | 0.63638
0.38776 | 0.39778 | 0.62784 | 0.63635
0.38773 | 0.39773 | 0.62779 | 0.63631
0.38768 | 0.39771 | 0.62776 | 0.63627
0.38765 | 0.39768 | 0.62772 | 0.63622
0.38763 | 0.39764 | 0.62767 | 0.63617
0.3876 | 0.39762 | 0.62761 | 0.6361
0.38758 | 0.39757 | 0.62754 | 0.63607
0.38755 | 0.3975 | 0.62749 | 0.63602
0.3875 | 0.39747 | 0.62746 | 0.63597
0.38747 | 0.39745 | 0.62743 | 0.63593
0.38744 | 0.39742 | 0.62736 | 0.6359
0.3874 | 0.3974 | 0.62731 | 0.63585
0.38736 | 0.39736 | 0.62725 | 0.63581
0.38733 | 0.39731 | 0.62718 | 0.63577
0.3873 | 0.39728 | 0.62713 | 0.63568
0.38725 | 0.39722 | 0.6271 | 0.63564
0.38723 | 0.39719 | 0.62705 | 0.63559
0.38719 | 0.39717 | 0.627 | 0.63556
0.38715 | 0.39716 | 0.62698 | 0.63551
0.38711 | 0.39713 | 0.62694 | 0.63546
0.38709 | 0.39712 | 0.62689 | 0.63537
0.38704 | 0.3971 | 0.62684 | 0.63532
0.38698 | 0.39707 | 0.62679 | 0.63529
0.38696 | 0.39705 | 0.62675 | 0.63526
0.38693 | 0.39699 | 0.62672 | 0.63522
0.38689 | 0.39697 | 0.62669 | 0.63519
0.38683 | 0.39693 | 0.62664 | 0.63515
0.3868 | 0.39688 | 0.62662 | 0.63508
0.38678 | 0.39685 | 0.62658 | 0.63503
0.38674 | 0.39682 | 0.62654 | 0.63498
0.38672 | 0.39677 | 0.62651 | 0.63494
0.38668 | 0.39671 | 0.62645 | 0.63489
0.38664 | 0.39668 | 0.62639 | 0.63486
0.3866 | 0.39665 | 0.62634 | 0.6348
0.38656 | 0.39662 | 0.6263 | 0.63477
0.38652 | 0.39659 | 0.62626 | 0.63474
0.38649 | 0.39653 | 0.6262 | 0.6347
0.38642 | 0.3965 | 0.62615 | 0.63468
0.3864 | 0.39647 | 0.62611 | 0.63459
0.38637 | 0.39644 | 0.62608 | 0.63456
0.38632 | 0.39639 | 0.62603 | 0.63452
0.3863 | 0.39632 | 0.62597 | 0.63447
0.38627 | 0.39629 | 0.62591 | 0.63441
0.38622 | 0.39627 | 0.62588 | 0.63435
0.38621 | 0.39623 | 0.62583 | 0.6343
0.38618 | 0.3962 | 0.62578 | 0.63426
0.38613 | 0.39617 | 0.62574 | 0.6342
0.3861 | 0.39614 | 0.62571 | 0.63416
0.38606 | 0.3961 | 0.62568 | 0.63411
0.38604 | 0.39607 | 0.62564 | 0.63407
0.38602 | 0.39605 | 0.62559 | 0.63401
0.38599 | 0.396 | 0.62554 | 0.63397
0.38595 | 0.39597 | 0.62546 | 0.63392
0.3859 | 0.39594 | 0.62539 | 0.63388
0.38588 | 0.3959 | 0.62535 | 0.63384
0.38585 | 0.39587 | 0.6253 | 0.63379
0.38581 | 0.39585 | 0.62525 | 0.63372
0.38578 | 0.39578 | 0.62521 | 0.63367
0.38575 | 0.39574 | 0.62515 | 0.63359
0.38569 | 0.39571 | 0.6251 | 0.63357
0.38564 | 0.39568 | 0.62505 | 0.63353
0.38562 | 0.39563 | 0.62501 | 0.63348
0.38558 | 0.3956 | 0.62498 | 0.63342
0.38555 | 0.39554 | 0.6249 | 0.63338
0.38551 | 0.39551 | 0.62483 | 0.63333
0.38549 | 0.39547 | 0.6248 | 0.6333
0.38544 | 0.39545 | 0.62477 | 0.63325
0.38539 | 0.39541 | 0.62474 | 0.6332
0.38537 | 0.39537 | 0.62468 | 0.63316
0.38534 | 0.39532 | 0.62464 | 0.63312
0.38531 | 0.39529 | 0.62459 | 0.63306
0.38526 | 0.39527 | 0.62454 | 0.63301
0.38524 | 0.39523 | 0.6245 | 0.63295
0.38521 | 0.39521 | 0.62447 | 0.63291
0.38518 | 0.39517 | 0.62442 | 0.63286
0.38516 | 0.39513 | 0.62437 | 0.6328
0.38509 | 0.39508 | 0.6243 | 0.63275
0.38505 | 0.39506 | 0.62425 | 0.63272
0.38501 | 0.39505 | 0.62422 | 0.63268
0.38496 | 0.39501 | 0.62418 | 0.63262
0.38493 | 0.39499 | 0.62413 | 0.63255
0.3849 | 0.39495 | 0.62407 | 0.63252
0.38486 | 0.39492 | 0.62404 | 0.63248
0.38483 | 0.39489 | 0.62402 | 0.63243
0.38477 | 0.39487 | 0.624 | 0.6324
0.38472 | 0.39483 | 0.62396 | 0.63236
0.38469 | 0.39481 | 0.62391 | 0.63232
0.38465 | 0.39479 | 0.62386 | 0.63226
0.38462 | 0.39476 | 0.62381 | 0.63222
0.38458 | 0.39472 | 0.62378 | 0.63219
0.38454 | 0.39468 | 0.62374 | 0.63214
0.38452 | 0.39464 | 0.62372 | 0.63209
0.38449 | 0.39459 | 0.62367 | 0.63204
0.38447 | 0.39457 | 0.62358 | 0.63201
0.38443 | 0.39454 | 0.62356 | 0.63196
0.3844 | 0.3945 | 0.62353 | 0.63192
0.38437 | 0.39447 | 0.62347 | 0.63188
0.38436 | 0.39446 | 0.62344 | 0.63184
0.38432 | 0.39441 | 0.6234 | 0.63179
0.38428 | 0.3944 | 0.62337 | 0.63176
0.38423 | 0.39437 | 0.62334 | 0.63173
0.3842 | 0.39434 | 0.6233 | 0.63171
0.38418 | 0.3943 | 0.62324 | 0.63168
0.38416 | 0.39428 | 0.62319 | 0.63162
0.38411 | 0.39425 | 0.62313 | 0.63159
0.38408 | 0.3942 | 0.62309 | 0.63154
0.38403 | 0.39418 | 0.62305 | 0.63149
0.38399 | 0.39415 | 0.623 | 0.63145
0.38396 | 0.39412 | 0.62295 | 0.63141
0.38394 | 0.39409 | 0.6229 | 0.63137
0.38391 | 0.39408 | 0.62284 | 0.63133
0.38388 | 0.39405 | 0.62279 | 0.63128
0.38385 | 0.39402 | 0.62276 | 0.63125
0.38384 | 0.39398 | 0.62273 | 0.6312
0.38382 | 0.39395 | 0.62269 | 0.63116
0.38379 | 0.39392 | 0.62264 | 0.63113
0.38373 | 0.39387 | 0.62256 | 0.63108
0.3837 | 0.39385 | 0.62252 | 0.63104
0.38368 | 0.39383 | 0.62247 | 0.63098
0.38364 | 0.39381 | 0.62241 | 0.63093
0.38359 | 0.39377 | 0.62237 | 0.6309
0.38354 | 0.39373 | 0.62233 | 0.63087
0.38351 | 0.39371 | 0.62229 | 0.63082
0.38346 | 0.39368 | 0.62224 | 0.63077
0.38344 | 0.39366 | 0.62222 | 0.63072
0.38337 | 0.39363 | 0.62219 | 0.63068
0.38336 | 0.39359 | 0.62215 | 0.63065
0.38333 | 0.39355 | 0.62209 | 0.63061
0.3833 | 0.39351 | 0.62205 | 0.63057
0.38328 | 0.39348 | 0.62199 | 0.63054
0.38326 | 0.39344 | 0.62195 | 0.6305
0.38324 | 0.3934 | 0.62188 | 0.63046
0.38322 | 0.39337 | 0.62183 | 0.6304
0.3832 | 0.3933 | 0.6218 | 0.63036
0.38316 | 0.39327 | 0.62176 | 0.6303
0.38313 | 0.39324 | 0.62172 | 0.63024
0.38309 | 0.39321 | 0.62168 | 0.6302
0.38306 | 0.39317 | 0.62164 | 0.63016
0.38302 | 0.39314 | 0.6216 | 0.63013
0.38299 | 0.39311 | 0.62156 | 0.63008
0.38295 | 0.39309 | 0.62152 | 0.63005
0.3829 | 0.39307 | 0.62146 | 0.62999
0.38287 | 0.39304 | 0.6214 | 0.62994
0.38283 | 0.39302 | 0.62135 | 0.62989
0.38278 | 0.39299 | 0.62132 | 0.62986
0.38272 | 0.39297 | 0.62126 | 0.62981
0.38269 | 0.39294 | 0.62122 | 0.62977
0.38266 | 0.39291 | 0.62119 | 0.62973
0.38264 | 0.39288 | 0.62113 | 0.62969
0.38257 | 0.39286 | 0.62109 | 0.62962
0.38254 | 0.39284 | 0.62104 | 0.62959
0.38251 | 0.39282 | 0.621 | 0.62957
0.38247 | 0.39278 | 0.62097 | 0.62953
0.38243 | 0.39275 | 0.6209 | 0.6295
0.38241 | 0.39271 | 0.62086 | 0.62947
0.38239 | 0.39268 | 0.62082 | 0.62944
0.38236 | 0.39263 | 0.62077 | 0.6294
0.38233 | 0.39261 | 0.62075 | 0.62933
0.38229 | 0.39257 | 0.62071 | 0.62929
0.38227 | 0.39252 | 0.62067 | 0.62924
0.38225 | 0.39249 | 0.6206 | 0.62921
0.38221 | 0.39243 | 0.62054 | 0.62917
0.38219 | 0.3924 | 0.62051 | 0.62911
0.38216 | 0.39238 | 0.62048 | 0.62907
0.38212 | 0.39235 | 0.62044 | 0.62903
0.3821 | 0.39232 | 0.6204 | 0.62899
0.38207 | 0.3923 | 0.62035 | 0.62892
0.38205 | 0.39228 | 0.62031 | 0.62888
0.38202 | 0.39224 | 0.62025 | 0.62883
0.38197 | 0.39222 | 0.6202 | 0.62878
0.38195 | 0.3922 | 0.62017 | 0.62876
0.38193 | 0.39217 | 0.62012 | 0.62873
0.3819 | 0.39215 | 0.6201 | 0.62871
0.38187 | 0.39211 | 0.62006 | 0.62865
0.38186 | 0.3921 | 0.62003 | 0.62859
0.38182 | 0.39206 | 0.61996 | 0.62854
0.38179 | 0.39204 | 0.61993 | 0.6285
0.38176 | 0.39201 | 0.6199 | 0.62847
0.38173 | 0.39196 | 0.61985 | 0.62841
0.38169 | 0.39193 | 0.61981 | 0.62839
0.38165 | 0.3919 | 0.61976 | 0.62836
0.38162 | 0.39185 | 0.61972 | 0.62833
0.38158 | 0.39182 | 0.61966 | 0.62829
0.38154 | 0.39179 | 0.61962 | 0.62823
0.38151 | 0.39176 | 0.61953 | 0.62819
0.38148 | 0.39174 | 0.61951 | 0.62813
0.38146 | 0.39172 | 0.61946 | 0.62807
0.38143 | 0.39167 | 0.61938 | 0.62805
0.38138 | 0.39163 | 0.61932 | 0.62802
0.38135 | 0.3916 | 0.61925 | 0.62797
0.38132 | 0.39156 | 0.61922 | 0.62793
0.3813 | 0.39153 | 0.61918 | 0.62789
0.38128 | 0.39149 | 0.61915 | 0.62784
0.38124 | 0.39147 | 0.6191 | 0.62781
0.38121 | 0.39143 | 0.61906 | 0.62776
0.38118 | 0.39139 | 0.61899 | 0.6277
0.38115 | 0.39136 | 0.61895 | 0.62766
0.38113 | 0.39132 | 0.61889 | 0.62761
0.3811 | 0.39129 | 0.61884 | 0.62756
0.38107 | 0.39125 | 0.61879 | 0.62753
0.38105 | 0.39124 | 0.61873 | 0.6275
0.38102 | 0.39117 | 0.61869 | 0.62745
0.38099 | 0.39114 | 0.61862 | 0.6274
0.38093 | 0.3911 | 0.61859 | 0.62736
0.38089 | 0.39106 | 0.61854 | 0.62732
0.38086 | 0.39104 | 0.61847 | 0.62726
0.38083 | 0.39101 | 0.61841 | 0.62721
0.38079 | 0.39099 | 0.61838 | 0.62716
0.38077 | 0.39096 | 0.61834 | 0.62712
0.38074 | 0.39093 | 0.61828 | 0.62709
0.38071 | 0.39089 | 0.61826 | 0.62704
0.38068 | 0.39086 | 0.61823 | 0.62699
0.38065 | 0.39082 | 0.61817 | 0.62695
0.38061 | 0.39079 | 0.61813 | 0.62689
0.38058 | 0.39075 | 0.61808 | 0.62685
0.38056 | 0.39072 | 0.61804 | 0.62681
0.38052 | 0.3907 | 0.618 | 0.62677
0.38046 | 0.39066 | 0.61796 | 0.62674
0.38044 | 0.39062 | 0.61792 | 0.62671
0.38039 | 0.3906 | 0.61788 | 0.62667
0.38036 | 0.39057 | 0.61786 | 0.62663
0.38033 | 0.39054 | 0.61781 | 0.6266
0.38027 | 0.3905 | 0.61774 | 0.62654
0.38025 | 0.39047 | 0.61768 | 0.62652
0.38022 | 0.39044 | 0.61766 | 0.62648
0.38019 | 0.3904 | 0.61761 | 0.62645
0.38015 | 0.39037 | 0.61755 | 0.62641
0.38011 | 0.39035 | 0.6175 | 0.62634
0.38009 | 0.39032 | 0.61743 | 0.62631
0.38007 | 0.39027 | 0.61737 | 0.62629
0.38004 | 0.39026 | 0.61732 | 0.6262
0.38001 | 0.39023 | 0.61727 | 0.62616
0.37998 | 0.3902 | 0.61723 | 0.62608
0.37995 | 0.39018 | 0.61719 | 0.62603
0.37993 | 0.39015 | 0.61716 | 0.62597
0.37991 | 0.39013 | 0.61713 | 0.62591
0.37989 | 0.3901 | 0.61708 | 0.62588
0.37985 | 0.39007 | 0.61702 | 0.62584
0.37982 | 0.39005 | 0.61697 | 0.6258
0.37978 | 0.39001 | 0.61693 | 0.62577
0.37975 | 0.38998 | 0.61688 | 0.62572
0.37971 | 0.38995 | 0.61683 | 0.62569
0.37968 | 0.38993 | 0.61679 | 0.62565
0.37967 | 0.38988 | 0.61675 | 0.62559
0.37964 | 0.38984 | 0.61671 | 0.62554
0.37961 | 0.38981 | 0.61666 | 0.6255
0.37959 | 0.38979 | 0.61661 | 0.62547
0.37957 | 0.38977 | 0.61657 | 0.62543
0.37955 | 0.38974 | 0.61651 | 0.6254
0.37953 | 0.38971 | 0.61648 | 0.62534
0.37949 | 0.38968 | 0.61645 | 0.62532
0.37947 | 0.38966 | 0.6164 | 0.62526
0.37942 | 0.38964 | 0.61634 | 0.62522
0.37939 | 0.3896 | 0.61627 | 0.62518
0.37934 | 0.38956 | 0.61622 | 0.62514
0.37933 | 0.38952 | 0.61615 | 0.62509
0.3793 | 0.38951 | 0.61612 | 0.62505
0.37927 | 0.38947 | 0.61606 | 0.62499
0.37925 | 0.38944 | 0.61604 | 0.62494
0.37922 | 0.38941 | 0.61599 | 0.62487
0.3792 | 0.38938 | 0.61594 | 0.62484
0.37915 | 0.38935 | 0.61589 | 0.6248
0.37912 | 0.38931 | 0.61586 | 0.62478
0.37909 | 0.38928 | 0.61582 | 0.62474
0.37906 | 0.38924 | 0.61579 | 0.62471
0.37903 | 0.3892 | 0.61575 | 0.62467
0.37899 | 0.38919 | 0.61568 | 0.62463
0.37896 | 0.38917 | 0.61563 | 0.6246
0.37893 | 0.38914 | 0.61558 | 0.62454
0.37888 | 0.38911 | 0.61554 | 0.62448
0.37885 | 0.38909 | 0.6155 | 0.62444
0.37881 | 0.38907 | 0.61545 | 0.62437
0.37877 | 0.38904 | 0.61541 | 0.62432
0.37875 | 0.38902 | 0.61537 | 0.62428
0.3787 | 0.389 | 0.6153 | 0.62424
0.37867 | 0.38898 | 0.61525 | 0.62418
0.37864 | 0.38895 | 0.61518 | 0.62413
0.37862 | 0.38891 | 0.61513 | 0.62407
0.3786 | 0.3889 | 0.61509 | 0.62404
0.37856 | 0.38887 | 0.61504 | 0.62398
0.37852 | 0.38884 | 0.615 | 0.62395
0.37848 | 0.38881 | 0.61496 | 0.6239
0.37846 | 0.38876 | 0.61492 | 0.62384
0.37842 | 0.38872 | 0.61488 | 0.62381
0.3784 | 0.38869 | 0.61484 | 0.62378
0.37838 | 0.38865 | 0.61481 | 0.62375
0.37833 | 0.38862 | 0.61477 | 0.6237
0.3783 | 0.38857 | 0.61472 | 0.62367
0.37826 | 0.38856 | 0.61465 | 0.62365
0.37824 | 0.38853 | 0.6146 | 0.62357
0.37821 | 0.38851 | 0.61456 | 0.62354
0.37818 | 0.38848 | 0.61454 | 0.62349
0.37815 | 0.38845 | 0.61449 | 0.62345
0.3781 | 0.38842 | 0.61442 | 0.62342
0.37808 | 0.38839 | 0.61439 | 0.6234
0.37806 | 0.38837 | 0.61433 | 0.62338
0.37804 | 0.38836 | 0.61427 | 0.62334
0.37803 | 0.38834 | 0.61422 | 0.62328
0.37801 | 0.38831 | 0.61418 | 0.62323
0.37798 | 0.38828 | 0.61413 | 0.62319
0.37796 | 0.38824 | 0.61407 | 0.62315
0.37793 | 0.3882 | 0.61405 | 0.62312
0.37791 | 0.38817 | 0.61401 | 0.62306
0.37788 | 0.38815 | 0.61398 | 0.62302
0.37785 | 0.38811 | 0.61394 | 0.62299
0.37782 | 0.38807 | 0.61387 | 0.62292
0.37779 | 0.38804 | 0.61384 | 0.62288
0.37777 | 0.38803 | 0.61382 | 0.62282
0.37774 | 0.38797 | 0.61377 | 0.62279
0.37769 | 0.38794 | 0.6137 | 0.62275
0.37765 | 0.3879 | 0.61365 | 0.6227
0.37762 | 0.38788 | 0.6136 | 0.62265
0.3776 | 0.38786 | 0.61356 | 0.6226
0.37756 | 0.38784 | 0.61352 | 0.62257
0.37753 | 0.38781 | 0.61348 | 0.62252
0.37749 | 0.38778 | 0.61344 | 0.62247
0.37745 | 0.38775 | 0.61341 | 0.62243
0.37742 | 0.38771 | 0.61337 | 0.62239
0.3774 | 0.3877 | 0.61333 | 0.62236
0.37735 | 0.38766 | 0.61329 | 0.62232
0.37733 | 0.38763 | 0.61325 | 0.62227
0.37731 | 0.3876 | 0.61322 | 0.62222
0.37728 | 0.38756 | 0.61317 | 0.62219
0.37725 | 0.38753 | 0.61313 | 0.62213
0.37722 | 0.3875 | 0.61308 | 0.62209
0.37719 | 0.38745 | 0.61304 | 0.62203
0.37718 | 0.38741 | 0.613 | 0.622
0.37716 | 0.38739 | 0.61298 | 0.62197
0.37714 | 0.38737 | 0.61293 | 0.62194
0.37711 | 0.38732 | 0.6129 | 0.62188
0.37709 | 0.3873 | 0.61284 | 0.62183
0.37707 | 0.38726 | 0.61278 | 0.62179
0.37705 | 0.38722 | 0.61274 | 0.62173
0.37703 | 0.38719 | 0.61271 | 0.62168
0.377 | 0.38716 | 0.61265 | 0.62163
0.37697 | 0.38713 | 0.61262 | 0.6216
0.37695 | 0.38711 | 0.61259 | 0.62155
0.37692 | 0.38709 | 0.61254 | 0.62151
0.37689 | 0.38706 | 0.6125 | 0.62147
0.37687 | 0.38704 | 0.61245 | 0.62143
0.37684 | 0.38701 | 0.61241 | 0.62138
0.37682 | 0.38697 | 0.61237 | 0.62133
0.3768 | 0.38695 | 0.61233 | 0.6213
0.37679 | 0.38691 | 0.6123 | 0.62125
0.37676 | 0.38688 | 0.61226 | 0.6212
0.37674 | 0.38685 | 0.61223 | 0.62116
0.37671 | 0.38682 | 0.61219 | 0.62112
0.37668 | 0.3868 | 0.61216 | 0.62106
0.37666 | 0.38679 | 0.61211 | 0.62102
0.37662 | 0.38677 | 0.61206 | 0.62096
0.37658 | 0.38674 | 0.612 | 0.6209
0.37655 | 0.38671 | 0.61193 | 0.62087
0.37653 | 0.38668 | 0.6119 | 0.62082
0.3765 | 0.38666 | 0.61188 | 0.6208
0.37647 | 0.38664 | 0.61184 | 0.62074
0.37644 | 0.38662 | 0.6118 | 0.62071
0.37642 | 0.38659 | 0.61175 | 0.62068
0.3764 | 0.38656 | 0.61169 | 0.62065
0.37637 | 0.38653 | 0.61164 | 0.62063
0.37635 | 0.3865 | 0.6116 | 0.6206
0.37633 | 0.38646 | 0.61157 | 0.62053
0.37632 | 0.38644 | 0.61152 | 0.62049
0.37627 | 0.38643 | 0.6115 | 0.62045
0.37624 | 0.38638 | 0.61145 | 0.62042
0.37622 | 0.38635 | 0.61141 | 0.62038
0.37618 | 0.38632 | 0.61137 | 0.62033
0.37617 | 0.3863 | 0.61132 | 0.6203
0.37615 | 0.38626 | 0.61128 | 0.62027
0.37611 | 0.38624 | 0.61125 | 0.62019
0.37607 | 0.38621 | 0.61121 | 0.62015
0.37602 | 0.38617 | 0.61118 | 0.62012
0.37598 | 0.38615 | 0.61112 | 0.62006
0.37594 | 0.38612 | 0.61106 | 0.61998
0.37591 | 0.38609 | 0.611 | 0.61993
0.37589 | 0.38605 | 0.61095 | 0.61989
0.37587 | 0.386 | 0.6109 | 0.61984
0.37583 | 0.38596 | 0.61085 | 0.61979
0.3758 | 0.38595 | 0.61082 | 0.61976
0.37578 | 0.38592 | 0.61078 | 0.6197
0.37575 | 0.38588 | 0.61076 | 0.61966
0.37573 | 0.38586 | 0.61073 | 0.61963
0.3757 | 0.38584 | 0.61069 | 0.61959
0.37567 | 0.38581 | 0.61065 | 0.61955
0.37565 | 0.38579 | 0.61062 | 0.61952
0.37563 | 0.38576 | 0.61059 | 0.61947
0.37561 | 0.38575 | 0.61053 | 0.61944
0.37557 | 0.38572 | 0.61048 | 0.6194
0.37554 | 0.38569 | 0.61043 | 0.61935
0.37551 | 0.38567 | 0.61039 | 0.61932
0.37549 | 0.38563 | 0.61034 | 0.61927
0.37547 | 0.38561 | 0.61029 | 0.61922
0.37545 | 0.38558 | 0.61025 | 0.61918
0.37541 | 0.38555 | 0.6102 | 0.61914
0.37539 | 0.3855 | 0.61016 | 0.61909
0.37536 | 0.38549 | 0.61013 | 0.61905
0.37533 | 0.38546 | 0.61009 | 0.619
0.3753 | 0.38544 | 0.61006 | 0.61898
0.37529 | 0.38541 | 0.61001 | 0.61896
0.37525 | 0.38538 | 0.60998 | 0.61892
0.37522 | 0.38536 | 0.60992 | 0.61888
0.37518 | 0.38533 | 0.60989 | 0.61886
0.37515 | 0.38531 | 0.60984 | 0.61882
0.37513 | 0.38528 | 0.60981 | 0.61876
0.3751 | 0.38526 | 0.60978 | 0.61873
0.37507 | 0.38525 | 0.60973 | 0.61868
0.37505 | 0.38522 | 0.60969 | 0.61865
0.37501 | 0.38519 | 0.60965 | 0.61862
0.37498 | 0.38516 | 0.60961 | 0.61858
0.37493 | 0.38515 | 0.60957 | 0.61855
0.3749 | 0.38511 | 0.60953 | 0.61849
0.37487 | 0.38508 | 0.6095 | 0.61846
0.37483 | 0.38505 | 0.60943 | 0.61839
0.3748 | 0.38503 | 0.6094 | 0.61835
0.37479 | 0.38501 | 0.60936 | 0.61832
0.37478 | 0.38498 | 0.60934 | 0.61828
0.37475 | 0.38495 | 0.6093 | 0.61827
0.37471 | 0.38492 | 0.60926 | 0.61822
0.37469 | 0.3849 | 0.60922 | 0.61818
0.37465 | 0.38484 | 0.60917 | 0.61814
0.37461 | 0.3848 | 0.60911 | 0.6181
0.3746 | 0.38477 | 0.60906 | 0.61805
0.37457 | 0.38474 | 0.60903 | 0.618
0.37453 | 0.38471 | 0.60899 | 0.61797
0.3745 | 0.38469 | 0.60893 | 0.61793
0.37446 | 0.38467 | 0.60888 | 0.61789
0.37444 | 0.38462 | 0.60884 | 0.61785
0.3744 | 0.3846 | 0.6088 | 0.61783
0.37437 | 0.38457 | 0.60876 | 0.6178
0.37433 | 0.38453 | 0.60873 | 0.61779
0.3743 | 0.3845 | 0.60868 | 0.61775
0.37428 | 0.38449 | 0.60861 | 0.6177
0.37423 | 0.38445 | 0.60856 | 0.61768
0.37422 | 0.38443 | 0.60852 | 0.61764
0.37418 | 0.3844 | 0.60849 | 0.61761
0.37414 | 0.38438 | 0.60843 | 0.61758
0.37412 | 0.38435 | 0.60838 | 0.61754
0.3741 | 0.38431 | 0.60835 | 0.6175
0.37407 | 0.38428 | 0.60831 | 0.61746
0.37403 | 0.38426 | 0.60827 | 0.61742
0.37399 | 0.38422 | 0.60822 | 0.61736
0.37394 | 0.38419 | 0.6082 | 0.61734
0.3739 | 0.38416 | 0.60816 | 0.61726
0.37387 | 0.38412 | 0.60812 | 0.61722
0.37385 | 0.38409 | 0.60808 | 0.61716
0.37381 | 0.38408 | 0.60805 | 0.61709
0.37378 | 0.38404 | 0.60798 | 0.61706
0.37374 | 0.38402 | 0.60794 | 0.61704
0.37372 | 0.384 | 0.60791 | 0.617
0.3737 | 0.38396 | 0.60786 | 0.61697
0.37367 | 0.38394 | 0.6078 | 0.61694
0.37364 | 0.38391 | 0.60774 | 0.6169
0.37361 | 0.38386 | 0.60771 | 0.61686
0.37358 | 0.38383 | 0.60764 | 0.61683
0.37353 | 0.38379 | 0.6076 | 0.61676
0.37351 | 0.38377 | 0.60757 | 0.61672
0.37348 | 0.38371 | 0.60753 | 0.61668
0.37346 | 0.38367 | 0.6075 | 0.61664
0.37343 | 0.38363 | 0.60747 | 0.61662
0.3734 | 0.38358 | 0.60742 | 0.61658
0.37337 | 0.38356 | 0.6074 | 0.61653
0.37336 | 0.38352 | 0.60737 | 0.6165
0.37333 | 0.38349 | 0.60734 | 0.61648
0.37329 | 0.38346 | 0.60729 | 0.61645
0.37325 | 0.38342 | 0.60725 | 0.61641
0.37322 | 0.3834 | 0.6072 | 0.61638
0.37321 | 0.38336 | 0.60716 | 0.61632
0.3732 | 0.38333 | 0.6071 | 0.61629
0.37315 | 0.38332 | 0.60705 | 0.61625
0.37311 | 0.38329 | 0.60702 | 0.61619
0.37308 | 0.38326 | 0.60699 | 0.61616
0.37305 | 0.38323 | 0.60696 | 0.61613
0.37304 | 0.3832 | 0.60691 | 0.61609
0.37299 | 0.38317 | 0.60688 | 0.61604
0.37296 | 0.38316 | 0.60685 | 0.61599
0.37294 | 0.38314 | 0.60681 | 0.61593
0.3729 | 0.38311 | 0.60678 | 0.61589
0.37289 | 0.38308 | 0.60676 | 0.61584
0.37288 | 0.38305 | 0.60672 | 0.6158
0.37286 | 0.38302 | 0.60669 | 0.61578
0.37282 | 0.38298 | 0.60664 | 0.61574
0.3728 | 0.38297 | 0.60659 | 0.6157
0.37277 | 0.38294 | 0.60656 | 0.61566
0.37274 | 0.38292 | 0.60653 | 0.61561
0.37269 | 0.3829 | 0.60649 | 0.61559
0.37267 | 0.38287 | 0.60643 | 0.61554
0.37263 | 0.38284 | 0.60639 | 0.61549
0.37261 | 0.38282 | 0.60634 | 0.61545
0.37258 | 0.38278 | 0.6063 | 0.61542
0.37256 | 0.38274 | 0.60626 | 0.6154
0.37254 | 0.38272 | 0.6062 | 0.61533
0.37251 | 0.3827 | 0.60615 | 0.6153
0.37249 | 0.38267 | 0.60611 | 0.61525
0.37247 | 0.38265 | 0.60608 | 0.61519
0.37244 | 0.38263 | 0.60602 | 0.61515
0.37241 | 0.3826 | 0.60595 | 0.61511
0.37238 | 0.38257 | 0.60591 | 0.61507
0.37236 | 0.38254 | 0.60589 | 0.61504
0.37232 | 0.38252 | 0.60584 | 0.61501
0.37231 | 0.3825 | 0.6058 | 0.61497
0.37228 | 0.38248 | 0.60578 | 0.61493
0.37226 | 0.38243 | 0.60573 | 0.61491
0.37224 | 0.38239 | 0.60568 | 0.61487
0.37221 | 0.38237 | 0.60566 | 0.61484
0.37219 | 0.38235 | 0.60562 | 0.6148
0.37218 | 0.38232 | 0.6056 | 0.61477
0.37216 | 0.38231 | 0.60554 | 0.61472
0.37212 | 0.38228 | 0.60551 | 0.61469
0.3721 | 0.38226 | 0.60546 | 0.61466
0.37207 | 0.38222 | 0.60543 | 0.61459
0.37205 | 0.38219 | 0.6054 | 0.61456
0.37203 | 0.38217 | 0.60537 | 0.61452
0.37199 | 0.38216 | 0.6053 | 0.61448
0.37195 | 0.38212 | 0.60524 | 0.61441
0.37192 | 0.38209 | 0.60519 | 0.61438
0.37188 | 0.38205 | 0.60514 | 0.61436
0.37185 | 0.38202 | 0.60509 | 0.61431
0.37183 | 0.38199 | 0.60505 | 0.61429
0.3718 | 0.38196 | 0.60498 | 0.61426
0.37177 | 0.38193 | 0.60491 | 0.61423
0.37173 | 0.3819 | 0.60488 | 0.61421
0.3717 | 0.38188 | 0.60485 | 0.61416
0.37167 | 0.38184 | 0.60482 | 0.61413
0.37164 | 0.38181 | 0.60478 | 0.61407
0.37162 | 0.38178 | 0.60475 | 0.61405
0.37159 | 0.38175 | 0.60471 | 0.61401
0.37157 | 0.38173 | 0.60468 | 0.61397
0.37153 | 0.38171 | 0.60462 | 0.61392
0.37151 | 0.38169 | 0.60458 | 0.61388
0.37149 | 0.38165 | 0.60453 | 0.61385
0.37144 | 0.3816 | 0.6045 | 0.61382
0.37142 | 0.38159 | 0.60447 | 0.61379
0.3714 | 0.38156 | 0.60442 | 0.61375
0.37137 | 0.38154 | 0.60441 | 0.6137
0.37135 | 0.38151 | 0.60438 | 0.61368
0.37131 | 0.38146 | 0.60436 | 0.61363
0.3713 | 0.38145 | 0.60432 | 0.61359
0.37127 | 0.38141 | 0.60427 | 0.61356
0.37122 | 0.38139 | 0.60425 | 0.61354
0.37119 | 0.38136 | 0.6042 | 0.61348
0.37117 | 0.38133 | 0.60416 | 0.61344
0.37114 | 0.38129 | 0.60409 | 0.6134
0.37111 | 0.38128 | 0.60406 | 0.61337
0.37108 | 0.38125 | 0.60402 | 0.61332
0.37105 | 0.38123 | 0.60399 | 0.61327
0.37102 | 0.38119 | 0.60395 | 0.61323
0.37099 | 0.38116 | 0.60392 | 0.61319
0.37096 | 0.38113 | 0.60388 | 0.61316
0.37093 | 0.38111 | 0.60385 | 0.61312
0.37089 | 0.38108 | 0.60382 | 0.61309
0.37086 | 0.38106 | 0.60378 | 0.61307
0.37084 | 0.38103 | 0.60374 | 0.61303
0.3708 | 0.381 | 0.60372 | 0.61297
0.37078 | 0.38097 | 0.60367 | 0.61293
0.37075 | 0.38093 | 0.60364 | 0.61287
0.37072 | 0.38092 | 0.6036 | 0.61282
0.3707 | 0.3809 | 0.60355 | 0.61279
0.37067 | 0.38087 | 0.60351 | 0.61274
0.37064 | 0.38085 | 0.60345 | 0.61271
0.37059 | 0.38081 | 0.60342 | 0.61268
0.37057 | 0.38079 | 0.6034 | 0.61263
0.37053 | 0.38077 | 0.60336 | 0.61261
0.37048 | 0.38074 | 0.60331 | 0.61257
0.37046 | 0.3807 | 0.60326 | 0.61255
0.37043 | 0.38065 | 0.60323 | 0.6125
0.37041 | 0.38063 | 0.6032 | 0.61247
0.37039 | 0.3806 | 0.60317 | 0.61244
0.37035 | 0.38058 | 0.60311 | 0.6124
0.37033 | 0.38054 | 0.60306 | 0.61235
0.37027 | 0.38051 | 0.60302 | 0.61231
0.37024 | 0.38047 | 0.60297 | 0.61227
0.37022 | 0.38042 | 0.60293 | 0.61223
0.37019 | 0.38039 | 0.60289 | 0.61219
0.37017 | 0.38037 | 0.60286 | 0.61215
0.37012 | 0.38033 | 0.60282 | 0.61209
0.3701 | 0.38029 | 0.60278 | 0.61206
0.37008 | 0.38026 | 0.60274 | 0.61203
0.37006 | 0.38025 | 0.60272 | 0.61199
0.37002 | 0.38021 | 0.6027 | 0.61195
0.36998 | 0.38019 | 0.60267 | 0.6119
0.36997 | 0.38017 | 0.60263 | 0.61188
0.36994 | 0.38014 | 0.6026 | 0.61183
0.36992 | 0.38011 | 0.60255 | 0.61179
0.36989 | 0.38008 | 0.60253 | 0.61176
0.36987 | 0.38006 | 0.6025 | 0.61172
0.36983 | 0.38004 | 0.60244 | 0.61168
0.3698 | 0.38001 | 0.60237 | 0.61163
0.36978 | 0.37999 | 0.60232 | 0.61159
0.36976 | 0.37997 | 0.60227 | 0.61156
0.36975 | 0.37995 | 0.60222 | 0.61153
0.3697 | 0.37992 | 0.60219 | 0.61151
0.36968 | 0.3799 | 0.60216 | 0.61148
0.36965 | 0.37987 | 0.60212 | 0.61144
0.36964 | 0.37986 | 0.60206 | 0.61139
0.36961 | 0.37983 | 0.60204 | 0.61136
0.36958 | 0.3798 | 0.602 | 0.61131
0.36955 | 0.37979 | 0.60195 | 0.61128
0.36952 | 0.37975 | 0.60189 | 0.61123
0.36949 | 0.37973 | 0.60187 | 0.61119
0.36948 | 0.3797 | 0.60182 | 0.61115
0.36945 | 0.37967 | 0.60178 | 0.61109
0.36943 | 0.37965 | 0.60176 | 0.61105
0.3694 | 0.37963 | 0.60173 | 0.61101
0.36939 | 0.37959 | 0.6017 | 0.61096
0.36936 | 0.37957 | 0.60167 | 0.61093
0.36933 | 0.37953 | 0.60161 | 0.61088
0.36929 | 0.37951 | 0.60156 | 0.61086
0.36927 | 0.37948 | 0.60154 | 0.61083
0.36923 | 0.37945 | 0.60149 | 0.61077
0.36922 | 0.37943 | 0.60145 | 0.61073
0.3692 | 0.37941 | 0.6014 | 0.6107
0.36918 | 0.37936 | 0.60137 | 0.61066
0.36915 | 0.37934 | 0.60133 | 0.61062
0.3691 | 0.37932 | 0.60129 | 0.61058
0.36907 | 0.3793 | 0.60126 | 0.61054
0.36905 | 0.37927 | 0.6012 | 0.61049
0.36903 | 0.37926 | 0.60116 | 0.61045
0.369 | 0.37922 | 0.60111 | 0.61043
0.36897 | 0.3792 | 0.60107 | 0.61038
0.36896 | 0.37918 | 0.60102 | 0.61035
0.36894 | 0.37915 | 0.60097 | 0.61032
0.36892 | 0.37913 | 0.60091 | 0.61029
0.36889 | 0.37912 | 0.6009 | 0.61023
0.36887 | 0.37908 | 0.60084 | 0.6102
0.36886 | 0.37906 | 0.6008 | 0.61016
0.36883 | 0.37902 | 0.60072 | 0.61012
0.36881 | 0.37899 | 0.60068 | 0.61008
0.36878 | 0.37897 | 0.60064 | 0.61004
0.36875 | 0.37894 | 0.60061 | 0.61
0.36872 | 0.3789 | 0.60054 | 0.60996
0.3687 | 0.37888 | 0.6005 | 0.60992
0.36868 | 0.37885 | 0.60046 | 0.60988
0.36863 | 0.37883 | 0.60044 | 0.60983
0.36861 | 0.37878 | 0.6004 | 0.6098
0.36859 | 0.37875 | 0.60035 | 0.60974
0.36858 | 0.37873 | 0.60029 | 0.60971
0.36856 | 0.3787 | 0.60024 | 0.60969
0.36854 | 0.37867 | 0.60018 | 0.60966
0.3685 | 0.37864 | 0.60013 | 0.60962
0.36847 | 0.37861 | 0.6001 | 0.60958
0.36845 | 0.37857 | 0.60003 | 0.60955
0.36842 | 0.37854 | 0.59998 | 0.60949
0.36841 | 0.37852 | 0.59993 | 0.60947
0.36838 | 0.3785 | 0.5999 | 0.60944
0.36836 | 0.37848 | 0.59987 | 0.6094
0.36834 | 0.37846 | 0.59983 | 0.60935
0.36832 | 0.37842 | 0.59978 | 0.60932
0.3683 | 0.37839 | 0.59974 | 0.6093
0.36827 | 0.37837 | 0.59967 | 0.60925
0.36825 | 0.37835 | 0.59963 | 0.60922
0.36823 | 0.37834 | 0.5996 | 0.60918
0.3682 | 0.37832 | 0.59955 | 0.60915
0.36819 | 0.3783 | 0.59952 | 0.6091
0.36815 | 0.37829 | 0.59949 | 0.60906
0.36811 | 0.37827 | 0.59945 | 0.60902
0.36809 | 0.37825 | 0.59942 | 0.60898
0.36807 | 0.37823 | 0.59937 | 0.60893
0.36805 | 0.3782 | 0.59932 | 0.60888
0.36803 | 0.37817 | 0.59926 | 0.60885
0.368 | 0.37814 | 0.59921 | 0.6088
0.36798 | 0.37813 | 0.59914 | 0.60878
0.36796 | 0.37811 | 0.59909 | 0.60874
0.36794 | 0.37808 | 0.59905 | 0.60869
0.36793 | 0.37804 | 0.59903 | 0.60865
0.3679 | 0.37802 | 0.59898 | 0.6086
0.36788 | 0.37798 | 0.59894 | 0.60857
0.36786 | 0.37796 | 0.5989 | 0.60853
0.36783 | 0.37791 | 0.59887 | 0.60849
0.36782 | 0.37789 | 0.59881 | 0.60847
0.36778 | 0.37787 | 0.59876 | 0.6084
0.36774 | 0.37783 | 0.59873 | 0.60836
0.36772 | 0.3778 | 0.5987 | 0.60831
0.36771 | 0.37777 | 0.59868 | 0.60827
0.36768 | 0.37773 | 0.59864 | 0.60823
0.36766 | 0.37771 | 0.59859 | 0.60818
0.36761 | 0.3777 | 0.59855 | 0.60813
0.36759 | 0.37768 | 0.59852 | 0.6081
0.36756 | 0.37766 | 0.59848 | 0.60802
0.36754 | 0.37762 | 0.59844 | 0.60797
0.36751 | 0.3776 | 0.5984 | 0.60793
0.36747 | 0.37757 | 0.59836 | 0.60789
0.36745 | 0.37755 | 0.59834 | 0.60784
0.36743 | 0.37753 | 0.59831 | 0.6078
0.36741 | 0.3775 | 0.59827 | 0.60777
0.36739 | 0.37749 | 0.59823 | 0.60772
0.36735 | 0.37746 | 0.5982 | 0.60767
0.36733 | 0.37745 | 0.59815 | 0.60765
0.36729 | 0.37743 | 0.59811 | 0.60759
0.36727 | 0.3774 | 0.59807 | 0.60757
0.36726 | 0.37737 | 0.598 | 0.60753
0.36724 | 0.37735 | 0.59796 | 0.60749
0.36722 | 0.37733 | 0.59793 | 0.60746
0.36719 | 0.37731 | 0.59788 | 0.6074
0.36716 | 0.37729 | 0.59784 | 0.60736
0.36714 | 0.37728 | 0.59781 | 0.60732
0.36713 | 0.37725 | 0.59775 | 0.60729
0.36709 | 0.37724 | 0.59773 | 0.60725
0.36705 | 0.37721 | 0.59768 | 0.60722
0.36702 | 0.37718 | 0.59766 | 0.60717
0.36698 | 0.37717 | 0.59762 | 0.60713
0.36695 | 0.37713 | 0.59754 | 0.6071
0.36692 | 0.37709 | 0.59749 | 0.60706
0.3669 | 0.37704 | 0.59745 | 0.60701
0.36688 | 0.37701 | 0.59742 | 0.60697
0.36684 | 0.37699 | 0.59736 | 0.60693
0.36682 | 0.37696 | 0.59732 | 0.60687
0.36679 | 0.37694 | 0.59728 | 0.60682
0.36677 | 0.37689 | 0.59725 | 0.60678
0.36675 | 0.37687 | 0.59723 | 0.60674
0.36672 | 0.37684 | 0.59718 | 0.60671
0.36668 | 0.37682 | 0.59713 | 0.60668
0.36667 | 0.37679 | 0.59709 | 0.60661
0.36665 | 0.37677 | 0.59706 | 0.60658
0.36663 | 0.37675 | 0.59702 | 0.60656
0.36661 | 0.37672 | 0.59698 | 0.60647
0.36658 | 0.37669 | 0.59692 | 0.60643
0.36657 | 0.37665 | 0.59689 | 0.6064
0.36655 | 0.37661 | 0.59686 | 0.60635
0.36651 | 0.3766 | 0.59682 | 0.60632
0.36649 | 0.37657 | 0.59677 | 0.60628
0.36646 | 0.37656 | 0.59675 | 0.60624
0.36643 | 0.37653 | 0.5967 | 0.6062
0.36639 | 0.3765 | 0.59666 | 0.60617
0.36637 | 0.37647 | 0.59661 | 0.60612
0.36636 | 0.37644 | 0.59657 | 0.60609
0.36634 | 0.37642 | 0.59653 | 0.60605
0.36631 | 0.37639 | 0.5965 | 0.606
0.36629 | 0.37638 | 0.59646 | 0.60596
0.36625 | 0.37636 | 0.5964 | 0.60593
0.36624 | 0.37634 | 0.59634 | 0.6059
0.36621 | 0.37631 | 0.5963 | 0.60587
0.36618 | 0.3763 | 0.59625 | 0.60584
0.36614 | 0.37628 | 0.59619 | 0.6058
0.36612 | 0.37627 | 0.59616 | 0.60575
0.36609 | 0.37624 | 0.59612 | 0.6057
0.36605 | 0.37622 | 0.59608 | 0.60566
0.36603 | 0.37619 | 0.59605 | 0.60564
0.366 | 0.37616 | 0.59601 | 0.6056
0.36597 | 0.37614 | 0.59595 | 0.60555
0.36596 | 0.37612 | 0.5959 | 0.60552
0.36593 | 0.3761 | 0.59586 | 0.60546
0.36589 | 0.37609 | 0.59582 | 0.60543
0.36587 | 0.37606 | 0.59577 | 0.60539
0.36584 | 0.37604 | 0.59573 | 0.60536
0.36582 | 0.37601 | 0.5957 | 0.60532
0.3658 | 0.37599 | 0.59567 | 0.60527
0.36578 | 0.37596 | 0.59564 | 0.60524
0.36575 | 0.37593 | 0.59561 | 0.60519
0.36572 | 0.37591 | 0.59556 | 0.60516
0.36571 | 0.37588 | 0.59553 | 0.60509
0.36569 | 0.37587 | 0.59548 | 0.60507
0.36566 | 0.37585 | 0.59544 | 0.60502
0.36564 | 0.37583 | 0.59542 | 0.60497
0.36561 | 0.37582 | 0.59538 | 0.60493
0.36559 | 0.3758 | 0.59533 | 0.60491
0.36556 | 0.37578 | 0.59528 | 0.60487
0.36554 | 0.37574 | 0.59524 | 0.60485
0.36552 | 0.37572 | 0.5952 | 0.60482
0.36548 | 0.3757 | 0.59515 | 0.60478
0.36546 | 0.37567 | 0.59513 | 0.60476
0.36544 | 0.37565 | 0.59509 | 0.6047
0.3654 | 0.37562 | 0.59506 | 0.60464
0.36536 | 0.37558 | 0.59503 | 0.6046
0.36534 | 0.37556 | 0.59501 | 0.60456
0.36531 | 0.37555 | 0.59496 | 0.60451
0.36528 | 0.37554 | 0.59493 | 0.60448
0.36526 | 0.37552 | 0.5949 | 0.60446
0.36523 | 0.3755 | 0.59485 | 0.60442
0.36521 | 0.37548 | 0.59481 | 0.6044
0.36518 | 0.37546 | 0.59477 | 0.60436
0.36515 | 0.37543 | 0.59471 | 0.60433
0.36512 | 0.37541 | 0.59466 | 0.6043
0.36509 | 0.37537 | 0.59463 | 0.60426
0.36507 | 0.37535 | 0.59459 | 0.60425
0.36505 | 0.37534 | 0.59457 | 0.6042
0.36504 | 0.37532 | 0.59454 | 0.60417
0.36501 | 0.3753 | 0.5945 | 0.60411
0.36498 | 0.37527 | 0.59448 | 0.60409
0.36496 | 0.37525 | 0.59441 | 0.60404
0.36494 | 0.37522 | 0.59436 | 0.60401
0.36492 | 0.37518 | 0.59434 | 0.60399
0.36488 | 0.37515 | 0.5943 | 0.60395
0.36486 | 0.37512 | 0.59426 | 0.6039
0.36483 | 0.37509 | 0.59423 | 0.60384
0.3648 | 0.37506 | 0.59419 | 0.60381
0.36479 | 0.37503 | 0.59414 | 0.60377
0.36476 | 0.37501 | 0.59411 | 0.60371
0.36474 | 0.37498 | 0.59409 | 0.60367
0.36471 | 0.37496 | 0.59404 | 0.60364
0.36469 | 0.37492 | 0.59402 | 0.6036
0.36464 | 0.37491 | 0.59396 | 0.60358
0.36462 | 0.37488 | 0.59392 | 0.60355
0.36458 | 0.37487 | 0.59388 | 0.60351
0.36457 | 0.37484 | 0.59385 | 0.60347
0.36454 | 0.37481 | 0.59381 | 0.60343
0.36451 | 0.37478 | 0.59379 | 0.60339
0.36448 | 0.37477 | 0.59376 | 0.60335
0.36443 | 0.37474 | 0.59374 | 0.6033
0.36442 | 0.37472 | 0.59371 | 0.60326
0.3644 | 0.3747 | 0.59365 | 0.60323
0.36437 | 0.37468 | 0.59361 | 0.6032
0.36433 | 0.37465 | 0.59357 | 0.60316
0.36431 | 0.37463 | 0.59351 | 0.60313
0.36429 | 0.37462 | 0.59347 | 0.60307
0.36427 | 0.37459 | 0.59344 | 0.60304
0.36425 | 0.37457 | 0.5934 | 0.60299
0.36423 | 0.37455 | 0.59337 | 0.60297
0.36422 | 0.37453 | 0.59333 | 0.60294
0.36419 | 0.3745 | 0.5933 | 0.6029
0.36418 | 0.37448 | 0.59326 | 0.60288
0.36417 | 0.37446 | 0.59322 | 0.60285
0.36415 | 0.37443 | 0.59316 | 0.60282
0.36412 | 0.37441 | 0.59312 | 0.60279
0.36408 | 0.37438 | 0.59308 | 0.60276
0.36407 | 0.37437 | 0.59303 | 0.60273
0.36404 | 0.37434 | 0.59299 | 0.60269
0.36402 | 0.37433 | 0.59295 | 0.60266
0.36399 | 0.3743 | 0.59292 | 0.60261
0.36396 | 0.37428 | 0.59288 | 0.60257
0.36393 | 0.37425 | 0.59285 | 0.60254
0.36391 | 0.37424 | 0.5928 | 0.6025
0.36389 | 0.37421 | 0.59276 | 0.60246
0.36388 | 0.37419 | 0.59272 | 0.60242
0.36387 | 0.37417 | 0.59268 | 0.60237
0.36384 | 0.37415 | 0.59264 | 0.60232
0.36382 | 0.37412 | 0.59259 | 0.6023
0.3638 | 0.3741 | 0.59256 | 0.60226
0.36378 | 0.37408 | 0.59251 | 0.60221
0.36377 | 0.37405 | 0.59245 | 0.60218
0.36375 | 0.37404 | 0.5924 | 0.60214
0.36373 | 0.37402 | 0.59236 | 0.6021
0.36371 | 0.37399 | 0.59232 | 0.60206
0.3637 | 0.37397 | 0.59227 | 0.60203
0.36368 | 0.37394 | 0.59223 | 0.60199
0.36366 | 0.37391 | 0.59219 | 0.60195
0.36364 | 0.37388 | 0.59215 | 0.60191
0.36363 | 0.37386 | 0.5921 | 0.60189
0.3636 | 0.37385 | 0.59206 | 0.60186
0.36357 | 0.37383 | 0.59202 | 0.60179
0.36353 | 0.37381 | 0.59197 | 0.60177
0.36352 | 0.37378 | 0.59193 | 0.60174
0.36349 | 0.37374 | 0.59191 | 0.6017
0.36346 | 0.37372 | 0.59186 | 0.60166
0.36343 | 0.37369 | 0.59184 | 0.60163
0.3634 | 0.37366 | 0.59179 | 0.60159
0.36338 | 0.37364 | 0.59174 | 0.60157
0.36336 | 0.37362 | 0.59167 | 0.60154
0.36332 | 0.3736 | 0.59164 | 0.6015
0.36329 | 0.37358 | 0.59161 | 0.60147
0.36325 | 0.37355 | 0.59157 | 0.60144
0.36321 | 0.37353 | 0.59154 | 0.60139
0.3632 | 0.37351 | 0.59149 | 0.60137
0.36318 | 0.37347 | 0.59146 | 0.60134
0.36316 | 0.37344 | 0.59142 | 0.6013
0.36312 | 0.37341 | 0.5914 | 0.60126
0.36309 | 0.37337 | 0.59137 | 0.60123
0.36306 | 0.37335 | 0.59136 | 0.60118
0.36305 | 0.37333 | 0.59132 | 0.60115
0.36302 | 0.37331 | 0.59125 | 0.60112
0.36299 | 0.37329 | 0.59121 | 0.60109
0.36297 | 0.37326 | 0.59118 | 0.60104
0.36295 | 0.37324 | 0.59115 | 0.60102
0.36293 | 0.37322 | 0.59112 | 0.60097
0.36291 | 0.37319 | 0.59105 | 0.60092
0.36289 | 0.37318 | 0.59103 | 0.6009
0.36286 | 0.37316 | 0.59099 | 0.60087
0.36282 | 0.37313 | 0.59097 | 0.60083
0.36279 | 0.37311 | 0.59093 | 0.60078
0.36277 | 0.3731 | 0.59088 | 0.60075
0.36274 | 0.37308 | 0.59082 | 0.60071
0.36273 | 0.37307 | 0.59078 | 0.60069
0.36271 | 0.37306 | 0.59076 | 0.60063
0.36267 | 0.37303 | 0.59072 | 0.60059
0.36265 | 0.37301 | 0.59068 | 0.60054
0.36261 | 0.37297 | 0.59065 | 0.6005
0.3626 | 0.37294 | 0.59061 | 0.60048
0.36258 | 0.37292 | 0.59058 | 0.60044
0.36255 | 0.37289 | 0.59054 | 0.60039
0.36252 | 0.37287 | 0.59049 | 0.60035
0.3625 | 0.37285 | 0.59043 | 0.60031
0.36248 | 0.37283 | 0.59038 | 0.60026
0.36246 | 0.37282 | 0.59035 | 0.60023
0.36243 | 0.37279 | 0.59034 | 0.60019
0.3624 | 0.37278 | 0.5903 | 0.60017
0.36236 | 0.37274 | 0.59026 | 0.60013
0.36234 | 0.37272 | 0.59023 | 0.60009
0.36232 | 0.37268 | 0.5902 | 0.60005
0.36227 | 0.37264 | 0.59016 | 0.6
0.36225 | 0.37261 | 0.59011 | 0.59996
0.36222 | 0.37259 | 0.59009 | 0.59994
0.3622 | 0.37256 | 0.59004 | 0.5999
0.36217 | 0.37253 | 0.59 | 0.59985
0.36215 | 0.37249 | 0.58996 | 0.59981
0.36211 | 0.37246 | 0.58993 | 0.59977
0.36207 | 0.37243 | 0.58989 | 0.59973
0.36206 | 0.37241 | 0.58986 | 0.5997
0.36202 | 0.37238 | 0.58982 | 0.59967
0.36199 | 0.37235 | 0.58977 | 0.59964
0.36196 | 0.37234 | 0.58974 | 0.59961
0.36193 | 0.37232 | 0.58969 | 0.59958
0.36191 | 0.3723 | 0.58963 | 0.59952
0.3619 | 0.37227 | 0.58958 | 0.59951
0.36188 | 0.37225 | 0.58956 | 0.59948
0.36187 | 0.37223 | 0.58951 | 0.59943
0.36184 | 0.37221 | 0.58946 | 0.5994
0.36183 | 0.37218 | 0.58943 | 0.59938
0.36181 | 0.37216 | 0.58939 | 0.59935
0.36179 | 0.37213 | 0.58936 | 0.59933
0.36176 | 0.3721 | 0.58931 | 0.59928
0.36173 | 0.37206 | 0.58927 | 0.59925
0.36171 | 0.37204 | 0.58922 | 0.59922
0.36168 | 0.37201 | 0.58918 | 0.59918
0.36166 | 0.37199 | 0.58915 | 0.59915
0.36164 | 0.37198 | 0.58911 | 0.59911
0.36161 | 0.37195 | 0.58907 | 0.59907
0.36159 | 0.37193 | 0.58903 | 0.59905
0.36156 | 0.37191 | 0.589 | 0.59902
0.36155 | 0.37187 | 0.58898 | 0.59899
0.36154 | 0.37185 | 0.58893 | 0.59896
0.36151 | 0.37184 | 0.5889 | 0.59892
0.3615 | 0.37182 | 0.58887 | 0.59889
0.36146 | 0.37179 | 0.58883 | 0.59885
0.36142 | 0.37177 | 0.58878 | 0.5988
0.36141 | 0.37175 | 0.58876 | 0.59875
0.36138 | 0.37173 | 0.58873 | 0.59872
0.36137 | 0.3717 | 0.58869 | 0.59868
0.36135 | 0.37167 | 0.58867 | 0.59866
0.36132 | 0.37165 | 0.58863 | 0.59862
0.36128 | 0.37163 | 0.58859 | 0.59856
0.36125 | 0.37162 | 0.58855 | 0.59852
0.36124 | 0.37161 | 0.58851 | 0.59849
0.36123 | 0.37157 | 0.58847 | 0.59845
0.36121 | 0.37154 | 0.58844 | 0.59842
0.36118 | 0.37152 | 0.5884 | 0.59837
0.36116 | 0.3715 | 0.58835 | 0.59834
0.36113 | 0.37147 | 0.58832 | 0.59831
0.3611 | 0.37144 | 0.58829 | 0.59829
0.36108 | 0.37142 | 0.58825 | 0.59825
0.36105 | 0.3714 | 0.58823 | 0.59824
0.36103 | 0.37137 | 0.5882 | 0.5982
0.36099 | 0.37135 | 0.58816 | 0.59816
0.36097 | 0.37133 | 0.58812 | 0.59812
0.36095 | 0.3713 | 0.58809 | 0.59809
0.36093 | 0.37128 | 0.58804 | 0.59805
0.36091 | 0.37126 | 0.58802 | 0.59803
0.36089 | 0.37123 | 0.58798 | 0.59799
0.36088 | 0.37121 | 0.58797 | 0.59793
0.36087 | 0.37118 | 0.58794 | 0.5979
0.36085 | 0.37116 | 0.58792 | 0.59786
0.36083 | 0.37114 | 0.58788 | 0.59783
0.3608 | 0.37111 | 0.58785 | 0.5978
0.36077 | 0.37109 | 0.58782 | 0.59776
0.36075 | 0.37105 | 0.58778 | 0.59774
0.36073 | 0.37104 | 0.58773 | 0.59772
0.36072 | 0.37102 | 0.58769 | 0.5977
0.3607 | 0.37098 | 0.58766 | 0.59764
0.36068 | 0.37096 | 0.58762 | 0.59762
0.36065 | 0.37095 | 0.58757 | 0.59758
0.36062 | 0.37093 | 0.58754 | 0.59755
0.3606 | 0.3709 | 0.58751 | 0.59753
0.36057 | 0.37088 | 0.58748 | 0.5975
0.36054 | 0.37085 | 0.58744 | 0.59746
0.36051 | 0.37083 | 0.5874 | 0.59743
0.36049 | 0.3708 | 0.58737 | 0.59738
0.36046 | 0.37078 | 0.58732 | 0.59733
0.36043 | 0.37076 | 0.58727 | 0.59729
0.36042 | 0.37074 | 0.58722 | 0.59725
0.36039 | 0.37072 | 0.5872 | 0.5972
0.36038 | 0.37071 | 0.58717 | 0.59716
0.36033 | 0.37068 | 0.58713 | 0.59713
0.36029 | 0.37066 | 0.5871 | 0.5971
0.36027 | 0.37065 | 0.58707 | 0.59707
0.36025 | 0.37063 | 0.58704 | 0.59704
0.36023 | 0.37062 | 0.58699 | 0.597
0.3602 | 0.37059 | 0.58694 | 0.59697
0.36018 | 0.37056 | 0.58692 | 0.59694
0.36016 | 0.37054 | 0.58689 | 0.59689
0.36013 | 0.3705 | 0.58686 | 0.59687
0.36011 | 0.37047 | 0.58682 | 0.59683
0.36008 | 0.37046 | 0.58678 | 0.59681
0.36004 | 0.37043 | 0.58673 | 0.59677
0.36002 | 0.3704 | 0.5867 | 0.59674
0.35999 | 0.37039 | 0.58666 | 0.59671
0.35997 | 0.37037 | 0.58662 | 0.59668
0.35996 | 0.37036 | 0.58661 | 0.59665
0.35994 | 0.37033 | 0.58657 | 0.59661
0.35991 | 0.37032 | 0.58654 | 0.59657
0.35987 | 0.37031 | 0.58649 | 0.59653
0.35984 | 0.37028 | 0.58645 | 0.5965
0.35982 | 0.37025 | 0.58642 | 0.59647
0.3598 | 0.37022 | 0.58639 | 0.59644
0.35977 | 0.3702 | 0.58636 | 0.5964
0.35975 | 0.37018 | 0.58633 | 0.59638
0.3597 | 0.37016 | 0.58631 | 0.59635
0.35968 | 0.37014 | 0.58629 | 0.5963
0.35966 | 0.37012 | 0.58625 | 0.59628
0.35963 | 0.3701 | 0.58623 | 0.59626
0.3596 | 0.37007 | 0.58619 | 0.59623
0.35959 | 0.37005 | 0.58616 | 0.5962
0.35956 | 0.37004 | 0.58614 | 0.59619
0.35954 | 0.37002 | 0.58609 | 0.59615
0.35952 | 0.37 | 0.58606 | 0.59611
0.3595 | 0.36998 | 0.58604 | 0.59609
0.35947 | 0.36996 | 0.58602 | 0.59606
0.35944 | 0.36994 | 0.58598 | 0.59602
0.35942 | 0.36992 | 0.58593 | 0.59598
0.35939 | 0.3699 | 0.58589 | 0.59593
0.35936 | 0.36987 | 0.58587 | 0.59589
0.35934 | 0.36985 | 0.58584 | 0.59586
0.35933 | 0.36982 | 0.5858 | 0.59583
0.3593 | 0.3698 | 0.58575 | 0.59578
0.35927 | 0.36978 | 0.58568 | 0.59574
0.35925 | 0.36975 | 0.5856 | 0.59569
0.35922 | 0.36972 | 0.58556 | 0.59568
0.3592 | 0.3697 | 0.58551 | 0.59565
0.35918 | 0.36968 | 0.58547 | 0.59563
0.35916 | 0.36966 | 0.58543 | 0.59557
0.35916 | 0.36964 | 0.58541 | 0.59553
0.35912 | 0.36962 | 0.58538 | 0.5955
0.35909 | 0.36959 | 0.58534 | 0.59548
0.35907 | 0.36957 | 0.58526 | 0.59544
0.35904 | 0.36954 | 0.58523 | 0.59541
0.35902 | 0.36952 | 0.5852 | 0.59537
0.35901 | 0.3695 | 0.58516 | 0.59535
0.35898 | 0.36948 | 0.58511 | 0.59532
0.35896 | 0.36946 | 0.58507 | 0.59529
0.35895 | 0.36943 | 0.58502 | 0.59527
0.35894 | 0.3694 | 0.58496 | 0.59523
0.35891 | 0.36939 | 0.58492 | 0.59518
0.35889 | 0.36938 | 0.58489 | 0.59512
0.35888 | 0.36936 | 0.58484 | 0.59509
0.35884 | 0.36933 | 0.5848 | 0.59506
0.35882 | 0.36932 | 0.58477 | 0.59502
0.35879 | 0.36931 | 0.58473 | 0.59497
0.35877 | 0.3693 | 0.5847 | 0.59494
0.35873 | 0.36925 | 0.58468 | 0.5949
0.35871 | 0.36922 | 0.58464 | 0.59488
0.35869 | 0.36919 | 0.58461 | 0.59484
0.35866 | 0.36917 | 0.58458 | 0.59481
0.35865 | 0.36914 | 0.58454 | 0.59475
0.35863 | 0.36912 | 0.58451 | 0.59472
0.3586 | 0.3691 | 0.58448 | 0.59467
0.35858 | 0.36908 | 0.58445 | 0.59466
0.35856 | 0.36905 | 0.58443 | 0.59461
0.35854 | 0.36902 | 0.58441 | 0.59458
0.35852 | 0.36901 | 0.58438 | 0.59454
0.3585 | 0.36899 | 0.58434 | 0.59451
0.35848 | 0.36897 | 0.58431 | 0.59448
0.35847 | 0.36895 | 0.58429 | 0.59444
0.35845 | 0.36893 | 0.58427 | 0.59441
0.35843 | 0.36892 | 0.58424 | 0.59437
0.3584 | 0.36889 | 0.5842 | 0.59434
0.35838 | 0.36885 | 0.58418 | 0.5943
0.35836 | 0.36884 | 0.58413 | 0.59427
0.35833 | 0.36881 | 0.58409 | 0.59423
0.35831 | 0.36879 | 0.58406 | 0.59419
0.3583 | 0.36876 | 0.58403 | 0.59417
0.35827 | 0.36874 | 0.58398 | 0.5941
0.35825 | 0.36871 | 0.58394 | 0.59405
0.35822 | 0.36868 | 0.58392 | 0.59401
0.35821 | 0.36866 | 0.58389 | 0.59397
0.35818 | 0.36863 | 0.58385 | 0.59392
0.35816 | 0.3686 | 0.58382 | 0.5939
0.35814 | 0.36858 | 0.58378 | 0.59387
0.35813 | 0.36856 | 0.58375 | 0.59382
0.35811 | 0.36853 | 0.58372 | 0.59379
0.35809 | 0.3685 | 0.58368 | 0.59377
0.35806 | 0.36848 | 0.58365 | 0.59373
0.35802 | 0.36846 | 0.58362 | 0.59368
0.35799 | 0.36844 | 0.58358 | 0.59363
0.35797 | 0.36841 | 0.58353 | 0.59361
0.35795 | 0.36839 | 0.58352 | 0.59356
0.35792 | 0.36836 | 0.58347 | 0.59353
0.3579 | 0.36835 | 0.58341 | 0.59348
0.35789 | 0.36833 | 0.58338 | 0.59345
0.35786 | 0.36829 | 0.58335 | 0.59343
0.35784 | 0.36827 | 0.58332 | 0.59339
0.35782 | 0.36825 | 0.58328 | 0.59336
0.35779 | 0.36824 | 0.58323 | 0.59335
0.35777 | 0.36823 | 0.58319 | 0.59331
0.35775 | 0.36821 | 0.58315 | 0.59327
0.35774 | 0.36819 | 0.58312 | 0.59323
0.35772 | 0.36818 | 0.58311 | 0.5932
0.3577 | 0.36815 | 0.58308 | 0.59318
0.35768 | 0.36813 | 0.58305 | 0.59314
0.35766 | 0.36811 | 0.58303 | 0.59311
0.35764 | 0.36808 | 0.583 | 0.59307
0.35761 | 0.36807 | 0.58295 | 0.59304
0.35759 | 0.36804 | 0.58291 | 0.593
0.35756 | 0.368 | 0.58287 | 0.59296
0.35752 | 0.36798 | 0.58283 | 0.59293
0.35751 | 0.36796 | 0.58276 | 0.59291
0.35749 | 0.36795 | 0.58272 | 0.59288
0.35746 | 0.36793 | 0.58266 | 0.59285
0.35744 | 0.36791 | 0.58264 | 0.59281
0.35741 | 0.36788 | 0.58261 | 0.59278
0.35738 | 0.36785 | 0.58259 | 0.59275
0.35735 | 0.36783 | 0.58254 | 0.59271
0.35732 | 0.36782 | 0.58251 | 0.59266
0.35729 | 0.36781 | 0.58247 | 0.59264
0.35726 | 0.36779 | 0.58243 | 0.5926
0.35724 | 0.36777 | 0.5824 | 0.59257
0.35722 | 0.36776 | 0.58236 | 0.59252
0.3572 | 0.36774 | 0.58233 | 0.59247
0.35718 | 0.36772 | 0.58229 | 0.59244
0.35716 | 0.36768 | 0.58225 | 0.59242
0.35714 | 0.36765 | 0.58222 | 0.59239
0.35712 | 0.36763 | 0.58219 | 0.59236
0.35709 | 0.36761 | 0.58217 | 0.59233
0.35707 | 0.36758 | 0.58214 | 0.59231
0.35704 | 0.36756 | 0.58211 | 0.5923
0.35702 | 0.36754 | 0.58209 | 0.59226
0.357 | 0.36753 | 0.58205 | 0.59222
0.35698 | 0.3675 | 0.58202 | 0.59217
0.35695 | 0.36747 | 0.58199 | 0.59214
0.35694 | 0.36744 | 0.58194 | 0.59209
0.35693 | 0.36741 | 0.58191 | 0.59204
0.35689 | 0.36739 | 0.58189 | 0.59201
0.35687 | 0.36737 | 0.58186 | 0.59198
0.35686 | 0.36735 | 0.58183 | 0.59194
0.35683 | 0.36732 | 0.5818 | 0.59191
0.3568 | 0.3673 | 0.58176 | 0.59187
0.35678 | 0.36727 | 0.58172 | 0.59185
0.35677 | 0.36725 | 0.58167 | 0.59182
0.35676 | 0.36723 | 0.58166 | 0.59179
0.35674 | 0.36721 | 0.58162 | 0.59174
0.35672 | 0.36719 | 0.58158 | 0.5917
0.3567 | 0.36718 | 0.58155 | 0.59167
0.35668 | 0.36716 | 0.58154 | 0.59164
0.35666 | 0.36713 | 0.5815 | 0.59161
0.35663 | 0.36711 | 0.58145 | 0.59159
0.35661 | 0.36709 | 0.58142 | 0.59157
0.35659 | 0.36708 | 0.58139 | 0.59154
0.35655 | 0.36706 | 0.58134 | 0.5915
0.35653 | 0.36704 | 0.58132 | 0.59147
0.35651 | 0.36701 | 0.58127 | 0.59144
0.35649 | 0.36699 | 0.58124 | 0.59142
0.35647 | 0.36698 | 0.5812 | 0.5914
0.35646 | 0.36696 | 0.58116 | 0.59139
0.35643 | 0.36693 | 0.58111 | 0.59135
0.35642 | 0.36691 | 0.58106 | 0.59132
0.35641 | 0.36689 | 0.58104 | 0.59129
0.3564 | 0.36687 | 0.58099 | 0.59126
0.35637 | 0.36685 | 0.58098 | 0.59122
0.35635 | 0.36683 | 0.58095 | 0.5912
0.35634 | 0.36682 | 0.58092 | 0.59115
0.35631 | 0.36678 | 0.58088 | 0.59112
0.35629 | 0.36677 | 0.58085 | 0.59108
0.35627 | 0.36675 | 0.58081 | 0.59105
0.35624 | 0.36674 | 0.58078 | 0.59102
0.35623 | 0.36672 | 0.58075 | 0.59098
0.35621 | 0.36669 | 0.58073 | 0.59096
0.35618 | 0.36665 | 0.5807 | 0.59092
0.35616 | 0.36662 | 0.58067 | 0.59089
0.35614 | 0.36661 | 0.58064 | 0.59085
0.35612 | 0.36659 | 0.58061 | 0.59082
0.35609 | 0.36657 | 0.58058 | 0.59078
0.35607 | 0.36656 | 0.58054 | 0.59073
0.35605 | 0.36654 | 0.58051 | 0.5907
0.35603 | 0.36653 | 0.58048 | 0.59067
0.356 | 0.36651 | 0.58043 | 0.59063
0.35598 | 0.36649 | 0.5804 | 0.59058
0.35596 | 0.36647 | 0.58034 | 0.59053
0.35594 | 0.36644 | 0.58031 | 0.5905
0.35591 | 0.36641 | 0.58028 | 0.59045
0.35588 | 0.36639 | 0.58024 | 0.59042
0.35586 | 0.36638 | 0.58021 | 0.59039
0.35584 | 0.36636 | 0.58016 | 0.59036
0.35582 | 0.36635 | 0.58014 | 0.59034
0.35581 | 0.36633 | 0.58011 | 0.5903
0.3558 | 0.36632 | 0.58005 | 0.59028
0.35576 | 0.36629 | 0.58001 | 0.59025
0.35574 | 0.36626 | 0.57998 | 0.59022
0.35571 | 0.36624 | 0.57995 | 0.59017
0.3557 | 0.36622 | 0.57991 | 0.59013
0.35567 | 0.36621 | 0.57988 | 0.5901
0.35565 | 0.36619 | 0.57985 | 0.59008
0.35564 | 0.36617 | 0.57982 | 0.59005
0.35562 | 0.36613 | 0.57978 | 0.59003
0.3556 | 0.3661 | 0.57975 | 0.58999
0.35558 | 0.36607 | 0.57972 | 0.58994
0.35556 | 0.36606 | 0.57968 | 0.5899
0.35554 | 0.36604 | 0.57965 | 0.58987
0.35551 | 0.36601 | 0.57962 | 0.58983
0.35548 | 0.36599 | 0.57955 | 0.58979
0.35546 | 0.36596 | 0.57951 | 0.58975
0.35544 | 0.36594 | 0.5795 | 0.58971
0.35543 | 0.36592 | 0.57947 | 0.58968
0.3554 | 0.3659 | 0.57944 | 0.58966
0.35538 | 0.36588 | 0.57943 | 0.58961
0.35536 | 0.36586 | 0.57936 | 0.58956
0.35534 | 0.36583 | 0.57932 | 0.58953
0.35531 | 0.36582 | 0.57928 | 0.58951
0.35529 | 0.36579 | 0.57923 | 0.58946
0.35527 | 0.36578 | 0.57919 | 0.58943
0.35523 | 0.36575 | 0.57917 | 0.58939
0.3552 | 0.36574 | 0.57913 | 0.58938
0.35518 | 0.36571 | 0.57907 | 0.58935
0.35516 | 0.36569 | 0.57904 | 0.58932
0.35513 | 0.36567 | 0.57901 | 0.58929
0.35511 | 0.36566 | 0.57898 | 0.58924
0.35509 | 0.36564 | 0.57894 | 0.5892
0.35506 | 0.36562 | 0.57892 | 0.58917
0.35506 | 0.3656 | 0.57888 | 0.58913
0.35503 | 0.36557 | 0.57885 | 0.58908
0.355 | 0.36554 | 0.57883 | 0.58906
0.35499 | 0.36551 | 0.57881 | 0.58904
0.35495 | 0.36548 | 0.57878 | 0.58899
0.35493 | 0.36546 | 0.57876 | 0.58896
0.35492 | 0.36544 | 0.57873 | 0.58892
0.35491 | 0.36542 | 0.57868 | 0.58888
0.3549 | 0.36541 | 0.57864 | 0.58887
0.35487 | 0.3654 | 0.57858 | 0.58882
0.35485 | 0.36537 | 0.57853 | 0.58877
0.35483 | 0.36536 | 0.5785 | 0.58873
0.35481 | 0.36533 | 0.57847 | 0.58866
0.3548 | 0.3653 | 0.57845 | 0.58862
0.35478 | 0.36528 | 0.57839 | 0.58858
0.35475 | 0.36525 | 0.57835 | 0.58853
0.35474 | 0.36522 | 0.57832 | 0.58852
0.35472 | 0.3652 | 0.57828 | 0.58849
0.3547 | 0.36519 | 0.57826 | 0.58845
0.35468 | 0.36516 | 0.57823 | 0.5884
0.35465 | 0.36514 | 0.5782 | 0.58838
0.35464 | 0.36512 | 0.57816 | 0.58836
0.35461 | 0.36511 | 0.57813 | 0.58831
0.35459 | 0.3651 | 0.5781 | 0.58828
0.35458 | 0.36508 | 0.57807 | 0.58825
0.35456 | 0.36507 | 0.57804 | 0.58823
0.35453 | 0.36505 | 0.57801 | 0.58819
0.35451 | 0.36502 | 0.57797 | 0.58817
0.35449 | 0.365 | 0.57795 | 0.58812
0.35446 | 0.36497 | 0.57791 | 0.58809
0.35445 | 0.36496 | 0.57787 | 0.58806
0.35443 | 0.36492 | 0.57783 | 0.58803
0.3544 | 0.36489 | 0.5778 | 0.588
0.35438 | 0.36487 | 0.57776 | 0.58796
0.35435 | 0.36486 | 0.57772 | 0.58794
0.35433 | 0.36484 | 0.57768 | 0.5879
0.35431 | 0.36482 | 0.57765 | 0.58786
0.35429 | 0.36481 | 0.57761 | 0.58782
0.35425 | 0.36478 | 0.57758 | 0.58779
0.35423 | 0.36477 | 0.57754 | 0.58776
0.35421 | 0.36475 | 0.57751 | 0.58774
0.35418 | 0.36473 | 0.57748 | 0.58772
0.35417 | 0.36472 | 0.57743 | 0.58768
0.35415 | 0.36471 | 0.57739 | 0.58764
0.35414 | 0.36469 | 0.57735 | 0.58759
0.35412 | 0.36466 | 0.57731 | 0.58754
0.35411 | 0.36464 | 0.57728 | 0.58751
0.35409 | 0.36462 | 0.57725 | 0.5875
0.35407 | 0.3646 | 0.5772 | 0.58747
0.35406 | 0.36457 | 0.57717 | 0.58744
0.35403 | 0.36456 | 0.57712 | 0.58742
0.35401 | 0.36455 | 0.57709 | 0.58738
0.35399 | 0.36453 | 0.57706 | 0.58736
0.35397 | 0.36449 | 0.57702 | 0.58732
0.35396 | 0.36447 | 0.57696 | 0.58727
0.35394 | 0.36445 | 0.57692 | 0.58724
0.35392 | 0.36442 | 0.57688 | 0.58721
0.35389 | 0.36441 | 0.57681 | 0.58718
0.35388 | 0.36439 | 0.57677 | 0.58715
0.35387 | 0.36437 | 0.57676 | 0.58711
0.35384 | 0.36436 | 0.57672 | 0.58708
0.35382 | 0.36433 | 0.5767 | 0.58705
0.35381 | 0.36431 | 0.57664 | 0.58702
0.35379 | 0.3643 | 0.5766 | 0.58699
0.35377 | 0.36429 | 0.57654 | 0.58694
0.35374 | 0.36426 | 0.57651 | 0.5869
0.35372 | 0.36423 | 0.57647 | 0.58686
0.35371 | 0.36421 | 0.57643 | 0.58682
0.35369 | 0.36419 | 0.57638 | 0.58678
0.35368 | 0.36417 | 0.57636 | 0.58673
0.35366 | 0.36411 | 0.57631 | 0.5867
0.35363 | 0.3641 | 0.57627 | 0.58667
0.35361 | 0.36409 | 0.57625 | 0.58663
0.35357 | 0.36407 | 0.5762 | 0.5866
0.35355 | 0.36406 | 0.57618 | 0.58656
0.35353 | 0.36405 | 0.57614 | 0.58654
0.35351 | 0.36403 | 0.5761 | 0.58651
0.35348 | 0.36402 | 0.57605 | 0.58647
0.35347 | 0.364 | 0.57602 | 0.58645
0.35345 | 0.36399 | 0.57598 | 0.58642
0.35343 | 0.36397 | 0.57594 | 0.58639
0.35342 | 0.36396 | 0.57591 | 0.58635
0.3534 | 0.36394 | 0.57587 | 0.58632
0.35338 | 0.36391 | 0.57583 | 0.5863
0.35336 | 0.36389 | 0.57579 | 0.58625
0.35334 | 0.36387 | 0.57573 | 0.58622
0.35332 | 0.36386 | 0.5757 | 0.58617
0.3533 | 0.36384 | 0.57567 | 0.58614
0.35327 | 0.36381 | 0.57563 | 0.58609
0.35325 | 0.3638 | 0.57559 | 0.58606
0.35323 | 0.36378 | 0.57557 | 0.58603
0.35322 | 0.36377 | 0.57553 | 0.58599
0.35321 | 0.36375 | 0.57551 | 0.58596
0.35318 | 0.36374 | 0.57549 | 0.58589
0.35318 | 0.36372 | 0.57546 | 0.58586
0.35316 | 0.3637 | 0.57545 | 0.58582
0.35315 | 0.36368 | 0.57541 | 0.58576
0.35313 | 0.36366 | 0.57537 | 0.58573
0.3531 | 0.36364 | 0.57533 | 0.58569
0.35309 | 0.36363 | 0.57531 | 0.58565
0.35307 | 0.3636 | 0.57527 | 0.58562
0.35305 | 0.36359 | 0.57521 | 0.58556
0.35303 | 0.36357 | 0.57518 | 0.58552
0.353 | 0.36354 | 0.57512 | 0.5855
0.35297 | 0.36353 | 0.57509 | 0.58548
0.35295 | 0.3635 | 0.57507 | 0.58543
0.35292 | 0.36348 | 0.57505 | 0.5854
0.35291 | 0.36345 | 0.57501 | 0.58536
0.35289 | 0.36344 | 0.57495 | 0.58532
0.35287 | 0.36342 | 0.5749 | 0.5853
0.35285 | 0.36341 | 0.57487 | 0.58526
0.35283 | 0.36339 | 0.57482 | 0.58521
0.35282 | 0.36337 | 0.57478 | 0.58518
0.35279 | 0.36335 | 0.57474 | 0.58515
0.35278 | 0.36334 | 0.57471 | 0.58512
0.35276 | 0.36331 | 0.57468 | 0.58509
0.35274 | 0.36329 | 0.57462 | 0.58506
0.35271 | 0.36328 | 0.57459 | 0.58502
0.35269 | 0.36326 | 0.57455 | 0.585
0.35267 | 0.36324 | 0.57452 | 0.58495
0.35264 | 0.36321 | 0.57449 | 0.58494
0.35262 | 0.36319 | 0.57445 | 0.58491
0.3526 | 0.36317 | 0.57441 | 0.58488
0.35258 | 0.36316 | 0.57435 | 0.58487
0.35256 | 0.36314 | 0.57431 | 0.58484
0.35254 | 0.36312 | 0.57427 | 0.5848
0.35253 | 0.3631 | 0.57424 | 0.58476
0.35251 | 0.36308 | 0.57418 | 0.58473
0.35249 | 0.36307 | 0.57414 | 0.58471
0.35246 | 0.36305 | 0.57411 | 0.58467
0.35244 | 0.36303 | 0.57407 | 0.58464
0.35243 | 0.36301 | 0.57404 | 0.58462
0.35241 | 0.363 | 0.574 | 0.58458
0.35238 | 0.36298 | 0.57396 | 0.58452
0.35237 | 0.36297 | 0.57393 | 0.58447
0.35236 | 0.36294 | 0.5739 | 0.58443
0.35233 | 0.36292 | 0.57387 | 0.58439
0.35231 | 0.3629 | 0.57384 | 0.58436
0.35229 | 0.36288 | 0.57382 | 0.58432
0.35228 | 0.36287 | 0.57378 | 0.58429
0.35225 | 0.36286 | 0.57375 | 0.58426
0.35223 | 0.36283 | 0.57372 | 0.58421
0.35221 | 0.36281 | 0.57368 | 0.58419
0.35218 | 0.3628 | 0.57365 | 0.58416
0.35217 | 0.36279 | 0.57362 | 0.58414
0.35215 | 0.36278 | 0.57359 | 0.58411
0.35213 | 0.36275 | 0.57356 | 0.5841
0.3521 | 0.36274 | 0.57353 | 0.58405
0.35208 | 0.36271 | 0.57349 | 0.58402
0.35206 | 0.36269 | 0.57345 | 0.584
0.35204 | 0.36268 | 0.57341 | 0.58395
0.35202 | 0.36265 | 0.57339 | 0.58392
0.352 | 0.36263 | 0.57335 | 0.58388
0.35198 | 0.36262 | 0.57331 | 0.58385
0.35196 | 0.36259 | 0.57326 | 0.58381
0.35193 | 0.36257 | 0.57323 | 0.58376
0.3519 | 0.36255 | 0.57322 | 0.58372
0.35189 | 0.36254 | 0.57317 | 0.5837
0.35187 | 0.36251 | 0.57315 | 0.58367
0.35185 | 0.36249 | 0.5731 | 0.58361
0.35184 | 0.36248 | 0.57307 | 0.58358
0.35181 | 0.36244 | 0.57302 | 0.58354
0.35181 | 0.36244 | 0.573 | 0.58351
0.35179 | 0.36242 | 0.57296 | 0.58347
0.35178 | 0.3624 | 0.57293 | 0.58344
0.35176 | 0.36238 | 0.5729 | 0.5834
0.35174 | 0.36236 | 0.57287 | 0.58336
0.35172 | 0.36234 | 0.57281 | 0.58332
0.35171 | 0.36232 | 0.57276 | 0.58329
0.35169 | 0.36231 | 0.57272 | 0.58327
0.35167 | 0.36228 | 0.57269 | 0.58322
0.35165 | 0.36226 | 0.57265 | 0.5832
0.35162 | 0.36224 | 0.57261 | 0.58317
0.35161 | 0.36222 | 0.57256 | 0.58313
0.35158 | 0.3622 | 0.57254 | 0.58309
0.35156 | 0.36218 | 0.57252 | 0.58306
0.35154 | 0.36216 | 0.57249 | 0.58303
0.35153 | 0.36214 | 0.57246 | 0.58301
0.35151 | 0.36213 | 0.57244 | 0.58297
0.3515 | 0.36211 | 0.5724 | 0.58294
0.35147 | 0.3621 | 0.57236 | 0.5829
0.35146 | 0.36209 | 0.57232 | 0.58287
0.35145 | 0.36207 | 0.57229 | 0.58283
0.35143 | 0.36206 | 0.57226 | 0.58279
0.35141 | 0.36204 | 0.57222 | 0.58276
0.35139 | 0.36202 | 0.57219 | 0.58274
0.35137 | 0.36201 | 0.57215 | 0.58271
0.35136 | 0.36199 | 0.57212 | 0.58269
0.35134 | 0.36196 | 0.57209 | 0.58267
0.35132 | 0.36194 | 0.57204 | 0.5826
0.3513 | 0.36192 | 0.57201 | 0.58257
0.35127 | 0.36191 | 0.57198 | 0.58256
0.35125 | 0.3619 | 0.57194 | 0.58251
0.35123 | 0.36188 | 0.5719 | 0.58248
0.3512 | 0.36186 | 0.57186 | 0.58244
0.3512 | 0.36184 | 0.57182 | 0.58242
0.35118 | 0.36181 | 0.5718 | 0.58239
0.35116 | 0.3618 | 0.57175 | 0.58237
0.35115 | 0.36177 | 0.57172 | 0.58234
0.35112 | 0.36176 | 0.57168 | 0.5823
0.35111 | 0.36174 | 0.57164 | 0.58224
0.3511 | 0.36172 | 0.5716 | 0.58221
0.35107 | 0.3617 | 0.57156 | 0.58219
0.35105 | 0.36168 | 0.57154 | 0.58215
0.35102 | 0.36167 | 0.5715 | 0.58212
0.351 | 0.36165 | 0.57146 | 0.58209
0.35098 | 0.36163 | 0.57143 | 0.58205
0.35096 | 0.36161 | 0.57139 | 0.582
0.35094 | 0.3616 | 0.57137 | 0.58198
0.35091 | 0.36158 | 0.57135 | 0.58193
0.35089 | 0.36157 | 0.57132 | 0.5819
0.35086 | 0.36155 | 0.57127 | 0.58188
0.35082 | 0.36153 | 0.57123 | 0.58184
0.3508 | 0.3615 | 0.5712 | 0.58181
0.35078 | 0.36148 | 0.57117 | 0.58178
0.35074 | 0.36146 | 0.57113 | 0.58174
0.35073 | 0.36144 | 0.57108 | 0.5817
0.35072 | 0.36143 | 0.57105 | 0.58166
0.3507 | 0.3614 | 0.57102 | 0.58163
0.35068 | 0.36138 | 0.57099 | 0.58159
0.35066 | 0.36137 | 0.57098 | 0.58154
0.35065 | 0.36134 | 0.57094 | 0.58148
0.35062 | 0.36132 | 0.5709 | 0.58145
0.35061 | 0.3613 | 0.57087 | 0.58138
0.35059 | 0.36128 | 0.57085 | 0.58137
0.35056 | 0.36127 | 0.57083 | 0.58133
0.35054 | 0.36125 | 0.57078 | 0.5813
0.35051 | 0.36122 | 0.57076 | 0.58125
0.35048 | 0.36119 | 0.57071 | 0.58122
0.35047 | 0.36118 | 0.57067 | 0.5812
0.35045 | 0.36117 | 0.57064 | 0.58117
0.35044 | 0.36115 | 0.57061 | 0.58114
0.35041 | 0.36112 | 0.57058 | 0.58111
0.35039 | 0.36108 | 0.57056 | 0.58107
0.35036 | 0.36107 | 0.57054 | 0.58104
0.35034 | 0.36106 | 0.5705 | 0.58101
0.35032 | 0.36104 | 0.57047 | 0.58097
0.3503 | 0.36102 | 0.57045 | 0.58094
0.35028 | 0.361 | 0.5704 | 0.58091
0.35025 | 0.36098 | 0.57036 | 0.58089
0.35023 | 0.36095 | 0.57032 | 0.58085
0.3502 | 0.36093 | 0.57028 | 0.58083
0.35018 | 0.36091 | 0.57023 | 0.5808
0.35017 | 0.36089 | 0.57019 | 0.58077
0.35015 | 0.36087 | 0.57012 | 0.58074
0.35012 | 0.36084 | 0.57009 | 0.58071
0.35011 | 0.36083 | 0.57006 | 0.58067
0.35008 | 0.36082 | 0.57001 | 0.58064
0.35005 | 0.3608 | 0.56998 | 0.58062
0.35004 | 0.36078 | 0.56994 | 0.58059
0.35002 | 0.36075 | 0.56991 | 0.58057
0.35 | 0.36072 | 0.5699 | 0.58055
0.34999 | 0.3607 | 0.56987 | 0.58052
0.34997 | 0.36068 | 0.56984 | 0.58049
0.34994 | 0.36066 | 0.56981 | 0.58047
0.34993 | 0.36064 | 0.56977 | 0.58044
0.34991 | 0.36062 | 0.56972 | 0.58042
0.34989 | 0.36061 | 0.56968 | 0.58039
0.34987 | 0.3606 | 0.56966 | 0.58034
0.34984 | 0.36058 | 0.56963 | 0.58031
0.34981 | 0.36056 | 0.5696 | 0.58028
0.34979 | 0.36054 | 0.56956 | 0.58025
0.34977 | 0.36051 | 0.56954 | 0.58023
0.34974 | 0.36049 | 0.56949 | 0.58022
0.34972 | 0.36047 | 0.56947 | 0.58018
0.3497 | 0.36045 | 0.56944 | 0.58015
0.34969 | 0.36044 | 0.56942 | 0.58011
0.34967 | 0.36042 | 0.56939 | 0.58006
0.34965 | 0.36041 | 0.56936 | 0.58004
0.34963 | 0.36039 | 0.56934 | 0.58
0.34961 | 0.36036 | 0.56931 | 0.57997
0.34959 | 0.36034 | 0.56929 | 0.57994
0.34957 | 0.36033 | 0.56924 | 0.57991
0.34956 | 0.36031 | 0.56922 | 0.57989
0.34954 | 0.36029 | 0.5692 | 0.57986
0.34952 | 0.36027 | 0.56916 | 0.57983
0.3495 | 0.36024 | 0.56912 | 0.57979
0.34949 | 0.36022 | 0.56907 | 0.57975
0.34947 | 0.3602 | 0.56903 | 0.57969
0.34944 | 0.36017 | 0.569 | 0.57965
0.34942 | 0.36015 | 0.56896 | 0.57961
0.34941 | 0.36013 | 0.56893 | 0.57957
0.34938 | 0.36011 | 0.56889 | 0.57955
0.34936 | 0.3601 | 0.56885 | 0.57952
0.34934 | 0.36007 | 0.56881 | 0.57949
0.34934 | 0.36004 | 0.56877 | 0.57944
0.34932 | 0.36003 | 0.56875 | 0.5794
0.3493 | 0.36001 | 0.56872 | 0.57936
0.34929 | 0.35998 | 0.56868 | 0.57932
0.34927 | 0.35997 | 0.56864 | 0.57929
0.34926 | 0.35995 | 0.5686 | 0.57926
0.34924 | 0.35994 | 0.56856 | 0.57923
0.34923 | 0.35992 | 0.56853 | 0.57922
0.34921 | 0.35989 | 0.5685 | 0.57919
0.34919 | 0.35988 | 0.56848 | 0.57917
0.34918 | 0.35985 | 0.56845 | 0.57914
0.34915 | 0.35983 | 0.5684 | 0.57911
0.34913 | 0.35982 | 0.56837 | 0.57908
0.34912 | 0.3598 | 0.56834 | 0.57907
0.3491 | 0.35977 | 0.5683 | 0.57903
0.34908 | 0.35976 | 0.56828 | 0.579
0.34907 | 0.35973 | 0.56827 | 0.57898
0.34905 | 0.35969 | 0.56824 | 0.57894
0.34903 | 0.35968 | 0.56819 | 0.57891
0.34901 | 0.35967 | 0.56816 | 0.57888
0.34898 | 0.35966 | 0.56814 | 0.57886
0.34896 | 0.35963 | 0.56812 | 0.57882
0.34894 | 0.35961 | 0.56808 | 0.57879
0.34893 | 0.35959 | 0.56806 | 0.57875
0.34891 | 0.35957 | 0.56801 | 0.57871
0.34889 | 0.35955 | 0.56799 | 0.57868
0.34888 | 0.35953 | 0.56794 | 0.57866
0.34887 | 0.3595 | 0.56791 | 0.57862
0.34885 | 0.35948 | 0.56788 | 0.5786
0.34884 | 0.35946 | 0.56785 | 0.57855
0.34881 | 0.35944 | 0.56782 | 0.57849
0.3488 | 0.35942 | 0.56778 | 0.57844
0.34878 | 0.35941 | 0.56774 | 0.5784
0.34877 | 0.35939 | 0.56771 | 0.57837
0.34875 | 0.35935 | 0.56769 | 0.57835
0.34872 | 0.35933 | 0.56766 | 0.57831
0.34871 | 0.35932 | 0.56763 | 0.57828
0.3487 | 0.3593 | 0.5676 | 0.57825
0.34868 | 0.35928 | 0.56756 | 0.57822
0.34866 | 0.35926 | 0.56754 | 0.5782
0.34865 | 0.35925 | 0.56751 | 0.57816
0.34864 | 0.35922 | 0.56749 | 0.57812
0.34862 | 0.35922 | 0.56745 | 0.5781
0.3486 | 0.35921 | 0.56742 | 0.57805
0.34858 | 0.35919 | 0.56739 | 0.57803
0.34857 | 0.35918 | 0.56735 | 0.578
0.34855 | 0.35916 | 0.56731 | 0.57798
0.34854 | 0.35914 | 0.56726 | 0.57795
0.34852 | 0.35913 | 0.56723 | 0.57792
0.3485 | 0.3591 | 0.56718 | 0.57788
0.34848 | 0.35908 | 0.56715 | 0.57786
0.34846 | 0.35905 | 0.56712 | 0.57782
0.34845 | 0.35902 | 0.56708 | 0.57779
0.34843 | 0.359 | 0.56703 | 0.57777
0.34842 | 0.35899 | 0.567 | 0.57773
0.3484 | 0.35897 | 0.56698 | 0.5777
0.34838 | 0.35896 | 0.56695 | 0.57766
0.34835 | 0.35894 | 0.56694 | 0.57762
0.34834 | 0.35891 | 0.5669 | 0.5776
0.34832 | 0.35889 | 0.56686 | 0.57758
0.34831 | 0.35887 | 0.56683 | 0.57753
0.34829 | 0.35886 | 0.5668 | 0.57751
0.34828 | 0.35885 | 0.56677 | 0.5775
0.34826 | 0.35883 | 0.56675 | 0.57746
0.34823 | 0.35882 | 0.56671 | 0.57742
0.34821 | 0.3588 | 0.56668 | 0.5774
0.34819 | 0.35879 | 0.56662 | 0.57738
0.34817 | 0.35878 | 0.56659 | 0.57735
0.34816 | 0.35876 | 0.56656 | 0.57733
0.34815 | 0.35875 | 0.56653 | 0.5773
0.34813 | 0.35874 | 0.5665 | 0.57728
0.34811 | 0.35872 | 0.56648 | 0.57725
0.3481 | 0.3587 | 0.56645 | 0.57723
0.34807 | 0.35869 | 0.56641 | 0.5772
0.34805 | 0.35866 | 0.56637 | 0.57718
0.34802 | 0.35865 | 0.56634 | 0.57715
0.34801 | 0.35863 | 0.5663 | 0.57711
0.34799 | 0.3586 | 0.56627 | 0.57709
0.34797 | 0.35858 | 0.56624 | 0.57704
0.34795 | 0.35856 | 0.56621 | 0.57701
0.34793 | 0.35855 | 0.56617 | 0.57696
0.34792 | 0.35853 | 0.56614 | 0.57693
0.3479 | 0.35852 | 0.5661 | 0.5769
0.34788 | 0.35849 | 0.56608 | 0.57687
0.34787 | 0.35847 | 0.56604 | 0.57684
0.34785 | 0.35845 | 0.56601 | 0.57681
0.34783 | 0.35843 | 0.56598 | 0.57679
0.34781 | 0.35841 | 0.56595 | 0.57674
0.3478 | 0.3584 | 0.56591 | 0.57672
0.34778 | 0.35838 | 0.56587 | 0.57667
0.34777 | 0.35836 | 0.56583 | 0.57665
0.34774 | 0.35834 | 0.56581 | 0.57663
0.34773 | 0.35832 | 0.56577 | 0.5766
0.34771 | 0.3583 | 0.56574 | 0.57657
0.3477 | 0.35828 | 0.5657 | 0.57654
0.34769 | 0.35826 | 0.56567 | 0.5765
0.34767 | 0.35825 | 0.56564 | 0.57647
0.34765 | 0.35823 | 0.56561 | 0.57645
0.34763 | 0.35821 | 0.56555 | 0.57642
0.34761 | 0.3582 | 0.56551 | 0.57639
0.3476 | 0.35819 | 0.56549 | 0.57634
0.34758 | 0.35816 | 0.56546 | 0.57631
0.34757 | 0.35814 | 0.56542 | 0.57628
0.34755 | 0.35813 | 0.56538 | 0.57626
0.34753 | 0.35811 | 0.56535 | 0.57623
0.34751 | 0.35809 | 0.56532 | 0.57621
0.3475 | 0.35807 | 0.56526 | 0.57618
0.34748 | 0.35806 | 0.56523 | 0.57616
0.34747 | 0.35803 | 0.56518 | 0.57614
0.34744 | 0.35802 | 0.56516 | 0.5761
0.34743 | 0.35799 | 0.56512 | 0.57607
0.34742 | 0.35797 | 0.56509 | 0.57605
0.3474 | 0.35795 | 0.56506 | 0.57601
0.34737 | 0.35793 | 0.56502 | 0.57598
0.34735 | 0.35792 | 0.565 | 0.57595
0.34733 | 0.3579 | 0.56497 | 0.57591
0.34731 | 0.35789 | 0.56492 | 0.57587
0.34729 | 0.35788 | 0.5649 | 0.57583
0.34727 | 0.35786 | 0.56486 | 0.5758
0.34725 | 0.35785 | 0.56483 | 0.57575
0.34724 | 0.35783 | 0.56479 | 0.57574
0.34723 | 0.35782 | 0.56475 | 0.57572
0.34722 | 0.3578 | 0.56473 | 0.57567
0.3472 | 0.35778 | 0.5647 | 0.57563
0.34718 | 0.35777 | 0.56466 | 0.57559
0.34716 | 0.35774 | 0.56462 | 0.57557
0.34713 | 0.35772 | 0.56459 | 0.57553
0.34712 | 0.35769 | 0.56456 | 0.57549
0.34709 | 0.35768 | 0.56451 | 0.57547
0.34707 | 0.35767 | 0.56446 | 0.57543
0.34705 | 0.35766 | 0.56445 | 0.57538
0.34702 | 0.35764 | 0.56442 | 0.57534
0.34699 | 0.35762 | 0.5644 | 0.57531
0.34697 | 0.3576 | 0.56437 | 0.57527
0.34695 | 0.35758 | 0.56434 | 0.57524
0.34692 | 0.35757 | 0.56432 | 0.57523
0.34691 | 0.35757 | 0.56428 | 0.57519
0.34689 | 0.35755 | 0.56424 | 0.57516
0.34687 | 0.35753 | 0.56422 | 0.57514
0.34685 | 0.3575 | 0.56417 | 0.57511
0.34683 | 0.35749 | 0.56413 | 0.57508
0.34681 | 0.35747 | 0.56411 | 0.57504
0.34679 | 0.35746 | 0.56408 | 0.575
0.34677 | 0.35744 | 0.56403 | 0.57497
0.34675 | 0.35741 | 0.56401 | 0.57493
0.34673 | 0.3574 | 0.56398 | 0.57489
0.34671 | 0.35738 | 0.56396 | 0.57484
0.3467 | 0.35736 | 0.56392 | 0.57482
0.34668 | 0.35734 | 0.5639 | 0.5748
0.34667 | 0.35733 | 0.56386 | 0.57478
0.34665 | 0.3573 | 0.56383 | 0.57473
0.34662 | 0.35729 | 0.5638 | 0.5747
0.34661 | 0.35727 | 0.56378 | 0.57466
0.34659 | 0.35724 | 0.56374 | 0.57464
0.34659 | 0.35722 | 0.56371 | 0.57461
0.34657 | 0.3572 | 0.56367 | 0.57457
0.34655 | 0.35718 | 0.56364 | 0.57455
0.34654 | 0.35716 | 0.56361 | 0.57453
0.34653 | 0.35715 | 0.56359 | 0.5745
0.34651 | 0.35712 | 0.56355 | 0.57447
0.3465 | 0.3571 | 0.56353 | 0.57444
0.34648 | 0.35708 | 0.56351 | 0.5744
0.34646 | 0.35707 | 0.56345 | 0.57437
0.34644 | 0.35705 | 0.56343 | 0.57433
0.34643 | 0.35703 | 0.5634 | 0.57429
0.34642 | 0.35703 | 0.56338 | 0.57426
0.3464 | 0.35701 | 0.56336 | 0.57422
0.34639 | 0.357 | 0.5633 | 0.57419
0.34637 | 0.35697 | 0.56327 | 0.57417
0.34635 | 0.35696 | 0.56324 | 0.57413
0.34633 | 0.35694 | 0.5632 | 0.57408
0.34629 | 0.35693 | 0.56317 | 0.57406
0.34628 | 0.35692 | 0.56314 | 0.57403
0.34624 | 0.3569 | 0.56311 | 0.57402
0.34622 | 0.35688 | 0.56309 | 0.57398
0.34621 | 0.35687 | 0.56305 | 0.57395
0.3462 | 0.35685 | 0.56302 | 0.5739
0.34617 | 0.35683 | 0.56298 | 0.57387
0.34615 | 0.35682 | 0.56296 | 0.57385
0.34613 | 0.3568 | 0.56294 | 0.57382
0.34612 | 0.35678 | 0.56291 | 0.57379
0.3461 | 0.35677 | 0.56288 | 0.57377
0.34608 | 0.35674 | 0.56287 | 0.57373
0.34607 | 0.35672 | 0.56285 | 0.5737
0.34605 | 0.3567 | 0.56281 | 0.57365
0.34604 | 0.35669 | 0.56278 | 0.57363
0.34601 | 0.35667 | 0.56273 | 0.5736
0.34599 | 0.35665 | 0.5627 | 0.57357
0.34598 | 0.35664 | 0.56266 | 0.57354
0.34597 | 0.35662 | 0.56262 | 0.57351
0.34595 | 0.3566 | 0.56258 | 0.5735
0.34592 | 0.35658 | 0.56252 | 0.57347
0.34591 | 0.35656 | 0.5625 | 0.57343
0.34589 | 0.35654 | 0.56246 | 0.5734
0.34588 | 0.35652 | 0.56243 | 0.57336
0.34586 | 0.35651 | 0.5624 | 0.57333
0.34584 | 0.3565 | 0.56237 | 0.57331
0.34583 | 0.35648 | 0.56234 | 0.57326
0.34581 | 0.35647 | 0.56232 | 0.57324
0.34579 | 0.35645 | 0.5623 | 0.57321
0.34578 | 0.35643 | 0.56228 | 0.57317
0.34576 | 0.3564 | 0.56224 | 0.57314
0.34575 | 0.35638 | 0.56222 | 0.5731
0.34574 | 0.35637 | 0.56218 | 0.57308
0.34571 | 0.35635 | 0.56216 | 0.57306
0.34569 | 0.35634 | 0.56213 | 0.57302
0.34568 | 0.35632 | 0.5621 | 0.57298
0.34567 | 0.35631 | 0.56208 | 0.57295
0.34564 | 0.35627 | 0.56204 | 0.57292
0.34563 | 0.35626 | 0.562 | 0.57289
0.34562 | 0.35624 | 0.56198 | 0.57287
0.3456 | 0.35623 | 0.56196 | 0.57281
0.34559 | 0.3562 | 0.56191 | 0.57277
0.34558 | 0.35619 | 0.56189 | 0.57275
0.34556 | 0.35617 | 0.56186 | 0.57271
0.34554 | 0.35615 | 0.56182 | 0.57268
0.34552 | 0.35614 | 0.56179 | 0.57264
0.34549 | 0.35612 | 0.56176 | 0.57261
0.34548 | 0.35611 | 0.56172 | 0.57258
0.34546 | 0.3561 | 0.56168 | 0.57255
0.34545 | 0.35608 | 0.56165 | 0.57253
0.34543 | 0.35607 | 0.56163 | 0.5725
0.3454 | 0.35605 | 0.5616 | 0.57247
0.34537 | 0.35603 | 0.56157 | 0.57245
0.34536 | 0.35601 | 0.56152 | 0.57242
0.34534 | 0.35599 | 0.56149 | 0.57238
0.34532 | 0.35598 | 0.56145 | 0.57234
0.34531 | 0.35597 | 0.56142 | 0.57231
0.3453 | 0.35595 | 0.5614 | 0.57229
0.34527 | 0.35594 | 0.56137 | 0.57226
0.34525 | 0.35592 | 0.56133 | 0.57222
0.34524 | 0.3559 | 0.56131 | 0.57218
0.34522 | 0.35588 | 0.56126 | 0.57212
0.3452 | 0.35588 | 0.5612 | 0.57209
0.34518 | 0.35586 | 0.56117 | 0.57207
0.34516 | 0.35584 | 0.56113 | 0.57203
0.34515 | 0.35583 | 0.5611 | 0.57199
0.34513 | 0.35581 | 0.56105 | 0.57198
0.34511 | 0.3558 | 0.56102 | 0.57194
0.34508 | 0.35578 | 0.561 | 0.5719
0.34507 | 0.35574 | 0.56095 | 0.57188
0.34505 | 0.35573 | 0.56091 | 0.57184
0.34503 | 0.35568 | 0.56089 | 0.57181
0.34502 | 0.35567 | 0.56087 | 0.57177
0.34499 | 0.35565 | 0.56084 | 0.57172
0.34498 | 0.35564 | 0.56081 | 0.57169
0.34495 | 0.35562 | 0.56079 | 0.57166
0.34494 | 0.35562 | 0.56076 | 0.57162
0.34492 | 0.3556 | 0.56074 | 0.57158
0.3449 | 0.35559 | 0.5607 | 0.57155
0.34489 | 0.35558 | 0.56065 | 0.57153
0.34487 | 0.35556 | 0.56061 | 0.57149
0.34484 | 0.35554 | 0.56058 | 0.57147
0.34482 | 0.35553 | 0.56056 | 0.57144
0.34481 | 0.35551 | 0.56052 | 0.57141
0.34478 | 0.35549 | 0.56049 | 0.57139
0.34477 | 0.35548 | 0.56044 | 0.57137
0.34474 | 0.35546 | 0.56041 | 0.57134
0.34472 | 0.35545 | 0.56039 | 0.57131
0.3447 | 0.35543 | 0.56037 | 0.57127
0.34468 | 0.35541 | 0.56031 | 0.57124
0.34467 | 0.35538 | 0.56027 | 0.57122
0.34466 | 0.35537 | 0.56021 | 0.57118
0.34466 | 0.35535 | 0.56019 | 0.57116
0.34462 | 0.35534 | 0.56017 | 0.57113
0.34461 | 0.35532 | 0.56014 | 0.57109
0.34459 | 0.3553 | 0.5601 | 0.57106
0.34457 | 0.35528 | 0.56008 | 0.57103
0.34455 | 0.35526 | 0.56004 | 0.57099
0.34454 | 0.35525 | 0.56 | 0.57097
0.34452 | 0.35524 | 0.55997 | 0.57094
0.34449 | 0.35521 | 0.55993 | 0.5709
0.34448 | 0.35519 | 0.5599 | 0.57088
0.34446 | 0.35516 | 0.55988 | 0.57084
0.34444 | 0.35514 | 0.55984 | 0.5708
0.34442 | 0.35514 | 0.55981 | 0.57079
0.3444 | 0.35512 | 0.55977 | 0.57077
0.34438 | 0.35511 | 0.55975 | 0.57074
0.34436 | 0.35509 | 0.55971 | 0.57071
0.34434 | 0.35507 | 0.55968 | 0.57068
0.34433 | 0.35505 | 0.55965 | 0.57065
0.34432 | 0.35503 | 0.55962 | 0.57062
0.3443 | 0.35502 | 0.55959 | 0.5706
0.34429 | 0.35499 | 0.55955 | 0.57058
0.34427 | 0.35497 | 0.55951 | 0.57054
0.34426 | 0.35495 | 0.55947 | 0.57051
0.34424 | 0.35494 | 0.55945 | 0.57047
0.34422 | 0.35492 | 0.55944 | 0.57045
0.3442 | 0.3549 | 0.5594 | 0.57043
0.34418 | 0.35488 | 0.55936 | 0.5704
0.34417 | 0.35486 | 0.55933 | 0.57038
0.34413 | 0.35485 | 0.55929 | 0.57036
0.34412 | 0.35483 | 0.55927 | 0.57032
0.34411 | 0.35481 | 0.55922 | 0.57028
0.34409 | 0.35479 | 0.55918 | 0.57027
0.34407 | 0.35477 | 0.55914 | 0.57024
0.34406 | 0.35476 | 0.55912 | 0.57021
0.34405 | 0.35474 | 0.55909 | 0.57018
0.34403 | 0.35473 | 0.55905 | 0.57014
0.34401 | 0.35472 | 0.55898 | 0.5701
0.344 | 0.3547 | 0.55896 | 0.57003
0.34399 | 0.35469 | 0.55894 | 0.57
0.34397 | 0.35468 | 0.55891 | 0.56996
0.34396 | 0.35467 | 0.55889 | 0.56991
0.34394 | 0.35465 | 0.55885 | 0.56988
0.34393 | 0.35464 | 0.55883 | 0.56985
0.34391 | 0.35462 | 0.55881 | 0.56983
0.34389 | 0.3546 | 0.55877 | 0.5698
0.34389 | 0.35459 | 0.55874 | 0.56977
0.34387 | 0.35457 | 0.55869 | 0.56975
0.34386 | 0.35456 | 0.55865 | 0.56971
0.34384 | 0.35454 | 0.55861 | 0.56969
0.34383 | 0.35452 | 0.55857 | 0.56966
0.3438 | 0.3545 | 0.55854 | 0.56964
0.34379 | 0.35449 | 0.5585 | 0.5696
0.34377 | 0.35447 | 0.55845 | 0.56958
0.34376 | 0.35445 | 0.55842 | 0.56955
0.34375 | 0.35443 | 0.55838 | 0.56952
0.34373 | 0.35442 | 0.55835 | 0.56949
0.34371 | 0.35439 | 0.55832 | 0.56947
0.3437 | 0.35438 | 0.55829 | 0.56943
0.34368 | 0.35436 | 0.55825 | 0.5694
0.34365 | 0.35435 | 0.55822 | 0.56937
0.34364 | 0.35433 | 0.5582 | 0.56935
0.34362 | 0.35431 | 0.55815 | 0.56932
0.34361 | 0.3543 | 0.55811 | 0.56929
0.34359 | 0.35428 | 0.55808 | 0.56924
0.34358 | 0.35427 | 0.55804 | 0.56921
0.34357 | 0.35425 | 0.55802 | 0.56917
0.34355 | 0.35423 | 0.55798 | 0.56913
0.34353 | 0.35421 | 0.55794 | 0.56911
0.34351 | 0.35419 | 0.55791 | 0.56908
0.3435 | 0.35417 | 0.55789 | 0.56906
0.34348 | 0.35416 | 0.55786 | 0.56904
0.34347 | 0.35414 | 0.55782 | 0.56899
0.34345 | 0.35412 | 0.55778 | 0.56895
0.34344 | 0.3541 | 0.55775 | 0.56892
0.34343 | 0.35408 | 0.55772 | 0.56889
0.34342 | 0.35407 | 0.55767 | 0.56885
0.3434 | 0.35405 | 0.55765 | 0.56882
0.34339 | 0.35404 | 0.55762 | 0.56879
0.34338 | 0.35403 | 0.55757 | 0.56875
0.34337 | 0.35402 | 0.55754 | 0.56872
0.34334 | 0.35399 | 0.55749 | 0.56868
0.34333 | 0.35398 | 0.55746 | 0.56865
0.34331 | 0.35397 | 0.55744 | 0.56862
0.3433 | 0.35395 | 0.55741 | 0.56858
0.34328 | 0.35394 | 0.55738 | 0.56854
0.34327 | 0.35393 | 0.55735 | 0.56851
0.34325 | 0.35392 | 0.55732 | 0.56848
0.34323 | 0.3539 | 0.55728 | 0.56845
0.34321 | 0.35389 | 0.55723 | 0.56841
0.3432 | 0.35386 | 0.5572 | 0.56838
0.34318 | 0.35384 | 0.55716 | 0.56835
0.34316 | 0.35383 | 0.55713 | 0.56833
0.34314 | 0.35382 | 0.5571 | 0.5683
0.34312 | 0.3538 | 0.55705 | 0.56828
0.34311 | 0.35379 | 0.55703 | 0.56826
0.3431 | 0.35378 | 0.55699 | 0.5682
0.34308 | 0.35376 | 0.55697 | 0.56817
0.34307 | 0.35374 | 0.55695 | 0.56815
0.34305 | 0.35372 | 0.55691 | 0.56808
0.34302 | 0.35371 | 0.55689 | 0.56806
0.34301 | 0.35369 | 0.55686 | 0.56805
0.34299 | 0.35368 | 0.55683 | 0.56803
0.34298 | 0.35366 | 0.5568 | 0.568
0.34296 | 0.35365 | 0.55677 | 0.56797
0.34295 | 0.35364 | 0.55674 | 0.56794
0.34293 | 0.35362 | 0.55671 | 0.56793
0.34292 | 0.35361 | 0.55668 | 0.5679
0.34291 | 0.35359 | 0.55664 | 0.56788
0.3429 | 0.35357 | 0.55661 | 0.56784
0.34288 | 0.35356 | 0.55656 | 0.56781
0.34285 | 0.35355 | 0.55651 | 0.56776
0.34282 | 0.35353 | 0.55648 | 0.56772
0.3428 | 0.35351 | 0.55647 | 0.5677
0.34279 | 0.3535 | 0.55642 | 0.56768
0.34277 | 0.35348 | 0.55639 | 0.56765
0.34275 | 0.35347 | 0.55635 | 0.5676
0.34273 | 0.35344 | 0.55631 | 0.56757
0.34272 | 0.35342 | 0.55627 | 0.56755
0.34271 | 0.3534 | 0.55621 | 0.56751
0.34269 | 0.35339 | 0.55616 | 0.56747
0.34266 | 0.35337 | 0.55612 | 0.56744
0.34264 | 0.35336 | 0.55607 | 0.5674
0.34262 | 0.35334 | 0.55602 | 0.56737
0.3426 | 0.35332 | 0.556 | 0.56734
0.34258 | 0.35331 | 0.55597 | 0.5673
0.34256 | 0.3533 | 0.55594 | 0.56728
0.34256 | 0.35329 | 0.55591 | 0.56725
0.34252 | 0.35328 | 0.55587 | 0.56721
0.34251 | 0.35326 | 0.55582 | 0.56717
0.3425 | 0.35324 | 0.55579 | 0.56714
0.34249 | 0.35323 | 0.55577 | 0.5671
0.34247 | 0.35322 | 0.55576 | 0.56707
0.34245 | 0.35321 | 0.55573 | 0.56703
0.34244 | 0.35319 | 0.55568 | 0.56702
0.34243 | 0.35318 | 0.55565 | 0.56699
0.34241 | 0.35317 | 0.55562 | 0.56697
0.34239 | 0.35316 | 0.55559 | 0.56694
0.34238 | 0.35314 | 0.55555 | 0.56689
0.34236 | 0.35313 | 0.55552 | 0.56685
0.34234 | 0.3531 | 0.55548 | 0.56679
0.34232 | 0.35309 | 0.55546 | 0.56677
0.3423 | 0.35307 | 0.55544 | 0.56674
0.34229 | 0.35305 | 0.5554 | 0.56671
0.34228 | 0.35303 | 0.55537 | 0.56668
0.34226 | 0.35303 | 0.55534 | 0.56666
0.34225 | 0.35301 | 0.55531 | 0.56664
0.34223 | 0.353 | 0.55529 | 0.56661
0.3422 | 0.35298 | 0.55526 | 0.56658
0.34218 | 0.35296 | 0.55523 | 0.56654
0.34217 | 0.35293 | 0.55521 | 0.56651
0.34215 | 0.35291 | 0.55518 | 0.56646
0.34214 | 0.35289 | 0.55514 | 0.56642
0.34211 | 0.35287 | 0.5551 | 0.5664
0.34208 | 0.35286 | 0.55509 | 0.56637
0.34206 | 0.35285 | 0.55507 | 0.56634
0.34205 | 0.35284 | 0.55504 | 0.56631
0.34202 | 0.35281 | 0.55501 | 0.56628
0.342 | 0.35279 | 0.55499 | 0.56626
0.34198 | 0.35277 | 0.55495 | 0.56623
0.34197 | 0.35276 | 0.55492 | 0.56621
0.34196 | 0.35275 | 0.55489 | 0.56616
0.34194 | 0.35273 | 0.55486 | 0.56612
0.34192 | 0.35272 | 0.55484 | 0.56609
0.34191 | 0.3527 | 0.55481 | 0.56605
0.34188 | 0.35268 | 0.55475 | 0.56602
0.34185 | 0.35265 | 0.55471 | 0.56598
0.34183 | 0.35263 | 0.55468 | 0.56595
0.34182 | 0.35262 | 0.55463 | 0.56592
0.34181 | 0.3526 | 0.55457 | 0.56587
0.34179 | 0.35258 | 0.55454 | 0.56585
0.34177 | 0.35257 | 0.55451 | 0.56581
0.34176 | 0.35256 | 0.55448 | 0.56578
0.34174 | 0.35255 | 0.55445 | 0.56575
0.34173 | 0.35254 | 0.55441 | 0.5657
0.34171 | 0.35251 | 0.55439 | 0.56565
0.3417 | 0.35249 | 0.55437 | 0.56561
0.34167 | 0.35247 | 0.55433 | 0.56558
0.34165 | 0.35245 | 0.5543 | 0.56556
0.34164 | 0.35244 | 0.55427 | 0.56552
0.34161 | 0.35242 | 0.55424 | 0.56549
0.34159 | 0.3524 | 0.55421 | 0.56547
0.34157 | 0.35239 | 0.55417 | 0.56544
0.34155 | 0.35237 | 0.55414 | 0.5654
0.34154 | 0.35236 | 0.55411 | 0.56538
0.34153 | 0.35235 | 0.55409 | 0.56535
0.34152 | 0.35233 | 0.55406 | 0.56532
0.3415 | 0.35231 | 0.55401 | 0.56529
0.34149 | 0.35231 | 0.55398 | 0.56527
0.34147 | 0.3523 | 0.55394 | 0.56524
0.34146 | 0.35228 | 0.5539 | 0.56522
0.34144 | 0.35227 | 0.55387 | 0.56518
0.34142 | 0.35225 | 0.55384 | 0.56514
0.34141 | 0.35224 | 0.55381 | 0.56513
0.3414 | 0.35223 | 0.55378 | 0.5651
0.34138 | 0.35221 | 0.55376 | 0.56506
0.34137 | 0.3522 | 0.55373 | 0.56504
0.34135 | 0.35218 | 0.55367 | 0.56502
0.34133 | 0.35217 | 0.55365 | 0.56497
0.34131 | 0.35216 | 0.55361 | 0.56494
0.3413 | 0.35214 | 0.55358 | 0.5649
0.34129 | 0.35213 | 0.55355 | 0.56487
0.34126 | 0.35211 | 0.55353 | 0.56485
0.34125 | 0.35209 | 0.5535 | 0.56482
0.34123 | 0.35207 | 0.55346 | 0.56478
0.34121 | 0.35206 | 0.55343 | 0.56476
0.34119 | 0.35205 | 0.5534 | 0.56474
0.34118 | 0.35203 | 0.55337 | 0.56471
0.34117 | 0.35202 | 0.5533 | 0.56468
0.34116 | 0.352 | 0.55327 | 0.56466
0.34114 | 0.35199 | 0.55324 | 0.56462
0.34113 | 0.35197 | 0.55322 | 0.5646
0.34111 | 0.35196 | 0.55319 | 0.56457
0.34111 | 0.35195 | 0.55316 | 0.56453
0.34109 | 0.35193 | 0.55313 | 0.56452
0.34108 | 0.35191 | 0.55311 | 0.56448
0.34106 | 0.35189 | 0.55306 | 0.56446
0.34104 | 0.35188 | 0.55303 | 0.56443
0.34102 | 0.35185 | 0.553 | 0.5644
0.34101 | 0.35184 | 0.55297 | 0.56437
0.34099 | 0.35183 | 0.55294 | 0.56432
0.34098 | 0.35182 | 0.55292 | 0.5643
0.34096 | 0.3518 | 0.55289 | 0.56424
0.34094 | 0.35179 | 0.55286 | 0.56421
0.34092 | 0.35177 | 0.55283 | 0.56418
0.34089 | 0.35175 | 0.5528 | 0.56414
0.34088 | 0.35174 | 0.55278 | 0.56411
0.34086 | 0.35173 | 0.55276 | 0.56409
0.34085 | 0.3517 | 0.55272 | 0.56407
0.34083 | 0.35169 | 0.55269 | 0.56402
0.34081 | 0.35167 | 0.55266 | 0.56401
0.34079 | 0.35166 | 0.55262 | 0.56398
0.34078 | 0.35165 | 0.55258 | 0.56395
0.34076 | 0.35164 | 0.55255 | 0.56393
0.34074 | 0.35162 | 0.55252 | 0.56389
0.34072 | 0.3516 | 0.55247 | 0.56387
0.34071 | 0.35159 | 0.55245 | 0.56383
0.34069 | 0.35158 | 0.55241 | 0.5638
0.34069 | 0.35156 | 0.55238 | 0.56377
0.34068 | 0.35154 | 0.55236 | 0.56375
0.34066 | 0.35152 | 0.55234 | 0.56373
0.34064 | 0.3515 | 0.5523 | 0.56369
0.34062 | 0.35147 | 0.55227 | 0.56368
0.34061 | 0.35146 | 0.55223 | 0.56364
0.34059 | 0.35144 | 0.55217 | 0.56362
0.34057 | 0.35143 | 0.55214 | 0.5636
0.34055 | 0.3514 | 0.55209 | 0.56358
0.34053 | 0.35139 | 0.55207 | 0.56354
0.3405 | 0.35137 | 0.55205 | 0.56351
0.34048 | 0.35136 | 0.55202 | 0.56348
0.34046 | 0.35135 | 0.55198 | 0.56343
0.34045 | 0.35132 | 0.55196 | 0.56339
0.34043 | 0.3513 | 0.55194 | 0.56335
0.34042 | 0.35128 | 0.55192 | 0.56331
0.3404 | 0.35127 | 0.55187 | 0.56327
0.34039 | 0.35125 | 0.55184 | 0.56324
0.34038 | 0.35125 | 0.55181 | 0.5632
0.34036 | 0.35124 | 0.55178 | 0.56316
0.34034 | 0.35122 | 0.55174 | 0.56314
0.34032 | 0.35121 | 0.5517 | 0.56309
0.34031 | 0.3512 | 0.55167 | 0.56307
0.34029 | 0.35119 | 0.55165 | 0.56304
0.34027 | 0.35118 | 0.55162 | 0.563
0.34026 | 0.35117 | 0.55159 | 0.56296
0.34025 | 0.35115 | 0.55156 | 0.56294
0.34024 | 0.35113 | 0.55154 | 0.56292
0.34022 | 0.35111 | 0.55152 | 0.56289
0.3402 | 0.3511 | 0.55149 | 0.56287
0.34018 | 0.35108 | 0.55146 | 0.56282
0.34017 | 0.35106 | 0.55142 | 0.56278
0.34015 | 0.35105 | 0.5514 | 0.56273
0.34014 | 0.35104 | 0.55136 | 0.5627
0.34013 | 0.35102 | 0.55133 | 0.56266
0.34011 | 0.35101 | 0.55128 | 0.56264
0.34008 | 0.351 | 0.55125 | 0.56262
0.34006 | 0.35099 | 0.55122 | 0.56259
0.34003 | 0.35096 | 0.55118 | 0.56256
0.34002 | 0.35096 | 0.55115 | 0.56252
0.34 | 0.35095 | 0.55112 | 0.56249
0.33999 | 0.35093 | 0.55109 | 0.56247
0.33997 | 0.35091 | 0.55106 | 0.56243
0.33995 | 0.3509 | 0.55102 | 0.56239
0.33993 | 0.35088 | 0.55098 | 0.56234
0.33991 | 0.35086 | 0.55092 | 0.56231
0.3399 | 0.35084 | 0.55089 | 0.56226
0.33989 | 0.35084 | 0.55086 | 0.56223
0.33988 | 0.35083 | 0.55083 | 0.5622
0.33986 | 0.3508 | 0.5508 | 0.56218
0.33984 | 0.3508 | 0.55076 | 0.56213
0.33983 | 0.35078 | 0.55074 | 0.56209
0.33982 | 0.35076 | 0.55071 | 0.56207
0.3398 | 0.35074 | 0.55067 | 0.56204
0.33979 | 0.35072 | 0.55062 | 0.56201
0.33977 | 0.3507 | 0.55058 | 0.562
0.33975 | 0.35069 | 0.55053 | 0.56198
0.33974 | 0.35067 | 0.5505 | 0.5619
0.33973 | 0.35065 | 0.55045 | 0.56187
0.33971 | 0.35063 | 0.55043 | 0.56185
0.3397 | 0.35061 | 0.55041 | 0.56181
0.33968 | 0.3506 | 0.55037 | 0.56177
0.33966 | 0.35059 | 0.55035 | 0.56175
0.33963 | 0.35057 | 0.55031 | 0.56171
0.33961 | 0.35055 | 0.55028 | 0.56168
0.3396 | 0.35054 | 0.55024 | 0.56165
0.33958 | 0.35051 | 0.55022 | 0.56162
0.33956 | 0.35049 | 0.55019 | 0.56158
0.33955 | 0.35047 | 0.55016 | 0.56156
0.33955 | 0.35045 | 0.55013 | 0.56152
0.33953 | 0.35044 | 0.55009 | 0.5615
0.33951 | 0.35043 | 0.55005 | 0.56147
0.33949 | 0.35041 | 0.55002 | 0.56144
0.33948 | 0.35039 | 0.54997 | 0.5614
0.33947 | 0.35038 | 0.54993 | 0.56138
0.33945 | 0.35037 | 0.54991 | 0.56136
0.33944 | 0.35034 | 0.54988 | 0.56132
0.33943 | 0.35033 | 0.54987 | 0.5613
0.33942 | 0.35032 | 0.54985 | 0.56126
0.33941 | 0.35031 | 0.54982 | 0.56122
0.33939 | 0.3503 | 0.54979 | 0.56119
0.33937 | 0.35028 | 0.54976 | 0.56116
0.33936 | 0.35027 | 0.54971 | 0.56113
0.33935 | 0.35026 | 0.54968 | 0.56111
0.33933 | 0.35024 | 0.54966 | 0.56109
0.33931 | 0.35023 | 0.54964 | 0.56106
0.3393 | 0.35021 | 0.54959 | 0.56104
0.33928 | 0.35018 | 0.54955 | 0.56101
0.33927 | 0.35017 | 0.54953 | 0.56098
0.33926 | 0.35016 | 0.54947 | 0.56095
0.33924 | 0.35015 | 0.54944 | 0.56093
0.33922 | 0.35014 | 0.54941 | 0.56091
0.3392 | 0.35012 | 0.54937 | 0.56089
0.33918 | 0.35011 | 0.54933 | 0.56084
0.33917 | 0.35009 | 0.54932 | 0.56082
0.33916 | 0.35008 | 0.54928 | 0.56079
0.33915 | 0.35006 | 0.54925 | 0.56078
0.33913 | 0.35004 | 0.54922 | 0.56074
0.33912 | 0.35003 | 0.54919 | 0.56072
0.3391 | 0.35002 | 0.54916 | 0.56071
0.33908 | 0.35001 | 0.54913 | 0.56069
0.33907 | 0.35 | 0.54911 | 0.56065
0.33906 | 0.34998 | 0.54908 | 0.56063
0.33902 | 0.34998 | 0.54903 | 0.56061
0.33901 | 0.34996 | 0.54901 | 0.56058
0.339 | 0.34994 | 0.54897 | 0.56056
0.33898 | 0.34992 | 0.54894 | 0.56054
0.33896 | 0.3499 | 0.5489 | 0.56051
0.33896 | 0.34989 | 0.54885 | 0.56047
0.33895 | 0.34988 | 0.54884 | 0.56045
0.33894 | 0.34987 | 0.54882 | 0.56041
0.33893 | 0.34984 | 0.54879 | 0.56039
0.33891 | 0.34983 | 0.54876 | 0.56036
0.3389 | 0.34982 | 0.54875 | 0.56033
0.33889 | 0.34981 | 0.54871 | 0.56029
0.33888 | 0.3498 | 0.54868 | 0.56025
0.33886 | 0.34978 | 0.54862 | 0.56022
0.33885 | 0.34977 | 0.5486 | 0.56019
0.33883 | 0.34975 | 0.54856 | 0.56016
0.33882 | 0.34973 | 0.54854 | 0.56012
0.3388 | 0.34972 | 0.54851 | 0.5601
0.33879 | 0.34971 | 0.54848 | 0.56006
0.33877 | 0.3497 | 0.54843 | 0.56004
0.33875 | 0.34968 | 0.54841 | 0.56
0.33873 | 0.34966 | 0.54836 | 0.55998
0.33871 | 0.34965 | 0.54834 | 0.55995
0.33869 | 0.34964 | 0.5483 | 0.55992
0.33868 | 0.34963 | 0.54826 | 0.5599
0.33865 | 0.34961 | 0.54823 | 0.55987
0.33864 | 0.3496 | 0.5482 | 0.55982
0.33863 | 0.34959 | 0.54816 | 0.5598
0.33862 | 0.34957 | 0.54813 | 0.55977
0.3386 | 0.34956 | 0.5481 | 0.55974
0.33858 | 0.34954 | 0.54807 | 0.55971
0.33857 | 0.34952 | 0.54804 | 0.55968
0.33856 | 0.34952 | 0.54803 | 0.55965
0.33854 | 0.3495 | 0.54801 | 0.55963
0.33853 | 0.34948 | 0.54799 | 0.55961
0.33851 | 0.34947 | 0.54795 | 0.55958
0.3385 | 0.34946 | 0.54791 | 0.55956
0.33849 | 0.34944 | 0.54789 | 0.55953
0.33847 | 0.34941 | 0.54786 | 0.55949
0.33845 | 0.3494 | 0.54783 | 0.55945
0.33843 | 0.34939 | 0.54781 | 0.55941
0.33842 | 0.34937 | 0.54778 | 0.55936
0.33841 | 0.34936 | 0.54775 | 0.55934
0.33839 | 0.34934 | 0.54772 | 0.55931
0.33839 | 0.34933 | 0.54769 | 0.55927
0.33837 | 0.34932 | 0.54766 | 0.55924
0.33835 | 0.3493 | 0.54763 | 0.55922
0.33834 | 0.34929 | 0.54759 | 0.55919
0.33832 | 0.34928 | 0.54757 | 0.55916
0.33831 | 0.34927 | 0.54752 | 0.55912
0.33829 | 0.34926 | 0.54746 | 0.5591
0.33828 | 0.34925 | 0.54742 | 0.55908
0.33826 | 0.34922 | 0.54739 | 0.55905
0.33824 | 0.3492 | 0.54736 | 0.559
0.33823 | 0.34919 | 0.54734 | 0.55898
0.33821 | 0.34917 | 0.54733 | 0.55895
0.3382 | 0.34915 | 0.54729 | 0.55892
0.33817 | 0.34914 | 0.54726 | 0.5589
0.33815 | 0.34912 | 0.54724 | 0.55887
0.33814 | 0.3491 | 0.54721 | 0.55883
0.33812 | 0.34908 | 0.54719 | 0.55879
0.3381 | 0.34906 | 0.54715 | 0.55876
0.33809 | 0.34904 | 0.54711 | 0.55874
0.33807 | 0.34903 | 0.54708 | 0.55871
0.33806 | 0.34901 | 0.54703 | 0.55868
0.33804 | 0.349 | 0.547 | 0.55863
0.33802 | 0.34898 | 0.54697 | 0.5586
0.338 | 0.34896 | 0.54694 | 0.55858
0.33798 | 0.34894 | 0.5469 | 0.55856
0.33797 | 0.34893 | 0.54687 | 0.55853
0.33796 | 0.34892 | 0.54684 | 0.5585
0.33794 | 0.34891 | 0.54682 | 0.55848
0.33792 | 0.34889 | 0.54679 | 0.55844
0.33791 | 0.34888 | 0.54676 | 0.55842
0.33789 | 0.34886 | 0.54674 | 0.55839
0.33787 | 0.34885 | 0.54672 | 0.55838
0.33787 | 0.34883 | 0.54669 | 0.55834
0.33785 | 0.34882 | 0.54665 | 0.55831
0.33783 | 0.3488 | 0.54662 | 0.55828
0.33782 | 0.34879 | 0.54657 | 0.55825
0.33781 | 0.34876 | 0.54654 | 0.55823
0.3378 | 0.34875 | 0.5465 | 0.5582
0.33778 | 0.34873 | 0.54648 | 0.55817
0.33776 | 0.34871 | 0.54644 | 0.55814
0.33775 | 0.3487 | 0.5464 | 0.55811
0.33772 | 0.34869 | 0.54638 | 0.55809
0.33771 | 0.34868 | 0.54636 | 0.55804
0.3377 | 0.34867 | 0.54632 | 0.55801
0.33768 | 0.34866 | 0.5463 | 0.55797
0.33766 | 0.34864 | 0.54627 | 0.55795
0.33764 | 0.34864 | 0.54624 | 0.55793
0.33763 | 0.34862 | 0.54622 | 0.55792
0.33761 | 0.34861 | 0.54619 | 0.5579
0.3376 | 0.34859 | 0.54617 | 0.55787
0.33759 | 0.34859 | 0.54613 | 0.55784
0.33757 | 0.34857 | 0.54611 | 0.55782
0.33755 | 0.34855 | 0.54607 | 0.5578
0.33754 | 0.34853 | 0.54605 | 0.55776
0.33752 | 0.3485 | 0.54601 | 0.55772
0.33751 | 0.34849 | 0.54597 | 0.5577
0.33749 | 0.34847 | 0.54594 | 0.55768
0.33748 | 0.34845 | 0.5459 | 0.55765
0.33746 | 0.34843 | 0.54586 | 0.55762
0.33744 | 0.34842 | 0.54583 | 0.55759
0.33743 | 0.3484 | 0.54579 | 0.55755
0.33741 | 0.34839 | 0.54576 | 0.55753
0.3374 | 0.34837 | 0.54573 | 0.55751
0.33738 | 0.34836 | 0.5457 | 0.55749
0.33737 | 0.34833 | 0.54566 | 0.55746
0.33735 | 0.34832 | 0.54564 | 0.55745
0.33734 | 0.3483 | 0.54562 | 0.55742
0.33732 | 0.34829 | 0.54559 | 0.55739
0.3373 | 0.34827 | 0.54556 | 0.55737
0.33729 | 0.34826 | 0.54552 | 0.55734
0.33728 | 0.34825 | 0.5455 | 0.55732
0.33726 | 0.34823 | 0.54546 | 0.5573
0.33725 | 0.34821 | 0.54543 | 0.55728
0.33723 | 0.3482 | 0.54541 | 0.55726
0.33721 | 0.34819 | 0.54538 | 0.55722
0.3372 | 0.34817 | 0.54535 | 0.5572
0.33718 | 0.34816 | 0.54531 | 0.55716
0.33716 | 0.34814 | 0.54529 | 0.55714
0.33714 | 0.34813 | 0.54525 | 0.55711
0.33712 | 0.34811 | 0.54522 | 0.55708
0.33711 | 0.3481 | 0.54519 | 0.55705
0.3371 | 0.34808 | 0.54516 | 0.55704
0.33708 | 0.34806 | 0.54513 | 0.557
0.33706 | 0.34804 | 0.5451 | 0.55697
0.33704 | 0.34802 | 0.54508 | 0.55695
0.33702 | 0.34801 | 0.54505 | 0.55692
0.337 | 0.34799 | 0.54501 | 0.55688
0.33698 | 0.34797 | 0.54496 | 0.55684
0.33697 | 0.34795 | 0.54493 | 0.55681
0.33695 | 0.34794 | 0.54489 | 0.55679
0.33693 | 0.34793 | 0.54485 | 0.55675
0.33692 | 0.34792 | 0.54483 | 0.55672
0.3369 | 0.3479 | 0.5448 | 0.5567
0.33689 | 0.34789 | 0.54478 | 0.55666
0.33689 | 0.34787 | 0.54473 | 0.55663
0.33687 | 0.34786 | 0.54469 | 0.55662
0.33686 | 0.34784 | 0.54467 | 0.55657
0.33684 | 0.34783 | 0.54466 | 0.55654
0.33683 | 0.34782 | 0.54464 | 0.55652
0.33682 | 0.3478 | 0.54462 | 0.55649
0.3368 | 0.34779 | 0.54459 | 0.55647
0.33679 | 0.34778 | 0.54457 | 0.55644
0.33677 | 0.34776 | 0.54454 | 0.55642
0.33675 | 0.34775 | 0.54451 | 0.55639
0.33674 | 0.34773 | 0.54447 | 0.55633
0.33672 | 0.34771 | 0.54443 | 0.55631
0.3367 | 0.3477 | 0.54441 | 0.55627
0.33668 | 0.34767 | 0.54438 | 0.55625
0.33666 | 0.34766 | 0.54435 | 0.55623
0.33665 | 0.34764 | 0.54431 | 0.55621
0.33664 | 0.34764 | 0.54426 | 0.55618
0.33662 | 0.34762 | 0.54423 | 0.55614
0.3366 | 0.34761 | 0.5442 | 0.55611
0.33659 | 0.34759 | 0.54418 | 0.55609
0.33658 | 0.34758 | 0.54414 | 0.55606
0.33656 | 0.34757 | 0.54411 | 0.55602
0.33654 | 0.34755 | 0.54407 | 0.55599
0.33652 | 0.34754 | 0.54405 | 0.55597
0.33651 | 0.34751 | 0.54403 | 0.55594
0.3365 | 0.3475 | 0.54401 | 0.55591
0.33647 | 0.34749 | 0.54398 | 0.55588
0.33645 | 0.34747 | 0.54395 | 0.55584
0.33644 | 0.34746 | 0.54391 | 0.5558
0.33642 | 0.34744 | 0.54389 | 0.55578
0.3364 | 0.34743 | 0.54384 | 0.55575
0.33639 | 0.34742 | 0.54381 | 0.55573
0.33638 | 0.34742 | 0.5438 | 0.5557
0.33637 | 0.34741 | 0.54376 | 0.55567
0.33635 | 0.3474 | 0.54373 | 0.55564
0.33634 | 0.34738 | 0.54369 | 0.55562
0.33631 | 0.34736 | 0.54366 | 0.55558
0.33629 | 0.34734 | 0.54363 | 0.55556
0.33628 | 0.34732 | 0.5436 | 0.55553
0.33627 | 0.3473 | 0.54356 | 0.55551
0.33626 | 0.34728 | 0.54353 | 0.55548
0.33625 | 0.34727 | 0.5435 | 0.55545
0.33623 | 0.34726 | 0.54348 | 0.55543
0.33621 | 0.34724 | 0.54346 | 0.5554
0.33619 | 0.34723 | 0.54344 | 0.55538
0.33618 | 0.34722 | 0.5434 | 0.55535
0.33617 | 0.3472 | 0.54335 | 0.55529
0.33616 | 0.34718 | 0.54332 | 0.55527
0.33614 | 0.34716 | 0.54329 | 0.55524
0.33612 | 0.34714 | 0.54324 | 0.55521
0.3361 | 0.34713 | 0.54322 | 0.55518
0.33608 | 0.34712 | 0.54319 | 0.55516
0.33607 | 0.3471 | 0.54317 | 0.55513
0.33606 | 0.34709 | 0.54314 | 0.55508
0.33605 | 0.34707 | 0.54311 | 0.55505
0.33604 | 0.34706 | 0.54309 | 0.555
0.33602 | 0.34703 | 0.54307 | 0.55498
0.33601 | 0.34701 | 0.54304 | 0.55496
0.336 | 0.347 | 0.54303 | 0.55492
0.33599 | 0.34699 | 0.54299 | 0.55489
0.33597 | 0.34698 | 0.54296 | 0.55485
0.33596 | 0.34695 | 0.54293 | 0.55482
0.33595 | 0.34694 | 0.5429 | 0.55478
0.33593 | 0.34692 | 0.54287 | 0.55476
0.33592 | 0.3469 | 0.54283 | 0.55474
0.3359 | 0.34688 | 0.54281 | 0.55469
0.33588 | 0.34687 | 0.54277 | 0.55467
0.33586 | 0.34684 | 0.54274 | 0.55465
0.33585 | 0.34682 | 0.54272 | 0.55461
0.33584 | 0.34681 | 0.54268 | 0.55459
0.33582 | 0.34679 | 0.54263 | 0.55457
0.33581 | 0.34678 | 0.54261 | 0.55453
0.33581 | 0.34677 | 0.54259 | 0.55448
0.33579 | 0.34675 | 0.54256 | 0.55444
0.33577 | 0.34673 | 0.54253 | 0.55441
0.33576 | 0.34671 | 0.54249 | 0.55436
0.33575 | 0.34669 | 0.54246 | 0.55432
0.33573 | 0.34668 | 0.54242 | 0.55428
0.33571 | 0.34667 | 0.5424 | 0.55426
0.33569 | 0.34666 | 0.54238 | 0.55422
0.33568 | 0.34664 | 0.54236 | 0.55417
0.33566 | 0.34663 | 0.54233 | 0.55415
0.33565 | 0.34662 | 0.5423 | 0.55413
0.33563 | 0.34661 | 0.54226 | 0.5541
0.33562 | 0.34659 | 0.54225 | 0.55408
0.33561 | 0.34657 | 0.54223 | 0.55404
0.33559 | 0.34656 | 0.54221 | 0.55401
0.33555 | 0.34654 | 0.54219 | 0.55395
0.33553 | 0.34651 | 0.54215 | 0.55392
0.33552 | 0.3465 | 0.5421 | 0.55389
0.3355 | 0.34649 | 0.54207 | 0.55387
0.33549 | 0.34647 | 0.54203 | 0.55384
0.33548 | 0.34646 | 0.54198 | 0.55381
0.33546 | 0.34644 | 0.54196 | 0.55379
0.33544 | 0.34643 | 0.54192 | 0.55377
0.33543 | 0.34641 | 0.5419 | 0.55374
0.33542 | 0.3464 | 0.54187 | 0.55371
0.3354 | 0.34638 | 0.54185 | 0.55369
0.33539 | 0.34637 | 0.5418 | 0.55367
0.33537 | 0.34635 | 0.54177 | 0.55364
0.33536 | 0.34633 | 0.54174 | 0.55362
0.33535 | 0.34632 | 0.54171 | 0.55359
0.33534 | 0.3463 | 0.54166 | 0.55355
0.33533 | 0.34628 | 0.54162 | 0.55353
0.33531 | 0.34627 | 0.54158 | 0.5535
0.33531 | 0.34625 | 0.54156 | 0.55348
0.33529 | 0.34624 | 0.54154 | 0.55346
0.33527 | 0.34621 | 0.54152 | 0.55342
0.33525 | 0.3462 | 0.54148 | 0.55341
0.33523 | 0.34618 | 0.54142 | 0.55336
0.33522 | 0.34617 | 0.5414 | 0.55333
0.3352 | 0.34615 | 0.54137 | 0.55328
0.33519 | 0.34613 | 0.54132 | 0.55326
0.33516 | 0.34612 | 0.54131 | 0.55323
0.33514 | 0.3461 | 0.54128 | 0.5532
0.33513 | 0.34609 | 0.54123 | 0.55317
0.33512 | 0.34608 | 0.54121 | 0.55314
0.3351 | 0.34607 | 0.54118 | 0.5531
0.33509 | 0.34605 | 0.54115 | 0.55309
0.33508 | 0.34604 | 0.54112 | 0.55306
0.33507 | 0.34603 | 0.54109 | 0.55304
0.33505 | 0.34602 | 0.54107 | 0.55301
0.33504 | 0.34601 | 0.54105 | 0.55298
0.33503 | 0.346 | 0.54102 | 0.55295
0.33501 | 0.34599 | 0.54099 | 0.55292
0.335 | 0.34597 | 0.54095 | 0.5529
0.33498 | 0.34594 | 0.54092 | 0.55287
0.33496 | 0.34593 | 0.5409 | 0.55284
0.33495 | 0.34591 | 0.54086 | 0.55282
0.33494 | 0.34589 | 0.54083 | 0.55278
0.33491 | 0.34588 | 0.5408 | 0.55274
0.3349 | 0.34587 | 0.54076 | 0.5527
0.33488 | 0.34585 | 0.54074 | 0.55266
0.33487 | 0.34583 | 0.54071 | 0.55264
0.33485 | 0.34582 | 0.54067 | 0.5526
0.33483 | 0.3458 | 0.54064 | 0.55257
0.33482 | 0.34579 | 0.54059 | 0.55255
0.3348 | 0.34578 | 0.54057 | 0.55253
0.33479 | 0.34576 | 0.54055 | 0.55251
0.33477 | 0.34574 | 0.54051 | 0.55249
0.33475 | 0.34572 | 0.54048 | 0.55245
0.33474 | 0.3457 | 0.54045 | 0.55242
0.33472 | 0.34569 | 0.54042 | 0.55238
0.33471 | 0.34568 | 0.54038 | 0.55237
0.33469 | 0.34566 | 0.54035 | 0.55232
0.33468 | 0.34565 | 0.54032 | 0.55228
0.33467 | 0.34562 | 0.54029 | 0.55226
0.33465 | 0.34561 | 0.54025 | 0.55222
0.33464 | 0.3456 | 0.54023 | 0.5522
0.33464 | 0.34558 | 0.54019 | 0.55216
0.33462 | 0.34557 | 0.54016 | 0.55214
0.33461 | 0.34556 | 0.54014 | 0.55212
0.33459 | 0.34554 | 0.5401 | 0.5521
0.33457 | 0.34553 | 0.54008 | 0.55207
0.33455 | 0.34551 | 0.54005 | 0.55204
0.33454 | 0.34549 | 0.54002 | 0.55201
0.33452 | 0.34548 | 0.53997 | 0.55199
0.3345 | 0.34546 | 0.53993 | 0.55196
0.33449 | 0.34545 | 0.5399 | 0.55191
0.33447 | 0.34545 | 0.53988 | 0.55188
0.33446 | 0.34544 | 0.53987 | 0.55186
0.33444 | 0.34542 | 0.53982 | 0.55183
0.33443 | 0.34542 | 0.53979 | 0.55181
0.33441 | 0.34541 | 0.53976 | 0.55178
0.3344 | 0.3454 | 0.53974 | 0.55175
0.33438 | 0.34538 | 0.53971 | 0.55172
0.33436 | 0.34537 | 0.53967 | 0.5517
0.33435 | 0.34536 | 0.53965 | 0.55168
0.33434 | 0.34534 | 0.53962 | 0.55166
0.33433 | 0.34532 | 0.5396 | 0.55162
0.33431 | 0.34531 | 0.53957 | 0.55161
0.33429 | 0.34531 | 0.53955 | 0.55158
0.33427 | 0.34528 | 0.53951 | 0.55156
0.33425 | 0.34527 | 0.53948 | 0.55149
0.33424 | 0.34524 | 0.53946 | 0.55146
0.33423 | 0.34523 | 0.53942 | 0.55143
0.33422 | 0.34521 | 0.53939 | 0.55141
0.3342 | 0.3452 | 0.53935 | 0.55136
0.33419 | 0.34518 | 0.53932 | 0.55133
0.33418 | 0.34517 | 0.53929 | 0.55131
0.33417 | 0.34515 | 0.53926 | 0.5513
0.33415 | 0.34514 | 0.53922 | 0.55127
0.33414 | 0.34512 | 0.53918 | 0.55123
0.33412 | 0.34511 | 0.53913 | 0.5512
0.3341 | 0.3451 | 0.53908 | 0.55117
0.33409 | 0.34508 | 0.53905 | 0.55116
0.33408 | 0.34507 | 0.53901 | 0.55113
0.33405 | 0.34505 | 0.53899 | 0.55111
0.33404 | 0.34503 | 0.53896 | 0.55108
0.33403 | 0.34501 | 0.53894 | 0.55106
0.33402 | 0.345 | 0.53891 | 0.55102
0.334 | 0.34498 | 0.53889 | 0.55098
0.33398 | 0.34496 | 0.53887 | 0.55096
0.33397 | 0.34494 | 0.53884 | 0.55093
0.33396 | 0.34493 | 0.5388 | 0.55089
0.33394 | 0.34491 | 0.53878 | 0.55088
0.33393 | 0.3449 | 0.53875 | 0.55085
0.33391 | 0.34488 | 0.53871 | 0.5508
0.3339 | 0.34486 | 0.53868 | 0.55078
0.33388 | 0.34484 | 0.53864 | 0.55074
0.33386 | 0.34483 | 0.53862 | 0.55069
0.33385 | 0.34482 | 0.53859 | 0.55067
0.33383 | 0.3448 | 0.53856 | 0.55065
0.33382 | 0.34479 | 0.53853 | 0.55062
0.33381 | 0.34477 | 0.5385 | 0.55059
0.33378 | 0.34475 | 0.53847 | 0.55056
0.33376 | 0.34474 | 0.53844 | 0.55054
0.33375 | 0.34473 | 0.53841 | 0.5505
0.33374 | 0.34472 | 0.53838 | 0.55048
0.33371 | 0.34471 | 0.53835 | 0.55044
0.3337 | 0.3447 | 0.53833 | 0.55043
0.33369 | 0.34468 | 0.53831 | 0.55041
0.33367 | 0.34467 | 0.53827 | 0.55037
0.33365 | 0.34466 | 0.53826 | 0.55034
0.33363 | 0.34464 | 0.53823 | 0.55031
0.33362 | 0.34463 | 0.53821 | 0.55029
0.3336 | 0.34461 | 0.53818 | 0.55026
0.33359 | 0.34461 | 0.53816 | 0.55024
0.33357 | 0.34459 | 0.53814 | 0.55018
0.33356 | 0.34458 | 0.53812 | 0.55015
0.33355 | 0.34456 | 0.5381 | 0.55013
0.33353 | 0.34455 | 0.53807 | 0.5501
0.33352 | 0.34453 | 0.53804 | 0.55007
0.33351 | 0.34452 | 0.538 | 0.55004
0.33349 | 0.3445 | 0.53798 | 0.55
0.33347 | 0.34448 | 0.53795 | 0.54997
0.33346 | 0.34446 | 0.53792 | 0.54995
0.33344 | 0.34444 | 0.53789 | 0.54993
0.33343 | 0.34443 | 0.53786 | 0.5499
0.33342 | 0.34441 | 0.53782 | 0.54987
0.3334 | 0.34439 | 0.53779 | 0.54984
0.33339 | 0.34437 | 0.53774 | 0.54982
0.33338 | 0.34435 | 0.53771 | 0.5498
0.33337 | 0.34434 | 0.53768 | 0.54977
0.33335 | 0.34433 | 0.53765 | 0.54975
0.33333 | 0.34431 | 0.53763 | 0.54971
0.33332 | 0.34429 | 0.53762 | 0.54967
0.33331 | 0.34427 | 0.53758 | 0.54966
0.33329 | 0.34426 | 0.53755 | 0.54963
0.33328 | 0.34424 | 0.53752 | 0.5496
0.33327 | 0.34423 | 0.53748 | 0.54957
0.33325 | 0.34422 | 0.53745 | 0.54956
0.33324 | 0.3442 | 0.53742 | 0.54953
0.33322 | 0.34418 | 0.53739 | 0.5495
0.3332 | 0.34417 | 0.53736 | 0.54949
0.33319 | 0.34416 | 0.53733 | 0.54946
0.33318 | 0.34414 | 0.53729 | 0.54943
0.33316 | 0.34413 | 0.53726 | 0.54941
0.33315 | 0.34411 | 0.53723 | 0.54939
0.33314 | 0.34409 | 0.53719 | 0.54937
0.33311 | 0.34408 | 0.53715 | 0.54935
0.3331 | 0.34407 | 0.53712 | 0.54931
0.33309 | 0.34406 | 0.53709 | 0.54929
0.33308 | 0.34404 | 0.53707 | 0.54927
0.33306 | 0.34404 | 0.53702 | 0.54924
0.33303 | 0.34402 | 0.53699 | 0.54921
0.33303 | 0.34401 | 0.53697 | 0.54919
0.33301 | 0.34399 | 0.53694 | 0.54916
0.333 | 0.34397 | 0.53691 | 0.54914
0.33299 | 0.34395 | 0.53686 | 0.54909
0.33297 | 0.34395 | 0.53684 | 0.54906
0.33296 | 0.34394 | 0.53679 | 0.54904
0.33295 | 0.34393 | 0.53677 | 0.549
0.33293 | 0.34391 | 0.53674 | 0.54898
0.33291 | 0.34389 | 0.53671 | 0.54894
0.3329 | 0.34387 | 0.53667 | 0.54891
0.33289 | 0.34385 | 0.53663 | 0.54887
0.33287 | 0.34384 | 0.53659 | 0.54885
0.33286 | 0.34383 | 0.53657 | 0.54884
0.33284 | 0.34382 | 0.53655 | 0.54883
0.33283 | 0.34381 | 0.5365 | 0.54878
0.33282 | 0.3438 | 0.53647 | 0.54876
0.3328 | 0.34379 | 0.53644 | 0.54873
0.33279 | 0.34377 | 0.53641 | 0.5487
0.33278 | 0.34377 | 0.53637 | 0.54868
0.33277 | 0.34375 | 0.53634 | 0.54865
0.33275 | 0.34373 | 0.5363 | 0.54863
0.33273 | 0.34371 | 0.53628 | 0.54861
0.33271 | 0.34369 | 0.53625 | 0.54859
0.3327 | 0.34368 | 0.53622 | 0.54857
0.33269 | 0.34366 | 0.5362 | 0.54856
0.33268 | 0.34365 | 0.53618 | 0.54852
0.33267 | 0.34364 | 0.53615 | 0.54849
0.33265 | 0.34362 | 0.53613 | 0.54847
0.33264 | 0.34361 | 0.5361 | 0.54845
0.33263 | 0.3436 | 0.53606 | 0.54843
0.33262 | 0.34359 | 0.53604 | 0.54839
0.33261 | 0.34357 | 0.53601 | 0.54835
0.33259 | 0.34356 | 0.53599 | 0.54832
0.33258 | 0.34355 | 0.53597 | 0.5483
0.33257 | 0.34353 | 0.53595 | 0.54828
0.33256 | 0.34352 | 0.53593 | 0.54825
0.33254 | 0.34351 | 0.53591 | 0.54822
0.33253 | 0.34349 | 0.53588 | 0.5482
0.33251 | 0.34348 | 0.53585 | 0.54817
0.3325 | 0.34347 | 0.53583 | 0.54814
0.33248 | 0.34344 | 0.5358 | 0.5481
0.33247 | 0.34343 | 0.53577 | 0.54807
0.33245 | 0.34342 | 0.53574 | 0.54804
0.33243 | 0.34341 | 0.5357 | 0.54802
0.33241 | 0.3434 | 0.53566 | 0.54798
0.33239 | 0.34339 | 0.53563 | 0.54794
0.33237 | 0.34338 | 0.53559 | 0.54791
0.33235 | 0.34336 | 0.53557 | 0.54789
0.33233 | 0.34335 | 0.53554 | 0.54786
0.33231 | 0.34334 | 0.53551 | 0.54783
0.33229 | 0.34332 | 0.53549 | 0.5478
0.33228 | 0.3433 | 0.53547 | 0.54777
0.33227 | 0.34328 | 0.53545 | 0.54774
0.33225 | 0.34326 | 0.53541 | 0.5477
0.33224 | 0.34325 | 0.53536 | 0.54766
0.33222 | 0.34324 | 0.53532 | 0.54764
0.33219 | 0.34323 | 0.5353 | 0.54762
0.33218 | 0.34321 | 0.53527 | 0.54757
0.33217 | 0.3432 | 0.53525 | 0.54755
0.33215 | 0.34319 | 0.5352 | 0.54752
0.33214 | 0.34317 | 0.53517 | 0.5475
0.33213 | 0.34316 | 0.53515 | 0.54747
0.33211 | 0.34315 | 0.53512 | 0.54744
0.3321 | 0.34314 | 0.53508 | 0.54742
0.33209 | 0.34313 | 0.53506 | 0.54738
0.33207 | 0.34312 | 0.53502 | 0.54734
0.33206 | 0.3431 | 0.53499 | 0.54731
0.33205 | 0.34308 | 0.53496 | 0.54729
0.33203 | 0.34306 | 0.53492 | 0.54727
0.33201 | 0.34305 | 0.5349 | 0.54724
0.332 | 0.34304 | 0.53486 | 0.54722
0.33199 | 0.34302 | 0.53484 | 0.54719
0.33198 | 0.34301 | 0.5348 | 0.54716
0.33197 | 0.343 | 0.53478 | 0.54712
0.33195 | 0.34299 | 0.53474 | 0.54711
0.33193 | 0.34297 | 0.53472 | 0.54708
0.33192 | 0.34295 | 0.53469 | 0.54706
0.33191 | 0.34294 | 0.53467 | 0.54702
0.33188 | 0.34293 | 0.53464 | 0.547
0.33187 | 0.34291 | 0.53461 | 0.54697
0.33186 | 0.3429 | 0.53459 | 0.54694
0.33184 | 0.34287 | 0.53457 | 0.54691
0.33183 | 0.34286 | 0.53454 | 0.54687
0.33182 | 0.34285 | 0.53451 | 0.54683
0.3318 | 0.34284 | 0.53447 | 0.5468
0.33179 | 0.34282 | 0.53443 | 0.54677
0.33177 | 0.34281 | 0.53439 | 0.54674
0.33176 | 0.34279 | 0.53437 | 0.54672
0.33175 | 0.34278 | 0.53433 | 0.54668
0.33173 | 0.34276 | 0.53431 | 0.54665
0.33172 | 0.34274 | 0.53429 | 0.54663
0.33171 | 0.34273 | 0.53426 | 0.5466
0.33169 | 0.34272 | 0.53424 | 0.54658
0.33168 | 0.3427 | 0.53421 | 0.54655
0.33166 | 0.34269 | 0.53418 | 0.54653
0.33165 | 0.34267 | 0.53416 | 0.54652
0.33164 | 0.34266 | 0.53413 | 0.54649
0.33163 | 0.34264 | 0.5341 | 0.54646
0.33161 | 0.34264 | 0.53407 | 0.54643
0.3316 | 0.34262 | 0.53403 | 0.5464
0.33159 | 0.34261 | 0.534 | 0.54638
0.33158 | 0.34259 | 0.53395 | 0.54635
0.33156 | 0.34258 | 0.53392 | 0.5463
0.33155 | 0.34257 | 0.53389 | 0.54629
0.33154 | 0.34256 | 0.53386 | 0.54627
0.33152 | 0.34255 | 0.53382 | 0.54622
0.33151 | 0.34252 | 0.53379 | 0.54619
0.33149 | 0.34251 | 0.53376 | 0.54614
0.33148 | 0.3425 | 0.53374 | 0.54611
0.33146 | 0.34248 | 0.53371 | 0.54608
0.33145 | 0.34247 | 0.53368 | 0.54606
0.33144 | 0.34245 | 0.53364 | 0.54604
0.33143 | 0.34242 | 0.53361 | 0.54601
0.33141 | 0.34241 | 0.53359 | 0.546
0.3314 | 0.3424 | 0.53356 | 0.54595
0.33139 | 0.34239 | 0.53355 | 0.54593
0.33137 | 0.34238 | 0.53353 | 0.54589
0.33136 | 0.34237 | 0.5335 | 0.54586
0.33135 | 0.34236 | 0.53348 | 0.54583
0.33134 | 0.34233 | 0.53346 | 0.5458
0.33132 | 0.34232 | 0.53343 | 0.54578
0.33131 | 0.34231 | 0.5334 | 0.54576
0.3313 | 0.34229 | 0.53337 | 0.54573
0.33128 | 0.34228 | 0.53334 | 0.54571
0.33127 | 0.34226 | 0.53331 | 0.54568
0.33125 | 0.34225 | 0.53327 | 0.54566
0.33124 | 0.34224 | 0.53325 | 0.54563
0.33122 | 0.34224 | 0.53322 | 0.54561
0.3312 | 0.34222 | 0.53319 | 0.54558
0.33119 | 0.34222 | 0.53317 | 0.54557
0.33118 | 0.34221 | 0.53315 | 0.54554
0.33117 | 0.34219 | 0.53311 | 0.54551
0.33116 | 0.34218 | 0.53309 | 0.54547
0.33114 | 0.34216 | 0.53306 | 0.54545
0.33113 | 0.34215 | 0.53303 | 0.54543
0.33112 | 0.34214 | 0.53299 | 0.5454
0.33111 | 0.34213 | 0.53295 | 0.54538
0.3311 | 0.34212 | 0.53292 | 0.54536
0.33108 | 0.34211 | 0.5329 | 0.54533
0.33106 | 0.34209 | 0.53285 | 0.54531
0.33105 | 0.34208 | 0.53282 | 0.54529
0.33104 | 0.34206 | 0.53281 | 0.54524
0.33102 | 0.34204 | 0.53277 | 0.54521
0.331 | 0.34202 | 0.53275 | 0.54518
0.331 | 0.34201 | 0.53272 | 0.54516
0.33099 | 0.34199 | 0.53269 | 0.54513
0.33098 | 0.34198 | 0.53267 | 0.5451
0.33097 | 0.34197 | 0.53265 | 0.54508
0.33095 | 0.34196 | 0.53262 | 0.54505
0.33094 | 0.34194 | 0.53259 | 0.54501
0.33092 | 0.34193 | 0.53256 | 0.54499
0.3309 | 0.34192 | 0.53253 | 0.54495
0.33089 | 0.3419 | 0.5325 | 0.54493
0.33087 | 0.34189 | 0.53247 | 0.54489
0.33086 | 0.34188 | 0.53243 | 0.54487
0.33085 | 0.34187 | 0.5324 | 0.54483
0.33084 | 0.34184 | 0.53237 | 0.54481
0.33083 | 0.34183 | 0.53234 | 0.54478
0.33082 | 0.34181 | 0.53231 | 0.54475
0.3308 | 0.3418 | 0.53228 | 0.54473
0.33079 | 0.34179 | 0.53223 | 0.54469
0.33078 | 0.34176 | 0.53221 | 0.54467
0.33076 | 0.34174 | 0.53217 | 0.54464
0.33076 | 0.34173 | 0.53213 | 0.5446
0.33075 | 0.34172 | 0.5321 | 0.54459
0.33073 | 0.3417 | 0.53206 | 0.54456
0.33071 | 0.34169 | 0.53202 | 0.54453
0.3307 | 0.34168 | 0.532 | 0.5445
0.33069 | 0.34167 | 0.53197 | 0.54446
0.33068 | 0.34165 | 0.53193 | 0.54444
0.33066 | 0.34164 | 0.53191 | 0.54442
0.33064 | 0.34163 | 0.53188 | 0.54441
0.33063 | 0.34162 | 0.53185 | 0.54439
0.33061 | 0.34161 | 0.53181 | 0.54436
0.3306 | 0.3416 | 0.53178 | 0.54435
0.33058 | 0.34159 | 0.53176 | 0.54431
0.33057 | 0.34158 | 0.53173 | 0.54429
0.33056 | 0.34157 | 0.5317 | 0.54425
0.33055 | 0.34155 | 0.53167 | 0.54422
0.33054 | 0.34154 | 0.53164 | 0.5442
0.33053 | 0.34152 | 0.53161 | 0.54418
0.33052 | 0.3415 | 0.53157 | 0.54415
0.33051 | 0.3415 | 0.53156 | 0.54411
0.33049 | 0.34149 | 0.53153 | 0.54408
0.33047 | 0.34146 | 0.5315 | 0.54405
0.33046 | 0.34145 | 0.53148 | 0.54401
0.33044 | 0.34143 | 0.53144 | 0.54398
0.33043 | 0.34142 | 0.5314 | 0.54395
0.33042 | 0.34141 | 0.53138 | 0.54393
0.33041 | 0.3414 | 0.53134 | 0.54391
0.3304 | 0.34138 | 0.53133 | 0.54389
0.33038 | 0.34136 | 0.53131 | 0.54385
0.33036 | 0.34135 | 0.53126 | 0.54384
0.33035 | 0.34134 | 0.53124 | 0.54381
0.33033 | 0.34132 | 0.53121 | 0.54378
0.33032 | 0.3413 | 0.53119 | 0.54376
0.33031 | 0.34129 | 0.53116 | 0.54373
0.33029 | 0.34127 | 0.53112 | 0.5437
0.33027 | 0.34125 | 0.53107 | 0.54366
0.33025 | 0.34123 | 0.53104 | 0.54362
0.33024 | 0.34122 | 0.53102 | 0.5436
0.33022 | 0.34121 | 0.53098 | 0.54357
0.33021 | 0.34119 | 0.53094 | 0.54356
0.33019 | 0.34118 | 0.53091 | 0.54352
0.33017 | 0.34117 | 0.53088 | 0.54349
0.33015 | 0.34115 | 0.53084 | 0.54346
0.33014 | 0.34114 | 0.53081 | 0.54342
0.33014 | 0.34114 | 0.53077 | 0.54339
0.33012 | 0.34112 | 0.53074 | 0.54336
0.33011 | 0.3411 | 0.53071 | 0.54334
0.3301 | 0.34109 | 0.53068 | 0.54332
0.33009 | 0.34108 | 0.53064 | 0.54329
0.33007 | 0.34106 | 0.53061 | 0.54328
0.33006 | 0.34105 | 0.53059 | 0.54323
0.33005 | 0.34104 | 0.53056 | 0.54319
0.33003 | 0.34103 | 0.53054 | 0.54317
0.33002 | 0.34102 | 0.53052 | 0.54314
0.33001 | 0.341 | 0.53049 | 0.54312
0.32999 | 0.34098 | 0.53046 | 0.54309
0.32998 | 0.34097 | 0.53043 | 0.54307
0.32997 | 0.34096 | 0.5304 | 0.54304
0.32996 | 0.34096 | 0.53038 | 0.54302
0.32994 | 0.34094 | 0.53036 | 0.54298
0.32993 | 0.34093 | 0.53032 | 0.54297
0.32992 | 0.34091 | 0.53028 | 0.54293
0.3299 | 0.3409 | 0.53024 | 0.5429
0.32989 | 0.34089 | 0.53022 | 0.54288
0.32988 | 0.34087 | 0.53019 | 0.54286
0.32986 | 0.34086 | 0.53017 | 0.54283
0.32985 | 0.34085 | 0.53014 | 0.54278
0.32984 | 0.34084 | 0.53011 | 0.54274
0.32983 | 0.34082 | 0.53007 | 0.54268
0.32982 | 0.34081 | 0.53002 | 0.54266
0.32979 | 0.34081 | 0.52997 | 0.54264
0.32978 | 0.34079 | 0.52993 | 0.5426
0.32977 | 0.34078 | 0.52991 | 0.54258
0.32976 | 0.34077 | 0.52988 | 0.54256
0.32975 | 0.34076 | 0.52983 | 0.54254
0.32973 | 0.34075 | 0.52978 | 0.54251
0.32972 | 0.34074 | 0.52977 | 0.54247
0.3297 | 0.34072 | 0.52973 | 0.54244
0.32968 | 0.34071 | 0.52971 | 0.54242
0.32967 | 0.3407 | 0.52969 | 0.5424
0.32965 | 0.34068 | 0.52965 | 0.54235
0.32963 | 0.34067 | 0.52962 | 0.54232
0.32961 | 0.34067 | 0.52959 | 0.54229
0.3296 | 0.34065 | 0.52954 | 0.54225
0.32959 | 0.34063 | 0.5295 | 0.54222
0.32958 | 0.34062 | 0.52947 | 0.5422
0.32956 | 0.3406 | 0.52943 | 0.54215
0.32955 | 0.34059 | 0.52941 | 0.54213
0.32953 | 0.34057 | 0.52938 | 0.5421
0.32951 | 0.34055 | 0.52936 | 0.54207
0.32949 | 0.34054 | 0.52933 | 0.54203
0.32948 | 0.34052 | 0.52931 | 0.54202
0.32946 | 0.34051 | 0.52929 | 0.54199
0.32945 | 0.3405 | 0.52927 | 0.54197
0.32943 | 0.34049 | 0.52925 | 0.54195
0.32941 | 0.34048 | 0.5292 | 0.54192
0.3294 | 0.34046 | 0.52918 | 0.5419
0.32939 | 0.34045 | 0.52915 | 0.54187
0.32938 | 0.34044 | 0.52912 | 0.54184
0.32937 | 0.34042 | 0.52908 | 0.54179
0.32936 | 0.34041 | 0.52905 | 0.54176
0.32935 | 0.3404 | 0.52902 | 0.54172
0.32934 | 0.34039 | 0.52899 | 0.5417
0.32933 | 0.34037 | 0.52896 | 0.54167
0.32931 | 0.34036 | 0.52893 | 0.54164
0.32929 | 0.34035 | 0.5289 | 0.54162
0.32928 | 0.34033 | 0.52887 | 0.54158
0.32926 | 0.34031 | 0.52882 | 0.54157
0.32925 | 0.3403 | 0.52879 | 0.54154
0.32923 | 0.34028 | 0.52875 | 0.5415
0.32922 | 0.34027 | 0.52874 | 0.54147
0.32921 | 0.34025 | 0.52871 | 0.54143
0.32919 | 0.34024 | 0.52869 | 0.5414
0.32919 | 0.34023 | 0.52867 | 0.54138
0.32916 | 0.34022 | 0.52863 | 0.54134
0.32915 | 0.3402 | 0.5286 | 0.54132
0.32914 | 0.34019 | 0.52858 | 0.54129
0.32913 | 0.34017 | 0.52855 | 0.54124
0.32912 | 0.34016 | 0.52853 | 0.54122
0.3291 | 0.34014 | 0.5285 | 0.54119
0.32908 | 0.34013 | 0.52847 | 0.54116
0.32907 | 0.34011 | 0.52844 | 0.54113
0.32905 | 0.34009 | 0.52839 | 0.5411
0.32903 | 0.34008 | 0.52836 | 0.54106
0.32902 | 0.34007 | 0.52834 | 0.54104
0.32901 | 0.34005 | 0.52831 | 0.54102
0.32899 | 0.34004 | 0.52829 | 0.54098
0.32898 | 0.34003 | 0.52824 | 0.54094
0.32896 | 0.34001 | 0.52822 | 0.54091
0.32894 | 0.33999 | 0.5282 | 0.54087
0.32893 | 0.33999 | 0.52817 | 0.54084
0.32891 | 0.33997 | 0.52814 | 0.54081
0.32889 | 0.33995 | 0.5281 | 0.54078
0.32888 | 0.33993 | 0.52807 | 0.54077
0.32887 | 0.33992 | 0.52805 | 0.54073
0.32886 | 0.33991 | 0.52803 | 0.54071
0.32884 | 0.33989 | 0.52801 | 0.54067
0.32882 | 0.33988 | 0.52797 | 0.54066
0.3288 | 0.33987 | 0.52792 | 0.54063
0.32878 | 0.33985 | 0.52789 | 0.54061
0.32877 | 0.33984 | 0.52786 | 0.54058
0.32876 | 0.33983 | 0.52784 | 0.54055
0.32875 | 0.33981 | 0.52782 | 0.54051
0.32874 | 0.3398 | 0.52779 | 0.54046
0.32872 | 0.33978 | 0.52776 | 0.54042
0.32871 | 0.33977 | 0.52773 | 0.5404
0.3287 | 0.33976 | 0.52771 | 0.54035
0.3287 | 0.33975 | 0.52769 | 0.54032
0.32869 | 0.33973 | 0.52765 | 0.54029
0.32868 | 0.33971 | 0.52762 | 0.54028
0.32867 | 0.3397 | 0.52761 | 0.54025
0.32866 | 0.33969 | 0.52757 | 0.54022
0.32865 | 0.33968 | 0.52753 | 0.5402
0.32864 | 0.33966 | 0.5275 | 0.54017
0.32862 | 0.33964 | 0.52746 | 0.54013
0.32861 | 0.33964 | 0.52743 | 0.54009
0.3286 | 0.33963 | 0.52741 | 0.54008
0.32858 | 0.33962 | 0.52738 | 0.54005
0.32857 | 0.33961 | 0.52731 | 0.54002
0.32856 | 0.33959 | 0.52729 | 0.54
0.32855 | 0.33958 | 0.52726 | 0.53995
0.32854 | 0.33956 | 0.52722 | 0.53991
0.32853 | 0.33955 | 0.52719 | 0.53988
0.32851 | 0.33954 | 0.52716 | 0.53986
0.3285 | 0.33952 | 0.52714 | 0.53982
0.32849 | 0.33951 | 0.52711 | 0.53979
0.32847 | 0.33949 | 0.52709 | 0.53976
0.32847 | 0.33947 | 0.52705 | 0.53972
0.32845 | 0.33946 | 0.52703 | 0.53969
0.32844 | 0.33946 | 0.52701 | 0.53966
0.32843 | 0.33944 | 0.52698 | 0.53963
0.32842 | 0.33943 | 0.52695 | 0.53961
0.32839 | 0.33941 | 0.52689 | 0.53959
0.32838 | 0.33941 | 0.52686 | 0.53954
0.32837 | 0.3394 | 0.52681 | 0.53952
0.32835 | 0.33939 | 0.52679 | 0.53949
0.32835 | 0.33938 | 0.52675 | 0.53946
0.32834 | 0.33936 | 0.52671 | 0.53943
0.32832 | 0.33934 | 0.52669 | 0.5394
0.3283 | 0.33934 | 0.52667 | 0.53937
0.32829 | 0.33932 | 0.52664 | 0.53935
0.32828 | 0.33931 | 0.52661 | 0.53933
0.32827 | 0.33929 | 0.52658 | 0.5393
0.32825 | 0.33928 | 0.52656 | 0.53927
0.32824 | 0.33927 | 0.52652 | 0.53924
0.32823 | 0.33925 | 0.52649 | 0.53922
0.32822 | 0.33923 | 0.52646 | 0.5392
0.32821 | 0.33922 | 0.52643 | 0.53917
0.3282 | 0.33922 | 0.52639 | 0.53914
0.32818 | 0.3392 | 0.52636 | 0.5391
0.32817 | 0.33919 | 0.52632 | 0.53908
0.32815 | 0.33917 | 0.52629 | 0.53904
0.32814 | 0.33916 | 0.52627 | 0.53901
0.32813 | 0.33914 | 0.52625 | 0.53899
0.32812 | 0.33914 | 0.52621 | 0.53896
0.3281 | 0.33912 | 0.52619 | 0.53893
0.32809 | 0.33911 | 0.52617 | 0.53889
0.32807 | 0.33909 | 0.52613 | 0.53887
0.32806 | 0.33907 | 0.52611 | 0.53885
0.32805 | 0.33906 | 0.52609 | 0.53883
0.32803 | 0.33905 | 0.52605 | 0.53882
0.32801 | 0.33904 | 0.52603 | 0.53879
0.328 | 0.33902 | 0.526 | 0.53877
0.32798 | 0.339 | 0.52597 | 0.53874
0.32797 | 0.33899 | 0.52594 | 0.53872
0.32796 | 0.33898 | 0.52591 | 0.53869
0.32794 | 0.33897 | 0.52587 | 0.53865
0.32793 | 0.33896 | 0.52584 | 0.53863
0.32792 | 0.33894 | 0.52581 | 0.53861
0.32791 | 0.33893 | 0.52577 | 0.53857
0.32789 | 0.33892 | 0.52574 | 0.53855
0.32789 | 0.3389 | 0.52573 | 0.5385
0.32787 | 0.3389 | 0.5257 | 0.53846
0.32785 | 0.33888 | 0.52568 | 0.53842
0.32784 | 0.33886 | 0.52563 | 0.53838
0.32783 | 0.33884 | 0.52559 | 0.53837
0.32781 | 0.33883 | 0.52556 | 0.53835
0.32781 | 0.3388 | 0.52552 | 0.53831
0.32779 | 0.33879 | 0.5255 | 0.53828
0.32778 | 0.33878 | 0.52547 | 0.53824
0.32777 | 0.33877 | 0.52545 | 0.53821
0.32776 | 0.33875 | 0.52541 | 0.53818
0.32775 | 0.33874 | 0.52539 | 0.53817
0.32773 | 0.33872 | 0.52535 | 0.53815
0.32772 | 0.33871 | 0.52531 | 0.53812
0.32771 | 0.3387 | 0.52528 | 0.53807
0.32769 | 0.3387 | 0.52524 | 0.53804
0.32768 | 0.33869 | 0.52522 | 0.538
0.32766 | 0.33867 | 0.52517 | 0.53797
0.32765 | 0.33866 | 0.52515 | 0.53794
0.32764 | 0.33865 | 0.52512 | 0.53792
0.32762 | 0.33864 | 0.52507 | 0.53789
0.32761 | 0.33862 | 0.52503 | 0.53786
0.32759 | 0.33861 | 0.52499 | 0.53783
0.32758 | 0.3386 | 0.52497 | 0.5378
0.32757 | 0.33858 | 0.52494 | 0.53779
0.32755 | 0.33857 | 0.52492 | 0.53775
0.32754 | 0.33856 | 0.52488 | 0.53773
0.32753 | 0.33854 | 0.52484 | 0.5377
0.32751 | 0.33853 | 0.52482 | 0.53765
0.3275 | 0.33852 | 0.5248 | 0.53762
0.32749 | 0.3385 | 0.52477 | 0.53758
0.32747 | 0.33849 | 0.52474 | 0.53755
0.32745 | 0.33847 | 0.5247 | 0.53752
0.32743 | 0.33846 | 0.52467 | 0.5375
0.32741 | 0.33845 | 0.52463 | 0.53749
0.32739 | 0.33843 | 0.5246 | 0.53745
0.32737 | 0.33842 | 0.52457 | 0.53741
0.32736 | 0.3384 | 0.52452 | 0.53739
0.32734 | 0.33839 | 0.52451 | 0.53736
0.32734 | 0.33838 | 0.52448 | 0.53733
0.32732 | 0.33837 | 0.52445 | 0.53729
0.32731 | 0.33836 | 0.52441 | 0.53727
0.32729 | 0.33835 | 0.5244 | 0.53723
0.32728 | 0.33833 | 0.52437 | 0.5372
0.32727 | 0.33832 | 0.52434 | 0.53718
0.32726 | 0.33831 | 0.52432 | 0.53715
0.32725 | 0.33829 | 0.52428 | 0.53713
0.32724 | 0.33826 | 0.52425 | 0.5371
0.32723 | 0.33825 | 0.52423 | 0.53707
0.32721 | 0.33823 | 0.52421 | 0.53704
0.3272 | 0.33822 | 0.52419 | 0.53701
0.32718 | 0.33821 | 0.52415 | 0.537
0.32717 | 0.33819 | 0.5241 | 0.53697
0.32714 | 0.33819 | 0.52408 | 0.53695
0.32713 | 0.33816 | 0.52406 | 0.53692
0.32711 | 0.33815 | 0.52403 | 0.53689
0.32709 | 0.33814 | 0.524 | 0.53687
0.32709 | 0.33812 | 0.52398 | 0.53684
0.32707 | 0.3381 | 0.52395 | 0.53681
0.32705 | 0.33809 | 0.52392 | 0.53678
0.32704 | 0.33808 | 0.52389 | 0.53675
0.32702 | 0.33807 | 0.52384 | 0.53672
0.32701 | 0.33805 | 0.52383 | 0.5367
0.327 | 0.33803 | 0.5238 | 0.53667
0.32699 | 0.33802 | 0.52376 | 0.53664
0.32698 | 0.33801 | 0.52374 | 0.53662
0.32697 | 0.33799 | 0.52373 | 0.53659
0.32696 | 0.33798 | 0.5237 | 0.53656
0.32694 | 0.33797 | 0.52368 | 0.53654
0.32693 | 0.33795 | 0.52365 | 0.53652
0.32692 | 0.33794 | 0.52362 | 0.53648
0.32691 | 0.33793 | 0.52359 | 0.53646
0.32689 | 0.33791 | 0.52356 | 0.53644
0.32689 | 0.3379 | 0.52354 | 0.53641
0.32687 | 0.33788 | 0.52352 | 0.53638
0.32685 | 0.33787 | 0.52349 | 0.53634
0.32684 | 0.33786 | 0.52345 | 0.53631
0.32683 | 0.33785 | 0.52342 | 0.53629
0.32681 | 0.33783 | 0.52339 | 0.53626
0.3268 | 0.33782 | 0.52336 | 0.53625
0.32679 | 0.33781 | 0.52333 | 0.53621
0.32679 | 0.3378 | 0.52331 | 0.53618
0.32677 | 0.33779 | 0.52329 | 0.53616
0.32676 | 0.33778 | 0.52327 | 0.53613
0.32675 | 0.33777 | 0.52324 | 0.53611
0.32674 | 0.33776 | 0.52323 | 0.5361
0.32672 | 0.33774 | 0.52319 | 0.53607
0.32671 | 0.33773 | 0.52316 | 0.53605
0.3267 | 0.33771 | 0.52312 | 0.53602
0.32669 | 0.3377 | 0.52308 | 0.53599
0.32668 | 0.33768 | 0.52304 | 0.53596
0.32666 | 0.33766 | 0.52299 | 0.53594
0.32665 | 0.33765 | 0.52296 | 0.53591
0.32664 | 0.33763 | 0.52292 | 0.5359
0.32662 | 0.33762 | 0.52287 | 0.53586
0.3266 | 0.3376 | 0.52283 | 0.53584
0.32658 | 0.3376 | 0.52281 | 0.5358
0.32658 | 0.33758 | 0.52279 | 0.53578
0.32656 | 0.33756 | 0.52272 | 0.53576
0.32655 | 0.33754 | 0.52268 | 0.53573
0.32653 | 0.33753 | 0.52265 | 0.5357
0.32653 | 0.33751 | 0.52263 | 0.53568
0.32652 | 0.3375 | 0.5226 | 0.53566
0.3265 | 0.33748 | 0.52255 | 0.53563
0.32649 | 0.33747 | 0.52252 | 0.53561
0.32647 | 0.33746 | 0.5225 | 0.53557
0.32646 | 0.33745 | 0.52246 | 0.53555
0.32645 | 0.33743 | 0.52242 | 0.5355
0.32644 | 0.33741 | 0.52241 | 0.53546
0.32642 | 0.3374 | 0.52238 | 0.53542
0.3264 | 0.33738 | 0.52234 | 0.5354
0.32639 | 0.33738 | 0.52232 | 0.53539
0.32637 | 0.33736 | 0.52229 | 0.53534
0.32636 | 0.33733 | 0.52226 | 0.5353
0.32635 | 0.33732 | 0.52223 | 0.53528
0.32634 | 0.33731 | 0.52221 | 0.53527
0.32632 | 0.3373 | 0.52218 | 0.53523
0.32631 | 0.33729 | 0.52215 | 0.53521
0.3263 | 0.33727 | 0.5221 | 0.53519
0.32628 | 0.33726 | 0.52207 | 0.53516
0.32626 | 0.33724 | 0.52206 | 0.53512
0.32625 | 0.33723 | 0.52204 | 0.53508
0.32623 | 0.3372 | 0.52201 | 0.53506
0.32622 | 0.33719 | 0.52197 | 0.53505
0.32621 | 0.33717 | 0.52193 | 0.53503
0.32619 | 0.33716 | 0.5219 | 0.535
0.32619 | 0.33714 | 0.52188 | 0.53495
0.32617 | 0.33712 | 0.52185 | 0.53491
0.32614 | 0.33711 | 0.52181 | 0.53489
0.32613 | 0.3371 | 0.52179 | 0.53486
0.32611 | 0.33707 | 0.52176 | 0.53484
0.3261 | 0.33707 | 0.52173 | 0.53482
0.32609 | 0.33705 | 0.52171 | 0.53478
0.32608 | 0.33704 | 0.52168 | 0.53476
0.32606 | 0.33703 | 0.52164 | 0.53472
0.32605 | 0.33702 | 0.52161 | 0.5347
0.32603 | 0.33701 | 0.52159 | 0.53467
0.32602 | 0.337 | 0.52156 | 0.53465
0.32601 | 0.33699 | 0.52153 | 0.53463
0.32599 | 0.33697 | 0.52151 | 0.5346
0.32598 | 0.33696 | 0.52147 | 0.53457
0.32596 | 0.33695 | 0.52145 | 0.53455
0.32594 | 0.33694 | 0.52143 | 0.53452
0.32593 | 0.33692 | 0.52138 | 0.53448
0.32592 | 0.33691 | 0.52135 | 0.53444
0.32591 | 0.33688 | 0.52132 | 0.53441
0.3259 | 0.33687 | 0.52129 | 0.53437
0.32588 | 0.33686 | 0.52127 | 0.53436
0.32587 | 0.33685 | 0.52124 | 0.53434
0.32585 | 0.33684 | 0.52122 | 0.53432
0.32583 | 0.33683 | 0.5212 | 0.53428
0.32582 | 0.33682 | 0.52118 | 0.53425
0.32581 | 0.33681 | 0.52115 | 0.53422
0.32579 | 0.33679 | 0.52111 | 0.53418
0.32578 | 0.33678 | 0.52108 | 0.53417
0.32577 | 0.33677 | 0.52103 | 0.53415
0.32574 | 0.33675 | 0.521 | 0.53411
0.32573 | 0.33674 | 0.52097 | 0.53409
0.32572 | 0.33673 | 0.52094 | 0.53407
0.32571 | 0.33671 | 0.52091 | 0.53404
0.3257 | 0.33669 | 0.52088 | 0.53402
0.32568 | 0.33668 | 0.52086 | 0.53399
0.32566 | 0.33667 | 0.52083 | 0.53396
0.32565 | 0.33666 | 0.52081 | 0.53392
0.32563 | 0.33665 | 0.52076 | 0.53388
0.32562 | 0.33664 | 0.52074 | 0.53386
0.32561 | 0.33662 | 0.52071 | 0.53382
0.3256 | 0.33661 | 0.52066 | 0.53381
0.32558 | 0.33659 | 0.52064 | 0.53379
0.32557 | 0.33658 | 0.52061 | 0.53377
0.32556 | 0.33657 | 0.52057 | 0.53374
0.32554 | 0.33655 | 0.52054 | 0.53372
0.32553 | 0.33655 | 0.52051 | 0.53368
0.32552 | 0.33653 | 0.52048 | 0.53364
0.32552 | 0.33652 | 0.52045 | 0.5336
0.32549 | 0.33651 | 0.5204 | 0.53357
0.32548 | 0.3365 | 0.52036 | 0.53355
0.32547 | 0.33649 | 0.52033 | 0.53352
0.32545 | 0.33647 | 0.5203 | 0.53349
0.32544 | 0.33645 | 0.52029 | 0.53347
0.32543 | 0.33643 | 0.52026 | 0.53343
0.32542 | 0.33642 | 0.52022 | 0.53339
0.32541 | 0.33641 | 0.52021 | 0.53337
0.32539 | 0.3364 | 0.52018 | 0.53335
0.32538 | 0.33638 | 0.52015 | 0.5333
0.32537 | 0.33637 | 0.52011 | 0.53327
0.32536 | 0.33636 | 0.5201 | 0.53325
0.32535 | 0.33635 | 0.52007 | 0.53322
0.32533 | 0.33634 | 0.52004 | 0.53317
0.32532 | 0.33633 | 0.52 | 0.53315
0.32532 | 0.33632 | 0.51997 | 0.53312
0.3253 | 0.33631 | 0.51994 | 0.5331
0.32529 | 0.33629 | 0.51992 | 0.53308
0.32527 | 0.33629 | 0.51988 | 0.53305
0.32526 | 0.33627 | 0.51983 | 0.53302
0.32526 | 0.33626 | 0.51982 | 0.53299
0.32524 | 0.33625 | 0.5198 | 0.53297
0.32523 | 0.33624 | 0.51977 | 0.53294
0.32522 | 0.33622 | 0.51975 | 0.53292
0.3252 | 0.33621 | 0.51971 | 0.53288
0.32519 | 0.3362 | 0.51968 | 0.53286
0.32518 | 0.33619 | 0.51967 | 0.53283
0.32516 | 0.33617 | 0.51964 | 0.53279
0.32515 | 0.33616 | 0.51962 | 0.53278
0.32513 | 0.33614 | 0.51958 | 0.53276
0.32512 | 0.33612 | 0.51953 | 0.53273
0.32511 | 0.33611 | 0.51949 | 0.53271
0.3251 | 0.33609 | 0.51944 | 0.5327
0.32509 | 0.33608 | 0.5194 | 0.53267
0.32508 | 0.33608 | 0.51937 | 0.53264
0.32507 | 0.33606 | 0.51935 | 0.5326
0.32506 | 0.33604 | 0.51932 | 0.53257
0.32505 | 0.33603 | 0.51928 | 0.53253
0.32504 | 0.33602 | 0.51924 | 0.53251
0.32502 | 0.33601 | 0.51921 | 0.53249
0.32501 | 0.336 | 0.51918 | 0.53245
0.325 | 0.33599 | 0.51916 | 0.53244
0.32499 | 0.33598 | 0.51913 | 0.53241
0.32498 | 0.33597 | 0.5191 | 0.53239
0.32496 | 0.33596 | 0.51906 | 0.53236
0.32495 | 0.33595 | 0.51905 | 0.53232
0.32494 | 0.33594 | 0.51903 | 0.5323
0.32493 | 0.33593 | 0.51901 | 0.53228
0.32492 | 0.33591 | 0.51898 | 0.53226
0.3249 | 0.3359 | 0.51895 | 0.53224
0.32489 | 0.33589 | 0.51892 | 0.5322
0.32487 | 0.33587 | 0.51889 | 0.53218
0.32487 | 0.33585 | 0.51886 | 0.53215
0.32485 | 0.33584 | 0.51883 | 0.53211
0.32483 | 0.33583 | 0.5188 | 0.53209
0.32483 | 0.33581 | 0.51878 | 0.53206
0.32481 | 0.33579 | 0.51874 | 0.53203
0.32479 | 0.33578 | 0.51871 | 0.53201
0.32477 | 0.33578 | 0.51869 | 0.53197
0.32476 | 0.33576 | 0.51867 | 0.53195
0.32475 | 0.33576 | 0.51864 | 0.53192
0.32473 | 0.33575 | 0.51862 | 0.5319
0.32471 | 0.33574 | 0.5186 | 0.53188
0.3247 | 0.33572 | 0.51856 | 0.53185
0.32469 | 0.33571 | 0.51853 | 0.53184
0.32469 | 0.33569 | 0.5185 | 0.53181
0.32468 | 0.33569 | 0.51847 | 0.53178
0.32467 | 0.33567 | 0.51844 | 0.53175
0.32466 | 0.33566 | 0.5184 | 0.53173
0.32465 | 0.33565 | 0.51837 | 0.5317
0.32464 | 0.33564 | 0.51834 | 0.53166
0.32463 | 0.33562 | 0.51831 | 0.53163
0.32462 | 0.33561 | 0.51828 | 0.53162
0.32461 | 0.3356 | 0.51825 | 0.53159
0.3246 | 0.33559 | 0.51822 | 0.53157
0.32458 | 0.33558 | 0.51819 | 0.53156
0.32457 | 0.33557 | 0.51816 | 0.53153
0.32456 | 0.33556 | 0.51814 | 0.5315
0.32454 | 0.33555 | 0.51811 | 0.53146
0.32452 | 0.33552 | 0.51809 | 0.53143
0.32451 | 0.3355 | 0.51805 | 0.53139
0.3245 | 0.33548 | 0.51803 | 0.53135
0.32449 | 0.33547 | 0.518 | 0.53132
0.32448 | 0.33546 | 0.51799 | 0.53129
0.32446 | 0.33544 | 0.51795 | 0.53127
0.32445 | 0.33543 | 0.51794 | 0.53123
0.32444 | 0.33541 | 0.5179 | 0.5312
0.32442 | 0.3354 | 0.51789 | 0.53118
0.32441 | 0.33539 | 0.51785 | 0.53116
0.3244 | 0.33538 | 0.51783 | 0.53114
0.32439 | 0.33536 | 0.51781 | 0.53109
0.32438 | 0.33535 | 0.5178 | 0.53106
0.32437 | 0.33533 | 0.51777 | 0.53103
0.32436 | 0.33532 | 0.51774 | 0.53101
0.32435 | 0.33531 | 0.5177 | 0.53098
0.32434 | 0.3353 | 0.51764 | 0.53096
0.32432 | 0.33529 | 0.5176 | 0.53092
0.32431 | 0.33528 | 0.51758 | 0.53089
0.3243 | 0.33527 | 0.51754 | 0.53085
0.32429 | 0.33526 | 0.51751 | 0.53084
0.32428 | 0.33525 | 0.51748 | 0.53082
0.32427 | 0.33524 | 0.51743 | 0.5308
0.32426 | 0.33522 | 0.51741 | 0.53076
0.32425 | 0.33521 | 0.51739 | 0.53075
0.32423 | 0.3352 | 0.51737 | 0.53072
0.32421 | 0.33519 | 0.51734 | 0.5307
0.3242 | 0.33517 | 0.51731 | 0.53067
0.32419 | 0.33517 | 0.51726 | 0.53065
0.32417 | 0.33515 | 0.51724 | 0.5306
0.32416 | 0.33514 | 0.51722 | 0.53058
0.32414 | 0.33512 | 0.51719 | 0.53055
0.32412 | 0.33511 | 0.51716 | 0.5305
0.3241 | 0.3351 | 0.51713 | 0.53047
0.32409 | 0.33509 | 0.5171 | 0.53044
0.32407 | 0.33508 | 0.51707 | 0.5304
0.32406 | 0.33506 | 0.51704 | 0.53038
0.32404 | 0.33505 | 0.51701 | 0.53036
0.32402 | 0.33504 | 0.51698 | 0.53032
0.32401 | 0.33501 | 0.51696 | 0.5303
0.324 | 0.335 | 0.5169 | 0.53028
0.32398 | 0.33498 | 0.51687 | 0.53025
0.32398 | 0.33497 | 0.51685 | 0.53023
0.32396 | 0.33496 | 0.51682 | 0.53021
0.32394 | 0.33495 | 0.5168 | 0.53019
0.32393 | 0.33494 | 0.51677 | 0.53015
0.32391 | 0.33493 | 0.51674 | 0.53013
0.3239 | 0.33492 | 0.51671 | 0.53011
0.32389 | 0.33491 | 0.51668 | 0.53009
0.32387 | 0.33489 | 0.51665 | 0.53006
0.32386 | 0.33488 | 0.51663 | 0.53003
0.32385 | 0.33487 | 0.5166 | 0.52999
0.32384 | 0.33485 | 0.51656 | 0.52996
0.32382 | 0.33484 | 0.51653 | 0.52993
0.32381 | 0.33483 | 0.5165 | 0.5299
0.3238 | 0.33482 | 0.51646 | 0.52987
0.32379 | 0.3348 | 0.51643 | 0.52986
0.32377 | 0.33478 | 0.51641 | 0.52983
0.32376 | 0.33478 | 0.51638 | 0.52981
0.32375 | 0.33476 | 0.51636 | 0.52979
0.32375 | 0.33475 | 0.51633 | 0.52977
0.32373 | 0.33475 | 0.5163 | 0.52976
0.32371 | 0.33473 | 0.51628 | 0.52972
0.32369 | 0.33472 | 0.51626 | 0.52969
0.32367 | 0.33471 | 0.51623 | 0.52967
0.32366 | 0.33469 | 0.5162 | 0.52964
0.32363 | 0.33468 | 0.51617 | 0.52961
0.32363 | 0.33467 | 0.51614 | 0.52959
0.32361 | 0.33465 | 0.51611 | 0.52955
0.3236 | 0.33463 | 0.51608 | 0.52953
0.32359 | 0.33463 | 0.51605 | 0.52951
0.32358 | 0.33462 | 0.51603 | 0.52948
0.32356 | 0.3346 | 0.516 | 0.52944
0.32355 | 0.33459 | 0.51597 | 0.52942
0.32354 | 0.33458 | 0.51594 | 0.5294
0.32352 | 0.33457 | 0.51593 | 0.52936
0.32352 | 0.33455 | 0.51587 | 0.52934
0.32351 | 0.33454 | 0.51582 | 0.52931
0.32349 | 0.33453 | 0.51579 | 0.52926
0.32348 | 0.33451 | 0.51577 | 0.52924
0.32347 | 0.3345 | 0.51572 | 0.52919
0.32346 | 0.33448 | 0.51569 | 0.52917
0.32345 | 0.33447 | 0.51565 | 0.52913
0.32344 | 0.33446 | 0.51561 | 0.5291
0.32343 | 0.33445 | 0.51559 | 0.52906
0.32341 | 0.33443 | 0.51555 | 0.52903
0.3234 | 0.33442 | 0.51553 | 0.52901
0.32339 | 0.33441 | 0.51551 | 0.52899
0.32338 | 0.3344 | 0.51548 | 0.52896
0.32337 | 0.33439 | 0.51545 | 0.52893
0.32336 | 0.33438 | 0.51543 | 0.52889
0.32335 | 0.33437 | 0.51539 | 0.52888
0.32334 | 0.33435 | 0.51537 | 0.52886
0.32333 | 0.33435 | 0.51534 | 0.52883
0.32332 | 0.33433 | 0.51531 | 0.52879
0.3233 | 0.33432 | 0.51528 | 0.52875
0.3233 | 0.3343 | 0.51526 | 0.52871
0.32328 | 0.33429 | 0.51523 | 0.52868
0.32325 | 0.33428 | 0.51519 | 0.52865
0.32324 | 0.33427 | 0.51518 | 0.5286
0.32323 | 0.33426 | 0.51515 | 0.52857
0.32322 | 0.33424 | 0.51512 | 0.52855
0.32321 | 0.33423 | 0.5151 | 0.52853
0.3232 | 0.33422 | 0.51508 | 0.5285
0.32318 | 0.3342 | 0.51504 | 0.52847
0.32317 | 0.33419 | 0.51501 | 0.52845
0.32315 | 0.33417 | 0.51498 | 0.52841
0.32314 | 0.33415 | 0.51495 | 0.5284
0.32313 | 0.33415 | 0.51492 | 0.52838
0.32311 | 0.33414 | 0.5149 | 0.52834
0.3231 | 0.33412 | 0.51487 | 0.52831
0.3231 | 0.33411 | 0.51484 | 0.52829
0.32308 | 0.3341 | 0.51482 | 0.52827
0.32307 | 0.33408 | 0.5148 | 0.52825
0.32306 | 0.33407 | 0.51477 | 0.52822
0.32305 | 0.33406 | 0.51475 | 0.52818
0.32303 | 0.33405 | 0.51472 | 0.52815
0.32302 | 0.33403 | 0.51468 | 0.52811
0.323 | 0.33402 | 0.51465 | 0.52807
0.32299 | 0.33401 | 0.51462 | 0.52804
0.32297 | 0.334 | 0.51459 | 0.52802
0.32295 | 0.33399 | 0.51456 | 0.528
0.32294 | 0.33398 | 0.51452 | 0.52797
0.32293 | 0.33397 | 0.51448 | 0.52794
0.32292 | 0.33395 | 0.51447 | 0.5279
0.3229 | 0.33394 | 0.51444 | 0.52789
0.32289 | 0.33394 | 0.51441 | 0.52786
0.32288 | 0.33392 | 0.51438 | 0.52783
0.32287 | 0.33391 | 0.51437 | 0.5278
0.32286 | 0.3339 | 0.51431 | 0.52776
0.32285 | 0.33389 | 0.51428 | 0.52773
0.32284 | 0.33388 | 0.51426 | 0.5277
0.32283 | 0.33387 | 0.51422 | 0.52767
0.32282 | 0.33386 | 0.5142 | 0.52764
0.32281 | 0.33384 | 0.51417 | 0.52762
0.32279 | 0.33383 | 0.51415 | 0.52761
0.32278 | 0.33381 | 0.51413 | 0.52759
0.32277 | 0.3338 | 0.51409 | 0.52756
0.32275 | 0.33378 | 0.51407 | 0.52754
0.32273 | 0.33377 | 0.51405 | 0.52751
0.32272 | 0.33376 | 0.51402 | 0.52748
0.32271 | 0.33375 | 0.514 | 0.52745
0.3227 | 0.33374 | 0.51397 | 0.52742
0.32269 | 0.33372 | 0.51394 | 0.52739
0.32267 | 0.33371 | 0.51392 | 0.52738
0.32266 | 0.3337 | 0.5139 | 0.52735
0.32266 | 0.33369 | 0.51387 | 0.52733
0.32265 | 0.33367 | 0.51384 | 0.5273
0.32264 | 0.33366 | 0.51381 | 0.52727
0.32262 | 0.33364 | 0.51378 | 0.52724
0.32261 | 0.33363 | 0.51374 | 0.52721
0.3226 | 0.33363 | 0.51372 | 0.52717
0.32258 | 0.33361 | 0.51369 | 0.52715
0.32257 | 0.3336 | 0.51366 | 0.52713
0.32256 | 0.3336 | 0.51364 | 0.5271
0.32255 | 0.33359 | 0.51361 | 0.52708
0.32253 | 0.33358 | 0.51358 | 0.52705
0.32252 | 0.33357 | 0.51356 | 0.52703
0.32251 | 0.33356 | 0.51354 | 0.52699
0.3225 | 0.33355 | 0.51351 | 0.52698
0.32249 | 0.33354 | 0.51346 | 0.52694
0.32248 | 0.33352 | 0.5134 | 0.52692
0.32247 | 0.33351 | 0.51336 | 0.5269
0.32246 | 0.3335 | 0.51333 | 0.52685
0.32245 | 0.33349 | 0.51331 | 0.52683
0.32244 | 0.33348 | 0.51328 | 0.52681
0.32242 | 0.33346 | 0.51325 | 0.52679
0.3224 | 0.33345 | 0.51323 | 0.52674
0.32239 | 0.33343 | 0.51319 | 0.52672
0.32238 | 0.33342 | 0.51317 | 0.5267
0.32236 | 0.33341 | 0.51315 | 0.52667
0.32235 | 0.3334 | 0.51312 | 0.52664
0.32234 | 0.3334 | 0.51309 | 0.52662
0.32232 | 0.33338 | 0.51306 | 0.5266
0.32231 | 0.33337 | 0.51302 | 0.52657
0.3223 | 0.33336 | 0.51299 | 0.52655
0.32229 | 0.33334 | 0.51297 | 0.52651
0.32228 | 0.33333 | 0.51295 | 0.52648
0.32227 | 0.33332 | 0.51293 | 0.52644
0.32225 | 0.33331 | 0.51289 | 0.52643
0.32224 | 0.3333 | 0.51287 | 0.5264
0.32222 | 0.33329 | 0.51285 | 0.52638
0.32221 | 0.33328 | 0.51282 | 0.52635
0.3222 | 0.33328 | 0.5128 | 0.52633
0.32218 | 0.33327 | 0.51278 | 0.5263
0.32217 | 0.33325 | 0.51274 | 0.52627
0.32215 | 0.33324 | 0.5127 | 0.52625
0.32214 | 0.33322 | 0.51267 | 0.52624
0.32213 | 0.33322 | 0.51265 | 0.52621
0.32212 | 0.33321 | 0.51262 | 0.52618
0.32211 | 0.3332 | 0.51259 | 0.52614
0.3221 | 0.33318 | 0.51254 | 0.52611
0.32209 | 0.33317 | 0.51252 | 0.52609
0.32208 | 0.33316 | 0.51249 | 0.52605
0.32206 | 0.33315 | 0.51247 | 0.52602
0.32206 | 0.33313 | 0.51243 | 0.52601
0.32204 | 0.33312 | 0.5124 | 0.52598
0.32203 | 0.33311 | 0.51238 | 0.52594
0.32202 | 0.3331 | 0.51234 | 0.52592
0.32201 | 0.33309 | 0.51232 | 0.5259
0.322 | 0.33308 | 0.51228 | 0.52587
0.32199 | 0.33307 | 0.51226 | 0.52585
0.32198 | 0.33306 | 0.51224 | 0.52583
0.32197 | 0.33305 | 0.51221 | 0.52581
0.32196 | 0.33304 | 0.51217 | 0.52579
0.32194 | 0.33303 | 0.51216 | 0.52576
0.32193 | 0.33301 | 0.51213 | 0.52573
0.32191 | 0.333 | 0.51211 | 0.5257
0.3219 | 0.33299 | 0.51209 | 0.52567
0.32189 | 0.33297 | 0.51207 | 0.52565
0.32188 | 0.33295 | 0.51203 | 0.52563
0.32187 | 0.33294 | 0.51199 | 0.52561
0.32185 | 0.33293 | 0.51198 | 0.52559
0.32184 | 0.33291 | 0.51194 | 0.52557
0.32183 | 0.33289 | 0.5119 | 0.52555
0.32182 | 0.33288 | 0.51186 | 0.52552
0.32181 | 0.33287 | 0.51184 | 0.52548
0.32179 | 0.33286 | 0.51182 | 0.52546
0.32178 | 0.33285 | 0.51179 | 0.52543
0.32177 | 0.33284 | 0.51177 | 0.52541
0.32175 | 0.33283 | 0.51173 | 0.52538
0.32173 | 0.33281 | 0.5117 | 0.52537
0.32172 | 0.3328 | 0.51166 | 0.52534
0.32171 | 0.33279 | 0.51163 | 0.52531
0.3217 | 0.33277 | 0.51161 | 0.52528
0.32169 | 0.33276 | 0.51157 | 0.52524
0.32168 | 0.33275 | 0.51155 | 0.52522
0.32167 | 0.33274 | 0.51153 | 0.52518
0.32166 | 0.33273 | 0.51151 | 0.52517
0.32165 | 0.33271 | 0.51147 | 0.52514
0.32164 | 0.3327 | 0.51145 | 0.5251
0.32162 | 0.33269 | 0.51143 | 0.52508
0.32161 | 0.33268 | 0.51141 | 0.52506
0.3216 | 0.33267 | 0.5114 | 0.52504
0.32159 | 0.33265 | 0.51137 | 0.525
0.32157 | 0.33263 | 0.51135 | 0.52497
0.32156 | 0.33262 | 0.51133 | 0.52495
0.32155 | 0.33261 | 0.51129 | 0.52494
0.32153 | 0.3326 | 0.51124 | 0.52491
0.32152 | 0.33259 | 0.51122 | 0.52487
0.32151 | 0.33257 | 0.5112 | 0.52485
0.32149 | 0.33256 | 0.51118 | 0.52482
0.32147 | 0.33255 | 0.51115 | 0.5248
0.32146 | 0.33253 | 0.51112 | 0.52478
0.32145 | 0.33252 | 0.51109 | 0.52476
0.32144 | 0.33251 | 0.51108 | 0.52472
0.32143 | 0.33249 | 0.51104 | 0.5247
0.32141 | 0.33248 | 0.51102 | 0.52467
0.3214 | 0.33246 | 0.51097 | 0.52465
0.32138 | 0.33245 | 0.51094 | 0.52464
0.32137 | 0.33244 | 0.5109 | 0.5246
0.32135 | 0.33243 | 0.51089 | 0.52459
0.32134 | 0.33241 | 0.51086 | 0.52457
0.32133 | 0.3324 | 0.51084 | 0.52454
0.32132 | 0.33239 | 0.51081 | 0.5245
0.32131 | 0.33238 | 0.51078 | 0.52448
0.3213 | 0.33235 | 0.51074 | 0.52446
0.32128 | 0.33234 | 0.5107 | 0.52444
0.32127 | 0.33233 | 0.51068 | 0.52441
0.32125 | 0.33232 | 0.51065 | 0.52439
0.32123 | 0.33231 | 0.51063 | 0.52437
0.32122 | 0.33229 | 0.5106 | 0.52434
0.32121 | 0.33228 | 0.51056 | 0.5243
0.32119 | 0.33226 | 0.51054 | 0.52427
0.32118 | 0.33225 | 0.5105 | 0.52424
0.32117 | 0.33224 | 0.51048 | 0.52421
0.32116 | 0.33223 | 0.51044 | 0.52418
0.32115 | 0.33221 | 0.51041 | 0.52416
0.32114 | 0.3322 | 0.51038 | 0.52413
0.32113 | 0.33219 | 0.51036 | 0.5241
0.32111 | 0.33218 | 0.51034 | 0.52408
0.32109 | 0.33217 | 0.5103 | 0.52406
0.32108 | 0.33215 | 0.51028 | 0.52403
0.32107 | 0.33214 | 0.51026 | 0.52401
0.32104 | 0.33213 | 0.51024 | 0.52399
0.32104 | 0.33212 | 0.51022 | 0.52396
0.32102 | 0.33211 | 0.51018 | 0.52392
0.32102 | 0.3321 | 0.51017 | 0.52391
0.321 | 0.3321 | 0.51012 | 0.52388
0.32098 | 0.33208 | 0.51009 | 0.52386
0.32097 | 0.33207 | 0.51007 | 0.52382
0.32096 | 0.33206 | 0.51005 | 0.5238
0.32095 | 0.33205 | 0.51001 | 0.52378
0.32094 | 0.33203 | 0.50999 | 0.52376
0.32093 | 0.33202 | 0.50995 | 0.52373
0.32092 | 0.33201 | 0.50992 | 0.5237
0.32091 | 0.332 | 0.50989 | 0.52367
0.3209 | 0.33199 | 0.50987 | 0.52365
0.32088 | 0.33198 | 0.50985 | 0.52361
0.32087 | 0.33196 | 0.50982 | 0.5236
0.32086 | 0.33195 | 0.50979 | 0.52356
0.32084 | 0.33194 | 0.50977 | 0.52353
0.32083 | 0.33193 | 0.50975 | 0.52349
0.32082 | 0.33191 | 0.5097 | 0.52347
0.3208 | 0.3319 | 0.50968 | 0.52345
0.32078 | 0.33189 | 0.50965 | 0.52342
0.32077 | 0.33188 | 0.50963 | 0.52339
0.32075 | 0.33186 | 0.5096 | 0.52336
0.32074 | 0.33185 | 0.50957 | 0.52333
0.32072 | 0.33184 | 0.50951 | 0.5233
0.32071 | 0.33183 | 0.50948 | 0.52328
0.32069 | 0.33182 | 0.50946 | 0.52326
0.32068 | 0.3318 | 0.50943 | 0.52324
0.32067 | 0.33178 | 0.50939 | 0.52321
0.32066 | 0.33178 | 0.50936 | 0.52319
0.32065 | 0.33177 | 0.50934 | 0.52317
0.32064 | 0.33175 | 0.50931 | 0.52314
0.32062 | 0.33174 | 0.50928 | 0.52312
0.32061 | 0.33173 | 0.50926 | 0.5231
0.3206 | 0.33172 | 0.50922 | 0.52307
0.32059 | 0.33171 | 0.5092 | 0.52304
0.32058 | 0.3317 | 0.50918 | 0.52301
0.32056 | 0.33169 | 0.50915 | 0.52299
0.32055 | 0.33168 | 0.50912 | 0.52296
0.32054 | 0.33167 | 0.50909 | 0.52293
0.32053 | 0.33165 | 0.50905 | 0.52291
0.32052 | 0.33164 | 0.50903 | 0.52289
0.3205 | 0.33163 | 0.509 | 0.52286
0.32049 | 0.33162 | 0.50896 | 0.52284
0.32048 | 0.33161 | 0.50892 | 0.5228
0.32047 | 0.3316 | 0.50889 | 0.52277
0.32046 | 0.33159 | 0.50885 | 0.52275
0.32045 | 0.33159 | 0.50882 | 0.52273
0.32044 | 0.33156 | 0.50879 | 0.5227
0.32043 | 0.33156 | 0.50877 | 0.52266
0.32041 | 0.33155 | 0.50873 | 0.52264
0.3204 | 0.33154 | 0.5087 | 0.52261
0.32039 | 0.33153 | 0.50867 | 0.52259
0.32038 | 0.33151 | 0.50864 | 0.52257
0.32037 | 0.33149 | 0.50861 | 0.52254
0.32036 | 0.33149 | 0.50857 | 0.52252
0.32035 | 0.33147 | 0.50854 | 0.5225
0.32034 | 0.33146 | 0.50852 | 0.52246
0.32033 | 0.33144 | 0.50849 | 0.52244
0.32031 | 0.33143 | 0.50847 | 0.5224
0.3203 | 0.33142 | 0.50843 | 0.52238
0.32029 | 0.33141 | 0.50842 | 0.52236
0.32027 | 0.3314 | 0.50839 | 0.52233
0.32026 | 0.33139 | 0.50836 | 0.5223
0.32025 | 0.33138 | 0.50833 | 0.52227
0.32024 | 0.33137 | 0.50829 | 0.52225
0.32023 | 0.33136 | 0.50826 | 0.52223
0.32021 | 0.33135 | 0.50824 | 0.52221
0.3202 | 0.33133 | 0.50821 | 0.52217
0.32019 | 0.33132 | 0.50819 | 0.52216
0.32017 | 0.33131 | 0.50816 | 0.52213
0.32016 | 0.33129 | 0.50812 | 0.52209
0.32015 | 0.33127 | 0.5081 | 0.52206
0.32012 | 0.33126 | 0.50805 | 0.52203
0.32011 | 0.33124 | 0.508 | 0.52201
0.3201 | 0.33123 | 0.50797 | 0.52198
0.32009 | 0.33122 | 0.50795 | 0.52196
0.32008 | 0.33121 | 0.50791 | 0.52195
0.32007 | 0.3312 | 0.50789 | 0.52191
0.32006 | 0.33119 | 0.50786 | 0.52188
0.32005 | 0.33117 | 0.50783 | 0.52185
0.32003 | 0.33116 | 0.50779 | 0.52183
0.32001 | 0.33115 | 0.50776 | 0.5218
0.32 | 0.33115 | 0.50774 | 0.52177
0.31999 | 0.33114 | 0.5077 | 0.52174
0.31997 | 0.33112 | 0.50766 | 0.52171
0.31996 | 0.33111 | 0.50761 | 0.52168
0.31994 | 0.3311 | 0.50759 | 0.52166
0.31992 | 0.33108 | 0.50755 | 0.52164
0.31991 | 0.33107 | 0.50751 | 0.52161
0.31989 | 0.33106 | 0.50747 | 0.52158
0.31988 | 0.33105 | 0.50746 | 0.52154
0.31987 | 0.33103 | 0.50743 | 0.52149
0.31986 | 0.33101 | 0.5074 | 0.52146
0.31985 | 0.331 | 0.50737 | 0.52143
0.31983 | 0.33099 | 0.50735 | 0.5214
0.31982 | 0.33098 | 0.50733 | 0.52136
0.31981 | 0.33096 | 0.5073 | 0.52134
0.31979 | 0.33095 | 0.50727 | 0.52132
0.31977 | 0.33094 | 0.50726 | 0.5213
0.31976 | 0.33093 | 0.50723 | 0.52126
0.31975 | 0.33092 | 0.5072 | 0.52124
0.31973 | 0.3309 | 0.50717 | 0.52121
0.31972 | 0.33089 | 0.50714 | 0.52119
0.31971 | 0.33088 | 0.5071 | 0.52117
0.3197 | 0.33087 | 0.50707 | 0.52115
0.31969 | 0.33085 | 0.50704 | 0.52113
0.31967 | 0.33084 | 0.50701 | 0.5211
0.31966 | 0.33083 | 0.50698 | 0.52109
0.31965 | 0.33081 | 0.50696 | 0.52105
0.31964 | 0.3308 | 0.50691 | 0.52103
0.31962 | 0.33078 | 0.50689 | 0.521
0.31961 | 0.33077 | 0.50687 | 0.52097
0.3196 | 0.33076 | 0.50683 | 0.52094
0.31959 | 0.33075 | 0.50681 | 0.52091
0.31957 | 0.33074 | 0.50679 | 0.52087
0.31956 | 0.33073 | 0.50673 | 0.52085
0.31956 | 0.33071 | 0.50671 | 0.52083
0.31955 | 0.33071 | 0.50666 | 0.52079
0.31954 | 0.33069 | 0.50663 | 0.52076
0.31952 | 0.33067 | 0.5066 | 0.52074
0.31951 | 0.33066 | 0.50657 | 0.52071
0.3195 | 0.33065 | 0.50654 | 0.52069
0.3195 | 0.33064 | 0.50651 | 0.52066
0.31948 | 0.33062 | 0.50649 | 0.52062
0.31947 | 0.33061 | 0.50647 | 0.52059
0.31945 | 0.3306 | 0.50645 | 0.52055
0.31944 | 0.33059 | 0.50643 | 0.52054
0.31943 | 0.33058 | 0.5064 | 0.52051
0.31942 | 0.33056 | 0.50638 | 0.52048
0.3194 | 0.33055 | 0.50635 | 0.52044
0.31939 | 0.33054 | 0.50633 | 0.52039
0.31938 | 0.33053 | 0.5063 | 0.52036
0.31937 | 0.33052 | 0.50627 | 0.52033
0.31935 | 0.33051 | 0.50625 | 0.5203
0.31934 | 0.33049 | 0.50621 | 0.52028
0.31933 | 0.33049 | 0.50617 | 0.52025
0.31932 | 0.33048 | 0.50613 | 0.52023
0.3193 | 0.33047 | 0.50609 | 0.5202
0.31929 | 0.33046 | 0.50606 | 0.52014
0.31928 | 0.33045 | 0.50603 | 0.52012
0.31926 | 0.33044 | 0.50601 | 0.52008
0.31926 | 0.33044 | 0.50599 | 0.52004
0.31925 | 0.33042 | 0.50596 | 0.52002
0.31923 | 0.3304 | 0.50592 | 0.52001
0.31922 | 0.33039 | 0.50589 | 0.51997
0.31921 | 0.33038 | 0.50587 | 0.51994
0.3192 | 0.33037 | 0.50585 | 0.5199
0.31919 | 0.33036 | 0.50581 | 0.51987
0.31918 | 0.33035 | 0.50577 | 0.51984
0.31917 | 0.33034 | 0.50574 | 0.5198
0.31916 | 0.33033 | 0.50571 | 0.51978
0.31915 | 0.33032 | 0.50568 | 0.51976
0.31913 | 0.33031 | 0.50566 | 0.51972
0.31912 | 0.3303 | 0.50562 | 0.51969
0.31911 | 0.33028 | 0.50559 | 0.51967
0.3191 | 0.33026 | 0.50555 | 0.51965
0.31909 | 0.33025 | 0.50553 | 0.51963
0.31908 | 0.33024 | 0.5055 | 0.5196
0.31907 | 0.33023 | 0.50547 | 0.51958
0.31906 | 0.33022 | 0.50545 | 0.51956
0.31905 | 0.33021 | 0.50542 | 0.51953
0.31904 | 0.3302 | 0.5054 | 0.5195
0.31903 | 0.33019 | 0.50538 | 0.51947
0.31901 | 0.33018 | 0.50535 | 0.51945
0.319 | 0.33017 | 0.50531 | 0.51942
0.319 | 0.33016 | 0.50528 | 0.51939
0.31898 | 0.33014 | 0.50525 | 0.51937
0.31898 | 0.33013 | 0.50523 | 0.51933
0.31897 | 0.33012 | 0.50521 | 0.51931
0.31896 | 0.33011 | 0.50519 | 0.51928
0.31894 | 0.33009 | 0.50518 | 0.51926
0.31894 | 0.33007 | 0.50516 | 0.51924
0.31893 | 0.33005 | 0.50514 | 0.51922
0.3189 | 0.33004 | 0.50512 | 0.51919
0.31889 | 0.33004 | 0.50509 | 0.51916
0.31889 | 0.33002 | 0.50507 | 0.51914
0.31887 | 0.33001 | 0.50502 | 0.5191
0.31885 | 0.33 | 0.50499 | 0.51908
0.31884 | 0.32999 | 0.50496 | 0.51907
0.31883 | 0.32998 | 0.50493 | 0.51903
0.31882 | 0.32997 | 0.5049 | 0.519
0.31881 | 0.32996 | 0.50488 | 0.51898
0.3188 | 0.32995 | 0.50484 | 0.51894
0.31879 | 0.32993 | 0.50482 | 0.51892
0.31878 | 0.32992 | 0.5048 | 0.5189
0.31877 | 0.32991 | 0.50477 | 0.51887
0.31876 | 0.32991 | 0.50473 | 0.51885
0.31875 | 0.3299 | 0.5047 | 0.51883
0.31873 | 0.32989 | 0.50468 | 0.51879
0.31872 | 0.32988 | 0.50465 | 0.51876
0.31871 | 0.32987 | 0.50462 | 0.51873
0.3187 | 0.32985 | 0.50458 | 0.5187
0.31869 | 0.32984 | 0.50454 | 0.51867
0.31868 | 0.32983 | 0.50451 | 0.51864
0.31867 | 0.32982 | 0.50449 | 0.5186
0.31865 | 0.32982 | 0.50445 | 0.51857
0.31864 | 0.32981 | 0.50443 | 0.51854
0.31863 | 0.32979 | 0.50441 | 0.51851
0.31861 | 0.32978 | 0.50438 | 0.51848
0.3186 | 0.32977 | 0.50435 | 0.51846
0.31859 | 0.32976 | 0.50432 | 0.51843
0.31858 | 0.32975 | 0.50426 | 0.5184
0.31857 | 0.32973 | 0.50423 | 0.51838
0.31856 | 0.32972 | 0.5042 | 0.51835
0.31854 | 0.32971 | 0.50418 | 0.51831
0.31853 | 0.3297 | 0.50414 | 0.51828
0.31852 | 0.32969 | 0.50411 | 0.51825
0.31851 | 0.32967 | 0.50406 | 0.51822
0.31849 | 0.32966 | 0.50402 | 0.5182
0.31848 | 0.32965 | 0.504 | 0.51818
0.31847 | 0.32964 | 0.50398 | 0.51815
0.31847 | 0.32963 | 0.50395 | 0.51813
0.31845 | 0.32962 | 0.50392 | 0.51811
0.31844 | 0.32961 | 0.5039 | 0.51809
0.31843 | 0.3296 | 0.50387 | 0.51806
0.31841 | 0.32958 | 0.50385 | 0.51804
0.31839 | 0.32957 | 0.50383 | 0.51801
0.31839 | 0.32956 | 0.5038 | 0.51799
0.31838 | 0.32955 | 0.50376 | 0.51796
0.31837 | 0.32954 | 0.50374 | 0.51793
0.31835 | 0.32953 | 0.50371 | 0.51791
0.31834 | 0.32951 | 0.50369 | 0.51789
0.31832 | 0.32951 | 0.50367 | 0.51787
0.31831 | 0.3295 | 0.50365 | 0.51785
0.31829 | 0.32948 | 0.50363 | 0.51782
0.31828 | 0.32947 | 0.50359 | 0.51781
0.31827 | 0.32946 | 0.50356 | 0.51778
0.31826 | 0.32945 | 0.50354 | 0.51775
0.31824 | 0.32944 | 0.50352 | 0.51772
0.31824 | 0.32943 | 0.50349 | 0.5177
0.31822 | 0.32942 | 0.50345 | 0.51765
0.31822 | 0.32941 | 0.50342 | 0.51763
0.3182 | 0.32941 | 0.50339 | 0.51761
0.31819 | 0.32939 | 0.50336 | 0.51758
0.31817 | 0.32938 | 0.50333 | 0.51756
0.31817 | 0.32937 | 0.50331 | 0.51754
0.31815 | 0.32936 | 0.5033 | 0.5175
0.31814 | 0.32934 | 0.50327 | 0.51748
0.31813 | 0.32933 | 0.50324 | 0.51745
0.31812 | 0.32932 | 0.50321 | 0.51744
0.31811 | 0.32932 | 0.50318 | 0.51741
0.3181 | 0.32931 | 0.50316 | 0.51738
0.31809 | 0.3293 | 0.50312 | 0.51736
0.31808 | 0.32929 | 0.50307 | 0.51732
0.31807 | 0.32928 | 0.50303 | 0.5173
0.31805 | 0.32927 | 0.50302 | 0.51728
0.31804 | 0.32925 | 0.50298 | 0.51725
0.31801 | 0.32924 | 0.50295 | 0.51723
0.318 | 0.32923 | 0.50293 | 0.5172
0.31799 | 0.32923 | 0.50289 | 0.51716
0.31798 | 0.32921 | 0.50287 | 0.51714
0.31796 | 0.3292 | 0.50283 | 0.51712
0.31795 | 0.32919 | 0.50279 | 0.5171
0.31794 | 0.32918 | 0.50275 | 0.51708
0.31793 | 0.32916 | 0.50271 | 0.51705
0.31792 | 0.32915 | 0.50268 | 0.51703
0.31791 | 0.32914 | 0.50265 | 0.51701
0.31789 | 0.32913 | 0.50264 | 0.517
0.31788 | 0.32912 | 0.50262 | 0.51698
0.31786 | 0.32911 | 0.50259 | 0.51695
0.31785 | 0.3291 | 0.50255 | 0.51693
0.31783 | 0.32908 | 0.50252 | 0.5169
0.31781 | 0.32907 | 0.50247 | 0.51687
0.31779 | 0.32906 | 0.50244 | 0.51685
0.31777 | 0.32905 | 0.5024 | 0.51682
0.31776 | 0.32904 | 0.50238 | 0.51678
0.31774 | 0.32903 | 0.50236 | 0.51676
0.31772 | 0.32901 | 0.50232 | 0.51674
0.31771 | 0.329 | 0.50229 | 0.51672
0.31769 | 0.32898 | 0.50226 | 0.51671
0.31767 | 0.32897 | 0.50224 | 0.51667
0.31766 | 0.32895 | 0.50222 | 0.51664
0.31766 | 0.32894 | 0.50219 | 0.51662
0.31764 | 0.32892 | 0.50217 | 0.5166
0.31763 | 0.32891 | 0.50214 | 0.51658
0.31761 | 0.3289 | 0.5021 | 0.51654
0.3176 | 0.32889 | 0.50207 | 0.51652
0.31759 | 0.32887 | 0.50204 | 0.5165
0.31758 | 0.32886 | 0.50201 | 0.51647
0.31757 | 0.32885 | 0.50199 | 0.51644
0.31756 | 0.32883 | 0.50196 | 0.51643
0.31755 | 0.32881 | 0.50194 | 0.51641
0.31754 | 0.32879 | 0.50192 | 0.51638
0.31753 | 0.32878 | 0.5019 | 0.51634
0.31751 | 0.32877 | 0.50188 | 0.51631
0.3175 | 0.32876 | 0.50186 | 0.51628
0.31749 | 0.32875 | 0.50184 | 0.51626
0.31748 | 0.32874 | 0.50179 | 0.51624
0.31746 | 0.32874 | 0.50176 | 0.51621
0.31746 | 0.32872 | 0.50173 | 0.51618
0.31744 | 0.32871 | 0.5017 | 0.51613
0.31743 | 0.3287 | 0.50167 | 0.51611
0.31742 | 0.32869 | 0.50165 | 0.5161
0.31741 | 0.32868 | 0.50162 | 0.51607
0.3174 | 0.32867 | 0.5016 | 0.51605
0.31739 | 0.32865 | 0.50158 | 0.51602
0.31737 | 0.32864 | 0.50154 | 0.51598
0.31736 | 0.32863 | 0.50151 | 0.51596
0.31735 | 0.32862 | 0.50149 | 0.51593
0.31734 | 0.32861 | 0.50146 | 0.51591
0.31733 | 0.32859 | 0.50144 | 0.51588
0.31731 | 0.32859 | 0.50142 | 0.51586
0.3173 | 0.32857 | 0.5014 | 0.51582
0.31729 | 0.32856 | 0.50137 | 0.5158
0.31727 | 0.32855 | 0.50134 | 0.51576
0.31726 | 0.32854 | 0.50132 | 0.51573
0.31725 | 0.32853 | 0.50129 | 0.5157
0.31724 | 0.32851 | 0.50127 | 0.51568
0.31723 | 0.3285 | 0.50125 | 0.51565
0.31722 | 0.32848 | 0.50122 | 0.51562
0.31721 | 0.32847 | 0.50119 | 0.51557
0.31719 | 0.32847 | 0.50117 | 0.51555
0.31718 | 0.32846 | 0.50113 | 0.51552
0.31716 | 0.32845 | 0.50111 | 0.5155
0.31715 | 0.32842 | 0.50107 | 0.51549
0.31714 | 0.3284 | 0.50105 | 0.51548
0.31713 | 0.32839 | 0.50102 | 0.51545
0.31712 | 0.32838 | 0.50097 | 0.51544
0.31711 | 0.32836 | 0.50095 | 0.51543
0.3171 | 0.32835 | 0.50092 | 0.51539
0.31709 | 0.32833 | 0.50089 | 0.51537
0.31708 | 0.32832 | 0.50086 | 0.51535
0.31707 | 0.3283 | 0.50082 | 0.51533
0.31705 | 0.32829 | 0.5008 | 0.5153
0.31704 | 0.32828 | 0.50077 | 0.51528
0.31702 | 0.32827 | 0.50075 | 0.51524
0.31701 | 0.32825 | 0.50072 | 0.51522
0.317 | 0.32824 | 0.5007 | 0.5152
0.31698 | 0.32823 | 0.50068 | 0.51515
0.31697 | 0.32822 | 0.50066 | 0.51513
0.31696 | 0.3282 | 0.50061 | 0.5151
0.31695 | 0.32819 | 0.50058 | 0.51507
0.31693 | 0.32818 | 0.50056 | 0.51505
0.31692 | 0.32817 | 0.50051 | 0.51502
0.31691 | 0.32816 | 0.50048 | 0.51499
0.3169 | 0.32815 | 0.50046 | 0.51494
0.31689 | 0.32814 | 0.50044 | 0.51492
0.31688 | 0.32813 | 0.50041 | 0.51489
0.31687 | 0.32812 | 0.50037 | 0.51486
0.31686 | 0.32811 | 0.50035 | 0.51482
0.31685 | 0.32809 | 0.5003 | 0.51479
0.31683 | 0.32807 | 0.50027 | 0.51477
0.31682 | 0.32806 | 0.50024 | 0.51474
0.31681 | 0.32804 | 0.50022 | 0.51472
0.3168 | 0.32803 | 0.50019 | 0.5147
0.31679 | 0.32802 | 0.50016 | 0.51468
0.31677 | 0.328 | 0.50014 | 0.51465
0.31676 | 0.328 | 0.50011 | 0.51461
0.31675 | 0.32799 | 0.50008 | 0.51459
0.31673 | 0.32798 | 0.50006 | 0.51458
0.31673 | 0.32797 | 0.50004 | 0.51456
0.31672 | 0.32795 | 0.50002 | 0.51455
0.3167 | 0.32793 | 0.49998 | 0.51453
0.3167 | 0.32793 | 0.49995 | 0.51449
0.31669 | 0.32791 | 0.49992 | 0.51446
0.31667 | 0.3279 | 0.49988 | 0.51444
0.31666 | 0.32788 | 0.49985 | 0.51441
0.31663 | 0.32787 | 0.4998 | 0.51439
0.31662 | 0.32786 | 0.49978 | 0.51437
0.31661 | 0.32785 | 0.49974 | 0.51435
0.3166 | 0.32784 | 0.49971 | 0.51434
0.31659 | 0.32784 | 0.49967 | 0.51431
0.31658 | 0.32783 | 0.49964 | 0.51429
0.31656 | 0.32781 | 0.49962 | 0.51426
0.31655 | 0.32779 | 0.49959 | 0.51424
0.31653 | 0.32778 | 0.49956 | 0.51421
0.31652 | 0.32777 | 0.49953 | 0.51417
0.3165 | 0.32776 | 0.49949 | 0.51416
0.3165 | 0.32775 | 0.49947 | 0.51414
0.31648 | 0.32774 | 0.49943 | 0.51412
0.31647 | 0.32773 | 0.4994 | 0.51407
0.31646 | 0.32771 | 0.49936 | 0.51404
0.31645 | 0.3277 | 0.49933 | 0.514
0.31644 | 0.32769 | 0.4993 | 0.51398
0.31643 | 0.32768 | 0.49929 | 0.51395
0.31641 | 0.32767 | 0.49928 | 0.51392
0.3164 | 0.32766 | 0.49923 | 0.5139
0.31638 | 0.32765 | 0.49919 | 0.51388
0.31636 | 0.32764 | 0.49916 | 0.51386
0.31634 | 0.32763 | 0.49914 | 0.51383
0.31634 | 0.32762 | 0.49912 | 0.51381
0.31632 | 0.32761 | 0.49909 | 0.51379
0.31631 | 0.3276 | 0.49907 | 0.51376
0.3163 | 0.32759 | 0.49903 | 0.51374
0.31629 | 0.32757 | 0.499 | 0.51372
0.31627 | 0.32756 | 0.49898 | 0.51369
0.31626 | 0.32755 | 0.49896 | 0.51367
0.31625 | 0.32754 | 0.49893 | 0.51365
0.31624 | 0.32753 | 0.49891 | 0.51359
0.31623 | 0.32752 | 0.49888 | 0.51356
0.31622 | 0.3275 | 0.49887 | 0.51352
0.31621 | 0.32748 | 0.49883 | 0.5135
0.3162 | 0.32748 | 0.4988 | 0.51348
0.31619 | 0.32747 | 0.49877 | 0.51346
0.31618 | 0.32746 | 0.49875 | 0.51343
0.31617 | 0.32744 | 0.49873 | 0.5134
0.31616 | 0.32743 | 0.4987 | 0.51337
0.31615 | 0.32742 | 0.49867 | 0.51335
0.31614 | 0.32741 | 0.49865 | 0.51331
0.31612 | 0.3274 | 0.49862 | 0.51329
0.31611 | 0.32738 | 0.49859 | 0.51325
0.3161 | 0.32737 | 0.49857 | 0.51323
0.31609 | 0.32736 | 0.49855 | 0.51322
0.31608 | 0.32735 | 0.49853 | 0.51319
0.31607 | 0.32734 | 0.4985 | 0.51315
0.31606 | 0.32732 | 0.49847 | 0.51312
0.31605 | 0.32731 | 0.49843 | 0.51311
0.31604 | 0.32729 | 0.4984 | 0.51308
0.31603 | 0.32728 | 0.49837 | 0.51307
0.31601 | 0.32727 | 0.49834 | 0.51305
0.316 | 0.32726 | 0.49831 | 0.51302
0.31599 | 0.32724 | 0.49828 | 0.513
0.31598 | 0.32723 | 0.49826 | 0.51298
0.31597 | 0.32722 | 0.49823 | 0.51296
0.31596 | 0.32721 | 0.4982 | 0.51292
0.31594 | 0.32719 | 0.49817 | 0.5129
0.31593 | 0.32718 | 0.49815 | 0.51286
0.31592 | 0.32717 | 0.49811 | 0.51283
0.31591 | 0.32716 | 0.49809 | 0.5128
0.3159 | 0.32714 | 0.49804 | 0.51277
0.31589 | 0.32712 | 0.49801 | 0.51274
0.31587 | 0.32711 | 0.49798 | 0.51272
0.31587 | 0.3271 | 0.49796 | 0.5127
0.31585 | 0.32708 | 0.49793 | 0.51267
0.31583 | 0.32708 | 0.49788 | 0.51263
0.31582 | 0.32707 | 0.49786 | 0.5126
0.31581 | 0.32706 | 0.49783 | 0.51257
0.3158 | 0.32705 | 0.4978 | 0.51255
0.31579 | 0.32704 | 0.49779 | 0.51252
0.31578 | 0.32704 | 0.49777 | 0.51249
0.31578 | 0.32703 | 0.49773 | 0.51247
0.31576 | 0.32701 | 0.49771 | 0.51245
0.31575 | 0.32701 | 0.49768 | 0.51243
0.31574 | 0.327 | 0.49765 | 0.5124
0.31573 | 0.32699 | 0.49763 | 0.51238
0.31572 | 0.32697 | 0.49762 | 0.51233
0.31571 | 0.32696 | 0.49759 | 0.5123
0.3157 | 0.32695 | 0.49757 | 0.51229
0.31569 | 0.32694 | 0.49754 | 0.51225
0.31568 | 0.32693 | 0.49751 | 0.51222
0.31568 | 0.32692 | 0.49749 | 0.51219
0.31567 | 0.32691 | 0.49747 | 0.51217
0.31565 | 0.32691 | 0.49742 | 0.51215
0.31564 | 0.32689 | 0.4974 | 0.51213
0.31563 | 0.32688 | 0.49735 | 0.51211
0.31562 | 0.32688 | 0.49732 | 0.5121
0.31561 | 0.32687 | 0.49729 | 0.51208
0.3156 | 0.32686 | 0.49726 | 0.51206
0.31559 | 0.32685 | 0.49724 | 0.51202
0.31558 | 0.32683 | 0.49721 | 0.51199
0.31557 | 0.32681 | 0.49719 | 0.51195
0.31556 | 0.3268 | 0.49717 | 0.51192
0.31555 | 0.32679 | 0.49714 | 0.5119
0.31554 | 0.32678 | 0.49711 | 0.51188
0.31553 | 0.32677 | 0.49707 | 0.51185
0.31552 | 0.32677 | 0.49704 | 0.51183
0.31551 | 0.32676 | 0.49701 | 0.5118
0.31549 | 0.32675 | 0.49699 | 0.51178
0.31548 | 0.32674 | 0.49696 | 0.51175
0.31546 | 0.32672 | 0.49694 | 0.51173
0.31544 | 0.3267 | 0.49691 | 0.51171
0.31543 | 0.32669 | 0.4969 | 0.51168
0.31543 | 0.32668 | 0.49687 | 0.51166
0.31542 | 0.32667 | 0.49685 | 0.51164
0.31542 | 0.32665 | 0.49682 | 0.51161
0.3154 | 0.32664 | 0.49678 | 0.51158
0.31539 | 0.32663 | 0.49675 | 0.51155
0.31538 | 0.32662 | 0.49673 | 0.51152
0.31537 | 0.32661 | 0.49667 | 0.5115
0.31536 | 0.3266 | 0.49664 | 0.51146
0.31535 | 0.32658 | 0.49661 | 0.51143
0.31534 | 0.32657 | 0.49659 | 0.5114
0.31533 | 0.32656 | 0.49657 | 0.51137
0.31531 | 0.32654 | 0.49655 | 0.51136
0.3153 | 0.32652 | 0.49651 | 0.51132
0.31529 | 0.32651 | 0.49648 | 0.5113
0.31528 | 0.3265 | 0.49645 | 0.51128
0.31527 | 0.32649 | 0.49642 | 0.51126
0.31526 | 0.32648 | 0.49638 | 0.51125
0.31524 | 0.32647 | 0.49637 | 0.51123
0.31523 | 0.32646 | 0.49635 | 0.5112
0.31521 | 0.32646 | 0.49632 | 0.51118
0.31521 | 0.32644 | 0.4963 | 0.51116
0.31519 | 0.32642 | 0.49628 | 0.51114
0.31518 | 0.32641 | 0.49625 | 0.51111
0.31517 | 0.3264 | 0.49622 | 0.51108
0.31515 | 0.32638 | 0.4962 | 0.51106
0.31514 | 0.32637 | 0.49616 | 0.51103
0.31513 | 0.32636 | 0.49614 | 0.51101
0.31512 | 0.32635 | 0.49611 | 0.51097
0.3151 | 0.32635 | 0.49609 | 0.51095
0.31509 | 0.32634 | 0.49606 | 0.51093
0.31508 | 0.32632 | 0.49603 | 0.51089
0.31505 | 0.3263 | 0.49601 | 0.51088
0.31504 | 0.32629 | 0.49597 | 0.51085
0.31503 | 0.32627 | 0.49594 | 0.51083
0.31503 | 0.32626 | 0.49591 | 0.51082
0.31502 | 0.32625 | 0.49588 | 0.5108
0.31501 | 0.32624 | 0.49584 | 0.51077
0.31499 | 0.32623 | 0.49582 | 0.51075
0.31499 | 0.32622 | 0.49578 | 0.51073
0.31497 | 0.3262 | 0.49576 | 0.5107
0.31496 | 0.32619 | 0.49573 | 0.51069
0.31495 | 0.32618 | 0.4957 | 0.51066
0.31494 | 0.32617 | 0.49568 | 0.51064
0.31492 | 0.32615 | 0.49565 | 0.51062
0.31492 | 0.32614 | 0.49563 | 0.5106
0.3149 | 0.32613 | 0.4956 | 0.51059
0.31488 | 0.32612 | 0.49557 | 0.51057
0.31487 | 0.32611 | 0.49554 | 0.51052
0.31487 | 0.32609 | 0.49551 | 0.51048
0.31484 | 0.32607 | 0.49547 | 0.51046
0.31483 | 0.32607 | 0.49545 | 0.51044
0.31482 | 0.32606 | 0.49542 | 0.51041
0.3148 | 0.32604 | 0.4954 | 0.51037
0.31479 | 0.32604 | 0.49537 | 0.51034
0.31478 | 0.32602 | 0.49535 | 0.51032
0.31476 | 0.32602 | 0.49533 | 0.51029
0.31475 | 0.32601 | 0.49531 | 0.51027
0.31474 | 0.32599 | 0.49528 | 0.51025
0.31473 | 0.32597 | 0.49522 | 0.51023
0.31471 | 0.32597 | 0.4952 | 0.51019
0.3147 | 0.32596 | 0.49517 | 0.51016
0.31469 | 0.32594 | 0.49513 | 0.51014
0.31468 | 0.32593 | 0.4951 | 0.51012
0.31467 | 0.32592 | 0.49508 | 0.51009
0.31466 | 0.3259 | 0.49503 | 0.51005
0.31465 | 0.32589 | 0.49501 | 0.51002
0.31464 | 0.32587 | 0.49498 | 0.50999
0.31463 | 0.32586 | 0.49495 | 0.50997
0.31462 | 0.32585 | 0.4949 | 0.50993
0.31461 | 0.32584 | 0.49488 | 0.50991
0.3146 | 0.32583 | 0.49486 | 0.50989
0.31459 | 0.32582 | 0.49484 | 0.50986
0.31458 | 0.32581 | 0.49481 | 0.50984
0.31457 | 0.3258 | 0.49479 | 0.50981
0.31455 | 0.32578 | 0.49477 | 0.50979
0.31455 | 0.32577 | 0.49474 | 0.50975
0.31453 | 0.32575 | 0.49472 | 0.50973
0.31452 | 0.32574 | 0.4947 | 0.50969
0.31451 | 0.32573 | 0.49467 | 0.50966
0.3145 | 0.32571 | 0.49464 | 0.50965
0.31449 | 0.3257 | 0.49462 | 0.50961
0.31448 | 0.32569 | 0.49459 | 0.50959
0.31447 | 0.32568 | 0.49456 | 0.50957
0.31446 | 0.32567 | 0.49454 | 0.50955
0.31446 | 0.32565 | 0.49452 | 0.50952
0.31444 | 0.32564 | 0.4945 | 0.5095
0.31443 | 0.32563 | 0.49448 | 0.50946
0.31442 | 0.32562 | 0.49446 | 0.50944
0.31441 | 0.32561 | 0.49443 | 0.50943
0.31439 | 0.3256 | 0.49441 | 0.5094
0.31438 | 0.32559 | 0.49437 | 0.50938
0.31437 | 0.32558 | 0.49435 | 0.50936
0.31436 | 0.32557 | 0.49433 | 0.50935
0.31433 | 0.32555 | 0.49428 | 0.50932
0.31432 | 0.32554 | 0.49423 | 0.50929
0.31431 | 0.32554 | 0.49421 | 0.50926
0.3143 | 0.32552 | 0.49418 | 0.50923
0.31429 | 0.32551 | 0.49415 | 0.50919
0.31428 | 0.3255 | 0.49413 | 0.50917
0.31427 | 0.32549 | 0.4941 | 0.50914
0.31426 | 0.32548 | 0.49406 | 0.50911
0.31425 | 0.32548 | 0.49402 | 0.50908
0.31424 | 0.32547 | 0.49399 | 0.50905
0.31424 | 0.32546 | 0.49396 | 0.50902
0.31423 | 0.32545 | 0.49393 | 0.50899
0.31422 | 0.32543 | 0.49389 | 0.50895
0.31421 | 0.32542 | 0.49385 | 0.50892
0.3142 | 0.32541 | 0.49381 | 0.50889
0.31419 | 0.3254 | 0.49378 | 0.50886
0.31417 | 0.32539 | 0.49373 | 0.50884
0.31415 | 0.32538 | 0.49372 | 0.50881
0.31415 | 0.32538 | 0.49369 | 0.50877
0.31414 | 0.32537 | 0.49368 | 0.50875
0.31413 | 0.32536 | 0.49365 | 0.5087
0.31412 | 0.32535 | 0.49362 | 0.50867
0.3141 | 0.32534 | 0.4936 | 0.50865
0.31409 | 0.32534 | 0.49358 | 0.50863
0.31408 | 0.32533 | 0.49355 | 0.50861
0.31406 | 0.32532 | 0.49352 | 0.50859
0.31404 | 0.32531 | 0.49347 | 0.50857
0.31403 | 0.3253 | 0.49345 | 0.50855
0.31402 | 0.32528 | 0.49342 | 0.50852
0.31401 | 0.32527 | 0.4934 | 0.5085
0.314 | 0.32525 | 0.49338 | 0.50847
0.31398 | 0.32524 | 0.49335 | 0.50844
0.31396 | 0.32523 | 0.49332 | 0.5084
0.31396 | 0.32522 | 0.4933 | 0.50838
0.31395 | 0.32521 | 0.49327 | 0.50836
0.31394 | 0.32519 | 0.49323 | 0.50835
0.31393 | 0.32518 | 0.4932 | 0.50832
0.31392 | 0.32516 | 0.49316 | 0.50828
0.31391 | 0.32515 | 0.49314 | 0.50826
0.3139 | 0.32514 | 0.49311 | 0.50824
0.31389 | 0.32513 | 0.49309 | 0.50821
0.31387 | 0.32512 | 0.49308 | 0.50819
0.31386 | 0.3251 | 0.49304 | 0.50817
0.31385 | 0.32509 | 0.49303 | 0.50813
0.31384 | 0.32508 | 0.49301 | 0.50812
0.31383 | 0.32507 | 0.49298 | 0.5081
0.31382 | 0.32507 | 0.49296 | 0.50808
0.31381 | 0.32506 | 0.49294 | 0.50805
0.3138 | 0.32504 | 0.49291 | 0.50802
0.31378 | 0.32503 | 0.49288 | 0.508
0.31377 | 0.32502 | 0.49286 | 0.50799
0.31376 | 0.325 | 0.49283 | 0.50797
0.31374 | 0.32499 | 0.4928 | 0.50794
0.31373 | 0.32499 | 0.49277 | 0.50791
0.31372 | 0.32497 | 0.49274 | 0.50789
0.31371 | 0.32495 | 0.49271 | 0.50788
0.31369 | 0.32494 | 0.49268 | 0.50785
0.31368 | 0.32493 | 0.49265 | 0.50783
0.31367 | 0.32492 | 0.4926 | 0.50781
0.31366 | 0.32491 | 0.49258 | 0.50778
0.31365 | 0.3249 | 0.49256 | 0.50776
0.31363 | 0.32489 | 0.49252 | 0.50772
0.31363 | 0.32488 | 0.49248 | 0.5077
0.31362 | 0.32487 | 0.49245 | 0.50768
0.31361 | 0.32486 | 0.49242 | 0.50766
0.3136 | 0.32485 | 0.4924 | 0.50763
0.31358 | 0.32483 | 0.49238 | 0.5076
0.31358 | 0.32483 | 0.49236 | 0.50757
0.31357 | 0.32482 | 0.49233 | 0.50754
0.31356 | 0.32481 | 0.49231 | 0.50752
0.31354 | 0.3248 | 0.49228 | 0.50749
0.31353 | 0.32479 | 0.49226 | 0.50747
0.31352 | 0.32478 | 0.49224 | 0.50743
0.31351 | 0.32477 | 0.49221 | 0.50742
0.31349 | 0.32476 | 0.49218 | 0.5074
0.31348 | 0.32474 | 0.49216 | 0.50738
0.31347 | 0.32473 | 0.49214 | 0.50735
0.31346 | 0.32472 | 0.49211 | 0.50733
0.31345 | 0.32471 | 0.49208 | 0.50731
0.31344 | 0.32469 | 0.49205 | 0.50729
0.31343 | 0.32468 | 0.49203 | 0.50727
0.31341 | 0.32467 | 0.492 | 0.50723
0.3134 | 0.32467 | 0.49198 | 0.50721
0.31339 | 0.32465 | 0.49195 | 0.50718
0.31338 | 0.32465 | 0.49194 | 0.50717
0.31337 | 0.32463 | 0.4919 | 0.50714
0.31336 | 0.32462 | 0.49186 | 0.50713
0.31335 | 0.32461 | 0.49184 | 0.50711
0.31334 | 0.3246 | 0.49182 | 0.50708
0.31332 | 0.32459 | 0.4918 | 0.50705
0.31331 | 0.32459 | 0.49177 | 0.50703
0.3133 | 0.32457 | 0.49175 | 0.507
0.31328 | 0.32456 | 0.49173 | 0.50698
0.31327 | 0.32456 | 0.4917 | 0.50696
0.31326 | 0.32455 | 0.49166 | 0.50692
0.31326 | 0.32454 | 0.49163 | 0.50689
0.31324 | 0.32452 | 0.4916 | 0.50687
0.31323 | 0.32451 | 0.49157 | 0.50685
0.31322 | 0.32449 | 0.49154 | 0.50682
0.31321 | 0.32448 | 0.4915 | 0.50679
0.3132 | 0.32447 | 0.49149 | 0.50677
0.31318 | 0.32446 | 0.49146 | 0.50674
0.31317 | 0.32444 | 0.49143 | 0.50671
0.31316 | 0.32444 | 0.49139 | 0.50669
0.31315 | 0.32442 | 0.49137 | 0.50667
0.31314 | 0.32441 | 0.49133 | 0.50665
0.31312 | 0.3244 | 0.49131 | 0.50663
0.31311 | 0.32439 | 0.49128 | 0.50661
0.3131 | 0.32438 | 0.49127 | 0.50658
0.31309 | 0.32438 | 0.49124 | 0.50655
0.31308 | 0.32436 | 0.49122 | 0.50652
0.31307 | 0.32435 | 0.49119 | 0.50649
0.31306 | 0.32434 | 0.49115 | 0.50646
0.31305 | 0.32433 | 0.49112 | 0.50643
0.31304 | 0.32432 | 0.49107 | 0.5064
0.31303 | 0.32431 | 0.49104 | 0.50639
0.31302 | 0.3243 | 0.491 | 0.50635
0.31301 | 0.32429 | 0.49098 | 0.50633
0.313 | 0.32428 | 0.49097 | 0.50629
0.31298 | 0.32427 | 0.49096 | 0.50628
0.31297 | 0.32425 | 0.49093 | 0.50626
0.31295 | 0.32423 | 0.4909 | 0.50623
0.31294 | 0.32422 | 0.49089 | 0.5062
0.31293 | 0.32421 | 0.49086 | 0.50617
0.31293 | 0.3242 | 0.49083 | 0.50615
0.31291 | 0.32419 | 0.4908 | 0.50613
0.3129 | 0.32418 | 0.49077 | 0.50611
0.31289 | 0.32417 | 0.49073 | 0.50607
0.31288 | 0.32416 | 0.49071 | 0.50605
0.31285 | 0.32415 | 0.49068 | 0.50603
0.31284 | 0.32413 | 0.49067 | 0.50601
0.31283 | 0.32412 | 0.49063 | 0.50597
0.31281 | 0.32411 | 0.49061 | 0.50595
0.3128 | 0.3241 | 0.49059 | 0.50592
0.31279 | 0.32409 | 0.49056 | 0.5059
0.31277 | 0.32408 | 0.49052 | 0.50587
0.31276 | 0.32406 | 0.4905 | 0.50584
0.31276 | 0.32405 | 0.49044 | 0.50582
0.31275 | 0.32403 | 0.49042 | 0.50579
0.31274 | 0.32402 | 0.4904 | 0.50576
0.31273 | 0.32401 | 0.49038 | 0.50572
0.31272 | 0.324 | 0.49036 | 0.5057
0.31271 | 0.32399 | 0.49033 | 0.50566
0.3127 | 0.32398 | 0.49029 | 0.50564
0.31269 | 0.32397 | 0.49027 | 0.50562
0.31268 | 0.32396 | 0.49022 | 0.5056
0.31267 | 0.32394 | 0.49019 | 0.50559
0.31265 | 0.32394 | 0.49016 | 0.50556
0.31264 | 0.32393 | 0.49015 | 0.50553
0.31263 | 0.32391 | 0.49011 | 0.50551
0.31261 | 0.3239 | 0.49008 | 0.50549
0.3126 | 0.32389 | 0.49004 | 0.50546
0.31258 | 0.32388 | 0.49002 | 0.50544
0.31257 | 0.32386 | 0.48999 | 0.50541
0.31256 | 0.32385 | 0.48995 | 0.50537
0.31255 | 0.32385 | 0.48993 | 0.50535
0.31255 | 0.32384 | 0.48991 | 0.50533
0.31253 | 0.32383 | 0.48989 | 0.5053
0.31252 | 0.32381 | 0.48986 | 0.50527
0.31251 | 0.3238 | 0.48984 | 0.50525
0.3125 | 0.3238 | 0.4898 | 0.50523
0.31249 | 0.32379 | 0.48978 | 0.5052
0.31248 | 0.32378 | 0.48975 | 0.50519
0.31247 | 0.32376 | 0.48973 | 0.50517
0.31246 | 0.32375 | 0.4897 | 0.50515
0.31245 | 0.32374 | 0.48967 | 0.50512
0.31244 | 0.32373 | 0.48965 | 0.5051
0.31243 | 0.32372 | 0.48962 | 0.50507
0.31242 | 0.32371 | 0.48957 | 0.50505
0.3124 | 0.32369 | 0.48955 | 0.50503
0.31239 | 0.32368 | 0.48951 | 0.50501
0.31238 | 0.32367 | 0.4895 | 0.50499
0.31237 | 0.32366 | 0.48946 | 0.50496
0.31235 | 0.32364 | 0.48943 | 0.50494
0.31235 | 0.32364 | 0.4894 | 0.50492
0.31234 | 0.32363 | 0.48937 | 0.5049
0.31233 | 0.32362 | 0.48934 | 0.50488
0.31232 | 0.3236 | 0.48931 | 0.50485
0.31231 | 0.32359 | 0.48929 | 0.50482
0.3123 | 0.32358 | 0.48927 | 0.50477
0.31228 | 0.32357 | 0.48925 | 0.50474
0.31227 | 0.32356 | 0.48922 | 0.50472
0.31226 | 0.32355 | 0.48919 | 0.5047
0.31225 | 0.32354 | 0.48917 | 0.50466
0.31224 | 0.32352 | 0.48914 | 0.50463
0.31222 | 0.32351 | 0.48912 | 0.50461
0.31221 | 0.32349 | 0.4891 | 0.50459
0.31221 | 0.32348 | 0.48908 | 0.50456
0.3122 | 0.32347 | 0.48906 | 0.50454
0.31219 | 0.32346 | 0.48904 | 0.50452
0.31218 | 0.32345 | 0.48902 | 0.50449
0.31217 | 0.32344 | 0.48899 | 0.50446
0.31216 | 0.32343 | 0.48896 | 0.50443
0.31215 | 0.32342 | 0.48894 | 0.5044
0.31214 | 0.32341 | 0.48891 | 0.50437
0.31213 | 0.3234 | 0.48888 | 0.50434
0.31212 | 0.32339 | 0.48886 | 0.50431
0.31211 | 0.32338 | 0.48884 | 0.50428
0.3121 | 0.32337 | 0.48881 | 0.50426
0.31209 | 0.32335 | 0.48878 | 0.50424
0.31209 | 0.32334 | 0.48875 | 0.50422
0.31208 | 0.32333 | 0.48872 | 0.50419
0.31207 | 0.32332 | 0.4887 | 0.50416
0.31206 | 0.32331 | 0.48867 | 0.50413
0.31205 | 0.3233 | 0.48864 | 0.50409
0.31204 | 0.32329 | 0.48862 | 0.50407
0.31203 | 0.32328 | 0.4886 | 0.50405
0.31201 | 0.32326 | 0.48857 | 0.50402
0.312 | 0.32325 | 0.48852 | 0.504
0.31199 | 0.32324 | 0.48848 | 0.50397
0.31198 | 0.32322 | 0.48844 | 0.50394
0.31196 | 0.32321 | 0.48842 | 0.50393
0.31195 | 0.3232 | 0.4884 | 0.5039
0.31194 | 0.32318 | 0.48838 | 0.50387
0.31193 | 0.32317 | 0.48834 | 0.50384
0.31192 | 0.32316 | 0.48831 | 0.50381
0.31191 | 0.32315 | 0.48827 | 0.5038
0.3119 | 0.32313 | 0.48825 | 0.50378
0.31189 | 0.32312 | 0.48823 | 0.50376
0.31188 | 0.32311 | 0.48819 | 0.50372
0.31187 | 0.32309 | 0.48818 | 0.50369
0.31186 | 0.32309 | 0.48814 | 0.50367
0.31186 | 0.32307 | 0.48811 | 0.50363
0.31184 | 0.32306 | 0.48809 | 0.5036
0.31184 | 0.32305 | 0.48808 | 0.50357
0.31183 | 0.32304 | 0.48803 | 0.50353
0.31182 | 0.32303 | 0.48802 | 0.50348
0.31181 | 0.32302 | 0.48798 | 0.50345
0.3118 | 0.32301 | 0.48794 | 0.50341
0.3118 | 0.323 | 0.48791 | 0.50338
0.31179 | 0.32299 | 0.48788 | 0.50336
0.31177 | 0.32297 | 0.48786 | 0.50334
0.31177 | 0.32296 | 0.48783 | 0.50332
0.31176 | 0.32296 | 0.48781 | 0.50329
0.31174 | 0.32295 | 0.48778 | 0.50326
0.31173 | 0.32293 | 0.48775 | 0.50323
0.31172 | 0.32292 | 0.4877 | 0.5032
0.31171 | 0.32291 | 0.48768 | 0.50316
0.3117 | 0.3229 | 0.48766 | 0.50314
0.31169 | 0.32289 | 0.48762 | 0.50312
0.31167 | 0.32287 | 0.4876 | 0.50311
0.31166 | 0.32286 | 0.48757 | 0.50307
0.31165 | 0.32284 | 0.48755 | 0.50305
0.31164 | 0.32283 | 0.48753 | 0.50301
0.31163 | 0.32282 | 0.4875 | 0.503
0.31162 | 0.3228 | 0.48747 | 0.50297
0.3116 | 0.3228 | 0.48743 | 0.50294
0.31158 | 0.32279 | 0.48742 | 0.50291
0.31157 | 0.32277 | 0.48739 | 0.50287
0.31156 | 0.32277 | 0.48737 | 0.50285
0.31155 | 0.32276 | 0.48735 | 0.50283
0.31154 | 0.32275 | 0.48733 | 0.50281
0.31153 | 0.32274 | 0.48726 | 0.50279
0.31151 | 0.32273 | 0.48724 | 0.50276
0.3115 | 0.32272 | 0.48722 | 0.50275
0.31149 | 0.3227 | 0.48721 | 0.5027
0.31147 | 0.32269 | 0.48719 | 0.50267
0.31145 | 0.32269 | 0.48716 | 0.50265
0.31144 | 0.32268 | 0.48715 | 0.50263
0.31143 | 0.32267 | 0.48712 | 0.5026
0.31142 | 0.32266 | 0.48709 | 0.50258
0.3114 | 0.32264 | 0.48705 | 0.50255
0.3114 | 0.32263 | 0.48702 | 0.50252
0.31138 | 0.32262 | 0.48699 | 0.5025
0.31137 | 0.3226 | 0.48697 | 0.50247
0.31135 | 0.3226 | 0.48694 | 0.50246
0.31134 | 0.32259 | 0.48692 | 0.50244
0.31133 | 0.32257 | 0.4869 | 0.50243
0.31132 | 0.32256 | 0.48688 | 0.50241
0.31131 | 0.32254 | 0.48684 | 0.50237
0.3113 | 0.32254 | 0.48681 | 0.50235
0.31129 | 0.32253 | 0.48678 | 0.50231
0.31127 | 0.32252 | 0.48676 | 0.50229
0.31126 | 0.3225 | 0.48673 | 0.50226
0.31125 | 0.3225 | 0.48671 | 0.50221
0.31124 | 0.32249 | 0.48668 | 0.50219
0.31123 | 0.32247 | 0.48664 | 0.50217
0.31121 | 0.32246 | 0.48661 | 0.50215
0.3112 | 0.32245 | 0.48658 | 0.50212
0.3112 | 0.32244 | 0.48656 | 0.50209
0.31118 | 0.32243 | 0.48653 | 0.50208
0.31117 | 0.32242 | 0.4865 | 0.50205
0.31116 | 0.32241 | 0.48647 | 0.50201
0.31115 | 0.32239 | 0.48645 | 0.50198
0.31113 | 0.32239 | 0.48643 | 0.50195
0.31112 | 0.32238 | 0.48639 | 0.50192
0.31111 | 0.32237 | 0.48637 | 0.50189
0.3111 | 0.32236 | 0.48635 | 0.50187
0.31109 | 0.32235 | 0.48633 | 0.50184
0.31108 | 0.32234 | 0.48629 | 0.50181
0.31106 | 0.32232 | 0.48627 | 0.50179
0.31105 | 0.32231 | 0.48624 | 0.50176
0.31105 | 0.32229 | 0.48621 | 0.50174
0.31104 | 0.32229 | 0.48619 | 0.50171
0.31102 | 0.32227 | 0.48617 | 0.50169
0.31102 | 0.32226 | 0.48614 | 0.50167
0.311 | 0.32225 | 0.48612 | 0.50164
0.311 | 0.32224 | 0.48609 | 0.50161
0.31099 | 0.32223 | 0.48607 | 0.50158
0.31098 | 0.32222 | 0.48603 | 0.50157
0.31097 | 0.32221 | 0.48601 | 0.50153
0.31096 | 0.32219 | 0.48598 | 0.50151
0.31095 | 0.32218 | 0.48595 | 0.50147
0.31094 | 0.32217 | 0.48592 | 0.50145
0.31093 | 0.32217 | 0.48589 | 0.50143
0.31092 | 0.32216 | 0.48586 | 0.50141
0.3109 | 0.32214 | 0.48584 | 0.50139
0.31089 | 0.32213 | 0.48581 | 0.50137
0.31088 | 0.32212 | 0.48578 | 0.50135
0.31087 | 0.32211 | 0.48575 | 0.50133
0.31086 | 0.32211 | 0.48572 | 0.5013
0.31085 | 0.3221 | 0.48569 | 0.50127
0.31084 | 0.32208 | 0.48566 | 0.50124
0.31082 | 0.32208 | 0.48564 | 0.50121
0.31081 | 0.32207 | 0.48562 | 0.50118
0.3108 | 0.32206 | 0.4856 | 0.50116
0.31078 | 0.32205 | 0.48558 | 0.50113
0.31077 | 0.32204 | 0.48556 | 0.50111
0.31076 | 0.32203 | 0.48555 | 0.50108
0.31074 | 0.32202 | 0.48553 | 0.50106
0.31073 | 0.32201 | 0.48548 | 0.50105
0.31072 | 0.32199 | 0.48546 | 0.501
0.31071 | 0.32198 | 0.48545 | 0.50098
0.3107 | 0.32197 | 0.48543 | 0.50096
0.31069 | 0.32196 | 0.48539 | 0.50094
0.31068 | 0.32195 | 0.48537 | 0.50092
0.31067 | 0.32194 | 0.48533 | 0.5009
0.31066 | 0.32193 | 0.48531 | 0.50088
0.31065 | 0.32192 | 0.48529 | 0.50085
0.31064 | 0.32191 | 0.48525 | 0.50083
0.31063 | 0.32191 | 0.4852 | 0.5008
0.31062 | 0.3219 | 0.48517 | 0.50077
0.31061 | 0.32189 | 0.48515 | 0.50075
0.3106 | 0.32188 | 0.48513 | 0.50073
0.31059 | 0.32187 | 0.48511 | 0.5007
0.31058 | 0.32186 | 0.48509 | 0.50069
0.31058 | 0.32185 | 0.48505 | 0.50067
0.31057 | 0.32184 | 0.48502 | 0.50065
0.31056 | 0.32183 | 0.48498 | 0.50062
0.31055 | 0.32182 | 0.48495 | 0.5006
0.31054 | 0.3218 | 0.48493 | 0.50057
0.31053 | 0.32179 | 0.48491 | 0.50054
0.31052 | 0.32178 | 0.48489 | 0.50051
0.31051 | 0.32177 | 0.48486 | 0.50049
0.31049 | 0.32175 | 0.48484 | 0.50046
0.31048 | 0.32175 | 0.48482 | 0.50043
0.31047 | 0.32174 | 0.48479 | 0.50041
0.31046 | 0.32173 | 0.48477 | 0.50039
0.31045 | 0.32172 | 0.48474 | 0.50037
0.31044 | 0.32171 | 0.48471 | 0.50034
0.31043 | 0.3217 | 0.48468 | 0.50032
0.31041 | 0.32169 | 0.48465 | 0.5003
0.3104 | 0.32168 | 0.48461 | 0.50028
0.31038 | 0.32167 | 0.48457 | 0.50024
0.31037 | 0.32166 | 0.48456 | 0.50021
0.31036 | 0.32165 | 0.48454 | 0.50019
0.31035 | 0.32164 | 0.48452 | 0.50017
0.31034 | 0.32163 | 0.4845 | 0.50015
0.31033 | 0.32162 | 0.48448 | 0.50012
0.31031 | 0.32161 | 0.48446 | 0.5001
0.3103 | 0.3216 | 0.48443 | 0.50008
0.31029 | 0.32159 | 0.48439 | 0.50007
0.31027 | 0.32158 | 0.48437 | 0.50005
0.31026 | 0.32157 | 0.48434 | 0.50002
0.31025 | 0.32155 | 0.4843 | 0.49999
0.31024 | 0.32154 | 0.48427 | 0.49996
0.31023 | 0.32153 | 0.48424 | 0.49993
0.31022 | 0.32152 | 0.4842 | 0.4999
0.31021 | 0.32151 | 0.48417 | 0.49988
0.3102 | 0.32149 | 0.48413 | 0.49986
0.31019 | 0.32148 | 0.48411 | 0.49983
0.31018 | 0.32147 | 0.48408 | 0.4998
0.31017 | 0.32146 | 0.48405 | 0.49978
0.31015 | 0.32145 | 0.48403 | 0.49976
0.31014 | 0.32144 | 0.484 | 0.49973
0.31013 | 0.32142 | 0.48398 | 0.49972
0.31012 | 0.32142 | 0.48395 | 0.49968
0.31011 | 0.3214 | 0.48391 | 0.49966
0.31009 | 0.32139 | 0.48389 | 0.49962
0.31009 | 0.32138 | 0.48385 | 0.49959
0.31008 | 0.32137 | 0.48379 | 0.49958
0.31007 | 0.32136 | 0.48376 | 0.49955
0.31006 | 0.32135 | 0.48373 | 0.49952
0.31004 | 0.32132 | 0.48371 | 0.4995
0.31003 | 0.32131 | 0.48368 | 0.49949
0.31002 | 0.32131 | 0.48367 | 0.49947
0.31001 | 0.3213 | 0.48364 | 0.49944
0.31 | 0.32129 | 0.48361 | 0.49942
0.30999 | 0.32128 | 0.48358 | 0.4994
0.30998 | 0.32127 | 0.48355 | 0.49936
0.30996 | 0.32126 | 0.48352 | 0.49935
0.30995 | 0.32124 | 0.48349 | 0.49932
0.30994 | 0.32123 | 0.48346 | 0.49931
0.30993 | 0.32122 | 0.48343 | 0.49927
0.30992 | 0.32121 | 0.4834 | 0.49925
0.30991 | 0.3212 | 0.48337 | 0.49922
0.3099 | 0.32118 | 0.48333 | 0.4992
0.30989 | 0.32118 | 0.48329 | 0.49918
0.30988 | 0.32117 | 0.48326 | 0.49916
0.30987 | 0.32115 | 0.48322 | 0.49914
0.30986 | 0.32114 | 0.48319 | 0.49911
0.30985 | 0.32113 | 0.48317 | 0.4991
0.30984 | 0.32112 | 0.48315 | 0.49907
0.30982 | 0.32111 | 0.48313 | 0.49904
0.30981 | 0.3211 | 0.48311 | 0.499
0.3098 | 0.32109 | 0.48309 | 0.49898
0.30979 | 0.32108 | 0.48305 | 0.49895
0.30978 | 0.32106 | 0.48303 | 0.49892
0.30977 | 0.32105 | 0.483 | 0.4989
0.30976 | 0.32104 | 0.48297 | 0.49887
0.30974 | 0.32103 | 0.48296 | 0.49884
0.30973 | 0.32102 | 0.48293 | 0.49882
0.30972 | 0.32101 | 0.48291 | 0.4988
0.30971 | 0.321 | 0.48289 | 0.49876
0.3097 | 0.32099 | 0.48287 | 0.49874
0.30969 | 0.32098 | 0.48284 | 0.49871
0.30968 | 0.32097 | 0.48281 | 0.49867
0.30966 | 0.32096 | 0.48278 | 0.49865
0.30965 | 0.32095 | 0.48276 | 0.49862
0.30963 | 0.32094 | 0.48273 | 0.4986
0.30962 | 0.32093 | 0.4827 | 0.49856
0.3096 | 0.32093 | 0.48268 | 0.49852
0.3096 | 0.32092 | 0.48265 | 0.4985
0.30959 | 0.32091 | 0.48262 | 0.49846
0.30958 | 0.32091 | 0.4826 | 0.49842
0.30957 | 0.32089 | 0.48258 | 0.4984
0.30956 | 0.32088 | 0.48255 | 0.49837
0.30955 | 0.32087 | 0.48252 | 0.49834
0.30953 | 0.32086 | 0.4825 | 0.49832
0.30952 | 0.32085 | 0.48247 | 0.4983
0.30951 | 0.32084 | 0.48245 | 0.49827
0.3095 | 0.32083 | 0.48242 | 0.49825
0.30949 | 0.32082 | 0.48239 | 0.49822
0.30948 | 0.32081 | 0.48237 | 0.49817
0.30947 | 0.32081 | 0.48234 | 0.49814
0.30945 | 0.3208 | 0.48231 | 0.4981
0.30944 | 0.32079 | 0.48227 | 0.49807
0.30943 | 0.32078 | 0.48225 | 0.49805
0.30943 | 0.32076 | 0.4822 | 0.49803
0.30942 | 0.32075 | 0.48217 | 0.498
0.3094 | 0.32075 | 0.48215 | 0.49797
0.30939 | 0.32073 | 0.4821 | 0.49794
0.30939 | 0.32072 | 0.48208 | 0.49791
0.30938 | 0.32072 | 0.48206 | 0.49789
0.30937 | 0.32071 | 0.48204 | 0.49787
0.30936 | 0.3207 | 0.48201 | 0.49783
0.30934 | 0.32069 | 0.48198 | 0.4978
0.30934 | 0.32068 | 0.48195 | 0.49779
0.30933 | 0.32067 | 0.48191 | 0.49777
0.30932 | 0.32066 | 0.48188 | 0.49773
0.30931 | 0.32065 | 0.48185 | 0.49771
0.30929 | 0.32064 | 0.4818 | 0.49768
0.30928 | 0.32063 | 0.48176 | 0.49766
0.30926 | 0.32062 | 0.48172 | 0.49764
0.30925 | 0.3206 | 0.4817 | 0.49762
0.30923 | 0.3206 | 0.48168 | 0.4976
0.30922 | 0.32059 | 0.48164 | 0.49759
0.30921 | 0.32058 | 0.48162 | 0.49755
0.3092 | 0.32056 | 0.48159 | 0.49751
0.30919 | 0.32055 | 0.48156 | 0.49749
0.30918 | 0.32054 | 0.48154 | 0.49746
0.30916 | 0.32053 | 0.48152 | 0.49745
0.30915 | 0.32051 | 0.48148 | 0.49742
0.30914 | 0.3205 | 0.48147 | 0.49738
0.30913 | 0.32049 | 0.48145 | 0.49736
0.30912 | 0.32048 | 0.48142 | 0.49734
0.30911 | 0.32047 | 0.48139 | 0.49733
0.30909 | 0.32046 | 0.48136 | 0.49731
0.30908 | 0.32045 | 0.48133 | 0.49728
0.30907 | 0.32043 | 0.4813 | 0.49727
0.30906 | 0.32041 | 0.48129 | 0.49724
0.30906 | 0.3204 | 0.48124 | 0.49722
0.30905 | 0.32039 | 0.48122 | 0.49719
0.30904 | 0.32038 | 0.48121 | 0.49717
0.30902 | 0.32037 | 0.48118 | 0.49714
0.30901 | 0.32036 | 0.48116 | 0.4971
0.309 | 0.32035 | 0.48111 | 0.49708
0.30899 | 0.32034 | 0.48109 | 0.49706
0.30898 | 0.32033 | 0.48108 | 0.49703
0.30898 | 0.32032 | 0.48105 | 0.49701
0.30897 | 0.32031 | 0.48102 | 0.49699
0.30896 | 0.3203 | 0.481 | 0.49697
0.30895 | 0.32028 | 0.48098 | 0.49694
0.30894 | 0.32027 | 0.48095 | 0.49692
0.30893 | 0.32026 | 0.48089 | 0.4969
0.30892 | 0.32025 | 0.48087 | 0.49688
0.30891 | 0.32024 | 0.48085 | 0.49685
0.3089 | 0.32022 | 0.48083 | 0.49682
0.30889 | 0.32021 | 0.4808 | 0.49678
0.30887 | 0.3202 | 0.48077 | 0.49676
0.30886 | 0.32019 | 0.48075 | 0.49673
0.30885 | 0.32018 | 0.48074 | 0.49672
0.30884 | 0.32017 | 0.48069 | 0.4967
0.30883 | 0.32016 | 0.48067 | 0.49667
0.30881 | 0.32014 | 0.48063 | 0.49665
0.3088 | 0.32014 | 0.48061 | 0.49662
0.30879 | 0.32013 | 0.48059 | 0.49659
0.30878 | 0.32012 | 0.48056 | 0.49657
0.30877 | 0.32011 | 0.48054 | 0.49655
0.30877 | 0.3201 | 0.48052 | 0.4965
0.30875 | 0.3201 | 0.48049 | 0.49648
0.30874 | 0.32009 | 0.48045 | 0.49645
0.30873 | 0.32008 | 0.48044 | 0.49642
0.30871 | 0.32006 | 0.48041 | 0.4964
0.3087 | 0.32005 | 0.48038 | 0.49638
0.30869 | 0.32004 | 0.48037 | 0.49636
0.30868 | 0.32003 | 0.48034 | 0.49633
0.30867 | 0.32003 | 0.48032 | 0.4963
0.30866 | 0.32002 | 0.48029 | 0.49628
0.30866 | 0.32001 | 0.48027 | 0.49626
0.30865 | 0.32 | 0.48025 | 0.49623
0.30864 | 0.31999 | 0.48022 | 0.49621
0.30863 | 0.31998 | 0.48018 | 0.4962
0.30862 | 0.31997 | 0.48015 | 0.49619
0.30861 | 0.31996 | 0.48013 | 0.49616
0.3086 | 0.31995 | 0.4801 | 0.49614
0.30859 | 0.31994 | 0.48008 | 0.49613
0.30858 | 0.31993 | 0.48004 | 0.4961
0.30858 | 0.31992 | 0.48002 | 0.49606
0.30856 | 0.31991 | 0.47998 | 0.49604
0.30855 | 0.3199 | 0.47995 | 0.49601
0.30854 | 0.31989 | 0.47992 | 0.49599
0.30853 | 0.31988 | 0.4799 | 0.49596
0.30851 | 0.31986 | 0.47988 | 0.49594
0.3085 | 0.31985 | 0.47986 | 0.49591
0.30849 | 0.31984 | 0.47983 | 0.49589
0.30848 | 0.31983 | 0.4798 | 0.49586
0.30847 | 0.31982 | 0.47977 | 0.49584
0.30846 | 0.31981 | 0.47974 | 0.49581
0.30845 | 0.3198 | 0.4797 | 0.49579
0.30844 | 0.31979 | 0.47968 | 0.49576
0.30843 | 0.31978 | 0.47964 | 0.49574
0.30842 | 0.31977 | 0.47962 | 0.49572
0.30841 | 0.31975 | 0.4796 | 0.4957
0.3084 | 0.31974 | 0.47957 | 0.49568
0.30839 | 0.31973 | 0.47954 | 0.49565
0.30838 | 0.31972 | 0.47952 | 0.49563
0.30837 | 0.31971 | 0.47949 | 0.49561
0.30835 | 0.3197 | 0.47946 | 0.4956
0.30834 | 0.31969 | 0.47943 | 0.49557
0.30833 | 0.31968 | 0.47941 | 0.49554
0.30832 | 0.31967 | 0.47937 | 0.49553
0.30831 | 0.31966 | 0.47936 | 0.49549
0.3083 | 0.31965 | 0.47932 | 0.49547
0.30829 | 0.31963 | 0.4793 | 0.49546
0.30827 | 0.31962 | 0.47928 | 0.49544
0.30827 | 0.31961 | 0.47925 | 0.49541
0.30825 | 0.3196 | 0.47921 | 0.49538
0.30824 | 0.31959 | 0.47918 | 0.49535
0.30823 | 0.31958 | 0.47914 | 0.49532
0.30822 | 0.31957 | 0.47912 | 0.49531
0.30821 | 0.31955 | 0.4791 | 0.49529
0.3082 | 0.31955 | 0.47906 | 0.49527
0.30818 | 0.31954 | 0.47902 | 0.49524
0.30818 | 0.31953 | 0.479 | 0.49521
0.30817 | 0.31952 | 0.47897 | 0.49519
0.30816 | 0.31951 | 0.47893 | 0.49517
0.30815 | 0.31949 | 0.4789 | 0.49515
0.30814 | 0.31948 | 0.47886 | 0.49513
0.30813 | 0.31947 | 0.47884 | 0.49512
0.30812 | 0.31946 | 0.47881 | 0.49508
0.30811 | 0.31945 | 0.47878 | 0.49506
0.3081 | 0.31944 | 0.47875 | 0.49503
0.30808 | 0.31942 | 0.47872 | 0.495
0.30807 | 0.31941 | 0.47868 | 0.49498
0.30806 | 0.31941 | 0.47865 | 0.49495
0.30805 | 0.3194 | 0.47861 | 0.49492
0.30803 | 0.31939 | 0.47859 | 0.49489
0.30802 | 0.31938 | 0.47856 | 0.49487
0.30801 | 0.31937 | 0.47854 | 0.49485
0.308 | 0.31936 | 0.4785 | 0.49483
0.30799 | 0.31935 | 0.47848 | 0.49481
0.30798 | 0.31934 | 0.47845 | 0.49479
0.30796 | 0.31933 | 0.47842 | 0.49475
0.30795 | 0.31932 | 0.4784 | 0.49474
0.30793 | 0.31932 | 0.47839 | 0.49472
0.30792 | 0.31931 | 0.47836 | 0.49469
0.30791 | 0.31929 | 0.47834 | 0.49467
0.30789 | 0.31928 | 0.47831 | 0.49464
0.30788 | 0.31928 | 0.47828 | 0.49459
0.30786 | 0.31927 | 0.47825 | 0.49458
0.30786 | 0.31926 | 0.47823 | 0.49456
0.30784 | 0.31925 | 0.4782 | 0.49454
0.30783 | 0.31923 | 0.47818 | 0.49451
0.30781 | 0.31922 | 0.47817 | 0.49449
0.30781 | 0.31921 | 0.47814 | 0.49447
0.30779 | 0.3192 | 0.47811 | 0.49444
0.30778 | 0.31919 | 0.47808 | 0.49441
0.30778 | 0.31919 | 0.47805 | 0.49439
0.30777 | 0.31918 | 0.47804 | 0.49437
0.30775 | 0.31916 | 0.47802 | 0.49435
0.30774 | 0.31916 | 0.47799 | 0.49433
0.30773 | 0.31915 | 0.47797 | 0.49432
0.30771 | 0.31914 | 0.47795 | 0.49429
0.30771 | 0.31913 | 0.47793 | 0.49427
0.3077 | 0.31912 | 0.4779 | 0.49424
0.30769 | 0.3191 | 0.47786 | 0.49421
0.30767 | 0.31909 | 0.47783 | 0.49418
0.30766 | 0.31908 | 0.47781 | 0.49414
0.30765 | 0.31907 | 0.47779 | 0.49412
0.30764 | 0.31906 | 0.47777 | 0.4941
0.30762 | 0.31904 | 0.47774 | 0.49406
0.30761 | 0.31904 | 0.47773 | 0.49403
0.30761 | 0.31902 | 0.47771 | 0.494
0.30759 | 0.31901 | 0.47768 | 0.49398
0.30757 | 0.319 | 0.47766 | 0.49396
0.30757 | 0.31899 | 0.47763 | 0.49393
0.30755 | 0.31898 | 0.47761 | 0.49391
0.30754 | 0.31897 | 0.47759 | 0.49388
0.30753 | 0.31895 | 0.47755 | 0.49384
0.30752 | 0.31894 | 0.47753 | 0.49381
0.3075 | 0.31893 | 0.4775 | 0.49378
0.30749 | 0.31892 | 0.47749 | 0.49375
0.30747 | 0.31891 | 0.47747 | 0.49372
0.30747 | 0.3189 | 0.47744 | 0.4937
0.30746 | 0.31889 | 0.47743 | 0.49368
0.30745 | 0.31888 | 0.4774 | 0.49366
0.30744 | 0.31887 | 0.47737 | 0.49363
0.30744 | 0.31886 | 0.47734 | 0.49361
0.30743 | 0.31885 | 0.47732 | 0.49359
0.30741 | 0.31884 | 0.47729 | 0.49357
0.3074 | 0.31883 | 0.47726 | 0.49354
0.30739 | 0.31883 | 0.47724 | 0.49352
0.30738 | 0.31882 | 0.47722 | 0.4935
0.30737 | 0.31881 | 0.47719 | 0.49348
0.30736 | 0.31879 | 0.47715 | 0.49347
0.30734 | 0.31879 | 0.47711 | 0.49344
0.30733 | 0.31877 | 0.47707 | 0.49341
0.30733 | 0.31876 | 0.47704 | 0.49337
0.30731 | 0.31875 | 0.47702 | 0.49334
0.30731 | 0.31875 | 0.477 | 0.49333
0.3073 | 0.31874 | 0.47697 | 0.49331
0.30729 | 0.31873 | 0.47695 | 0.49329
0.30727 | 0.31872 | 0.47693 | 0.49327
0.30726 | 0.31871 | 0.47691 | 0.49324
0.30725 | 0.3187 | 0.47691 | 0.49322
0.30723 | 0.31869 | 0.47687 | 0.4932
0.30722 | 0.31868 | 0.47683 | 0.49317
0.30721 | 0.31866 | 0.4768 | 0.49315
0.3072 | 0.31866 | 0.47678 | 0.49313
0.30719 | 0.31865 | 0.47675 | 0.49309
0.30718 | 0.31864 | 0.47673 | 0.49307
0.30717 | 0.31863 | 0.4767 | 0.49305
0.30715 | 0.31862 | 0.47666 | 0.49302
0.30714 | 0.31861 | 0.47664 | 0.493
0.30713 | 0.3186 | 0.47662 | 0.49298
0.30712 | 0.31859 | 0.47659 | 0.49295
0.30711 | 0.31858 | 0.47657 | 0.49293
0.3071 | 0.31857 | 0.47654 | 0.49291
0.30709 | 0.31856 | 0.47651 | 0.4929
0.30708 | 0.31855 | 0.47649 | 0.49286
0.30707 | 0.31854 | 0.47647 | 0.49284
0.30706 | 0.31853 | 0.47645 | 0.49283
0.30705 | 0.31851 | 0.47641 | 0.4928
0.30704 | 0.3185 | 0.47639 | 0.49278
0.30703 | 0.31849 | 0.47637 | 0.49275
0.30702 | 0.31847 | 0.47635 | 0.49272
0.30701 | 0.31847 | 0.47634 | 0.49271
0.307 | 0.31845 | 0.47631 | 0.49268
0.30699 | 0.31844 | 0.47628 | 0.49266
0.30698 | 0.31844 | 0.47625 | 0.49263
0.30697 | 0.31843 | 0.47623 | 0.49261
0.30695 | 0.31842 | 0.47621 | 0.49258
0.30694 | 0.31841 | 0.47618 | 0.49256
0.30693 | 0.31839 | 0.47615 | 0.49253
0.30692 | 0.31838 | 0.47612 | 0.4925
0.30691 | 0.31836 | 0.47609 | 0.49248
0.3069 | 0.31835 | 0.47607 | 0.49245
0.30689 | 0.31834 | 0.47605 | 0.49244
0.30688 | 0.31833 | 0.47601 | 0.49241
0.30686 | 0.31832 | 0.47597 | 0.49239
0.30685 | 0.31831 | 0.47593 | 0.49237
0.30684 | 0.3183 | 0.47592 | 0.49235
0.30683 | 0.31829 | 0.47589 | 0.49232
0.30682 | 0.31827 | 0.47587 | 0.49229
0.30681 | 0.31825 | 0.47585 | 0.49227
0.3068 | 0.31824 | 0.47583 | 0.49225
0.30679 | 0.31823 | 0.4758 | 0.49221
0.30678 | 0.31822 | 0.47578 | 0.49217
0.30678 | 0.31822 | 0.47575 | 0.49215
0.30677 | 0.31821 | 0.47572 | 0.49213
0.30675 | 0.3182 | 0.47569 | 0.4921
0.30674 | 0.31819 | 0.47567 | 0.49208
0.30673 | 0.31817 | 0.47564 | 0.49207
0.30671 | 0.31816 | 0.47562 | 0.49205
0.3067 | 0.31815 | 0.4756 | 0.49202
0.3067 | 0.31814 | 0.47557 | 0.49198
0.30669 | 0.31813 | 0.47554 | 0.49195
0.30668 | 0.31812 | 0.47551 | 0.49193
0.30667 | 0.3181 | 0.47548 | 0.49191
0.30667 | 0.31809 | 0.47546 | 0.49188
0.30665 | 0.31809 | 0.47543 | 0.49186
0.30663 | 0.31807 | 0.47539 | 0.49184
0.30662 | 0.31806 | 0.47536 | 0.4918
0.30661 | 0.31806 | 0.47533 | 0.49178
0.3066 | 0.31805 | 0.4753 | 0.49175
0.30659 | 0.31803 | 0.47528 | 0.49173
0.30658 | 0.31802 | 0.47525 | 0.49171
0.30657 | 0.31801 | 0.47522 | 0.49168
0.30656 | 0.31799 | 0.47519 | 0.49165
0.30655 | 0.31798 | 0.47516 | 0.49163
0.30653 | 0.31798 | 0.47513 | 0.49161
0.30652 | 0.31797 | 0.4751 | 0.49157
0.30651 | 0.31796 | 0.47508 | 0.49155
0.3065 | 0.31795 | 0.47505 | 0.49152
0.30648 | 0.31794 | 0.47501 | 0.4915
0.30647 | 0.31793 | 0.47498 | 0.49147
0.30646 | 0.31792 | 0.47495 | 0.49145
0.30645 | 0.31791 | 0.47491 | 0.49143
0.30644 | 0.31789 | 0.47488 | 0.49139
0.30643 | 0.31788 | 0.47486 | 0.49137
0.30642 | 0.31787 | 0.47482 | 0.49133
0.3064 | 0.31786 | 0.47479 | 0.49131
0.30638 | 0.31785 | 0.47476 | 0.49129
0.30637 | 0.31785 | 0.47473 | 0.49126
0.30635 | 0.31783 | 0.47471 | 0.49124
0.30634 | 0.31782 | 0.47467 | 0.49121
0.30632 | 0.31781 | 0.47465 | 0.49119
0.30631 | 0.31781 | 0.47462 | 0.49117
0.3063 | 0.3178 | 0.47459 | 0.49113
0.3063 | 0.31779 | 0.47455 | 0.49111
0.30627 | 0.31777 | 0.47451 | 0.49109
0.30627 | 0.31776 | 0.4745 | 0.49106
0.30626 | 0.31776 | 0.47447 | 0.49105
0.30624 | 0.31774 | 0.47445 | 0.49102
0.30623 | 0.31773 | 0.47443 | 0.49099
0.30622 | 0.31771 | 0.47439 | 0.49096
0.30622 | 0.3177 | 0.47437 | 0.49094
0.30621 | 0.31769 | 0.47436 | 0.4909
0.3062 | 0.31767 | 0.47433 | 0.49088
0.30618 | 0.31766 | 0.47431 | 0.49086
0.30617 | 0.31765 | 0.47428 | 0.49083
0.30616 | 0.31764 | 0.47426 | 0.4908
0.30615 | 0.31763 | 0.47424 | 0.49079
0.30614 | 0.31761 | 0.47422 | 0.49077
0.30613 | 0.3176 | 0.4742 | 0.49075
0.30612 | 0.31759 | 0.47416 | 0.49073
0.30612 | 0.31758 | 0.47412 | 0.49071
0.30611 | 0.31757 | 0.47409 | 0.49069
0.3061 | 0.31756 | 0.47407 | 0.49067
0.30608 | 0.31755 | 0.47403 | 0.49064
0.30607 | 0.31754 | 0.47401 | 0.49062
0.30606 | 0.31752 | 0.47397 | 0.49059
0.30604 | 0.31751 | 0.47393 | 0.49057
0.30604 | 0.3175 | 0.4739 | 0.49054
0.30603 | 0.31749 | 0.47388 | 0.49052
0.30602 | 0.31748 | 0.47385 | 0.49048
0.30601 | 0.31746 | 0.47382 | 0.49046
0.30601 | 0.31745 | 0.47378 | 0.49043
0.30599 | 0.31744 | 0.47376 | 0.49041
0.30598 | 0.31743 | 0.47374 | 0.49039
0.30597 | 0.31742 | 0.47372 | 0.49037
0.30597 | 0.3174 | 0.47369 | 0.49034
0.30595 | 0.3174 | 0.47367 | 0.49032
0.30594 | 0.31739 | 0.47364 | 0.49031
0.30593 | 0.31738 | 0.4736 | 0.49029
0.30591 | 0.31737 | 0.47358 | 0.49026
0.30591 | 0.31736 | 0.47354 | 0.49023
0.3059 | 0.31735 | 0.47351 | 0.4902
0.30589 | 0.31734 | 0.47349 | 0.49018
0.30588 | 0.31733 | 0.47347 | 0.49017
0.30586 | 0.31732 | 0.47345 | 0.49015
0.30585 | 0.3173 | 0.47342 | 0.49013
0.30584 | 0.3173 | 0.47339 | 0.49011
0.30582 | 0.31729 | 0.47336 | 0.49006
0.30581 | 0.31727 | 0.47335 | 0.49005
0.30579 | 0.31725 | 0.47332 | 0.49001
0.30578 | 0.31725 | 0.4733 | 0.48999
0.30577 | 0.31724 | 0.47329 | 0.48995
0.30576 | 0.31722 | 0.47328 | 0.48991
0.30575 | 0.31722 | 0.47325 | 0.48988
0.30574 | 0.31721 | 0.47322 | 0.48985
0.30573 | 0.3172 | 0.47317 | 0.48983
0.30572 | 0.31719 | 0.47315 | 0.4898
0.30571 | 0.31718 | 0.47312 | 0.48977
0.3057 | 0.31717 | 0.4731 | 0.48975
0.30569 | 0.31717 | 0.47308 | 0.48972
0.30568 | 0.31715 | 0.47305 | 0.4897
0.30568 | 0.31715 | 0.47302 | 0.48968
0.30567 | 0.31713 | 0.473 | 0.48966
0.30565 | 0.31712 | 0.47295 | 0.48964
0.30564 | 0.31712 | 0.47291 | 0.48962
0.30563 | 0.31711 | 0.47288 | 0.4896
0.30562 | 0.31709 | 0.47285 | 0.48958
0.3056 | 0.31708 | 0.47282 | 0.48955
0.30559 | 0.31707 | 0.4728 | 0.48953
0.30558 | 0.31706 | 0.47278 | 0.48951
0.30558 | 0.31705 | 0.47276 | 0.48948
0.30557 | 0.31705 | 0.47273 | 0.48944
0.30556 | 0.31704 | 0.47269 | 0.48942
0.30555 | 0.31702 | 0.47266 | 0.48938
0.30554 | 0.31701 | 0.47264 | 0.48936
0.30553 | 0.317 | 0.47262 | 0.48934
0.30552 | 0.31699 | 0.4726 | 0.48932
0.30551 | 0.31698 | 0.47257 | 0.48929
0.3055 | 0.31697 | 0.47256 | 0.48927
0.30549 | 0.31696 | 0.47252 | 0.48925
0.30548 | 0.31695 | 0.47249 | 0.48923
0.30547 | 0.31693 | 0.47246 | 0.48921
0.30546 | 0.31692 | 0.47243 | 0.48919
0.30545 | 0.31692 | 0.4724 | 0.48916
0.30544 | 0.3169 | 0.47236 | 0.48914
0.30543 | 0.31689 | 0.47234 | 0.48911
0.30542 | 0.31688 | 0.47232 | 0.48907
0.30541 | 0.31688 | 0.47229 | 0.48905
0.30541 | 0.31686 | 0.47226 | 0.48902
0.30539 | 0.31685 | 0.47224 | 0.48898
0.30539 | 0.31685 | 0.47221 | 0.48896
0.30538 | 0.31683 | 0.4722 | 0.48894
0.30537 | 0.31682 | 0.47217 | 0.48892
0.30536 | 0.31681 | 0.47214 | 0.48888
0.30534 | 0.31681 | 0.4721 | 0.48885
0.30533 | 0.3168 | 0.47208 | 0.48884
0.30532 | 0.31679 | 0.47206 | 0.48881
0.30531 | 0.31677 | 0.47202 | 0.48879
0.3053 | 0.31676 | 0.47199 | 0.48877
0.30529 | 0.31675 | 0.47196 | 0.48875
0.30527 | 0.31674 | 0.47195 | 0.48873
0.30526 | 0.31674 | 0.47192 | 0.4887
0.30525 | 0.31672 | 0.47189 | 0.48867
0.30523 | 0.31671 | 0.47187 | 0.48865
0.30522 | 0.31671 | 0.47185 | 0.48862
0.30521 | 0.3167 | 0.47182 | 0.48859
0.3052 | 0.31668 | 0.4718 | 0.48855
0.30518 | 0.31668 | 0.47178 | 0.48852
0.30516 | 0.31667 | 0.47176 | 0.48851
0.30515 | 0.31666 | 0.47173 | 0.48848
0.30514 | 0.31664 | 0.47171 | 0.48845
0.30513 | 0.31663 | 0.47169 | 0.48844
0.30511 | 0.31662 | 0.47166 | 0.48841
0.30511 | 0.31661 | 0.47164 | 0.48838
0.3051 | 0.3166 | 0.47161 | 0.48835
0.30509 | 0.31659 | 0.47158 | 0.48831
0.30508 | 0.31658 | 0.47156 | 0.48827
0.30507 | 0.31657 | 0.47154 | 0.48824
0.30507 | 0.31656 | 0.4715 | 0.48821
0.30505 | 0.31655 | 0.47148 | 0.48819
0.30505 | 0.31654 | 0.47145 | 0.48816
0.30504 | 0.31653 | 0.47143 | 0.48813
0.30503 | 0.31652 | 0.47141 | 0.4881
0.30502 | 0.31651 | 0.47137 | 0.48807
0.30501 | 0.31649 | 0.47133 | 0.48805
0.305 | 0.31647 | 0.47131 | 0.48803
0.30499 | 0.31646 | 0.47127 | 0.48801
0.30498 | 0.31645 | 0.47123 | 0.488
0.30497 | 0.31644 | 0.47118 | 0.48798
0.30496 | 0.31643 | 0.47116 | 0.48796
0.30495 | 0.31642 | 0.47114 | 0.48793
0.30494 | 0.31641 | 0.47111 | 0.48791
0.30492 | 0.3164 | 0.47107 | 0.48789
0.30491 | 0.31639 | 0.47104 | 0.48787
0.30489 | 0.31639 | 0.47101 | 0.48784
0.30488 | 0.31638 | 0.47096 | 0.48782
0.30487 | 0.31637 | 0.47095 | 0.48779
0.30487 | 0.31635 | 0.47092 | 0.48774
0.30486 | 0.31634 | 0.4709 | 0.48772
0.30485 | 0.31634 | 0.47087 | 0.48768
0.30483 | 0.31632 | 0.47085 | 0.48765
0.30482 | 0.3163 | 0.47082 | 0.48762
0.30481 | 0.31629 | 0.4708 | 0.4876
0.30479 | 0.31629 | 0.47078 | 0.48757
0.30478 | 0.31627 | 0.47074 | 0.48755
0.30478 | 0.31627 | 0.47072 | 0.48752
0.30476 | 0.31625 | 0.47069 | 0.48748
0.30475 | 0.31625 | 0.47066 | 0.48746
0.30474 | 0.31623 | 0.47064 | 0.48745
0.30473 | 0.31622 | 0.47062 | 0.48743
0.30472 | 0.31621 | 0.47059 | 0.48739
0.30471 | 0.3162 | 0.47057 | 0.48736
0.30471 | 0.31619 | 0.47054 | 0.48735
0.3047 | 0.31618 | 0.47051 | 0.4873
0.30468 | 0.31617 | 0.47048 | 0.48728
0.30467 | 0.31616 | 0.47045 | 0.48725
0.30466 | 0.31614 | 0.47044 | 0.48723
0.30465 | 0.31613 | 0.47041 | 0.4872
0.30463 | 0.31612 | 0.47038 | 0.48717
0.30462 | 0.31611 | 0.47035 | 0.48714
0.30462 | 0.31609 | 0.47032 | 0.48713
0.30461 | 0.31608 | 0.4703 | 0.4871
0.30459 | 0.31607 | 0.47027 | 0.48708
0.30458 | 0.31606 | 0.47026 | 0.48705
0.30456 | 0.31606 | 0.47023 | 0.48702
0.30455 | 0.31605 | 0.47021 | 0.48698
0.30454 | 0.31604 | 0.47018 | 0.48697
0.30453 | 0.31603 | 0.47013 | 0.48694
0.30452 | 0.31602 | 0.4701 | 0.48693
0.30451 | 0.31601 | 0.47009 | 0.48691
0.3045 | 0.316 | 0.47007 | 0.48687
0.30448 | 0.31599 | 0.47004 | 0.48684
0.30447 | 0.31598 | 0.47001 | 0.48681
0.30446 | 0.31597 | 0.46999 | 0.48679
0.30445 | 0.31596 | 0.46996 | 0.48676
0.30444 | 0.31595 | 0.46993 | 0.48673
0.30443 | 0.31594 | 0.46989 | 0.48671
0.30442 | 0.31593 | 0.46986 | 0.48669
0.30441 | 0.31592 | 0.46984 | 0.48667
0.3044 | 0.31592 | 0.4698 | 0.48664
0.30439 | 0.31591 | 0.46978 | 0.48662
0.30437 | 0.3159 | 0.46975 | 0.48659
0.30436 | 0.31589 | 0.46972 | 0.48657
0.30436 | 0.31587 | 0.4697 | 0.48655
0.30434 | 0.31586 | 0.46967 | 0.48652
0.30433 | 0.31584 | 0.46964 | 0.48649
0.30431 | 0.31583 | 0.46961 | 0.48646
0.30431 | 0.31582 | 0.46957 | 0.48645
0.3043 | 0.31581 | 0.46954 | 0.48642
0.30429 | 0.31579 | 0.46952 | 0.4864
0.30429 | 0.31578 | 0.46949 | 0.48637
0.30428 | 0.31577 | 0.46946 | 0.48635
0.30427 | 0.31576 | 0.46942 | 0.48633
0.30426 | 0.31575 | 0.46938 | 0.48631
0.30425 | 0.31574 | 0.46935 | 0.48628
0.30425 | 0.31573 | 0.46933 | 0.48626
0.30424 | 0.31572 | 0.46931 | 0.48624
0.30422 | 0.31571 | 0.46927 | 0.48622
0.30421 | 0.3157 | 0.46923 | 0.4862
0.3042 | 0.31569 | 0.46921 | 0.48616
0.30419 | 0.31568 | 0.4692 | 0.48613
0.30418 | 0.31566 | 0.46917 | 0.48611
0.30417 | 0.31564 | 0.46914 | 0.4861
0.30416 | 0.31564 | 0.4691 | 0.48605
0.30414 | 0.31563 | 0.46909 | 0.48603
0.30413 | 0.31562 | 0.46905 | 0.48598
0.30413 | 0.31561 | 0.46902 | 0.48595
0.30412 | 0.3156 | 0.469 | 0.48592
0.30411 | 0.31559 | 0.46898 | 0.48589
0.30409 | 0.31558 | 0.46896 | 0.48586
0.30408 | 0.31557 | 0.46894 | 0.48583
0.30407 | 0.31556 | 0.4689 | 0.4858
0.30406 | 0.31555 | 0.46884 | 0.48578
0.30406 | 0.31554 | 0.46883 | 0.48575
0.30405 | 0.31553 | 0.46878 | 0.48574
0.30404 | 0.31552 | 0.46876 | 0.48571
0.30403 | 0.31551 | 0.46875 | 0.48569
0.30402 | 0.31549 | 0.46873 | 0.48567
0.30401 | 0.31548 | 0.46871 | 0.48565
0.304 | 0.31547 | 0.46869 | 0.48563
0.30399 | 0.31546 | 0.46866 | 0.48561
0.30398 | 0.31546 | 0.46863 | 0.48558
0.30397 | 0.31544 | 0.46861 | 0.48556
0.30395 | 0.31543 | 0.46859 | 0.48554
0.30394 | 0.31542 | 0.46856 | 0.48551
0.30393 | 0.3154 | 0.46854 | 0.48548
0.30392 | 0.31539 | 0.46852 | 0.48546
0.30391 | 0.31538 | 0.4685 | 0.48543
0.3039 | 0.31537 | 0.46847 | 0.4854
0.30388 | 0.31536 | 0.46844 | 0.48537
0.30388 | 0.31536 | 0.46841 | 0.48535
0.30386 | 0.31535 | 0.46839 | 0.48533
0.30385 | 0.31534 | 0.46837 | 0.4853
0.30384 | 0.31533 | 0.46834 | 0.48528
0.30383 | 0.31532 | 0.46832 | 0.48525
0.30383 | 0.31531 | 0.4683 | 0.48523
0.30382 | 0.3153 | 0.46828 | 0.48521
0.30381 | 0.31529 | 0.46824 | 0.48518
0.3038 | 0.31528 | 0.46822 | 0.48515
0.3038 | 0.31528 | 0.4682 | 0.48513
0.30378 | 0.31527 | 0.46818 | 0.48512
0.30377 | 0.31526 | 0.46815 | 0.48509
0.30376 | 0.31524 | 0.46812 | 0.48506
0.30375 | 0.31523 | 0.46809 | 0.48504
0.30374 | 0.31522 | 0.46807 | 0.48502
0.30372 | 0.31521 | 0.46804 | 0.485
0.30371 | 0.3152 | 0.46801 | 0.48499
0.30369 | 0.31519 | 0.46799 | 0.48497
0.30368 | 0.31518 | 0.46797 | 0.48495
0.30367 | 0.31517 | 0.46794 | 0.48491
0.30366 | 0.31516 | 0.46791 | 0.48489
0.30365 | 0.31515 | 0.46788 | 0.48486
0.30363 | 0.31515 | 0.46786 | 0.48484
0.30362 | 0.31514 | 0.46783 | 0.48481
0.30361 | 0.31512 | 0.46781 | 0.48479
0.3036 | 0.31511 | 0.46777 | 0.48477
0.30358 | 0.3151 | 0.46775 | 0.48475
0.30357 | 0.31508 | 0.46772 | 0.48472
0.30356 | 0.31507 | 0.4677 | 0.48469
0.30355 | 0.31506 | 0.46768 | 0.48468
0.30354 | 0.31505 | 0.46765 | 0.48466
0.30353 | 0.31505 | 0.46762 | 0.48463
0.30352 | 0.31503 | 0.4676 | 0.48461
0.30351 | 0.31502 | 0.46757 | 0.48458
0.3035 | 0.31501 | 0.46754 | 0.48455
0.3035 | 0.31501 | 0.46751 | 0.48453
0.30349 | 0.31501 | 0.46749 | 0.48448
0.30347 | 0.315 | 0.46746 | 0.48446
0.30346 | 0.31499 | 0.46744 | 0.48444
0.30345 | 0.31498 | 0.46742 | 0.48443
0.30344 | 0.31497 | 0.46739 | 0.48441
0.30343 | 0.31496 | 0.46737 | 0.48439
0.30342 | 0.31494 | 0.46734 | 0.48437
0.30341 | 0.31493 | 0.4673 | 0.48435
0.3034 | 0.31491 | 0.46728 | 0.48433
0.30338 | 0.3149 | 0.46726 | 0.4843
0.30338 | 0.31489 | 0.46723 | 0.48429
0.30337 | 0.31487 | 0.46721 | 0.48427
0.30336 | 0.31486 | 0.46718 | 0.48425
0.30335 | 0.31485 | 0.46714 | 0.48423
0.30334 | 0.31484 | 0.46711 | 0.4842
0.30332 | 0.31482 | 0.46707 | 0.48418
0.30331 | 0.31482 | 0.46706 | 0.48417
0.30331 | 0.3148 | 0.46704 | 0.48414
0.3033 | 0.31479 | 0.46702 | 0.4841
0.30328 | 0.31478 | 0.46699 | 0.48407
0.30327 | 0.31477 | 0.46698 | 0.48403
0.30326 | 0.31476 | 0.46695 | 0.48402
0.30325 | 0.31475 | 0.46692 | 0.48399
0.30324 | 0.31474 | 0.4669 | 0.48397
0.30323 | 0.31473 | 0.46687 | 0.48394
0.30322 | 0.31471 | 0.46683 | 0.48392
0.30321 | 0.3147 | 0.46681 | 0.4839
0.30319 | 0.31469 | 0.46677 | 0.48387
0.30317 | 0.31467 | 0.46676 | 0.48385
0.30316 | 0.31466 | 0.46674 | 0.48382
0.30316 | 0.31465 | 0.46671 | 0.4838
0.30315 | 0.31464 | 0.46669 | 0.48377
0.30314 | 0.31463 | 0.46666 | 0.48375
0.30313 | 0.31462 | 0.46663 | 0.48373
0.30312 | 0.31461 | 0.4666 | 0.48369
0.3031 | 0.3146 | 0.46655 | 0.48366
0.3031 | 0.31459 | 0.46653 | 0.48363
0.30308 | 0.31458 | 0.46649 | 0.48361
0.30306 | 0.31457 | 0.46646 | 0.48358
0.30305 | 0.31456 | 0.46644 | 0.48356
0.30303 | 0.31455 | 0.46642 | 0.48355
0.30302 | 0.31454 | 0.46639 | 0.48352
0.303 | 0.31453 | 0.46636 | 0.4835
0.30299 | 0.31453 | 0.46633 | 0.48346
0.30297 | 0.31452 | 0.4663 | 0.48345
0.30295 | 0.31451 | 0.46627 | 0.48342
0.30294 | 0.3145 | 0.46624 | 0.4834
0.30293 | 0.31449 | 0.4662 | 0.48337
0.30292 | 0.31448 | 0.46617 | 0.48335
0.3029 | 0.31446 | 0.46615 | 0.48332
0.3029 | 0.31445 | 0.46612 | 0.4833
0.30289 | 0.31444 | 0.4661 | 0.48326
0.30288 | 0.31443 | 0.46607 | 0.48323
0.30287 | 0.31441 | 0.46605 | 0.48321
0.30286 | 0.3144 | 0.46602 | 0.48318
0.30285 | 0.31439 | 0.46599 | 0.48316
0.30284 | 0.31438 | 0.46598 | 0.48315
0.30283 | 0.31437 | 0.46595 | 0.48312
0.30282 | 0.31436 | 0.46592 | 0.4831
0.3028 | 0.31435 | 0.4659 | 0.48307
0.30279 | 0.31434 | 0.46588 | 0.48302
0.30278 | 0.31433 | 0.46582 | 0.48299
0.30277 | 0.31432 | 0.46578 | 0.48298
0.30275 | 0.31431 | 0.46576 | 0.48296
0.30274 | 0.3143 | 0.46572 | 0.48293
0.30273 | 0.31429 | 0.46569 | 0.4829
0.30272 | 0.31428 | 0.46566 | 0.48288
0.30271 | 0.31427 | 0.46563 | 0.48285
0.3027 | 0.31426 | 0.4656 | 0.48282
0.30269 | 0.31425 | 0.46556 | 0.4828
0.30267 | 0.31425 | 0.46552 | 0.48278
0.30266 | 0.31424 | 0.46548 | 0.48275
0.30265 | 0.31424 | 0.46546 | 0.48272
0.30264 | 0.31422 | 0.46543 | 0.4827
0.30263 | 0.31422 | 0.46542 | 0.48268
0.30261 | 0.3142 | 0.46539 | 0.48266
0.3026 | 0.31419 | 0.46535 | 0.48264
0.30259 | 0.31418 | 0.46532 | 0.48263
0.30258 | 0.31416 | 0.4653 | 0.48261
0.30257 | 0.31415 | 0.46529 | 0.4826
0.30256 | 0.31414 | 0.46526 | 0.48257
0.30255 | 0.31414 | 0.46524 | 0.48256
0.30253 | 0.31412 | 0.46523 | 0.48252
0.30252 | 0.31411 | 0.4652 | 0.4825
0.30251 | 0.31411 | 0.46517 | 0.48247
0.3025 | 0.3141 | 0.46514 | 0.48244
0.3025 | 0.31409 | 0.46511 | 0.48242
0.30249 | 0.31408 | 0.46508 | 0.48239
0.30248 | 0.31407 | 0.46507 | 0.48236
0.30246 | 0.31406 | 0.46504 | 0.48234
0.30245 | 0.31405 | 0.46502 | 0.48232
0.30245 | 0.31404 | 0.46498 | 0.48229
0.30244 | 0.31404 | 0.46496 | 0.48227
0.30243 | 0.31402 | 0.46495 | 0.48225
0.30242 | 0.31401 | 0.46492 | 0.48223
0.30241 | 0.314 | 0.46489 | 0.48221
0.3024 | 0.31398 | 0.46486 | 0.48219
0.30239 | 0.31398 | 0.46484 | 0.48217
0.30237 | 0.31396 | 0.46482 | 0.48214
0.30236 | 0.31395 | 0.46479 | 0.48211
0.30235 | 0.31394 | 0.46476 | 0.48209
0.30234 | 0.31393 | 0.46473 | 0.48206
0.30233 | 0.31392 | 0.46472 | 0.48202
0.30231 | 0.31391 | 0.4647 | 0.48199
0.3023 | 0.31391 | 0.46467 | 0.48197
0.30229 | 0.3139 | 0.46464 | 0.48194
0.30228 | 0.31389 | 0.46461 | 0.48192
0.30227 | 0.31388 | 0.46459 | 0.4819
0.30226 | 0.31387 | 0.46455 | 0.48187
0.30225 | 0.31386 | 0.46454 | 0.48184
0.30224 | 0.31385 | 0.46452 | 0.48181
0.30223 | 0.31384 | 0.4645 | 0.4818
0.30222 | 0.31384 | 0.46447 | 0.48175
0.30221 | 0.31383 | 0.46445 | 0.48173
0.3022 | 0.31381 | 0.46442 | 0.4817
0.30219 | 0.31381 | 0.46438 | 0.48166
0.30219 | 0.3138 | 0.46436 | 0.48164
0.30218 | 0.31378 | 0.46434 | 0.48162
0.30217 | 0.31376 | 0.46432 | 0.48158
0.30216 | 0.31376 | 0.46429 | 0.48156
0.30215 | 0.31375 | 0.46428 | 0.48152
0.30214 | 0.31374 | 0.46425 | 0.48149
0.30213 | 0.31373 | 0.46422 | 0.48145
0.30211 | 0.31372 | 0.46419 | 0.48143
0.30211 | 0.31371 | 0.46417 | 0.48141
0.30209 | 0.3137 | 0.46415 | 0.48139
0.30208 | 0.31369 | 0.46413 | 0.48137
0.30207 | 0.31368 | 0.46411 | 0.48135
0.30206 | 0.31367 | 0.46409 | 0.48133
0.30205 | 0.31366 | 0.46408 | 0.48132
0.30204 | 0.31365 | 0.46405 | 0.48129
0.30203 | 0.31364 | 0.46402 | 0.48128
0.30202 | 0.31363 | 0.46401 | 0.48126
0.30201 | 0.31362 | 0.46399 | 0.48125
0.30199 | 0.31361 | 0.46398 | 0.48122
0.30198 | 0.3136 | 0.46395 | 0.4812
0.30197 | 0.31359 | 0.46393 | 0.48118
0.30196 | 0.31358 | 0.4639 | 0.48117
0.30195 | 0.31358 | 0.46389 | 0.48115
0.30194 | 0.31357 | 0.46387 | 0.48112
0.30193 | 0.31356 | 0.46386 | 0.48109
0.30192 | 0.31354 | 0.46383 | 0.48108
0.30191 | 0.31354 | 0.46382 | 0.48106
0.30191 | 0.31352 | 0.4638 | 0.48104
0.30189 | 0.31351 | 0.46378 | 0.48102
0.30188 | 0.3135 | 0.46376 | 0.481
0.30187 | 0.31349 | 0.46375 | 0.48099
0.30186 | 0.31348 | 0.46374 | 0.48097
0.30184 | 0.31347 | 0.46371 | 0.48095
0.30184 | 0.31345 | 0.4637 | 0.48093
0.30183 | 0.31344 | 0.46368 | 0.48091
0.30182 | 0.31343 | 0.46366 | 0.48086
0.30181 | 0.31343 | 0.46365 | 0.48084
0.30179 | 0.31341 | 0.46364 | 0.48082
0.30179 | 0.31341 | 0.46362 | 0.48079
0.30177 | 0.3134 | 0.46358 | 0.48078
0.30176 | 0.31338 | 0.46358 | 0.48075
0.30176 | 0.31338 | 0.46355 | 0.48072
0.30175 | 0.31336 | 0.46353 | 0.48071
0.30174 | 0.31336 | 0.46352 | 0.48069
0.30173 | 0.31335 | 0.46351 | 0.48067
0.30172 | 0.31333 | 0.46348 | 0.48065
0.30171 | 0.31332 | 0.46346 | 0.48063
0.30171 | 0.31331 | 0.46342 | 0.4806
0.30169 | 0.3133 | 0.46341 | 0.48056
0.30168 | 0.31329 | 0.4634 | 0.48054
0.30167 | 0.31328 | 0.46337 | 0.48052
0.30166 | 0.31327 | 0.46336 | 0.4805
0.30165 | 0.31326 | 0.46333 | 0.48048
0.30164 | 0.31325 | 0.46331 | 0.48043
0.30163 | 0.31324 | 0.4633 | 0.4804
0.30162 | 0.31323 | 0.46326 | 0.48038
0.3016 | 0.31322 | 0.46325 | 0.48036
0.3016 | 0.31321 | 0.46321 | 0.48034
0.30159 | 0.3132 | 0.46318 | 0.48032
0.30158 | 0.31319 | 0.46316 | 0.48029
0.30157 | 0.31318 | 0.46316 | 0.48027
0.30156 | 0.31318 | 0.46314 | 0.48026
0.30155 | 0.31317 | 0.46313 | 0.48024
0.30153 | 0.31315 | 0.46311 | 0.48022
0.30152 | 0.31314 | 0.46309 | 0.4802
0.30152 | 0.31313 | 0.46306 | 0.48017
0.30151 | 0.31312 | 0.46305 | 0.48013
0.3015 | 0.31311 | 0.46303 | 0.4801
0.3015 | 0.3131 | 0.46303 | 0.48009
0.30149 | 0.3131 | 0.46301 | 0.48005
0.30148 | 0.31308 | 0.463 | 0.48003
0.30147 | 0.31307 | 0.46298 | 0.48002
0.30146 | 0.31306 | 0.46297 | 0.47999
0.30145 | 0.31305 | 0.46296 | 0.47995
0.30143 | 0.31304 | 0.46294 | 0.47994
0.30143 | 0.31302 | 0.46292 | 0.47991
0.30142 | 0.31301 | 0.46291 | 0.47988
0.30141 | 0.31299 | 0.46289 | 0.47985
0.3014 | 0.31298 | 0.46287 | 0.47982
0.30139 | 0.31297 | 0.46285 | 0.47979
0.30138 | 0.31296 | 0.46283 | 0.47978
0.30137 | 0.31296 | 0.4628 | 0.47975
0.30135 | 0.31295 | 0.46278 | 0.47973
0.30134 | 0.31294 | 0.46277 | 0.47969
0.30133 | 0.31293 | 0.46274 | 0.47965
0.30133 | 0.31292 | 0.46271 | 0.47963
0.30131 | 0.31292 | 0.46269 | 0.47961
0.3013 | 0.3129 | 0.46269 | 0.47958
0.30129 | 0.31289 | 0.46267 | 0.47955
0.30128 | 0.31288 | 0.46266 | 0.47953
0.30127 | 0.31287 | 0.46264 | 0.47951
0.30125 | 0.31285 | 0.46263 | 0.47948
0.30124 | 0.31284 | 0.46261 | 0.47945
0.30122 | 0.31284 | 0.46259 | 0.47942
0.30121 | 0.31283 | 0.46257 | 0.47938
0.30119 | 0.31281 | 0.46256 | 0.47935
0.30118 | 0.3128 | 0.46254 | 0.47933
0.30117 | 0.31279 | 0.46252 | 0.4793
0.30116 | 0.31278 | 0.46249 | 0.47928
0.30115 | 0.31277 | 0.46248 | 0.47926
0.30114 | 0.31276 | 0.46245 | 0.47924
0.30113 | 0.31275 | 0.46243 | 0.47922
0.30112 | 0.31274 | 0.46241 | 0.47919
0.30111 | 0.31273 | 0.4624 | 0.47915
0.3011 | 0.31271 | 0.46238 | 0.47914
0.30109 | 0.31271 | 0.46237 | 0.47912
0.30108 | 0.3127 | 0.46235 | 0.4791
0.30107 | 0.31269 | 0.46232 | 0.47906
0.30106 | 0.31269 | 0.46231 | 0.47903
0.30105 | 0.31268 | 0.46229 | 0.479
0.30104 | 0.31266 | 0.46227 | 0.47898
0.30104 | 0.31265 | 0.46224 | 0.47896
0.30103 | 0.31265 | 0.46222 | 0.47893
0.30102 | 0.31263 | 0.4622 | 0.47891
0.30101 | 0.31262 | 0.46219 | 0.47887
0.30099 | 0.31261 | 0.46217 | 0.47886
0.30098 | 0.3126 | 0.46216 | 0.47883
0.30098 | 0.31259 | 0.46215 | 0.47881
0.30096 | 0.31259 | 0.46213 | 0.47879
0.30096 | 0.31257 | 0.46211 | 0.47876
0.30095 | 0.31256 | 0.46209 | 0.47874
0.30094 | 0.31255 | 0.46207 | 0.47873
0.30093 | 0.31253 | 0.46206 | 0.47871
0.30092 | 0.31252 | 0.46204 | 0.47869
0.30092 | 0.31251 | 0.46202 | 0.47867
0.30091 | 0.3125 | 0.462 | 0.47865
0.3009 | 0.31249 | 0.46198 | 0.47864
0.30089 | 0.31248 | 0.46196 | 0.47863
0.30088 | 0.31247 | 0.46195 | 0.47861
0.30087 | 0.31246 | 0.46192 | 0.47859
0.30086 | 0.31245 | 0.4619 | 0.47855
0.30084 | 0.31245 | 0.46187 | 0.47853
0.30083 | 0.31244 | 0.46186 | 0.47851
0.30081 | 0.31243 | 0.46185 | 0.47849
0.30081 | 0.31242 | 0.46182 | 0.47846
0.3008 | 0.31241 | 0.4618 | 0.47844
0.30079 | 0.3124 | 0.46177 | 0.47841
0.30078 | 0.31239 | 0.46176 | 0.47839
0.30077 | 0.31238 | 0.46174 | 0.47838
0.30076 | 0.31237 | 0.46173 | 0.47836
0.30075 | 0.31236 | 0.46171 | 0.47835
0.30074 | 0.31235 | 0.46169 | 0.47832
0.30074 | 0.31234 | 0.46168 | 0.4783
0.30073 | 0.31233 | 0.46165 | 0.47827
0.30072 | 0.31232 | 0.46163 | 0.47825
0.30071 | 0.31231 | 0.46161 | 0.47822
0.3007 | 0.31229 | 0.46159 | 0.4782
0.3007 | 0.31229 | 0.46158 | 0.47816
0.30069 | 0.31227 | 0.46157 | 0.47814
0.30068 | 0.31226 | 0.46155 | 0.4781
0.30067 | 0.31225 | 0.46153 | 0.47807
0.30066 | 0.31224 | 0.4615 | 0.47804
0.30065 | 0.31223 | 0.46148 | 0.47803
0.30063 | 0.31222 | 0.46148 | 0.47801
0.30062 | 0.31221 | 0.46145 | 0.47798
0.30061 | 0.31221 | 0.46143 | 0.47795
0.3006 | 0.3122 | 0.46141 | 0.47793
0.30059 | 0.31219 | 0.4614 | 0.47791
0.30058 | 0.31218 | 0.46138 | 0.47789
0.30057 | 0.31217 | 0.46137 | 0.47787
0.30056 | 0.31215 | 0.46136 | 0.47786
0.30055 | 0.31214 | 0.46134 | 0.47783
0.30054 | 0.31213 | 0.46131 | 0.47779
0.30053 | 0.31212 | 0.4613 | 0.47776
0.30053 | 0.31211 | 0.46129 | 0.47774
0.30051 | 0.3121 | 0.46128 | 0.47772
0.3005 | 0.31209 | 0.46126 | 0.4777
0.3005 | 0.31208 | 0.46122 | 0.47768
0.30049 | 0.31207 | 0.46121 | 0.47765
0.30048 | 0.31206 | 0.4612 | 0.47763
0.30047 | 0.31205 | 0.46118 | 0.47761
0.30046 | 0.31205 | 0.46117 | 0.47758
0.30046 | 0.31204 | 0.46115 | 0.47756
0.30045 | 0.31202 | 0.46114 | 0.47753
0.30043 | 0.31201 | 0.46112 | 0.47752
0.30043 | 0.312 | 0.46111 | 0.47749
0.30041 | 0.31199 | 0.46108 | 0.47746
0.3004 | 0.31198 | 0.46106 | 0.47744
0.30039 | 0.31197 | 0.46105 | 0.47741
0.30038 | 0.31196 | 0.46103 | 0.47739
0.30037 | 0.31195 | 0.46101 | 0.47737
0.30035 | 0.31194 | 0.461 | 0.47734
0.30034 | 0.31193 | 0.46098 | 0.47731
0.30033 | 0.31192 | 0.46096 | 0.47728
0.30032 | 0.31191 | 0.46095 | 0.47726
0.30031 | 0.3119 | 0.46092 | 0.47723
0.3003 | 0.31189 | 0.46092 | 0.47722
0.30029 | 0.31188 | 0.4609 | 0.4772
0.30028 | 0.31187 | 0.46089 | 0.47718
0.30027 | 0.31186 | 0.46087 | 0.47715
0.30025 | 0.31185 | 0.46085 | 0.47713
0.30025 | 0.31184 | 0.46082 | 0.47711
0.30023 | 0.31183 | 0.46081 | 0.47707
0.30022 | 0.31181 | 0.4608 | 0.47705
0.3002 | 0.31179 | 0.46076 | 0.47705
0.3002 | 0.31178 | 0.46075 | 0.47703
0.30019 | 0.31177 | 0.46073 | 0.477
0.30018 | 0.31176 | 0.46071 | 0.47697
0.30017 | 0.31175 | 0.46068 | 0.47695
0.30016 | 0.31174 | 0.46065 | 0.47691
0.30015 | 0.31173 | 0.46065 | 0.47689
0.30015 | 0.31173 | 0.46063 | 0.47685
0.30014 | 0.31171 | 0.46062 | 0.47683
0.30013 | 0.31171 | 0.4606 | 0.47679
0.30012 | 0.3117 | 0.46057 | 0.47678
0.30011 | 0.31168 | 0.46056 | 0.47676
0.3001 | 0.31167 | 0.46054 | 0.47674
0.30009 | 0.31166 | 0.46054 | 0.47672
0.30008 | 0.31165 | 0.46052 | 0.4767
0.30007 | 0.31164 | 0.46049 | 0.47667
0.30006 | 0.31162 | 0.46048 | 0.47663
0.30005 | 0.31161 | 0.46047 | 0.4766
0.30003 | 0.3116 | 0.46045 | 0.47657
0.30002 | 0.31159 | 0.46044 | 0.47656
0.30001 | 0.31157 | 0.46043 | 0.47653
0.3 | 0.31156 | 0.4604 | 0.47651
0.29999 | 0.31155 | 0.46038 | 0.47648
0.29998 | 0.31154 | 0.46036 | 0.47647
0.29997 | 0.31153 | 0.46035 | 0.47645
0.29996 | 0.31153 | 0.46032 | 0.47643
0.29994 | 0.31152 | 0.46031 | 0.47639
0.29994 | 0.31151 | 0.46028 | 0.47637
0.29993 | 0.31149 | 0.46027 | 0.47635
0.29991 | 0.31148 | 0.46024 | 0.47633
0.2999 | 0.31147 | 0.46022 | 0.47631
0.29989 | 0.31146 | 0.46021 | 0.47628
0.29988 | 0.31145 | 0.46019 | 0.47627
0.29987 | 0.31145 | 0.46017 | 0.47624
0.29986 | 0.31143 | 0.46016 | 0.47621
0.29985 | 0.31143 | 0.46015 | 0.47619
0.29984 | 0.31142 | 0.46013 | 0.47617
0.29984 | 0.31141 | 0.46013 | 0.47614
0.29983 | 0.3114 | 0.4601 | 0.47612
0.29981 | 0.31139 | 0.46009 | 0.4761
0.29979 | 0.31138 | 0.46007 | 0.47608
0.29979 | 0.31136 | 0.46005 | 0.47605
0.29978 | 0.31136 | 0.46003 | 0.47602
0.29977 | 0.31135 | 0.46002 | 0.47599
0.29976 | 0.31134 | 0.46001 | 0.47597
0.29975 | 0.31133 | 0.45998 | 0.47595
0.29973 | 0.31132 | 0.45995 | 0.47593
0.29971 | 0.31131 | 0.45994 | 0.4759
0.2997 | 0.3113 | 0.45992 | 0.47588
0.29969 | 0.31129 | 0.45991 | 0.47585
0.29967 | 0.31128 | 0.45989 | 0.47582
0.29966 | 0.31126 | 0.45988 | 0.47579
0.29966 | 0.31125 | 0.45986 | 0.47576
0.29965 | 0.31124 | 0.45984 | 0.47573
0.29964 | 0.31123 | 0.45982 | 0.47569
0.29963 | 0.31122 | 0.45981 | 0.47567
0.29962 | 0.31121 | 0.45978 | 0.47563
0.29961 | 0.3112 | 0.45977 | 0.47561
0.2996 | 0.31119 | 0.45975 | 0.47558
0.29958 | 0.31118 | 0.45974 | 0.47556
0.29957 | 0.31116 | 0.45972 | 0.47554
0.29956 | 0.31115 | 0.45971 | 0.47552
0.29956 | 0.31114 | 0.45969 | 0.4755
0.29955 | 0.31113 | 0.45967 | 0.47548
0.29954 | 0.31113 | 0.45966 | 0.47547
0.29953 | 0.31112 | 0.45962 | 0.47546
0.29952 | 0.31111 | 0.45961 | 0.47543
0.29951 | 0.3111 | 0.4596 | 0.47541
0.29949 | 0.31109 | 0.45958 | 0.47538
0.29948 | 0.31108 | 0.45956 | 0.47536
0.29948 | 0.31107 | 0.45954 | 0.47534
0.29946 | 0.31106 | 0.45952 | 0.4753
0.29946 | 0.31105 | 0.45951 | 0.47527
0.29945 | 0.31105 | 0.4595 | 0.47525
0.29943 | 0.31104 | 0.45948 | 0.47523
0.29942 | 0.31103 | 0.45946 | 0.4752
0.29941 | 0.31102 | 0.45945 | 0.47518
0.2994 | 0.31101 | 0.45943 | 0.47514
0.29939 | 0.311 | 0.45941 | 0.47511
0.29939 | 0.31099 | 0.4594 | 0.47508
0.29937 | 0.31098 | 0.45939 | 0.47506
0.29936 | 0.31097 | 0.45938 | 0.47503
0.29935 | 0.31096 | 0.45937 | 0.47501
0.29934 | 0.31095 | 0.45935 | 0.47499
0.29932 | 0.31094 | 0.45935 | 0.47497
0.29932 | 0.31093 | 0.45933 | 0.47494
0.2993 | 0.31092 | 0.45932 | 0.47491
0.29929 | 0.31092 | 0.45931 | 0.4749
0.29928 | 0.3109 | 0.45931 | 0.47489
0.29927 | 0.31089 | 0.4593 | 0.47486
0.29927 | 0.31089 | 0.45929 | 0.47483
0.29926 | 0.31088 | 0.45927 | 0.47482
0.29925 | 0.31087 | 0.45925 | 0.4748
0.29924 | 0.31085 | 0.45925 | 0.47478
0.29922 | 0.31085 | 0.45923 | 0.47476
0.29921 | 0.31084 | 0.45923 | 0.47472
0.29921 | 0.31083 | 0.45922 | 0.4747
0.2992 | 0.31082 | 0.4592 | 0.47468
0.29919 | 0.31081 | 0.45919 | 0.47467
0.29918 | 0.3108 | 0.45919 | 0.47466
0.29916 | 0.31078 | 0.45917 | 0.47464
0.29915 | 0.31077 | 0.45915 | 0.47463
0.29914 | 0.31075 | 0.45915 | 0.4746
0.29913 | 0.31074 | 0.45914 | 0.47458
0.29912 | 0.31073 | 0.45912 | 0.47456
0.29911 | 0.31072 | 0.45911 | 0.47455
0.2991 | 0.31072 | 0.4591 | 0.47453
0.2991 | 0.31071 | 0.45908 | 0.47452
0.29909 | 0.3107 | 0.45907 | 0.47451
0.29908 | 0.31069 | 0.45906 | 0.4745
0.29907 | 0.31067 | 0.45905 | 0.4745
0.29906 | 0.31066 | 0.45904 | 0.47449
0.29905 | 0.31065 | 0.45902 | 0.47447
0.29905 | 0.31064 | 0.45901 | 0.47446
0.29903 | 0.31063 | 0.459 | 0.47445
0.29902 | 0.31063 | 0.45899 | 0.47444
0.29901 | 0.31062 | 0.45897 | 0.47443
0.29901 | 0.31061 | 0.45897 | 0.47442
0.299 | 0.3106 | 0.45896 | 0.4744
0.29899 | 0.31059 | 0.45894 | 0.4744
0.29898 | 0.31058 | 0.45892 | 0.47439
0.29896 | 0.31058 | 0.45891 | 0.47437
0.29896 | 0.31056 | 0.4589 | 0.47437
0.29895 | 0.31055 | 0.45889 | 0.47435
0.29894 | 0.31054 | 0.45889 | 0.47433
0.29893 | 0.31053 | 0.45887 | 0.47432
0.29892 | 0.31051 | 0.45885 | 0.47431
0.2989 | 0.3105 | 0.45885 | 0.4743
0.29889 | 0.3105 | 0.45884 | 0.47428
0.29888 | 0.31049 | 0.45883 | 0.47428
0.29887 | 0.31048 | 0.45882 | 0.47427
0.29886 | 0.31047 | 0.45881 | 0.47426
0.29885 | 0.31046 | 0.4588 | 0.47424
0.29884 | 0.31045 | 0.45879 | 0.47424
0.29883 | 0.31044 | 0.45878 | 0.47422
0.29882 | 0.31043 | 0.45877 | 0.47422
0.29881 | 0.31042 | 0.45875 | 0.47421
0.2988 | 0.31041 | 0.45874 | 0.4742
0.29879 | 0.31041 | 0.45872 | 0.47419
0.29878 | 0.3104 | 0.45872 | 0.47417
0.29877 | 0.31038 | 0.4587 | 0.47416
0.29876 | 0.31037 | 0.45869 | 0.47415
0.29875 | 0.31036 | 0.45869 | 0.47414
0.29873 | 0.31036 | 0.45868 | 0.47413
0.29872 | 0.31035 | 0.45866 | 0.47412
0.2987 | 0.31034 | 0.45865 | 0.47411
0.29869 | 0.31033 | 0.45864 | 0.4741
0.29869 | 0.31032 | 0.45863 | 0.47408
0.29868 | 0.31031 | 0.45863 | 0.47408
0.29867 | 0.31029 | 0.45861 | 0.47407
0.29866 | 0.31028 | 0.45861 | 0.47406
0.29865 | 0.31028 | 0.45861 | 0.47405
0.29863 | 0.31027 | 0.45859 | 0.47404
0.29862 | 0.31026 | 0.45858 | 0.47404
0.29861 | 0.31025 | 0.45857 | 0.47402
0.29861 | 0.31024 | 0.45856 | 0.47402
0.2986 | 0.31023 | 0.45855 | 0.47401
0.29858 | 0.31022 | 0.45853 | 0.474
0.29858 | 0.31021 | 0.45852 | 0.47399
0.29857 | 0.3102 | 0.45851 | 0.47399
0.29856 | 0.31019 | 0.45851 | 0.47398
0.29854 | 0.31019 | 0.45849 | 0.47397
0.29853 | 0.31018 | 0.45848 | 0.47395
0.29852 | 0.31017 | 0.45847 | 0.47393
0.29851 | 0.31016 | 0.45846 | 0.47393
0.2985 | 0.31015 | 0.45845 | 0.47391
0.29849 | 0.31015 | 0.45844 | 0.4739
0.29848 | 0.31014 | 0.45843 | 0.47389
0.29847 | 0.31013 | 0.45841 | 0.47388
0.29846 | 0.31012 | 0.4584 | 0.47386
0.29845 | 0.31012 | 0.4584 | 0.47386
0.29844 | 0.31011 | 0.45839 | 0.47385
0.29842 | 0.31009 | 0.45838 | 0.47384
0.29842 | 0.31008 | 0.45837 | 0.47382
0.2984 | 0.31006 | 0.45836 | 0.47381
0.29839 | 0.31005 | 0.45834 | 0.4738
0.29838 | 0.31004 | 0.45832 | 0.47379
0.29837 | 0.31003 | 0.45832 | 0.47378
0.29836 | 0.31002 | 0.45829 | 0.47377
0.29835 | 0.31001 | 0.45829 | 0.47376
0.29834 | 0.31001 | 0.45827 | 0.47375
0.29833 | 0.31 | 0.45826 | 0.47374
0.29832 | 0.30999 | 0.45825 | 0.47373
0.2983 | 0.30998 | 0.45823 | 0.47372
0.29829 | 0.30997 | 0.45822 | 0.47372
0.29828 | 0.30996 | 0.45821 | 0.47371
0.29827 | 0.30995 | 0.45819 | 0.47369
0.29826 | 0.30993 | 0.45818 | 0.47368
0.29825 | 0.30992 | 0.45818 | 0.47368
0.29825 | 0.30991 | 0.45817 | 0.47365
0.29823 | 0.3099 | 0.45815 | 0.47365
0.29822 | 0.30988 | 0.45815 | 0.47364
0.29821 | 0.30987 | 0.45813 | 0.47363
0.2982 | 0.30986 | 0.45812 | 0.47361
0.29818 | 0.30986 | 0.45811 | 0.4736
0.29817 | 0.30985 | 0.4581 | 0.4736
0.29816 | 0.30984 | 0.45809 | 0.47359
0.29816 | 0.30983 | 0.45808 | 0.47358
0.29815 | 0.30982 | 0.45807 | 0.47357
0.29814 | 0.30981 | 0.45805 | 0.47357
0.29813 | 0.3098 | 0.45804 | 0.47356
0.29812 | 0.30979 | 0.45803 | 0.47355
0.2981 | 0.30977 | 0.45802 | 0.47353
0.29809 | 0.30976 | 0.45801 | 0.47352
0.29808 | 0.30974 | 0.458 | 0.47352
0.29807 | 0.30973 | 0.458 | 0.47351
0.29806 | 0.30972 | 0.45798 | 0.4735
0.29806 | 0.30971 | 0.45797 | 0.47349
0.29805 | 0.3097 | 0.45796 | 0.47348
0.29804 | 0.30969 | 0.45794 | 0.47347
0.29803 | 0.30968 | 0.45793 | 0.47346
0.29803 | 0.30967 | 0.45791 | 0.47345
0.29801 | 0.30966 | 0.45789 | 0.47344
0.29801 | 0.30965 | 0.45788 | 0.47343
0.298 | 0.30964 | 0.45786 | 0.47342
0.29798 | 0.30963 | 0.45785 | 0.47341
0.29798 | 0.30962 | 0.45784 | 0.4734
0.29797 | 0.30961 | 0.45784 | 0.47339
0.29796 | 0.3096 | 0.45782 | 0.47338
0.29795 | 0.30959 | 0.45782 | 0.47337
0.29793 | 0.30959 | 0.45781 | 0.47336
0.29792 | 0.30958 | 0.4578 | 0.47335
0.29791 | 0.30957 | 0.45778 | 0.47334
0.2979 | 0.30956 | 0.45777 | 0.47334
0.29789 | 0.30956 | 0.45774 | 0.47332
0.29788 | 0.30955 | 0.45774 | 0.47331
0.29787 | 0.30954 | 0.45773 | 0.47329
0.29786 | 0.30953 | 0.45772 | 0.47328
0.29785 | 0.30952 | 0.45771 | 0.47327
0.29784 | 0.30952 | 0.4577 | 0.47326
0.29783 | 0.30951 | 0.45769 | 0.47326
0.29782 | 0.3095 | 0.45767 | 0.47324
0.29782 | 0.30949 | 0.45767 | 0.47324
0.29781 | 0.30948 | 0.45766 | 0.47322
0.2978 | 0.30947 | 0.45765 | 0.47321
0.29779 | 0.30946 | 0.45764 | 0.4732
0.29778 | 0.30945 | 0.45762 | 0.47319
0.29778 | 0.30944 | 0.45761 | 0.47318
0.29777 | 0.30943 | 0.4576 | 0.47316
0.29776 | 0.30941 | 0.45759 | 0.47316
0.29775 | 0.30941 | 0.45758 | 0.47314
0.29774 | 0.30939 | 0.45756 | 0.47314
0.29773 | 0.30938 | 0.45754 | 0.47312
0.29772 | 0.30937 | 0.45754 | 0.47311
0.29771 | 0.30936 | 0.45752 | 0.47311
0.29769 | 0.30935 | 0.4575 | 0.4731
0.29769 | 0.30934 | 0.4575 | 0.47308
0.29768 | 0.30933 | 0.45748 | 0.47308
0.29766 | 0.30932 | 0.45747 | 0.47307
0.29766 | 0.30931 | 0.45746 | 0.47305
0.29765 | 0.3093 | 0.45745 | 0.47303
0.29764 | 0.3093 | 0.45744 | 0.47303
0.29763 | 0.30928 | 0.45743 | 0.47302
0.29761 | 0.30928 | 0.45741 | 0.473
0.29761 | 0.30926 | 0.4574 | 0.47299
0.2976 | 0.30925 | 0.45739 | 0.47299
0.29759 | 0.30923 | 0.45738 | 0.47298
0.29758 | 0.30922 | 0.45737 | 0.47296
0.29757 | 0.30921 | 0.45735 | 0.47295
0.29757 | 0.3092 | 0.45734 | 0.47295
0.29756 | 0.30919 | 0.45732 | 0.47293
0.29755 | 0.30918 | 0.45732 | 0.47292
0.29754 | 0.30917 | 0.45731 | 0.47291
0.29753 | 0.30917 | 0.4573 | 0.47291
0.29751 | 0.30915 | 0.45729 | 0.4729
0.2975 | 0.30914 | 0.45727 | 0.47289
0.2975 | 0.30913 | 0.45727 | 0.47288
0.29749 | 0.30912 | 0.45726 | 0.47286
0.29748 | 0.30912 | 0.45726 | 0.47284
0.29746 | 0.3091 | 0.45725 | 0.47284
0.29745 | 0.30909 | 0.45724 | 0.47282
0.29744 | 0.30908 | 0.45723 | 0.47282
0.29743 | 0.30907 | 0.4572 | 0.47281
0.29741 | 0.30906 | 0.45719 | 0.4728
0.29741 | 0.30905 | 0.45718 | 0.47279
0.2974 | 0.30904 | 0.45717 | 0.47277
0.29739 | 0.30903 | 0.45716 | 0.47277
0.29738 | 0.30902 | 0.45715 | 0.47275
0.29737 | 0.30901 | 0.45713 | 0.47274
0.29736 | 0.309 | 0.45712 | 0.47271
0.29735 | 0.30899 | 0.45712 | 0.4727
0.29734 | 0.30898 | 0.4571 | 0.4727
0.29732 | 0.30897 | 0.45708 | 0.47268
0.29731 | 0.30896 | 0.45708 | 0.47267
0.2973 | 0.30895 | 0.45706 | 0.47267
0.29729 | 0.30894 | 0.45705 | 0.47266
0.29728 | 0.30893 | 0.45704 | 0.47265
0.29728 | 0.30892 | 0.45703 | 0.47264
0.29727 | 0.30891 | 0.45702 | 0.47263
0.29725 | 0.3089 | 0.457 | 0.47262
0.29725 | 0.30889 | 0.45699 | 0.47262
0.29724 | 0.30888 | 0.45698 | 0.47261
0.29723 | 0.30887 | 0.45697 | 0.4726
0.29722 | 0.30885 | 0.45696 | 0.47259
0.29721 | 0.30883 | 0.45694 | 0.47258
0.29721 | 0.30882 | 0.45693 | 0.47257
0.2972 | 0.3088 | 0.45692 | 0.47256
0.29719 | 0.30879 | 0.45691 | 0.47255
0.29718 | 0.30878 | 0.4569 | 0.47254
0.29717 | 0.30877 | 0.45689 | 0.47254
0.29716 | 0.30876 | 0.45687 | 0.47253
0.29715 | 0.30875 | 0.45686 | 0.47252
0.29714 | 0.30874 | 0.45685 | 0.47251
0.29714 | 0.30873 | 0.45684 | 0.4725
0.29713 | 0.30872 | 0.45682 | 0.47249
0.29712 | 0.30871 | 0.45681 | 0.47247
0.29711 | 0.3087 | 0.4568 | 0.47246
0.2971 | 0.30868 | 0.45679 | 0.47245
0.29709 | 0.30867 | 0.45677 | 0.47244
0.29707 | 0.30867 | 0.45676 | 0.47243
0.29707 | 0.30866 | 0.45675 | 0.47241
0.29706 | 0.30864 | 0.45674 | 0.4724
0.29705 | 0.30863 | 0.45673 | 0.47239
0.29704 | 0.30862 | 0.45671 | 0.47238
0.29703 | 0.30861 | 0.45671 | 0.47236
0.29702 | 0.3086 | 0.4567 | 0.47236
0.297 | 0.30859 | 0.45668 | 0.47234
0.29699 | 0.30858 | 0.45667 | 0.47233
0.29697 | 0.30856 | 0.45666 | 0.47232
0.29696 | 0.30855 | 0.45665 | 0.4723
0.29695 | 0.30854 | 0.45664 | 0.47229
0.29694 | 0.30853 | 0.45663 | 0.47229
0.29692 | 0.30852 | 0.45662 | 0.47228
0.29691 | 0.30851 | 0.45662 | 0.47227
0.2969 | 0.3085 | 0.45659 | 0.47225
0.29688 | 0.30848 | 0.45659 | 0.47225
0.29688 | 0.30848 | 0.45658 | 0.47224
0.29686 | 0.30847 | 0.45657 | 0.47223
0.29685 | 0.30846 | 0.45656 | 0.47222
0.29684 | 0.30845 | 0.45654 | 0.47221
0.29683 | 0.30844 | 0.45652 | 0.47219
0.29682 | 0.30843 | 0.45651 | 0.47219
0.29681 | 0.30842 | 0.4565 | 0.47217
0.2968 | 0.30841 | 0.45649 | 0.47217
0.29679 | 0.3084 | 0.45649 | 0.47216
0.29678 | 0.30839 | 0.45647 | 0.47214
0.29677 | 0.30838 | 0.45646 | 0.47213
0.29676 | 0.30837 | 0.45645 | 0.47213
0.29675 | 0.30836 | 0.45644 | 0.47211
0.29674 | 0.30834 | 0.45643 | 0.4721
0.29672 | 0.30833 | 0.45642 | 0.47209
0.29671 | 0.30832 | 0.45641 | 0.47208
0.29669 | 0.30831 | 0.45639 | 0.47208
0.29668 | 0.30831 | 0.45638 | 0.47207
0.29667 | 0.3083 | 0.45637 | 0.47206
0.29666 | 0.30829 | 0.45635 | 0.47206
0.29665 | 0.30828 | 0.45634 | 0.47204
0.29664 | 0.30826 | 0.45633 | 0.47204
0.29662 | 0.30825 | 0.45632 | 0.47203
0.29662 | 0.30824 | 0.45631 | 0.47202
0.29661 | 0.30823 | 0.45629 | 0.47201
0.2966 | 0.30822 | 0.45628 | 0.472
0.29659 | 0.30822 | 0.45627 | 0.47197
0.29659 | 0.3082 | 0.45625 | 0.47196
0.29657 | 0.30819 | 0.45624 | 0.47195
0.29656 | 0.30818 | 0.45623 | 0.47194
0.29655 | 0.30817 | 0.45621 | 0.47194
0.29655 | 0.30816 | 0.45621 | 0.47192
0.29654 | 0.30815 | 0.4562 | 0.47191
0.29653 | 0.30814 | 0.45619 | 0.4719
0.29651 | 0.30813 | 0.45618 | 0.47189
0.2965 | 0.30812 | 0.45617 | 0.47187
0.29649 | 0.30811 | 0.45616 | 0.47185
0.29648 | 0.3081 | 0.45615 | 0.47184
0.29647 | 0.30809 | 0.45614 | 0.47184
0.29646 | 0.30808 | 0.45613 | 0.47183
0.29645 | 0.30807 | 0.45611 | 0.47182
0.29644 | 0.30805 | 0.4561 | 0.47182
0.29643 | 0.30804 | 0.45608 | 0.4718
0.29642 | 0.30803 | 0.45608 | 0.47179
0.29641 | 0.30803 | 0.45607 | 0.47178
0.29641 | 0.30801 | 0.45605 | 0.47176
0.29639 | 0.308 | 0.45603 | 0.47176
0.29639 | 0.30799 | 0.45602 | 0.47174
0.29638 | 0.30798 | 0.45601 | 0.47172
0.29637 | 0.30796 | 0.456 | 0.47172
0.29635 | 0.30796 | 0.45599 | 0.47171
0.29634 | 0.30795 | 0.45597 | 0.47169
0.29633 | 0.30793 | 0.45597 | 0.47168
0.29631 | 0.30792 | 0.45595 | 0.47167
0.2963 | 0.30792 | 0.45593 | 0.47167
0.29629 | 0.30791 | 0.45593 | 0.47165
0.29628 | 0.30789 | 0.45591 | 0.47164
0.29627 | 0.30788 | 0.45591 | 0.47163
0.29626 | 0.30788 | 0.45589 | 0.47162
0.29625 | 0.30787 | 0.45588 | 0.47161
0.29624 | 0.30786 | 0.45588 | 0.4716
0.29623 | 0.30785 | 0.45586 | 0.4716
0.29622 | 0.30784 | 0.45585 | 0.47158
0.29621 | 0.30783 | 0.45584 | 0.47157
0.29619 | 0.30782 | 0.45583 | 0.47157
0.29618 | 0.30781 | 0.45582 | 0.47155
0.29617 | 0.3078 | 0.45581 | 0.47153
0.29616 | 0.30779 | 0.4558 | 0.47151
0.29615 | 0.30778 | 0.45578 | 0.4715
0.29614 | 0.30776 | 0.45576 | 0.47149
0.29613 | 0.30775 | 0.45575 | 0.47148
0.29613 | 0.30773 | 0.45574 | 0.47147
0.29612 | 0.30772 | 0.45573 | 0.47146
0.2961 | 0.30772 | 0.45572 | 0.47145
0.29609 | 0.30771 | 0.4557 | 0.47144
0.29609 | 0.3077 | 0.45569 | 0.47143
0.29608 | 0.30769 | 0.45568 | 0.47141
0.29607 | 0.30768 | 0.45567 | 0.4714
0.29605 | 0.30767 | 0.45566 | 0.4714
0.29604 | 0.30766 | 0.45565 | 0.47138
0.29603 | 0.30764 | 0.45564 | 0.47137
0.29602 | 0.30763 | 0.45563 | 0.47136
0.29602 | 0.30762 | 0.45562 | 0.47135
0.29601 | 0.30761 | 0.45562 | 0.47134
0.296 | 0.3076 | 0.45559 | 0.47133
0.29599 | 0.30759 | 0.45558 | 0.47132
0.29598 | 0.30758 | 0.45557 | 0.47131
0.29597 | 0.30757 | 0.45556 | 0.4713
0.29597 | 0.30757 | 0.45555 | 0.47129
0.29596 | 0.30756 | 0.45554 | 0.47128
0.29595 | 0.30755 | 0.45553 | 0.47127
0.29594 | 0.30754 | 0.45552 | 0.47126
0.29593 | 0.30753 | 0.45552 | 0.47125
0.29592 | 0.30753 | 0.4555 | 0.47124
0.29591 | 0.30752 | 0.4555 | 0.47124
0.29589 | 0.30751 | 0.45549 | 0.47123
0.29588 | 0.30749 | 0.45548 | 0.47121
0.29587 | 0.30748 | 0.45546 | 0.47121
0.29586 | 0.30747 | 0.45545 | 0.47119
0.29585 | 0.30746 | 0.45544 | 0.47118
0.29584 | 0.30745 | 0.45543 | 0.47118
0.29583 | 0.30744 | 0.45542 | 0.47117
0.29582 | 0.30743 | 0.4554 | 0.47115
0.29581 | 0.30741 | 0.45539 | 0.47115
0.2958 | 0.3074 | 0.45538 | 0.47114
0.29579 | 0.30739 | 0.45538 | 0.47113
0.29578 | 0.30739 | 0.45537 | 0.47113
0.29576 | 0.30738 | 0.45534 | 0.47112
0.29575 | 0.30737 | 0.45534 | 0.47111
0.29574 | 0.30736 | 0.45532 | 0.47109
0.29574 | 0.30735 | 0.45531 | 0.47109
0.29573 | 0.30735 | 0.4553 | 0.47108
0.29571 | 0.30734 | 0.45529 | 0.47107
0.2957 | 0.30733 | 0.45528 | 0.47106
0.29569 | 0.30732 | 0.45526 | 0.47105
0.29568 | 0.30732 | 0.45525 | 0.47103
0.29566 | 0.30731 | 0.45524 | 0.47102
0.29565 | 0.3073 | 0.45523 | 0.47102
0.29564 | 0.30729 | 0.45521 | 0.471
0.29563 | 0.30727 | 0.4552 | 0.471
0.29563 | 0.30727 | 0.45519 | 0.47099
0.29562 | 0.30726 | 0.45517 | 0.47097
0.29561 | 0.30725 | 0.45517 | 0.47097
0.29559 | 0.30724 | 0.45515 | 0.47096
0.29558 | 0.30723 | 0.45515 | 0.47095
0.29557 | 0.30722 | 0.45514 | 0.47093
0.29556 | 0.30721 | 0.45513 | 0.47092
0.29555 | 0.3072 | 0.45512 | 0.47091
0.29554 | 0.30719 | 0.45511 | 0.47089
0.29553 | 0.30717 | 0.4551 | 0.47089
0.29552 | 0.30717 | 0.45509 | 0.47087
0.2955 | 0.30715 | 0.45508 | 0.47085
0.29549 | 0.30715 | 0.45508 | 0.47084
0.29548 | 0.30713 | 0.45507 | 0.47084
0.29548 | 0.30712 | 0.45504 | 0.47082
0.29547 | 0.30711 | 0.45503 | 0.4708
0.29546 | 0.3071 | 0.45502 | 0.4708
0.29545 | 0.30709 | 0.45501 | 0.47079
0.29544 | 0.30708 | 0.455 | 0.47078
0.29544 | 0.30707 | 0.45499 | 0.47077
0.29542 | 0.30706 | 0.45497 | 0.47076
0.29541 | 0.30705 | 0.45496 | 0.47076
0.2954 | 0.30704 | 0.45495 | 0.47075
0.29539 | 0.30703 | 0.45495 | 0.47074
0.29538 | 0.30702 | 0.45493 | 0.47073
0.29536 | 0.30701 | 0.45492 | 0.47071
0.29535 | 0.307 | 0.45491 | 0.4707
0.29534 | 0.30699 | 0.4549 | 0.4707
0.29534 | 0.30698 | 0.45489 | 0.47068
0.29532 | 0.30697 | 0.45488 | 0.47067
0.29531 | 0.30696 | 0.45486 | 0.47066
0.2953 | 0.30695 | 0.45486 | 0.47065
0.29529 | 0.30694 | 0.45484 | 0.47063
0.29528 | 0.30693 | 0.45483 | 0.47062
0.29527 | 0.30692 | 0.45483 | 0.47062
0.29526 | 0.30691 | 0.45482 | 0.47061
0.29525 | 0.3069 | 0.45481 | 0.4706
0.29523 | 0.30689 | 0.4548 | 0.47059
0.29522 | 0.30688 | 0.45479 | 0.47057
0.29521 | 0.30687 | 0.45478 | 0.47056
0.29521 | 0.30686 | 0.45477 | 0.47055
0.2952 | 0.30685 | 0.45476 | 0.47053
0.29519 | 0.30684 | 0.45476 | 0.47053
0.29518 | 0.30683 | 0.45474 | 0.47052
0.29517 | 0.30683 | 0.45473 | 0.47052
0.29515 | 0.30682 | 0.45472 | 0.47051
0.29514 | 0.30681 | 0.4547 | 0.4705
0.29513 | 0.3068 | 0.4547 | 0.47049
0.29512 | 0.30679 | 0.45469 | 0.47048
0.29512 | 0.30678 | 0.45467 | 0.47047
0.2951 | 0.30677 | 0.45467 | 0.47046
0.29509 | 0.30676 | 0.45465 | 0.47045
0.29507 | 0.30675 | 0.45465 | 0.47045
0.29506 | 0.30674 | 0.45464 | 0.47044
0.29505 | 0.30673 | 0.45463 | 0.47042
0.29503 | 0.30672 | 0.45461 | 0.47042
0.29502 | 0.30672 | 0.4546 | 0.47041
0.29501 | 0.30671 | 0.4546 | 0.4704
0.29499 | 0.30669 | 0.45459 | 0.47039
0.29498 | 0.30669 | 0.45458 | 0.47039
0.29497 | 0.30668 | 0.45457 | 0.47037
0.29496 | 0.30667 | 0.45455 | 0.47036
0.29495 | 0.30666 | 0.45455 | 0.47036
0.29495 | 0.30665 | 0.45453 | 0.47035
0.29494 | 0.30664 | 0.45453 | 0.47034
0.29493 | 0.30663 | 0.45452 | 0.47033
0.29492 | 0.30662 | 0.45452 | 0.47032
0.29491 | 0.30661 | 0.45451 | 0.47032
0.2949 | 0.30661 | 0.4545 | 0.47031
0.29489 | 0.3066 | 0.45449 | 0.47029
0.29488 | 0.30659 | 0.45448 | 0.47028
0.29486 | 0.30658 | 0.45447 | 0.47027
0.29485 | 0.30657 | 0.45446 | 0.47027
0.29484 | 0.30656 | 0.45444 | 0.47026
0.29483 | 0.30655 | 0.45443 | 0.47025
0.29483 | 0.30654 | 0.45442 | 0.47024
0.29481 | 0.30653 | 0.45441 | 0.47023
0.2948 | 0.30652 | 0.45441 | 0.47021
0.2948 | 0.30651 | 0.4544 | 0.4702
0.29479 | 0.30651 | 0.45438 | 0.47018
0.29478 | 0.3065 | 0.45438 | 0.47018
0.29477 | 0.30649 | 0.45436 | 0.47017
0.29476 | 0.30648 | 0.45436 | 0.47016
0.29474 | 0.30647 | 0.45434 | 0.47015
0.29473 | 0.30646 | 0.45433 | 0.47014
0.29472 | 0.30645 | 0.45433 | 0.47014
0.2947 | 0.30645 | 0.45432 | 0.47013
0.2947 | 0.30643 | 0.45431 | 0.47013
0.29468 | 0.30642 | 0.4543 | 0.47011
0.29468 | 0.30642 | 0.45429 | 0.47009
0.29466 | 0.30641 | 0.45428 | 0.47009
0.29465 | 0.30639 | 0.45427 | 0.47008
0.29464 | 0.30639 | 0.45425 | 0.47007
0.29463 | 0.30638 | 0.45423 | 0.47005
0.29461 | 0.30637 | 0.45422 | 0.47005
0.2946 | 0.30636 | 0.45421 | 0.47003
0.29459 | 0.30636 | 0.4542 | 0.47003
0.29458 | 0.30635 | 0.45419 | 0.47001
0.29458 | 0.30634 | 0.45418 | 0.47
0.29457 | 0.30633 | 0.45417 | 0.46999
0.29456 | 0.30632 | 0.45415 | 0.46998
0.29455 | 0.30631 | 0.45413 | 0.46997
0.29454 | 0.3063 | 0.45413 | 0.46996
0.29453 | 0.30629 | 0.45411 | 0.46994
0.29452 | 0.30628 | 0.45411 | 0.46993
0.29451 | 0.30627 | 0.45409 | 0.46992
0.29451 | 0.30626 | 0.45408 | 0.46991
0.29449 | 0.30625 | 0.45407 | 0.4699
0.29448 | 0.30624 | 0.45406 | 0.46988
0.29447 | 0.30623 | 0.45404 | 0.46988
0.29446 | 0.30622 | 0.45403 | 0.46987
0.29445 | 0.30621 | 0.45402 | 0.46986
0.29444 | 0.3062 | 0.45401 | 0.46984
0.29443 | 0.30619 | 0.454 | 0.46983
0.29442 | 0.30619 | 0.45399 | 0.46982
0.29441 | 0.30618 | 0.45398 | 0.4698
0.2944 | 0.30617 | 0.45397 | 0.4698
0.29439 | 0.30615 | 0.45396 | 0.46978
0.29437 | 0.30615 | 0.45395 | 0.46977
0.29436 | 0.30613 | 0.45394 | 0.46977
0.29435 | 0.30612 | 0.45393 | 0.46975
0.29435 | 0.30611 | 0.45393 | 0.46974
0.29434 | 0.3061 | 0.45391 | 0.46973
0.29433 | 0.30609 | 0.45389 | 0.46972
0.29432 | 0.30608 | 0.45388 | 0.46971
0.29431 | 0.30607 | 0.45385 | 0.46969
0.2943 | 0.30607 | 0.45384 | 0.46968
0.29429 | 0.30606 | 0.45384 | 0.46968
0.29429 | 0.30605 | 0.45383 | 0.46966
0.29428 | 0.30604 | 0.45382 | 0.46965
0.29426 | 0.30603 | 0.4538 | 0.46964
0.29425 | 0.30602 | 0.4538 | 0.46963
0.29424 | 0.30601 | 0.45379 | 0.46962
0.29423 | 0.306 | 0.45378 | 0.46961
0.29422 | 0.30599 | 0.45377 | 0.46961
0.29421 | 0.30599 | 0.45375 | 0.46958
0.2942 | 0.30598 | 0.45374 | 0.46958
0.29419 | 0.30597 | 0.45374 | 0.46956
0.29418 | 0.30596 | 0.45373 | 0.46955
0.29417 | 0.30595 | 0.45372 | 0.46954
0.29416 | 0.30594 | 0.45372 | 0.46954
0.29415 | 0.30593 | 0.45371 | 0.46952
0.29414 | 0.30592 | 0.4537 | 0.46951
0.29413 | 0.30591 | 0.45368 | 0.4695
0.29412 | 0.3059 | 0.45367 | 0.46948
0.29412 | 0.30589 | 0.45367 | 0.46947
0.29411 | 0.30589 | 0.45365 | 0.46946
0.29409 | 0.30587 | 0.45364 | 0.46946
0.29409 | 0.30586 | 0.45363 | 0.46944
0.29408 | 0.30585 | 0.45362 | 0.46943
0.29407 | 0.30584 | 0.45362 | 0.46941
0.29406 | 0.30583 | 0.45361 | 0.46941
0.29405 | 0.30582 | 0.4536 | 0.46939
0.29404 | 0.30581 | 0.45358 | 0.46938
0.29403 | 0.3058 | 0.45357 | 0.46937
0.29403 | 0.30579 | 0.45356 | 0.46936
0.29402 | 0.30578 | 0.45355 | 0.46935
0.294 | 0.30578 | 0.45354 | 0.46934
0.29399 | 0.30576 | 0.45353 | 0.46933
0.29399 | 0.30575 | 0.45352 | 0.46933
0.29398 | 0.30574 | 0.45351 | 0.46931
0.29397 | 0.30573 | 0.45351 | 0.46931
0.29395 | 0.30572 | 0.45349 | 0.46928
0.29394 | 0.30571 | 0.45348 | 0.46928
0.29394 | 0.3057 | 0.45345 | 0.46927
0.29393 | 0.30569 | 0.45345 | 0.46925
0.29392 | 0.30568 | 0.45344 | 0.46924
0.29391 | 0.30567 | 0.45343 | 0.46924
0.2939 | 0.30566 | 0.45341 | 0.46922
0.29389 | 0.30565 | 0.45339 | 0.46921
0.29388 | 0.30564 | 0.45339 | 0.4692
0.29386 | 0.30563 | 0.45337 | 0.4692
0.29386 | 0.30563 | 0.45337 | 0.46919
0.29384 | 0.30561 | 0.45335 | 0.46918
0.29383 | 0.3056 | 0.45334 | 0.46917
0.29382 | 0.30559 | 0.45333 | 0.46916
0.29381 | 0.30559 | 0.45332 | 0.46915
0.2938 | 0.30558 | 0.45331 | 0.46913
0.29379 | 0.30557 | 0.4533 | 0.46913
0.29378 | 0.30556 | 0.45329 | 0.46911
0.29377 | 0.30555 | 0.45328 | 0.4691
0.29376 | 0.30554 | 0.45327 | 0.46909
0.29375 | 0.30553 | 0.45326 | 0.46908
0.29374 | 0.30552 | 0.45325 | 0.46907
0.29374 | 0.30551 | 0.45324 | 0.46905
0.29373 | 0.3055 | 0.45323 | 0.46905
0.29372 | 0.30549 | 0.45322 | 0.46904
0.29371 | 0.30548 | 0.4532 | 0.46903
0.29369 | 0.30547 | 0.4532 | 0.46901
0.29368 | 0.30546 | 0.45319 | 0.469
0.29367 | 0.30546 | 0.45317 | 0.46899
0.29365 | 0.30545 | 0.45317 | 0.46897
0.29365 | 0.30544 | 0.45316 | 0.46897
0.29364 | 0.30544 | 0.45315 | 0.46896
0.29362 | 0.30543 | 0.45313 | 0.46895
0.29362 | 0.30542 | 0.45313 | 0.46894
0.2936 | 0.30541 | 0.45311 | 0.46893
0.29359 | 0.3054 | 0.4531 | 0.46892
0.29358 | 0.30539 | 0.45309 | 0.4689
0.29357 | 0.30538 | 0.45307 | 0.4689
0.29356 | 0.30537 | 0.45305 | 0.46888
0.29355 | 0.30535 | 0.45305 | 0.46887
0.29354 | 0.30535 | 0.45303 | 0.46886
0.29353 | 0.30534 | 0.45302 | 0.46885
0.29352 | 0.30533 | 0.45301 | 0.46884
0.2935 | 0.30532 | 0.45299 | 0.46883
0.29348 | 0.30531 | 0.45298 | 0.46882
0.29348 | 0.3053 | 0.45297 | 0.46881
0.29347 | 0.3053 | 0.45296 | 0.46881
0.29347 | 0.30529 | 0.45295 | 0.4688
0.29345 | 0.30529 | 0.45294 | 0.46879
0.29343 | 0.30528 | 0.45293 | 0.46878
0.29343 | 0.30527 | 0.45292 | 0.46877
0.29342 | 0.30526 | 0.45291 | 0.46876
0.29341 | 0.30525 | 0.4529 | 0.46875
0.2934 | 0.30524 | 0.45289 | 0.46874
0.29339 | 0.30523 | 0.45287 | 0.46874
0.29338 | 0.30522 | 0.45286 | 0.46873
0.29337 | 0.30521 | 0.45284 | 0.46871
0.29336 | 0.30521 | 0.45283 | 0.46871
0.29335 | 0.3052 | 0.45282 | 0.4687
0.29335 | 0.30519 | 0.45281 | 0.46868
0.29334 | 0.30517 | 0.4528 | 0.46868
0.29332 | 0.30516 | 0.45278 | 0.46867
0.29331 | 0.30515 | 0.45277 | 0.46866
0.2933 | 0.30514 | 0.45276 | 0.46865
0.29329 | 0.30513 | 0.45276 | 0.46865
0.29328 | 0.30512 | 0.45274 | 0.46863
0.29327 | 0.30511 | 0.45273 | 0.46862
0.29326 | 0.3051 | 0.45272 | 0.46861
0.29325 | 0.30509 | 0.45271 | 0.4686
0.29324 | 0.30509 | 0.45269 | 0.46858
0.29323 | 0.30508 | 0.45268 | 0.46857
0.29322 | 0.30507 | 0.45268 | 0.46855
0.29321 | 0.30506 | 0.45266 | 0.46854
0.2932 | 0.30505 | 0.45265 | 0.46854
0.29319 | 0.30505 | 0.45264 | 0.46852
0.29318 | 0.30504 | 0.45262 | 0.46851
0.29317 | 0.30503 | 0.45262 | 0.4685
0.29316 | 0.30501 | 0.4526 | 0.4685
0.29315 | 0.305 | 0.4526 | 0.46849
0.29314 | 0.305 | 0.45259 | 0.46848
0.29314 | 0.30499 | 0.45258 | 0.46847
0.29313 | 0.30497 | 0.45257 | 0.46846
0.29312 | 0.30496 | 0.45256 | 0.46846
0.29311 | 0.30495 | 0.45254 | 0.46845
0.2931 | 0.30494 | 0.45253 | 0.46844
0.29309 | 0.30494 | 0.45252 | 0.46842
0.29308 | 0.30493 | 0.45251 | 0.46842
0.29307 | 0.30492 | 0.4525 | 0.46841
0.29305 | 0.30491 | 0.45249 | 0.4684
0.29304 | 0.30489 | 0.45249 | 0.46839
0.29303 | 0.30488 | 0.45247 | 0.46838
0.29301 | 0.30488 | 0.45246 | 0.46837
0.29301 | 0.30487 | 0.45245 | 0.46836
0.293 | 0.30486 | 0.45243 | 0.46835
0.29298 | 0.30485 | 0.45242 | 0.46834
0.29298 | 0.30484 | 0.45241 | 0.46833
0.29297 | 0.30484 | 0.4524 | 0.46832
0.29296 | 0.30483 | 0.45239 | 0.46832
0.29295 | 0.30482 | 0.45238 | 0.46831
0.29294 | 0.30481 | 0.45237 | 0.4683
0.29293 | 0.30481 | 0.45235 | 0.46828
0.29292 | 0.30479 | 0.45235 | 0.46828
0.29292 | 0.30478 | 0.45234 | 0.46826
0.29291 | 0.30477 | 0.45233 | 0.46825
0.2929 | 0.30475 | 0.45231 | 0.46824
0.29288 | 0.30474 | 0.4523 | 0.46823
0.29287 | 0.30473 | 0.45228 | 0.46822
0.29286 | 0.30472 | 0.45228 | 0.46822
0.29284 | 0.30471 | 0.45227 | 0.46822
0.29283 | 0.3047 | 0.45225 | 0.4682
0.29282 | 0.30468 | 0.45224 | 0.46819
0.2928 | 0.30468 | 0.45223 | 0.46818
0.2928 | 0.30467 | 0.45221 | 0.46817
0.29278 | 0.30466 | 0.45221 | 0.46815
0.29277 | 0.30465 | 0.4522 | 0.46815
0.29275 | 0.30464 | 0.45218 | 0.46813
0.29274 | 0.30463 | 0.45216 | 0.46812
0.29274 | 0.30462 | 0.45216 | 0.4681
0.29272 | 0.30462 | 0.45215 | 0.46809
0.29271 | 0.30461 | 0.45214 | 0.46809
0.2927 | 0.3046 | 0.45213 | 0.46808
0.29269 | 0.30459 | 0.45212 | 0.46807
0.29269 | 0.30457 | 0.4521 | 0.46805
0.29268 | 0.30455 | 0.4521 | 0.46804
0.29267 | 0.30454 | 0.45209 | 0.46803
0.29265 | 0.30453 | 0.45207 | 0.46802
0.29264 | 0.30451 | 0.45207 | 0.468
0.29263 | 0.3045 | 0.45204 | 0.46799
0.29262 | 0.3045 | 0.45204 | 0.46798
0.29261 | 0.30449 | 0.45203 | 0.46797
0.2926 | 0.30447 | 0.45201 | 0.46796
0.2926 | 0.30446 | 0.45201 | 0.46795
0.29259 | 0.30445 | 0.452 | 0.46794
0.29258 | 0.30444 | 0.45198 | 0.46794
0.29257 | 0.30443 | 0.45197 | 0.46793
0.29256 | 0.30442 | 0.45195 | 0.46791
0.29256 | 0.30442 | 0.45195 | 0.46789
0.29254 | 0.30441 | 0.45193 | 0.46788
0.29253 | 0.3044 | 0.45192 | 0.46788
0.29252 | 0.30438 | 0.45192 | 0.46787
0.29251 | 0.30438 | 0.4519 | 0.46786
0.29251 | 0.30437 | 0.45189 | 0.46785
0.2925 | 0.30436 | 0.45189 | 0.46784
0.29248 | 0.30436 | 0.45187 | 0.46783
0.29247 | 0.30434 | 0.45186 | 0.46781
0.29246 | 0.30433 | 0.45185 | 0.46781
0.29245 | 0.30433 | 0.45184 | 0.4678
0.29244 | 0.30431 | 0.45182 | 0.46779
0.29243 | 0.30431 | 0.45181 | 0.46778
0.29242 | 0.3043 | 0.4518 | 0.46777
0.29241 | 0.30429 | 0.45178 | 0.46777
0.29241 | 0.30427 | 0.45177 | 0.46775
0.29239 | 0.30426 | 0.45176 | 0.46774
0.29238 | 0.30425 | 0.45175 | 0.46774
0.29237 | 0.30424 | 0.45173 | 0.46773
0.29236 | 0.30423 | 0.45172 | 0.46773
0.29235 | 0.30421 | 0.45171 | 0.46772
0.29234 | 0.30421 | 0.45171 | 0.4677
0.29232 | 0.3042 | 0.45169 | 0.46768
0.29232 | 0.30419 | 0.45168 | 0.46768
0.2923 | 0.30419 | 0.45167 | 0.46766
0.29229 | 0.30417 | 0.45166 | 0.46766
0.29228 | 0.30416 | 0.45166 | 0.46765
0.29227 | 0.30416 | 0.45164 | 0.46764
0.29226 | 0.30415 | 0.45164 | 0.46763
0.29224 | 0.30414 | 0.45162 | 0.46762
0.29223 | 0.30413 | 0.45161 | 0.46761
0.29223 | 0.30412 | 0.4516 | 0.46759
0.29222 | 0.30411 | 0.45159 | 0.46758
0.29221 | 0.3041 | 0.45157 | 0.46757
0.2922 | 0.30409 | 0.45155 | 0.46756
0.29219 | 0.30408 | 0.45155 | 0.46756
0.29218 | 0.30407 | 0.45153 | 0.46755
0.29217 | 0.30406 | 0.45153 | 0.46753
0.29216 | 0.30406 | 0.45151 | 0.46751
0.29215 | 0.30404 | 0.45151 | 0.46751
0.29213 | 0.30403 | 0.45149 | 0.46749
0.29213 | 0.30403 | 0.45148 | 0.46749
0.29211 | 0.30402 | 0.45146 | 0.46748
0.2921 | 0.30401 | 0.45145 | 0.46747
0.29209 | 0.304 | 0.45144 | 0.46746
0.29208 | 0.304 | 0.45143 | 0.46745
0.29208 | 0.30399 | 0.45141 | 0.46744
0.29207 | 0.30397 | 0.4514 | 0.46743
0.29205 | 0.30396 | 0.45139 | 0.46742
0.29204 | 0.30396 | 0.45138 | 0.46742
0.29204 | 0.30395 | 0.45137 | 0.4674
0.29203 | 0.30394 | 0.45136 | 0.46739
0.29202 | 0.30393 | 0.45134 | 0.46738
0.29202 | 0.30392 | 0.45133 | 0.46738
0.292 | 0.30391 | 0.45133 | 0.46736
0.29199 | 0.3039 | 0.45131 | 0.46736
0.29198 | 0.30389 | 0.45131 | 0.46735
0.29197 | 0.30387 | 0.45129 | 0.46734
0.29196 | 0.30386 | 0.45127 | 0.46733
0.29196 | 0.30385 | 0.45126 | 0.46733
0.29195 | 0.30384 | 0.45125 | 0.46731
0.29194 | 0.30383 | 0.45124 | 0.4673
0.29192 | 0.30381 | 0.45124 | 0.46728
0.29191 | 0.30381 | 0.45122 | 0.46728
0.2919 | 0.3038 | 0.45121 | 0.46726
0.29189 | 0.30379 | 0.4512 | 0.46726
0.29188 | 0.30378 | 0.45119 | 0.46724
0.29186 | 0.30378 | 0.45118 | 0.46723
0.29185 | 0.30377 | 0.45117 | 0.46722
0.29184 | 0.30375 | 0.45115 | 0.46722
0.29183 | 0.30375 | 0.45115 | 0.46721
0.29182 | 0.30374 | 0.45113 | 0.46719
0.29181 | 0.30372 | 0.45112 | 0.46719
0.29181 | 0.30372 | 0.4511 | 0.46717
0.2918 | 0.3037 | 0.45109 | 0.46716
0.29178 | 0.30369 | 0.45108 | 0.46716
0.29178 | 0.30368 | 0.45106 | 0.46715
0.29177 | 0.30367 | 0.45105 | 0.46715
0.29176 | 0.30366 | 0.45104 | 0.46713
0.29175 | 0.30366 | 0.45102 | 0.46713
0.29174 | 0.30365 | 0.45102 | 0.46712
0.29173 | 0.30363 | 0.45101 | 0.46709
0.29173 | 0.30362 | 0.45099 | 0.46708
0.29172 | 0.30361 | 0.45098 | 0.46707
0.29171 | 0.3036 | 0.45096 | 0.46707
0.2917 | 0.30359 | 0.45095 | 0.46706
0.29169 | 0.30358 | 0.45094 | 0.46705
0.29169 | 0.30358 | 0.45093 | 0.46704
0.29168 | 0.30356 | 0.45092 | 0.46704
0.29167 | 0.30356 | 0.45092 | 0.46702
0.29166 | 0.30355 | 0.4509 | 0.46701
0.29165 | 0.30354 | 0.45089 | 0.467
0.29164 | 0.30353 | 0.45088 | 0.46699
0.29163 | 0.30351 | 0.45087 | 0.46698
0.29162 | 0.3035 | 0.45086 | 0.46697
0.2916 | 0.30349 | 0.45085 | 0.46696
0.29159 | 0.30348 | 0.45084 | 0.46695
0.29158 | 0.30347 | 0.45082 | 0.46694
0.29157 | 0.30346 | 0.45082 | 0.46693
0.29156 | 0.30344 | 0.4508 | 0.46692
0.29155 | 0.30343 | 0.4508 | 0.46691
0.29154 | 0.30342 | 0.45079 | 0.46691
0.29153 | 0.30341 | 0.45077 | 0.46689
0.29151 | 0.3034 | 0.45075 | 0.46689
0.2915 | 0.30339 | 0.45074 | 0.46687
0.29148 | 0.30337 | 0.45073 | 0.46686
0.29146 | 0.30336 | 0.45073 | 0.46685
0.29145 | 0.30336 | 0.45071 | 0.46684
0.29144 | 0.30335 | 0.4507 | 0.46683
0.29143 | 0.30334 | 0.45068 | 0.46682
0.29142 | 0.30332 | 0.45067 | 0.46681
0.29141 | 0.30331 | 0.45066 | 0.4668
0.2914 | 0.3033 | 0.45065 | 0.46679
0.29139 | 0.3033 | 0.45064 | 0.46678
0.29138 | 0.30328 | 0.45063 | 0.46677
0.29137 | 0.30327 | 0.45062 | 0.46676
0.29136 | 0.30327 | 0.45061 | 0.46676
0.29135 | 0.30325 | 0.4506 | 0.46675
0.29133 | 0.30324 | 0.45059 | 0.46673
0.29132 | 0.30323 | 0.45058 | 0.46672
0.29132 | 0.30322 | 0.45057 | 0.46671
0.29131 | 0.30321 | 0.45056 | 0.46669
0.2913 | 0.3032 | 0.45055 | 0.46669
0.29129 | 0.30318 | 0.45053 | 0.46668
0.29128 | 0.30318 | 0.45052 | 0.46667
0.29127 | 0.30317 | 0.45051 | 0.46666
0.29126 | 0.30316 | 0.45051 | 0.46666
0.29125 | 0.30315 | 0.4505 | 0.46664
0.29124 | 0.30315 | 0.45048 | 0.46664
0.29123 | 0.30314 | 0.45047 | 0.46663
0.29121 | 0.30313 | 0.45044 | 0.46662
0.2912 | 0.30311 | 0.45044 | 0.46661
0.2912 | 0.3031 | 0.45042 | 0.4666
0.29119 | 0.30309 | 0.45041 | 0.46658
0.29118 | 0.30308 | 0.4504 | 0.46657
0.29117 | 0.30307 | 0.45039 | 0.46656
0.29117 | 0.30306 | 0.45038 | 0.46655
0.29116 | 0.30306 | 0.45038 | 0.46654
0.29114 | 0.30305 | 0.45037 | 0.46652
0.29113 | 0.30304 | 0.45036 | 0.46651
0.29112 | 0.30303 | 0.45035 | 0.46651
0.2911 | 0.30302 | 0.45034 | 0.46649
0.29109 | 0.30301 | 0.45033 | 0.46649
0.29108 | 0.303 | 0.45032 | 0.46648
0.29107 | 0.30299 | 0.45031 | 0.46647
0.29105 | 0.30298 | 0.45031 | 0.46645
0.29104 | 0.30297 | 0.45029 | 0.46645
0.29103 | 0.30297 | 0.45028 | 0.46643
0.29102 | 0.30296 | 0.45027 | 0.46642
0.29101 | 0.30294 | 0.45025 | 0.46641
0.291 | 0.30293 | 0.45024 | 0.4664
0.29099 | 0.30292 | 0.45023 | 0.4664
0.29098 | 0.30291 | 0.45022 | 0.46638
0.29098 | 0.3029 | 0.45021 | 0.46638
0.29097 | 0.3029 | 0.4502 | 0.46637
0.29096 | 0.30289 | 0.45018 | 0.46636
0.29094 | 0.30288 | 0.45018 | 0.46635
0.29093 | 0.30287 | 0.45017 | 0.46634
0.29092 | 0.30287 | 0.45017 | 0.46634
0.29091 | 0.30285 | 0.45015 | 0.46633
0.2909 | 0.30285 | 0.45014 | 0.46632
0.29089 | 0.30284 | 0.45013 | 0.46631
0.29088 | 0.30283 | 0.45012 | 0.4663
0.29087 | 0.30281 | 0.45011 | 0.46629
0.29086 | 0.30281 | 0.4501 | 0.46628
0.29085 | 0.3028 | 0.45008 | 0.46627
0.29083 | 0.30279 | 0.45007 | 0.46625
0.29082 | 0.30278 | 0.45007 | 0.46625
0.29081 | 0.30277 | 0.45005 | 0.46623
0.29081 | 0.30276 | 0.45005 | 0.46623
0.2908 | 0.30275 | 0.45004 | 0.4662
0.29079 | 0.30274 | 0.45002 | 0.4662
0.29078 | 0.30273 | 0.45002 | 0.46619
0.29077 | 0.30272 | 0.45 | 0.46618
0.29076 | 0.30271 | 0.44999 | 0.46617
0.29076 | 0.3027 | 0.44998 | 0.46615
0.29074 | 0.30269 | 0.44997 | 0.46615
0.29074 | 0.30268 | 0.44995 | 0.46614
0.29073 | 0.30267 | 0.44995 | 0.46613
0.29072 | 0.30266 | 0.44991 | 0.46612
0.29071 | 0.30265 | 0.44991 | 0.46611
0.29071 | 0.30264 | 0.4499 | 0.4661
0.2907 | 0.30263 | 0.44989 | 0.46609
0.29069 | 0.30262 | 0.44987 | 0.46608
0.29068 | 0.30261 | 0.44986 | 0.46607
0.29067 | 0.3026 | 0.44984 | 0.46605
0.29066 | 0.30259 | 0.44983 | 0.46603
0.29065 | 0.30258 | 0.44982 | 0.46603
0.29064 | 0.30257 | 0.44981 | 0.46602
0.29062 | 0.30256 | 0.4498 | 0.46601
0.29061 | 0.30254 | 0.44979 | 0.466
0.2906 | 0.30253 | 0.44978 | 0.46599
0.29059 | 0.30252 | 0.44976 | 0.46598
0.29058 | 0.30251 | 0.44975 | 0.46597
0.29057 | 0.30251 | 0.44974 | 0.46596
0.29056 | 0.3025 | 0.44974 | 0.46595
0.29055 | 0.30249 | 0.44973 | 0.46593
0.29054 | 0.30248 | 0.44972 | 0.46592
0.29053 | 0.30247 | 0.44971 | 0.4659
0.29052 | 0.30246 | 0.44971 | 0.46589
0.29051 | 0.30245 | 0.44969 | 0.46587
0.2905 | 0.30244 | 0.44969 | 0.46586
0.29048 | 0.30243 | 0.44968 | 0.46585
0.29047 | 0.30243 | 0.44968 | 0.46583
0.29046 | 0.30242 | 0.44966 | 0.46583
0.29045 | 0.30241 | 0.44965 | 0.46581
0.29043 | 0.3024 | 0.44964 | 0.4658
0.29043 | 0.30239 | 0.44963 | 0.46579
0.29041 | 0.30238 | 0.44962 | 0.46577
0.29041 | 0.30237 | 0.44961 | 0.46577
0.29039 | 0.30236 | 0.4496 | 0.46575
0.29039 | 0.30235 | 0.44958 | 0.46574
0.29037 | 0.30234 | 0.44958 | 0.46573
0.29036 | 0.30233 | 0.44957 | 0.46571
0.29036 | 0.30232 | 0.44956 | 0.4657
0.29035 | 0.30232 | 0.44956 | 0.46569
0.29034 | 0.30231 | 0.44955 | 0.46568
0.29033 | 0.3023 | 0.44954 | 0.46567
0.29032 | 0.30229 | 0.44952 | 0.46565
0.2903 | 0.30228 | 0.44951 | 0.46565
0.29029 | 0.30227 | 0.4495 | 0.46564
0.29028 | 0.30226 | 0.44949 | 0.46562
0.29027 | 0.30225 | 0.44947 | 0.46561
0.29025 | 0.30224 | 0.44946 | 0.4656
0.29025 | 0.30223 | 0.44945 | 0.46559
0.29024 | 0.30222 | 0.44945 | 0.46558
0.29023 | 0.30221 | 0.44943 | 0.46558
0.29022 | 0.3022 | 0.44942 | 0.46557
0.29021 | 0.3022 | 0.44941 | 0.46556
0.2902 | 0.30219 | 0.4494 | 0.46555
0.29019 | 0.30218 | 0.44938 | 0.46554
0.29018 | 0.30217 | 0.44937 | 0.46553
0.29017 | 0.30216 | 0.44936 | 0.46552
0.29016 | 0.30215 | 0.44935 | 0.46551
0.29015 | 0.30214 | 0.44933 | 0.46549
0.29014 | 0.30213 | 0.44932 | 0.46549
0.29013 | 0.30212 | 0.44931 | 0.46548
0.29012 | 0.30211 | 0.4493 | 0.46547
0.29011 | 0.3021 | 0.44928 | 0.46546
0.2901 | 0.30209 | 0.44928 | 0.46545
0.29009 | 0.30208 | 0.44926 | 0.46544
0.29008 | 0.30207 | 0.44926 | 0.46543
0.29007 | 0.30206 | 0.44924 | 0.46542
0.29006 | 0.30205 | 0.44923 | 0.4654
0.29005 | 0.30204 | 0.44921 | 0.46539
0.29004 | 0.30203 | 0.44921 | 0.46539
0.29003 | 0.30202 | 0.4492 | 0.46538
0.29002 | 0.30201 | 0.44919 | 0.46537
0.29001 | 0.302 | 0.44917 | 0.46536
0.29 | 0.30198 | 0.44914 | 0.46534
0.28999 | 0.30198 | 0.44914 | 0.46534
0.28999 | 0.30197 | 0.44912 | 0.46533
0.28998 | 0.30196 | 0.4491 | 0.46532
0.28997 | 0.30195 | 0.4491 | 0.46531
0.28996 | 0.30195 | 0.44908 | 0.4653
0.28996 | 0.30193 | 0.44907 | 0.46529
0.28994 | 0.30193 | 0.44906 | 0.46528
0.28992 | 0.30192 | 0.44905 | 0.46528
0.28992 | 0.30191 | 0.44904 | 0.46526
0.28991 | 0.3019 | 0.44902 | 0.46525
0.2899 | 0.30189 | 0.44901 | 0.46524
0.2899 | 0.30188 | 0.449 | 0.46522
0.28989 | 0.30187 | 0.44899 | 0.46521
0.28988 | 0.30186 | 0.44898 | 0.4652
0.28987 | 0.30185 | 0.44897 | 0.46519
0.28986 | 0.30184 | 0.44896 | 0.46518
0.28985 | 0.30183 | 0.44894 | 0.46517
0.28984 | 0.30182 | 0.44893 | 0.46516
0.28983 | 0.3018 | 0.44892 | 0.46515
0.28982 | 0.30179 | 0.44891 | 0.46514
0.28981 | 0.30178 | 0.4489 | 0.46514
0.28979 | 0.30177 | 0.44889 | 0.46512
0.28978 | 0.30176 | 0.44888 | 0.46511
0.28977 | 0.30175 | 0.44887 | 0.46511
0.28976 | 0.30174 | 0.44886 | 0.4651
0.28975 | 0.30174 | 0.44885 | 0.46509
0.28974 | 0.30173 | 0.44885 | 0.46508
0.28973 | 0.30171 | 0.44884 | 0.46508
0.28971 | 0.30171 | 0.44883 | 0.46506
0.2897 | 0.3017 | 0.44882 | 0.46505
0.28969 | 0.30169 | 0.44881 | 0.46504
0.28968 | 0.30168 | 0.4488 | 0.46503
0.28967 | 0.30168 | 0.44879 | 0.46502
0.28966 | 0.30167 | 0.44878 | 0.465
0.28966 | 0.30166 | 0.44876 | 0.465
0.28966 | 0.30165 | 0.44876 | 0.46498
0.28964 | 0.30164 | 0.44875 | 0.46497
0.28963 | 0.30163 | 0.44874 | 0.46496
0.28962 | 0.30162 | 0.44873 | 0.46494
0.28961 | 0.30161 | 0.44872 | 0.46494
0.28961 | 0.30161 | 0.44871 | 0.46493
0.2896 | 0.3016 | 0.44869 | 0.46492
0.28959 | 0.30159 | 0.44868 | 0.46491
0.28958 | 0.30158 | 0.44867 | 0.4649
0.28957 | 0.30157 | 0.44865 | 0.4649
0.28956 | 0.30157 | 0.44865 | 0.46489
0.28955 | 0.30156 | 0.44863 | 0.46488
0.28955 | 0.30155 | 0.44863 | 0.46487
0.28954 | 0.30154 | 0.44862 | 0.46485
0.28953 | 0.30153 | 0.44862 | 0.46484
0.28952 | 0.30152 | 0.44861 | 0.46483
0.28951 | 0.30151 | 0.4486 | 0.46481
0.2895 | 0.3015 | 0.44859 | 0.46481
0.28949 | 0.3015 | 0.44857 | 0.46478
0.28948 | 0.30149 | 0.44856 | 0.46478
0.28947 | 0.30148 | 0.44854 | 0.46476
0.28947 | 0.30147 | 0.44853 | 0.46475
0.28946 | 0.30146 | 0.44851 | 0.46474
0.28945 | 0.30145 | 0.4485 | 0.46473
0.28943 | 0.30144 | 0.44849 | 0.46472
0.28942 | 0.30143 | 0.44848 | 0.4647
0.28941 | 0.30142 | 0.44847 | 0.46469
0.2894 | 0.30141 | 0.44846 | 0.46469
0.28939 | 0.3014 | 0.44844 | 0.46468
0.28938 | 0.30139 | 0.44844 | 0.46467
0.28938 | 0.30138 | 0.44842 | 0.46466
0.28937 | 0.30137 | 0.44841 | 0.46466
0.28936 | 0.30136 | 0.4484 | 0.46464
0.28935 | 0.30136 | 0.44839 | 0.46463
0.28934 | 0.30134 | 0.44838 | 0.46461
0.28933 | 0.30133 | 0.44838 | 0.46459
0.28932 | 0.30132 | 0.44836 | 0.46459
0.28931 | 0.30131 | 0.44834 | 0.46457
0.28931 | 0.3013 | 0.44834 | 0.46456
0.28929 | 0.30129 | 0.44832 | 0.46455
0.28928 | 0.30128 | 0.44831 | 0.46454
0.28927 | 0.30127 | 0.4483 | 0.46454
0.28926 | 0.30126 | 0.4483 | 0.46453
0.28925 | 0.30124 | 0.44829 | 0.46452
0.28924 | 0.30124 | 0.44828 | 0.46449
0.28923 | 0.30123 | 0.44826 | 0.46449
0.28922 | 0.30122 | 0.44826 | 0.46448
0.28921 | 0.30122 | 0.44824 | 0.46447
0.28919 | 0.3012 | 0.44824 | 0.46445
0.28919 | 0.30119 | 0.44823 | 0.46443
0.28918 | 0.30118 | 0.44821 | 0.46442
0.28917 | 0.30117 | 0.44821 | 0.46441
0.28916 | 0.30117 | 0.44819 | 0.46441
0.28916 | 0.30116 | 0.44818 | 0.4644
0.28916 | 0.30114 | 0.44816 | 0.46439
0.28915 | 0.30113 | 0.44815 | 0.46438
0.28914 | 0.30112 | 0.44814 | 0.46437
0.28913 | 0.30112 | 0.44812 | 0.46435
0.28913 | 0.30111 | 0.44811 | 0.46435
0.28912 | 0.3011 | 0.4481 | 0.46434
0.28911 | 0.30109 | 0.44809 | 0.46433
0.2891 | 0.30108 | 0.44807 | 0.46431
0.28909 | 0.30107 | 0.44806 | 0.4643
0.28908 | 0.30106 | 0.44806 | 0.46428
0.28907 | 0.30105 | 0.44804 | 0.46428
0.28905 | 0.30104 | 0.44803 | 0.46427
0.28904 | 0.30103 | 0.44803 | 0.46427
0.28903 | 0.30102 | 0.44801 | 0.46426
0.28903 | 0.30101 | 0.448 | 0.46425
0.28902 | 0.301 | 0.448 | 0.46424
0.28901 | 0.30099 | 0.44798 | 0.46423
0.289 | 0.30098 | 0.44797 | 0.46423
0.28898 | 0.30097 | 0.44796 | 0.46422
0.28897 | 0.30096 | 0.44795 | 0.46421
0.28896 | 0.30095 | 0.44794 | 0.46419
0.28896 | 0.30094 | 0.44792 | 0.46419
0.28895 | 0.30093 | 0.44792 | 0.46417
0.28894 | 0.30092 | 0.4479 | 0.46417
0.28892 | 0.30091 | 0.44789 | 0.46415
0.28891 | 0.3009 | 0.44788 | 0.46415
0.2889 | 0.30089 | 0.44788 | 0.46414
0.28889 | 0.30089 | 0.44785 | 0.46412
0.28889 | 0.30087 | 0.44784 | 0.46411
0.28888 | 0.30087 | 0.44783 | 0.4641
0.28887 | 0.30086 | 0.44782 | 0.4641
0.28886 | 0.30085 | 0.4478 | 0.46409
0.28885 | 0.30083 | 0.44779 | 0.46408
0.28884 | 0.30082 | 0.44777 | 0.46407
0.28883 | 0.30081 | 0.44776 | 0.46405
0.28881 | 0.30079 | 0.44776 | 0.46404
0.2888 | 0.30079 | 0.44775 | 0.46404
0.2888 | 0.30078 | 0.44774 | 0.46403
0.28879 | 0.30077 | 0.44773 | 0.46402
0.28878 | 0.30077 | 0.44771 | 0.46401
0.28878 | 0.30076 | 0.4477 | 0.46399
0.28877 | 0.30075 | 0.44769 | 0.46398
0.28876 | 0.30074 | 0.44768 | 0.46397
0.28875 | 0.30073 | 0.44766 | 0.46395
0.28875 | 0.30072 | 0.44765 | 0.46394
0.28874 | 0.30072 | 0.44764 | 0.46393
0.28873 | 0.30071 | 0.44763 | 0.46392
0.28872 | 0.3007 | 0.44762 | 0.46392
0.28871 | 0.3007 | 0.44761 | 0.46391
0.2887 | 0.30069 | 0.44761 | 0.46389
0.28869 | 0.30068 | 0.44759 | 0.46389
0.28868 | 0.30067 | 0.44758 | 0.46388
0.28867 | 0.30066 | 0.44756 | 0.46387
0.28866 | 0.30065 | 0.44755 | 0.46387
0.28864 | 0.30064 | 0.44754 | 0.46385
0.28863 | 0.30063 | 0.44752 | 0.46385
0.28863 | 0.30062 | 0.44751 | 0.46384
0.28861 | 0.30061 | 0.44751 | 0.46383
0.2886 | 0.30061 | 0.44749 | 0.46383
0.28859 | 0.30059 | 0.44748 | 0.46382
0.28858 | 0.30059 | 0.44747 | 0.4638
0.28857 | 0.30058 | 0.44745 | 0.4638
0.28857 | 0.30057 | 0.44744 | 0.46378
0.28856 | 0.30056 | 0.44743 | 0.46377
0.28855 | 0.30055 | 0.44742 | 0.46375
0.28854 | 0.30054 | 0.4474 | 0.46375
0.28853 | 0.30053 | 0.44739 | 0.46373
0.28853 | 0.30052 | 0.44738 | 0.46371
0.28851 | 0.30051 | 0.44737 | 0.46371
0.2885 | 0.3005 | 0.44736 | 0.4637
0.28849 | 0.30049 | 0.44735 | 0.46369
0.28848 | 0.30047 | 0.44734 | 0.46368
0.28847 | 0.30046 | 0.44733 | 0.46366
0.28846 | 0.30045 | 0.44732 | 0.46364
0.28845 | 0.30044 | 0.44731 | 0.46363
0.28844 | 0.30043 | 0.4473 | 0.46362
0.28843 | 0.30042 | 0.44729 | 0.46361
0.28841 | 0.30041 | 0.44728 | 0.46361
0.2884 | 0.3004 | 0.44727 | 0.46359
0.28839 | 0.30039 | 0.44726 | 0.46359
0.28839 | 0.30039 | 0.44725 | 0.46357
0.28838 | 0.30037 | 0.44724 | 0.46357
0.28837 | 0.30037 | 0.44722 | 0.46356
0.28836 | 0.30036 | 0.44721 | 0.46356
0.28835 | 0.30035 | 0.4472 | 0.46355
0.28834 | 0.30034 | 0.44718 | 0.46353
0.28833 | 0.30034 | 0.44718 | 0.46352
0.28832 | 0.30033 | 0.44716 | 0.46351
0.28831 | 0.30033 | 0.44714 | 0.4635
0.2883 | 0.30031 | 0.44713 | 0.46349
0.28829 | 0.30031 | 0.44713 | 0.46347
0.28828 | 0.3003 | 0.44711 | 0.46346
0.28827 | 0.30028 | 0.4471 | 0.46345
0.28827 | 0.30028 | 0.44709 | 0.46344
0.28826 | 0.30026 | 0.44709 | 0.46344
0.28825 | 0.30025 | 0.44707 | 0.46342
0.28824 | 0.30025 | 0.44705 | 0.46341
0.28823 | 0.30024 | 0.44704 | 0.4634
0.28822 | 0.30023 | 0.44703 | 0.46339
0.28821 | 0.30022 | 0.44702 | 0.46338
0.2882 | 0.3002 | 0.44701 | 0.46336
0.28819 | 0.30019 | 0.44701 | 0.46335
0.28818 | 0.30018 | 0.44699 | 0.46334
0.28817 | 0.30017 | 0.44698 | 0.46333
0.28816 | 0.30016 | 0.44697 | 0.46332
0.28815 | 0.30016 | 0.44696 | 0.46332
0.28814 | 0.30015 | 0.44695 | 0.46331
0.28812 | 0.30014 | 0.44695 | 0.4633
0.28812 | 0.30012 | 0.44694 | 0.46329
0.28811 | 0.30011 | 0.44692 | 0.46327
0.2881 | 0.3001 | 0.4469 | 0.46326
0.28809 | 0.3001 | 0.44689 | 0.46324
0.28808 | 0.30009 | 0.44688 | 0.46323
0.28808 | 0.30007 | 0.44687 | 0.46322
0.28807 | 0.30006 | 0.44686 | 0.46321
0.28806 | 0.30005 | 0.44685 | 0.4632
0.28805 | 0.30004 | 0.44683 | 0.4632
0.28804 | 0.30003 | 0.44682 | 0.46319
0.28803 | 0.30001 | 0.4468 | 0.46317
0.28802 | 0.29999 | 0.44679 | 0.46316
0.28801 | 0.29998 | 0.44679 | 0.46315
0.288 | 0.29997 | 0.44678 | 0.46313
0.288 | 0.29996 | 0.44676 | 0.46312
0.28798 | 0.29994 | 0.44676 | 0.46311
0.28797 | 0.29993 | 0.44674 | 0.46309
0.28796 | 0.29992 | 0.44673 | 0.46308
0.28795 | 0.29991 | 0.44672 | 0.46307
0.28794 | 0.2999 | 0.44671 | 0.46306
0.28793 | 0.29989 | 0.4467 | 0.46305
0.28792 | 0.29988 | 0.44669 | 0.46303
0.2879 | 0.29987 | 0.44668 | 0.46302
0.28789 | 0.29986 | 0.44666 | 0.46301
0.28788 | 0.29986 | 0.44666 | 0.463
0.28787 | 0.29985 | 0.44665 | 0.46299
0.28786 | 0.29984 | 0.44663 | 0.46298
0.28785 | 0.29983 | 0.44663 | 0.46297
0.28784 | 0.29982 | 0.44662 | 0.46296
0.28783 | 0.29981 | 0.44661 | 0.46295
0.28783 | 0.29979 | 0.4466 | 0.46294
0.28781 | 0.29978 | 0.44658 | 0.46293
0.28781 | 0.29977 | 0.44657 | 0.46292
0.2878 | 0.29976 | 0.44655 | 0.46291
0.28779 | 0.29976 | 0.44653 | 0.4629
0.28778 | 0.29975 | 0.44652 | 0.46289
0.28777 | 0.29974 | 0.44652 | 0.46289
0.28776 | 0.29973 | 0.44651 | 0.46288
0.28775 | 0.29972 | 0.44649 | 0.46286
0.28775 | 0.29971 | 0.44648 | 0.46286
0.28773 | 0.29969 | 0.44647 | 0.46285
0.28772 | 0.29968 | 0.44646 | 0.46284
0.28771 | 0.29967 | 0.44645 | 0.46283
0.28769 | 0.29966 | 0.44644 | 0.46282
0.28768 | 0.29965 | 0.44643 | 0.46281
0.28768 | 0.29964 | 0.44642 | 0.46279
0.28767 | 0.29963 | 0.44641 | 0.46279
0.28766 | 0.29962 | 0.4464 | 0.46277
0.28765 | 0.29961 | 0.44639 | 0.46276
0.28764 | 0.29961 | 0.44637 | 0.46275
0.28763 | 0.29959 | 0.44637 | 0.46275
0.28761 | 0.29958 | 0.44635 | 0.46274
0.2876 | 0.29957 | 0.44634 | 0.46273
0.28759 | 0.29956 | 0.44633 | 0.46272
0.28758 | 0.29955 | 0.44632 | 0.4627
0.28756 | 0.29955 | 0.44631 | 0.46269
0.28755 | 0.29954 | 0.4463 | 0.46268
0.28755 | 0.29953 | 0.44629 | 0.46266
0.28753 | 0.29952 | 0.44627 | 0.46265
0.28752 | 0.29952 | 0.44626 | 0.46264
0.28751 | 0.29951 | 0.44626 | 0.46263
0.2875 | 0.2995 | 0.44625 | 0.46262
0.28749 | 0.29949 | 0.44624 | 0.46261
0.28747 | 0.29948 | 0.44622 | 0.4626
0.28746 | 0.29947 | 0.44621 | 0.46259
0.28745 | 0.29945 | 0.4462 | 0.46258
0.28744 | 0.29944 | 0.44619 | 0.46258
0.28743 | 0.29944 | 0.44618 | 0.46257
0.28742 | 0.29943 | 0.44616 | 0.46256
0.28741 | 0.29942 | 0.44616 | 0.46254
0.28741 | 0.29941 | 0.44615 | 0.46254
0.2874 | 0.2994 | 0.44614 | 0.46253
0.28738 | 0.29939 | 0.44612 | 0.46252
0.28737 | 0.29938 | 0.44611 | 0.46251
0.28736 | 0.29937 | 0.4461 | 0.4625
0.28735 | 0.29936 | 0.44609 | 0.46248
0.28734 | 0.29935 | 0.44608 | 0.46248
0.28732 | 0.29934 | 0.44607 | 0.46246
0.28732 | 0.29933 | 0.44607 | 0.46246
0.28731 | 0.29931 | 0.44605 | 0.46245
0.28729 | 0.29931 | 0.44605 | 0.46243
0.28729 | 0.2993 | 0.44603 | 0.46243
0.28728 | 0.2993 | 0.44602 | 0.46242
0.28727 | 0.29928 | 0.44602 | 0.46241
0.28726 | 0.29927 | 0.446 | 0.4624
0.28725 | 0.29927 | 0.44599 | 0.4624
0.28724 | 0.29926 | 0.44598 | 0.46239
0.28723 | 0.29924 | 0.44597 | 0.46237
0.28722 | 0.29923 | 0.44596 | 0.46236
0.28721 | 0.29922 | 0.44594 | 0.46235
0.2872 | 0.29921 | 0.44593 | 0.46234
0.28719 | 0.29921 | 0.44592 | 0.46234
0.28719 | 0.2992 | 0.4459 | 0.46233
0.28718 | 0.29919 | 0.44589 | 0.46232
0.28717 | 0.29918 | 0.44588 | 0.46231
0.28716 | 0.29917 | 0.44586 | 0.4623
0.28715 | 0.29917 | 0.44585 | 0.46229
0.28714 | 0.29916 | 0.44585 | 0.46228
0.28713 | 0.29915 | 0.44583 | 0.46227
0.28712 | 0.29914 | 0.44582 | 0.46226
0.28711 | 0.29913 | 0.4458 | 0.46224
0.2871 | 0.29913 | 0.44579 | 0.46224
0.2871 | 0.29912 | 0.44577 | 0.46223
0.28709 | 0.29911 | 0.44575 | 0.46223
0.28708 | 0.2991 | 0.44573 | 0.46222
0.28706 | 0.29909 | 0.44572 | 0.4622
0.28706 | 0.29908 | 0.44571 | 0.46219
0.28705 | 0.29907 | 0.4457 | 0.46217
0.28704 | 0.29906 | 0.44569 | 0.46217
0.28703 | 0.29905 | 0.44569 | 0.46216
0.28702 | 0.29904 | 0.44567 | 0.46214
0.28701 | 0.29903 | 0.44566 | 0.46214
0.287 | 0.29901 | 0.44565 | 0.46212
0.28699 | 0.299 | 0.44564 | 0.46211
0.28699 | 0.29899 | 0.44563 | 0.4621
0.28698 | 0.29898 | 0.44563 | 0.46209
0.28697 | 0.29897 | 0.44562 | 0.46208
0.28696 | 0.29896 | 0.44561 | 0.46207
0.28694 | 0.29895 | 0.4456 | 0.46205
0.28694 | 0.29895 | 0.44559 | 0.46204
0.28693 | 0.29894 | 0.44558 | 0.46204
0.28692 | 0.29894 | 0.44557 | 0.46202
0.28691 | 0.29893 | 0.44556 | 0.46201
0.2869 | 0.29892 | 0.44555 | 0.46201
0.2869 | 0.29891 | 0.44554 | 0.462
0.28689 | 0.2989 | 0.44553 | 0.46199
0.28688 | 0.29889 | 0.44551 | 0.46198
0.28687 | 0.29888 | 0.4455 | 0.46198
0.28686 | 0.29887 | 0.4455 | 0.46197
0.28685 | 0.29886 | 0.44548 | 0.46195
0.28684 | 0.29885 | 0.44547 | 0.46194
0.28683 | 0.29885 | 0.44546 | 0.46193
0.28683 | 0.29884 | 0.44545 | 0.46192
0.28681 | 0.29883 | 0.44544 | 0.4619
0.28681 | 0.29882 | 0.44543 | 0.46189
0.2868 | 0.29881 | 0.44542 | 0.46188
0.28679 | 0.2988 | 0.44541 | 0.46187
0.28678 | 0.29879 | 0.4454 | 0.46186
0.28677 | 0.29878 | 0.44539 | 0.46183
0.28676 | 0.29877 | 0.44538 | 0.46182
0.28675 | 0.29875 | 0.44538 | 0.46182
0.28673 | 0.29874 | 0.44537 | 0.46181
0.28672 | 0.29873 | 0.44536 | 0.46179
0.28671 | 0.29872 | 0.44535 | 0.46178
0.2867 | 0.29871 | 0.44535 | 0.46176
0.28669 | 0.29871 | 0.44532 | 0.46176
0.28669 | 0.2987 | 0.44531 | 0.46174
0.28668 | 0.29869 | 0.4453 | 0.46173
0.28667 | 0.29868 | 0.44529 | 0.46173
0.28665 | 0.29867 | 0.44527 | 0.46171
0.28664 | 0.29866 | 0.44526 | 0.46171
0.28663 | 0.29866 | 0.44525 | 0.46169
0.28662 | 0.29865 | 0.44524 | 0.46169
0.28661 | 0.29864 | 0.44522 | 0.46167
0.2866 | 0.29863 | 0.44522 | 0.46165
0.28659 | 0.29863 | 0.44521 | 0.46163
0.28658 | 0.29861 | 0.44519 | 0.46162
0.28657 | 0.29861 | 0.44519 | 0.46161
0.28656 | 0.2986 | 0.44518 | 0.4616
0.28654 | 0.29859 | 0.44517 | 0.4616
0.28653 | 0.29858 | 0.44515 | 0.46158
0.28652 | 0.29857 | 0.44514 | 0.46158
0.28652 | 0.29856 | 0.44513 | 0.46157
0.28651 | 0.29854 | 0.44512 | 0.46156
0.2865 | 0.29854 | 0.4451 | 0.46156
0.28649 | 0.29852 | 0.44509 | 0.46154
0.28648 | 0.29851 | 0.44508 | 0.46153
0.28647 | 0.2985 | 0.44507 | 0.46152
0.28646 | 0.29849 | 0.44506 | 0.46151
0.28645 | 0.29848 | 0.44505 | 0.4615
0.28643 | 0.29847 | 0.44504 | 0.46149
0.28642 | 0.29846 | 0.44502 | 0.46147
0.28641 | 0.29845 | 0.44501 | 0.46146
0.2864 | 0.29844 | 0.445 | 0.46145
0.28639 | 0.29843 | 0.44498 | 0.46144
0.28637 | 0.29842 | 0.44498 | 0.46141
0.28637 | 0.2984 | 0.44496 | 0.4614
0.28636 | 0.2984 | 0.44495 | 0.4614
0.28634 | 0.29838 | 0.44494 | 0.46138
0.28634 | 0.29837 | 0.44493 | 0.46138
0.28633 | 0.29836 | 0.44492 | 0.46137
0.28632 | 0.29835 | 0.4449 | 0.46136
0.28631 | 0.29834 | 0.44489 | 0.46135
0.2863 | 0.29833 | 0.44488 | 0.46133
0.2863 | 0.29832 | 0.44488 | 0.46132
0.28628 | 0.2983 | 0.44486 | 0.46131
0.28627 | 0.29829 | 0.44485 | 0.46131
0.28626 | 0.29829 | 0.44483 | 0.46129
0.28625 | 0.29827 | 0.44482 | 0.46128
0.28624 | 0.29826 | 0.44481 | 0.46128
0.28623 | 0.29825 | 0.4448 | 0.46127
0.28622 | 0.29825 | 0.44478 | 0.46126
0.28621 | 0.29824 | 0.44477 | 0.46124
0.2862 | 0.29822 | 0.44477 | 0.46123
0.28619 | 0.29821 | 0.44475 | 0.46122
0.28619 | 0.29821 | 0.44474 | 0.46121
0.28618 | 0.2982 | 0.44474 | 0.46119
0.28617 | 0.29819 | 0.44473 | 0.46119
0.28615 | 0.29819 | 0.44472 | 0.46117
0.28615 | 0.29818 | 0.44471 | 0.46116
0.28614 | 0.29817 | 0.44469 | 0.46115
0.28613 | 0.29816 | 0.44469 | 0.46114
0.28612 | 0.29815 | 0.44467 | 0.46113
0.28611 | 0.29814 | 0.44466 | 0.46113
0.2861 | 0.29813 | 0.44465 | 0.46112
0.28609 | 0.29812 | 0.44464 | 0.46111
0.28608 | 0.29812 | 0.44463 | 0.46109
0.28607 | 0.29811 | 0.44462 | 0.46108
0.28607 | 0.29809 | 0.4446 | 0.46107
0.28606 | 0.29808 | 0.4446 | 0.46106
0.28605 | 0.29807 | 0.44458 | 0.46105
0.28604 | 0.29806 | 0.44458 | 0.46104
0.28603 | 0.29806 | 0.44456 | 0.46102
0.28602 | 0.29805 | 0.44455 | 0.46101
0.286 | 0.29804 | 0.44454 | 0.461
0.28599 | 0.29803 | 0.44453 | 0.461
0.28598 | 0.29802 | 0.44452 | 0.46098
0.28597 | 0.29801 | 0.4445 | 0.46097
0.28596 | 0.29801 | 0.44449 | 0.46096
0.28595 | 0.298 | 0.44448 | 0.46094
0.28594 | 0.298 | 0.44447 | 0.46094
0.28593 | 0.29799 | 0.44446 | 0.46093
0.28592 | 0.29798 | 0.44445 | 0.46092
0.28591 | 0.29797 | 0.44444 | 0.46091
0.28589 | 0.29796 | 0.44443 | 0.46091
0.28588 | 0.29795 | 0.44441 | 0.46089
0.28587 | 0.29794 | 0.44441 | 0.46088
0.28586 | 0.29793 | 0.44441 | 0.46088
0.28585 | 0.29791 | 0.4444 | 0.46086
0.28585 | 0.29791 | 0.44438 | 0.46085
0.28584 | 0.2979 | 0.44438 | 0.46085
0.28583 | 0.29789 | 0.44437 | 0.46083
0.28582 | 0.29788 | 0.44436 | 0.46082
0.28581 | 0.29787 | 0.44434 | 0.46081
0.2858 | 0.29786 | 0.44433 | 0.4608
0.28579 | 0.29784 | 0.44432 | 0.46079
0.28578 | 0.29784 | 0.44431 | 0.46078
0.28577 | 0.29783 | 0.44431 | 0.46077
0.28576 | 0.29782 | 0.44429 | 0.46076
0.28575 | 0.29781 | 0.44427 | 0.46075
0.28574 | 0.2978 | 0.44426 | 0.46074
0.28573 | 0.2978 | 0.44424 | 0.46073
0.28572 | 0.29778 | 0.44424 | 0.46073
0.28571 | 0.29777 | 0.44422 | 0.46071
0.2857 | 0.29776 | 0.44421 | 0.4607
0.28569 | 0.29775 | 0.4442 | 0.46069
0.28568 | 0.29775 | 0.44419 | 0.46067
0.28567 | 0.29774 | 0.44417 | 0.46067
0.28566 | 0.29773 | 0.44416 | 0.46066
0.28566 | 0.29771 | 0.44415 | 0.46065
0.28565 | 0.2977 | 0.44414 | 0.46064
0.28564 | 0.29769 | 0.44412 | 0.46063
0.28563 | 0.29769 | 0.44412 | 0.46061
0.28562 | 0.29767 | 0.44411 | 0.46061
0.28562 | 0.29766 | 0.44409 | 0.46059
0.28561 | 0.29765 | 0.44407 | 0.46058
0.2856 | 0.29765 | 0.44407 | 0.46057
0.28559 | 0.29763 | 0.44406 | 0.46056
0.28558 | 0.29762 | 0.44404 | 0.46056
0.28557 | 0.29761 | 0.44404 | 0.46054
0.28557 | 0.2976 | 0.44402 | 0.46053
0.28556 | 0.2976 | 0.44401 | 0.46052
0.28555 | 0.29759 | 0.444 | 0.46051
0.28554 | 0.29758 | 0.444 | 0.46049
0.28553 | 0.29757 | 0.44398 | 0.46049
0.28551 | 0.29756 | 0.44398 | 0.46048
0.2855 | 0.29755 | 0.44397 | 0.46046
0.2855 | 0.29754 | 0.44395 | 0.46046
0.28549 | 0.29753 | 0.44394 | 0.46045
0.28548 | 0.29753 | 0.44392 | 0.46043
0.28547 | 0.29752 | 0.44392 | 0.46043
0.28547 | 0.29751 | 0.44391 | 0.46042
0.28546 | 0.2975 | 0.4439 | 0.46041
0.28545 | 0.29749 | 0.44388 | 0.46039
0.28544 | 0.29749 | 0.44387 | 0.46039
0.28543 | 0.29748 | 0.44386 | 0.46038
0.28542 | 0.29746 | 0.44385 | 0.46037
0.2854 | 0.29745 | 0.44385 | 0.46035
0.28539 | 0.29745 | 0.44384 | 0.46035
0.28538 | 0.29744 | 0.44383 | 0.46034
0.28537 | 0.29743 | 0.44381 | 0.46032
0.28536 | 0.29741 | 0.4438 | 0.4603
0.28535 | 0.29741 | 0.44379 | 0.46029
0.28534 | 0.2974 | 0.44377 | 0.46028
0.28533 | 0.29739 | 0.44376 | 0.46027
0.28532 | 0.29738 | 0.44376 | 0.46026
0.28531 | 0.29738 | 0.44375 | 0.46025
0.28531 | 0.29737 | 0.44373 | 0.46023
0.2853 | 0.29736 | 0.44372 | 0.46022
0.28528 | 0.29735 | 0.4437 | 0.4602
0.28528 | 0.29734 | 0.4437 | 0.46019
0.28527 | 0.29733 | 0.44368 | 0.46018
0.28526 | 0.29731 | 0.44367 | 0.46016
0.28526 | 0.29731 | 0.44365 | 0.46016
0.28525 | 0.2973 | 0.44364 | 0.46015
0.28523 | 0.29728 | 0.44362 | 0.46014
0.28523 | 0.29728 | 0.44361 | 0.46013
0.28521 | 0.29728 | 0.4436 | 0.46012
0.28519 | 0.29727 | 0.44359 | 0.46011
0.28519 | 0.29726 | 0.44358 | 0.4601
0.28518 | 0.29725 | 0.44357 | 0.46008
0.28517 | 0.29724 | 0.44356 | 0.46008
0.28516 | 0.29723 | 0.44355 | 0.46007
0.28516 | 0.29722 | 0.44353 | 0.46006
0.28514 | 0.29721 | 0.44352 | 0.46004
0.28513 | 0.29721 | 0.44351 | 0.46004
0.28512 | 0.2972 | 0.4435 | 0.46002
0.28511 | 0.29719 | 0.44349 | 0.46001
0.2851 | 0.29718 | 0.44348 | 0.46
0.28509 | 0.29717 | 0.44347 | 0.45999
0.28507 | 0.29716 | 0.44346 | 0.45998
0.28506 | 0.29715 | 0.44345 | 0.45998
0.28505 | 0.29713 | 0.44344 | 0.45996
0.28504 | 0.29712 | 0.44342 | 0.45995
0.28503 | 0.29711 | 0.44342 | 0.45994
0.28502 | 0.2971 | 0.44341 | 0.45993
0.28501 | 0.2971 | 0.44339 | 0.45991
0.28499 | 0.29709 | 0.44338 | 0.45991
0.28498 | 0.29708 | 0.44337 | 0.45989
0.28498 | 0.29707 | 0.44336 | 0.45988
0.28497 | 0.29705 | 0.44335 | 0.45987
0.28496 | 0.29704 | 0.44334 | 0.45986
0.28495 | 0.29703 | 0.44333 | 0.45985
0.28494 | 0.29702 | 0.4433 | 0.45983
0.28493 | 0.29701 | 0.44329 | 0.45982
0.28492 | 0.297 | 0.44328 | 0.45981
0.28491 | 0.29699 | 0.44328 | 0.45981
0.2849 | 0.29698 | 0.44326 | 0.4598
0.28489 | 0.29698 | 0.44325 | 0.45979
0.28488 | 0.29697 | 0.44323 | 0.45978
0.28487 | 0.29696 | 0.44322 | 0.45977
0.28486 | 0.29695 | 0.44321 | 0.45975
0.28485 | 0.29694 | 0.44319 | 0.45975
0.28484 | 0.29692 | 0.44319 | 0.45973
0.28483 | 0.29692 | 0.44317 | 0.45973
0.28483 | 0.29691 | 0.44315 | 0.45971
0.28482 | 0.2969 | 0.44315 | 0.4597
0.28481 | 0.29689 | 0.44313 | 0.45969
0.2848 | 0.29689 | 0.44312 | 0.45967
0.28479 | 0.29688 | 0.44311 | 0.45966
0.28479 | 0.29687 | 0.4431 | 0.45965
0.28478 | 0.29686 | 0.44309 | 0.45965
0.28477 | 0.29685 | 0.44308 | 0.45964
0.28476 | 0.29683 | 0.44306 | 0.45963
0.28475 | 0.29683 | 0.44305 | 0.45961
0.28474 | 0.29682 | 0.44305 | 0.4596
0.28473 | 0.29682 | 0.44303 | 0.45959
0.28472 | 0.29681 | 0.44301 | 0.45958
0.2847 | 0.2968 | 0.44301 | 0.45957
0.2847 | 0.29679 | 0.44299 | 0.45956
0.28469 | 0.29679 | 0.44298 | 0.45955
0.28468 | 0.29678 | 0.44297 | 0.45955
0.28467 | 0.29677 | 0.44296 | 0.45953
0.28466 | 0.29676 | 0.44295 | 0.45951
0.28466 | 0.29675 | 0.44294 | 0.4595
0.28465 | 0.29674 | 0.44293 | 0.45949
0.28464 | 0.29673 | 0.44292 | 0.45948
0.28464 | 0.29672 | 0.4429 | 0.45947
0.28463 | 0.29672 | 0.4429 | 0.45946
0.28462 | 0.29671 | 0.44288 | 0.45945
0.28461 | 0.2967 | 0.44287 | 0.45944
0.2846 | 0.29668 | 0.44286 | 0.45943
0.2846 | 0.29667 | 0.44285 | 0.45943
0.28459 | 0.29665 | 0.44283 | 0.45941
0.28458 | 0.29664 | 0.44283 | 0.4594
0.28457 | 0.29664 | 0.44281 | 0.45938
0.28456 | 0.29662 | 0.44281 | 0.45938
0.28455 | 0.29662 | 0.4428 | 0.45937
0.28454 | 0.29661 | 0.44279 | 0.45935
0.28452 | 0.2966 | 0.44278 | 0.45935
0.28451 | 0.29659 | 0.44276 | 0.45934
0.2845 | 0.29657 | 0.44276 | 0.45933
0.28449 | 0.29657 | 0.44275 | 0.45933
0.28448 | 0.29656 | 0.44274 | 0.45931
0.28446 | 0.29655 | 0.44273 | 0.45931
0.28446 | 0.29654 | 0.44273 | 0.4593
0.28445 | 0.29653 | 0.44271 | 0.45928
0.28443 | 0.29653 | 0.4427 | 0.45926
0.28442 | 0.29651 | 0.44269 | 0.45926
0.28441 | 0.29651 | 0.44268 | 0.45925
0.28441 | 0.2965 | 0.44266 | 0.45924
0.2844 | 0.29649 | 0.44266 | 0.45923
0.28439 | 0.29648 | 0.44264 | 0.45922
0.28438 | 0.29647 | 0.44263 | 0.4592
0.28437 | 0.29647 | 0.44262 | 0.4592
0.28436 | 0.29646 | 0.44261 | 0.45919
0.28435 | 0.29645 | 0.4426 | 0.45918
0.28434 | 0.29644 | 0.44259 | 0.45916
0.28434 | 0.29643 | 0.44258 | 0.45915
0.28433 | 0.29642 | 0.44257 | 0.45914
0.28432 | 0.29641 | 0.44256 | 0.45913
0.28431 | 0.29641 | 0.44255 | 0.45912
0.2843 | 0.29639 | 0.44255 | 0.45911
0.28429 | 0.29638 | 0.44253 | 0.4591
0.28428 | 0.29637 | 0.44253 | 0.45909
0.28427 | 0.29637 | 0.44252 | 0.45908
0.28425 | 0.29635 | 0.44251 | 0.45907
0.28424 | 0.29634 | 0.4425 | 0.45906
0.28423 | 0.29633 | 0.44249 | 0.45905
0.28422 | 0.29632 | 0.44248 | 0.45905
0.28422 | 0.29631 | 0.44246 | 0.45903
0.28421 | 0.2963 | 0.44245 | 0.45903
0.2842 | 0.2963 | 0.44243 | 0.45901
0.28419 | 0.29629 | 0.44242 | 0.459
0.28417 | 0.29628 | 0.4424 | 0.459
0.28416 | 0.29627 | 0.4424 | 0.45899
0.28415 | 0.29626 | 0.44239 | 0.45897
0.28414 | 0.29624 | 0.44237 | 0.45897
0.28413 | 0.29623 | 0.44236 | 0.45896
0.28411 | 0.29623 | 0.44235 | 0.45895
0.28411 | 0.29622 | 0.44232 | 0.45894
0.2841 | 0.29621 | 0.44232 | 0.45893
0.28409 | 0.2962 | 0.4423 | 0.45893
0.28408 | 0.29619 | 0.44229 | 0.45892
0.28407 | 0.29618 | 0.44228 | 0.45891
0.28406 | 0.29617 | 0.44226 | 0.4589
0.28405 | 0.29615 | 0.44226 | 0.4589
0.28404 | 0.29615 | 0.44224 | 0.45889
0.28403 | 0.29614 | 0.44222 | 0.45888
0.28403 | 0.29613 | 0.44221 | 0.45887
0.28401 | 0.29613 | 0.44221 | 0.45886
0.284 | 0.29612 | 0.4422 | 0.45885
0.28399 | 0.29611 | 0.44219 | 0.45884
0.28398 | 0.2961 | 0.44217 | 0.45882
0.28397 | 0.29609 | 0.44217 | 0.45882
0.28395 | 0.29608 | 0.44216 | 0.45881
0.28394 | 0.29607 | 0.44214 | 0.4588
0.28393 | 0.29607 | 0.44213 | 0.45879
0.28393 | 0.29606 | 0.44212 | 0.45879
0.28391 | 0.29605 | 0.44211 | 0.45878
0.28391 | 0.29604 | 0.4421 | 0.45877
0.2839 | 0.29603 | 0.44209 | 0.45875
0.28389 | 0.29602 | 0.44208 | 0.45875
0.28388 | 0.29602 | 0.44207 | 0.45873
0.28387 | 0.29601 | 0.44205 | 0.45872
0.28386 | 0.296 | 0.44203 | 0.45871
0.28385 | 0.29599 | 0.44202 | 0.45871
0.28385 | 0.29598 | 0.44201 | 0.45869
0.28384 | 0.29597 | 0.44199 | 0.45868
0.28383 | 0.29596 | 0.44199 | 0.45867
0.28382 | 0.29596 | 0.44197 | 0.45866
0.28381 | 0.29595 | 0.44196 | 0.45865
0.2838 | 0.29593 | 0.44195 | 0.45865
0.28379 | 0.29592 | 0.44194 | 0.45863
0.28378 | 0.29591 | 0.44194 | 0.45863
0.28377 | 0.2959 | 0.44193 | 0.45862
0.28376 | 0.29589 | 0.44192 | 0.4586
0.28375 | 0.29588 | 0.4419 | 0.4586
0.28373 | 0.29587 | 0.44189 | 0.45859
0.28372 | 0.29586 | 0.44188 | 0.45858
0.28371 | 0.29586 | 0.44188 | 0.45857
0.2837 | 0.29585 | 0.44186 | 0.45856
0.28369 | 0.29584 | 0.44185 | 0.45854
0.28368 | 0.29583 | 0.44184 | 0.45852
0.28366 | 0.29581 | 0.44184 | 0.45852
0.28365 | 0.29581 | 0.44183 | 0.45851
0.28364 | 0.2958 | 0.44181 | 0.4585
0.28363 | 0.29579 | 0.44179 | 0.45849
0.28363 | 0.29578 | 0.44178 | 0.45848
0.28362 | 0.29577 | 0.44177 | 0.45848
0.28361 | 0.29576 | 0.44176 | 0.45847
0.28359 | 0.29575 | 0.44175 | 0.45846
0.28359 | 0.29574 | 0.44173 | 0.45845
0.28358 | 0.29573 | 0.44171 | 0.45844
0.28357 | 0.29572 | 0.44171 | 0.45843
0.28356 | 0.29571 | 0.4417 | 0.45843
0.28355 | 0.29571 | 0.44167 | 0.45842
0.28354 | 0.2957 | 0.44167 | 0.45841
0.28353 | 0.29569 | 0.44166 | 0.45839
0.28352 | 0.29568 | 0.44165 | 0.45839
0.28352 | 0.29567 | 0.44164 | 0.45838
0.28351 | 0.29565 | 0.44163 | 0.45837
0.2835 | 0.29565 | 0.44162 | 0.45836
0.28349 | 0.29564 | 0.44161 | 0.45835
0.28348 | 0.29563 | 0.44161 | 0.45834
0.28348 | 0.29562 | 0.4416 | 0.45833
0.28346 | 0.29561 | 0.44159 | 0.45832
0.28345 | 0.29561 | 0.44158 | 0.45832
0.28344 | 0.2956 | 0.44157 | 0.45829
0.28343 | 0.29559 | 0.44156 | 0.45828
0.28342 | 0.29558 | 0.44153 | 0.45827
0.28341 | 0.29557 | 0.44153 | 0.45826
0.2834 | 0.29556 | 0.44151 | 0.45825
0.28339 | 0.29556 | 0.44151 | 0.45824
0.28338 | 0.29555 | 0.4415 | 0.45823
0.28337 | 0.29554 | 0.44149 | 0.45822
0.28336 | 0.29553 | 0.44147 | 0.45821
0.28335 | 0.29551 | 0.44146 | 0.4582
0.28334 | 0.2955 | 0.44145 | 0.45819
0.28333 | 0.29549 | 0.44145 | 0.45818
0.28331 | 0.29549 | 0.44142 | 0.45817
0.28331 | 0.29548 | 0.44141 | 0.45816
0.28329 | 0.29547 | 0.4414 | 0.45815
0.28328 | 0.29546 | 0.44139 | 0.45814
0.28328 | 0.29545 | 0.44138 | 0.45813
0.28326 | 0.29544 | 0.44138 | 0.45813
0.28326 | 0.29543 | 0.44135 | 0.45812
0.28325 | 0.29542 | 0.44134 | 0.45812
0.28324 | 0.29541 | 0.44132 | 0.45811
0.28323 | 0.2954 | 0.44132 | 0.45809
0.28323 | 0.29539 | 0.4413 | 0.45809
0.28321 | 0.29538 | 0.4413 | 0.45807
0.2832 | 0.29538 | 0.44129 | 0.45807
0.28319 | 0.29537 | 0.44128 | 0.45805
0.28318 | 0.29536 | 0.44126 | 0.45804
0.28317 | 0.29535 | 0.44126 | 0.45803
0.28316 | 0.29534 | 0.44123 | 0.45803
0.28315 | 0.29533 | 0.44122 | 0.45802
0.28314 | 0.29532 | 0.44121 | 0.45801
0.28314 | 0.2953 | 0.4412 | 0.458
0.28313 | 0.2953 | 0.44118 | 0.45799
0.28312 | 0.29529 | 0.44118 | 0.45799
0.28311 | 0.29528 | 0.44117 | 0.45797
0.2831 | 0.29527 | 0.44115 | 0.45796
0.28309 | 0.29527 | 0.44114 | 0.45795
0.28308 | 0.29526 | 0.44114 | 0.45795
0.28307 | 0.29526 | 0.44112 | 0.45794
0.28306 | 0.29525 | 0.44111 | 0.45792
0.28305 | 0.29524 | 0.4411 | 0.45792
0.28304 | 0.29523 | 0.44108 | 0.45791
0.28303 | 0.29522 | 0.44108 | 0.45789
0.28302 | 0.29522 | 0.44106 | 0.45788
0.28301 | 0.29521 | 0.44104 | 0.45788
0.283 | 0.2952 | 0.44104 | 0.45786
0.28299 | 0.29519 | 0.44102 | 0.45786
0.28297 | 0.29518 | 0.44102 | 0.45785
0.28297 | 0.29517 | 0.441 | 0.45784
0.28295 | 0.29516 | 0.44099 | 0.45783
0.28294 | 0.29515 | 0.44097 | 0.45781
0.28294 | 0.29515 | 0.44096 | 0.45781
0.28292 | 0.29514 | 0.44095 | 0.4578
0.28292 | 0.29513 | 0.44095 | 0.45779
0.28291 | 0.29512 | 0.44094 | 0.45778
0.2829 | 0.29511 | 0.44093 | 0.45777
0.28289 | 0.2951 | 0.44091 | 0.45776
0.28289 | 0.29508 | 0.4409 | 0.45775
0.28288 | 0.29506 | 0.4409 | 0.45774
0.28287 | 0.29506 | 0.44089 | 0.45772
0.28287 | 0.29505 | 0.44088 | 0.45771
0.28286 | 0.29504 | 0.44087 | 0.45771
0.28285 | 0.29502 | 0.44085 | 0.45769
0.28284 | 0.29501 | 0.44084 | 0.45768
0.28283 | 0.29501 | 0.44083 | 0.45767
0.28283 | 0.295 | 0.44082 | 0.45766
0.28282 | 0.29499 | 0.44082 | 0.45764
0.28281 | 0.29498 | 0.44081 | 0.45764
0.2828 | 0.29497 | 0.44079 | 0.45762
0.28279 | 0.29496 | 0.44078 | 0.45762
0.28278 | 0.29495 | 0.44077 | 0.45761
0.28278 | 0.29494 | 0.44077 | 0.4576
0.28277 | 0.29493 | 0.44075 | 0.4576
0.28276 | 0.29492 | 0.44074 | 0.45759
0.28275 | 0.29491 | 0.44073 | 0.45758
0.28273 | 0.2949 | 0.44073 | 0.45757
0.28272 | 0.29489 | 0.44071 | 0.45756
0.28271 | 0.29488 | 0.4407 | 0.45756
0.28269 | 0.29487 | 0.44068 | 0.45755
0.28268 | 0.29486 | 0.44068 | 0.45753
0.28267 | 0.29486 | 0.44067 | 0.45753
0.28266 | 0.29485 | 0.44065 | 0.45752
0.28266 | 0.29484 | 0.44064 | 0.45751
0.28265 | 0.29483 | 0.44062 | 0.4575
0.28263 | 0.29482 | 0.44061 | 0.45749
0.28262 | 0.29479 | 0.44059 | 0.45748
0.28261 | 0.29478 | 0.44059 | 0.45747
0.2826 | 0.29478 | 0.44058 | 0.45746
0.28259 | 0.29477 | 0.44057 | 0.45746
0.28258 | 0.29476 | 0.44056 | 0.45745
0.28257 | 0.29475 | 0.44055 | 0.45745
0.28256 | 0.29474 | 0.44054 | 0.45744
0.28255 | 0.29473 | 0.44053 | 0.45743
0.28254 | 0.29471 | 0.44052 | 0.45742
0.28253 | 0.2947 | 0.44051 | 0.45741
0.28252 | 0.29469 | 0.44049 | 0.4574
0.2825 | 0.29468 | 0.44048 | 0.4574
0.28249 | 0.29467 | 0.44047 | 0.45738
0.28248 | 0.29466 | 0.44046 | 0.45737
0.28247 | 0.29465 | 0.44045 | 0.45737
0.28246 | 0.29464 | 0.44044 | 0.45736
0.28245 | 0.29463 | 0.44043 | 0.45735
0.28244 | 0.29462 | 0.44042 | 0.45734
0.28243 | 0.29461 | 0.44041 | 0.45733
0.28242 | 0.2946 | 0.4404 | 0.45731
0.28241 | 0.29459 | 0.44039 | 0.4573
0.28241 | 0.29458 | 0.44038 | 0.4573
0.2824 | 0.29457 | 0.44037 | 0.45728
0.28239 | 0.29456 | 0.44037 | 0.45728
0.28238 | 0.29454 | 0.44036 | 0.45726
0.28237 | 0.29453 | 0.44035 | 0.45725
0.28236 | 0.29452 | 0.44034 | 0.45723
0.28236 | 0.29451 | 0.44033 | 0.45723
0.28235 | 0.2945 | 0.44032 | 0.45721
0.28234 | 0.29449 | 0.44031 | 0.4572
0.28233 | 0.29448 | 0.44029 | 0.4572
0.28233 | 0.29447 | 0.44029 | 0.45719
0.28232 | 0.29446 | 0.44028 | 0.45718
0.28231 | 0.29446 | 0.44026 | 0.45717
0.2823 | 0.29445 | 0.44025 | 0.45717
0.28229 | 0.29444 | 0.44023 | 0.45716
0.28228 | 0.29443 | 0.44023 | 0.45716
0.28227 | 0.29442 | 0.44022 | 0.45714
0.28226 | 0.29442 | 0.44019 | 0.45713
0.28226 | 0.29441 | 0.44019 | 0.45712
0.28225 | 0.2944 | 0.44016 | 0.45711
0.28223 | 0.29439 | 0.44016 | 0.4571
0.28222 | 0.29438 | 0.44015 | 0.45709
0.28221 | 0.29437 | 0.44012 | 0.45708
0.2822 | 0.29435 | 0.44011 | 0.45708
0.28219 | 0.29434 | 0.4401 | 0.45706
0.28219 | 0.29433 | 0.44009 | 0.45705
0.28218 | 0.29432 | 0.44008 | 0.45705
0.28217 | 0.29431 | 0.44006 | 0.45703
0.28216 | 0.2943 | 0.44005 | 0.45702
0.28214 | 0.29429 | 0.44004 | 0.45701
0.28213 | 0.29428 | 0.44003 | 0.457
0.28212 | 0.29427 | 0.44002 | 0.45699
0.28212 | 0.29425 | 0.44 | 0.45698
0.28211 | 0.29424 | 0.44 | 0.45697
0.2821 | 0.29424 | 0.43998 | 0.45696
0.28209 | 0.29423 | 0.43998 | 0.45696
0.28208 | 0.29422 | 0.43996 | 0.45694
0.28207 | 0.29421 | 0.43996 | 0.45693
0.28207 | 0.29421 | 0.43994 | 0.45692
0.28206 | 0.2942 | 0.43993 | 0.45691
0.28205 | 0.29419 | 0.43993 | 0.4569
0.28204 | 0.29418 | 0.43992 | 0.45688
0.28203 | 0.29417 | 0.43991 | 0.45688
0.28202 | 0.29416 | 0.43989 | 0.45687
0.282 | 0.29415 | 0.43989 | 0.45686
0.28199 | 0.29414 | 0.43987 | 0.45686
0.28198 | 0.29413 | 0.43985 | 0.45684
0.28196 | 0.29412 | 0.43984 | 0.45682
0.28195 | 0.29411 | 0.43983 | 0.45682
0.28194 | 0.2941 | 0.43982 | 0.45681
0.28193 | 0.29409 | 0.4398 | 0.4568
0.28193 | 0.29408 | 0.43979 | 0.45679
0.28192 | 0.29407 | 0.43978 | 0.45678
0.2819 | 0.29405 | 0.43978 | 0.45676
0.28189 | 0.29405 | 0.43976 | 0.45676
0.28188 | 0.29404 | 0.43975 | 0.45674
0.28187 | 0.29404 | 0.43974 | 0.45673
0.28186 | 0.29402 | 0.43973 | 0.45672
0.28185 | 0.29401 | 0.43972 | 0.45672
0.28184 | 0.294 | 0.4397 | 0.45671
0.28183 | 0.29399 | 0.43968 | 0.4567
0.28183 | 0.29398 | 0.43968 | 0.45669
0.28181 | 0.29397 | 0.43967 | 0.45668
0.28181 | 0.29396 | 0.43966 | 0.45668
0.2818 | 0.29394 | 0.43964 | 0.45666
0.28179 | 0.29393 | 0.43963 | 0.45666
0.28178 | 0.29393 | 0.43961 | 0.45665
0.28176 | 0.29392 | 0.4396 | 0.45664
0.28175 | 0.29391 | 0.4396 | 0.45663
0.28175 | 0.2939 | 0.43959 | 0.45662
0.28174 | 0.29389 | 0.43959 | 0.45661
0.28173 | 0.29388 | 0.43957 | 0.4566
0.28171 | 0.29387 | 0.43957 | 0.4566
0.28171 | 0.29386 | 0.43954 | 0.45659
0.2817 | 0.29385 | 0.43953 | 0.45658
0.2817 | 0.29384 | 0.43952 | 0.45657
0.28169 | 0.29384 | 0.43951 | 0.45656
0.28168 | 0.29383 | 0.4395 | 0.45655
0.28167 | 0.29382 | 0.4395 | 0.45654
0.28165 | 0.29381 | 0.43948 | 0.45653
0.28165 | 0.2938 | 0.43948 | 0.45652
0.28164 | 0.29379 | 0.43946 | 0.45651
0.28163 | 0.29378 | 0.43945 | 0.45651
0.28162 | 0.29377 | 0.43945 | 0.4565
0.28161 | 0.29376 | 0.43943 | 0.45649
0.2816 | 0.29375 | 0.43943 | 0.45648
0.28159 | 0.29374 | 0.43942 | 0.45647
0.28158 | 0.29373 | 0.4394 | 0.45646
0.28157 | 0.29372 | 0.4394 | 0.45646
0.28157 | 0.29371 | 0.43939 | 0.45644
0.28156 | 0.2937 | 0.43938 | 0.45644
0.28155 | 0.29369 | 0.43938 | 0.45642
0.28154 | 0.29368 | 0.43937 | 0.45641
0.28152 | 0.29368 | 0.43936 | 0.4564
0.28151 | 0.29367 | 0.43933 | 0.45639
0.2815 | 0.29366 | 0.43932 | 0.45638
0.2815 | 0.29365 | 0.43931 | 0.45636
0.28149 | 0.29364 | 0.43929 | 0.45635
0.28148 | 0.29364 | 0.43927 | 0.45634
0.28148 | 0.29363 | 0.43927 | 0.45634
0.28147 | 0.29362 | 0.43926 | 0.45633
0.28146 | 0.2936 | 0.43925 | 0.45632
0.28145 | 0.2936 | 0.43924 | 0.45631
0.28145 | 0.29359 | 0.43923 | 0.4563
0.28144 | 0.29358 | 0.43922 | 0.45629
0.28143 | 0.29357 | 0.43921 | 0.45627
0.28142 | 0.29356 | 0.4392 | 0.45626
0.28141 | 0.29355 | 0.43919 | 0.45625
0.2814 | 0.29354 | 0.43917 | 0.45624
0.2814 | 0.29354 | 0.43916 | 0.45624
0.28139 | 0.29353 | 0.43915 | 0.45622
0.28138 | 0.29352 | 0.43913 | 0.45621
0.28137 | 0.29351 | 0.43912 | 0.4562
0.28136 | 0.2935 | 0.43911 | 0.45618
0.28135 | 0.2935 | 0.4391 | 0.45617
0.28134 | 0.29349 | 0.43908 | 0.45616
0.28133 | 0.29348 | 0.43907 | 0.45616
0.28132 | 0.29347 | 0.43906 | 0.45614
0.28132 | 0.29346 | 0.43905 | 0.45614
0.2813 | 0.29345 | 0.43903 | 0.45614
0.28129 | 0.29343 | 0.43903 | 0.45612
0.28129 | 0.29343 | 0.43902 | 0.45611
0.28128 | 0.29342 | 0.43901 | 0.4561
0.28127 | 0.29341 | 0.439 | 0.45609
0.28125 | 0.2934 | 0.43899 | 0.45608
0.28125 | 0.29339 | 0.43898 | 0.45607
0.28123 | 0.29338 | 0.43897 | 0.45605
0.28122 | 0.29337 | 0.43896 | 0.45605
0.28121 | 0.29336 | 0.43895 | 0.45604
0.28121 | 0.29335 | 0.43895 | 0.45603
0.2812 | 0.29334 | 0.43894 | 0.45601
0.28119 | 0.29334 | 0.43893 | 0.456
0.28118 | 0.29333 | 0.43892 | 0.45599
0.28117 | 0.29332 | 0.4389 | 0.45598
0.28116 | 0.29332 | 0.43889 | 0.45597
0.28115 | 0.29331 | 0.43889 | 0.45595
0.28114 | 0.2933 | 0.43887 | 0.45594
0.28113 | 0.29329 | 0.43885 | 0.45593
0.28112 | 0.29329 | 0.43884 | 0.45592
0.2811 | 0.29328 | 0.43884 | 0.45591
0.28109 | 0.29327 | 0.43883 | 0.4559
0.28108 | 0.29326 | 0.43882 | 0.45589
0.28108 | 0.29325 | 0.4388 | 0.45588
0.28107 | 0.29324 | 0.4388 | 0.45587
0.28106 | 0.29323 | 0.43879 | 0.45587
0.28104 | 0.29322 | 0.43878 | 0.45585
0.28103 | 0.29321 | 0.43877 | 0.45584
0.28102 | 0.2932 | 0.43875 | 0.45584
0.28101 | 0.2932 | 0.43874 | 0.45582
0.281 | 0.29319 | 0.43872 | 0.45582
0.28099 | 0.29318 | 0.43871 | 0.45581
0.28099 | 0.29317 | 0.4387 | 0.4558
0.28098 | 0.29317 | 0.43869 | 0.45579
0.28097 | 0.29316 | 0.43868 | 0.45578
0.28095 | 0.29315 | 0.43867 | 0.45577
0.28094 | 0.29314 | 0.43866 | 0.45576
0.28092 | 0.29314 | 0.43865 | 0.45574
0.28091 | 0.29313 | 0.43863 | 0.45573
0.28091 | 0.29313 | 0.43863 | 0.45572
0.28089 | 0.29312 | 0.43861 | 0.45572
0.28088 | 0.29311 | 0.4386 | 0.45571
0.28088 | 0.29309 | 0.43859 | 0.4557
0.28087 | 0.29308 | 0.43857 | 0.45569
0.28086 | 0.29307 | 0.43856 | 0.45568
0.28085 | 0.29307 | 0.43855 | 0.45567
0.28084 | 0.29305 | 0.43854 | 0.45566
0.28083 | 0.29304 | 0.43853 | 0.45565
0.28082 | 0.29303 | 0.43851 | 0.45565
0.28081 | 0.29302 | 0.4385 | 0.45563
0.28079 | 0.29301 | 0.43849 | 0.45563
0.28079 | 0.293 | 0.43847 | 0.45561
0.28078 | 0.29299 | 0.43846 | 0.45561
0.28077 | 0.29298 | 0.43845 | 0.4556
0.28076 | 0.29296 | 0.43844 | 0.45559
0.28075 | 0.29295 | 0.43843 | 0.45558
0.28074 | 0.29294 | 0.43841 | 0.45557
0.28073 | 0.29292 | 0.4384 | 0.45556
0.28072 | 0.29292 | 0.43839 | 0.45555
0.28071 | 0.29291 | 0.43838 | 0.45554
0.2807 | 0.2929 | 0.43837 | 0.45554
0.28069 | 0.2929 | 0.43836 | 0.45552
0.28068 | 0.29288 | 0.43834 | 0.45552
0.28067 | 0.29288 | 0.43833 | 0.4555
0.28066 | 0.29287 | 0.43832 | 0.45549
0.28066 | 0.29287 | 0.43829 | 0.45548
0.28065 | 0.29286 | 0.43828 | 0.45546
0.28064 | 0.29285 | 0.43827 | 0.45545
0.28063 | 0.29285 | 0.43826 | 0.45545
0.28062 | 0.29284 | 0.43825 | 0.45543
0.28062 | 0.29283 | 0.43824 | 0.45542
0.28061 | 0.29282 | 0.43823 | 0.45541
0.28059 | 0.29282 | 0.43821 | 0.4554
0.28058 | 0.2928 | 0.4382 | 0.45538
0.28057 | 0.29279 | 0.43819 | 0.45537
0.28056 | 0.29278 | 0.43817 | 0.45537
0.28056 | 0.29277 | 0.43816 | 0.45536
0.28055 | 0.29276 | 0.43815 | 0.45535
0.28054 | 0.29274 | 0.43813 | 0.45534
0.28053 | 0.29274 | 0.43812 | 0.45533
0.28052 | 0.29273 | 0.43812 | 0.45532
0.28051 | 0.29273 | 0.43811 | 0.45532
0.28049 | 0.29272 | 0.4381 | 0.4553
0.28049 | 0.29271 | 0.4381 | 0.45529
0.28048 | 0.2927 | 0.43808 | 0.45529
0.28047 | 0.29269 | 0.43807 | 0.45526
0.28046 | 0.29268 | 0.43806 | 0.45526
0.28045 | 0.29267 | 0.43806 | 0.45524
0.28045 | 0.29265 | 0.43805 | 0.45523
0.28044 | 0.29264 | 0.43804 | 0.45522
0.28043 | 0.29264 | 0.43803 | 0.4552
0.28041 | 0.29263 | 0.43802 | 0.45519
0.2804 | 0.29262 | 0.43801 | 0.45518
0.2804 | 0.29261 | 0.438 | 0.45517
0.28038 | 0.29261 | 0.438 | 0.45516
0.28038 | 0.2926 | 0.43798 | 0.45515
0.28037 | 0.29259 | 0.43797 | 0.45514
0.28036 | 0.29258 | 0.43796 | 0.45513
0.28035 | 0.29257 | 0.43796 | 0.45512
0.28034 | 0.29256 | 0.43794 | 0.45511
0.28033 | 0.29255 | 0.43793 | 0.45511
0.28032 | 0.29253 | 0.43792 | 0.45509
0.28032 | 0.29252 | 0.4379 | 0.45508
0.28031 | 0.29251 | 0.43789 | 0.45507
0.28029 | 0.2925 | 0.43788 | 0.45506
0.28029 | 0.29249 | 0.43786 | 0.45506
0.28028 | 0.29248 | 0.43784 | 0.45505
0.28027 | 0.29248 | 0.43783 | 0.45504
0.28025 | 0.29246 | 0.43781 | 0.45503
0.28024 | 0.29245 | 0.43781 | 0.45502
0.28023 | 0.29244 | 0.4378 | 0.45501
0.28022 | 0.29243 | 0.43779 | 0.455
0.28021 | 0.29243 | 0.43777 | 0.45499
0.2802 | 0.29242 | 0.43776 | 0.45498
0.28019 | 0.29241 | 0.43776 | 0.45496
0.28019 | 0.2924 | 0.43774 | 0.45496
0.28018 | 0.29239 | 0.43773 | 0.45495
0.28017 | 0.29238 | 0.43771 | 0.45494
0.28015 | 0.29238 | 0.43771 | 0.45492
0.28013 | 0.29236 | 0.4377 | 0.45491
0.28012 | 0.29235 | 0.43768 | 0.45489
0.28011 | 0.29235 | 0.43768 | 0.45488
0.28011 | 0.29234 | 0.43766 | 0.45486
0.2801 | 0.29233 | 0.43765 | 0.45486
0.28009 | 0.29232 | 0.43763 | 0.45485
0.28008 | 0.29232 | 0.43763 | 0.45485
0.28007 | 0.29231 | 0.43761 | 0.45483
0.28006 | 0.2923 | 0.4376 | 0.45483
0.28005 | 0.29228 | 0.43759 | 0.45482
0.28004 | 0.29227 | 0.43758 | 0.45481
0.28003 | 0.29226 | 0.43757 | 0.4548
0.28002 | 0.29225 | 0.43755 | 0.45479
0.28001 | 0.29224 | 0.43755 | 0.45478
0.28 | 0.29224 | 0.43754 | 0.45478
0.27998 | 0.29223 | 0.43752 | 0.45477
0.27997 | 0.29222 | 0.43751 | 0.45476
0.27996 | 0.29221 | 0.4375 | 0.45475
0.27995 | 0.29221 | 0.43749 | 0.45474
0.27995 | 0.2922 | 0.43748 | 0.45472
0.27994 | 0.29218 | 0.43746 | 0.4547
0.27993 | 0.29217 | 0.43744 | 0.45469
0.27992 | 0.29216 | 0.43744 | 0.45468
0.27991 | 0.29215 | 0.43743 | 0.45467
0.2799 | 0.29215 | 0.43742 | 0.45467
0.27989 | 0.29214 | 0.4374 | 0.45465
0.27988 | 0.29213 | 0.43738 | 0.45464
0.27988 | 0.29212 | 0.43736 | 0.45464
0.27987 | 0.29211 | 0.43735 | 0.45463
0.27986 | 0.2921 | 0.43733 | 0.45462
0.27984 | 0.29209 | 0.43733 | 0.45461
0.27983 | 0.29208 | 0.43732 | 0.4546
0.27981 | 0.29208 | 0.4373 | 0.45459
0.27981 | 0.29207 | 0.4373 | 0.45457
0.2798 | 0.29206 | 0.43729 | 0.45456
0.27979 | 0.29205 | 0.43727 | 0.45456
0.27978 | 0.29204 | 0.43726 | 0.45454
0.27977 | 0.29203 | 0.43725 | 0.45453
0.27976 | 0.29203 | 0.43724 | 0.45453
0.27975 | 0.29202 | 0.43723 | 0.45452
0.27974 | 0.29201 | 0.43722 | 0.45452
0.27973 | 0.292 | 0.43721 | 0.45451
0.27972 | 0.292 | 0.4372 | 0.4545
0.27971 | 0.29199 | 0.43719 | 0.45449
0.2797 | 0.29198 | 0.43717 | 0.45448
0.27969 | 0.29197 | 0.43717 | 0.45447
0.27969 | 0.29196 | 0.43716 | 0.45446
0.27967 | 0.29195 | 0.43715 | 0.45445
0.27966 | 0.29194 | 0.43713 | 0.45444
0.27965 | 0.29194 | 0.43712 | 0.45443
0.27964 | 0.29192 | 0.43711 | 0.45441
0.27963 | 0.29191 | 0.4371 | 0.45441
0.27962 | 0.29191 | 0.4371 | 0.4544
0.27961 | 0.2919 | 0.43709 | 0.45439
0.2796 | 0.29189 | 0.43708 | 0.45438
0.2796 | 0.29188 | 0.43707 | 0.45437
0.27959 | 0.29187 | 0.43706 | 0.45436
0.27958 | 0.29187 | 0.43705 | 0.45434
0.27957 | 0.29186 | 0.43703 | 0.45433
0.27956 | 0.29186 | 0.43702 | 0.45432
0.27955 | 0.29184 | 0.43701 | 0.45431
0.27954 | 0.29184 | 0.437 | 0.4543
0.27952 | 0.29183 | 0.43699 | 0.45429
0.27952 | 0.29182 | 0.43698 | 0.45428
0.2795 | 0.29182 | 0.43697 | 0.45427
0.27949 | 0.29181 | 0.43696 | 0.45426
0.27948 | 0.2918 | 0.43694 | 0.45424
0.27946 | 0.2918 | 0.43693 | 0.45424
0.27945 | 0.29179 | 0.43692 | 0.45423
0.27945 | 0.29178 | 0.43691 | 0.45421
0.27944 | 0.29177 | 0.43691 | 0.4542
0.27943 | 0.29176 | 0.43689 | 0.45419
0.27942 | 0.29175 | 0.43688 | 0.45418
0.27941 | 0.29174 | 0.43687 | 0.45417
0.27941 | 0.29173 | 0.43687 | 0.45415
0.2794 | 0.29172 | 0.43686 | 0.45414
0.27939 | 0.29171 | 0.43685 | 0.45413
0.27938 | 0.29171 | 0.43683 | 0.45413
0.27937 | 0.2917 | 0.43683 | 0.45411
0.27936 | 0.29169 | 0.43682 | 0.4541
0.27935 | 0.29168 | 0.43681 | 0.45409
0.27935 | 0.29167 | 0.4368 | 0.45409
0.27933 | 0.29166 | 0.4368 | 0.45407
0.27933 | 0.29165 | 0.43678 | 0.45406
0.27932 | 0.29164 | 0.43678 | 0.45405
0.27931 | 0.29163 | 0.43677 | 0.45403
0.27931 | 0.29162 | 0.43676 | 0.45403
0.27929 | 0.29161 | 0.43675 | 0.45402
0.27928 | 0.2916 | 0.43674 | 0.454
0.27927 | 0.2916 | 0.43673 | 0.45399
0.27927 | 0.29159 | 0.43672 | 0.45397
0.27926 | 0.29159 | 0.43671 | 0.45396
0.27925 | 0.29158 | 0.43669 | 0.45395
0.27924 | 0.29157 | 0.43669 | 0.45394
0.27923 | 0.29157 | 0.43667 | 0.45393
0.27922 | 0.29156 | 0.43666 | 0.45392
0.27922 | 0.29155 | 0.43665 | 0.45391
0.27921 | 0.29154 | 0.43664 | 0.4539
0.2792 | 0.29153 | 0.43663 | 0.4539
0.27919 | 0.29152 | 0.43662 | 0.45388
0.27918 | 0.29151 | 0.43662 | 0.45388
0.27917 | 0.2915 | 0.43661 | 0.45387
0.27916 | 0.29149 | 0.4366 | 0.45385
0.27915 | 0.29148 | 0.43659 | 0.45384
0.27914 | 0.29148 | 0.43658 | 0.45383
0.27913 | 0.29147 | 0.43658 | 0.45381
0.27912 | 0.29146 | 0.43657 | 0.4538
0.27912 | 0.29145 | 0.43656 | 0.4538
0.27911 | 0.29144 | 0.43656 | 0.45379
0.2791 | 0.29143 | 0.43655 | 0.45378
0.27909 | 0.29142 | 0.43654 | 0.45377
0.27908 | 0.29142 | 0.43653 | 0.45376
0.27906 | 0.29141 | 0.43652 | 0.45375
0.27905 | 0.2914 | 0.4365 | 0.45374
0.27904 | 0.2914 | 0.43649 | 0.45372
0.27902 | 0.29139 | 0.43648 | 0.45371
0.27902 | 0.29138 | 0.43648 | 0.45371
0.27901 | 0.29137 | 0.43647 | 0.4537
0.279 | 0.29136 | 0.43647 | 0.45369
0.27899 | 0.29135 | 0.43646 | 0.45368
0.27898 | 0.29134 | 0.43646 | 0.45366
0.27897 | 0.29133 | 0.43644 | 0.45366
0.27896 | 0.29132 | 0.43644 | 0.45365
0.27895 | 0.29131 | 0.43644 | 0.45364
0.27893 | 0.2913 | 0.43643 | 0.45363
0.27892 | 0.29129 | 0.43642 | 0.45362
0.27891 | 0.29128 | 0.4364 | 0.45361
0.2789 | 0.29127 | 0.43639 | 0.4536
0.27889 | 0.29126 | 0.43638 | 0.4536
0.27889 | 0.29125 | 0.43637 | 0.45358
0.27887 | 0.29124 | 0.43636 | 0.45358
0.27886 | 0.29124 | 0.43635 | 0.45357
0.27885 | 0.29123 | 0.43634 | 0.45356
0.27884 | 0.29122 | 0.43633 | 0.45355
0.27883 | 0.29122 | 0.43632 | 0.45354
0.27882 | 0.2912 | 0.43632 | 0.45353
0.27881 | 0.29119 | 0.43631 | 0.45352
0.27881 | 0.29118 | 0.4363 | 0.45352
0.2788 | 0.29118 | 0.43628 | 0.45351
0.27879 | 0.29117 | 0.43627 | 0.4535
0.27878 | 0.29116 | 0.43627 | 0.45348
0.27877 | 0.29115 | 0.43625 | 0.45347
0.27876 | 0.29114 | 0.43625 | 0.45346
0.27876 | 0.29112 | 0.43624 | 0.45345
0.27875 | 0.29112 | 0.43623 | 0.45344
0.27874 | 0.29111 | 0.43622 | 0.45343
0.27873 | 0.2911 | 0.43622 | 0.45342
0.27872 | 0.29109 | 0.4362 | 0.45341
0.27871 | 0.29108 | 0.43619 | 0.4534
0.2787 | 0.29107 | 0.43618 | 0.45339
0.2787 | 0.29106 | 0.43618 | 0.45338
0.27869 | 0.29105 | 0.43617 | 0.45337
0.27868 | 0.29104 | 0.43617 | 0.45336
0.27868 | 0.29103 | 0.43616 | 0.45334
0.27867 | 0.29102 | 0.43615 | 0.45334
0.27866 | 0.29101 | 0.43614 | 0.45333
0.27866 | 0.291 | 0.43614 | 0.45331
0.27864 | 0.29099 | 0.43613 | 0.45331
0.27864 | 0.29098 | 0.43612 | 0.4533
0.27863 | 0.29098 | 0.43611 | 0.45329
0.27862 | 0.29096 | 0.43611 | 0.45328
0.27862 | 0.29095 | 0.4361 | 0.45326
0.27861 | 0.29094 | 0.43608 | 0.45326
0.2786 | 0.29093 | 0.43608 | 0.45325
0.27859 | 0.29092 | 0.43607 | 0.45324
0.27858 | 0.29091 | 0.43606 | 0.45321
0.27857 | 0.2909 | 0.43605 | 0.4532
0.27856 | 0.29089 | 0.43605 | 0.45318
0.27855 | 0.29088 | 0.43603 | 0.45317
0.27854 | 0.29087 | 0.43603 | 0.45316
0.27854 | 0.29086 | 0.43601 | 0.45315
0.27853 | 0.29086 | 0.43601 | 0.45314
0.27852 | 0.29085 | 0.43599 | 0.45313
0.27851 | 0.29084 | 0.43599 | 0.45311
0.2785 | 0.29083 | 0.43598 | 0.4531
0.27849 | 0.29082 | 0.43597 | 0.45309
0.27848 | 0.29082 | 0.43596 | 0.45309
0.27847 | 0.29081 | 0.43595 | 0.45306
0.27847 | 0.29079 | 0.43594 | 0.45306
0.27846 | 0.29078 | 0.43592 | 0.45305
0.27845 | 0.29077 | 0.43591 | 0.45304
0.27844 | 0.29076 | 0.43591 | 0.45304
0.27843 | 0.29075 | 0.4359 | 0.45303
0.27842 | 0.29074 | 0.43589 | 0.45302
0.27841 | 0.29073 | 0.43588 | 0.45301
0.2784 | 0.29072 | 0.43588 | 0.453
0.27838 | 0.29071 | 0.43587 | 0.45299
0.27837 | 0.2907 | 0.43586 | 0.45297
0.27836 | 0.29069 | 0.43585 | 0.45297
0.27835 | 0.29068 | 0.43584 | 0.45296
0.27835 | 0.29067 | 0.43584 | 0.45295
0.27834 | 0.29066 | 0.43583 | 0.45295
0.27833 | 0.29065 | 0.43582 | 0.45293
0.27832 | 0.29063 | 0.43581 | 0.45293
0.2783 | 0.29062 | 0.43581 | 0.45292
0.27829 | 0.29061 | 0.43579 | 0.45291
0.27829 | 0.2906 | 0.43578 | 0.4529
0.27828 | 0.29059 | 0.43577 | 0.4529
0.27826 | 0.29058 | 0.43576 | 0.45289
0.27825 | 0.29057 | 0.43574 | 0.45289
0.27824 | 0.29057 | 0.43573 | 0.45287
0.27823 | 0.29056 | 0.43573 | 0.45287
0.27822 | 0.29055 | 0.43573 | 0.45286
0.27821 | 0.29054 | 0.43571 | 0.45284
0.2782 | 0.29053 | 0.43571 | 0.45284
0.27818 | 0.29052 | 0.4357 | 0.45282
0.27818 | 0.29051 | 0.43569 | 0.45281
0.27817 | 0.2905 | 0.43568 | 0.4528
0.27815 | 0.29049 | 0.43567 | 0.45278
0.27814 | 0.29049 | 0.43566 | 0.45277
0.27813 | 0.29048 | 0.43566 | 0.45277
0.27812 | 0.29047 | 0.43565 | 0.45276
0.27811 | 0.29046 | 0.43564 | 0.45275
0.2781 | 0.29045 | 0.43563 | 0.45273
0.27809 | 0.29045 | 0.43563 | 0.45272
0.27808 | 0.29044 | 0.43562 | 0.45271
0.27807 | 0.29043 | 0.43561 | 0.4527
0.27806 | 0.29041 | 0.4356 | 0.45269
0.27805 | 0.29041 | 0.43558 | 0.45268
0.27804 | 0.2904 | 0.43558 | 0.45267
0.27803 | 0.29039 | 0.43557 | 0.45266
0.27801 | 0.29038 | 0.43555 | 0.45265
0.27801 | 0.29037 | 0.43555 | 0.45263
0.27799 | 0.29036 | 0.43554 | 0.45263
0.27799 | 0.29035 | 0.43553 | 0.45262
0.27797 | 0.29034 | 0.43552 | 0.45262
0.27796 | 0.29033 | 0.43551 | 0.45261
0.27795 | 0.29032 | 0.43549 | 0.45261
0.27795 | 0.29031 | 0.43548 | 0.4526
0.27794 | 0.2903 | 0.43547 | 0.45259
0.27793 | 0.29029 | 0.43546 | 0.45258
0.27792 | 0.29028 | 0.43545 | 0.45256
0.2779 | 0.29027 | 0.43545 | 0.45256
0.27789 | 0.29026 | 0.43544 | 0.45254
0.27789 | 0.29025 | 0.43542 | 0.45254
0.27788 | 0.29024 | 0.43541 | 0.45251
0.27787 | 0.29023 | 0.4354 | 0.45251
0.27786 | 0.29022 | 0.43539 | 0.45249
0.27785 | 0.2902 | 0.43539 | 0.45249
0.27784 | 0.29019 | 0.43538 | 0.45248
0.27783 | 0.29017 | 0.43538 | 0.45247
0.27782 | 0.29016 | 0.43537 | 0.45247
0.27781 | 0.29015 | 0.43535 | 0.45245
0.27779 | 0.29014 | 0.43535 | 0.45245
0.27778 | 0.29014 | 0.43534 | 0.45244
0.27777 | 0.29013 | 0.43533 | 0.45243
0.27776 | 0.29012 | 0.43532 | 0.45242
0.27775 | 0.29012 | 0.43532 | 0.45241
0.27775 | 0.29011 | 0.4353 | 0.4524
0.27774 | 0.2901 | 0.43529 | 0.45238
0.27772 | 0.29009 | 0.43528 | 0.45238
0.27771 | 0.29008 | 0.43527 | 0.45237
0.2777 | 0.29007 | 0.43526 | 0.45236
0.27769 | 0.29006 | 0.43525 | 0.45236
0.27769 | 0.29005 | 0.43524 | 0.45235
0.27768 | 0.29004 | 0.43523 | 0.45234
0.27767 | 0.29003 | 0.43522 | 0.45233
0.27767 | 0.29002 | 0.43521 | 0.45231
0.27765 | 0.29001 | 0.4352 | 0.4523
0.27764 | 0.29 | 0.4352 | 0.4523
0.27763 | 0.28999 | 0.43518 | 0.45228
0.27762 | 0.28998 | 0.43517 | 0.45228
0.27761 | 0.28997 | 0.43517 | 0.45227
0.27761 | 0.28996 | 0.43514 | 0.45226
0.2776 | 0.28996 | 0.43514 | 0.45225
0.27759 | 0.28995 | 0.43513 | 0.45224
0.27758 | 0.28994 | 0.43512 | 0.45224
0.27757 | 0.28993 | 0.43511 | 0.45222
0.27756 | 0.28992 | 0.4351 | 0.45221
0.27755 | 0.28992 | 0.43509 | 0.45219
0.27754 | 0.28991 | 0.43509 | 0.45218
0.27753 | 0.2899 | 0.43508 | 0.45217
0.27753 | 0.28989 | 0.43508 | 0.45217
0.27752 | 0.28988 | 0.43507 | 0.45215
0.27751 | 0.28987 | 0.43506 | 0.45215
0.27751 | 0.28986 | 0.43504 | 0.45214
0.2775 | 0.28984 | 0.43504 | 0.45212
0.27749 | 0.28984 | 0.43502 | 0.45211
0.27748 | 0.28983 | 0.435 | 0.4521
0.27747 | 0.28982 | 0.435 | 0.45209
0.27746 | 0.28982 | 0.43499 | 0.45208
0.27745 | 0.28981 | 0.43498 | 0.45208
0.27744 | 0.2898 | 0.43497 | 0.45207
0.27743 | 0.28979 | 0.43497 | 0.45206
0.27742 | 0.28978 | 0.43495 | 0.45205
0.27741 | 0.28977 | 0.43494 | 0.45204
0.27741 | 0.28976 | 0.43493 | 0.45202
0.2774 | 0.28975 | 0.43493 | 0.45201
0.2774 | 0.28974 | 0.43491 | 0.45201
0.27739 | 0.28973 | 0.4349 | 0.452
0.27738 | 0.28972 | 0.4349 | 0.45199
0.27737 | 0.28972 | 0.43489 | 0.45199
0.27736 | 0.28971 | 0.43488 | 0.45198
0.27735 | 0.2897 | 0.43487 | 0.45197
0.27733 | 0.28969 | 0.43486 | 0.45195
0.27733 | 0.28968 | 0.43484 | 0.45195
0.27731 | 0.28967 | 0.43484 | 0.45194
0.27731 | 0.28966 | 0.43483 | 0.45193
0.2773 | 0.28965 | 0.43482 | 0.45192
0.27728 | 0.28964 | 0.43482 | 0.45191
0.27726 | 0.28963 | 0.4348 | 0.4519
0.27726 | 0.28962 | 0.43479 | 0.45189
0.27724 | 0.28961 | 0.43479 | 0.45186
0.27723 | 0.2896 | 0.43478 | 0.45186
0.27723 | 0.28959 | 0.43477 | 0.45185
0.27722 | 0.28958 | 0.43476 | 0.45184
0.2772 | 0.28957 | 0.43476 | 0.45184
0.27719 | 0.28956 | 0.43475 | 0.45183
0.27718 | 0.28955 | 0.43474 | 0.45183
0.27717 | 0.28954 | 0.43473 | 0.45181
0.27716 | 0.28953 | 0.43473 | 0.4518
0.27715 | 0.28952 | 0.43472 | 0.4518
0.27714 | 0.28951 | 0.43471 | 0.45179
0.27712 | 0.2895 | 0.43468 | 0.45179
0.27711 | 0.28949 | 0.43467 | 0.45178
0.2771 | 0.28948 | 0.43466 | 0.45177
0.27709 | 0.28948 | 0.43465 | 0.45176
0.27708 | 0.28947 | 0.43464 | 0.45176
0.27707 | 0.28946 | 0.43462 | 0.45174
0.27706 | 0.28945 | 0.43461 | 0.45174
0.27705 | 0.28944 | 0.43461 | 0.45173
0.27704 | 0.28943 | 0.4346 | 0.45171
0.27703 | 0.28942 | 0.43459 | 0.4517
0.27702 | 0.28942 | 0.43458 | 0.4517
0.27701 | 0.28941 | 0.43457 | 0.4517
0.277 | 0.28939 | 0.43456 | 0.45168
0.27699 | 0.28938 | 0.43455 | 0.45166
0.27698 | 0.28936 | 0.43453 | 0.45165
0.27697 | 0.28936 | 0.43452 | 0.45165
0.27696 | 0.28935 | 0.43451 | 0.45163
0.27695 | 0.28934 | 0.4345 | 0.45162
0.27694 | 0.28933 | 0.43449 | 0.45161
0.27694 | 0.28933 | 0.43449 | 0.4516
0.27693 | 0.28932 | 0.43448 | 0.45159
0.27691 | 0.28931 | 0.43447 | 0.45158
0.2769 | 0.2893 | 0.43447 | 0.45157
0.27689 | 0.28929 | 0.43445 | 0.45157
0.27688 | 0.28928 | 0.43445 | 0.45155
0.27687 | 0.28927 | 0.43443 | 0.45155
0.27686 | 0.28926 | 0.43442 | 0.45153
0.27685 | 0.28925 | 0.43441 | 0.45153
0.27684 | 0.28924 | 0.4344 | 0.45152
0.27683 | 0.28923 | 0.43439 | 0.45152
0.27682 | 0.28922 | 0.43438 | 0.45151
0.27681 | 0.28921 | 0.43437 | 0.4515
0.2768 | 0.2892 | 0.43436 | 0.45149
0.2768 | 0.28918 | 0.43435 | 0.45148
0.27678 | 0.28918 | 0.43434 | 0.45148
0.27677 | 0.28917 | 0.43434 | 0.45146
0.27675 | 0.28916 | 0.43431 | 0.45146
0.27674 | 0.28915 | 0.43431 | 0.45145
0.27673 | 0.28914 | 0.4343 | 0.45143
0.27673 | 0.28913 | 0.43429 | 0.45143
0.27672 | 0.28912 | 0.43427 | 0.45141
0.27671 | 0.28911 | 0.43427 | 0.4514
0.2767 | 0.2891 | 0.43425 | 0.45138
0.27669 | 0.28909 | 0.43424 | 0.45137
0.27668 | 0.28908 | 0.43424 | 0.45137
0.27667 | 0.28907 | 0.43423 | 0.45136
0.27665 | 0.28907 | 0.43422 | 0.45135
0.27665 | 0.28906 | 0.43422 | 0.45135
0.27664 | 0.28905 | 0.4342 | 0.45134
0.27663 | 0.28904 | 0.43419 | 0.45132
0.27663 | 0.28903 | 0.43418 | 0.45131
0.27661 | 0.28902 | 0.43418 | 0.4513
0.27661 | 0.28902 | 0.43417 | 0.45129
0.2766 | 0.289 | 0.43415 | 0.45128
0.27659 | 0.28899 | 0.43414 | 0.45127
0.27658 | 0.28899 | 0.43413 | 0.45126
0.27657 | 0.28898 | 0.43412 | 0.45126
0.27656 | 0.28897 | 0.43411 | 0.45124
0.27655 | 0.28896 | 0.4341 | 0.45123
0.27654 | 0.28895 | 0.43409 | 0.45123
0.27653 | 0.28894 | 0.43407 | 0.45122
0.27652 | 0.28893 | 0.43406 | 0.45121
0.27651 | 0.28892 | 0.43405 | 0.45121
0.2765 | 0.28891 | 0.43405 | 0.45119
0.27649 | 0.2889 | 0.43404 | 0.45119
0.27649 | 0.28889 | 0.43403 | 0.45118
0.27648 | 0.28888 | 0.43403 | 0.45117
0.27647 | 0.28888 | 0.43402 | 0.45116
0.27646 | 0.28886 | 0.43401 | 0.45115
0.27645 | 0.28886 | 0.434 | 0.45114
0.27644 | 0.28885 | 0.43399 | 0.45113
0.27643 | 0.28885 | 0.43398 | 0.45112
0.27641 | 0.28884 | 0.43397 | 0.4511
0.2764 | 0.28883 | 0.43395 | 0.4511
0.2764 | 0.28882 | 0.43394 | 0.45109
0.27639 | 0.28881 | 0.43393 | 0.45108
0.27638 | 0.2888 | 0.43392 | 0.45107
0.27638 | 0.28879 | 0.43391 | 0.45106
0.27637 | 0.28878 | 0.4339 | 0.45105
0.27636 | 0.28876 | 0.4339 | 0.45105
0.27635 | 0.28875 | 0.4339 | 0.45104
0.27634 | 0.28875 | 0.43389 | 0.45102
0.27633 | 0.28874 | 0.43387 | 0.45101
0.27632 | 0.28873 | 0.43386 | 0.451
0.27632 | 0.28872 | 0.43386 | 0.45099
0.27631 | 0.28871 | 0.43385 | 0.45098
0.2763 | 0.28871 | 0.43383 | 0.45097
0.27629 | 0.2887 | 0.43382 | 0.45096
0.27628 | 0.28869 | 0.43381 | 0.45095
0.27627 | 0.28867 | 0.4338 | 0.45095
0.27626 | 0.28867 | 0.43379 | 0.45094
0.27626 | 0.28866 | 0.43379 | 0.45093
0.27625 | 0.28865 | 0.43378 | 0.45092
0.27624 | 0.28864 | 0.43377 | 0.4509
0.27623 | 0.28863 | 0.43376 | 0.4509
0.27622 | 0.28863 | 0.43376 | 0.45089
0.27621 | 0.28862 | 0.43374 | 0.45088
0.2762 | 0.28861 | 0.43373 | 0.45087
0.27619 | 0.2886 | 0.43372 | 0.45086
0.27618 | 0.28859 | 0.43372 | 0.45085
0.27616 | 0.28858 | 0.43369 | 0.45084
0.27616 | 0.28856 | 0.43368 | 0.45083
0.27615 | 0.28855 | 0.43366 | 0.45082
0.27614 | 0.28855 | 0.43365 | 0.4508
0.27613 | 0.28854 | 0.43364 | 0.45079
0.27612 | 0.28853 | 0.43364 | 0.45079
0.27611 | 0.28852 | 0.43363 | 0.45078
0.2761 | 0.28851 | 0.43362 | 0.45077
0.27609 | 0.28851 | 0.43361 | 0.45075
0.27609 | 0.2885 | 0.43359 | 0.45074
0.27608 | 0.28849 | 0.43359 | 0.45073
0.27607 | 0.28848 | 0.43358 | 0.45072
0.27606 | 0.28848 | 0.43357 | 0.45071
0.27605 | 0.28847 | 0.43357 | 0.45069
0.27605 | 0.28846 | 0.43355 | 0.45068
0.27604 | 0.28845 | 0.43355 | 0.45067
0.27603 | 0.28844 | 0.43353 | 0.45066
0.27602 | 0.28843 | 0.43352 | 0.45066
0.27601 | 0.28843 | 0.43351 | 0.45064
0.27599 | 0.28842 | 0.4335 | 0.45063
0.27599 | 0.2884 | 0.43349 | 0.45062
0.27597 | 0.28839 | 0.43349 | 0.45061
0.27597 | 0.28838 | 0.43347 | 0.4506
0.27596 | 0.28837 | 0.43346 | 0.45059
0.27595 | 0.28836 | 0.43346 | 0.45058
0.27594 | 0.28836 | 0.43345 | 0.45057
0.27593 | 0.28834 | 0.43344 | 0.45056
0.27592 | 0.28833 | 0.43342 | 0.45055
0.27591 | 0.28832 | 0.43342 | 0.45055
0.2759 | 0.28832 | 0.43339 | 0.45053
0.27588 | 0.2883 | 0.43338 | 0.45052
0.27587 | 0.2883 | 0.43336 | 0.45051
0.27586 | 0.28828 | 0.43335 | 0.4505
0.27586 | 0.28827 | 0.43333 | 0.4505
0.27584 | 0.28826 | 0.43331 | 0.45049
0.27584 | 0.28825 | 0.4333 | 0.45048
0.27583 | 0.28824 | 0.43329 | 0.45047
0.27581 | 0.28824 | 0.43329 | 0.45046
0.27581 | 0.28823 | 0.43328 | 0.45045
0.2758 | 0.28822 | 0.43327 | 0.45044
0.27579 | 0.28821 | 0.43326 | 0.45043
0.27578 | 0.2882 | 0.43325 | 0.45043
0.27577 | 0.2882 | 0.43324 | 0.45042
0.27576 | 0.28819 | 0.43323 | 0.45041
0.27576 | 0.28818 | 0.43322 | 0.45041
0.27575 | 0.28817 | 0.43321 | 0.45039
0.27574 | 0.28816 | 0.43319 | 0.45039
0.27573 | 0.28815 | 0.43318 | 0.45037
0.27572 | 0.28814 | 0.43316 | 0.45035
0.27571 | 0.28812 | 0.43316 | 0.45035
0.2757 | 0.28811 | 0.43315 | 0.45034
0.27569 | 0.28811 | 0.43314 | 0.45032
0.27568 | 0.2881 | 0.43313 | 0.4503
0.27567 | 0.28809 | 0.43312 | 0.4503
0.27566 | 0.28808 | 0.43311 | 0.45029
0.27565 | 0.28807 | 0.4331 | 0.45028
0.27563 | 0.28806 | 0.43308 | 0.45027
0.27563 | 0.28805 | 0.43307 | 0.45026
0.27562 | 0.28805 | 0.43307 | 0.45025
0.27561 | 0.28804 | 0.43306 | 0.45023
0.27559 | 0.28803 | 0.43305 | 0.45022
0.27558 | 0.28802 | 0.43305 | 0.45021
0.27557 | 0.28801 | 0.43304 | 0.45021
0.27556 | 0.288 | 0.43303 | 0.45018
0.27555 | 0.28799 | 0.43301 | 0.45018
0.27554 | 0.28798 | 0.43299 | 0.45017
0.27553 | 0.28797 | 0.43298 | 0.45016
0.27552 | 0.28797 | 0.43297 | 0.45016
0.27551 | 0.28796 | 0.43296 | 0.45014
0.2755 | 0.28795 | 0.43294 | 0.45013
0.27549 | 0.28794 | 0.43294 | 0.45012
0.27548 | 0.28793 | 0.43292 | 0.45012
0.27548 | 0.28793 | 0.43292 | 0.45011
0.27547 | 0.28792 | 0.4329 | 0.45011
0.27546 | 0.28791 | 0.4329 | 0.45009
0.27545 | 0.28789 | 0.43288 | 0.45008
0.27545 | 0.28789 | 0.43287 | 0.45007
0.27544 | 0.28788 | 0.43286 | 0.45006
0.27543 | 0.28787 | 0.43285 | 0.45004
0.27542 | 0.28786 | 0.43285 | 0.45003
0.27541 | 0.28784 | 0.43284 | 0.45002
0.27541 | 0.28784 | 0.43283 | 0.45001
0.2754 | 0.28783 | 0.43282 | 0.45
0.27539 | 0.28782 | 0.43281 | 0.44999
0.27538 | 0.28781 | 0.4328 | 0.44998
0.27537 | 0.28781 | 0.43279 | 0.44997
0.27536 | 0.2878 | 0.43278 | 0.44996
0.27535 | 0.28778 | 0.43278 | 0.44996
0.27534 | 0.28777 | 0.43277 | 0.44995
0.27533 | 0.28776 | 0.43276 | 0.44994
0.27532 | 0.28775 | 0.43274 | 0.44994
0.27531 | 0.28774 | 0.43274 | 0.44993
0.27529 | 0.28774 | 0.43274 | 0.44993
0.27529 | 0.28773 | 0.43271 | 0.44991
0.27528 | 0.28772 | 0.43271 | 0.4499
0.27527 | 0.28771 | 0.4327 | 0.44989
0.27526 | 0.28771 | 0.43269 | 0.44987
0.27525 | 0.2877 | 0.43268 | 0.44987
0.27524 | 0.28769 | 0.43267 | 0.44986
0.27523 | 0.28768 | 0.43266 | 0.44985
0.27522 | 0.28767 | 0.43265 | 0.44984
0.27521 | 0.28767 | 0.43264 | 0.44983
0.2752 | 0.28766 | 0.43263 | 0.44983
0.27519 | 0.28765 | 0.43262 | 0.44983
0.27518 | 0.28765 | 0.4326 | 0.44981
0.27517 | 0.28764 | 0.43259 | 0.4498
0.27517 | 0.28763 | 0.43258 | 0.44979
0.27516 | 0.28762 | 0.43257 | 0.44978
0.27515 | 0.28761 | 0.43256 | 0.44978
0.27513 | 0.2876 | 0.43255 | 0.44976
0.27512 | 0.28759 | 0.43254 | 0.44975
0.2751 | 0.28758 | 0.43254 | 0.44975
0.27509 | 0.28757 | 0.43253 | 0.44973
0.27508 | 0.28756 | 0.43252 | 0.44972
0.27507 | 0.28755 | 0.43251 | 0.44972
0.27506 | 0.28755 | 0.4325 | 0.4497
0.27505 | 0.28754 | 0.4325 | 0.4497
0.27505 | 0.28752 | 0.43248 | 0.44969
0.27504 | 0.28752 | 0.43247 | 0.44968
0.27503 | 0.28751 | 0.43247 | 0.44967
0.27502 | 0.2875 | 0.43246 | 0.44967
0.27501 | 0.28749 | 0.43244 | 0.44965
0.275 | 0.28748 | 0.43244 | 0.44964
0.27499 | 0.28747 | 0.43243 | 0.44963
0.27498 | 0.28746 | 0.43241 | 0.44963
0.27497 | 0.28744 | 0.4324 | 0.44962
0.27497 | 0.28744 | 0.43238 | 0.44962
0.27496 | 0.28743 | 0.43237 | 0.44959
0.27495 | 0.28743 | 0.43236 | 0.44959
0.27494 | 0.28742 | 0.43235 | 0.44957
0.27492 | 0.28741 | 0.43233 | 0.44957
0.27491 | 0.2874 | 0.43233 | 0.44957
0.27491 | 0.28739 | 0.43231 | 0.44955
0.27489 | 0.28738 | 0.4323 | 0.44955
0.27489 | 0.28738 | 0.4323 | 0.44953
0.27488 | 0.28737 | 0.43228 | 0.44952
0.27487 | 0.28735 | 0.43227 | 0.44952
0.27487 | 0.28734 | 0.43227 | 0.4495
0.27486 | 0.28734 | 0.43226 | 0.44949
0.27485 | 0.28733 | 0.43225 | 0.44948
0.27484 | 0.28732 | 0.43224 | 0.44948
0.27483 | 0.28731 | 0.43224 | 0.44946
0.27482 | 0.2873 | 0.43223 | 0.44945
0.27481 | 0.2873 | 0.43222 | 0.44945
0.2748 | 0.28729 | 0.43221 | 0.44943
0.27479 | 0.28728 | 0.43219 | 0.44942
0.27478 | 0.28728 | 0.43218 | 0.44941
0.27477 | 0.28727 | 0.43217 | 0.4494
0.27476 | 0.28726 | 0.43216 | 0.44939
0.27475 | 0.28725 | 0.43216 | 0.44938
0.27474 | 0.28724 | 0.43214 | 0.44937
0.27473 | 0.28723 | 0.43213 | 0.44936
0.27472 | 0.28722 | 0.43213 | 0.44936
0.27471 | 0.28722 | 0.43211 | 0.44934
0.2747 | 0.28721 | 0.4321 | 0.44933
0.2747 | 0.2872 | 0.43209 | 0.44932
0.27469 | 0.28719 | 0.43208 | 0.44932
0.27468 | 0.28718 | 0.43207 | 0.44931
0.27467 | 0.28717 | 0.43205 | 0.4493
0.27466 | 0.28716 | 0.43203 | 0.44929
0.27465 | 0.28716 | 0.43201 | 0.44929
0.27464 | 0.28715 | 0.43201 | 0.44928
0.27464 | 0.28714 | 0.432 | 0.44927
0.27463 | 0.28714 | 0.43199 | 0.44925
0.27462 | 0.28713 | 0.43198 | 0.44924
0.27461 | 0.28711 | 0.43197 | 0.44923
0.27461 | 0.2871 | 0.43196 | 0.44922
0.27459 | 0.28709 | 0.43195 | 0.44921
0.27459 | 0.28709 | 0.43194 | 0.4492
0.27457 | 0.28707 | 0.43194 | 0.4492
0.27457 | 0.28706 | 0.43193 | 0.44919
0.27456 | 0.28706 | 0.43191 | 0.44918
0.27455 | 0.28704 | 0.4319 | 0.44917
0.27454 | 0.28704 | 0.43189 | 0.44916
0.27453 | 0.28703 | 0.43187 | 0.44916
0.27452 | 0.28702 | 0.43187 | 0.44914
0.27451 | 0.28701 | 0.43186 | 0.44914
0.27451 | 0.287 | 0.43184 | 0.44911
0.2745 | 0.28699 | 0.43183 | 0.44911
0.27449 | 0.28698 | 0.43181 | 0.4491
0.27448 | 0.28697 | 0.43181 | 0.44909
0.27447 | 0.28696 | 0.43179 | 0.44908
0.27446 | 0.28695 | 0.43179 | 0.44907
0.27445 | 0.28694 | 0.43177 | 0.44906
0.27444 | 0.28693 | 0.43177 | 0.44905
0.27443 | 0.28691 | 0.43175 | 0.44904
0.27442 | 0.28691 | 0.43175 | 0.44903
0.27441 | 0.2869 | 0.43174 | 0.44903
0.2744 | 0.28689 | 0.43173 | 0.44902
0.2744 | 0.28688 | 0.43172 | 0.449
0.27439 | 0.28687 | 0.43171 | 0.44899
0.27438 | 0.28686 | 0.4317 | 0.44898
0.27437 | 0.28686 | 0.4317 | 0.44897
0.27436 | 0.28684 | 0.43169 | 0.44896
0.27435 | 0.28684 | 0.43168 | 0.44895
0.27434 | 0.28683 | 0.43167 | 0.44894
0.27433 | 0.28682 | 0.43166 | 0.44893
0.27432 | 0.28681 | 0.43165 | 0.44892
0.27431 | 0.2868 | 0.43164 | 0.44891
0.2743 | 0.28679 | 0.43163 | 0.4489
0.27429 | 0.28678 | 0.43162 | 0.44889
0.27427 | 0.28677 | 0.43161 | 0.44888
0.27427 | 0.28677 | 0.4316 | 0.44888
0.27426 | 0.28676 | 0.43159 | 0.44886
0.27425 | 0.28675 | 0.43158 | 0.44885
0.27424 | 0.28674 | 0.43158 | 0.44884
0.27423 | 0.28673 | 0.43156 | 0.44882
0.27422 | 0.28672 | 0.43156 | 0.44881
0.27421 | 0.28671 | 0.43154 | 0.44879
0.2742 | 0.28671 | 0.43152 | 0.44879
0.27419 | 0.2867 | 0.43151 | 0.44879
0.27417 | 0.2867 | 0.4315 | 0.44878
0.27416 | 0.28669 | 0.43149 | 0.44877
0.27415 | 0.28668 | 0.43147 | 0.44876
0.27414 | 0.28667 | 0.43147 | 0.44874
0.27413 | 0.28666 | 0.43146 | 0.44873
0.27412 | 0.28665 | 0.43145 | 0.44873
0.27411 | 0.28664 | 0.43144 | 0.44872
0.2741 | 0.28664 | 0.43142 | 0.44871
0.27409 | 0.28663 | 0.43142 | 0.4487
0.27408 | 0.28662 | 0.43141 | 0.44869
0.27407 | 0.28661 | 0.43139 | 0.44868
0.27406 | 0.2866 | 0.43138 | 0.44868
0.27405 | 0.28659 | 0.43138 | 0.44867
0.27404 | 0.28658 | 0.43135 | 0.44866
0.27403 | 0.28658 | 0.43134 | 0.44865
0.27403 | 0.28657 | 0.43133 | 0.44864
0.27402 | 0.28656 | 0.43132 | 0.44863
0.27401 | 0.28654 | 0.43131 | 0.44862
0.274 | 0.28653 | 0.43131 | 0.44862
0.274 | 0.28652 | 0.43129 | 0.44861
0.27399 | 0.28651 | 0.43129 | 0.44859
0.27398 | 0.28651 | 0.43128 | 0.44857
0.27397 | 0.2865 | 0.43127 | 0.44857
0.27396 | 0.28649 | 0.43126 | 0.44857
0.27395 | 0.28648 | 0.43125 | 0.44855
0.27394 | 0.28647 | 0.43123 | 0.44854
0.27393 | 0.28647 | 0.43122 | 0.44854
0.27391 | 0.28646 | 0.43121 | 0.44854
0.27391 | 0.28645 | 0.4312 | 0.44851
0.2739 | 0.28645 | 0.43118 | 0.4485
0.27389 | 0.28644 | 0.43117 | 0.44849
0.27389 | 0.28643 | 0.43116 | 0.44847
0.27388 | 0.28642 | 0.43116 | 0.44846
0.27387 | 0.28641 | 0.43115 | 0.44845
0.27386 | 0.2864 | 0.43114 | 0.44843
0.27385 | 0.2864 | 0.43113 | 0.44842
0.27384 | 0.28639 | 0.43112 | 0.44842
0.27383 | 0.28638 | 0.43112 | 0.44841
0.27382 | 0.28637 | 0.4311 | 0.44839
0.27381 | 0.28636 | 0.43109 | 0.44838
0.27381 | 0.28636 | 0.43108 | 0.44837
0.27379 | 0.28635 | 0.43107 | 0.44836
0.27378 | 0.28634 | 0.43106 | 0.44835
0.27377 | 0.28633 | 0.43105 | 0.44833
0.27376 | 0.28632 | 0.43105 | 0.44833
0.27375 | 0.28631 | 0.43104 | 0.44832
0.27375 | 0.2863 | 0.43103 | 0.44831
0.27374 | 0.28628 | 0.43102 | 0.44829
0.27373 | 0.28627 | 0.43101 | 0.44829
0.27372 | 0.28626 | 0.431 | 0.44828
0.27371 | 0.28625 | 0.43099 | 0.44827
0.2737 | 0.28625 | 0.43098 | 0.44827
0.27369 | 0.28624 | 0.43097 | 0.44825
0.27368 | 0.28623 | 0.43096 | 0.44824
0.27367 | 0.28622 | 0.43095 | 0.44824
0.27366 | 0.28621 | 0.43094 | 0.44822
0.27366 | 0.2862 | 0.43093 | 0.44821
0.27365 | 0.2862 | 0.43092 | 0.4482
0.27363 | 0.28619 | 0.4309 | 0.44818
0.27363 | 0.28618 | 0.43089 | 0.44817
0.27362 | 0.28617 | 0.43088 | 0.44815
0.27361 | 0.28616 | 0.43087 | 0.44814
0.27359 | 0.28615 | 0.43085 | 0.44812
0.27358 | 0.28615 | 0.43085 | 0.44812
0.27356 | 0.28613 | 0.43083 | 0.44811
0.27356 | 0.28612 | 0.43083 | 0.4481
0.27355 | 0.28611 | 0.43082 | 0.44809
0.27354 | 0.2861 | 0.43081 | 0.44809
0.27353 | 0.28609 | 0.43079 | 0.44808
0.27352 | 0.28608 | 0.43079 | 0.44808
0.2735 | 0.28607 | 0.43078 | 0.44806
0.27349 | 0.28606 | 0.43077 | 0.44805
0.27348 | 0.28605 | 0.43076 | 0.44804
0.27347 | 0.28605 | 0.43075 | 0.44803
0.27347 | 0.28604 | 0.43074 | 0.44803
0.27345 | 0.28603 | 0.43073 | 0.44801
0.27344 | 0.28602 | 0.43071 | 0.448
0.27344 | 0.28601 | 0.4307 | 0.44799
0.27342 | 0.28601 | 0.43069 | 0.44799
0.27341 | 0.286 | 0.43068 | 0.44798
0.2734 | 0.28599 | 0.43066 | 0.44797
0.27339 | 0.28598 | 0.43066 | 0.44796
0.27339 | 0.28597 | 0.43065 | 0.44795
0.27338 | 0.28596 | 0.43064 | 0.44794
0.27337 | 0.28595 | 0.43064 | 0.44793
0.27336 | 0.28594 | 0.43062 | 0.44791
0.27335 | 0.28594 | 0.43061 | 0.4479
0.27333 | 0.28593 | 0.43059 | 0.4479
0.27332 | 0.28592 | 0.43057 | 0.44789
0.27331 | 0.28591 | 0.43056 | 0.44788
0.27331 | 0.28591 | 0.43055 | 0.44787
0.2733 | 0.2859 | 0.43054 | 0.44786
0.27329 | 0.28589 | 0.43054 | 0.44785
0.27329 | 0.28588 | 0.43052 | 0.44784
0.27328 | 0.28588 | 0.43052 | 0.44783
0.27327 | 0.28587 | 0.4305 | 0.44782
0.27326 | 0.28586 | 0.4305 | 0.44781
0.27325 | 0.28585 | 0.43049 | 0.4478
0.27324 | 0.28584 | 0.43047 | 0.44779
0.27323 | 0.28584 | 0.43045 | 0.44779
0.27321 | 0.28583 | 0.43044 | 0.44777
0.2732 | 0.28582 | 0.43042 | 0.44775
0.27318 | 0.28581 | 0.43042 | 0.44775
0.27317 | 0.2858 | 0.43041 | 0.44773
0.27316 | 0.28579 | 0.43039 | 0.44772
0.27315 | 0.28579 | 0.43038 | 0.44771
0.27314 | 0.28578 | 0.43038 | 0.4477
0.27313 | 0.28577 | 0.43037 | 0.44768
0.27312 | 0.28576 | 0.43035 | 0.44766
0.27311 | 0.28575 | 0.43034 | 0.44765
0.2731 | 0.28574 | 0.43032 | 0.44764
0.27309 | 0.28573 | 0.43031 | 0.44763
0.27308 | 0.28572 | 0.4303 | 0.44762
0.27307 | 0.28572 | 0.43029 | 0.44761
0.27306 | 0.2857 | 0.43028 | 0.4476
0.27305 | 0.2857 | 0.43027 | 0.44759
0.27304 | 0.28569 | 0.43026 | 0.44758
0.27303 | 0.28568 | 0.43025 | 0.44756
0.27301 | 0.28568 | 0.43024 | 0.44756
0.273 | 0.28567 | 0.43023 | 0.44754
0.27298 | 0.28565 | 0.43022 | 0.44752
0.27297 | 0.28565 | 0.43021 | 0.44752
0.27296 | 0.28564 | 0.4302 | 0.44751
0.27295 | 0.28563 | 0.43019 | 0.4475
0.27294 | 0.28562 | 0.43019 | 0.44749
0.27293 | 0.28561 | 0.43018 | 0.44748
0.27292 | 0.2856 | 0.43017 | 0.44747
0.27291 | 0.28559 | 0.43015 | 0.44746
0.2729 | 0.28558 | 0.43014 | 0.44745
0.27289 | 0.28557 | 0.43012 | 0.44744
0.27288 | 0.28556 | 0.43011 | 0.44743
0.27288 | 0.28555 | 0.4301 | 0.44741
0.27287 | 0.28553 | 0.43008 | 0.4474
0.27286 | 0.28552 | 0.43007 | 0.44739
0.27285 | 0.28551 | 0.43006 | 0.44738
0.27284 | 0.28551 | 0.43005 | 0.44737
0.27282 | 0.28549 | 0.43004 | 0.44737
0.27281 | 0.28549 | 0.43004 | 0.44736
0.27281 | 0.28548 | 0.43002 | 0.44735
0.2728 | 0.28547 | 0.43002 | 0.44733
0.27279 | 0.28545 | 0.43 | 0.44732
0.27278 | 0.28544 | 0.43 | 0.44731
0.27278 | 0.28543 | 0.42998 | 0.4473
0.27277 | 0.28542 | 0.42998 | 0.44728
0.27277 | 0.28541 | 0.42996 | 0.44727
0.27275 | 0.2854 | 0.42996 | 0.44726
0.27274 | 0.28539 | 0.42995 | 0.44725
0.27274 | 0.28538 | 0.42995 | 0.44724
0.27272 | 0.28537 | 0.42994 | 0.44723
0.27271 | 0.28536 | 0.42992 | 0.44723
0.2727 | 0.28534 | 0.4299 | 0.44722
0.2727 | 0.28534 | 0.42989 | 0.44719
0.27269 | 0.28533 | 0.42987 | 0.44719
0.27267 | 0.28533 | 0.42986 | 0.44718
0.27267 | 0.28532 | 0.42985 | 0.44716
0.27266 | 0.28531 | 0.42984 | 0.44715
0.27265 | 0.2853 | 0.42983 | 0.44714
0.27264 | 0.28529 | 0.42983 | 0.44714
0.27263 | 0.28528 | 0.42982 | 0.44712
0.27262 | 0.28527 | 0.4298 | 0.44711
0.27261 | 0.28526 | 0.42979 | 0.44709
0.2726 | 0.28525 | 0.42977 | 0.44709
0.27259 | 0.28524 | 0.42976 | 0.44707
0.27258 | 0.28523 | 0.42975 | 0.44706
0.27257 | 0.28522 | 0.42973 | 0.44705
0.27255 | 0.28521 | 0.42973 | 0.44705
0.27254 | 0.2852 | 0.42972 | 0.44704
0.27253 | 0.28519 | 0.42971 | 0.44703
0.27252 | 0.28519 | 0.4297 | 0.44701
0.27251 | 0.28518 | 0.42969 | 0.447
0.2725 | 0.28517 | 0.42968 | 0.447
0.2725 | 0.28516 | 0.42967 | 0.44698
0.27248 | 0.28515 | 0.42966 | 0.44697
0.27247 | 0.28514 | 0.42966 | 0.44696
0.27246 | 0.28513 | 0.42965 | 0.44695
0.27244 | 0.28512 | 0.42964 | 0.44694
0.27243 | 0.28512 | 0.42964 | 0.44694
0.27242 | 0.2851 | 0.42962 | 0.44692
0.27241 | 0.28508 | 0.42959 | 0.44692
0.2724 | 0.28507 | 0.42959 | 0.4469
0.27239 | 0.28506 | 0.42958 | 0.44689
0.27238 | 0.28504 | 0.42957 | 0.44688
0.27237 | 0.28504 | 0.42956 | 0.44687
0.27236 | 0.28503 | 0.42954 | 0.44686
0.27235 | 0.28502 | 0.42952 | 0.44685
0.27234 | 0.28501 | 0.42951 | 0.44684
0.27233 | 0.28501 | 0.42951 | 0.44684
0.27232 | 0.285 | 0.42949 | 0.44683
0.27231 | 0.28499 | 0.42948 | 0.44682
0.2723 | 0.28498 | 0.42947 | 0.4468
0.27229 | 0.28497 | 0.42946 | 0.4468
0.27228 | 0.28496 | 0.42945 | 0.44678
0.27228 | 0.28495 | 0.42944 | 0.44677
0.27227 | 0.28494 | 0.42942 | 0.44676
0.27226 | 0.28493 | 0.42941 | 0.44675
0.27225 | 0.28492 | 0.4294 | 0.44674
0.27224 | 0.28491 | 0.42938 | 0.44672
0.27223 | 0.2849 | 0.42938 | 0.44672
0.27222 | 0.28489 | 0.42936 | 0.44671
0.27222 | 0.28488 | 0.42936 | 0.4467
0.27221 | 0.28487 | 0.42934 | 0.44669
0.2722 | 0.28486 | 0.42934 | 0.44668
0.2722 | 0.28485 | 0.42933 | 0.44667
0.27219 | 0.28484 | 0.42931 | 0.44666
0.27217 | 0.28483 | 0.4293 | 0.44665
0.27216 | 0.28482 | 0.4293 | 0.44664
0.27215 | 0.2848 | 0.42929 | 0.44662
0.27214 | 0.2848 | 0.42928 | 0.4466
0.27213 | 0.28479 | 0.42927 | 0.4466
0.27212 | 0.28477 | 0.42925 | 0.44659
0.27211 | 0.28476 | 0.42924 | 0.44657
0.27211 | 0.28474 | 0.42923 | 0.44655
0.2721 | 0.28474 | 0.42921 | 0.44654
0.27209 | 0.28472 | 0.42921 | 0.44652
0.27208 | 0.28471 | 0.4292 | 0.44652
0.27207 | 0.2847 | 0.42919 | 0.4465
0.27207 | 0.2847 | 0.42918 | 0.44649
0.27206 | 0.28469 | 0.42917 | 0.44648
0.27205 | 0.28469 | 0.42916 | 0.44648
0.27204 | 0.28468 | 0.42914 | 0.44646
0.27203 | 0.28467 | 0.42914 | 0.44645
0.27202 | 0.28466 | 0.42913 | 0.44645
0.27202 | 0.28465 | 0.42912 | 0.44643
0.27201 | 0.28464 | 0.42911 | 0.44641
0.272 | 0.28463 | 0.4291 | 0.4464
0.27199 | 0.28462 | 0.42908 | 0.44638
0.27199 | 0.28462 | 0.42908 | 0.44638
0.27198 | 0.28461 | 0.42906 | 0.44637
0.27197 | 0.2846 | 0.42905 | 0.44635
0.27196 | 0.28459 | 0.42903 | 0.44634
0.27195 | 0.28459 | 0.42903 | 0.44633
0.27195 | 0.28458 | 0.42901 | 0.44633
0.27194 | 0.28457 | 0.429 | 0.44632
0.27194 | 0.28456 | 0.429 | 0.44631
0.27193 | 0.28455 | 0.42899 | 0.44631
0.27192 | 0.28454 | 0.42898 | 0.4463
0.27191 | 0.28453 | 0.42897 | 0.44628
0.27191 | 0.28452 | 0.42896 | 0.44627
0.27189 | 0.28451 | 0.42895 | 0.44626
0.27189 | 0.2845 | 0.42894 | 0.44625
0.27188 | 0.28449 | 0.42893 | 0.44623
0.27186 | 0.28448 | 0.42892 | 0.44622
0.27185 | 0.28448 | 0.42891 | 0.44621
0.27184 | 0.28447 | 0.4289 | 0.4462
0.27183 | 0.28447 | 0.4289 | 0.4462
0.27183 | 0.28446 | 0.42887 | 0.44619
0.27182 | 0.28444 | 0.42887 | 0.44618
0.2718 | 0.28443 | 0.42885 | 0.44618
0.27179 | 0.28442 | 0.42884 | 0.44616
0.27179 | 0.28441 | 0.42883 | 0.44616
0.27178 | 0.2844 | 0.42881 | 0.44615
0.27176 | 0.28439 | 0.42881 | 0.44615
0.27175 | 0.28438 | 0.4288 | 0.44614
0.27175 | 0.28437 | 0.42879 | 0.44613
0.27174 | 0.28436 | 0.42877 | 0.44611
0.27173 | 0.28435 | 0.42877 | 0.44611
0.27172 | 0.28435 | 0.42876 | 0.4461
0.27172 | 0.28434 | 0.42875 | 0.44609
0.27171 | 0.28433 | 0.42874 | 0.44608
0.2717 | 0.28432 | 0.42873 | 0.44607
0.27169 | 0.28431 | 0.42872 | 0.44606
0.27168 | 0.28431 | 0.42871 | 0.44606
0.27166 | 0.2843 | 0.4287 | 0.44605
0.27166 | 0.28429 | 0.4287 | 0.44603
0.27165 | 0.28428 | 0.42868 | 0.44603
0.27164 | 0.28427 | 0.42867 | 0.44602
0.27163 | 0.28426 | 0.42866 | 0.44601
0.27162 | 0.28425 | 0.42866 | 0.44599
0.27161 | 0.28424 | 0.42865 | 0.44599
0.27159 | 0.28423 | 0.42863 | 0.44598
0.27158 | 0.28422 | 0.42861 | 0.44597
0.27157 | 0.28421 | 0.4286 | 0.44597
0.27156 | 0.28421 | 0.42858 | 0.44596
0.27155 | 0.2842 | 0.42858 | 0.44595
0.27154 | 0.28419 | 0.42856 | 0.44593
0.27153 | 0.28419 | 0.42854 | 0.44592
0.27152 | 0.28418 | 0.42854 | 0.44591
0.27151 | 0.28417 | 0.42852 | 0.44591
0.27151 | 0.28416 | 0.4285 | 0.44589
0.2715 | 0.28415 | 0.4285 | 0.44587
0.27149 | 0.28414 | 0.42848 | 0.44586
0.27148 | 0.28414 | 0.42846 | 0.44585
0.27147 | 0.28413 | 0.42845 | 0.44584
0.27146 | 0.28412 | 0.42845 | 0.44583
0.27145 | 0.28411 | 0.42843 | 0.44582
0.27144 | 0.2841 | 0.42843 | 0.44581
0.27143 | 0.28409 | 0.42841 | 0.4458
0.27142 | 0.28408 | 0.4284 | 0.44579
0.27141 | 0.28407 | 0.42839 | 0.44577
0.2714 | 0.28406 | 0.42838 | 0.44577
0.27139 | 0.28405 | 0.42836 | 0.44576
0.27138 | 0.28405 | 0.42835 | 0.44575
0.27137 | 0.28404 | 0.42833 | 0.44575
0.27137 | 0.28403 | 0.42833 | 0.44573
0.27136 | 0.28402 | 0.4283 | 0.44572
0.27135 | 0.28402 | 0.4283 | 0.44571
0.27135 | 0.28401 | 0.42829 | 0.4457
0.27134 | 0.284 | 0.42828 | 0.44569
0.27133 | 0.28399 | 0.42827 | 0.44568
0.27132 | 0.28398 | 0.42826 | 0.44567
0.27132 | 0.28397 | 0.42825 | 0.44566
0.2713 | 0.28396 | 0.42824 | 0.44566
0.27129 | 0.28395 | 0.42823 | 0.44565
0.27128 | 0.28394 | 0.42823 | 0.44563
0.27127 | 0.28394 | 0.42821 | 0.44563
0.27126 | 0.28393 | 0.4282 | 0.44562
0.27125 | 0.28391 | 0.42819 | 0.4456
0.27124 | 0.2839 | 0.42818 | 0.44558
0.27123 | 0.28389 | 0.42817 | 0.44558
0.27122 | 0.28389 | 0.42816 | 0.44556
0.2712 | 0.28388 | 0.42815 | 0.44555
0.2712 | 0.28387 | 0.42813 | 0.44554
0.27119 | 0.28386 | 0.42813 | 0.44552
0.27118 | 0.28385 | 0.42811 | 0.44552
0.27117 | 0.28385 | 0.4281 | 0.44549
0.27115 | 0.28384 | 0.4281 | 0.44548
0.27115 | 0.28382 | 0.42809 | 0.44547
0.27114 | 0.28382 | 0.42809 | 0.44546
0.27113 | 0.2838 | 0.42806 | 0.44545
0.27111 | 0.28379 | 0.42805 | 0.44544
0.2711 | 0.28378 | 0.42804 | 0.44543
0.27109 | 0.28377 | 0.42801 | 0.44541
0.27108 | 0.28377 | 0.428 | 0.4454
0.27107 | 0.28376 | 0.42799 | 0.44538
0.27106 | 0.28375 | 0.42798 | 0.44537
0.27105 | 0.28374 | 0.42797 | 0.44536
0.27104 | 0.28373 | 0.42796 | 0.44534
0.27103 | 0.28372 | 0.42795 | 0.44533
0.27102 | 0.28371 | 0.42792 | 0.44532
0.27102 | 0.2837 | 0.42792 | 0.44531
0.27101 | 0.28369 | 0.42791 | 0.4453
0.271 | 0.28368 | 0.4279 | 0.44529
0.27099 | 0.28367 | 0.42789 | 0.44528
0.27098 | 0.28366 | 0.42788 | 0.44526
0.27098 | 0.28365 | 0.42787 | 0.44525
0.27097 | 0.28364 | 0.42786 | 0.44523
0.27096 | 0.28363 | 0.42784 | 0.44521
0.27095 | 0.28362 | 0.42783 | 0.44519
0.27093 | 0.28362 | 0.42782 | 0.44518
0.27092 | 0.28361 | 0.42781 | 0.44517
0.2709 | 0.2836 | 0.4278 | 0.44516
0.27089 | 0.28358 | 0.42778 | 0.44515
0.27088 | 0.28358 | 0.42777 | 0.44515
0.27087 | 0.28357 | 0.42776 | 0.44514
0.27086 | 0.28356 | 0.42774 | 0.44513
0.27086 | 0.28355 | 0.42774 | 0.44512
0.27085 | 0.28354 | 0.42773 | 0.44511
0.27084 | 0.28353 | 0.42772 | 0.44511
0.27083 | 0.28351 | 0.42771 | 0.44509
0.27082 | 0.28351 | 0.4277 | 0.44509
0.27081 | 0.28349 | 0.42769 | 0.44508
0.2708 | 0.28348 | 0.42769 | 0.44507
0.27079 | 0.28347 | 0.42767 | 0.44506
0.27078 | 0.28346 | 0.42765 | 0.44505
0.27077 | 0.28345 | 0.42765 | 0.44505
0.27076 | 0.28344 | 0.42763 | 0.44503
0.27076 | 0.28343 | 0.42762 | 0.44502
0.27074 | 0.28342 | 0.42761 | 0.44502
0.27074 | 0.28341 | 0.42759 | 0.44498
0.27073 | 0.28341 | 0.42759 | 0.44496
0.27071 | 0.2834 | 0.42757 | 0.44496
0.27071 | 0.28339 | 0.42756 | 0.44495
0.2707 | 0.28338 | 0.42755 | 0.44494
0.2707 | 0.28337 | 0.42754 | 0.44493
0.27069 | 0.28337 | 0.42753 | 0.44491
0.27068 | 0.28336 | 0.42752 | 0.44491
0.27067 | 0.28335 | 0.42751 | 0.44489
0.27066 | 0.28335 | 0.4275 | 0.44488
0.27065 | 0.28334 | 0.42749 | 0.44487
0.27065 | 0.28333 | 0.42748 | 0.44486
0.27064 | 0.28332 | 0.42747 | 0.44484
0.27063 | 0.28331 | 0.42744 | 0.44483
0.27062 | 0.2833 | 0.42743 | 0.44483
0.27061 | 0.28329 | 0.42742 | 0.4448
0.2706 | 0.28328 | 0.42741 | 0.44478
0.27059 | 0.28328 | 0.4274 | 0.44478
0.27058 | 0.28327 | 0.42739 | 0.44478
0.27057 | 0.28326 | 0.42737 | 0.44477
0.27056 | 0.28325 | 0.42736 | 0.44476
0.27055 | 0.28324 | 0.42735 | 0.44475
0.27053 | 0.28323 | 0.42735 | 0.44474
0.27052 | 0.28322 | 0.42733 | 0.44473
0.27051 | 0.28321 | 0.42733 | 0.44471
0.2705 | 0.28321 | 0.42731 | 0.4447
0.27049 | 0.28319 | 0.42731 | 0.4447
0.27048 | 0.28318 | 0.42729 | 0.44468
0.27047 | 0.28317 | 0.42728 | 0.44467
0.27047 | 0.28316 | 0.42727 | 0.44465
0.27046 | 0.28316 | 0.42726 | 0.44465
0.27045 | 0.28315 | 0.42724 | 0.44464
0.27043 | 0.28314 | 0.42724 | 0.44463
0.27043 | 0.28313 | 0.42723 | 0.44461
0.27042 | 0.28312 | 0.42722 | 0.4446
0.27041 | 0.28312 | 0.42721 | 0.44459
0.2704 | 0.28311 | 0.42719 | 0.44458
0.27039 | 0.28311 | 0.42718 | 0.44457
0.27037 | 0.2831 | 0.42716 | 0.44457
0.27036 | 0.28309 | 0.42715 | 0.44456
0.27035 | 0.28308 | 0.42714 | 0.44454
0.27035 | 0.28307 | 0.42713 | 0.44454
0.27034 | 0.28306 | 0.42711 | 0.44453
0.27034 | 0.28305 | 0.4271 | 0.44452
0.27033 | 0.28304 | 0.42709 | 0.44451
0.27032 | 0.28303 | 0.42708 | 0.4445
0.27031 | 0.28302 | 0.42707 | 0.44449
0.2703 | 0.28301 | 0.42706 | 0.44448
0.27029 | 0.283 | 0.42705 | 0.44448
0.27028 | 0.28299 | 0.42704 | 0.44447
0.27028 | 0.28298 | 0.42704 | 0.44446
0.27027 | 0.28298 | 0.42703 | 0.44445
0.27025 | 0.28296 | 0.42702 | 0.44444
0.27024 | 0.28295 | 0.42701 | 0.44444
0.27023 | 0.28294 | 0.427 | 0.44442
0.27022 | 0.28294 | 0.42699 | 0.44441
0.27021 | 0.28292 | 0.42698 | 0.4444
0.2702 | 0.28291 | 0.42696 | 0.44439
0.27019 | 0.28291 | 0.42696 | 0.44437
0.27017 | 0.2829 | 0.42694 | 0.44436
0.27016 | 0.28289 | 0.42694 | 0.44436
0.27016 | 0.28288 | 0.42693 | 0.44434
0.27015 | 0.28287 | 0.42692 | 0.44433
0.27014 | 0.28286 | 0.42691 | 0.44432
0.27013 | 0.28286 | 0.42689 | 0.44431
0.27012 | 0.28284 | 0.42688 | 0.4443
0.27011 | 0.28284 | 0.42687 | 0.44428
0.27009 | 0.28283 | 0.42685 | 0.44427
0.27008 | 0.28282 | 0.42685 | 0.44426
0.27008 | 0.28281 | 0.42683 | 0.44425
0.27007 | 0.2828 | 0.42682 | 0.44424
0.27007 | 0.28279 | 0.42681 | 0.44423
0.27005 | 0.28279 | 0.4268 | 0.44421
0.27004 | 0.28277 | 0.42679 | 0.44419
0.27004 | 0.28276 | 0.42678 | 0.44418
0.27003 | 0.28276 | 0.42676 | 0.44416
0.27002 | 0.28275 | 0.42675 | 0.44416
0.27001 | 0.28274 | 0.42674 | 0.44415
0.27 | 0.28274 | 0.42673 | 0.44414
0.27 | 0.28272 | 0.42672 | 0.44413
0.26999 | 0.28271 | 0.42671 | 0.44412
0.26998 | 0.2827 | 0.4267 | 0.44411
0.26997 | 0.28269 | 0.42669 | 0.4441
0.26996 | 0.28268 | 0.42668 | 0.44409
0.26996 | 0.28267 | 0.42668 | 0.44408
0.26995 | 0.28266 | 0.42666 | 0.44406
0.26994 | 0.28265 | 0.42665 | 0.44406
0.26994 | 0.28264 | 0.42663 | 0.44404
0.26992 | 0.28264 | 0.42663 | 0.44404
0.26992 | 0.28262 | 0.42662 | 0.44403
0.2699 | 0.28261 | 0.4266 | 0.44401
0.2699 | 0.28261 | 0.4266 | 0.444
0.26989 | 0.28259 | 0.42659 | 0.44399
0.26988 | 0.28258 | 0.42657 | 0.44398
0.26987 | 0.28257 | 0.42656 | 0.44397
0.26986 | 0.28257 | 0.42654 | 0.44396
0.26985 | 0.28256 | 0.42654 | 0.44395
0.26985 | 0.28255 | 0.42652 | 0.44394
0.26983 | 0.28254 | 0.42651 | 0.44393
0.26982 | 0.28253 | 0.4265 | 0.44392
0.26981 | 0.28252 | 0.42649 | 0.44392
0.2698 | 0.28251 | 0.42648 | 0.4439
0.26979 | 0.2825 | 0.42647 | 0.44389
0.26978 | 0.28249 | 0.42645 | 0.44388
0.26977 | 0.28247 | 0.42644 | 0.44387
0.26976 | 0.28246 | 0.42643 | 0.44386
0.26976 | 0.28245 | 0.42642 | 0.44385
0.26975 | 0.28244 | 0.42641 | 0.44383
0.26974 | 0.28243 | 0.4264 | 0.44382
0.26973 | 0.28242 | 0.42639 | 0.4438
0.26972 | 0.28241 | 0.42638 | 0.4438
0.26971 | 0.28241 | 0.42637 | 0.44379
0.26971 | 0.28239 | 0.42636 | 0.44378
0.2697 | 0.28239 | 0.42635 | 0.44378
0.26968 | 0.28238 | 0.42634 | 0.44377
0.26968 | 0.28237 | 0.42634 | 0.44376
0.26966 | 0.28236 | 0.42632 | 0.44375
0.26965 | 0.28235 | 0.42631 | 0.44373
0.26964 | 0.28234 | 0.42629 | 0.44371
0.26963 | 0.28233 | 0.42628 | 0.4437
0.26963 | 0.28232 | 0.42628 | 0.44369
0.26961 | 0.28232 | 0.42625 | 0.44368
0.2696 | 0.28231 | 0.42624 | 0.44367
0.26959 | 0.2823 | 0.42624 | 0.44366
0.26958 | 0.28229 | 0.42623 | 0.44365
0.26957 | 0.28228 | 0.42621 | 0.44364
0.26957 | 0.28227 | 0.42621 | 0.44363
0.26956 | 0.28227 | 0.4262 | 0.44361
0.26955 | 0.28226 | 0.42619 | 0.44359
0.26955 | 0.28225 | 0.42616 | 0.44358
0.26953 | 0.28225 | 0.42616 | 0.44356
0.26952 | 0.28224 | 0.42615 | 0.44355
0.26951 | 0.28222 | 0.42614 | 0.44354
0.2695 | 0.28222 | 0.42614 | 0.44352
0.2695 | 0.28221 | 0.42613 | 0.44352
0.26949 | 0.2822 | 0.42611 | 0.44351
0.26948 | 0.28219 | 0.4261 | 0.44349
0.26947 | 0.28218 | 0.42609 | 0.44348
0.26947 | 0.28217 | 0.42608 | 0.44348
0.26945 | 0.28217 | 0.42607 | 0.44346
0.26944 | 0.28216 | 0.42607 | 0.44346
0.26943 | 0.28215 | 0.42606 | 0.44344
0.26943 | 0.28215 | 0.42604 | 0.44343
0.26942 | 0.28214 | 0.42603 | 0.44342
0.26941 | 0.28213 | 0.42602 | 0.44342
0.26939 | 0.28212 | 0.42602 | 0.44339
0.26938 | 0.28211 | 0.42601 | 0.44339
0.26937 | 0.2821 | 0.42599 | 0.44338
0.26936 | 0.28209 | 0.42599 | 0.44337
0.26934 | 0.28209 | 0.42597 | 0.44336
0.26933 | 0.28208 | 0.42596 | 0.44334
0.26932 | 0.28206 | 0.42594 | 0.44333
0.26932 | 0.28205 | 0.42594 | 0.44332
0.26931 | 0.28204 | 0.42593 | 0.44332
0.2693 | 0.28203 | 0.42591 | 0.44331
0.2693 | 0.28203 | 0.42591 | 0.44329
0.26929 | 0.28201 | 0.4259 | 0.44329
0.26928 | 0.28201 | 0.42589 | 0.44327
0.26928 | 0.282 | 0.42588 | 0.44327
0.26926 | 0.28199 | 0.42587 | 0.44325
0.26926 | 0.28198 | 0.42585 | 0.44323
0.26924 | 0.28197 | 0.42585 | 0.44323
0.26924 | 0.28196 | 0.42583 | 0.44322
0.26923 | 0.28195 | 0.42583 | 0.4432
0.26922 | 0.28194 | 0.42581 | 0.44319
0.26921 | 0.28194 | 0.42581 | 0.44318
0.2692 | 0.28192 | 0.4258 | 0.44316
0.26919 | 0.28191 | 0.42579 | 0.44315
0.26918 | 0.2819 | 0.42577 | 0.44313
0.26918 | 0.28189 | 0.42575 | 0.44312
0.26916 | 0.28188 | 0.42575 | 0.44312
0.26914 | 0.28187 | 0.42574 | 0.4431
0.26913 | 0.28186 | 0.42573 | 0.44307
0.26912 | 0.28186 | 0.42571 | 0.44307
0.26911 | 0.28185 | 0.4257 | 0.44305
0.26911 | 0.28184 | 0.42569 | 0.44304
0.2691 | 0.28183 | 0.42568 | 0.44303
0.26909 | 0.28182 | 0.42567 | 0.44302
0.26908 | 0.28181 | 0.42566 | 0.44302
0.26908 | 0.28181 | 0.42566 | 0.44301
0.26906 | 0.2818 | 0.42563 | 0.44299
0.26905 | 0.28179 | 0.42562 | 0.44299
0.26904 | 0.28178 | 0.42561 | 0.44297
0.26903 | 0.28176 | 0.4256 | 0.44296
0.26902 | 0.28176 | 0.42559 | 0.44296
0.269 | 0.28175 | 0.42559 | 0.44295
0.26899 | 0.28174 | 0.42557 | 0.44294
0.26898 | 0.28173 | 0.42557 | 0.44293
0.26897 | 0.28172 | 0.42556 | 0.44292
0.26897 | 0.28171 | 0.42555 | 0.44291
0.26896 | 0.2817 | 0.42554 | 0.4429
0.26895 | 0.28169 | 0.42553 | 0.44288
0.26895 | 0.28168 | 0.42551 | 0.44288
0.26893 | 0.28167 | 0.4255 | 0.44285
0.26892 | 0.28166 | 0.4255 | 0.44284
0.26892 | 0.28165 | 0.42549 | 0.44282
0.2689 | 0.28164 | 0.42548 | 0.44281
0.26889 | 0.28163 | 0.42546 | 0.4428
0.26889 | 0.28162 | 0.42546 | 0.44279
0.26888 | 0.28162 | 0.42544 | 0.44278
0.26887 | 0.28161 | 0.42544 | 0.44277
0.26886 | 0.2816 | 0.42543 | 0.44277
0.26886 | 0.28159 | 0.42542 | 0.44276
0.26885 | 0.28157 | 0.42541 | 0.44273
0.26884 | 0.28156 | 0.4254 | 0.44273
0.26883 | 0.28155 | 0.42538 | 0.44271
0.26882 | 0.28154 | 0.42537 | 0.4427
0.26881 | 0.28154 | 0.42536 | 0.44269
0.2688 | 0.28153 | 0.42535 | 0.44268
0.26879 | 0.28152 | 0.42535 | 0.44267
0.26879 | 0.28151 | 0.42533 | 0.44266
0.26878 | 0.2815 | 0.42532 | 0.44265
0.26877 | 0.28149 | 0.4253 | 0.44263
0.26875 | 0.28148 | 0.42529 | 0.44262
0.26874 | 0.28148 | 0.42528 | 0.44262
0.26873 | 0.28146 | 0.42527 | 0.4426
0.26872 | 0.28145 | 0.42526 | 0.44259
0.26872 | 0.28144 | 0.42525 | 0.44259
0.26871 | 0.28144 | 0.42523 | 0.44257
0.2687 | 0.28143 | 0.42522 | 0.44256
0.26869 | 0.28141 | 0.4252 | 0.44254
0.26867 | 0.2814 | 0.42519 | 0.44253
0.26867 | 0.28139 | 0.42519 | 0.44252
0.26866 | 0.28138 | 0.42517 | 0.44251
0.26866 | 0.28137 | 0.42516 | 0.44251
0.26865 | 0.28136 | 0.42515 | 0.4425
0.26864 | 0.28135 | 0.42514 | 0.44248
0.26864 | 0.28133 | 0.42513 | 0.44248
0.26863 | 0.28132 | 0.42511 | 0.44247
0.26862 | 0.28131 | 0.4251 | 0.44244
0.26861 | 0.2813 | 0.42508 | 0.44244
0.2686 | 0.28129 | 0.42507 | 0.44243
0.26859 | 0.28128 | 0.42506 | 0.44241
0.26858 | 0.28128 | 0.42505 | 0.4424
0.26857 | 0.28126 | 0.42505 | 0.44239
0.26856 | 0.28125 | 0.42504 | 0.44238
0.26855 | 0.28124 | 0.42503 | 0.44237
0.26855 | 0.28123 | 0.42501 | 0.44235
0.26854 | 0.28122 | 0.425 | 0.44235
0.26853 | 0.28121 | 0.42499 | 0.44233
0.26852 | 0.2812 | 0.42497 | 0.44232
0.26851 | 0.28119 | 0.42495 | 0.44231
0.26851 | 0.28119 | 0.42495 | 0.44231
0.2685 | 0.28118 | 0.42493 | 0.44229
0.26849 | 0.28116 | 0.42492 | 0.44228
0.26848 | 0.28115 | 0.42491 | 0.44226
0.26848 | 0.28115 | 0.4249 | 0.44225
0.26846 | 0.28114 | 0.42489 | 0.44224
0.26844 | 0.28113 | 0.42487 | 0.44223
0.26843 | 0.28112 | 0.42485 | 0.44222
0.26842 | 0.2811 | 0.42484 | 0.4422
0.26842 | 0.28109 | 0.42483 | 0.4422
0.26841 | 0.28108 | 0.42482 | 0.44218
0.2684 | 0.28107 | 0.42481 | 0.44217
0.26839 | 0.28106 | 0.4248 | 0.44216
0.26838 | 0.28106 | 0.42478 | 0.44215
0.26837 | 0.28104 | 0.42477 | 0.44214
0.26837 | 0.28104 | 0.42477 | 0.44213
0.26836 | 0.28103 | 0.42476 | 0.44212
0.26834 | 0.28102 | 0.42475 | 0.44211
0.26833 | 0.28101 | 0.42473 | 0.44211
0.26832 | 0.281 | 0.42472 | 0.44208
0.2683 | 0.281 | 0.42471 | 0.44206
0.26829 | 0.28098 | 0.4247 | 0.44205
0.26828 | 0.28098 | 0.42469 | 0.44204
0.26828 | 0.28097 | 0.42469 | 0.44203
0.26826 | 0.28096 | 0.42467 | 0.44203
0.26825 | 0.28095 | 0.42465 | 0.442
0.26825 | 0.28093 | 0.42464 | 0.44199
0.26824 | 0.28093 | 0.42463 | 0.44198
0.26823 | 0.28092 | 0.42462 | 0.44197
0.26821 | 0.28091 | 0.4246 | 0.44197
0.2682 | 0.2809 | 0.4246 | 0.44196
0.2682 | 0.28089 | 0.42457 | 0.44194
0.26819 | 0.28088 | 0.42456 | 0.44192
0.26818 | 0.28087 | 0.42455 | 0.44191
0.26817 | 0.28086 | 0.42454 | 0.4419
0.26816 | 0.28085 | 0.42453 | 0.44189
0.26814 | 0.28084 | 0.42451 | 0.44187
0.26813 | 0.28083 | 0.4245 | 0.44186
0.26813 | 0.28082 | 0.42448 | 0.44185
0.26812 | 0.28081 | 0.42448 | 0.44184
0.26811 | 0.2808 | 0.42446 | 0.44183
0.2681 | 0.28079 | 0.42445 | 0.44182
0.26809 | 0.28078 | 0.42444 | 0.44181
0.26808 | 0.28078 | 0.42442 | 0.4418
0.26808 | 0.28077 | 0.42442 | 0.44179
0.26807 | 0.28076 | 0.4244 | 0.44177
0.26806 | 0.28076 | 0.42439 | 0.44175
0.26805 | 0.28075 | 0.42437 | 0.44174
0.26804 | 0.28073 | 0.42436 | 0.44172
0.26803 | 0.28073 | 0.42436 | 0.44172
0.26802 | 0.28072 | 0.42434 | 0.4417
0.26802 | 0.28071 | 0.42434 | 0.44169
0.26801 | 0.2807 | 0.42432 | 0.44169
0.26799 | 0.28069 | 0.42431 | 0.44167
0.26798 | 0.28069 | 0.4243 | 0.44165
0.26797 | 0.28067 | 0.42429 | 0.44164
0.26795 | 0.28067 | 0.42428 | 0.44163
0.26794 | 0.28066 | 0.42427 | 0.44161
0.26794 | 0.28066 | 0.42425 | 0.4416
0.26793 | 0.28065 | 0.42423 | 0.44158
0.26792 | 0.28064 | 0.42422 | 0.44157
0.26791 | 0.28063 | 0.4242 | 0.44156
0.2679 | 0.28062 | 0.42418 | 0.44154
0.26789 | 0.28061 | 0.42417 | 0.44153
0.26789 | 0.2806 | 0.42416 | 0.44152
0.26788 | 0.28058 | 0.42415 | 0.44152
0.26787 | 0.28057 | 0.42415 | 0.4415
0.26787 | 0.28056 | 0.42413 | 0.44149
0.26786 | 0.28056 | 0.42411 | 0.44148
0.26785 | 0.28054 | 0.4241 | 0.44148
0.26784 | 0.28054 | 0.42409 | 0.44146
0.26784 | 0.28052 | 0.42409 | 0.44145
0.26783 | 0.28051 | 0.42408 | 0.44144
0.26782 | 0.2805 | 0.42407 | 0.44143
0.26781 | 0.28049 | 0.42406 | 0.44142
0.2678 | 0.28049 | 0.42406 | 0.44141
0.2678 | 0.28048 | 0.42403 | 0.44141
0.26779 | 0.28047 | 0.42402 | 0.44141
0.26778 | 0.28046 | 0.42401 | 0.4414
0.26778 | 0.28046 | 0.424 | 0.44138
0.26776 | 0.28045 | 0.424 | 0.44137
0.26776 | 0.28045 | 0.42399 | 0.44136
0.26775 | 0.28044 | 0.42398 | 0.44133
0.26774 | 0.28043 | 0.42396 | 0.44132
0.26773 | 0.28042 | 0.42395 | 0.44131
0.26773 | 0.28041 | 0.42394 | 0.4413
0.26772 | 0.2804 | 0.42392 | 0.44129
0.26772 | 0.2804 | 0.42391 | 0.44127
0.2677 | 0.28039 | 0.4239 | 0.44125
0.26769 | 0.28038 | 0.42389 | 0.44124
0.26768 | 0.28037 | 0.42387 | 0.44123
0.26768 | 0.28036 | 0.42385 | 0.44121
0.26766 | 0.28035 | 0.42385 | 0.4412
0.26765 | 0.28034 | 0.42384 | 0.44119
0.26764 | 0.28033 | 0.42383 | 0.44118
0.26764 | 0.28032 | 0.42381 | 0.44117
0.26763 | 0.28031 | 0.42379 | 0.44116
0.26762 | 0.2803 | 0.42378 | 0.44116
0.26761 | 0.28029 | 0.42377 | 0.44115
0.26761 | 0.28028 | 0.42375 | 0.44113
0.2676 | 0.28027 | 0.42374 | 0.44112
0.26759 | 0.28026 | 0.42373 | 0.44111
0.26759 | 0.28025 | 0.42373 | 0.4411
0.26758 | 0.28024 | 0.42372 | 0.44109
0.26757 | 0.28024 | 0.4237 | 0.44107
0.26756 | 0.28023 | 0.42369 | 0.44106
0.26755 | 0.28021 | 0.42367 | 0.44105
0.26754 | 0.2802 | 0.42365 | 0.44104
0.26753 | 0.2802 | 0.42364 | 0.44102
0.26751 | 0.28019 | 0.42362 | 0.44102
0.26751 | 0.28018 | 0.4236 | 0.44101
0.26749 | 0.28017 | 0.4236 | 0.44099
0.26748 | 0.28016 | 0.42358 | 0.44098
0.26747 | 0.28016 | 0.42357 | 0.44096
0.26746 | 0.28015 | 0.42356 | 0.44095
0.26745 | 0.28013 | 0.42355 | 0.44094
0.26744 | 0.28012 | 0.42354 | 0.44093
0.26743 | 0.28012 | 0.42353 | 0.44092
0.26742 | 0.28011 | 0.42352 | 0.4409
0.26742 | 0.2801 | 0.42351 | 0.44088
0.26741 | 0.2801 | 0.4235 | 0.44086
0.2674 | 0.28009 | 0.42349 | 0.44086
0.2674 | 0.28008 | 0.42347 | 0.44085
0.26739 | 0.28007 | 0.42347 | 0.44083
0.26737 | 0.28006 | 0.42345 | 0.44081
0.26736 | 0.28005 | 0.42345 | 0.4408
0.26736 | 0.28004 | 0.42343 | 0.44079
0.26735 | 0.28003 | 0.42342 | 0.44078
0.26734 | 0.28002 | 0.42341 | 0.44076
0.26732 | 0.28002 | 0.42339 | 0.44075
0.26732 | 0.28001 | 0.42338 | 0.44072
0.26731 | 0.28001 | 0.42337 | 0.44072
0.2673 | 0.28 | 0.42336 | 0.4407
0.26729 | 0.27999 | 0.42335 | 0.44069
0.26729 | 0.27998 | 0.42334 | 0.44068
0.26728 | 0.27997 | 0.42333 | 0.44067
0.26726 | 0.27996 | 0.42332 | 0.44067
0.26726 | 0.27996 | 0.42331 | 0.44066
0.26724 | 0.27995 | 0.4233 | 0.44064
0.26723 | 0.27994 | 0.42329 | 0.44063
0.26722 | 0.27992 | 0.42329 | 0.44062
0.26721 | 0.27992 | 0.42327 | 0.4406
0.2672 | 0.27991 | 0.42326 | 0.44059
0.26719 | 0.2799 | 0.42325 | 0.44058
0.26718 | 0.27989 | 0.42323 | 0.44057
0.26717 | 0.27987 | 0.42322 | 0.44057
0.26716 | 0.27986 | 0.42321 | 0.44056
0.26715 | 0.27985 | 0.4232 | 0.44055
0.26715 | 0.27984 | 0.42318 | 0.44053
0.26714 | 0.27983 | 0.42318 | 0.44052
0.26713 | 0.27982 | 0.42316 | 0.44051
0.26712 | 0.27982 | 0.42315 | 0.4405
0.26711 | 0.27981 | 0.42313 | 0.44048
0.2671 | 0.2798 | 0.42312 | 0.44047
0.26709 | 0.27979 | 0.42311 | 0.44045
0.26708 | 0.27978 | 0.42311 | 0.44044
0.26707 | 0.27977 | 0.42309 | 0.44042
0.26706 | 0.27976 | 0.42309 | 0.44041
0.26706 | 0.27975 | 0.42307 | 0.44039
0.26705 | 0.27973 | 0.42306 | 0.44038
0.26704 | 0.27972 | 0.42305 | 0.44037
0.26703 | 0.27971 | 0.42304 | 0.44035
0.26702 | 0.27971 | 0.42303 | 0.44035
0.26701 | 0.2797 | 0.42301 | 0.44034
0.267 | 0.27969 | 0.423 | 0.44033
0.26699 | 0.27968 | 0.42299 | 0.44032
0.26698 | 0.27966 | 0.42299 | 0.4403
0.26697 | 0.27965 | 0.42298 | 0.44028
0.26696 | 0.27964 | 0.42297 | 0.44026
0.26695 | 0.27964 | 0.42295 | 0.44026
0.26695 | 0.27963 | 0.42294 | 0.44024
0.26694 | 0.27962 | 0.42293 | 0.44022
0.26693 | 0.27961 | 0.42292 | 0.44022
0.26692 | 0.2796 | 0.4229 | 0.44021
0.26691 | 0.27959 | 0.42289 | 0.44019
0.2669 | 0.27958 | 0.42287 | 0.44018
0.2669 | 0.27957 | 0.42285 | 0.44017
0.26688 | 0.27956 | 0.42284 | 0.44015
0.26687 | 0.27955 | 0.42283 | 0.44014
0.26686 | 0.27954 | 0.42281 | 0.44013
0.26685 | 0.27953 | 0.42279 | 0.44012
0.26685 | 0.27952 | 0.42278 | 0.44011
0.26684 | 0.27952 | 0.42276 | 0.44009
0.26683 | 0.2795 | 0.42275 | 0.44007
0.26682 | 0.27949 | 0.42273 | 0.44005
0.26682 | 0.27948 | 0.42273 | 0.44004
0.26681 | 0.27947 | 0.42271 | 0.44002
0.2668 | 0.27946 | 0.42269 | 0.44001
0.26679 | 0.27945 | 0.42268 | 0.44
0.26678 | 0.27944 | 0.42268 | 0.43999
0.26677 | 0.27943 | 0.42267 | 0.43998
0.26677 | 0.27942 | 0.42266 | 0.43996
0.26676 | 0.27941 | 0.42265 | 0.43995
0.26675 | 0.2794 | 0.42264 | 0.43994
0.26674 | 0.27939 | 0.42262 | 0.43993
0.26674 | 0.27939 | 0.42261 | 0.43992
0.26673 | 0.27938 | 0.4226 | 0.43991
0.26671 | 0.27938 | 0.42259 | 0.4399
0.26671 | 0.27937 | 0.42258 | 0.43988
0.2667 | 0.27936 | 0.42258 | 0.43987
0.26669 | 0.27935 | 0.42256 | 0.43986
0.26668 | 0.27934 | 0.42254 | 0.43985
0.26667 | 0.27933 | 0.42253 | 0.43984
0.26667 | 0.27933 | 0.42251 | 0.43983
0.26666 | 0.27932 | 0.42249 | 0.43981
0.26666 | 0.27932 | 0.42249 | 0.43981
0.26664 | 0.2793 | 0.42247 | 0.4398
0.26663 | 0.27929 | 0.42247 | 0.43979
0.26662 | 0.27928 | 0.42245 | 0.43976
0.26661 | 0.27928 | 0.42244 | 0.43974
0.2666 | 0.27927 | 0.42243 | 0.43973
0.26659 | 0.27926 | 0.42241 | 0.43972
0.26659 | 0.27925 | 0.4224 | 0.4397
0.26657 | 0.27924 | 0.42237 | 0.43969
0.26656 | 0.27923 | 0.42236 | 0.43968
0.26655 | 0.27922 | 0.42235 | 0.43967
0.26655 | 0.27922 | 0.42233 | 0.43966
0.26654 | 0.27921 | 0.42232 | 0.43966
0.26653 | 0.2792 | 0.42231 | 0.43964
0.26652 | 0.27919 | 0.4223 | 0.43962
0.26651 | 0.27918 | 0.42228 | 0.43961
0.2665 | 0.27917 | 0.42227 | 0.43959
0.2665 | 0.27916 | 0.42224 | 0.43957
0.26649 | 0.27915 | 0.42223 | 0.43956
0.26648 | 0.27914 | 0.42223 | 0.43956
0.26647 | 0.27914 | 0.42222 | 0.43954
0.26646 | 0.27913 | 0.42219 | 0.43952
0.26645 | 0.27912 | 0.42218 | 0.43951
0.26644 | 0.27911 | 0.42217 | 0.43949
0.26643 | 0.2791 | 0.42217 | 0.43948
0.26642 | 0.2791 | 0.42215 | 0.43947
0.26641 | 0.27909 | 0.42214 | 0.43945
0.2664 | 0.27909 | 0.42212 | 0.43944
0.26639 | 0.27908 | 0.42211 | 0.43943
0.26638 | 0.27907 | 0.42209 | 0.43941
0.26637 | 0.27906 | 0.42208 | 0.43939
0.26636 | 0.27905 | 0.42207 | 0.43936
0.26636 | 0.27904 | 0.42205 | 0.43934
0.26635 | 0.27903 | 0.42204 | 0.43933
0.26634 | 0.27902 | 0.42203 | 0.43932
0.26633 | 0.27901 | 0.42201 | 0.43932
0.26632 | 0.27901 | 0.42201 | 0.43931
0.26631 | 0.27899 | 0.422 | 0.43929
0.26631 | 0.27899 | 0.42199 | 0.43928
0.2663 | 0.27898 | 0.42197 | 0.43927
0.2663 | 0.27897 | 0.42196 | 0.43926
0.26628 | 0.27897 | 0.42195 | 0.43925
0.26627 | 0.27896 | 0.42193 | 0.43924
0.26626 | 0.27895 | 0.42191 | 0.43923
0.26625 | 0.27894 | 0.4219 | 0.43922
0.26624 | 0.27893 | 0.42189 | 0.43921
0.26623 | 0.27892 | 0.42188 | 0.43919
0.26622 | 0.27891 | 0.42187 | 0.43919
0.26621 | 0.2789 | 0.42186 | 0.43918
0.2662 | 0.27889 | 0.42185 | 0.43917
0.26619 | 0.27888 | 0.42184 | 0.43916
0.26618 | 0.27887 | 0.42182 | 0.43915
0.26617 | 0.27886 | 0.42181 | 0.43914
0.26616 | 0.27886 | 0.42179 | 0.43912
0.26614 | 0.27884 | 0.42179 | 0.43911
0.26613 | 0.27883 | 0.42178 | 0.43909
0.26612 | 0.27882 | 0.42177 | 0.43909
0.26611 | 0.27881 | 0.42176 | 0.43907
0.2661 | 0.2788 | 0.42174 | 0.43906
0.26609 | 0.27879 | 0.42174 | 0.43905
0.26608 | 0.27878 | 0.42172 | 0.43903
0.26607 | 0.27877 | 0.42171 | 0.43903
0.26607 | 0.27876 | 0.42169 | 0.43901
0.26606 | 0.27875 | 0.42169 | 0.43898
0.26604 | 0.27875 | 0.42167 | 0.43897
0.26604 | 0.27874 | 0.42166 | 0.43897
0.26603 | 0.27873 | 0.42165 | 0.43895
0.26602 | 0.27872 | 0.42164 | 0.43894
0.26601 | 0.27871 | 0.42164 | 0.43892
0.26601 | 0.2787 | 0.42162 | 0.43891
0.266 | 0.2787 | 0.42161 | 0.43889
0.26599 | 0.27869 | 0.4216 | 0.43889
0.26598 | 0.27868 | 0.42159 | 0.43887
0.26597 | 0.27867 | 0.42157 | 0.43885
0.26596 | 0.27865 | 0.42157 | 0.43884
0.26595 | 0.27864 | 0.42156 | 0.43882
0.26595 | 0.27863 | 0.42154 | 0.4388
0.26593 | 0.27862 | 0.42153 | 0.43878
0.26593 | 0.27862 | 0.42153 | 0.43876
0.26592 | 0.27861 | 0.42151 | 0.43875
0.2659 | 0.2786 | 0.42151 | 0.43874
0.2659 | 0.27858 | 0.4215 | 0.43873
0.26589 | 0.27858 | 0.42149 | 0.43872
0.26589 | 0.27856 | 0.42147 | 0.4387
0.26588 | 0.27855 | 0.42146 | 0.43869
0.26587 | 0.27854 | 0.42145 | 0.43868
0.26585 | 0.27853 | 0.42144 | 0.43867
0.26584 | 0.27852 | 0.42143 | 0.43866
0.26583 | 0.27851 | 0.42142 | 0.43865
0.26583 | 0.27851 | 0.42141 | 0.43864
0.26582 | 0.2785 | 0.42141 | 0.43862
0.26581 | 0.27849 | 0.42139 | 0.43862
0.2658 | 0.27848 | 0.42138 | 0.43861
0.26579 | 0.27847 | 0.42137 | 0.4386
0.26579 | 0.27845 | 0.42135 | 0.43859
0.26577 | 0.27845 | 0.42134 | 0.43858
0.26576 | 0.27844 | 0.42133 | 0.43857
0.26575 | 0.27843 | 0.42132 | 0.43855
0.26574 | 0.27842 | 0.42131 | 0.43854
0.26573 | 0.27841 | 0.4213 | 0.43852
0.26572 | 0.2784 | 0.42129 | 0.43851
0.26572 | 0.27839 | 0.42129 | 0.4385
0.26571 | 0.27838 | 0.42126 | 0.43849
0.2657 | 0.27837 | 0.42126 | 0.43847
0.26569 | 0.27836 | 0.42124 | 0.43846
0.26568 | 0.27835 | 0.42123 | 0.43843
0.26567 | 0.27835 | 0.42123 | 0.43842
0.26566 | 0.27834 | 0.42121 | 0.43841
0.26565 | 0.27833 | 0.42121 | 0.4384
0.26564 | 0.27832 | 0.42118 | 0.43839
0.26564 | 0.27831 | 0.42117 | 0.43838
0.26563 | 0.2783 | 0.42115 | 0.43836
0.26561 | 0.27829 | 0.42114 | 0.43835
0.2656 | 0.27828 | 0.42113 | 0.43834
0.2656 | 0.27828 | 0.42112 | 0.43834
0.26559 | 0.27827 | 0.42111 | 0.43833
0.26558 | 0.27826 | 0.42109 | 0.4383
0.26557 | 0.27825 | 0.42108 | 0.43829
0.26556 | 0.27824 | 0.42106 | 0.43829
0.26556 | 0.27823 | 0.42106 | 0.43827
0.26555 | 0.27822 | 0.42104 | 0.43826
0.26555 | 0.27822 | 0.42103 | 0.43825
0.26554 | 0.2782 | 0.42101 | 0.43824
0.26553 | 0.27819 | 0.42101 | 0.43823
0.26552 | 0.27818 | 0.421 | 0.43822
0.26552 | 0.27817 | 0.42098 | 0.4382
0.2655 | 0.27816 | 0.42096 | 0.43819
0.26549 | 0.27815 | 0.42096 | 0.43818
0.26548 | 0.27814 | 0.42095 | 0.43816
0.26547 | 0.27813 | 0.42094 | 0.43814
0.26546 | 0.27812 | 0.42092 | 0.43813
0.26546 | 0.27812 | 0.42092 | 0.43811
0.26544 | 0.27811 | 0.42091 | 0.4381
0.26543 | 0.2781 | 0.4209 | 0.43808
0.26543 | 0.27809 | 0.42089 | 0.43807
0.26542 | 0.27808 | 0.42088 | 0.43806
0.26541 | 0.27808 | 0.42086 | 0.43804
0.26539 | 0.27807 | 0.42085 | 0.43802
0.26538 | 0.27806 | 0.42084 | 0.438
0.26537 | 0.27805 | 0.42083 | 0.43798
0.26536 | 0.27805 | 0.4208 | 0.43797
0.26535 | 0.27804 | 0.4208 | 0.43796
0.26535 | 0.27803 | 0.42078 | 0.43795
0.26534 | 0.27802 | 0.42076 | 0.43794
0.26533 | 0.27802 | 0.42076 | 0.43792
0.26532 | 0.27801 | 0.42074 | 0.43792
0.26532 | 0.278 | 0.42073 | 0.4379
0.26531 | 0.27799 | 0.42072 | 0.43789
0.2653 | 0.27798 | 0.42071 | 0.43786
0.26529 | 0.27797 | 0.4207 | 0.43786
0.26528 | 0.27796 | 0.42069 | 0.43784
0.26527 | 0.27796 | 0.42068 | 0.43783
0.26526 | 0.27795 | 0.42066 | 0.43782
0.26525 | 0.27794 | 0.42065 | 0.43781
0.26524 | 0.27794 | 0.42064 | 0.4378
0.26523 | 0.27793 | 0.42063 | 0.43779
0.26522 | 0.27792 | 0.42061 | 0.43778
0.26521 | 0.2779 | 0.4206 | 0.43776
0.2652 | 0.27789 | 0.42059 | 0.43775
0.26518 | 0.27788 | 0.42058 | 0.43773
0.26517 | 0.27788 | 0.42057 | 0.43771
0.26517 | 0.27787 | 0.42056 | 0.43768
0.26516 | 0.27785 | 0.42055 | 0.43768
0.26515 | 0.27785 | 0.42054 | 0.43767
0.26514 | 0.27784 | 0.42052 | 0.43766
0.26513 | 0.27782 | 0.4205 | 0.43764
0.26513 | 0.27781 | 0.4205 | 0.43763
0.26512 | 0.2778 | 0.42049 | 0.43762
0.26511 | 0.27779 | 0.42048 | 0.4376
0.26511 | 0.27778 | 0.42047 | 0.43759
0.2651 | 0.27777 | 0.42046 | 0.43758
0.26508 | 0.27776 | 0.42043 | 0.43758
0.26507 | 0.27775 | 0.42043 | 0.43757
0.26506 | 0.27775 | 0.42042 | 0.43754
0.26505 | 0.27774 | 0.4204 | 0.43751
0.26504 | 0.27773 | 0.42039 | 0.43751
0.26503 | 0.27772 | 0.42039 | 0.43748
0.26502 | 0.27771 | 0.42036 | 0.43747
0.26501 | 0.2777 | 0.42035 | 0.43746
0.265 | 0.2777 | 0.42033 | 0.43745
0.26499 | 0.27769 | 0.42032 | 0.43743
0.26498 | 0.27768 | 0.42031 | 0.43742
0.26497 | 0.27768 | 0.4203 | 0.43741
0.26496 | 0.27767 | 0.42029 | 0.4374
0.26496 | 0.27766 | 0.42028 | 0.43738
0.26495 | 0.27765 | 0.42027 | 0.43737
0.26494 | 0.27764 | 0.42026 | 0.43736
0.26493 | 0.27764 | 0.42025 | 0.43735
0.26492 | 0.27762 | 0.42023 | 0.43733
0.26492 | 0.27761 | 0.42022 | 0.43732
0.26491 | 0.2776 | 0.42022 | 0.43729
0.2649 | 0.2776 | 0.4202 | 0.43726
0.26489 | 0.27759 | 0.42019 | 0.43726
0.26488 | 0.27758 | 0.42018 | 0.43724
0.26488 | 0.27757 | 0.42017 | 0.43723
0.26487 | 0.27756 | 0.42016 | 0.43722
0.26486 | 0.27755 | 0.42015 | 0.4372
0.26486 | 0.27754 | 0.42013 | 0.4372
0.26485 | 0.27753 | 0.4201 | 0.43718
0.26484 | 0.27753 | 0.42009 | 0.43717
0.26483 | 0.27751 | 0.42008 | 0.43715
0.26482 | 0.27751 | 0.42007 | 0.43713
0.26481 | 0.2775 | 0.42005 | 0.43712
0.26481 | 0.27749 | 0.42004 | 0.43711
0.2648 | 0.27748 | 0.42004 | 0.43708
0.26479 | 0.27747 | 0.42003 | 0.43706
0.26478 | 0.27746 | 0.42002 | 0.43705
0.26477 | 0.27745 | 0.42001 | 0.43704
0.26476 | 0.27744 | 0.42 | 0.43702
0.26475 | 0.27744 | 0.41999 | 0.43701
0.26475 | 0.27743 | 0.41997 | 0.43699
0.26474 | 0.27741 | 0.41996 | 0.43698
0.26473 | 0.2774 | 0.41995 | 0.43696
0.26472 | 0.27739 | 0.41993 | 0.43694
0.26471 | 0.27738 | 0.41992 | 0.43692
0.26471 | 0.27737 | 0.41991 | 0.43691
0.2647 | 0.27736 | 0.4199 | 0.4369
0.26469 | 0.27736 | 0.41988 | 0.43689
0.26468 | 0.27735 | 0.41987 | 0.43688
0.26467 | 0.27734 | 0.41986 | 0.43686
0.26466 | 0.27733 | 0.41985 | 0.43684
0.26465 | 0.27733 | 0.41982 | 0.43683
0.26465 | 0.27732 | 0.4198 | 0.43682
0.26463 | 0.27731 | 0.41979 | 0.43681
0.26462 | 0.2773 | 0.41979 | 0.4368
0.26462 | 0.27729 | 0.41976 | 0.4368
0.26461 | 0.27728 | 0.41975 | 0.43678
0.2646 | 0.27727 | 0.41974 | 0.43676
0.26459 | 0.27726 | 0.41972 | 0.43675
0.26458 | 0.27726 | 0.41972 | 0.43674
0.26457 | 0.27725 | 0.4197 | 0.43672
0.26456 | 0.27724 | 0.41969 | 0.43672
0.26455 | 0.27723 | 0.41968 | 0.43671
0.26454 | 0.27722 | 0.41968 | 0.4367
0.26452 | 0.27721 | 0.41966 | 0.43669
0.26452 | 0.27721 | 0.41965 | 0.43668
0.26451 | 0.27719 | 0.41964 | 0.43667
0.2645 | 0.27718 | 0.41962 | 0.43666
0.26449 | 0.27718 | 0.41961 | 0.43664
0.26448 | 0.27717 | 0.4196 | 0.43662
0.26446 | 0.27717 | 0.41959 | 0.43661
0.26445 | 0.27716 | 0.41958 | 0.43659
0.26444 | 0.27715 | 0.41956 | 0.43657
0.26443 | 0.27714 | 0.41955 | 0.43655
0.26442 | 0.27713 | 0.41954 | 0.43654
0.26441 | 0.27712 | 0.41953 | 0.43653
0.2644 | 0.27711 | 0.41952 | 0.43652
0.26439 | 0.2771 | 0.41951 | 0.4365
0.26438 | 0.27709 | 0.41949 | 0.43649
0.26437 | 0.27708 | 0.41947 | 0.43647
0.26436 | 0.27707 | 0.41946 | 0.43645
0.26435 | 0.27706 | 0.41945 | 0.43644
0.26434 | 0.27705 | 0.41943 | 0.43642
0.26433 | 0.27704 | 0.41943 | 0.43641
0.26432 | 0.27703 | 0.41941 | 0.43639
0.26431 | 0.27703 | 0.41941 | 0.43637
0.2643 | 0.27701 | 0.41939 | 0.43636
0.26429 | 0.27701 | 0.41939 | 0.43635
0.26428 | 0.277 | 0.41937 | 0.43633
0.26428 | 0.27698 | 0.41935 | 0.43631
0.26426 | 0.27698 | 0.41935 | 0.43629
0.26425 | 0.27697 | 0.41933 | 0.43628
0.26424 | 0.27696 | 0.41932 | 0.43626
0.26424 | 0.27695 | 0.41931 | 0.43625
0.26423 | 0.27694 | 0.41929 | 0.43625
0.26422 | 0.27693 | 0.41928 | 0.43623
0.26421 | 0.27692 | 0.41926 | 0.43622
0.2642 | 0.27691 | 0.41924 | 0.43621
0.26419 | 0.27691 | 0.41923 | 0.43619
0.26418 | 0.2769 | 0.41922 | 0.43617
0.26417 | 0.27689 | 0.41921 | 0.43617
0.26416 | 0.27688 | 0.4192 | 0.43616
0.26415 | 0.27687 | 0.4192 | 0.43614
0.26415 | 0.27687 | 0.41918 | 0.43613
0.26413 | 0.27686 | 0.41918 | 0.43611
0.26413 | 0.27685 | 0.41917 | 0.4361
0.26412 | 0.27685 | 0.41915 | 0.43609
0.26411 | 0.27684 | 0.41913 | 0.43607
0.26409 | 0.27683 | 0.41912 | 0.43605
0.26408 | 0.27682 | 0.41911 | 0.43604
0.26407 | 0.27681 | 0.4191 | 0.43602
0.26406 | 0.27681 | 0.41909 | 0.43601
0.26405 | 0.2768 | 0.41908 | 0.436
0.26404 | 0.27679 | 0.41907 | 0.43598
0.26403 | 0.27678 | 0.41905 | 0.43598
0.26403 | 0.27677 | 0.41903 | 0.43596
0.26402 | 0.27677 | 0.41902 | 0.43595
0.26401 | 0.27676 | 0.41901 | 0.43594
0.264 | 0.27674 | 0.41898 | 0.43593
0.26399 | 0.27674 | 0.41897 | 0.43589
0.26398 | 0.27673 | 0.41896 | 0.43589
0.26397 | 0.27671 | 0.41894 | 0.43587
0.26397 | 0.2767 | 0.41894 | 0.43586
0.26396 | 0.27669 | 0.41893 | 0.43585
0.26395 | 0.27668 | 0.41891 | 0.43584
0.26394 | 0.27667 | 0.41891 | 0.43583
0.26393 | 0.27666 | 0.4189 | 0.43581
0.26392 | 0.27665 | 0.41887 | 0.43578
0.26391 | 0.27664 | 0.41887 | 0.43577
0.2639 | 0.27663 | 0.41886 | 0.43575
0.26389 | 0.27662 | 0.41884 | 0.43575
0.26388 | 0.27661 | 0.41882 | 0.43573
0.26387 | 0.27661 | 0.41881 | 0.43571
0.26387 | 0.2766 | 0.4188 | 0.43571
0.26386 | 0.27659 | 0.41879 | 0.43569
0.26385 | 0.27658 | 0.41878 | 0.43567
0.26384 | 0.27657 | 0.41877 | 0.43565
0.26383 | 0.27656 | 0.41875 | 0.43564
0.26383 | 0.27655 | 0.41874 | 0.43562
0.26382 | 0.27654 | 0.41874 | 0.4356
0.26381 | 0.27654 | 0.41873 | 0.43558
0.26379 | 0.27652 | 0.41872 | 0.43557
0.26379 | 0.27651 | 0.41871 | 0.43555
0.26378 | 0.2765 | 0.41871 | 0.43552
0.26376 | 0.27649 | 0.41869 | 0.43552
0.26375 | 0.27649 | 0.41868 | 0.43549
0.26374 | 0.27648 | 0.41867 | 0.43549
0.26374 | 0.27647 | 0.41865 | 0.43547
0.26373 | 0.27646 | 0.41865 | 0.43545
0.26372 | 0.27645 | 0.41862 | 0.43543
0.26371 | 0.27644 | 0.4186 | 0.43542
0.2637 | 0.27643 | 0.41859 | 0.43541
0.26369 | 0.27642 | 0.41859 | 0.4354
0.26368 | 0.27641 | 0.41856 | 0.43538
0.26368 | 0.2764 | 0.41854 | 0.43536
0.26367 | 0.27639 | 0.41852 | 0.43534
0.26366 | 0.27638 | 0.4185 | 0.43532
0.26365 | 0.27637 | 0.41849 | 0.4353
0.26364 | 0.27636 | 0.41849 | 0.43529
0.26363 | 0.27636 | 0.41848 | 0.43528
0.26362 | 0.27635 | 0.41847 | 0.43526
0.26361 | 0.27634 | 0.41846 | 0.43524
0.2636 | 0.27633 | 0.41845 | 0.43522
0.26359 | 0.27633 | 0.41844 | 0.4352
0.26358 | 0.27632 | 0.41843 | 0.43518
0.26357 | 0.27631 | 0.41841 | 0.43517
0.26356 | 0.27631 | 0.41841 | 0.43516
0.26355 | 0.2763 | 0.4184 | 0.43514
0.26354 | 0.27629 | 0.41839 | 0.43512
0.26353 | 0.27628 | 0.41838 | 0.43512
0.26352 | 0.27628 | 0.41837 | 0.43511
0.26351 | 0.27627 | 0.41835 | 0.4351
0.2635 | 0.27626 | 0.41835 | 0.43508
0.26349 | 0.27626 | 0.41833 | 0.43507
0.26348 | 0.27625 | 0.41831 | 0.43506
0.26347 | 0.27625 | 0.4183 | 0.43505
0.26346 | 0.27624 | 0.41829 | 0.43503
0.26344 | 0.27624 | 0.41827 | 0.43503
0.26343 | 0.27623 | 0.41826 | 0.43501
0.26342 | 0.27622 | 0.41825 | 0.43499
0.26341 | 0.2762 | 0.41824 | 0.43498
0.2634 | 0.2762 | 0.41823 | 0.43496
0.26339 | 0.27619 | 0.41822 | 0.43495
0.26338 | 0.27619 | 0.41821 | 0.43494
0.26337 | 0.27617 | 0.4182 | 0.43492
0.26336 | 0.27616 | 0.41818 | 0.43491
0.26335 | 0.27615 | 0.41817 | 0.43489
0.26334 | 0.27614 | 0.41816 | 0.43487
0.26333 | 0.27613 | 0.41815 | 0.43486
0.26332 | 0.27612 | 0.41812 | 0.43485
0.26332 | 0.27611 | 0.41811 | 0.43485
0.26331 | 0.2761 | 0.4181 | 0.43484
0.2633 | 0.27609 | 0.41809 | 0.43482
0.26329 | 0.27608 | 0.41808 | 0.4348
0.26328 | 0.27607 | 0.41807 | 0.43479
0.26328 | 0.27606 | 0.41807 | 0.43478
0.26327 | 0.27606 | 0.41805 | 0.43476
0.26326 | 0.27605 | 0.41804 | 0.43475
0.26325 | 0.27604 | 0.41803 | 0.43473
0.26324 | 0.27603 | 0.41802 | 0.43471
0.26323 | 0.27602 | 0.41801 | 0.43468
0.26323 | 0.27601 | 0.41799 | 0.43465
0.26322 | 0.276 | 0.41797 | 0.43464
0.2632 | 0.27599 | 0.41796 | 0.43462
0.26319 | 0.27598 | 0.41795 | 0.43461
0.26319 | 0.27597 | 0.41794 | 0.4346
0.26318 | 0.27596 | 0.41793 | 0.43459
0.26317 | 0.27596 | 0.41792 | 0.43457
0.26316 | 0.27595 | 0.4179 | 0.43455
0.26315 | 0.27594 | 0.41789 | 0.43453
0.26314 | 0.27593 | 0.41788 | 0.43452
0.26313 | 0.27592 | 0.41786 | 0.43451
0.26312 | 0.27591 | 0.41784 | 0.43449
0.26311 | 0.27591 | 0.41783 | 0.43447
0.2631 | 0.2759 | 0.41781 | 0.43445
0.26309 | 0.27589 | 0.41779 | 0.43445
0.26308 | 0.27588 | 0.41778 | 0.43443
0.26307 | 0.27588 | 0.41776 | 0.43441
0.26306 | 0.27587 | 0.41775 | 0.4344
0.26305 | 0.27587 | 0.41772 | 0.43438
0.26304 | 0.27586 | 0.41772 | 0.43436
0.26303 | 0.27585 | 0.41771 | 0.43435
0.26302 | 0.27584 | 0.4177 | 0.43434
0.26301 | 0.27583 | 0.41768 | 0.43433
0.263 | 0.27582 | 0.41767 | 0.43431
0.26299 | 0.27582 | 0.41765 | 0.4343
0.26298 | 0.27581 | 0.41764 | 0.43429
0.26296 | 0.2758 | 0.41762 | 0.43428
0.26296 | 0.27578 | 0.41761 | 0.43425
0.26295 | 0.27577 | 0.4176 | 0.43424
0.26293 | 0.27576 | 0.41759 | 0.43423
0.26293 | 0.27576 | 0.41757 | 0.43421
0.26292 | 0.27575 | 0.41756 | 0.43419
0.26292 | 0.27574 | 0.41755 | 0.43418
0.2629 | 0.27573 | 0.41753 | 0.43417
0.26289 | 0.27572 | 0.41749 | 0.43416
0.26289 | 0.27571 | 0.41748 | 0.43413
0.26288 | 0.2757 | 0.41746 | 0.43412
0.26287 | 0.27569 | 0.41745 | 0.43409
0.26286 | 0.27569 | 0.41743 | 0.43408
0.26285 | 0.27568 | 0.41743 | 0.43407
0.26284 | 0.27567 | 0.41742 | 0.43406
0.26283 | 0.27566 | 0.4174 | 0.43404
0.26282 | 0.27565 | 0.41739 | 0.43403
0.26281 | 0.27564 | 0.41738 | 0.43402
0.2628 | 0.27563 | 0.41735 | 0.43401
0.26279 | 0.27562 | 0.41733 | 0.43398
0.26277 | 0.27561 | 0.41731 | 0.43396
0.26276 | 0.27559 | 0.4173 | 0.43395
0.26275 | 0.27558 | 0.41729 | 0.43394
0.26274 | 0.27558 | 0.41727 | 0.43393
0.26273 | 0.27556 | 0.41726 | 0.43392
0.26272 | 0.27555 | 0.41724 | 0.4339
0.26271 | 0.27554 | 0.41724 | 0.43389
0.26271 | 0.27553 | 0.41722 | 0.43387
0.26269 | 0.27552 | 0.41721 | 0.43385
0.26268 | 0.27551 | 0.41719 | 0.43384
0.26268 | 0.27551 | 0.41718 | 0.43382
0.26266 | 0.2755 | 0.41717 | 0.4338
0.26266 | 0.27549 | 0.41716 | 0.43379
0.26264 | 0.27549 | 0.41715 | 0.43376
0.26264 | 0.27548 | 0.41714 | 0.43374
0.26263 | 0.27546 | 0.41713 | 0.43373
0.26262 | 0.27546 | 0.41712 | 0.43372
0.26261 | 0.27545 | 0.4171 | 0.43371
0.2626 | 0.27544 | 0.41709 | 0.43369
0.26259 | 0.27543 | 0.41708 | 0.43368
0.26258 | 0.27542 | 0.41705 | 0.43367
0.26257 | 0.27541 | 0.41704 | 0.43365
0.26255 | 0.2754 | 0.41703 | 0.43364
0.26254 | 0.27539 | 0.41701 | 0.43363
0.26253 | 0.27538 | 0.417 | 0.43362
0.26253 | 0.27537 | 0.41699 | 0.43361
0.26251 | 0.27536 | 0.41697 | 0.4336
0.2625 | 0.27536 | 0.41696 | 0.43359
0.26249 | 0.27534 | 0.41694 | 0.43356
0.26248 | 0.27534 | 0.41692 | 0.43354
0.26247 | 0.27532 | 0.41691 | 0.43354
0.26246 | 0.27531 | 0.4169 | 0.43352
0.26245 | 0.2753 | 0.4169 | 0.43351
0.26244 | 0.27529 | 0.41685 | 0.4335
0.26243 | 0.27528 | 0.41684 | 0.43348
0.26242 | 0.27527 | 0.41683 | 0.43347
0.26241 | 0.27526 | 0.41682 | 0.43345
0.2624 | 0.27526 | 0.41681 | 0.43344
0.26239 | 0.27525 | 0.4168 | 0.43343
0.26239 | 0.27524 | 0.41678 | 0.43342
0.26238 | 0.27523 | 0.41677 | 0.43339
0.26237 | 0.27521 | 0.41675 | 0.43339
0.26236 | 0.27521 | 0.41675 | 0.43337
0.26235 | 0.27519 | 0.41674 | 0.43336
0.26234 | 0.27518 | 0.41673 | 0.43334
0.26234 | 0.27518 | 0.41671 | 0.43333
0.26233 | 0.27517 | 0.4167 | 0.43332
0.26232 | 0.27516 | 0.41669 | 0.43329
0.2623 | 0.27515 | 0.41667 | 0.43328
0.2623 | 0.27514 | 0.41667 | 0.43325
0.26228 | 0.27513 | 0.41666 | 0.43324
0.26227 | 0.27513 | 0.41664 | 0.43323
0.26226 | 0.27511 | 0.41663 | 0.4332
0.26225 | 0.2751 | 0.41661 | 0.43319
0.26223 | 0.2751 | 0.41658 | 0.43318
0.26223 | 0.27509 | 0.41656 | 0.43316
0.26222 | 0.27507 | 0.41654 | 0.43313
0.26221 | 0.27506 | 0.41654 | 0.43311
0.2622 | 0.27505 | 0.41652 | 0.43311
0.26218 | 0.27504 | 0.41651 | 0.43308
0.26218 | 0.27503 | 0.4165 | 0.43307
0.26216 | 0.27502 | 0.41649 | 0.43306
0.26215 | 0.27501 | 0.41647 | 0.43304
0.26215 | 0.275 | 0.41646 | 0.43303
0.26214 | 0.27499 | 0.41645 | 0.43302
0.26213 | 0.27499 | 0.41644 | 0.43301
0.26212 | 0.27498 | 0.41642 | 0.43299
0.26211 | 0.27497 | 0.41641 | 0.43297
0.2621 | 0.27497 | 0.41641 | 0.43295
0.26209 | 0.27496 | 0.4164 | 0.43294
0.26209 | 0.27495 | 0.41639 | 0.43292
0.26208 | 0.27494 | 0.41637 | 0.43291
0.26207 | 0.27493 | 0.41637 | 0.43289
0.26206 | 0.27493 | 0.41635 | 0.43288
0.26205 | 0.27492 | 0.41633 | 0.43287
0.26204 | 0.27491 | 0.41631 | 0.43284
0.26203 | 0.2749 | 0.4163 | 0.43281
0.26203 | 0.27489 | 0.41628 | 0.4328
0.26202 | 0.27488 | 0.41627 | 0.43278
0.26201 | 0.27487 | 0.41625 | 0.43277
0.262 | 0.27487 | 0.41624 | 0.43276
0.26199 | 0.27486 | 0.41623 | 0.43275
0.26198 | 0.27485 | 0.41622 | 0.43272
0.26197 | 0.27484 | 0.41622 | 0.4327
0.26197 | 0.27483 | 0.41621 | 0.43267
0.26196 | 0.27482 | 0.41619 | 0.43266
0.26195 | 0.27481 | 0.41618 | 0.43265
0.26194 | 0.2748 | 0.41616 | 0.43262
0.26193 | 0.2748 | 0.41615 | 0.43259
0.26192 | 0.27478 | 0.41613 | 0.43258
0.26191 | 0.27477 | 0.41611 | 0.43257
0.2619 | 0.27476 | 0.41609 | 0.43256
0.26189 | 0.27475 | 0.41609 | 0.43255
0.26187 | 0.27473 | 0.41607 | 0.43254
0.26186 | 0.27472 | 0.41606 | 0.43251
0.26186 | 0.27471 | 0.41605 | 0.43249
0.26185 | 0.27471 | 0.41605 | 0.43246
0.26185 | 0.2747 | 0.41602 | 0.43244
0.26183 | 0.27469 | 0.41601 | 0.43243
0.26183 | 0.27468 | 0.41599 | 0.43241
0.26181 | 0.27467 | 0.41596 | 0.4324
0.26181 | 0.27466 | 0.41595 | 0.43239
0.2618 | 0.27465 | 0.41595 | 0.43237
0.26179 | 0.27465 | 0.41594 | 0.43235
0.26178 | 0.27464 | 0.41591 | 0.43234
0.26176 | 0.27463 | 0.41591 | 0.43232
0.26176 | 0.27462 | 0.41589 | 0.4323
0.26175 | 0.27461 | 0.41587 | 0.43228
0.26174 | 0.2746 | 0.41585 | 0.43226
0.26173 | 0.27459 | 0.41584 | 0.43224
0.26172 | 0.27458 | 0.41583 | 0.43222
0.26171 | 0.27456 | 0.41581 | 0.4322
0.2617 | 0.27456 | 0.4158 | 0.43219
0.26169 | 0.27455 | 0.41579 | 0.43218
0.26169 | 0.27454 | 0.41578 | 0.43216
0.26167 | 0.27453 | 0.41577 | 0.43215
0.26166 | 0.27452 | 0.41576 | 0.43214
0.26165 | 0.27451 | 0.41576 | 0.43212
0.26164 | 0.2745 | 0.41575 | 0.43211
0.26163 | 0.27449 | 0.41573 | 0.43208
0.26162 | 0.27448 | 0.41573 | 0.43207
0.26161 | 0.27446 | 0.41572 | 0.43205
0.26161 | 0.27445 | 0.41571 | 0.43203
0.2616 | 0.27445 | 0.41569 | 0.43201
0.26159 | 0.27444 | 0.41567 | 0.43199
0.26158 | 0.27443 | 0.41565 | 0.43197
0.26157 | 0.27442 | 0.41562 | 0.43195
0.26156 | 0.27442 | 0.41561 | 0.43194
0.26155 | 0.27441 | 0.4156 | 0.43191
0.26154 | 0.27441 | 0.41557 | 0.43189
0.26153 | 0.2744 | 0.41554 | 0.43187
0.26151 | 0.27439 | 0.41553 | 0.43185
0.26151 | 0.27438 | 0.41551 | 0.43184
0.2615 | 0.27436 | 0.4155 | 0.43183
0.26149 | 0.27435 | 0.41548 | 0.43182
0.26147 | 0.27434 | 0.41547 | 0.4318
0.26147 | 0.27433 | 0.41545 | 0.43178
0.26146 | 0.27432 | 0.41545 | 0.43177
0.26145 | 0.27431 | 0.41543 | 0.43175
0.26144 | 0.2743 | 0.41541 | 0.43173
0.26143 | 0.27429 | 0.41539 | 0.43172
0.26142 | 0.27428 | 0.41537 | 0.43169
0.26141 | 0.27427 | 0.41535 | 0.43167
0.2614 | 0.27426 | 0.41533 | 0.43166
0.26139 | 0.27426 | 0.41532 | 0.43164
0.26138 | 0.27425 | 0.41531 | 0.43163
0.26137 | 0.27424 | 0.4153 | 0.43161
0.26137 | 0.27423 | 0.41528 | 0.43159
0.26136 | 0.27422 | 0.41527 | 0.43157
0.26135 | 0.27421 | 0.41525 | 0.43155
0.26134 | 0.2742 | 0.41524 | 0.43151
0.26133 | 0.27419 | 0.41522 | 0.43151
0.26133 | 0.27418 | 0.4152 | 0.43149
0.26132 | 0.27417 | 0.41518 | 0.43147
0.2613 | 0.27416 | 0.41517 | 0.43145
0.2613 | 0.27415 | 0.41516 | 0.43143
0.26129 | 0.27414 | 0.41515 | 0.43142
0.26127 | 0.27413 | 0.41514 | 0.4314
0.26126 | 0.27412 | 0.41512 | 0.43139
0.26125 | 0.27411 | 0.4151 | 0.43138
0.26125 | 0.2741 | 0.41508 | 0.43138
0.26124 | 0.2741 | 0.41507 | 0.43136
0.26124 | 0.27409 | 0.41506 | 0.43134
0.26123 | 0.27408 | 0.41504 | 0.43133
0.26122 | 0.27407 | 0.41503 | 0.43131
0.26121 | 0.27405 | 0.41502 | 0.4313
0.2612 | 0.27404 | 0.41501 | 0.43129
0.26119 | 0.27403 | 0.41499 | 0.43128
0.26118 | 0.27402 | 0.41497 | 0.43126
0.26117 | 0.27401 | 0.41495 | 0.43125
0.26116 | 0.274 | 0.41492 | 0.43123
0.26115 | 0.27399 | 0.41491 | 0.43123
0.26114 | 0.27398 | 0.4149 | 0.4312
0.26113 | 0.27397 | 0.41489 | 0.43119
0.26112 | 0.27396 | 0.41486 | 0.43117
0.26112 | 0.27396 | 0.41485 | 0.43116
0.26111 | 0.27395 | 0.41483 | 0.43115
0.2611 | 0.27394 | 0.4148 | 0.43112
0.26109 | 0.27394 | 0.4148 | 0.43111
0.26109 | 0.27393 | 0.41478 | 0.43109
0.26107 | 0.27391 | 0.41476 | 0.43106
0.26106 | 0.27391 | 0.41475 | 0.43105
0.26105 | 0.2739 | 0.41473 | 0.43103
0.26104 | 0.27388 | 0.41471 | 0.431
0.26103 | 0.27386 | 0.4147 | 0.43098
0.26103 | 0.27386 | 0.41468 | 0.43096
0.26102 | 0.27385 | 0.41467 | 0.43095
0.26101 | 0.27384 | 0.41465 | 0.43094
0.26099 | 0.27384 | 0.41463 | 0.43093
0.26098 | 0.27383 | 0.41462 | 0.43091
0.26098 | 0.27382 | 0.41462 | 0.43089
0.26097 | 0.27381 | 0.4146 | 0.43088
0.26096 | 0.27379 | 0.41457 | 0.43087
0.26095 | 0.27378 | 0.41455 | 0.43085
0.26094 | 0.27377 | 0.41454 | 0.43084
0.26093 | 0.27377 | 0.41451 | 0.43082
0.26092 | 0.27376 | 0.41449 | 0.43081
0.26091 | 0.27375 | 0.41447 | 0.43079
0.2609 | 0.27374 | 0.41446 | 0.43078
0.26089 | 0.27373 | 0.41445 | 0.43076
0.26088 | 0.27372 | 0.41443 | 0.43074
0.26087 | 0.27371 | 0.41442 | 0.43073
0.26086 | 0.27369 | 0.41441 | 0.43071
0.26085 | 0.27369 | 0.41439 | 0.4307
0.26084 | 0.27368 | 0.41438 | 0.43067
0.26083 | 0.27368 | 0.41436 | 0.43065
0.26082 | 0.27366 | 0.41435 | 0.43063
0.26081 | 0.27365 | 0.41434 | 0.43062
0.2608 | 0.27365 | 0.41433 | 0.4306
0.26079 | 0.27363 | 0.41431 | 0.43058
0.26078 | 0.27363 | 0.41431 | 0.43057
0.26077 | 0.27362 | 0.4143 | 0.43055
0.26077 | 0.27362 | 0.41428 | 0.43054
0.26076 | 0.27361 | 0.41427 | 0.43052
0.26075 | 0.2736 | 0.41425 | 0.43049
0.26074 | 0.27359 | 0.41422 | 0.43047
0.26073 | 0.27358 | 0.4142 | 0.43045
0.26073 | 0.27357 | 0.41418 | 0.43043
0.26072 | 0.27357 | 0.41416 | 0.43043
0.26072 | 0.27356 | 0.41414 | 0.43041
0.26071 | 0.27355 | 0.41412 | 0.43039
0.2607 | 0.27353 | 0.41411 | 0.43037
0.26069 | 0.27352 | 0.4141 | 0.43035
0.26069 | 0.27352 | 0.41409 | 0.43034
0.26068 | 0.27351 | 0.41407 | 0.43032
0.26067 | 0.2735 | 0.41405 | 0.4303
0.26066 | 0.27349 | 0.41403 | 0.43027
0.26065 | 0.27348 | 0.41402 | 0.43026
0.26064 | 0.27347 | 0.414 | 0.43023
0.26063 | 0.27346 | 0.41398 | 0.43022
0.26063 | 0.27345 | 0.41398 | 0.4302
0.26062 | 0.27345 | 0.41396 | 0.43019
0.26061 | 0.27344 | 0.41395 | 0.43017
0.2606 | 0.27343 | 0.41392 | 0.43015
0.26059 | 0.27343 | 0.41391 | 0.43014
0.26058 | 0.27342 | 0.4139 | 0.43011
0.26057 | 0.27342 | 0.41389 | 0.43009
0.26055 | 0.27341 | 0.41388 | 0.43008
0.26055 | 0.27341 | 0.41386 | 0.43007
0.26054 | 0.2734 | 0.41386 | 0.43005
0.26053 | 0.27339 | 0.41384 | 0.43003
0.26052 | 0.27338 | 0.41383 | 0.43
0.26051 | 0.27336 | 0.41381 | 0.42998
0.2605 | 0.27335 | 0.4138 | 0.42997
0.2605 | 0.27335 | 0.41379 | 0.42996
0.26048 | 0.27334 | 0.41378 | 0.42993
0.26047 | 0.27333 | 0.41377 | 0.42992
0.26046 | 0.27332 | 0.41375 | 0.42991
0.26045 | 0.27331 | 0.41373 | 0.42987
0.26044 | 0.2733 | 0.41371 | 0.42985
0.26043 | 0.2733 | 0.41369 | 0.42983
0.26043 | 0.27328 | 0.41367 | 0.42982
0.26042 | 0.27328 | 0.41365 | 0.42981
0.26041 | 0.27327 | 0.41364 | 0.42979
0.2604 | 0.27326 | 0.41362 | 0.42977
0.26039 | 0.27325 | 0.41361 | 0.42975
0.26039 | 0.27325 | 0.41359 | 0.42975
0.26038 | 0.27324 | 0.41357 | 0.42974
0.26037 | 0.27323 | 0.41356 | 0.42973
0.26036 | 0.27321 | 0.41355 | 0.42972
0.26035 | 0.27321 | 0.41354 | 0.4297
0.26034 | 0.2732 | 0.41351 | 0.42969
0.26033 | 0.27319 | 0.4135 | 0.42967
0.26032 | 0.27318 | 0.41347 | 0.42966
0.26031 | 0.27317 | 0.41344 | 0.42965
0.2603 | 0.27316 | 0.41342 | 0.42964
0.2603 | 0.27316 | 0.4134 | 0.42963
0.26028 | 0.27315 | 0.41339 | 0.42961
0.26028 | 0.27314 | 0.41338 | 0.42959
0.26027 | 0.27313 | 0.41336 | 0.42957
0.26026 | 0.27312 | 0.41336 | 0.42954
0.26025 | 0.27312 | 0.41333 | 0.42951
0.26024 | 0.2731 | 0.41331 | 0.42948
0.26024 | 0.27309 | 0.41329 | 0.42947
0.26023 | 0.27309 | 0.41328 | 0.42946
0.26022 | 0.27308 | 0.41325 | 0.42944
0.26021 | 0.27307 | 0.41323 | 0.42943
0.26019 | 0.27306 | 0.41322 | 0.4294
0.26019 | 0.27304 | 0.4132 | 0.42939
0.26018 | 0.27303 | 0.41319 | 0.42937
0.26017 | 0.27302 | 0.41317 | 0.42935
0.26016 | 0.27301 | 0.41316 | 0.42934
0.26015 | 0.27301 | 0.41315 | 0.42931
0.26014 | 0.273 | 0.41314 | 0.42929
0.26013 | 0.27299 | 0.41311 | 0.42927
0.26012 | 0.27298 | 0.4131 | 0.42924
0.26012 | 0.27298 | 0.41309 | 0.42921
0.26011 | 0.27296 | 0.41309 | 0.42919
0.2601 | 0.27295 | 0.41307 | 0.42918
0.26009 | 0.27294 | 0.41305 | 0.42917
0.26009 | 0.27293 | 0.41303 | 0.42916
0.26008 | 0.27292 | 0.41301 | 0.42914
0.26008 | 0.27292 | 0.413 | 0.42913
0.26006 | 0.27291 | 0.41298 | 0.4291
0.26005 | 0.27289 | 0.41296 | 0.42908
0.26004 | 0.27288 | 0.41294 | 0.42907
0.26004 | 0.27287 | 0.41293 | 0.42905
0.26003 | 0.27287 | 0.41291 | 0.42902
0.26001 | 0.27286 | 0.41289 | 0.429
0.26 | 0.27285 | 0.41288 | 0.42899
0.26 | 0.27284 | 0.41286 | 0.42898
0.25999 | 0.27283 | 0.41284 | 0.42896
0.25998 | 0.27282 | 0.41282 | 0.42895
0.25997 | 0.27281 | 0.41281 | 0.42893
0.25996 | 0.2728 | 0.4128 | 0.42892
0.25994 | 0.27279 | 0.41278 | 0.42889
0.25993 | 0.27278 | 0.41277 | 0.42887
0.25992 | 0.27277 | 0.41276 | 0.42887
0.2599 | 0.27277 | 0.41275 | 0.42885
0.25989 | 0.27276 | 0.41273 | 0.42884
0.25987 | 0.27275 | 0.41272 | 0.42881
0.25986 | 0.27274 | 0.4127 | 0.42879
0.25985 | 0.27273 | 0.41269 | 0.42876
0.25984 | 0.27273 | 0.41267 | 0.42874
0.25983 | 0.27272 | 0.41266 | 0.42872
0.25982 | 0.27271 | 0.41264 | 0.42868
0.25982 | 0.2727 | 0.41263 | 0.42867
0.25981 | 0.2727 | 0.41261 | 0.42865
0.25981 | 0.27269 | 0.41258 | 0.42864
0.2598 | 0.27268 | 0.41256 | 0.42861
0.25979 | 0.27267 | 0.41254 | 0.4286
0.25978 | 0.27266 | 0.41253 | 0.42859
0.25977 | 0.27265 | 0.4125 | 0.42856
0.25977 | 0.27265 | 0.4125 | 0.42855
0.25976 | 0.27264 | 0.41248 | 0.42853
0.25975 | 0.27263 | 0.41246 | 0.42851
0.25974 | 0.27263 | 0.41244 | 0.42849
0.25973 | 0.27262 | 0.41243 | 0.42848
0.25973 | 0.27262 | 0.41241 | 0.42846
0.25972 | 0.27261 | 0.41239 | 0.42844
0.25971 | 0.2726 | 0.41235 | 0.42843
0.2597 | 0.2726 | 0.41234 | 0.42842
0.25969 | 0.27259 | 0.41231 | 0.42841
0.25968 | 0.27258 | 0.4123 | 0.4284
0.25967 | 0.27258 | 0.41228 | 0.42837
0.25966 | 0.27257 | 0.41227 | 0.42836
0.25965 | 0.27255 | 0.41224 | 0.42835
0.25964 | 0.27255 | 0.41222 | 0.42832
0.25963 | 0.27254 | 0.4122 | 0.4283
0.25962 | 0.27253 | 0.41219 | 0.42828
0.25962 | 0.27253 | 0.41217 | 0.42827
0.2596 | 0.27252 | 0.41214 | 0.42825
0.2596 | 0.27251 | 0.41214 | 0.42823
0.25959 | 0.2725 | 0.41212 | 0.42822
0.25957 | 0.27249 | 0.4121 | 0.4282
0.25956 | 0.27248 | 0.41209 | 0.42818
0.25955 | 0.27247 | 0.41208 | 0.42816
0.25955 | 0.27247 | 0.41206 | 0.42815
0.25954 | 0.27245 | 0.41204 | 0.42814
0.25953 | 0.27244 | 0.41203 | 0.42813
0.25952 | 0.27244 | 0.41202 | 0.42811
0.25951 | 0.27243 | 0.41201 | 0.4281
0.2595 | 0.27242 | 0.41199 | 0.42809
0.25949 | 0.2724 | 0.41198 | 0.42807
0.25948 | 0.2724 | 0.41195 | 0.42805
0.25947 | 0.27239 | 0.41194 | 0.42803
0.25946 | 0.27238 | 0.41191 | 0.42801
0.25945 | 0.27237 | 0.41191 | 0.428
0.25945 | 0.27236 | 0.41189 | 0.42797
0.25944 | 0.27236 | 0.41187 | 0.42795
0.25943 | 0.27235 | 0.41187 | 0.42792
0.25942 | 0.27235 | 0.41186 | 0.42791
0.25941 | 0.27233 | 0.41184 | 0.42789
0.2594 | 0.27233 | 0.41181 | 0.42788
0.25939 | 0.27231 | 0.4118 | 0.42787
0.25938 | 0.2723 | 0.41178 | 0.42785
0.25937 | 0.2723 | 0.41176 | 0.42784
0.25936 | 0.27229 | 0.41173 | 0.42781
0.25935 | 0.27228 | 0.4117 | 0.4278
0.25934 | 0.27227 | 0.41169 | 0.42778
0.25933 | 0.27227 | 0.41168 | 0.42776
0.25932 | 0.27226 | 0.41166 | 0.42775
0.25931 | 0.27225 | 0.41164 | 0.42773
0.25929 | 0.27224 | 0.4116 | 0.42771
0.25928 | 0.27223 | 0.41159 | 0.42768
0.25927 | 0.27222 | 0.41156 | 0.42767
0.25926 | 0.27222 | 0.41155 | 0.42765
0.25925 | 0.27221 | 0.41153 | 0.42764
0.25924 | 0.2722 | 0.41151 | 0.42762
0.25923 | 0.27219 | 0.4115 | 0.4276
0.25921 | 0.27219 | 0.41149 | 0.42758
0.2592 | 0.27218 | 0.41144 | 0.42756
0.25919 | 0.27217 | 0.41142 | 0.42756
0.25919 | 0.27216 | 0.4114 | 0.42755
0.25918 | 0.27215 | 0.41137 | 0.42753
0.25917 | 0.27215 | 0.41136 | 0.42752
0.25916 | 0.27213 | 0.41135 | 0.42749
0.25915 | 0.27213 | 0.41133 | 0.42748
0.25913 | 0.27212 | 0.41131 | 0.42747
0.25913 | 0.27211 | 0.41129 | 0.42746
0.25912 | 0.27209 | 0.41128 | 0.42743
0.25911 | 0.27208 | 0.41127 | 0.42742
0.2591 | 0.27208 | 0.41125 | 0.4274
0.25909 | 0.27206 | 0.41122 | 0.42737
0.25908 | 0.27205 | 0.4112 | 0.42736
0.25907 | 0.27205 | 0.41118 | 0.42734
0.25906 | 0.27203 | 0.41117 | 0.42733
0.25906 | 0.27203 | 0.41114 | 0.42731
0.25905 | 0.27202 | 0.41112 | 0.4273
0.25905 | 0.27201 | 0.41112 | 0.42727
0.25904 | 0.272 | 0.4111 | 0.42725
0.25903 | 0.27199 | 0.41108 | 0.42724
0.25901 | 0.27198 | 0.41106 | 0.42722
0.259 | 0.27197 | 0.41104 | 0.42721
0.259 | 0.27196 | 0.41102 | 0.42719
0.25899 | 0.27195 | 0.41099 | 0.42717
0.25897 | 0.27194 | 0.41098 | 0.42715
0.25896 | 0.27193 | 0.41096 | 0.42713
0.25895 | 0.27192 | 0.41094 | 0.42711
0.25894 | 0.27191 | 0.41094 | 0.4271
0.25894 | 0.27191 | 0.41092 | 0.42708
0.25892 | 0.2719 | 0.41092 | 0.42706
0.25892 | 0.27189 | 0.4109 | 0.42705
0.25891 | 0.27189 | 0.41089 | 0.42701
0.2589 | 0.27188 | 0.41086 | 0.427
0.25888 | 0.27187 | 0.41084 | 0.42698
0.25887 | 0.27187 | 0.41083 | 0.42697
0.25886 | 0.27186 | 0.4108 | 0.42695
0.25885 | 0.27186 | 0.41079 | 0.42693
0.25884 | 0.27185 | 0.41078 | 0.42692
0.25883 | 0.27184 | 0.41076 | 0.4269
0.25882 | 0.27183 | 0.41073 | 0.42689
0.25881 | 0.27182 | 0.41072 | 0.42687
0.2588 | 0.27182 | 0.4107 | 0.42686
0.25879 | 0.27181 | 0.41068 | 0.42684
0.25878 | 0.2718 | 0.41067 | 0.42682
0.25878 | 0.27179 | 0.41065 | 0.4268
0.25877 | 0.27179 | 0.41063 | 0.42679
0.25876 | 0.27178 | 0.41062 | 0.42678
0.25875 | 0.27177 | 0.41061 | 0.42677
0.25874 | 0.27176 | 0.41058 | 0.42675
0.25872 | 0.27175 | 0.41053 | 0.42673
0.25871 | 0.27174 | 0.41051 | 0.42672
0.2587 | 0.27173 | 0.41049 | 0.4267
0.25869 | 0.27172 | 0.41047 | 0.42669
0.25868 | 0.27171 | 0.41045 | 0.42666
0.25868 | 0.27171 | 0.41042 | 0.42665
0.25867 | 0.2717 | 0.41041 | 0.42662
0.25866 | 0.2717 | 0.4104 | 0.4266
0.25865 | 0.27169 | 0.41038 | 0.42658
0.25864 | 0.27168 | 0.41037 | 0.42656
0.25862 | 0.27167 | 0.41035 | 0.42654
0.25862 | 0.27166 | 0.41034 | 0.42653
0.25861 | 0.27165 | 0.41032 | 0.42652
0.2586 | 0.27164 | 0.4103 | 0.42651
0.25859 | 0.27163 | 0.41029 | 0.42649
0.25858 | 0.27163 | 0.41028 | 0.42647
0.25857 | 0.27161 | 0.41027 | 0.42644
0.25856 | 0.27161 | 0.41025 | 0.42643
0.25856 | 0.2716 | 0.41024 | 0.42642
0.25855 | 0.2716 | 0.41021 | 0.4264
0.25853 | 0.27159 | 0.41019 | 0.42638
0.25852 | 0.27158 | 0.41019 | 0.42637
0.25851 | 0.27157 | 0.41017 | 0.42636
0.2585 | 0.27156 | 0.41016 | 0.42634
0.25849 | 0.27155 | 0.41013 | 0.42632
0.25848 | 0.27154 | 0.41012 | 0.4263
0.25847 | 0.27153 | 0.4101 | 0.42628
0.25847 | 0.27152 | 0.41008 | 0.42625
0.25846 | 0.27152 | 0.41007 | 0.42624
0.25845 | 0.27151 | 0.41005 | 0.42622
0.25844 | 0.2715 | 0.41003 | 0.42619
0.25843 | 0.27149 | 0.41002 | 0.42618
0.25843 | 0.27149 | 0.41 | 0.42615
0.25841 | 0.27147 | 0.40998 | 0.42613
0.25841 | 0.27146 | 0.40996 | 0.42612
0.2584 | 0.27145 | 0.40994 | 0.4261
0.25839 | 0.27145 | 0.40991 | 0.42609
0.25838 | 0.27144 | 0.40989 | 0.42606
0.25837 | 0.27143 | 0.40989 | 0.42604
0.25836 | 0.27142 | 0.40987 | 0.42603
0.25835 | 0.27141 | 0.40986 | 0.42602
0.25834 | 0.2714 | 0.40984 | 0.42599
0.25833 | 0.27139 | 0.40981 | 0.42598
0.25832 | 0.27139 | 0.40979 | 0.42597
0.25832 | 0.27138 | 0.40977 | 0.42596
0.2583 | 0.27137 | 0.40975 | 0.42594
0.2583 | 0.27136 | 0.40973 | 0.42593
0.25829 | 0.27135 | 0.40972 | 0.42591
0.25828 | 0.27134 | 0.40969 | 0.4259
0.25827 | 0.27133 | 0.40967 | 0.42588
0.25827 | 0.27131 | 0.40965 | 0.42585
0.25826 | 0.27131 | 0.40964 | 0.42584
0.25825 | 0.2713 | 0.40962 | 0.42581
0.25824 | 0.27129 | 0.4096 | 0.42578
0.25823 | 0.27128 | 0.40958 | 0.42577
0.25823 | 0.27127 | 0.40955 | 0.42576
0.25822 | 0.27126 | 0.40953 | 0.42574
0.25821 | 0.27125 | 0.40952 | 0.42574
0.2582 | 0.27124 | 0.40951 | 0.42572
0.2582 | 0.27123 | 0.40948 | 0.42569
0.25819 | 0.27122 | 0.40946 | 0.42566
0.25818 | 0.27121 | 0.40944 | 0.42563
0.25818 | 0.27121 | 0.40943 | 0.42561
0.25816 | 0.2712 | 0.40941 | 0.42559
0.25815 | 0.27119 | 0.40938 | 0.42557
0.25814 | 0.27118 | 0.40937 | 0.42555
0.25814 | 0.27117 | 0.40935 | 0.42553
0.25813 | 0.27116 | 0.40933 | 0.4255
0.25812 | 0.27115 | 0.40932 | 0.42549
0.25811 | 0.27114 | 0.4093 | 0.42547
0.2581 | 0.27113 | 0.40928 | 0.42545
0.25809 | 0.27113 | 0.40926 | 0.42544
0.25807 | 0.27111 | 0.40924 | 0.42542
0.25807 | 0.2711 | 0.40922 | 0.4254
0.25805 | 0.2711 | 0.40921 | 0.42538
0.25805 | 0.27109 | 0.40919 | 0.42537
0.25804 | 0.27109 | 0.40917 | 0.42535
0.25803 | 0.27108 | 0.40914 | 0.42533
0.25802 | 0.27107 | 0.40913 | 0.42532
0.25802 | 0.27106 | 0.40912 | 0.42531
0.25801 | 0.27105 | 0.40911 | 0.4253
0.258 | 0.27104 | 0.4091 | 0.42527
0.25799 | 0.27103 | 0.40909 | 0.42526
0.25798 | 0.27102 | 0.40906 | 0.42525
0.25797 | 0.27102 | 0.40905 | 0.42523
0.25796 | 0.27101 | 0.40902 | 0.42522
0.25795 | 0.27101 | 0.409 | 0.42521
0.25795 | 0.271 | 0.409 | 0.4252
0.25793 | 0.271 | 0.40898 | 0.42519
0.25792 | 0.27098 | 0.40897 | 0.42518
0.25792 | 0.27098 | 0.40894 | 0.42515
0.2579 | 0.27096 | 0.40893 | 0.42514
0.25789 | 0.27095 | 0.40892 | 0.42512
0.25789 | 0.27094 | 0.4089 | 0.42511
0.25788 | 0.27094 | 0.4089 | 0.42509
0.25786 | 0.27093 | 0.40888 | 0.42508
0.25785 | 0.27092 | 0.40885 | 0.42506
0.25785 | 0.27091 | 0.40883 | 0.42504
0.25784 | 0.2709 | 0.40881 | 0.42502
0.25783 | 0.2709 | 0.40879 | 0.425
0.25782 | 0.27089 | 0.40878 | 0.42498
0.25781 | 0.27088 | 0.40877 | 0.42495
0.2578 | 0.27088 | 0.40876 | 0.42493
0.25779 | 0.27086 | 0.40872 | 0.42491
0.25778 | 0.27086 | 0.40869 | 0.42489
0.25776 | 0.27085 | 0.40868 | 0.42488
0.25776 | 0.27084 | 0.40866 | 0.42485
0.25775 | 0.27084 | 0.40864 | 0.42483
0.25774 | 0.27083 | 0.40862 | 0.42482
0.25774 | 0.27082 | 0.4086 | 0.4248
0.25773 | 0.27081 | 0.40858 | 0.42479
0.25772 | 0.2708 | 0.40856 | 0.42478
0.25771 | 0.27079 | 0.40854 | 0.42475
0.2577 | 0.27078 | 0.40852 | 0.42473
0.25768 | 0.27077 | 0.40851 | 0.42472
0.25768 | 0.27076 | 0.40849 | 0.42469
0.25766 | 0.27075 | 0.40848 | 0.42467
0.25765 | 0.27074 | 0.40846 | 0.42465
0.25764 | 0.27073 | 0.40844 | 0.42463
0.25763 | 0.27073 | 0.40842 | 0.42461
0.25762 | 0.27072 | 0.40841 | 0.4246
0.25762 | 0.27072 | 0.40839 | 0.42458
0.2576 | 0.2707 | 0.40837 | 0.42457
0.2576 | 0.27069 | 0.40835 | 0.42456
0.25759 | 0.27069 | 0.40833 | 0.42452
0.25758 | 0.27068 | 0.40832 | 0.4245
0.25757 | 0.27067 | 0.4083 | 0.42449
0.25756 | 0.27065 | 0.40828 | 0.42448
0.25755 | 0.27064 | 0.40827 | 0.42447
0.25755 | 0.27063 | 0.40825 | 0.42444
0.25754 | 0.27061 | 0.40822 | 0.42443
0.25754 | 0.27061 | 0.40819 | 0.42442
0.25753 | 0.2706 | 0.40817 | 0.42439
0.25751 | 0.27059 | 0.40815 | 0.42436
0.2575 | 0.27058 | 0.40813 | 0.42435
0.25749 | 0.27057 | 0.40811 | 0.42433
0.25748 | 0.27055 | 0.40809 | 0.42431
0.25747 | 0.27055 | 0.40806 | 0.42429
0.25746 | 0.27054 | 0.40805 | 0.42427
0.25745 | 0.27053 | 0.40802 | 0.42424
0.25744 | 0.27052 | 0.40801 | 0.42422
0.25743 | 0.27051 | 0.40799 | 0.4242
0.25742 | 0.2705 | 0.40796 | 0.42418
0.25741 | 0.27049 | 0.40795 | 0.42416
0.25739 | 0.27049 | 0.40794 | 0.42414
0.25738 | 0.27048 | 0.40792 | 0.42413
0.25737 | 0.27047 | 0.4079 | 0.42411
0.25735 | 0.27046 | 0.40788 | 0.42409
0.25734 | 0.27045 | 0.40787 | 0.42407
0.25732 | 0.27044 | 0.40785 | 0.42405
0.25731 | 0.27043 | 0.40782 | 0.42403
0.2573 | 0.27042 | 0.4078 | 0.424
0.25729 | 0.27041 | 0.40778 | 0.42399
0.25728 | 0.2704 | 0.40776 | 0.42396
0.25728 | 0.27039 | 0.40775 | 0.42394
0.25727 | 0.27038 | 0.40772 | 0.42394
0.25726 | 0.27037 | 0.40768 | 0.42393
0.25725 | 0.27036 | 0.40766 | 0.42391
0.25723 | 0.27036 | 0.40765 | 0.4239
0.25722 | 0.27035 | 0.40763 | 0.42388
0.25721 | 0.27034 | 0.40761 | 0.42386
0.25721 | 0.27034 | 0.40759 | 0.42385
0.2572 | 0.27033 | 0.40757 | 0.42384
0.25718 | 0.27031 | 0.40756 | 0.42382
0.25718 | 0.2703 | 0.40755 | 0.4238
0.25717 | 0.27029 | 0.40752 | 0.42378
0.25715 | 0.27028 | 0.40749 | 0.42377
0.25714 | 0.27027 | 0.40748 | 0.42376
0.25713 | 0.27025 | 0.40746 | 0.42374
0.25711 | 0.27024 | 0.40745 | 0.42372
0.2571 | 0.27024 | 0.40744 | 0.42371
0.25709 | 0.27023 | 0.40743 | 0.4237
0.25708 | 0.27022 | 0.40741 | 0.42369
0.25708 | 0.27021 | 0.4074 | 0.42366
0.25707 | 0.27019 | 0.40738 | 0.42364
0.25706 | 0.27018 | 0.40736 | 0.42363
0.25705 | 0.27017 | 0.40734 | 0.42361
0.25704 | 0.27016 | 0.40732 | 0.4236
0.25703 | 0.27015 | 0.4073 | 0.42357
0.25702 | 0.27015 | 0.40728 | 0.42355
0.25702 | 0.27014 | 0.40726 | 0.42354
0.25701 | 0.27013 | 0.40725 | 0.42352
0.257 | 0.27012 | 0.40724 | 0.4235
0.25699 | 0.27011 | 0.40722 | 0.42348
0.25698 | 0.2701 | 0.40717 | 0.42347
0.25697 | 0.27008 | 0.40715 | 0.42344
0.25696 | 0.27007 | 0.40713 | 0.42343
0.25695 | 0.27006 | 0.40711 | 0.42341
0.25694 | 0.27006 | 0.40709 | 0.42338
0.25693 | 0.27005 | 0.40707 | 0.42337
0.25692 | 0.27004 | 0.40705 | 0.42335
0.25691 | 0.27003 | 0.40704 | 0.42333
0.2569 | 0.27003 | 0.40702 | 0.42332
0.25689 | 0.27002 | 0.40701 | 0.4233
0.25689 | 0.27001 | 0.40699 | 0.42329
0.25687 | 0.27 | 0.40698 | 0.42327
0.25686 | 0.26999 | 0.40695 | 0.42327
0.25685 | 0.26998 | 0.40693 | 0.42325
0.25685 | 0.26997 | 0.40692 | 0.42323
0.25684 | 0.26996 | 0.40691 | 0.42321
0.25683 | 0.26995 | 0.40691 | 0.42319
0.25682 | 0.26993 | 0.40689 | 0.42315
0.25681 | 0.26993 | 0.40687 | 0.42314
0.2568 | 0.26992 | 0.40683 | 0.42312
0.25679 | 0.26991 | 0.40681 | 0.4231
0.25678 | 0.2699 | 0.4068 | 0.42308
0.25677 | 0.26988 | 0.40678 | 0.42306
0.25676 | 0.26987 | 0.40676 | 0.42305
0.25675 | 0.26987 | 0.40674 | 0.42302
0.25674 | 0.26986 | 0.40672 | 0.423
0.25673 | 0.26986 | 0.40671 | 0.42299
0.25672 | 0.26985 | 0.40668 | 0.42298
0.25671 | 0.26983 | 0.40667 | 0.42296
0.2567 | 0.26981 | 0.40663 | 0.42292
0.25668 | 0.2698 | 0.40661 | 0.42291
0.25667 | 0.26979 | 0.40659 | 0.42289
0.25666 | 0.26978 | 0.40657 | 0.42287
0.25665 | 0.26977 | 0.40655 | 0.42285
0.25664 | 0.26977 | 0.40654 | 0.42284
0.25664 | 0.26975 | 0.40653 | 0.42283
0.25663 | 0.26975 | 0.4065 | 0.42282
0.25661 | 0.26974 | 0.40649 | 0.4228
0.2566 | 0.26973 | 0.40646 | 0.42278
0.25659 | 0.26972 | 0.40644 | 0.42276
0.25658 | 0.26971 | 0.40642 | 0.42274
0.25657 | 0.2697 | 0.4064 | 0.42273
0.25656 | 0.26969 | 0.40637 | 0.4227
0.25655 | 0.26967 | 0.40635 | 0.42268
0.25654 | 0.26966 | 0.40634 | 0.42265
0.25654 | 0.26965 | 0.40632 | 0.42263
0.25653 | 0.26964 | 0.4063 | 0.42262
0.25652 | 0.26962 | 0.40629 | 0.4226
0.25651 | 0.26962 | 0.40628 | 0.42258
0.25651 | 0.26961 | 0.40623 | 0.42256
0.2565 | 0.26959 | 0.40621 | 0.42254
0.25649 | 0.26958 | 0.40619 | 0.42253
0.25648 | 0.26957 | 0.40617 | 0.42251
0.25646 | 0.26956 | 0.40615 | 0.4225
0.25645 | 0.26956 | 0.40612 | 0.42248
0.25644 | 0.26955 | 0.40611 | 0.42246
0.25643 | 0.26954 | 0.40608 | 0.42245
0.25642 | 0.26952 | 0.40606 | 0.42244
0.25642 | 0.26951 | 0.40604 | 0.42242
0.2564 | 0.2695 | 0.40602 | 0.4224
0.2564 | 0.26949 | 0.40599 | 0.42238
0.25638 | 0.26947 | 0.40598 | 0.42237
0.25638 | 0.26946 | 0.40596 | 0.42235
0.25636 | 0.26946 | 0.40594 | 0.42233
0.25636 | 0.26945 | 0.40591 | 0.42231
0.25634 | 0.26944 | 0.40589 | 0.42229
0.25633 | 0.26943 | 0.40589 | 0.42227
0.25632 | 0.26942 | 0.40587 | 0.42226
0.25631 | 0.26941 | 0.40585 | 0.42224
0.2563 | 0.2694 | 0.40583 | 0.42222
0.25629 | 0.26939 | 0.40581 | 0.4222
0.25628 | 0.26938 | 0.40579 | 0.42218
0.25627 | 0.26937 | 0.40577 | 0.42217
0.25625 | 0.26936 | 0.40575 | 0.42215
0.25625 | 0.26935 | 0.40574 | 0.42213
0.25624 | 0.26934 | 0.40572 | 0.42212
0.25623 | 0.26933 | 0.40569 | 0.4221
0.25622 | 0.26933 | 0.40568 | 0.42208
0.25621 | 0.26932 | 0.40566 | 0.42207
0.2562 | 0.26931 | 0.40565 | 0.42204
0.25619 | 0.2693 | 0.40563 | 0.42203
0.25618 | 0.2693 | 0.40563 | 0.42202
0.25617 | 0.26929 | 0.40561 | 0.42201
0.25617 | 0.26928 | 0.40559 | 0.42199
0.25615 | 0.26927 | 0.40557 | 0.42197
0.25614 | 0.26926 | 0.40556 | 0.42194
0.25613 | 0.26926 | 0.40555 | 0.42194
0.25613 | 0.26924 | 0.40554 | 0.42191
0.25612 | 0.26923 | 0.40551 | 0.42189
0.2561 | 0.26922 | 0.40548 | 0.42187
0.2561 | 0.26921 | 0.40545 | 0.42186
0.25609 | 0.2692 | 0.40543 | 0.42185
0.25608 | 0.26919 | 0.40541 | 0.42183
0.25607 | 0.26918 | 0.4054 | 0.42182
0.25605 | 0.26917 | 0.40538 | 0.42181
0.25604 | 0.26916 | 0.40537 | 0.4218
0.25603 | 0.26916 | 0.40535 | 0.42178
0.25602 | 0.26915 | 0.40534 | 0.42176
0.25602 | 0.26914 | 0.40531 | 0.42175
0.25601 | 0.26913 | 0.4053 | 0.42174
0.256 | 0.26912 | 0.40527 | 0.42171
0.25599 | 0.26911 | 0.40524 | 0.4217
0.25598 | 0.2691 | 0.40522 | 0.42168
0.25597 | 0.26909 | 0.40521 | 0.42167
0.25596 | 0.26908 | 0.4052 | 0.42165
0.25594 | 0.26907 | 0.40519 | 0.42163
0.25593 | 0.26907 | 0.40517 | 0.42161
0.25591 | 0.26906 | 0.40516 | 0.42159
0.2559 | 0.26906 | 0.40515 | 0.42157
0.2559 | 0.26905 | 0.40513 | 0.42155
0.25589 | 0.26904 | 0.40511 | 0.42154
0.25588 | 0.26902 | 0.40509 | 0.42152
0.25588 | 0.26901 | 0.40508 | 0.4215
0.25587 | 0.269 | 0.40506 | 0.42148
0.25586 | 0.26899 | 0.40502 | 0.42145
0.25585 | 0.26898 | 0.40501 | 0.42141
0.25584 | 0.26896 | 0.40499 | 0.4214
0.25583 | 0.26896 | 0.40499 | 0.42139
0.25582 | 0.26894 | 0.40497 | 0.42138
0.25581 | 0.26893 | 0.40494 | 0.42136
0.2558 | 0.26892 | 0.40493 | 0.42134
0.25579 | 0.26891 | 0.40491 | 0.42134
0.25578 | 0.26891 | 0.40489 | 0.42132
0.25578 | 0.2689 | 0.40488 | 0.4213
0.25577 | 0.2689 | 0.40486 | 0.42129
0.25575 | 0.26888 | 0.40485 | 0.42128
0.25574 | 0.26888 | 0.40483 | 0.42126
0.25573 | 0.26888 | 0.40479 | 0.42124
0.25572 | 0.26887 | 0.40478 | 0.42123
0.25571 | 0.26886 | 0.40476 | 0.42122
0.2557 | 0.26886 | 0.40475 | 0.42121
0.25569 | 0.26885 | 0.40474 | 0.42118
0.25567 | 0.26884 | 0.40472 | 0.42116
0.25567 | 0.26884 | 0.4047 | 0.42114
0.25566 | 0.26883 | 0.40469 | 0.42111
0.25565 | 0.26882 | 0.40468 | 0.4211
0.25564 | 0.26881 | 0.40465 | 0.42108
0.25563 | 0.2688 | 0.40463 | 0.42106
0.25562 | 0.2688 | 0.40462 | 0.42104
0.25561 | 0.26879 | 0.4046 | 0.42102
0.25559 | 0.26878 | 0.40458 | 0.421
0.25559 | 0.26877 | 0.40455 | 0.42097
0.25558 | 0.26876 | 0.40453 | 0.42095
0.25557 | 0.26876 | 0.4045 | 0.42093
0.25556 | 0.26875 | 0.40449 | 0.42092
0.25555 | 0.26874 | 0.40448 | 0.4209
0.25554 | 0.26873 | 0.40447 | 0.42088
0.25553 | 0.26872 | 0.40444 | 0.42086
0.25552 | 0.26871 | 0.40443 | 0.42085
0.25551 | 0.2687 | 0.40441 | 0.42084
0.2555 | 0.26869 | 0.4044 | 0.42083
0.25549 | 0.26868 | 0.40437 | 0.42081
0.25548 | 0.26868 | 0.40436 | 0.4208
0.25546 | 0.26867 | 0.40434 | 0.42078
0.25545 | 0.26865 | 0.40432 | 0.42077
0.25544 | 0.26864 | 0.4043 | 0.42075
0.25542 | 0.26863 | 0.40429 | 0.42074
0.25542 | 0.26862 | 0.40428 | 0.42073
0.25541 | 0.26861 | 0.40426 | 0.42071
0.2554 | 0.26861 | 0.40426 | 0.4207
0.2554 | 0.2686 | 0.40425 | 0.42066
0.25539 | 0.26859 | 0.40423 | 0.42065
0.25537 | 0.26858 | 0.40421 | 0.42063
0.25536 | 0.26857 | 0.4042 | 0.42062
0.25536 | 0.26857 | 0.40419 | 0.4206
0.25535 | 0.26855 | 0.40416 | 0.42059
0.25533 | 0.26854 | 0.40414 | 0.42057
0.25532 | 0.26853 | 0.40412 | 0.42055
0.25531 | 0.26853 | 0.4041 | 0.42053
0.2553 | 0.26852 | 0.40409 | 0.42051
0.25529 | 0.26851 | 0.40408 | 0.4205
0.25529 | 0.2685 | 0.40406 | 0.42048
0.25528 | 0.2685 | 0.40403 | 0.42047
0.25527 | 0.26848 | 0.40402 | 0.42046
0.25526 | 0.26848 | 0.404 | 0.42045
0.25525 | 0.26847 | 0.40399 | 0.42044
0.25524 | 0.26846 | 0.40396 | 0.42042
0.25523 | 0.26845 | 0.40395 | 0.42041
0.25522 | 0.26844 | 0.40392 | 0.42039
0.2552 | 0.26844 | 0.40389 | 0.42037
0.2552 | 0.26843 | 0.40388 | 0.42036
0.25518 | 0.26842 | 0.40385 | 0.42034
0.25518 | 0.26841 | 0.40383 | 0.42033
0.25517 | 0.2684 | 0.4038 | 0.42033
0.25516 | 0.26839 | 0.40378 | 0.42031
0.25515 | 0.26838 | 0.40377 | 0.42029
0.25514 | 0.26837 | 0.40375 | 0.42027
0.25513 | 0.26837 | 0.40373 | 0.42025
0.25512 | 0.26836 | 0.40371 | 0.42022
0.25512 | 0.26835 | 0.40369 | 0.42021
0.25511 | 0.26835 | 0.40367 | 0.4202
0.2551 | 0.26834 | 0.40365 | 0.42018
0.25509 | 0.26833 | 0.40361 | 0.42016
0.25508 | 0.26832 | 0.40359 | 0.42014
0.25507 | 0.26831 | 0.40357 | 0.42012
0.25506 | 0.26831 | 0.40355 | 0.42011
0.25504 | 0.26829 | 0.40353 | 0.4201
0.25504 | 0.26829 | 0.40352 | 0.42008
0.25503 | 0.26828 | 0.4035 | 0.42006
0.25503 | 0.26827 | 0.40348 | 0.42004
0.25502 | 0.26826 | 0.40345 | 0.42002
0.25501 | 0.26826 | 0.40344 | 0.42001
0.25501 | 0.26825 | 0.40342 | 0.41998
0.255 | 0.26824 | 0.40338 | 0.41997
0.25499 | 0.26823 | 0.40336 | 0.41996
0.25498 | 0.26823 | 0.40334 | 0.41994
0.25498 | 0.26822 | 0.40333 | 0.41992
0.25497 | 0.26821 | 0.4033 | 0.4199
0.25496 | 0.2682 | 0.40329 | 0.41989
0.25495 | 0.2682 | 0.40327 | 0.41988
0.25494 | 0.26819 | 0.40325 | 0.41986
0.25493 | 0.26819 | 0.40323 | 0.41984
0.25492 | 0.26817 | 0.40321 | 0.41981
0.25491 | 0.26817 | 0.4032 | 0.4198
0.2549 | 0.26816 | 0.40318 | 0.41978
0.25489 | 0.26815 | 0.40316 | 0.41977
0.25489 | 0.26815 | 0.40314 | 0.41975
0.25487 | 0.26814 | 0.40313 | 0.41971
0.25486 | 0.26813 | 0.40312 | 0.41969
0.25485 | 0.26812 | 0.4031 | 0.41968
0.25485 | 0.26811 | 0.40309 | 0.41965
0.25484 | 0.2681 | 0.40307 | 0.41963
0.25483 | 0.26809 | 0.40306 | 0.41962
0.25482 | 0.26809 | 0.40305 | 0.4196
0.25481 | 0.26808 | 0.40303 | 0.41957
0.2548 | 0.26807 | 0.40301 | 0.41956
0.2548 | 0.26806 | 0.403 | 0.41954
0.25479 | 0.26806 | 0.40297 | 0.41952
0.25478 | 0.26805 | 0.40295 | 0.41947
0.25477 | 0.26804 | 0.40292 | 0.41946
0.25476 | 0.26803 | 0.40291 | 0.41944
0.25476 | 0.26802 | 0.40289 | 0.41942
0.25475 | 0.26801 | 0.40288 | 0.41941
0.25473 | 0.268 | 0.40286 | 0.41939
0.25473 | 0.26799 | 0.40285 | 0.41937
0.25472 | 0.26798 | 0.40283 | 0.41935
0.25471 | 0.26797 | 0.40282 | 0.41934
0.2547 | 0.26796 | 0.40278 | 0.41933
0.2547 | 0.26795 | 0.40277 | 0.4193
0.25469 | 0.26794 | 0.40275 | 0.41928
0.25468 | 0.26793 | 0.40274 | 0.41926
0.25467 | 0.26792 | 0.40273 | 0.41924
0.25466 | 0.26791 | 0.40271 | 0.41922
0.25466 | 0.2679 | 0.40269 | 0.41921
0.25465 | 0.26789 | 0.40268 | 0.41919
0.25464 | 0.26788 | 0.40265 | 0.41918
0.25463 | 0.26788 | 0.40263 | 0.41916
0.25462 | 0.26786 | 0.40261 | 0.41915
0.25461 | 0.26785 | 0.4026 | 0.41914
0.2546 | 0.26784 | 0.40258 | 0.41911
0.25458 | 0.26783 | 0.40255 | 0.41909
0.25458 | 0.26782 | 0.40253 | 0.41906
0.25457 | 0.26781 | 0.4025 | 0.41905
0.25456 | 0.2678 | 0.40248 | 0.41903
0.25455 | 0.26778 | 0.40248 | 0.41902
0.25454 | 0.26777 | 0.40246 | 0.41901
0.25453 | 0.26776 | 0.40244 | 0.41898
0.25452 | 0.26775 | 0.40243 | 0.41897
0.25451 | 0.26775 | 0.40242 | 0.41895
0.2545 | 0.26774 | 0.40239 | 0.41893
0.25449 | 0.26773 | 0.40236 | 0.41891
0.25448 | 0.26772 | 0.40234 | 0.4189
0.25447 | 0.26771 | 0.40232 | 0.41886
0.25446 | 0.2677 | 0.40231 | 0.41885
0.25446 | 0.2677 | 0.40229 | 0.41884
0.25445 | 0.26769 | 0.40226 | 0.41882
0.25443 | 0.26768 | 0.40223 | 0.4188
0.25442 | 0.26767 | 0.40221 | 0.41878
0.25441 | 0.26766 | 0.40219 | 0.41876
0.25441 | 0.26765 | 0.40218 | 0.41875
0.2544 | 0.26764 | 0.40216 | 0.41873
0.25439 | 0.26763 | 0.40215 | 0.41871
0.25437 | 0.26762 | 0.40211 | 0.41868
0.25436 | 0.26761 | 0.4021 | 0.41868
0.25435 | 0.2676 | 0.40207 | 0.41865
0.25435 | 0.26759 | 0.40206 | 0.41863
0.25434 | 0.26758 | 0.40204 | 0.41861
0.25433 | 0.26757 | 0.40202 | 0.4186
0.25432 | 0.26756 | 0.402 | 0.41857
0.25431 | 0.26755 | 0.40198 | 0.41855
0.2543 | 0.26754 | 0.40197 | 0.41854
0.25429 | 0.26753 | 0.40196 | 0.41852
0.25428 | 0.26753 | 0.40194 | 0.4185
0.25427 | 0.26752 | 0.4019 | 0.41848
0.25426 | 0.26751 | 0.40189 | 0.41848
0.25425 | 0.26751 | 0.40185 | 0.41846
0.25424 | 0.2675 | 0.40183 | 0.41844
0.25423 | 0.26749 | 0.40182 | 0.41843
0.25422 | 0.26748 | 0.4018 | 0.41842
0.25421 | 0.26747 | 0.40179 | 0.4184
0.2542 | 0.26746 | 0.40176 | 0.41839
0.25419 | 0.26745 | 0.40174 | 0.41836
0.25418 | 0.26744 | 0.40172 | 0.41835
0.25416 | 0.26743 | 0.40171 | 0.41833
0.25415 | 0.26743 | 0.4017 | 0.41831
0.25415 | 0.26741 | 0.40169 | 0.41829
0.25414 | 0.2674 | 0.40165 | 0.41826
0.25413 | 0.2674 | 0.40162 | 0.41824
0.25412 | 0.26739 | 0.40161 | 0.41823
0.25411 | 0.26738 | 0.40159 | 0.41821
0.2541 | 0.26737 | 0.40158 | 0.4182
0.25409 | 0.26737 | 0.40156 | 0.41818
0.25408 | 0.26736 | 0.40155 | 0.41816
0.25407 | 0.26735 | 0.40153 | 0.41815
0.25405 | 0.26735 | 0.40151 | 0.41813
0.25404 | 0.26734 | 0.4015 | 0.41811
0.25403 | 0.26733 | 0.40149 | 0.41809
0.25402 | 0.26732 | 0.40147 | 0.41808
0.25401 | 0.26731 | 0.40145 | 0.41806
0.254 | 0.2673 | 0.40143 | 0.41804
0.254 | 0.26729 | 0.40141 | 0.41803
0.25399 | 0.26729 | 0.40139 | 0.41801
0.25398 | 0.26728 | 0.40137 | 0.41798
0.25397 | 0.26727 | 0.40134 | 0.41796
0.25395 | 0.26726 | 0.40132 | 0.41796
0.25394 | 0.26724 | 0.4013 | 0.41794
0.25393 | 0.26724 | 0.40129 | 0.41793
0.25392 | 0.26723 | 0.40126 | 0.41791
0.25391 | 0.26722 | 0.40124 | 0.41788
0.2539 | 0.26721 | 0.40122 | 0.41786
0.25389 | 0.26721 | 0.4012 | 0.41784
0.25388 | 0.2672 | 0.40118 | 0.41782
0.25387 | 0.26719 | 0.40116 | 0.4178
0.25387 | 0.26718 | 0.40115 | 0.41778
0.25385 | 0.26717 | 0.40112 | 0.41777
0.25385 | 0.26716 | 0.40111 | 0.41775
0.25383 | 0.26715 | 0.4011 | 0.41774
0.25382 | 0.26714 | 0.40107 | 0.41771
0.25381 | 0.26713 | 0.40104 | 0.4177
0.25381 | 0.26712 | 0.40102 | 0.41767
0.2538 | 0.26712 | 0.40099 | 0.41764
0.25379 | 0.26711 | 0.40097 | 0.41763
0.25378 | 0.26709 | 0.40095 | 0.41761
0.25377 | 0.26709 | 0.40093 | 0.41759
0.25376 | 0.26708 | 0.40091 | 0.41758
0.25375 | 0.26707 | 0.40089 | 0.41756
0.25375 | 0.26706 | 0.40088 | 0.41755
0.25373 | 0.26705 | 0.40085 | 0.41754
0.25372 | 0.26704 | 0.40084 | 0.41753
0.25371 | 0.26703 | 0.40083 | 0.41751
0.2537 | 0.26702 | 0.4008 | 0.4175
0.25368 | 0.26702 | 0.40078 | 0.41747
0.25367 | 0.26701 | 0.40076 | 0.41745
0.25367 | 0.26699 | 0.40074 | 0.41743
0.25365 | 0.26698 | 0.40072 | 0.41741
0.25364 | 0.26697 | 0.40069 | 0.4174
0.25364 | 0.26696 | 0.40068 | 0.41738
0.25363 | 0.26696 | 0.40066 | 0.41736
0.25362 | 0.26695 | 0.40062 | 0.41734
0.25361 | 0.26694 | 0.4006 | 0.41733
0.25361 | 0.26692 | 0.40058 | 0.41732
0.2536 | 0.26691 | 0.40056 | 0.41731
0.25359 | 0.2669 | 0.40054 | 0.41729
0.25358 | 0.26689 | 0.40052 | 0.41728
0.25357 | 0.26688 | 0.4005 | 0.41727
0.25356 | 0.26688 | 0.40048 | 0.41726
0.25355 | 0.26687 | 0.40047 | 0.41724
0.25354 | 0.26687 | 0.40045 | 0.41722
0.25354 | 0.26686 | 0.40043 | 0.41721
0.25353 | 0.26685 | 0.40041 | 0.4172
0.25352 | 0.26684 | 0.40038 | 0.41717
0.25351 | 0.26683 | 0.40037 | 0.41715
0.2535 | 0.26682 | 0.40035 | 0.41713
0.25348 | 0.26681 | 0.40033 | 0.41712
0.25347 | 0.2668 | 0.40031 | 0.41711
0.25346 | 0.26679 | 0.40028 | 0.41709
0.25344 | 0.26678 | 0.40026 | 0.41707
0.25343 | 0.26678 | 0.40023 | 0.41705
0.25342 | 0.26676 | 0.40022 | 0.41704
0.25341 | 0.26676 | 0.40018 | 0.41702
0.25341 | 0.26675 | 0.40016 | 0.41699
0.2534 | 0.26674 | 0.40013 | 0.41698
0.25339 | 0.26673 | 0.4001 | 0.41696
0.25338 | 0.26671 | 0.40009 | 0.41695
0.25337 | 0.2667 | 0.40008 | 0.41693
0.25336 | 0.2667 | 0.40005 | 0.41692
0.25335 | 0.26669 | 0.40004 | 0.4169
0.25333 | 0.26667 | 0.40001 | 0.41688
0.25333 | 0.26667 | 0.39998 | 0.41686
0.25332 | 0.26666 | 0.39994 | 0.41684
0.25331 | 0.26665 | 0.39992 | 0.41681
0.2533 | 0.26664 | 0.3999 | 0.4168
0.25329 | 0.26663 | 0.39988 | 0.41678
0.25328 | 0.26662 | 0.39986 | 0.41676
0.25328 | 0.26661 | 0.39985 | 0.41674
0.25327 | 0.2666 | 0.39983 | 0.41673
0.25325 | 0.26659 | 0.39982 | 0.41673
0.25324 | 0.26658 | 0.3998 | 0.41671
0.25323 | 0.26657 | 0.39979 | 0.4167
0.25322 | 0.26656 | 0.39976 | 0.41668
0.2532 | 0.26655 | 0.39974 | 0.41666
0.25319 | 0.26654 | 0.39972 | 0.41664
0.25318 | 0.26653 | 0.39969 | 0.41662
0.25317 | 0.26652 | 0.39967 | 0.4166
0.25317 | 0.26651 | 0.39964 | 0.41658
0.25316 | 0.2665 | 0.39963 | 0.41658
0.25315 | 0.26648 | 0.39961 | 0.41656
0.25314 | 0.26648 | 0.39959 | 0.41655
0.25313 | 0.26647 | 0.39956 | 0.41652
0.25312 | 0.26646 | 0.39954 | 0.41651
0.25312 | 0.26645 | 0.39952 | 0.41649
0.2531 | 0.26645 | 0.39951 | 0.41647
0.25309 | 0.26644 | 0.3995 | 0.41646
0.25308 | 0.26643 | 0.39949 | 0.41644
0.25307 | 0.26642 | 0.39947 | 0.41643
0.25306 | 0.26642 | 0.39946 | 0.41643
0.25305 | 0.26641 | 0.39945 | 0.41641
0.25304 | 0.2664 | 0.39944 | 0.4164
0.25303 | 0.26639 | 0.39941 | 0.41639
0.25301 | 0.26638 | 0.39939 | 0.41637
0.253 | 0.26636 | 0.39938 | 0.41636
0.25299 | 0.26636 | 0.39936 | 0.41635
0.25298 | 0.26635 | 0.39935 | 0.41631
0.25297 | 0.26634 | 0.39933 | 0.4163
0.25296 | 0.26633 | 0.39932 | 0.41628
0.25295 | 0.26632 | 0.3993 | 0.41627
0.25294 | 0.26631 | 0.39929 | 0.41625
0.25293 | 0.26631 | 0.39927 | 0.41624
0.25292 | 0.2663 | 0.39924 | 0.41623
0.25291 | 0.26629 | 0.39923 | 0.41622
0.2529 | 0.26629 | 0.39922 | 0.41621
0.25289 | 0.26628 | 0.39919 | 0.41619
0.25288 | 0.26627 | 0.39916 | 0.41617
0.25287 | 0.26626 | 0.39914 | 0.41617
0.25286 | 0.26626 | 0.39913 | 0.41615
0.25285 | 0.26625 | 0.39912 | 0.41614
0.25284 | 0.26624 | 0.39909 | 0.41612
0.25283 | 0.26623 | 0.39907 | 0.41611
0.25283 | 0.26622 | 0.39905 | 0.4161
0.25282 | 0.26621 | 0.39904 | 0.41608
0.2528 | 0.2662 | 0.39901 | 0.41607
0.25279 | 0.26619 | 0.39899 | 0.41606
0.25277 | 0.26618 | 0.39898 | 0.41604
0.25277 | 0.26617 | 0.39897 | 0.41603
0.25276 | 0.26616 | 0.39895 | 0.41601
0.25275 | 0.26615 | 0.39895 | 0.41599
0.25274 | 0.26614 | 0.39894 | 0.41596
0.25273 | 0.26613 | 0.39892 | 0.41593
0.25272 | 0.26612 | 0.3989 | 0.41592
0.25271 | 0.26612 | 0.39888 | 0.4159
0.25269 | 0.26611 | 0.39886 | 0.41589
0.25268 | 0.2661 | 0.39884 | 0.41588
0.25268 | 0.26609 | 0.39882 | 0.41587
0.25267 | 0.26609 | 0.3988 | 0.41585
0.25266 | 0.26608 | 0.39879 | 0.41584
0.25265 | 0.26607 | 0.39879 | 0.41583
0.25264 | 0.26606 | 0.39878 | 0.41582
0.25263 | 0.26605 | 0.39876 | 0.4158
0.25262 | 0.26604 | 0.39874 | 0.41579
0.25261 | 0.26603 | 0.39873 | 0.41577
0.25261 | 0.26602 | 0.39872 | 0.41575
0.2526 | 0.26601 | 0.39871 | 0.41573
0.2526 | 0.266 | 0.39868 | 0.41572
0.25259 | 0.26599 | 0.39867 | 0.41571
0.25257 | 0.26597 | 0.39865 | 0.41569
0.25256 | 0.26597 | 0.39861 | 0.41568
0.25255 | 0.26596 | 0.39858 | 0.41567
0.25254 | 0.26595 | 0.39856 | 0.41565
0.25254 | 0.26594 | 0.39854 | 0.41564
0.25253 | 0.26593 | 0.39853 | 0.41562
0.25252 | 0.26593 | 0.39851 | 0.41561
0.25251 | 0.26592 | 0.3985 | 0.41559
0.2525 | 0.26591 | 0.39847 | 0.41558
0.25249 | 0.2659 | 0.39843 | 0.41557
0.25249 | 0.26589 | 0.39841 | 0.41556
0.25248 | 0.26588 | 0.3984 | 0.41553
0.25247 | 0.26588 | 0.39839 | 0.41552
0.25246 | 0.26587 | 0.39836 | 0.4155
0.25245 | 0.26586 | 0.39835 | 0.41549
0.25244 | 0.26585 | 0.39833 | 0.41548
0.25244 | 0.26585 | 0.39831 | 0.41546
0.25243 | 0.26584 | 0.3983 | 0.41545
0.25242 | 0.26583 | 0.39827 | 0.41543
0.2524 | 0.26582 | 0.39826 | 0.41541
0.2524 | 0.26581 | 0.39824 | 0.4154
0.25239 | 0.26579 | 0.39822 | 0.41537
0.25237 | 0.26579 | 0.3982 | 0.41535
0.25237 | 0.26578 | 0.39818 | 0.41533
0.25236 | 0.26577 | 0.39816 | 0.41531
0.25235 | 0.26577 | 0.39814 | 0.4153
0.25234 | 0.26576 | 0.39812 | 0.41528
0.25233 | 0.26575 | 0.39809 | 0.41525
0.25232 | 0.26574 | 0.39807 | 0.41523
0.2523 | 0.26573 | 0.39805 | 0.41522
0.25229 | 0.26572 | 0.39802 | 0.4152
0.25228 | 0.26571 | 0.39801 | 0.41519
0.25227 | 0.26571 | 0.39799 | 0.41518
0.25226 | 0.2657 | 0.39797 | 0.41517
0.25225 | 0.26569 | 0.39796 | 0.41515
0.25225 | 0.26568 | 0.39792 | 0.41513
0.25224 | 0.26567 | 0.39791 | 0.41511
0.25223 | 0.26566 | 0.39787 | 0.41509
0.25222 | 0.26565 | 0.39786 | 0.41507
0.25221 | 0.26564 | 0.39784 | 0.41506
0.2522 | 0.26563 | 0.39783 | 0.41503
0.25219 | 0.26563 | 0.3978 | 0.41502
0.25218 | 0.26562 | 0.39778 | 0.415
0.25217 | 0.26561 | 0.39776 | 0.41498
0.25216 | 0.2656 | 0.39774 | 0.41496
0.25215 | 0.26559 | 0.39774 | 0.41494
0.25214 | 0.26558 | 0.39772 | 0.41493
0.25214 | 0.26557 | 0.3977 | 0.41492
0.25213 | 0.26556 | 0.39768 | 0.4149
0.25212 | 0.26555 | 0.39766 | 0.41488
0.25211 | 0.26553 | 0.39765 | 0.41487
0.2521 | 0.26552 | 0.39763 | 0.41484
0.25209 | 0.26552 | 0.39762 | 0.41481
0.25207 | 0.26551 | 0.39759 | 0.4148
0.25206 | 0.2655 | 0.39756 | 0.41478
0.25205 | 0.2655 | 0.39755 | 0.41477
0.25204 | 0.26549 | 0.39752 | 0.41474
0.25203 | 0.26548 | 0.39751 | 0.41473
0.25202 | 0.26547 | 0.39748 | 0.41472
0.25202 | 0.26547 | 0.39745 | 0.41469
0.25201 | 0.26546 | 0.39743 | 0.41467
0.252 | 0.26544 | 0.39742 | 0.41466
0.25198 | 0.26543 | 0.3974 | 0.41465
0.25198 | 0.26542 | 0.39739 | 0.41462
0.25197 | 0.26541 | 0.39737 | 0.4146
0.25196 | 0.2654 | 0.39735 | 0.41458
0.25195 | 0.26539 | 0.39734 | 0.41456
0.25194 | 0.26538 | 0.39733 | 0.41454
0.25193 | 0.26537 | 0.3973 | 0.41452
0.25192 | 0.26536 | 0.39727 | 0.4145
0.25191 | 0.26535 | 0.39726 | 0.4145
0.2519 | 0.26534 | 0.39725 | 0.41449
0.25189 | 0.26534 | 0.39723 | 0.41445
0.25187 | 0.26533 | 0.39721 | 0.41443
0.25187 | 0.26532 | 0.3972 | 0.41442
0.25186 | 0.26532 | 0.39718 | 0.4144
0.25185 | 0.26531 | 0.39717 | 0.41438
0.25184 | 0.2653 | 0.39715 | 0.41436
0.25184 | 0.2653 | 0.39714 | 0.41433
0.25182 | 0.26529 | 0.39712 | 0.41431
0.25181 | 0.26528 | 0.39711 | 0.41429
0.2518 | 0.26527 | 0.39709 | 0.41427
0.25178 | 0.26527 | 0.39708 | 0.41425
0.25178 | 0.26526 | 0.39706 | 0.41424
0.25177 | 0.26525 | 0.39703 | 0.41422
0.25176 | 0.26524 | 0.39701 | 0.41421
0.25175 | 0.26523 | 0.39698 | 0.41419
0.25174 | 0.26522 | 0.39697 | 0.41416
0.25173 | 0.26521 | 0.39695 | 0.41414
0.25172 | 0.2652 | 0.39694 | 0.41412
0.25172 | 0.26519 | 0.39692 | 0.41411
0.25171 | 0.26518 | 0.39691 | 0.4141
0.2517 | 0.26517 | 0.39688 | 0.41409
0.25168 | 0.26517 | 0.39686 | 0.41408
0.25167 | 0.26516 | 0.39685 | 0.41405
0.25166 | 0.26515 | 0.39684 | 0.41404
0.25165 | 0.26514 | 0.39682 | 0.41401
0.25164 | 0.26513 | 0.39679 | 0.414
0.25163 | 0.26512 | 0.39677 | 0.41397
0.25162 | 0.26512 | 0.39676 | 0.41394
0.25161 | 0.26511 | 0.39673 | 0.41393
0.2516 | 0.2651 | 0.39671 | 0.41391
0.25159 | 0.26509 | 0.39668 | 0.41388
0.25158 | 0.26508 | 0.39667 | 0.41386
0.25157 | 0.26507 | 0.39665 | 0.41383
0.25156 | 0.26506 | 0.39664 | 0.41382
0.25155 | 0.26505 | 0.39661 | 0.4138
0.25154 | 0.26505 | 0.39658 | 0.41379
0.25153 | 0.26503 | 0.39656 | 0.41377
0.25152 | 0.26502 | 0.39653 | 0.41376
0.25151 | 0.26501 | 0.3965 | 0.41375
0.2515 | 0.265 | 0.39647 | 0.41372
0.25149 | 0.26499 | 0.39644 | 0.41371
0.25148 | 0.26498 | 0.39642 | 0.4137
0.25147 | 0.26497 | 0.3964 | 0.41369
0.25146 | 0.26496 | 0.39637 | 0.41367
0.25145 | 0.26495 | 0.39635 | 0.41364
0.25143 | 0.26494 | 0.39632 | 0.41362
0.25142 | 0.26493 | 0.3963 | 0.4136
0.25142 | 0.26491 | 0.39629 | 0.41359
0.25141 | 0.2649 | 0.39626 | 0.41357
0.2514 | 0.26489 | 0.39625 | 0.41355
0.25139 | 0.26489 | 0.39623 | 0.41354
0.25138 | 0.26488 | 0.39621 | 0.41352
0.25137 | 0.26487 | 0.39619 | 0.4135
0.25136 | 0.26486 | 0.39617 | 0.41348
0.25135 | 0.26485 | 0.39616 | 0.41346
0.25134 | 0.26484 | 0.39615 | 0.41344
0.25132 | 0.26483 | 0.39613 | 0.41343
0.25132 | 0.26482 | 0.39611 | 0.41341
0.2513 | 0.26481 | 0.39609 | 0.41339
0.25129 | 0.2648 | 0.39606 | 0.41338
0.25128 | 0.26479 | 0.39605 | 0.41336
0.25127 | 0.26478 | 0.39604 | 0.41335
0.25126 | 0.26477 | 0.39602 | 0.41333
0.25125 | 0.26476 | 0.39599 | 0.41332
0.25125 | 0.26475 | 0.39598 | 0.41329
0.25124 | 0.26474 | 0.39596 | 0.41328
0.25123 | 0.26473 | 0.39594 | 0.41326
0.25122 | 0.26472 | 0.39592 | 0.41324
0.25121 | 0.26472 | 0.3959 | 0.41322
0.2512 | 0.26471 | 0.39589 | 0.41321
0.25119 | 0.2647 | 0.39587 | 0.41321
0.25118 | 0.26468 | 0.39585 | 0.41319
0.25118 | 0.26467 | 0.39584 | 0.41317
0.25117 | 0.26467 | 0.39581 | 0.41316
0.25116 | 0.26466 | 0.3958 | 0.41315
0.25115 | 0.26465 | 0.39579 | 0.41314
0.25114 | 0.26464 | 0.39577 | 0.41313
0.25113 | 0.26463 | 0.39576 | 0.41311
0.25112 | 0.26463 | 0.39575 | 0.4131
0.25111 | 0.26462 | 0.39574 | 0.41309
0.25111 | 0.26461 | 0.39573 | 0.41307
0.25109 | 0.2646 | 0.39572 | 0.41306
0.25109 | 0.2646 | 0.3957 | 0.41304
0.25108 | 0.26459 | 0.39567 | 0.41302
0.25107 | 0.26458 | 0.39565 | 0.41301
0.25106 | 0.26457 | 0.39563 | 0.41299
0.25105 | 0.26456 | 0.39561 | 0.41298
0.25103 | 0.26455 | 0.3956 | 0.41296
0.25103 | 0.26453 | 0.39558 | 0.41294
0.25102 | 0.26452 | 0.39556 | 0.41292
0.25101 | 0.26451 | 0.39554 | 0.4129
0.251 | 0.2645 | 0.39552 | 0.41288
0.25099 | 0.26448 | 0.39551 | 0.41286
0.25098 | 0.26447 | 0.39549 | 0.41284
0.25097 | 0.26447 | 0.39547 | 0.41282
0.25097 | 0.26446 | 0.39545 | 0.41281
0.25096 | 0.26445 | 0.39541 | 0.41279
0.25095 | 0.26444 | 0.39539 | 0.41278
0.25094 | 0.26443 | 0.39537 | 0.41277
0.25092 | 0.26443 | 0.39535 | 0.41274
0.25092 | 0.26442 | 0.39532 | 0.41273
0.2509 | 0.26441 | 0.39531 | 0.41271
0.25089 | 0.26441 | 0.3953 | 0.4127
0.25089 | 0.2644 | 0.39528 | 0.41269
0.25087 | 0.26439 | 0.39526 | 0.41268
0.25086 | 0.26438 | 0.39524 | 0.41267
0.25085 | 0.26437 | 0.39523 | 0.41265
0.25085 | 0.26436 | 0.39521 | 0.41263
0.25084 | 0.26436 | 0.39519 | 0.41261
0.25083 | 0.26435 | 0.39518 | 0.4126
0.25082 | 0.26434 | 0.39516 | 0.41257
0.25081 | 0.26434 | 0.39514 | 0.41256
0.2508 | 0.26433 | 0.39512 | 0.41254
0.25079 | 0.26432 | 0.39509 | 0.41252
0.25078 | 0.26432 | 0.39508 | 0.41251
0.25077 | 0.26431 | 0.39507 | 0.41249
0.25076 | 0.2643 | 0.39506 | 0.41247
0.25075 | 0.26429 | 0.39505 | 0.41245
0.25075 | 0.26429 | 0.39503 | 0.41244
0.25074 | 0.26427 | 0.39502 | 0.41243
0.25073 | 0.26426 | 0.39498 | 0.41242
0.25072 | 0.26425 | 0.39497 | 0.4124
0.25071 | 0.26424 | 0.39495 | 0.41239
0.25071 | 0.26424 | 0.39491 | 0.41237
0.25069 | 0.26423 | 0.3949 | 0.41235
0.25068 | 0.26422 | 0.39489 | 0.41233
0.25067 | 0.26421 | 0.39486 | 0.41232
0.25067 | 0.2642 | 0.39483 | 0.4123
0.25066 | 0.26419 | 0.39481 | 0.41228
0.25065 | 0.26417 | 0.39479 | 0.41225
0.25064 | 0.26416 | 0.39477 | 0.41224
0.25063 | 0.26416 | 0.39475 | 0.41223
0.25061 | 0.26414 | 0.39473 | 0.41221
0.2506 | 0.26413 | 0.39472 | 0.4122
0.25059 | 0.26412 | 0.39469 | 0.41218
0.25058 | 0.26412 | 0.39467 | 0.41216
0.25057 | 0.26411 | 0.39465 | 0.41214
0.25057 | 0.2641 | 0.39463 | 0.41213
0.25056 | 0.26409 | 0.39462 | 0.41211
0.25055 | 0.26408 | 0.39459 | 0.41209
0.25054 | 0.26407 | 0.39456 | 0.41207
0.25054 | 0.26407 | 0.39454 | 0.41205
0.25052 | 0.26406 | 0.39453 | 0.41204
0.25051 | 0.26405 | 0.39452 | 0.41203
0.25049 | 0.26404 | 0.39448 | 0.41201
0.25048 | 0.26402 | 0.39446 | 0.41199
0.25047 | 0.26402 | 0.39445 | 0.41198
0.25045 | 0.26401 | 0.39443 | 0.41197
0.25044 | 0.264 | 0.39442 | 0.41195
0.25043 | 0.26399 | 0.3944 | 0.41193
0.25042 | 0.26398 | 0.39438 | 0.41191
0.25041 | 0.26397 | 0.39436 | 0.41189
0.2504 | 0.26396 | 0.39434 | 0.41187
0.25039 | 0.26396 | 0.39432 | 0.41185
0.25038 | 0.26395 | 0.3943 | 0.41183
0.25037 | 0.26394 | 0.39427 | 0.41181
0.25035 | 0.26393 | 0.39426 | 0.4118
0.25035 | 0.26393 | 0.39424 | 0.41178
0.25034 | 0.26392 | 0.39422 | 0.41175
0.25033 | 0.26391 | 0.39421 | 0.41173
0.25032 | 0.2639 | 0.3942 | 0.41172
0.25031 | 0.26389 | 0.39419 | 0.4117
0.2503 | 0.26389 | 0.39417 | 0.41169
0.25029 | 0.26387 | 0.39416 | 0.41166
0.25029 | 0.26386 | 0.39415 | 0.41164
0.25028 | 0.26386 | 0.39413 | 0.41162
0.25027 | 0.26385 | 0.39411 | 0.41159
0.25026 | 0.26384 | 0.3941 | 0.41157
0.25025 | 0.26383 | 0.39409 | 0.41155
0.25025 | 0.26383 | 0.39407 | 0.41154
0.25023 | 0.26382 | 0.39405 | 0.41152
0.25022 | 0.26382 | 0.39404 | 0.4115
0.25022 | 0.26381 | 0.39402 | 0.41148
0.2502 | 0.2638 | 0.39401 | 0.41147
0.25019 | 0.26379 | 0.39399 | 0.41145
0.25018 | 0.26377 | 0.39398 | 0.41143
0.25018 | 0.26376 | 0.39397 | 0.41141
0.25017 | 0.26375 | 0.39395 | 0.4114
0.25016 | 0.26374 | 0.39393 | 0.41138
0.25015 | 0.26373 | 0.39392 | 0.41135
0.25014 | 0.26373 | 0.39391 | 0.41134
0.25013 | 0.26372 | 0.39389 | 0.41131
0.25012 | 0.26371 | 0.39388 | 0.41129
0.25011 | 0.2637 | 0.39387 | 0.41127
0.2501 | 0.26369 | 0.39385 | 0.41124
0.25009 | 0.26368 | 0.39384 | 0.41122
0.25008 | 0.26367 | 0.39383 | 0.41121
0.25008 | 0.26366 | 0.39381 | 0.41119
0.25007 | 0.26365 | 0.3938 | 0.41116
0.25006 | 0.26364 | 0.39377 | 0.41114
0.25005 | 0.26363 | 0.39376 | 0.41113
0.25004 | 0.26362 | 0.39375 | 0.41112
0.25003 | 0.26361 | 0.39374 | 0.41108
0.25002 | 0.2636 | 0.39373 | 0.41106
0.25001 | 0.26359 | 0.3937 | 0.41104
0.25 | 0.26358 | 0.39368 | 0.41103
0.24999 | 0.26357 | 0.39367 | 0.41101
0.24998 | 0.26357 | 0.39364 | 0.41099
0.24997 | 0.26356 | 0.39363 | 0.41098
0.24996 | 0.26355 | 0.3936 | 0.41097
0.24995 | 0.26355 | 0.39356 | 0.41095
0.24994 | 0.26354 | 0.39354 | 0.41093
0.24993 | 0.26353 | 0.39352 | 0.41091
0.24992 | 0.26352 | 0.39351 | 0.41089
0.24991 | 0.26351 | 0.39349 | 0.41087
0.2499 | 0.26351 | 0.39348 | 0.41085
0.24989 | 0.2635 | 0.39346 | 0.41082
0.24988 | 0.2635 | 0.39344 | 0.41081
0.24988 | 0.26349 | 0.39343 | 0.4108
0.24987 | 0.26348 | 0.39342 | 0.41078
0.24986 | 0.26347 | 0.39339 | 0.41076
0.24985 | 0.26346 | 0.39337 | 0.41075
0.24984 | 0.26345 | 0.39336 | 0.41074
0.24983 | 0.26344 | 0.39334 | 0.41072
0.24982 | 0.26344 | 0.39333 | 0.4107
0.24982 | 0.26342 | 0.39331 | 0.41068
0.2498 | 0.26341 | 0.39329 | 0.41066
0.24979 | 0.26341 | 0.39327 | 0.41064
0.24978 | 0.26339 | 0.39326 | 0.41062
0.24977 | 0.26338 | 0.39325 | 0.41061
0.24976 | 0.26338 | 0.39323 | 0.41059
0.24975 | 0.26336 | 0.39321 | 0.41058
0.24973 | 0.26335 | 0.39319 | 0.41056
0.24971 | 0.26334 | 0.39318 | 0.41055
0.2497 | 0.26333 | 0.39316 | 0.41053
0.24969 | 0.26332 | 0.39314 | 0.41051
0.24968 | 0.26331 | 0.39312 | 0.41049
0.24968 | 0.26331 | 0.3931 | 0.41048
0.24967 | 0.26329 | 0.39308 | 0.41046
0.24966 | 0.26328 | 0.39305 | 0.41044
0.24965 | 0.26327 | 0.39304 | 0.41043
0.24965 | 0.26327 | 0.39302 | 0.41042
0.24964 | 0.26326 | 0.39299 | 0.41039
0.24963 | 0.26325 | 0.39297 | 0.41037
0.24962 | 0.26324 | 0.39295 | 0.41035
0.24961 | 0.26323 | 0.39293 | 0.41034
0.24961 | 0.26322 | 0.39291 | 0.41032
0.24959 | 0.26321 | 0.39289 | 0.41031
0.24958 | 0.26319 | 0.39287 | 0.41028
0.24957 | 0.26319 | 0.39284 | 0.41025
0.24957 | 0.26318 | 0.39283 | 0.41024
0.24956 | 0.26317 | 0.39281 | 0.41022
0.24955 | 0.26316 | 0.39278 | 0.4102
0.24954 | 0.26315 | 0.39277 | 0.41019
0.24953 | 0.26314 | 0.39275 | 0.41018
0.24952 | 0.26313 | 0.39274 | 0.41017
0.2495 | 0.26313 | 0.3927 | 0.41015
0.24949 | 0.26312 | 0.39269 | 0.41013
0.24948 | 0.26311 | 0.39267 | 0.41012
0.24946 | 0.2631 | 0.39265 | 0.4101
0.24945 | 0.26309 | 0.39263 | 0.41009
0.24945 | 0.26309 | 0.39261 | 0.41008
0.24944 | 0.26308 | 0.3926 | 0.41006
0.24942 | 0.26307 | 0.39259 | 0.41005
0.24942 | 0.26307 | 0.39258 | 0.41003
0.24941 | 0.26306 | 0.39256 | 0.41002
0.2494 | 0.26305 | 0.39255 | 0.41
0.24939 | 0.26304 | 0.39252 | 0.40998
0.24938 | 0.26303 | 0.3925 | 0.40996
0.24937 | 0.26302 | 0.39248 | 0.40994
0.24936 | 0.26301 | 0.39248 | 0.40991
0.24935 | 0.263 | 0.39245 | 0.40989
0.24934 | 0.26299 | 0.39245 | 0.40988
0.24933 | 0.26298 | 0.39243 | 0.40986
0.24932 | 0.26297 | 0.39241 | 0.40982
0.24931 | 0.26296 | 0.39238 | 0.4098
0.2493 | 0.26296 | 0.39237 | 0.40978
0.24929 | 0.26295 | 0.39235 | 0.40974
0.24928 | 0.26293 | 0.39233 | 0.40973
0.24927 | 0.26293 | 0.39232 | 0.40971
0.24927 | 0.26292 | 0.3923 | 0.40969
0.24926 | 0.26291 | 0.39229 | 0.40968
0.24925 | 0.2629 | 0.39226 | 0.40966
0.24924 | 0.26289 | 0.39225 | 0.40965
0.24922 | 0.26288 | 0.39223 | 0.40964
0.24921 | 0.26287 | 0.39221 | 0.40962
0.24921 | 0.26287 | 0.3922 | 0.4096
0.24919 | 0.26286 | 0.39216 | 0.40958
0.24919 | 0.26285 | 0.39214 | 0.40958
0.24918 | 0.26284 | 0.39213 | 0.40956
0.24917 | 0.26283 | 0.39211 | 0.40955
0.24916 | 0.2628 | 0.39208 | 0.40953
0.24915 | 0.26279 | 0.39207 | 0.40951
0.24914 | 0.26279 | 0.39205 | 0.40949
0.24913 | 0.26278 | 0.39204 | 0.40946
0.24912 | 0.26276 | 0.39202 | 0.40945
0.24912 | 0.26276 | 0.39201 | 0.40944
0.24911 | 0.26275 | 0.39199 | 0.40942
0.2491 | 0.26274 | 0.39196 | 0.40941
0.24909 | 0.26273 | 0.39194 | 0.40938
0.24907 | 0.26272 | 0.39193 | 0.40937
0.24906 | 0.26272 | 0.39191 | 0.40935
0.24905 | 0.26271 | 0.39188 | 0.40933
0.24904 | 0.2627 | 0.39187 | 0.40931
0.24903 | 0.26269 | 0.39185 | 0.40929
0.24902 | 0.26269 | 0.39183 | 0.40927
0.24901 | 0.26268 | 0.39182 | 0.40924
0.24901 | 0.26267 | 0.39181 | 0.40921
0.24899 | 0.26266 | 0.39179 | 0.4092
0.24898 | 0.26265 | 0.39177 | 0.40919
0.24898 | 0.26264 | 0.39175 | 0.40917
0.24896 | 0.26264 | 0.39173 | 0.40916
0.24895 | 0.26263 | 0.39171 | 0.40915
0.24894 | 0.26262 | 0.3917 | 0.40914
0.24893 | 0.26262 | 0.39167 | 0.40912
0.24892 | 0.2626 | 0.39166 | 0.4091
0.24891 | 0.2626 | 0.39165 | 0.40909
0.2489 | 0.26259 | 0.39164 | 0.40907
0.2489 | 0.26258 | 0.39163 | 0.40905
0.24889 | 0.26257 | 0.39161 | 0.40904
0.24888 | 0.26256 | 0.39159 | 0.40903
0.24888 | 0.26256 | 0.39157 | 0.40901
0.24887 | 0.26254 | 0.39155 | 0.409
0.24885 | 0.26253 | 0.39153 | 0.40899
0.24884 | 0.26251 | 0.39152 | 0.40897
0.24884 | 0.2625 | 0.39149 | 0.40895
0.24882 | 0.26249 | 0.39147 | 0.40894
0.24881 | 0.26248 | 0.39145 | 0.40892
0.2488 | 0.26247 | 0.39143 | 0.4089
0.24879 | 0.26247 | 0.39141 | 0.40889
0.24879 | 0.26245 | 0.39141 | 0.40886
0.24878 | 0.26244 | 0.39139 | 0.40885
0.24877 | 0.26243 | 0.39137 | 0.40883
0.24876 | 0.26242 | 0.39135 | 0.40882
0.24876 | 0.26241 | 0.39134 | 0.4088
0.24875 | 0.26241 | 0.39132 | 0.40879
0.24874 | 0.2624 | 0.3913 | 0.40876
0.24873 | 0.26239 | 0.39128 | 0.40873
0.24873 | 0.26238 | 0.39126 | 0.40872
0.24871 | 0.26237 | 0.39124 | 0.4087
0.2487 | 0.26236 | 0.39122 | 0.40869
0.24869 | 0.26235 | 0.39121 | 0.40868
0.24868 | 0.26234 | 0.39119 | 0.40867
0.24866 | 0.26233 | 0.39117 | 0.40865
0.24864 | 0.26232 | 0.39115 | 0.40862
0.24864 | 0.26231 | 0.39113 | 0.4086
0.24862 | 0.2623 | 0.39111 | 0.40859
0.24861 | 0.26229 | 0.39109 | 0.40858
0.2486 | 0.26227 | 0.39108 | 0.40855
0.24859 | 0.26226 | 0.39106 | 0.40853
0.24858 | 0.26225 | 0.39104 | 0.40852
0.24857 | 0.26224 | 0.39102 | 0.40852
0.24856 | 0.26224 | 0.39101 | 0.40848
0.24855 | 0.26223 | 0.39099 | 0.40847
0.24854 | 0.26223 | 0.39098 | 0.40846
0.24854 | 0.26222 | 0.39095 | 0.40843
0.24854 | 0.2622 | 0.39095 | 0.40841
0.24852 | 0.2622 | 0.39092 | 0.40839
0.24852 | 0.26219 | 0.39091 | 0.40838
0.24851 | 0.26218 | 0.3909 | 0.40836
0.24849 | 0.26217 | 0.39087 | 0.40834
0.24848 | 0.26216 | 0.39087 | 0.40832
0.24847 | 0.26215 | 0.39084 | 0.40831
0.24846 | 0.26214 | 0.39083 | 0.4083
0.24845 | 0.26212 | 0.39081 | 0.40828
0.24845 | 0.26212 | 0.39077 | 0.40825
0.24843 | 0.26211 | 0.39075 | 0.40824
0.24843 | 0.26211 | 0.39072 | 0.40823
0.24841 | 0.2621 | 0.39071 | 0.40821
0.2484 | 0.26209 | 0.39068 | 0.40821
0.2484 | 0.26207 | 0.39066 | 0.40818
0.24839 | 0.26207 | 0.39065 | 0.40817
0.24838 | 0.26206 | 0.39062 | 0.40815
0.24837 | 0.26206 | 0.3906 | 0.40813
0.24836 | 0.26205 | 0.39059 | 0.40811
0.24835 | 0.26204 | 0.39057 | 0.40809
0.24835 | 0.26203 | 0.39055 | 0.40807
0.24834 | 0.26202 | 0.39053 | 0.40806
0.24832 | 0.26201 | 0.3905 | 0.40804
0.24831 | 0.262 | 0.39048 | 0.40803
0.2483 | 0.26199 | 0.39045 | 0.40801
0.24829 | 0.26198 | 0.39043 | 0.40799
0.24828 | 0.26197 | 0.39042 | 0.40797
0.24827 | 0.26197 | 0.39041 | 0.40795
0.24826 | 0.26196 | 0.39038 | 0.40793
0.24824 | 0.26195 | 0.39036 | 0.40792
0.24822 | 0.26194 | 0.39034 | 0.40791
0.24821 | 0.26193 | 0.39033 | 0.4079
0.24821 | 0.26193 | 0.39032 | 0.40787
0.24819 | 0.26191 | 0.39031 | 0.40785
0.24818 | 0.2619 | 0.3903 | 0.40783
0.24818 | 0.26189 | 0.39029 | 0.4078
0.24817 | 0.26188 | 0.39028 | 0.40778
0.24816 | 0.26187 | 0.39025 | 0.40776
0.24815 | 0.26185 | 0.39024 | 0.40774
0.24814 | 0.26185 | 0.39022 | 0.40773
0.24813 | 0.26184 | 0.39021 | 0.4077
0.24811 | 0.26184 | 0.3902 | 0.40768
0.2481 | 0.26183 | 0.39019 | 0.40767
0.24809 | 0.26182 | 0.39017 | 0.40766
0.24809 | 0.26181 | 0.39015 | 0.40765
0.24808 | 0.26181 | 0.39014 | 0.40763
0.24807 | 0.2618 | 0.39012 | 0.40762
0.24806 | 0.26178 | 0.39011 | 0.4076
0.24805 | 0.26178 | 0.39009 | 0.40758
0.24804 | 0.26177 | 0.39007 | 0.40757
0.24803 | 0.26175 | 0.39004 | 0.40755
0.24803 | 0.26174 | 0.39002 | 0.40753
0.24802 | 0.26173 | 0.39001 | 0.40752
0.24801 | 0.26173 | 0.38999 | 0.4075
0.248 | 0.26172 | 0.38996 | 0.40748
0.24799 | 0.26171 | 0.38995 | 0.40747
0.24797 | 0.2617 | 0.38993 | 0.40746
0.24796 | 0.2617 | 0.38991 | 0.40743
0.24795 | 0.26169 | 0.38989 | 0.40742
0.24794 | 0.26168 | 0.38989 | 0.4074
0.24792 | 0.26166 | 0.38987 | 0.40737
0.24791 | 0.26166 | 0.38986 | 0.40736
0.2479 | 0.26164 | 0.38982 | 0.40735
0.24789 | 0.26163 | 0.38979 | 0.40733
0.24788 | 0.26163 | 0.38978 | 0.40731
0.24788 | 0.26162 | 0.38976 | 0.4073
0.24786 | 0.26162 | 0.38974 | 0.40727
0.24786 | 0.26161 | 0.38972 | 0.40726
0.24784 | 0.2616 | 0.38971 | 0.40725
0.24783 | 0.26159 | 0.38968 | 0.40723
0.24783 | 0.26158 | 0.38967 | 0.40722
0.24781 | 0.26158 | 0.38966 | 0.4072
0.24781 | 0.26157 | 0.38963 | 0.40718
0.2478 | 0.26156 | 0.38962 | 0.40717
0.24779 | 0.26155 | 0.38961 | 0.40715
0.24778 | 0.26154 | 0.38958 | 0.40713
0.24777 | 0.26153 | 0.38956 | 0.4071
0.24776 | 0.26152 | 0.38954 | 0.40708
0.24776 | 0.26151 | 0.38953 | 0.40706
0.24774 | 0.26151 | 0.38952 | 0.40706
0.24773 | 0.2615 | 0.38951 | 0.40703
0.24773 | 0.26149 | 0.38948 | 0.40702
0.24772 | 0.26148 | 0.38947 | 0.407
0.24772 | 0.26147 | 0.38945 | 0.40698
0.24771 | 0.26146 | 0.38943 | 0.40696
0.2477 | 0.26146 | 0.38942 | 0.40695
0.24769 | 0.26145 | 0.38939 | 0.40694
0.24767 | 0.26144 | 0.38937 | 0.40692
0.24766 | 0.26142 | 0.38935 | 0.4069
0.24766 | 0.26141 | 0.38934 | 0.40689
0.24765 | 0.2614 | 0.38932 | 0.40688
0.24764 | 0.26139 | 0.3893 | 0.40687
0.24763 | 0.26138 | 0.38929 | 0.40685
0.24762 | 0.26137 | 0.38927 | 0.40683
0.24762 | 0.26137 | 0.38925 | 0.40682
0.2476 | 0.26136 | 0.38924 | 0.40681
0.24759 | 0.26135 | 0.38921 | 0.40679
0.24759 | 0.26134 | 0.38919 | 0.40677
0.24757 | 0.26133 | 0.38918 | 0.40675
0.24757 | 0.26133 | 0.38916 | 0.40674
0.24756 | 0.26132 | 0.38912 | 0.40672
0.24755 | 0.26131 | 0.38909 | 0.4067
0.24754 | 0.2613 | 0.38908 | 0.40668
0.24753 | 0.26129 | 0.38906 | 0.40667
0.24752 | 0.26128 | 0.38904 | 0.40666
0.24751 | 0.26127 | 0.38901 | 0.40664
0.2475 | 0.26127 | 0.389 | 0.40662
0.2475 | 0.26126 | 0.38898 | 0.4066
0.24749 | 0.26125 | 0.38896 | 0.40659
0.24747 | 0.26124 | 0.38895 | 0.40657
0.24747 | 0.26123 | 0.38893 | 0.40655
0.24746 | 0.26121 | 0.38891 | 0.40654
0.24745 | 0.26121 | 0.38889 | 0.40653
0.24744 | 0.2612 | 0.38886 | 0.40651
0.24743 | 0.26119 | 0.38884 | 0.40649
0.24742 | 0.26117 | 0.38882 | 0.40648
0.24742 | 0.26116 | 0.3888 | 0.40646
0.24741 | 0.26115 | 0.38878 | 0.40643
0.2474 | 0.26114 | 0.38876 | 0.40642
0.24739 | 0.26113 | 0.38875 | 0.4064
0.24739 | 0.26112 | 0.38873 | 0.40638
0.24737 | 0.26111 | 0.38871 | 0.40637
0.24736 | 0.2611 | 0.38868 | 0.40635
0.24735 | 0.2611 | 0.38867 | 0.40632
0.24734 | 0.26109 | 0.38866 | 0.40631
0.24733 | 0.26108 | 0.38864 | 0.40629
0.24732 | 0.26108 | 0.38862 | 0.40628
0.2473 | 0.26107 | 0.38861 | 0.40626
0.24729 | 0.26107 | 0.38859 | 0.40625
0.24728 | 0.26105 | 0.38857 | 0.40623
0.24727 | 0.26105 | 0.38856 | 0.40621
0.24726 | 0.26104 | 0.38853 | 0.4062
0.24726 | 0.26103 | 0.38852 | 0.40618
0.24725 | 0.26102 | 0.38849 | 0.40616
0.24724 | 0.261 | 0.38848 | 0.40615
0.24723 | 0.26099 | 0.38846 | 0.40613
0.24722 | 0.26099 | 0.38844 | 0.40612
0.24722 | 0.26098 | 0.38843 | 0.40612
0.24721 | 0.26097 | 0.3884 | 0.4061
0.2472 | 0.26096 | 0.38839 | 0.40608
0.24719 | 0.26095 | 0.38838 | 0.40606
0.24719 | 0.26095 | 0.38836 | 0.40604
0.24718 | 0.26094 | 0.38835 | 0.40603
0.24717 | 0.26092 | 0.38834 | 0.40602
0.24716 | 0.26092 | 0.38832 | 0.406
0.24715 | 0.26091 | 0.3883 | 0.40597
0.24714 | 0.2609 | 0.38829 | 0.40595
0.24714 | 0.26089 | 0.38828 | 0.40594
0.24713 | 0.26089 | 0.38826 | 0.40591
0.24712 | 0.26088 | 0.38824 | 0.40589
0.24711 | 0.26087 | 0.38822 | 0.40588
0.2471 | 0.26086 | 0.38821 | 0.40586
0.24709 | 0.26085 | 0.38819 | 0.40584
0.24709 | 0.26084 | 0.38817 | 0.40583
0.24707 | 0.26084 | 0.38816 | 0.40581
0.24706 | 0.26083 | 0.38815 | 0.4058
0.24705 | 0.26082 | 0.38813 | 0.40579
0.24704 | 0.26081 | 0.38811 | 0.40577
0.24703 | 0.2608 | 0.38809 | 0.40574
0.24702 | 0.26079 | 0.38807 | 0.40572
0.24701 | 0.26078 | 0.38805 | 0.40569
0.24701 | 0.26077 | 0.38804 | 0.40568
0.247 | 0.26077 | 0.38803 | 0.40566
0.24699 | 0.26076 | 0.388 | 0.40564
0.24698 | 0.26075 | 0.38799 | 0.40563
0.24698 | 0.26075 | 0.38798 | 0.40561
0.24697 | 0.26074 | 0.38796 | 0.40559
0.24695 | 0.26073 | 0.38793 | 0.40556
0.24694 | 0.26072 | 0.38791 | 0.40555
0.24693 | 0.26071 | 0.38789 | 0.40554
0.24693 | 0.2607 | 0.38785 | 0.40553
0.24692 | 0.26069 | 0.38783 | 0.40551
0.24691 | 0.26068 | 0.38782 | 0.40549
0.2469 | 0.26067 | 0.38781 | 0.40547
0.24689 | 0.26066 | 0.3878 | 0.40545
0.24688 | 0.26065 | 0.38778 | 0.40543
0.24687 | 0.26064 | 0.38776 | 0.40542
0.24686 | 0.26064 | 0.38775 | 0.40541
0.24685 | 0.26063 | 0.38773 | 0.4054
0.24684 | 0.26062 | 0.38771 | 0.40539
0.24683 | 0.26061 | 0.38769 | 0.40537
0.24681 | 0.2606 | 0.38767 | 0.40536
0.24681 | 0.2606 | 0.38764 | 0.40534
0.2468 | 0.26059 | 0.38761 | 0.40532
0.2468 | 0.26058 | 0.3876 | 0.4053
0.24679 | 0.26057 | 0.38757 | 0.40528
0.24678 | 0.26057 | 0.38756 | 0.40527
0.24678 | 0.26056 | 0.38754 | 0.40525
0.24676 | 0.26055 | 0.38753 | 0.40523
0.24675 | 0.26054 | 0.38751 | 0.40522
0.24674 | 0.26054 | 0.38749 | 0.4052
0.24673 | 0.26053 | 0.38746 | 0.40518
0.24672 | 0.26051 | 0.38744 | 0.40516
0.24671 | 0.26051 | 0.38742 | 0.40515
0.24671 | 0.2605 | 0.38741 | 0.40513
0.2467 | 0.26049 | 0.38738 | 0.4051
0.24669 | 0.26048 | 0.38736 | 0.40509
0.24668 | 0.26047 | 0.38734 | 0.40506
0.24667 | 0.26046 | 0.38732 | 0.40504
0.24666 | 0.26046 | 0.3873 | 0.40503
0.24664 | 0.26045 | 0.38728 | 0.40501
0.24662 | 0.26045 | 0.38726 | 0.40499
0.24662 | 0.26044 | 0.38725 | 0.40498
0.24661 | 0.26043 | 0.38722 | 0.40496
0.2466 | 0.26042 | 0.3872 | 0.40494
0.24659 | 0.26041 | 0.38718 | 0.40493
0.24658 | 0.26039 | 0.38716 | 0.40491
0.24657 | 0.26039 | 0.38714 | 0.40489
0.24656 | 0.26038 | 0.38713 | 0.40487
0.24655 | 0.26037 | 0.3871 | 0.40486
0.24654 | 0.26036 | 0.38709 | 0.40484
0.24653 | 0.26035 | 0.38707 | 0.40483
0.24652 | 0.26034 | 0.38706 | 0.40481
0.24651 | 0.26033 | 0.38703 | 0.40478
0.2465 | 0.26031 | 0.38702 | 0.40477
0.2465 | 0.2603 | 0.387 | 0.40474
0.24649 | 0.26029 | 0.38698 | 0.40473
0.24647 | 0.26029 | 0.38695 | 0.40471
0.24647 | 0.26027 | 0.38694 | 0.40468
0.24646 | 0.26026 | 0.38692 | 0.40467
0.24645 | 0.26025 | 0.38689 | 0.40465
0.24644 | 0.26024 | 0.38687 | 0.40464
0.24643 | 0.26024 | 0.38686 | 0.40463
0.24642 | 0.26023 | 0.38684 | 0.40461
0.24641 | 0.26021 | 0.3868 | 0.40459
0.2464 | 0.26021 | 0.38679 | 0.40458
0.24639 | 0.2602 | 0.38678 | 0.40456
0.24638 | 0.2602 | 0.38676 | 0.40453
0.24637 | 0.26019 | 0.38674 | 0.40452
0.24636 | 0.26018 | 0.38672 | 0.40451
0.24635 | 0.26017 | 0.3867 | 0.40449
0.24633 | 0.26015 | 0.38667 | 0.40447
0.24632 | 0.26014 | 0.38664 | 0.40444
0.24631 | 0.26014 | 0.38662 | 0.40443
0.2463 | 0.26013 | 0.38659 | 0.40441
0.24629 | 0.26012 | 0.38658 | 0.40439
0.24628 | 0.26011 | 0.38657 | 0.40438
0.24627 | 0.2601 | 0.38654 | 0.40435
0.24626 | 0.26009 | 0.38651 | 0.40433
0.24625 | 0.26009 | 0.38649 | 0.40431
0.24625 | 0.26008 | 0.38647 | 0.40429
0.24624 | 0.26007 | 0.38645 | 0.40427
0.24623 | 0.26006 | 0.38642 | 0.40425
0.24622 | 0.26005 | 0.3864 | 0.40425
0.24621 | 0.26004 | 0.38639 | 0.40423
0.2462 | 0.26003 | 0.38636 | 0.40421
0.24619 | 0.26002 | 0.38635 | 0.4042
0.24618 | 0.26001 | 0.38633 | 0.40418
0.24617 | 0.26 | 0.38632 | 0.40416
0.24616 | 0.25999 | 0.38631 | 0.40414
0.24616 | 0.25998 | 0.38628 | 0.40413
0.24614 | 0.25997 | 0.38626 | 0.40411
0.24613 | 0.25997 | 0.38624 | 0.4041
0.24613 | 0.25995 | 0.38623 | 0.40408
0.24612 | 0.25995 | 0.38621 | 0.40405
0.24611 | 0.25994 | 0.38619 | 0.40405
0.2461 | 0.25993 | 0.38617 | 0.40403
0.24609 | 0.25993 | 0.38616 | 0.40402
0.24607 | 0.25992 | 0.38613 | 0.404
0.24607 | 0.25991 | 0.38612 | 0.40398
0.24606 | 0.2599 | 0.38609 | 0.40395
0.24605 | 0.25989 | 0.38607 | 0.40394
0.24604 | 0.25988 | 0.38606 | 0.40393
0.24603 | 0.25988 | 0.38604 | 0.40392
0.24602 | 0.25987 | 0.38603 | 0.40392
0.246 | 0.25986 | 0.38601 | 0.4039
0.246 | 0.25985 | 0.386 | 0.40388
0.24599 | 0.25985 | 0.38598 | 0.40387
0.24598 | 0.25984 | 0.38597 | 0.40385
0.24598 | 0.25983 | 0.38594 | 0.40383
0.24597 | 0.25982 | 0.38592 | 0.40382
0.24596 | 0.25981 | 0.38591 | 0.40379
0.24595 | 0.25981 | 0.38589 | 0.40379
0.24594 | 0.25979 | 0.38586 | 0.40377
0.24593 | 0.25978 | 0.38585 | 0.40375
0.24592 | 0.25977 | 0.38584 | 0.40373
0.24591 | 0.25977 | 0.38582 | 0.40371
0.2459 | 0.25976 | 0.3858 | 0.40369
0.24589 | 0.25975 | 0.38578 | 0.40367
0.24588 | 0.25975 | 0.38576 | 0.40365
0.24587 | 0.25974 | 0.38575 | 0.40363
0.24586 | 0.25973 | 0.38574 | 0.40363
0.24585 | 0.25972 | 0.38572 | 0.40361
0.24583 | 0.25971 | 0.3857 | 0.4036
0.24583 | 0.2597 | 0.38567 | 0.40359
0.24582 | 0.25969 | 0.38565 | 0.40357
0.24581 | 0.25967 | 0.38564 | 0.40355
0.24579 | 0.25966 | 0.3856 | 0.40353
0.24578 | 0.25966 | 0.38559 | 0.40352
0.24577 | 0.25964 | 0.38557 | 0.4035
0.24576 | 0.25964 | 0.38555 | 0.40348
0.24575 | 0.25963 | 0.38554 | 0.40347
0.24574 | 0.25962 | 0.38553 | 0.40346
0.24573 | 0.25962 | 0.38551 | 0.40344
0.24572 | 0.2596 | 0.38549 | 0.40341
0.24571 | 0.2596 | 0.38546 | 0.40337
0.2457 | 0.25959 | 0.38545 | 0.40336
0.24569 | 0.25958 | 0.38542 | 0.40335
0.24568 | 0.25957 | 0.38539 | 0.40334
0.24567 | 0.25956 | 0.38535 | 0.40331
0.24566 | 0.25955 | 0.38533 | 0.40329
0.24564 | 0.25954 | 0.3853 | 0.40328
0.24563 | 0.25952 | 0.38528 | 0.40327
0.24563 | 0.25951 | 0.38528 | 0.40324
0.24561 | 0.25951 | 0.38524 | 0.40322
0.2456 | 0.2595 | 0.38522 | 0.40321
0.24559 | 0.25949 | 0.38519 | 0.40319
0.24558 | 0.25949 | 0.38518 | 0.40318
0.24557 | 0.25948 | 0.38516 | 0.40317
0.24556 | 0.25946 | 0.38514 | 0.40315
0.24554 | 0.25946 | 0.38513 | 0.40314
0.24553 | 0.25945 | 0.38511 | 0.4031
0.24552 | 0.25944 | 0.38509 | 0.40307
0.24551 | 0.25943 | 0.38508 | 0.40305
0.2455 | 0.25942 | 0.38506 | 0.40303
0.24548 | 0.25941 | 0.38504 | 0.40302
0.24548 | 0.2594 | 0.38502 | 0.403
0.24547 | 0.25939 | 0.38501 | 0.40299
0.24546 | 0.25937 | 0.38499 | 0.40298
0.24545 | 0.25936 | 0.38498 | 0.40296
0.24544 | 0.25935 | 0.38496 | 0.40295
0.24542 | 0.25935 | 0.38494 | 0.40293
0.24542 | 0.25934 | 0.38493 | 0.40291
0.2454 | 0.25933 | 0.38491 | 0.40288
0.24539 | 0.25932 | 0.38489 | 0.40286
0.24538 | 0.25931 | 0.38488 | 0.40285
0.24537 | 0.2593 | 0.38487 | 0.40284
0.24536 | 0.25929 | 0.38484 | 0.4028
0.24536 | 0.25929 | 0.38481 | 0.40279
0.24535 | 0.25928 | 0.3848 | 0.40276
0.24534 | 0.25927 | 0.38478 | 0.40274
0.24533 | 0.25926 | 0.38476 | 0.40272
0.24531 | 0.25924 | 0.38474 | 0.40271
0.2453 | 0.25924 | 0.38472 | 0.4027
0.24529 | 0.25923 | 0.38469 | 0.40269
0.24528 | 0.25922 | 0.38468 | 0.40267
0.24527 | 0.25921 | 0.38466 | 0.40266
0.24526 | 0.2592 | 0.38463 | 0.40264
0.24525 | 0.25919 | 0.38462 | 0.40262
0.24524 | 0.25918 | 0.3846 | 0.40261
0.24523 | 0.25917 | 0.38459 | 0.40259
0.24522 | 0.25916 | 0.38457 | 0.40258
0.24521 | 0.25916 | 0.38455 | 0.40256
0.24519 | 0.25914 | 0.38454 | 0.40255
0.24518 | 0.25914 | 0.38452 | 0.40254
0.24518 | 0.25913 | 0.38449 | 0.40253
0.24516 | 0.25912 | 0.38447 | 0.40251
0.24515 | 0.25911 | 0.38446 | 0.4025
0.24514 | 0.25911 | 0.38444 | 0.40249
0.24513 | 0.2591 | 0.38443 | 0.40246
0.24512 | 0.25909 | 0.38442 | 0.40245
0.24511 | 0.25909 | 0.38439 | 0.40244
0.2451 | 0.25908 | 0.38438 | 0.40242
0.24508 | 0.25907 | 0.38437 | 0.40239
0.24508 | 0.25906 | 0.38434 | 0.40238
0.24507 | 0.25905 | 0.38432 | 0.40236
0.24506 | 0.25904 | 0.38429 | 0.40234
0.24505 | 0.25903 | 0.38426 | 0.40233
0.24504 | 0.25902 | 0.38425 | 0.40232
0.24503 | 0.25902 | 0.38424 | 0.4023
0.24502 | 0.25901 | 0.38423 | 0.40229
0.24501 | 0.259 | 0.38421 | 0.40227
0.245 | 0.25899 | 0.38418 | 0.40226
0.24499 | 0.25898 | 0.38417 | 0.40225
0.24499 | 0.25897 | 0.38415 | 0.40224
0.24497 | 0.25897 | 0.38415 | 0.40222
0.24497 | 0.25896 | 0.38412 | 0.40222
0.24496 | 0.25896 | 0.38407 | 0.4022
0.24494 | 0.25894 | 0.38404 | 0.40219
0.24494 | 0.25893 | 0.38403 | 0.40218
0.24493 | 0.25893 | 0.38401 | 0.40216
0.24491 | 0.25891 | 0.38399 | 0.40215
0.2449 | 0.2589 | 0.38397 | 0.40214
0.24489 | 0.2589 | 0.38395 | 0.40213
0.24488 | 0.25889 | 0.38393 | 0.40211
0.24487 | 0.25888 | 0.38391 | 0.40209
0.24486 | 0.25887 | 0.3839 | 0.40208
0.24485 | 0.25886 | 0.38387 | 0.40206
0.24484 | 0.25884 | 0.38385 | 0.40204
0.24483 | 0.25884 | 0.38384 | 0.40202
0.24482 | 0.25883 | 0.38381 | 0.40201
0.24481 | 0.25882 | 0.38379 | 0.402
0.24479 | 0.25882 | 0.38377 | 0.40198
0.24478 | 0.25881 | 0.38373 | 0.40195
0.24477 | 0.2588 | 0.38372 | 0.40193
0.24477 | 0.25879 | 0.3837 | 0.40192
0.24475 | 0.25878 | 0.38368 | 0.40191
0.24474 | 0.25877 | 0.38367 | 0.4019
0.24473 | 0.25876 | 0.38364 | 0.40188
0.24473 | 0.25875 | 0.38363 | 0.40186
0.24472 | 0.25874 | 0.38361 | 0.40185
0.2447 | 0.25873 | 0.38359 | 0.40184
0.24469 | 0.25872 | 0.38356 | 0.40183
0.24469 | 0.25872 | 0.38354 | 0.40181
0.24468 | 0.25871 | 0.38352 | 0.40178
0.24467 | 0.2587 | 0.38351 | 0.40174
0.24467 | 0.25869 | 0.38348 | 0.40171
0.24465 | 0.25868 | 0.38347 | 0.4017
0.24464 | 0.25867 | 0.38345 | 0.40168
0.24464 | 0.25866 | 0.38343 | 0.40166
0.24462 | 0.25866 | 0.38341 | 0.40165
0.24462 | 0.25865 | 0.38339 | 0.40164
0.2446 | 0.25864 | 0.38336 | 0.40163
0.24459 | 0.25863 | 0.38333 | 0.40162
0.24459 | 0.25862 | 0.38332 | 0.40159
0.24457 | 0.25861 | 0.3833 | 0.40159
0.24456 | 0.2586 | 0.38328 | 0.40157
0.24455 | 0.25859 | 0.38326 | 0.40154
0.24455 | 0.25859 | 0.38325 | 0.40153
0.24453 | 0.25858 | 0.38323 | 0.40152
0.24452 | 0.25857 | 0.38322 | 0.4015
0.24451 | 0.25856 | 0.3832 | 0.40149
0.24449 | 0.25855 | 0.38317 | 0.40147
0.24449 | 0.25854 | 0.38315 | 0.40145
0.24448 | 0.25854 | 0.38313 | 0.40142
0.24447 | 0.25852 | 0.38312 | 0.40141
0.24447 | 0.25851 | 0.3831 | 0.40138
0.24446 | 0.2585 | 0.38308 | 0.40136
0.24444 | 0.25849 | 0.38305 | 0.40134
0.24443 | 0.25848 | 0.38304 | 0.40133
0.24442 | 0.25847 | 0.38302 | 0.40132
0.24442 | 0.25846 | 0.383 | 0.4013
0.2444 | 0.25845 | 0.38297 | 0.40129
0.24439 | 0.25844 | 0.38295 | 0.40126
0.24437 | 0.25842 | 0.38294 | 0.40125
0.24437 | 0.25842 | 0.38292 | 0.40122
0.24436 | 0.25841 | 0.3829 | 0.40121
0.24435 | 0.2584 | 0.38288 | 0.40119
0.24433 | 0.25839 | 0.38286 | 0.40117
0.24432 | 0.25839 | 0.38282 | 0.40115
0.24431 | 0.25838 | 0.38281 | 0.40113
0.2443 | 0.25837 | 0.38279 | 0.40111
0.2443 | 0.25836 | 0.38277 | 0.40109
0.24428 | 0.25836 | 0.38276 | 0.40108
0.24427 | 0.25834 | 0.38275 | 0.40105
0.24426 | 0.25833 | 0.38273 | 0.40103
0.24425 | 0.25833 | 0.38272 | 0.40101
0.24423 | 0.25832 | 0.3827 | 0.40099
0.24422 | 0.25831 | 0.38268 | 0.40098
0.24421 | 0.2583 | 0.38266 | 0.40097
0.24419 | 0.25829 | 0.38263 | 0.40096
0.24418 | 0.25828 | 0.38262 | 0.40094
0.24417 | 0.25827 | 0.38261 | 0.40092
0.24416 | 0.25827 | 0.3826 | 0.4009
0.24415 | 0.25826 | 0.38257 | 0.40088
0.24414 | 0.25825 | 0.38256 | 0.40086
0.24413 | 0.25824 | 0.38255 | 0.40085
0.24412 | 0.25824 | 0.38251 | 0.40084
0.24411 | 0.25823 | 0.38251 | 0.40082
0.2441 | 0.25822 | 0.38249 | 0.40081
0.24409 | 0.25821 | 0.38246 | 0.40079
0.24408 | 0.2582 | 0.38245 | 0.40077
0.24407 | 0.25819 | 0.38242 | 0.40075
0.24406 | 0.25818 | 0.3824 | 0.40072
0.24405 | 0.25817 | 0.38238 | 0.4007
0.24405 | 0.25817 | 0.38237 | 0.40069
0.24404 | 0.25816 | 0.38235 | 0.40067
0.24403 | 0.25815 | 0.38233 | 0.40066
0.24402 | 0.25815 | 0.38231 | 0.40065
0.24401 | 0.25814 | 0.38229 | 0.40062
0.244 | 0.25813 | 0.38226 | 0.40061
0.24399 | 0.25812 | 0.38224 | 0.40058
0.24399 | 0.25811 | 0.38221 | 0.40057
0.24398 | 0.2581 | 0.38219 | 0.40055
0.24397 | 0.25809 | 0.38217 | 0.40051
0.24396 | 0.25809 | 0.38215 | 0.40048
0.24394 | 0.25808 | 0.38213 | 0.40047
0.24393 | 0.25807 | 0.38211 | 0.40045
0.24392 | 0.25806 | 0.38208 | 0.40043
0.24391 | 0.25805 | 0.38204 | 0.40041
0.2439 | 0.25804 | 0.38203 | 0.4004
0.24389 | 0.25803 | 0.38199 | 0.40038
0.24389 | 0.25802 | 0.38197 | 0.40036
0.24388 | 0.25801 | 0.38194 | 0.40035
0.24387 | 0.258 | 0.38191 | 0.40034
0.24386 | 0.25799 | 0.38189 | 0.40031
0.24386 | 0.25798 | 0.38186 | 0.4003
0.24385 | 0.25797 | 0.38184 | 0.40029
0.24383 | 0.25796 | 0.38182 | 0.40027
0.24382 | 0.25795 | 0.38178 | 0.40026
0.24382 | 0.25793 | 0.38175 | 0.40023
0.24381 | 0.25792 | 0.38173 | 0.40022
0.2438 | 0.25791 | 0.3817 | 0.40021
0.24379 | 0.2579 | 0.38169 | 0.40019
0.24378 | 0.2579 | 0.38166 | 0.40018
0.24377 | 0.25788 | 0.38164 | 0.40017
0.24376 | 0.25788 | 0.38163 | 0.40015
0.24376 | 0.25787 | 0.3816 | 0.40013
0.24374 | 0.25787 | 0.38157 | 0.4001
0.24373 | 0.25786 | 0.38155 | 0.40008
0.24371 | 0.25785 | 0.38153 | 0.40007
0.24371 | 0.25784 | 0.3815 | 0.40006
0.24369 | 0.25783 | 0.38148 | 0.40005
0.24369 | 0.25782 | 0.38146 | 0.40003
0.24368 | 0.25781 | 0.38144 | 0.40002
0.24367 | 0.2578 | 0.38141 | 0.4
0.24365 | 0.25779 | 0.38139 | 0.39998
0.24364 | 0.25778 | 0.38137 | 0.39997
0.24363 | 0.25777 | 0.38136 | 0.39996
0.24362 | 0.25776 | 0.38134 | 0.39994
0.24361 | 0.25776 | 0.38133 | 0.39992
0.2436 | 0.25775 | 0.38131 | 0.3999
0.24359 | 0.25774 | 0.38129 | 0.39988
0.24358 | 0.25773 | 0.38127 | 0.39986
0.24358 | 0.25773 | 0.38126 | 0.39984
0.24357 | 0.25772 | 0.38123 | 0.39982
0.24356 | 0.25771 | 0.38121 | 0.39981
0.24355 | 0.2577 | 0.38119 | 0.3998
0.24353 | 0.25769 | 0.38117 | 0.39978
0.24353 | 0.25768 | 0.38116 | 0.39977
0.24352 | 0.25767 | 0.38112 | 0.39975
0.24351 | 0.25766 | 0.3811 | 0.39974
0.2435 | 0.25765 | 0.38109 | 0.39972
0.24349 | 0.25765 | 0.38106 | 0.39971
0.24348 | 0.25764 | 0.38104 | 0.39968
0.24347 | 0.25763 | 0.38103 | 0.39966
0.24346 | 0.25762 | 0.381 | 0.39965
0.24345 | 0.25761 | 0.38098 | 0.39963
0.24344 | 0.2576 | 0.38097 | 0.39962
0.24343 | 0.25759 | 0.38095 | 0.39959
0.24341 | 0.25758 | 0.38093 | 0.39957
0.2434 | 0.25757 | 0.38093 | 0.39956
0.2434 | 0.25756 | 0.38092 | 0.39955
0.24339 | 0.25755 | 0.3809 | 0.39954
0.24338 | 0.25754 | 0.38089 | 0.39953
0.24337 | 0.25754 | 0.38087 | 0.39951
0.24335 | 0.25753 | 0.38085 | 0.39948
0.24334 | 0.25752 | 0.38083 | 0.39946
0.24333 | 0.25751 | 0.38082 | 0.39945
0.24332 | 0.25751 | 0.38079 | 0.39942
0.24331 | 0.2575 | 0.38078 | 0.3994
0.24329 | 0.25749 | 0.38076 | 0.39937
0.24328 | 0.25748 | 0.38073 | 0.39935
0.24327 | 0.25748 | 0.38072 | 0.39934
0.24326 | 0.25747 | 0.38071 | 0.39934
0.24325 | 0.25746 | 0.38069 | 0.39932
0.24324 | 0.25746 | 0.38066 | 0.3993
0.24323 | 0.25745 | 0.38065 | 0.39928
0.24322 | 0.25744 | 0.38064 | 0.39927
0.24322 | 0.25743 | 0.38063 | 0.39925
0.24321 | 0.25743 | 0.38061 | 0.39924
0.24321 | 0.25742 | 0.38058 | 0.39922
0.24319 | 0.25741 | 0.38055 | 0.39921
0.24318 | 0.2574 | 0.38052 | 0.39919
0.24318 | 0.25738 | 0.38051 | 0.39919
0.24317 | 0.25737 | 0.38049 | 0.39918
0.24315 | 0.25737 | 0.38047 | 0.39917
0.24314 | 0.25736 | 0.38045 | 0.39915
0.24313 | 0.25735 | 0.38043 | 0.39913
0.24313 | 0.25734 | 0.38041 | 0.39911
0.24311 | 0.25733 | 0.38038 | 0.39909
0.2431 | 0.25732 | 0.38036 | 0.39909
0.2431 | 0.25732 | 0.38035 | 0.39906
0.24309 | 0.25731 | 0.38031 | 0.39904
0.24308 | 0.2573 | 0.3803 | 0.39903
0.24307 | 0.25729 | 0.38028 | 0.39902
0.24306 | 0.25728 | 0.38026 | 0.399
0.24305 | 0.25728 | 0.38023 | 0.39899
0.24304 | 0.25727 | 0.38022 | 0.39898
0.24303 | 0.25726 | 0.3802 | 0.39896
0.24302 | 0.25725 | 0.38018 | 0.39894
0.243 | 0.25725 | 0.38016 | 0.39892
0.24299 | 0.25724 | 0.38014 | 0.3989
0.24299 | 0.25723 | 0.38012 | 0.39889
0.24297 | 0.25722 | 0.3801 | 0.39886
0.24296 | 0.25721 | 0.38008 | 0.39884
0.24296 | 0.2572 | 0.38006 | 0.39881
0.24295 | 0.25719 | 0.38003 | 0.3988
0.24295 | 0.25717 | 0.38001 | 0.39878
0.24294 | 0.25716 | 0.38 | 0.39877
0.24293 | 0.25716 | 0.37998 | 0.39876
0.24292 | 0.25715 | 0.37996 | 0.39875
0.24291 | 0.25714 | 0.37995 | 0.39874
0.2429 | 0.25713 | 0.37993 | 0.39873
0.24289 | 0.25711 | 0.37991 | 0.39871
0.24288 | 0.25711 | 0.37988 | 0.39869
0.24288 | 0.2571 | 0.37988 | 0.39867
0.24287 | 0.2571 | 0.37985 | 0.39866
0.24286 | 0.25709 | 0.37984 | 0.39864
0.24285 | 0.25708 | 0.37983 | 0.39862
0.24284 | 0.25708 | 0.37981 | 0.39861
0.24283 | 0.25707 | 0.37979 | 0.39859
0.24282 | 0.25706 | 0.37976 | 0.39857
0.24281 | 0.25706 | 0.37975 | 0.39855
0.2428 | 0.25705 | 0.37973 | 0.39854
0.24279 | 0.25704 | 0.37971 | 0.39851
0.24278 | 0.25703 | 0.3797 | 0.39849
0.24277 | 0.25702 | 0.37968 | 0.39847
0.24275 | 0.25701 | 0.37966 | 0.39845
0.24274 | 0.257 | 0.37964 | 0.39844
0.24273 | 0.25699 | 0.37962 | 0.39842
0.24272 | 0.25698 | 0.3796 | 0.3984
0.24271 | 0.25697 | 0.37958 | 0.39838
0.2427 | 0.25696 | 0.37957 | 0.39836
0.24268 | 0.25695 | 0.37955 | 0.39834
0.24268 | 0.25694 | 0.37953 | 0.39833
0.24267 | 0.25693 | 0.37953 | 0.39831
0.24266 | 0.25692 | 0.3795 | 0.3983
0.24265 | 0.25691 | 0.37949 | 0.39828
0.24264 | 0.25691 | 0.37947 | 0.39825
0.24263 | 0.2569 | 0.37945 | 0.39824
0.24262 | 0.2569 | 0.37943 | 0.39823
0.24261 | 0.25689 | 0.3794 | 0.39822
0.2426 | 0.25688 | 0.37938 | 0.39821
0.24259 | 0.25688 | 0.37936 | 0.3982
0.24258 | 0.25687 | 0.37934 | 0.39818
0.24256 | 0.25686 | 0.37932 | 0.39817
0.24255 | 0.25685 | 0.3793 | 0.39815
0.24254 | 0.25684 | 0.37928 | 0.39813
0.24253 | 0.25683 | 0.37926 | 0.3981
0.24251 | 0.25682 | 0.37923 | 0.39809
0.24251 | 0.25682 | 0.37922 | 0.39807
0.2425 | 0.25681 | 0.3792 | 0.39805
0.24249 | 0.2568 | 0.37918 | 0.39802
0.24249 | 0.25679 | 0.37916 | 0.398
0.24248 | 0.25678 | 0.37916 | 0.39799
0.24246 | 0.25677 | 0.37914 | 0.39798
0.24245 | 0.25676 | 0.37911 | 0.39797
0.24244 | 0.25675 | 0.37909 | 0.39795
0.24243 | 0.25674 | 0.37907 | 0.39793
0.24242 | 0.25673 | 0.37905 | 0.39791
0.24241 | 0.25672 | 0.37902 | 0.3979
0.24241 | 0.25671 | 0.37898 | 0.39787
0.2424 | 0.2567 | 0.37897 | 0.39784
0.24239 | 0.2567 | 0.37895 | 0.39784
0.24238 | 0.25669 | 0.37894 | 0.39782
0.24237 | 0.25668 | 0.37894 | 0.3978
0.24236 | 0.25667 | 0.37891 | 0.39778
0.24236 | 0.25665 | 0.3789 | 0.39777
0.24234 | 0.25665 | 0.37887 | 0.39774
0.24234 | 0.25664 | 0.37885 | 0.39771
0.24233 | 0.25662 | 0.37884 | 0.3977
0.24232 | 0.2566 | 0.37882 | 0.39769
0.24231 | 0.25659 | 0.37879 | 0.39767
0.2423 | 0.25659 | 0.37878 | 0.39766
0.24229 | 0.25658 | 0.37876 | 0.39764
0.24228 | 0.25657 | 0.37872 | 0.39762
0.24227 | 0.25656 | 0.37871 | 0.3976
0.24226 | 0.25656 | 0.37869 | 0.39758
0.24225 | 0.25655 | 0.37867 | 0.39756
0.24224 | 0.25654 | 0.37866 | 0.39755
0.24223 | 0.25653 | 0.37864 | 0.39753
0.24222 | 0.25652 | 0.37862 | 0.39751
0.24221 | 0.25652 | 0.37859 | 0.39749
0.2422 | 0.25651 | 0.37857 | 0.39748
0.2422 | 0.25651 | 0.37855 | 0.39746
0.24219 | 0.2565 | 0.37854 | 0.39745
0.24218 | 0.25649 | 0.37852 | 0.39744
0.24217 | 0.25648 | 0.37851 | 0.39742
0.24216 | 0.25647 | 0.3785 | 0.39741
0.24215 | 0.25646 | 0.37848 | 0.39739
0.24214 | 0.25645 | 0.37847 | 0.39736
0.24213 | 0.25644 | 0.37845 | 0.39735
0.24211 | 0.25644 | 0.37844 | 0.39733
0.2421 | 0.25643 | 0.37843 | 0.39731
0.24209 | 0.25642 | 0.37841 | 0.3973
0.24208 | 0.25641 | 0.37839 | 0.39728
0.24207 | 0.2564 | 0.37838 | 0.39726
0.24206 | 0.2564 | 0.37837 | 0.39725
0.24205 | 0.25639 | 0.37833 | 0.39724
0.24204 | 0.25638 | 0.37831 | 0.39722
0.24202 | 0.25637 | 0.3783 | 0.39719
0.24202 | 0.25637 | 0.37829 | 0.39718
0.24201 | 0.25636 | 0.37827 | 0.39716
0.24199 | 0.25634 | 0.37825 | 0.39714
0.24198 | 0.25633 | 0.37823 | 0.39713
0.24197 | 0.25632 | 0.37821 | 0.39712
0.24196 | 0.25631 | 0.37819 | 0.39711
0.24194 | 0.25631 | 0.37818 | 0.3971
0.24193 | 0.2563 | 0.37816 | 0.39706
0.24192 | 0.25629 | 0.37813 | 0.39703
0.24191 | 0.25628 | 0.37811 | 0.39702
0.24189 | 0.25627 | 0.37809 | 0.397
0.24188 | 0.25626 | 0.37807 | 0.39699
0.24187 | 0.25625 | 0.37804 | 0.39697
0.24186 | 0.25624 | 0.37802 | 0.39696
0.24185 | 0.25623 | 0.378 | 0.39694
0.24184 | 0.25622 | 0.37799 | 0.39693
0.24183 | 0.25621 | 0.37797 | 0.39691
0.24181 | 0.25621 | 0.37795 | 0.39689
0.2418 | 0.2562 | 0.37793 | 0.39686
0.24179 | 0.25619 | 0.37791 | 0.39684
0.24178 | 0.25617 | 0.37789 | 0.39683
0.24177 | 0.25617 | 0.37788 | 0.39681
0.24176 | 0.25616 | 0.37787 | 0.39679
0.24176 | 0.25614 | 0.37786 | 0.39676
0.24175 | 0.25613 | 0.37784 | 0.39674
0.24174 | 0.25613 | 0.37783 | 0.39672
0.24174 | 0.25612 | 0.37781 | 0.3967
0.24172 | 0.2561 | 0.3778 | 0.39667
0.24171 | 0.2561 | 0.37778 | 0.39665
0.2417 | 0.25608 | 0.37777 | 0.39664
0.24169 | 0.25607 | 0.37776 | 0.39662
0.24168 | 0.25607 | 0.37774 | 0.39659
0.24166 | 0.25606 | 0.37772 | 0.39657
0.24165 | 0.25605 | 0.3777 | 0.39656
0.24164 | 0.25604 | 0.37768 | 0.39654
0.24163 | 0.25603 | 0.37765 | 0.39652
0.24163 | 0.25603 | 0.37765 | 0.3965
0.24162 | 0.25602 | 0.37763 | 0.39648
0.24161 | 0.25601 | 0.37761 | 0.39647
0.2416 | 0.256 | 0.3776 | 0.39645
0.24158 | 0.25599 | 0.37757 | 0.39642
0.24157 | 0.25598 | 0.37756 | 0.39641
0.24157 | 0.25597 | 0.37754 | 0.3964
0.24156 | 0.25597 | 0.37752 | 0.39638
0.24155 | 0.25596 | 0.3775 | 0.39637
0.24154 | 0.25595 | 0.37749 | 0.39636
0.24153 | 0.25594 | 0.37747 | 0.39634
0.24151 | 0.25593 | 0.37746 | 0.39632
0.2415 | 0.25593 | 0.37742 | 0.39631
0.24149 | 0.25592 | 0.37741 | 0.39629
0.24148 | 0.25591 | 0.3774 | 0.39627
0.24147 | 0.2559 | 0.37738 | 0.39626
0.24146 | 0.25589 | 0.37735 | 0.39625
0.24145 | 0.25587 | 0.37733 | 0.39621
0.24144 | 0.25586 | 0.37731 | 0.39618
0.24144 | 0.25585 | 0.37728 | 0.39617
0.24142 | 0.25584 | 0.37726 | 0.39616
0.2414 | 0.25583 | 0.37724 | 0.39614
0.24139 | 0.25582 | 0.37722 | 0.39613
0.24138 | 0.25581 | 0.3772 | 0.39612
0.24137 | 0.2558 | 0.37717 | 0.39611
0.24136 | 0.2558 | 0.37716 | 0.39609
0.24135 | 0.25579 | 0.37714 | 0.39609
0.24135 | 0.25578 | 0.37712 | 0.39607
0.24134 | 0.25577 | 0.37709 | 0.39605
0.24132 | 0.25576 | 0.37708 | 0.39604
0.24132 | 0.25575 | 0.37706 | 0.39602
0.2413 | 0.25575 | 0.37702 | 0.396
0.24129 | 0.25574 | 0.37702 | 0.39598
0.24127 | 0.25573 | 0.377 | 0.39597
0.24127 | 0.25572 | 0.37697 | 0.39594
0.24126 | 0.25571 | 0.37694 | 0.39591
0.24125 | 0.2557 | 0.37692 | 0.3959
0.24124 | 0.25569 | 0.3769 | 0.39589
0.24123 | 0.25569 | 0.3769 | 0.39587
0.24122 | 0.25568 | 0.37688 | 0.39584
0.24122 | 0.25567 | 0.37686 | 0.39583
0.24121 | 0.25565 | 0.37684 | 0.39581
0.2412 | 0.25564 | 0.37682 | 0.39579
0.24119 | 0.25564 | 0.3768 | 0.39578
0.24118 | 0.25563 | 0.37678 | 0.39576
0.24117 | 0.25562 | 0.37677 | 0.39574
0.24116 | 0.25561 | 0.37676 | 0.39573
0.24115 | 0.2556 | 0.37674 | 0.39571
0.24114 | 0.25559 | 0.37672 | 0.3957
0.24113 | 0.25558 | 0.3767 | 0.39567
0.24112 | 0.25557 | 0.37669 | 0.39565
0.24111 | 0.25556 | 0.37668 | 0.39563
0.2411 | 0.25555 | 0.37666 | 0.39559
0.24109 | 0.25554 | 0.37665 | 0.39559
0.24108 | 0.25553 | 0.37663 | 0.39557
0.24107 | 0.25552 | 0.37661 | 0.39555
0.24106 | 0.25552 | 0.37659 | 0.39554
0.24105 | 0.25551 | 0.37656 | 0.39552
0.24104 | 0.25549 | 0.37654 | 0.39551
0.24103 | 0.25548 | 0.37652 | 0.39549
0.24103 | 0.25547 | 0.3765 | 0.39548
0.24101 | 0.25545 | 0.37649 | 0.39545
0.241 | 0.25544 | 0.37648 | 0.39544
0.24099 | 0.25544 | 0.37647 | 0.39543
0.24098 | 0.25543 | 0.37644 | 0.39541
0.24097 | 0.25542 | 0.37642 | 0.3954
0.24095 | 0.25541 | 0.37639 | 0.39539
0.24094 | 0.2554 | 0.37637 | 0.39537
0.24093 | 0.25539 | 0.37635 | 0.39535
0.24092 | 0.25539 | 0.37632 | 0.39532
0.24092 | 0.25538 | 0.37631 | 0.3953
0.24091 | 0.25537 | 0.37628 | 0.39529
0.2409 | 0.25536 | 0.37624 | 0.39527
0.24088 | 0.25535 | 0.37622 | 0.39524
0.24088 | 0.25533 | 0.3762 | 0.39523
0.24087 | 0.25532 | 0.37619 | 0.39521
0.24087 | 0.25531 | 0.37617 | 0.3952
0.24085 | 0.2553 | 0.37615 | 0.39519
0.24084 | 0.2553 | 0.37613 | 0.39517
0.24083 | 0.25528 | 0.37609 | 0.39516
0.24082 | 0.25527 | 0.37607 | 0.39514
0.2408 | 0.25527 | 0.37606 | 0.39514
0.24079 | 0.25526 | 0.37605 | 0.39512
0.24078 | 0.25525 | 0.37602 | 0.39511
0.24076 | 0.25524 | 0.37601 | 0.39509
0.24076 | 0.25524 | 0.37599 | 0.39508
0.24074 | 0.25523 | 0.37597 | 0.39507
0.24073 | 0.25521 | 0.37596 | 0.39505
0.24072 | 0.25521 | 0.37594 | 0.39503
0.24071 | 0.2552 | 0.37593 | 0.39501
0.2407 | 0.25519 | 0.37591 | 0.395
0.24069 | 0.25518 | 0.3759 | 0.39499
0.24068 | 0.25518 | 0.37589 | 0.39498
0.24068 | 0.25516 | 0.37588 | 0.39496
0.24067 | 0.25516 | 0.37586 | 0.39493
0.24066 | 0.25515 | 0.37583 | 0.39492
0.24065 | 0.25514 | 0.3758 | 0.39489
0.24064 | 0.25513 | 0.37578 | 0.39488
0.24063 | 0.25512 | 0.37576 | 0.39486
0.24062 | 0.25512 | 0.37574 | 0.39485
0.24061 | 0.2551 | 0.37572 | 0.39483
0.24061 | 0.25509 | 0.3757 | 0.39482
0.2406 | 0.25507 | 0.37568 | 0.39479
0.24058 | 0.25506 | 0.37567 | 0.39478
0.24058 | 0.25506 | 0.37566 | 0.39476
0.24057 | 0.25505 | 0.37565 | 0.39474
0.24055 | 0.25504 | 0.37562 | 0.39472
0.24054 | 0.25503 | 0.37561 | 0.39469
0.24053 | 0.25502 | 0.3756 | 0.39467
0.24052 | 0.25501 | 0.37559 | 0.39465
0.24051 | 0.25501 | 0.37557 | 0.39464
0.2405 | 0.25499 | 0.37556 | 0.39463
0.2405 | 0.25499 | 0.37555 | 0.39462
0.24049 | 0.25498 | 0.37553 | 0.3946
0.24047 | 0.25497 | 0.37549 | 0.39459
0.24046 | 0.25496 | 0.37547 | 0.39457
0.24045 | 0.25495 | 0.37546 | 0.39456
0.24043 | 0.25494 | 0.37544 | 0.39454
0.24041 | 0.25493 | 0.37542 | 0.39452
0.2404 | 0.25493 | 0.37539 | 0.3945
0.2404 | 0.25492 | 0.37538 | 0.39448
0.24039 | 0.25491 | 0.37536 | 0.39447
0.24038 | 0.2549 | 0.37535 | 0.39445
0.24037 | 0.2549 | 0.37532 | 0.39443
0.24036 | 0.25489 | 0.3753 | 0.39442
0.24035 | 0.25488 | 0.37526 | 0.3944
0.24034 | 0.25487 | 0.37525 | 0.39437
0.24032 | 0.25486 | 0.37523 | 0.39437
0.24031 | 0.25486 | 0.37523 | 0.39435
0.24031 | 0.25485 | 0.37521 | 0.39434
0.24029 | 0.25484 | 0.37519 | 0.39433
0.24029 | 0.25484 | 0.37516 | 0.39431
0.24027 | 0.25483 | 0.37515 | 0.39428
0.24027 | 0.25482 | 0.37512 | 0.39427
0.24025 | 0.2548 | 0.3751 | 0.39425
0.24025 | 0.25479 | 0.37509 | 0.39423
0.24024 | 0.25479 | 0.37507 | 0.39422
0.24022 | 0.25478 | 0.37505 | 0.39421
0.24022 | 0.25477 | 0.37503 | 0.3942
0.24021 | 0.25476 | 0.37502 | 0.39418
0.2402 | 0.25475 | 0.37501 | 0.39416
0.2402 | 0.25474 | 0.37499 | 0.39414
0.24018 | 0.25473 | 0.37497 | 0.39413
0.24017 | 0.25473 | 0.37495 | 0.39411
0.24017 | 0.25472 | 0.37494 | 0.39409
0.24015 | 0.25471 | 0.37492 | 0.39406
0.24013 | 0.25471 | 0.3749 | 0.39405
0.24012 | 0.2547 | 0.37489 | 0.39403
0.2401 | 0.25468 | 0.37486 | 0.39403
0.24009 | 0.25467 | 0.37484 | 0.39402
0.24008 | 0.25466 | 0.37483 | 0.39401
0.24007 | 0.25466 | 0.37481 | 0.39399
0.24005 | 0.25465 | 0.37479 | 0.39398
0.24004 | 0.25464 | 0.37477 | 0.39395
0.24003 | 0.25464 | 0.37474 | 0.39394
0.24002 | 0.25463 | 0.37472 | 0.39393
0.24002 | 0.25462 | 0.37469 | 0.39391
0.24 | 0.25461 | 0.37466 | 0.39391
0.24 | 0.2546 | 0.37465 | 0.39389
0.23999 | 0.25459 | 0.37463 | 0.39388
0.23998 | 0.25458 | 0.37461 | 0.39387
0.23996 | 0.25457 | 0.37459 | 0.39386
0.23993 | 0.25456 | 0.37457 | 0.39384
0.23993 | 0.25455 | 0.37454 | 0.39383
0.23992 | 0.25454 | 0.37451 | 0.39381
0.23991 | 0.25454 | 0.37451 | 0.3938
0.2399 | 0.25453 | 0.3745 | 0.39377
0.23989 | 0.25452 | 0.37449 | 0.39375
0.23988 | 0.25451 | 0.37447 | 0.39373
0.23988 | 0.2545 | 0.37445 | 0.39372
0.23987 | 0.25449 | 0.37443 | 0.39371
0.23985 | 0.25448 | 0.37442 | 0.3937
0.23984 | 0.25447 | 0.37441 | 0.39368
0.23983 | 0.25446 | 0.37439 | 0.39366
0.23982 | 0.25446 | 0.37438 | 0.39364
0.2398 | 0.25443 | 0.37436 | 0.39363
0.23979 | 0.25442 | 0.37434 | 0.39361
0.23979 | 0.25442 | 0.37432 | 0.39358
0.23978 | 0.25441 | 0.37428 | 0.39357
0.23977 | 0.2544 | 0.37425 | 0.39355
0.23976 | 0.25439 | 0.37423 | 0.39353
0.23975 | 0.25438 | 0.3742 | 0.39352
0.23974 | 0.25437 | 0.37418 | 0.3935
0.23973 | 0.25436 | 0.37417 | 0.39348
0.23971 | 0.25435 | 0.37415 | 0.39347
0.2397 | 0.25434 | 0.37413 | 0.39346
0.23969 | 0.25433 | 0.37412 | 0.39343
0.23968 | 0.25431 | 0.3741 | 0.39339
0.23967 | 0.25431 | 0.37408 | 0.39337
0.23966 | 0.2543 | 0.37406 | 0.39336
0.23966 | 0.25429 | 0.37405 | 0.39334
0.23964 | 0.25428 | 0.37402 | 0.39332
0.23963 | 0.25427 | 0.374 | 0.3933
0.23963 | 0.25427 | 0.37396 | 0.39329
0.23962 | 0.25426 | 0.37395 | 0.39327
0.2396 | 0.25425 | 0.37392 | 0.39325
0.23959 | 0.25423 | 0.3739 | 0.39324
0.23958 | 0.25422 | 0.37388 | 0.39322
0.23957 | 0.25421 | 0.37386 | 0.3932
0.23956 | 0.2542 | 0.37384 | 0.39317
0.23955 | 0.25419 | 0.37383 | 0.39315
0.23954 | 0.25419 | 0.37381 | 0.39313
0.23953 | 0.25418 | 0.37379 | 0.39312
0.23952 | 0.25417 | 0.37377 | 0.39311
0.2395 | 0.25417 | 0.37374 | 0.39308
0.23949 | 0.25416 | 0.37373 | 0.39305
0.23948 | 0.25415 | 0.37371 | 0.39304
0.23947 | 0.25414 | 0.37369 | 0.39302
0.23946 | 0.25413 | 0.37367 | 0.39299
0.23945 | 0.25413 | 0.37366 | 0.39298
0.23944 | 0.25412 | 0.37365 | 0.39296
0.23943 | 0.25412 | 0.37363 | 0.39294
0.23943 | 0.2541 | 0.37361 | 0.39291
0.23941 | 0.2541 | 0.3736 | 0.3929
0.2394 | 0.25409 | 0.37358 | 0.39289
0.23939 | 0.25408 | 0.37357 | 0.39285
0.23939 | 0.25408 | 0.37355 | 0.39283
0.23937 | 0.25407 | 0.37353 | 0.39282
0.23937 | 0.25406 | 0.37351 | 0.3928
0.23936 | 0.25405 | 0.37348 | 0.39278
0.23935 | 0.25405 | 0.37343 | 0.39277
0.23934 | 0.25404 | 0.37342 | 0.39274
0.23933 | 0.25404 | 0.37339 | 0.39273
0.23932 | 0.25403 | 0.37337 | 0.39271
0.23931 | 0.25402 | 0.37336 | 0.39269
0.2393 | 0.25401 | 0.37334 | 0.39267
0.23929 | 0.254 | 0.37333 | 0.39266
0.23928 | 0.254 | 0.37331 | 0.39264
0.23927 | 0.25398 | 0.37329 | 0.39262
0.23926 | 0.25397 | 0.37327 | 0.3926
0.23925 | 0.25396 | 0.37326 | 0.39259
0.23923 | 0.25395 | 0.37325 | 0.39258
0.23922 | 0.25394 | 0.37322 | 0.39255
0.23921 | 0.25393 | 0.37321 | 0.39254
0.2392 | 0.25393 | 0.37318 | 0.39251
0.23919 | 0.25392 | 0.37316 | 0.3925
0.23919 | 0.25391 | 0.37314 | 0.39249
0.23918 | 0.2539 | 0.37313 | 0.39248
0.23917 | 0.2539 | 0.37311 | 0.39246
0.23916 | 0.25389 | 0.3731 | 0.39245
0.23915 | 0.25388 | 0.37308 | 0.39242
0.23914 | 0.25387 | 0.37306 | 0.39241
0.23913 | 0.25386 | 0.37304 | 0.39241
0.23911 | 0.25386 | 0.37303 | 0.39238
0.2391 | 0.25385 | 0.37301 | 0.39237
0.23909 | 0.25384 | 0.37299 | 0.39235
0.23908 | 0.25383 | 0.37298 | 0.39233
0.23908 | 0.25382 | 0.37296 | 0.39231
0.23906 | 0.25382 | 0.37295 | 0.39229
0.23905 | 0.25381 | 0.37293 | 0.39227
0.23903 | 0.2538 | 0.37292 | 0.39225
0.23902 | 0.25379 | 0.3729 | 0.39223
0.23902 | 0.25378 | 0.37288 | 0.39221
0.23901 | 0.25377 | 0.37286 | 0.3922
0.239 | 0.25377 | 0.37285 | 0.39218
0.23899 | 0.25376 | 0.37284 | 0.39215
0.23898 | 0.25374 | 0.37282 | 0.39213
0.23897 | 0.25373 | 0.37281 | 0.39211
0.23896 | 0.25372 | 0.37278 | 0.3921
0.23895 | 0.25371 | 0.37277 | 0.39208
0.23894 | 0.2537 | 0.37275 | 0.39206
0.23893 | 0.25369 | 0.37274 | 0.39204
0.23892 | 0.25368 | 0.37272 | 0.39203
0.23891 | 0.25367 | 0.3727 | 0.39201
0.2389 | 0.25366 | 0.37268 | 0.392
0.23889 | 0.25366 | 0.37266 | 0.39199
0.23888 | 0.25365 | 0.37265 | 0.39196
0.23887 | 0.25364 | 0.37263 | 0.39194
0.23886 | 0.25363 | 0.37261 | 0.39193
0.23885 | 0.25362 | 0.37259 | 0.3919
0.23883 | 0.25361 | 0.37257 | 0.39188
0.23881 | 0.2536 | 0.37255 | 0.39187
0.23881 | 0.2536 | 0.37252 | 0.39185
0.2388 | 0.25359 | 0.3725 | 0.39184
0.23879 | 0.25358 | 0.37248 | 0.39182
0.23878 | 0.25357 | 0.37246 | 0.39179
0.23877 | 0.25356 | 0.37244 | 0.39177
0.23876 | 0.25355 | 0.37242 | 0.39175
0.23875 | 0.25354 | 0.37241 | 0.39175
0.23874 | 0.25353 | 0.37239 | 0.39172
0.23873 | 0.25352 | 0.37236 | 0.3917
0.23872 | 0.25351 | 0.37235 | 0.39169
0.23871 | 0.2535 | 0.37232 | 0.39167
0.23869 | 0.25349 | 0.37231 | 0.39165
0.23868 | 0.25348 | 0.37229 | 0.39163
0.23867 | 0.25347 | 0.37226 | 0.39162
0.23866 | 0.25346 | 0.37225 | 0.39161
0.23865 | 0.25345 | 0.37222 | 0.39159
0.23864 | 0.25345 | 0.37221 | 0.39158
0.23863 | 0.25344 | 0.37219 | 0.39156
0.23862 | 0.25343 | 0.37217 | 0.39154
0.23861 | 0.25342 | 0.37215 | 0.39151
0.2386 | 0.25342 | 0.37213 | 0.39149
0.23858 | 0.25341 | 0.37212 | 0.39148
0.23857 | 0.25339 | 0.3721 | 0.39146
0.23856 | 0.25338 | 0.37208 | 0.39145
0.23855 | 0.25337 | 0.37207 | 0.39144
0.23854 | 0.25336 | 0.37206 | 0.39142
0.23853 | 0.25335 | 0.37204 | 0.39139
0.23851 | 0.25333 | 0.37202 | 0.39136
0.2385 | 0.25332 | 0.37199 | 0.39134
0.2385 | 0.25332 | 0.37197 | 0.39133
0.23849 | 0.25331 | 0.37196 | 0.39132
0.23848 | 0.2533 | 0.37195 | 0.3913
0.23846 | 0.25329 | 0.37193 | 0.39129
0.23845 | 0.25328 | 0.3719 | 0.39126
0.23845 | 0.25327 | 0.37188 | 0.39125
0.23844 | 0.25325 | 0.37187 | 0.39123
0.23843 | 0.25325 | 0.37187 | 0.39121
0.23842 | 0.25324 | 0.37184 | 0.39119
0.23841 | 0.25323 | 0.37182 | 0.39117
0.2384 | 0.25322 | 0.3718 | 0.39115
0.23838 | 0.25321 | 0.37178 | 0.39113
0.23837 | 0.2532 | 0.37176 | 0.39112
0.23836 | 0.25319 | 0.37174 | 0.3911
0.23835 | 0.25317 | 0.37172 | 0.39109
0.23834 | 0.25316 | 0.3717 | 0.39108
0.23833 | 0.25315 | 0.37169 | 0.39107
0.23831 | 0.25314 | 0.37167 | 0.39106
0.2383 | 0.25313 | 0.37166 | 0.39104
0.23829 | 0.25312 | 0.37163 | 0.39102
0.23828 | 0.25311 | 0.37161 | 0.391
0.23827 | 0.2531 | 0.37159 | 0.39099
0.23827 | 0.25309 | 0.37156 | 0.39096
0.23826 | 0.25308 | 0.37154 | 0.39096
0.23824 | 0.25307 | 0.37152 | 0.39094
0.23823 | 0.25306 | 0.3715 | 0.39092
0.23823 | 0.25305 | 0.37148 | 0.3909
0.23821 | 0.25304 | 0.37147 | 0.39089
0.2382 | 0.25303 | 0.37145 | 0.39088
0.23819 | 0.25302 | 0.37142 | 0.39087
0.23818 | 0.25302 | 0.37141 | 0.39085
0.23817 | 0.25301 | 0.37139 | 0.39083
0.23816 | 0.25301 | 0.37137 | 0.39081
0.23815 | 0.25299 | 0.37136 | 0.39079
0.23814 | 0.25298 | 0.37134 | 0.39078
0.23813 | 0.25297 | 0.37132 | 0.39076
0.23812 | 0.25296 | 0.37129 | 0.39075
0.23811 | 0.25295 | 0.37127 | 0.39073
0.2381 | 0.25294 | 0.37124 | 0.39071
0.23809 | 0.25293 | 0.37123 | 0.39069
0.23808 | 0.25292 | 0.37121 | 0.39068
0.23807 | 0.25292 | 0.37119 | 0.39066
0.23806 | 0.25291 | 0.37117 | 0.39065
0.23805 | 0.25289 | 0.37115 | 0.39063
0.23804 | 0.25288 | 0.37113 | 0.39061
0.23802 | 0.25288 | 0.37112 | 0.39059
0.23802 | 0.25286 | 0.37111 | 0.39058
0.23801 | 0.25285 | 0.3711 | 0.39057
0.238 | 0.25284 | 0.37109 | 0.39055
0.23799 | 0.25284 | 0.37106 | 0.39052
0.23799 | 0.25283 | 0.37103 | 0.3905
0.23798 | 0.25282 | 0.37099 | 0.39049
0.23797 | 0.25281 | 0.37097 | 0.39047
0.23796 | 0.2528 | 0.37095 | 0.39046
0.23794 | 0.25278 | 0.37093 | 0.39044
0.23793 | 0.25277 | 0.37091 | 0.39042
0.23792 | 0.25276 | 0.3709 | 0.3904
0.23791 | 0.25275 | 0.37089 | 0.39037
0.2379 | 0.25274 | 0.37087 | 0.39035
0.23789 | 0.25274 | 0.37086 | 0.39034
0.23787 | 0.25273 | 0.37085 | 0.39031
0.23786 | 0.25273 | 0.37082 | 0.3903
0.23785 | 0.25272 | 0.3708 | 0.39028
0.23785 | 0.25271 | 0.37078 | 0.39026
0.23783 | 0.2527 | 0.37076 | 0.39024
0.23783 | 0.25269 | 0.37075 | 0.39021
0.23782 | 0.25268 | 0.37074 | 0.3902
0.23781 | 0.25267 | 0.37072 | 0.39018
0.2378 | 0.25266 | 0.3707 | 0.39016
0.23779 | 0.25265 | 0.37068 | 0.39015
0.23777 | 0.25264 | 0.37066 | 0.39014
0.23776 | 0.25263 | 0.37063 | 0.39012
0.23775 | 0.25262 | 0.37062 | 0.39011
0.23774 | 0.25261 | 0.37059 | 0.3901
0.23774 | 0.25261 | 0.37057 | 0.39008
0.23773 | 0.2526 | 0.37054 | 0.39007
0.23772 | 0.25258 | 0.37052 | 0.39005
0.23771 | 0.25257 | 0.37051 | 0.39003
0.2377 | 0.25256 | 0.37048 | 0.39002
0.23768 | 0.25255 | 0.37046 | 0.39
0.23768 | 0.25255 | 0.37044 | 0.38999
0.23767 | 0.25254 | 0.37042 | 0.38997
0.23765 | 0.25253 | 0.37041 | 0.38995
0.23765 | 0.25252 | 0.37039 | 0.38994
0.23763 | 0.2525 | 0.37037 | 0.38991
0.23762 | 0.2525 | 0.37036 | 0.38991
0.23761 | 0.25249 | 0.37035 | 0.38988
0.2376 | 0.25248 | 0.37034 | 0.38986
0.23758 | 0.25247 | 0.37032 | 0.38984
0.23758 | 0.25247 | 0.37031 | 0.38983
0.23757 | 0.25246 | 0.37029 | 0.38982
0.23755 | 0.25245 | 0.37027 | 0.3898
0.23754 | 0.25244 | 0.37025 | 0.38979
0.23753 | 0.25243 | 0.37023 | 0.38977
0.23752 | 0.25242 | 0.37021 | 0.38975
0.23751 | 0.25242 | 0.37019 | 0.38973
0.2375 | 0.2524 | 0.37018 | 0.38972
0.23749 | 0.25239 | 0.37015 | 0.38971
0.23748 | 0.25239 | 0.37012 | 0.38969
0.23746 | 0.25237 | 0.37011 | 0.38967
0.23745 | 0.25237 | 0.37008 | 0.38966
0.23744 | 0.25236 | 0.37006 | 0.38964
0.23743 | 0.25235 | 0.37005 | 0.38962
0.23741 | 0.25234 | 0.37003 | 0.3896
0.2374 | 0.25233 | 0.37002 | 0.38957
0.23739 | 0.25233 | 0.36999 | 0.38956
0.23737 | 0.25232 | 0.36997 | 0.38953
0.23737 | 0.25231 | 0.36996 | 0.38952
0.23736 | 0.25231 | 0.36995 | 0.38949
0.23735 | 0.2523 | 0.36993 | 0.38946
0.23733 | 0.25229 | 0.36991 | 0.38945
0.23732 | 0.25228 | 0.36989 | 0.38943
0.23731 | 0.25227 | 0.36987 | 0.38942
0.2373 | 0.25226 | 0.36986 | 0.3894
0.2373 | 0.25225 | 0.36984 | 0.38937
0.23729 | 0.25223 | 0.36982 | 0.38936
0.23727 | 0.25222 | 0.36981 | 0.38935
0.23726 | 0.25221 | 0.36979 | 0.38934
0.23725 | 0.25221 | 0.36977 | 0.38933
0.23724 | 0.2522 | 0.36975 | 0.38932
0.23723 | 0.25219 | 0.36974 | 0.38931
0.23722 | 0.25217 | 0.36972 | 0.38929
0.2372 | 0.25217 | 0.36969 | 0.38927
0.23719 | 0.25216 | 0.36966 | 0.38926
0.23719 | 0.25215 | 0.36965 | 0.38924
0.23718 | 0.25214 | 0.36963 | 0.38921
0.23717 | 0.25213 | 0.36961 | 0.3892
0.23716 | 0.25212 | 0.36958 | 0.38918
0.23715 | 0.25212 | 0.36957 | 0.38917
0.23713 | 0.25211 | 0.36955 | 0.38914
0.23712 | 0.2521 | 0.36952 | 0.38913
0.23711 | 0.25209 | 0.3695 | 0.38911
0.23708 | 0.25209 | 0.36947 | 0.38909
0.23707 | 0.25208 | 0.36946 | 0.38907
0.23706 | 0.25207 | 0.36944 | 0.38906
0.23705 | 0.25206 | 0.36939 | 0.38905
0.23704 | 0.25206 | 0.36937 | 0.38904
0.23703 | 0.25205 | 0.36935 | 0.38902
0.23701 | 0.25203 | 0.36934 | 0.38901
0.237 | 0.25203 | 0.36931 | 0.389
0.23699 | 0.25201 | 0.3693 | 0.38899
0.23698 | 0.252 | 0.36929 | 0.38897
0.23697 | 0.252 | 0.36927 | 0.38896
0.23696 | 0.25199 | 0.36926 | 0.38895
0.23695 | 0.25198 | 0.36924 | 0.38894
0.23694 | 0.25197 | 0.36923 | 0.38893
0.23693 | 0.25196 | 0.3692 | 0.38892
0.23691 | 0.25195 | 0.36918 | 0.3889
0.23691 | 0.25194 | 0.36916 | 0.38888
0.2369 | 0.25193 | 0.36914 | 0.38887
0.23689 | 0.25192 | 0.36912 | 0.38886
0.23687 | 0.25192 | 0.3691 | 0.38883
0.23687 | 0.2519 | 0.36908 | 0.38881
0.23685 | 0.25189 | 0.36907 | 0.3888
0.23684 | 0.25188 | 0.36905 | 0.38879
0.23684 | 0.25188 | 0.36903 | 0.38876
0.23683 | 0.25187 | 0.36901 | 0.38875
0.23682 | 0.25186 | 0.36899 | 0.38874
0.23681 | 0.25184 | 0.36898 | 0.38873
0.2368 | 0.25183 | 0.36896 | 0.38871
0.23679 | 0.25182 | 0.36893 | 0.38871
0.23678 | 0.25181 | 0.36891 | 0.38869
0.23675 | 0.2518 | 0.36889 | 0.38867
0.23675 | 0.2518 | 0.36888 | 0.38864
0.23674 | 0.25178 | 0.36887 | 0.38863
0.23673 | 0.25177 | 0.36885 | 0.38861
0.23673 | 0.25176 | 0.36882 | 0.38861
0.23671 | 0.25175 | 0.36881 | 0.3886
0.23669 | 0.25174 | 0.36879 | 0.38859
0.23668 | 0.25173 | 0.36877 | 0.38858
0.23667 | 0.25172 | 0.36875 | 0.38856
0.23666 | 0.25171 | 0.36874 | 0.38855
0.23665 | 0.2517 | 0.36873 | 0.38854
0.23664 | 0.25169 | 0.36871 | 0.38851
0.23663 | 0.25168 | 0.36868 | 0.3885
0.23661 | 0.25167 | 0.36867 | 0.38849
0.2366 | 0.25166 | 0.36864 | 0.38847
0.2366 | 0.25165 | 0.36861 | 0.38846
0.23658 | 0.25165 | 0.36858 | 0.38845
0.23657 | 0.25164 | 0.36856 | 0.38844
0.23656 | 0.25163 | 0.36854 | 0.38842
0.23655 | 0.25161 | 0.36852 | 0.38841
0.23654 | 0.2516 | 0.3685 | 0.3884
0.23654 | 0.25159 | 0.36848 | 0.38839
0.23653 | 0.25158 | 0.36847 | 0.38837
0.23652 | 0.25157 | 0.36845 | 0.38835
0.2365 | 0.25156 | 0.36844 | 0.38834
0.23649 | 0.25156 | 0.36843 | 0.38833
0.23649 | 0.25155 | 0.36842 | 0.38832
0.23647 | 0.25154 | 0.3684 | 0.3883
0.23646 | 0.25153 | 0.36839 | 0.38829
0.23646 | 0.25152 | 0.36837 | 0.38828
0.23645 | 0.2515 | 0.36835 | 0.38826
0.23643 | 0.2515 | 0.36832 | 0.38825
0.23642 | 0.25149 | 0.36831 | 0.38823
0.23641 | 0.25148 | 0.36829 | 0.38821
0.23641 | 0.25147 | 0.36827 | 0.38819
0.2364 | 0.25146 | 0.36825 | 0.38817
0.23639 | 0.25145 | 0.36824 | 0.38815
0.23637 | 0.25144 | 0.36822 | 0.38814
0.23636 | 0.25143 | 0.36821 | 0.38812
0.23635 | 0.25143 | 0.36819 | 0.38811
0.23634 | 0.25142 | 0.36818 | 0.38809
0.23633 | 0.25141 | 0.36815 | 0.38808
0.23632 | 0.2514 | 0.36813 | 0.38806
0.2363 | 0.25139 | 0.36811 | 0.38804
0.23629 | 0.25138 | 0.36807 | 0.38803
0.23627 | 0.25137 | 0.36805 | 0.38801
0.23626 | 0.25137 | 0.36803 | 0.38798
0.23626 | 0.25136 | 0.36802 | 0.38797
0.23625 | 0.25135 | 0.36801 | 0.38796
0.23623 | 0.25134 | 0.368 | 0.38794
0.23622 | 0.25133 | 0.36798 | 0.38794
0.23621 | 0.25132 | 0.36796 | 0.38793
0.2362 | 0.25132 | 0.36795 | 0.38791
0.23619 | 0.2513 | 0.36793 | 0.3879
0.23618 | 0.25129 | 0.36791 | 0.38788
0.23618 | 0.25128 | 0.3679 | 0.38787
0.23617 | 0.25128 | 0.36788 | 0.38784
0.23616 | 0.25126 | 0.36787 | 0.38783
0.23615 | 0.25126 | 0.36785 | 0.38781
0.23614 | 0.25125 | 0.36783 | 0.3878
0.23613 | 0.25124 | 0.36781 | 0.38779
0.23612 | 0.25124 | 0.3678 | 0.38777
0.2361 | 0.25122 | 0.36777 | 0.38775
0.23609 | 0.25121 | 0.36775 | 0.38773
0.23608 | 0.2512 | 0.36773 | 0.38771
0.23607 | 0.25119 | 0.36772 | 0.38769
0.23606 | 0.25118 | 0.3677 | 0.38768
0.23605 | 0.25118 | 0.36769 | 0.38766
0.23604 | 0.25117 | 0.36768 | 0.38764
0.23602 | 0.25116 | 0.36766 | 0.38761
0.23602 | 0.25115 | 0.36764 | 0.38759
0.23601 | 0.25114 | 0.36762 | 0.38759
0.236 | 0.25113 | 0.3676 | 0.38757
0.236 | 0.25112 | 0.36758 | 0.38755
0.23598 | 0.25111 | 0.36756 | 0.38753
0.23597 | 0.2511 | 0.36755 | 0.38752
0.23596 | 0.25109 | 0.36752 | 0.38751
0.23595 | 0.25108 | 0.36749 | 0.38749
0.23594 | 0.25108 | 0.36748 | 0.38746
0.23593 | 0.25107 | 0.36747 | 0.38744
0.23593 | 0.25107 | 0.36744 | 0.38742
0.23591 | 0.25106 | 0.36743 | 0.38739
0.23591 | 0.25105 | 0.36741 | 0.38736
0.2359 | 0.25104 | 0.3674 | 0.38734
0.23588 | 0.25104 | 0.36737 | 0.38731
0.23587 | 0.25102 | 0.36736 | 0.38728
0.23586 | 0.25102 | 0.36734 | 0.38726
0.23584 | 0.25101 | 0.36732 | 0.38725
0.23583 | 0.251 | 0.3673 | 0.38724
0.23582 | 0.251 | 0.36727 | 0.38722
0.23581 | 0.25099 | 0.36724 | 0.38719
0.2358 | 0.25098 | 0.36723 | 0.38717
0.23579 | 0.25097 | 0.36721 | 0.38715
0.23578 | 0.25096 | 0.3672 | 0.38714
0.23577 | 0.25095 | 0.36719 | 0.38713
0.23575 | 0.25094 | 0.36717 | 0.38711
0.23574 | 0.25093 | 0.36715 | 0.3871
0.23573 | 0.25093 | 0.36712 | 0.38709
0.23572 | 0.25092 | 0.3671 | 0.38707
0.23571 | 0.25091 | 0.36708 | 0.38705
0.2357 | 0.2509 | 0.36707 | 0.38704
0.23569 | 0.25089 | 0.36706 | 0.38702
0.23568 | 0.25089 | 0.36705 | 0.38699
0.23566 | 0.25088 | 0.36702 | 0.38698
0.23565 | 0.25087 | 0.367 | 0.38697
0.23563 | 0.25086 | 0.36698 | 0.38696
0.23563 | 0.25085 | 0.36696 | 0.38692
0.23562 | 0.25084 | 0.36695 | 0.3869
0.23561 | 0.25083 | 0.36693 | 0.38687
0.2356 | 0.25082 | 0.36692 | 0.38684
0.23559 | 0.25081 | 0.36691 | 0.38683
0.23558 | 0.2508 | 0.36689 | 0.38682
0.23557 | 0.25079 | 0.36687 | 0.3868
0.23556 | 0.25078 | 0.36684 | 0.38678
0.23554 | 0.25077 | 0.36683 | 0.38676
0.23553 | 0.25076 | 0.36681 | 0.38675
0.23552 | 0.25075 | 0.3668 | 0.38673
0.2355 | 0.25073 | 0.36678 | 0.38669
0.23549 | 0.25072 | 0.36675 | 0.38667
0.23548 | 0.25071 | 0.36674 | 0.38665
0.23547 | 0.25071 | 0.36671 | 0.38664
0.23546 | 0.2507 | 0.36668 | 0.38662
0.23545 | 0.25069 | 0.36667 | 0.38661
0.23544 | 0.25068 | 0.36666 | 0.38658
0.23543 | 0.25066 | 0.36665 | 0.38656
0.23542 | 0.25065 | 0.36664 | 0.38655
0.23541 | 0.25064 | 0.36662 | 0.38652
0.2354 | 0.25063 | 0.36661 | 0.38651
0.23539 | 0.25061 | 0.36658 | 0.38649
0.23539 | 0.25061 | 0.36655 | 0.38648
0.23537 | 0.2506 | 0.36653 | 0.38646
0.23537 | 0.25059 | 0.36651 | 0.38645
0.23536 | 0.25058 | 0.3665 | 0.38642
0.23535 | 0.25057 | 0.36648 | 0.3864
0.23534 | 0.25057 | 0.36646 | 0.38638
0.23533 | 0.25056 | 0.36644 | 0.38636
0.23532 | 0.25055 | 0.36642 | 0.38634
0.23531 | 0.25054 | 0.3664 | 0.38634
0.23529 | 0.25054 | 0.36638 | 0.38631
0.23528 | 0.25053 | 0.36635 | 0.38629
0.23527 | 0.25052 | 0.36633 | 0.38627
0.23527 | 0.25052 | 0.3663 | 0.38625
0.23525 | 0.2505 | 0.36628 | 0.38623
0.23525 | 0.25049 | 0.36625 | 0.38623
0.23523 | 0.25048 | 0.36624 | 0.38621
0.23522 | 0.25047 | 0.36622 | 0.38619
0.2352 | 0.25046 | 0.36621 | 0.38618
0.2352 | 0.25045 | 0.3662 | 0.38616
0.23518 | 0.25045 | 0.36618 | 0.38614
0.23517 | 0.25044 | 0.36617 | 0.38613
0.23516 | 0.25043 | 0.36614 | 0.38612
0.23515 | 0.25043 | 0.36613 | 0.38611
0.23514 | 0.25042 | 0.36611 | 0.3861
0.23514 | 0.25041 | 0.36608 | 0.38608
0.23512 | 0.2504 | 0.36606 | 0.38607
0.23512 | 0.25039 | 0.36605 | 0.38605
0.23511 | 0.25038 | 0.36605 | 0.38604
0.2351 | 0.25038 | 0.36602 | 0.38601
0.23509 | 0.25037 | 0.36601 | 0.386
0.23508 | 0.25036 | 0.36598 | 0.38598
0.23507 | 0.25035 | 0.36595 | 0.38596
0.23506 | 0.25034 | 0.36593 | 0.38593
0.23505 | 0.25034 | 0.36591 | 0.38592
0.23505 | 0.25033 | 0.3659 | 0.3859
0.23504 | 0.25031 | 0.36587 | 0.38589
0.23502 | 0.2503 | 0.36585 | 0.38589
0.23502 | 0.25029 | 0.36583 | 0.38587
0.235 | 0.25028 | 0.36582 | 0.38586
0.23499 | 0.25027 | 0.36579 | 0.38584
0.23498 | 0.25026 | 0.36576 | 0.38582
0.23498 | 0.25025 | 0.36574 | 0.38581
0.23497 | 0.25024 | 0.36573 | 0.3858
0.23496 | 0.25023 | 0.36571 | 0.38576
0.23494 | 0.25022 | 0.36569 | 0.38575
0.23494 | 0.25022 | 0.36568 | 0.38573
0.23493 | 0.25021 | 0.36565 | 0.38572
0.23491 | 0.2502 | 0.36564 | 0.38568
0.2349 | 0.2502 | 0.36562 | 0.38566
0.23489 | 0.25019 | 0.3656 | 0.38565
0.23488 | 0.25018 | 0.36558 | 0.38563
0.23487 | 0.25017 | 0.36554 | 0.38562
0.23485 | 0.25016 | 0.36553 | 0.3856
0.23484 | 0.25014 | 0.36551 | 0.38559
0.23483 | 0.25013 | 0.36549 | 0.38556
0.23481 | 0.25012 | 0.36548 | 0.38554
0.2348 | 0.25012 | 0.36547 | 0.38553
0.23479 | 0.2501 | 0.36543 | 0.38552
0.23477 | 0.25009 | 0.36541 | 0.3855
0.23476 | 0.25007 | 0.36538 | 0.38548
0.23475 | 0.25006 | 0.36537 | 0.38546
0.23474 | 0.25005 | 0.36536 | 0.38544
0.23473 | 0.25004 | 0.36535 | 0.38542
0.23472 | 0.25003 | 0.36533 | 0.38541
0.23472 | 0.25002 | 0.3653 | 0.38539
0.23471 | 0.25001 | 0.36528 | 0.38538
0.2347 | 0.25 | 0.36526 | 0.38537
0.23468 | 0.24999 | 0.36524 | 0.38535
0.23467 | 0.24998 | 0.36522 | 0.38534
0.23466 | 0.24997 | 0.36521 | 0.38531
0.23466 | 0.24996 | 0.36519 | 0.38528
0.23465 | 0.24995 | 0.36516 | 0.38527
0.23464 | 0.24995 | 0.36514 | 0.38525
0.23463 | 0.24994 | 0.36513 | 0.38524
0.23462 | 0.24993 | 0.36512 | 0.38522
0.23461 | 0.24992 | 0.36509 | 0.3852
0.2346 | 0.24991 | 0.36507 | 0.38517
0.23459 | 0.24991 | 0.36506 | 0.38516
0.23458 | 0.2499 | 0.36504 | 0.38514
0.23456 | 0.24989 | 0.36503 | 0.38513
0.23455 | 0.24988 | 0.36501 | 0.38512
0.23454 | 0.24987 | 0.365 | 0.38511
0.23453 | 0.24986 | 0.36499 | 0.38509
0.23453 | 0.24985 | 0.36498 | 0.38507
0.23451 | 0.24984 | 0.36496 | 0.38505
0.2345 | 0.24983 | 0.36495 | 0.38504
0.23449 | 0.24982 | 0.36493 | 0.38502
0.23448 | 0.24981 | 0.36491 | 0.38501
0.23447 | 0.2498 | 0.36489 | 0.385
0.23446 | 0.24979 | 0.36486 | 0.38498
0.23445 | 0.24977 | 0.36485 | 0.38496
0.23444 | 0.24976 | 0.36481 | 0.38493
0.23442 | 0.24975 | 0.3648 | 0.38492
0.23441 | 0.24974 | 0.36477 | 0.3849
0.2344 | 0.24973 | 0.36475 | 0.38489
0.23438 | 0.24972 | 0.36474 | 0.38487
0.23437 | 0.24971 | 0.36471 | 0.38486
0.23436 | 0.24971 | 0.36469 | 0.38483
0.23434 | 0.2497 | 0.36466 | 0.38481
0.23433 | 0.24969 | 0.36465 | 0.3848
0.23432 | 0.24968 | 0.36462 | 0.38479
0.23431 | 0.24967 | 0.36461 | 0.38476
0.2343 | 0.24966 | 0.36459 | 0.38475
0.23428 | 0.24965 | 0.36457 | 0.38473
0.23427 | 0.24964 | 0.36456 | 0.38472
0.23427 | 0.24963 | 0.36453 | 0.38471
0.23425 | 0.24962 | 0.36452 | 0.3847
0.23424 | 0.24961 | 0.36451 | 0.38469
0.23423 | 0.2496 | 0.3645 | 0.38467
0.23421 | 0.24959 | 0.36449 | 0.38465
0.2342 | 0.24958 | 0.36447 | 0.38464
0.23419 | 0.24957 | 0.36445 | 0.38462
0.23418 | 0.24956 | 0.36444 | 0.3846
0.23417 | 0.24955 | 0.36442 | 0.38458
0.23416 | 0.24954 | 0.36441 | 0.38456
0.23414 | 0.24953 | 0.36439 | 0.38455
0.23413 | 0.24952 | 0.36437 | 0.38454
0.23412 | 0.2495 | 0.36435 | 0.38451
0.2341 | 0.24949 | 0.36433 | 0.38448
0.23408 | 0.24948 | 0.36431 | 0.38447
0.23407 | 0.24948 | 0.36429 | 0.38445
0.23406 | 0.24947 | 0.36427 | 0.38444
0.23405 | 0.24946 | 0.36426 | 0.38443
0.23404 | 0.24945 | 0.36425 | 0.3844
0.23401 | 0.24943 | 0.36422 | 0.38439
0.234 | 0.24942 | 0.36421 | 0.38437
0.23399 | 0.24941 | 0.36419 | 0.38435
0.23398 | 0.2494 | 0.36417 | 0.38434
0.23396 | 0.2494 | 0.36415 | 0.38432
0.23395 | 0.24939 | 0.36412 | 0.38431
0.23394 | 0.24938 | 0.36411 | 0.38429
0.23393 | 0.24937 | 0.36409 | 0.38427
0.23392 | 0.24936 | 0.36407 | 0.38425
0.2339 | 0.24934 | 0.36406 | 0.38424
0.23389 | 0.24933 | 0.36405 | 0.38422
0.23388 | 0.24932 | 0.36403 | 0.38421
0.23387 | 0.24932 | 0.36401 | 0.38419
0.23386 | 0.24931 | 0.36398 | 0.38417
0.23385 | 0.2493 | 0.36397 | 0.38415
0.23384 | 0.2493 | 0.36395 | 0.38414
0.23382 | 0.24928 | 0.36393 | 0.38412
0.23381 | 0.24928 | 0.36392 | 0.38411
0.23381 | 0.24927 | 0.3639 | 0.38409
0.2338 | 0.24926 | 0.36388 | 0.38407
0.23379 | 0.24926 | 0.36386 | 0.38405
0.23378 | 0.24925 | 0.36384 | 0.38402
0.23378 | 0.24925 | 0.36382 | 0.38401
0.23377 | 0.24924 | 0.3638 | 0.384
0.23376 | 0.24923 | 0.36379 | 0.38399
0.23375 | 0.24922 | 0.36376 | 0.38397
0.23374 | 0.24921 | 0.36374 | 0.38396
0.23372 | 0.2492 | 0.36372 | 0.38394
0.23372 | 0.24919 | 0.36371 | 0.3839
0.23371 | 0.24918 | 0.36369 | 0.38389
0.23369 | 0.24917 | 0.36367 | 0.38388
0.23368 | 0.24916 | 0.36366 | 0.38386
0.23367 | 0.24915 | 0.36365 | 0.38384
0.23365 | 0.24914 | 0.36364 | 0.38382
0.23364 | 0.24913 | 0.36363 | 0.3838
0.23362 | 0.24913 | 0.36362 | 0.38379
0.23361 | 0.24911 | 0.3636 | 0.38377
0.2336 | 0.2491 | 0.36358 | 0.38376
0.23359 | 0.24908 | 0.36355 | 0.38374
0.23358 | 0.24907 | 0.36353 | 0.38372
0.23357 | 0.24906 | 0.36351 | 0.38371
0.23356 | 0.24906 | 0.36349 | 0.38369
0.23355 | 0.24904 | 0.36348 | 0.38368
0.23354 | 0.24904 | 0.36345 | 0.38365
0.23353 | 0.24903 | 0.36344 | 0.38363
0.23351 | 0.24903 | 0.36342 | 0.38361
0.2335 | 0.24902 | 0.3634 | 0.38359
0.23349 | 0.24901 | 0.36338 | 0.38358
0.23348 | 0.249 | 0.36336 | 0.38356
0.23346 | 0.24899 | 0.36334 | 0.38355
0.23345 | 0.24898 | 0.36333 | 0.38354
0.23344 | 0.24897 | 0.3633 | 0.38352
0.23343 | 0.24895 | 0.36328 | 0.38351
0.23342 | 0.24894 | 0.36325 | 0.3835
0.23341 | 0.24893 | 0.36324 | 0.38348
0.2334 | 0.24893 | 0.36321 | 0.38346
0.23339 | 0.24892 | 0.3632 | 0.38344
0.23338 | 0.2489 | 0.36318 | 0.38341
0.23337 | 0.24889 | 0.36316 | 0.38339
0.23336 | 0.24888 | 0.36314 | 0.38338
0.23335 | 0.24887 | 0.36313 | 0.38337
0.23334 | 0.24886 | 0.36311 | 0.38336
0.23332 | 0.24885 | 0.36309 | 0.38335
0.23331 | 0.24884 | 0.36307 | 0.38333
0.2333 | 0.24883 | 0.36305 | 0.38332
0.23329 | 0.24882 | 0.36304 | 0.38331
0.23328 | 0.24881 | 0.36302 | 0.3833
0.23328 | 0.24881 | 0.36301 | 0.38327
0.23327 | 0.2488 | 0.36298 | 0.38325
0.23325 | 0.2488 | 0.36296 | 0.38324
0.23324 | 0.24879 | 0.36294 | 0.38323
0.23323 | 0.24878 | 0.36293 | 0.38321
0.23323 | 0.24877 | 0.36291 | 0.38319
0.23322 | 0.24876 | 0.36288 | 0.38318
0.23321 | 0.24876 | 0.36285 | 0.38317
0.23319 | 0.24875 | 0.36282 | 0.38316
0.23319 | 0.24874 | 0.3628 | 0.38314
0.23317 | 0.24873 | 0.36278 | 0.38313
0.23317 | 0.24873 | 0.36276 | 0.38312
0.23316 | 0.24872 | 0.36274 | 0.3831
0.23315 | 0.24871 | 0.36273 | 0.38309
0.23314 | 0.2487 | 0.36271 | 0.38308
0.23313 | 0.24868 | 0.36269 | 0.38307
0.23312 | 0.24867 | 0.36267 | 0.38304
0.23311 | 0.24867 | 0.36266 | 0.38303
0.2331 | 0.24866 | 0.36265 | 0.38301
0.23308 | 0.24864 | 0.36263 | 0.38299
0.23308 | 0.24864 | 0.36261 | 0.38297
0.23306 | 0.24863 | 0.36257 | 0.38296
0.23305 | 0.24862 | 0.36256 | 0.38295
0.23304 | 0.24861 | 0.36254 | 0.38294
0.23303 | 0.2486 | 0.36252 | 0.38293
0.23303 | 0.24859 | 0.36249 | 0.38291
0.23301 | 0.24858 | 0.36246 | 0.3829
0.233 | 0.24857 | 0.36244 | 0.38289
0.23299 | 0.24856 | 0.36242 | 0.38286
0.23298 | 0.24856 | 0.3624 | 0.38285
0.23297 | 0.24855 | 0.36238 | 0.38283
0.23295 | 0.24853 | 0.36237 | 0.38281
0.23295 | 0.24852 | 0.36236 | 0.3828
0.23293 | 0.24851 | 0.36234 | 0.38279
0.23292 | 0.24851 | 0.36233 | 0.38277
0.23291 | 0.2485 | 0.3623 | 0.38276
0.2329 | 0.24849 | 0.36228 | 0.38273
0.23289 | 0.24848 | 0.36226 | 0.38272
0.23289 | 0.24847 | 0.36224 | 0.3827
0.23288 | 0.24847 | 0.36222 | 0.3827
0.23287 | 0.24846 | 0.36219 | 0.38268
0.23286 | 0.24844 | 0.36217 | 0.38266
0.23285 | 0.24844 | 0.36215 | 0.38265
0.23284 | 0.24843 | 0.36213 | 0.38262
0.23282 | 0.24842 | 0.3621 | 0.3826
0.2328 | 0.24841 | 0.36209 | 0.38259
0.2328 | 0.24841 | 0.36207 | 0.38258
0.23279 | 0.24839 | 0.36205 | 0.38256
0.23278 | 0.24839 | 0.36203 | 0.38254
0.23277 | 0.24838 | 0.36201 | 0.38252
0.23277 | 0.24837 | 0.36199 | 0.38251
0.23276 | 0.24836 | 0.36197 | 0.38249
0.23275 | 0.24835 | 0.36194 | 0.38247
0.23274 | 0.24834 | 0.36192 | 0.38245
0.23273 | 0.24833 | 0.3619 | 0.38244
0.23272 | 0.24833 | 0.36189 | 0.38243
0.23271 | 0.24832 | 0.36187 | 0.38241
0.2327 | 0.24831 | 0.36185 | 0.38239
0.23268 | 0.2483 | 0.36182 | 0.38237
0.23267 | 0.24829 | 0.36181 | 0.38235
0.23266 | 0.24828 | 0.3618 | 0.38234
0.23265 | 0.24827 | 0.36178 | 0.38231
0.23264 | 0.24826 | 0.36177 | 0.38229
0.23264 | 0.24825 | 0.36175 | 0.38227
0.23262 | 0.24823 | 0.36174 | 0.38226
0.23261 | 0.24823 | 0.36171 | 0.38224
0.2326 | 0.24822 | 0.36169 | 0.38222
0.23259 | 0.24821 | 0.36167 | 0.38221
0.23257 | 0.2482 | 0.36166 | 0.38218
0.23256 | 0.24819 | 0.36164 | 0.38216
0.23255 | 0.24818 | 0.36162 | 0.38214
0.23254 | 0.24817 | 0.36159 | 0.38213
0.23253 | 0.24817 | 0.36158 | 0.38212
0.23251 | 0.24816 | 0.36156 | 0.38211
0.2325 | 0.24815 | 0.36154 | 0.38209
0.23249 | 0.24814 | 0.36152 | 0.38208
0.23248 | 0.24813 | 0.3615 | 0.38206
0.23247 | 0.24812 | 0.36148 | 0.38205
0.23246 | 0.24812 | 0.36144 | 0.38203
0.23245 | 0.24811 | 0.36142 | 0.38202
0.23244 | 0.2481 | 0.3614 | 0.38201
0.23243 | 0.2481 | 0.36138 | 0.38199
0.23242 | 0.24809 | 0.36135 | 0.38198
0.23241 | 0.24807 | 0.36133 | 0.38196
0.2324 | 0.24806 | 0.36131 | 0.38195
0.23239 | 0.24805 | 0.36127 | 0.38193
0.23238 | 0.24804 | 0.36125 | 0.38192
0.23237 | 0.24804 | 0.36123 | 0.38189
0.23237 | 0.24803 | 0.36122 | 0.38187
0.23235 | 0.24802 | 0.3612 | 0.38185
0.23235 | 0.24801 | 0.36119 | 0.38184
0.23234 | 0.248 | 0.36117 | 0.38182
0.23233 | 0.24799 | 0.36116 | 0.38179
0.23232 | 0.24799 | 0.36114 | 0.38177
0.23231 | 0.24798 | 0.36113 | 0.38175
0.2323 | 0.24797 | 0.36111 | 0.38173
0.23229 | 0.24796 | 0.36109 | 0.38172
0.23228 | 0.24795 | 0.36108 | 0.38171
0.23227 | 0.24794 | 0.36105 | 0.3817
0.23227 | 0.24794 | 0.36103 | 0.38169
0.23226 | 0.24793 | 0.36101 | 0.38168
0.23225 | 0.24792 | 0.36099 | 0.38166
0.23224 | 0.24792 | 0.36096 | 0.38165
0.23223 | 0.24791 | 0.36095 | 0.38163
0.23221 | 0.2479 | 0.36093 | 0.38161
0.2322 | 0.2479 | 0.3609 | 0.3816
0.23218 | 0.24789 | 0.36089 | 0.38159
0.23217 | 0.24788 | 0.36086 | 0.38157
0.23216 | 0.24787 | 0.36085 | 0.38155
0.23215 | 0.24786 | 0.36082 | 0.38152
0.23214 | 0.24784 | 0.36081 | 0.38151
0.23213 | 0.24783 | 0.3608 | 0.38149
0.23212 | 0.24782 | 0.36079 | 0.38148
0.23211 | 0.24781 | 0.36078 | 0.38146
0.2321 | 0.2478 | 0.36075 | 0.38144
0.23209 | 0.2478 | 0.36073 | 0.38143
0.23208 | 0.24779 | 0.36071 | 0.38141
0.23206 | 0.24778 | 0.3607 | 0.38138
0.23206 | 0.24777 | 0.36067 | 0.38136
0.23205 | 0.24776 | 0.36064 | 0.38134
0.23204 | 0.24775 | 0.36064 | 0.38132
0.23203 | 0.24774 | 0.36061 | 0.38131
0.23202 | 0.24774 | 0.36059 | 0.3813
0.23201 | 0.24773 | 0.36057 | 0.38129
0.232 | 0.24772 | 0.36056 | 0.38127
0.23199 | 0.24771 | 0.36055 | 0.38126
0.23198 | 0.2477 | 0.36051 | 0.38122
0.23197 | 0.24769 | 0.3605 | 0.38121
0.23196 | 0.24768 | 0.36047 | 0.38119
0.23195 | 0.24767 | 0.36044 | 0.38117
0.23195 | 0.24767 | 0.36043 | 0.38114
0.23194 | 0.24766 | 0.36041 | 0.38112
0.23193 | 0.24765 | 0.36039 | 0.38111
0.23192 | 0.24764 | 0.36037 | 0.38108
0.23191 | 0.24763 | 0.36036 | 0.38107
0.2319 | 0.24763 | 0.36034 | 0.38105
0.23189 | 0.24761 | 0.36033 | 0.38104
0.23188 | 0.2476 | 0.36031 | 0.38102
0.23188 | 0.24759 | 0.36029 | 0.38101
0.23186 | 0.24758 | 0.36027 | 0.38098
0.23185 | 0.24757 | 0.36026 | 0.38097
0.23184 | 0.24756 | 0.36023 | 0.38095
0.23182 | 0.24755 | 0.36022 | 0.38094
0.23182 | 0.24754 | 0.3602 | 0.38092
0.23181 | 0.24753 | 0.36019 | 0.38091
0.2318 | 0.24752 | 0.36017 | 0.38089
0.23179 | 0.24751 | 0.36015 | 0.38086
0.23178 | 0.2475 | 0.36013 | 0.38086
0.23177 | 0.24748 | 0.3601 | 0.38084
0.23175 | 0.24748 | 0.36009 | 0.38082
0.23174 | 0.24747 | 0.36007 | 0.3808
0.23173 | 0.24746 | 0.36005 | 0.38078
0.23172 | 0.24745 | 0.36004 | 0.38077
0.23171 | 0.24744 | 0.36002 | 0.38076
0.23169 | 0.24742 | 0.35999 | 0.38074
0.23168 | 0.24742 | 0.35997 | 0.38073
0.23167 | 0.24741 | 0.35994 | 0.38071
0.23166 | 0.24739 | 0.35994 | 0.38069
0.23165 | 0.24739 | 0.35992 | 0.38068
0.23164 | 0.24737 | 0.3599 | 0.38065
0.23164 | 0.24736 | 0.35988 | 0.38063
0.23163 | 0.24735 | 0.35986 | 0.38062
0.23162 | 0.24735 | 0.35985 | 0.3806
0.23161 | 0.24734 | 0.35983 | 0.38059
0.2316 | 0.24733 | 0.35981 | 0.38056
0.23159 | 0.24732 | 0.35979 | 0.38055
0.23158 | 0.24732 | 0.35977 | 0.38054
0.23157 | 0.24731 | 0.35975 | 0.38052
0.23156 | 0.24729 | 0.35972 | 0.3805
0.23156 | 0.24728 | 0.35969 | 0.38048
0.23155 | 0.24728 | 0.35967 | 0.38045
0.23154 | 0.24726 | 0.35965 | 0.38044
0.23153 | 0.24725 | 0.35962 | 0.38042
0.23152 | 0.24724 | 0.35961 | 0.38041
0.23151 | 0.24724 | 0.35959 | 0.38039
0.2315 | 0.24723 | 0.35956 | 0.38038
0.2315 | 0.24722 | 0.35955 | 0.38036
0.23148 | 0.24721 | 0.35953 | 0.38034
0.23147 | 0.2472 | 0.35951 | 0.38033
0.23146 | 0.24719 | 0.35948 | 0.38031
0.23145 | 0.24718 | 0.35947 | 0.38031
0.23144 | 0.24717 | 0.35945 | 0.38029
0.23143 | 0.24716 | 0.35943 | 0.38027
0.23141 | 0.24715 | 0.35942 | 0.38025
0.23141 | 0.24714 | 0.3594 | 0.38023
0.23139 | 0.24713 | 0.35937 | 0.3802
0.23139 | 0.24712 | 0.35935 | 0.38018
0.23138 | 0.24711 | 0.35934 | 0.38017
0.23136 | 0.2471 | 0.35932 | 0.38016
0.23135 | 0.24709 | 0.3593 | 0.38014
0.23134 | 0.24709 | 0.35929 | 0.38013
0.23134 | 0.24707 | 0.35926 | 0.38012
0.23133 | 0.24706 | 0.35924 | 0.38011
0.23132 | 0.24705 | 0.35923 | 0.38009
0.23131 | 0.24704 | 0.35922 | 0.38007
0.2313 | 0.24703 | 0.35921 | 0.38006
0.23128 | 0.24702 | 0.35918 | 0.38004
0.23126 | 0.24701 | 0.35917 | 0.38003
0.23125 | 0.24701 | 0.35916 | 0.38
0.23124 | 0.247 | 0.35913 | 0.37999
0.23123 | 0.24698 | 0.3591 | 0.37997
0.23121 | 0.24697 | 0.35909 | 0.37996
0.2312 | 0.24696 | 0.35907 | 0.37995
0.23118 | 0.24695 | 0.35905 | 0.37994
0.23117 | 0.24694 | 0.35904 | 0.37992
0.23117 | 0.24693 | 0.35901 | 0.37991
0.23115 | 0.24692 | 0.35899 | 0.3799
0.23114 | 0.24691 | 0.35897 | 0.37988
0.23112 | 0.24691 | 0.35894 | 0.37987
0.23111 | 0.2469 | 0.35892 | 0.37985
0.2311 | 0.24689 | 0.35888 | 0.37983
0.23109 | 0.24688 | 0.35886 | 0.37982
0.23108 | 0.24687 | 0.35885 | 0.37981
0.23107 | 0.24686 | 0.35883 | 0.3798
0.23106 | 0.24685 | 0.35881 | 0.37978
0.23105 | 0.24684 | 0.35879 | 0.37976
0.23104 | 0.24683 | 0.35878 | 0.37975
0.23103 | 0.24683 | 0.35875 | 0.37973
0.23102 | 0.24682 | 0.35872 | 0.37971
0.23101 | 0.24681 | 0.3587 | 0.3797
0.231 | 0.2468 | 0.35868 | 0.37968
0.23099 | 0.24679 | 0.35866 | 0.37967
0.23098 | 0.24678 | 0.35863 | 0.37966
0.23097 | 0.24677 | 0.35861 | 0.37964
0.23096 | 0.24676 | 0.3586 | 0.37963
0.23095 | 0.24675 | 0.35859 | 0.37961
0.23094 | 0.24674 | 0.35857 | 0.3796
0.23093 | 0.24673 | 0.35855 | 0.37959
0.23092 | 0.24673 | 0.35853 | 0.37957
0.23091 | 0.24671 | 0.35849 | 0.37955
0.2309 | 0.24671 | 0.35846 | 0.37953
0.23089 | 0.2467 | 0.35845 | 0.37951
0.23088 | 0.24669 | 0.35843 | 0.3795
0.23086 | 0.24668 | 0.35841 | 0.37948
0.23085 | 0.24667 | 0.35838 | 0.37946
0.23083 | 0.24666 | 0.35838 | 0.37945
0.23082 | 0.24665 | 0.35836 | 0.37944
0.23081 | 0.24665 | 0.35834 | 0.37941
0.2308 | 0.24663 | 0.35831 | 0.3794
0.23078 | 0.24661 | 0.3583 | 0.37938
0.23077 | 0.2466 | 0.35828 | 0.37936
0.23077 | 0.2466 | 0.35827 | 0.37934
0.23076 | 0.24659 | 0.35823 | 0.37933
0.23074 | 0.24658 | 0.3582 | 0.3793
0.23073 | 0.24658 | 0.35819 | 0.37928
0.23072 | 0.24656 | 0.35818 | 0.37925
0.23071 | 0.24655 | 0.35817 | 0.37924
0.2307 | 0.24655 | 0.35815 | 0.37921
0.23069 | 0.24654 | 0.35812 | 0.3792
0.23067 | 0.24653 | 0.35808 | 0.37918
0.23066 | 0.24652 | 0.35806 | 0.37917
0.23065 | 0.24651 | 0.35804 | 0.37915
0.23063 | 0.2465 | 0.35803 | 0.37912
0.23062 | 0.24649 | 0.358 | 0.3791
0.23061 | 0.24648 | 0.35799 | 0.37909
0.2306 | 0.24647 | 0.35796 | 0.37905
0.2306 | 0.24647 | 0.35795 | 0.37903
0.23059 | 0.24646 | 0.35793 | 0.37901
0.23057 | 0.24645 | 0.35792 | 0.379
0.23056 | 0.24643 | 0.3579 | 0.37899
0.23055 | 0.24642 | 0.35788 | 0.37898
0.23054 | 0.24641 | 0.35787 | 0.37896
0.23054 | 0.24641 | 0.35785 | 0.37895
0.23052 | 0.24639 | 0.35784 | 0.37894
0.23051 | 0.24638 | 0.35781 | 0.37893
0.2305 | 0.24638 | 0.35779 | 0.37891
0.23049 | 0.24636 | 0.35777 | 0.37889
0.23048 | 0.24636 | 0.35775 | 0.37887
0.23047 | 0.24635 | 0.35774 | 0.37885
0.23047 | 0.24633 | 0.35773 | 0.37884
0.23043 | 0.24632 | 0.35771 | 0.37883
0.23042 | 0.24631 | 0.35769 | 0.37881
0.23041 | 0.2463 | 0.35768 | 0.37879
0.23039 | 0.24629 | 0.35765 | 0.37877
0.23038 | 0.24628 | 0.35764 | 0.37876
0.23036 | 0.24628 | 0.35762 | 0.37874
0.23035 | 0.24626 | 0.35759 | 0.37873
0.23034 | 0.24625 | 0.35757 | 0.37871
0.23033 | 0.24624 | 0.35756 | 0.37869
0.23032 | 0.24624 | 0.35754 | 0.37867
0.23031 | 0.24623 | 0.35752 | 0.37865
0.2303 | 0.24621 | 0.35751 | 0.37864
0.23029 | 0.24621 | 0.35749 | 0.37863
0.23027 | 0.24619 | 0.35748 | 0.3786
0.23026 | 0.24618 | 0.35746 | 0.37858
0.23025 | 0.24618 | 0.35744 | 0.37856
0.23024 | 0.24617 | 0.35743 | 0.37854
0.23023 | 0.24616 | 0.35741 | 0.37852
0.23022 | 0.24615 | 0.35739 | 0.37851
0.23021 | 0.24614 | 0.35737 | 0.3785
0.23019 | 0.24613 | 0.35734 | 0.37849
0.23019 | 0.24612 | 0.35732 | 0.37847
0.23018 | 0.24611 | 0.35729 | 0.37845
0.23017 | 0.24611 | 0.35727 | 0.37844
0.23016 | 0.2461 | 0.35726 | 0.37842
0.23015 | 0.24609 | 0.35724 | 0.37841
0.23013 | 0.24608 | 0.35721 | 0.3784
0.23011 | 0.24606 | 0.3572 | 0.37838
0.2301 | 0.24605 | 0.35718 | 0.37837
0.2301 | 0.24604 | 0.35717 | 0.37837
0.23008 | 0.24603 | 0.35715 | 0.37835
0.23007 | 0.24603 | 0.35714 | 0.37833
0.23006 | 0.24602 | 0.35712 | 0.37832
0.23006 | 0.24601 | 0.3571 | 0.3783
0.23005 | 0.246 | 0.35709 | 0.37829
0.23003 | 0.24599 | 0.35707 | 0.37827
0.23002 | 0.24598 | 0.35705 | 0.37825
0.23001 | 0.24597 | 0.35702 | 0.37824
0.23 | 0.24596 | 0.35699 | 0.37823
0.22999 | 0.24595 | 0.35697 | 0.37821
0.22998 | 0.24595 | 0.35696 | 0.3782
0.22997 | 0.24594 | 0.35694 | 0.37818
0.22996 | 0.24593 | 0.35692 | 0.37817
0.22996 | 0.24592 | 0.35691 | 0.37816
0.22995 | 0.24591 | 0.35689 | 0.37814
0.22993 | 0.2459 | 0.35687 | 0.37812
0.22993 | 0.24589 | 0.35685 | 0.37811
0.22992 | 0.24588 | 0.35683 | 0.37809
0.22991 | 0.24587 | 0.35681 | 0.37808
0.2299 | 0.24587 | 0.35679 | 0.37805
0.22988 | 0.24586 | 0.35677 | 0.37803
0.22987 | 0.24585 | 0.35676 | 0.378
0.22985 | 0.24584 | 0.35673 | 0.37799
0.22984 | 0.24583 | 0.3567 | 0.37797
0.22983 | 0.24583 | 0.35668 | 0.37795
0.22982 | 0.24581 | 0.35667 | 0.37793
0.22981 | 0.2458 | 0.35666 | 0.37791
0.2298 | 0.24579 | 0.35664 | 0.3779
0.22979 | 0.24578 | 0.35662 | 0.37787
0.22978 | 0.24578 | 0.3566 | 0.37785
0.22977 | 0.24577 | 0.35659 | 0.37783
0.22975 | 0.24576 | 0.35656 | 0.37781
0.22974 | 0.24575 | 0.35654 | 0.37781
0.22973 | 0.24574 | 0.35653 | 0.37778
0.22972 | 0.24573 | 0.35651 | 0.37776
0.22971 | 0.24572 | 0.35649 | 0.37774
0.22969 | 0.24571 | 0.35647 | 0.37772
0.22969 | 0.24571 | 0.35645 | 0.37769
0.22968 | 0.2457 | 0.35644 | 0.37767
0.22966 | 0.24568 | 0.35642 | 0.37765
0.22965 | 0.24568 | 0.3564 | 0.37763
0.22963 | 0.24567 | 0.35638 | 0.37762
0.22963 | 0.24566 | 0.35635 | 0.37761
0.22961 | 0.24565 | 0.35635 | 0.3776
0.2296 | 0.24564 | 0.35633 | 0.37758
0.22958 | 0.24564 | 0.3563 | 0.37755
0.22958 | 0.24563 | 0.35628 | 0.37753
0.22957 | 0.24562 | 0.35626 | 0.37751
0.22956 | 0.2456 | 0.35624 | 0.3775
0.22955 | 0.2456 | 0.35622 | 0.3775
0.22953 | 0.24559 | 0.3562 | 0.37749
0.22952 | 0.24558 | 0.35618 | 0.37747
0.22951 | 0.24557 | 0.35616 | 0.37745
0.2295 | 0.24556 | 0.35615 | 0.37744
0.22948 | 0.24555 | 0.35614 | 0.37743
0.22947 | 0.24554 | 0.35612 | 0.37741
0.22946 | 0.24553 | 0.35611 | 0.37739
0.22944 | 0.24551 | 0.35609 | 0.37738
0.22943 | 0.2455 | 0.35608 | 0.37737
0.22942 | 0.24549 | 0.35606 | 0.37735
0.2294 | 0.24548 | 0.35603 | 0.37734
0.22938 | 0.24548 | 0.35601 | 0.37732
0.22936 | 0.24547 | 0.356 | 0.37729
0.22935 | 0.24545 | 0.35599 | 0.37728
0.22934 | 0.24544 | 0.35597 | 0.37726
0.22933 | 0.24543 | 0.35596 | 0.37724
0.22932 | 0.24541 | 0.35594 | 0.37723
0.22931 | 0.24541 | 0.35592 | 0.37721
0.22929 | 0.2454 | 0.35591 | 0.37719
0.22928 | 0.24539 | 0.35589 | 0.37717
0.22926 | 0.24538 | 0.35588 | 0.37716
0.22926 | 0.24537 | 0.35586 | 0.37715
0.22925 | 0.24536 | 0.35585 | 0.37712
0.22924 | 0.24534 | 0.35581 | 0.37711
0.22923 | 0.24533 | 0.35579 | 0.37709
0.22922 | 0.24532 | 0.35577 | 0.37708
0.22921 | 0.24531 | 0.35576 | 0.37707
0.2292 | 0.2453 | 0.35575 | 0.37706
0.22919 | 0.2453 | 0.35574 | 0.37704
0.22918 | 0.24528 | 0.35572 | 0.37702
0.22917 | 0.24526 | 0.35571 | 0.37701
0.22916 | 0.24526 | 0.3557 | 0.37698
0.22915 | 0.24525 | 0.35569 | 0.37696
0.22914 | 0.24524 | 0.35566 | 0.37695
0.22912 | 0.24522 | 0.35564 | 0.37693
0.22911 | 0.24521 | 0.35563 | 0.37693
0.2291 | 0.2452 | 0.35561 | 0.37691
0.22909 | 0.24519 | 0.3556 | 0.3769
0.22908 | 0.24518 | 0.35559 | 0.37688
0.22907 | 0.24517 | 0.35557 | 0.37685
0.22906 | 0.24516 | 0.35555 | 0.37683
0.22905 | 0.24515 | 0.35552 | 0.37681
0.22904 | 0.24515 | 0.3555 | 0.37679
0.22903 | 0.24514 | 0.35549 | 0.37677
0.22902 | 0.24513 | 0.35546 | 0.37675
0.22901 | 0.24512 | 0.35543 | 0.37673
0.229 | 0.24511 | 0.3554 | 0.37671
0.22899 | 0.2451 | 0.35539 | 0.37671
0.22898 | 0.24509 | 0.35538 | 0.3767
0.22897 | 0.24508 | 0.35537 | 0.37668
0.22895 | 0.24507 | 0.35536 | 0.37666
0.22894 | 0.24506 | 0.35534 | 0.37664
0.22893 | 0.24505 | 0.35532 | 0.37663
0.22893 | 0.24504 | 0.35532 | 0.37662
0.22892 | 0.24503 | 0.35531 | 0.3766
0.2289 | 0.24503 | 0.35529 | 0.37657
0.22889 | 0.24502 | 0.35527 | 0.37656
0.22888 | 0.24501 | 0.35525 | 0.37654
0.22887 | 0.245 | 0.35524 | 0.37653
0.22885 | 0.24499 | 0.35522 | 0.37652
0.22884 | 0.24498 | 0.35521 | 0.3765
0.22883 | 0.24498 | 0.3552 | 0.37649
0.22882 | 0.24496 | 0.35518 | 0.37648
0.22881 | 0.24496 | 0.35515 | 0.37645
0.2288 | 0.24494 | 0.35513 | 0.37644
0.22878 | 0.24492 | 0.35512 | 0.37641
0.22877 | 0.24491 | 0.35509 | 0.37641
0.22876 | 0.24491 | 0.35507 | 0.37639
0.22874 | 0.24489 | 0.35505 | 0.37638
0.22873 | 0.24488 | 0.35503 | 0.37637
0.22872 | 0.24487 | 0.35501 | 0.37636
0.22871 | 0.24486 | 0.35498 | 0.37635
0.2287 | 0.24485 | 0.35497 | 0.37633
0.22869 | 0.24484 | 0.35495 | 0.37631
0.22867 | 0.24483 | 0.35494 | 0.37631
0.22866 | 0.24483 | 0.35492 | 0.37629
0.22865 | 0.24482 | 0.35491 | 0.37628
0.22864 | 0.24481 | 0.3549 | 0.37626
0.22863 | 0.2448 | 0.35488 | 0.37624
0.22862 | 0.24479 | 0.35486 | 0.37622
0.22862 | 0.24478 | 0.35485 | 0.37621
0.22861 | 0.24477 | 0.35482 | 0.37619
0.2286 | 0.24476 | 0.35479 | 0.37618
0.22859 | 0.24475 | 0.35477 | 0.37616
0.22858 | 0.24474 | 0.35474 | 0.37613
0.22857 | 0.24473 | 0.35473 | 0.37612
0.22856 | 0.24472 | 0.35471 | 0.37611
0.22854 | 0.2447 | 0.3547 | 0.37609
0.22854 | 0.2447 | 0.35468 | 0.37607
0.22853 | 0.24469 | 0.35466 | 0.37606
0.22851 | 0.24468 | 0.35465 | 0.37604
0.22851 | 0.24467 | 0.35462 | 0.37603
0.2285 | 0.24466 | 0.35461 | 0.37602
0.22848 | 0.24465 | 0.35458 | 0.37601
0.22847 | 0.24464 | 0.35456 | 0.37599
0.22845 | 0.24463 | 0.35454 | 0.37597
0.22844 | 0.24462 | 0.35452 | 0.37595
0.22844 | 0.24461 | 0.3545 | 0.37594
0.22843 | 0.2446 | 0.35448 | 0.37592
0.22841 | 0.24459 | 0.35447 | 0.37591
0.2284 | 0.24457 | 0.35445 | 0.3759
0.22839 | 0.24456 | 0.35444 | 0.37586
0.22837 | 0.24455 | 0.35442 | 0.37585
0.22836 | 0.24454 | 0.35441 | 0.37583
0.22835 | 0.24453 | 0.35439 | 0.37581
0.22833 | 0.24453 | 0.35437 | 0.37579
0.22833 | 0.24452 | 0.35436 | 0.37577
0.22831 | 0.24451 | 0.35434 | 0.37575
0.2283 | 0.24451 | 0.3543 | 0.37574
0.22829 | 0.2445 | 0.35428 | 0.37573
0.22828 | 0.24449 | 0.35426 | 0.37572
0.22827 | 0.24447 | 0.35425 | 0.3757
0.22826 | 0.24446 | 0.35422 | 0.37569
0.22825 | 0.24445 | 0.35421 | 0.37568
0.22824 | 0.24444 | 0.35418 | 0.37567
0.22823 | 0.24443 | 0.35415 | 0.37567
0.22822 | 0.24442 | 0.35412 | 0.37564
0.22821 | 0.24441 | 0.3541 | 0.37563
0.2282 | 0.2444 | 0.35407 | 0.37562
0.22818 | 0.24439 | 0.35406 | 0.3756
0.22817 | 0.24438 | 0.35404 | 0.37559
0.22815 | 0.24437 | 0.35403 | 0.37557
0.22814 | 0.24437 | 0.35401 | 0.37556
0.22813 | 0.24435 | 0.35398 | 0.37556
0.22812 | 0.24435 | 0.35396 | 0.37554
0.22809 | 0.24434 | 0.35394 | 0.37553
0.22808 | 0.24433 | 0.35393 | 0.37552
0.22807 | 0.24431 | 0.35391 | 0.37551
0.22806 | 0.24429 | 0.3539 | 0.3755
0.22805 | 0.24429 | 0.35388 | 0.37548
0.22805 | 0.24428 | 0.35386 | 0.37546
0.22803 | 0.24427 | 0.35385 | 0.37544
0.22803 | 0.24426 | 0.35383 | 0.37542
0.22802 | 0.24425 | 0.35381 | 0.37541
0.22801 | 0.24423 | 0.35379 | 0.3754
0.22799 | 0.24422 | 0.35378 | 0.37538
0.22798 | 0.24421 | 0.35376 | 0.37537
0.22797 | 0.2442 | 0.35374 | 0.37536
0.22795 | 0.2442 | 0.35372 | 0.37534
0.22794 | 0.24419 | 0.35369 | 0.37532
0.22794 | 0.24418 | 0.35367 | 0.37531
0.22793 | 0.24417 | 0.35366 | 0.3753
0.22792 | 0.24416 | 0.35364 | 0.37528
0.22791 | 0.24415 | 0.35363 | 0.37526
0.22791 | 0.24414 | 0.35362 | 0.37526
0.2279 | 0.24413 | 0.35361 | 0.37523
0.22789 | 0.24412 | 0.3536 | 0.37522
0.22788 | 0.2441 | 0.35358 | 0.37521
0.22787 | 0.24409 | 0.35357 | 0.37519
0.22786 | 0.24409 | 0.35355 | 0.37517
0.22785 | 0.24408 | 0.35353 | 0.37516
0.22784 | 0.24407 | 0.3535 | 0.37515
0.22783 | 0.24406 | 0.35348 | 0.37513
0.22782 | 0.24405 | 0.35345 | 0.3751
0.22781 | 0.24404 | 0.35342 | 0.37509
0.2278 | 0.24404 | 0.35341 | 0.37508
0.22779 | 0.24402 | 0.35339 | 0.37507
0.22777 | 0.24401 | 0.35337 | 0.37505
0.22776 | 0.244 | 0.35335 | 0.37503
0.22776 | 0.24399 | 0.35333 | 0.37502
0.22774 | 0.24399 | 0.35331 | 0.375
0.22774 | 0.24398 | 0.35329 | 0.37498
0.22773 | 0.24397 | 0.35327 | 0.37498
0.22772 | 0.24396 | 0.35326 | 0.37495
0.22771 | 0.24394 | 0.35324 | 0.37494
0.2277 | 0.24393 | 0.35321 | 0.37493
0.22769 | 0.24392 | 0.3532 | 0.37491
0.22767 | 0.24391 | 0.35319 | 0.3749
0.22766 | 0.2439 | 0.35316 | 0.37488
0.22766 | 0.24389 | 0.35314 | 0.37487
0.22764 | 0.24388 | 0.35313 | 0.37485
0.22763 | 0.24387 | 0.35311 | 0.37484
0.22761 | 0.24386 | 0.3531 | 0.37481
0.2276 | 0.24385 | 0.35309 | 0.3748
0.22759 | 0.24384 | 0.35308 | 0.37479
0.22758 | 0.24383 | 0.35306 | 0.37478
0.22757 | 0.24382 | 0.35304 | 0.37475
0.22756 | 0.24381 | 0.35301 | 0.37473
0.22755 | 0.24379 | 0.35298 | 0.37471
0.22754 | 0.24378 | 0.35297 | 0.37469
0.22753 | 0.24376 | 0.35296 | 0.37467
0.22752 | 0.24374 | 0.35294 | 0.37465
0.2275 | 0.24374 | 0.35291 | 0.37464
0.22749 | 0.24373 | 0.3529 | 0.37463
0.22749 | 0.24372 | 0.35289 | 0.37461
0.22748 | 0.24371 | 0.35286 | 0.37459
0.22747 | 0.2437 | 0.35284 | 0.37457
0.22746 | 0.24369 | 0.35282 | 0.37456
0.22745 | 0.24368 | 0.3528 | 0.37454
0.22743 | 0.24367 | 0.35278 | 0.37452
0.22742 | 0.24366 | 0.35276 | 0.37451
0.22741 | 0.24365 | 0.35275 | 0.3745
0.2274 | 0.24364 | 0.35271 | 0.37449
0.22739 | 0.24363 | 0.35269 | 0.37447
0.22738 | 0.24362 | 0.35267 | 0.37446
0.22737 | 0.24361 | 0.35264 | 0.37444
0.22736 | 0.24361 | 0.35263 | 0.37443
0.22735 | 0.2436 | 0.35262 | 0.37442
0.22734 | 0.24358 | 0.3526 | 0.37441
0.22733 | 0.24357 | 0.35258 | 0.37439
0.22732 | 0.24356 | 0.35257 | 0.37436
0.2273 | 0.24355 | 0.35255 | 0.37434
0.22729 | 0.24355 | 0.35254 | 0.37433
0.22728 | 0.24354 | 0.35252 | 0.37432
0.22726 | 0.24353 | 0.3525 | 0.37431
0.22725 | 0.24352 | 0.35249 | 0.37429
0.22725 | 0.24351 | 0.35247 | 0.37427
0.22723 | 0.2435 | 0.35245 | 0.37424
0.22721 | 0.24349 | 0.35243 | 0.37423
0.2272 | 0.24349 | 0.35241 | 0.37421
0.22718 | 0.24348 | 0.35239 | 0.3742
0.22717 | 0.24347 | 0.35237 | 0.37417
0.22716 | 0.24346 | 0.35236 | 0.37416
0.22715 | 0.24345 | 0.35234 | 0.37414
0.22714 | 0.24344 | 0.35233 | 0.37413
0.22712 | 0.24343 | 0.3523 | 0.37412
0.22711 | 0.24342 | 0.35229 | 0.3741
0.22709 | 0.24341 | 0.35227 | 0.37408
0.22708 | 0.2434 | 0.35226 | 0.37406
0.22707 | 0.24339 | 0.35224 | 0.37404
0.22706 | 0.24337 | 0.35222 | 0.37403
0.22705 | 0.24337 | 0.3522 | 0.37401
0.22704 | 0.24336 | 0.35218 | 0.374
0.22703 | 0.24335 | 0.35217 | 0.37399
0.22702 | 0.24335 | 0.35214 | 0.37396
0.227 | 0.24334 | 0.35212 | 0.37395
0.227 | 0.24334 | 0.35211 | 0.37393
0.22698 | 0.24333 | 0.3521 | 0.37392
0.22697 | 0.24332 | 0.35208 | 0.37391
0.22695 | 0.2433 | 0.35207 | 0.3739
0.22694 | 0.24329 | 0.35205 | 0.37389
0.22693 | 0.24329 | 0.35203 | 0.37387
0.22692 | 0.24328 | 0.35202 | 0.37385
0.2269 | 0.24327 | 0.352 | 0.37384
0.22689 | 0.24326 | 0.35197 | 0.37382
0.22688 | 0.24326 | 0.35194 | 0.37379
0.22687 | 0.24325 | 0.35193 | 0.37377
0.22687 | 0.24323 | 0.35192 | 0.37374
0.22686 | 0.24323 | 0.3519 | 0.37372
0.22685 | 0.24321 | 0.35189 | 0.3737
0.22684 | 0.24321 | 0.35187 | 0.37368
0.22683 | 0.2432 | 0.35184 | 0.37366
0.22681 | 0.24319 | 0.35183 | 0.37364
0.2268 | 0.24319 | 0.35182 | 0.37363
0.2268 | 0.24318 | 0.3518 | 0.37361
0.22678 | 0.24317 | 0.35178 | 0.37359
0.22678 | 0.24316 | 0.35176 | 0.37358
0.22677 | 0.24315 | 0.35174 | 0.37357
0.22676 | 0.24314 | 0.35173 | 0.37354
0.22675 | 0.24313 | 0.3517 | 0.37353
0.22674 | 0.24312 | 0.35169 | 0.37352
0.22673 | 0.24311 | 0.35166 | 0.37351
0.22672 | 0.2431 | 0.35165 | 0.37349
0.22671 | 0.24309 | 0.35163 | 0.37348
0.2267 | 0.24308 | 0.35162 | 0.37347
0.22669 | 0.24307 | 0.35159 | 0.37344
0.22668 | 0.24306 | 0.35157 | 0.37342
0.22667 | 0.24305 | 0.35155 | 0.3734
0.22667 | 0.24304 | 0.35151 | 0.37338
0.22666 | 0.24303 | 0.3515 | 0.37337
0.22665 | 0.24302 | 0.35147 | 0.37336
0.22664 | 0.24301 | 0.35145 | 0.37335
0.22663 | 0.24301 | 0.35144 | 0.37334
0.22662 | 0.243 | 0.35142 | 0.37333
0.22661 | 0.24299 | 0.3514 | 0.37331
0.2266 | 0.24298 | 0.35138 | 0.3733
0.2266 | 0.24297 | 0.35136 | 0.37329
0.22659 | 0.24296 | 0.35135 | 0.37327
0.22658 | 0.24295 | 0.35133 | 0.37325
0.22656 | 0.24294 | 0.35132 | 0.37323
0.22655 | 0.24293 | 0.3513 | 0.37321
0.22654 | 0.24292 | 0.35127 | 0.37319
0.22653 | 0.24291 | 0.35123 | 0.37317
0.22652 | 0.24291 | 0.35122 | 0.37315
0.22651 | 0.24289 | 0.3512 | 0.37313
0.2265 | 0.24289 | 0.35119 | 0.37311
0.22649 | 0.24288 | 0.35116 | 0.3731
0.22648 | 0.24287 | 0.35114 | 0.37309
0.22647 | 0.24286 | 0.35113 | 0.37307
0.22646 | 0.24285 | 0.35111 | 0.37305
0.22645 | 0.24284 | 0.35109 | 0.37303
0.22644 | 0.24283 | 0.35107 | 0.37301
0.22642 | 0.24282 | 0.35105 | 0.37299
0.22641 | 0.24282 | 0.35104 | 0.37297
0.2264 | 0.24281 | 0.35103 | 0.37296
0.22639 | 0.2428 | 0.35101 | 0.37295
0.22638 | 0.24279 | 0.35099 | 0.37293
0.22636 | 0.24278 | 0.35097 | 0.37292
0.22635 | 0.24278 | 0.35096 | 0.37291
0.22634 | 0.24276 | 0.35092 | 0.3729
0.22633 | 0.24275 | 0.35089 | 0.37288
0.22632 | 0.24274 | 0.35087 | 0.37286
0.22631 | 0.24272 | 0.35086 | 0.37284
0.22629 | 0.24271 | 0.35084 | 0.37283
0.22628 | 0.24271 | 0.35083 | 0.37281
0.22627 | 0.24269 | 0.3508 | 0.37279
0.22626 | 0.24268 | 0.35078 | 0.37277
0.22624 | 0.24267 | 0.35077 | 0.37275
0.22623 | 0.24266 | 0.35075 | 0.37274
0.22622 | 0.24265 | 0.35073 | 0.37273
0.22622 | 0.24264 | 0.35072 | 0.37271
0.22621 | 0.24262 | 0.35071 | 0.37269
0.2262 | 0.24261 | 0.35069 | 0.37268
0.22619 | 0.2426 | 0.35067 | 0.37266
0.22618 | 0.24259 | 0.35063 | 0.37264
0.22616 | 0.24258 | 0.35062 | 0.37262
0.22616 | 0.24257 | 0.3506 | 0.3726
0.22614 | 0.24257 | 0.35057 | 0.37259
0.22613 | 0.24256 | 0.35055 | 0.37257
0.22612 | 0.24255 | 0.35055 | 0.37255
0.22611 | 0.24255 | 0.35052 | 0.37253
0.2261 | 0.24253 | 0.35049 | 0.37251
0.22609 | 0.24252 | 0.35047 | 0.37249
0.22608 | 0.24251 | 0.35045 | 0.37248
0.22607 | 0.2425 | 0.35042 | 0.37247
0.22606 | 0.24249 | 0.35041 | 0.37245
0.22606 | 0.24248 | 0.35039 | 0.37242
0.22604 | 0.24248 | 0.35037 | 0.37241
0.22603 | 0.24246 | 0.35034 | 0.37239
0.22602 | 0.24245 | 0.35032 | 0.37238
0.22601 | 0.24245 | 0.3503 | 0.37235
0.22599 | 0.24244 | 0.35028 | 0.37232
0.22598 | 0.24242 | 0.35027 | 0.37231
0.22597 | 0.24241 | 0.35026 | 0.3723
0.22596 | 0.2424 | 0.35024 | 0.37226
0.22596 | 0.24239 | 0.35022 | 0.37224
0.22595 | 0.24238 | 0.35019 | 0.37222
0.22594 | 0.24237 | 0.35017 | 0.37221
0.22593 | 0.24236 | 0.35015 | 0.3722
0.22592 | 0.24234 | 0.35013 | 0.37218
0.22591 | 0.24233 | 0.35011 | 0.37217
0.2259 | 0.24231 | 0.35008 | 0.37215
0.22588 | 0.24231 | 0.35007 | 0.37213
0.22587 | 0.2423 | 0.35004 | 0.37212
0.22586 | 0.24229 | 0.35003 | 0.3721
0.22584 | 0.24228 | 0.35002 | 0.37208
0.22583 | 0.24227 | 0.35 | 0.37205
0.22582 | 0.24225 | 0.34999 | 0.37204
0.22581 | 0.24224 | 0.34997 | 0.37201
0.22579 | 0.24223 | 0.34995 | 0.372
0.22578 | 0.24222 | 0.34994 | 0.37198
0.22577 | 0.24221 | 0.3499 | 0.37196
0.22576 | 0.2422 | 0.34989 | 0.37193
0.22575 | 0.2422 | 0.34987 | 0.3719
0.22573 | 0.24219 | 0.34986 | 0.37189
0.22572 | 0.24218 | 0.34984 | 0.37187
0.22571 | 0.24217 | 0.34982 | 0.37185
0.2257 | 0.24216 | 0.34981 | 0.37184
0.22569 | 0.24215 | 0.34978 | 0.37182
0.22568 | 0.24214 | 0.34976 | 0.37181
0.22567 | 0.24213 | 0.34973 | 0.3718
0.22566 | 0.24212 | 0.34971 | 0.37179
0.22565 | 0.24211 | 0.34969 | 0.37177
0.22565 | 0.24209 | 0.34968 | 0.37175
0.22564 | 0.24209 | 0.34966 | 0.37174
0.22563 | 0.24208 | 0.34964 | 0.37171
0.22561 | 0.24207 | 0.34962 | 0.3717
0.2256 | 0.24205 | 0.34961 | 0.37169
0.22559 | 0.24204 | 0.34959 | 0.37167
0.22558 | 0.24203 | 0.34958 | 0.37166
0.22557 | 0.24202 | 0.34956 | 0.37163
0.22556 | 0.24202 | 0.34954 | 0.37161
0.22555 | 0.24201 | 0.34952 | 0.3716
0.22553 | 0.242 | 0.34949 | 0.37158
0.22552 | 0.24199 | 0.34947 | 0.37157
0.22551 | 0.24198 | 0.34945 | 0.37155
0.22551 | 0.24197 | 0.34943 | 0.37153
0.2255 | 0.24196 | 0.34942 | 0.37152
0.22549 | 0.24196 | 0.3494 | 0.3715
0.22548 | 0.24195 | 0.34938 | 0.37148
0.22547 | 0.24194 | 0.34937 | 0.37147
0.22546 | 0.24192 | 0.34936 | 0.37146
0.22544 | 0.24192 | 0.34934 | 0.37144
0.22542 | 0.24191 | 0.34933 | 0.37143
0.22541 | 0.24189 | 0.34931 | 0.37142
0.2254 | 0.24188 | 0.3493 | 0.37139
0.22539 | 0.24187 | 0.34929 | 0.37138
0.22538 | 0.24186 | 0.34926 | 0.37136
0.22537 | 0.24185 | 0.34924 | 0.37135
0.22537 | 0.24184 | 0.34921 | 0.37134
0.22535 | 0.24183 | 0.3492 | 0.37132
0.22535 | 0.24182 | 0.34918 | 0.3713
0.22534 | 0.24182 | 0.34915 | 0.37129
0.22533 | 0.2418 | 0.34912 | 0.37128
0.22532 | 0.24179 | 0.34911 | 0.37125
0.2253 | 0.24179 | 0.34909 | 0.37123
0.22529 | 0.24178 | 0.34907 | 0.37121
0.22528 | 0.24177 | 0.34905 | 0.3712
0.22527 | 0.24176 | 0.34902 | 0.37118
0.22526 | 0.24175 | 0.349 | 0.37116
0.22525 | 0.24173 | 0.34897 | 0.37115
0.22524 | 0.24172 | 0.34895 | 0.37113
0.22523 | 0.24171 | 0.34894 | 0.37111
0.22522 | 0.2417 | 0.34892 | 0.3711
0.22521 | 0.24168 | 0.3489 | 0.37108
0.2252 | 0.24167 | 0.34889 | 0.37107
0.22519 | 0.24166 | 0.34888 | 0.37104
0.22518 | 0.24166 | 0.34886 | 0.37103
0.22518 | 0.24164 | 0.34885 | 0.37101
0.22517 | 0.24163 | 0.34883 | 0.37099
0.22515 | 0.24162 | 0.34882 | 0.37098
0.22515 | 0.24161 | 0.3488 | 0.37095
0.22513 | 0.24161 | 0.34878 | 0.37093
0.22512 | 0.2416 | 0.34877 | 0.3709
0.22511 | 0.24158 | 0.34875 | 0.37088
0.2251 | 0.24158 | 0.34873 | 0.37085
0.22508 | 0.24156 | 0.3487 | 0.37084
0.22507 | 0.24155 | 0.34868 | 0.37083
0.22506 | 0.24154 | 0.34867 | 0.37081
0.22504 | 0.24154 | 0.34866 | 0.37081
0.22503 | 0.24153 | 0.34864 | 0.37079
0.22502 | 0.24152 | 0.34863 | 0.37078
0.22502 | 0.24151 | 0.3486 | 0.37076
0.22499 | 0.24149 | 0.34859 | 0.37075
0.22498 | 0.24148 | 0.34856 | 0.37073
0.22497 | 0.24147 | 0.34854 | 0.37071
0.22497 | 0.24146 | 0.34853 | 0.3707
0.22496 | 0.24145 | 0.34851 | 0.37069
0.22495 | 0.24144 | 0.34848 | 0.37067
0.22494 | 0.24143 | 0.34846 | 0.37066
0.22493 | 0.24142 | 0.34845 | 0.37065
0.22492 | 0.24142 | 0.34843 | 0.37064
0.2249 | 0.24141 | 0.34843 | 0.37062
0.22489 | 0.2414 | 0.34841 | 0.3706
0.22489 | 0.24139 | 0.34837 | 0.37057
0.22487 | 0.24139 | 0.34836 | 0.37055
0.22486 | 0.24138 | 0.34834 | 0.37054
0.22484 | 0.24137 | 0.34831 | 0.37051
0.22484 | 0.24135 | 0.34828 | 0.3705
0.22483 | 0.24135 | 0.34827 | 0.37049
0.22481 | 0.24134 | 0.34826 | 0.37047
0.2248 | 0.24133 | 0.34825 | 0.37045
0.22479 | 0.24132 | 0.34823 | 0.37043
0.22477 | 0.2413 | 0.34822 | 0.37042
0.22476 | 0.24129 | 0.3482 | 0.37039
0.22474 | 0.24128 | 0.34818 | 0.37037
0.22474 | 0.24127 | 0.34816 | 0.37037
0.22473 | 0.24126 | 0.34814 | 0.37035
0.22472 | 0.24126 | 0.34812 | 0.37034
0.22471 | 0.24125 | 0.3481 | 0.37032
0.2247 | 0.24124 | 0.34809 | 0.3703
0.22469 | 0.24122 | 0.34808 | 0.37029
0.22468 | 0.24121 | 0.34806 | 0.37028
0.22467 | 0.24121 | 0.34804 | 0.37026
0.22466 | 0.24119 | 0.34801 | 0.37024
0.22465 | 0.24118 | 0.348 | 0.37023
0.22464 | 0.24117 | 0.34798 | 0.37022
0.22463 | 0.24116 | 0.34797 | 0.37021
0.22462 | 0.24114 | 0.34795 | 0.3702
0.2246 | 0.24114 | 0.34794 | 0.37018
0.22458 | 0.24113 | 0.34792 | 0.37016
0.22457 | 0.24112 | 0.3479 | 0.37014
0.22456 | 0.24111 | 0.34788 | 0.37013
0.22456 | 0.2411 | 0.34788 | 0.37012
0.22455 | 0.24109 | 0.34785 | 0.3701
0.22454 | 0.24108 | 0.34783 | 0.37008
0.22453 | 0.24107 | 0.34782 | 0.37006
0.22452 | 0.24107 | 0.34781 | 0.37005
0.22451 | 0.24105 | 0.34778 | 0.37003
0.2245 | 0.24105 | 0.34777 | 0.37002
0.2245 | 0.24103 | 0.34777 | 0.37
0.22448 | 0.24102 | 0.34774 | 0.36998
0.22447 | 0.24102 | 0.34773 | 0.36997
0.22446 | 0.241 | 0.34772 | 0.36995
0.22445 | 0.241 | 0.3477 | 0.36994
0.22443 | 0.24099 | 0.34769 | 0.36993
0.22442 | 0.24097 | 0.34766 | 0.36991
0.22441 | 0.24096 | 0.34765 | 0.3699
0.2244 | 0.24096 | 0.34762 | 0.36987
0.22439 | 0.24094 | 0.34761 | 0.36986
0.22438 | 0.24093 | 0.34759 | 0.36984
0.22436 | 0.24092 | 0.34757 | 0.36982
0.22436 | 0.24091 | 0.34755 | 0.36981
0.22434 | 0.24091 | 0.34754 | 0.3698
0.22433 | 0.2409 | 0.34752 | 0.36979
0.22432 | 0.24088 | 0.34751 | 0.36977
0.22431 | 0.24087 | 0.34749 | 0.36975
0.22431 | 0.24087 | 0.34748 | 0.36974
0.2243 | 0.24085 | 0.34746 | 0.36972
0.22428 | 0.24084 | 0.34744 | 0.3697
0.22427 | 0.24083 | 0.34742 | 0.36968
0.22426 | 0.24082 | 0.34741 | 0.36967
0.22425 | 0.24081 | 0.34739 | 0.36965
0.22424 | 0.2408 | 0.34738 | 0.36963
0.22423 | 0.2408 | 0.34737 | 0.36961
0.22421 | 0.24078 | 0.34736 | 0.36959
0.22421 | 0.24078 | 0.34733 | 0.36958
0.22419 | 0.24077 | 0.34732 | 0.36956
0.22418 | 0.24076 | 0.3473 | 0.36955
0.22418 | 0.24075 | 0.34729 | 0.36953
0.22416 | 0.24073 | 0.34727 | 0.36952
0.22416 | 0.24072 | 0.34725 | 0.36951
0.22415 | 0.24071 | 0.34724 | 0.36949
0.22414 | 0.2407 | 0.34721 | 0.36947
0.22412 | 0.24069 | 0.34719 | 0.36945
0.22411 | 0.24068 | 0.34718 | 0.36943
0.2241 | 0.24067 | 0.34716 | 0.36942
0.22409 | 0.24066 | 0.34715 | 0.36941
0.22408 | 0.24064 | 0.34713 | 0.36939
0.22407 | 0.24064 | 0.34712 | 0.36938
0.22406 | 0.24063 | 0.34707 | 0.36936
0.22404 | 0.24062 | 0.34706 | 0.36933
0.22402 | 0.24061 | 0.34703 | 0.3693
0.22401 | 0.24059 | 0.34702 | 0.36929
0.224 | 0.24059 | 0.34701 | 0.36927
0.224 | 0.24057 | 0.34699 | 0.36925
0.22399 | 0.24056 | 0.34697 | 0.36924
0.22397 | 0.24056 | 0.34695 | 0.36923
0.22396 | 0.24055 | 0.34694 | 0.36921
0.22395 | 0.24054 | 0.34692 | 0.36919
0.22394 | 0.24053 | 0.3469 | 0.36918
0.22393 | 0.24053 | 0.34689 | 0.36915
0.22392 | 0.24052 | 0.34688 | 0.36914
0.22391 | 0.24051 | 0.34684 | 0.36913
0.2239 | 0.2405 | 0.34683 | 0.36912
0.22389 | 0.24049 | 0.3468 | 0.36911
0.22387 | 0.24048 | 0.34679 | 0.36911
0.22386 | 0.24047 | 0.34676 | 0.36908
0.22385 | 0.24046 | 0.34676 | 0.36907
0.22384 | 0.24045 | 0.34673 | 0.36905
0.22384 | 0.24044 | 0.3467 | 0.36903
0.22383 | 0.24043 | 0.34669 | 0.36902
0.22383 | 0.24042 | 0.34667 | 0.369
0.22382 | 0.24041 | 0.34665 | 0.36898
0.22381 | 0.24041 | 0.34664 | 0.36896
0.2238 | 0.2404 | 0.34663 | 0.36894
0.22379 | 0.24039 | 0.3466 | 0.36892
0.22378 | 0.24039 | 0.34659 | 0.3689
0.22377 | 0.24037 | 0.34657 | 0.36887
0.22376 | 0.24036 | 0.34655 | 0.36886
0.22374 | 0.24035 | 0.34652 | 0.36883
0.22374 | 0.24034 | 0.34651 | 0.36882
0.22372 | 0.24033 | 0.3465 | 0.36881
0.22371 | 0.24032 | 0.34649 | 0.36879
0.2237 | 0.24031 | 0.34647 | 0.36878
0.22369 | 0.2403 | 0.34645 | 0.36876
0.22368 | 0.2403 | 0.34643 | 0.36875
0.22366 | 0.24029 | 0.34641 | 0.36873
0.22365 | 0.24028 | 0.34639 | 0.36871
0.22363 | 0.24027 | 0.34637 | 0.3687
0.22362 | 0.24026 | 0.34635 | 0.36869
0.22362 | 0.24025 | 0.34634 | 0.36867
0.2236 | 0.24024 | 0.34631 | 0.36865
0.2236 | 0.24024 | 0.34628 | 0.36862
0.22358 | 0.24023 | 0.34627 | 0.3686
0.22357 | 0.24022 | 0.34625 | 0.36858
0.22356 | 0.24021 | 0.34623 | 0.36855
0.22355 | 0.24021 | 0.3462 | 0.36853
0.22354 | 0.24019 | 0.34619 | 0.36852
0.22352 | 0.24018 | 0.34617 | 0.3685
0.22351 | 0.24017 | 0.34616 | 0.36849
0.2235 | 0.24015 | 0.34614 | 0.36848
0.22349 | 0.24014 | 0.34613 | 0.36845
0.22348 | 0.24013 | 0.34612 | 0.36844
0.22347 | 0.24012 | 0.34609 | 0.36842
0.22346 | 0.24012 | 0.34608 | 0.36841
0.22345 | 0.24011 | 0.34605 | 0.3684
0.22344 | 0.2401 | 0.34603 | 0.36838
0.22343 | 0.24008 | 0.34601 | 0.36837
0.22342 | 0.24007 | 0.34598 | 0.36836
0.2234 | 0.24006 | 0.34596 | 0.36834
0.2234 | 0.24006 | 0.34594 | 0.36833
0.22339 | 0.24005 | 0.34592 | 0.36832
0.22338 | 0.24004 | 0.34592 | 0.3683
0.22337 | 0.24003 | 0.3459 | 0.36828
0.22336 | 0.24002 | 0.34589 | 0.36826
0.22335 | 0.24 | 0.34587 | 0.36825
0.22334 | 0.23999 | 0.34585 | 0.36824
0.22332 | 0.23998 | 0.34584 | 0.36822
0.22331 | 0.23997 | 0.34583 | 0.36821
0.22329 | 0.23996 | 0.34581 | 0.3682
0.22329 | 0.23996 | 0.34579 | 0.36817
0.22328 | 0.23995 | 0.34577 | 0.36815
0.22327 | 0.23993 | 0.34575 | 0.36814
0.22325 | 0.23992 | 0.3457 | 0.36812
0.22324 | 0.23991 | 0.34568 | 0.3681
0.22323 | 0.2399 | 0.34566 | 0.36809
0.22322 | 0.23989 | 0.34565 | 0.36808
0.22321 | 0.23988 | 0.34564 | 0.36807
0.22319 | 0.23987 | 0.34563 | 0.36804
0.22318 | 0.23986 | 0.34561 | 0.36803
0.22317 | 0.23985 | 0.34559 | 0.36801
0.22316 | 0.23983 | 0.34556 | 0.36799
0.22315 | 0.23983 | 0.34555 | 0.36798
0.22314 | 0.23982 | 0.34552 | 0.36795
0.22313 | 0.23981 | 0.3455 | 0.36793
0.22312 | 0.2398 | 0.34548 | 0.36792
0.22312 | 0.23979 | 0.34546 | 0.3679
0.2231 | 0.23978 | 0.34544 | 0.3679
0.22309 | 0.23977 | 0.34543 | 0.36788
0.22308 | 0.23976 | 0.34542 | 0.36785
0.22306 | 0.23976 | 0.34541 | 0.36783
0.22305 | 0.23975 | 0.34538 | 0.3678
0.22303 | 0.23974 | 0.34536 | 0.36779
0.22302 | 0.23973 | 0.34536 | 0.36778
0.22301 | 0.23971 | 0.34533 | 0.36776
0.223 | 0.2397 | 0.34531 | 0.36775
0.22299 | 0.2397 | 0.34529 | 0.36774
0.22298 | 0.23969 | 0.34527 | 0.36772
0.22297 | 0.23968 | 0.34525 | 0.3677
0.22296 | 0.23967 | 0.34523 | 0.36769
0.22294 | 0.23967 | 0.34522 | 0.36767
0.22292 | 0.23965 | 0.3452 | 0.36765
0.22291 | 0.23964 | 0.34517 | 0.36764
0.2229 | 0.23963 | 0.34516 | 0.36761
0.22289 | 0.23962 | 0.34513 | 0.36758
0.22287 | 0.2396 | 0.3451 | 0.36756
0.22286 | 0.23959 | 0.34507 | 0.36755
0.22285 | 0.23958 | 0.34505 | 0.36754
0.22284 | 0.23957 | 0.34503 | 0.36752
0.22283 | 0.23956 | 0.34502 | 0.36751
0.22282 | 0.23955 | 0.34501 | 0.36749
0.22282 | 0.23954 | 0.34499 | 0.36746
0.22281 | 0.23953 | 0.34498 | 0.36745
0.2228 | 0.23952 | 0.34496 | 0.36744
0.22279 | 0.23952 | 0.34495 | 0.36742
0.22278 | 0.23951 | 0.34492 | 0.3674
0.22277 | 0.2395 | 0.34491 | 0.36737
0.22275 | 0.23949 | 0.34489 | 0.36734
0.22274 | 0.23948 | 0.34488 | 0.36732
0.22273 | 0.23947 | 0.34486 | 0.3673
0.22272 | 0.23946 | 0.34485 | 0.36728
0.22271 | 0.23944 | 0.34483 | 0.36727
0.22269 | 0.23944 | 0.34481 | 0.36725
0.22268 | 0.23943 | 0.3448 | 0.36724
0.22267 | 0.23941 | 0.34479 | 0.36722
0.22265 | 0.2394 | 0.34478 | 0.36721
0.22264 | 0.23939 | 0.34476 | 0.3672
0.22263 | 0.23938 | 0.34473 | 0.36718
0.22262 | 0.23937 | 0.34471 | 0.36716
0.22261 | 0.23936 | 0.34468 | 0.36715
0.2226 | 0.23935 | 0.34467 | 0.36714
0.22259 | 0.23934 | 0.34465 | 0.36713
0.22258 | 0.23933 | 0.34463 | 0.36712
0.22257 | 0.23932 | 0.34462 | 0.36711
0.22256 | 0.2393 | 0.34461 | 0.3671
0.22255 | 0.2393 | 0.34458 | 0.36708
0.22254 | 0.23929 | 0.34455 | 0.36707
0.22253 | 0.23927 | 0.34453 | 0.36706
0.22252 | 0.23927 | 0.34451 | 0.36705
0.22251 | 0.23926 | 0.34449 | 0.36703
0.2225 | 0.23925 | 0.34447 | 0.36701
0.22248 | 0.23924 | 0.34446 | 0.36701
0.22248 | 0.23923 | 0.34443 | 0.36698
0.22247 | 0.23922 | 0.3444 | 0.36696
0.22246 | 0.23921 | 0.34439 | 0.36694
0.22245 | 0.2392 | 0.34437 | 0.36692
0.22243 | 0.2392 | 0.34435 | 0.36691
0.22242 | 0.23919 | 0.34434 | 0.3669
0.22241 | 0.23918 | 0.34432 | 0.36688
0.2224 | 0.23916 | 0.34431 | 0.36686
0.22239 | 0.23914 | 0.34429 | 0.36685
0.22238 | 0.23913 | 0.34427 | 0.36683
0.22237 | 0.23912 | 0.34426 | 0.36682
0.22236 | 0.23911 | 0.34423 | 0.36679
0.22235 | 0.2391 | 0.34421 | 0.36677
0.22234 | 0.23908 | 0.34419 | 0.36676
0.22233 | 0.23907 | 0.34417 | 0.36673
0.22231 | 0.23906 | 0.34416 | 0.36671
0.2223 | 0.23905 | 0.34415 | 0.3667
0.22229 | 0.23904 | 0.34413 | 0.36669
0.22228 | 0.23903 | 0.34411 | 0.36668
0.22227 | 0.23902 | 0.34409 | 0.36667
0.22226 | 0.23901 | 0.34407 | 0.36664
0.22225 | 0.23901 | 0.34406 | 0.36663
0.22225 | 0.239 | 0.34403 | 0.36661
0.22223 | 0.23899 | 0.34402 | 0.36659
0.22222 | 0.23897 | 0.34399 | 0.36658
0.22221 | 0.23896 | 0.34398 | 0.36656
0.2222 | 0.23895 | 0.34395 | 0.36655
0.2222 | 0.23895 | 0.34394 | 0.36654
0.22218 | 0.23894 | 0.34392 | 0.36653
0.22217 | 0.23893 | 0.34391 | 0.36652
0.22215 | 0.23892 | 0.34389 | 0.36651
0.22214 | 0.23891 | 0.34387 | 0.36649
0.22213 | 0.23889 | 0.34386 | 0.36647
0.22212 | 0.23889 | 0.34384 | 0.36644
0.2221 | 0.23887 | 0.34383 | 0.36642
0.2221 | 0.23886 | 0.34382 | 0.3664
0.22209 | 0.23885 | 0.34379 | 0.36638
0.22207 | 0.23885 | 0.34377 | 0.36637
0.22206 | 0.23884 | 0.34376 | 0.36636
0.22205 | 0.23883 | 0.34375 | 0.36635
0.22205 | 0.23882 | 0.34372 | 0.36633
0.22203 | 0.23881 | 0.34371 | 0.3663
0.22202 | 0.23881 | 0.34368 | 0.36628
0.22202 | 0.2388 | 0.34367 | 0.36626
0.22201 | 0.2388 | 0.34363 | 0.36624
0.222 | 0.23879 | 0.34361 | 0.36623
0.22199 | 0.23878 | 0.34358 | 0.36621
0.22198 | 0.23877 | 0.34356 | 0.36619
0.22196 | 0.23876 | 0.34356 | 0.36617
0.22195 | 0.23875 | 0.34355 | 0.36616
0.22194 | 0.23875 | 0.34353 | 0.36614
0.22194 | 0.23873 | 0.34352 | 0.36613
0.22192 | 0.23873 | 0.34349 | 0.36611
0.22191 | 0.23872 | 0.34347 | 0.36608
0.2219 | 0.23871 | 0.34346 | 0.36607
0.22189 | 0.2387 | 0.34344 | 0.36606
0.22188 | 0.23869 | 0.34342 | 0.36604
0.22187 | 0.23868 | 0.3434 | 0.36603
0.22186 | 0.23868 | 0.34337 | 0.36602
0.22186 | 0.23867 | 0.34336 | 0.366
0.22184 | 0.23866 | 0.34334 | 0.36598
0.22183 | 0.23865 | 0.34332 | 0.36596
0.22181 | 0.23864 | 0.34331 | 0.36595
0.2218 | 0.23863 | 0.3433 | 0.36594
0.2218 | 0.23862 | 0.34329 | 0.36592
0.22178 | 0.23861 | 0.34327 | 0.3659
0.22177 | 0.2386 | 0.34325 | 0.36588
0.22176 | 0.23859 | 0.34323 | 0.36587
0.22175 | 0.23859 | 0.34321 | 0.36585
0.22174 | 0.23858 | 0.3432 | 0.36584
0.22173 | 0.23856 | 0.34319 | 0.36583
0.22172 | 0.23856 | 0.34316 | 0.36581
0.22171 | 0.23855 | 0.34315 | 0.3658
0.22169 | 0.23854 | 0.34314 | 0.36578
0.22169 | 0.23853 | 0.34312 | 0.36577
0.22168 | 0.23852 | 0.3431 | 0.36575
0.22167 | 0.23852 | 0.34308 | 0.36574
0.22166 | 0.23851 | 0.34307 | 0.36572
0.22164 | 0.2385 | 0.34305 | 0.3657
0.22162 | 0.23849 | 0.34304 | 0.36568
0.22161 | 0.23848 | 0.34303 | 0.36567
0.2216 | 0.23847 | 0.343 | 0.36566
0.22159 | 0.23846 | 0.34298 | 0.36564
0.22158 | 0.23846 | 0.34297 | 0.36561
0.22157 | 0.23844 | 0.34295 | 0.3656
0.22156 | 0.23844 | 0.34292 | 0.36558
0.22154 | 0.23843 | 0.34291 | 0.36557
0.22153 | 0.23842 | 0.34289 | 0.36555
0.22153 | 0.2384 | 0.34287 | 0.36553
0.22151 | 0.23839 | 0.34284 | 0.36551
0.22149 | 0.23838 | 0.34282 | 0.3655
0.22148 | 0.23836 | 0.3428 | 0.36549
0.22147 | 0.23836 | 0.34279 | 0.36547
0.22146 | 0.23835 | 0.34276 | 0.36545
0.22144 | 0.23834 | 0.34274 | 0.36544
0.22143 | 0.23833 | 0.34271 | 0.36542
0.22142 | 0.23832 | 0.34269 | 0.36541
0.22141 | 0.23831 | 0.34267 | 0.36539
0.2214 | 0.2383 | 0.34265 | 0.36537
0.22138 | 0.23829 | 0.34263 | 0.36535
0.22137 | 0.23828 | 0.34262 | 0.36533
0.22136 | 0.23827 | 0.3426 | 0.36531
0.22135 | 0.23827 | 0.34259 | 0.36529
0.22134 | 0.23826 | 0.34258 | 0.36527
0.22133 | 0.23824 | 0.34255 | 0.36526
0.22132 | 0.23823 | 0.34254 | 0.36524
0.22131 | 0.23823 | 0.34252 | 0.36522
0.2213 | 0.23822 | 0.3425 | 0.36519
0.22128 | 0.23821 | 0.34248 | 0.36517
0.22127 | 0.2382 | 0.34247 | 0.36515
0.22126 | 0.23819 | 0.34246 | 0.36512
0.22125 | 0.23818 | 0.34243 | 0.36511
0.22124 | 0.23818 | 0.3424 | 0.36509
0.22123 | 0.23816 | 0.34237 | 0.36507
0.22121 | 0.23815 | 0.34236 | 0.36505
0.22121 | 0.23815 | 0.34233 | 0.36504
0.2212 | 0.23814 | 0.34231 | 0.36503
0.22118 | 0.23813 | 0.34229 | 0.36501
0.22117 | 0.23812 | 0.34226 | 0.36499
0.22115 | 0.23811 | 0.34224 | 0.36497
0.22114 | 0.23811 | 0.34223 | 0.36496
0.22113 | 0.2381 | 0.34221 | 0.36494
0.22112 | 0.23809 | 0.34219 | 0.36493
0.2211 | 0.23808 | 0.34217 | 0.3649
0.22109 | 0.23807 | 0.34216 | 0.36488
0.22108 | 0.23806 | 0.34213 | 0.36486
0.22108 | 0.23805 | 0.34212 | 0.36484
0.22106 | 0.23804 | 0.34208 | 0.36482
0.22105 | 0.23803 | 0.34207 | 0.3648
0.22103 | 0.23802 | 0.34204 | 0.36476
0.22102 | 0.23801 | 0.34203 | 0.36473
0.22101 | 0.238 | 0.34203 | 0.36471
0.221 | 0.23799 | 0.34201 | 0.36469
0.22099 | 0.23798 | 0.34199 | 0.36468
0.22099 | 0.23796 | 0.34197 | 0.36465
0.22098 | 0.23795 | 0.34195 | 0.36463
0.22097 | 0.23794 | 0.34193 | 0.3646
0.22096 | 0.23793 | 0.34192 | 0.36458
0.22095 | 0.23792 | 0.34189 | 0.36455
0.22094 | 0.23792 | 0.34187 | 0.36453
0.22093 | 0.23791 | 0.34185 | 0.36452
0.22092 | 0.2379 | 0.34184 | 0.3645
0.22091 | 0.2379 | 0.34181 | 0.36448
0.2209 | 0.23789 | 0.34179 | 0.36447
0.22088 | 0.23788 | 0.34176 | 0.36446
0.22087 | 0.23787 | 0.34174 | 0.36444
0.22086 | 0.23786 | 0.34171 | 0.36442
0.22085 | 0.23785 | 0.34169 | 0.36441
0.22083 | 0.23784 | 0.34166 | 0.3644
0.22082 | 0.23784 | 0.34165 | 0.36439
0.22081 | 0.23783 | 0.34163 | 0.36437
0.22079 | 0.23782 | 0.34161 | 0.36436
0.22077 | 0.23781 | 0.34159 | 0.36435
0.22077 | 0.2378 | 0.34157 | 0.36434
0.22075 | 0.23779 | 0.34155 | 0.36433
0.22074 | 0.23778 | 0.34152 | 0.36431
0.22073 | 0.23777 | 0.34151 | 0.36428
0.22072 | 0.23776 | 0.34149 | 0.36427
0.22072 | 0.23776 | 0.34148 | 0.36425
0.22071 | 0.23775 | 0.34146 | 0.36422
0.22071 | 0.23774 | 0.34145 | 0.36421
0.22069 | 0.23773 | 0.34143 | 0.3642
0.22067 | 0.23772 | 0.34141 | 0.36418
0.22066 | 0.23771 | 0.3414 | 0.36416
0.22065 | 0.2377 | 0.34139 | 0.36413
0.22065 | 0.23769 | 0.34137 | 0.36412
0.22064 | 0.23768 | 0.34135 | 0.36409
0.22062 | 0.23767 | 0.34133 | 0.36408
0.22061 | 0.23766 | 0.3413 | 0.36406
0.2206 | 0.23765 | 0.34128 | 0.36405
0.22059 | 0.23764 | 0.34127 | 0.36404
0.22059 | 0.23762 | 0.34125 | 0.36402
0.22058 | 0.23762 | 0.34122 | 0.36401
0.22057 | 0.23761 | 0.3412 | 0.36399
0.22056 | 0.23759 | 0.34118 | 0.36396
0.22054 | 0.23758 | 0.34115 | 0.36395
0.22053 | 0.23757 | 0.34114 | 0.36393
0.22052 | 0.23756 | 0.34112 | 0.36393
0.2205 | 0.23755 | 0.34111 | 0.3639
0.22049 | 0.23754 | 0.34109 | 0.36388
0.22048 | 0.23753 | 0.34107 | 0.36387
0.22047 | 0.23753 | 0.34105 | 0.36385
0.22046 | 0.23752 | 0.34103 | 0.36383
0.22045 | 0.23751 | 0.341 | 0.36382
0.22044 | 0.2375 | 0.34099 | 0.36379
0.22044 | 0.2375 | 0.34097 | 0.36378
0.22043 | 0.23749 | 0.34096 | 0.36377
0.22042 | 0.23748 | 0.34095 | 0.36375
0.2204 | 0.23747 | 0.34093 | 0.36373
0.22039 | 0.23746 | 0.34092 | 0.36371
0.22038 | 0.23745 | 0.3409 | 0.3637
0.22036 | 0.23744 | 0.34089 | 0.36367
0.22035 | 0.23743 | 0.34087 | 0.36366
0.22035 | 0.23742 | 0.34085 | 0.36365
0.22034 | 0.23741 | 0.34083 | 0.36363
0.22033 | 0.2374 | 0.34079 | 0.36362
0.22032 | 0.23739 | 0.34077 | 0.3636
0.22029 | 0.23739 | 0.34076 | 0.36358
0.22028 | 0.23737 | 0.34073 | 0.36357
0.22028 | 0.23736 | 0.34071 | 0.36355
0.22027 | 0.23736 | 0.34069 | 0.36353
0.22026 | 0.23735 | 0.34067 | 0.3635
0.22025 | 0.23733 | 0.34065 | 0.36348
0.22024 | 0.23733 | 0.34062 | 0.36346
0.22023 | 0.23731 | 0.3406 | 0.36345
0.22022 | 0.23731 | 0.34059 | 0.36342
0.22021 | 0.2373 | 0.34057 | 0.3634
0.2202 | 0.23729 | 0.34056 | 0.36339
0.22019 | 0.23728 | 0.34055 | 0.36338
0.22018 | 0.23728 | 0.34054 | 0.36335
0.22017 | 0.23727 | 0.34051 | 0.36332
0.22016 | 0.23726 | 0.3405 | 0.36331
0.22015 | 0.23725 | 0.34049 | 0.36329
0.22014 | 0.23724 | 0.34047 | 0.36327
0.22013 | 0.23723 | 0.34046 | 0.36324
0.22012 | 0.23722 | 0.34044 | 0.36323
0.22011 | 0.2372 | 0.34042 | 0.36321
0.2201 | 0.23719 | 0.34041 | 0.36319
0.22008 | 0.23719 | 0.3404 | 0.36317
0.22006 | 0.23718 | 0.34038 | 0.36316
0.22005 | 0.23717 | 0.34035 | 0.36315
0.22004 | 0.23716 | 0.34033 | 0.36312
0.22002 | 0.23715 | 0.34031 | 0.36311
0.22002 | 0.23714 | 0.34028 | 0.36309
0.22001 | 0.23712 | 0.34026 | 0.36306
0.22 | 0.23711 | 0.34023 | 0.36304
0.21999 | 0.2371 | 0.34021 | 0.36302
0.21998 | 0.23709 | 0.34019 | 0.363
0.21997 | 0.23708 | 0.34016 | 0.36298
0.21996 | 0.23707 | 0.34015 | 0.36295
0.21995 | 0.23706 | 0.34012 | 0.36293
0.21994 | 0.23705 | 0.34011 | 0.36292
0.21993 | 0.23705 | 0.34009 | 0.36289
0.21992 | 0.23703 | 0.34007 | 0.36288
0.21991 | 0.23703 | 0.34006 | 0.36287
0.2199 | 0.23702 | 0.34004 | 0.36285
0.21989 | 0.237 | 0.34002 | 0.36284
0.21989 | 0.23699 | 0.34 | 0.36283
0.21988 | 0.23698 | 0.33999 | 0.36281
0.21986 | 0.23697 | 0.33997 | 0.36279
0.21985 | 0.23696 | 0.33994 | 0.36278
0.21984 | 0.23695 | 0.33993 | 0.36276
0.21983 | 0.23695 | 0.33991 | 0.36274
0.21982 | 0.23694 | 0.33989 | 0.36273
0.21981 | 0.23693 | 0.33986 | 0.36271
0.2198 | 0.23692 | 0.33984 | 0.36269
0.21979 | 0.23691 | 0.33983 | 0.36268
0.21978 | 0.2369 | 0.33981 | 0.36264
0.21977 | 0.23689 | 0.33979 | 0.36262
0.21976 | 0.23688 | 0.33976 | 0.36261
0.21975 | 0.23687 | 0.33974 | 0.36259
0.21974 | 0.23686 | 0.33972 | 0.36257
0.21973 | 0.23686 | 0.33971 | 0.36256
0.21972 | 0.23685 | 0.33971 | 0.36255
0.21971 | 0.23685 | 0.33968 | 0.36253
0.2197 | 0.23683 | 0.33965 | 0.36251
0.21969 | 0.23683 | 0.33963 | 0.3625
0.21968 | 0.23681 | 0.33962 | 0.36249
0.21967 | 0.2368 | 0.33961 | 0.36247
0.21966 | 0.23679 | 0.33959 | 0.36246
0.21965 | 0.23678 | 0.33958 | 0.36244
0.21965 | 0.23677 | 0.33957 | 0.36244
0.21963 | 0.23677 | 0.33955 | 0.36241
0.21962 | 0.23676 | 0.33954 | 0.3624
0.21961 | 0.23675 | 0.3395 | 0.36238
0.21959 | 0.23674 | 0.33949 | 0.36236
0.21958 | 0.23673 | 0.33946 | 0.36234
0.21957 | 0.23672 | 0.33945 | 0.3623
0.21957 | 0.23671 | 0.33942 | 0.36228
0.21956 | 0.2367 | 0.33939 | 0.36226
0.21955 | 0.23668 | 0.33938 | 0.36223
0.21953 | 0.23666 | 0.33936 | 0.36222
0.21952 | 0.23665 | 0.33935 | 0.3622
0.21951 | 0.23664 | 0.33933 | 0.36218
0.21949 | 0.23663 | 0.33931 | 0.36216
0.21948 | 0.23662 | 0.33929 | 0.36214
0.21947 | 0.23661 | 0.33927 | 0.36212
0.21946 | 0.2366 | 0.33926 | 0.36209
0.21944 | 0.23659 | 0.33923 | 0.36207
0.21943 | 0.23658 | 0.33921 | 0.36206
0.21942 | 0.23657 | 0.3392 | 0.36205
0.21941 | 0.23656 | 0.33918 | 0.36203
0.2194 | 0.23655 | 0.33915 | 0.36201
0.21939 | 0.23654 | 0.33914 | 0.36199
0.21938 | 0.23654 | 0.33912 | 0.36197
0.21937 | 0.23653 | 0.3391 | 0.36195
0.21936 | 0.23652 | 0.33908 | 0.36194
0.21935 | 0.23651 | 0.33906 | 0.36191
0.21934 | 0.2365 | 0.33905 | 0.36189
0.21933 | 0.23649 | 0.33901 | 0.36188
0.21932 | 0.23648 | 0.339 | 0.36186
0.21931 | 0.23648 | 0.33896 | 0.36185
0.2193 | 0.23647 | 0.33895 | 0.36184
0.21929 | 0.23646 | 0.33894 | 0.36181
0.21928 | 0.23646 | 0.33893 | 0.3618
0.21926 | 0.23645 | 0.33892 | 0.36178
0.21925 | 0.23643 | 0.3389 | 0.36176
0.21924 | 0.23642 | 0.33887 | 0.36174
0.21923 | 0.23641 | 0.33886 | 0.36171
0.21921 | 0.2364 | 0.33884 | 0.36169
0.2192 | 0.23639 | 0.33881 | 0.36168
0.21919 | 0.23638 | 0.33879 | 0.36166
0.21918 | 0.23636 | 0.33877 | 0.36164
0.21917 | 0.23636 | 0.33874 | 0.36163
0.21916 | 0.23635 | 0.33872 | 0.36161
0.21915 | 0.23634 | 0.33869 | 0.36159
0.21915 | 0.23633 | 0.33867 | 0.36156
0.21914 | 0.23632 | 0.33865 | 0.36155
0.21913 | 0.23631 | 0.33861 | 0.36153
0.21911 | 0.2363 | 0.3386 | 0.36153
0.2191 | 0.23629 | 0.33859 | 0.36151
0.2191 | 0.23628 | 0.33858 | 0.36149
0.21909 | 0.23628 | 0.33855 | 0.36147
0.21908 | 0.23627 | 0.33854 | 0.36147
0.21907 | 0.23626 | 0.33851 | 0.36143
0.21906 | 0.23625 | 0.33846 | 0.36142
0.21905 | 0.23623 | 0.33845 | 0.3614
0.21904 | 0.23622 | 0.33844 | 0.36139
0.21903 | 0.23621 | 0.33842 | 0.36138
0.21901 | 0.23621 | 0.3384 | 0.36137
0.219 | 0.2362 | 0.33837 | 0.36135
0.219 | 0.23619 | 0.33836 | 0.36133
0.21899 | 0.23618 | 0.33834 | 0.36132
0.21898 | 0.23617 | 0.33832 | 0.3613
0.21897 | 0.23616 | 0.33831 | 0.36129
0.21896 | 0.23615 | 0.33829 | 0.36127
0.21895 | 0.23614 | 0.33826 | 0.36125
0.21894 | 0.23613 | 0.33823 | 0.36123
0.21893 | 0.23612 | 0.33821 | 0.3612
0.21892 | 0.2361 | 0.33819 | 0.36118
0.21891 | 0.23609 | 0.33817 | 0.36116
0.2189 | 0.23608 | 0.33815 | 0.36115
0.21889 | 0.23607 | 0.33813 | 0.36111
0.21888 | 0.23606 | 0.33812 | 0.3611
0.21887 | 0.23605 | 0.33809 | 0.36109
0.21887 | 0.23604 | 0.33807 | 0.36108
0.21886 | 0.23604 | 0.33805 | 0.36106
0.21885 | 0.23603 | 0.33804 | 0.36105
0.21883 | 0.23602 | 0.33802 | 0.36105
0.21882 | 0.236 | 0.33799 | 0.36104
0.21881 | 0.23598 | 0.33796 | 0.36101
0.2188 | 0.23597 | 0.33794 | 0.36101
0.21879 | 0.23596 | 0.33791 | 0.36099
0.21877 | 0.23595 | 0.33788 | 0.36098
0.21876 | 0.23594 | 0.33785 | 0.36096
0.21875 | 0.23592 | 0.33784 | 0.36095
0.21874 | 0.23592 | 0.33782 | 0.36093
0.21873 | 0.23591 | 0.3378 | 0.36091
0.21872 | 0.23589 | 0.33779 | 0.36087
0.21871 | 0.23588 | 0.33777 | 0.36085
0.2187 | 0.23588 | 0.33775 | 0.36083
0.21869 | 0.23587 | 0.33773 | 0.36081
0.21868 | 0.23586 | 0.33771 | 0.36079
0.21867 | 0.23584 | 0.33769 | 0.36078
0.21866 | 0.23583 | 0.33766 | 0.36076
0.21865 | 0.23582 | 0.33765 | 0.36075
0.21864 | 0.23581 | 0.33764 | 0.36074
0.21863 | 0.2358 | 0.33761 | 0.36072
0.21863 | 0.23579 | 0.33759 | 0.3607
0.21862 | 0.23577 | 0.33757 | 0.36067
0.21861 | 0.23576 | 0.33755 | 0.36065
0.2186 | 0.23576 | 0.33753 | 0.36064
0.21858 | 0.23574 | 0.33751 | 0.36063
0.21857 | 0.23574 | 0.33749 | 0.3606
0.21857 | 0.23573 | 0.33747 | 0.36057
0.21855 | 0.23571 | 0.33744 | 0.36056
0.21854 | 0.2357 | 0.33742 | 0.36054
0.21853 | 0.23569 | 0.33739 | 0.36053
0.21852 | 0.23568 | 0.33737 | 0.36052
0.2185 | 0.23567 | 0.33736 | 0.3605
0.21849 | 0.23567 | 0.33734 | 0.36049
0.21848 | 0.23566 | 0.33731 | 0.36048
0.21846 | 0.23565 | 0.33729 | 0.36046
0.21845 | 0.23564 | 0.33727 | 0.36045
0.21843 | 0.23563 | 0.33724 | 0.36041
0.21843 | 0.23563 | 0.3372 | 0.3604
0.21842 | 0.23562 | 0.33718 | 0.36038
0.21841 | 0.23561 | 0.33717 | 0.36037
0.2184 | 0.2356 | 0.33715 | 0.36035
0.21838 | 0.23558 | 0.33713 | 0.36032
0.21838 | 0.23557 | 0.33712 | 0.36031
0.21836 | 0.23556 | 0.33711 | 0.3603
0.21836 | 0.23555 | 0.33708 | 0.36028
0.21834 | 0.23554 | 0.33706 | 0.36027
0.21834 | 0.23553 | 0.33703 | 0.36025
0.21833 | 0.23551 | 0.33701 | 0.36023
0.21832 | 0.2355 | 0.337 | 0.36021
0.21831 | 0.2355 | 0.33698 | 0.36021
0.21831 | 0.23549 | 0.33696 | 0.36019
0.21829 | 0.23548 | 0.33694 | 0.36017
0.21828 | 0.23547 | 0.33692 | 0.36016
0.21827 | 0.23546 | 0.3369 | 0.36015
0.21826 | 0.23544 | 0.33689 | 0.36014
0.21825 | 0.23544 | 0.33687 | 0.36013
0.21824 | 0.23543 | 0.33685 | 0.36012
0.21823 | 0.23541 | 0.33683 | 0.3601
0.21822 | 0.2354 | 0.33681 | 0.36008
0.21821 | 0.2354 | 0.33679 | 0.36004
0.21819 | 0.23538 | 0.33676 | 0.36003
0.21819 | 0.23537 | 0.33673 | 0.36001
0.21818 | 0.23536 | 0.33672 | 0.36
0.21817 | 0.23535 | 0.33669 | 0.35997
0.21815 | 0.23534 | 0.33667 | 0.35995
0.21814 | 0.23533 | 0.33665 | 0.35994
0.21814 | 0.23531 | 0.33662 | 0.35993
0.21813 | 0.2353 | 0.3366 | 0.35991
0.21812 | 0.23529 | 0.33658 | 0.35988
0.21811 | 0.23528 | 0.33656 | 0.35986
0.2181 | 0.23528 | 0.33655 | 0.35985
0.21809 | 0.23527 | 0.33653 | 0.35983
0.21809 | 0.23526 | 0.3365 | 0.3598
0.21807 | 0.23525 | 0.33649 | 0.35977
0.21805 | 0.23524 | 0.33647 | 0.35976
0.21804 | 0.23523 | 0.33645 | 0.35974
0.21803 | 0.23522 | 0.33643 | 0.35973
0.21801 | 0.23521 | 0.33641 | 0.35971
0.21801 | 0.2352 | 0.33638 | 0.35969
0.21799 | 0.23518 | 0.33637 | 0.35968
0.21798 | 0.23517 | 0.33634 | 0.35965
0.21797 | 0.23516 | 0.33631 | 0.35964
0.21796 | 0.23515 | 0.3363 | 0.35961
0.21794 | 0.23514 | 0.33629 | 0.3596
0.21793 | 0.23513 | 0.33626 | 0.35958
0.21792 | 0.23512 | 0.33624 | 0.35956
0.21791 | 0.23511 | 0.33621 | 0.35954
0.2179 | 0.2351 | 0.33619 | 0.35953
0.21789 | 0.23509 | 0.33616 | 0.35951
0.21788 | 0.23508 | 0.33614 | 0.35949
0.21787 | 0.23507 | 0.33612 | 0.35949
0.21787 | 0.23507 | 0.3361 | 0.35946
0.21786 | 0.23505 | 0.33608 | 0.35945
0.21785 | 0.23504 | 0.33607 | 0.35944
0.21783 | 0.23503 | 0.33605 | 0.35943
0.21782 | 0.23501 | 0.33604 | 0.35941
0.21782 | 0.235 | 0.33602 | 0.35939
0.2178 | 0.23499 | 0.336 | 0.35937
0.21779 | 0.23498 | 0.33597 | 0.35935
0.21778 | 0.23496 | 0.33595 | 0.35933
0.21777 | 0.23495 | 0.33593 | 0.3593
0.21775 | 0.23494 | 0.33591 | 0.35928
0.21774 | 0.23493 | 0.33589 | 0.35927
0.21773 | 0.23492 | 0.33587 | 0.35926
0.21772 | 0.23491 | 0.33584 | 0.35924
0.21771 | 0.23489 | 0.33582 | 0.35922
0.2177 | 0.23489 | 0.3358 | 0.35921
0.21769 | 0.23487 | 0.33578 | 0.35919
0.21767 | 0.23487 | 0.33576 | 0.35917
0.21766 | 0.23486 | 0.33574 | 0.35914
0.21766 | 0.23484 | 0.33572 | 0.35913
0.21765 | 0.23483 | 0.33569 | 0.35911
0.21764 | 0.23483 | 0.33567 | 0.35909
0.21763 | 0.23482 | 0.33565 | 0.35908
0.21762 | 0.23481 | 0.33564 | 0.35906
0.21761 | 0.2348 | 0.33562 | 0.35905
0.2176 | 0.2348 | 0.33559 | 0.35902
0.21758 | 0.23479 | 0.33557 | 0.35901
0.21757 | 0.23478 | 0.33556 | 0.359
0.21756 | 0.23477 | 0.33553 | 0.35898
0.21755 | 0.23475 | 0.33551 | 0.35897
0.21755 | 0.23474 | 0.3355 | 0.35895
0.21754 | 0.23473 | 0.33548 | 0.35892
0.21753 | 0.23472 | 0.33546 | 0.35892
0.21751 | 0.23471 | 0.33546 | 0.3589
0.2175 | 0.23471 | 0.33543 | 0.35889
0.2175 | 0.2347 | 0.33542 | 0.35887
0.21749 | 0.23469 | 0.3354 | 0.35884
0.21748 | 0.23467 | 0.3354 | 0.35882
0.21747 | 0.23466 | 0.33538 | 0.3588
0.21746 | 0.23465 | 0.33537 | 0.35876
0.21745 | 0.23464 | 0.33535 | 0.35875
0.21744 | 0.23464 | 0.33533 | 0.35874
0.21744 | 0.23463 | 0.33531 | 0.35872
0.21742 | 0.23463 | 0.3353 | 0.3587
0.21741 | 0.23461 | 0.33529 | 0.35868
0.2174 | 0.2346 | 0.33528 | 0.35867
0.21738 | 0.23459 | 0.33526 | 0.35865
0.21737 | 0.23459 | 0.33524 | 0.35864
0.21736 | 0.23457 | 0.33522 | 0.35861
0.21735 | 0.23456 | 0.33519 | 0.35859
0.21733 | 0.23455 | 0.33517 | 0.35857
0.21732 | 0.23454 | 0.33516 | 0.35855
0.21731 | 0.23453 | 0.33515 | 0.35853
0.2173 | 0.23452 | 0.33512 | 0.35852
0.21729 | 0.23451 | 0.3351 | 0.3585
0.21726 | 0.2345 | 0.33508 | 0.35848
0.21726 | 0.23449 | 0.33505 | 0.35846
0.21724 | 0.23448 | 0.33503 | 0.35844
0.21723 | 0.23447 | 0.33502 | 0.35843
0.21722 | 0.23445 | 0.33498 | 0.35842
0.2172 | 0.23444 | 0.33496 | 0.35839
0.21719 | 0.23443 | 0.33494 | 0.35838
0.21717 | 0.23443 | 0.33493 | 0.35835
0.21716 | 0.23442 | 0.33491 | 0.35834
0.21715 | 0.23441 | 0.33489 | 0.35832
0.21712 | 0.2344 | 0.33487 | 0.3583
0.21711 | 0.23439 | 0.33485 | 0.35829
0.21709 | 0.23438 | 0.33483 | 0.35826
0.21708 | 0.23437 | 0.3348 | 0.35825
0.21707 | 0.23436 | 0.33478 | 0.35824
0.21706 | 0.23434 | 0.33476 | 0.35822
0.21705 | 0.23434 | 0.33474 | 0.3582
0.21704 | 0.23432 | 0.33471 | 0.35818
0.21703 | 0.23432 | 0.3347 | 0.35817
0.21702 | 0.23431 | 0.33468 | 0.35815
0.21701 | 0.2343 | 0.33465 | 0.35813
0.217 | 0.23428 | 0.33463 | 0.35812
0.21699 | 0.23427 | 0.33461 | 0.3581
0.21698 | 0.23426 | 0.33459 | 0.35808
0.21697 | 0.23425 | 0.33457 | 0.35805
0.21696 | 0.23424 | 0.33456 | 0.35803
0.21695 | 0.23423 | 0.33452 | 0.35802
0.21695 | 0.23423 | 0.33449 | 0.35801
0.21693 | 0.23422 | 0.33446 | 0.35799
0.2169 | 0.2342 | 0.33444 | 0.35797
0.21689 | 0.23419 | 0.33443 | 0.35795
0.21688 | 0.23419 | 0.33439 | 0.35792
0.21687 | 0.23418 | 0.33438 | 0.3579
0.21686 | 0.23417 | 0.33437 | 0.35788
0.21685 | 0.23416 | 0.33435 | 0.35785
0.21683 | 0.23414 | 0.33431 | 0.35782
0.21682 | 0.23413 | 0.33427 | 0.35781
0.21681 | 0.23413 | 0.33426 | 0.35779
0.2168 | 0.23412 | 0.33423 | 0.35778
0.21679 | 0.23411 | 0.33421 | 0.35776
0.21678 | 0.2341 | 0.33419 | 0.35775
0.21677 | 0.23408 | 0.33416 | 0.35773
0.21676 | 0.23407 | 0.33414 | 0.35771
0.21675 | 0.23406 | 0.33412 | 0.35769
0.21673 | 0.23405 | 0.3341 | 0.35767
0.21672 | 0.23404 | 0.33408 | 0.35766
0.21672 | 0.23404 | 0.33406 | 0.35765
0.21671 | 0.23403 | 0.33403 | 0.35763
0.21669 | 0.23401 | 0.33402 | 0.35761
0.21669 | 0.234 | 0.33401 | 0.3576
0.21667 | 0.23399 | 0.33399 | 0.3576
0.21667 | 0.23398 | 0.33397 | 0.35758
0.21665 | 0.23397 | 0.33394 | 0.35756
0.21664 | 0.23396 | 0.33393 | 0.35754
0.21663 | 0.23395 | 0.33391 | 0.35753
0.21662 | 0.23394 | 0.3339 | 0.3575
0.21661 | 0.23393 | 0.33388 | 0.35749
0.21661 | 0.23393 | 0.33387 | 0.35746
0.2166 | 0.23391 | 0.33385 | 0.35745
0.21659 | 0.2339 | 0.33384 | 0.35743
0.21657 | 0.23389 | 0.33382 | 0.35742
0.21656 | 0.23388 | 0.3338 | 0.3574
0.21655 | 0.23387 | 0.33378 | 0.35737
0.21654 | 0.23386 | 0.33374 | 0.35736
0.21653 | 0.23385 | 0.33373 | 0.35733
0.21652 | 0.23384 | 0.33371 | 0.35731
0.21651 | 0.23383 | 0.33368 | 0.35729
0.2165 | 0.23381 | 0.33365 | 0.35728
0.21648 | 0.2338 | 0.33363 | 0.35726
0.21647 | 0.23379 | 0.33362 | 0.35724
0.21646 | 0.23378 | 0.33359 | 0.35723
0.21645 | 0.23377 | 0.33357 | 0.35722
0.21644 | 0.23376 | 0.33355 | 0.35721
0.21643 | 0.23375 | 0.33353 | 0.35719
0.21642 | 0.23374 | 0.33351 | 0.35717
0.21641 | 0.23373 | 0.3335 | 0.35715
0.21639 | 0.23372 | 0.33348 | 0.35712
0.21638 | 0.23371 | 0.33347 | 0.3571
0.21637 | 0.23371 | 0.33344 | 0.35709
0.21636 | 0.2337 | 0.33342 | 0.35707
0.21635 | 0.23369 | 0.3334 | 0.35705
0.21634 | 0.23368 | 0.33336 | 0.35704
0.21633 | 0.23368 | 0.33334 | 0.35702
0.21632 | 0.23366 | 0.33333 | 0.357
0.21631 | 0.23365 | 0.33329 | 0.35698
0.2163 | 0.23364 | 0.33327 | 0.35695
0.21629 | 0.23363 | 0.33325 | 0.35693
0.21628 | 0.23362 | 0.33324 | 0.35692
0.21627 | 0.23361 | 0.33323 | 0.3569
0.21626 | 0.2336 | 0.33321 | 0.35688
0.21625 | 0.23358 | 0.33319 | 0.35687
0.21624 | 0.23357 | 0.33316 | 0.35684
0.21623 | 0.23355 | 0.33314 | 0.35682
0.21622 | 0.23353 | 0.33312 | 0.35681
0.21621 | 0.23353 | 0.3331 | 0.3568
0.2162 | 0.23352 | 0.33309 | 0.35678
0.21619 | 0.23351 | 0.33308 | 0.35677
0.21619 | 0.2335 | 0.33306 | 0.35676
0.21617 | 0.23349 | 0.33303 | 0.35675
0.21616 | 0.23348 | 0.33302 | 0.35673
0.21615 | 0.23347 | 0.33301 | 0.35672
0.21614 | 0.23346 | 0.33299 | 0.3567
0.21613 | 0.23345 | 0.33298 | 0.35667
0.21612 | 0.23344 | 0.33295 | 0.35666
0.21611 | 0.23344 | 0.33293 | 0.35664
0.21611 | 0.23342 | 0.33292 | 0.35662
0.21609 | 0.23341 | 0.3329 | 0.35661
0.21609 | 0.2334 | 0.33288 | 0.35658
0.21608 | 0.23339 | 0.33287 | 0.35656
0.21607 | 0.23337 | 0.33285 | 0.35655
0.21606 | 0.23337 | 0.33283 | 0.35652
0.21606 | 0.23336 | 0.33281 | 0.35651
0.21605 | 0.23335 | 0.33279 | 0.35649
0.21604 | 0.23334 | 0.33277 | 0.35647
0.21602 | 0.23332 | 0.33275 | 0.35645
0.216 | 0.23332 | 0.33273 | 0.35641
0.21599 | 0.2333 | 0.33271 | 0.35639
0.21598 | 0.2333 | 0.33269 | 0.35637
0.21597 | 0.23328 | 0.33268 | 0.35636
0.21597 | 0.23327 | 0.33266 | 0.35634
0.21596 | 0.23326 | 0.33263 | 0.35633
0.21595 | 0.23325 | 0.33262 | 0.35631
0.21594 | 0.23324 | 0.3326 | 0.3563
0.21594 | 0.23323 | 0.33258 | 0.35628
0.21592 | 0.23322 | 0.33257 | 0.35627
0.21591 | 0.23322 | 0.33255 | 0.35625
0.21589 | 0.23321 | 0.33254 | 0.35624
0.21588 | 0.2332 | 0.33252 | 0.35622
0.21587 | 0.23319 | 0.3325 | 0.3562
0.21587 | 0.23319 | 0.33248 | 0.35618
0.21585 | 0.23317 | 0.33245 | 0.35615
0.21584 | 0.23316 | 0.33242 | 0.35614
0.21582 | 0.23315 | 0.3324 | 0.35612
0.21581 | 0.23314 | 0.33239 | 0.35609
0.21579 | 0.23313 | 0.33237 | 0.35607
0.21578 | 0.23311 | 0.33234 | 0.35605
0.21577 | 0.2331 | 0.3323 | 0.35603
0.21576 | 0.23309 | 0.33228 | 0.35602
0.21574 | 0.23308 | 0.33227 | 0.356
0.21572 | 0.23307 | 0.33225 | 0.35599
0.21571 | 0.23306 | 0.33223 | 0.35596
0.2157 | 0.23305 | 0.3322 | 0.35594
0.21569 | 0.23304 | 0.33219 | 0.35593
0.21567 | 0.23304 | 0.33217 | 0.35592
0.21565 | 0.23303 | 0.33214 | 0.3559
0.21564 | 0.23302 | 0.33212 | 0.35588
0.21563 | 0.23301 | 0.3321 | 0.35585
0.21563 | 0.233 | 0.33207 | 0.35584
0.21562 | 0.233 | 0.33205 | 0.35583
0.21561 | 0.23299 | 0.33204 | 0.35581
0.2156 | 0.23297 | 0.33202 | 0.35579
0.21559 | 0.23296 | 0.33201 | 0.35578
0.21558 | 0.23295 | 0.33199 | 0.35576
0.21558 | 0.23294 | 0.33196 | 0.35575
0.21556 | 0.23293 | 0.33195 | 0.35571
0.21556 | 0.23292 | 0.33192 | 0.35569
0.21554 | 0.23291 | 0.3319 | 0.35567
0.21553 | 0.2329 | 0.33187 | 0.35564
0.21552 | 0.23288 | 0.33185 | 0.35562
0.21551 | 0.23287 | 0.33183 | 0.35561
0.2155 | 0.23286 | 0.33181 | 0.35559
0.21549 | 0.23285 | 0.33177 | 0.35557
0.21548 | 0.23283 | 0.33175 | 0.35555
0.21547 | 0.23282 | 0.33172 | 0.35552
0.21546 | 0.23281 | 0.33169 | 0.35551
0.21545 | 0.2328 | 0.33168 | 0.3555
0.21544 | 0.23279 | 0.33167 | 0.35549
0.21543 | 0.23278 | 0.33166 | 0.35548
0.21542 | 0.23277 | 0.33162 | 0.35547
0.21541 | 0.23276 | 0.33161 | 0.35545
0.2154 | 0.23275 | 0.33159 | 0.35543
0.21539 | 0.23275 | 0.33157 | 0.35541
0.21538 | 0.23273 | 0.33156 | 0.35538
0.21537 | 0.23273 | 0.33154 | 0.35536
0.21536 | 0.23272 | 0.33152 | 0.35535
0.21534 | 0.23271 | 0.33151 | 0.35533
0.21533 | 0.2327 | 0.33148 | 0.35532
0.21532 | 0.23268 | 0.33147 | 0.35529
0.2153 | 0.23267 | 0.33145 | 0.35528
0.21529 | 0.23266 | 0.33143 | 0.35526
0.21528 | 0.23265 | 0.33141 | 0.35523
0.21527 | 0.23264 | 0.33139 | 0.35522
0.21525 | 0.23263 | 0.33136 | 0.3552
0.21525 | 0.23262 | 0.33135 | 0.35519
0.21524 | 0.23261 | 0.33132 | 0.35517
0.21523 | 0.2326 | 0.33129 | 0.35516
0.21522 | 0.23259 | 0.33127 | 0.35514
0.2152 | 0.23258 | 0.33125 | 0.35513
0.21518 | 0.23257 | 0.33124 | 0.3551
0.21517 | 0.23256 | 0.33123 | 0.35508
0.21516 | 0.23255 | 0.33121 | 0.35506
0.21514 | 0.23254 | 0.33119 | 0.35505
0.21513 | 0.23253 | 0.33116 | 0.35502
0.21512 | 0.23251 | 0.33115 | 0.355
0.21511 | 0.23251 | 0.33113 | 0.35499
0.2151 | 0.23249 | 0.3311 | 0.35497
0.21509 | 0.23248 | 0.33107 | 0.35496
0.21508 | 0.23248 | 0.33106 | 0.35492
0.21506 | 0.23247 | 0.33103 | 0.3549
0.21504 | 0.23246 | 0.33101 | 0.35489
0.21504 | 0.23245 | 0.331 | 0.35487
0.21502 | 0.23244 | 0.33098 | 0.35486
0.21502 | 0.23243 | 0.33096 | 0.35484
0.21501 | 0.23242 | 0.33095 | 0.35483
0.215 | 0.23241 | 0.33093 | 0.35481
0.21498 | 0.2324 | 0.33089 | 0.35479
0.21497 | 0.23239 | 0.33089 | 0.35477
0.21496 | 0.23238 | 0.33086 | 0.35474
0.21495 | 0.23236 | 0.33085 | 0.35473
0.21493 | 0.23235 | 0.33083 | 0.35471
0.21492 | 0.23234 | 0.3308 | 0.35469
0.21491 | 0.23233 | 0.33077 | 0.35468
0.21489 | 0.23232 | 0.33075 | 0.35466
0.21488 | 0.23231 | 0.33073 | 0.35464
0.21487 | 0.2323 | 0.33072 | 0.35462
0.21485 | 0.23228 | 0.33069 | 0.35461
0.21484 | 0.23228 | 0.33068 | 0.35459
0.21483 | 0.23227 | 0.33065 | 0.35458
0.21482 | 0.23226 | 0.33063 | 0.35455
0.2148 | 0.23225 | 0.33061 | 0.35454
0.21479 | 0.23224 | 0.33059 | 0.35452
0.21478 | 0.23223 | 0.33056 | 0.3545
0.21477 | 0.23222 | 0.33055 | 0.35448
0.21476 | 0.23221 | 0.33054 | 0.35447
0.21475 | 0.2322 | 0.33051 | 0.35443
0.21475 | 0.2322 | 0.33049 | 0.35442
0.21474 | 0.23219 | 0.33047 | 0.3544
0.21472 | 0.23218 | 0.33044 | 0.35439
0.2147 | 0.23216 | 0.33042 | 0.35437
0.21469 | 0.23215 | 0.3304 | 0.35435
0.21468 | 0.23214 | 0.33039 | 0.35433
0.21468 | 0.23212 | 0.33036 | 0.35431
0.21466 | 0.23212 | 0.33033 | 0.3543
0.21465 | 0.23211 | 0.3303 | 0.35428
0.21464 | 0.2321 | 0.33029 | 0.35425
0.21462 | 0.23208 | 0.33026 | 0.35423
0.21461 | 0.23207 | 0.33025 | 0.3542
0.2146 | 0.23206 | 0.33023 | 0.35417
0.21459 | 0.23205 | 0.33021 | 0.35416
0.21458 | 0.23204 | 0.3302 | 0.35414
0.21457 | 0.23203 | 0.33018 | 0.35412
0.21456 | 0.23201 | 0.33017 | 0.35411
0.21455 | 0.232 | 0.33014 | 0.35407
0.21454 | 0.23199 | 0.33012 | 0.35406
0.21452 | 0.23198 | 0.3301 | 0.35404
0.21452 | 0.23197 | 0.33008 | 0.35403
0.21451 | 0.23196 | 0.33006 | 0.35402
0.2145 | 0.23195 | 0.33004 | 0.354
0.21448 | 0.23194 | 0.33003 | 0.35398
0.21447 | 0.23194 | 0.33001 | 0.35395
0.21446 | 0.23193 | 0.33 | 0.35392
0.21444 | 0.23192 | 0.32998 | 0.3539
0.21444 | 0.23191 | 0.32995 | 0.35387
0.21443 | 0.2319 | 0.32993 | 0.35385
0.21442 | 0.23189 | 0.3299 | 0.35384
0.2144 | 0.23187 | 0.32987 | 0.35381
0.21439 | 0.23186 | 0.32985 | 0.35379
0.21438 | 0.23186 | 0.32982 | 0.35378
0.21437 | 0.23184 | 0.3298 | 0.35375
0.21436 | 0.23183 | 0.32978 | 0.35374
0.21435 | 0.23182 | 0.32977 | 0.35373
0.21434 | 0.23181 | 0.32974 | 0.35372
0.21432 | 0.23181 | 0.32972 | 0.3537
0.21431 | 0.2318 | 0.32971 | 0.35369
0.2143 | 0.23179 | 0.32969 | 0.35366
0.21429 | 0.23178 | 0.32966 | 0.35365
0.21427 | 0.23177 | 0.32964 | 0.35364
0.21426 | 0.23176 | 0.32961 | 0.35362
0.21425 | 0.23175 | 0.32958 | 0.3536
0.21424 | 0.23174 | 0.32957 | 0.35357
0.21423 | 0.23173 | 0.32956 | 0.35356
0.21422 | 0.23172 | 0.32953 | 0.35354
0.2142 | 0.23171 | 0.32949 | 0.35352
0.21419 | 0.2317 | 0.32947 | 0.3535
0.21418 | 0.23169 | 0.32945 | 0.35349
0.21417 | 0.23168 | 0.32942 | 0.35347
0.21417 | 0.23167 | 0.3294 | 0.35344
0.21416 | 0.23166 | 0.32936 | 0.35344
0.21415 | 0.23165 | 0.32934 | 0.35341
0.21413 | 0.23163 | 0.32932 | 0.3534
0.21412 | 0.23163 | 0.32931 | 0.35338
0.21411 | 0.23161 | 0.32929 | 0.35337
0.2141 | 0.23161 | 0.32928 | 0.35335
0.2141 | 0.2316 | 0.32926 | 0.35333
0.21409 | 0.23159 | 0.32924 | 0.35329
0.21408 | 0.23158 | 0.32921 | 0.35328
0.21407 | 0.23156 | 0.32919 | 0.35326
0.21406 | 0.23155 | 0.32916 | 0.35324
0.21405 | 0.23154 | 0.32915 | 0.35323
0.21405 | 0.23153 | 0.32913 | 0.35321
0.21403 | 0.23152 | 0.32911 | 0.3532
0.21402 | 0.23151 | 0.32909 | 0.35318
0.21401 | 0.2315 | 0.32907 | 0.35317
0.214 | 0.2315 | 0.32905 | 0.35315
0.21399 | 0.23148 | 0.32902 | 0.35313
0.21398 | 0.23147 | 0.32901 | 0.35311
0.21397 | 0.23146 | 0.32899 | 0.35309
0.21396 | 0.23145 | 0.32896 | 0.35308
0.21395 | 0.23144 | 0.32893 | 0.35306
0.21393 | 0.23144 | 0.32892 | 0.35304
0.21392 | 0.23143 | 0.32889 | 0.35301
0.21391 | 0.23142 | 0.32888 | 0.35299
0.2139 | 0.23141 | 0.32886 | 0.35297
0.21389 | 0.23139 | 0.32882 | 0.35296
0.21388 | 0.23139 | 0.32879 | 0.35294
0.21387 | 0.23138 | 0.32877 | 0.35292
0.21386 | 0.23137 | 0.32875 | 0.3529
0.21385 | 0.23136 | 0.32872 | 0.35288
0.21384 | 0.23134 | 0.32869 | 0.35286
0.21384 | 0.23133 | 0.32867 | 0.35283
0.21383 | 0.23132 | 0.32863 | 0.35282
0.21382 | 0.23132 | 0.32861 | 0.3528
0.2138 | 0.23131 | 0.3286 | 0.35278
0.2138 | 0.2313 | 0.32859 | 0.35276
0.21378 | 0.23129 | 0.32856 | 0.35274
0.21377 | 0.23128 | 0.32853 | 0.35273
0.21376 | 0.23127 | 0.3285 | 0.3527
0.21375 | 0.23126 | 0.32849 | 0.35268
0.21374 | 0.23125 | 0.32846 | 0.35266
0.21373 | 0.23124 | 0.32844 | 0.35263
0.21371 | 0.23123 | 0.3284 | 0.35262
0.2137 | 0.23121 | 0.32839 | 0.35259
0.21369 | 0.2312 | 0.32836 | 0.35256
0.21367 | 0.23119 | 0.32834 | 0.35255
0.21367 | 0.23118 | 0.32831 | 0.35253
0.21366 | 0.23118 | 0.32828 | 0.35249
0.21365 | 0.23116 | 0.32827 | 0.35247
0.21364 | 0.23115 | 0.32826 | 0.35245
0.21363 | 0.23114 | 0.32824 | 0.35242
0.21362 | 0.23112 | 0.32822 | 0.35241
0.21361 | 0.23111 | 0.32821 | 0.35237
0.2136 | 0.2311 | 0.32819 | 0.35235
0.21359 | 0.23109 | 0.32817 | 0.35233
0.21358 | 0.23108 | 0.32814 | 0.35232
0.21357 | 0.23108 | 0.32813 | 0.3523
0.21356 | 0.23106 | 0.3281 | 0.35229
0.21354 | 0.23105 | 0.32808 | 0.35228
0.21353 | 0.23105 | 0.32806 | 0.35225
0.21352 | 0.23104 | 0.32804 | 0.35224
0.21351 | 0.23103 | 0.32801 | 0.35221
0.21349 | 0.23102 | 0.32799 | 0.3522
0.21348 | 0.23101 | 0.32797 | 0.35217
0.21347 | 0.231 | 0.32795 | 0.35216
0.21346 | 0.23099 | 0.32793 | 0.35214
0.21345 | 0.23098 | 0.32792 | 0.35212
0.21343 | 0.23097 | 0.3279 | 0.35211
0.21342 | 0.23097 | 0.32788 | 0.35209
0.21341 | 0.23095 | 0.32786 | 0.35207
0.2134 | 0.23095 | 0.32782 | 0.35206
0.21339 | 0.23093 | 0.32781 | 0.35204
0.21338 | 0.23093 | 0.32779 | 0.35202
0.21337 | 0.23092 | 0.32778 | 0.35198
0.21336 | 0.23091 | 0.32775 | 0.35197
0.21334 | 0.2309 | 0.32773 | 0.35195
0.21333 | 0.23089 | 0.3277 | 0.35192
0.21332 | 0.23088 | 0.32769 | 0.3519
0.21331 | 0.23087 | 0.32767 | 0.35188
0.2133 | 0.23086 | 0.32765 | 0.35187
0.21329 | 0.23085 | 0.32764 | 0.35185
0.21329 | 0.23084 | 0.32763 | 0.35183
0.21327 | 0.23083 | 0.3276 | 0.35181
0.21326 | 0.23082 | 0.32758 | 0.35179
0.21325 | 0.23081 | 0.32755 | 0.35177
0.21324 | 0.2308 | 0.32754 | 0.35175
0.21324 | 0.2308 | 0.32752 | 0.35173
0.21322 | 0.23079 | 0.32749 | 0.35171
0.21321 | 0.23078 | 0.32747 | 0.35169
0.2132 | 0.23077 | 0.32746 | 0.35166
0.21319 | 0.23075 | 0.32743 | 0.35164
0.21319 | 0.23074 | 0.32742 | 0.35162
0.21318 | 0.23072 | 0.32739 | 0.3516
0.21317 | 0.23072 | 0.32738 | 0.35158
0.21316 | 0.23071 | 0.32734 | 0.35156
0.21315 | 0.2307 | 0.32731 | 0.35154
0.21314 | 0.23069 | 0.3273 | 0.35152
0.21312 | 0.23069 | 0.32727 | 0.3515
0.21312 | 0.23068 | 0.32725 | 0.35149
0.21311 | 0.23067 | 0.32722 | 0.35147
0.2131 | 0.23065 | 0.32721 | 0.35144
0.21309 | 0.23065 | 0.32718 | 0.35143
0.21307 | 0.23064 | 0.32716 | 0.3514
0.21306 | 0.23063 | 0.32715 | 0.35139
0.21305 | 0.23062 | 0.32714 | 0.35136
0.21304 | 0.23061 | 0.32712 | 0.35133
0.21303 | 0.2306 | 0.3271 | 0.35131
0.21302 | 0.23059 | 0.32708 | 0.35129
0.21301 | 0.23058 | 0.32706 | 0.35127
0.21299 | 0.23057 | 0.32704 | 0.35125
0.21298 | 0.23056 | 0.32702 | 0.35122
0.21297 | 0.23055 | 0.327 | 0.3512
0.21296 | 0.23054 | 0.32697 | 0.35115
0.21295 | 0.23053 | 0.32695 | 0.35113
0.21295 | 0.23051 | 0.32693 | 0.35111
0.21293 | 0.2305 | 0.32692 | 0.35109
0.21292 | 0.23049 | 0.32691 | 0.35107
0.2129 | 0.23048 | 0.32687 | 0.35105
0.21289 | 0.23047 | 0.32686 | 0.35101
0.21288 | 0.23046 | 0.32683 | 0.351
0.21287 | 0.23044 | 0.32681 | 0.35098
0.21286 | 0.23044 | 0.3268 | 0.35096
0.21285 | 0.23043 | 0.32678 | 0.35093
0.21284 | 0.23042 | 0.32676 | 0.35091
0.21283 | 0.23041 | 0.32674 | 0.35089
0.21282 | 0.2304 | 0.32672 | 0.35087
0.21281 | 0.23039 | 0.32671 | 0.35086
0.2128 | 0.23037 | 0.32668 | 0.35085
0.21278 | 0.23036 | 0.32667 | 0.35083
0.21277 | 0.23035 | 0.32666 | 0.35081
0.21276 | 0.23034 | 0.32663 | 0.35079
0.21274 | 0.23032 | 0.3266 | 0.35077
0.21273 | 0.23031 | 0.32658 | 0.35075
0.21273 | 0.2303 | 0.32656 | 0.35074
0.21272 | 0.23029 | 0.32652 | 0.35072
0.21271 | 0.23028 | 0.32649 | 0.3507
0.2127 | 0.23027 | 0.32648 | 0.35069
0.21269 | 0.23026 | 0.32646 | 0.35067
0.21268 | 0.23024 | 0.32644 | 0.35066
0.21266 | 0.23023 | 0.32642 | 0.35063
0.21265 | 0.23022 | 0.32639 | 0.35061
0.21264 | 0.23021 | 0.32637 | 0.35057
0.21263 | 0.23021 | 0.32635 | 0.35055
0.21262 | 0.2302 | 0.32635 | 0.35053
0.2126 | 0.23019 | 0.32632 | 0.35051
0.21259 | 0.23018 | 0.32629 | 0.35049
0.21258 | 0.23017 | 0.32628 | 0.35048
0.21257 | 0.23016 | 0.32624 | 0.35044
0.21256 | 0.23016 | 0.32622 | 0.35042
0.21255 | 0.23014 | 0.32619 | 0.35038
0.21253 | 0.23014 | 0.32616 | 0.35035
0.21252 | 0.23013 | 0.32614 | 0.35034
0.2125 | 0.23012 | 0.32613 | 0.35033
0.21249 | 0.2301 | 0.32608 | 0.35029
0.21248 | 0.23009 | 0.32606 | 0.35027
0.21246 | 0.23008 | 0.32604 | 0.35025
0.21246 | 0.23007 | 0.32602 | 0.35023
0.21245 | 0.23005 | 0.326 | 0.3502
0.21244 | 0.23003 | 0.32599 | 0.35019
0.21243 | 0.23002 | 0.32598 | 0.35016
0.21241 | 0.23001 | 0.32596 | 0.35014
0.21241 | 0.23 | 0.32593 | 0.35012
0.21239 | 0.22999 | 0.32592 | 0.35011
0.21238 | 0.22998 | 0.3259 | 0.35009
0.21237 | 0.22997 | 0.32587 | 0.35007
0.21236 | 0.22996 | 0.32585 | 0.35006
0.21235 | 0.22994 | 0.32584 | 0.35004
0.21234 | 0.22993 | 0.32583 | 0.35003
0.21232 | 0.22992 | 0.32579 | 0.35001
0.21232 | 0.22991 | 0.32578 | 0.34998
0.21231 | 0.22991 | 0.32575 | 0.34997
0.21229 | 0.2299 | 0.32573 | 0.34995
0.21229 | 0.22989 | 0.32571 | 0.34993
0.21228 | 0.22987 | 0.32569 | 0.34992
0.21227 | 0.22986 | 0.32566 | 0.3499
0.21225 | 0.22985 | 0.32564 | 0.34989
0.21224 | 0.22984 | 0.32561 | 0.34985
0.21223 | 0.22983 | 0.32559 | 0.34982
0.21223 | 0.22982 | 0.32556 | 0.3498
0.21221 | 0.2298 | 0.32555 | 0.34979
0.2122 | 0.22979 | 0.32553 | 0.34977
0.21219 | 0.22978 | 0.32549 | 0.34974
0.21218 | 0.22977 | 0.32547 | 0.34972
0.21217 | 0.22976 | 0.32546 | 0.34971
0.21216 | 0.22975 | 0.32545 | 0.34969
0.21216 | 0.22974 | 0.32542 | 0.34967
0.21215 | 0.22973 | 0.32539 | 0.34964
0.21214 | 0.22972 | 0.32537 | 0.34962
0.21213 | 0.22971 | 0.32534 | 0.3496
0.21212 | 0.2297 | 0.32531 | 0.34958
0.21211 | 0.22969 | 0.32531 | 0.34955
0.2121 | 0.22968 | 0.32527 | 0.34953
0.21209 | 0.22967 | 0.32526 | 0.34951
0.21208 | 0.22966 | 0.32525 | 0.34948
0.21207 | 0.22965 | 0.32523 | 0.34947
0.21206 | 0.22964 | 0.3252 | 0.34945
0.21205 | 0.22963 | 0.32518 | 0.34943
0.21204 | 0.22962 | 0.32517 | 0.34942
0.21203 | 0.22961 | 0.32514 | 0.3494
0.21202 | 0.22961 | 0.32513 | 0.34938
0.21201 | 0.22959 | 0.32511 | 0.34936
0.212 | 0.22958 | 0.32509 | 0.34935
0.21199 | 0.22957 | 0.32506 | 0.34933
0.21199 | 0.22956 | 0.32504 | 0.34931
0.21198 | 0.22955 | 0.32501 | 0.34929
0.21197 | 0.22954 | 0.325 | 0.34927
0.21196 | 0.22953 | 0.32498 | 0.34925
0.21195 | 0.22952 | 0.32496 | 0.34924
0.21194 | 0.22951 | 0.32493 | 0.34922
0.21193 | 0.2295 | 0.32492 | 0.34921
0.21192 | 0.22948 | 0.3249 | 0.34919
0.21191 | 0.22947 | 0.32487 | 0.34917
0.2119 | 0.22946 | 0.32486 | 0.34916
0.21189 | 0.22945 | 0.32485 | 0.34915
0.21188 | 0.22944 | 0.32482 | 0.34913
0.21187 | 0.22943 | 0.3248 | 0.3491
0.21186 | 0.22943 | 0.32478 | 0.34908
0.21185 | 0.22941 | 0.32475 | 0.34907
0.21184 | 0.2294 | 0.32473 | 0.34904
0.21183 | 0.22938 | 0.32471 | 0.34902
0.21182 | 0.22937 | 0.32468 | 0.349
0.21182 | 0.22936 | 0.32466 | 0.34898
0.21181 | 0.22935 | 0.32465 | 0.34896
0.2118 | 0.22933 | 0.32462 | 0.34892
0.21178 | 0.22932 | 0.32461 | 0.34889
0.21177 | 0.22932 | 0.32458 | 0.34887
0.21177 | 0.22931 | 0.32455 | 0.34885
0.21176 | 0.2293 | 0.32453 | 0.34884
0.21175 | 0.22929 | 0.32452 | 0.34882
0.21174 | 0.22928 | 0.32448 | 0.34881
0.21172 | 0.22927 | 0.32446 | 0.34879
0.21171 | 0.22926 | 0.32443 | 0.34877
0.2117 | 0.22925 | 0.32441 | 0.34875
0.21169 | 0.22924 | 0.32439 | 0.34873
0.21168 | 0.22923 | 0.32437 | 0.34871
0.21167 | 0.22921 | 0.32436 | 0.3487
0.21166 | 0.2292 | 0.32433 | 0.34868
0.21165 | 0.22919 | 0.3243 | 0.34867
0.21164 | 0.22918 | 0.32429 | 0.34865
0.21163 | 0.22917 | 0.32427 | 0.34862
0.21162 | 0.22915 | 0.32424 | 0.3486
0.21161 | 0.22915 | 0.32423 | 0.34858
0.2116 | 0.22914 | 0.3242 | 0.34856
0.21159 | 0.22913 | 0.32417 | 0.34855
0.21159 | 0.22911 | 0.32415 | 0.34852
0.21158 | 0.2291 | 0.32413 | 0.3485
0.21157 | 0.22909 | 0.32411 | 0.34848
0.21155 | 0.22908 | 0.32409 | 0.34847
0.21154 | 0.22907 | 0.32406 | 0.34845
0.21153 | 0.22906 | 0.32402 | 0.34844
0.21152 | 0.22905 | 0.32401 | 0.34843
0.2115 | 0.22904 | 0.32399 | 0.3484
0.21149 | 0.22903 | 0.32397 | 0.34838
0.21147 | 0.22902 | 0.32394 | 0.34836
0.21146 | 0.22901 | 0.32392 | 0.34834
0.21145 | 0.229 | 0.3239 | 0.34831
0.21144 | 0.22899 | 0.32389 | 0.34829
0.21142 | 0.22898 | 0.32387 | 0.34826
0.21142 | 0.22897 | 0.32384 | 0.34822
0.2114 | 0.22895 | 0.3238 | 0.34819
0.21139 | 0.22894 | 0.32378 | 0.34818
0.21138 | 0.22892 | 0.32376 | 0.34817
0.21137 | 0.22892 | 0.32374 | 0.34815
0.21136 | 0.22891 | 0.32371 | 0.34812
0.21135 | 0.2289 | 0.32369 | 0.3481
0.21134 | 0.22889 | 0.32367 | 0.34809
0.21133 | 0.22888 | 0.32365 | 0.34808
0.21132 | 0.22886 | 0.32362 | 0.34805
0.21131 | 0.22885 | 0.32358 | 0.34803
0.2113 | 0.22884 | 0.32356 | 0.348
0.21129 | 0.22882 | 0.32355 | 0.34798
0.21128 | 0.22881 | 0.32353 | 0.34796
0.21127 | 0.2288 | 0.3235 | 0.34794
0.21126 | 0.22879 | 0.32348 | 0.34792
0.21125 | 0.22878 | 0.32345 | 0.3479
0.21124 | 0.22877 | 0.32342 | 0.34787
0.21123 | 0.22875 | 0.32339 | 0.34786
0.21122 | 0.22874 | 0.32338 | 0.34784
0.21121 | 0.22873 | 0.32334 | 0.34783
0.2112 | 0.22872 | 0.32331 | 0.34782
0.21119 | 0.22871 | 0.32329 | 0.3478
0.21118 | 0.2287 | 0.32327 | 0.34778
0.21117 | 0.22869 | 0.32326 | 0.34775
0.21116 | 0.22868 | 0.32322 | 0.34772
0.21115 | 0.22867 | 0.32319 | 0.34769
0.21115 | 0.22866 | 0.32317 | 0.34768
0.21114 | 0.22865 | 0.32315 | 0.34766
0.21113 | 0.22864 | 0.32312 | 0.34765
0.21112 | 0.22863 | 0.3231 | 0.34762
0.21111 | 0.22861 | 0.32309 | 0.3476
0.2111 | 0.2286 | 0.32306 | 0.34758
0.21109 | 0.22859 | 0.32304 | 0.34754
0.21108 | 0.22858 | 0.32303 | 0.34752
0.21106 | 0.22857 | 0.323 | 0.3475
0.21105 | 0.22856 | 0.32298 | 0.34748
0.21104 | 0.22855 | 0.32296 | 0.34745
0.21101 | 0.22854 | 0.32295 | 0.34744
0.21101 | 0.22854 | 0.32291 | 0.34742
0.211 | 0.22851 | 0.3229 | 0.3474
0.21099 | 0.2285 | 0.32288 | 0.34738
0.21099 | 0.22849 | 0.32285 | 0.34736
0.21098 | 0.22848 | 0.32284 | 0.34734
0.21096 | 0.22847 | 0.32281 | 0.34732
0.21095 | 0.22845 | 0.32279 | 0.34731
0.21094 | 0.22845 | 0.32277 | 0.34729
0.21093 | 0.22843 | 0.32275 | 0.34728
0.21092 | 0.22843 | 0.32273 | 0.34725
0.21091 | 0.22841 | 0.32271 | 0.34723
0.21089 | 0.2284 | 0.32269 | 0.34721
0.21088 | 0.22839 | 0.32268 | 0.34719
0.21086 | 0.22838 | 0.32266 | 0.34717
0.21084 | 0.22837 | 0.32262 | 0.34716
0.21084 | 0.22835 | 0.32261 | 0.34714
0.21084 | 0.22835 | 0.32258 | 0.34713
0.21082 | 0.22833 | 0.32255 | 0.34709
0.21081 | 0.22832 | 0.32252 | 0.34706
0.2108 | 0.22831 | 0.3225 | 0.34705
0.21079 | 0.2283 | 0.32247 | 0.34703
0.21078 | 0.22829 | 0.32243 | 0.34701
0.21077 | 0.22827 | 0.32243 | 0.34697
0.21075 | 0.22826 | 0.32241 | 0.34695
0.21075 | 0.22825 | 0.32239 | 0.34694
0.21074 | 0.22824 | 0.32237 | 0.34692
0.21073 | 0.22822 | 0.32235 | 0.3469
0.21072 | 0.22822 | 0.32231 | 0.34688
0.21071 | 0.22821 | 0.32228 | 0.34685
0.2107 | 0.2282 | 0.32227 | 0.34682
0.21068 | 0.2282 | 0.32225 | 0.3468
0.21067 | 0.22819 | 0.32223 | 0.34678
0.21066 | 0.22818 | 0.32221 | 0.34675
0.21064 | 0.22817 | 0.32219 | 0.34674
0.21064 | 0.22816 | 0.32216 | 0.34671
0.21062 | 0.22814 | 0.32214 | 0.34668
0.21061 | 0.22812 | 0.32213 | 0.34664
0.2106 | 0.22812 | 0.3221 | 0.34662
0.2106 | 0.22811 | 0.32207 | 0.34658
0.21059 | 0.2281 | 0.32205 | 0.34655
0.21057 | 0.22809 | 0.32202 | 0.34653
0.21057 | 0.22808 | 0.322 | 0.34651
0.21055 | 0.22807 | 0.32198 | 0.34648
0.21053 | 0.22806 | 0.32194 | 0.34647
0.21052 | 0.22805 | 0.32192 | 0.34645
0.21051 | 0.22804 | 0.32191 | 0.34644
0.21049 | 0.22803 | 0.32189 | 0.34642
0.21048 | 0.22801 | 0.32187 | 0.34641
0.21046 | 0.228 | 0.32185 | 0.34637
0.21045 | 0.22798 | 0.32181 | 0.34634
0.21044 | 0.22798 | 0.32179 | 0.34633
0.21043 | 0.22797 | 0.32178 | 0.34632
0.21042 | 0.22795 | 0.32175 | 0.3463
0.2104 | 0.22794 | 0.32172 | 0.34629
0.21039 | 0.22793 | 0.32171 | 0.34628
0.21039 | 0.22792 | 0.32169 | 0.34624
0.21037 | 0.22791 | 0.32166 | 0.34622
0.21036 | 0.22789 | 0.32164 | 0.3462
0.21034 | 0.22787 | 0.32162 | 0.34616
0.21033 | 0.22785 | 0.3216 | 0.34614
0.21032 | 0.22784 | 0.32157 | 0.3461
0.21031 | 0.22783 | 0.32156 | 0.34607
0.21029 | 0.22782 | 0.32153 | 0.34603
0.21028 | 0.22781 | 0.32151 | 0.34602
0.21027 | 0.2278 | 0.32147 | 0.346
0.21026 | 0.22778 | 0.32145 | 0.34599
0.21025 | 0.22778 | 0.32142 | 0.34597
0.21024 | 0.22777 | 0.32139 | 0.34595
0.21023 | 0.22776 | 0.32135 | 0.34594
0.21022 | 0.22775 | 0.32134 | 0.34591
0.21021 | 0.22774 | 0.32132 | 0.34589
0.21019 | 0.22773 | 0.3213 | 0.34588
0.21018 | 0.22772 | 0.32127 | 0.34584
0.21017 | 0.22771 | 0.32125 | 0.34581
0.21015 | 0.2277 | 0.32123 | 0.34579
0.21015 | 0.22769 | 0.32122 | 0.34578
0.21014 | 0.22767 | 0.32121 | 0.34575
0.21012 | 0.22766 | 0.32118 | 0.34574
0.21011 | 0.22764 | 0.32115 | 0.34572
0.2101 | 0.22763 | 0.32113 | 0.34569
0.21008 | 0.22762 | 0.32112 | 0.34567
0.21007 | 0.22761 | 0.32109 | 0.34564
0.21006 | 0.2276 | 0.32108 | 0.34563
0.21004 | 0.22758 | 0.32105 | 0.3456
0.21003 | 0.22757 | 0.32101 | 0.34558
0.21002 | 0.22756 | 0.32099 | 0.34556
0.21002 | 0.22754 | 0.32096 | 0.34554
0.21001 | 0.22753 | 0.32095 | 0.34551
0.21 | 0.22752 | 0.32093 | 0.3455
0.21 | 0.22751 | 0.32091 | 0.34549
0.20999 | 0.22749 | 0.32089 | 0.34547
0.20997 | 0.22748 | 0.32086 | 0.34546
0.20995 | 0.22747 | 0.32084 | 0.34544
0.20995 | 0.22745 | 0.32082 | 0.34542
0.20993 | 0.22744 | 0.32081 | 0.34541
0.20992 | 0.22743 | 0.32077 | 0.34539
0.20991 | 0.22741 | 0.32075 | 0.34537
0.20989 | 0.22741 | 0.32073 | 0.34535
0.20988 | 0.22739 | 0.32071 | 0.34533
0.20987 | 0.22737 | 0.32069 | 0.34531
0.20986 | 0.22736 | 0.32068 | 0.34528
0.20984 | 0.22735 | 0.32064 | 0.34526
0.20983 | 0.22735 | 0.32062 | 0.34525
0.20982 | 0.22734 | 0.3206 | 0.34524
0.20981 | 0.22733 | 0.32057 | 0.3452
0.2098 | 0.22732 | 0.32055 | 0.34518
0.20979 | 0.22731 | 0.32052 | 0.34516
0.20978 | 0.2273 | 0.32049 | 0.34513
0.20976 | 0.22729 | 0.32047 | 0.3451
0.20975 | 0.22728 | 0.32045 | 0.34507
0.20973 | 0.22727 | 0.32042 | 0.34504
0.20972 | 0.22726 | 0.32039 | 0.34502
0.20971 | 0.22725 | 0.32037 | 0.34499
0.2097 | 0.22723 | 0.32034 | 0.34497
0.20969 | 0.22722 | 0.32031 | 0.34495
0.20967 | 0.22721 | 0.32028 | 0.34494
0.20966 | 0.2272 | 0.32026 | 0.34491
0.20965 | 0.22718 | 0.32025 | 0.34489
0.20964 | 0.22717 | 0.32022 | 0.34487
0.20963 | 0.22716 | 0.32019 | 0.34485
0.20962 | 0.22715 | 0.32017 | 0.34483
0.20961 | 0.22714 | 0.32015 | 0.34481
0.2096 | 0.22713 | 0.32012 | 0.34479
0.20959 | 0.22712 | 0.3201 | 0.34475
0.20958 | 0.22712 | 0.32008 | 0.34473
0.20957 | 0.2271 | 0.32006 | 0.34471
0.20956 | 0.2271 | 0.32003 | 0.34469
0.20956 | 0.22708 | 0.32001 | 0.34465
0.20954 | 0.22707 | 0.31999 | 0.34463
0.20953 | 0.22706 | 0.31998 | 0.34462
0.20953 | 0.22705 | 0.31996 | 0.3446
0.20952 | 0.22704 | 0.31995 | 0.34459
0.20951 | 0.22702 | 0.31993 | 0.34457
0.2095 | 0.22701 | 0.3199 | 0.34456
0.20949 | 0.227 | 0.31986 | 0.34455
0.20948 | 0.22698 | 0.31983 | 0.34452
0.20946 | 0.22698 | 0.31981 | 0.34449
0.20944 | 0.22697 | 0.31979 | 0.34447
0.20943 | 0.22695 | 0.31975 | 0.34445
0.20942 | 0.22695 | 0.31973 | 0.34443
0.20941 | 0.22694 | 0.31971 | 0.3444
0.2094 | 0.22693 | 0.31969 | 0.34439
0.20939 | 0.22691 | 0.31968 | 0.34437
0.20937 | 0.2269 | 0.31967 | 0.34435
0.20937 | 0.22689 | 0.31964 | 0.34433
0.20935 | 0.22687 | 0.31962 | 0.34432
0.20934 | 0.22686 | 0.31958 | 0.34429
0.20933 | 0.22685 | 0.31957 | 0.34428
0.20931 | 0.22684 | 0.31955 | 0.34426
0.2093 | 0.22683 | 0.31952 | 0.34425
0.20929 | 0.22683 | 0.31951 | 0.34423
0.20929 | 0.22681 | 0.31948 | 0.34419
0.20928 | 0.2268 | 0.31946 | 0.34418
0.20927 | 0.22679 | 0.31944 | 0.34414
0.20926 | 0.22678 | 0.31941 | 0.34412
0.20925 | 0.22677 | 0.31939 | 0.34411
0.20924 | 0.22676 | 0.31937 | 0.34409
0.20923 | 0.22675 | 0.31933 | 0.34407
0.20922 | 0.22673 | 0.31932 | 0.34406
0.20921 | 0.22672 | 0.31929 | 0.34403
0.2092 | 0.2267 | 0.31928 | 0.34402
0.20918 | 0.2267 | 0.31926 | 0.344
0.20918 | 0.22669 | 0.31925 | 0.34398
0.20917 | 0.22668 | 0.31922 | 0.34396
0.20916 | 0.22666 | 0.3192 | 0.34394
0.20915 | 0.22665 | 0.31917 | 0.34391
0.20913 | 0.22664 | 0.31915 | 0.34389
0.20912 | 0.22664 | 0.31913 | 0.34386
0.20911 | 0.22662 | 0.3191 | 0.34385
0.2091 | 0.22661 | 0.31907 | 0.34383
0.20909 | 0.2266 | 0.31904 | 0.34379
0.20908 | 0.2266 | 0.31901 | 0.34377
0.20907 | 0.22659 | 0.31899 | 0.34374
0.20905 | 0.22657 | 0.31896 | 0.34371
0.20904 | 0.22656 | 0.31893 | 0.34368
0.20903 | 0.22655 | 0.3189 | 0.34366
0.20903 | 0.22654 | 0.31888 | 0.34363
0.20902 | 0.22653 | 0.31887 | 0.34362
0.20901 | 0.22652 | 0.31885 | 0.3436
0.209 | 0.22651 | 0.31883 | 0.34357
0.20899 | 0.22649 | 0.3188 | 0.34356
0.20898 | 0.22649 | 0.31878 | 0.34354
0.20897 | 0.22648 | 0.31876 | 0.34352
0.20896 | 0.22646 | 0.31874 | 0.3435
0.20894 | 0.22645 | 0.31872 | 0.34348
0.20893 | 0.22643 | 0.3187 | 0.34346
0.20892 | 0.22641 | 0.31868 | 0.34342
0.20891 | 0.2264 | 0.31866 | 0.3434
0.2089 | 0.22639 | 0.31864 | 0.34339
0.20888 | 0.22637 | 0.31862 | 0.34337
0.20887 | 0.22636 | 0.31859 | 0.34333
0.20885 | 0.22635 | 0.31857 | 0.3433
0.20885 | 0.22634 | 0.31855 | 0.34328
0.20883 | 0.22634 | 0.31853 | 0.34326
0.20882 | 0.22632 | 0.31851 | 0.34324
0.20881 | 0.22631 | 0.31848 | 0.34321
0.2088 | 0.2263 | 0.31847 | 0.3432
0.20879 | 0.22629 | 0.31845 | 0.34318
0.20878 | 0.22628 | 0.31844 | 0.34315
0.20877 | 0.22627 | 0.31843 | 0.34313
0.20876 | 0.22626 | 0.3184 | 0.3431
0.20875 | 0.22626 | 0.31839 | 0.34307
0.20875 | 0.22625 | 0.31836 | 0.34306
0.20874 | 0.22624 | 0.31833 | 0.34304
0.20872 | 0.22622 | 0.31832 | 0.34303
0.20871 | 0.22621 | 0.31829 | 0.34301
0.20869 | 0.2262 | 0.31827 | 0.343
0.20868 | 0.22619 | 0.31824 | 0.34298
0.20868 | 0.22618 | 0.3182 | 0.34295
0.20867 | 0.22616 | 0.31817 | 0.34294
0.20865 | 0.22615 | 0.31814 | 0.34291
0.20864 | 0.22613 | 0.31813 | 0.34288
0.20863 | 0.22613 | 0.31811 | 0.34285
0.20862 | 0.22611 | 0.3181 | 0.34283
0.20861 | 0.2261 | 0.31807 | 0.34281
0.20859 | 0.22609 | 0.31805 | 0.34279
0.20858 | 0.22608 | 0.31802 | 0.34277
0.20857 | 0.22607 | 0.31799 | 0.34276
0.20856 | 0.22606 | 0.31797 | 0.34274
0.20855 | 0.22605 | 0.31794 | 0.34273
0.20854 | 0.22604 | 0.31792 | 0.34271
0.20853 | 0.22602 | 0.3179 | 0.34268
0.20852 | 0.22601 | 0.31787 | 0.34266
0.20851 | 0.22599 | 0.31784 | 0.34265
0.2085 | 0.22599 | 0.31782 | 0.34264
0.20849 | 0.22597 | 0.3178 | 0.34263
0.20848 | 0.22596 | 0.31777 | 0.3426
0.20847 | 0.22595 | 0.31774 | 0.34258
0.20846 | 0.22594 | 0.31772 | 0.34256
0.20845 | 0.22593 | 0.3177 | 0.34254
0.20844 | 0.22592 | 0.31767 | 0.34253
0.20843 | 0.22591 | 0.31765 | 0.34251
0.20842 | 0.2259 | 0.31763 | 0.3425
0.20841 | 0.22589 | 0.31761 | 0.34248
0.2084 | 0.22588 | 0.31759 | 0.34246
0.20839 | 0.22587 | 0.31756 | 0.34243
0.20838 | 0.22586 | 0.31753 | 0.3424
0.20837 | 0.22584 | 0.3175 | 0.34238
0.20837 | 0.22583 | 0.31748 | 0.34236
0.20836 | 0.22582 | 0.31745 | 0.34233
0.20835 | 0.2258 | 0.31744 | 0.34231
0.20833 | 0.22579 | 0.31743 | 0.34229
0.20833 | 0.22577 | 0.31741 | 0.34227
0.20832 | 0.22576 | 0.31739 | 0.34225
0.20831 | 0.22575 | 0.31735 | 0.34223
0.2083 | 0.22573 | 0.31733 | 0.34221
0.20829 | 0.22573 | 0.31732 | 0.34218
0.20828 | 0.22571 | 0.31729 | 0.34216
0.20826 | 0.22569 | 0.31727 | 0.34214
0.20825 | 0.22568 | 0.31725 | 0.34213
0.20824 | 0.22566 | 0.31722 | 0.3421
0.20823 | 0.22565 | 0.31718 | 0.34208
0.20822 | 0.22563 | 0.31716 | 0.34206
0.2082 | 0.22562 | 0.31713 | 0.34205
0.20819 | 0.22562 | 0.31712 | 0.34203
0.20818 | 0.2256 | 0.31711 | 0.342
0.20817 | 0.22559 | 0.31708 | 0.34199
0.20815 | 0.22558 | 0.31705 | 0.34197
0.20814 | 0.22555 | 0.31704 | 0.34195
0.20813 | 0.22554 | 0.31701 | 0.34194
0.20811 | 0.22553 | 0.31698 | 0.34191
0.20811 | 0.22551 | 0.31695 | 0.3419
0.2081 | 0.2255 | 0.31691 | 0.34187
0.20809 | 0.22549 | 0.3169 | 0.34184
0.20808 | 0.22549 | 0.31688 | 0.34181
0.20807 | 0.22548 | 0.31684 | 0.34179
0.20807 | 0.22546 | 0.31682 | 0.34177
0.20806 | 0.22544 | 0.31679 | 0.34174
0.20804 | 0.22543 | 0.31678 | 0.34172
0.20803 | 0.22542 | 0.31675 | 0.34169
0.20802 | 0.22541 | 0.31672 | 0.34167
0.20802 | 0.2254 | 0.3167 | 0.34164
0.208 | 0.22538 | 0.31667 | 0.34162
0.20799 | 0.22536 | 0.31666 | 0.3416
0.20798 | 0.22535 | 0.31665 | 0.34159
0.20797 | 0.22534 | 0.31662 | 0.34156
0.20795 | 0.22532 | 0.3166 | 0.34154
0.20794 | 0.22531 | 0.31659 | 0.34153
0.20793 | 0.22529 | 0.31657 | 0.3415
0.20792 | 0.22528 | 0.31656 | 0.34148
0.2079 | 0.22526 | 0.31654 | 0.34146
0.2079 | 0.22525 | 0.31651 | 0.34145
0.20789 | 0.22524 | 0.31649 | 0.34144
0.20788 | 0.22523 | 0.31646 | 0.34142
0.20786 | 0.22521 | 0.31644 | 0.34141
0.20785 | 0.2252 | 0.31641 | 0.3414
0.20784 | 0.22518 | 0.31639 | 0.34139
0.20783 | 0.22517 | 0.31637 | 0.34136
0.20782 | 0.22516 | 0.31636 | 0.34134
0.2078 | 0.22515 | 0.31633 | 0.34133
0.20779 | 0.22514 | 0.31631 | 0.34132
0.20778 | 0.22513 | 0.31628 | 0.34129
0.20777 | 0.22512 | 0.31626 | 0.34128
0.20776 | 0.22511 | 0.31623 | 0.34123
0.20775 | 0.2251 | 0.31621 | 0.34121
0.20774 | 0.22508 | 0.31619 | 0.34119
0.20772 | 0.22507 | 0.31616 | 0.34117
0.20771 | 0.22506 | 0.31612 | 0.34116
0.2077 | 0.22504 | 0.31609 | 0.34114
0.20768 | 0.22503 | 0.31608 | 0.34113
0.20766 | 0.22502 | 0.31605 | 0.34111
0.20765 | 0.225 | 0.31604 | 0.34107
0.20763 | 0.22499 | 0.316 | 0.34103
0.20762 | 0.22498 | 0.31599 | 0.34102
0.20761 | 0.22497 | 0.31597 | 0.341
0.20761 | 0.22495 | 0.31595 | 0.34097
0.2076 | 0.22494 | 0.31592 | 0.34095
0.20759 | 0.22493 | 0.3159 | 0.34089
0.20758 | 0.22492 | 0.31588 | 0.34088
0.20757 | 0.22491 | 0.31587 | 0.34084
0.20756 | 0.2249 | 0.31584 | 0.34082
0.20756 | 0.22489 | 0.31582 | 0.3408
0.20754 | 0.22487 | 0.3158 | 0.34078
0.20753 | 0.22486 | 0.31578 | 0.34075
0.20752 | 0.22484 | 0.31575 | 0.34073
0.20751 | 0.22483 | 0.31573 | 0.34072
0.2075 | 0.22483 | 0.31569 | 0.34068
0.20749 | 0.2248 | 0.31566 | 0.34066
0.20748 | 0.22479 | 0.31564 | 0.34064
0.20747 | 0.22478 | 0.31562 | 0.34062
0.20746 | 0.22476 | 0.31561 | 0.34061
0.20746 | 0.22473 | 0.31559 | 0.34059
0.20745 | 0.22472 | 0.31557 | 0.34056
0.20743 | 0.22471 | 0.31555 | 0.34054
0.20742 | 0.2247 | 0.31551 | 0.34052
0.20741 | 0.22469 | 0.31548 | 0.34051
0.20739 | 0.22468 | 0.31545 | 0.34049
0.20738 | 0.22467 | 0.31543 | 0.34047
0.20737 | 0.22466 | 0.3154 | 0.34047
0.20736 | 0.22465 | 0.31536 | 0.34043
0.20734 | 0.22464 | 0.31534 | 0.34041
0.20733 | 0.22463 | 0.31532 | 0.34039
0.20733 | 0.22461 | 0.3153 | 0.34037
0.20731 | 0.2246 | 0.31527 | 0.34035
0.2073 | 0.22459 | 0.31526 | 0.34033
0.20729 | 0.22457 | 0.31524 | 0.34029
0.20727 | 0.22456 | 0.3152 | 0.34027
0.20726 | 0.22455 | 0.31516 | 0.34024
0.20725 | 0.22452 | 0.31514 | 0.34022
0.20724 | 0.2245 | 0.31511 | 0.34019
0.20723 | 0.22449 | 0.31509 | 0.34018
0.20722 | 0.22447 | 0.31507 | 0.34016
0.20721 | 0.22446 | 0.31504 | 0.34015
0.2072 | 0.22445 | 0.31502 | 0.34013
0.20719 | 0.22444 | 0.31499 | 0.34011
0.20718 | 0.22442 | 0.31495 | 0.34009
0.20717 | 0.22441 | 0.31493 | 0.34006
0.20716 | 0.2244 | 0.31491 | 0.34005
0.20715 | 0.22439 | 0.31489 | 0.34003
0.20714 | 0.22437 | 0.31487 | 0.34
0.20714 | 0.22436 | 0.31485 | 0.33997
0.20713 | 0.22435 | 0.31481 | 0.33995
0.20712 | 0.22435 | 0.31479 | 0.33994
0.20711 | 0.22434 | 0.31477 | 0.33992
0.2071 | 0.22432 | 0.31476 | 0.33988
0.20709 | 0.22431 | 0.31473 | 0.33986
0.20707 | 0.22429 | 0.3147 | 0.33984
0.20706 | 0.22428 | 0.31468 | 0.33982
0.20706 | 0.22427 | 0.31466 | 0.3398
0.20704 | 0.22427 | 0.31463 | 0.33977
0.20703 | 0.22425 | 0.3146 | 0.33973
0.20702 | 0.22423 | 0.31459 | 0.3397
0.207 | 0.22422 | 0.31457 | 0.33968
0.20698 | 0.22421 | 0.31455 | 0.33966
0.20697 | 0.2242 | 0.31454 | 0.33963
0.20696 | 0.22419 | 0.31451 | 0.33961
0.20695 | 0.22417 | 0.31447 | 0.33958
0.20694 | 0.22415 | 0.31445 | 0.33956
0.20692 | 0.22414 | 0.31442 | 0.33955
0.20691 | 0.22414 | 0.31441 | 0.33953
0.2069 | 0.22413 | 0.3144 | 0.33952
0.20688 | 0.22412 | 0.31438 | 0.33949
0.20686 | 0.22411 | 0.31436 | 0.33947
0.20685 | 0.2241 | 0.31433 | 0.33945
0.20684 | 0.22409 | 0.3143 | 0.33943
0.20683 | 0.22408 | 0.31427 | 0.33942
0.20681 | 0.22407 | 0.31426 | 0.33938
0.2068 | 0.22405 | 0.31424 | 0.33936
0.20679 | 0.22404 | 0.31421 | 0.33935
0.20678 | 0.22402 | 0.3142 | 0.33933
0.20677 | 0.22401 | 0.31418 | 0.33931
0.20674 | 0.22401 | 0.31416 | 0.33929
0.20673 | 0.22399 | 0.31415 | 0.33926
0.20672 | 0.22398 | 0.31412 | 0.33924
0.2067 | 0.22397 | 0.3141 | 0.33922
0.20669 | 0.22396 | 0.31409 | 0.33917
0.20668 | 0.22395 | 0.31407 | 0.33915
0.20667 | 0.22393 | 0.31406 | 0.33911
0.20666 | 0.22392 | 0.31404 | 0.33908
0.20665 | 0.2239 | 0.31403 | 0.33904
0.20664 | 0.22388 | 0.31399 | 0.33903
0.20663 | 0.22386 | 0.31397 | 0.339
0.20663 | 0.22385 | 0.31395 | 0.33898
0.20661 | 0.22384 | 0.31393 | 0.33894
0.2066 | 0.22383 | 0.31391 | 0.33892
0.20658 | 0.22382 | 0.31389 | 0.3389
0.20658 | 0.22381 | 0.31388 | 0.33887
0.20657 | 0.2238 | 0.31385 | 0.33885
0.20655 | 0.22378 | 0.31383 | 0.33882
0.20655 | 0.22376 | 0.31378 | 0.3388
0.20653 | 0.22374 | 0.31376 | 0.33878
0.20653 | 0.22374 | 0.31372 | 0.33875
0.20652 | 0.22372 | 0.31369 | 0.33871
0.20651 | 0.22372 | 0.31363 | 0.3387
0.2065 | 0.2237 | 0.31359 | 0.33868
0.20649 | 0.2237 | 0.31357 | 0.33866
0.20647 | 0.22368 | 0.31353 | 0.33865
0.20647 | 0.22367 | 0.3135 | 0.33863
0.20646 | 0.22366 | 0.31346 | 0.33861
0.20645 | 0.22365 | 0.31345 | 0.33858
0.20643 | 0.22363 | 0.31343 | 0.33856
0.20641 | 0.22361 | 0.3134 | 0.33853
0.2064 | 0.22359 | 0.31335 | 0.33852
0.20638 | 0.22357 | 0.31333 | 0.33849
0.20637 | 0.22356 | 0.31331 | 0.33846
0.20636 | 0.22354 | 0.31329 | 0.33843
0.20634 | 0.22353 | 0.31326 | 0.33841
0.20633 | 0.22353 | 0.31324 | 0.33839
0.20632 | 0.22352 | 0.31322 | 0.33837
0.20631 | 0.2235 | 0.31319 | 0.33835
0.2063 | 0.22349 | 0.31317 | 0.3383
0.20629 | 0.22348 | 0.31315 | 0.33828
0.20628 | 0.22347 | 0.3131 | 0.33826
0.20627 | 0.22345 | 0.31308 | 0.33823
0.20627 | 0.22344 | 0.31306 | 0.33819
0.20626 | 0.22343 | 0.31304 | 0.33817
0.20624 | 0.22342 | 0.31302 | 0.33816
0.20624 | 0.22341 | 0.313 | 0.33814
0.20622 | 0.22339 | 0.31298 | 0.33809
0.20621 | 0.22338 | 0.31296 | 0.33806
0.2062 | 0.22336 | 0.31295 | 0.33803
0.20618 | 0.22335 | 0.31294 | 0.338
0.20617 | 0.22334 | 0.31288 | 0.338
0.20616 | 0.22332 | 0.31287 | 0.33797
0.20614 | 0.22331 | 0.31282 | 0.33795
0.20613 | 0.22329 | 0.31278 | 0.33792
0.20612 | 0.22328 | 0.31275 | 0.33788
0.20611 | 0.22327 | 0.31272 | 0.33785
0.2061 | 0.22326 | 0.3127 | 0.33781
0.20608 | 0.22323 | 0.31267 | 0.3378
0.20607 | 0.22322 | 0.31266 | 0.33778
0.20606 | 0.22321 | 0.31261 | 0.33775
0.20604 | 0.2232 | 0.31258 | 0.33773
0.20603 | 0.22318 | 0.31252 | 0.33771
0.20602 | 0.22317 | 0.31252 | 0.33769
0.20601 | 0.22315 | 0.31247 | 0.33767
0.206 | 0.22314 | 0.31243 | 0.33764
0.20599 | 0.22314 | 0.31241 | 0.33762
0.20598 | 0.22312 | 0.31239 | 0.3376
0.20597 | 0.22312 | 0.31236 | 0.33757
0.20597 | 0.22309 | 0.31232 | 0.33755
0.20596 | 0.22308 | 0.3123 | 0.33752
0.20595 | 0.22306 | 0.31228 | 0.3375
0.20594 | 0.22305 | 0.31224 | 0.33747
0.20592 | 0.22304 | 0.31221 | 0.33743
0.2059 | 0.22303 | 0.31219 | 0.3374
0.20589 | 0.22301 | 0.31218 | 0.33738
0.20588 | 0.223 | 0.31215 | 0.33736
0.20587 | 0.22298 | 0.31211 | 0.33734
0.20586 | 0.22297 | 0.31208 | 0.33732
0.20585 | 0.22295 | 0.31205 | 0.3373
0.20583 | 0.22294 | 0.312 | 0.33725
0.20581 | 0.22292 | 0.31197 | 0.33723
0.2058 | 0.22291 | 0.31196 | 0.3372
0.20579 | 0.22289 | 0.31193 | 0.33715
0.20578 | 0.22288 | 0.31191 | 0.33713
0.20576 | 0.22287 | 0.31187 | 0.33712
0.20576 | 0.22286 | 0.31186 | 0.33709
0.20574 | 0.22284 | 0.31182 | 0.33707
0.20573 | 0.22283 | 0.31179 | 0.33706
0.20572 | 0.22282 | 0.31175 | 0.33702
0.20571 | 0.22281 | 0.31171 | 0.33699
0.20569 | 0.22279 | 0.31168 | 0.33697
0.20568 | 0.22278 | 0.31165 | 0.33694
0.20568 | 0.22276 | 0.31162 | 0.33693
0.20566 | 0.22275 | 0.31158 | 0.33691
0.20565 | 0.22274 | 0.31155 | 0.33687
0.20564 | 0.22273 | 0.31154 | 0.33683
0.20562 | 0.22272 | 0.31151 | 0.33681
0.20561 | 0.22271 | 0.31149 | 0.33679
0.20561 | 0.22269 | 0.31147 | 0.33677
0.2056 | 0.22267 | 0.31143 | 0.33675
0.20559 | 0.22266 | 0.31141 | 0.33672
0.20558 | 0.22264 | 0.31136 | 0.3367
0.20557 | 0.22263 | 0.31135 | 0.33668
0.20556 | 0.22262 | 0.31132 | 0.33666
0.20554 | 0.2226 | 0.31129 | 0.33663
0.20554 | 0.22258 | 0.31125 | 0.33661
0.20552 | 0.22257 | 0.31124 | 0.33658
0.20551 | 0.22256 | 0.31122 | 0.33655
0.2055 | 0.22254 | 0.3112 | 0.33654
0.20549 | 0.22253 | 0.31118 | 0.33651
0.20548 | 0.22252 | 0.31115 | 0.33647
0.20547 | 0.22251 | 0.31113 | 0.33646
0.20546 | 0.22249 | 0.31111 | 0.33643
0.20545 | 0.22248 | 0.31109 | 0.3364
0.20544 | 0.22246 | 0.31104 | 0.33637
0.20543 | 0.22245 | 0.311 | 0.33635
0.20542 | 0.22244 | 0.31097 | 0.33634
0.20541 | 0.22243 | 0.31095 | 0.3363
0.2054 | 0.22242 | 0.31091 | 0.33629
0.20539 | 0.22241 | 0.31089 | 0.33627
0.20538 | 0.2224 | 0.31086 | 0.33625
0.20538 | 0.22239 | 0.31084 | 0.33622
0.20537 | 0.22237 | 0.3108 | 0.3362
0.20536 | 0.22236 | 0.31079 | 0.33618
0.20535 | 0.22235 | 0.31076 | 0.33616
0.20533 | 0.22234 | 0.31074 | 0.33614
0.20532 | 0.22233 | 0.31072 | 0.3361
0.20531 | 0.22232 | 0.31068 | 0.33607
0.20529 | 0.2223 | 0.31064 | 0.33604
0.20527 | 0.2223 | 0.31061 | 0.33601
0.20527 | 0.22229 | 0.3106 | 0.33599
0.20525 | 0.22228 | 0.31056 | 0.33597
0.20524 | 0.22226 | 0.31054 | 0.33594
0.20524 | 0.22225 | 0.31052 | 0.33593
0.20522 | 0.22224 | 0.3105 | 0.3359
0.20522 | 0.22223 | 0.31046 | 0.33588
0.2052 | 0.22221 | 0.31044 | 0.33586
0.20519 | 0.2222 | 0.31042 | 0.33584
0.20517 | 0.22219 | 0.3104 | 0.33581
0.20517 | 0.22218 | 0.31038 | 0.3358
0.20515 | 0.22217 | 0.31035 | 0.33577
0.20514 | 0.22216 | 0.31032 | 0.33574
0.20513 | 0.22214 | 0.3103 | 0.33571
0.20511 | 0.22214 | 0.31027 | 0.33569
0.20509 | 0.22212 | 0.31025 | 0.33566
0.20508 | 0.2221 | 0.31023 | 0.33563
0.20507 | 0.22209 | 0.3102 | 0.33562
0.20506 | 0.22208 | 0.31018 | 0.33558
0.20505 | 0.22206 | 0.31015 | 0.33557
0.20504 | 0.22205 | 0.31011 | 0.33555
0.20502 | 0.22203 | 0.31008 | 0.33553
0.20502 | 0.22202 | 0.31005 | 0.3355
0.20501 | 0.22201 | 0.31002 | 0.33546
0.205 | 0.22199 | 0.31 | 0.33544
0.20499 | 0.22198 | 0.30995 | 0.33542
0.20497 | 0.22197 | 0.30992 | 0.33539
0.20496 | 0.22195 | 0.30988 | 0.33538
0.20495 | 0.22193 | 0.30985 | 0.33536
0.20494 | 0.22192 | 0.30982 | 0.33534
0.20493 | 0.22191 | 0.3098 | 0.33531
0.20492 | 0.2219 | 0.30977 | 0.3353
0.2049 | 0.22188 | 0.30976 | 0.33527
0.20489 | 0.22187 | 0.30973 | 0.33525
0.20487 | 0.22186 | 0.3097 | 0.33524
0.20486 | 0.22184 | 0.30965 | 0.33522
0.20484 | 0.22183 | 0.30963 | 0.33521
0.20483 | 0.22182 | 0.30961 | 0.33518
0.20482 | 0.22181 | 0.30958 | 0.33517
0.20481 | 0.2218 | 0.30955 | 0.33514
0.20478 | 0.22177 | 0.30952 | 0.33511
0.20477 | 0.22176 | 0.3095 | 0.3351
0.20476 | 0.22175 | 0.30944 | 0.33508
0.20474 | 0.22173 | 0.30942 | 0.33507
0.20473 | 0.22172 | 0.3094 | 0.33506
0.20471 | 0.22171 | 0.30937 | 0.33503
0.2047 | 0.22169 | 0.30934 | 0.33498
0.20468 | 0.22166 | 0.30931 | 0.33494
0.20467 | 0.22165 | 0.30927 | 0.33491
0.20466 | 0.22164 | 0.30924 | 0.33489
0.20465 | 0.22162 | 0.30923 | 0.33486
0.20464 | 0.22161 | 0.30921 | 0.33485
0.20463 | 0.22159 | 0.3092 | 0.33483
0.20461 | 0.22157 | 0.30917 | 0.33481
0.20459 | 0.22156 | 0.30916 | 0.33479
0.20458 | 0.22155 | 0.30912 | 0.33476
0.20457 | 0.22153 | 0.30911 | 0.33474
0.20455 | 0.22152 | 0.30908 | 0.33473
0.20454 | 0.22151 | 0.30906 | 0.33471
0.20453 | 0.2215 | 0.30903 | 0.3347
0.20452 | 0.22148 | 0.30901 | 0.33467
0.20451 | 0.22147 | 0.30897 | 0.33464
0.2045 | 0.22146 | 0.30895 | 0.33462
0.20448 | 0.22145 | 0.30893 | 0.33458
0.20446 | 0.22144 | 0.30891 | 0.33455
0.20445 | 0.22143 | 0.30888 | 0.33453
0.20443 | 0.22141 | 0.30885 | 0.33449
0.20442 | 0.2214 | 0.30883 | 0.33447
0.20441 | 0.22139 | 0.30881 | 0.33444
0.2044 | 0.22137 | 0.30879 | 0.33441
0.20438 | 0.22136 | 0.30877 | 0.3344
0.20437 | 0.22136 | 0.30872 | 0.33435
0.20436 | 0.22135 | 0.30868 | 0.33434
0.20435 | 0.22132 | 0.30866 | 0.33431
0.20434 | 0.22131 | 0.30864 | 0.33429
0.20433 | 0.22129 | 0.30863 | 0.33426
0.20433 | 0.22126 | 0.30861 | 0.33425
0.20431 | 0.22126 | 0.30859 | 0.33424
0.2043 | 0.22124 | 0.30856 | 0.33421
0.20429 | 0.22123 | 0.30853 | 0.3342
0.20428 | 0.22121 | 0.30851 | 0.33417
0.20427 | 0.2212 | 0.30849 | 0.33415
0.20426 | 0.22118 | 0.30845 | 0.33413
0.20424 | 0.22116 | 0.30843 | 0.33407
0.20423 | 0.22116 | 0.3084 | 0.33405
0.20422 | 0.22115 | 0.30838 | 0.33403
0.20421 | 0.22113 | 0.30834 | 0.334
0.2042 | 0.22111 | 0.30831 | 0.33398
0.20419 | 0.22109 | 0.30829 | 0.33395
0.20418 | 0.22108 | 0.30825 | 0.33392
0.20417 | 0.22107 | 0.30824 | 0.3339
0.20417 | 0.22106 | 0.30821 | 0.33388
0.20414 | 0.22104 | 0.3082 | 0.33386
0.20413 | 0.22103 | 0.30817 | 0.33384
0.20411 | 0.22102 | 0.30814 | 0.33381
0.20411 | 0.22101 | 0.30812 | 0.33378
0.20409 | 0.221 | 0.30808 | 0.33373
0.20407 | 0.22098 | 0.30803 | 0.33372
0.20406 | 0.22096 | 0.30796 | 0.3337
0.20404 | 0.22093 | 0.30792 | 0.33367
0.20403 | 0.22092 | 0.3079 | 0.33365
0.20402 | 0.2209 | 0.30787 | 0.33364
0.20402 | 0.22088 | 0.30782 | 0.33361
0.204 | 0.22086 | 0.30778 | 0.33359
0.20399 | 0.22085 | 0.30776 | 0.33357
0.20397 | 0.22083 | 0.30774 | 0.33354
0.20397 | 0.22081 | 0.30773 | 0.3335
0.20396 | 0.2208 | 0.30771 | 0.33347
0.20395 | 0.22079 | 0.30768 | 0.33344
0.20394 | 0.22077 | 0.30765 | 0.33342
0.20392 | 0.22076 | 0.30762 | 0.3334
0.20391 | 0.22075 | 0.3076 | 0.33337
0.20389 | 0.22073 | 0.30759 | 0.33335
0.20387 | 0.22072 | 0.30754 | 0.33332
0.20386 | 0.2207 | 0.30749 | 0.3333
0.20384 | 0.22069 | 0.30747 | 0.33328
0.20384 | 0.22068 | 0.30746 | 0.33327
0.20383 | 0.22066 | 0.30742 | 0.33324
0.20381 | 0.22065 | 0.3074 | 0.33321
0.2038 | 0.22063 | 0.30737 | 0.33319
0.20379 | 0.22063 | 0.30734 | 0.33315
0.20377 | 0.2206 | 0.3073 | 0.33313
0.20376 | 0.22058 | 0.30727 | 0.33312
0.20374 | 0.22056 | 0.30724 | 0.33308
0.20373 | 0.22055 | 0.30722 | 0.33303
0.20372 | 0.22053 | 0.3072 | 0.33299
0.20369 | 0.22052 | 0.30719 | 0.33296
0.20368 | 0.22051 | 0.30716 | 0.33292
0.20367 | 0.2205 | 0.30713 | 0.33288
0.20366 | 0.22048 | 0.3071 | 0.33287
0.20364 | 0.22047 | 0.30706 | 0.33284
0.20363 | 0.22046 | 0.30704 | 0.33282
0.20362 | 0.22044 | 0.307 | 0.33279
0.20361 | 0.22043 | 0.30698 | 0.33276
0.2036 | 0.22041 | 0.30695 | 0.33275
0.20358 | 0.2204 | 0.30692 | 0.33272
0.20356 | 0.22038 | 0.30689 | 0.33269
0.20355 | 0.22036 | 0.30687 | 0.33266
0.20353 | 0.22035 | 0.30685 | 0.33262
0.20352 | 0.22034 | 0.30682 | 0.3326
0.2035 | 0.22032 | 0.30679 | 0.33258
0.20348 | 0.22032 | 0.30678 | 0.33255
0.20347 | 0.22031 | 0.30676 | 0.33252
0.20346 | 0.2203 | 0.30675 | 0.3325
0.20344 | 0.22029 | 0.30669 | 0.33248
0.20342 | 0.22028 | 0.30666 | 0.33245
0.20341 | 0.22027 | 0.30664 | 0.33241
0.20339 | 0.22026 | 0.30661 | 0.33239
0.20337 | 0.22024 | 0.30658 | 0.33237
0.20336 | 0.22023 | 0.30656 | 0.33235
0.20333 | 0.22022 | 0.30654 | 0.33232
0.20332 | 0.2202 | 0.30649 | 0.3323
0.2033 | 0.22019 | 0.30649 | 0.33229
0.20329 | 0.22016 | 0.30645 | 0.33228
0.20328 | 0.22014 | 0.30643 | 0.33225
0.20326 | 0.22012 | 0.30641 | 0.33223
0.20325 | 0.22011 | 0.30637 | 0.33219
0.20323 | 0.22009 | 0.30635 | 0.33215
0.20322 | 0.22008 | 0.30633 | 0.33213
0.20321 | 0.22007 | 0.3063 | 0.33207
0.2032 | 0.22004 | 0.30629 | 0.33204
0.20319 | 0.22002 | 0.30626 | 0.33201
0.20317 | 0.22001 | 0.30624 | 0.33199
0.20316 | 0.22 | 0.30621 | 0.33196
0.20315 | 0.21998 | 0.30618 | 0.33193
0.20314 | 0.21997 | 0.30615 | 0.3319
0.20313 | 0.21996 | 0.30614 | 0.33188
0.20311 | 0.21994 | 0.3061 | 0.33186
0.2031 | 0.21994 | 0.30608 | 0.33183
0.20309 | 0.21993 | 0.30605 | 0.3318
0.20307 | 0.21992 | 0.30604 | 0.33178
0.20306 | 0.2199 | 0.30601 | 0.33175
0.20304 | 0.21989 | 0.30599 | 0.33173
0.20303 | 0.21988 | 0.30596 | 0.33171
0.20302 | 0.21986 | 0.30595 | 0.33168
0.20301 | 0.21985 | 0.30592 | 0.33166
0.203 | 0.21983 | 0.30589 | 0.33164
0.20298 | 0.21982 | 0.30587 | 0.33162
0.20298 | 0.21981 | 0.30583 | 0.33161
0.20297 | 0.21979 | 0.30581 | 0.33159
0.20296 | 0.21977 | 0.30577 | 0.33157
0.20295 | 0.21975 | 0.30575 | 0.33154
0.20293 | 0.21974 | 0.30572 | 0.33152
0.20292 | 0.21972 | 0.30571 | 0.33149
0.20291 | 0.21971 | 0.30567 | 0.33146
0.20289 | 0.2197 | 0.30565 | 0.33142
0.20288 | 0.21968 | 0.30562 | 0.33138
0.20287 | 0.21967 | 0.30558 | 0.33137
0.20286 | 0.21966 | 0.30555 | 0.33136
0.20284 | 0.21965 | 0.30552 | 0.33134
0.20283 | 0.21963 | 0.30549 | 0.33131
0.20281 | 0.21961 | 0.30547 | 0.33129
0.2028 | 0.2196 | 0.30542 | 0.33127
0.20279 | 0.21958 | 0.30541 | 0.33126
0.20277 | 0.21956 | 0.30539 | 0.33122
0.20275 | 0.21955 | 0.30537 | 0.33119
0.20274 | 0.21953 | 0.30534 | 0.33116
0.20272 | 0.21952 | 0.30533 | 0.33113
0.2027 | 0.21951 | 0.30529 | 0.33112
0.20269 | 0.2195 | 0.30525 | 0.3311
0.20268 | 0.2195 | 0.30522 | 0.33107
0.20266 | 0.21949 | 0.30518 | 0.33104
0.20266 | 0.21948 | 0.30515 | 0.33101
0.20265 | 0.21946 | 0.30512 | 0.33098
0.20263 | 0.21944 | 0.3051 | 0.33096
0.20262 | 0.21942 | 0.30507 | 0.33094
0.2026 | 0.21941 | 0.30504 | 0.33091
0.20259 | 0.2194 | 0.30498 | 0.33089
0.20258 | 0.21938 | 0.30494 | 0.33086
0.20256 | 0.21937 | 0.30491 | 0.33083
0.20255 | 0.21935 | 0.30488 | 0.33081
0.20254 | 0.21934 | 0.30486 | 0.33078
0.20253 | 0.21933 | 0.30483 | 0.33076
0.20251 | 0.21932 | 0.30481 | 0.33072
0.20249 | 0.21929 | 0.30478 | 0.33068
0.20249 | 0.21928 | 0.30475 | 0.33065
0.20248 | 0.21926 | 0.3047 | 0.3306
0.20247 | 0.21925 | 0.30467 | 0.33057
0.20246 | 0.21923 | 0.30465 | 0.33053
0.20244 | 0.21921 | 0.30463 | 0.33049
0.20242 | 0.21919 | 0.30461 | 0.33047
0.20242 | 0.21918 | 0.30458 | 0.33045
0.2024 | 0.21917 | 0.30454 | 0.33043
0.20238 | 0.21916 | 0.30451 | 0.33041
0.20237 | 0.21914 | 0.30449 | 0.33039
0.20235 | 0.21913 | 0.30446 | 0.33037
0.20234 | 0.21911 | 0.30443 | 0.33035
0.20233 | 0.21909 | 0.3044 | 0.33032
0.20232 | 0.21907 | 0.30439 | 0.3303
0.20231 | 0.21905 | 0.30437 | 0.33027
0.20229 | 0.21903 | 0.30433 | 0.33024
0.20228 | 0.219 | 0.30431 | 0.3302
0.20227 | 0.21899 | 0.30429 | 0.33019
0.20225 | 0.21898 | 0.30428 | 0.33016
0.20224 | 0.21896 | 0.30424 | 0.33014
0.20222 | 0.21895 | 0.30422 | 0.33011
0.20221 | 0.21894 | 0.30417 | 0.33009
0.20221 | 0.21892 | 0.30414 | 0.33007
0.20219 | 0.21891 | 0.30412 | 0.33004
0.20216 | 0.2189 | 0.3041 | 0.33001
0.20215 | 0.21889 | 0.30408 | 0.32999
0.20213 | 0.21887 | 0.30406 | 0.32997
0.20211 | 0.21886 | 0.30402 | 0.32995
0.2021 | 0.21884 | 0.30398 | 0.32992
0.20209 | 0.21882 | 0.30394 | 0.32989
0.20208 | 0.21881 | 0.30391 | 0.32986
0.20206 | 0.2188 | 0.30388 | 0.32983
0.20204 | 0.21878 | 0.30385 | 0.32982
0.20203 | 0.21876 | 0.30384 | 0.32979
0.20202 | 0.21874 | 0.30382 | 0.32977
0.20201 | 0.21873 | 0.30378 | 0.32976
0.202 | 0.21872 | 0.30375 | 0.32973
0.20199 | 0.21871 | 0.30372 | 0.3297
0.20197 | 0.21869 | 0.3037 | 0.32967
0.20194 | 0.21867 | 0.30367 | 0.32965
0.20192 | 0.21865 | 0.30365 | 0.32963
0.20191 | 0.21864 | 0.30361 | 0.32962
0.20189 | 0.21862 | 0.30357 | 0.32958
0.20188 | 0.21861 | 0.30355 | 0.32956
0.20186 | 0.21859 | 0.30352 | 0.32955
0.20185 | 0.21857 | 0.30348 | 0.32953
0.20184 | 0.21855 | 0.30346 | 0.32952
0.20183 | 0.21855 | 0.30343 | 0.3295
0.20182 | 0.21853 | 0.30342 | 0.32947
0.2018 | 0.21852 | 0.3034 | 0.32945
0.20179 | 0.2185 | 0.30336 | 0.32942
0.20178 | 0.21849 | 0.30333 | 0.32939
0.20174 | 0.21847 | 0.3033 | 0.32936
0.20173 | 0.21845 | 0.30324 | 0.32934
0.20172 | 0.21843 | 0.30322 | 0.3293
0.2017 | 0.21841 | 0.30319 | 0.32928
0.20169 | 0.21839 | 0.30315 | 0.32924
0.20167 | 0.21838 | 0.30313 | 0.32921
0.20166 | 0.21836 | 0.3031 | 0.32918
0.20165 | 0.21835 | 0.30306 | 0.32916
0.20164 | 0.21834 | 0.30304 | 0.32914
0.20163 | 0.21832 | 0.30302 | 0.32911
0.20161 | 0.21831 | 0.30299 | 0.32909
0.2016 | 0.21828 | 0.30297 | 0.32908
0.20158 | 0.21827 | 0.30293 | 0.32904
0.20157 | 0.21826 | 0.30291 | 0.32901
0.20156 | 0.21825 | 0.3029 | 0.32899
0.20154 | 0.21823 | 0.30287 | 0.32897
0.20152 | 0.21822 | 0.30284 | 0.32892
0.20151 | 0.21821 | 0.30283 | 0.32891
0.2015 | 0.2182 | 0.30278 | 0.32888
0.20149 | 0.21818 | 0.30275 | 0.32884
0.20147 | 0.21817 | 0.30273 | 0.32882
0.20145 | 0.21816 | 0.30268 | 0.32879
0.20144 | 0.21814 | 0.30266 | 0.32875
0.20143 | 0.21813 | 0.30262 | 0.32872
0.20142 | 0.21812 | 0.30257 | 0.32869
0.20141 | 0.2181 | 0.30255 | 0.32865
0.20139 | 0.21809 | 0.30252 | 0.32863
0.20137 | 0.21808 | 0.3025 | 0.32861
0.20135 | 0.21806 | 0.30248 | 0.32859
0.20133 | 0.21805 | 0.30243 | 0.32858
0.20131 | 0.21803 | 0.30241 | 0.32856
0.20129 | 0.21802 | 0.30238 | 0.32853
0.20127 | 0.21801 | 0.30237 | 0.3285
0.20125 | 0.218 | 0.30232 | 0.32849
0.20124 | 0.21798 | 0.3023 | 0.32845
0.20122 | 0.21797 | 0.30226 | 0.32841
0.20121 | 0.21796 | 0.30223 | 0.32839
0.2012 | 0.21795 | 0.3022 | 0.32836
0.20117 | 0.21792 | 0.30217 | 0.32835
0.20115 | 0.21791 | 0.30214 | 0.32833
0.20114 | 0.2179 | 0.30211 | 0.3283
0.20112 | 0.21788 | 0.30207 | 0.32828
0.2011 | 0.21787 | 0.30204 | 0.32825
0.20109 | 0.21785 | 0.30202 | 0.3282
0.20108 | 0.21783 | 0.302 | 0.32818
0.20106 | 0.21782 | 0.30196 | 0.32814
0.20105 | 0.21781 | 0.30195 | 0.3281
0.20104 | 0.21779 | 0.30191 | 0.32807
0.20103 | 0.21777 | 0.3019 | 0.32804
0.20101 | 0.21776 | 0.30187 | 0.32802
0.201 | 0.21774 | 0.30183 | 0.32796
0.20098 | 0.21772 | 0.30181 | 0.32794
0.20096 | 0.2177 | 0.30178 | 0.32791
0.20095 | 0.21769 | 0.30176 | 0.32789
0.20094 | 0.21766 | 0.30175 | 0.32786
0.20092 | 0.21765 | 0.30172 | 0.32784
0.20091 | 0.21764 | 0.3017 | 0.32782
0.20089 | 0.21762 | 0.30169 | 0.32778
0.20088 | 0.2176 | 0.30165 | 0.32777
0.20086 | 0.21758 | 0.30161 | 0.32773
0.20084 | 0.21757 | 0.30158 | 0.32771
0.20083 | 0.21756 | 0.30156 | 0.32769
0.20081 | 0.21755 | 0.30154 | 0.32763
0.20079 | 0.21752 | 0.30152 | 0.32761
0.20077 | 0.2175 | 0.30149 | 0.32758
0.20076 | 0.21748 | 0.30143 | 0.32756
0.20074 | 0.21746 | 0.30141 | 0.32753
0.20072 | 0.21745 | 0.30136 | 0.3275
0.2007 | 0.21744 | 0.30135 | 0.32746
0.20069 | 0.21743 | 0.30131 | 0.32745
0.20068 | 0.21741 | 0.30128 | 0.32743
0.20066 | 0.21739 | 0.30125 | 0.3274
0.20064 | 0.21737 | 0.30122 | 0.32739
0.20063 | 0.21736 | 0.30119 | 0.32734
0.20063 | 0.21733 | 0.30117 | 0.3273
0.20061 | 0.21731 | 0.30115 | 0.32728
0.20059 | 0.2173 | 0.30113 | 0.32723
0.20058 | 0.21729 | 0.30111 | 0.32719
0.20056 | 0.21727 | 0.30108 | 0.32718
0.20055 | 0.21726 | 0.30106 | 0.32713
0.20054 | 0.21723 | 0.30103 | 0.32711
0.20051 | 0.21723 | 0.30098 | 0.32706
0.2005 | 0.21721 | 0.30095 | 0.32702
0.20048 | 0.2172 | 0.30094 | 0.327
0.20046 | 0.21718 | 0.30092 | 0.32696
0.20045 | 0.21717 | 0.30089 | 0.32694
0.20043 | 0.21715 | 0.30087 | 0.32692
0.20041 | 0.21714 | 0.30084 | 0.32687
0.20038 | 0.21712 | 0.30082 | 0.32684
0.20037 | 0.21709 | 0.30079 | 0.32681
0.20034 | 0.21707 | 0.30077 | 0.32678
0.20033 | 0.21706 | 0.30075 | 0.32676
0.20032 | 0.21704 | 0.30071 | 0.32672
0.20031 | 0.21702 | 0.30069 | 0.32668
0.20027 | 0.217 | 0.30067 | 0.32665
0.20026 | 0.21698 | 0.30063 | 0.32662
0.20025 | 0.21697 | 0.30061 | 0.3266
0.20022 | 0.21696 | 0.3006 | 0.32657
0.20021 | 0.21694 | 0.30057 | 0.32652
0.20019 | 0.21694 | 0.30055 | 0.3265
0.20018 | 0.21692 | 0.30052 | 0.32646
0.20016 | 0.2169 | 0.3005 | 0.32643
0.20014 | 0.21689 | 0.30046 | 0.3264
0.20012 | 0.21688 | 0.30042 | 0.32637
0.20011 | 0.21686 | 0.30039 | 0.32632
0.20009 | 0.21684 | 0.30036 | 0.32629
0.20007 | 0.21681 | 0.30032 | 0.32626
0.20005 | 0.21679 | 0.3003 | 0.32622
0.20004 | 0.21677 | 0.30028 | 0.3262
0.20002 | 0.21675 | 0.30026 | 0.32615
0.2 | 0.21674 | 0.30022 | 0.32612
0.19999 | 0.21672 | 0.30019 | 0.3261
0.19996 | 0.21671 | 0.30016 | 0.32607
0.19994 | 0.2167 | 0.30014 | 0.32604
0.19994 | 0.21669 | 0.3001 | 0.32601
0.19992 | 0.21668 | 0.30005 | 0.32596
0.19991 | 0.21666 | 0.30003 | 0.32593
0.19989 | 0.21665 | 0.30002 | 0.3259
0.19987 | 0.21663 | 0.29998 | 0.32586
0.19986 | 0.21662 | 0.29995 | 0.32584
0.19984 | 0.21661 | 0.29994 | 0.3258
0.19982 | 0.21659 | 0.29989 | 0.32577
0.1998 | 0.21658 | 0.29985 | 0.32574
0.19979 | 0.21657 | 0.29981 | 0.3257
0.19978 | 0.21656 | 0.29977 | 0.32569
0.19976 | 0.21654 | 0.29973 | 0.32565
0.19975 | 0.21653 | 0.2997 | 0.32562
0.19974 | 0.2165 | 0.29967 | 0.32558
0.19973 | 0.21647 | 0.29965 | 0.32555
0.19971 | 0.21646 | 0.2996 | 0.32551
0.1997 | 0.21645 | 0.29957 | 0.32549
0.19968 | 0.21643 | 0.29949 | 0.32546
0.19968 | 0.21641 | 0.29946 | 0.32543
0.19966 | 0.21638 | 0.29944 | 0.3254
0.19965 | 0.21637 | 0.29938 | 0.32536
0.19963 | 0.21635 | 0.29937 | 0.32532
0.19962 | 0.21633 | 0.29933 | 0.32528
0.19961 | 0.21631 | 0.29928 | 0.32525
0.19959 | 0.21629 | 0.29925 | 0.3252
0.19957 | 0.21628 | 0.29923 | 0.32517
0.19957 | 0.21627 | 0.29919 | 0.32514
0.19955 | 0.21624 | 0.29918 | 0.32512
0.19953 | 0.21622 | 0.29916 | 0.32507
0.19952 | 0.21621 | 0.29913 | 0.32503
0.19951 | 0.21619 | 0.2991 | 0.32501
0.19949 | 0.21618 | 0.29907 | 0.32498
0.19948 | 0.21616 | 0.29902 | 0.32495
0.19946 | 0.21614 | 0.29898 | 0.32492
0.19944 | 0.21611 | 0.29894 | 0.32488
0.19942 | 0.21609 | 0.2989 | 0.32485
0.19941 | 0.21608 | 0.29884 | 0.32481
0.1994 | 0.21606 | 0.29879 | 0.32477
0.19939 | 0.21605 | 0.29875 | 0.32473
0.19937 | 0.21603 | 0.29871 | 0.3247
0.19936 | 0.21601 | 0.29868 | 0.32466
0.19934 | 0.216 | 0.29865 | 0.32463
0.19932 | 0.21598 | 0.29862 | 0.32459
0.19931 | 0.21596 | 0.29859 | 0.32455
0.1993 | 0.21594 | 0.29856 | 0.32454
0.19929 | 0.21591 | 0.29853 | 0.32452
0.19928 | 0.2159 | 0.29851 | 0.32447
0.19926 | 0.21588 | 0.29849 | 0.32445
0.19925 | 0.21586 | 0.29846 | 0.32443
0.19924 | 0.21583 | 0.29843 | 0.3244
0.19922 | 0.21581 | 0.29839 | 0.32436
0.1992 | 0.21579 | 0.29838 | 0.32434
0.19919 | 0.21577 | 0.29837 | 0.3243
0.19917 | 0.21575 | 0.29833 | 0.32427
0.19915 | 0.21573 | 0.29829 | 0.32426
0.19914 | 0.2157 | 0.29826 | 0.32423
0.19912 | 0.21568 | 0.29821 | 0.32419
0.1991 | 0.21567 | 0.29817 | 0.32416
0.19908 | 0.21566 | 0.29814 | 0.32414
0.19907 | 0.21565 | 0.29811 | 0.3241
0.19905 | 0.21562 | 0.29807 | 0.32407
0.19903 | 0.21561 | 0.29802 | 0.32401
0.19901 | 0.21558 | 0.298 | 0.32398
0.19899 | 0.21556 | 0.29798 | 0.32396
0.19898 | 0.21555 | 0.29796 | 0.32393
0.19896 | 0.21554 | 0.29792 | 0.32389
0.19895 | 0.21552 | 0.2979 | 0.32387
0.19894 | 0.2155 | 0.29787 | 0.32385
0.19891 | 0.21548 | 0.29785 | 0.32383
0.19888 | 0.21547 | 0.29782 | 0.32381
0.19886 | 0.21545 | 0.2978 | 0.3238
0.19883 | 0.21544 | 0.29777 | 0.32378
0.19881 | 0.2154 | 0.29775 | 0.32374
0.19879 | 0.21538 | 0.29773 | 0.32369
0.19878 | 0.21537 | 0.29771 | 0.32367
0.19877 | 0.21536 | 0.2977 | 0.32364
0.19873 | 0.21534 | 0.29765 | 0.32358
0.19872 | 0.21532 | 0.29762 | 0.32355
0.1987 | 0.21531 | 0.29759 | 0.3235
0.19868 | 0.21529 | 0.29756 | 0.32347
0.19866 | 0.21527 | 0.29752 | 0.32344
0.19864 | 0.21526 | 0.29744 | 0.3234
0.19862 | 0.21524 | 0.29741 | 0.32336
0.19861 | 0.21523 | 0.29739 | 0.3233
0.19859 | 0.21521 | 0.29734 | 0.32326
0.19857 | 0.2152 | 0.29729 | 0.32323
0.19855 | 0.21519 | 0.29724 | 0.32318
0.19854 | 0.21517 | 0.29722 | 0.32313
0.19852 | 0.21515 | 0.29719 | 0.32311
0.1985 | 0.21512 | 0.29717 | 0.32307
0.19849 | 0.21511 | 0.29714 | 0.32303
0.19847 | 0.21507 | 0.29712 | 0.32302
0.19845 | 0.21506 | 0.29711 | 0.32298
0.19844 | 0.21503 | 0.29706 | 0.32293
0.19842 | 0.21501 | 0.29703 | 0.3229
0.19841 | 0.215 | 0.29701 | 0.32286
0.1984 | 0.21498 | 0.29699 | 0.32282
0.19838 | 0.21495 | 0.29694 | 0.32277
0.19837 | 0.21493 | 0.29691 | 0.32274
0.19834 | 0.21492 | 0.29689 | 0.32271
0.19833 | 0.21489 | 0.29686 | 0.32267
0.1983 | 0.21487 | 0.29683 | 0.32265
0.1983 | 0.21485 | 0.29681 | 0.32262
0.19827 | 0.21482 | 0.29678 | 0.3226
0.19825 | 0.2148 | 0.29673 | 0.32257
0.19823 | 0.21479 | 0.2967 | 0.32253
0.1982 | 0.21477 | 0.29667 | 0.3225
0.19819 | 0.21474 | 0.29665 | 0.32248
0.19817 | 0.21471 | 0.29662 | 0.32245
0.19815 | 0.21469 | 0.29659 | 0.3224
0.19812 | 0.21467 | 0.29655 | 0.32236
0.19811 | 0.21466 | 0.29649 | 0.32231
0.19809 | 0.21463 | 0.29646 | 0.32228
0.19807 | 0.21462 | 0.29642 | 0.32224
0.19804 | 0.2146 | 0.2964 | 0.32219
0.19802 | 0.21459 | 0.29636 | 0.32216
0.198 | 0.21457 | 0.29634 | 0.32213
0.19798 | 0.21455 | 0.29631 | 0.3221
0.19797 | 0.21454 | 0.29627 | 0.32207
0.19796 | 0.21451 | 0.29623 | 0.32204
0.19794 | 0.2145 | 0.29619 | 0.32201
0.19792 | 0.21448 | 0.29616 | 0.32196
0.19791 | 0.21446 | 0.29611 | 0.32192
0.1979 | 0.21445 | 0.29609 | 0.32188
0.19788 | 0.21443 | 0.29607 | 0.32184
0.19786 | 0.21441 | 0.29604 | 0.32182
0.19785 | 0.21438 | 0.29601 | 0.32179
0.19782 | 0.21437 | 0.29597 | 0.32176
0.1978 | 0.21436 | 0.29593 | 0.32173
0.19778 | 0.21434 | 0.29588 | 0.3217
0.19776 | 0.2143 | 0.29584 | 0.32164
0.19774 | 0.21427 | 0.2958 | 0.32161
0.19773 | 0.21425 | 0.29576 | 0.32159
0.19771 | 0.21422 | 0.29572 | 0.32155
0.1977 | 0.2142 | 0.2957 | 0.32152
0.19767 | 0.21416 | 0.29566 | 0.32148
0.19765 | 0.21413 | 0.29564 | 0.32142
0.19763 | 0.21411 | 0.29561 | 0.32139
0.1976 | 0.21408 | 0.29557 | 0.32137
0.19757 | 0.21406 | 0.29556 | 0.32134
0.19753 | 0.21404 | 0.29552 | 0.3213
0.19753 | 0.21403 | 0.29548 | 0.32126
0.19751 | 0.21401 | 0.29546 | 0.32117
0.19748 | 0.21398 | 0.29543 | 0.32114
0.19745 | 0.21396 | 0.29541 | 0.32112
0.19743 | 0.21394 | 0.29538 | 0.32108
0.19741 | 0.21392 | 0.29535 | 0.32103
0.19739 | 0.2139 | 0.29529 | 0.32101
0.19738 | 0.21387 | 0.29525 | 0.32098
0.19736 | 0.21385 | 0.29523 | 0.32095
0.19733 | 0.21382 | 0.2952 | 0.32088
0.19731 | 0.2138 | 0.29518 | 0.32086
0.19729 | 0.21378 | 0.29515 | 0.32081
0.19727 | 0.21374 | 0.29513 | 0.32076
0.19725 | 0.21371 | 0.29511 | 0.32072
0.19722 | 0.21368 | 0.29508 | 0.32064
0.1972 | 0.21366 | 0.29505 | 0.3206
0.19719 | 0.21364 | 0.29502 | 0.32057
0.19717 | 0.21362 | 0.29498 | 0.32054
0.19715 | 0.2136 | 0.29495 | 0.3205
0.19713 | 0.21358 | 0.2949 | 0.32046
0.19711 | 0.21357 | 0.29485 | 0.32044
0.19708 | 0.21355 | 0.29483 | 0.32041
0.19707 | 0.21353 | 0.29482 | 0.32037
0.19705 | 0.2135 | 0.29477 | 0.32032
0.19703 | 0.21347 | 0.29476 | 0.32028
0.197 | 0.21345 | 0.29472 | 0.32023
0.19699 | 0.21343 | 0.29466 | 0.3202
0.19698 | 0.21342 | 0.29462 | 0.32014
0.19694 | 0.21338 | 0.29459 | 0.32009
0.19692 | 0.21338 | 0.29455 | 0.32006
0.19689 | 0.21335 | 0.29451 | 0.32001
0.19687 | 0.21334 | 0.29445 | 0.31999
0.19686 | 0.21332 | 0.29439 | 0.31993
0.19684 | 0.21331 | 0.29435 | 0.31992
0.19683 | 0.21328 | 0.29432 | 0.31988
0.19682 | 0.21325 | 0.29428 | 0.31986
0.19679 | 0.21322 | 0.29423 | 0.31982
0.19677 | 0.2132 | 0.2942 | 0.31979
0.19674 | 0.21318 | 0.29412 | 0.31977
0.19672 | 0.21315 | 0.2941 | 0.31974
0.1967 | 0.21312 | 0.29403 | 0.31967
0.19667 | 0.21309 | 0.29401 | 0.31963
0.19664 | 0.21307 | 0.29397 | 0.31958
0.19661 | 0.21304 | 0.29395 | 0.31957
0.19659 | 0.21302 | 0.2939 | 0.31952
0.19657 | 0.21298 | 0.29384 | 0.31948
0.19655 | 0.21295 | 0.2938 | 0.31943
0.19653 | 0.21293 | 0.29373 | 0.31937
0.19651 | 0.21291 | 0.2937 | 0.31931
0.19649 | 0.2129 | 0.29367 | 0.31926
0.19648 | 0.21288 | 0.29364 | 0.31922
0.19646 | 0.21286 | 0.2936 | 0.31917
0.19643 | 0.21284 | 0.29356 | 0.3191
0.19641 | 0.21282 | 0.29352 | 0.31907
0.19639 | 0.21281 | 0.29349 | 0.31903
0.19636 | 0.21279 | 0.29346 | 0.31899
0.19634 | 0.21274 | 0.29344 | 0.31894
0.19631 | 0.21271 | 0.29342 | 0.3189
0.19628 | 0.21268 | 0.29338 | 0.31887
0.19627 | 0.21265 | 0.29334 | 0.31883
0.19625 | 0.21263 | 0.29328 | 0.31878
0.19621 | 0.21261 | 0.29323 | 0.31875
0.19619 | 0.21259 | 0.29321 | 0.3187
0.19617 | 0.21254 | 0.29319 | 0.31866
0.19614 | 0.21251 | 0.29314 | 0.31863
0.19612 | 0.21247 | 0.29309 | 0.31856
0.1961 | 0.21244 | 0.29307 | 0.31849
0.19608 | 0.21242 | 0.29299 | 0.31846
0.19607 | 0.21239 | 0.2929 | 0.3184
0.19604 | 0.21237 | 0.29286 | 0.31833
0.19602 | 0.21235 | 0.29282 | 0.31829
0.19599 | 0.21231 | 0.29278 | 0.31827
0.19596 | 0.21229 | 0.29275 | 0.31824
0.19594 | 0.21227 | 0.29272 | 0.3182
0.19592 | 0.21224 | 0.29266 | 0.31816
0.19589 | 0.21221 | 0.29261 | 0.31811
0.19587 | 0.21217 | 0.29258 | 0.31809
0.19585 | 0.21214 | 0.29255 | 0.31805
0.19582 | 0.21212 | 0.29252 | 0.31801
0.19579 | 0.21209 | 0.2925 | 0.31796
0.19578 | 0.21205 | 0.29247 | 0.31791
0.19574 | 0.21202 | 0.29244 | 0.31782
0.19572 | 0.21199 | 0.29239 | 0.31777
0.19569 | 0.21196 | 0.29237 | 0.31775
0.19568 | 0.21193 | 0.29232 | 0.31772
0.19565 | 0.21191 | 0.29228 | 0.31769
0.19563 | 0.21187 | 0.29226 | 0.31766
0.19559 | 0.21185 | 0.29222 | 0.31763
0.19557 | 0.21184 | 0.29219 | 0.31761
0.19554 | 0.21181 | 0.29215 | 0.31756
0.1955 | 0.21179 | 0.29212 | 0.3175
0.19548 | 0.21177 | 0.29209 | 0.31746
0.19545 | 0.21175 | 0.29205 | 0.31743
0.19543 | 0.21174 | 0.29201 | 0.31738
0.1954 | 0.21172 | 0.29194 | 0.31734
0.19539 | 0.2117 | 0.29188 | 0.31731
0.19536 | 0.21168 | 0.29185 | 0.31728
0.19535 | 0.21166 | 0.2918 | 0.31726
0.19532 | 0.21164 | 0.29177 | 0.3172
0.1953 | 0.21161 | 0.29171 | 0.31715
0.19528 | 0.21158 | 0.29168 | 0.31711
0.19524 | 0.21155 | 0.29165 | 0.31708
0.19523 | 0.21152 | 0.2916 | 0.31704
0.1952 | 0.2115 | 0.29156 | 0.317
0.19518 | 0.21147 | 0.29152 | 0.31698
0.19514 | 0.21143 | 0.29149 | 0.31695
0.1951 | 0.2114 | 0.29142 | 0.31693
0.19507 | 0.21138 | 0.29138 | 0.31689
0.19504 | 0.21135 | 0.29134 | 0.31686
0.19501 | 0.21132 | 0.29129 | 0.31681
0.19499 | 0.21126 | 0.29127 | 0.31677
0.19494 | 0.21122 | 0.29122 | 0.31676
0.19491 | 0.21119 | 0.29117 | 0.31673
0.19488 | 0.21116 | 0.29112 | 0.3167
0.19486 | 0.21114 | 0.2911 | 0.31667
0.19483 | 0.21109 | 0.29108 | 0.31665
0.1948 | 0.21107 | 0.29103 | 0.31661
0.19479 | 0.21104 | 0.29095 | 0.3166
0.19475 | 0.21102 | 0.2909 | 0.31656
0.19473 | 0.211 | 0.29083 | 0.31651
0.1947 | 0.21096 | 0.29079 | 0.31648
0.19467 | 0.21094 | 0.29074 | 0.31645
0.19463 | 0.21091 | 0.29069 | 0.31641
0.19461 | 0.21088 | 0.29067 | 0.31637
0.19459 | 0.21085 | 0.29064 | 0.31632
0.19457 | 0.21083 | 0.29062 | 0.3163
0.19454 | 0.21079 | 0.29059 | 0.31626
0.19452 | 0.21077 | 0.29053 | 0.31621
0.1945 | 0.21075 | 0.2905 | 0.31616
0.19448 | 0.21072 | 0.29046 | 0.31611
0.19446 | 0.2107 | 0.29041 | 0.31607
0.19443 | 0.21067 | 0.29038 | 0.31604
0.19441 | 0.21065 | 0.29032 | 0.31599
0.1944 | 0.21059 | 0.29028 | 0.31595
0.19437 | 0.21057 | 0.29024 | 0.31589
0.19433 | 0.21055 | 0.29021 | 0.3158
0.19428 | 0.21049 | 0.29014 | 0.31577
0.19426 | 0.21047 | 0.29011 | 0.31573
0.19422 | 0.21045 | 0.29006 | 0.31569
0.19421 | 0.21041 | 0.29 | 0.31567
0.19418 | 0.21039 | 0.28996 | 0.31562
0.19415 | 0.21036 | 0.28992 | 0.31556
0.19412 | 0.21034 | 0.28989 | 0.31554
0.1941 | 0.21032 | 0.28983 | 0.31547
0.19407 | 0.21029 | 0.28979 | 0.31543
0.19403 | 0.21026 | 0.28973 | 0.31538
0.19401 | 0.21023 | 0.28968 | 0.31534
0.19398 | 0.21019 | 0.28963 | 0.31531
0.19396 | 0.21017 | 0.28958 | 0.31527
0.19392 | 0.21014 | 0.28955 | 0.31522
0.1939 | 0.2101 | 0.2895 | 0.31519
0.19388 | 0.21007 | 0.28945 | 0.31511
0.19386 | 0.21003 | 0.28941 | 0.31505
0.19382 | 0.21 | 0.28935 | 0.315
0.1938 | 0.20996 | 0.28931 | 0.31495
0.19377 | 0.20993 | 0.28924 | 0.31488
0.19372 | 0.20988 | 0.28918 | 0.31485
0.1937 | 0.20986 | 0.28909 | 0.31481
0.19367 | 0.20983 | 0.28905 | 0.31477
0.19363 | 0.20979 | 0.28896 | 0.3147
0.19361 | 0.20977 | 0.28893 | 0.31466
0.19355 | 0.20974 | 0.28888 | 0.31464
0.19353 | 0.2097 | 0.28882 | 0.31459
0.19348 | 0.20969 | 0.28878 | 0.31455
0.19344 | 0.20965 | 0.28874 | 0.31449
0.19341 | 0.20963 | 0.28872 | 0.31442
0.19338 | 0.2096 | 0.28866 | 0.31438
0.19334 | 0.20958 | 0.2886 | 0.31432
0.19331 | 0.20956 | 0.28857 | 0.31428
0.19329 | 0.20951 | 0.28851 | 0.31421
0.19326 | 0.20948 | 0.28845 | 0.31419
0.19323 | 0.20945 | 0.28842 | 0.31412
0.19321 | 0.20941 | 0.28836 | 0.31407
0.19318 | 0.20936 | 0.2883 | 0.31404
0.19317 | 0.20934 | 0.28825 | 0.31401
0.19314 | 0.2093 | 0.28819 | 0.31397
0.19313 | 0.20925 | 0.28816 | 0.31394
0.19308 | 0.20923 | 0.28811 | 0.31389
0.19306 | 0.2092 | 0.28807 | 0.31387
0.19304 | 0.20918 | 0.28802 | 0.31381
0.19302 | 0.20915 | 0.28796 | 0.31379
0.19299 | 0.20912 | 0.28793 | 0.31373
0.19297 | 0.20908 | 0.28789 | 0.31367
0.19294 | 0.20901 | 0.28784 | 0.31363
0.19291 | 0.20899 | 0.28777 | 0.31356
0.19286 | 0.20895 | 0.28774 | 0.31354
0.19284 | 0.20893 | 0.2877 | 0.31349
0.19282 | 0.20887 | 0.28765 | 0.31345
0.19281 | 0.20882 | 0.28756 | 0.31339
0.19278 | 0.20877 | 0.28753 | 0.31332
0.19274 | 0.20874 | 0.2875 | 0.31327
0.19272 | 0.20871 | 0.28745 | 0.31324
0.19269 | 0.20868 | 0.28741 | 0.31321
0.19266 | 0.20864 | 0.28737 | 0.31315
0.19262 | 0.20863 | 0.28733 | 0.31312
0.1926 | 0.20859 | 0.28725 | 0.31306
0.19255 | 0.20854 | 0.28718 | 0.31302
0.1925 | 0.2085 | 0.28713 | 0.31296
0.19248 | 0.20847 | 0.2871 | 0.31291
0.19246 | 0.20842 | 0.28707 | 0.31288
0.19245 | 0.20839 | 0.287 | 0.31282
0.19241 | 0.20837 | 0.28695 | 0.31273
0.1924 | 0.20833 | 0.28691 | 0.31269
0.19237 | 0.20829 | 0.28685 | 0.31262
0.19234 | 0.20826 | 0.28682 | 0.31258
0.1923 | 0.20823 | 0.28676 | 0.31253
0.19227 | 0.20818 | 0.28674 | 0.31249
0.19223 | 0.20815 | 0.28669 | 0.31243
0.19221 | 0.20812 | 0.28665 | 0.3124
0.19215 | 0.20809 | 0.28659 | 0.31233
0.19212 | 0.20805 | 0.28654 | 0.31225
0.19208 | 0.20801 | 0.28652 | 0.31223
0.19205 | 0.20798 | 0.28647 | 0.31218
0.19202 | 0.20795 | 0.28643 | 0.31212
0.19199 | 0.20792 | 0.28633 | 0.31209
0.19195 | 0.20786 | 0.28627 | 0.31205
0.19191 | 0.20785 | 0.28617 | 0.31197
0.19186 | 0.2078 | 0.2861 | 0.31187
0.19184 | 0.20775 | 0.28605 | 0.31179
0.1918 | 0.20772 | 0.28599 | 0.31175
0.19176 | 0.20762 | 0.28597 | 0.31167
0.19172 | 0.20758 | 0.28593 | 0.31161
0.19169 | 0.20754 | 0.2859 | 0.31156
0.19164 | 0.20747 | 0.28585 | 0.3115
0.19159 | 0.20744 | 0.28578 | 0.31147
0.19155 | 0.20737 | 0.28573 | 0.31142
0.19151 | 0.20734 | 0.28564 | 0.31137
0.19148 | 0.20732 | 0.28559 | 0.31129
0.19145 | 0.20727 | 0.28555 | 0.31122
0.19142 | 0.20723 | 0.2855 | 0.31115
0.19138 | 0.20715 | 0.28546 | 0.31106
0.19132 | 0.20709 | 0.28542 | 0.31102
0.19128 | 0.20706 | 0.28537 | 0.31098
0.19124 | 0.207 | 0.28532 | 0.31094
0.1912 | 0.20694 | 0.28528 | 0.3108
0.19116 | 0.20688 | 0.28526 | 0.31075
0.19112 | 0.20684 | 0.28523 | 0.31073
0.19108 | 0.20673 | 0.28521 | 0.31065
0.19104 | 0.20668 | 0.28515 | 0.31061
0.191 | 0.20663 | 0.2851 | 0.31057
0.19097 | 0.20659 | 0.28505 | 0.31053
0.19093 | 0.20656 | 0.28501 | 0.31048
0.1909 | 0.20651 | 0.28495 | 0.31045
0.19087 | 0.20643 | 0.28491 | 0.31039
0.19085 | 0.20638 | 0.28483 | 0.31034
0.1908 | 0.2063 | 0.28478 | 0.3103
0.19076 | 0.20621 | 0.28473 | 0.31021
0.1907 | 0.20613 | 0.28467 | 0.31016
0.19066 | 0.20608 | 0.28462 | 0.31004
0.19063 | 0.206 | 0.28457 | 0.30998
0.19059 | 0.20594 | 0.28454 | 0.30994
0.19051 | 0.20588 | 0.28449 | 0.30986
0.19049 | 0.20583 | 0.28445 | 0.30981
0.19042 | 0.2058 | 0.28439 | 0.30974
0.19039 | 0.20575 | 0.28431 | 0.30966
0.19035 | 0.2057 | 0.28421 | 0.30962
0.19032 | 0.20567 | 0.28417 | 0.30954
0.19027 | 0.20561 | 0.28407 | 0.30952
0.19023 | 0.20553 | 0.28401 | 0.30947
0.19018 | 0.20547 | 0.28392 | 0.30942
0.19015 | 0.20543 | 0.28387 | 0.30938
0.19004 | 0.20538 | 0.2838 | 0.30932
0.18999 | 0.20532 | 0.28373 | 0.30927
0.18994 | 0.20527 | 0.28369 | 0.30923
0.18988 | 0.2052 | 0.28363 | 0.30918
0.18985 | 0.20518 | 0.28358 | 0.30912
0.1898 | 0.20515 | 0.28351 | 0.30908
0.18974 | 0.20498 | 0.28344 | 0.30902
0.18967 | 0.20495 | 0.28341 | 0.30892
0.18964 | 0.20489 | 0.28335 | 0.30887
0.18959 | 0.20483 | 0.28333 | 0.30877
0.18952 | 0.20478 | 0.28331 | 0.30869
0.18945 | 0.20473 | 0.28329 | 0.30864
0.18941 | 0.20464 | 0.28321 | 0.30861
0.18937 | 0.2046 | 0.28316 | 0.30855
0.18934 | 0.20449 | 0.28314 | 0.30847
0.18927 | 0.20439 | 0.28307 | 0.30843
0.18923 | 0.20431 | 0.283 | 0.30839
0.18911 | 0.20424 | 0.28295 | 0.30831
0.18905 | 0.20417 | 0.28289 | 0.30825
0.18894 | 0.20412 | 0.28284 | 0.30817
0.18889 | 0.20408 | 0.28277 | 0.3081
0.18883 | 0.20398 | 0.28274 | 0.30805
0.18878 | 0.2039 | 0.28269 | 0.30799
0.18873 | 0.20384 | 0.28264 | 0.30795
0.1887 | 0.20376 | 0.28261 | 0.30792
0.1886 | 0.20369 | 0.28256 | 0.30787
0.18852 | 0.2036 | 0.28251 | 0.30775
0.18842 | 0.20352 | 0.28244 | 0.30771
0.18831 | 0.20348 | 0.28234 | 0.30765
0.18829 | 0.2034 | 0.28231 | 0.3076
0.18822 | 0.20335 | 0.28228 | 0.30746
0.18818 | 0.20328 | 0.28222 | 0.30743
0.18811 | 0.20321 | 0.28215 | 0.30737
0.18807 | 0.20314 | 0.2821 | 0.30732
0.18802 | 0.20306 | 0.28205 | 0.30726
0.18794 | 0.20299 | 0.28198 | 0.30721
0.18785 | 0.2029 | 0.28193 | 0.30717
0.18779 | 0.20283 | 0.28191 | 0.30711
0.18776 | 0.20279 | 0.28188 | 0.30699
0.18768 | 0.2026 | 0.28183 | 0.30692
0.18765 | 0.20256 | 0.28179 | 0.30686
0.18762 | 0.20247 | 0.2817 | 0.3068
0.18756 | 0.20236 | 0.28161 | 0.30676
0.18753 | 0.20225 | 0.28156 | 0.30672
0.18738 | 0.20207 | 0.28146 | 0.30664
0.18733 | 0.20194 | 0.28139 | 0.3066
0.18727 | 0.20184 | 0.28134 | 0.30654
0.18722 | 0.20168 | 0.28128 | 0.30647
0.18718 | 0.20161 | 0.28124 | 0.30641
0.18709 | 0.20152 | 0.2812 | 0.3063
0.18698 | 0.20146 | 0.28113 | 0.30626
0.18695 | 0.20139 | 0.2811 | 0.30614
0.18689 | 0.20131 | 0.28103 | 0.30607
0.18677 | 0.20125 | 0.28098 | 0.30601
0.18672 | 0.2012 | 0.28094 | 0.30592
0.1867 | 0.20109 | 0.28085 | 0.30589
0.18666 | 0.20102 | 0.2808 | 0.30577
0.18661 | 0.20096 | 0.2807 | 0.30572
0.18654 | 0.20087 | 0.28063 | 0.30567
0.18647 | 0.20076 | 0.28055 | 0.30559
0.18641 | 0.20061 | 0.28047 | 0.30551
0.18635 | 0.20055 | 0.28043 | 0.30541
0.18623 | 0.20042 | 0.28034 | 0.30533
0.18613 | 0.20037 | 0.28031 | 0.30526
0.18607 | 0.20028 | 0.28018 | 0.3052
0.18601 | 0.20021 | 0.28013 | 0.30514
0.18597 | 0.20014 | 0.2801 | 0.30502
0.18585 | 0.19998 | 0.28001 | 0.30496
0.18572 | 0.19987 | 0.27987 | 0.30486
0.18561 | 0.19975 | 0.27978 | 0.30478
0.1855 | 0.19963 | 0.27971 | 0.30471
0.18545 | 0.19952 | 0.27964 | 0.30461
0.18537 | 0.19946 | 0.27959 | 0.30453
0.18529 | 0.19928 | 0.27944 | 0.30443
0.18523 | 0.19919 | 0.27937 | 0.30439
0.18515 | 0.1991 | 0.27928 | 0.30432
0.18512 | 0.19895 | 0.27924 | 0.30421
0.18501 | 0.1988 | 0.27914 | 0.3041
0.18493 | 0.19873 | 0.27905 | 0.30405
0.18483 | 0.19863 | 0.27898 | 0.30398
0.1847 | 0.19849 | 0.27891 | 0.30387
0.18459 | 0.19843 | 0.27888 | 0.3038
0.18448 | 0.19832 | 0.27873 | 0.30364
0.18441 | 0.19823 | 0.2787 | 0.30359
0.18434 | 0.19812 | 0.2786 | 0.30345
0.18412 | 0.19801 | 0.27852 | 0.30342
0.18392 | 0.19796 | 0.27847 | 0.30333
0.18386 | 0.19783 | 0.2784 | 0.3032
0.18377 | 0.19772 | 0.27834 | 0.3031
0.18367 | 0.19758 | 0.27827 | 0.30302
0.18357 | 0.19746 | 0.2782 | 0.30296
0.18337 | 0.19741 | 0.27816 | 0.30289
0.18329 | 0.19718 | 0.27805 | 0.30282
0.18308 | 0.19689 | 0.278 | 0.30277
0.18289 | 0.19667 | 0.27784 | 0.30266
0.1825 | 0.19624 | 0.27778 | 0.30254
0.18243 | 0.19614 | 0.27771 | 0.30247
0.18238 | 0.19598 | 0.27768 | 0.3024
0.18216 | 0.1958 | 0.27765 | 0.30232
0.1821 | 0.19555 | 0.27759 | 0.30216
0.18207 | 0.19551 | 0.27749 | 0.30211
0.18201 | 0.1954 | 0.27736 | 0.30206
0.18198 | 0.19534 | 0.27731 | 0.30198
0.18181 | 0.1953 | 0.27719 | 0.30192
0.18172 | 0.19526 | 0.27713 | 0.30183
0.18167 | 0.1952 | 0.27707 | 0.30169
0.18161 | 0.19506 | 0.27701 | 0.30163
0.18156 | 0.19501 | 0.27693 | 0.30154
0.18151 | 0.19494 | 0.27689 | 0.30139
0.18142 | 0.1948 | 0.2768 | 0.3013
0.1813 | 0.19472 | 0.27674 | 0.3012
0.18126 | 0.19464 | 0.27667 | 0.30115
0.18118 | 0.19457 | 0.27655 | 0.30101
0.18115 | 0.19438 | 0.27646 | 0.30088
0.18109 | 0.19418 | 0.27635 | 0.30077
0.18101 | 0.19407 | 0.27627 | 0.30066
0.18092 | 0.19394 | 0.2762 | 0.30053
0.18083 | 0.19385 | 0.27615 | 0.30043
0.18076 | 0.19381 | 0.27606 | 0.30036
0.18073 | 0.19372 | 0.27601 | 0.30021
0.18057 | 0.1936 | 0.27595 | 0.30011
0.18053 | 0.19354 | 0.27587 | 0.30002
0.18038 | 0.19345 | 0.27576 | 0.29991
0.18022 | 0.19335 | 0.27572 | 0.29979
0.18014 | 0.19327 | 0.27565 | 0.29969
0.1801 | 0.19319 | 0.27554 | 0.29958
0.17996 | 0.19299 | 0.27548 | 0.2995
0.17987 | 0.1929 | 0.27536 | 0.29932
0.1795 | 0.19284 | 0.27522 | 0.29925
0.1794 | 0.19272 | 0.27513 | 0.29912
0.17937 | 0.1927 | 0.27506 | 0.29901
0.17929 | 0.19251 | 0.27499 | 0.29891
0.17925 | 0.19247 | 0.27491 | 0.29875
0.1792 | 0.19241 | 0.27479 | 0.29859
0.17913 | 0.19238 | 0.27471 | 0.29838
0.17906 | 0.19231 | 0.2746 | 0.29831
0.17883 | 0.19207 | 0.27443 | 0.29823
0.17871 | 0.19203 | 0.27433 | 0.29813
0.17863 | 0.19187 | 0.27423 | 0.29807
0.17852 | 0.19181 | 0.27414 | 0.29795
0.17845 | 0.19171 | 0.27403 | 0.29786
0.1784 | 0.19166 | 0.27395 | 0.2977
0.17817 | 0.19146 | 0.27388 | 0.29753
0.17801 | 0.19135 | 0.27375 | 0.29745
0.17786 | 0.1913 | 0.27363 | 0.29732
0.17779 | 0.19126 | 0.27351 | 0.29724
0.17774 | 0.19105 | 0.27341 | 0.29716
0.17765 | 0.19098 | 0.27337 | 0.29702
0.17749 | 0.19091 | 0.27324 | 0.29688
0.17745 | 0.1907 | 0.27311 | 0.2968
0.17725 | 0.19055 | 0.27302 | 0.29657
0.17716 | 0.19048 | 0.27289 | 0.29638
0.17714 | 0.19023 | 0.27278 | 0.29633
0.17692 | 0.19013 | 0.27267 | 0.29626
0.17673 | 0.19006 | 0.27253 | 0.29618
0.17667 | 0.18998 | 0.2725 | 0.29613
0.17654 | 0.18991 | 0.27236 | 0.29599
0.17642 | 0.18982 | 0.27219 | 0.29588
0.17629 | 0.18961 | 0.272 | 0.29567
0.17621 | 0.18948 | 0.2719 | 0.29559
0.17596 | 0.18938 | 0.27179 | 0.29545
0.17575 | 0.18916 | 0.27162 | 0.29531
0.17552 | 0.18897 | 0.27148 | 0.29523
0.17543 | 0.18889 | 0.27134 | 0.29517
0.17537 | 0.18865 | 0.2712 | 0.29505
0.17517 | 0.18834 | 0.27109 | 0.29497
0.17476 | 0.18818 | 0.27103 | 0.29484
0.17456 | 0.18798 | 0.27092 | 0.2947
0.17434 | 0.18791 | 0.27075 | 0.29454
0.17415 | 0.18789 | 0.27064 | 0.29437
0.17401 | 0.18767 | 0.27049 | 0.29427
0.1738 | 0.18707 | 0.27042 | 0.29418
0.17347 | 0.18665 | 0.27028 | 0.29406
0.17331 | 0.18641 | 0.27019 | 0.29387
0.17319 | 0.18595 | 0.26995 | 0.29368
0.17318 | 0.18588 | 0.26986 | 0.29353
0.17293 | 0.18578 | 0.26976 | 0.2934
0.17283 | 0.18565 | 0.26962 | 0.29326
0.17265 | 0.18536 | 0.2695 | 0.29311
0.17249 | 0.18526 | 0.26932 | 0.29303
0.17219 | 0.18493 | 0.26923 | 0.29291
0.17204 | 0.18464 | 0.26907 | 0.29282
0.17194 | 0.1843 | 0.26889 | 0.29269
0.17179 | 0.18417 | 0.26872 | 0.29252
0.1716 | 0.18395 | 0.26853 | 0.29239
0.17119 | 0.18364 | 0.26821 | 0.2923
0.17107 | 0.1834 | 0.26808 | 0.29214
0.17087 | 0.18311 | 0.26792 | 0.2919
0.17069 | 0.18297 | 0.26778 | 0.29168
0.17069 | 0.18279 | 0.26759 | 0.29152
0.1705 | 0.18247 | 0.26749 | 0.29137
0.1702 | 0.18225 | 0.2671 | 0.29111
0.17002 | 0.1822 | 0.26691 | 0.29094
0.16959 | 0.18183 | 0.26659 | 0.29054
0.16946 | 0.18178 | 0.26637 | 0.29021
0.16919 | 0.18156 | 0.26609 | 0.29002
0.16867 | 0.18134 | 0.26562 | 0.28989
0.16854 | 0.1811 | 0.26528 | 0.28946
0.16839 | 0.18099 | 0.26503 | 0.28906
0.16805 | 0.18041 | 0.26459 | 0.28853
0.16768 | 0.18033 | 0.26403 | 0.2884
0.16705 | 0.1799 | 0.26355 | 0.2877
0.16688 | 0.1796 | 0.26286 | 0.28754
0.16669 | 0.17953 | 0.26255 | 0.28706
0.16625 | 0.17893 | 0.26213 | 0.28664
0.16596 | 0.17854 | 0.2617 | 0.28629
0.16566 | 0.17806 | 0.26127 | 0.28592
0.16529 | 0.17711 | 0.2599 | 0.28483
0.16499 | 0.17684 | 0.25962 | 0.28418
0.16437 | 0.17668 | 0.25937 | 0.2841
0.16354 | 0.1759 | 0.25912 | 0.28343
0.16339 | 0.17523 | 0.25274 | 0.27716
0.1619 | 0.1741 | 0.24966 | 0.27428
0.1584 | 0.17049 | 0.24948 | 0.27375
0.1481 | 0.15823 | 0.24907 | 0.27318
0.14746 | 0.15779 | 0.24875 | 0.2729
0.14718 | 0.15739 | 0.24748 | 0.27156
0.14673 | 0.15671 | 0.2469 | 0.27141
0.14621 | 0.15614 | 0.24617 | 0.2705
0.14448 | 0.15577 | 0.24585 | 0.27022
0.14429 | 0.15437 | 0.2449 | 0.2694
0.13924 | 0.15066 | 0.24444 | 0.26914
0.13885 | 0.14983 | 0.24293 | 0.26757
0.13758 | 0.14786 | 0.24197 | 0.26667
0.13642 | 0.14729 | 0.23854 | 0.26311
0.13142 | 0.13908 | 0.23688 | 0.26164
0.13094 | 0.1368 | 0.2357 | 0.26078
0.12878 | 0.13494 | 0.22618 | 0.24981
0.12785 | 0.13396 | 0.22602 | 0.24947
0.1265 | 0.13316 | 0.22442 | 0.24777
0.1231 | 0.13001 | 0.2241 | 0.24719
0.12131 | 0.12786 | 0.22309 | 0.24621
0.11851 | 0.12491 | 0.22223 | 0.24577
0.11579 | 0.12293 | 0.21852 | 0.24198
0.11094 | 0.11753 | 0.21779 | 0.24122
0.10865 | 0.11631 | 0.21569 | 0.23871
0.10795 | 0.1145 | 0.21407 | 0.23671
0.10275 | 0.10935 | 0.21136 | 0.23365
0.099416 | 0.10678 | 0.19979 | 0.223
0.064039 | 0.066994 | 0.19891 | 0.22164
0.063629 | 0.066734 | 0.19605 | 0.21736
0.056039 | 0.058996 | 0.19428 | 0.21651
|  | 0.19292 | 0.2144
|  | 0.17386 | 0.1929
|  | 0.16541 | 0.18505
|  | 0.15191 | 0.17019
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0

## Misc_calcs
United Energy
Lower Mornington Peninsula supply area
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 4 | TRUE
| Option 3 | 4 | TRUE
| Option 4 |  | TRUE
| Option 5 | Not used | FALSE
| First year | 4
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
United Energy
Lower Mornington Peninsula supply area
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | FALSE |  |  | FALSE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
United Energy
| Reliability in worst-served areas | per MWh | 0
| Network resilience | per MWh | 38562.334
| Enabling solar exports | per MWh | 862.6028
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.34751
| Customer value of time - business | per minute customer time | 0.34751
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020