## Cover
United Energy
Regulatory proposal 2026-31
EW transformer
| Model number: | 4.01
2025-01-31
15

## Summary
United Energy
EW transformer replacement
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | Replace transformer #2 completed in 2028-2029 |  | -2.4452 | 3.9407 | 1.4955
| Option 3 | Refurbish transformer #2 completed in 2027-2028 |  | -0.52847 | 1.4499 | 0.92138
| Option 4 | 0
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | Replace transformer #2 completed in 2028-2029 |  | 1.4955
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 0 | 1.5407 | 3.0814 | 0 | 0 |  | 4.6221
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
Capex and risk ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 1.4955 | 0.92138 |  |  |  | Option 2
| Capex 10% higher |  | 0 | 1.251 | 0.86854 |  |  |  | Option 2
| Capex 10% lower |  | 0 | 1.74 | 0.97423 |  |  |  | Option 2
| Total benefits 10% higher |  | 0 | 1.8896 | 1.0664 |  |  |  | Option 2
| Total benefits 10% lower |  | 0 | 1.1014 | 0.7764 |  |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | 0.85689 | 0.72355 |  |  |  | Option 2
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
United Energy
EW transformer replacement
Project
|  | Business: |  | United Energy
|  | Descripton: |  | EW transformer replacement
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | Replace transformer #2 completed in 2028-2029
|  | Option 3 |  | Refurbish transformer #2 completed in 2027-2028
Option 4
Option 5
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | EW |  | Elwood | 32343.3946 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 0 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 38560 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 862.6028 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.34751 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.34751 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
United Energy
EW transformer replacement
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 32343.3946 | 2023-12-31 |  | 118694.3988 | 126511.5012 | 135871.4645 | 143387.5264 | 150590.5028 | 159321.5275 | 169604.1304 | 180835.6038 | 189773.0263 | 194795.8685 | 199873.9792 | 205007.1714 | 210195.2632 | 215438.0773 | 220735.4411 | 226087.1864 | 231493.1491 | 236953.1696 | 242467.0921 | 248034.7648 | 253656.0398 | 259330.7727 | 265058.8228 | 270840.0531 | 276674.3297
| Safety consequence | (after DF) |  | 2023-12-31 |  | 471.4924 | 485.6406 | 499.9606 | 514.4516 | 529.1126 | 543.9429 | 558.9415 | 574.1077 | 589.4407 | 604.9397 | 620.604 | 636.4328 | 652.4254 | 668.5811 | 684.8991 | 701.3788 | 718.0195 | 734.8206 | 751.7814 | 768.9011 | 786.1794 | 803.6154 | 803.6154 | 803.6154 | 803.6154
| Unplanned replacement risk |  |  | 2023-12-31 |  | 13240.0796 | 13637.3796 | 14039.5039 | 14446.4277 | 14858.1268 | 15274.5778 | 15695.7573 | 16121.6429 | 16552.2123 | 16987.4438 | 17427.316 | 17871.8081 | 18320.8996 | 18774.5704 | 19232.8008 | 19695.5714 | 20162.8632 | 20634.6575 | 21110.936 | 21591.6806 | 22076.8738 | 22566.4979 | 22566.4979 | 22566.4979 | 22566.4979
| Unplanned fault risk | (after DF) |  | 2023-12-31 |  | 1804.3769 | 1858.5216 | 1913.3236 | 1968.7798 | 2024.8867 | 2081.6412 | 2139.0402 | 2197.0805 | 2255.7591 | 2315.0731 | 2375.0195 | 2435.5955 | 2496.7983 | 2558.6252 | 2621.0735 | 2684.1406 | 2747.8238 | 2812.1206 | 2877.0285 | 2942.545 | 3008.6679 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945
| Unplanned environmental risk |  |  | 2023-12-31 |  | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 253073.3477 | 261356.043 | 271187.2527 | 279180.1854 | 286865.629 | 296084.6894 | 306860.8694 | 318591.4349 | 328033.4383 | 333566.325 | 339159.9186 | 344814.0078 | 350528.3865 | 356302.854 | 362137.2146 | 368031.2772 | 373984.8556 | 379997.7683 | 386069.8379 | 392200.8917 | 398390.7607 | 404639.2804 | 410367.3306 | 416148.5609 | 421982.8375
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38560 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
United Energy
EW transformer replacement
OPTION 2 | Replace transformer #2 completed in 2028-2029
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Replace 1 transformer |  | 50 | 2023-12-31 | 0 | 1384390.1633 | 2768780.3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 1384390.1633 | 2768780.3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 32343.3946 | 2023-12-31 | 118694.3988 | 126511.5012 | 135871.4645 | 4392.5682 | 8199.1715 | 12075.6659 | 16193.9044 | 20594.1949 | 24903.5229 | 28764.6325 | 32640.793 | 36539.8816 | 40467.6843 | 44428.5775 | 48425.9478 | 52462.4637 | 56540.2592 | 60661.0606 | 64826.2785 | 69037.0745 | 73294.4112 | 77599.0905 | 81951.7828 | 86353.0503 | 90803.3652
| Safety consequence | (after DF) |  | 2023-12-31 | 471.4924 | 485.6406 | 499.9606 | 257.4698 | 265.3492 | 273.5511 | 282.0468 | 290.8183 | 299.8527 | 309.1398 | 318.6717 | 328.4415 | 338.4436 | 348.6727 | 359.1245 | 369.795 | 380.6806 | 391.7779 | 403.0839 | 414.5959 | 426.3113 | 438.2276 | 438.2276 | 438.2276 | 438.2276
| Unplanned replacement risk |  |  | 2023-12-31 | 13240.0796 | 13637.3796 | 14039.5039 | 7230.0668 | 7451.3285 | 7681.6476 | 7920.2181 | 8166.533 | 8420.2282 | 8681.0228 | 8948.6896 | 9223.0387 | 9503.9076 | 9791.1546 | 10084.6544 | 10384.2947 | 10689.9742 | 11001.6003 | 11319.088 | 11642.3589 | 11971.3401 | 12305.9636 | 12305.9636 | 12305.9636 | 12305.9636
| Unplanned fault risk | (after DF) |  | 2023-12-31 | 1804.3769 | 1858.5216 | 1913.3236 | 985.3238 | 1015.4777 | 1046.8659 | 1079.3786 | 1112.9468 | 1147.5207 | 1183.0622 | 1219.5402 | 1256.9289 | 1295.2061 | 1334.3525 | 1374.3511 | 1415.1865 | 1456.8449 | 1499.3138 | 1542.5815 | 1586.6373 | 1631.4713 | 1677.0743 | 1677.0743 | 1677.0743 | 1677.0743
| Unplanned environmental risk |  |  | 2023-12-31 | 118863 | 118863 | 118863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 253073.3477 | 261356.043 | 271187.2527 | 12865.4286 | 16931.3269 | 21077.7306 | 25475.548 | 30164.493 | 34771.1245 | 38937.8573 | 43127.6945 | 47348.2907 | 51605.2415 | 55902.7573 | 60244.0778 | 64631.74 | 69067.7589 | 73553.7525 | 78091.0319 | 82680.6666 | 87323.5339 | 92020.3559 | 96373.0482 | 100774.3157 | 105224.6306
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38560 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - residential | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - business | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 266314.7569 | 269934.3021 | 275006.9588 | 281385.3215 | 288426.9419 | 293262.3139 | 294628.4677 | 296032.2241 | 297465.7171 | 298923.145 | 300400.0968 | 301893.1368 | 303399.5372 | 304917.0967 | 306444.0158 | 307978.806 | 309520.225 | 311067.2268 | 312618.9245 | 313994.2824 | 315374.2452 | 316758.2069
Capital expenditure
| Replace 1 transformer |  |  | 2023-12-31 | 0 | -1384390.1633 | -2768780.3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Replace 1 transformer |  |  | 2023-12-31 | 0 | -1384390.1633 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49 | -4153170.49
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Replace 1 transformer |  |  | 2023-12-31 | 0 | 0 | -59021.6882 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | -59021.6882 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | -59021.6882 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 266314.7569 | 269934.3021 | 275006.9588 | 281385.3215 | 288426.9419 | 293262.3139 | 294628.4677 | 296032.2241 | 297465.7171 | 298923.145 | 300400.0968 | 301893.1368 | 303399.5372 | 304917.0967 | 306444.0158 | 307978.806 | 309520.225 | 311067.2268 | 312618.9245 | 313994.2824 | 315374.2452 | 316758.2069
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | -59021.6882 | 89249.6924 | 92869.2376 | 97941.8943 | 104320.257 | 111361.8775 | 116197.2494 | 117563.4033 | 118967.1596 | 120400.6526 | 121858.0806 | 123335.0323 | 124828.0724 | 126334.4727 | 127852.0323 | 129378.9513 | 130913.7416 | 132455.1606 | 134002.1623 | 135553.8601 | 136929.2179 | 138309.1807 | 139693.1425
| First capex year |  |  | 2
| First year |  |  | 2
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | 0 | -59021.6882 | 89249.6924 | 92869.2376 | 97941.8943 | 104320.257 | 111361.8775 | 116197.2494 | 117563.4033 | 118967.1596 | 120400.6526 | 121858.0806 | 123335.0323 | 124828.0724 | 126334.4727 | 127852.0323 | 129378.9513 | 130913.7416 | 132455.1606 | 134002.1623 | 135553.8601 | 136929.2179 | 138309.1807 | 139693.1425
| Total annualised capex |  |  |  | 0 | 0 | -59021.6882 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645 | -177065.0645
| Total benefits |  |  |  | 0 | 0 | 0 | 266314.7569 | 269934.3021 | 275006.9588 | 281385.3215 | 288426.9419 | 293262.3139 | 294628.4677 | 296032.2241 | 297465.7171 | 298923.145 | 300400.0968 | 301893.1368 | 303399.5372 | 304917.0967 | 306444.0158 | 307978.806 | 309520.225 | 311067.2268 | 312618.9245 | 313994.2824 | 315374.2452 | 316758.2069
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | 0 | -64923.857 | 71543.186 | 75162.7312 | 80235.3879 | 86613.7506 | 93655.371 | 98490.743 | 99856.8968 | 101260.6532 | 102694.1462 | 104151.5741 | 105628.5259 | 107121.5659 | 108627.9663 | 110145.5258 | 111672.4449 | 113207.2351 | 114748.6541 | 116295.6559 | 117847.3536 | 119222.7115 | 120602.6743 | 121986.636
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | 0 | -53119.5193 | 106956.1989 | 110575.7441 | 115648.4008 | 122026.7634 | 129068.3839 | 133903.7559 | 135269.9097 | 136673.6661 | 138107.159 | 139564.587 | 141041.5388 | 142534.5788 | 144040.9792 | 145558.5387 | 147085.4577 | 148620.248 | 150161.667 | 151708.6688 | 153260.3665 | 154635.7244 | 156015.6872 | 157399.6489
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | 0 | -59021.6882 | 115881.1681 | 119862.6678 | 125442.5902 | 132458.7891 | 140204.5717 | 145523.4808 | 147026.25 | 148570.382 | 150147.2243 | 151750.3951 | 153375.042 | 155017.3861 | 156674.4264 | 158343.7419 | 160023.3529 | 161711.6222 | 163407.1831 | 165108.885 | 166815.7525 | 168328.6462 | 169846.6052 | 171368.9632
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | 0 | -59021.6882 | 62618.2167 | 65875.8074 | 70441.1985 | 76181.7249 | 82519.1833 | 86871.018 | 88100.5565 | 89363.9372 | 90654.0809 | 91965.7661 | 93295.0226 | 94638.7587 | 95994.519 | 97360.3226 | 98734.5497 | 100115.861 | 101503.1381 | 102895.4397 | 104291.9676 | 105529.7897 | 106771.7562 | 108017.3218
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | 0 | -64923.857 | 44911.7103 | 48169.301 | 52734.692 | 58475.2184 | 64812.6768 | 69164.5116 | 70394.05 | 71657.4308 | 72947.5745 | 74259.2596 | 75588.5162 | 76932.2522 | 78288.0126 | 79653.8162 | 81028.0433 | 82409.3545 | 83796.6316 | 85188.9332 | 86585.4612 | 87823.2833 | 89065.2498 | 90310.8153
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | -59021.6882 | 89249.6924 | 92869.2376 | 97941.8943 | 104320.257 | 111361.8775 | 116197.2494 | 117563.4033 | 118967.1596 | 120400.6526 | 121858.0806 | 123335.0323 | 124828.0724 | 126334.4727 | 127852.0323 | 129378.9513 | 130913.7416 | 132455.1606 | 134002.1623 | 135553.8601 | 136929.2179 | 138309.1807 | 139693.1425
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | -59021.6882 | 89249.6924 | 92869.2376 | 97941.8943 | 104320.257 | 111361.8775 | 116197.2494 | 117563.4033 | 118967.1596 | 120400.6526 | 121858.0806 | 123335.0323 | 124828.0724 | 126334.4727 | 127852.0323 | 129378.9513 | 130913.7416 | 132455.1606 | 134002.1623 | 135553.8601 | 136929.2179 | 138309.1807 | 139693.1425
sens | 0 | 0% | 0% | Option 2sens | 0 | 0 | -59021.6882 | 89249.6924 | 92869.2376 | 97941.8943 | 104320.257 | 111361.8775 | 116197.2494 | 117563.4033 | 118967.1596 | 120400.6526 | 121858.0806 | 123335.0323 | 124828.0724 | 126334.4727 | 127852.0323 | 129378.9513 | 130913.7416 | 132455.1606 | 134002.1623 | 135553.8601 | 136929.2179 | 138309.1807 | 139693.1425

## Option3
United Energy
EW transformer replacement
OPTION 3 | Refurbish transformer #2 completed in 2027-2028
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Refurbish 1 transformer |  | 10 | 2023-12-31 | 0 | 500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 32343.3946 | 2023-12-31 | 118694.3988 | 126511.5012 | 128862.9506 | 135990.2233 | 142820.4368 | 151099.7183 | 160850.3454 | 171500.6833 | 179975.2143 | 184737.142 | 189551.385 | 194417.7635 | 199336.1023 | 204306.2308 | 209327.9827 | 214401.1958 | 219525.7119 | 224701.377 | 229928.0408 | 235205.5566 | 240533.7814 | 245912.5757 | 251341.8034 | 256821.3318 | 262351.0312
| Safety consequence | (after DF) |  | 2023-12-31 | 471.4924 | 485.6406 | 494.961 | 509.3071 | 523.8215 | 538.5034 | 553.3521 | 568.3666 | 583.5463 | 598.8903 | 614.398 | 630.0685 | 645.9011 | 661.8953 | 678.0501 | 694.365 | 710.8393 | 727.4724 | 744.2635 | 761.2121 | 778.3176 | 795.5792 | 795.5792 | 795.5792 | 795.5792
| Unplanned replacements |  |  | 2023-12-31 | 13240.0796 | 13637.3796 | 13337.5287 | 13724.1063 | 14115.2205 | 14510.8489 | 14910.9695 | 15315.5608 | 15724.6017 | 16138.0716 | 16555.9502 | 16978.2177 | 17404.8547 | 17835.8419 | 18271.1608 | 18710.7928 | 19154.72 | 19602.9246 | 20055.3892 | 20512.0966 | 20973.0301 | 21438.173 | 21438.173 | 21438.173 | 21438.173
| Environmental consequence | (after DF) |  | 2023-12-31 | 1804.3769 | 1858.5216 | 1913.3236 | 1968.7798 | 2024.8867 | 2081.6412 | 2139.0402 | 2197.0805 | 2255.7591 | 2315.0731 | 2375.0195 | 2435.5955 | 2496.7983 | 2558.6252 | 2621.0735 | 2684.1406 | 2747.8238 | 2812.1206 | 2877.0285 | 2942.545 | 3008.6679 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945
| < Other risk - enter description > |  |  | 2023-12-31 | 118863 | 118863 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 253073.3477 | 261356.043 | 174324.514 | 181908.1664 | 189200.1155 | 197946.4619 | 208169.4571 | 219297.4412 | 228254.8713 | 233504.927 | 238812.5026 | 244177.3952 | 249599.4065 | 255078.3433 | 260614.0171 | 266206.2442 | 271854.8451 | 277559.6446 | 283320.472 | 289137.1604 | 295009.5469 | 300937.4724 | 306366.7002 | 311846.2285 | 317375.9279
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38560 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 96862.7387 | 97272.019 | 97665.5135 | 98138.2275 | 98691.4123 | 99293.9937 | 99778.567 | 100061.3981 | 100347.416 | 100636.6126 | 100928.9801 | 101224.5108 | 101523.1974 | 101825.033 | 102130.0106 | 102438.1237 | 102749.3659 | 103063.7313 | 103381.2139 | 103701.808 | 104000.6304 | 104302.3324 | 104606.9096
Capital expenditure
| Refurbish 1 transformer |  |  | 2023-12-31 | 0 | -500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Refurbish 1 transformer |  |  | 2023-12-31 | 0 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | -500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Refurbish 1 transformer |  |  | 2023-12-31 | 0 | 0 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 96862.7387 | 97272.019 | 97665.5135 | 98138.2275 | 98691.4123 | 99293.9937 | 99778.567 | 100061.3981 | 100347.416 | 100636.6126 | 100928.9801 | 101224.5108 | 101523.1974 | 101825.033 | 102130.0106 | 102438.1237 | 102749.3659 | 103063.7313 | 103381.2139 | 103701.808 | 104000.6304 | 104302.3324 | 104606.9096
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 36742.0548 | 37151.3351 | 37544.8296 | 38017.5436 | 38570.7283 | 39173.3098 | 39657.8831 | 39940.7141 | 40226.7321 | 40515.9287 | 100928.9801 | 101224.5108 | 101523.1974 | 101825.033 | 102130.0106 | 102438.1237 | 102749.3659 | 103063.7313 | 103381.2139 | 103701.808 | 104000.6304 | 104302.3324 | 104606.9096
| First capex year |  |  | 2
| First year |  |  | 2
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | 0 | 36742.0548 | 37151.3351 | 37544.8296 | 38017.5436 | 38570.7283 | 39173.3098 | 39657.8831 | 39940.7141 | 40226.7321 | 40515.9287 | 100928.9801 | 101224.5108 | 101523.1974 | 101825.033 | 102130.0106 | 102438.1237 | 102749.3659 | 103063.7313 | 103381.2139 | 103701.808 | 104000.6304 | 104302.3324 | 104606.9096
| Total annualised capex |  |  |  | 0 | 0 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | -60120.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 96862.7387 | 97272.019 | 97665.5135 | 98138.2275 | 98691.4123 | 99293.9937 | 99778.567 | 100061.3981 | 100347.416 | 100636.6126 | 100928.9801 | 101224.5108 | 101523.1974 | 101825.033 | 102130.0106 | 102438.1237 | 102749.3659 | 103063.7313 | 103381.2139 | 103701.808 | 104000.6304 | 104302.3324 | 104606.9096
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | 0 | 30729.9864 | 31139.2667 | 31532.7612 | 32005.4752 | 32558.66 | 33161.2414 | 33645.8147 | 33928.6458 | 34214.6637 | 34503.8603 | 100928.9801 | 101224.5108 | 101523.1974 | 101825.033 | 102130.0106 | 102438.1237 | 102749.3659 | 103063.7313 | 103381.2139 | 103701.808 | 104000.6304 | 104302.3324 | 104606.9096
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | 0 | 42754.1232 | 43163.4035 | 43556.898 | 44029.612 | 44582.7967 | 45185.3782 | 45669.9515 | 45952.7825 | 46238.8004 | 46527.9971 | 100928.9801 | 101224.5108 | 101523.1974 | 101825.033 | 102130.0106 | 102438.1237 | 102749.3659 | 103063.7313 | 103381.2139 | 103701.808 | 104000.6304 | 104302.3324 | 104606.9096
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | 0 | 46428.3286 | 46878.537 | 47311.3809 | 47831.3663 | 48439.8696 | 49102.7091 | 49635.7398 | 49946.854 | 50261.4737 | 50579.5899 | 111021.8781 | 111346.9619 | 111675.5172 | 112007.5363 | 112343.0116 | 112681.936 | 113024.3025 | 113370.1044 | 113719.3352 | 114071.9888 | 114400.6935 | 114732.5656 | 115067.6006
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | 0 | 27055.7809 | 27424.1332 | 27778.2782 | 28203.7208 | 28701.5871 | 29243.9104 | 29680.0264 | 29934.5743 | 30191.9905 | 30452.2674 | 90836.0821 | 91102.0597 | 91370.8777 | 91642.5297 | 91917.0095 | 92194.3113 | 92474.4293 | 92757.3582 | 93043.0925 | 93331.6272 | 93600.5674 | 93872.0991 | 94146.2186
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | 0 | 21043.7125 | 21412.0648 | 21766.2098 | 22191.6524 | 22689.5187 | 23231.842 | 23667.958 | 23922.5059 | 24179.9221 | 24440.199 | 90836.0821 | 91102.0597 | 91370.8777 | 91642.5297 | 91917.0095 | 92194.3113 | 92474.4293 | 92757.3582 | 93043.0925 | 93331.6272 | 93600.5674 | 93872.0991 | 94146.2186
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 36742.0548 | 37151.3351 | 37544.8296 | 38017.5436 | 38570.7283 | 39173.3098 | 39657.8831 | 39940.7141 | 40226.7321 | 40515.9287 | 100928.9801 | 101224.5108 | 101523.1974 | 101825.033 | 102130.0106 | 102438.1237 | 102749.3659 | 103063.7313 | 103381.2139 | 103701.808 | 104000.6304 | 104302.3324 | 104606.9096
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 36742.0548 | 37151.3351 | 37544.8296 | 38017.5436 | 38570.7283 | 39173.3098 | 39657.8831 | 39940.7141 | 40226.7321 | 40515.9287 | 100928.9801 | 101224.5108 | 101523.1974 | 101825.033 | 102130.0106 | 102438.1237 | 102749.3659 | 103063.7313 | 103381.2139 | 103701.808 | 104000.6304 | 104302.3324 | 104606.9096
sens | 0 | 0% | 0% | Option 3sens | 0 | 0 | 36742.0548 | 37151.3351 | 37544.8296 | 38017.5436 | 38570.7283 | 39173.3098 | 39657.8831 | 39940.7141 | 40226.7321 | 40515.9287 | 100928.9801 | 101224.5108 | 101523.1974 | 101825.033 | 102130.0106 | 102438.1237 | 102749.3659 | 103063.7313 | 103381.2139 | 103701.808 | 104000.6304 | 104302.3324 | 104606.9096

## Option4
United Energy
EW transformer replacement
OPTION 4 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 32343.3946 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38560 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option5
United Energy
EW transformer replacement
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 32343.3946 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38560 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
United Energy
EW transformer replacement
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 3617293.0986 | 2026-06-30 |  | 132096.4975 | 140796.2496 | 151213.0712 | 159577.7915 | 167594.075 | 177310.9428 | 188754.5816 | 201254.2304 | 211200.8009 | 216790.7855 | 222442.2791 | 228155.0736 | 233928.9666 | 239763.7607 | 245659.2639 | 251615.2889 | 257631.6532 | 263708.1791 | 269844.6932 | 276041.0265 | 282297.0145 | 288612.4965 | 294987.316 | 301421.3203 | 307914.3605
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 5385463.7905 | 2026-06-30 |  | 281648.5291 | 290866.4454 | 301807.723 | 310703.159 | 319256.3863 | 329516.3952 | 341509.3423 | 354564.4369 | 365072.562 | 371230.1815 | 377455.3626 | 383747.8699 | 390107.4743 | 396533.9522 | 403027.0858 | 409586.6626 | 416212.4754 | 422904.3219 | 429662.0051 | 436485.3323 | 443374.1158 | 450328.1724 | 456702.9919 | 463136.9962 | 469630.0364
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 1041529.5931 | 2026-06-30 |  | 132096.4975 | 140796.2496 | 151213.0712 | 4888.5447 | 9124.9617 | 13439.1613 | 18022.401 | 22919.5399 | 27715.4455 | 32012.5233 | 36326.3513 | 40665.6963 | 45036.9976 | 49445.1257 | 53893.8497 | 58386.1393 | 62924.3695 | 67510.4614 | 72145.9851 | 76832.2333 | 81570.2772 | 86361.0092 | 91205.1755 | 96103.4017 | 101056.2134
Option 2 | Capital expenditure | Option 2Capital expenditure | -4290692.6188 | 2026-06-30 |  | 0 | -1540705.3203 | -3081410.6407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 1444767.3148 | 2026-06-30 |  | 281648.5291 | 290866.4454 | 301807.723 | 14318.0982 | 18843.0878 | 23457.6729 | 28352.0595 | 33570.4457 | 38697.2241 | 43334.4338 | 47997.3567 | 52694.5115 | 57432.1259 | 62214.8856 | 67046.396 | 71929.4808 | 76866.3824 | 81858.9014 | 86908.497 | 92016.3595 | 97183.4653 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -2445212.5523 | 2026-06-30 |  | 0 | 0 | -65685.9832 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | -197057.9495 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 3940696.4757 | 2026-06-30 |  | 0 | 0 | 0 | 296385.0608 | 300413.2985 | 306058.7223 | 313157.2828 | 320993.9912 | 326375.3378 | 327895.7477 | 329458.0059 | 331053.3584 | 332675.3484 | 334319.0667 | 335980.6898 | 337657.1818 | 339346.093 | 341045.4205 | 342753.5081 | 344468.9728 | 346190.6506 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | 0 | -65685.9832 | 99327.1114 | 103355.349 | 109000.7728 | 116099.3333 | 123936.0418 | 129317.3884 | 130837.7982 | 132400.0565 | 133995.4089 | 135617.3989 | 137261.1172 | 138922.7404 | 140599.2324 | 142288.1436 | 143987.4711 | 145695.5586 | 147411.0233 | 149132.7011 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 1495483.9234 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -2445212.5523 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 3940696.4757 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 3444002.4712 | 2026-06-30 |  | 132096.4975 | 140796.2496 | 143413.2074 | 151345.2393 | 158946.6703 | 168160.7874 | 179012.3836 | 190865.2793 | 200296.692 | 205596.3016 | 210954.1335 | 216369.9877 | 221843.6692 | 227374.988 | 232963.7592 | 238609.8022 | 244312.941 | 250073.0042 | 255889.8244 | 261763.2384 | 267693.0872 | 273679.2154 | 279721.4716 | 285819.708 | 291973.7804
Option 3 | Capital expenditure | Option 3Capital expenditure | -528470.2661 | 2026-06-30 |  | 0 | -556456.3232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 3935609.5443 | 2026-06-30 |  | 281648.5291 | 290866.4454 | 194007.9562 | 202447.8989 | 210563.2012 | 220297.1207 | 231674.4214 | 244058.8956 | 254027.7329 | 259870.5862 | 265777.4543 | 271748.1111 | 277782.336 | 283879.914 | 290040.6355 | 296264.2957 | 302550.6951 | 308899.6387 | 315310.9363 | 321784.4023 | 328319.8555 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -528470.2661 | 2026-06-30 |  | 0 | 0 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | -66909.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 1449854.2462 | 2026-06-30 |  | 0 | 0 | 107799.7669 | 108255.2601 | 108693.1851 | 109219.2745 | 109834.9208 | 110505.5413 | 111044.8291 | 111359.5953 | 111677.9083 | 111999.7589 | 112325.1383 | 112654.0382 | 112986.4503 | 113322.3669 | 113661.7803 | 114004.6833 | 114351.0687 | 114700.9299 | 115054.2603 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | 0 | 40890.6974 | 41346.1906 | 41784.1156 | 42310.205 | 42925.8514 | 43596.4718 | 44135.7596 | 44450.5259 | 44768.8388 | 45090.6894 | 112325.1383 | 112654.0382 | 112986.4503 | 113322.3669 | 113661.7803 | 114004.6833 | 114351.0687 | 114700.9299 | 115054.2603 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | 921383.9801 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -528470.2661 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 1449854.2462 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 0 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | 0 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 0 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0.19706 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.28165 | 0.29087 | 0.30181 | 0.3107 | 0.31926 | 0.32952 | 0.34151 | 0.35456 | 0.36507 | 0.37123 | 0.37746 | 0.38375 | 0.39011 | 0.39653 | 0.40303 | 0.40959 | 0.41621 | 0.4229 | 0.42966 | 0.43649 | 0.44337 | 0.45033 | 0.4567 | 0.46314 | 0.46963
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 0.27667 |  |  | Option 1 (base case) risk cost | 0.11869 | 0.12651 | 0.13587 | 0.14339 | 0.15059 | 0.15932 | 0.1696 | 0.18084 | 0.18977 | 0.1948 | 0.19987 | 0.20501 | 0.2102 | 0.21544 | 0.22074 | 0.22609 | 0.23149 | 0.23695 | 0.24247 | 0.24803 | 0.25366 | 0.25933 | 0.26506 | 0.27084 | 0.27667

## Sensitivity_calcs
United Energy
EW transformer replacement
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 145695.5586 | 147411.0233 | 149132.7011 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 1495483.9234 |  | 0 | 0 | 0 | -65685.9832 | 99327.1114 | 103355.349 | 109000.7728 | 116099.3333 | 123936.0418 | 129317.3884 | 130837.7982 | 132400.0565 | 133995.4089 | 135617.3989 | 137261.1172 | 138922.7404 | 140599.2324 | 142288.1436 | 143987.4711 | 145695.5586 | 147411.0233 | 149132.7011 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 1250962.6681 |  | 0 | 0 | 0 | -72254.5815 | 79621.3164 | 83649.5541 | 89294.9779 | 96393.5383 | 104230.2468 | 109611.5934 | 111132.0033 | 112694.2615 | 114289.614 | 115911.604 | 117555.3223 | 119216.9454 | 120893.4374 | 122582.3486 | 124281.6761 | 125989.7636 | 127705.2283 | 129426.9062 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 1740005.1786 |  | 0 | 0 | 0 | -59117.3848 | 119032.9063 | 123061.144 | 128706.5678 | 135805.1282 | 143641.8367 | 149023.1833 | 150543.5932 | 152105.8514 | 153701.2039 | 155323.1939 | 156966.9121 | 158628.5353 | 160305.0273 | 161993.9385 | 163693.266 | 165401.3535 | 167116.8182 | 168838.4961 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 1889553.5709 |  | 0 | 0 | 0 | -65685.9832 | 128965.6175 | 133396.6789 | 139606.645 | 147415.0616 | 156035.4409 | 161954.9221 | 163627.373 | 165345.8571 | 167100.7448 | 168884.9338 | 170693.0239 | 172520.8093 | 174364.9505 | 176222.7529 | 178092.0131 | 179970.9094 | 181857.9206 | 183751.7662 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 1101414.2758 |  | 0 | 0 | 0 | -65685.9832 | 69688.6053 | 73314.0192 | 78394.9006 | 84783.605 | 91836.6426 | 96679.8546 | 98048.2235 | 99454.2559 | 100890.0731 | 102349.8641 | 103829.2105 | 105324.6714 | 106833.5142 | 108353.5343 | 109882.929 | 111420.2078 | 112964.126 | 114513.6361 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | 856893.0206 |  | 0 | 0 | 0 | -72254.5815 | 49982.8104 | 53608.2242 | 58689.1056 | 65077.8101 | 72130.8477 | 76974.0596 | 78342.4285 | 79748.4609 | 81184.2781 | 82644.0691 | 84123.4156 | 85618.8764 | 87127.7192 | 88647.7393 | 90177.1341 | 91714.4128 | 93258.3311 | 94807.8411 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 1495483.9234 |  | 0 | 0 | 0 | -65685.9832 | 99327.1114 | 103355.349 | 109000.7728 | 116099.3333 | 123936.0418 | 129317.3884 | 130837.7982 | 132400.0565 | 133995.4089 | 135617.3989 | 137261.1172 | 138922.7404 | 140599.2324 | 142288.1436 | 143987.4711 | 145695.5586 | 147411.0233 | 149132.7011 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 1495483.9234 |  | 0 | 0 | 0 | -65685.9832 | 99327.1114 | 103355.349 | 109000.7728 | 116099.3333 | 123936.0418 | 129317.3884 | 130837.7982 | 132400.0565 | 133995.4089 | 135617.3989 | 137261.1172 | 138922.7404 | 140599.2324 | 142288.1436 | 143987.4711 | 145695.5586 | 147411.0233 | 149132.7011 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 1495483.9234 |  | 0 | 0 | 0 | -65685.9832 | 99327.1114 | 103355.349 | 109000.7728 | 116099.3333 | 123936.0418 | 129317.3884 | 130837.7982 | 132400.0565 | 133995.4089 | 135617.3989 | 137261.1172 | 138922.7404 | 140599.2324 | 142288.1436 | 143987.4711 | 145695.5586 | 147411.0233 | 149132.7011 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | 0 | 40890.6974 | 41346.1906 | 41784.1156 | 42310.205 | 42925.8514 | 43596.4718 | 44135.7596 | 44450.5259 | 44768.8388 | 45090.6894 | 112325.1383 | 112654.0382 | 112986.4503 | 113322.3669 | 113661.7803 | 114004.6833 | 114351.0687 | 114700.9299 | 115054.2603 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | 921383.9801 |  | 0 | 0 | 0 | 40890.6974 | 41346.1906 | 41784.1156 | 42310.205 | 42925.8514 | 43596.4718 | 44135.7596 | 44450.5259 | 44768.8388 | 45090.6894 | 112325.1383 | 112654.0382 | 112986.4503 | 113322.3669 | 113661.7803 | 114004.6833 | 114351.0687 | 114700.9299 | 115054.2603 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | 868536.9535 |  | 0 | 0 | 0 | 34199.7905 | 34655.2837 | 35093.2087 | 35619.2981 | 36234.9444 | 36905.5649 | 37444.8527 | 37759.6189 | 38077.9319 | 38399.7825 | 112325.1383 | 112654.0382 | 112986.4503 | 113322.3669 | 113661.7803 | 114004.6833 | 114351.0687 | 114700.9299 | 115054.2603 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | 974231.0067 |  | 0 | 0 | 0 | 47581.6044 | 48037.0976 | 48475.0226 | 49001.112 | 49616.7583 | 50287.3788 | 50826.6666 | 51141.4328 | 51459.7458 | 51781.5963 | 112325.1383 | 112654.0382 | 112986.4503 | 113322.3669 | 113661.7803 | 114004.6833 | 114351.0687 | 114700.9299 | 115054.2603 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | 1066369.4048 |  | 0 | 0 | 0 | 51670.6741 | 52171.7167 | 52653.4342 | 53232.1325 | 53909.3434 | 54647.026 | 55240.2425 | 55586.4854 | 55936.6297 | 56290.6653 | 123557.6521 | 123919.442 | 124285.0954 | 124654.6036 | 125027.9584 | 125405.1516 | 125786.1756 | 126171.0229 | 126559.6863 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | 776398.5555 |  | 0 | 0 | 0 | 30110.7207 | 30520.6646 | 30914.7971 | 31388.2776 | 31942.3593 | 32545.9177 | 33031.2767 | 33314.5663 | 33601.048 | 33890.7135 | 101092.6245 | 101388.6344 | 101687.8053 | 101990.1302 | 102295.6023 | 102604.215 | 102915.9619 | 103230.8369 | 103548.8343 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | 723551.5289 |  | 0 | 0 | 0 | 23419.8138 | 23829.7577 | 24223.8902 | 24697.3706 | 25251.4523 | 25855.0108 | 26340.3698 | 26623.6594 | 26910.1411 | 27199.8066 | 101092.6245 | 101388.6344 | 101687.8053 | 101990.1302 | 102295.6023 | 102604.215 | 102915.9619 | 103230.8369 | 103548.8343 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 921383.9801 |  | 0 | 0 | 0 | 40890.6974 | 41346.1906 | 41784.1156 | 42310.205 | 42925.8514 | 43596.4718 | 44135.7596 | 44450.5259 | 44768.8388 | 45090.6894 | 112325.1383 | 112654.0382 | 112986.4503 | 113322.3669 | 113661.7803 | 114004.6833 | 114351.0687 | 114700.9299 | 115054.2603 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 921383.9801 |  | 0 | 0 | 0 | 40890.6974 | 41346.1906 | 41784.1156 | 42310.205 | 42925.8514 | 43596.4718 | 44135.7596 | 44450.5259 | 44768.8388 | 45090.6894 | 112325.1383 | 112654.0382 | 112986.4503 | 113322.3669 | 113661.7803 | 114004.6833 | 114351.0687 | 114700.9299 | 115054.2603 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | 921383.9801 |  | 0 | 0 | 0 | 40890.6974 | 41346.1906 | 41784.1156 | 42310.205 | 42925.8514 | 43596.4718 | 44135.7596 | 44450.5259 | 44768.8388 | 45090.6894 | 112325.1383 | 112654.0382 | 112986.4503 | 113322.3669 | 113661.7803 | 114004.6833 | 114351.0687 | 114700.9299 | 115054.2603 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 1 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 1.4955 | 0.92138 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 1.251 | 0.86854 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 1.74 | 0.97423 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 1.8896 | 1.0664 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 1.1014 | 0.7764 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | 0.85689 | 0.72355 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_costs
United Energy
EW transformer replacement
WORKINGS - COSTS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total opex ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace transformer #2 completed in 2028-2029
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | Capex | 0 | 1384390.1633 | 2768780.3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total capex ($) | 0 | 1384390.1633 | 2768780.3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total opex ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Refurbish transformer #2 completed in 2027-2028
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | Capex | 2027-28: 500000
|  | Total capex ($) | 0 | 500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total opex ($) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Workings_risks
United Energy
EW transformer replacement
WORKINGS - RISKS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Transformer risks
|  | Energy at Risk ($, Weighted) | 118694.3988 | 126511.5012 | 135871.4645 | 143387.5264 | 150590.5028 | 159321.5275 | 169604.1304 | 180835.6038 | 189773.0263 | 194795.8685 | 199873.9792 | 205007.1714 | 210195.2632 | 215438.0773 | 220735.4411 | 226087.1864 | 231493.1491 | 236953.1696 | 242467.0921 | 248034.7648 | 253656.0398 | 259330.7727 | 265058.8228 | 270840.0531 | 276674.3297
|  | Safety Risk | 471.4924 | 485.6406 | 499.9606 | 514.4516 | 529.1126 | 543.9429 | 558.9415 | 574.1077 | 589.4407 | 604.9397 | 620.604 | 636.4328 | 652.4254 | 668.5811 | 684.8991 | 701.3788 | 718.0195 | 734.8206 | 751.7814 | 768.9011 | 786.1794 | 803.6154 | 803.6154 | 803.6154 | 803.6154
|  | Unplanned Replacement Risk | 13240.0796 | 13637.3796 | 14039.5039 | 14446.4277 | 14858.1268 | 15274.5778 | 15695.7573 | 16121.6429 | 16552.2123 | 16987.4438 | 17427.316 | 17871.8081 | 18320.8996 | 18774.5704 | 19232.8008 | 19695.5714 | 20162.8632 | 20634.6575 | 21110.936 | 21591.6806 | 22076.8738 | 22566.4979 | 22566.4979 | 22566.4979 | 22566.4979
|  | Unplanned Fault Risk | 1804.3769 | 1858.5216 | 1913.3236 | 1968.7798 | 2024.8867 | 2081.6412 | 2139.0402 | 2197.0805 | 2255.7591 | 2315.0731 | 2375.0195 | 2435.5955 | 2496.7983 | 2558.6252 | 2621.0735 | 2684.1406 | 2747.8238 | 2812.1206 | 2877.0285 | 2942.545 | 3008.6679 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945
|  | Unplanned Enviromental Risk | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863
|  | Total transformer risks | 253073.3477 | 261356.043 | 271187.2527 | 279180.1854 | 286865.629 | 296084.6894 | 306860.8694 | 318591.4349 | 328033.4383 | 333566.325 | 339159.9186 | 344814.0078 | 350528.3865 | 356302.854 | 362137.2146 | 368031.2772 | 373984.8556 | 379997.7683 | 386069.8379 | 392200.8917 | 398390.7607 | 404639.2804 | 410367.3306 | 416148.5609 | 421982.8375
Option 2 - Replace transformer #2 completed in 2028-2029
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Transformer risks
|  | Energy at Risk ($, Weighted) | 118694.3988 | 126511.5012 | 135871.4645 | 4392.5682 | 8199.1715 | 12075.6659 | 16193.9044 | 20594.1949 | 24903.5229 | 28764.6325 | 32640.793 | 36539.8816 | 40467.6843 | 44428.5775 | 48425.9478 | 52462.4637 | 56540.2592 | 60661.0606 | 64826.2785 | 69037.0745 | 73294.4112 | 77599.0905 | 81951.7828 | 86353.0503 | 90803.3652
|  | Safety Risk | 471.4924 | 485.6406 | 499.9606 | 257.4698 | 265.3492 | 273.5511 | 282.0468 | 290.8183 | 299.8527 | 309.1398 | 318.6717 | 328.4415 | 338.4436 | 348.6727 | 359.1245 | 369.795 | 380.6806 | 391.7779 | 403.0839 | 414.5959 | 426.3113 | 438.2276 | 438.2276 | 438.2276 | 438.2276
|  | Unplanned Replacement Risk | 13240.0796 | 13637.3796 | 14039.5039 | 7230.0668 | 7451.3285 | 7681.6476 | 7920.2181 | 8166.533 | 8420.2282 | 8681.0228 | 8948.6896 | 9223.0387 | 9503.9076 | 9791.1546 | 10084.6544 | 10384.2947 | 10689.9742 | 11001.6003 | 11319.088 | 11642.3589 | 11971.3401 | 12305.9636 | 12305.9636 | 12305.9636 | 12305.9636
|  | Unplanned Fault Risk | 1804.3769 | 1858.5216 | 1913.3236 | 985.3238 | 1015.4777 | 1046.8659 | 1079.3786 | 1112.9468 | 1147.5207 | 1183.0622 | 1219.5402 | 1256.9289 | 1295.2061 | 1334.3525 | 1374.3511 | 1415.1865 | 1456.8449 | 1499.3138 | 1542.5815 | 1586.6373 | 1631.4713 | 1677.0743 | 1677.0743 | 1677.0743 | 1677.0743
|  | Unplanned Enviromental Risk | 118863 | 118863 | 118863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total transformer risks | 253073.3477 | 261356.043 | 271187.2527 | 12865.4286 | 16931.3269 | 21077.7306 | 25475.548 | 30164.493 | 34771.1245 | 38937.8573 | 43127.6945 | 47348.2907 | 51605.2415 | 55902.7573 | 60244.0778 | 64631.74 | 69067.7589 | 73553.7525 | 78091.0319 | 82680.6666 | 87323.5339 | 92020.3559 | 96373.0482 | 100774.3157 | 105224.6306
Option 3 - Refurbish transformer #2 completed in 2027-2028
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Transformer risks
|  | Energy at Risk ($, Weighted) | 118694.3988 | 126511.5012 | 128862.9506 | 135990.2233 | 142820.4368 | 151099.7183 | 160850.3454 | 171500.6833 | 179975.2143 | 184737.142 | 189551.385 | 194417.7635 | 199336.1023 | 204306.2308 | 209327.9827 | 214401.1958 | 219525.7119 | 224701.377 | 229928.0408 | 235205.5566 | 240533.7814 | 245912.5757 | 251341.8034 | 256821.3318 | 262351.0312
|  | Safety Risk | 471.4924 | 485.6406 | 494.961 | 509.3071 | 523.8215 | 538.5034 | 553.3521 | 568.3666 | 583.5463 | 598.8903 | 614.398 | 630.0685 | 645.9011 | 661.8953 | 678.0501 | 694.365 | 710.8393 | 727.4724 | 744.2635 | 761.2121 | 778.3176 | 795.5792 | 795.5792 | 795.5792 | 795.5792
|  | Unplanned Replacement Risk | 13240.0796 | 13637.3796 | 13337.5287 | 13724.1063 | 14115.2205 | 14510.8489 | 14910.9695 | 15315.5608 | 15724.6017 | 16138.0716 | 16555.9502 | 16978.2177 | 17404.8547 | 17835.8419 | 18271.1608 | 18710.7928 | 19154.72 | 19602.9246 | 20055.3892 | 20512.0966 | 20973.0301 | 21438.173 | 21438.173 | 21438.173 | 21438.173
|  | Unplanned Fault Risk | 1804.3769 | 1858.5216 | 1913.3236 | 1968.7798 | 2024.8867 | 2081.6412 | 2139.0402 | 2197.0805 | 2255.7591 | 2315.0731 | 2375.0195 | 2435.5955 | 2496.7983 | 2558.6252 | 2621.0735 | 2684.1406 | 2747.8238 | 2812.1206 | 2877.0285 | 2942.545 | 3008.6679 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945
|  | Unplanned Enviromental Risk | 118863 | 118863 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75
|  | Total transformer risks | 253073.3477 | 261356.043 | 174324.514 | 181908.1664 | 189200.1155 | 197946.4619 | 208169.4571 | 219297.4412 | 228254.8713 | 233504.927 | 238812.5026 | 244177.3952 | 249599.4065 | 255078.3433 | 260614.0171 | 266206.2442 | 271854.8451 | 277559.6446 | 283320.472 | 289137.1604 | 295009.5469 | 300937.4724 | 306366.7002 | 311846.2285 | 317375.9279

## Tx risks
United Energy
EW transformer replacement
Input Data - Station Configuration |  | Constants |  |  | POF METHOD | WEIBULL | Modifier (x) | Comment
Substation: | EW | Major Failure CoC |  |  | PoF (#1) | 0.1289% | 100%
Asset Type | Transformer | Minor Failure CoC |  |  | PoF (#2) | 0.1289% | 100%
VCR | 32.343 | Major Failure CoC - used | 4983804.588 |  | PoF (#3) | 100% | 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 169800 |  | PoF (#4) | 0% | 100%
Scenario #1: EW - Transformer | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 100% | 0 | Energy | 3351.7815 | 3574.2427 | 3810.0308 | 4091.0085 | 4324.1663 | 4537.5342 | 4805.2221 | 5125.6025 | 5448.0924 | 5736.1516 | 5887.974 | 6041.4669 | 6196.6247 | 6353.4419 | 6511.9132 | 6672.0333 | 6833.7972 | 6997.1999 | 7162.2366 | 7328.9025 | 7497.1931 | 7667.1039 | 7838.6305 | 8011.7687 | 8186.5144 | 8362.8635 | 8540.812 | 8720.3561 | 8720.3561 | 8720.3561 | 8720.3561 | 8720.3561
Online Monitoring | 0% | 0 | Energy | 3656.0695 | 3892.9792 | 4148.4529 | 4457.4944 | 4688.0798 | 4932.5744 | 5207.8058 | 5519.9969 | 5925.0581 | 6174.0284 | 6337.4403 | 6502.6503 | 6669.6523 | 6838.4403 | 7009.0088 | 7181.3519 | 7355.4642 | 7531.3405 | 7708.9754 | 7888.364 | 8069.5013 | 8252.3824 | 8437.0028 | 8623.3577 | 8811.4428 | 9001.2537 | 9192.7862 | 9386.0361 | 9386.0361 | 9386.0361 | 9386.0361 | 9386.0361
Physical Separation | 0% | 300000 | Energy | 3351.7815 | 3574.2427 | 3810.0308 | 4091.0085 | 4324.1663 | 4537.5342 | 4805.2221 | 5125.6025 | 5448.0924 | 5736.1516 | 5887.974 | 6041.4669 | 6196.6247 | 6353.4419 | 6511.9132 | 6672.0333 | 6833.7972 | 6997.1999 | 7162.2366 | 7328.9025 | 7497.1931 | 7667.1039 | 7838.6305 | 8011.7687 | 8186.5144 | 8362.8635 | 8540.812 | 8720.3561 | 8720.3561 | 8720.3561 | 8720.3561 | 8720.3561
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.2578% | 0.2657% | 0.2736% | 0.2817% | 0.2899% | 0.2981% | 0.3065% | 0.3149% | 0.3235% | 0.3321% | 0.3409% | 0.3497% | 0.3586% | 0.3676% | 0.3767% | 0.3859% | 0.3952% | 0.4046% | 0.414% | 0.4236% | 0.4332% | 0.443% | 0.4528% | 0.4528% | 0.4528% | 0.4528% | 0.4528% | 0.4528% | 0.4528% | 0.4528% | 0.4528% | 0.4528%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 1.031% | 1.063% | 1.095% | 1.127% | 1.159% | 1.193% | 1.226% | 1.26% | 1.294% | 1.328% | 1.363% | 1.399% | 1.434% | 1.47% | 1.507% | 1.544% | 1.581% | 1.618% | 1.656% | 1.694% | 1.733% | 1.772% | 1.811% | 1.811% | 1.811% | 1.811% | 1.811% | 1.811% | 1.811% | 1.811% | 1.811% | 1.811%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 111359.1452 | 118694.3988 | 126511.5012 | 135871.4645 | 143387.5264 | 150590.5028 | 159321.5275 | 169604.1304 | 180835.6038 | 189773.0263 | 194795.8685 | 199873.9792 | 205007.1714 | 210195.2632 | 215438.0773 | 220735.4411 | 226087.1864 | 231493.1491 | 236953.1696 | 242467.0921 | 248034.7648 | 253656.0398 | 259330.7727 | 265058.8228 | 270840.0531 | 276674.3297 | 282561.5223 | 288501.5035 | 288501.5035 | 288501.5035 | 288501.5035 | 288501.5035
Replace 1 Asset | 0% | 4153170.49 | Safety Risk | 457.5168 | 471.4924 | 485.6406 | 499.9606 | 514.4516 | 529.1126 | 543.9429 | 558.9415 | 574.1077 | 589.4407 | 604.9397 | 620.604 | 636.4328 | 652.4254 | 668.5811 | 684.8991 | 701.3788 | 718.0195 | 734.8206 | 751.7814 | 768.9011 | 786.1794 | 803.6154 | 803.6154 | 803.6154 | 803.6154 | 803.6154 | 803.6154 | 803.6154 | 803.6154 | 803.6154 | 803.6154
Replace 2 Assets | 0% | 0 | Unplanned Replacement Risk | 12847.629 | 13240.0796 | 13637.3796 | 14039.5039 | 14446.4277 | 14858.1268 | 15274.5778 | 15695.7573 | 16121.6429 | 16552.2123 | 16987.4438 | 17427.316 | 17871.8081 | 18320.8996 | 18774.5704 | 19232.8008 | 19695.5714 | 20162.8632 | 20634.6575 | 21110.936 | 21591.6806 | 22076.8738 | 22566.4979 | 22566.4979 | 22566.4979 | 22566.4979 | 22566.4979 | 22566.4979 | 22566.4979 | 22566.4979 | 22566.4979 | 22566.4979
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 1750.8932 | 1804.3769 | 1858.5216 | 1913.3236 | 1968.7798 | 2024.8867 | 2081.6412 | 2139.0402 | 2197.0805 | 2255.7591 | 2315.0731 | 2375.0195 | 2435.5955 | 2496.7983 | 2558.6252 | 2621.0735 | 2684.1406 | 2747.8238 | 2812.1206 | 2877.0285 | 2942.545 | 3008.6679 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863 | 118863
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Total Life Cycle Cost | 245278.1842 | 253073.3477 | 261356.043 | 271187.2527 | 279180.1854 | 286865.629 | 296084.6894 | 306860.8694 | 318591.4349 | 328033.4383 | 333566.325 | 339159.9186 | 344814.0078 | 350528.3865 | 356302.854 | 362137.2146 | 368031.2772 | 373984.8556 | 379997.7683 | 386069.8379 | 392200.8917 | 398390.7607 | 404639.2804 | 410367.3306 | 416148.5609 | 421982.8375 | 427870.03 | 433810.0113 | 433810.0113 | 433810.0113 | 433810.0113 | 433810.0113
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: WEIBULL; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | EW | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.1289%; 100% 2028: 100%
Asset Type | Transformer | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.1289%; 100% 2028: 100%
VCR | 32.343 | Major Failure CoC - used | 4983804.588 | PoF (#4) 2026: PoF (#3); 0% 2027: 100%; 100% 2028: 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 169800 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #2: EW - Transformer | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 100% | 0 | Energy | 3351.7815 | 3574.2427 | 3810.0308 | 4091.0085 | 132.4676 | 247.0542 | 364.2085 | 489.3956 | 620.4479 | 752.7433 | 869.4507 | 986.613 | 1104.4683 | 1223.1916 | 1342.9151 | 1463.7411 | 1585.7504 | 1709.0074 | 1833.5643 | 1959.4637 | 2086.7409 | 2215.4247 | 2345.5396 | 2477.1057 | 2610.1401 | 2744.657 | 2880.6685 | 3018.1845 | 3018.1845 | 3018.1845 | 3018.1845 | 3018.1845
Online Monitoring | 0% | 0 | Energy | 3656.0695 | 3892.9792 | 4148.4529 | 4457.4944 | 143.6158 | 268.5629 | 394.7221 | 527.0526 | 674.7665 | 810.205 | 935.8214 | 1061.9274 | 1188.7794 | 1316.5656 | 1445.4283 | 1575.4777 | 1706.8007 | 1839.4667 | 1973.5318 | 2109.042 | 2246.035 | 2384.5421 | 2524.5895 | 2666.1989 | 2809.3886 | 2954.1741 | 3100.5681 | 3248.5816 | 3248.5816 | 3248.5816 | 3248.5816 | 3248.5816
Physical Separation | 0% | 300000 | Energy | 3351.7815 | 3574.2427 | 3810.0308 | 4091.0085 | 132.4676 | 247.0542 | 364.2085 | 489.3956 | 620.4479 | 752.7433 | 869.4507 | 986.613 | 1104.4683 | 1223.1916 | 1342.9151 | 1463.7411 | 1585.7504 | 1709.0074 | 1833.5643 | 1959.4637 | 2086.7409 | 2215.4247 | 2345.5396 | 2477.1057 | 2610.1401 | 2744.657 | 2880.6685 | 3018.1845 | 3018.1845 | 3018.1845 | 3018.1845 | 3018.1845
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.2578% | 0.2657% | 0.2736% | 0.2817% | 0.1451% | 0.1495% | 0.1541% | 0.1589% | 0.1639% | 0.169% | 0.1742% | 0.1796% | 0.1851% | 0.1907% | 0.1965% | 0.2023% | 0.2084% | 0.2145% | 0.2207% | 0.2271% | 0.2336% | 0.2402% | 0.2469% | 0.2469% | 0.2469% | 0.2469% | 0.2469% | 0.2469% | 0.2469% | 0.2469% | 0.2469% | 0.2469%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 1.031% | 1.063% | 1.095% | 1.127% | 0.5803% | 0.598% | 0.6165% | 0.6357% | 0.6554% | 0.6758% | 0.6967% | 0.7182% | 0.7402% | 0.7628% | 0.7858% | 0.8094% | 0.8334% | 0.858% | 0.883% | 0.9085% | 0.9344% | 0.9608% | 0.9877% | 0.9877% | 0.9877% | 0.9877% | 0.9877% | 0.9877% | 0.9877% | 0.9877% | 0.9877% | 0.9877%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 111359.1452 | 118694.3988 | 126511.5012 | 135871.4645 | 4392.5682 | 8199.1715 | 12075.6659 | 16193.9044 | 20594.1949 | 24903.5229 | 28764.6325 | 32640.793 | 36539.8816 | 40467.6843 | 44428.5775 | 48425.9478 | 52462.4637 | 56540.2592 | 60661.0606 | 64826.2785 | 69037.0745 | 73294.4112 | 77599.0905 | 81951.7828 | 86353.0503 | 90803.3652 | 95303.1243 | 99852.6613 | 99852.6613 | 99852.6613 | 99852.6613 | 99852.6613
Replace 1 Asset | 100% | 4153170.49 | Safety Risk | 457.5168 | 471.4924 | 485.6406 | 499.9606 | 257.4698 | 265.3492 | 273.5511 | 282.0468 | 290.8183 | 299.8527 | 309.1398 | 318.6717 | 328.4415 | 338.4436 | 348.6727 | 359.1245 | 369.795 | 380.6806 | 391.7779 | 403.0839 | 414.5959 | 426.3113 | 438.2276 | 438.2276 | 438.2276 | 438.2276 | 438.2276 | 438.2276 | 438.2276 | 438.2276 | 438.2276 | 438.2276
Replace 2 Assets | 0% | 0 | Unplanned Replacement Risk | 12847.629 | 13240.0796 | 13637.3796 | 14039.5039 | 7230.0668 | 7451.3285 | 7681.6476 | 7920.2181 | 8166.533 | 8420.2282 | 8681.0228 | 8948.6896 | 9223.0387 | 9503.9076 | 9791.1546 | 10084.6544 | 10384.2947 | 10689.9742 | 11001.6003 | 11319.088 | 11642.3589 | 11971.3401 | 12305.9636 | 12305.9636 | 12305.9636 | 12305.9636 | 12305.9636 | 12305.9636 | 12305.9636 | 12305.9636 | 12305.9636 | 12305.9636
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 1750.8932 | 1804.3769 | 1858.5216 | 1913.3236 | 985.3238 | 1015.4777 | 1046.8659 | 1079.3786 | 1112.9468 | 1147.5207 | 1183.0622 | 1219.5402 | 1256.9289 | 1295.2061 | 1334.3525 | 1374.3511 | 1415.1865 | 1456.8449 | 1499.3138 | 1542.5815 | 1586.6373 | 1631.4713 | 1677.0743 | 1677.0743 | 1677.0743 | 1677.0743 | 1677.0743 | 1677.0743 | 1677.0743 | 1677.0743 | 1677.0743 | 1677.0743
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 118863 | 118863 | 118863 | 118863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645 | 177065.0645
|  |  | Total Life Cycle Cost | 245278.1842 | 253073.3477 | 261356.043 | 271187.2527 | 189930.493 | 193996.3914 | 198142.795 | 202540.6124 | 207229.5574 | 211836.1889 | 216002.9218 | 220192.759 | 224413.3552 | 228670.306 | 232967.8217 | 237309.1422 | 241696.8045 | 246132.8234 | 250618.817 | 255156.0964 | 259745.7311 | 264388.5984 | 269085.4204 | 273438.1127 | 277839.3802 | 282289.695 | 286789.4542 | 291338.9911 | 291338.9911 | 291338.9911 | 291338.9911 | 291338.9911
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: WEIBULL; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | EW | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.1289%; 100% 2028: 100%
Asset Type | Transformer | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.116%; 100% 2028: 90%
VCR | 32.343 | Major Failure CoC - used | 4983804.588 | PoF (#4) 2026: PoF (#3); 0% 2027: 100%; 100% 2028: 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 169800 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #3: EW - Transformer | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 100% | 0 | Energy | 3178.9652 | 3389.93 | 3613.5308 | 3879.9863 | 4101.0843 | 4303.4096 | 4557.248 | 4861.0545 | 5166.8563 | 5439.9992 | 5583.9351 | 5729.4522 | 5876.5452 | 6025.2088 | 6175.4378 | 6327.2272 | 6480.572 | 6635.4676 | 6791.9092 | 6949.8924 | 7109.4126 | 7270.4655 | 7433.047 | 7597.1529 | 7762.7792 | 7929.922 | 8098.5774 | 8268.7418 | 8268.7418 | 8268.7418 | 8268.7418 | 8268.7418
Online Monitoring | 0% | 0 | Energy | 3467.5643 | 3692.2302 | 3934.499 | 4227.5682 | 4446.2237 | 4678.0667 | 4939.0563 | 5235.093 | 5619.2005 | 5855.2688 | 6010.1922 | 6166.8176 | 6325.1391 | 6485.1511 | 6646.848 | 6810.2245 | 6975.2751 | 7141.9948 | 7310.3786 | 7480.4216 | 7652.119 | 7825.4661 | 8000.4585 | 8177.0916 | 8355.3613 | 8535.2631 | 8716.7931 | 8899.9472 | 8899.9472 | 8899.9472 | 8899.9472 | 8899.9472
Physical Separation | 0% | 300000 | Energy | 3178.9652 | 3389.93 | 3613.5308 | 3879.9863 | 4101.0843 | 4303.4096 | 4557.248 | 4861.0545 | 5166.8563 | 5439.9992 | 5583.9351 | 5729.4522 | 5876.5452 | 6025.2088 | 6175.4378 | 6327.2272 | 6480.572 | 6635.4676 | 6791.9092 | 6949.8924 | 7109.4126 | 7270.4655 | 7433.047 | 7597.1529 | 7762.7792 | 7929.922 | 8098.5774 | 8268.7418 | 8268.7418 | 8268.7418 | 8268.7418 | 8268.7418
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.2449% | 0.2524% | 0.26% | 0.2676% | 0.2754% | 0.2832% | 0.2912% | 0.2992% | 0.3073% | 0.3155% | 0.3238% | 0.3322% | 0.3407% | 0.3492% | 0.3579% | 0.3666% | 0.3754% | 0.3843% | 0.3933% | 0.4024% | 0.4116% | 0.4208% | 0.4302% | 0.4302% | 0.4302% | 0.4302% | 0.4302% | 0.4302% | 0.4302% | 0.4302% | 0.4302% | 0.4302%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 1.031% | 1.063% | 1.095% | 1.127% | 1.159% | 1.193% | 1.226% | 1.26% | 1.294% | 1.328% | 1.363% | 1.399% | 1.434% | 1.47% | 1.507% | 1.544% | 1.581% | 1.618% | 1.656% | 1.694% | 1.733% | 1.772% | 1.811% | 1.811% | 1.811% | 1.811% | 1.811% | 1.811% | 1.811% | 1.811% | 1.811% | 1.811%
Bunded | 0 | 300000
Refurbish Assets | 1 | 500000 | Energy at Risk ($, Weighted) | 105617.5193 | 112573.6947 | 119986.7484 | 128862.9506 | 135990.2233 | 142820.4368 | 151099.7183 | 160850.3454 | 171500.6833 | 179975.2143 | 184737.142 | 189551.385 | 194417.7635 | 199336.1023 | 204306.2308 | 209327.9827 | 214401.1958 | 219525.7119 | 224701.377 | 229928.0408 | 235205.5566 | 240533.7814 | 245912.5757 | 251341.8034 | 256821.3318 | 262351.0312 | 267930.7752 | 273560.4404 | 273560.4404 | 273560.4404 | 273560.4404 | 273560.4404
Replace 1 Asset | 0% | 4153170.49 | Safety Risk | 452.9416 | 466.7774 | 480.7842 | 494.961 | 509.3071 | 523.8215 | 538.5034 | 553.3521 | 568.3666 | 583.5463 | 598.8903 | 614.398 | 630.0685 | 645.9011 | 661.8953 | 678.0501 | 694.365 | 710.8393 | 727.4724 | 744.2635 | 761.2121 | 778.3176 | 795.5792 | 795.5792 | 795.5792 | 795.5792 | 795.5792 | 795.5792 | 795.5792 | 795.5792 | 795.5792 | 795.5792
Replace 2 Assets | 0% | 0 | Unplanned Replacement Risk | 12205.2476 | 12578.0756 | 12955.5107 | 13337.5287 | 13724.1063 | 14115.2205 | 14510.8489 | 14910.9695 | 15315.5608 | 15724.6017 | 16138.0716 | 16555.9502 | 16978.2177 | 17404.8547 | 17835.8419 | 18271.1608 | 18710.7928 | 19154.72 | 19602.9246 | 20055.3892 | 20512.0966 | 20973.0301 | 21438.173 | 21438.173 | 21438.173 | 21438.173 | 21438.173 | 21438.173 | 21438.173 | 21438.173 | 21438.173 | 21438.173
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 1750.8932 | 1804.3769 | 1858.5216 | 1913.3236 | 1968.7798 | 2024.8867 | 2081.6412 | 2139.0402 | 2197.0805 | 2255.7591 | 2315.0731 | 2375.0195 | 2435.5955 | 2496.7983 | 2558.6252 | 2621.0735 | 2684.1406 | 2747.8238 | 2812.1206 | 2877.0285 | 2942.545 | 3008.6679 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945 | 3075.3945
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75 | 29715.75
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839 | 60120.6839
|  |  | Total Life Cycle Cost | 149742.3517 | 157138.6747 | 164997.3148 | 234445.1979 | 242028.8504 | 249320.7994 | 258067.1458 | 268290.1411 | 279418.1251 | 288375.5552 | 293625.6109 | 298933.1866 | 304298.0791 | 309720.0904 | 315199.0272 | 320734.7011 | 326326.9281 | 331975.529 | 337680.3286 | 343441.156 | 349257.8443 | 355130.2308 | 361058.1564 | 366487.3841 | 371966.9125 | 377496.6118 | 383076.3559 | 388706.0211 | 388706.0211 | 388706.0211 | 388706.0211 | 388706.0211

## Misc_calcs
United Energy
EW transformer replacement
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 2 | TRUE
| Option 3 | 2 | TRUE
| Option 4 | Not used | FALSE
| Option 5 | Not used | FALSE
| First year | 2
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
United Energy
EW transformer replacement
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | TRUE | Not used |  | TRUE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
United Energy
| Reliability in worst-served areas | per MWh | 0
| Network resilience | per MWh | 38560
| Enabling solar exports | per MWh | 862.6028
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.34751
| Customer value of time - business | per minute customer time | 0.34751
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020