## Cover
United Energy
Regulatory proposal 2026-31
EW switchboard and relay
| Model number: | 4.03
2025-01-31
15

## Summary
United Energy
EW switchboard and relay replacement
SUMMARY
RESULTS
|  |  |  | PV of costs | PV of benefits | NPV
| Option |  |  | 2026-06-30 | 2026-06-30 | 2026-06-30
| Option 1 (base case) | No change to existing practices |  | 0 | 0 | 0
| Option 2 | SWBD and relay replacement completed in 2027-28 |  | -3.7336 | 4.4052 | 0.67156
| Option 3 | Relay replacement in 2026-27 and SWBD replacement in 2031-32 |  | -3.5204 | 3.0583 | -0.4621
| Option 4 | 0
| Option 5 | 0
NPV
| Preferred option: |  |  | 2026-06-30
| Option 2 | SWBD and relay replacement completed in 2027-28 |  | 0.67156
PREFERRED OPTION
Preferred Option
Option 2
| Expenditure forecast | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 |  | Total
| Capital expenditure |  | 3.7943 | 1.8972 | 0 | 0 | 0 |  | 5.6915
| Operating expenditure |  | 0 | 0 | 0 | 0 | 0 |  | 0
CHART
| Capex and risk ($M, 2026) |  | Value of expected unserved energy ($M, 2026)
SENSITIVITIES
| Sensitivity | 2026-06-30 | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | Preferred option
| None |  | 0 | 0.67156 | -0.4621 |  |  |  | Option 2
| Capex 10% higher |  | 0 | 0.2982 | -0.81414 |  |  |  | Option 2
| Capex 10% lower |  | 0 | 1.0449 | -0.11006 |  |  |  | Option 2
| Total benefits 10% higher |  | 0 | 1.1121 | -0.15627 |  |  |  | Option 2
| Total benefits 10% lower |  | 0 | 0.23104 | -0.76793 |  |  |  | Option 2
| Capex 10% higher & Total benefits 10% lower |  | 0 | -0.14232 | -1.12 |  |  |  | Option 1 (base case)
| 0 | [7 empty] | #NAME?
| 0 | [6 empty] | 0 | #NAME?
|  | 0 | [6 empty] | #NAME?
0

## Assumptions
United Energy
EW switchboard and relay replacement
Project
|  | Business: |  | United Energy
|  | Descripton: |  | EW switchboard and relay replacement
|  | Date of cost inputs: |  | December |  | 2023
|  | Option |  | Description
|  | Option 1 (base case) |  | No change to existing practices
|  | Option 2 |  | SWBD and relay replacement completed in 2027-28
|  | Option 3 |  | Relay replacement in 2026-27 and SWBD replacement in 2031-32
Option 4
Option 5
|  | Compliance project |  | No
|  | Expenditure starts |  | 2026-27 | [start]
Timing & WACC
|  | Input dollars |  |  |  | 2023-12-31 | [input_dollars]
|  | Pre-tax real WACC |  |  |  | 3.5% | [real_disc]
|  | VCR date |  |  |  | 2023-12-31 | [vcr_date]
|  | Analysis period (years) |  |  |  | 20 | [years]\
|  | Output dollars |  |  |  | 2026-06-30 | [output_dollars]
|  | Other benefits date |  |  |  | 2023-12-31 | [custval_date]
|  | Value of CO2 reductions input date |  |  |  | 2023-06-30
VCR
|  | Enter ZSS code >> | eg. AR | EW |  | Elwood | 32343.3946 | 2023 VCR ($/MWh)
Risks
SAFETY
|  | Value of statistical life |  |  |  | 5400000 | 2023-06-30
|  | Value of injury |  |  |  | 0 | 2023-12-31
Disproportionate factors applied to various bushfire and other risk valuations
|  | Harm to property from network |  |  |  | 1
|  | Harm to property from bushfire |  |  |  | 1
|  | Harm to environment |  |  |  | 1
|  | Safety - Public trespass |  |  |  | 1
|  | Safety - Single fatality or serious injury ^ |  |  |  | 3
|  | Safety from bushfire in HBRA |  |  |  | 3
|  | Safety - Multiple fatality or serious injury ^ |  |  |  | 6
|  | Safety from bushfire (REFCL declared areas) |  |  |  | 6
|  | Safety from bushfire (electric line construction areas) |  |  |  | 10
^ Public or employee
|  | Incident type |  |  |  | Value | Probability | DF selected | Description/comment
|  | Safety (fatality) |  |  |  | 5607473.5197 | 0 | 0 | 0
|  | Safety (injury) |  |  |  | 0 | 0 | 0 | 0
UNPLANNED REPLACEMENT/REPAIR
|  | Major failure (replace) |  |  |  | 0 | 2023-12-31
|  | Minor failure (repair) |  |  |  | 0 | 2023-12-31
|  | Premium for failure |  |  |  | 20%
Other benefits
| ENVIRONMENTAL | [8 empty] | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
|  | Value of CO2 reductions |  |  |  |  | 2023-06-30 | $/kWh |  | 0.02473 | 0.022341 | 0.020196 | 0.018063 | 0.015913 | 0.013715
| CUSTOMER VALUE |  |  |  |  | Value
|  | Reliability in worst-served areas |  |  |  | 0 | 2023-12-31 | per MWh
|  | Network resilience |  |  |  | 38560 | 2023-12-31 | per MWh
|  | Enabling solar exports |  |  |  | 862.6028 | 2023-12-31 | per MWh
|  | Aesthetics |  |  |  | 0 | 2023-12-31 | per customer
|  | Customer value of time - residential |  |  |  | 0.34751 | 2023-12-31 | per customer minute
|  | Customer value of time - business |  |  |  | 0.34751 | 2023-12-31 | per customer minute
|  | Communication |  |  |  | 0 | 2023-12-31 | per customer
|  | Information accessibility |  |  |  | 0 | 2023-12-31 | per customer
Sensitivities
[6 empty] | Capex | Total benefits
| 1 | Capex 10% higher |  |  |  | 10% | 0%
| 2 | Capex 10% lower |  |  |  | -10% | 0%
| 3 | Total benefits 10% higher |  |  |  | 0% | 10%
| 4 | Total benefits 10% lower |  |  |  | 0% | -10%
| 5 | Capex 10% higher & Total benefits 10% lower |  |  |  | 10% | -10%

## Option1 (base case)
United Energy
EW switchboard and relay replacement
OPTION 1 (base case)
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh |  | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 32343.3946 | 2023-12-31 |  | 222256.9687 | 230621.3865 | 241294.4417 | 248349.4867 | 254614.9523 | 263098.5245 | 273717.5252 | 285474.7711 | 293271.8635 | 295168.989 | 297038.3111 | 299004.0069 | 301061.605 | 303206.072 | 305431.7919 | 307732.5487 | 310101.5145 | 312531.2423 | 315013.6653 | 317540.1014 | 320101.2661 | 322687.2921 | 325287.7565 | 327891.7175 | 330487.7582
| Safety risk | (after DF) |  | 2023-12-31 |  | 449.828 | 495.0233 | 546.1301 | 603.0858 | 665.8121 | 734.2131 | 808.1735 | 887.5576 | 972.2073 | 1061.9414 | 1156.5538 | 1255.813 | 1359.461 | 1467.2128 | 1578.7557 | 1693.7496 | 1811.8263 | 1932.5907 | 2055.6206 | 2180.4681 | 2306.6605 | 2433.7019 | 2561.0751 | 2688.2435 | 2814.6538
| Unplanned replacement |  |  | 2023-12-31 |  | 14021.5374 | 14320.7932 | 14659.1913 | 15036.3178 | 15451.6538 | 15904.5636 | 16394.2849 | 16919.9183 | 17480.4179 | 18074.5827 | 18701.049 | 19358.2836 | 20044.5782 | 20758.0453 | 21496.6154 | 22258.0352 | 23039.8682 | 23839.4971 | 24654.1271 | 25480.7918 | 26316.3617 | 27157.5532 | 28000.9415 | 28842.974 | 29679.987
| Unplanned fault | (after DF) |  | 2023-12-31 |  | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  |  | 237232.3841 | 245941.2529 | 257003.813 | 264492.9404 | 271236.4682 | 280241.3512 | 291424.0337 | 303786.297 | 312228.5388 | 314809.5631 | 317399.9639 | 320122.1535 | 322969.6942 | 325935.3802 | 329011.213 | 332188.3834 | 335457.259 | 338807.3802 | 342227.463 | 345705.4114 | 349228.3383 | 352782.5972 | 356353.8231 | 359926.9849 | 363486.4491
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38560 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31
Capital expenditure
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
NPV | Net benefits |  |  | Option 1 (Base Case)NPV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 1 (Base Case)sens1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 1 (Base Case)sens2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 1 (Base Case)sens3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 1 (Base Case)sens4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 1 (Base Case)sens5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 1 (Base Case)sens |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option2
United Energy
EW switchboard and relay replacement
OPTION 2 | SWBD and relay replacement completed in 2027-28
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Switchboard |  | 50 | 2023-12-31 | 2045617.0626 | 1022808.5313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Relays |  | 25 | 2023-12-31 | 1363744.7084 | 681872.3542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 3409361.7711 | 1704680.8855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 32343.3946 | 2023-12-31 | 222256.9687 | 230621.3865 | 27788.8142 | 28658.0918 | 29541.7906 | 30802.3149 | 32421.9996 | 34283.7124 | 35828.263 | 36846.9426 | 38083.0986 | 39417.1569 | 40880.1969 | 42403.5809 | 44049.1832 | 45812.4833 | 47687.9981 | 49669.2037 | 51748.4655 | 53916.9787 | 56164.7225 | 58480.4301 | 60851.5781 | 63264.3977 | 65703.9097
| Safety risk | (after DF) |  | 2023-12-31 | 449.828 | 495.0233 | 38.5212 | 47.5977 | 62.7218 | 83.8844 | 111.0657 | 144.2327 | 183.3347 | 228.2999 | 279.0322 | 335.4074 | 397.2704 | 464.4319 | 536.6657 | 613.7068 | 695.2487 | 780.9424 | 870.3953 | 963.1703 | 1058.7868 | 1156.7207 | 1256.4065 | 1357.2394 | 1458.5786
| Unplanned replacement |  |  | 2023-12-31 | 14021.5374 | 14320.7932 | 1542.2263 | 1566.2657 | 1606.323 | 1662.3731 | 1734.3646 | 1822.2093 | 1925.7731 | 2044.8661 | 2179.2336 | 2328.5467 | 2492.3945 | 2670.2755 | 2861.5912 | 3065.6389 | 3281.6074 | 3508.5723 | 3745.4934 | 3991.2136 | 4244.4595 | 4503.8431 | 4767.8667 | 5034.9286 | 5303.3315
| Unplanned fault | (after DF) |  | 2023-12-31 | 504.05 | 504.05 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 237232.3841 | 245941.2529 | 29428.8617 | 30331.2552 | 31270.1355 | 32607.8724 | 34326.7299 | 36309.4544 | 37996.6708 | 39179.4086 | 40600.6643 | 42140.411 | 43829.1618 | 45597.5883 | 47506.7401 | 49551.129 | 51724.1542 | 54018.0184 | 56423.6542 | 58930.6627 | 61527.2688 | 64200.2939 | 66935.1514 | 69715.8657 | 72525.1198
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38560 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - residential | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time - business | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex saving |  |  | 2023-12-31 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 227574.9512 | 234161.6852 | 239966.3327 | 247633.4788 | 257097.3038 | 267476.8426 | 274231.868 | 275630.1545 | 276799.2996 | 277981.7425 | 279140.5325 | 280337.7919 | 281504.4729 | 282637.2544 | 283733.1048 | 284789.3618 | 285803.8088 | 286774.7487 | 287701.0696 | 288582.3033 | 289418.6717 | 290211.1192 | 290961.3293
Capital expenditure
| Switchboard |  |  | 2023-12-31 | -2045617.0626 | -1022808.5313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Relays |  |  | 2023-12-31 | -1363744.7084 | -681872.3542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Switchboard |  |  | 2023-12-31 | -2045617.0626 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939 | -3068425.5939
| Relays |  |  | 2023-12-31 | -1363744.7084 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Switchboard |  |  | 2023-12-31 | 0 | -87212.2437 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656 | -130818.3656
| Annualised capex - Relays |  |  | 2023-12-31 | 0 | -82743.8947 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -169956.1385 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077
| Annualised capex |  |  | 2023-12-31 | 0 | -169956.1385 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 227574.9512 | 234161.6852 | 239966.3327 | 247633.4788 | 257097.3038 | 267476.8426 | 274231.868 | 275630.1545 | 276799.2996 | 277981.7425 | 279140.5325 | 280337.7919 | 281504.4729 | 282637.2544 | 283733.1048 | 284789.3618 | 285803.8088 | 286774.7487 | 287701.0696 | 288582.3033 | 289418.6717 | 290211.1192 | 290961.3293
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
| Net benefits |  |  | 2023-12-31 | 0 | -169956.1385 | 22640.7435 | 29227.4775 | 35032.125 | 42699.2711 | 52163.0961 | 62542.6349 | 69297.6603 | 70695.9469 | 71865.0919 | 73047.5348 | 74206.3248 | 75403.5842 | 76570.2652 | 77703.0467 | 78798.8971 | 79855.1541 | 80869.6011 | 81840.541 | 82766.8619 | 83648.0956 | 84484.464 | 85276.9115 | 86027.1216
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 2NPV | 0 | -169956.1385 | 22640.7435 | 29227.4775 | 35032.125 | 42699.2711 | 52163.0961 | 62542.6349 | 69297.6603 | 70695.9469 | 71865.0919 | 73047.5348 | 74206.3248 | 75403.5842 | 76570.2652 | 77703.0467 | 78798.8971 | 79855.1541 | 80869.6011 | 81840.541 | 82766.8619 | 83648.0956 | 84484.464 | 85276.9115 | 86027.1216
| Total annualised capex |  |  |  | 0 | -169956.1385 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077 | -254934.2077
| Total benefits |  |  |  | 0 | 0 | 277574.9512 | 284161.6852 | 289966.3327 | 297633.4788 | 307097.3038 | 317476.8426 | 324231.868 | 325630.1545 | 326799.2996 | 327981.7425 | 329140.5325 | 330337.7919 | 331504.4729 | 332637.2544 | 333733.1048 | 334789.3618 | 335803.8088 | 336774.7487 | 337701.0696 | 338582.3033 | 339418.6717 | 340211.1192 | 340961.3293
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 2sens1 | 0 | -186951.7523 | -2852.6772 | 3734.0567 | 9538.7043 | 17205.8503 | 26669.6753 | 37049.2142 | 43804.2395 | 45202.5261 | 46371.6711 | 47554.114 | 48712.904 | 49910.1635 | 51076.8445 | 52209.6259 | 53305.4763 | 54361.7333 | 55376.1804 | 56347.1202 | 57273.4411 | 58154.6749 | 58991.0432 | 59783.4907 | 60533.7008
sens2 | Capex 10% lower | -10% | 0% | Option 2sens2 | 0 | -152960.5246 | 48134.1643 | 54720.8983 | 60525.5458 | 68192.6919 | 77656.5168 | 88036.0557 | 94791.0811 | 96189.3676 | 97358.5127 | 98540.9556 | 99699.7455 | 100897.005 | 102063.686 | 103196.4674 | 104292.3179 | 105348.5748 | 106363.0219 | 107333.9617 | 108260.2826 | 109141.5164 | 109977.8848 | 110770.3323 | 111520.5424
sens3 | Total benefits 10% higher | 0% | 10% | Option 2sens3 | 0 | -169956.1385 | 50398.2387 | 57643.646 | 64028.7583 | 72462.619 | 82872.8264 | 94290.3192 | 101720.8471 | 103258.9623 | 104545.0218 | 105845.709 | 107120.378 | 108437.3634 | 109720.7125 | 110966.7721 | 112172.2076 | 113334.0902 | 114449.982 | 115518.0158 | 116536.9688 | 117506.326 | 118426.3312 | 119298.0234 | 120123.2545
sens4 | Total benefits 10% lower | 0% | -10% | Option 2sens4 | 0 | -169956.1385 | -5116.7516 | 811.309 | 6035.4918 | 12935.9232 | 21453.3657 | 30794.9507 | 36874.4735 | 38132.9314 | 39185.1619 | 40249.3605 | 41292.2715 | 42369.805 | 43419.8179 | 44439.3212 | 45425.5866 | 46376.2179 | 47289.2203 | 48163.0661 | 48996.7549 | 49789.8653 | 50542.5968 | 51255.7996 | 51930.9887
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 2sens5 | 0 | -186951.7523 | -30610.1724 | -24682.1118 | -19457.929 | -12557.4976 | -4040.0551 | 5301.5299 | 11381.0527 | 12639.5106 | 13691.7412 | 14755.9398 | 15798.8507 | 16876.3843 | 17926.3972 | 18945.9005 | 19932.1659 | 20882.7971 | 21795.7995 | 22669.6453 | 23503.3342 | 24296.4445 | 25049.1761 | 25762.3788 | 26437.5679
sens | 0 | 0% | 0% | Option 2sens | 0 | -169956.1385 | 22640.7435 | 29227.4775 | 35032.125 | 42699.2711 | 52163.0961 | 62542.6349 | 69297.6603 | 70695.9469 | 71865.0919 | 73047.5348 | 74206.3248 | 75403.5842 | 76570.2652 | 77703.0467 | 78798.8971 | 79855.1541 | 80869.6011 | 81840.541 | 82766.8619 | 83648.0956 | 84484.464 | 85276.9115 | 86027.1216
sens | 0 | 0% | 0% | Option 2sens | 0 | -169956.1385 | 22640.7435 | 29227.4775 | 35032.125 | 42699.2711 | 52163.0961 | 62542.6349 | 69297.6603 | 70695.9469 | 71865.0919 | 73047.5348 | 74206.3248 | 75403.5842 | 76570.2652 | 77703.0467 | 78798.8971 | 79855.1541 | 80869.6011 | 81840.541 | 82766.8619 | 83648.0956 | 84484.464 | 85276.9115 | 86027.1216
sens | 0 | 0% | 0% | Option 2sens | 0 | -169956.1385 | 22640.7435 | 29227.4775 | 35032.125 | 42699.2711 | 52163.0961 | 62542.6349 | 69297.6603 | 70695.9469 | 71865.0919 | 73047.5348 | 74206.3248 | 75403.5842 | 76570.2652 | 77703.0467 | 78798.8971 | 79855.1541 | 80869.6011 | 81840.541 | 82766.8619 | 83648.0956 | 84484.464 | 85276.9115 | 86027.1216

## Option3
United Energy
EW switchboard and relay replacement
OPTION 3 | Relay replacement in 2026-27 and SWBD replacement in 2031-32
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| Switchboard |  | 50 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 2727489.4168 | 1363744.7084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Relays |  | 25 | 2023-12-31 | 1363744.7084 | 681872.3542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 1363744.7084 | 681872.3542 | 0 | 0 | 0 | 2727489.4168 | 1363744.7084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 32343.3946 | 2023-12-31 | 222256.9687 | 230621.3865 | 237173.7334 | 243325.4609 | 248675.9665 | 256237.8467 | 265871.6922 | 34283.7124 | 35828.263 | 36846.9426 | 38083.0986 | 39417.1569 | 40880.1969 | 42403.5809 | 44049.1832 | 45812.4833 | 47687.9981 | 49669.2037 | 51748.4655 | 53916.9787 | 56164.7225 | 58480.4301 | 60851.5781 | 63264.3977 | 65703.9097
| Safety risk | (after DF) |  | 2023-12-31 | 449.828 | 495.0233 | 304.7386 | 313.815 | 328.9392 | 350.1017 | 377.2831 | 144.2327 | 183.3347 | 228.2999 | 279.0322 | 335.4074 | 397.2704 | 464.4319 | 536.6657 | 613.7068 | 695.2487 | 780.9424 | 870.3953 | 963.1703 | 1058.7868 | 1156.7207 | 1256.4065 | 1357.2394 | 1458.5786
| Unplanned replacement |  |  | 2023-12-31 | 14021.5374 | 14320.7932 | 13048.8223 | 13072.8617 | 13112.919 | 13168.9691 | 13240.9606 | 1822.2093 | 1925.7731 | 2044.8661 | 2179.2336 | 2328.5467 | 2492.3945 | 2670.2755 | 2861.5912 | 3065.6389 | 3281.6074 | 3508.5723 | 3745.4934 | 3991.2136 | 4244.4595 | 4503.8431 | 4767.8667 | 5034.9286 | 5303.3315
| Unplanned fault |  |  | 2023-12-31 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 237232.3841 | 245941.2529 | 251031.3442 | 257216.1876 | 262621.8746 | 270260.9676 | 279993.9858 | 36309.4544 | 37996.6708 | 39179.4086 | 40600.6643 | 42140.411 | 43829.1618 | 45597.5883 | 47506.7401 | 49551.129 | 51724.1542 | 54018.0184 | 56423.6542 | 58930.6627 | 61527.2688 | 64200.2939 | 66935.1514 | 69715.8657 | 72525.1198
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38560 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex saving |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 5972.4688 | 7276.7528 | 8614.5936 | 9980.3837 | 11430.0479 | 267476.8426 | 274231.868 | 275630.1545 | 276799.2996 | 277981.7425 | 279140.5325 | 280337.7919 | 281504.4729 | 282637.2544 | 283733.1048 | 284789.3618 | 285803.8088 | 286774.7487 | 287701.0696 | 288582.3033 | 289418.6717 | 290211.1192 | 290961.3293
Capital expenditure
| Switchboard |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -2727489.4168 | -1363744.7084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Relays |  |  | 2023-12-31 | -1363744.7084 | -681872.3542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| Switchboard |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | -2727489.4168 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253 | -4091234.1253
| Relays |  |  | 2023-12-31 | -1363744.7084 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626 | -2045617.0626
| 0 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - Switchboard |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | -116282.9916 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875 | -174424.4875
| Annualised capex - Relays |  |  | 2023-12-31 | 0 | -82743.8947 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421
| Annualised capex - |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | -82743.8947 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -240398.8337 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296
| Annualised capex |  |  | 2023-12-31 | 0 | -82743.8947 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -240398.8337 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 5972.4688 | 7276.7528 | 8614.5936 | 9980.3837 | 11430.0479 | 267476.8426 | 274231.868 | 275630.1545 | 276799.2996 | 277981.7425 | 279140.5325 | 280337.7919 | 281504.4729 | 282637.2544 | 283733.1048 | 284789.3618 | 285803.8088 | 286774.7487 | 287701.0696 | 288582.3033 | 289418.6717 | 290211.1192 | 290961.3293
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
| Net benefits |  |  | 2023-12-31 | 0 | -82743.8947 | -118143.3733 | -116839.0893 | -115501.2485 | -114135.4584 | -228968.7859 | 18936.5131 | 25691.5384 | 27089.825 | 28258.97 | 29441.4129 | 30600.2029 | 31797.4624 | 32964.1434 | 34096.9248 | 35192.7752 | 36249.0322 | 37263.4793 | 38234.4191 | 39160.74 | 40041.9738 | 40878.3421 | 41670.7896 | 42420.9997
| First capex year |  |  | 1
| First year |  |  | 1
SENSITIVITIES
NPV | Net benefits |  |  | Option 3NPV | 0 | -82743.8947 | -118143.3733 | -116839.0893 | -115501.2485 | -114135.4584 | -228968.7859 | 18936.5131 | 25691.5384 | 27089.825 | 28258.97 | 29441.4129 | 30600.2029 | 31797.4624 | 32964.1434 | 34096.9248 | 35192.7752 | 36249.0322 | 37263.4793 | 38234.4191 | 39160.74 | 40041.9738 | 40878.3421 | 41670.7896 | 42420.9997
| Total annualised capex |  |  |  | 0 | -82743.8947 | -124115.8421 | -124115.8421 | -124115.8421 | -124115.8421 | -240398.8337 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296 | -298540.3296
| Total benefits |  |  |  | 0 | 0 | 5972.4688 | 7276.7528 | 8614.5936 | 9980.3837 | 11430.0479 | 317476.8426 | 324231.868 | 325630.1545 | 326799.2996 | 327981.7425 | 329140.5325 | 330337.7919 | 331504.4729 | 332637.2544 | 333733.1048 | 334789.3618 | 335803.8088 | 336774.7487 | 337701.0696 | 338582.3033 | 339418.6717 | 340211.1192 | 340961.3293
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 3sens1 | 0 | -91018.2842 | -130554.9575 | -129250.6735 | -127912.8327 | -126547.0427 | -253008.6692 | -10917.5199 | -4162.4945 | -2764.208 | -1595.0629 | -412.62 | 746.1699 | 1943.4294 | 3110.1104 | 4242.8918 | 5338.7423 | 6394.9992 | 7409.4463 | 8380.3862 | 9306.7071 | 10187.9408 | 11024.3092 | 11816.7567 | 12566.9668
sens2 | Capex 10% lower | -10% | 0% | Option 3sens2 | 0 | -74469.5053 | -105731.7891 | -104427.5051 | -103089.6643 | -101723.8742 | -204928.9025 | 48790.546 | 55545.5714 | 56943.8579 | 58113.003 | 59295.4459 | 60454.2359 | 61651.4953 | 62818.1763 | 63950.9578 | 65046.8082 | 66103.0652 | 67117.5122 | 68088.4521 | 69014.773 | 69896.0067 | 70732.3751 | 71524.8226 | 72275.0327
sens3 | Total benefits 10% higher | 0% | 10% | Option 3sens3 | 0 | -82743.8947 | -117546.1264 | -116111.414 | -114639.7891 | -113137.4201 | -227825.7811 | 50684.1973 | 58114.7252 | 59652.8404 | 60938.9 | 62239.5872 | 63514.2561 | 64831.2415 | 66114.5906 | 67360.6502 | 68566.0857 | 69727.9684 | 70843.8602 | 71911.894 | 72930.847 | 73900.2041 | 74820.2093 | 75691.9016 | 76517.1326
sens4 | Total benefits 10% lower | 0% | -10% | Option 3sens4 | 0 | -82743.8947 | -118740.6202 | -117566.7646 | -116362.7079 | -115133.4968 | -230111.7907 | -12811.1712 | -6731.6484 | -5473.1905 | -4420.9599 | -3356.7613 | -2313.8503 | -1236.3168 | -186.3039 | 833.1994 | 1819.4648 | 2770.096 | 3683.0984 | 4556.9442 | 5390.6331 | 6183.7434 | 6936.475 | 7649.6777 | 8324.8668
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 3sens5 | 0 | -91018.2842 | -131152.2044 | -129978.3488 | -128774.2921 | -127545.081 | -254151.674 | -42665.2041 | -36585.6813 | -35327.2234 | -34274.9929 | -33210.7943 | -32167.8833 | -31090.3498 | -30040.3369 | -29020.8336 | -28034.5682 | -27083.9369 | -26170.9346 | -25297.0887 | -24463.3999 | -23670.2895 | -22917.558 | -22204.3552 | -21529.1662
sens | 0 | 0% | 0% | Option 3sens | 0 | -82743.8947 | -118143.3733 | -116839.0893 | -115501.2485 | -114135.4584 | -228968.7859 | 18936.5131 | 25691.5384 | 27089.825 | 28258.97 | 29441.4129 | 30600.2029 | 31797.4624 | 32964.1434 | 34096.9248 | 35192.7752 | 36249.0322 | 37263.4793 | 38234.4191 | 39160.74 | 40041.9738 | 40878.3421 | 41670.7896 | 42420.9997
sens | 0 | 0% | 0% | Option 3sens | 0 | -82743.8947 | -118143.3733 | -116839.0893 | -115501.2485 | -114135.4584 | -228968.7859 | 18936.5131 | 25691.5384 | 27089.825 | 28258.97 | 29441.4129 | 30600.2029 | 31797.4624 | 32964.1434 | 34096.9248 | 35192.7752 | 36249.0322 | 37263.4793 | 38234.4191 | 39160.74 | 40041.9738 | 40878.3421 | 41670.7896 | 42420.9997
sens | 0 | 0% | 0% | Option 3sens | 0 | -82743.8947 | -118143.3733 | -116839.0893 | -115501.2485 | -114135.4584 | -228968.7859 | 18936.5131 | 25691.5384 | 27089.825 | 28258.97 | 29441.4129 | 30600.2029 | 31797.4624 | 32964.1434 | 34096.9248 | 35192.7752 | 36249.0322 | 37263.4793 | 38234.4191 | 39160.74 | 40041.9738 | 40878.3421 | 41670.7896 | 42420.9997

## Option4
United Energy
EW switchboard and relay replacement
OPTION 4 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 32343.3946 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38560 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 4NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 4sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 4sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 4sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 4sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 4sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 4sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Option5
United Energy
EW switchboard and relay replacement
OPTION 5 | 0
Not used
Count |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Value of CO2 reductions |  |  |  | $/MWh | 24.7305 | 22.3407 | 20.1963 | 18.0629 | 15.9134 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151 | 13.7151
|  |  |  | Units | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
INVESTMENT & OPERATING COST
| Capex |  | Asset life (yrs)
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  | 0 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RISK ASSUMPTIONS
| PoF (major) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PoF (reparable) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk (weighted) |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy at risk value | $/MWh | 32343.3946 | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Safety consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unplanned replacements |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental consequence | (after DF) |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Other risk - enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total risk cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTHER BENEFITS
| Reduction in CO2 emissions |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Value of reduction in CO2 emissions |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reliability in worst-served areas | $/MWh | 0 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Network resilience | $/MWh | 38560 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Enabling solar exports | $/MWh | 862.6028 | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Aesthetics | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (res) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer value of time (bus) | $/customer min | 0.34751 | mins | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communication | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Information accessibility | $/customer | 0 | customers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 1 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits 2 |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total other benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMMARY
| Risks mitigated vs base case |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital expenditure
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative capex
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualised capex
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex - < Enter description > |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Annualised capex |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating expenditure |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Risk mitigated |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other benefits value |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  |  | 2023-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| First capex year |  |  | 0
| First year |  |  | Not used
SENSITIVITIES
NPV | Net benefits |  |  | Option 5NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annualised capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total benefits |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Capex | Total benefits
sens1 | Capex 10% higher | 10% | 0% | Option 5sens1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens2 | Capex 10% lower | -10% | 0% | Option 5sens2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens3 | Total benefits 10% higher | 0% | 10% | Option 5sens3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens4 | Total benefits 10% lower | 0% | -10% | Option 5sens4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens5 | Capex 10% higher & Total benefits 10% lower | 10% | -10% | Option 5sens5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
sens | 0 | 0% | 0% | Option 5sens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consol
United Energy
EW switchboard and relay replacement
CONSOLIDATED
Discount factor |  |  |  |  | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE
[5 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
COSTS |  |  | PV
Option 1 (base case) | Energy at risk value | Option 1 (base case)Energy at risk value | 5312368.8278 | 2026-06-30 |  | 247352.5912 | 256661.4575 | 268539.6356 | 276391.2845 | 283364.2004 | 292805.6752 | 304623.6953 | 317708.4829 | 326385.9657 | 328497.3007 | 330577.6929 | 332765.3406 | 335055.2676 | 337441.8721 | 339918.9038 | 342479.4451 | 345115.8971 | 347819.972 | 350582.6919 | 353394.3946 | 356244.7472 | 359122.7682 | 362016.8579 | 364914.839 | 367804.0056
Option 1 (base case) | Capital expenditure | Option 1 (base case)Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | Option 1 (base case)Total risk cost | 4795648.2375 | 2026-06-30 |  | 264018.9204 | 273711.1307 | 286022.7936 | 294357.5382 | 301862.4956 | 311884.1438 | 324329.4925 | 338087.6117 | 347483.0894 | 350355.544 | 353238.4338 | 356267.993 | 359437.0571 | 362737.6065 | 366160.7398 | 369696.6528 | 373334.6259 | 377063.0181 | 380869.2715 | 384739.9242 | 388660.6342 | 392616.2139 | 396590.6763 | 400567.2933 | 404528.666
Option 1 (base case) |  | Option 1 (base case)
Option 1 (base case) | Annualised capex | Option 1 (base case)Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Operating expenditure | Option 1 (base case)Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Risk mitigated | Option 1 (base case)Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Other benefits value | Option 1 (base case)Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Net benefits | Option 1 (base case)Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | NPV | Option 1 (base case)NPV | 0 | 2026-06-30
Option 1 (base case) | PV of costs | Option 1 (base case)PV of costs | 0 | 2026-06-30
Option 1 (base case) | PV of benefits | Option 1 (base case)PV of benefits | 0 | 2026-06-30
Option 2 | Energy at risk value | Option 2Energy at risk value | 1173288.2545 | 2026-06-30 |  | 247352.5912 | 256661.4575 | 30926.5228 | 31893.9528 | 32877.4324 | 34280.2858 | 36082.8534 | 38154.777 | 39873.727 | 41007.4284 | 42383.162 | 43867.8524 | 45496.0881 | 47191.4814 | 49022.8931 | 50985.292 | 53072.5761 | 55277.4849 | 57591.5217 | 60004.8875 | 62506.4299 | 65083.6102 | 67722.4909 | 70407.7483 | 73122.712
Option 2 | Capital expenditure | Option 2Capital expenditure | -5531361.2095 | 2026-06-30 |  | -3794321.8312 | -1897160.9156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Total risk cost | Option 2Total risk cost | 1087531.4231 | 2026-06-30 |  | 264018.9204 | 273711.1307 | 32751.7524 | 33756.0375 | 34800.9292 | 36289.7136 | 38202.6518 | 40409.2509 | 42286.9754 | 43603.2593 | 45184.9928 | 46898.5963 | 48778.0284 | 50746.1326 | 52870.8518 | 55146.0781 | 57564.4653 | 60117.3359 | 62794.5983 | 65584.6798 | 0 | 0 | 0 | 0 | 0
Option 2 |  | Option 2
Option 2 | Annualised capex | Option 2Annualised capex | -3733597.1921 | 2026-06-30 |  | 0 | -189146.3358 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | -283719.5037 | 0 | 0 | 0 | 0 | 0
Option 2 | Operating expenditure | Option 2Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | Risk mitigated | Option 2Risk mitigated | 3708116.8144 | 2026-06-30 |  | 0 | 0 | 253271.0412 | 260601.5008 | 267061.5664 | 275594.4302 | 286126.8407 | 297678.3608 | 305196.1139 | 306752.2847 | 308053.441 | 309369.3967 | 310659.0287 | 311991.4739 | 313289.8879 | 314550.5747 | 315770.1605 | 316945.6823 | 318074.6732 | 319155.2445 | 0 | 0 | 0 | 0 | 0
Option 2 | Other benefits value | Option 2Other benefits value | 697035.4612 | 2026-06-30 |  | 0 | 0 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 0 | 0 | 0 | 0 | 0
Option 2 | Net benefits | Option 2Net benefits |  | 2026-06-30 |  | 0 | -189146.3358 | 25197.1698 | 32527.6293 | 38987.695 | 47520.5588 | 58052.9693 | 69604.4894 | 77122.2425 | 78678.4133 | 79979.5696 | 81295.5253 | 82585.1573 | 83917.6025 | 85216.0165 | 86476.7033 | 87696.2891 | 88871.8108 | 90000.8018 | 91081.373 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Option 2NPV | 671555.0835 | 2026-06-30
Option 2 | PV of costs | Option 2PV of costs | -3733597.1921 | 2026-06-30
Option 2 | PV of benefits | Option 2PV of benefits | 4405152.2755 | 2026-06-30
Option 3 | Energy at risk value | Option 3Energy at risk value | 2223208.0023 | 2026-06-30 |  | 247352.5912 | 256661.4575 | 263953.6473 | 270799.9826 | 276754.6279 | 285170.3401 | 295891.9685 | 38154.777 | 39873.727 | 41007.4284 | 42383.162 | 43867.8524 | 45496.0881 | 47191.4814 | 49022.8931 | 50985.292 | 53072.5761 | 55277.4849 | 57591.5217 | 60004.8875 | 62506.4299 | 65083.6102 | 67722.4909 | 70407.7483 | 73122.712
Option 3 | Capital expenditure | Option 3Capital expenditure | -5938350.6555 | 2026-06-30 |  | -1517728.7325 | -758864.3662 | 0 | 0 | 0 | -3035457.465 | -1517728.7325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Total risk cost | Option 3Total risk cost | 2195755.1162 | 2026-06-30 |  | 264018.9204 | 273711.1307 | 279375.9576 | 286259.148 | 292275.2055 | 300776.8486 | 311608.8477 | 40409.2509 | 42286.9754 | 43603.2593 | 45184.9928 | 46898.5963 | 48778.0284 | 50746.1326 | 52870.8518 | 55146.0781 | 57564.4653 | 60117.3359 | 62794.5983 | 65584.6798 | 0 | 0 | 0 | 0 | 0
Option 3
Option 3 | Annualised capex | Option 3Annualised capex | -3520422.9484 | 2026-06-30 |  | 0 | -92086.7269 | -138130.0903 | -138130.0903 | -138130.0903 | -138130.0903 | -267542.9023 | -332249.3082 | -332249.3082 | -332249.3082 | -332249.3082 | -332249.3082 | -332249.3082 | -332249.3082 | -332249.3082 | -332249.3082 | -332249.3082 | -332249.3082 | -332249.3082 | -332249.3082 | 0 | 0 | 0 | 0 | 0
Option 3 | Operating expenditure | Option 3Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Risk mitigated | Option 3Risk mitigated | 2599893.1212 | 2026-06-30 |  | 0 | 0 | 6646.836 | 8098.3902 | 9587.2902 | 11107.2952 | 12720.6448 | 297678.3608 | 305196.1139 | 306752.2847 | 308053.441 | 309369.3967 | 310659.0287 | 311991.4739 | 313289.8879 | 314550.5747 | 315770.1605 | 316945.6823 | 318074.6732 | 319155.2445 | 0 | 0 | 0 | 0 | 0
Option 3 | Other benefits value | Option 3Other benefits value | 458428.3682 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 55645.6323 | 0 | 0 | 0 | 0 | 0
Option 3 | Net benefits | Option 3Net benefits |  | 2026-06-30 |  | 0 | -92086.7269 | -131483.2543 | -130031.7001 | -128542.8001 | -127022.7951 | -254822.2574 | 21074.6849 | 28592.438 | 30148.6088 | 31449.7651 | 32765.7208 | 34055.3528 | 35387.798 | 36686.212 | 37946.8988 | 39166.4846 | 40342.0064 | 41470.9973 | 42551.5686 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Option 3NPV | -462101.459 | 2026-06-30
Option 3 | PV of costs | Option 3PV of costs | -3520422.9484 | 2026-06-30
Option 3 | PV of benefits | Option 3PV of benefits | 3058321.4894 | 2026-06-30
Option 4 | Energy at risk value | Option 4Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Capital expenditure | Option 4Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Total risk cost | Option 4Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | Option 4
Option 4 | Annualised capex | Option 4Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Operating expenditure | Option 4Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Risk mitigated | Option 4Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Other benefits value | Option 4Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Net benefits | Option 4Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Option 4NPV | 0 | 2026-06-30
Option 4 | PV of costs | Option 4PV of costs | 0 | 2026-06-30
Option 4 | PV of benefits | Option 4PV of benefits | 0 | 2026-06-30
Option 5 | Energy at risk value | Option 5Energy at risk value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Capital expenditure | Option 5Capital expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Total risk cost | Option 5Total risk cost | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | Option 5
Option 5 | Annualised capex | Option 5Annualised capex | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Operating expenditure | Option 5Operating expenditure | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Risk mitigated | Option 5Risk mitigated | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Other benefits value | Option 5Other benefits value | 0 | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Net benefits | Option 5Net benefits |  | 2026-06-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Option 5NPV | 0 | 2026-06-30
Option 5 | PV of costs | Option 5PV of costs | 0 | 2026-06-30
Option 5 | PV of benefits | Option 5PV of benefits | 0 | 2026-06-30
CHART DATA | [5 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Option 2 | Annualised capex | -1 |  |  | Option 2 annualised capex | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0.28372 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Total risk cost | 1 |  |  | Option 1 (base case) risk cost | 0.26402 | 0.27371 | 0.28602 | 0.29436 | 0.30186 | 0.31188 | 0.32433 | 0.33809 | 0.34748 | 0.35036 | 0.35324 | 0.35627 | 0.35944 | 0.36274 | 0.36616 | 0.3697 | 0.37333 | 0.37706 | 0.38087 | 0.38474 | 0.38866 | 0.39262 | 0.39659 | 0.40057 | 0.40453
[6 empty] | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51
Energy at risk | Energy at risk (weighted) | 0 |  |  | Energy at risk energy at risk (weighted) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 (base case) | Energy at risk value | 0.33049 |  |  | Option 1 (base case) risk cost | 0.22226 | 0.23062 | 0.24129 | 0.24835 | 0.25461 | 0.2631 | 0.27372 | 0.28547 | 0.29327 | 0.29517 | 0.29704 | 0.299 | 0.30106 | 0.30321 | 0.30543 | 0.30773 | 0.3101 | 0.31253 | 0.31501 | 0.31754 | 0.3201 | 0.32269 | 0.32529 | 0.32789 | 0.33049

## Sensitivity_calcs
United Energy
EW switchboard and relay replacement
SENSITIVITY CALCULATIONS
Discount factor | [6 empty] | 0 | 0.98295 | 0.94971 | 0.91759 | 0.88656 | 0.85658 | 0.82761 | 0.79963 | 0.77259 | 0.74646 | 0.72122 | 0.69683 | 0.67326 | 0.6505 | 0.6285 | 0.60725 | 0.58671 | 0.56687 | 0.5477 | 0.52918 | 0.51129 | 0.494 | 0.47729 | 0.46115 | 0.44556 | 0.43049
Count | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Analysis period | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[7 empty] | 2026-06-30 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
PV
[25 empty] | 90000.8018 | 91081.373 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | NPV | Net benefits | OPTION 1 (base case)NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens1 | Capex 10% higher | OPTION 1 (base case)sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens2 | Capex 10% lower | OPTION 1 (base case)sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens3 | Total benefits 10% higher | OPTION 1 (base case)sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens4 | Total benefits 10% lower | OPTION 1 (base case)sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens5 | Capex 10% higher & Total benefits 10% lower | OPTION 1 (base case)sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPTION 1 (base case) | sens | 0 | OPTION 1 (base case)sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 | NPV | Net benefits | Option 2NPV |  | 671555.0835 |  | 0 | 0 | -189146.3358 | 25197.1698 | 32527.6293 | 38987.695 | 47520.5588 | 58052.9693 | 69604.4894 | 77122.2425 | 78678.4133 | 79979.5696 | 81295.5253 | 82585.1573 | 83917.6025 | 85216.0165 | 86476.7033 | 87696.2891 | 88871.8108 | 90000.8018 | 91081.373 | 0 | 0 | 0 | 0 | 0
Option 2 | sens1 | Capex 10% higher | Option 2sens1 |  | 298195.3643 |  | 0 | 0 | -208060.9694 | -3174.7806 | 4155.679 | 10615.7446 | 19148.6084 | 29681.0189 | 41232.539 | 48750.2921 | 50306.4629 | 51607.6192 | 52923.5749 | 54213.2069 | 55545.6521 | 56844.0661 | 58104.7529 | 59324.3387 | 60499.8605 | 61628.8514 | 62709.4227 | 0 | 0 | 0 | 0 | 0
Option 2 | sens2 | Capex 10% lower | Option 2sens2 |  | 1044914.8027 |  | 0 | 0 | -170231.7022 | 53569.1202 | 60899.5797 | 67359.6454 | 75892.5092 | 86424.9197 | 97976.4397 | 105494.1929 | 107050.3637 | 108351.52 | 109667.4756 | 110957.1076 | 112289.5528 | 113587.9669 | 114848.6537 | 116068.2395 | 117243.7612 | 118372.7522 | 119453.3234 | 0 | 0 | 0 | 0 | 0
Option 2 | sens3 | Total benefits 10% higher | Option 2sens3 |  | 1112070.311 |  | 0 | 0 | -189146.3358 | 56088.8372 | 64152.3426 | 71258.4148 | 80644.565 | 92230.2166 | 104936.8887 | 113206.4171 | 114918.205 | 116349.4769 | 117797.0282 | 119215.6234 | 120681.3131 | 122109.5685 | 123496.324 | 124837.8684 | 126130.9423 | 127372.8324 | 128561.4607 | 0 | 0 | 0 | 0 | 0
Option 2 | sens4 | Total benefits 10% lower | Option 2sens4 |  | 231039.8559 |  | 0 | 0 | -189146.3358 | -5694.4975 | 902.916 | 6716.9751 | 14396.5525 | 23875.722 | 34272.09 | 41038.0679 | 42438.6216 | 43609.6623 | 44794.0224 | 45954.6912 | 47153.8918 | 48322.4645 | 49457.0826 | 50554.7098 | 51612.6794 | 52628.7713 | 53601.2854 | 0 | 0 | 0 | 0 | 0
Option 2 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 2sens5 |  | -142319.8633 |  | 0 | 0 | -208060.9694 | -34066.4479 | -27469.0344 | -21654.9753 | -13975.3978 | -4496.2284 | 5900.1397 | 12666.1175 | 14066.6712 | 15237.7119 | 16422.072 | 17582.7408 | 18781.9415 | 19950.5141 | 21085.1322 | 22182.7595 | 23240.729 | 24256.8209 | 25229.335 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 671555.0835 |  | 0 | 0 | -189146.3358 | 25197.1698 | 32527.6293 | 38987.695 | 47520.5588 | 58052.9693 | 69604.4894 | 77122.2425 | 78678.4133 | 79979.5696 | 81295.5253 | 82585.1573 | 83917.6025 | 85216.0165 | 86476.7033 | 87696.2891 | 88871.8108 | 90000.8018 | 91081.373 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 671555.0835 |  | 0 | 0 | -189146.3358 | 25197.1698 | 32527.6293 | 38987.695 | 47520.5588 | 58052.9693 | 69604.4894 | 77122.2425 | 78678.4133 | 79979.5696 | 81295.5253 | 82585.1573 | 83917.6025 | 85216.0165 | 86476.7033 | 87696.2891 | 88871.8108 | 90000.8018 | 91081.373 | 0 | 0 | 0 | 0 | 0
Option 2 | sens | 0 | Option 2sens |  | 671555.0835 |  | 0 | 0 | -189146.3358 | 25197.1698 | 32527.6293 | 38987.695 | 47520.5588 | 58052.9693 | 69604.4894 | 77122.2425 | 78678.4133 | 79979.5696 | 81295.5253 | 82585.1573 | 83917.6025 | 85216.0165 | 86476.7033 | 87696.2891 | 88871.8108 | 90000.8018 | 91081.373 | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0 | -92086.7269 | -131483.2543 | -130031.7001 | -128542.8001 | -127022.7951 | -254822.2574 | 21074.6849 | 28592.438 | 30148.6088 | 31449.7651 | 32765.7208 | 34055.3528 | 35387.798 | 36686.212 | 37946.8988 | 39166.4846 | 40342.0064 | 41470.9973 | 42551.5686 | 0 | 0 | 0 | 0 | 0
Option 3 | NPV | Net benefits | Option 3NPV |  | -462101.459 |  | 0 | 0 | -92086.7269 | -131483.2543 | -130031.7001 | -128542.8001 | -127022.7951 | -254822.2574 | 21074.6849 | 28592.438 | 30148.6088 | 31449.7651 | 32765.7208 | 34055.3528 | 35387.798 | 36686.212 | 37946.8988 | 39166.4846 | 40342.0064 | 41470.9973 | 42551.5686 | 0 | 0 | 0 | 0 | 0
Option 3 | sens1 | Capex 10% higher | Option 3sens1 |  | -814143.7538 |  | 0 | 0 | -101295.3995 | -145296.2633 | -143844.7091 | -142355.8092 | -140835.8041 | -281576.5477 | -12150.2459 | -4632.4928 | -3076.322 | -1775.1657 | -459.21 | 830.422 | 2162.8672 | 3461.2812 | 4721.968 | 5941.5538 | 7117.0755 | 8246.0665 | 9326.6377 | 0 | 0 | 0 | 0 | 0
Option 3 | sens2 | Capex 10% lower | Option 3sens2 |  | -110059.1642 |  | 0 | 0 | -82878.0542 | -117670.2452 | -116218.691 | -114729.7911 | -113209.7861 | -228067.9672 | 54299.6157 | 61817.3689 | 63373.5396 | 64674.6959 | 65990.6516 | 67280.2836 | 68612.7288 | 69911.1428 | 71171.8296 | 72391.4155 | 73566.9372 | 74695.9282 | 75776.4994 | 0 | 0 | 0 | 0 | 0
Option 3 | sens3 | Total benefits 10% higher | Option 3sens3 |  | -156269.3101 |  | 0 | 0 | -92086.7269 | -130818.5706 | -129221.8611 | -127584.0711 | -125912.0656 | -253550.193 | 56407.0842 | 64676.6127 | 66388.4005 | 67819.6724 | 69267.2237 | 70685.8189 | 72151.5086 | 73579.764 | 74966.5195 | 76308.0639 | 77601.1378 | 78843.0279 | 80031.6562 | 0 | 0 | 0 | 0 | 0
Option 3 | sens4 | Total benefits 10% lower | Option 3sens4 |  | -767933.6079 |  | 0 | 0 | -92086.7269 | -132147.9379 | -130841.5391 | -129501.5291 | -128133.5246 | -256094.3219 | -14257.7144 | -7491.7366 | -6091.1829 | -4920.1422 | -3735.7821 | -2575.1133 | -1375.9126 | -207.34 | 927.2781 | 2024.9053 | 3082.8749 | 4098.9668 | 5071.4809 | 0 | 0 | 0 | 0 | 0
Option 3 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 3sens5 |  | -1119975.9028 |  | 0 | 0 | -101295.3995 | -145960.9469 | -144654.5481 | -143314.5382 | -141946.5337 | -282848.6121 | -47482.6453 | -40716.6674 | -39316.1137 | -38145.073 | -36960.7129 | -35800.0441 | -34600.8435 | -33432.2708 | -32297.6527 | -31200.0255 | -30142.0559 | -29125.964 | -28153.4499 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -462101.459 |  | 0 | 0 | -92086.7269 | -131483.2543 | -130031.7001 | -128542.8001 | -127022.7951 | -254822.2574 | 21074.6849 | 28592.438 | 30148.6088 | 31449.7651 | 32765.7208 | 34055.3528 | 35387.798 | 36686.212 | 37946.8988 | 39166.4846 | 40342.0064 | 41470.9973 | 42551.5686 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -462101.459 |  | 0 | 0 | -92086.7269 | -131483.2543 | -130031.7001 | -128542.8001 | -127022.7951 | -254822.2574 | 21074.6849 | 28592.438 | 30148.6088 | 31449.7651 | 32765.7208 | 34055.3528 | 35387.798 | 36686.212 | 37946.8988 | 39166.4846 | 40342.0064 | 41470.9973 | 42551.5686 | 0 | 0 | 0 | 0 | 0
Option 3 | sens | 0 | Option 3sens |  | -462101.459 |  | 0 | 0 | -92086.7269 | -131483.2543 | -130031.7001 | -128542.8001 | -127022.7951 | -254822.2574 | 21074.6849 | 28592.438 | 30148.6088 | 31449.7651 | 32765.7208 | 34055.3528 | 35387.798 | 36686.212 | 37946.8988 | 39166.4846 | 40342.0064 | 41470.9973 | 42551.5686 | 0 | 0 | 0 | 0 | 0
Option 4 | NPV | Net benefits | Option 4NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens1 | Capex 10% higher | Option 4sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens2 | Capex 10% lower | Option 4sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens3 | Total benefits 10% higher | Option 4sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens4 | Total benefits 10% lower | Option 4sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 4sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | sens | 0 | Option 4sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | NPV | Net benefits | Option 5NPV |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens1 | Capex 10% higher | Option 5sens1 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens2 | Capex 10% lower | Option 5sens2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens3 | Total benefits 10% higher | Option 5sens3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens4 | Total benefits 10% lower | Option 5sens4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens5 | Capex 10% higher & Total benefits 10% lower | Option 5sens5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | sens | 0 | Option 5sens |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RESULTS
|  | 0 | 0 | 0 | 1 | 1 |  | 2028-29: #NAME?
|  | Option 1 (base case) | Option 2 | Option 3 | Option 4 | Option 5 |  | 2026-27: Max; 2028-29: Preferred
NPV | None | 0 | 0.67156 | -0.4621 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens1 | Capex 10% higher | 0 | 0.2982 | -0.81414 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens2 | Capex 10% lower | 0 | 1.0449 | -0.11006 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens3 | Total benefits 10% higher | 0 | 1.1121 | -0.15627 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens4 | Total benefits 10% lower | 0 | 0.23104 | -0.76793 |  |  |  | 2026-27: #NAME?; 2028-29: Option 2
sens5 | Capex 10% higher & Total benefits 10% lower | 0 | -0.14232 | -1.12 |  |  |  | 2026-27: #NAME?; 2028-29: Option 1 (base case)
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?
sens | 0 | [6 empty] | 2026-27: #NAME?; 2028-29: #NAME?

## Workings_costs
United Energy
EW switchboard and relay replacement
WORKINGS - COSTS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
|  | SWBD online monitoring annual cost ($) | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
|  | Relay annual maintenance cost ($) | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778
|  | Total opex cost ($) | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778
Option 2 - SWBD and relay replacement completed in 2027-28
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | SWBD capex profile ($) | 2045617.0626 | 1022808.5313 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Relay capex profile ($) | 1363744.7084 | 681872.3542 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total capex ($) | 3409361.7711 | 1704680.8855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
|  | SWBD online monitoring annual cost ($) | 2026-27: 50000; 2027-28: 50000
|  | Relay annual maintenance cost ($) | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778
|  | Total opex cost ($) | 52527.7778 | 52527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778
|  | Opex saving | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
Option 3 - Relay replacement in 2026-27 and SWBD replacement in 2031-32
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
|  | SWBD capex profile ($) | 2031-32: 2727489.4168; 2032-33: 1363744.7084; 2040-41: 0; 2041-42: 0; 2042-43: 0; 2043-44: 0; 2044-45: 0; 2045-46: 0; 2046-47: 0; 2047-48: 0; 2048-49: 0; 2049-50: 0; 2050-51: 0
|  | Relay capex profile ($) | 2026-27: 1363744.7084; 2027-28: 681872.3542; 2040-41: 0; 2041-42: 0; 2042-43: 0; 2043-44: 0; 2044-45: 0; 2045-46: 0; 2046-47: 0; 2047-48: 0; 2048-49: 0; 2049-50: 0; 2050-51: 0
|  | Total capex ($) | 1363744.7084 | 681872.3542 | 0 | 0 | 0 | 2727489.4168 | 1363744.7084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
Opex
|  | SWBD online monitoring annual cost ($) | 2026-27: 50000; 2027-28: 50000; 2028-29: 50000; 2029-30: 50000; 2030-31: 50000; 2031-32: 50000; 2032-33: 50000
|  | Relay annual maintenance cost ($) | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778
|  | Total opex cost ($) | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 52527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778 | 2527.7778
|  | Opex saving | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000

## Workings_risks
United Energy
EW switchboard and relay replacement
WORKINGS - RISKS
Option 1 - continue existing maintenance with no proactive replacement cost
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
SWBD risks
|  | Energy at Risk ($) | 219847.7453 | 227404.4742 | 237118.9401 | 243101.0385 | 248159.4634 | 255295.421 | 264371.0407 | 274318.1854 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604
|  | Safety Risk | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713
|  | Unplanned Replacement Risk | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088
|  | Unplanned Fault Risk | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05
|  | Total SWBD risks | 233694.317 | 241251.0459 | 250965.5118 | 256947.6102 | 262006.0351 | 269141.9928 | 278217.6124 | 288164.7571 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321 | 294149.3321
Relay risks
|  | Energy at Risk (MWh) | 0.074489 | 0.099461 | 0.1291 | 0.16227 | 0.19959 | 0.24126 | 0.28898 | 0.34494 | 0.40098 | 0.45964 | 0.51743 | 0.57821 | 0.64183 | 0.70813 | 0.77694 | 0.84808 | 0.92132 | 0.99645 | 1.0732 | 1.1513 | 1.2305 | 1.3105 | 1.3909 | 1.4714 | 1.5516
|  | Energy at Risk ($) | 2409.2234 | 3216.9123 | 4175.5016 | 5248.4483 | 6455.4889 | 7803.1035 | 9346.4845 | 11156.5857 | 12969.1031 | 14866.2286 | 16735.5507 | 18701.2465 | 20758.8446 | 22903.3117 | 25129.0315 | 27429.7883 | 29798.7541 | 32228.482 | 34710.9049 | 37237.341 | 39798.5057 | 42384.5317 | 44984.9961 | 47588.9571 | 50184.9978
|  | Safety Risk | 148.1151 | 193.3103 | 244.4171 | 301.3728 | 364.0992 | 432.5001 | 506.4605 | 585.8446 | 670.4944 | 760.2284 | 854.8408 | 954.1 | 1057.748 | 1165.4998 | 1277.0427 | 1392.0366 | 1510.1133 | 1630.8777 | 1753.9077 | 1878.7551 | 2004.9475 | 2131.9889 | 2259.3621 | 2386.5305 | 2512.9409
|  | Unplanned Replacement Risk | 980.7286 | 1279.9844 | 1618.3825 | 1995.5091 | 2410.845 | 2863.7548 | 3353.4762 | 3879.1096 | 4439.6091 | 5033.7739 | 5660.2402 | 6317.4748 | 7003.7694 | 7717.2366 | 8455.8066 | 9217.2264 | 9999.0595 | 10798.6884 | 11613.3183 | 12439.9831 | 13275.5529 | 14116.7445 | 14960.1327 | 15802.1652 | 16639.1783
|  | Total relay risks | 3538.1415 | 4690.3065 | 6038.4302 | 7545.4925 | 9230.6327 | 11099.5997 | 13206.7102 | 15621.8848 | 18079.6076 | 20660.6906 | 23251.1492 | 25973.3996 | 28821.0039 | 31786.7562 | 34862.6578 | 38039.8993 | 41308.8482 | 44659.0445 | 48079.2041 | 51557.2305 | 55080.2367 | 58634.5755 | 62205.8818 | 65779.1242 | 69338.6686
Total SWBD and relay risk
|  | Energy at Risk ($) | 222256.9687 | 230621.3865 | 241294.4417 | 248349.4867 | 254614.9523 | 263098.5245 | 273717.5252 | 285474.7711 | 293271.8635 | 295168.989 | 297038.3111 | 299004.0069 | 301061.605 | 303206.072 | 305431.7919 | 307732.5487 | 310101.5145 | 312531.2423 | 315013.6653 | 317540.1014 | 320101.2661 | 322687.2921 | 325287.7565 | 327891.7175 | 330487.7582
|  | Safety risk | 449.828 | 495.0233 | 546.1301 | 603.0858 | 665.8121 | 734.2131 | 808.1735 | 887.5576 | 972.2073 | 1061.9414 | 1156.5538 | 1255.813 | 1359.461 | 1467.2128 | 1578.7557 | 1693.7496 | 1811.8263 | 1932.5907 | 2055.6206 | 2180.4681 | 2306.6605 | 2433.7019 | 2561.0751 | 2688.2435 | 2814.6538
|  | Unplanned replacement | 14021.5374 | 14320.7932 | 14659.1913 | 15036.3178 | 15451.6538 | 15904.5636 | 16394.2849 | 16919.9183 | 17480.4179 | 18074.5827 | 18701.049 | 19358.2836 | 20044.5782 | 20758.0453 | 21496.6154 | 22258.0352 | 23039.8682 | 23839.4971 | 24654.1271 | 25480.7918 | 26316.3617 | 27157.5532 | 28000.9415 | 28842.974 | 29679.987
|  | Unplanned fault | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05
|  | Total SWBD and relay risks | 237232.3841 | 245941.2529 | 257003.813 | 264492.9404 | 271236.4682 | 280241.3512 | 291424.0337 | 303786.297 | 312228.5388 | 314809.5631 | 317399.9639 | 320122.1535 | 322969.6942 | 325935.3802 | 329011.213 | 332188.3834 | 335457.259 | 338807.3802 | 342227.463 | 345705.4114 | 349228.3383 | 352782.5972 | 356353.8231 | 359926.9849 | 363486.4491
Option 2 - SWBD and relay replacement completed in 2027-28
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
SWBD risks
|  | Energy at Risk ($) | 219847.7453 | 227404.4742 | 27734.0209 | 28433.6694 | 29025.2876 | 29859.8892 | 30921.3481 | 32084.7386 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792
|  | Safety Risk | 301.713 | 301.713 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956
|  | Unplanned Replacement Risk | 13040.8088 | 13040.8088 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128
|  | Unplanned Fault Risk | 504.05 | 504.05 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3
|  | Total SWBD risks | 233694.317 | 241251.0459 | 29363.0294 | 30062.6778 | 30654.296 | 31488.8976 | 32550.3565 | 33713.747 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876
Relay risks
|  | Energy at Risk (MWh) | 0.074489 | 0.099461 | 0.0016941 | 0.0069387 | 0.015969 | 0.029138 | 0.046397 | 0.067988 | 0.094102 | 0.1256 | 0.16382 | 0.20506 | 0.2503 | 0.2974 | 0.34828 | 0.4028 | 0.46078 | 0.52204 | 0.58633 | 0.65337 | 0.72287 | 0.79447 | 0.86778 | 0.94238 | 1.0178
|  | Energy at Risk ($) | 2409.2234 | 3216.9123 | 54.7933 | 224.4224 | 516.5031 | 942.4257 | 1500.6515 | 2198.9738 | 3043.5839 | 4062.2634 | 5298.4194 | 6632.4777 | 8095.5177 | 9618.9017 | 11264.504 | 13027.8041 | 14903.3189 | 16884.5245 | 18963.7864 | 21132.2996 | 23380.0433 | 25695.7509 | 28066.899 | 30479.7186 | 32919.2305
|  | Safety Risk | 148.1151 | 193.3103 | 3.0256 | 12.102 | 27.2262 | 48.3887 | 75.5701 | 108.7371 | 147.839 | 192.8042 | 243.5365 | 299.9118 | 361.7748 | 428.9362 | 501.1701 | 578.2111 | 659.753 | 745.4468 | 834.8996 | 927.6747 | 1023.2912 | 1121.2251 | 1220.9108 | 1321.7437 | 1423.083
|  | Unplanned Replacement Risk | 980.7286 | 1279.9844 | 8.0135 | 32.0529 | 72.1102 | 128.1603 | 200.1518 | 287.9965 | 391.5603 | 510.6533 | 645.0208 | 794.3339 | 958.1817 | 1136.0627 | 1327.3784 | 1531.4261 | 1747.3947 | 1974.3595 | 2211.2806 | 2457.0008 | 2710.2467 | 2969.6303 | 3233.654 | 3500.7158 | 3769.1187
|  | Total relay risks | 3538.1415 | 4690.3065 | 65.8341 | 268.5843 | 615.8555 | 1119.0039 | 1776.4198 | 2595.7753 | 3583.0773 | 4765.8466 | 6187.1405 | 7726.9285 | 9415.7245 | 11184.1981 | 13093.4008 | 15137.8442 | 17310.9274 | 19604.8529 | 22010.5529 | 24517.6285 | 27114.304 | 29787.4008 | 32522.3315 | 35303.1205 | 38112.45
Total SWBD and relay risk
|  | Energy at Risk ($) | 222256.9687 | 230621.3865 | 27788.8142 | 28658.0918 | 29541.7906 | 30802.3149 | 32421.9996 | 34283.7124 | 35828.263 | 36846.9426 | 38083.0986 | 39417.1569 | 40880.1969 | 42403.5809 | 44049.1832 | 45812.4833 | 47687.9981 | 49669.2037 | 51748.4655 | 53916.9787 | 56164.7225 | 58480.4301 | 60851.5781 | 63264.3977 | 65703.9097
|  | Safety risk | 449.828 | 495.0233 | 38.5212 | 47.5977 | 62.7218 | 83.8844 | 111.0657 | 144.2327 | 183.3347 | 228.2999 | 279.0322 | 335.4074 | 397.2704 | 464.4319 | 536.6657 | 613.7068 | 695.2487 | 780.9424 | 870.3953 | 963.1703 | 1058.7868 | 1156.7207 | 1256.4065 | 1357.2394 | 1458.5786
|  | Unplanned replacement | 14021.5374 | 14320.7932 | 1542.2263 | 1566.2657 | 1606.323 | 1662.3731 | 1734.3646 | 1822.2093 | 1925.7731 | 2044.8661 | 2179.2336 | 2328.5467 | 2492.3945 | 2670.2755 | 2861.5912 | 3065.6389 | 3281.6074 | 3508.5723 | 3745.4934 | 3991.2136 | 4244.4595 | 4503.8431 | 4767.8667 | 5034.9286 | 5303.3315
|  | Unplanned fault | 504.05 | 504.05 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3
|  | Total SWBD and relay risks | 237232.3841 | 245941.2529 | 29428.8617 | 30331.2552 | 31270.1355 | 32607.8724 | 34326.7299 | 36309.4544 | 37996.6708 | 39179.4086 | 40600.6643 | 42140.411 | 43829.1618 | 45597.5883 | 47506.7401 | 49551.129 | 51724.1542 | 54018.0184 | 56423.6542 | 58930.6627 | 61527.2688 | 64200.2939 | 66935.1514 | 69715.8657 | 72525.1198
Option 3 - Relay replacement in 2026-27 and SWBD replacement in 2031-32
|  |  | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51
SWBD risks
|  | Energy at Risk ($, Weighted) | 219847.7453 | 227404.4742 | 237118.9401 | 243101.0385 | 248159.4634 | 255295.421 | 264371.0407 | 32084.7386 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792
|  | Safety Risk | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956
|  | Unplanned Replacement Risk | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128
|  | Unplanned Fault Risk | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3
|  | Total SWBD risks | 233694.317 | 241251.0459 | 250965.5118 | 256947.6102 | 262006.0351 | 269141.9928 | 278217.6124 | 33713.747 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876 | 34413.6876
Relay risks
|  | Energy at Risk (MWh) | 0.074489 | 0.099461 | 0.0016941 | 0.0069387 | 0.015969 | 0.029138 | 0.046397 | 0.067988 | 0.094102 | 0.1256 | 0.16382 | 0.20506 | 0.2503 | 0.2974 | 0.34828 | 0.4028 | 0.46078 | 0.52204 | 0.58633 | 0.65337 | 0.72287 | 0.79447 | 0.86778 | 0.94238 | 1.0178
|  | Energy at Risk ($) | 2409.2234 | 3216.9123 | 54.7933 | 224.4224 | 516.5031 | 942.4257 | 1500.6515 | 2198.9738 | 3043.5839 | 4062.2634 | 5298.4194 | 6632.4777 | 8095.5177 | 9618.9017 | 11264.504 | 13027.8041 | 14903.3189 | 16884.5245 | 18963.7864 | 21132.2996 | 23380.0433 | 25695.7509 | 28066.899 | 30479.7186 | 32919.2305
|  | Safety Risk | 148.1151 | 193.3103 | 3.0256 | 12.102 | 27.2262 | 48.3887 | 75.5701 | 108.7371 | 147.839 | 192.8042 | 243.5365 | 299.9118 | 361.7748 | 428.9362 | 501.1701 | 578.2111 | 659.753 | 745.4468 | 834.8996 | 927.6747 | 1023.2912 | 1121.2251 | 1220.9108 | 1321.7437 | 1423.083
|  | Unplanned Replacement Risk | 980.7286 | 1279.9844 | 8.0135 | 32.0529 | 72.1102 | 128.1603 | 200.1518 | 287.9965 | 391.5603 | 510.6533 | 645.0208 | 794.3339 | 958.1817 | 1136.0627 | 1327.3784 | 1531.4261 | 1747.3947 | 1974.3595 | 2211.2806 | 2457.0008 | 2710.2467 | 2969.6303 | 3233.654 | 3500.7158 | 3769.1187
|  | Total relay risks | 3538.1415 | 4690.3065 | 65.8341 | 268.5843 | 615.8555 | 1119.0039 | 1776.4198 | 2595.7753 | 3583.0773 | 4765.8466 | 6187.1405 | 7726.9285 | 9415.7245 | 11184.1981 | 13093.4008 | 15137.8442 | 17310.9274 | 19604.8529 | 22010.5529 | 24517.6285 | 27114.304 | 29787.4008 | 32522.3315 | 35303.1205 | 38112.45
Total SWBD and relay risk
|  | Energy at Risk ($) | 222256.9687 | 230621.3865 | 237173.7334 | 243325.4609 | 248675.9665 | 256237.8467 | 265871.6922 | 34283.7124 | 35828.263 | 36846.9426 | 38083.0986 | 39417.1569 | 40880.1969 | 42403.5809 | 44049.1832 | 45812.4833 | 47687.9981 | 49669.2037 | 51748.4655 | 53916.9787 | 56164.7225 | 58480.4301 | 60851.5781 | 63264.3977 | 65703.9097
|  | Safety risk | 449.828 | 495.0233 | 304.7386 | 313.815 | 328.9392 | 350.1017 | 377.2831 | 144.2327 | 183.3347 | 228.2999 | 279.0322 | 335.4074 | 397.2704 | 464.4319 | 536.6657 | 613.7068 | 695.2487 | 780.9424 | 870.3953 | 963.1703 | 1058.7868 | 1156.7207 | 1256.4065 | 1357.2394 | 1458.5786
|  | Unplanned replacement | 14021.5374 | 14320.7932 | 13048.8223 | 13072.8617 | 13112.919 | 13168.9691 | 13240.9606 | 1822.2093 | 1925.7731 | 2044.8661 | 2179.2336 | 2328.5467 | 2492.3945 | 2670.2755 | 2861.5912 | 3065.6389 | 3281.6074 | 3508.5723 | 3745.4934 | 3991.2136 | 4244.4595 | 4503.8431 | 4767.8667 | 5034.9286 | 5303.3315
|  | Unplanned fault | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3
|  | Total SWBD and relay risks | 237232.3841 | 245941.2529 | 251031.3442 | 257216.1876 | 262621.8746 | 270260.9676 | 279993.9858 | 36309.4544 | 37996.6708 | 39179.4086 | 40600.6643 | 42140.411 | 43829.1618 | 45597.5883 | 47506.7401 | 49551.129 | 51724.1542 | 54018.0184 | 56423.6542 | 58930.6627 | 61527.2688 | 64200.2939 | 66935.1514 | 69715.8657 | 72525.1198

## SWBD risks
United Energy
EW switchboard and relay replacement
Input Data - Station Configuration |  | Constants |  |  | POF METHOD | FIXED | Modifier (x) | Comment
Substation: | EW | Major Failure CoC |  |  | PoF (#1) | 0.2125% | 100%
Asset Type | Indoor CB | Minor Failure CoC |  |  | PoF (#2) | 0.2125% | 100%
VCR | 32.343 | Major Failure CoC - used | 3068425.5939 |  | PoF (#3) | 100% | 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 118600 |  | PoF (#4) | 0% | 100%
Scenario #1: EW - Indoor CB | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 6404.8481 | 6624.5971 | 6852.9869 | 7144.096 | 7335.7844 | 7482.06 | 7704.4433 | 7994.0684 | 8269.2673 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244
Online Monitoring | 100% | 50000 | Energy | 6971.7168 | 7200.5487 | 7446.4505 | 7768.388 | 7937.6419 | 8117.6634 | 8334.215 | 8593.7743 | 8976.8158 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646 | 9108.3646
Physical Separation | 0% | 300000 | Energy | 6404.8481 | 6624.5971 | 6852.9869 | 7144.096 | 7335.7844 | 7482.06 | 7704.4433 | 7994.0684 | 8269.2673 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244 | 8477.2244
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425% | 0.425%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 212652.2726 | 219847.7453 | 227404.4742 | 237118.9401 | 243101.0385 | 248159.4634 | 255295.421 | 264371.0407 | 274318.1854 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604 | 280302.7604
Replace 1 Asset | 0% | 2557021.3283 | Safety Risk | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713 | 301.713
Replace 2 Assets | 0% | 5114042.6566 | Unplanned Replacement Risk | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088 | 13040.8088
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05 | 504.05
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750 | 51750
|  |  | Total Life Cycle Cost | 278248.8444 | 285444.317 | 293001.0459 | 302715.5118 | 308697.6102 | 313756.0351 | 320891.9928 | 329967.6124 | 339914.7571 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321 | 345899.3321
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: FIXED; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | EW | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.25%; 100% 2028: 100%
Asset Type | Indoor CB | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.25%; 100% 2028: 100%
VCR | 32.343 | Major Failure CoC - used | 3068425.5939 | PoF (#4) 2026: PoF (#3); 0% 2027: 100%; 100% 2028: 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 118600 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #2: EW - Indoor CB | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 7543.8712 | 7802.7024 | 8071.7111 | 835.5944 | 858.0137 | 875.1217 | 901.131 | 935.0048 | 967.1914 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135
Online Monitoring | 0% | 0 | Energy | 8211.5704 | 8481.1002 | 8770.7361 | 908.6027 | 928.398 | 949.4527 | 974.78 | 1005.1372 | 1049.9365 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322
Physical Separation | 0% | 300000 | Energy | 7543.8712 | 7802.7024 | 8071.7111 | 835.5944 | 858.0137 | 875.1217 | 901.131 | 935.0048 | 967.1914 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.5% | 0.5% | 0.5% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.5% | 0.5% | 0.5% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 250470.0435 | 258945.2307 | 267845.9229 | 27734.0209 | 28433.6694 | 29025.2876 | 29859.8892 | 30921.3481 | 32084.7386 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792
Replace 1 Asset | 0% | 2557021.3283 | Safety Risk | 354.9564 | 354.9564 | 354.9564 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956
Replace 2 Assets | 100% | 5114042.6566 | Unplanned Replacement Risk | 15342.128 | 15342.128 | 15342.128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 593 | 593 | 593 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093
|  |  | Total Life Cycle Cost | 266760.128 | 275235.3151 | 284136.0073 | 247393.6387 | 248093.2871 | 248684.9053 | 249519.507 | 250580.9659 | 251744.3564 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969
Input Data - Station Configuration |  | Constants |  | PoF (#4) 2026: POF METHOD; 0% 2027: FIXED; 100% 2028: Modifier (x); 100% 2029: Comment
Substation: | EW | Major Failure CoC |  | PoF (#4) 2026: PoF (#1); 0% 2027: 0.25%; 100% 2028: 100%
Asset Type | Indoor CB | Minor Failure CoC |  | PoF (#4) 2026: PoF (#2); 0% 2027: 0.25%; 100% 2028: 100%
VCR | 32.343 | Major Failure CoC - used | 3068425.5939 | PoF (#4) 2026: PoF (#3); 0% 2027: 100%; 100% 2028: 100%
Load Profile (PoE) | 50% | Minor Failure CoC - used | 118600 | PoF (#4) 2026: PoF (#4); 0% 2027: 0%; 100% 2028: 100%
Scenario #3: EW - Indoor CB | Setting | Unit Price | Model Output | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
Spare Available | 0% | 0 | Energy | 7543.8712 | 7802.7024 | 8071.7111 | 8414.5939 | 8640.3741 | 8812.6649 | 9074.5991 | 9415.734 | 967.1914 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135
Online Monitoring | 0% | 0 | Energy | 8211.5704 | 8481.1002 | 8770.7361 | 9149.9307 | 9349.2866 | 9561.3252 | 9816.3906 | 10122.1128 | 1049.9365 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322 | 1065.322
Physical Separation | 0% | 300000 | Energy | 7543.8712 | 7802.7024 | 8071.7111 | 8414.5939 | 8640.3741 | 8812.6649 | 9074.5991 | 9415.734 | 967.1914 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135 | 991.5135
More Frequent Maintenance | 0% | 4000 | Pr (Terminal Failure) | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05%
Staggered Maintenance | 0% | 650 | Pr (Repairable Failure) | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05% | 0.05%
Bunded | 0 | 300000
Refurbish Assets | 0 | 500000 | Energy at Risk ($, Weighted) | 250470.0435 | 258945.2307 | 267845.9229 | 279288.1088 | 286334.1273 | 292292.1967 | 300697.2866 | 311387.0083 | 32084.7386 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792 | 32784.6792
Replace 1 Asset | 0% | 2557021.3283 | Safety Risk | 354.9564 | 354.9564 | 354.9564 | 354.9564 | 354.9564 | 354.9564 | 354.9564 | 354.9564 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956 | 35.4956
Replace 2 Assets | 100% | 5114042.6566 | Unplanned Replacement Risk | 15342.128 | 15342.128 | 15342.128 | 15342.128 | 15342.128 | 15342.128 | 15342.128 | 15342.128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128 | 1534.2128
Replace 3 Assets | 0% | 0 | Unplanned Fault Risk | 593 | 593 | 593 | 593 | 593 | 593 | 593 | 593 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3
Addiitonal Asset | 0% | N/A | Unplanned Enviromental Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Transfers | 100% | 0 | Unplanned Fire Risk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-Network MW | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | Option Capital Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093 | 218030.6093
|  |  | Total Life Cycle Cost | 266760.128 | 275235.3151 | 284136.0073 | 295578.1932 | 302624.2117 | 308582.2811 | 316987.371 | 327677.0927 | 251744.3564 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969 | 252444.2969

## Misc_calcs
United Energy
EW switchboard and relay replacement
ESCALATION & OTHER
| Year end |  |  | 2021-06-30 | 2022-06-30 | 2023-06-30 | 2024-06-30 | 2025-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 3.498% | 7.832% | 4.052% | 3%
| HY ending |  |  | 2021-06-30 | 2021-12-31 | 2022-06-30 | 2022-12-31 | 2023-06-30 | 2023-12-31 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-12-31 | 2026-06-30
| FY ending |  |  | 2021-06-30 | 2022-06-30 | 2022-06-30 | 2023-06-30 | 2023-06-30 | 2024-06-30 | 2024-06-30 | 2025-06-30 | 2025-06-30 | 2026-06-30 | 2026-06-30
| Actual/forecast CPI (June to June) |  |  | 0% | 0.8606% | 0.8606% | 3.498% | 3.498% | 7.832% | 7.832% | 4.052% | 4.052% | 3% | 3%
| Actual cumulative HY escalation |  |  | 1 | 1.0043 | 1.0086 | 1.0261 | 1.0439 | 1.084 | 1.1256 | 1.1482 | 1.1713 | 1.1887 | 1.2064
| Convert from input dollars | 2023-12-31 | 1.084
| To output dollars | 2026-06-30 | 1.2064
| Conversion from input dollars to output dollars |  | 1.1129
| Convert from VCR date | 2023-12-31 | 1.084
| To input dollars | 2023-12-31 | 1.084
| VCR escalation |  | 1
| Start_year | 2026-27
FIRST YEAR
| Option | First year | Option included
| Option 2 | 1 | TRUE
| Option 3 | 1 | TRUE
| Option 4 | Not used | FALSE
| Option 5 | Not used | FALSE
| First year | 1
FLAGS
| Option 1 (base case) | FALSE | FALSE
FALSE
FALSE
| Option 2 | FALSE | FALSE
FALSE
FALSE
| Option 3 | FALSE | FALSE
FALSE
FALSE
| Option 4 | FALSE | FALSE
FALSE
FALSE
| Option 5 | FALSE | FALSE
FALSE
FALSE
Message | !! Capex asset life required !!
!

## Data
United Energy
EW switchboard and relay replacement
DATA
Options
|  | Not used | Text |  | Flags for compliance project
Option1 | Option 1 (base case) | FALSE |  | Option 1 (base case): No change to existing practices | FALSE
Option2 | Option 2 | FALSE |  |  | FALSE
Option3 | Option 3 | FALSE |  |  | FALSE
Option4 | Option 4 | TRUE | Not used |  | TRUE
Option5 | Option 5 | TRUE | Not used |  | TRUE
Compliance project |  |  | Yes | FALSE
No change to existing practices
Not applicable (compliance)
For conditional formatting of preferred option on Summary :
< Enter description >
Categories
Short categ
| Capital expenditure | -1
| Annualised capex | -1
| Operating expenditure | -1
| Risk mitigated | 1
| Other benefits value | 1
| Net benefits | 1
| Total risk cost | 1
Benefits
|  | Short categ | Flag to include | Units | Defined value
1 | Unserved energy | Energy | FALSE | MWh | FALSE
2 | Safety | Safety | FALSE | $ | TRUE
3 | Unplanned replacement | UnRepl | FALSE | $ | TRUE
4 | Bushfire | Fire | FALSE | $ | TRUE
5 | Reduction in CO2 emissions | Carbon | TRUE | MWh | FALSE
6 | Reliability in worst-served areas | Other | TRUE | MWh | FALSE
7 | Network resilience | Other | TRUE | MWh | FALSE
8 | Enabling solar exports | Other | TRUE | MWh | FALSE
9 | Aesthetics | Other | TRUE | Customers impacted | FALSE
10 | Customer value of time - residential | Other | TRUE | Customer minutes | FALSE
11 | Customer value of time - business | Other | TRUE | Customer minutes | FALSE
12 | Communication | Other | TRUE | Customers impacted | FALSE
13 | Information accessibility | Other | TRUE | Customers impacted | FALSE
Value of benefits
United Energy
| Reliability in worst-served areas | per MWh | 0
| Network resilience | per MWh | 38560
| Enabling solar exports | per MWh | 862.6028
| Aesthetics | per customer impacted | 0
| Customer value of time - residential | per minute customer time | 0.34751
| Customer value of time - business | per minute customer time | 0.34751
| Communication | per customer impacted | 0
| Information accessibility | per customer impacted | 0
Conversions
| thous_conv | 1000
| mill_conv | 1000000
Message
| Message | Enter asset life
Error message |  | Remove inputs prior to start year
Disproportionate factors applied to various bushfire and other risk valuations
| - Select - |  |  |  | 0
| Harm to property from network |  |  |  | 1
| Harm to property from bushfire |  |  |  | 1
| Harm to environment |  |  |  | 1
| Safety - Public trespass |  |  |  | 1
| Safety - Single fatality or serious injury ^ |  |  |  | 3
| Safety from bushfire in HBRA |  |  |  | 3
| Safety - Multiple fatality or serious injury ^ |  |  |  | 6
| Safety from bushfire (REFCL declared areas) |  |  |  | 6
| Safety from bushfire (electric line construction areas) |  |  |  | 10
Total annualised capex
Energy at risk value
Total other benefits
DROPDOWN LISTS
| Business |  |  |  | Type | Include | Dollar inputs - month |  |  | Not used options | Conversions | Dollar inputs - year | Compliance | Capex first year
| CitiPower | CP | CP: |  | - Select - | 0 | June | 6 | CY | Not used |  | 2026 | No | 2026-27
| Powercor | PA | PAL: |  | Capex | 1899-12-31 | December | 12 | FY |  |  | 2025 | Yes | 2025-26
| United Energy | UE | UE: |  | Opex | [6 empty] | 2024 |  | 2024-25
2023
2022
2021
2020