## Draft Decision
Table 10.1 Draft decision — Service Components caps floors and target for 2023–28
Parameter | Floor | Target | Cap
Unplanned outage circuit event rate (%)
Transmission line outage rate | 19.46 | 11.4185 | 6.02
Transformer outage - fault | 31.65 | 17.6114 | 8.23
Reactive plant - fault | 31.58 | 17.9565 | 9.48
Transmission line outage - forced outage | 19.52 | 8.3851 | 1.19
Transformer outage - forced outage | 12.3 | 8.0589 | 4.62
Reactive plant - forced outage | 24.63 | 13.7223 | 1.3
Loss of supply events frequency (no of events)
No. of events > 0.05 system minutes | 5 | 2.4 | 0
No. of events > 0.2 system minutes | 3 | 1.2 | 0
Average outage duration (minutes)
Average outage duration | 486.52 | 231.455 | 95.44
Proper operation of equipment (no of events)
Failure of protection system | 27 | 8.6 | 0
Material failure of SCADA | 2 | 0.4 | 0
Incorrect operational isolation of primary or secondary equipment | 12 | 7.6 | 3
Table 10.2 Draft decision — Market Impact Component parameter values for 2023–28
Parameter
Target | 7096
Unplanned outage event limit | 1207
Dollar per dispatch interval | 562.1808
Table 10.3 Draft decision — Network Capability Component for 2023–28
Priority project name | Proposed capex ($ million) | Proposed opex ($ million) | Amount approved ($ million)
1. Robertstown to Tungkillo Line Uprating | 2.4 |  | 2.4
2. Davenport to Cultana Line Uprating | 1.5 |  | 1.5
3. Transmission line ratings improvements | 1.8 | 4.2 | 5.9
4. Enhancing Reactive Power and Voltage Control Capability of Riverland | 5 |  | 5
Total | 10.7 | 4.2 | 14.8
Table 10.4 Draft decision — Distribution, Floors and Caps for 2023–28
Parameter | Distribution | Floor | Cap
|  | (95th percentile) | (5th percentile)
Unplanned outage circuit event rate
Transmission line outage rate | LogLogisitc | 19.46 | 6.02
Transformer outage - fault | LogLogistic | 31.65 | 8.23
Reactive plant - fault | Pearson5 | 31.58 | 9.48
Transmission line outage - forced outage | Weibull | 19.52 | 1.19
Transformer outage - forced outage | LogLogistic | 12.3 | 4.62
Reactive plant - forced outage | Uniform | 24.63 | 1.3
Loss of supply events frequency
No. of events > 0.05 system minutes | Poisson | 5 | 0
No. of events > 0.2 system minutes | Poisson | 3 | 0
Average outage duration
Average outage duration | Pearson6 | 486.52 | 95.44
Proper operation of equipment
Failure of protection system | Geomet | 27 | 0
Material failure of SCADA | Geomet | 2 | 0
Incorrect operational isolation of primary or secondary equipment | Poisson | 12 | 3

## SC-Target
7.9.1 - Historical performance and proposed floor, caps and targets for the service component of the STPIS
Parameter | Performance actuals | [5 empty] | Average of actual performance | Difference
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021 |  | 2020 | 2019 | 2016
Unplanned outage circuit event rate:
Transmission line outage - fault | 0.32086 | 0.073394 | 0.15179 | 0.10526 | 0.1594 | 0.081081 | 0.11418 |  |  | 0
Transformer outage – fault | 0.35294 | 0.13433 | 0.26866 | 0.23881 | 0.1343 | 0.10448 | 0.17611 |  |  | 0
Reactive plant – fault | 0.51351 | 0.18919 | 0.15789 | 0.31579 | 0.1053 | 0.12965 | 0.17957 |  |  | 0
Transmission line outage – forced outage | 0.080214 | 0.082569 | 0.089286 | 0.17544 | 0.0089 | 0.063063 | 0.083851 |  |  | 0
Transformer outage – forced outage | 0.036765 | 0.067164 | 0.08209 | 0.074627 | 0.0522 | 0.12687 | 0.080589 |  |  | 0
Reactive plant – forced outage | 0.18919 | 0.18919 | 0.078947 | 0.052632 | 0.1579 | 0.20745 | 0.13722 |  |  | 0
Loss of supply event frequency (number of events): | [9 empty] | 0
> (x) system minutes | 5 | 4 | 3 | 4 | 1 | 0 | 2.4 |  |  | 0
> (y) system minutes | 2 | 1 | 2 | 3 | 0 | 0 | 1.2 |  |  | 0
Average outage duration (minutes): | 250.5714 | 97.4 | 463 | 192 | 205 | 199.875 | 231.455 | 6.4886 | -190.3896 | 0
Proper operation of equipment (number of events): | [9 empty] | 0
Failure of protection system | 17 | 9 | 18 | 6 | 3 | 7 | 8.6 | -2 | -3 | -7
Material failure of SCADA | 2 | 0 | 2 | 0 | 0 | 0 | 0.4 |  |  | 0
Incorrect operational isolation of primary or secondary equipment | 10 | 7 | 13 | 6 | 4 | 8 | 7.6 |  |  | 0
Please check to see whether it is per 2020 outcomes and 2021 submission
Note on G5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirmed the numbers are the same as our submission for CY2021 for row 5-10
Note on E14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Confirmed number is correct. Number changed later in that year when received template for CY2020 from AER.1 AOD event was rejected. AOD increased from140 to 192. Changes did not affect final financial outcome for CY2019.
Note on F14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: confirmed number is correct as per outcome
Note on G14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The AOD for CY2021 was 195. The performance measure of that year was (205+195)/2=200.

## SC-AER Simulation Results
ElectraNet - distributions selected based on mechanical selection of lowest K-S distance statistic, 2017-2021 underlying input data. Calendar year data
| Distribution | KS Distance Statistic | Mean of sample | Mean of fitted distribution | SD of fitted distribution | Cap at 1SD | Cap at 2SD | Collar at 1SD | Collar at 2SD | 5th percentile of fitted distribution | 50th percentile of fitted distribution | 95th percentile of fitted distribution | Ave(2017-2021)
Transmission line outage - fault | LogLogisitc | 0.2452 | 0.1142 | 0.1156 | 0.0455 | 0.1611 | 0.2066 | 0.0701 | 0.0246 | 0.0602 | 0.1082 | 0.1946 | 0.11418
Transformer outage – fault | LogLogistic | 0.2901 | 0.1761 | 0.1761 | 0.0821 | 0.2582 | 0.3403 | 0.094 | 0.0119 | 0.0823 | 0.1613 | 0.3165 | 0.17611
Reactive plant – fault | Pearson5 | 0.15 | 0.1796 | 0.1789 | 0.0737 | 0.2526 | 0.3263 | 0.1052 | 0.0315 | 0.0948 | 0.1631 | 0.3158 | 0.17957
Transmission line outage – forced outage | Weibull | 0.2403 | 0.0839 | 0.0831 | 0.0582 | 0.1413 | 0.1995 | 0.0249 | -0.0333 | 0.0119 | 0.0713 | 0.1952 | 0.083851
Transformer outage – forced outage | LogLogistic | 0.1748 | 0.0806 | 0.0789 | 0.0252 | 0.1041 | 0.1293 | 0.0537 | 0.0285 | 0.0462 | 0.0754 | 0.123 | 0.080589
Reactive plant – forced outage | Uniform | 0.2089 | 0.1372 | 0.1297 | 0.0749 | 0.2046 | 0.2795 | 0.0548 | -0.0201 | 0.013 | 0.1297 | 0.2463 | 0.13722
Average outage duration | Pearson6 | 0.2754 | 231.48 | 233.31 | 142.14 | 375.45 | 517.59 | 91.17 | -50.97 | 95.44 | 197.83 | 486.52 | 231.455
Distributions fitted setting: lower limit with fixed bound of zero; unsure upper limit; no change to default "suppress questionable fits" setting
While @Risk allows beta general to be a candidate distribution, we have not included it as a candidate distribution as it uses 4 parameters and we only have 5 data points.
Where a candidate distribution has been estimated to have an infinite standard deviation we have ruled it out of consideration.
ElectraNet - distributions selected based on mechanical selection of lowest AIC, 2017-2021 underlying input data.
| Distribution | AIC | Mean of sample | Mean of fitted distribution | SD of fitted distribution | Cap at 1SD | Cap at 2SD | Collar at 1SD | Collar at 2SD | 5th percentile of fitted distribution | 50th percentile of fitted distribution | 95th percentile of fitted distribution
Number of events > (x) system minutes | Poisson | 22.6178 | 2.4 | 2.4 | 1.549 | 3.949 | 5.498 | 0.851 | -0.698 | 0 | 2 | 5 | 2.4
Number of events > (y) system minutes | Poisson | 18.1153 | 1.2 | 1.2 | 1.095 | 2.295 | 3.39 | 0.105 | -0.99 | 0 | 1 | 3 | 1.2
Failure of protection system | Geomet | 35.411 | 8.6 | 8.6 | 9.086 | 17.686 | 26.772 | -0.486 | -9.572 | 0 | 6 | 27 | 8.6
Material failure of SCADA | Geomet | 11.7091 | 0.4 | 0.4 | 0.748 | 1.148 | 1.896 | -0.348 | -1.096 | 0 | 0 | 2 | 0.4
Incorrect operational isolation of primary or secondary equipment | Poisson | 28.0725 | 7.6 | 7.6 | 2.757 | 10.357 | 13.114 | 4.843 | 2.086 | 3 | 7 | 12 | 7.6

## MIC - ENet Checked
ElectraNet data applied - STPIS Version 5 - Appendix F, Example 2, Table 6-2
Performance target and measure determination
|  | Regulatory period (RP) |  | Target set in RCP | Raw performance count |  |  | Capped unplanned count | Adjusted performance count | Outcomes Annual Compliance
|  |  |  | Target [1] | Planned | Unplanned | Total (Planned + Unplanned) | Min of Raw Unplanned or 0.17x(M) | (a) + (d) | Planned | Unplanned
|  | (RP) | year | (T) | (a) | (b) | (a) + (b) | (d) | (e)
|  | RP1 | 2015 |  | 10004 | 793 | 10797 | 715 | 10719 | 17237 | 871
|  | RP1 | 2016 |  | 11098.5 | 586 | 11684.5 | 586 | 11684.5 | 13862 | 820
|  | RP1 | 2017 |  | 2090 | 238 | 2328 | 238 | 2328
|  | RP2 | 2018 | 4208 | 6953 | 267 | 7220 | 267 | 7220
|  | RP2 | 2019 | 4208 | 7676.5 | 179 | 7855.5 | 1522.52 | 1701.52 | 174 | 7681.5
|  | RP2 | 2020 | 4208 | 3162 | 4063 | 7225 | 1522.52 | 4684.52 | 3162 | 4063
|  | RP2 | 2021 | 4208 | 9007 | 5511 | 14518 | 1522.52 | 10529.52
|  | Max |  |  |  |  | 14518 |  | 11684.5
|  | Min |  |  |  |  | 2328 |  | 1701.52 | 49.3
|  | Average of median 5 |  |  |  |  | 8956 |  | 7096
[7 empty] | [M] |  | [T]
PR3:
|  | MAR [1]: | 398923474.7045 | updated 21092022 |  |  |  |  | ElectraNet to Please check the values in these cells
|  | Dollar per dispatch interval: | 562.1808
PR3:
|  | Performance target: | 7096
Input:
|  | PR1 unplanned cap | 715
|  | PR2 unplanned cap | 1522.52 | RR18-23 Regulatory period
|  | PR3 unplanned cap | 1207 | RR23-28 Regulatory period
Note: The numbers below are referenced to tab "7.9 STPIS with 2021".
ElectraNet data applied - STPIS Version 5 - Appendix F, Example 2, Table 6-2
Performance target and measure determination
|  | Regulatory period (RP) |  | Target set in RCP | Raw performance count |  |  | Capped unplanned count | Adjusted performance count
|  |  |  | Target [1] | Planned | Unplanned | Total (Planned + Unplanned) | Min of Raw Unplanned or 0.17x(M) | (a) + (d)
|  | (RP) | year | (T) | (a) | (b) | (a) + (b) | (d) | (e)
|  | RP1 | 2015 |  | 10004 | 793 | 10797 | 793 | 10797
|  | RP1 | 2016 |  | 11098.5 | 586 | 11684.5 | 586 | 11684.5
|  | RP1 | 2017 |  | 2090 | 238 | 2328 | 238 | 2328
|  | RP2 | 2018 | 4208 | 6953 | 267 | 7220 | 267 | 7220
|  | RP2 | 2019 | 4208 | 7676.5 | 179 | 7855.5 | 179 | 7855.5
|  | RP2 | 2020 | 4208 | 3162 | 4063 | 7225 | 1522.588 | 4684.588
|  | RP2 | 2021 | 4208 | 9007 | 5511 | 14517 | 1522.588 | 10529.588
|  | Max |  |  |  |  | 14517 |  | 11684.5
|  | Min |  |  |  |  | 2328 |  | 2328
|  | Average of median 5 |  |  |  |  | 8956 |  | 8217
[7 empty] | [M] |  | [T]
PR3:
|  | MAR [1]: | 398923474.7045
|  | Dollar per dispatch interval: | 485.4855
PR3:
|  | Performance target: | 8217
Input:
|  | PR1 unplanned cap | 715
|  | PR2 unplanned cap | 1522.52 | RR18-23 Regulatory period
|  | PR3 unplanned cap | 1397 | RR23-28 Regulatory period
Note on I8: Author: why is the formula being cross off?
Note on F10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: numbers were the same as last reset submission
Note on G10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: numbers were the same as last reset submission
Note on F11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: numbers were the same as last reset submission
Note on G11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: numbers were the same as last reset submission
Note on F14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Number should be 179
Note on G14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: number should be 7677
Note on I14: Author: see below

## 7.9 STPIS with 2021
REGULATORY REPORTING STATEMENT
ElectraNet
2023-24 to 2027-28
7.9 SERVICE TARGET PERFORMANCE INCENTIVE SCHEME (STPIS)
There are FOUR tables on this worksheet. Each table has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
7.9.1 - Historical performance and proposed floor, caps and targets for the service component of the STPIS
Parameter | Performance actuals | [5 empty] | Average of actual performance | Floor | Target | Cap | Weighting (% of MAR)
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Unplanned outage circuit event rate:
Transmission line outage - fault | 32.09% | 7.339% | 15.18% | 10.53% | 15.94% |  | 0.16214 |  |  |  | 0.2%
Transformer outage – fault | 35.29% | 13.43% | 26.87% | 23.88% | 13.43% |  | 0.22581 |  |  |  | 0.2%
Reactive plant – fault | 51.35% | 18.92% | 15.79% | 31.58% | 10.53% |  | 0.25634 |  |  |  | 0.1%
Transmission line outage – forced outage | 8.021% | 8.257% | 8.929% | 17.54% | 0.89% |  | 0.087281 |  |  |  | 0.1%
Transformer outage – forced outage | 3.676% | 6.716% | 8.209% | 7.463% | 5.22% |  | 0.062569 |  |  |  | 0.1%
Reactive plant – forced outage | 18.92% | 18.92% | 7.895% | 5.263% | 15.79% |  | 0.13357 |  |  |  | 0.05%
Loss of supply event frequency (number of events):
> (x) system minutes | 5 | 4 | 3 | 4 | 1 |  | 3.4 |  |  |  | 0.15%
> (y) system minutes | 2 | 1 | 2 | 3 | 0 |  | 1.6 |  |  |  | 0.15%
Average outage duration (minutes): | 250.5714 | 97.4 | 463 | 192 | 205 |  | 241.5943 |  |  |  | 0.2%
Proper operation of equipment (number of events):
Failure of protection system | 17 | 9 | 18 | 6 | 3 |  | 10.6 |  |  |  | 0%
Material failure of SCADA | 2 | 0 | 2 | 0 | 0 |  | 0.8 |  |  |  | 0%
Incorrect operational isolation of primary or secondary equipment | 10 | 7 | 13 | 6 | 4 |  | 8 |  |  |  | 0%
7.9.2 - Proposed priority projects for the network capability incentive parameter
Project ranking | Transmission Circuit / Injection Point | Scope of works | If applicable, the present value of quantified benefits associated with the project ($0's, 2022-23) | Project cost ($0's, 2022-23)
|  |  |  | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | Opex | Capex
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
7.9.3 – Network limit information
Limit identification | Define limit | Reason for the limit | Is limit addressed by priority project | Supporting information reference
7.9.4 - Market impact component
Market impact parameter
|  | Planned outage count(DI) |  | Unplanned outage count (DI)
Year | Month | without exclusions | with exclusions | without exclusions | with exclusions | Market impact parameters
2014 | January | 268 | 7 | 133 | 0 | 0.58333
2014 | February | 143 | 0 | 53 | 0 | 0
2014 | March | 265 | 0 | 93 | 0 | 0
2014 | April | 20 | 0 | 17 | 0 | 0
2014 | May | 85 | 0 | 86 | 0 | 0
2014 | June | 248 | 0 | 35 | 0 | 0
2014 | July | 113 | 0 | 25 | 0 | 0
2014 | August | 38 | 15 | 84 | 0 | 1.25
2014 | September | 290 | 0 | 64 | 0 | 0
2014 | October | 383 | 39 | 113 | 9 | 3.25
2014 | November | 115 | 0 | 24 | 0 | 0
2014 | December | 99 | 26 | 274 | 0 | 2.1667
Total 2014 |  | 2067 | 87 | 1001 | 9 | 7.25
2015 | January | 29 | 0 | 546 | 283 | 0
2015 | February | 85 | 0 | 102 | 0 | 0
2015 | March | 600 | 537 | 42 | 0 | 44.75
2015 | April | 1180 | 593 | 155 | 37 | 49.4167
2015 | May | 1759 | 967 | 224 | 0 | 80.5833
2015 | June | 118 | 83 | 18 | 0 | 6.9167
2015 | July | 3927 | 2749 | 149 | 42 | 229.0833
2015 | August | 998 | 477 | 353 | 236 | 39.75
2015 | September | 2137 | 1593 | 148 | 33 | 132.75
2015 | October | 10781 | 1690 | 171 | 0 | 140.8333
2015 | November | 7919 | 870 | 591 | 81 | 72.5
2015 | December | 1180 | 445 | 188 | 81 | 37.0833
Total 2015 |  | 30713 | 10004 | 2687 | 793 | 833.6667
2016 | January | 693 | 217 | 6 | 0 | 18.0833
2016 | February | 414 | 0 | 4 | 3 | 0
2016 | March | 1845 | 737 | 246 | 184 | 61.4167
2016 | April | 1938 | 671 | 8 | 0 | 55.9167
2016 | May | 1542 | 746 | 122 | 23 | 62.1667
2016 | June | 3865 | 1318 | 26 | 0 | 109.8333
2016 | July | 4816 | 4390 | 95 | 4 | 365.8333
2016 | August | 5976 | 1228 | 203 | 7 | 102.3333
2016 | September | 5178 | 411 | 2497 | 0 | 34.25
2016 | October | 4103.5 | 430.5 | 8558 | 334 | 35.875
2016 | November | 8088 | 645 | 1014 | 31 | 53.75
2016 | December | 4857 | 305 | 202 | 0 | 25.4167
Total 2016 |  | 43315.5 | 11098.5 | 12981 | 586 | 924.875
2017 | January | 824 | 23 | 135 | 0 | 1.9167
2017 | February | 886 | 19 | 172 | 0 | 1.5833
2017 | March | 5065 | 2 | 96 | 38 | 0.16667
2017 | April | 963 | 106 | 0 | 0 | 8.8333
2017 | May | 732 | 0 | 0 | 0 | 0
2017 | June | 1234 | 414 | 0 | 0 | 34.5
2017 | July | 1599 | 204 | 75 | 0 | 17
2017 | August | 2755 | 172 | 0 | 0 | 14.3333
2017 | September | 3340 | 392 | 856 | 200 | 32.6667
2017 | October | 4737 | 336 | 17 | 0 | 28
2017 | November | 1358 | 422 | 105 | 0 | 35.1667
2017 | December | 3521 | 0 | 0 | 0 | 0
Total 2017 |  | 27014 | 2090 | 1456 | 238 | 174.1667
2018 | January | 207 | 67 | 2972 | 0 | 5.5833
2018 | February | 14 | 1 | 982 | 0 | 0.083333
2018 | March | 195 | 62 | 3338 | 0 | 5.1667
2018 | April | 101 | 73 | 14351 | 49 | 6.0833
2018 | May | 233 | 7 | 9283 | 7 | 0.58333
2018 | June | 88 | 53 | 3628 | 3 | 4.4167
2018 | July | 9553 | 3624 | 208 | 206 | 302
2018 | August | 12913 | 1113 | 756 | 0 | 92.75
2018 | September | 6473 | 468 | 7397 | 0 | 39
2018 | October | 10761 | 403 | 415 | 0 | 33.5833
2018 | November | 3762 | 754 | 95 | 2 | 62.8333
2018 | December | 4315 | 328 | 169 | 0 | 27.3333
Total 2018 |  | 48615 | 6953 | 43594 | 267 | 579.4167
2019 | January | 828 | 17 | 514 | 0 | 1.4167
2019 | February | 624 | 14 | 0 | 0 | 1.1667
2019 | March | 2096 | 356 | 3 | 3 | 29.6667
2019 | April | 2497 | 140.5 | 140 | 27 | 11.7083
2019 | May | 4031 | 914 | 144 | 51 | 76.1667
2019 | June | 2639 | 543 | 31 | 0 | 45.25
2019 | July | 4800 | 621 | 320 | 0 | 51.75
2019 | August | 5105 | 1161 | 0 | 0 | 96.75
2019 | September | 9320 | 1528 | 0 | 0 | 127.3333
2019 | October | 14353 | 1944 | 8 | 0 | 162
2019 | November | 7226 | 362 | 529 | 98 | 30.1667
2019 | December | 4470 | 76 | 126 | 0 | 6.3333
Total 2019 |  | 57989 | 7676.5 | 1815 | 179 | 639.7083
2020 | January | 7919 | 92 | 1506 | 0 | 7.6667
2020 | February | 10461 | 4 | 22013 | 0 | 0.33333
2020 | March | 9545 | 112 | 530 | 0 | 9.3333
2020 | April | 5459 | 16 | 0 | 0 | 1.3333
2020 | May | 5610 | 733 | 0 | 0 | 61.0833
2020 | June | 3531 | 174 | 0 | 0 | 14.5
2020 | July | 2165 | 121 | 156 | 156 | 10.0833
2020 | August | 6726 | 428 | 783 | 783 | 35.6667
2020 | September | 11630 | 593 | 1152 | 1152 | 49.4167
2020 | October | 15803 | 306 | 762 | 762 | 25.5
2020 | November | 15653 | 142 | 601 | 601 | 11.8333
2020 | December | 15758 | 441 | 609 | 609 | 36.75
Total 2020 |  | 110260 | 3162 | 28112 | 4063 | 263.5
2021 | January | 13837 | 163 | 652 | 652 | 13.5833
2021 | February | 12086 | 0 | 321 | 321 | 0
2021 | March | 19631 | 532 | 456 | 283 | 44.3333
2021 | April | 14775 | 134 | 140 | 139 | 11.1667
2021 | May | 10375 | 2237 | 156 | 156 | 186.4167
2021 | June | 8187 | 989 | 280 | 257 | 82.4167
2021 | July | 17049 | 547 | 225 | 225 | 45.5833
2021 | August | 14133 | 702 | 355 | 355 | 58.5
2021 | September | 22857 | 697 | 768 | 753 | 58.0833
2021 | October | 24446 | 957 | 1463 | 1302 | 79.75
2021 | November | 24599 | 1607 | 1405 | 928 | 133.9167
2021 | December | 9740 | 442 | 2912 | 140 | 36.8333
Total 2021 |  | 191715 | 9007 | 9133 | 5511 | 750.5833
7.9.4A - Market impact component - Targets
Market impact parameter
|  | Planned outage count(DI) |  | Unplanned outage count (DI) |  | Raw performance count | Capped unplanned count | Adjusted performance count
Year | Target | without exclusions | with exclusions | without exclusions | with exclusions | Total (Planned + Unplanned) | Min of Raw Unplanned or 0.17x(M) | planned + capped unplanned |  | 87 | 10004 | 11098.5 | 2090 | 6953 | 7676.5 | 3162 | 9007
|  |  | (a) |  | (b) | (a) + (b) | (d) |  |  | 9 | 793 | 586 | 238 | 267 | 179 | 4063 | 5511
|  | 3 | 4 | 5 | 6 |  |  |  |  | 9 | 793 | 586 | 238 | 267 | 179 | 4063 | 5511
Total 2014 |  | 2067 | 87 | 1001 | 9 | 96 | 9 | 96 |  | 96 | 10797 | 11684.5 | 2328 | 7220 | 7855.5 | 7225 | 14518
Total 2015 |  | 30713 | 10004 | 2687 | 793 | 10797 | 793 | 10797 |  | ok | ok | ok | ok | ok | ok | ok | ok
Total 2016 |  | 43315.5 | 11098.5 | 12981 | 586 | 11684.5 | 586 | 11684.5
Total 2017 |  | 27014 | 2090 | 1456 | 238 | 2328 | 238 | 2328
Total 2018 | 4208 | 48615 | 6953 | 43594 | 267 | 7220 | 267 | 7220
Total 2019 | 4208 | 57989 | 7676.5 | 1815 | 179 | 7855.5 | 179 | 7855.5
Total 2020 | 4208 | 110260 | 3162 | 28112 | 4063 | 7225 | 1522.588 | 4684.588
Total 2021 | 4208 | 191715 | 9007 | 9133 | 5511 | 14518 | 1522.588 | 10529.588
Max | [5 empty] | 14518 |  | 11684.5
Min | [5 empty] | 2328 |  | 2328
Raw target |  | 319973.5 | 41071 | 91646 | 6135
|  |  | Raw performance target - > |  | M | 8956.4
[5 empty] | Unplanned Event Limit 17% of M -> | 1522.588
[6 empty] | Adjusted performance count | T | 8217.3352
[6 empty] | MAR ($) real 2023 |  | 341740000
[6 empty] | 1% of MAR ($) |  | 3417400
[6 empty] | $ per DI |  | 415.8769
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY