## Final Decision
Table 10.1 Final decision — Service Components caps floors and target for 2023–28
Parameter | Floor | Target | Cap
Unplanned outage circuit event rate (%)
Transmission line outage - fault | 19.46% | 11.42% | 6.02%
Transformer outage - fault | 31.65% | 17.61% | 8.23%
Reactive plant - fault | 31.58% | 17.96% | 9.48%
Transmission line outage - forced outage | 19.52% | 8.385% | 1.19%
Transformer outage - forced outage | 12.3% | 8.059% | 4.62%
Reactive plant - forced outage | 24.63% | 13.72% | 1.3%
Loss of supply events frequency (no of events)
No. of events > 0.05 system minutes | 5 | 2.4 | 0
No. of events > 0.2 system minutes | 3 | 1.2 | 0
Average outage duration (minutes)
Average outage duration | 450.1 | 263.6648 | 88.06
Proper operation of equipment (no of events)
Failure of protection system | 27 | 8.6 | 0
Material failure of SCADA | 2 | 0.4 | 0
Incorrect operational isolation of primary or secondary equipment | 12 | 7.6 | 3
Table 10.2 Final decision — Market Impact Component parameter values for 2023–28
Parameter
Target | 8202
Unplanned outage event limit | 1395
Dollar per dispatch interval | 483.0478
Table 10.3 Final decision — Network Capability Component for 2023–28
Priority project name | Proposed capex ($ million) | Proposed opex ($ million) | Amount approved ($ million)
1. Robertstown to Tungkillo Line Uprating | 2.4 |  | 2.4
2. Davenport to Cultana Line Uprating | 1.5 |  | 1.5
3. Transmission line ratings improvements | 1.8 | 4.2 | 5.9
4. Enhancing Reactive Power and Voltage Control Capability of Riverland | 5 |  | 5
Total | 10.7 | 4.2 | 14.8
Table 10.4 Final decision — Distribution, Floors and Caps for 2023–28
Parameter | Distribution | Floor | Cap
|  | (95th percentile) | (5th percentile)
Unplanned outage circuit event rate
Transmission line outage - fault | LogLogisitc | 19.46% | 6.02%
Transformer outage - fault | LogLogistic | 31.65% | 8.23%
Reactive plant - fault | Pearson5 | 31.58% | 9.48%
Transmission line outage - forced outage | Weibull | 19.52% | 1.19%
Transformer outage - forced outage | LogLogistic | 12.3% | 4.62%
Reactive plant - forced outage | Uniform | 24.63% | 1.3%
Loss of supply events frequency
No. of events > 0.05 system minutes | Poisson | 5 | 0
No. of events > 0.2 system minutes | Poisson | 3 | 0
Average outage duration
Average outage duration | LogLogistic | 450.1 | 88.06
Proper operation of equipment
Failure of protection system | Geomet | 27 | 0
Material failure of SCADA | Geomet | 2 | 0
Incorrect operational isolation of primary or secondary equipment | Poisson | 12 | 3

## SC Input data and Target
7.9.1 - Historical performance and proposed floor, caps and targets for the service component of the STPIS
Parameter | Performance actuals | [5 empty] | Average of actual performance
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Unplanned outage circuit event rate:
Transmission line outage - fault | 0.32086 | 0.073394 | 0.15179 | 0.10526 | 0.1594 | 0.081081 | 0.11418
Transformer outage – fault | 0.35294 | 0.13433 | 0.26866 | 0.23881 | 0.1343 | 0.10448 | 0.17611
Reactive plant – fault | 0.51351 | 0.18919 | 0.15789 | 0.31579 | 0.1053 | 0.12965 | 0.17957
Transmission line outage – forced outage | 0.080214 | 0.082569 | 0.089286 | 0.17544 | 0.0089 | 0.063063 | 0.083851
Transformer outage – forced outage | 0.036765 | 0.067164 | 0.08209 | 0.074627 | 0.0522 | 0.12687 | 0.080589
Reactive plant – forced outage | 0.18919 | 0.18919 | 0.078947 | 0.052632 | 0.1579 | 0.20745 | 0.13722
Loss of supply event frequency (number of events):
> (x) system minutes | 5 | 4 | 3 | 4 | 1 | 0 | 2.4
> (y) system minutes | 2 | 1 | 2 | 3 | 0 | 0 | 1.2
Average outage duration (minutes): | 250.5714 | 97.4 | 462.6364 | 192.2727 | 204.75 | 195 | 263.6648
Proper operation of equipment (number of events):
Failure of protection system | 17 | 9 | 18 | 6 | 3 | 7 | 8.6
Material failure of SCADA | 2 | 0 | 2 | 0 | 0 | 0 | 0.4
Incorrect operational isolation of primary or secondary equipment | 10 | 7 | 13 | 6 | 4 | 8 | 7.6

## SC-AER Simulation Results
ElectraNet - distributions selected based on mechanical selection of lowest K-S distance statistic, 2017-2021 underlying input data. Calendar year data
| Distribution | KS Distance Statistic | Mean of sample | Mean of fitted distribution | SD of fitted distribution | Cap at 1SD | Cap at 2SD | Collar at 1SD | Collar at 2SD | 5th percentile of fitted distribution | 50th percentile of fitted distribution | 95th percentile of fitted distribution
Transmission line outage - fault | LogLogisitc | 0.2452 | 0.1142 | 0.1156 | 0.0455 | 0.1611 | 0.2066 | 0.0701 | 0.0246 | 0.0602 | 0.1082 | 0.1946
Transformer outage – fault | LogLogistic | 0.2901 | 0.1761 | 0.1761 | 0.0821 | 0.2582 | 0.3403 | 0.094 | 0.0119 | 0.0823 | 0.1613 | 0.3165
Reactive plant – fault | Pearson5 | 0.15 | 0.1796 | 0.1789 | 0.0737 | 0.2526 | 0.3263 | 0.1052 | 0.0315 | 0.0948 | 0.1631 | 0.3158
Transmission line outage – forced outage | Weibull | 0.2403 | 0.0839 | 0.0831 | 0.0582 | 0.1413 | 0.1995 | 0.0249 | -0.0333 | 0.0119 | 0.0713 | 0.1952
Transformer outage – forced outage | LogLogistic | 0.1748 | 0.0806 | 0.0789 | 0.0252 | 0.1041 | 0.1293 | 0.0537 | 0.0285 | 0.0462 | 0.0754 | 0.123
Reactive plant – forced outage | Uniform | 0.2089 | 0.1372 | 0.1297 | 0.0749 | 0.2046 | 0.2795 | 0.0548 | -0.0201 | 0.013 | 0.1297 | 0.2463
Average outage duration | LogLogistic | 0.2747 | 230.41 | 226.64 | 136.51 | 363.15 | 499.66 | 90.13 | -46.38 | 88.06 | 199.09 | 450.1
Distributions fitted setting: lower limit with fixed bound of zero; unsure upper limit; no change to default "suppress questionable fits" setting
While @Risk allows beta general to be a candidate distribution, we have not included it as a candidate distribution as it uses 4 parameters and we only have 5 data points.
Where a candidate distribution has been estimated to have an infinite standard deviation we have ruled it out of consideration.
ElectraNet - distributions selected based on mechanical selection of lowest AIC, 2017-2021 underlying input data.
| Distribution | AIC | Mean of sample | Mean of fitted distribution | SD of fitted distribution | Cap at 1SD | Cap at 2SD | Collar at 1SD | Collar at 2SD | 5th percentile of fitted distribution | 50th percentile of fitted distribution | 95th percentile of fitted distribution
Number of events > (x) system minutes | Poisson | 22.6178 | 2.4 | 2.4 | 1.549 | 3.949 | 5.498 | 0.851 | -0.698 | 0 | 2 | 5
Number of events > (y) system minutes | Poisson | 18.1153 | 1.2 | 1.2 | 1.095 | 2.295 | 3.39 | 0.105 | -0.99 | 0 | 1 | 3
Failure of protection system | Geomet | 35.411 | 8.6 | 8.6 | 9.086 | 17.686 | 26.772 | -0.486 | -9.572 | 0 | 6 | 27
Material failure of SCADA | Geomet | 11.7091 | 0.4 | 0.4 | 0.748 | 1.148 | 1.896 | -0.348 | -1.096 | 0 | 0 | 2
Incorrect operational isolation of primary or secondary equipment | Poisson | 28.0725 | 7.6 | 7.6 | 2.757 | 10.357 | 13.114 | 4.843 | 2.086 | 3 | 7 | 12

## MIC
ElectraNet data applied - STPIS Version 5 - Appendix F, Example 2, Table 6-2
Performance target and measure determination
| Regulatory period (RP) |  | Target set in RCP | Raw performance count |  |  | Capped unplanned count | Adjusted performance count
|  |  | Target [1] | Planned | Unplanned | Total (Planned + Unplanned) | Min of Raw Unplanned or 0.17x(M) | (a) + (d)
| (RP) | year | (T) | (a) | (b) | (a) + (b) | (d) | (e)
| RP1 | 2015 |  | 10004 | 793 | 10797 | 715 | 10719
| RP1 | 2016 |  | 11098.5 | 586 | 11684.5 | 586 | 11684.5
| RP1 | 2017 |  | 2090 | 238 | 2328 | 238 | 2328
| RP2 | 2018 | 4208 | 6953 | 267 | 7220 | 267 | 7220
| RP2 | 2019 | 4208 | 7676.5 | 179 | 7855.5 | 179 | 7855.5
| RP2 | 2020 | 4208 | 3162 | 4063 | 7225 | 1522.52 | 4684.52
| RP2 | 2021 | 4208 | 9007 | 5511 | 14518 | 1522.52 | 10529.52
| Max |  |  |  |  | 14518 |  | 11684.5
| Min |  |  |  |  | 2328 |  | 2328
| Average of median 5 |  |  |  |  | 8956 |  | 8202
[6 empty] | [M] |  | [T]
RP3:
| MAR [1]: | 396195771.2051
| Dollar per dispatch interval: | 483.0478
RP3:
| Performance target: | 8202
Input:
| RP1 unplanned cap | 715
| RP2 unplanned cap | 1522.52 | 18-23 Regulatory period
| RP3 unplanned cap | 1395 | 23-28 Regulatory period

## AER-ENet Smoothed Revenue
ElectraNet Final decision
Year | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | Total
MAR smoothed ($m, nominal) | 396.1958 | 435.25 | 447.9563 | 461.0335 | 474.4925 | 2214.9282
MAR smoothed ($m, 2022-23) | 384.9577 | 410.9085 | 410.9085 | 410.9085 | 410.9085 | 2028.5917

## 7.9 STPIS with 2021
REGULATORY REPORTING STATEMENT
ElectraNet
2023-24 to 2027-28
7.9 SERVICE TARGET PERFORMANCE INCENTIVE SCHEME (STPIS)
There are FOUR tables on this worksheet. Each table has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
7.9.1 - Historical performance and proposed floor, caps and targets for the service component of the STPIS
Parameter | Performance actuals | [5 empty] | Average of actual performance | Floor | Target | Cap | Weighting (% of MAR)
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Unplanned outage circuit event rate:
Transmission line outage - fault | 32.09% | 7.339% | 15.18% | 10.53% | 15.94% |  | 0.16214 |  |  |  | 0.2%
Transformer outage – fault | 35.29% | 13.43% | 26.87% | 23.88% | 13.43% |  | 0.22581 |  |  |  | 0.2%
Reactive plant – fault | 51.35% | 18.92% | 15.79% | 31.58% | 10.53% |  | 0.25634 |  |  |  | 0.1%
Transmission line outage – forced outage | 8.021% | 8.257% | 8.929% | 17.54% | 0.89% |  | 0.087281 |  |  |  | 0.1%
Transformer outage – forced outage | 3.676% | 6.716% | 8.209% | 7.463% | 5.22% |  | 0.062569 |  |  |  | 0.1%
Reactive plant – forced outage | 18.92% | 18.92% | 7.895% | 5.263% | 15.79% |  | 0.13357 |  |  |  | 0.05%
Loss of supply event frequency (number of events):
> (x) system minutes | 5 | 4 | 3 | 4 | 1 |  | 3.4 |  |  |  | 0.15%
> (y) system minutes | 2 | 1 | 2 | 3 | 0 |  | 1.6 |  |  |  | 0.15%
Average outage duration (minutes): | 250.5714 | 97.4 | 463 | 192 | 205 |  | 241.5943 |  |  |  | 0.2%
Proper operation of equipment (number of events):
Failure of protection system | 17 | 9 | 18 | 6 | 3 |  | 10.6 |  |  |  | 0%
Material failure of SCADA | 2 | 0 | 2 | 0 | 0 |  | 0.8 |  |  |  | 0%
Incorrect operational isolation of primary or secondary equipment | 10 | 7 | 13 | 6 | 4 |  | 8 |  |  |  | 0%
7.9.2 - Proposed priority projects for the network capability incentive parameter
Project ranking | Transmission Circuit / Injection Point | Scope of works | If applicable, the present value of quantified benefits associated with the project ($0's, 2022-23) | Project cost ($0's, 2022-23)
|  |  |  | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | Opex | Capex
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
7.9.3 – Network limit information
Limit identification | Define limit | Reason for the limit | Is limit addressed by priority project | Supporting information reference
7.9.4 - Market impact component
Market impact parameter
|  | Planned outage count(DI) |  | Unplanned outage count (DI)
Year | Month | without exclusions | with exclusions | without exclusions | with exclusions | Market impact parameters
2014 | January | 268 | 7 | 133 | 0 | 0.58333
2014 | February | 143 | 0 | 53 | 0 | 0
2014 | March | 265 | 0 | 93 | 0 | 0
2014 | April | 20 | 0 | 17 | 0 | 0
2014 | May | 85 | 0 | 86 | 0 | 0
2014 | June | 248 | 0 | 35 | 0 | 0
2014 | July | 113 | 0 | 25 | 0 | 0
2014 | August | 38 | 15 | 84 | 0 | 1.25
2014 | September | 290 | 0 | 64 | 0 | 0
2014 | October | 383 | 39 | 113 | 9 | 3.25
2014 | November | 115 | 0 | 24 | 0 | 0
2014 | December | 99 | 26 | 274 | 0 | 2.1667
Total 2014 |  | 2067 | 87 | 1001 | 9 | 7.25
2015 | January | 29 | 0 | 546 | 283 | 0
2015 | February | 85 | 0 | 102 | 0 | 0
2015 | March | 600 | 537 | 42 | 0 | 44.75
2015 | April | 1180 | 593 | 155 | 37 | 49.4167
2015 | May | 1759 | 967 | 224 | 0 | 80.5833
2015 | June | 118 | 83 | 18 | 0 | 6.9167
2015 | July | 3927 | 2749 | 149 | 42 | 229.0833
2015 | August | 998 | 477 | 353 | 236 | 39.75
2015 | September | 2137 | 1593 | 148 | 33 | 132.75
2015 | October | 10781 | 1690 | 171 | 0 | 140.8333
2015 | November | 7919 | 870 | 591 | 81 | 72.5
2015 | December | 1180 | 445 | 188 | 81 | 37.0833
Total 2015 |  | 30713 | 10004 | 2687 | 793 | 833.6667
2016 | January | 693 | 217 | 6 | 0 | 18.0833
2016 | February | 414 | 0 | 4 | 3 | 0
2016 | March | 1845 | 737 | 246 | 184 | 61.4167
2016 | April | 1938 | 671 | 8 | 0 | 55.9167
2016 | May | 1542 | 746 | 122 | 23 | 62.1667
2016 | June | 3865 | 1318 | 26 | 0 | 109.8333
2016 | July | 4816 | 4390 | 95 | 4 | 365.8333
2016 | August | 5976 | 1228 | 203 | 7 | 102.3333
2016 | September | 5178 | 411 | 2497 | 0 | 34.25
2016 | October | 4103.5 | 430.5 | 8558 | 334 | 35.875
2016 | November | 8088 | 645 | 1014 | 31 | 53.75
2016 | December | 4857 | 305 | 202 | 0 | 25.4167
Total 2016 |  | 43315.5 | 11098.5 | 12981 | 586 | 924.875
2017 | January | 824 | 23 | 135 | 0 | 1.9167
2017 | February | 886 | 19 | 172 | 0 | 1.5833
2017 | March | 5065 | 2 | 96 | 38 | 0.16667
2017 | April | 963 | 106 | 0 | 0 | 8.8333
2017 | May | 732 | 0 | 0 | 0 | 0
2017 | June | 1234 | 414 | 0 | 0 | 34.5
2017 | July | 1599 | 204 | 75 | 0 | 17
2017 | August | 2755 | 172 | 0 | 0 | 14.3333
2017 | September | 3340 | 392 | 856 | 200 | 32.6667
2017 | October | 4737 | 336 | 17 | 0 | 28
2017 | November | 1358 | 422 | 105 | 0 | 35.1667
2017 | December | 3521 | 0 | 0 | 0 | 0
Total 2017 |  | 27014 | 2090 | 1456 | 238 | 174.1667
2018 | January | 207 | 67 | 2972 | 0 | 5.5833
2018 | February | 14 | 1 | 982 | 0 | 0.083333
2018 | March | 195 | 62 | 3338 | 0 | 5.1667
2018 | April | 101 | 73 | 14351 | 49 | 6.0833
2018 | May | 233 | 7 | 9283 | 7 | 0.58333
2018 | June | 88 | 53 | 3628 | 3 | 4.4167
2018 | July | 9553 | 3624 | 208 | 206 | 302
2018 | August | 12913 | 1113 | 756 | 0 | 92.75
2018 | September | 6473 | 468 | 7397 | 0 | 39
2018 | October | 10761 | 403 | 415 | 0 | 33.5833
2018 | November | 3762 | 754 | 95 | 2 | 62.8333
2018 | December | 4315 | 328 | 169 | 0 | 27.3333
Total 2018 |  | 48615 | 6953 | 43594 | 267 | 579.4167
2019 | January | 828 | 17 | 514 | 0 | 1.4167
2019 | February | 624 | 14 | 0 | 0 | 1.1667
2019 | March | 2096 | 356 | 3 | 3 | 29.6667
2019 | April | 2497 | 140.5 | 140 | 27 | 11.7083
2019 | May | 4031 | 914 | 144 | 51 | 76.1667
2019 | June | 2639 | 543 | 31 | 0 | 45.25
2019 | July | 4800 | 621 | 320 | 0 | 51.75
2019 | August | 5105 | 1161 | 0 | 0 | 96.75
2019 | September | 9320 | 1528 | 0 | 0 | 127.3333
2019 | October | 14353 | 1944 | 8 | 0 | 162
2019 | November | 7226 | 362 | 529 | 98 | 30.1667
2019 | December | 4470 | 76 | 126 | 0 | 6.3333
Total 2019 |  | 57989 | 7676.5 | 1815 | 179 | 639.7083
2020 | January | 7919 | 92 | 1506 | 0 | 7.6667
2020 | February | 10461 | 4 | 22013 | 0 | 0.33333
2020 | March | 9545 | 112 | 530 | 0 | 9.3333
2020 | April | 5459 | 16 | 0 | 0 | 1.3333
2020 | May | 5610 | 733 | 0 | 0 | 61.0833
2020 | June | 3531 | 174 | 0 | 0 | 14.5
2020 | July | 2165 | 121 | 156 | 156 | 10.0833
2020 | August | 6726 | 428 | 783 | 783 | 35.6667
2020 | September | 11630 | 593 | 1152 | 1152 | 49.4167
2020 | October | 15803 | 306 | 762 | 762 | 25.5
2020 | November | 15653 | 142 | 601 | 601 | 11.8333
2020 | December | 15758 | 441 | 609 | 609 | 36.75
Total 2020 |  | 110260 | 3162 | 28112 | 4063 | 263.5
2021 | January | 13837 | 163 | 652 | 652 | 13.5833
2021 | February | 12086 | 0 | 321 | 321 | 0
2021 | March | 19631 | 532 | 456 | 283 | 44.3333
2021 | April | 14775 | 134 | 140 | 139 | 11.1667
2021 | May | 10375 | 2237 | 156 | 156 | 186.4167
2021 | June | 8187 | 989 | 280 | 257 | 82.4167
2021 | July | 17049 | 547 | 225 | 225 | 45.5833
2021 | August | 14133 | 702 | 355 | 355 | 58.5
2021 | September | 22857 | 697 | 768 | 753 | 58.0833
2021 | October | 24446 | 957 | 1463 | 1302 | 79.75
2021 | November | 24599 | 1607 | 1405 | 928 | 133.9167
2021 | December | 9740 | 442 | 2912 | 140 | 36.8333
Total 2021 |  | 191715 | 9007 | 9133 | 5511 | 750.5833
7.9.4A - Market impact component - Targets
Market impact parameter
|  | Planned outage count(DI) |  | Unplanned outage count (DI) |  | Raw performance count | Capped unplanned count | Adjusted performance count
Year | Target | without exclusions | with exclusions | without exclusions | with exclusions | Total (Planned + Unplanned) | Min of Raw Unplanned or 0.17x(M) | planned + capped unplanned |  | 87 | 10004 | 11098.5 | 2090 | 6953 | 7676.5 | 3162 | 9007
|  |  | (a) |  | (b) | (a) + (b) | (d) |  |  | 9 | 793 | 586 | 238 | 267 | 179 | 4063 | 5511
|  | 3 | 4 | 5 | 6 |  |  |  |  | 9 | 793 | 586 | 238 | 267 | 179 | 4063 | 5511
Total 2014 |  | 2067 | 87 | 1001 | 9 | 96 | 9 | 96 |  | 96 | 10797 | 11684.5 | 2328 | 7220 | 7855.5 | 7225 | 14518
Total 2015 |  | 30713 | 10004 | 2687 | 793 | 10797 | 793 | 10797 |  | ok | ok | ok | ok | ok | ok | ok | ok
Total 2016 |  | 43315.5 | 11098.5 | 12981 | 586 | 11684.5 | 586 | 11684.5
Total 2017 |  | 27014 | 2090 | 1456 | 238 | 2328 | 238 | 2328
Total 2018 | 4208 | 48615 | 6953 | 43594 | 267 | 7220 | 267 | 7220
Total 2019 | 4208 | 57989 | 7676.5 | 1815 | 179 | 7855.5 | 179 | 7855.5
Total 2020 | 4208 | 110260 | 3162 | 28112 | 4063 | 7225 | 1522.588 | 4684.588
Total 2021 | 4208 | 191715 | 9007 | 9133 | 5511 | 14518 | 1522.588 | 10529.588
Max | [5 empty] | 14518 |  | 11684.5
Min | [5 empty] | 2328 |  | 2328
Raw target |  | 319973.5 | 41071 | 91646 | 6135
|  |  | Raw performance target - > |  | M | 8956.4
[5 empty] | Unplanned Event Limit 17% of M -> | 1522.588
[6 empty] | Adjusted performance count | T | 8217.3352
[6 empty] | MAR ($) real 2023 |  | 341740000
[6 empty] | 1% of MAR ($) |  | 3417400
[6 empty] | $ per DI |  | 415.8769
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY