## Final Decision
Table 10.1 Final decision — Service Components caps floors and target for 2023–28
Parameter | Floor | Target | Cap
Unplanned outage circuit event rate (%)
Circuit outage rate - fault | 500% | 200% | 0%
Circuit outage rate - forced | 300% | 120% | 0%
Table 10.2 Final decision — Market Impact Component parameter values for 2023–28
Parameter
Target | 1258
Unplanned outage event limit | 214
Dollar per dispatch interval | 132.6657
Table 10.3 Final decision — Distribution, Floors and Caps for 2023–28
Parameter | Distribution | Floor | Cap
|  | (95th percentile) | (5th percentile)
Unplanned outage circuit event rate
Circuit outage rate - fault | Poisson | 5 | 0
Circuit outage rate - forced | Poisson | 3 | 0

## SC
7.9.1 - Historical performance and proposed floor, caps and targets for the service component of the STPIS
Parameter | Performance actuals | [5 empty] | Average of actual performance | Floor | Target | Cap | Weighting (% of MAR)
| 2017 | 2018 | 2019 | 2020 | 2021 | 2022
Unplanned outage circuit event rate:
Circuit outage rate - fault | 200% | 100% | 300% | 0% | 400% |  | 200% |  |  |  | 0.75%
Circuit outage rate - forced | 100% | 300% | 0% | 0% | 200% |  | 120% |  |  |  | 0.5%
Loss of supply event frequency (number of events):
> (x) system minutes | [6 empty] | N/A
> (y) system minutes | [6 empty] | N/A
Average outage duration (minutes):
Proper operation of equipment (number of events):
Failure of protection system | [6 empty] | N/A
Material failure of SCADA | [6 empty] | N/A |  |  |  | 0%
Incorrect operational isolation of primary or secondary equipment | [10 empty] | 0%

## SC - AER Simulation Results
Murraylink - distributions selected based on mechanical selection of lowest AIC, 2017-2021 underlying input data.
| Distribution | AIC | Mean of sample | Mean of fitted distribution | SD of fitted distribution | Cap at 1SD | Cap at 2SD | Collar at 1SD | Collar at 2SD | 5th percentile of fitted distribution | 50th percentile of fitted distribution | 95th percentile of fitted distribution
Circuit outage rate - fault | Poisson | 20.7963 | 2 | 2 | 1.41 | 3.41 | 4.82 | 0.59 | -0.82 | 0 | 2 | 5
Circuit outage rate - forced | Poisson | 18.1153 | 1.2 | 1.2 | 1.095 | 2.295 | 3.39 | 0.105 | -0.99 | 0 | 1 | 3

## MIC
Murraylink data applied - STPIS Version 5 - Appendix F, Example 2, Table 6-2
Performance target and measure determination
| Regulatory period (RP) |  | Target set in RCP | Raw performance count |  |  | Capped unplanned count | Adjusted performance count
|  |  | Target [1] | Planned | Unplanned | Total (Planned + Unplanned) | Min of Raw Unplanned or 0.17x(M) | (a) + (d)
| (RP) | year | (T) | (a) | (b) | (a) + (b) | (d) | (e)
| RP1 | 2015 |  | 454 | 90 | 544 | 63 | 517
| RP1 | 2016 |  | 1875 | 1081 | 2956 | 63 | 1938
| RP1 | 2017 |  | 228 | 436 | 664 | 63 | 291
| RP2 | 2018 | 372 | 2679 | 132 | 2811 | 132 | 2811
| RP2 | 2019 | 372 | 18 | 260 | 278 | 260 | 278
| RP2 | 2020 | 372 | 2427 | 46 | 2473 | 46 | 2473
| RP2 | 2021 | 372 | 750 | 2933 | 3683 | 321 | 1071
| Max |  |  |  |  | 3683 |  | 2811
| Min |  |  |  |  | 278 |  | 278
| Average of median 5 |  |  |  |  | 1890 |  | 1258
[6 empty] | [M] |  | [T]
RP3:
| MAR [1]: | 16689346.59
| Dollar per dispatch interval: | 132.6657
RP3:
| Performance target: | 1258
Input:
| RP1 unplanned cap | 63 | As per final decision for 2018-23 Appendix F example 1
| RP2 unplanned cap | 321 | 18-23 Regulatory period calculated Appendix F example 2
| RP3 unplanned cap | 214 | 23-28 Regulatory period Appendix F example 2

## FD MAR Values
Murraylink Final decision
Year | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | Total
MAR smoothed ($m, nominal) | 16.6893 | 17.3999 | 18.1406 | 18.9129 | 19.7181 | 90.8608
MAR smoothed ($m, 2022-23) | 16.216 | 16.4268 | 16.6403 | 16.8566 | 17.0758 | 83.2154