## Draft Decision
Table 10.1 Draft decision — Service Components caps floors and target for 2023–28
Parameter | Floor | Target | Cap
Unplanned outage circuit event rate (%)
Transmission line outage rate | 21.84 | 14.2889 | 8.8
Transformer outage - fault | 14.98 | 9.6582 | 5.87
Reactive plant - fault | 18.72 | 12.1382 | 6.81
Transmission line outage - forced outage | 15.24 | 8.6761 | 3.76
Transformer outage - forced outage | 17.45 | 9.8699 | 5.05
Reactive plant - forced outage | 13.68 | 9.8152 | 6.88
Loss of supply events frequency (no of events)
No. of events > 0.05 system minutes | 3 | 1.2 | 0
No. of events > 0.25 system minutes | 1 | 0.2 | 0
Average outage duration (minutes)
Average outage duration | 87.24 | 56.2149 | 35.28
Proper operation of equipment (no of events)
Failure of protection system | 19 | 12.8 | 7
Material failure of SCADA | 0 | 0 | 0
Incorrect operational isolation of primary or secondary equipment | 9 | 5.4 | 2
Table 10.2 Draft decision — Market Impact Component parameter values for 2023–28
Parameter
Target | 6476
Unplanned outage event limit | 1101
Dollar per dispatch interval | 1385.0648
Table 10.3 Draft decision — Network Capability Component for 2023–28
Priority project name | Proposed capex ($ million) | Proposed opex ($ million) | Amount approved ($ million)
1. Increase capacity for Generation between Darlington Point and Wagga | 0 | 0 | 0
2. Darlington Point 330/220 kV transformer tripping scheme | 0.4 | 0.0* | 0.4
3. Increase capacity for generation X5 voltage stability constraints | 5.5 | 0.1 | 5.6
4. 94T line dynamic ratings | 0.4 | 0.0* | 0.4
5. Yass 330/132 kV transformer dynamic ratings | 0 | 0 | 0
6. Maintain capacity during Climate Change – install dynamic line ratings on multiple lines | 5.9 |  | 5.9
Total | 12.2 | 0.1 | 12.3
* Values rounded up to millions
Table 10.4 Draft decision — Distribution, Floors and Caps for 2023–28
Parameter | Distribution | Floor | Cap
|  | (95th percentile) | (5th percentile)
Unplanned outage circuit event rate (%)
Transmission line outage rate | LogLogistic | 21.84 | 8.8
Transformer outage - fault | LogLogistic | 14.98 | 5.87
Reactive plant - fault | Gamma | 18.72 | 6.81
Transmission line outage - forced outage | Gamma | 15.24 | 3.76
Transformer outage - forced outage | Pearson5 | 17.45 | 5.05
Reactive plant - forced outage | Pearson5 | 13.68 | 6.88
Loss of supply events frequency
No. of events > 0.05 system minutes | Poisson | 3 | 0
No. of events > 0.2 system minutes | Poisson | 1 | 0
Average outage duration
Average outage duration | Pearson5 | 87.24 | 35.28
Proper operation of equipment
Failure of protection system | Poisson | 19 | 7
Material failure of SCADA | 0 | 0 | 0
Incorrect operational isolation of primary or secondary equipment | Poisson | 9 | 2

## SC
7.9.1 - Historical performance and proposed floor, caps and targets for the service component of the STPIS
Parameter | Performance actuals | [5 empty] | Average of actual performance
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Unplanned outage circuit event rate:
Transmission line outage - fault | 0.13744 | 0.12934 | 0.18024 | 0.1225 | 0.18648 | 0.09589 | 0.14289
Transformer outage – fault | 0.17558 | 0.094796 | 0.12861 | 0.067416 | 0.11837 | 0.073724 | 0.096582
Reactive plant – fault | 0.05886 | 0.1037 | 0.17723 | 0.13669 | 0.11972 | 0.069565 | 0.12138
Transmission line outage – forced outage | 0.13744 | 0.12934 | 0.085375 | 0.070671 | 0.11189 | 0.03653 | 0.086761
Transformer outage – forced outage | 0.19753 | 0.18959 | 0.078285 | 0.067416 | 0.09582 | 0.062382 | 0.098699
Reactive plant – forced outage | 0.22808 | 0.14074 | 0.081231 | 0.10072 | 0.091549 | 0.076522 | 0.098152
Loss of supply event frequency (number of events):
> (x) system minutes | 2 | 1 | 1 | 3 | 1 | 0 | 1.2
> (y) system minutes | 0 | 0 | 0 | 0 | 1 | 0 | 0.2
Average outage duration (minutes): | 169.1775 | 35.64 | 58.2 | 69.825 | 45.1714 | 72.2381 | 56.2149
Proper operation of equipment (number of events):
Failure of protection system | 20 | 11 | 20 | 12 | 11 | 10 | 12.8
Material failure of SCADA | 3 | 0 | 0 | 0 | 0 | 0 | 0
Incorrect operational isolation of primary or secondary equipment | 5 | 6 | 6 | 3 | 6 | 6 | 5.4
Please confirm this is consistent with Transgrid's STPIS outcome for 2020
Please confirm this is consistent with Transgrid's STPIS annual submission for 2021

## SC - AER Simulation Results
Transgrid - distributions selected based on mechanical selection of lowest K-S distance statistic, 2017-2021 underlying input data. Calendar year data
| Distribution | KS Distance Statistic | Mean of sample | Mean of fitted distribution | SD of fitted distribution | Cap at 1SD | Cap at 2SD | Collar at 1SD | Collar at 2SD | 5th percentile of fitted distribution | 50th percentile of fitted distribution | 95th percentile of fitted distribution
Transmission line outage - fault | LogLogistic | 0.2455 | 0.1429 | 0.1442 | 0.0424 | 0.1866 | 0.229 | 0.1018 | 0.0594 | 0.088 | 0.1387 | 0.2184
Transformer outage – fault | LogLogistic | 0.2195 | 0.0966 | 0.0978 | 0.0298 | 0.1276 | 0.1574 | 0.068 | 0.0382 | 0.0587 | 0.0938 | 0.1498
Reactive plant – fault | Gamma | 0.1436 | 0.1214 | 0.1214 | 0.0366 | 0.158 | 0.1946 | 0.0848 | 0.0482 | 0.0681 | 0.1177 | 0.1872
Transmission line outage – forced outage | Gamma | 0.1828 | 0.0868 | 0.0868 | 0.0356 | 0.1224 | 0.158 | 0.0512 | 0.0156 | 0.0376 | 0.0819 | 0.1524
Transformer outage – forced outage | Pearson5 | 0.2273 | 0.0987 | 0.0973 | 0.0417 | 0.139 | 0.1807 | 0.0556 | 0.0139 | 0.0505 | 0.0882 | 0.1745
Reactive plant – forced outage | Pearson5 | 0.1925 | 0.0982 | 0.098 | 0.0212 | 0.1192 | 0.1404 | 0.0768 | 0.0556 | 0.0688 | 0.0951 | 0.1368
Average outage duration | Pearson5 | 0.2221 | 56.21 | 56.47 | 16.56 | 73.03 | 89.59 | 39.91 | 23.35 | 35.28 | 53.64 | 87.24
Distributions fitted setting: lower limit with fixed bound of zero; unsure upper limit; no change to default "suppress questionable fits" setting
While @Risk allows beta general to be a candidate distribution, we have not included it as a candidate distribution as it uses 4 parameters and we only have 5 data points.
Where a candidate distribution has been estimated to have an infinite standard deviation we have ruled it out of consideration.
Transgrid - distributions selected based on mechanical selection of lowest AIC, 2017-2021 underlying input data.
| Distribution | AIC | Mean of sample | Mean of fitted distribution | SD of fitted distribution | Cap at 1SD | Cap at 2SD | Collar at 1SD | Collar at 2SD | 5th percentile of fitted distribution | 50th percentile of fitted distribution | 95th percentile of fitted distribution
Number of events > (x) system minutes | Poisson | 16.729 | 1.2 | 1.2 | 1.095 | 2.295 | 3.39 | 0.105 | -0.99 | 0 | 1 | 3
Number of events > (y) system minutes | Poisson | 8.5522 | 0.2 | 0.2 | 0.447 | 0.647 | 1.094 | -0.247 | -0.694 | 0 | 0 | 1
Failure of protection system | Poisson | 29.8681 | 12.8 | 12.8 | 3.578 | 16.378 | 19.956 | 9.222 | 5.644 | 7 | 13 | 19
Material failure of SCADA
Incorrect operational isolation of primary or secondary equipment | Poisson | 22.4853 | 5.4 | 5.4 | 2.324 | 7.724 | 10.048 | 3.076 | 0.752 | 2 | 5 | 9

## MIC
Transgrid data applied - STPIS Version 5 - Appendix F, Example 2, Table 6-2
Performance target and measure determination
| Regulatory period (RP) |  | Target set in RCP | Raw performance count |  |  | Capped unplanned count | Adjusted performance count |  | Outcomes RIN/Annual Compliance
|  |  | Target [1] | Planned | Unplanned | Total (Planned + Unplanned) | Min of Raw Unplanned or 0.17x(M) | (a) + (d) | Year | Planned | Unplanned | Planned Count Adjustment due to Force Majeure Exclusion Revision | Adjusted Planned Count | Total
| (RP) | year | (T) | (a) | (b) | (a) + (b) | (d) | (e)
| RP1 | 2015 |  | 1222 | 107 | 1329 | 107 | 1329 | 2011 | 814 | 56 | 0 | 814 | 870
| RP1 | 2016 |  | 3008 | 48 | 3056 | 48 | 3056 | 2012 | 492 | 281 | 0 | 492 | 773
| RP1 | 2017 |  | 6134.5 | 675 | 6809.5 | 229 | 6363.5 | 2013 | 585 | 8 | 0 | 585 | 593
| RP2 | 2018 | 1348 | 4488 | 2589 | 7077 | 1193 | 5681 | 2014 | 467.5 | 282 | -4 | 463.5 | 745.5
| RP2 | 2019 | 1348 | 1023 | 409 | 1432 | 409 | 1432 | 2015 | 1222 | 107 | -32 | 1190 | 1297
| RP2 | 2020 | 1348 | 14652 | 2067 | 16719 | 1193 | 15845 | 2016 | 3008 | 48 | 0 | 3008 | 3056
| RP2 | 2021 | 1348 | 33817 | 605 | 34422 | 605 | 34422 | 2017 | 6134.5 | 675 | 0 | 6134.5 | 6809.5
[9 empty] | 2018 | 4488 | 2589 | 0 | 4488 | 7077
| Max |  |  |  |  | 34422 |  | 34422 | 2019 | 1023 | 409 | 0 | 1023 | 1432
| Min |  |  |  |  | 1329 |  | 1329 | 2020 | 14652 | 2067 | 0 | 14652 | 16719
| Average of median 5 |  |  |  |  | 7019 |  | 6476 | 2021 | 33817 | 605 | 0 | 33817 | 34422
[6 empty] | [M] |  | [T]
PR3:
| MAR [1]: | 896967995.2452 | Updated 21092022
| Dollar per dispatch interval: | 1385.0648
PR3:
| Performance target: | 6476
Input:
| PR1 unplanned cap | 229
| PR2 unplanned cap | 1193 | RR18-23 Regulatory period
| PR3 unplanned cap | 1101 | RR23-28 Regulatory period
Note on P8: Stephen Antoon: Submitted to the AER as part of IR#011 in April 2022, as requested by the AER.