## Cover
Distribution Network Service Provider
Annual reporting template
This template is to be used by a DNSP to fulfil its annual reporting obligations to the AER.
Colour coding of input sheets:
Dark blue - Headings
Yellow - Input cells
Grey - No inputs required
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP - trading name: |  | ActewAGL
DNSP - Australian business number: |  | 76 670 568 688
Reporting year: |  | 2012-13
Business address | Address |  | 40 Bunda Street
| Suburb |  | Canberra
|  | State | ACT | Postcode | 2601
Postal address | Address |  | GPO Box 366
| Suburb |  | Canberra
|  | State | ACT | Postcode | 2601
Contact name/s | Robert Walker
Contact phone/s | 02 6248 3847
Contact email address/s | Robert.Walker@actewagl.com.au

## Contents
Electricity DNSP Annual Reporting Template
Table of contents
Cover sheet | 3. Quality of service and customer service
1. Service Target Performance Incentive Scheme | 4. General Information
1a. STPIS - Reliability | 5. Outages
1b. STPIS - Customer service | 5a. Network data - outages
1c. STPIS - Daily performance | 5b. Network data - feeder reliability
1d. STPIS - MED threshold | 5c. Network data - outages
1e. STPIS - Exclusions | 5d. Network data - planned outages
1f. STPIS - GSL | 6. Weighted average cost of debt
2. Demand | 7. Asset installation

## 1a. STPIS Reliability
ActewAGL
STPIS Data Reporting
2012-13
Reliability
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: SAIDI | Source : Apply Database (checked against monthly reports)
Unplanned SAIDI | CBD | Urban | Rural short | Rural long | Whole network
Total |  | 48.3 | 27 |  | 47.7474
Total - after removing excluded events |  | 28.2 | 25.9 |  | 28.6674
Table 2: SAIFI | Source : Apply Database (checked against monthly reports)
Unplanned SAIFI | CBD | Urban | Rural short | Rural long | Whole network
Total |  | 73.9216 | 61.9054 |  | 73.6053
Total - after removing excluded events |  | 60.8888 | 61.1946 |  | 60.8968
Table 3: Average distribution customer numbers
| CBD | Urban | Rural short | Rural long | Whole network
Customer numbers start of period |  | 168665 | 4521 |  | 173186
Customer numbers end of period |  | 172554 | 4702 |  | 177256
Average distribution customer numbers |  | 170609.5 | 4611.5 |  | 175221
2013 Report Tab 1a
Table 1: SAIDI | Source : Apply Database (checked against monthly reports)
Unplanned SAIDI | CBD | Urban | Rural short | Rural long | Whole network
Total |  | 48.3079 | 27.012 |  | 47.7474
Total - after removing excluded events |  | 28.7426 | 25.8879 |  | 28.6674
Table 2: SAIFI | Source : Apply Database (checked against monthly reports)
Unplanned SAIFI | CBD | Urban | Rural short | Rural long | Whole network
Total |  | 73.9216 | 61.9054 |  | 73.6053
Total - after removing excluded events |  | 60.8888 | 61.1946 |  | 60.8968
Table 3: Average distribution customer numbers
| CBD | Urban | Rural short | Rural long | Whole network
Customer numbers start of period |  | 168665 | 4521 |  | 173186
Customer numbers end of period |  | 172554 | 4702 |  | 177256
Average distribution customer numbers |  | 170609.5 | 4611.5 |  | 175221
Contents

## 1b. STPIS Customer Service
ActewAGL
STPIS Data Reporting
2012-13
Customer service
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Telephone answering |  |  | Source: Calls are recorded in the CISCO Phone Database
Telephone answering | Total - after removing excluded events | Total | Telephone answering is undertaken in accordance with procedure "Network Division Telephony - Regulatory Reporting (Fault calls) v.1
Total number of calls | 33150 | 35945
Number of calls answered within 30 seconds | 25596
Percentage of calls answered within 30 seconds | 77.21%
Table 2: New connections
Note: this is for newly energised properties only
New connections
Number of new connections
Number of new connections not provided on or before the agreed date
Percentage of new connections not provided on or before the agreed date
Table 3: Streetlight repair
Streetlight repair
Total number of streetlights
Total number of streetlight faults
Total number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neighbouring business
Faulty streetlights not repaired within 5 days of fault report or agreed date
Percentage of faulty streetlights not repaired within 5 days of fault report or agreed date
Table 4: Response to written enquiries
Note: this does not include Saturdays, Sundays and Public holidays |  |  | Please note: This relates to written complaints not written connection enquiries. Additionally, the ACT Consumer Protection Code 2010 states that complaints must be acknowledged immediately or as soon as practicable, and responses provided within 20 business days. Of the total written enquiries received over the period 11 (8%) were not responded to within the jurisdictional requirements and were subject to review by the ICRC in accordance with local laws.
Response to written enquiries
Number of written enquiries
Number of written enquiries not responded to in 5 days
Percentage of written enquiries not responded to in 5 days
Note on C11: Rob Walker: 5/11/13 This data is from Contact Service Queue Activity (by CSQ) report from CISCO phone platform. This is "Faults Electricity" - CSQ name ID. This value excludes Med and Abandoned Calls within 30s.
Note on C12: Rob Walker: 5/11/13 This data is from Contact Service Queue Activity (by CSQ) report from CISCO phone platform. This is "Faults Electricity" - CSQ name ID. This value excludes Med only.
Contents

## 1c. STPIS Daily Performance
ActewAGL
STPIS Data Reporting |  |  |  | 2012-07-01
2012-13 |  |  |  | 2013-07-01
Daily Performance
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Daily performance data (Unplanned SAIDI, Unplanned SAIFI)
Note: the excluded events to be removed from the data refer only to events listed in clause 3.3(a) of the STPIS, with respect to reliability data, and in clause 5.4(a) of the STPIS with respect to customer service parameters.
Customer service
Date | Network SAIDI all events total | Network SAIDI all events after removing excluded events | CBD SAIDI all events total | CBD SAIDI all events after removing excluded events | Urban SAIDI all events total | Urban SAIDI all events after removing excluded events | Long rural SAIDI all events total | Long rural all events after removing excluded events | Short rural SAIDI all events total | Short rural SAIDI all events after removing excluded events | Network SAIFI all events total | Network SAIFI all events after removing excluded events | CBD SAIFI all events total | CBD SAIFI all events after removing excluded events | Urban SAIFI all events total | Urban SAIFI all events after removing excluded events | Long rural SAIFI all events total | Long rural SAIFI all events after removing excluded events | Short rural SAIFI all events total | Short Rural SAIFI all events after removing excluded events | Total number of calls (after removing excluded events) | Total number of calls answered in 30 seconds (after removing excluded events) | MED
2012-07-01 | 0.012293 | 0.012293 |  |  | 0.0084579 | 0.0084579 |  |  | 0.0038352 | 0.0038352 | 5.1364e-05 | 5.1364e-05 |  |  | 3.995e-05 | 3.995e-05 |  |  | 1.1414e-05 | 1.1414e-05 | 41 | 34 | NO
2012-07-02 | 0.34859 | 0.34859 |  |  | 0.34859 | 0.34859 |  |  | 0 | 0 | 0.0015067 | 0.0015067 |  |  | 0.0015067 | 0.0015067 |  |  | 0 | 0 | 100 | 84 | NO
2012-07-03 | 0.42063 | 0.42063 |  |  | 0.42063 | 0.42063 |  |  | 0 | 0 | 0.0054274 | 0.0054274 |  |  | 0.0054274 | 0.0054274 |  |  | 0 | 0 | 138 | 96 | NO
2012-07-04 | 0.25726 | 0.25726 |  |  | 0.25726 | 0.25726 |  |  | 0 | 0 | 0.0013183 | 0.0013183 |  |  | 0.0013183 | 0.0013183 |  |  | 0 | 0 | 89 | 81 | NO
2012-07-05 | 0.54374 | 0.54374 |  |  | 0.54374 | 0.54374 |  |  | 0 | 0 | 0.0023399 | 0.0023399 |  |  | 0.0023399 | 0.0023399 |  |  | 0 | 0 | 94 | 74 | NO
2012-07-06 | 0.36694 | 0.36694 |  |  | 0.36619 | 0.36619 |  |  | 0.00075333 | 0.00075333 | 0.0013583 | 0.0013583 |  |  | 0.0013526 | 0.0013526 |  |  | 5.7071e-06 | 5.7071e-06 | 86 | 74 | NO
2012-07-07 | 0.44594 | 0.44594 |  |  | 0.44594 | 0.44594 |  |  | 0 | 0 | 0.014388 | 0.014388 |  |  | 0.014388 | 0.014388 |  |  | 0 | 0 | 143 | 104 | NO
2012-07-08 | 0.034345 | 0.034345 |  |  | 0.034345 | 0.034345 |  |  | 0 | 0 | 0.0003995 | 0.0003995 |  |  | 0.0003995 | 0.0003995 |  |  | 0 | 0 | 44 | 31 | NO
2012-07-09 | 0.034927 | 0.034927 |  |  | 0.034927 | 0.034927 |  |  | 0 | 0 | 0.0014268 | 0.0014268 |  |  | 0.0014268 | 0.0014268 |  |  | 0 | 0 | 182 | 136 | NO
2012-07-10 | 0.21463 | 0.21463 |  |  | 0.18919 | 0.18919 |  |  | 0.025442 | 0.025442 | 0.0010958 | 0.0010958 |  |  | 0.00094167 | 0.00094167 |  |  | 0.00015409 | 0.00015409 | 116 | 105 | NO
2012-07-11 | 0.23826 | 0.23826 |  |  | 0.23826 | 0.23826 |  |  | 0 | 0 | 0.0016836 | 0.0016836 |  |  | 0.0016836 | 0.0016836 |  |  | 0 | 0 | 116 | 92 | NO
2012-07-12 | 0.12803 | 0.12803 |  |  | 0.12803 | 0.12803 |  |  | 0 | 0 | 0.00073051 | 0.00073051 |  |  | 0.00073051 | 0.00073051 |  |  | 0 | 0 | 70 | 63 | NO
2012-07-13 | 0.1319 | 0.1319 |  |  | 0.1319 | 0.1319 |  |  | 0 | 0 | 0.00068485 | 0.00068485 |  |  | 0.00068485 | 0.00068485 |  |  | 0 | 0 | 77 | 68 | NO
2012-07-14 | 0.095845 | 0.095845 |  |  | 0.095845 | 0.095845 |  |  | 0 | 0 | 0.0004052 | 0.0004052 |  |  | 0.0004052 | 0.0004052 |  |  | 0 | 0 | 54 | 51 | NO
2012-07-15 | 0.078586 | 0.078586 |  |  | 0.078586 | 0.078586 |  |  | 0 | 0 | 0.00019404 | 0.00019404 |  |  | 0.00019404 | 0.00019404 |  |  | 0 | 0 | 28 | 25 | NO
2012-07-16 | 0.076018 | 0.076018 |  |  | 0.076018 | 0.076018 |  |  | 0 | 0 | 0.00037096 | 0.00037096 |  |  | 0.00037096 | 0.00037096 |  |  | 0 | 0 | 81 | 68 | NO
2012-07-17 | 0.1847 | 0.1847 |  |  | 0.1847 | 0.1847 |  |  | 0 | 0 | 0.0080013 | 0.0080013 |  |  | 0.0080013 | 0.0080013 |  |  | 0 | 0 | 56 | 51 | NO
2012-07-18 | 0.81987 | 0.81987 |  |  | 0.81987 | 0.81987 |  |  | 0 | 0 | 0.0086805 | 0.0086805 |  |  | 0.0086805 | 0.0086805 |  |  | 0 | 0 | 155 | 110 | NO
2012-07-19 | 0.17402 | 0.17402 |  |  | 0.17402 | 0.17402 |  |  | 0 | 0 | 0.00063349 | 0.00063349 |  |  | 0.00063349 | 0.00063349 |  |  | 0 | 0 | 53 | 47 | NO
2012-07-20 | 0.092386 | 0.092386 |  |  | 0.092044 | 0.092044 |  |  | 0.00034242 | 0.00034242 | 0.00041662 | 0.00041662 |  |  | 0.0004052 | 0.0004052 |  |  | 1.1414e-05 | 1.1414e-05 | 65 | 57 | NO
2012-07-21 | 0.0024312 | 0.0024312 |  |  | 0.0010958 | 0.0010958 |  |  | 0.0013355 | 0.0013355 | 1.7121e-05 | 1.7121e-05 |  |  | 5.7071e-06 | 5.7071e-06 |  |  | 1.1414e-05 | 1.1414e-05 | 26 | 21 | NO
2012-07-22 | 0.029551 | 0.029551 |  |  | 0.029551 | 0.029551 |  |  | 0 | 0 | 0.00021687 | 0.00021687 |  |  | 0.00021687 | 0.00021687 |  |  | 0 | 0 | 41 | 35 | NO
2012-07-23 | 0.07547 | 0.07547 |  |  | 0.07547 | 0.07547 |  |  | 0 | 0 | 0.0008047 | 0.0008047 |  |  | 0.0008047 | 0.0008047 |  |  | 0 | 0 | 97 | 91 | NO
2012-07-24 | 0.43978 | 0.43978 |  |  | 0.43474 | 0.43474 |  |  | 0.0050336 | 0.0050336 | 0.0023228 | 0.0023228 |  |  | 0.0023057 | 0.0023057 |  |  | 1.7121e-05 | 1.7121e-05 | 73 | 68 | NO
2012-07-25 | 0.3818 | 0.3818 |  |  | 0.3263 | 0.3263 |  |  | 0.055507 | 0.055507 | 0.0044059 | 0.0044059 |  |  | 0.0040007 | 0.0040007 |  |  | 0.0004052 | 0.0004052 | 77 | 70 | NO
2012-07-26 | 0.25795 | 0.25795 |  |  | 0.25795 | 0.25795 |  |  | 0 | 0 | 0.00091313 | 0.00091313 |  |  | 0.00091313 | 0.00091313 |  |  | 0 | 0 | 71 | 62 | NO
2012-07-27 | 0.43858 | 0.43858 |  |  | 0.41505 | 0.41505 |  |  | 0.023525 | 0.023525 | 0.0066202 | 0.0066202 |  |  | 0.0063919 | 0.0063919 |  |  | 0.00022828 | 0.00022828 | 125 | 92 | NO
2012-07-28 | 0.058109 | 0.058109 |  |  | 0.058109 | 0.058109 |  |  | 0 | 0 | 0.00078758 | 0.00078758 |  |  | 0.00078758 | 0.00078758 |  |  | 0 | 0 | 55 | 51 | NO
2012-07-29 | 0.023353 | 0.023353 |  |  | 0.023353 | 0.023353 |  |  | 0 | 0 | 0.00026253 | 0.00026253 |  |  | 0.00026253 | 0.00026253 |  |  | 0 | 0 | 20 | 18 | NO
2012-07-30 | 0.37369 | 0.37369 |  |  | 0.37369 | 0.37369 |  |  | 0 | 0 | 0.0017007 | 0.0017007 |  |  | 0.0017007 | 0.0017007 |  |  | 0 | 0 | 93 | 64 | NO
2012-07-31 | 0.2297 | 0.2297 |  |  | 0.2297 | 0.2297 |  |  | 0 | 0 | 0.0066659 | 0.0066659 |  |  | 0.0066659 | 0.0066659 |  |  | 0 | 0 | 129 | 95 | NO
2012-08-01 | 0.30435 | 0.30435 |  |  | 0.25925 | 0.25925 |  |  | 0.045097 | 0.045097 | 0.0014724 | 0.0014724 |  |  | 0.0013183 | 0.0013183 |  |  | 0.00015409 | 0.00015409 | 97 | 86 | NO
2012-08-02 | 0.49193 | 0.49193 |  |  | 0.49193 | 0.49193 |  |  | 0 | 0 | 0.0069113 | 0.0069113 |  |  | 0.0069113 | 0.0069113 |  |  | 0 | 0 | 130 | 99 | NO
2012-08-03 | 0.40796 | 0.40796 |  |  | 0.40796 | 0.40796 |  |  | 0 | 0 | 0.0017692 | 0.0017692 |  |  | 0.0017692 | 0.0017692 |  |  | 0 | 0 | 85 | 72 | NO
2012-08-04 | 0.0057185 | 0.0057185 |  |  | 0.0057185 | 0.0057185 |  |  | 0 | 0 | 0.00010273 | 0.00010273 |  |  | 0.00010273 | 0.00010273 |  |  | 0 | 0 | 31 | 31 | NO
2012-08-05 | 0.03277 | 0.03277 |  |  | 0.03277 | 0.03277 |  |  | 0 | 0 | 0.00034813 | 0.00034813 |  |  | 0.00034813 | 0.00034813 |  |  | 0 | 0 | 40 | 35 | NO
2012-08-06 | 0.10783 | 0.10783 |  |  | 0.10783 | 0.10783 |  |  | 0 | 0 | 0.00058212 | 0.00058212 |  |  | 0.00058212 | 0.00058212 |  |  | 0 | 0 | 83 | 72 | NO
2012-08-07 | 0.20545 | 0.20545 |  |  | 0.19611 | 0.19611 |  |  | 0.0093482 | 0.0093482 | 0.00069056 | 0.00069056 |  |  | 0.00066202 | 0.00066202 |  |  | 2.8535e-05 | 2.8535e-05 | 58 | 54 | NO
2012-08-08 | 0.13855 | 0.13855 |  |  | 0.073347 | 0.073347 |  |  | 0.065198 | 0.065198 | 0.00071909 | 0.00071909 |  |  | 0.00054788 | 0.00054788 |  |  | 0.00017121 | 0.00017121 | 72 | 60 | NO
2012-08-09 | 0.76087 | 0.76087 |  |  | 0.75679 | 0.75679 |  |  | 0.0040749 | 0.0040749 | 0.011271 | 0.011271 |  |  | 0.01126 | 0.01126 |  |  | 1.1414e-05 | 1.1414e-05 | 94 | 80 | NO
2012-08-10 | 0.17899 | 0.17899 |  |  | 0.17899 | 0.17899 |  |  | 0 | 0 | 0.00078758 | 0.00078758 |  |  | 0.00078758 | 0.00078758 |  |  | 0 | 0 | 104 | 88 | NO
2012-08-11 | 0.069649 | 0.069649 |  |  | 0.069649 | 0.069649 |  |  | 0 | 0 | 0.00033101 | 0.00033101 |  |  | 0.00033101 | 0.00033101 |  |  | 0 | 0 | 48 | 44 | NO
2012-08-12 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 28 | 27 | NO
2012-08-13 | 0.1079 | 0.1079 |  |  | 0.1079 | 0.1079 |  |  | 0 | 0 | 0.00057641 | 0.00057641 |  |  | 0.00057641 | 0.00057641 |  |  | 0 | 0 | 73 | 63 | NO
2012-08-14 | 0.34129 | 0.34129 |  |  | 0.34129 | 0.34129 |  |  | 0 | 0 | 0.0014211 | 0.0014211 |  |  | 0.0014211 | 0.0014211 |  |  | 0 | 0 | 105 | 77 | NO
2012-08-15 | 0.12314 | 0.12314 |  |  | 0.12314 | 0.12314 |  |  | 0 | 0 | 0.00057641 | 0.00057641 |  |  | 0.00057641 | 0.00057641 |  |  | 0 | 0 | 53 | 43 | NO
2012-08-16 | 0.24627 | 0.24627 |  |  | 0.24627 | 0.24627 |  |  | 0 | 0 | 0.00093025 | 0.00093025 |  |  | 0.00093025 | 0.00093025 |  |  | 0 | 0 | 83 | 73 | NO
2012-08-17 | 0.21295 | 0.21295 |  |  | 0.21295 | 0.21295 |  |  | 0 | 0 | 0.0039835 | 0.0039835 |  |  | 0.0039835 | 0.0039835 |  |  | 0 | 0 | 122 | 101 | NO
2012-08-18 | 0.080299 | 0.080299 |  |  | 0.064239 | 0.064239 |  |  | 0.01606 | 0.01606 | 0.00037096 | 0.00037096 |  |  | 0.00029106 | 0.00029106 |  |  | 7.9899e-05 | 7.9899e-05 | 62 | 52 | NO
2012-08-19 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 29 | 27 | NO
2012-08-20 | 0.31048 | 0.31048 |  |  | 0.31048 | 0.31048 |  |  | 0 | 0 | 0.0056272 | 0.0056272 |  |  | 0.0056272 | 0.0056272 |  |  | 0 | 0 | 166 | 110 | NO
2012-08-21 | 0.42468 | 0.42468 |  |  | 0.33732 | 0.33732 |  |  | 0.087353 | 0.087353 | 0.0015352 | 0.0015352 |  |  | 0.0013069 | 0.0013069 |  |  | 0.00022828 | 0.00022828 | 86 | 70 | NO
2012-08-22 | 0.19224 | 0.19224 |  |  | 0.19224 | 0.19224 |  |  | 0 | 0 | 0.00086177 | 0.00086177 |  |  | 0.00086177 | 0.00086177 |  |  | 0 | 0 | 89 | 82 | NO
2012-08-23 | 0.04044 | 0.04044 |  |  | 0.018388 | 0.018388 |  |  | 0.022052 | 0.022052 | 0.00061636 | 0.00061636 |  |  | 0.00035384 | 0.00035384 |  |  | 0.00026253 | 0.00026253 | 126 | 113 | NO
2012-08-24 | 0.098379 | 0.098379 |  |  | 0.098379 | 0.098379 |  |  | 0 | 0 | 0.00113 | 0.00113 |  |  | 0.00113 | 0.00113 |  |  | 0 | 0 | 63 | 61 | NO
2012-08-25 | 0.0058555 | 0.0058555 |  |  | 0.0058555 | 0.0058555 |  |  | 0 | 0 | 0.00010843 | 0.00010843 |  |  | 0.00010843 | 0.00010843 |  |  | 0 | 0 | 23 | 21 | NO
2012-08-26 | 0.023593 | 0.023593 |  |  | 0.023593 | 0.023593 |  |  | 0 | 0 | 0.00017121 | 0.00017121 |  |  | 0.00017121 | 0.00017121 |  |  | 0 | 0 | 26 | 17 | NO
2012-08-27 | 0.13824 | 0.13824 |  |  | 0.13824 | 0.13824 |  |  | 0 | 0 | 0.00047939 | 0.00047939 |  |  | 0.00047939 | 0.00047939 |  |  | 0 | 0 | 53 | 52 | NO
2012-08-28 | 0.057082 | 0.057082 |  |  | 0.042392 | 0.042392 |  |  | 0.01469 | 0.01469 | 0.00045657 | 0.00045657 |  |  | 0.00041662 | 0.00041662 |  |  | 3.995e-05 | 3.995e-05 | 82 | 79 | NO
2012-08-29 | 0.12738 | 0.12738 |  |  | 0.12738 | 0.12738 |  |  | 0 | 0 | 0.0011528 | 0.0011528 |  |  | 0.0011528 | 0.0011528 |  |  | 0 | 0 | 70 | 59 | NO
2012-08-30 | 0.1043 | 0.1043 |  |  | 0.10321 | 0.10321 |  |  | 0.0010958 | 0.0010958 | 0.00082753 | 0.00082753 |  |  | 0.00082182 | 0.00082182 |  |  | 5.7071e-06 | 5.7071e-06 | 64 | 47 | NO
2012-08-31 | 0.59839 | 0.59839 |  |  | 0.5738 | 0.5738 |  |  | 0.024586 | 0.024586 | 0.0019861 | 0.0019861 |  |  | 0.0016094 | 0.0016094 |  |  | 0.00037667 | 0.00037667 | 89 | 79 | NO
2012-09-01 | 0.0047255 | 0.0047255 |  |  | 0.0047255 | 0.0047255 |  |  | 0 | 0 | 0.0001598 | 0.0001598 |  |  | 0.0001598 | 0.0001598 |  |  | 0 | 0 | 37 | 32 | NO
2012-09-02 | 0.024107 | 0.024107 |  |  | 0.024107 | 0.024107 |  |  | 0 | 0 | 0.00021116 | 0.00021116 |  |  | 0.00021116 | 0.00021116 |  |  | 0 | 0 | 29 | 24 | NO
2012-09-03 | 0.018251 | 0.018251 |  |  | 0.018251 | 0.018251 |  |  | 0 | 0 | 0.00015409 | 0.00015409 |  |  | 0.00015409 | 0.00015409 |  |  | 0 | 0 | 78 | 63 | NO
2012-09-04 | 0.11262 | 0.11262 |  |  | 0.11262 | 0.11262 |  |  | 0 | 0 | 0.00038808 | 0.00038808 |  |  | 0.00038808 | 0.00038808 |  |  | 0 | 0 | 72 | 56 | NO
2012-09-05 | 0.11464 | 0.11464 |  |  | 0.11464 | 0.11464 |  |  | 0 | 0 | 0.0010786 | 0.0010786 |  |  | 0.0010786 | 0.0010786 |  |  | 0 | 0 | 147 | 120 | NO
2012-09-06 | 0.28723 | 0.28723 |  |  | 0.28723 | 0.28723 |  |  | 0 | 0 | 0.0010615 | 0.0010615 |  |  | 0.0010615 | 0.0010615 |  |  | 0 | 0 | 104 | 82 | NO
2012-09-07 | 0.14591 | 0.14591 |  |  | 0.14591 | 0.14591 |  |  | 0 | 0 | 0.0018833 | 0.0018833 |  |  | 0.0018833 | 0.0018833 |  |  | 0 | 0 | 106 | 92 | NO
2012-09-08 | 0.16125 | 0.16125 |  |  | 0.16125 | 0.16125 |  |  | 0 | 0 | 0.00053076 | 0.00053076 |  |  | 0.00053076 | 0.00053076 |  |  | 0 | 0 | 23 | 23 | NO
2012-09-09 | 0.60195 | 0.60195 |  |  | 0.59154 | 0.59154 |  |  | 0.01041 | 0.01041 | 0.014068 | 0.014068 |  |  | 0.013794 | 0.013794 |  |  | 0.00027394 | 0.00027394 | 123 | 90 | NO
2012-09-10 | 0.16799 | 0.16799 |  |  | 0.16799 | 0.16799 |  |  | 0 | 0 | 0.00099303 | 0.00099303 |  |  | 0.00099303 | 0.00099303 |  |  | 0 | 0 | 77 | 56 | NO
2012-09-11 | 0.1004 | 0.1004 |  |  | 0.098618 | 0.098618 |  |  | 0.0017806 | 0.0017806 | 0.00034813 | 0.00034813 |  |  | 0.00034242 | 0.00034242 |  |  | 5.7071e-06 | 5.7071e-06 | 61 | 56 | NO
2012-09-12 | 0.28099 | 0.28099 |  |  | 0.28099 | 0.28099 |  |  | 0 | 0 | 0.0015124 | 0.0015124 |  |  | 0.0015124 | 0.0015124 |  |  | 0 | 0 | 62 | 55 | NO
2012-09-13 | 0.47426 | 0.47426 |  |  | 0.45847 | 0.45847 |  |  | 0.015786 | 0.015786 | 0.0020203 | 0.0020203 |  |  | 0.0019746 | 0.0019746 |  |  | 4.5657e-05 | 4.5657e-05 | 80 | 67 | NO
2012-09-14 | 0.22525 | 0.22525 |  |  | 0.22525 | 0.22525 |  |  | 0 | 0 | 0.0011015 | 0.0011015 |  |  | 0.0011015 | 0.0011015 |  |  | 0 | 0 | 70 | 61 | NO
2012-09-15 | 0.049309 | 0.049309 |  |  | 0.049309 | 0.049309 |  |  | 0 | 0 | 0.00026253 | 0.00026253 |  |  | 0.00026253 | 0.00026253 |  |  | 0 | 0 | 39 | 36 | NO
2012-09-16 | 0.17142 | 0.17142 |  |  | 0.17142 | 0.17142 |  |  | 0 | 0 | 0.0025339 | 0.0025339 |  |  | 0.0025339 | 0.0025339 |  |  | 0 | 0 | 38 | 30 | NO
2012-09-17 | 0.28093 | 0.28093 |  |  | 0.28093 | 0.28093 |  |  | 0 | 0 | 0.0064832 | 0.0064832 |  |  | 0.0064832 | 0.0064832 |  |  | 0 | 0 | 108 | 80 | NO
2012-09-18 | 0.057767 | 0.057767 |  |  | 0.034482 | 0.034482 |  |  | 0.023285 | 0.023285 | 0.00029677 | 0.00029677 |  |  | 0.00023399 | 0.00023399 |  |  | 6.2778e-05 | 6.2778e-05 | 51 | 46 | NO
2012-09-19 | 0.019724 | 0.019724 |  |  | 0.016025 | 0.016025 |  |  | 0.0036982 | 0.0036982 | 0.00025111 | 0.00025111 |  |  | 0.00022258 | 0.00022258 |  |  | 2.8535e-05 | 2.8535e-05 | 54 | 43 | NO
2012-09-20 | 0.31034 | 0.31034 |  |  | 0.3024 | 0.3024 |  |  | 0.0079443 | 0.0079443 | 0.0061465 | 0.0061465 |  |  | 0.0061294 | 0.0061294 |  |  | 1.7121e-05 | 1.7121e-05 | 70 | 65 | NO
2012-09-21 | 0.11023 | 0.11023 |  |  | 0.11012 | 0.11012 |  |  | 0.00010273 | 0.00010273 | 0.00049652 | 0.00049652 |  |  | 0.00047369 | 0.00047369 |  |  | 2.2828e-05 | 2.2828e-05 | 59 | 48 | NO
2012-09-22 | 0.0080812 | 0.0080812 |  |  | 0.0065746 | 0.0065746 |  |  | 0.0015067 | 0.0015067 | 0.00011985 | 0.00011985 |  |  | 0.00010843 | 0.00010843 |  |  | 1.1414e-05 | 1.1414e-05 | 26 | 25 | NO
2012-09-23 | 0.01445 | 0.01445 |  |  | 0.01445 | 0.01445 |  |  | 0 | 0 | 0.00019975 | 0.00019975 |  |  | 0.00019975 | 0.00019975 |  |  | 0 | 0 | 37 | 27 | NO
2012-09-24 | 0.1684 | 0.1684 |  |  | 0.1684 | 0.1684 |  |  | 0 | 0 | 0.00043945 | 0.00043945 |  |  | 0.00043945 | 0.00043945 |  |  | 0 | 0 | 65 | 54 | NO
2012-09-25 | 0.14221 | 0.14221 |  |  | 0.1231 | 0.1231 |  |  | 0.019107 | 0.019107 | 0.00082753 | 0.00082753 |  |  | 0.00077046 | 0.00077046 |  |  | 5.7071e-05 | 5.7071e-05 | 88 | 76 | NO
2012-09-26 | 0.44597 | 0.44597 |  |  | 0.41043 | 0.41043 |  |  | 0.035544 | 0.035544 | 0.0023285 | 0.0023285 |  |  | 0.0022258 | 0.0022258 |  |  | 0.00010273 | 0.00010273 | 79 | 56 | NO
2012-09-27 | 0.25182 | 0.25182 |  |  | 0.25182 | 0.25182 |  |  | 0 | 0 | 0.0013868 | 0.0013868 |  |  | 0.0013868 | 0.0013868 |  |  | 0 | 0 | 57 | 41 | NO
2012-09-28 | 0.064581 | 0.064581 |  |  | 0.064581 | 0.064581 |  |  | 0 | 0 | 0.0026595 | 0.0026595 |  |  | 0.0026595 | 0.0026595 |  |  | 0 | 0 | 121 | 108 | NO
2012-09-29 | 0.00452 | 0.00452 |  |  | 0.0031503 | 0.0031503 |  |  | 0.0013697 | 0.0013697 | 0.00011414 | 0.00011414 |  |  | 0.00010273 | 0.00010273 |  |  | 1.1414e-05 | 1.1414e-05 | 50 | 48 | NO
2012-09-30 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 28 | 24 | NO
2012-10-01 | 0.04609 | 0.04609 |  |  | 0.04609 | 0.04609 |  |  | 0 | 0 | 0.00033101 | 0.00033101 |  |  | 0.00033101 | 0.00033101 |  |  | 0 | 0 | 36 | 34 | NO
2012-10-02 | 0.0059239 | 0.0059239 |  |  | 0.0059239 | 0.0059239 |  |  | 0 | 0 | 0.00014268 | 0.00014268 |  |  | 0.00014268 | 0.00014268 |  |  | 0 | 0 | 81 | 68 | NO
2012-10-03 | 0.032154 | 0.032154 |  |  | 0.032154 | 0.032154 |  |  | 0 | 0 | 0.00025111 | 0.00025111 |  |  | 0.00025111 | 0.00025111 |  |  | 0 | 0 | 73 | 54 | NO
2012-10-04 | 0.024894 | 0.024894 |  |  | 0.023935 | 0.023935 |  |  | 0.00095879 | 0.00095879 | 0.00035384 | 0.00035384 |  |  | 0.00034242 | 0.00034242 |  |  | 1.1414e-05 | 1.1414e-05 | 62 | 50 | NO
2012-10-05 | 0.02688 | 0.02688 |  |  | 0.02688 | 0.02688 |  |  | 0 | 0 | 0.0003196 | 0.0003196 |  |  | 0.0003196 | 0.0003196 |  |  | 0 | 0 | 87 | 74 | NO
2012-10-06 | 0.0095879 | 0.0095879 |  |  | 0.0095879 | 0.0095879 |  |  | 0 | 0 | 0.00022828 | 0.00022828 |  |  | 0.00022828 | 0.00022828 |  |  | 0 | 0 | 33 | 31 | NO
2012-10-07 | 0.0040064 | 0.0040064 |  |  | 0.0040064 | 0.0040064 |  |  | 0 | 0 | 3.4242e-05 | 3.4242e-05 |  |  | 3.4242e-05 | 3.4242e-05 |  |  | 0 | 0 | 28 | 21 | NO
2012-10-08 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 27 | 25 | NO
2012-10-09 | 0.063486 | 0.063486 |  |  | 0.063486 | 0.063486 |  |  | 0 | 0 | 0.00049652 | 0.00049652 |  |  | 0.00049652 | 0.00049652 |  |  | 0 | 0 | 61 | 51 | NO
2012-10-10 | 0.089441 | 0.089441 |  |  | 0.089441 | 0.089441 |  |  | 0 | 0 | 0.00086748 | 0.00086748 |  |  | 0.00086748 | 0.00086748 |  |  | 0 | 0 | 70 | 58 | NO
2012-10-11 | 0.3263 | 0.3263 |  |  | 0.3263 | 0.3263 |  |  | 0 | 0 | 0.0089487 | 0.0089487 |  |  | 0.0089487 | 0.0089487 |  |  | 0 | 0 | 113 | 94 | NO
2012-10-12 | 0.038626 | 0.038626 |  |  | 0.038626 | 0.038626 |  |  | 0 | 0 | 0.00047939 | 0.00047939 |  |  | 0.00047939 | 0.00047939 |  |  | 0 | 0 | 88 | 81 | NO
2012-10-13 | 0.28229 | 0.28229 |  |  | 0.28229 | 0.28229 |  |  | 0 | 0 | 0.00092455 | 0.00092455 |  |  | 0.00092455 | 0.00092455 |  |  | 0 | 0 | 38 | 34 | NO
2012-10-14 | 0.022429 | 0.022429 |  |  | 0.022429 | 0.022429 |  |  | 0 | 0 | 0.0003253 | 0.0003253 |  |  | 0.0003253 | 0.0003253 |  |  | 0 | 0 | 18 | 13 | NO
2012-10-15 | 0.22193 | 0.22193 |  |  | 0.22193 | 0.22193 |  |  | 0 | 0 | 0.0059182 | 0.0059182 |  |  | 0.0059182 | 0.0059182 |  |  | 0 | 0 | 96 | 67 | NO
2012-10-16 | 1.1365 | 1.1365 |  |  | 1.0831 | 1.0831 |  |  | 0.053418 | 0.053418 | 0.016579 | 0.016579 |  |  | 0.016288 | 0.016288 |  |  | 0.00029106 | 0.00029106 | 289 | 230 | NO
2012-10-17 | 0.38759 | 0.38759 |  |  | 0.37776 | 0.37776 |  |  | 0.0098276 | 0.0098276 | 0.0031731 | 0.0031731 |  |  | 0.0031275 | 0.0031275 |  |  | 4.5657e-05 | 4.5657e-05 | 128 | 111 | NO
2012-10-18 | 0.12896 | 0.12896 |  |  | 0.12896 | 0.12896 |  |  | 0 | 0 | 0.0010444 | 0.0010444 |  |  | 0.0010444 | 0.0010444 |  |  | 0 | 0 | 79 | 70 | NO
2012-10-19 | 0.90842 | 0.90842 |  |  | 0.90842 | 0.90842 |  |  | 0 | 0 | 0.020488 | 0.020488 |  |  | 0.020488 | 0.020488 |  |  | 0 | 0 | 127 | 83 | NO
2012-10-20 | 0.042666 | 0.042666 |  |  | 0.033626 | 0.033626 |  |  | 0.00904 | 0.00904 | 0.00025682 | 0.00025682 |  |  | 0.00020545 | 0.00020545 |  |  | 5.1364e-05 | 5.1364e-05 | 45 | 36 | NO
2012-10-21 | 0.081976 | 0.081976 |  |  | 0.081976 | 0.081976 |  |  | 0 | 0 | 0.0011871 | 0.0011871 |  |  | 0.0011871 | 0.0011871 |  |  | 0 | 0 | 47 | 39 | NO
2012-10-22 | 0.070266 | 0.070266 |  |  | 0.032736 | 0.032736 |  |  | 0.03753 | 0.03753 | 0.00034242 | 0.00034242 |  |  | 0.00019975 | 0.00019975 |  |  | 0.00014268 | 0.00014268 | 97 | 80 | NO
2012-10-23 | 0.18782 | 0.18782 |  |  | 0.18782 | 0.18782 |  |  | 0 | 0 | 0.0012327 | 0.0012327 |  |  | 0.0012327 | 0.0012327 |  |  | 0 | 0 | 57 | 45 | NO
2012-10-24 | 0.37742 | 0.37742 |  |  | 0.37742 | 0.37742 |  |  | 0 | 0 | 0.0023342 | 0.0023342 |  |  | 0.0023342 | 0.0023342 |  |  | 0 | 0 | 71 | 62 | NO
2012-10-25 | 0.28695 | 0.28695 |  |  | 0.18488 | 0.18488 |  |  | 0.10208 | 0.10208 | 0.0021972 | 0.0021972 |  |  | 0.0014838 | 0.0014838 |  |  | 0.00071338 | 0.00071338 | 118 | 104 | NO
2012-10-26 | 0.16543 | 0.16543 |  |  | 0.15515 | 0.15515 |  |  | 0.010273 | 0.010273 | 0.00094738 | 0.00094738 |  |  | 0.00091884 | 0.00091884 |  |  | 2.8535e-05 | 2.8535e-05 | 81 | 71 | NO
2012-10-27 | 0.21908 | 0.21908 |  |  | 0.21809 | 0.21809 |  |  | 0.00099303 | 0.00099303 | 0.00053076 | 0.00053076 |  |  | 0.00052505 | 0.00052505 |  |  | 5.7071e-06 | 5.7071e-06 | 30 | 27 | NO
2012-10-28 | 0.0025682 | 0.0025682 |  |  | 0.0025682 | 0.0025682 |  |  | 0 | 0 | 0.00010273 | 0.00010273 |  |  | 0.00010273 | 0.00010273 |  |  | 0 | 0 | 21 | 21 | NO
2012-10-29 | 0.098481 | 0.098481 |  |  | 0.077388 | 0.077388 |  |  | 0.021093 | 0.021093 | 0.00078758 | 0.00078758 |  |  | 0.00065061 | 0.00065061 |  |  | 0.00013697 | 0.00013697 | 81 | 71 | NO
2012-10-30 | 0.8862 | 0.8862 |  |  | 0.8862 | 0.8862 |  |  | 0 | 0 | 0.010558 | 0.010558 |  |  | 0.010558 | 0.010558 |  |  | 0 | 0 | 170 | 120 | NO
2012-10-31 | 0.26565 | 0.26565 |  |  | 0.26565 | 0.26565 |  |  | 0 | 0 | 0.0016665 | 0.0016665 |  |  | 0.0016665 | 0.0016665 |  |  | 0 | 0 | 120 | 95 | NO
2012-11-01 | 0.497 | 0.497 |  |  | 0.48398 | 0.48398 |  |  | 0.013012 | 0.013012 | 0.0065118 | 0.0065118 |  |  | 0.0063177 | 0.0063177 |  |  | 0.00019404 | 0.00019404 | 120 | 95 | NO
2012-11-02 | 0.19227 | 0.19227 |  |  | 0.19227 | 0.19227 |  |  | 0 | 0 | 0.0008047 | 0.0008047 |  |  | 0.0008047 | 0.0008047 |  |  | 0 | 0 | 87 | 80 | NO
2012-11-03 | 0.13286 | 0.13286 |  |  | 0.13286 | 0.13286 |  |  | 0 | 0 | 0.00069626 | 0.00069626 |  |  | 0.00069626 | 0.00069626 |  |  | 0 | 0 | 37 | 33 | NO
2012-11-04 | 0.041468 | 0.041468 |  |  | 0.041468 | 0.041468 |  |  | 0 | 0 | 0.00046798 | 0.00046798 |  |  | 0.00046798 | 0.00046798 |  |  | 0 | 0 | 36 | 29 | NO
2012-11-05 | 0.10971 | 0.10971 |  |  | 0.081703 | 0.081703 |  |  | 0.02801 | 0.02801 | 0.00063919 | 0.00063919 |  |  | 0.00055929 | 0.00055929 |  |  | 7.9899e-05 | 7.9899e-05 | 80 | 74 | NO
2012-11-06 | 0.33465 | 0.33465 |  |  | 0.33465 | 0.33465 |  |  | 0 | 0 | 0.0022657 | 0.0022657 |  |  | 0.0022657 | 0.0022657 |  |  | 0 | 0 | 146 | 118 | NO
2012-11-07 | 0.13539 | 0.13539 |  |  | 0.13539 | 0.13539 |  |  | 0 | 0 | 0.0017635 | 0.0017635 |  |  | 0.0017635 | 0.0017635 |  |  | 0 | 0 | 265 | 209 | NO
2012-11-08 | 0.061636 | 0.061636 |  |  | 0.061636 | 0.061636 |  |  | 0 | 0 | 0.00093596 | 0.00093596 |  |  | 0.00093596 | 0.00093596 |  |  | 0 | 0 | 108 | 93 | NO
2012-11-09 | 0.26202 | 0.26202 |  |  | 0.26202 | 0.26202 |  |  | 0 | 0 | 0.0014496 | 0.0014496 |  |  | 0.0014496 | 0.0014496 |  |  | 0 | 0 | 102 | 86 | NO
2012-11-10 | 0.02373 | 0.02373 |  |  | 0.02373 | 0.02373 |  |  | 0 | 0 | 0.00011985 | 0.00011985 |  |  | 0.00011985 | 0.00011985 |  |  | 0 | 0 | 36 | 34 | NO
2012-11-11 | 0.01267 | 0.01267 |  |  | 0.01267 | 0.01267 |  |  | 0 | 0 | 5.7071e-05 | 5.7071e-05 |  |  | 5.7071e-05 | 5.7071e-05 |  |  | 0 | 0 | 31 | 26 | NO
2012-11-12 | 0.004383 | 0.004383 |  |  | 0.004383 | 0.004383 |  |  | 0 | 0 | 3.4242e-05 | 3.4242e-05 |  |  | 3.4242e-05 | 3.4242e-05 |  |  | 0 | 0 | 99 | 78 | NO
2012-11-13 | 0.16508 | 0.16508 |  |  | 0.16508 | 0.16508 |  |  | 0 | 0 | 0.00051934 | 0.00051934 |  |  | 0.00051934 | 0.00051934 |  |  | 0 | 0 | 102 | 87 | NO
2012-11-14 | 0.20867 | 0.20867 |  |  | 0.20867 | 0.20867 |  |  | 0 | 0 | 0.0012156 | 0.0012156 |  |  | 0.0012156 | 0.0012156 |  |  | 0 | 0 | 207 | 136 | NO
2012-11-15 | 0.083038 | 0.083038 |  |  | 0.083038 | 0.083038 |  |  | 0 | 0 | 0.00068485 | 0.00068485 |  |  | 0.00068485 | 0.00068485 |  |  | 0 | 0 | 83 | 80 | NO
2012-11-16 | 0.15471 | 0.15471 |  |  | 0.14074 | 0.14074 |  |  | 0.013971 | 0.013971 | 0.0013297 | 0.0013297 |  |  | 0.0011871 | 0.0011871 |  |  | 0.00014268 | 0.00014268 | 88 | 75 | NO
2012-11-17 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 28 | 26 | NO
2012-11-18 | 0.029585 | 0.029585 |  |  | 0.029585 | 0.029585 |  |  | 0 | 0 | 0.00037096 | 0.00037096 |  |  | 0.00037096 | 0.00037096 |  |  | 0 | 0 | 31 | 29 | NO
2012-11-19 | 0.1017 | 0.1017 |  |  | 0.1017 | 0.1017 |  |  | 0 | 0 | 0.00057641 | 0.00057641 |  |  | 0.00057641 | 0.00057641 |  |  | 0 | 0 | 117 | 96 | NO
2012-11-20 | 0.14587 | 0.14587 |  |  | 0.14587 | 0.14587 |  |  | 0 | 0 | 0.00061636 | 0.00061636 |  |  | 0.00061636 | 0.00061636 |  |  | 0 | 0 | 84 | 79 | NO
2012-11-21 | 0.26086 | 0.26086 |  |  | 0.22425 | 0.22425 |  |  | 0.036605 | 0.036605 | 0.0014781 | 0.0014781 |  |  | 0.0013526 | 0.0013526 |  |  | 0.00012556 | 0.00012556 | 88 | 79 | NO
2012-11-22 | 0.34136 | 0.34136 |  |  | 0.33188 | 0.33188 |  |  | 0.0094852 | 0.0094852 | 0.0012213 | 0.0012213 |  |  | 0.0011928 | 0.0011928 |  |  | 2.8535e-05 | 2.8535e-05 | 79 | 70 | NO
2012-11-23 | 0.24405 | 0.24405 |  |  | 0.15358 | 0.15358 |  |  | 0.090469 | 0.090469 | 0.0014953 | 0.0014953 |  |  | 0.0012213 | 0.0012213 |  |  | 0.00027394 | 0.00027394 | 104 | 92 | NO
2012-11-24 | 0.0011642 | 0.0011642 |  |  | 0.0011642 | 0.0011642 |  |  | 0 | 0 | 1.7121e-05 | 1.7121e-05 |  |  | 1.7121e-05 | 1.7121e-05 |  |  | 0 | 0 | 22 | 20 | NO
2012-11-25 | 1.4304 | 1.4304 |  |  | 1.4304 | 1.4304 |  |  | 0 | 0 | 0.026487 | 0.026487 |  |  | 0.026487 | 0.026487 |  |  | 0 | 0 | 296 | 208 | NO
2012-11-26 | 0.074512 | 0.074512 |  |  | 0.074512 | 0.074512 |  |  | 0 | 0 | 0.00092455 | 0.00092455 |  |  | 0.00092455 | 0.00092455 |  |  | 0 | 0 | 94 | 88 | NO
2012-11-27 | 0.10831 | 0.10831 |  |  | 0.10831 | 0.10831 |  |  | 0 | 0 | 0.0091427 | 0.0091427 |  |  | 0.0091427 | 0.0091427 |  |  | 0 | 0 | 112 | 94 | NO
2012-11-28 | 0.39485 | 0.39485 |  |  | 0.39417 | 0.39417 |  |  | 0.00068485 | 0.00068485 | 0.01663 | 0.01663 |  |  | 0.016568 | 0.016568 |  |  | 6.2778e-05 | 6.2778e-05 | 244 | 203 | NO
2012-11-29 | 0.44515 | 0.44515 |  |  | 0.44515 | 0.44515 |  |  | 0 | 0 | 0.0090857 | 0.0090857 |  |  | 0.0090857 | 0.0090857 |  |  | 0 | 0 | 192 | 133 | NO
2012-11-30 | 0.21946 | 0.21946 |  |  | 0.21946 | 0.21946 |  |  | 0 | 0 | 0.014039 | 0.014039 |  |  | 0.014039 | 0.014039 |  |  | 0 | 0 | 110 | 86 | NO
2012-12-01 | 0.2887 | 0.2887 |  |  | 0.25011 | 0.25011 |  |  | 0.038591 | 0.038591 | 0.0013183 | 0.0013183 |  |  | 0.0010672 | 0.0010672 |  |  | 0.00025111 | 0.00025111 | 46 | 41 | NO
2012-12-02 | 0.064684 | 0.064684 |  |  | 0.064684 | 0.064684 |  |  | 0 | 0 | 0.00045086 | 0.00045086 |  |  | 0.00045086 | 0.00045086 |  |  | 0 | 0 | 22 | 20 | NO
2012-12-03 | 0.11057 | 0.11057 |  |  | 0.11057 | 0.11057 |  |  | 0 | 0 | 0.00059924 | 0.00059924 |  |  | 0.00059924 | 0.00059924 |  |  | 0 | 0 | 77 | 71 | NO
2012-12-04 | 0.34482 | 0.34482 |  |  | 0.18816 | 0.18816 |  |  | 0.15666 | 0.15666 | 0.0023114 | 0.0023114 |  |  | 0.001461 | 0.001461 |  |  | 0.00085035 | 0.00085035 | 173 | 121 | NO
2012-12-05 | 0.70656 | 0.70656 |  |  | 0.6681 | 0.6681 |  |  | 0.038454 | 0.038454 | 0.018103 | 0.018103 |  |  | 0.017287 | 0.017287 |  |  | 0.00081611 | 0.00081611 | 253 | 171 | NO
2012-12-06 | 0.30664 | 0.30664 |  |  | 0.30664 | 0.30664 |  |  | 0 | 0 | 0.0016893 | 0.0016893 |  |  | 0.0016893 | 0.0016893 |  |  | 0 | 0 | 82 | 65 | NO
2012-12-07 | 0.040029 | 0.040029 |  |  | 0.040029 | 0.040029 |  |  | 0 | 0 | 0.00041662 | 0.00041662 |  |  | 0.00041662 | 0.00041662 |  |  | 0 | 0 | 67 | 51 | NO
2012-12-08 | 0.046227 | 0.046227 |  |  | 0.046227 | 0.046227 |  |  | 0 | 0 | 0.00045086 | 0.00045086 |  |  | 0.00045086 | 0.00045086 |  |  | 0 | 0 | 35 | 31 | NO
2012-12-09 | 0.038728 | 0.038728 |  |  | 0.038728 | 0.038728 |  |  | 0 | 0 | 0.00045086 | 0.00045086 |  |  | 0.00045086 | 0.00045086 |  |  | 0 | 0 | 37 | 33 | NO
2012-12-10 | 0.088585 | 0.088585 |  |  | 0.074683 | 0.074683 |  |  | 0.013902 | 0.013902 | 0.0004851 | 0.0004851 |  |  | 0.00042803 | 0.00042803 |  |  | 5.7071e-05 | 5.7071e-05 | 90 | 77 | NO
2012-12-11 | 0.39619 | 0.39619 |  |  | 0.063143 | 0.063143 |  |  | 0.33304 | 0.33304 | 0.0014838 | 0.0014838 |  |  | 0.0006449 | 0.0006449 |  |  | 0.00083894 | 0.00083894 | 85 | 78 | NO
2012-12-12 | 0.1794 | 0.1794 |  |  | 0.11951 | 0.11951 |  |  | 0.05989 | 0.05989 | 0.00084465 | 0.00084465 |  |  | 0.00063349 | 0.00063349 |  |  | 0.00021116 | 0.00021116 | 101 | 93 | NO
2012-12-13 | 0.46474 | 0.46474 |  |  | 0.46419 | 0.46419 |  |  | 0.00054788 | 0.00054788 | 0.0095308 | 0.0095308 |  |  | 0.0095194 | 0.0095194 |  |  | 1.1414e-05 | 1.1414e-05 | 157 | 94 | NO
2012-12-14 | 0.029962 | 0.029962 |  |  | 0.029962 | 0.029962 |  |  | 0 | 0 | 0.010792 | 0.010792 |  |  | 0.010792 | 0.010792 |  |  | 0 | 0 | 111 | 97 | NO
2012-12-15 | 0.020511 | 0.020511 |  |  | 0.020511 | 0.020511 |  |  | 0 | 0 | 0.00014268 | 0.00014268 |  |  | 0.00014268 | 0.00014268 |  |  | 0 | 0 | 72 | 59 | NO
2012-12-16 | 0.0088688 | 0.0088688 |  |  | 0.0088688 | 0.0088688 |  |  | 0 | 0 | 9.702e-05 | 9.702e-05 |  |  | 9.702e-05 | 9.702e-05 |  |  | 0 | 0 | 30 | 22 | NO
2012-12-17 | 0.068416 | 0.068416 |  |  | 0.068416 | 0.068416 |  |  | 0 | 0 | 0.00059924 | 0.00059924 |  |  | 0.00059924 | 0.00059924 |  |  | 0 | 0 | 86 | 71 | NO
2012-12-18 | 0.054411 | 0.054411 |  |  | 0.052117 | 0.052117 |  |  | 0.0022942 | 0.0022942 | 0.00082182 | 0.00082182 |  |  | 0.00081041 | 0.00081041 |  |  | 1.1414e-05 | 1.1414e-05 | 76 | 66 | NO
2012-12-19 | 0.035064 | 0.035064 |  |  | 0.035064 | 0.035064 |  |  | 0 | 0 | 0.00033101 | 0.00033101 |  |  | 0.00033101 | 0.00033101 |  |  | 0 | 0 | 51 | 47 | NO
2012-12-20 | 0.014279 | 0.014279 |  |  | 0.014279 | 0.014279 |  |  | 0 | 0 | 0.00016551 | 0.00016551 |  |  | 0.00016551 | 0.00016551 |  |  | 0 | 0 | 90 | 79 | NO
2012-12-21 | 0.030133 | 0.030133 |  |  | 0.030133 | 0.030133 |  |  | 0 | 0 | 0.00045657 | 0.00045657 |  |  | 0.00045657 | 0.00045657 |  |  | 0 | 0 | 94 | 78 | NO
2012-12-22 | 0.0022258 | 0.0022258 |  |  | 0.0022258 | 0.0022258 |  |  | 0 | 0 | 5.7071e-05 | 5.7071e-05 |  |  | 5.7071e-05 | 5.7071e-05 |  |  | 0 | 0 | 29 | 27 | NO
2012-12-23 | 0.032325 | 0.032325 |  |  | 0.030442 | 0.030442 |  |  | 0.0018833 | 0.0018833 | 0.00073621 | 0.00073621 |  |  | 0.00071909 | 0.00071909 |  |  | 1.7121e-05 | 1.7121e-05 | 81 | 58 | NO
2012-12-24 | 0.22805 | 0.22805 |  |  | 0.21703 | 0.21703 |  |  | 0.011026 | 0.011026 | 0.0042232 | 0.0042232 |  |  | 0.0042118 | 0.0042118 |  |  | 1.1414e-05 | 1.1414e-05 | 182 | 144 | NO
2012-12-25 | 0.0044858 | 0.0044858 |  |  | 0.0044858 | 0.0044858 |  |  | 0 | 0 | 2.8535e-05 | 2.8535e-05 |  |  | 2.8535e-05 | 2.8535e-05 |  |  | 0 | 0 | 20 | 18 | NO
2012-12-26 | 0.0043488 | 0.0043488 |  |  | 0.0043488 | 0.0043488 |  |  | 0 | 0 | 0.00013126 | 0.00013126 |  |  | 0.00013126 | 0.00013126 |  |  | 0 | 0 | 25 | 21 | NO
2012-12-27 | 0.091051 | 0.091051 |  |  | 0.091051 | 0.091051 |  |  | 0 | 0 | 0.00069056 | 0.00069056 |  |  | 0.00069056 | 0.00069056 |  |  | 0 | 0 | 72 | 62 | NO
2012-12-28 | 0.014759 | 0.014759 |  |  | 0.013731 | 0.013731 |  |  | 0.0010273 | 0.0010273 | 0.00026823 | 0.00026823 |  |  | 0.00026253 | 0.00026253 |  |  | 5.7071e-06 | 5.7071e-06 | 46 | 44 | NO
2012-12-29 | 0.0113 | 0.0113 |  |  | 0.0113 | 0.0113 |  |  | 0 | 0 | 0.00018263 | 0.00018263 |  |  | 0.00018263 | 0.00018263 |  |  | 0 | 0 | 35 | 27 | NO
2012-12-30 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 21 | 20 | NO
2012-12-31 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 241 | 157 | NO
2013-01-01 | 0.0019861 | 0.0019861 |  |  | 0.0019861 | 0.0019861 |  |  | 0 | 0 | 0.00019975 | 0.00019975 |  |  | 0.00019975 | 0.00019975 |  |  | 0 | 0 | 35 | 29 | NO
2013-01-02 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 59 | 56 | NO
2013-01-03 | 0.024278 | 0.024278 |  |  | 0.024278 | 0.024278 |  |  | 0 | 0 | 0.0004851 | 0.0004851 |  |  | 0.0004851 | 0.0004851 |  |  | 0 | 0 | 111 | 98 | NO
2013-01-04 | 0.2198 | 0.2198 |  |  | 0.2198 | 0.2198 |  |  | 0 | 0 | 0.0050964 | 0.0050964 |  |  | 0.0050964 | 0.0050964 |  |  | 0 | 0 | 190 | 170 | NO
2013-01-05 | 0.041879 | 0.041879 |  |  | 0.041879 | 0.041879 |  |  | 0 | 0 | 0.00074192 | 0.00074192 |  |  | 0.00074192 | 0.00074192 |  |  | 0 | 0 | 78 | 62 | NO
2013-01-06 | 0.31024 | 0.31024 |  |  | 0.31024 | 0.31024 |  |  | 0 | 0 | 0.010912 | 0.010912 |  |  | 0.010912 | 0.010912 |  |  | 0 | 0 | 88 | 70 | NO
2013-01-07 | 0.19618 | 0.19618 |  |  | 0.19618 | 0.19618 |  |  | 0 | 0 | 0.0072651 | 0.0072651 |  |  | 0.0072651 | 0.0072651 |  |  | 0 | 0 | 134 | 95 | NO
2013-01-08 | 3.1452 |  |  |  | 3.1156 |  |  |  | 0.029585 |  | 0.062829 |  |  |  | 0.062647 |  |  |  | 0.00018263 |  |  |  | YES
2013-01-09 | 0.14313 | 0.14313 |  |  | 0.14313 | 0.14313 |  |  | 0 | 0 | 0.0014838 | 0.0014838 |  |  | 0.0014838 | 0.0014838 |  |  | 0 | 0 | 179 | 135 | NO
2013-01-10 | 0.083894 | 0.083894 |  |  | 0.082867 | 0.082867 |  |  | 0.0010273 | 0.0010273 | 0.0087547 | 0.0087547 |  |  | 0.008749 | 0.008749 |  |  | 5.7071e-06 | 5.7071e-06 | 130 | 105 | NO
2013-01-11 | 0.044755 | 0.044755 |  |  | 0.041536 | 0.041536 |  |  | 0.0032188 | 0.0032188 | 0.00077616 | 0.00077616 |  |  | 0.00076475 | 0.00076475 |  |  | 1.1414e-05 | 1.1414e-05 | 111 | 85 | NO
2013-01-12 | 0.15169 | 0.15169 |  |  | 0.14704 | 0.14704 |  |  | 0.004657 | 0.004657 | 0.0060324 | 0.0060324 |  |  | 0.0059696 | 0.0059696 |  |  | 6.2778e-05 | 6.2778e-05 | 100 | 70 | NO
2013-01-13 | 0.015889 | 0.015889 |  |  | 0.015889 | 0.015889 |  |  | 0 | 0 | 0.00034813 | 0.00034813 |  |  | 0.00034813 | 0.00034813 |  |  | 0 | 0 | 47 | 34 | NO
2013-01-14 | 0.035989 | 0.035989 |  |  | 0.035989 | 0.035989 |  |  | 0 | 0 | 0.00046798 | 0.00046798 |  |  | 0.00046798 | 0.00046798 |  |  | 0 | 0 | 88 | 75 | NO
2013-01-15 | 0.072971 | 0.072971 |  |  | 0.072971 | 0.072971 |  |  | 0 | 0 | 0.00034242 | 0.00034242 |  |  | 0.00034242 | 0.00034242 |  |  | 0 | 0 | 73 | 66 | NO
2013-01-16 | 0.2072 | 0.2072 |  |  | 0.2072 | 0.2072 |  |  | 0 | 0 | 0.00083894 | 0.00083894 |  |  | 0.00083894 | 0.00083894 |  |  | 0 | 0 | 104 | 94 | NO
2013-01-17 | 0.96704 | 0.96704 |  |  | 0.96704 | 0.96704 |  |  | 0 | 0 | 0.0025111 | 0.0025111 |  |  | 0.0025111 | 0.0025111 |  |  | 0 | 0 | 91 | 79 | NO
2013-01-18 | 0.69622 | 0.69622 |  |  | 0.69622 | 0.69622 |  |  | 0 | 0 | 0.00791 | 0.00791 |  |  | 0.00791 | 0.00791 |  |  | 0 | 0 | 209 | 169 | NO
2013-01-19 | 0.18186 | 0.18186 |  |  | 0.18186 | 0.18186 |  |  | 0 | 0 | 0.00049081 | 0.00049081 |  |  | 0.00049081 | 0.00049081 |  |  | 0 | 0 | 40 | 36 | NO
2013-01-20 | 0.19693 | 0.19693 |  |  | 0.19693 | 0.19693 |  |  | 0 | 0 | 0.0008846 | 0.0008846 |  |  | 0.0008846 | 0.0008846 |  |  | 0 | 0 | 28 | 23 | NO
2013-01-21 | 0.0028079 | 0.0028079 |  |  | 0.0022258 | 0.0022258 |  |  | 0.00058212 | 0.00058212 | 7.9899e-05 | 7.9899e-05 |  |  | 7.4192e-05 | 7.4192e-05 |  |  | 5.7071e-06 | 5.7071e-06 | 95 | 80 | NO
2013-01-22 | 0.071396 | 0.071396 |  |  | 0.071396 | 0.071396 |  |  | 0 | 0 | 0.0003196 | 0.0003196 |  |  | 0.0003196 | 0.0003196 |  |  | 0 | 0 | 81 | 73 | NO
2013-01-23 | 0.53045 | 0.53045 |  |  | 0.49025 | 0.49025 |  |  | 0.040201 | 0.040201 | 0.010016 | 0.010016 |  |  | 0.0098618 | 0.0098618 |  |  | 0.00015409 | 0.00015409 | 153 | 139 | NO
2013-01-24 | 0.22672 | 0.22672 |  |  | 0.22672 | 0.22672 |  |  | 0 | 0 | 0.0047711 | 0.0047711 |  |  | 0.0047711 | 0.0047711 |  |  | 0 | 0 | 63 | 57 | NO
2013-01-25 | 0.25822 | 0.25822 |  |  | 0.25822 | 0.25822 |  |  | 0 | 0 | 0.0010501 | 0.0010501 |  |  | 0.0010501 | 0.0010501 |  |  | 0 | 0 | 84 | 69 | NO
2013-01-26 | 15.9356 |  |  |  | 15.9356 |  |  |  | 0 |  | 0.078347 |  |  |  | 0.078347 |  |  |  | 0 |  |  |  | YES
2013-01-27 | 1.8338 | 1.8338 |  |  | 1.8338 | 1.8338 |  |  | 0 | 0 | 0.0060038 | 0.0060038 |  |  | 0.0060038 | 0.0060038 |  |  | 0 | 0 | 708 | 422 | NO
2013-01-28 | 0.10889 | 0.10889 |  |  | 0.10714 | 0.10714 |  |  | 0.0017464 | 0.0017464 | 0.0017007 | 0.0017007 |  |  | 0.001695 | 0.001695 |  |  | 5.7071e-06 | 5.7071e-06 | 162 | 109 | NO
2013-01-29 | 0.11975 | 0.11975 |  |  | 0.11975 | 0.11975 |  |  | 0 | 0 | 0.00091884 | 0.00091884 |  |  | 0.00091884 | 0.00091884 |  |  | 0 | 0 | 182 | 141 | NO
2013-01-30 | 0.06756 | 0.06756 |  |  | 0.064821 | 0.064821 |  |  | 0.0027394 | 0.0027394 | 0.0003995 | 0.0003995 |  |  | 0.00039379 | 0.00039379 |  |  | 5.7071e-06 | 5.7071e-06 | 101 | 92 | NO
2013-01-31 | 0.6341 | 0.6341 |  |  | 0.6341 | 0.6341 |  |  | 0 | 0 | 0.0020374 | 0.0020374 |  |  | 0.0020374 | 0.0020374 |  |  | 0 | 0 | 167 | 141 | NO
2013-02-01 | 0.45221 | 0.45221 |  |  | 0.45221 | 0.45221 |  |  | 0 | 0 | 0.002163 | 0.002163 |  |  | 0.002163 | 0.002163 |  |  | 0 | 0 | 169 | 116 | NO
2013-02-02 | 0.13807 | 0.13807 |  |  | 0.13807 | 0.13807 |  |  | 0 | 0 | 0.00091884 | 0.00091884 |  |  | 0.00091884 | 0.00091884 |  |  | 0 | 0 | 82 | 71 | NO
2013-02-03 | 0.025716 | 0.025716 |  |  | 0.025716 | 0.025716 |  |  | 0 | 0 | 0.00045086 | 0.00045086 |  |  | 0.00045086 | 0.00045086 |  |  | 0 | 0 | 22 | 21 | NO
2013-02-04 | 0.076703 | 0.076703 |  |  | 0.076703 | 0.076703 |  |  | 0 | 0 | 0.00081611 | 0.00081611 |  |  | 0.00081611 | 0.00081611 |  |  | 0 | 0 | 125 | 97 | NO
2013-02-05 | 0.44693 | 0.44693 |  |  | 0.38143 | 0.38143 |  |  | 0.065506 | 0.065506 | 0.0016208 | 0.0016208 |  |  | 0.0013355 | 0.0013355 |  |  | 0.00028535 | 0.00028535 | 157 | 104 | NO
2013-02-06 | 0.36372 | 0.36372 |  |  | 0.36372 | 0.36372 |  |  | 0 | 0 | 0.0017407 | 0.0017407 |  |  | 0.0017407 | 0.0017407 |  |  | 0 | 0 | 110 | 92 | NO
2013-02-07 | 0.13279 | 0.13279 |  |  | 0.13279 | 0.13279 |  |  | 0 | 0 | 0.00077616 | 0.00077616 |  |  | 0.00077616 | 0.00077616 |  |  | 0 | 0 | 83 | 67 | NO
2013-02-08 | 1.757 | 1.757 |  |  | 1.7518 | 1.7518 |  |  | 0.0052049 | 0.0052049 | 0.017875 | 0.017875 |  |  | 0.017817 | 0.017817 |  |  | 5.7071e-05 | 5.7071e-05 | 306 | 213 | NO
2013-02-09 | 0.068314 | 0.068314 |  |  | 0.068314 | 0.068314 |  |  | 0 | 0 | 0.00047939 | 0.00047939 |  |  | 0.00047939 | 0.00047939 |  |  | 0 | 0 | 60 | 57 | NO
2013-02-10 | 0.042289 | 0.042289 |  |  | 0.042289 | 0.042289 |  |  | 0 | 0 | 0.00067344 | 0.00067344 |  |  | 0.00067344 | 0.00067344 |  |  | 0 | 0 | 55 | 44 | NO
2013-02-11 | 0.32613 | 0.32613 |  |  | 0.32613 | 0.32613 |  |  | 0 | 0 | 0.0011414 | 0.0011414 |  |  | 0.0011414 | 0.0011414 |  |  | 0 | 0 | 107 | 82 | NO
2013-02-12 | 0.81819 | 0.81819 |  |  | 0.81819 | 0.81819 |  |  | 0 | 0 | 0.0023285 | 0.0023285 |  |  | 0.0023285 | 0.0023285 |  |  | 0 | 0 | 151 | 128 | NO
2013-02-13 | 0.44234 | 0.44234 |  |  | 0.44234 | 0.44234 |  |  | 0 | 0 | 0.0069341 | 0.0069341 |  |  | 0.0069341 | 0.0069341 |  |  | 0 | 0 | 140 | 110 | NO
2013-02-14 | 0.34096 | 0.34096 |  |  | 0.34096 | 0.34096 |  |  | 0 | 0 | 0.012567 | 0.012567 |  |  | 0.012567 | 0.012567 |  |  | 0 | 0 | 118 | 93 | NO
2013-02-15 | 0.11701 | 0.11701 |  |  | 0.11701 | 0.11701 |  |  | 0 | 0 | 0.00075333 | 0.00075333 |  |  | 0.00075333 | 0.00075333 |  |  | 0 | 0 | 89 | 78 | NO
2013-02-16 | 0.023935 | 0.023935 |  |  | 0.023935 | 0.023935 |  |  | 0 | 0 | 0.00014838 | 0.00014838 |  |  | 0.00014838 | 0.00014838 |  |  | 0 | 0 | 42 | 39 | NO
2013-02-17 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 35 | 29 | NO
2013-02-18 | 0.077388 | 0.077388 |  |  | 0.077388 | 0.077388 |  |  | 0 | 0 | 0.0025454 | 0.0025454 |  |  | 0.0025454 | 0.0025454 |  |  | 0 | 0 | 145 | 108 | NO
2013-02-19 | 0.24473 | 0.24473 |  |  | 0.24473 | 0.24473 |  |  | 0 | 0 | 0.0010558 | 0.0010558 |  |  | 0.0010558 | 0.0010558 |  |  | 0 | 0 | 118 | 102 | NO
2013-02-20 | 0.089818 | 0.089818 |  |  | 0.089818 | 0.089818 |  |  | 0 | 0 | 0.00070197 | 0.00070197 |  |  | 0.00070197 | 0.00070197 |  |  | 0 | 0 | 107 | 93 | NO
2013-02-21 | 0.31209 | 0.31209 |  |  | 0.31209 | 0.31209 |  |  | 0 | 0 | 0.0023799 | 0.0023799 |  |  | 0.0023799 | 0.0023799 |  |  | 0 | 0 | 105 | 91 | NO
2013-02-22 | 0.16293 | 0.16293 |  |  | 0.16293 | 0.16293 |  |  | 0 | 0 | 0.0012784 | 0.0012784 |  |  | 0.0012784 | 0.0012784 |  |  | 0 | 0 | 125 | 103 | NO
2013-02-23 | 0.014793 | 0.014793 |  |  | 0.014793 | 0.014793 |  |  | 0 | 0 | 6.8485e-05 | 6.8485e-05 |  |  | 6.8485e-05 | 6.8485e-05 |  |  | 0 | 0 | 54 | 47 | NO
2013-02-24 | 0.0015067 | 0.0015067 |  |  | 0.0015067 | 0.0015067 |  |  | 0 | 0 | 5.7071e-06 | 5.7071e-06 |  |  | 5.7071e-06 | 5.7071e-06 |  |  | 0 | 0 | 68 | 54 | NO
2013-02-25 | 0.16204 | 0.16204 |  |  | 0.16204 | 0.16204 |  |  | 0 | 0 | 0.0010901 | 0.0010901 |  |  | 0.0010901 | 0.0010901 |  |  | 0 | 0 | 167 | 148 | NO
2013-02-26 | 0.050131 | 0.050131 |  |  | 0.039173 | 0.039173 |  |  | 0.010958 | 0.010958 | 0.00034813 | 0.00034813 |  |  | 0.0003253 | 0.0003253 |  |  | 2.2828e-05 | 2.2828e-05 | 112 | 96 | NO
2013-02-27 | 0.042735 | 0.042735 |  |  | 0.042735 | 0.042735 |  |  | 0 | 0 | 0.0003253 | 0.0003253 |  |  | 0.0003253 | 0.0003253 |  |  | 0 | 0 | 80 | 74 | NO
2013-02-28 | 0.022292 | 0.022292 |  |  | 0.022292 | 0.022292 |  |  | 0 | 0 | 0.00039379 | 0.00039379 |  |  | 0.00039379 | 0.00039379 |  |  | 0 | 0 | 80 | 74 | NO
2013-03-01 | 0.45382 | 0.45382 |  |  | 0.44847 | 0.44847 |  |  | 0.0053418 | 0.0053418 | 0.0024883 | 0.0024883 |  |  | 0.0023513 | 0.0023513 |  |  | 0.00013697 | 0.00013697 | 117 | 95 | NO
2013-03-02 | 0.015032 | 0.015032 |  |  | 0.015032 | 0.015032 |  |  | 0 | 0 | 0.0002454 | 0.0002454 |  |  | 0.0002454 | 0.0002454 |  |  | 0 | 0 | 57 | 49 | NO
2013-03-03 | 0.00092455 | 0.00092455 |  |  | 0.00092455 | 0.00092455 |  |  | 0 | 0 | 0.00022828 | 0.00022828 |  |  | 0.00022828 | 0.00022828 |  |  | 0 | 0 | 36 | 24 | NO
2013-03-04 | 0.049378 | 0.049378 |  |  | 0.049378 | 0.049378 |  |  | 0 | 0 | 0.00049652 | 0.00049652 |  |  | 0.00049652 | 0.00049652 |  |  | 0 | 0 | 128 | 101 | NO
2013-03-05 | 0.1192 | 0.1192 |  |  | 0.10574 | 0.10574 |  |  | 0.013457 | 0.013457 | 0.00081611 | 0.00081611 |  |  | 0.00059924 | 0.00059924 |  |  | 0.00021687 | 0.00021687 | 116 | 103 | NO
2013-03-06 | 0.2372 | 0.2372 |  |  | 0.22942 | 0.22942 |  |  | 0.007773 | 0.007773 | 0.0009645 | 0.0009645 |  |  | 0.00087318 | 0.00087318 |  |  | 9.1313e-05 | 9.1313e-05 | 106 | 79 | NO
2013-03-07 | 0.2813 | 0.2813 |  |  | 0.27668 | 0.27668 |  |  | 0.0046227 | 0.0046227 | 0.0012441 | 0.0012441 |  |  | 0.001227 | 0.001227 |  |  | 1.7121e-05 | 1.7121e-05 | 99 | 75 | NO
2013-03-08 | 0.11773 | 0.11773 |  |  | 0.11773 | 0.11773 |  |  | 0 | 0 | 0.00087889 | 0.00087889 |  |  | 0.00087889 | 0.00087889 |  |  | 0 | 0 | 107 | 87 | NO
2013-03-09 | 0.040577 | 0.040577 |  |  | 0.040577 | 0.040577 |  |  | 0 | 0 | 0.0003196 | 0.0003196 |  |  | 0.0003196 | 0.0003196 |  |  | 0 | 0 | 44 | 42 | NO
2013-03-10 | 0.31359 | 0.31359 |  |  | 0.31359 | 0.31359 |  |  | 0 | 0 | 0.0075048 | 0.0075048 |  |  | 0.0075048 | 0.0075048 |  |  | 0 | 0 | 60 | 51 | NO
2013-03-11 | 0.00030818 | 0.00030818 |  |  | 0.00030818 | 0.00030818 |  |  | 0 | 0 | 5.7071e-06 | 5.7071e-06 |  |  | 5.7071e-06 | 5.7071e-06 |  |  | 0 | 0 | 36 | 33 | NO
2013-03-12 | 0.18405 | 0.18405 |  |  | 0.18405 | 0.18405 |  |  | 0 | 0 | 0.0010273 | 0.0010273 |  |  | 0.0010273 | 0.0010273 |  |  | 0 | 0 | 116 | 81 | NO
2013-03-13 | 0.28798 | 0.28798 |  |  | 0.28798 | 0.28798 |  |  | 0 | 0 | 0.0013811 | 0.0013811 |  |  | 0.0013811 | 0.0013811 |  |  | 0 | 0 | 129 | 93 | NO
2013-03-14 | 0.20532 | 0.20532 |  |  | 0.20532 | 0.20532 |  |  | 0 | 0 | 0.0008846 | 0.0008846 |  |  | 0.0008846 | 0.0008846 |  |  | 0 | 0 | 99 | 86 | NO
2013-03-15 | 0.67317 | 0.67317 |  |  | 0.67259 | 0.67259 |  |  | 0.00058212 | 0.00058212 | 0.0022372 | 0.0022372 |  |  | 0.0022315 | 0.0022315 |  |  | 5.7071e-06 | 5.7071e-06 | 126 | 103 | NO
2013-03-16 | 0.10995 | 0.10995 |  |  | 0.10961 | 0.10961 |  |  | 0.00034242 | 0.00034242 | 0.00068485 | 0.00068485 |  |  | 0.00067914 | 0.00067914 |  |  | 5.7071e-06 | 5.7071e-06 | 53 | 52 | NO
2013-03-17 | 0.010718 | 0.010718 |  |  | 0.001267 | 0.001267 |  |  | 0.0094509 | 0.0094509 | 2.2828e-05 | 2.2828e-05 |  |  | 5.7071e-06 | 5.7071e-06 |  |  | 1.7121e-05 | 1.7121e-05 | 28 | 25 | NO
2013-03-18 | 0.10454 | 0.10454 |  |  | 0.10454 | 0.10454 |  |  | 0 | 0 | 0.00079328 | 0.00079328 |  |  | 0.00079328 | 0.00079328 |  |  | 0 | 0 | 85 | 74 | NO
2013-03-19 | 0.2434 | 0.2434 |  |  | 0.2434 | 0.2434 |  |  | 0 | 0 | 0.0011814 | 0.0011814 |  |  | 0.0011814 | 0.0011814 |  |  | 0 | 0 | 81 | 70 | NO
2013-03-20 | 0.45553 | 0.45553 |  |  | 0.20874 | 0.20874 |  |  | 0.24679 | 0.24679 | 0.010147 | 0.010147 |  |  | 0.0012955 | 0.0012955 |  |  | 0.0088517 | 0.0088517 | 125 | 102 | NO
2013-03-21 | 0.27986 | 0.27986 |  |  | 0.27986 | 0.27986 |  |  | 0 | 0 | 0.0021801 | 0.0021801 |  |  | 0.0021801 | 0.0021801 |  |  | 0 | 0 | 185 | 155 | NO
2013-03-22 | 0.16988 | 0.16988 |  |  | 0.024757 | 0.024757 |  |  | 0.14512 | 0.14512 | 0.002163 | 0.002163 |  |  | 2.8535e-05 | 2.8535e-05 |  |  | 0.0021344 | 0.0021344 | 105 | 79 | NO
2013-03-23 | 0.16056 | 0.16056 |  |  | 0.16056 | 0.16056 |  |  | 0 | 0 | 0.00099874 | 0.00099874 |  |  | 0.00099874 | 0.00099874 |  |  | 0 | 0 | 82 | 63 | NO
2013-03-24 | 0.024244 | 0.024244 |  |  | 0.024244 | 0.024244 |  |  | 0 | 0 | 0.00013126 | 0.00013126 |  |  | 0.00013126 | 0.00013126 |  |  | 0 | 0 | 25 | 24 | NO
2013-03-25 | 0.12362 | 0.12362 |  |  | 0.12362 | 0.12362 |  |  | 0 | 0 | 0.00029677 | 0.00029677 |  |  | 0.00029677 | 0.00029677 |  |  | 0 | 0 | 85 | 78 | NO
2013-03-26 | 0.0929 | 0.0929 |  |  | 0.0929 | 0.0929 |  |  | 0 | 0 | 0.00067344 | 0.00067344 |  |  | 0.00067344 | 0.00067344 |  |  | 0 | 0 | 73 | 69 | NO
2013-03-27 | 0.19638 | 0.19638 |  |  | 0.19638 | 0.19638 |  |  | 0 | 0 | 0.00066773 | 0.00066773 |  |  | 0.00066773 | 0.00066773 |  |  | 0 | 0 | 56 | 53 | NO
2013-03-28 | 0.53322 | 0.53322 |  |  | 0.53281 | 0.53281 |  |  | 0.00041091 | 0.00041091 | 0.007248 | 0.007248 |  |  | 0.0072423 | 0.0072423 |  |  | 5.7071e-06 | 5.7071e-06 | 120 | 88 | NO
2013-03-29 | 0.21689 | 0.21689 |  |  | 0.21686 | 0.21686 |  |  | 3.4242e-05 | 3.4242e-05 | 0.00029106 | 0.00029106 |  |  | 0.00028535 | 0.00028535 |  |  | 5.7071e-06 | 5.7071e-06 | 44 | 42 | NO
2013-03-30 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 25 | 25 | NO
2013-03-31 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 23 | 19 | NO
2013-04-01 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 13 | 12 | NO
2013-04-02 | 0.022977 | 0.022977 |  |  | 0.022977 | 0.022977 |  |  | 0 | 0 | 9.702e-05 | 9.702e-05 |  |  | 9.702e-05 | 9.702e-05 |  |  | 0 | 0 | 96 | 84 | NO
2013-04-03 | 0.099337 | 0.099337 |  |  | 0.099337 | 0.099337 |  |  | 0 | 0 | 0.00058783 | 0.00058783 |  |  | 0.00058783 | 0.00058783 |  |  | 0 | 0 | 87 | 78 | NO
2013-04-04 | 0.11095 | 0.11095 |  |  | 0.11095 | 0.11095 |  |  | 0 | 0 | 0.00076475 | 0.00076475 |  |  | 0.00076475 | 0.00076475 |  |  | 0 | 0 | 88 | 80 | NO
2013-04-05 | 0.22805 | 0.22805 |  |  | 0.22805 | 0.22805 |  |  | 0 | 0 | 0.00081041 | 0.00081041 |  |  | 0.00081041 | 0.00081041 |  |  | 0 | 0 | 91 | 80 | NO
2013-04-06 | 0.22278 | 0.22278 |  |  | 0.22278 | 0.22278 |  |  | 0 | 0 | 0.0011985 | 0.0011985 |  |  | 0.0011985 | 0.0011985 |  |  | 0 | 0 | 52 | 49 | NO
2013-04-07 | 0.010512 | 0.010512 |  |  | 0.010512 | 0.010512 |  |  | 0 | 0 | 0.00018833 | 0.00018833 |  |  | 0.00018833 | 0.00018833 |  |  | 0 | 0 | 30 | 24 | NO
2013-04-08 | 0.24148 | 0.24148 |  |  | 0.24148 | 0.24148 |  |  | 0 | 0 | 0.0021573 | 0.0021573 |  |  | 0.0021573 | 0.0021573 |  |  | 0 | 0 | 147 | 125 | NO
2013-04-09 | 0.23935 | 0.23935 |  |  | 0.23935 | 0.23935 |  |  | 0 | 0 | 0.0012327 | 0.0012327 |  |  | 0.0012327 | 0.0012327 |  |  | 0 | 0 | 88 | 73 | NO
2013-04-10 | 0.23812 | 0.23812 |  |  | 0.23812 | 0.23812 |  |  | 0 | 0 | 0.0011871 | 0.0011871 |  |  | 0.0011871 | 0.0011871 |  |  | 0 | 0 | 115 | 91 | NO
2013-04-11 | 0.2674 | 0.2674 |  |  | 0.2674 | 0.2674 |  |  | 0 | 0 | 0.00098162 | 0.00098162 |  |  | 0.00098162 | 0.00098162 |  |  | 0 | 0 | 109 | 94 | NO
2013-04-12 | 0.31948 | 0.31948 |  |  | 0.31541 | 0.31541 |  |  | 0.0040749 | 0.0040749 | 0.0011642 | 0.0011642 |  |  | 0.0010901 | 0.0010901 |  |  | 7.4192e-05 | 7.4192e-05 | 97 | 89 | NO
2013-04-13 | 0.059068 | 0.059068 |  |  | 0.059068 | 0.059068 |  |  | 0 | 0 | 0.00058212 | 0.00058212 |  |  | 0.00058212 | 0.00058212 |  |  | 0 | 0 | 38 | 35 | NO
2013-04-14 | 0.01356 | 0.01356 |  |  | 0.01356 | 0.01356 |  |  | 0 | 0 | 0.00012556 | 0.00012556 |  |  | 0.00012556 | 0.00012556 |  |  | 0 | 0 | 28 | 23 | NO
2013-04-15 | 0.018388 | 0.018388 |  |  | 0.018388 | 0.018388 |  |  | 0 | 0 | 0.00033672 | 0.00033672 |  |  | 0.00033672 | 0.00033672 |  |  | 0 | 0 | 82 | 78 | NO
2013-04-16 | 0.26716 | 0.26716 |  |  | 0.26716 | 0.26716 |  |  | 0 | 0 | 0.00090743 | 0.00090743 |  |  | 0.00090743 | 0.00090743 |  |  | 0 | 0 | 103 | 93 | NO
2013-04-17 | 0.26254 | 0.26254 |  |  | 0.26254 | 0.26254 |  |  | 0 | 0 | 0.0020203 | 0.0020203 |  |  | 0.0020203 | 0.0020203 |  |  | 0 | 0 | 108 | 104 | NO
2013-04-18 | 0.37057 | 0.37057 |  |  | 0.37057 | 0.37057 |  |  | 0 | 0 | 0.0014268 | 0.0014268 |  |  | 0.0014268 | 0.0014268 |  |  | 0 | 0 | 77 | 72 | NO
2013-04-19 | 1.0342 | 1.0342 |  |  | 1.0048 | 1.0048 |  |  | 0.029312 | 0.029312 | 0.019786 | 0.019786 |  |  | 0.019707 | 0.019707 |  |  | 7.9899e-05 | 7.9899e-05 | 287 | 222 | NO
2013-04-20 | 0.070334 | 0.070334 |  |  | 0.070334 | 0.070334 |  |  | 0 | 0 | 0.00057641 | 0.00057641 |  |  | 0.00057641 | 0.00057641 |  |  | 0 | 0 | 50 | 48 | NO
2013-04-21 | 0.10841 | 0.10841 |  |  | 0.10841 | 0.10841 |  |  | 0 | 0 | 0.00073621 | 0.00073621 |  |  | 0.00073621 | 0.00073621 |  |  | 0 | 0 | 44 | 40 | NO
2013-04-22 | 0.087216 | 0.087216 |  |  | 0.087216 | 0.087216 |  |  | 0 | 0 | 0.00095879 | 0.00095879 |  |  | 0.00095879 | 0.00095879 |  |  | 0 | 0 | 147 | 143 | NO
2013-04-23 | 0.015204 | 0.015204 |  |  | 0.015204 | 0.015204 |  |  | 0 | 0 | 0.0003253 | 0.0003253 |  |  | 0.0003253 | 0.0003253 |  |  | 0 | 0 | 72 | 71 | NO
2013-04-24 | 0.34328 | 0.34328 |  |  | 0.34328 | 0.34328 |  |  | 0 | 0 | 0.0013583 | 0.0013583 |  |  | 0.0013583 | 0.0013583 |  |  | 0 | 0 | 87 | 85 | NO
2013-04-25 | 0.0049994 | 0.0049994 |  |  | 0.0049994 | 0.0049994 |  |  | 0 | 0 | 9.1313e-05 | 9.1313e-05 |  |  | 9.1313e-05 | 9.1313e-05 |  |  | 0 | 0 | 19 | 19 | NO
2013-04-26 | 0.0076361 | 0.0076361 |  |  | 0.0076361 | 0.0076361 |  |  | 0 | 0 | 0.00022828 | 0.00022828 |  |  | 0.00022828 | 0.00022828 |  |  | 0 | 0 | 83 | 74 | NO
2013-04-27 | 0.051329 | 0.051329 |  |  | 0.051329 | 0.051329 |  |  | 0 | 0 | 0.00014838 | 0.00014838 |  |  | 0.00014838 | 0.00014838 |  |  | 0 | 0 | 36 | 29 | NO
2013-04-28 | 0.024757 | 0.024757 |  |  | 0.024757 | 0.024757 |  |  | 0 | 0 | 0.00041662 | 0.00041662 |  |  | 0.00041662 | 0.00041662 |  |  | 0 | 0 | 24 | 22 | NO
2013-04-29 | 0.41735 | 0.41735 |  |  | 0.41724 | 0.41724 |  |  | 0.00010273 | 0.00010273 | 0.0048853 | 0.0048853 |  |  | 0.0048796 | 0.0048796 |  |  | 5.7071e-06 | 5.7071e-06 | 105 | 98 | NO
2013-04-30 | 0.18772 | 0.18772 |  |  | 0.18772 | 0.18772 |  |  | 0 | 0 | 0.0014667 | 0.0014667 |  |  | 0.0014667 | 0.0014667 |  |  | 0 | 0 | 148 | 138 | NO
2013-05-01 | 0.11704 | 0.11704 |  |  | 0.11704 | 0.11704 |  |  | 0 | 0 | 0.0010729 | 0.0010729 |  |  | 0.0010729 | 0.0010729 |  |  | 0 | 0 | 145 | 135 | NO
2013-05-02 | 0.31462 | 0.31462 |  |  | 0.31462 | 0.31462 |  |  | 0 | 0 | 0.001558 | 0.001558 |  |  | 0.001558 | 0.001558 |  |  | 0 | 0 | 138 | 132 | NO
2013-05-03 | 0.27668 | 0.27668 |  |  | 0.27668 | 0.27668 |  |  | 0 | 0 | 0.0016893 | 0.0016893 |  |  | 0.0016893 | 0.0016893 |  |  | 0 | 0 | 105 | 97 | NO
2013-05-04 | 0.12307 | 0.12307 |  |  | 0.12307 | 0.12307 |  |  | 0 | 0 | 0.00059354 | 0.00059354 |  |  | 0.00059354 | 0.00059354 |  |  | 0 | 0 | 35 | 33 | NO
2013-05-05 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 33 | 26 | NO
2013-05-06 | 0.027497 | 0.027497 |  |  | 0.027497 | 0.027497 |  |  | 0 | 0 | 0.00045086 | 0.00045086 |  |  | 0.00045086 | 0.00045086 |  |  | 0 | 0 | 105 | 97 | NO
2013-05-07 | 0.10869 | 0.10869 |  |  | 0.10869 | 0.10869 |  |  | 0 | 0 | 0.00067344 | 0.00067344 |  |  | 0.00067344 | 0.00067344 |  |  | 0 | 0 | 87 | 79 | NO
2013-05-08 | 0.16138 | 0.16138 |  |  | 0.16138 | 0.16138 |  |  | 0 | 0 | 0.00091313 | 0.00091313 |  |  | 0.00091313 | 0.00091313 |  |  | 0 | 0 | 82 | 76 | NO
2013-05-09 | 0.32345 | 0.32345 |  |  | 0.32215 | 0.32215 |  |  | 0.0013012 | 0.0013012 | 0.0013297 | 0.0013297 |  |  | 0.001324 | 0.001324 |  |  | 5.7071e-06 | 5.7071e-06 | 75 | 74 | NO
2013-05-10 | 0.5009 | 0.5009 |  |  | 0.5009 | 0.5009 |  |  | 0 | 0 | 0.0022258 | 0.0022258 |  |  | 0.0022258 | 0.0022258 |  |  | 0 | 0 | 71 | 70 | NO
2013-05-11 | 0.067252 | 0.067252 |  |  | 0.067252 | 0.067252 |  |  | 0 | 0 | 0.00034813 | 0.00034813 |  |  | 0.00034813 | 0.00034813 |  |  | 0 | 0 | 42 | 41 | NO
2013-05-12 | 0.29499 | 0.29499 |  |  | 0.29499 | 0.29499 |  |  | 0 | 0 | 0.0048339 | 0.0048339 |  |  | 0.0048339 | 0.0048339 |  |  | 0 | 0 | 54 | 51 | NO
2013-05-13 | 0.11156 | 0.11156 |  |  | 0.11156 | 0.11156 |  |  | 0 | 0 | 0.0011072 | 0.0011072 |  |  | 0.0011072 | 0.0011072 |  |  | 0 | 0 | 98 | 94 | NO
2013-05-14 | 0.88267 | 0.88267 |  |  | 0.76765 | 0.76765 |  |  | 0.11502 | 0.11502 | 0.012167 | 0.012167 |  |  | 0.011665 | 0.011665 |  |  | 0.00050222 | 0.00050222 | 202 | 164 | NO
2013-05-15 | 0.060815 | 0.060815 |  |  | 0.060027 | 0.060027 |  |  | 0.00078758 | 0.00078758 | 0.00058783 | 0.00058783 |  |  | 0.00058212 | 0.00058212 |  |  | 5.7071e-06 | 5.7071e-06 | 111 | 99 | NO
2013-05-16 | 0.18419 | 0.18419 |  |  | 0.18419 | 0.18419 |  |  | 0 | 0 | 0.0021002 | 0.0021002 |  |  | 0.0021002 | 0.0021002 |  |  | 0 | 0 | 80 | 77 | NO
2013-05-17 | 0.10084 | 0.10084 |  |  | 0.10084 | 0.10084 |  |  | 0 | 0 | 0.00061066 | 0.00061066 |  |  | 0.00061066 | 0.00061066 |  |  | 0 | 0 | 78 | 77 | NO
2013-05-18 | 0.091393 | 0.091393 |  |  | 0.091393 | 0.091393 |  |  | 0 | 0 | 0.00018263 | 0.00018263 |  |  | 0.00018263 | 0.00018263 |  |  | 0 | 0 | 51 | 50 | NO
2013-05-19 | 0.19415 | 0.19415 |  |  | 0.19415 | 0.19415 |  |  | 0 | 0 | 0.003955 | 0.003955 |  |  | 0.003955 | 0.003955 |  |  | 0 | 0 | 104 | 56 | NO
2013-05-20 | 0.24456 | 0.24456 |  |  | 0.24456 | 0.24456 |  |  | 0 | 0 | 0.00091313 | 0.00091313 |  |  | 0.00091313 | 0.00091313 |  |  | 0 | 0 | 125 | 118 | NO
2013-05-21 | 0.21319 | 0.21319 |  |  | 0.21319 | 0.21319 |  |  | 0 | 0 | 0.00090172 | 0.00090172 |  |  | 0.00090172 | 0.00090172 |  |  | 0 | 0 | 98 | 91 | NO
2013-05-22 | 0.22141 | 0.22141 |  |  | 0.22141 | 0.22141 |  |  | 0 | 0 | 0.0009702 | 0.0009702 |  |  | 0.0009702 | 0.0009702 |  |  | 0 | 0 | 105 | 96 | NO
2013-05-23 | 0.19977 | 0.19977 |  |  | 0.19977 | 0.19977 |  |  | 0 | 0 | 0.0011072 | 0.0011072 |  |  | 0.0011072 | 0.0011072 |  |  | 0 | 0 | 91 | 83 | NO
2013-05-24 | 0.27877 | 0.27877 |  |  | 0.27877 | 0.27877 |  |  | 0 | 0 | 0.002631 | 0.002631 |  |  | 0.002631 | 0.002631 |  |  | 0 | 0 | 128 | 120 | NO
2013-05-25 | 0.015204 | 0.015204 |  |  | 0.015204 | 0.015204 |  |  | 0 | 0 | 0.00013697 | 0.00013697 |  |  | 0.00013697 | 0.00013697 |  |  | 0 | 0 | 30 | 28 | NO
2013-05-26 | 0.038899 | 0.038899 |  |  | 0.038899 | 0.038899 |  |  | 0 | 0 | 0.00037096 | 0.00037096 |  |  | 0.00037096 | 0.00037096 |  |  | 0 | 0 | 30 | 26 | NO
2013-05-27 | 0.054582 | 0.054582 |  |  | 0.054582 | 0.054582 |  |  | 0 | 0 | 0.0003995 | 0.0003995 |  |  | 0.0003995 | 0.0003995 |  |  | 0 | 0 | 82 | 76 | NO
2013-05-28 | 0.1144 | 0.1144 |  |  | 0.1144 | 0.1144 |  |  | 0 | 0 | 0.00035955 | 0.00035955 |  |  | 0.00035955 | 0.00035955 |  |  | 0 | 0 | 77 | 76 | NO
2013-05-29 | 0.29746 | 0.29746 |  |  | 0.24203 | 0.24203 |  |  | 0.055439 | 0.055439 | 0.0009645 | 0.0009645 |  |  | 0.00074192 | 0.00074192 |  |  | 0.00022258 | 0.00022258 | 83 | 79 | NO
2013-05-30 | 0.025168 | 0.025168 |  |  | 0.025168 | 0.025168 |  |  | 0 | 0 | 0.00049081 | 0.00049081 |  |  | 0.00049081 | 0.00049081 |  |  | 0 | 0 | 102 | 98 | NO
2013-05-31 | 0.11844 | 0.11844 |  |  | 0.11844 | 0.11844 |  |  | 0 | 0 | 0.00082182 | 0.00082182 |  |  | 0.00082182 | 0.00082182 |  |  | 0 | 0 | 86 | 79 | NO
2013-06-01 | 0.026367 | 0.026367 |  |  | 0.026367 | 0.026367 |  |  | 0 | 0 | 0.00010273 | 0.00010273 |  |  | 0.00010273 | 0.00010273 |  |  | 0 | 0 | 48 | 46 | NO
2013-06-02 | 0.26613 | 0.26613 |  |  | 0.26613 | 0.26613 |  |  | 0 | 0 | 0.0040349 | 0.0040349 |  |  | 0.0040349 | 0.0040349 |  |  | 0 | 0 | 84 | 67 | NO
2013-06-03 | 0.56784 | 0.56784 |  |  | 0.56456 | 0.56456 |  |  | 0.0032873 | 0.0032873 | 0.0074135 | 0.0074135 |  |  | 0.0072708 | 0.0072708 |  |  | 0.00014268 | 0.00014268 | 180 | 155 | NO
2013-06-04 | 0.066499 | 0.066499 |  |  | 0.058281 | 0.058281 |  |  | 0.0082182 | 0.0082182 | 0.0010843 | 0.0010843 |  |  | 0.0010615 | 0.0010615 |  |  | 2.2828e-05 | 2.2828e-05 | 164 | 142 | NO
2013-06-05 | 0.063177 | 0.063177 |  |  | 0.012738 | 0.012738 |  |  | 0.050439 | 0.050439 | 0.00057071 | 0.00057071 |  |  | 0.00021116 | 0.00021116 |  |  | 0.00035955 | 0.00035955 | 131 | 124 | NO
2013-06-06 | 0.25928 | 0.25928 |  |  | 0.25928 | 0.25928 |  |  | 0 | 0 | 0.00069056 | 0.00069056 |  |  | 0.00069056 | 0.00069056 |  |  | 0 | 0 | 108 | 96 | NO
2013-06-07 | 0.15957 | 0.15957 |  |  | 0.11916 | 0.11916 |  |  | 0.040406 | 0.040406 | 0.0013126 | 0.0013126 |  |  | 0.000565 | 0.000565 |  |  | 0.00074763 | 0.00074763 | 103 | 93 | NO
2013-06-08 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 25 | 21 | NO
2013-06-09 | 0.0092797 | 0.0092797 |  |  | 0.0092797 | 0.0092797 |  |  | 0 | 0 | 0.00014838 | 0.00014838 |  |  | 0.00014838 | 0.00014838 |  |  | 0 | 0 | 25 | 23 | NO
2013-06-10 | 0.017395 | 0.017395 |  |  | 0.017395 | 0.017395 |  |  | 0 | 0 | 0.00011414 | 0.00011414 |  |  | 0.00011414 | 0.00011414 |  |  | 0 | 0 | 39 | 36 | NO
2013-06-11 | 0.16484 | 0.16484 |  |  | 0.16484 | 0.16484 |  |  | 0 | 0 | 0.00055929 | 0.00055929 |  |  | 0.00055929 | 0.00055929 |  |  | 0 | 0 | 134 | 112 | NO
2013-06-12 | 0.0053418 | 0.0053418 |  |  | 0.0053418 | 0.0053418 |  |  | 0 | 0 | 0.00020545 | 0.00020545 |  |  | 0.00020545 | 0.00020545 |  |  | 0 | 0 | 76 | 76 | NO
2013-06-13 | 0.011129 | 0.011129 |  |  | 0.011129 | 0.011129 |  |  | 0 | 0 | 0.00014268 | 0.00014268 |  |  | 0.00014268 | 0.00014268 |  |  | 0 | 0 | 141 | 132 | NO
2013-06-14 | 0.037427 | 0.037427 |  |  | 0.037427 | 0.037427 |  |  | 0 | 0 | 0.00037096 | 0.00037096 |  |  | 0.00037096 | 0.00037096 |  |  | 0 | 0 | 79 | 73 | NO
2013-06-15 | 0.029722 | 0.029722 |  |  | 0.029722 | 0.029722 |  |  | 0 | 0 | 0.00018263 | 0.00018263 |  |  | 0.00018263 | 0.00018263 |  |  | 0 | 0 | 37 | 34 | NO
2013-06-16 | 1.174 | 1.174 |  |  | 1.174 | 1.174 |  |  | 0 | 0 | 0.011642 | 0.011642 |  |  | 0.011642 | 0.011642 |  |  | 0 | 0 | 235 | 182 | NO
2013-06-17 | 0.071875 | 0.071875 |  |  | 0.071875 | 0.071875 |  |  | 0 | 0 | 0.00025111 | 0.00025111 |  |  | 0.00025111 | 0.00025111 |  |  | 0 | 0 | 126 | 112 | NO
2013-06-18 | 0.37328 | 0.37328 |  |  | 0.37328 | 0.37328 |  |  | 0 | 0 | 0.0014211 | 0.0014211 |  |  | 0.0014211 | 0.0014211 |  |  | 0 | 0 | 90 | 81 | NO
2013-06-19 | 0.41601 | 0.41601 |  |  | 0.41601 | 0.41601 |  |  | 0 | 0 | 0.0016493 | 0.0016493 |  |  | 0.0016493 | 0.0016493 |  |  | 0 | 0 | 118 | 105 | NO
2013-06-20 | 0.20658 | 0.20658 |  |  | 0.20658 | 0.20658 |  |  | 0 | 0 | 0.00070768 | 0.00070768 |  |  | 0.00070768 | 0.00070768 |  |  | 0 | 0 | 104 | 94 | NO
2013-06-21 | 0.21405 | 0.21405 |  |  | 0.21405 | 0.21405 |  |  | 0 | 0 | 0.001227 | 0.001227 |  |  | 0.001227 | 0.001227 |  |  | 0 | 0 | 114 | 101 | NO
2013-06-22 | 0.10036 | 0.10036 |  |  | 0.10036 | 0.10036 |  |  | 0 | 0 | 0.0003253 | 0.0003253 |  |  | 0.0003253 | 0.0003253 |  |  | 0 | 0 | 50 | 50 | NO
2013-06-23 | 0.64972 | 0.64972 |  |  | 0.64972 | 0.64972 |  |  | 0 | 0 | 0.015329 | 0.015329 |  |  | 0.015329 | 0.015329 |  |  | 0 | 0 | 390 | 319 | NO
2013-06-24 | 0.41831 | 0.41831 |  |  | 0.41831 | 0.41831 |  |  | 0 | 0 | 0.0068999 | 0.0068999 |  |  | 0.0068999 | 0.0068999 |  |  | 0 | 0 | 158 | 134 | NO
2013-06-25 | 0.47436 | 0.47436 |  |  | 0.47436 | 0.47436 |  |  | 0 | 0 | 0.01251 | 0.01251 |  |  | 0.01251 | 0.01251 |  |  | 0 | 0 | 139 | 122 | NO
2013-06-26 | 0.30363 | 0.30363 |  |  | 0.30363 | 0.30363 |  |  | 0 | 0 | 0.0012499 | 0.0012499 |  |  | 0.0012499 | 0.0012499 |  |  | 0 | 0 | 101 | 81 | NO
2013-06-27 | 0.37502 | 0.37502 |  |  | 0.37502 | 0.37502 |  |  | 0 | 0 | 0.0013868 | 0.0013868 |  |  | 0.0013868 | 0.0013868 |  |  | 0 | 0 | 118 | 105 | NO
2013-06-28 | 0.19731 | 0.19731 |  |  | 0.19731 | 0.19731 |  |  | 0 | 0 | 0.00087889 | 0.00087889 |  |  | 0.00087889 | 0.00087889 |  |  | 0 | 0 | 125 | 111 | NO
2013-06-29 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 55 | 50 | NO
2013-06-30 | 0.028079 | 0.028079 |  |  | 0.028079 | 0.028079 |  |  | 0 | 0 | 0.00022828 | 0.00022828 |  |  | 0.00022828 | 0.00022828 |  |  | 0 | 0 | 34 | 31 | NO
Contents

## 1d. STPIS MED Threshold
ActewAGL
STPIS Data Reporting
2012-13 |  |  |  | 2007-07-01
MED Threshold |  |  |  | 2008-07-01
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: MED threshold
MED threshold (t-med) year ending 30 June
Alpha - average of Ln(SAIDI)
Beta-standard deviation of Ln(SAIDI)
X Beta from the mean
Table 2: MED calculation
Date | Unplanned SAIDI - total (after removing exluded events allowed under clause 3.3(a) of the STPIS) | Total unplanned customer minutes off supply (after removing exluded events allowed under clause 3.3(a) of the STPIS) | Ln (SAIDI)
2007-07-01 | 0 | 0
2007-07-02 | 0.0090339 | 1422 | -4.7068
2007-07-03 | 0.00087671 | 138 | -7.0393
2007-07-04 | 0.025806 | 4062 | -3.6572
2007-07-05 | 0.40062 | 63060 | -0.91475
2007-07-06 | 0.0057176 | 900 | -5.1642
2007-07-07 | 0 | 0
2007-07-08 | 0.047609 | 7494 | -3.0447
2007-07-09 | 0 | 0
2007-07-10 | 0.15922 | 25062 | -1.8375
2007-07-11 | 0.025005 | 3936 | -3.6887
2007-07-12 | 0 | 0
2007-07-13 | 0.0045741 | 720 | -5.3873
2007-07-14 | 0 | 0
2007-07-15 | 0.25424 | 40020 | -1.3695
2007-07-16 | 0.016124 | 2538 | -4.1275
2007-07-17 | 0.11496 | 18096 | -2.1631
2007-07-18 | 0.079437 | 12504 | -2.5328
2007-07-19 | 0.035526 | 5592 | -3.3375
2007-07-20 | 0.00049553 | 78 | -7.6099
2007-07-21 | 0 | 0
2007-07-22 | 0.072157 | 11358 | -2.6289
2007-07-23 | 0.023785 | 3744 | -3.7387
2007-07-24 | 0.0030494 | 480 | -5.7928
2007-07-25 | 0 | 0
2007-07-26 | 0.042501 | 6690 | -3.1582
2007-07-27 | 0.024624 | 3876 | -3.704
2007-07-28 | 0.005184 | 816 | -5.2622
2007-07-29 | 0 | 0
2007-07-30 | 0.025196 | 3966 | -3.6811
2007-07-31 | 0 | 0
2007-08-01 | 0.0067468 | 1062 | -4.9987
2007-08-02 | 0.016848 | 2652 | -4.0835
2007-08-03 | 0.0072042 | 1134 | -4.9331
2007-08-04 | 0.0070518 | 1110 | -4.9545
2007-08-05 | 0 | 0
2007-08-06 | 0 | 0
2007-08-07 | 0.0076235 | 1200 | -4.8765
2007-08-08 | 0.00083859 | 132 | -7.0838
2007-08-09 | 0 | 0
2007-08-10 | 0.63214 | 99504 | -0.45864
2007-08-11 | 0 | 0
2007-08-12 | 0.21068 | 33162 | -1.5574
2007-08-13 | 0.08748 | 13770 | -2.4363
2007-08-14 | 0.023252 | 3660 | -3.7614
2007-08-15 | 0.37412 | 58890 | -0.98317
2007-08-16 | 0.22951 | 36126 | -1.4718
2007-08-17 | 0.0026682 | 420 | -5.9263
2007-08-18 | 0.0067087 | 1056 | -5.0043
2007-08-19 | 0 | 0
2007-08-20 | 0.2937 | 46230 | -1.2252
2007-08-21 | 0.0043073 | 678 | -5.4474
2007-08-22 | 0 | 0
2007-08-23 | 0.00019059 | 30 | -8.5654
2007-08-24 | 0 | 0
2007-08-25 | 0.0016009 | 252 | -6.4372
2007-08-26 | 0 | 0
2007-08-27 | 0 | 0
2007-08-28 | 0.023633 | 3720 | -3.7451
2007-08-29 | 0.024853 | 3912 | -3.6948
2007-08-30 | 0.30174 | 47496 | -1.1982
2007-08-31 | 0.0093388 | 1470 | -4.6736
2007-09-01 | 0.0017153 | 270 | -6.3682
2007-09-02 | 0.0093007 | 1464 | -4.6777
2007-09-03 | 0.25367 | 39930 | -1.3717
2007-09-04 | 0.0019821 | 312 | -6.2236
2007-09-05 | 0.021155 | 3330 | -3.8559
2007-09-06 | 0.00049553 | 78 | -7.6099
2007-09-07 | 0.076235 | 12000 | -2.5739
2007-09-08 | 0.024014 | 3780 | -3.7291
2007-09-09 | 0 | 0
2007-09-10 | 0 | 0
2007-09-11 | 0.0084621 | 1332 | -4.7722
2007-09-12 | 0 | 0
2007-09-13 | 0.056528 | 8898 | -2.873
2007-09-14 | 0.018106 | 2850 | -4.0115
2007-09-15 | 0.018563 | 2922 | -3.9866
2007-09-16 | 0.0099106 | 1560 | -4.6142
2007-09-17 | 0.001296 | 204 | -6.6485
2007-09-18 | 0.00080047 | 126 | -7.1303
2007-09-19 | 0 | 0
2007-09-20 | 0 | 0
2007-09-21 | 0.021155 | 3330 | -3.8559
2007-09-22 | 0.0046504 | 732 | -5.3708
2007-09-23 | 0.020279 | 3192 | -3.8982
2007-09-24 | 0.0021727 | 342 | -6.1318
2007-09-25 | 0.018487 | 2910 | -3.9907
2007-09-26 | 0 | 0
2007-09-27 | 0.050087 | 7884 | -2.994
2007-09-28 | 0.012426 | 1956 | -4.3879
2007-09-29 | 0.0051459 | 810 | -5.2696
2007-09-30 | 0.037775 | 5946 | -3.2761
2007-10-01 | 0.041053 | 6462 | -3.1929
2007-10-02 | 0.57325 | 90234 | -0.55643
2007-10-03 | 0.24029 | 37824 | -1.4259
2007-10-04 | 0.022299 | 3510 | -3.8032
2007-10-05 | 0.0086908 | 1368 | -4.7455
2007-10-06 | 0.16844 | 26514 | -1.7812
2007-10-07 | 0.0092626 | 1458 | -4.6818
2007-10-08 | 0.0059463 | 936 | -5.125
2007-10-09 | 0 | 0
2007-10-10 | 0.010444 | 1644 | -4.5617
2007-10-11 | 0.017877 | 2814 | -4.0242
2007-10-12 | 0.0065181 | 1026 | -5.0332
2007-10-13 | 0.011664 | 1836 | -4.4512
2007-10-14 | 0 | 0
2007-10-15 | 0.032324 | 5088 | -3.432
2007-10-16 | 0.38819 | 61104 | -0.94626
2007-10-17 | 0.028703 | 4518 | -3.5508
2007-10-18 | 0 | 0
2007-10-19 | 0 | 0
2007-10-20 | 0.027483 | 4326 | -3.5942
2007-10-21 | 0.68314 | 107532 | -0.38105
2007-10-22 | 0.25051 | 39432 | -1.3843
2007-10-23 | 0 | 0
2007-10-24 | 0.0056414 | 888 | -5.1776
2007-10-25 | 0.030227 | 4758 | -3.499
2007-10-26 | 0.00072423 | 114 | -7.2304
2007-10-27 | 0.026377 | 4152 | -3.6352
2007-10-28 | 0.18689 | 29418 | -1.6772
2007-10-29 | 0.049667 | 7818 | -3.0024
2007-10-30 | 0.16227 | 25542 | -1.8185
2007-10-31 | 0.0078141 | 1230 | -4.8518
2007-11-01 | 0 | 0
2007-11-02 | 0 | 0
2007-11-03 | 0 | 0
2007-11-04 | 0.022947 | 3612 | -3.7746
2007-11-05 | 0.055004 | 8658 | -2.9004
2007-11-06 | 0.0017153 | 270 | -6.3682
2007-11-07 | 0.0070518 | 1110 | -4.9545
2007-11-08 | 0 | 0
2007-11-09 | 0.16375 | 25776 | -1.8094
2007-11-10 | 0 | 0
2007-11-11 | 0 | 0
2007-11-12 | 0.024243 | 3816 | -3.7196
2007-11-13 | 0.028703 | 4518 | -3.5508
2007-11-14 | 0.064266 | 10116 | -2.7447
2007-11-15 | 0.012884 | 2028 | -4.3518
2007-11-16 | 0.020012 | 3150 | -3.9114
2007-11-17 | 0.24803 | 39042 | -1.3942
2007-11-18 | 0.011855 | 1866 | -4.435
2007-11-19 | 0.032171 | 5064 | -3.4367
2007-11-20 | 0 | 0
2007-11-21 | 0.019478 | 3066 | -3.9385
2007-11-22 | 0.04212 | 6630 | -3.1672
2007-11-23 | 0.023862 | 3756 | -3.7355
2007-11-24 | 0 | 0
2007-11-25 | 0.015247 | 2400 | -4.1834
2007-11-26 | 0.0039642 | 624 | -5.5304
2007-11-27 | 0.00041929 | 66 | -7.7769
2007-11-28 | 0.53807 | 84696 | -0.61977
2007-11-29 | 0.0078141 | 1230 | -4.8518
2007-11-30 | 0.11599 | 18258 | -2.1542
2007-12-01 | 0.23343 | 36744 | -1.4549
2007-12-02 | 0.00030494 | 48 | -8.0954
2007-12-03 | 0.024167 | 3804 | -3.7228
2007-12-04 | 0 | 0
2007-12-05 | 0.0088052 | 1386 | -4.7324
2007-12-06 | 0.016352 | 2574 | -4.1134
2007-12-07 | 0.85353 | 134352 | -0.15837
2007-12-08 | 0.014866 | 2340 | -4.2087
2007-12-09 | 0.0089958 | 1416 | -4.711
2007-12-10 | 0 | 0
2007-12-11 | 0 | 0
2007-12-12 | 0.89019 | 140122.2 | -0.11632
2007-12-13 | 0.0162 | 2550 | -4.1227
2007-12-14 | 0.04799 | 7554 | -3.0368
2007-12-15 | 0.040748 | 6414 | -3.2004
2007-12-16 | 0 | 0
2007-12-17 | 0 | 0
2007-12-18 | 0 | 0
2007-12-19 | 0 | 0
2007-12-20 | 0 | 0
2007-12-21 | 0.044598 | 7020 | -3.1101
2007-12-22 | 0.83432 | 131328 | -0.18114
2007-12-23 | 0.07128 | 11220 | -2.6411
2007-12-24 | 0.062703 | 9870 | -2.7693
2007-12-25 | 0 | 0
2007-12-26 | 0.01864 | 2934 | -3.9825
2007-12-27 | 0.61903 | 97440 | -0.4796
2007-12-28 | 1.1022 | 173496 | 0.097317
2007-12-29 | 0.00053365 | 84 | -7.5358
2007-12-30 | 0.23095 | 36354 | -1.4655
2007-12-31 | 0.44079 | 69384 | -0.81918
2008-01-01 | 0.0049172 | 774 | -5.315
2008-01-02 | 0.01742 | 2742 | -4.0502
2008-01-03 | 0.021117 | 3324 | -3.8577
2008-01-04 | 0.5549 | 87345 | -0.58897
2008-01-05 | 0.12987 | 20442 | -2.0412
2008-01-06 | 0 | 0
2008-01-07 | 0.017229 | 2712 | -4.0612
2008-01-08 | 0 | 0
2008-01-09 | 0.010635 | 1674 | -4.5436
2008-01-10 | 0.011207 | 1764 | -4.4913
2008-01-11 | 0.0094532 | 1488 | -4.6614
2008-01-12 | 0.12198 | 19200 | -2.1039
2008-01-13 | 0.18701 | 29436 | -1.6766
2008-01-14 | 0.012503 | 1968 | -4.3818
2008-01-15 | 0.048638 | 7656 | -3.0233
2008-01-16 | 0.27307 | 42984 | -1.298
2008-01-17 | 0.022756 | 3582 | -3.7829
2008-01-18 | 0 | 0
2008-01-19 | 0 | 0
2008-01-20 | 0.020317 | 3198 | -3.8963
2008-01-21 | 0.016086 | 2532 | -4.1298
2008-01-22 | 0.29069 | 45756 | -1.2355
2008-01-23 | 0.017534 | 2760 | -4.0436
2008-01-24 | 0.0053365 | 840 | -5.2332
2008-01-25 | 0.015781 | 2484 | -4.149
2008-01-26 | 0.0054889 | 864 | -5.205
2008-01-27 | 0.054584 | 8592 | -2.908
2008-01-28 | 0.010139 | 1596 | -4.5913
2008-01-29 | 0.0022489 | 354 | -6.0973
2008-01-30 | 0.11843 | 18642 | -2.1334
2008-01-31 | 0 | 0
2008-02-01 | 0.043264 | 6810 | -3.1404
2008-02-02 | 0.0062894 | 990 | -5.0689
2008-02-03 | 0.011207 | 1764 | -4.4913
2008-02-04 | 0.30418 | 47880 | -1.1901
2008-02-05 | 0 | 0
2008-02-06 | 0.0010292 | 162 | -6.879
2008-02-07 | 0.014142 | 2226 | -4.2586
2008-02-08 | 0.016467 | 2592 | -4.1064
2008-02-09 | 0.041624 | 6552 | -3.1791
2008-02-10 | 0.0088433 | 1392 | -4.7281
2008-02-11 | 0 | 0
2008-02-12 | 0.073453 | 11562 | -2.6111
2008-02-13 | 0.0096056 | 1512 | -4.6454
2008-02-14 | 0.055156 | 8682 | -2.8976
2008-02-15 | 0.015743 | 2478 | -4.1514
2008-02-16 | 0.018144 | 2856 | -4.0094
2008-02-17 | 0 | 0
2008-02-18 | 0.0066706 | 1050 | -5.01
2008-02-19 | 0.0046885 | 738 | -5.3626
2008-02-20 | 0.01033 | 1626 | -4.5727
2008-02-21 | 0.14607 | 22992 | -1.9237
2008-02-22 | 0.10177 | 16020 | -2.285
2008-02-23 | 0 | 0
2008-02-24 | 0 | 0
2008-02-25 | 0.50959 | 80214 | -0.67414
2008-02-26 | 0 | 0
2008-02-27 | 0 | 0
2008-02-28 | 0.0088433 | 1392 | -4.7281
2008-02-29 | 0.12819 | 20178 | -2.0542
2008-03-01 | 0 | 0
2008-03-02 | 0.01761 | 2772 | -4.0393
2008-03-03 | 0.00091482 | 144 | -6.9968
2008-03-04 | 0.024853 | 3912 | -3.6948
2008-03-05 | 0.015056 | 2370 | -4.1959
2008-03-06 | 0.019554 | 3078 | -3.9346
2008-03-07 | 0.15377 | 24204 | -1.8723
2008-03-08 | 0.012655 | 1992 | -4.3697
2008-03-09 | 0 | 0
2008-03-10 | 0 | 0
2008-03-11 | 0.022909 | 3606 | -3.7762
2008-03-12 | 0.0054127 | 852 | -5.219
2008-03-13 | 0.042463 | 6684 | -3.1591
2008-03-14 | 0.019745 | 3108 | -3.9249
2008-03-15 | 0.0015628 | 246 | -6.4613
2008-03-16 | 0.16776 | 26406 | -1.7852
2008-03-17 | 0 | 0
2008-03-18 | 0.0026682 | 420 | -5.9263
2008-03-19 | 0.0083859 | 1320 | -4.7812
2008-03-20 | 0.0083096 | 1308 | -4.7903
2008-03-21 | 0.029732 | 4680 | -3.5155
2008-03-22 | 0 | 0
2008-03-23 | 0 | 0
2008-03-24 | 0.037127 | 5844 | -3.2934
2008-03-25 | 1.0955 | 172434 | 0.091177
2008-03-26 | 0.020279 | 3192 | -3.8982
2008-03-27 | 0 | 0
2008-03-28 | 0.11496 | 18096 | -2.1631
2008-03-29 | 0.015133 | 2382 | -4.1909
2008-03-30 | 0.013799 | 2172 | -4.2832
2008-03-31 | 0.0035449 | 558 | -5.6422
2008-04-01 | 0.011092 | 1746 | -4.5015
2008-04-02 | 0.20202 | 31800 | -1.5994
2008-04-03 | 0.39456 | 62106 | -0.93
2008-04-04 | 0.014294 | 2250 | -4.2479
2008-04-05 | 0 | 0
2008-04-06 | 0.0080428 | 1266 | -4.823
2008-04-07 | 0 | 0
2008-04-08 | 0.20103 | 31644 | -1.6043
2008-04-09 | 0.0042692 | 672 | -5.4563
2008-04-10 | 0.0074329 | 1170 | -4.9018
2008-04-11 | 0.0060988 | 960 | -5.0997
2008-04-12 | 0.011816 | 1860 | -4.4383
2008-04-13 | 0.3264 | 51378 | -1.1196
2008-04-14 | 0.018754 | 2952 | -3.9764
2008-04-15 | 0.058815 | 9258 | -2.8333
2008-04-16 | 0.01296 | 2040 | -4.3459
2008-04-17 | 0.00049553 | 78 | -7.6099
2008-04-18 | 0 | 0
2008-04-19 | 0 | 0
2008-04-20 | 0 | 0
2008-04-21 | 0.015781 | 2484 | -4.149
2008-04-22 | 0.016657 | 2622 | -4.0949
2008-04-23 | 0.0072805 | 1146 | -4.9226
2008-04-24 | 0.021841 | 3438 | -3.8239
2008-04-25 | 0 | 0
2008-04-26 | 0 | 0
2008-04-27 | 0.021346 | 3360 | -3.8469
2008-04-28 | 0.0030113 | 474 | -5.8054
2008-04-29 | 0.025272 | 3978 | -3.6781
2008-04-30 | 0.077912 | 12264 | -2.5522
2008-05-01 | 0.041129 | 6474 | -3.191
2008-05-02 | 0.007776 | 1224 | -4.8567
2008-05-03 | 0.0048791 | 768 | -5.3228
2008-05-04 | 0.0020965 | 330 | -6.1675
2008-05-05 | 0.44407 | 69900 | -0.81177
2008-05-06 | 0.077112 | 12138 | -2.5625
2008-05-07 | 0.0016391 | 258 | -6.4136
2008-05-08 | 0.50087 | 78840 | -0.69142
2008-05-09 | 0 | 0
2008-05-10 | 0.00015247 | 24 | -8.7885
2008-05-11 | 0.021918 | 3450 | -3.8205
2008-05-12 | 0 | 0
2008-05-13 | 0.035106 | 5526 | -3.3494
2008-05-14 | 0.063008 | 9918 | -2.7645
2008-05-15 | 0 | 0
2008-05-16 | 0.030799 | 4848 | -3.4803
2008-05-17 | 0 | 0
2008-05-18 | 0.0058701 | 924 | -5.1379
2008-05-19 | 0 | 0
2008-05-20 | 0.89477 | 140844 | -0.11119
2008-05-21 | 0 | 0
2008-05-22 | 0.00068612 | 108 | -7.2845
2008-05-23 | 0 | 0
2008-05-24 | 0.01174 | 1848 | -4.4447
2008-05-25 | 0.013227 | 2082 | -4.3255
2008-05-26 | 0.014447 | 2274 | -4.2373
2008-05-27 | 0.01174 | 1848 | -4.4447
2008-05-28 | 0.00045741 | 72 | -7.6899
2008-05-29 | 0.17591 | 27690 | -1.7378
2008-05-30 | 0.070823 | 11148 | -2.6476
2008-05-31 | 0.013722 | 2160 | -4.2887
2008-06-01 | 0 | 0
2008-06-02 | 0.0024776 | 390 | -6.0004
2008-06-03 | 0.17511 | 27564 | -1.7423
2008-06-04 | 0.0024776 | 390 | -6.0004
2008-06-05 | 0.049096 | 7728 | -3.014
2008-06-06 | 0.013227 | 2082 | -4.3255
2008-06-07 | 0 | 0
2008-06-08 | 0.011359 | 1788 | -4.4777
2008-06-09 | 0 | 0
2008-06-10 | 0.0027445 | 432 | -5.8982
2008-06-11 | 0.0022489 | 354 | -6.0973
2008-06-12 | 0.23497 | 36985.8 | -1.4483
2008-06-13 | 0 | 0
2008-06-14 | 0 | 0
2008-06-15 | 0.005832 | 918 | -5.1444
2008-06-16 | 0 | 0
2008-06-17 | 0 | 0
2008-06-18 | 0.0062513 | 984 | -5.075
2008-06-19 | 0.54969 | 86526 | -0.59839
2008-06-20 | 0 | 0
2008-06-21 | 0.0078522 | 1236 | -4.847
2008-06-22 | 0 | 0
2008-06-23 | 0.010406 | 1638 | -4.5654
2008-06-24 | 0.0028207 | 444 | -5.8708
2008-06-25 | 0.014599 | 2298 | -4.2268
2008-06-26 | 0.0056795 | 894 | -5.1709
2008-06-27 | 0.78995 | 124344 | -0.23579
2008-06-28 | 0.046808 | 7368 | -3.0617
2008-06-29 | 0 | 0
2008-06-30 | 0.095751 | 15072 | -2.346
2008-07-01 | 0.03628 | 5796 | -3.3165
2008-07-02 | 0.039397 | 6294 | -3.2341
2008-07-03 | 0 | 0
2008-07-04 | 0.007962 | 1272 | -4.8331
2008-07-05 | 0.015736 | 2514 | -4.1518
2008-07-06 | 0 | 0
2008-07-07 | 0.3459 | 55260 | -1.0616
2008-07-08 | 0.013145 | 2100 | -4.3317
2008-07-09 | 0.011192 | 1788 | -4.4926
2008-07-10 | 0 | 0
2008-07-11 | 0.026966 | 4308 | -3.6132
2008-07-12 | 0.0086756 | 1386 | -4.7472
2008-07-13 | 0 | 0
2008-07-14 | 0 | 0
2008-07-15 | 0 | 0
2008-07-16 | 0 | 0
2008-07-17 | 0.0016149 | 258 | -6.4285
2008-07-18 | 0.0094643 | 1512 | -4.6602
2008-07-19 | 0.39784 | 63558 | -0.92171
2008-07-20 | 0.0098023 | 1566 | -4.6251
2008-07-21 | 0.0075489 | 1206 | -4.8864
2008-07-22 | 0.013708 | 2190 | -4.2898
2008-07-23 | 0.0041312 | 660 | -5.4892
2008-07-24 | 0.0090512 | 1446 | -4.7049
2008-07-25 | 0 | 0
2008-07-26 | 0.039322 | 6282 | -3.236
2008-07-27 | 0.027942 | 4464 | -3.5776
2008-07-28 | 0.01014 | 1620 | -4.5912
2008-07-29 | 0.002967 | 474 | -5.8202
2008-07-30 | 0 | 0
2008-07-31 | 0 | 0
2008-08-01 | 0.66476 | 106200 | -0.40834
2008-08-02 | 0 | 0
2008-08-03 | 0.011455 | 1830 | -4.4693
2008-08-04 | 0.01491 | 2382 | -4.2057
2008-08-05 | 0.0084127 | 1344 | -4.778
2008-08-06 | 0.0098774 | 1578 | -4.6175
2008-08-07 | 0.39852 | 63666 | -0.92001
2008-08-08 | 0.015924 | 2544 | -4.1399
2008-08-09 | 0 | 0
2008-08-10 | 0 | 0
2008-08-11 | 0.021558 | 3444 | -3.837
2008-08-12 | 0.0005258 | 84 | -7.5506
2008-08-13 | 0.07962 | 12720 | -2.5305
2008-08-14 | 0 | 0
2008-08-15 | 0 | 0
2008-08-16 | 0.011718 | 1872 | -4.4467
2008-08-17 | 0 | 0
2008-08-18 | 0.46492 | 74274 | -0.7659
2008-08-19 | 0.10486 | 16752 | -2.2551
2008-08-20 | 0.098925 | 15804 | -2.3134
2008-08-21 | 0.043078 | 6882 | -3.1448
2008-08-22 | 0.092352 | 14754 | -2.3821
2008-08-23 | 0.0075865 | 1212 | -4.8814
2008-08-24 | 0 | 0
2008-08-25 | 0 | 0
2008-08-26 | 0.011117 | 1776 | -4.4993
2008-08-27 | 0 | 0
2008-08-28 | 0.47855 | 76452 | -0.737
2008-08-29 | 0.0056335 | 900 | -5.179
2008-08-30 | 0.010779 | 1722 | -4.5302
2008-08-31 | 0 | 0
2008-09-01 | 0 | 0
2008-09-02 | 0.0061969 | 990 | -5.0837
2008-09-03 | 0.00022534 | 36 | -8.3979
2008-09-04 | 0 | 0
2008-09-05 | 0.118 | 18852 | -2.137
2008-09-06 | 0 | 0
2008-09-07 | 0 | 0
2008-09-08 | 0.014572 | 2328 | -4.2287
2008-09-09 | 0.031059 | 4962 | -3.4719
2008-09-10 | 0.022684 | 3624 | -3.7861
2008-09-11 | 0.12536 | 20028 | -2.0765
2008-09-12 | 0 | 0
2008-09-13 | 0 | 0
2008-09-14 | 0.043115 | 6888 | -3.1439
2008-09-15 | 3.1618 | 505122 | 1.1511
2008-09-16 | 0.099751 | 15936 | -2.3051
2008-09-17 | 0 | 0
2008-09-18 | 0.19402 | 30996 | -1.6398
2008-09-19 | 0.38248 | 61104 | -0.96108
2008-09-20 | 0.0163 | 2604 | -4.1166
2008-09-21 | 0 | 0
2008-09-22 | 0.016487 | 2634 | -4.1052
2008-09-23 | 0.0063471 | 1014 | -5.0598
2008-09-24 | 0.01168 | 1866 | -4.4499
2008-09-25 | 0.020206 | 3228 | -3.9018
2008-09-26 | 0.060128 | 9606 | -2.8113
2008-09-27 | 0.025726 | 4110 | -3.6602
2008-09-28 | 0.012957 | 2070 | -4.3461
2008-09-29 | 0.012844 | 2052 | -4.3548
2008-09-30 | 0 | 0
2008-10-01 | 0 | 0
2008-10-02 | 0 | 0
2008-10-03 | 0.25614 | 40920 | -1.362
2008-10-04 | 0 | 0
2008-10-05 | 0 | 0
2008-10-06 | 0.0046195 | 738 | -5.3775
2008-10-07 | 0.045669 | 7296 | -3.0863
2008-10-08 | 0.014647 | 2340 | -4.2235
2008-10-09 | 0.010629 | 1698 | -4.5442
2008-10-10 | 0.011042 | 1764 | -4.5061
2008-10-11 | 0 | 0
2008-10-12 | 0.009577 | 1530 | -4.6484
2008-10-13 | 0.49398 | 78918 | -0.70525
2008-10-14 | 0.018891 | 3018 | -3.9691
2008-10-15 | 0.016037 | 2562 | -4.1329
2008-10-16 | 0 | 0
2008-10-17 | 0 | 0
2008-10-18 | 0 | 0
2008-10-19 | 0 | 0
2008-10-20 | 0.0052955 | 846 | -5.2409
2008-10-21 | 0.023811 | 3804 | -3.7376
2008-10-22 | 0.42229 | 67464 | -0.86207
2008-10-23 | 0.64605 | 103212 | -0.43688
2008-10-24 | 0.018816 | 3006 | -3.973
2008-10-25 | 0 | 0
2008-10-26 | 0 | 0
2008-10-27 | 0.1645 | 26280 | -1.8049
2008-10-28 | 0 | 0
2008-10-29 | 0.012769 | 2040 | -4.3607
2008-10-30 | 0.073611 | 11760 | -2.609
2008-10-31 | 0.26752 | 42738 | -1.3186
2008-11-01 | 0.016976 | 2712 | -4.076
2008-11-02 | 0 | 0
2008-11-03 | 0.0062344 | 996 | -5.0777
2008-11-04 | 0.018591 | 2970 | -3.9851
2008-11-05 | 0.0016901 | 270 | -6.383
2008-11-06 | 0.060091 | 9600 | -2.8119
2008-11-07 | 0 | 0
2008-11-08 | 0.61999 | 99048 | -0.47806
2008-11-09 | 0 | 0
2008-11-10 | 0.3409 | 54462 | -1.0762
2008-11-11 | 0.31991 | 51108 | -1.1397
2008-11-12 | 0.12446 | 19884 | -2.0837
2008-11-13 | 0.0070607 | 1128 | -4.9532
2008-11-14 | 0.013746 | 2196 | -4.287
2008-11-15 | 0 | 0
2008-11-16 | 0.023097 | 3690 | -3.768
2008-11-17 | 0 | 0
2008-11-18 | 0.019267 | 3078 | -3.9494
2008-11-19 | 0.52527 | 83916 | -0.64384
2008-11-20 | 0.0040561 | 648 | -5.5075
2008-11-21 | 0.75557 | 120708 | -0.28029
2008-11-22 | 0 | 0
2008-11-23 | 0.5943 | 94944 | -0.52037
2008-11-24 | 0.25448 | 40656 | -1.3685
2008-11-25 | 0 | 0
2008-11-26 | 0 | 0
2008-11-27 | 0.010816 | 1728 | -4.5267
2008-11-28 | 0.017163 | 2742 | -4.065
2008-11-29 | 0.00082625 | 132 | -7.0986
2008-11-30 | 0 | 0
2008-12-01 | 0.2425 | 38742 | -1.4167
2008-12-02 | 0.034327 | 5484 | -3.3718
2008-12-03 | 0.014121 | 2256 | -4.2601
2008-12-04 | 0 | 0
2008-12-05 | 0.19781 | 31602 | -1.6204
2008-12-06 | 0.0086756 | 1386 | -4.7472
2008-12-07 | 0.0088258 | 1410 | -4.7301
2008-12-08 | 0.016337 | 2610 | -4.1143
2008-12-09 | 0.10114 | 16158 | -2.2912
2008-12-10 | 0.35803 | 57198 | -1.0271
2008-12-11 | 0.0048824 | 780 | -5.3221
2008-12-12 | 0.083113 | 13278 | -2.4876
2008-12-13 | 0.15642 | 24990 | -1.8552
2008-12-14 | 0 | 0
2008-12-15 | 0.019417 | 3102 | -3.9416
2008-12-16 | 0 | 0
2008-12-17 | 0 | 0
2008-12-18 | 0.0091263 | 1458 | -4.6966
2008-12-19 | 0.017201 | 2748 | -4.0628
2008-12-20 | 0.00041312 | 66 | -7.7918
2008-12-21 | 0 | 0
2008-12-22 | 0.00056335 | 90 | -7.4816
2008-12-23 | 0.2096 | 33486 | -1.5625
2008-12-24 | 0.003981 | 636 | -5.5262
2008-12-25 | 0 | 0
2008-12-26 | 0.45241 | 72276 | -0.79317
2008-12-27 | 0.85603 | 136758 | -0.15545
2008-12-28 | 0.0029294 | 468 | -5.8329
2008-12-29 | 0.063847 | 10200 | -2.7513
2008-12-30 | 0.022083 | 3528 | -3.8129
2008-12-31 | 0 | 0
2009-01-01 | 0.025877 | 4134 | -3.6544
2009-01-02 | 0 | 0
2009-01-03 | 0 | 0
2009-01-04 | 0.00090136 | 144 | -7.0116
2009-01-05 | 0.67212 | 107376 | -0.39732
2009-01-06 | 0.12844 | 20520 | -2.0523
2009-01-07 | 0.035341 | 5646 | -3.3427
2009-01-08 | 0.014647 | 2340 | -4.2235
2009-01-09 | 0.0049199 | 786 | -5.3145
2009-01-10 | 0 | 0
2009-01-11 | 0 | 0
2009-01-12 | 0.024187 | 3864 | -3.722
2009-01-13 | 0.030834 | 4926 | -3.4791
2009-01-14 | 0.051227 | 8184 | -2.9715
2009-01-15 | 0.063884 | 10206 | -2.7507
2009-01-16 | 0.02952 | 4716 | -3.5227
2009-01-17 | 0.0054457 | 870 | -5.2129
2009-01-18 | 0.0060466 | 966 | -5.1083
2009-01-19 | 0 | 0
2009-01-20 | 0.08071 | 12894 | -2.5169
2009-01-21 | 0.010065 | 1608 | -4.5987
2009-01-22 | 1.3869 | 221574 | 0.3271
2009-01-23 | 0.37016 | 59136 | -0.99382
2009-01-24 | 0.12773 | 20406 | -2.0578
2009-01-25 | 0.013821 | 2208 | -4.2816
2009-01-26 | 0.52106 | 83244 | -0.65188
2009-01-27 | 0.021107 | 3372 | -3.8582
2009-01-28 | 0.0071358 | 1140 | -4.9426
2009-01-29 | 0.051641 | 8250 | -2.9634
2009-01-30 | 0.056185 | 8976 | -2.8791
2009-01-31 | 0.011192 | 1788 | -4.4926
2009-02-01 | 0 | 0
2009-02-02 | 0.074625 | 11922 | -2.5953
2009-02-03 | 0.053293 | 8514 | -2.9319
2009-02-04 | 0.001014 | 162 | -6.8938
2009-02-05 | 0.019792 | 3162 | -3.9225
2009-02-06 | 0.16604 | 26526 | -1.7955
2009-02-07 | 0.03166 | 5058 | -3.4527
2009-02-08 | 0.087845 | 14034 | -2.4322
2009-02-09 | 0.0045819 | 732 | -5.3856
2009-02-10 | 0.022459 | 3588 | -3.7961
2009-02-11 | 0.011042 | 1764 | -4.5061
2009-02-12 | 0.29764 | 47550 | -1.2119
2009-02-13 | 0.0056711 | 906 | -5.1724
2009-02-14 | 0.0018027 | 288 | -6.3185
2009-02-15 | 0 | 0
2009-02-16 | 0.016525 | 2640 | -4.1029
2009-02-17 | 0.004657 | 744 | -5.3694
2009-02-18 | 0.010704 | 1710 | -4.5372
2009-02-19 | 0.0022534 | 360 | -6.0953
2009-02-20 | 0 | 0
2009-02-21 | 0.00056335 | 90 | -7.4816
2009-02-22 | 0 | 0
2009-02-23 | 0.040824 | 6522 | -3.1985
2009-02-24 | 0.026478 | 4230 | -3.6315
2009-02-25 | 0.0083001 | 1326 | -4.7915
2009-02-26 | 0.009239 | 1476 | -4.6843
2009-02-27 | 0.019079 | 3048 | -3.9592
2009-02-28 | 0.2511 | 40116 | -1.3819
2009-03-01 | 0.012957 | 2070 | -4.3461
2009-03-02 | 0.03151 | 5034 | -3.4574
2009-03-03 | 0.0025539 | 408 | -5.9701
2009-03-04 | 0.27 | 43134 | -1.3093
2009-03-05 | 0.070757 | 11304 | -2.6485
2009-03-06 | 0.0038684 | 618 | -5.5549
2009-03-07 | 0.012582 | 2010 | -4.3755
2009-03-08 | 0 | 0
2009-03-09 | 0 | 0
2009-03-10 | 0.0080747 | 1290 | -4.819
2009-03-11 | 0 | 0
2009-03-12 | 0.0065349 | 1044 | -5.0306
2009-03-13 | 0 | 0
2009-03-14 | 0.076991 | 12300 | -2.5641
2009-03-15 | 0.014985 | 2394 | -4.2007
2009-03-16 | 0.014497 | 2316 | -4.2338
2009-03-17 | 0.020318 | 3246 | -3.8962
2009-03-18 | 0 | 0
2009-03-19 | 0.0023285 | 372 | -6.0625
2009-03-20 | 0.012093 | 1932 | -4.4151
2009-03-21 | 0.032205 | 5145 | -3.4356
2009-03-22 | 0.04766 | 7614 | -3.0437
2009-03-23 | 0.0039059 | 624 | -5.5453
2009-03-24 | 0.021257 | 3396 | -3.8511
2009-03-25 | 0.00661 | 1056 | -5.0192
2009-03-26 | 0.21828 | 34872 | -1.522
2009-03-27 | 0.002629 | 420 | -5.9412
2009-03-28 | 0 | 0
2009-03-29 | 2.534 | 404820 | 0.92978
2009-03-30 | 0.0030045 | 480 | -5.8076
2009-03-31 | 0.0044317 | 708 | -5.419
2009-04-01 | 0.0056335 | 900 | -5.179
2009-04-02 | 0.0072485 | 1158 | -4.927
2009-04-03 | 0 | 0
2009-04-04 | 0.028919 | 4620 | -3.5433
2009-04-05 | 0 | 0
2009-04-06 | 0.0043941 | 702 | -5.4275
2009-04-07 | 0.06471 | 10338 | -2.7378
2009-04-08 | 0.24438 | 39042 | -1.409
2009-04-09 | 0.0049951 | 798 | -5.2993
2009-04-10 | 0.0035679 | 570 | -5.6358
2009-04-11 | 0.10944 | 17484 | -2.2124
2009-04-12 | 0.036505 | 5832 | -3.3103
2009-04-13 | 0.018553 | 2964 | -3.9871
2009-04-14 | 0.30072 | 48042 | -1.2016
2009-04-15 | 0.5193 | 82962 | -0.65528
2009-04-16 | 0 | 0
2009-04-17 | 0 | 0
2009-04-18 | 0 | 0
2009-04-19 | 0 | 0
2009-04-20 | 0.0034928 | 558 | -5.6571
2009-04-21 | 0 | 0
2009-04-22 | 0.031322 | 5004 | -3.4634
2009-04-23 | 0.25614 | 40920 | -1.362
2009-04-24 | 0.69074 | 110352 | -0.36998
2009-04-25 | 0 | 0
2009-04-26 | 0.32629 | 52128 | -1.12
2009-04-27 | 0 | 0
2009-04-28 | 0.055209 | 8820 | -2.8966
2009-04-29 | 0.050476 | 8064 | -2.9863
2009-04-30 | 0.14046 | 22440 | -1.9628
2009-05-01 | 0 | 0
2009-05-02 | 0.34064 | 54420 | -1.0769
2009-05-03 | 0 | 0
2009-05-04 | 0 | 0
2009-05-05 | 0 | 0
2009-05-06 | 0 | 0
2009-05-07 | 0.0033801 | 540 | -5.6898
2009-05-08 | 0.005258 | 840 | -5.248
2009-05-09 | 0 | 0
2009-05-10 | 0 | 0
2009-05-11 | 0.26526 | 42378 | -1.327
2009-05-12 | 0.14861 | 23742 | -1.9064
2009-05-13 | 0.015323 | 2448 | -4.1784
2009-05-14 | 0 | 0
2009-05-15 | 0.0014272 | 228 | -6.5521
2009-05-16 | 0.015398 | 2460 | -4.1735
2009-05-17 | 0.021633 | 3456 | -3.8335
2009-05-18 | 0.031247 | 4992 | -3.4658
2009-05-19 | 0.020468 | 3270 | -3.8889
2009-05-20 | 0.11515 | 18396 | -2.1615
2009-05-21 | 0.00011267 | 18 | -9.091
2009-05-22 | 0.011117 | 1776 | -4.4993
2009-05-23 | 0.22587 | 36084 | -1.4878
2009-05-24 | 0 | 0
2009-05-25 | 0.25569 | 40848 | -1.3638
2009-05-26 | 0.0063095 | 1008 | -5.0657
2009-05-27 | 0 | 0
2009-05-28 | 0.0031172 | 498 | -5.7708
2009-05-29 | 0.00078869 | 126 | -7.1451
2009-05-30 | 0.00067602 | 108 | -7.2993
2009-05-31 | 0 | 0
2009-06-01 | 0.010441 | 1668 | -4.562
2009-06-02 | 0.0089761 | 1434 | -4.7132
2009-06-03 | 0.014722 | 2352 | -4.2184
2009-06-04 | 0.0058589 | 936 | -5.1398
2009-06-05 | 0 | 0
2009-06-06 | 0.029294 | 4680 | -3.5304
2009-06-07 | 0 | 0
2009-06-08 | 0 | 0
2009-06-09 | 0.00041312 | 66 | -7.7918
2009-06-10 | 0.23477 | 37506 | -1.4492
2009-06-11 | 0.20465 | 32694 | -1.5865
2009-06-12 | 0.025464 | 4068 | -3.6705
2009-06-13 | 0 | 0
2009-06-14 | 0 | 0
2009-06-15 | 0.0030045 | 480 | -5.8076
2009-06-16 | 0.0066476 | 1062 | -5.0135
2009-06-17 | 0.0050326 | 804 | -5.2918
2009-06-18 | 0.1064 | 16998 | -2.2406
2009-06-19 | 0.0010891 | 174 | -6.8224
2009-06-20 | 0.2419 | 38646 | -1.4192
2009-06-21 | 1.9001 | 303552 | 0.64189
2009-06-22 | 0.009915 | 1584 | -4.6137
2009-06-23 | 0 | 0
2009-06-24 | 0.0064973 | 1038 | -5.0364
2009-06-25 | 0 | 0
2009-06-26 | 0.021783 | 3480 | -3.8266
2009-06-27 | 0.0032674 | 522 | -5.7237
2009-06-28 | 0 | 0
2009-06-29 | 0.38364 | 61290 | -0.95804
2009-06-30 | 0.049312 | 7878 | -3.0096
2009-07-01 | 0.028237 | 4602 | -3.5671
2009-07-02 | 0 | 0
2009-07-03 | 0 | 0
2009-07-04 | 0.00033133 | 54 | -8.0124
2009-07-05 | 0 | 0
2009-07-06 | 0.30026 | 48936 | -1.2031
2009-07-07 | 0 | 0
2009-07-08 | 0.00055221 | 90 | -7.5016
2009-07-09 | 1.1469 | 186930 | 0.1371
2009-07-10 | 0.025512 | 4158 | -3.6686
2009-07-11 | 0.015793 | 2574 | -4.1482
2009-07-12 | 0 | 0
2009-07-13 | 0.0038287 | 624 | -5.5652
2009-07-14 | 0.060191 | 9810 | -2.8102
2009-07-15 | 0 | 0
2009-07-16 | 0.034458 | 5616 | -3.368
2009-07-17 | 0.015683 | 2556 | -4.1552
2009-07-18 | 0.044288 | 7218 | -3.1171
2009-07-19 | 0 | 0
2009-07-20 | 0.0015462 | 252 | -6.472
2009-07-21 | 0.10753 | 17526 | -2.2299
2009-07-22 | 0.01156 | 1884 | -4.4602
2009-07-23 | 0.25321 | 41268 | -1.3735
2009-07-24 | 0 | 0
2009-07-25 | 0 | 0
2009-07-26 | 0.0096085 | 1566 | -4.6451
2009-07-27 | 0.0091299 | 1488 | -4.6962
2009-07-28 | 0 | 0
2009-07-29 | 0.0050435 | 822 | -5.2896
2009-07-30 | 0.066634 | 10860 | -2.7085
2009-07-31 | 0 | 0
2009-08-01 | 0.048595 | 7920 | -3.0242
2009-08-02 | 0 | 0
2009-08-03 | 0.032065 | 5226 | -3.44
2009-08-04 | 0 | 0
2009-08-05 | 0.41245 | 67221.6 | -0.88564
2009-08-06 | 0.34569 | 56340 | -1.0622
2009-08-07 | 0.021095 | 3438 | -3.8587
2009-08-08 | 0.026138 | 4260 | -3.6444
2009-08-09 | 0.052792 | 8604 | -2.9414
2009-08-10 | 0.013842 | 2256 | -4.28
2009-08-11 | 0.033096 | 5394 | -3.4083
2009-08-12 | 0.027795 | 4530 | -3.5829
2009-08-13 | 0.011412 | 1860 | -4.4731
2009-08-14 | 0.036336 | 5922 | -3.315
2009-08-15 | 0.0042336 | 690 | -5.4647
2009-08-16 | 0.010934 | 1782 | -4.5159
2009-08-17 | 0.013805 | 2250 | -4.2827
2009-08-18 | 0.044398 | 7236 | -3.1146
2009-08-19 | 0.052092 | 8490 | -2.9547
2009-08-20 | 0.57239 | 93288 | -0.55794
2009-08-21 | 0.77457 | 126240 | -0.25545
2009-08-22 | 0.020837 | 3396 | -3.871
2009-08-23 | 0 | 0
2009-08-24 | 0 | 0
2009-08-25 | 3.1343 | 510822 | 1.1424
2009-08-26 | 0.65478 | 106716 | -0.42346
2009-08-27 | 0.027022 | 4404 | -3.6111
2009-08-28 | 0.010492 | 1710 | -4.5571
2009-08-29 | 0.028237 | 4602 | -3.5671
2009-08-30 | 0 | 0
2009-08-31 | 0.00073628 | 120 | -7.2139
2009-09-01 | 0.0034237 | 558 | -5.677
2009-09-02 | 0.024371 | 3972 | -3.7144
2009-09-03 | 0.22961 | 37422 | -1.4714
2009-09-04 | 0.072819 | 11868 | -2.6198
2009-09-05 | 0.044582 | 7266 | -3.1104
2009-09-06 | 0 | 0
2009-09-07 | 0.92249 | 150348 | -0.080678
2009-09-08 | 0 | 0
2009-09-09 | 0 | 0
2009-09-10 | 0.28259 | 46056 | -1.2638
2009-09-11 | 0.01653 | 2694 | -4.1026
2009-09-12 | 0.0071788 | 1170 | -4.9366
2009-09-13 | 0 | 0
2009-09-14 | 0.2644 | 43092 | -1.3303
2009-09-15 | 0.027647 | 4506 | -3.5882
2009-09-16 | 0.0032028 | 522 | -5.7437
2009-09-17 | 0 | 0
2009-09-18 | 0.042889 | 6990 | -3.1492
2009-09-19 | 0.011965 | 1950 | -4.4258
2009-09-20 | 0.024629 | 4014 | -3.7038
2009-09-21 | 0.005743 | 936 | -5.1598
2009-09-22 | 0.60702 | 98932.8 | -0.49919
2009-09-23 | 0.062142 | 10128 | -2.7783
2009-09-24 | 0.0030924 | 504 | -5.7788
2009-09-25 | 0.011486 | 1872 | -4.4666
2009-09-26 | 0 | 0
2009-09-27 | 0 | 0
2009-09-28 | 0.00080991 | 132 | -7.1186
2009-09-29 | 0.0036814 | 600 | -5.6045
2009-09-30 | 0.00073628 | 120 | -7.2139
2009-10-01 | 0.50811 | 82812 | -0.67706
2009-10-02 | 0.00018407 | 30 | -8.6002
2009-10-03 | 0.015536 | 2532 | -4.1646
2009-10-04 | 0 | 0
2009-10-05 | 0.012848 | 2094 | -4.3546
2009-10-06 | 0.0047122 | 768 | -5.3576
2009-10-07 | 0 | 0
2009-10-08 | 0.38633 | 62964 | -0.95107
2009-10-09 | 0 | 0
2009-10-10 | 0.0054485 | 888 | -5.2124
2009-10-11 | 0 | 0
2009-10-12 | 0.44185 | 72012.6 | -0.81679
2009-10-13 | 0.068732 | 11202 | -2.6775
2009-10-14 | 0.55859 | 91039.8 | -0.58233
2009-10-15 | 0.014799 | 2412 | -4.2132
2009-10-16 | 0.0024666 | 402 | -6.0049
2009-10-17 | 0.0032765 | 534 | -5.721
2009-10-18 | 0 | 0
2009-10-19 | 0.0010676 | 174 | -6.8423
2009-10-20 | 0 | 0
2009-10-21 | 0.0043809 | 714 | -5.4305
2009-10-22 | 0 | 0
2009-10-23 | 0.0016198 | 264 | -6.4254
2009-10-24 | 0.011449 | 1866 | -4.4698
2009-10-25 | 0.27081 | 44136 | -1.3064
2009-10-26 | 0 | 0
2009-10-27 | 0.0097926 | 1596 | -4.6261
2009-10-28 | 0.003166 | 516 | -5.7553
2009-10-29 | 0 | 0
2009-10-30 | 0.02404 | 3918 | -3.728
2009-10-31 | 0.0078414 | 1278 | -4.8483
2009-11-01 | 0.42314 | 68964 | -0.86005
2009-11-02 | 0.94542 | 154084.8 | -0.056127
2009-11-03 | 0.0082464 | 1344 | -4.798
2009-11-04 | 0.0088354 | 1440 | -4.729
2009-11-05 | 0 | 0
2009-11-06 | 0.012038 | 1962 | -4.4197
2009-11-07 | 0.0047858 | 780 | -5.3421
2009-11-08 | 0 | 0
2009-11-09 | 0.0098294 | 1602 | -4.6224
2009-11-10 | 0 | 0
2009-11-11 | 0 | 0
2009-11-12 | 0.0049699 | 810 | -5.3044
2009-11-13 | 0.0055221 | 900 | -5.199
2009-11-14 | 0 | 0
2009-11-15 | 0.0075469 | 1230 | -4.8866
2009-11-16 | 0.044913 | 7320 | -3.103
2009-11-17 | 0.08644 | 14088 | -2.4483
2009-11-18 | 0.0050804 | 828 | -5.2824
2009-11-19 | 0 | 0
2009-11-20 | 0.38625 | 62952 | -0.95126
2009-11-21 | 0.016014 | 2610 | -4.1343
2009-11-22 | 0.027427 | 4470 | -3.5962
2009-11-23 | 0.01918 | 3126 | -3.9539
2009-11-24 | 0.015462 | 2520 | -4.1694
2009-11-25 | 0.011192 | 1824 | -4.4926
2009-11-26 | 0.065345 | 10650 | -2.7281
2009-11-27 | 0.043294 | 7056 | -3.1398
2009-11-28 | 0.75528 | 123096 | -0.28067
2009-11-29 | 0.096527 | 15732 | -2.3379
2009-11-30 | 0.027058 | 4410 | -3.6098
2009-12-01 | 0.0084673 | 1380 | -4.7715
2009-12-02 | 0.014799 | 2412 | -4.2132
2009-12-03 | 0.04241 | 6912 | -3.1604
2009-12-04 | 0 | 0
2009-12-05 | 0 | 0
2009-12-06 | 0.036041 | 5874 | -3.3231
2009-12-07 | 0.012922 | 2106 | -4.3488
2009-12-08 | 0.036225 | 5904 | -3.318
2009-12-09 | 0.042741 | 6966 | -3.1526
2009-12-10 | 0.0086513 | 1410 | -4.75
2009-12-11 | 0.0059639 | 972 | -5.122
2009-12-12 | 0 | 0
2009-12-13 | 0.32967 | 53730 | -1.1097
2009-12-14 | 0 | 0
2009-12-15 | 0.034495 | 5622 | -3.3669
2009-12-16 | 0.023119 | 3768 | -3.7671
2009-12-17 | 0.071677 | 11682 | -2.6356
2009-12-18 | 0.017487 | 2850 | -4.0463
2009-12-19 | 0 | 0
2009-12-20 | 0.020469 | 3336 | -3.8889
2009-12-21 | 0 | 0
2009-12-22 | 0 | 0
2009-12-23 | 0.1149 | 18726 | -2.1637
2009-12-24 | 0 | 0
2009-12-25 | 0.031955 | 5208 | -3.4434
2009-12-26 | 0.00080991 | 132 | -7.1186
2009-12-27 | 0 | 0
2009-12-28 | 0.15057 | 24540 | -1.8933
2009-12-29 | 0 | 0
2009-12-30 | 0.1671 | 27234 | -1.7892
2009-12-31 | 0 | 0
2010-01-01 | 0.0060007 | 978 | -5.1159
2010-01-02 | 0.13761 | 22428 | -1.9833
2010-01-03 | 1.0266 | 167322 | 0.02629
2010-01-04 | 0.036078 | 5880 | -3.3221
2010-01-05 | 0.00069947 | 114 | -7.2652
2010-01-06 | 0 | 0
2010-01-07 | 0.0097926 | 1596 | -4.6261
2010-01-08 | 0.014689 | 2394 | -4.2207
2010-01-09 | 0.25409 | 41412 | -1.3701
2010-01-10 | 0.14254 | 23232 | -1.9481
2010-01-11 | 0.039097 | 6372 | -3.2417
2010-01-12 | 0.12171 | 19836 | -2.1061
2010-01-13 | 0.011523 | 1878 | -4.4634
2010-01-14 | 0.0042704 | 696 | -5.456
2010-01-15 | 0.019843 | 3234 | -3.9199
2010-01-16 | 0.094833 | 15456 | -2.3556
2010-01-17 | 0.020285 | 3306 | -3.8979
2010-01-18 | 0.0076942 | 1254 | -4.8673
2010-01-19 | 0.020947 | 3414 | -3.8657
2010-01-20 | 0.011928 | 1944 | -4.4289
2010-01-21 | 0 | 0
2010-01-22 | 0.025807 | 4206 | -3.6571
2010-01-23 | 0.05062 | 8250 | -2.9834
2010-01-24 | 0.20767 | 33846 | -1.5718
2010-01-25 | 0.00029451 | 48 | -8.1302
2010-01-26 | 0.24566 | 40038 | -1.4038
2010-01-27 | 0 | 0
2010-01-28 | 0.020137 | 3282 | -3.9052
2010-01-29 | 0.11493 | 18732 | -2.1634
2010-01-30 | 0.0062216 | 1014 | -5.0797
2010-01-31 | 0.0025034 | 408 | -5.9901
2010-02-01 | 0.036078 | 5880 | -3.3221
2010-02-02 | 0.027058 | 4410 | -3.6098
2010-02-03 | 0.1558 | 25392 | -1.8592
2010-02-04 | 0.035599 | 5802 | -3.3354
2010-02-05 | 0.026101 | 4254 | -3.6458
2010-02-06 | 0 | 0
2010-02-07 | 0.031918 | 5202 | -3.4446
2010-02-08 | 0.015241 | 2484 | -4.1838
2010-02-09 | 0.021315 | 3474 | -3.8483
2010-02-10 | 0.65242 | 106332 | -0.42706
2010-02-11 | 0.45351 | 73914 | -0.79073
2010-02-12 | 0.039502 | 6438 | -3.2314
2010-02-13 | 0.008909 | 1452 | -4.7207
2010-02-14 | 0.096601 | 15744 | -2.3372
2010-02-15 | 0.12344 | 20118 | -2.092
2010-02-16 | 0 | 0
2010-02-17 | 0.00029451 | 48 | -8.1302
2010-02-18 | 0.014799 | 2412 | -4.2132
2010-02-19 | 0.014358 | 2340 | -4.2435
2010-02-20 | 0.019254 | 3138 | -3.95
2010-02-21 | 0.2729 | 44478 | -1.2986
2010-02-22 | 0.0018775 | 306 | -6.2778
2010-02-23 | 0 | 0
2010-02-24 | 0.041085 | 6696 | -3.1921
2010-02-25 | 0.11928 | 19440 | -2.1263
2010-02-26 | 0.046349 | 7554 | -3.0716
2010-02-27 | 0.090968 | 14826 | -2.3972
2010-02-28 | 0.053565 | 8730 | -2.9269
2010-03-01 | 0.036777 | 5994 | -3.3029
2010-03-02 | 0.19114 | 31152 | -1.6548
2010-03-03 | 0.011486 | 1872 | -4.4666
2010-03-04 | 0 | 0
2010-03-05 | 0.0064057 | 1044 | -5.0506
2010-03-06 | 0.010639 | 1734 | -4.5432
2010-03-07 | 0.62139 | 101274 | -0.4758
2010-03-08 | 0.042815 | 6978 | -3.1509
2010-03-09 | 0.0069947 | 1140 | -4.9626
2010-03-10 | 0.038729 | 6312 | -3.2512
2010-03-11 | 0.0032397 | 528 | -5.7323
2010-03-12 | 0.047858 | 7800 | -3.0395
2010-03-13 | 0.019327 | 3150 | -3.9462
2010-03-14 | 0.013584 | 2214 | -4.2988
2010-03-15 | 0.029415 | 4794 | -3.5263
2010-03-16 | 0.043551 | 7098 | -3.1338
2010-03-17 | 0 | 0
2010-03-18 | 0.038324 | 6246 | -3.2617
2010-03-19 | 0.23532 | 38352 | -1.4468
2010-03-20 | 0 | 0
2010-03-21 | 0.02566 | 4182 | -3.6628
2010-03-22 | 0.044545 | 7260 | -3.1113
2010-03-23 | 0.012001 | 1956 | -4.4227
2010-03-24 | 0.013658 | 2226 | -4.2934
2010-03-25 | 0.0040496 | 660 | -5.5091
2010-03-26 | 0 | 0
2010-03-27 | 0.00033133 | 54 | -8.0124
2010-03-28 | 0 | 0
2010-03-29 | 0.056436 | 9198 | -2.8746
2010-03-30 | 0.22008 | 35868 | -1.5138
2010-03-31 | 0.53804 | 87690 | -0.61982
2010-04-01 | 0.0076205 | 1242 | -4.8769
2010-04-02 | 0.029599 | 4824 | -3.52
2010-04-03 | 0 | 0
2010-04-04 | 0 | 0
2010-04-05 | 0 | 0
2010-04-06 | 0.00018407 | 30 | -8.6002
2010-04-07 | 0 | 0
2010-04-08 | 0.010013 | 1632 | -4.6038
2010-04-09 | 0.025365 | 4134 | -3.6744
2010-04-10 | 0 | 0
2010-04-11 | 0.04749 | 7740 | -3.0472
2010-04-12 | 0 | 0
2010-04-13 | 0.00022089 | 36 | -8.4179
2010-04-14 | 0 | 0
2010-04-15 | 0.08563 | 13956 | -2.4577
2010-04-16 | 0.0061848 | 1008 | -5.0857
2010-04-17 | 0.0010308 | 168 | -6.8774
2010-04-18 | 0 | 0
2010-04-19 | 0 | 0
2010-04-20 | 0.0092404 | 1506 | -4.6842
2010-04-21 | 0 | 0
2010-04-22 | 0.00033133 | 54 | -8.0124
2010-04-23 | 0.00033133 | 54 | -8.0124
2010-04-24 | 0.00069947 | 114 | -7.2652
2010-04-25 | 0 | 0
2010-04-26 | 0 | 0
2010-04-27 | 0.0002577 | 42 | -8.2637
2010-04-28 | 0.0022089 | 360 | -6.1153
2010-04-29 | 0.015425 | 2514 | -4.1718
2010-04-30 | 0.0072524 | 1182 | -4.9264
2010-05-01 | 0 | 0
2010-05-02 | 0.0092772 | 1512 | -4.6802
2010-05-03 | 0 | 0
2010-05-04 | 0.091115 | 14850 | -2.3956
2010-05-05 | 0 | 0
2010-05-06 | 0.19541 | 31848 | -1.6327
2010-05-07 | 0 | 0
2010-05-08 | 0.011891 | 1938 | -4.432
2010-05-09 | 0.0025034 | 408 | -5.9901
2010-05-10 | 0.016456 | 2682 | -4.1071
2010-05-11 | 0.28248 | 46038 | -1.2642
2010-05-12 | 0 | 0
2010-05-13 | 0.55004 | 89646 | -0.59776
2010-05-14 | 0.046901 | 7644 | -3.0597
2010-05-15 | 0.0054485 | 888 | -5.2124
2010-05-16 | 0.10256 | 16716 | -2.2773
2010-05-17 | 0 | 0
2010-05-18 | 0.021923 | 3573 | -3.8202
2010-05-19 | 0 | 0
2010-05-20 | 0 | 0
2010-05-21 | 0.036299 | 5916 | -3.316
2010-05-22 | 0 | 0
2010-05-23 | 0.058461 | 9528 | -2.8394
2010-05-24 | 0.040385 | 6582 | -3.2093
2010-05-25 | 0.17527 | 28566 | -1.7414
2010-05-26 | 0 | 0
2010-05-27 | 0.32829 | 53505 | -1.1139
2010-05-28 | 0.00022089 | 36 | -8.4179
2010-05-29 | 0.031734 | 5172 | -3.4504
2010-05-30 | 0.030924 | 5040 | -3.4762
2010-05-31 | 0.075911 | 12372 | -2.5782
2010-06-01 | 0.0050435 | 822 | -5.2896
2010-06-02 | 0 | 0
2010-06-03 | 0.030114 | 4908 | -3.5028
2010-06-04 | 0.016125 | 2628 | -4.1274
2010-06-05 | 0 | 0
2010-06-06 | 0.0046386 | 756 | -5.3733
2010-06-07 | 0 | 0
2010-06-08 | 0.028936 | 4716 | -3.5427
2010-06-09 | 0.0055958 | 912 | -5.1857
2010-06-10 | 0.13724 | 22368 | -1.986
2010-06-11 | 1.2747 | 207750 | 0.2427
2010-06-12 | 0.021095 | 3438 | -3.8587
2010-06-13 | 0 | 0
2010-06-14 | 0.0062216 | 1014 | -5.0797
2010-06-15 | 0 | 0
2010-06-16 | 0.034532 | 5628 | -3.3659
2010-06-17 | 0.14225 | 23184 | -1.9502
2010-06-18 | 0.0007731 | 126 | -7.1651
2010-06-19 | 0 | 0
2010-06-20 | 0 | 0
2010-06-21 | 0.0055589 | 906 | -5.1923
2010-06-22 | 0.024702 | 4026 | -3.7009
2010-06-23 | 0.066707 | 10872 | -2.7074
2010-06-24 | 0.050141 | 8172 | -2.9929
2010-06-25 | 0.5136 | 83706 | -0.66632
2010-06-26 | 0 | 0
2010-06-27 | 0.0080255 | 1308 | -4.8251
2010-06-28 | 0.0040127 | 654 | -5.5183
2010-06-29 | 0 | 0
2010-06-30 | 0.086771 | 14142 | -2.4445
2010-07-01 | 0.00053919 | 90 | -7.5255
2010-07-02 | 0.0058591 | 978 | -5.1398
2010-07-03 | 0.19335 | 32274 | -1.6432
2010-07-04 | 0.37405 | 62436 | -0.98336
2010-07-05 | 0.12887 | 21510 | -2.049
2010-07-06 | 0.024299 | 4056 | -3.7173
2010-07-07 | 0.010532 | 1758 | -4.5533
2010-07-08 | 0.0045292 | 756 | -5.3972
2010-07-09 | 0.01614 | 2694 | -4.1265
2010-07-10 | 0.0050324 | 840 | -5.2919
2010-07-11 | 0.0047808 | 798 | -5.3432
2010-07-12 | 0.28106 | 46914 | -1.2692
2010-07-13 | 0.15058 | 25134 | -1.8933
2010-07-14 | 0.34355 | 57345 | -1.0684
2010-07-15 | 0.021424 | 3576 | -3.8433
2010-07-16 | 0.021747 | 3630 | -3.8283
2010-07-17 | 0.015457 | 2580 | -4.1697
2010-07-18 | 0.016894 | 2820 | -4.0808
2010-07-19 | 0.23958 | 39990 | -1.4289
2010-07-20 | 0.025701 | 4290 | -3.6612
2010-07-21 | 0 | 0
2010-07-22 | 0 | 0
2010-07-23 | 0.019626 | 3276 | -3.9309
2010-07-24 | 0.074264 | 12396 | -2.6001
2010-07-25 | 0.027391 | 4572 | -3.5976
2010-07-26 | 0 | 0
2010-07-27 | 0.017254 | 2880 | -4.0597
2010-07-28 | 0 | 0
2010-07-29 | 0 | 0
2010-07-30 | 0.0011143 | 186 | -6.7995
2010-07-31 | 0 | 0
2010-08-01 | 0 | 0
2010-08-02 | 0.11255 | 18786 | -2.1844
2010-08-03 | 0.10147 | 16938 | -2.2879
2010-08-04 | 0 | 0
2010-08-05 | 0.066787 | 11148 | -2.7062
2010-08-06 | 0.053092 | 8862 | -2.9357
2010-08-07 | 0 | 0
2010-08-08 | 0.0053559 | 894 | -5.2296
2010-08-09 | 0.0082316 | 1374 | -4.7998
2010-08-10 | 0.52176 | 87091.2 | -0.65055
2010-08-11 | 0.020777 | 3468 | -3.8739
2010-08-12 | 0.043243 | 7218 | -3.1409
2010-08-13 | 0.066356 | 11076 | -2.7127
2010-08-14 | 0 | 0
2010-08-15 | 0.4678 | 78084 | -0.75972
2010-08-16 | 0.018224 | 3042 | -4.005
2010-08-17 | 0.0012581 | 210 | -6.6782
2010-08-18 | 0.016823 | 2808 | -4.085
2010-08-19 | 0.11161 | 18630 | -2.1927
2010-08-20 | 0.34468 | 57534 | -1.0651
2010-08-21 | 0.025162 | 4200 | -3.6824
2010-08-22 | 0.020273 | 3384 | -3.8984
2010-08-23 | 0.27885 | 46545 | -1.2771
2010-08-24 | 0 | 0
2010-08-25 | 0.83484 | 139350 | -0.18052
2010-08-26 | 0.0087348 | 1458 | -4.7404
2010-08-27 | 0 | 0
2010-08-28 | 0.061611 | 10284 | -2.7869
2010-08-29 | 0 | 0
2010-08-30 | 0.024659 | 4116 | -3.7026
2010-08-31 | 0.0036665 | 612 | -5.6085
2010-09-01 | 0.013444 | 2244 | -4.3092
2010-09-02 | 0.0097413 | 1626 | -4.6314
2010-09-03 | 0 | 0
2010-09-04 | 1.7132 | 285963 | 0.53836
2010-09-05 | 0.54649 | 91219.2 | -0.60424
2010-09-06 | 0.024191 | 4038 | -3.7218
2010-09-07 | 0.0020848 | 348 | -6.1731
2010-09-08 | 0.00046729 | 78 | -7.6686
2010-09-09 | 0.66722 | 111372 | -0.40463
2010-09-10 | 0.058196 | 9714 | -2.8439
2010-09-11 | 0.016463 | 2748 | -4.1066
2010-09-12 | 0 | 0
2010-09-13 | 0.019339 | 3228 | -3.9456
2010-09-14 | 0 | 0
2010-09-15 | 0.014091 | 2352 | -4.2622
2010-09-16 | 0.057405 | 9582 | -2.8576
2010-09-17 | 0.69955 | 116767.8 | -0.35732
2010-09-18 | 0.044609 | 7446 | -3.1098
2010-09-19 | 0 | 0
2010-09-20 | 0.012653 | 2112 | -4.3699
2010-09-21 | 0.0097413 | 1626 | -4.6314
2010-09-22 | 0.0098851 | 1650 | -4.6167
2010-09-23 | 0.0017973 | 300 | -6.3215
2010-09-24 | 0 | 0
2010-09-25 | 0.22782 | 38028 | -1.4792
2010-09-26 | 0 | 0
2010-09-27 | 0 | 0
2010-09-28 | 0.011467 | 1914 | -4.4683
2010-09-29 | 0.027175 | 4536 | -3.6055
2010-09-30 | 0.0041697 | 696 | -5.4799
2010-10-01 | 0.080446 | 13428 | -2.5202
2010-10-02 | 0.0042416 | 708 | -5.4628
2010-10-03 | 0 | 0
2010-10-04 | 0 | 0
2010-10-05 | 0.03821 | 6378 | -3.2647
2010-10-06 | 0.035766 | 5970 | -3.3308
2010-10-07 | 0.04486 | 7488 | -3.1042
2010-10-08 | 0 | 0
2010-10-09 | 0 | 0
2010-10-10 | 0 | 0
2010-10-11 | 0.015457 | 2580 | -4.1697
2010-10-12 | 0.016499 | 2754 | -4.1045
2010-10-13 | 0.0051043 | 852 | -5.2777
2010-10-14 | 0.035119 | 5862 | -3.349
2010-10-15 | 0.60171 | 100437 | -0.50798
2010-10-16 | 0.2848 | 47538 | -1.256
2010-10-17 | 0.0061467 | 1026 | -5.0918
2010-10-18 | 0 | 0
2010-10-19 | 0 | 0
2010-10-20 | 0.033537 | 5598 | -3.3951
2010-10-21 | 0.0079799 | 1332 | -4.8308
2010-10-22 | 0 | 0
2010-10-23 | 0.67355 | 112428 | -0.39519
2010-10-24 | 0 | 0
2010-10-25 | 0.048706 | 8130 | -3.0219
2010-10-26 | 0 | 0
2010-10-27 | 0.025701 | 4290 | -3.6612
2010-10-28 | 0 | 0
2010-10-29 | 0.0090224 | 1506 | -4.708
2010-10-30 | 0.0024084 | 402 | -6.0288
2010-10-31 | 0 | 0
2010-11-01 | 0 | 0
2010-11-02 | 0.015313 | 2556 | -4.1791
2010-11-03 | 0.027822 | 4644 | -3.5819
2010-11-04 | 0.0094178 | 1572 | -4.6652
2010-11-05 | 0.2917 | 48690 | -1.232
2010-11-06 | 0 | 0
2010-11-07 | 0 | 0
2010-11-08 | 0.050072 | 8358 | -2.9943
2010-11-09 | 0.044069 | 7356 | -3.122
2010-11-10 | 0.015924 | 2658 | -4.1399
2010-11-11 | 0.023221 | 3876 | -3.7627
2010-11-12 | 0.018296 | 3054 | -4.0011
2010-11-13 | 0.00532 | 888 | -5.2363
2010-11-14 | 0.0065781 | 1098 | -5.024
2010-11-15 | 0 | 0
2010-11-16 | 0.012689 | 2118 | -4.367
2010-11-17 | 0.005284 | 882 | -5.2431
2010-11-18 | 0.0090224 | 1506 | -4.708
2010-11-19 | 0.019806 | 3306 | -3.9218
2010-11-20 | 0.0086989 | 1452 | -4.7446
2010-11-21 | 0.58879 | 98280 | -0.52969
2010-11-22 | 0 | 0
2010-11-23 | 0.91661 | 153000 | -0.087068
2010-11-24 | 0 | 0
2010-11-25 | 0 | 0
2010-11-26 | 0.15243 | 25443 | -1.8811
2010-11-27 | 0.033789 | 5640 | -3.3876
2010-11-28 | 0.0070454 | 1176 | -4.9554
2010-11-29 | 0.14709 | 24552 | -1.9167
2010-11-30 | 0.0021567 | 360 | -6.1392
2010-12-01 | 0.025126 | 4194 | -3.6839
2010-12-02 | 0.13138 | 21930 | -2.0297
2010-12-03 | 0.25741 | 42966 | -1.3571
2010-12-04 | 1.8252 | 304657.2 | 0.60168
2010-12-05 | 0.033465 | 5586 | -3.3972
2010-12-06 | 1.3441 | 224353.8 | 0.29572
2010-12-07 | 0.0044573 | 744 | -5.4132
2010-12-08 | 1.4522 | 242399.82 | 0.37308
2010-12-09 | 0.38153 | 63684 | -0.96357
2010-12-10 | 0.21062 | 35155.8 | -1.5577
2010-12-11 | 0 | 0
2010-12-12 | 0.077463 | 12930 | -2.558
2010-12-13 | 0.019842 | 3312 | -3.92
2010-12-14 | 0.08972 | 14976 | -2.4111
2010-12-15 | 0.049965 | 8340 | -2.9964
2010-12-16 | 0.03839 | 6408 | -3.26
2010-12-17 | 0.025701 | 4290 | -3.6612
2010-12-18 | 0.047269 | 7890 | -3.0519
2010-12-19 | 0.02944 | 4914 | -3.5254
2010-12-20 | 0.0069016 | 1152 | -4.976
2010-12-21 | 0 | 0
2010-12-22 | 0.12588 | 21012 | -2.0724
2010-12-23 | 0.24203 | 40399.8 | -1.4187
2010-12-24 | 0.060029 | 10020 | -2.8129
2010-12-25 | 0.26102 | 43569 | -1.3432
2010-12-26 | 0.006614 | 1104 | -5.0186
2010-12-27 | 0.018548 | 3096 | -3.9874
2010-12-28 | 0.049569 | 8274 | -3.0044
2010-12-29 | 0.013228 | 2208 | -4.3254
2010-12-30 | 0 | 0
2010-12-31 | 0.22617 | 37752 | -1.4865
2011-01-01 | 0.012078 | 2016 | -4.4164
2011-01-02 | 0.2018 | 33684 | -1.6005
2011-01-03 | 0.0089505 | 1494 | -4.716
2011-01-04 | 0.019159 | 3198 | -3.955
2011-01-05 | 0.0068656 | 1146 | -4.9812
2011-01-06 | 0.024767 | 4134 | -3.6983
2011-01-07 | 0.075809 | 12654 | -2.5795
2011-01-08 | 0.00025162 | 42 | -8.2876
2011-01-09 | 0.053954 | 9006 | -2.9196
2011-01-10 | 0.08228 | 13734 | -2.4976
2011-01-11 | 0.043998 | 7344 | -3.1236
2011-01-12 | 0.00025162 | 42 | -8.2876
2011-01-13 | 0.22394 | 37380 | -1.4964
2011-01-14 | 0.0037384 | 624 | -5.5891
2011-01-15 | 0.27693 | 46224 | -1.284
2011-01-16 | 0.0085551 | 1428 | -4.7612
2011-01-17 | 0.0094897 | 1584 | -4.6576
2011-01-18 | 0.047772 | 7974 | -3.0413
2011-01-19 | 0.0008627 | 144 | -7.0554
2011-01-20 | 0 | 0
2011-01-21 | 1.4496 | 241962 | 0.37128
2011-01-22 | 0.47562 | 79389 | -0.74315
2011-01-23 | 0.80193 | 133857.6 | -0.22073
2011-01-24 | 0.007297 | 1218 | -4.9203
2011-01-25 | 0 | 0
2011-01-26 | 0 | 0
2011-01-27 | 0.52571 | 87750 | -0.64301
2011-01-28 | 0.21143 | 35290.8 | -1.5539
2011-01-29 | 0 | 0
2011-01-30 | 0.061431 | 10254 | -2.7898
2011-01-31 | 0.37333 | 62316 | -0.98529
2011-02-01 | 0.80065 | 133644 | -0.22233
2011-02-02 | 1.0795 | 180186 | 0.076484
2011-02-03 | 0.65267 | 108942 | -0.42669
2011-02-04 | 1.7847 | 297894 | 0.57923
2011-02-05 | 1.674 | 279415.2 | 0.51519
2011-02-06 | 0.29537 | 49302 | -1.2195
2011-02-07 | 0.12049 | 20112 | -2.1162
2011-02-08 | 0.021927 | 3660 | -3.82
2011-02-09 | 0.1128 | 18828 | -2.1822
2011-02-10 | 0.009274 | 1548 | -4.6805
2011-02-11 | 0 | 0
2011-02-12 | 0 | 0
2011-02-13 | 0.0032351 | 540 | -5.7337
2011-02-14 | 0.0067578 | 1128 | -4.9971
2011-02-15 | 0.0013659 | 228 | -6.5959
2011-02-16 | 0.0058951 | 984 | -5.1336
2011-02-17 | 0.0076564 | 1278 | -4.8722
2011-02-18 | 0 | 0
2011-02-19 | 0 | 0
2011-02-20 | 0.014486 | 2418 | -4.2346
2011-02-21 | 0.45594 | 76104 | -0.7854
2011-02-22 | 0.010245 | 1710 | -4.581
2011-02-23 | 0.0055356 | 924 | -5.1965
2011-02-24 | 0.00093459 | 156 | -6.9754
2011-02-25 | 0 | 0
2011-02-26 | 0.071388 | 11916 | -2.6396
2011-02-27 | 0.020633 | 3444 | -3.8809
2011-02-28 | 0.13623 | 22740 | -1.9934
2011-03-01 | 0.0028397 | 474 | -5.8641
2011-03-02 | 0.038893 | 6492 | -3.2469
2011-03-03 | 0.030302 | 5058 | -3.4965
2011-03-04 | 0.0013659 | 228 | -6.5959
2011-03-05 | 0.041841 | 6984 | -3.1739
2011-03-06 | 0.01445 | 2412 | -4.237
2011-03-07 | 0 | 0
2011-03-08 | 0.23616 | 39420 | -1.4432
2011-03-09 | 0.0076564 | 1278 | -4.8722
2011-03-10 | 0 | 0
2011-03-11 | 0.5284 | 88200 | -0.6379
2011-03-12 | 0 | 0
2011-03-13 | 0.0062186 | 1038 | -5.0802
2011-03-14 | 0.0062905 | 1050 | -5.0687
2011-03-15 | 0 | 0
2011-03-16 | 0 | 0
2011-03-17 | 0 | 0
2011-03-18 | 0.016463 | 2748 | -4.1066
2011-03-19 | 0.093746 | 15648 | -2.3672
2011-03-20 | 0.046442 | 7752 | -3.0696
2011-03-21 | 0.51809 | 86478 | -0.65762
2011-03-22 | 0.017937 | 2994 | -4.0209
2011-03-23 | 0.090655 | 15132 | -2.4007
2011-03-24 | 0.0088426 | 1476 | -4.7282
2011-03-25 | 0.0048527 | 810 | -5.3282
2011-03-26 | 0 | 0
2011-03-27 | 0.0096334 | 1608 | -4.6425
2011-03-28 | 0.023976 | 4002 | -3.7307
2011-03-29 | 0 | 0
2011-03-30 | 0.71122 | 118716 | -0.34077
2011-03-31 | 0.04087 | 6822 | -3.1974
2011-04-01 | 0.32599 | 54414 | -1.1209
2011-04-02 | 0.025162 | 4200 | -3.6824
2011-04-03 | 0.014666 | 2448 | -4.2222
2011-04-04 | 0.020309 | 3390 | -3.8967
2011-04-05 | 0.0015457 | 258 | -6.4723
2011-04-06 | 0 | 0
2011-04-07 | 0 | 0
2011-04-08 | 0.011503 | 1920 | -4.4652
2011-04-09 | 0.017362 | 2898 | -4.0535
2011-04-10 | 0.016499 | 2754 | -4.1045
2011-04-11 | 0 | 0
2011-04-12 | 0 | 0
2011-04-13 | 0 | 0
2011-04-14 | 0.10356 | 17286 | -2.2676
2011-04-15 | 0 | 0
2011-04-16 | 0.090979 | 15186 | -2.3971
2011-04-17 | 0.42739 | 71340 | -0.85005
2011-04-18 | 0 | 0
2011-04-19 | 0.0020489 | 342 | -6.1905
2011-04-20 | 0.28338 | 47301 | -1.261
2011-04-21 | 0 | 0
2011-04-22 | 0 | 0
2011-04-23 | 0.3256 | 54348 | -1.1221
2011-04-24 | 0.00050324 | 84 | -7.5944
2011-04-25 | 0.010927 | 1824 | -4.5165
2011-04-26 | 0.0061467 | 1026 | -5.0918
2011-04-27 | 0.0012581 | 210 | -6.6782
2011-04-28 | 0.65374 | 109122 | -0.42504
2011-04-29 | 0.013552 | 2262 | -4.3013
2011-04-30 | 0.010173 | 1698 | -4.5881
2011-05-01 | 0 | 0
2011-05-02 | 0.45137 | 75342 | -0.79547
2011-05-03 | 0.0040259 | 672 | -5.515
2011-05-04 | 0.15255 | 25464 | -1.8802
2011-05-05 | 0.029691 | 4956 | -3.5169
2011-05-06 | 0.0065421 | 1092 | -5.0295
2011-05-07 | 0.63663 | 106266 | -0.45156
2011-05-08 | 0.00025162 | 42 | -8.2876
2011-05-09 | 0.013911 | 2322 | -4.2751
2011-05-10 | 0.0069016 | 1152 | -4.976
2011-05-11 | 0.02908 | 4854 | -3.5377
2011-05-12 | 0.30363 | 50682 | -1.1919
2011-05-13 | 0.068009 | 11352 | -2.6881
2011-05-14 | 0.070813 | 11820 | -2.6477
2011-05-15 | 0 | 0
2011-05-16 | 0.36061 | 60192 | -1.02
2011-05-17 | 0.021783 | 3636 | -3.8266
2011-05-18 | 0.41742 | 69675 | -0.87366
2011-05-19 | 0.0074048 | 1236 | -4.9056
2011-05-20 | 0.37703 | 62934 | -0.97542
2011-05-21 | 0.011143 | 1860 | -4.4969
2011-05-22 | 0.6885 | 114924 | -0.37323
2011-05-23 | 0.00053919 | 90 | -7.5255
2011-05-24 | 0.014738 | 2460 | -4.2173
2011-05-25 | 0.20406 | 34062 | -1.5893
2011-05-26 | 0.00028757 | 48 | -8.1541
2011-05-27 | 0 | 0
2011-05-28 | 0.26101 | 43567.8 | -1.3432
2011-05-29 | 0 | 0
2011-05-30 | 0 | 0
2011-05-31 | 0.0064343 | 1074 | -5.0461
2011-06-01 | 0.0065781 | 1098 | -5.024
2011-06-02 | 0.013911 | 2322 | -4.2751
2011-06-03 | 0 | 0
2011-06-04 | 0.0077643 | 1296 | -4.8582
2011-06-05 | 0.094681 | 15804 | -2.3572
2011-06-06 | 0.0020848 | 348 | -6.1731
2011-06-07 | 0.024156 | 4032 | -3.7232
2011-06-08 | 0 | 0
2011-06-09 | 0.028757 | 4800 | -3.5489
2011-06-10 | 0.19608 | 32730 | -1.6292
2011-06-11 | 0 | 0
2011-06-12 | 0.015097 | 2520 | -4.1932
2011-06-13 | 0 | 0
2011-06-14 | 0 | 0
2011-06-15 | 0.60573 | 101107.8 | -0.50132
2011-06-16 | 0.0188 | 3138 | -3.9739
2011-06-17 | 0.069735 | 11640 | -2.6631
2011-06-18 | 0.0633 | 10566 | -2.7599
2011-06-19 | 0.0010784 | 180 | -6.8323
2011-06-20 | 0.0079799 | 1332 | -4.8308
2011-06-21 | 1.0262 | 171294 | 0.025876
2011-06-22 | 0 | 0
2011-06-23 | 0.010316 | 1722 | -4.574
2011-06-24 | 0 | 0
2011-06-25 | 0.052804 | 8814 | -2.9412
2011-06-26 | 0.78444 | 130938 | -0.24278
2011-06-27 | 0.0061467 | 1026 | -5.0918
2011-06-28 | 0.069735 | 11640 | -2.6631
2011-06-29 | 0 | 0
2011-06-30 | 0.052624 | 8784 | -2.9446
2011-07-01 | 0.040512 | 6930 | -3.2062
2011-07-02 | 0 | 0
2011-07-03 | 0.11505 | 19680 | -2.1624
2011-07-04 | 0.024623 | 4212 | -3.7041
2011-07-05 | 0.58761 | 100518 | -0.53169
2011-07-06 | 0.18032 | 30846 | -1.713
2011-07-07 | 0.019326 | 3306 | -3.9463
2011-07-08 | 0.043669 | 7470 | -3.1311
2011-07-09 | 0.013714 | 2346 | -4.2893
2011-07-10 | 0.070571 | 12072 | -2.6511
2011-07-11 | 0.010768 | 1842 | -4.5312
2011-07-12 | 0.0004209 | 72 | -7.7731
2011-07-13 | 0.020414 | 3492 | -3.8915
2011-07-14 | 0.50084 | 85674 | -0.69147
2011-07-15 | 0.044861 | 7674 | -3.1042
2011-07-16 | 0.001403 | 240 | -6.5691
2011-07-17 | 0.019923 | 3408 | -3.9159
2011-07-18 | 0.20635 | 35298 | -1.5782
2011-07-19 | 0.030901 | 5286 | -3.477
2011-07-20 | 0.003262 | 558 | -5.7254
2011-07-21 | 0.0015082 | 258 | -6.4968
2011-07-22 | 0.26201 | 44820 | -1.3394
2011-07-23 | 0.025184 | 4308 | -3.6815
2011-07-24 | 0 | 0
2011-07-25 | 0.47337 | 80976 | -0.74787
2011-07-26 | 0.20649 | 35322 | -1.5775
2011-07-27 | 0.018309 | 3132 | -4.0004
2011-07-28 | 0.020519 | 3510 | -3.8864
2011-07-29 | 1.06 | 181320 | 0.05824
2011-07-30 | 0 | 0
2011-07-31 | 0.00063135 | 108 | -7.3676
2011-08-01 | 0.0002806 | 48 | -8.1786
2011-08-02 | 0.14598 | 24972 | -1.9243
2011-08-03 | 0 | 0
2011-08-04 | 0.00052613 | 90 | -7.55
2011-08-05 | 0.038302 | 6552 | -3.2623
2011-08-06 | 0.0013679 | 234 | -6.5945
2011-08-07 | 0.038933 | 6660 | -3.2459
2011-08-08 | 0.2201 | 37650 | -1.5137
2011-08-09 | 0.73998 | 126582 | -0.30113
2011-08-10 | 0 | 0
2011-08-11 | 0.31757 | 54324 | -1.1471
2011-08-12 | 0.0037881 | 648 | -5.5759
2011-08-13 | 0.0017538 | 300 | -6.346
2011-08-14 | 0.0025254 | 432 | -5.9814
2011-08-15 | 0.34696 | 59352 | -1.0585
2011-08-16 | 0 | 0
2011-08-17 | 0 | 0
2011-08-18 | 0.15366 | 26286 | -1.873
2011-08-19 | 0.017432 | 2982 | -4.0494
2011-08-20 | 0.0054016 | 924 | -5.2211
2011-08-21 | 0.15615 | 26712 | -1.8569
2011-08-22 | 0.0078568 | 1344 | -4.8464
2011-08-23 | 0.0049105 | 840 | -5.3164
2011-08-24 | 0.0094001 | 1608 | -4.667
2011-08-25 | 0.024693 | 4224 | -3.7012
2011-08-26 | 0.0088039 | 1506 | -4.7326
2011-08-27 | 0.039004 | 6672 | -3.2441
2011-08-28 | 0.01154 | 1974 | -4.462
2011-08-29 | 0 | 0
2011-08-30 | 0.03967 | 6786 | -3.2272
2011-08-31 | 0.00052613 | 90 | -7.55
2011-09-01 | 0.071132 | 12168 | -2.6432
2011-09-02 | 0.27979 | 47862 | -1.2737
2011-09-03 | 0.0042441 | 726 | -5.4622
2011-09-04 | 0 | 0
2011-09-05 | 0.029042 | 4968 | -3.539
2011-09-06 | 1.1213 | 191814 | 0.1145
2011-09-07 | 0.013995 | 2394 | -4.2691
2011-09-08 | 0 | 0
2011-09-09 | 0.033742 | 5772 | -3.389
2011-09-10 | 0.14749 | 25230 | -1.914
2011-09-11 | 0.00094703 | 162 | -6.9622
2011-09-12 | 0.19677 | 33660 | -1.6257
2011-09-13 | 0.0048053 | 822 | -5.338
2011-09-14 | 0 | 0
2011-09-15 | 0.0002806 | 48 | -8.1786
2011-09-16 | 0 | 0
2011-09-17 | 0.01154 | 1974 | -4.462
2011-09-18 | 0.011294 | 1932 | -4.4835
2011-09-19 | 0.002315 | 396 | -6.0684
2011-09-20 | 0.1088 | 18612 | -2.2182
2011-09-21 | 0.0049807 | 852 | -5.3022
2011-09-22 | 0.033111 | 5664 | -3.4079
2011-09-23 | 0.028972 | 4956 | -3.5414
2011-09-24 | 0 | 0
2011-09-25 | 0.0041389 | 708 | -5.4873
2011-09-26 | 0.015152 | 2592 | -4.1896
2011-09-27 | 0.48635 | 83196 | -0.72082
2011-09-28 | 0.89954 | 153876 | -0.10588
2011-09-29 | 0.0074008 | 1266 | -4.9062
2011-09-30 | 0 | 0
2011-10-01 | 0.023325 | 3990 | -3.7582
2011-10-02 | 0 | 0
2011-10-03 | 0.013995 | 2394 | -4.2691
2011-10-04 | 0.020238 | 3462 | -3.9002
2011-10-05 | 0.0092598 | 1584 | -4.6821
2011-10-06 | 0 | 0
2011-10-07 | 0 | 0
2011-10-08 | 0 | 0
2011-10-09 | 0 | 0
2011-10-10 | 0 | 0
2011-10-11 | 0.0021747 | 372 | -6.1309
2011-10-12 | 0.027288 | 4668 | -3.6013
2011-10-13 | 0.0009821 | 168 | -6.9258
2011-10-14 | 0.025535 | 4368 | -3.6677
2011-10-15 | 0.00049105 | 84 | -7.619
2011-10-16 | 0 | 0
2011-10-17 | 0 | 0
2011-10-18 | 0.013329 | 2280 | -4.3178
2011-10-19 | 0.0015433 | 264 | -6.4738
2011-10-20 | 0 | 0
2011-10-21 | 0.013048 | 2232 | -4.3391
2011-10-22 | 0.01189 | 2034 | -4.432
2011-10-23 | 0 | 0
2011-10-24 | 0.0061381 | 1050 | -5.0932
2011-10-25 | 0.0071202 | 1218 | -4.9448
2011-10-26 | 0.0075411 | 1290 | -4.8874
2011-10-27 | 0.00077165 | 132 | -7.167
2011-10-28 | 0.0050157 | 858 | -5.2952
2011-10-29 | 0 | 0
2011-10-30 | 0.017643 | 3018 | -4.0374
2011-10-31 | 0.0040336 | 690 | -5.5131
2011-11-01 | 0.007471 | 1278 | -4.8967
2011-11-02 | 0.011329 | 1938 | -4.4804
2011-11-03 | 0 | 0
2011-11-04 | 0 | 0
2011-11-05 | 0.031392 | 5370 | -3.4612
2011-11-06 | 0.20778 | 35544 | -1.5713
2011-11-07 | 0.017678 | 3024 | -4.0354
2011-11-08 | 0.053791 | 9201.6 | -2.9226
2011-11-09 | 0.054857 | 9384 | -2.903
2011-11-10 | 0.41336 | 70710 | -0.88344
2011-11-11 | 0 | 0
2011-11-12 | 0.059768 | 10224 | -2.8173
2011-11-13 | 0.017082 | 2922 | -4.0698
2011-11-14 | 0.11326 | 19374 | -2.1781
2011-11-15 | 0.0054366 | 930 | -5.2146
2011-11-16 | 0.0023851 | 408 | -6.0385
2011-11-17 | 0.013434 | 2298 | -4.31
2011-11-18 | 0.0070852 | 1212 | -4.9498
2011-11-19 | 0.03753 | 6420 | -3.2826
2011-11-20 | 0.4088 | 69930 | -0.89453
2011-11-21 | 0.0090143 | 1542 | -4.7089
2011-11-22 | 0 | 0
2011-11-23 | 0 | 0
2011-11-24 | 0 | 0
2011-11-25 | 0 | 0
2011-11-26 | 0 | 0
2011-11-27 | 0 | 0
2011-11-28 | 0 | 0
2011-11-29 | 0.49414 | 84528 | -0.70494
2011-11-30 | 0.18576 | 31776 | -1.6833
2011-12-01 | 0.01631 | 2790 | -4.116
2011-12-02 | 0 | 0
2011-12-03 | 0 | 0
2011-12-04 | 0 | 0
2011-12-05 | 0.086846 | 14856 | -2.4436
2011-12-06 | 0.00045598 | 78 | -7.6931
2011-12-07 | 0.030796 | 5268 | -3.4804
2011-12-08 | 0.012101 | 2070 | -4.4145
2011-12-09 | 0.010908 | 1866 | -4.5182
2011-12-10 | 0.006559 | 1122 | -5.0269
2011-12-11 | 0.98056 | 167736 | -0.019632
2011-12-12 | 0 | 0
2011-12-13 | 0 | 0
2011-12-14 | 0.001403 | 240 | -6.5691
2011-12-15 | 0.024482 | 4188 | -3.7098
2011-12-16 | 0.30449 | 52086 | -1.1891
2011-12-17 | 0 | 0
2011-12-18 | 0.0061732 | 1056 | -5.0875
2011-12-19 | 0.015819 | 2706 | -4.1466
2011-12-20 | 0.0037881 | 648 | -5.5759
2011-12-21 | 0 | 0
2011-12-22 | 0.16945 | 28986 | -1.7752
2011-12-23 | 0 | 0
2011-12-24 | 0 | 0
2011-12-25 | 0 | 0
2011-12-26 | 0.10186 | 17424 | -2.2842
2011-12-27 | 0 | 0
2011-12-28 | 0.013434 | 2298 | -4.31
2011-12-29 | 0.010207 | 1746 | -4.5847
2011-12-30 | 0 | 0
2011-12-31 | 0.017257 | 2952 | -4.0595
2012-01-01 | 0.24777 | 42384 | -1.3953
2012-01-02 | 0.00038583 | 66 | -7.8601
2012-01-03 | 0.021782 | 3726 | -3.8267
2012-01-04 | 0.76874 | 131502 | -0.263
2012-01-05 | 0.0031217 | 534 | -5.7694
2012-01-06 | 0 | 0
2012-01-07 | 0 | 0
2012-01-08 | 0 | 0
2012-01-09 | 0.17236 | 29484 | -1.7582
2012-01-10 | 0.018765 | 3210 | -3.9758
2012-01-11 | 0.89571 | 153222 | -0.11014
2012-01-12 | 0.068888 | 11784 | -2.6753
2012-01-13 | 0.03504 | 5994 | -3.3513
2012-01-14 | 0.016941 | 2898 | -4.078
2012-01-15 | 0.025359 | 4338 | -3.6746
2012-01-16 | 0.021291 | 3642 | -3.8495
2012-01-17 | 0.012732 | 2178 | -4.3636
2012-01-18 | 0 | 0
2012-01-19 | 0.0078919 | 1350 | -4.8419
2012-01-20 | 0.27906 | 47736 | -1.2763
2012-01-21 | 0.0282 | 4824 | -3.5684
2012-01-22 | 0 | 0
2012-01-23 | 0 | 0
2012-01-24 | 0.0044545 | 762 | -5.4138
2012-01-25 | 0.012837 | 2196 | -4.3554
2012-01-26 | 0.013679 | 2340 | -4.2919
2012-01-27 | 0.17934 | 30678 | -1.7185
2012-01-28 | 0 | 0
2012-01-29 | 0 | 0
2012-01-30 | 0.036653 | 6270 | -3.3062
2012-01-31 | 0.034865 | 5964 | -3.3563
2012-02-01 | 0.016415 | 2808 | -4.1096
2012-02-02 | 0.017713 | 3030 | -4.0335
2012-02-03 | 0.045036 | 7704 | -3.1003
2012-02-04 | 0 | 0
2012-02-05 | 0.0049456 | 846 | -5.3093
2012-02-06 | 0.013329 | 2280 | -4.3178
2012-02-07 | 0 | 0
2012-02-08 | 0.0004209 | 72 | -7.7731
2012-02-09 | 0.0038583 | 660 | -5.5575
2012-02-10 | 0.012873 | 2202 | -4.3527
2012-02-11 | 0 | 0
2012-02-12 | 0.007927 | 1356 | -4.8375
2012-02-13 | 0.018976 | 3246 | -3.9646
2012-02-14 | 0 | 0
2012-02-15 | 0 | 0
2012-02-16 | 0 | 0
2012-02-17 | 0.41859 | 71604 | -0.87087
2012-02-18 | 0.94591 | 161808 | -0.055613
2012-02-19 | 0.18649 | 31902 | -1.6794
2012-02-20 | 0.015608 | 2670 | -4.1599
2012-02-21 | 0.046334 | 7926 | -3.0719
2012-02-22 | 0.011575 | 1980 | -4.4589
2012-02-23 | 0.013574 | 2322 | -4.2996
2012-02-24 | 0.21505 | 36786 | -1.5369
2012-02-25 | 0.041704 | 7134 | -3.1772
2012-02-26 | 0.02578 | 4410 | -3.6581
2012-02-27 | 0.18941 | 32400 | -1.6639
2012-02-28 | 0.065731 | 11244 | -2.7222
2012-02-29 | 0.090704 | 15516 | -2.4002
2012-03-01 | 0.099964 | 17100 | -2.3029
2012-03-02 | 0.021711 | 3714 | -3.8299
2012-03-03 | 0.089126 | 15246 | -2.4177
2012-03-04 | 0.20593 | 35226 | -1.5802
2012-03-05 | 0.59631 | 102006 | -0.51699
2012-03-06 | 0.057102 | 9768 | -2.8629
2012-03-07 | 0.38386 | 65664 | -0.95747
2012-03-08 | 0.28688 | 49074 | -1.2487
2012-03-09 | 0.10677 | 18264 | -2.2371
2012-03-10 | 0 | 0
2012-03-11 | 0.024447 | 4182 | -3.7112
2012-03-12 | 0.012802 | 2190 | -4.3581
2012-03-13 | 0.017362 | 2970 | -4.0535
2012-03-14 | 0.66324 | 113454 | -0.41063
2012-03-15 | 0.13535 | 23154 | -1.9999
2012-03-16 | 0.029638 | 5070 | -3.5187
2012-03-17 | 0.0097509 | 1668 | -4.6304
2012-03-18 | 0 | 0
2012-03-19 | 0.017327 | 2964 | -4.0555
2012-03-20 | 0.0069098 | 1182 | -4.9748
2012-03-21 | 0.0086636 | 1482 | -4.7486
2012-03-22 | 0.017748 | 3036 | -4.0315
2012-03-23 | 0.24395 | 41730 | -1.4108
2012-03-24 | 0 | 0
2012-03-25 | 0.0064889 | 1110 | -5.0377
2012-03-26 | 0.0044896 | 768 | -5.406
2012-03-27 | 0.36973 | 63246 | -0.99499
2012-03-28 | 0 | 0
2012-03-29 | 0.51364 | 87864 | -0.66623
2012-03-30 | 0 | 0
2012-03-31 | 0 | 0
2012-04-01 | 1.7379 | 297288 | 0.55268
2012-04-02 | 0.18421 | 31512 | -1.6917
2012-04-03 | 0.01873 | 3204 | -3.9776
2012-04-04 | 0.031568 | 5400 | -3.4556
2012-04-05 | 0 | 0
2012-04-06 | 0.0078568 | 1344 | -4.8464
2012-04-07 | 0.0064187 | 1098 | -5.0485
2012-04-08 | 0 | 0
2012-04-09 | 0.006559 | 1122 | -5.0269
2012-04-10 | 0.26036 | 44538 | -1.3457
2012-04-11 | 0.21533 | 36834 | -1.5356
2012-04-12 | 0.34346 | 58752 | -1.0687
2012-04-13 | 0.092528 | 15828 | -2.3802
2012-04-14 | 0.0040336 | 690 | -5.5131
2012-04-15 | 0 | 0
2012-04-16 | 0 | 0
2012-04-17 | 0.030094 | 5148 | -3.5034
2012-04-18 | 0.03027 | 5178 | -3.4976
2012-04-19 | 0.020764 | 3552 | -3.8745
2012-04-20 | 0.059803 | 10230 | -2.8167
2012-04-21 | 0.0033321 | 570 | -5.7041
2012-04-22 | 0 | 0
2012-04-23 | 0.010523 | 1800 | -4.5542
2012-04-24 | 0.019572 | 3348 | -3.9337
2012-04-25 | 0.01652 | 2826 | -4.1032
2012-04-26 | 0.01887 | 3228 | -3.9702
2012-04-27 | 0.0016836 | 288 | -6.3868
2012-04-28 | 0 | 0
2012-04-29 | 0 | 0
2012-04-30 | 0 | 0
2012-05-01 | 0.049912 | 8538 | -2.9975
2012-05-02 | 0.0009821 | 168 | -6.9258
2012-05-03 | 0.01887 | 3228 | -3.9702
2012-05-04 | 0.0036127 | 618 | -5.6233
2012-05-05 | 0.0026657 | 456 | -5.9273
2012-05-06 | 0 | 0
2012-05-07 | 0.077341 | 13230 | -2.5595
2012-05-08 | 0.027429 | 4692 | -3.5962
2012-05-09 | 0.62795 | 107418 | -0.4653
2012-05-10 | 0.00021045 | 36 | -8.4663
2012-05-11 | 0.081585 | 13956 | -2.5061
2012-05-12 | 0.018976 | 3246 | -3.9646
2012-05-13 | 0.0010172 | 174 | -6.8907
2012-05-14 | 0.016626 | 2844 | -4.0968
2012-05-15 | 0.063872 | 10926 | -2.7509
2012-05-16 | 0 | 0
2012-05-17 | 0.005612 | 960 | -5.1828
2012-05-18 | 0.020203 | 3456 | -3.9019
2012-05-19 | 0.56727 | 97038 | -0.56692
2012-05-20 | 0.0024202 | 414 | -6.0239
2012-05-21 | 0 | 0
2012-05-22 | 1.0273 | 175734 | 0.026948
2012-05-23 | 0.56282 | 96276 | -0.5748
2012-05-24 | 0.020238 | 3462 | -3.9002
2012-05-25 | 0.014451 | 2472 | -4.237
2012-05-26 | 0.01424 | 2436 | -4.2517
2012-05-27 | 0.048298 | 8262 | -3.0304
2012-05-28 | 0 | 0
2012-05-29 | 0.0010873 | 186 | -6.824
2012-05-30 | 0.010979 | 1878 | -4.5118
2012-05-31 | 0 | 0
2012-06-01 | 0 | 0
2012-06-02 | 0.0086285 | 1476 | -4.7527
2012-06-03 | 0.0069098 | 1182 | -4.9748
2012-06-04 | 0.0933 | 15960 | -2.3719
2012-06-05 | 2.2627 | 387054 | 0.81654
2012-06-06 | 0.016345 | 2796 | -4.1138
2012-06-07 | 0.00094703 | 162 | -6.9622
2012-06-08 | 0.24012 | 41076 | -1.4266
2012-06-09 | 0.04437 | 7590 | -3.1152
2012-06-10 | 0 | 0
2012-06-11 | 0 | 0
2012-06-12 | 0 | 0
2012-06-13 | 0.008874 | 1518 | -4.7246
2012-06-14 | 0 | 0
2012-06-15 | 0.04907 | 8394 | -3.0145
2012-06-16 | 0 | 0
2012-06-17 | 0 | 0
2012-06-18 | 0.030585 | 5232 | -3.4872
2012-06-19 | 0.017152 | 2934 | -4.0657
2012-06-20 | 0.0072956 | 1248 | -4.9205
2012-06-21 | 0.018414 | 3150 | -3.9946
2012-06-22 | 0 | 0
2012-06-23 | 0.039565 | 6768 | -3.2298
2012-06-24 | 0.00087688 | 150 | -7.0391
2012-06-25 | 0.0044545 | 762 | -5.4138
2012-06-26 | 0.0081725 | 1398 | -4.807
2012-06-27 | 0.0001403 | 24 | -8.8717
2012-06-28 | 0 | 0
2012-06-29 | 0 | 0
2012-06-30 | 0 | 0
Contents

## 1e. STPIS Exclusions
ActewAGL
STPIS Data Reporting | [12 empty] | Weather
2012-13 | [12 empty] | Equipment failure
Exclusions | [12 empty] | Operational error
Vegetation
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports. | [12 empty] | Animals
Third party impacts
Table 1: Exclusions | [12 empty] | Transmission failure
| Outage ID |  | Cause of event |  |  | Unplanned customer minutes off supply (Mins) |  |  |  | Unplanned customer minutes off-supply (including excluded events and MEDs) | Unplanned customer minutes off-supply (after removing excluded events and MED) |  | Load shedding |  | Planned customer minutes off-supply
Date of event (DD/MM/YYYY) |  | Outage ID | Feeder ID / name | Feeder classification | Cause of event | Number of customers interrupted | Duration of interruption (Mins) | Total unplanned customer minutes off supply | Exclusion category (Use Exclusion categories listed in section 3.3 (a) of the AER's STPIS ) | Unplanned SAIDI impact | Unplanned SAIFI impact | Further information (Please provide separate explanation to confirm the outage was not due to inadequate transmission connection planning ) |  | Inter-distributor connection failure
2013-01-08 |  | - | Theodore | Urban | Planned | 1 | 112 | 114 | 1 | 0.00065061 | 5.7071e-06 | MED |  | Other
2013-01-08 |  | - | Chippindall | Urban | Equipment | 28 | 45 | 1260 | 1 | 0.0071909 | 0.0001598 | MED
2013-01-08 |  | - | Folingsby | Urban | Weather | 40 | 27 | 1080 | 1 | 0.0061636 | 0.00022828 | MED
2013-01-08 |  | - | Seal | Urban | Environment | 1285 | 51 | 65550 | 1 | 0.3741 | 0.0073336 | MED
2013-01-08 |  | - | Verbrugghen | Urban | Weather | 53 | 220 | 11658 | 1 | 0.066533 | 0.00030248 | MED
2013-01-08 |  | - | Marconi | Urban | Environment | 13 | 17 | 228 | 1 | 0.0013012 | 7.4192e-05 | MED
2013-01-08 |  | - | Cotter 11kV | Rural short | Environment | 32 | 162 | 5184 | 1 | 0.029585 | 0.00018263 | MED
2013-01-08 |  | - | Hilder | Urban | Environment | 40 | 108 | 4320 | 1 | 0.024655 | 0.00022828 | MED
2013-01-08 |  | - | Weir | Urban | Equipment | 23 | 421 | 9684 | 1 | 0.055267 | 0.00013126 | MED
2013-01-08 |  | - | Macrossan | Urban | Weather | 27 | 237 | 6402 | 1 | 0.036537 | 0.00015409 | MED
2013-01-08 |  | - | Latham | Urban | Environment | 42 | 38 | 1596 | 1 | 0.0091085 | 0.0002397 | MED
2013-01-08 |  | - | Curtin North | Urban | Weather | 15 | 262 | 3930 | 1 | 0.022429 | 8.5606e-05 | MED
2013-01-08 |  | - | Stott | Urban | Equipment | 1755 | 33.9 | 59634 | 1 | 0.34034 | 0.010016 | MED
2013-01-08 |  | - | Seal | Urban | Weather | 35 | 143 | 5004 | 1 | 0.028558 | 0.00019975 | MED
2013-01-08 |  | - | Cooleman | Urban | Weather | 18 | 63 | 1134 | 1 | 0.0064718 | 0.00010273 | MED
2013-01-08 |  | - | Fielder | Urban | Environment | 13 | 168 | 2184 | 1 | 0.012464 | 7.4192e-05 | MED
2013-01-08 |  | - | Conolly | Urban | Weather | 31 | 380 | 11778 | 1 | 0.067218 | 0.00017692 | MED
2013-01-08 |  | - | Latham | Urban | Weather | 42 | 274 | 11508 | 1 | 0.065677 | 0.0002397 | MED
2013-01-08 |  | - | Bissenberger | Urban | Weather | 28 | 61 | 1710 | 1 | 0.0097591 | 0.0001598 | MED
2013-01-08 |  | - | Meacham | Urban | Weather | 46 | 77 | 3540 | 1 | 0.020203 | 0.00026253 | MED
2013-01-08 |  | - | Conley | Urban | Weather | 41 | 57 | 2334 | 1 | 0.01332 | 0.00023399 | MED
2013-01-08 |  | - | Athllon | Urban | Weather | 1438 | 36 | 51768 | 1 | 0.29544 | 0.0082068 | MED
2013-01-08 |  | - | Markell | Urban | Weather | 34 | 177 | 6018 | 1 | 0.034345 | 0.00019404 | MED
2013-01-08 |  | - | Verbrugghen | Urban | Weather | 29 | 83 | 2406 | 1 | 0.013731 | 0.00016551 | MED
2013-01-08 |  | - | Jackie Howe | Urban | Weather | 16 | 253 | 4050 | 1 | 0.023114 | 9.1313e-05 | MED
2013-01-08 |  | - | Willoughby | Urban | Environment | 28 | 223 | 6246 | 1 | 0.035646 | 0.0001598 | MED
2013-01-08 |  | - | McInnes | Urban | Weather | 1156 | 38 | 43926 | 1 | 0.25069 | 0.0065974 | MED
2013-01-08 |  | - | Athllon | Urban | Weather | 1438 | 28 | 40260 | 1 | 0.22977 | 0.0082068 | MED
2013-01-08 |  | - | Sainsbury | Urban | Weather | 42 | 64 | 2688 | 1 | 0.015341 | 0.0002397 | MED
2013-01-08 |  | - | Symers | Urban | Equipment | 29 | 284 | 8238 | 1 | 0.047015 | 0.00016551 | MED
2013-01-08 |  | - | Wilson | Urban | Weather | 19 | 58 | 1104 | 1 | 0.0063006 | 0.00010843 | MED
2013-01-08 |  | - | Streeton | Urban | Weather | 1065 | 29 | 30888 | 1 | 0.17628 | 0.006078 | MED
2013-01-08 |  | - | Power House | Urban | Environment | 1030 | 51 | 52530 | 1 | 0.29979 | 0.0058783 | MED
2013-01-08 |  | - | Hawkesbury | Urban | Environment | 39 | 267 | 10410 | 1 | 0.059411 | 0.00022258 | MED
2013-01-08 |  | - | O'Loghlen | Urban | Weather | 33 | 95 | 3138 | 1 | 0.017909 | 0.00018833 | MED
2013-01-08 |  | - | Belconnen Way North | Urban | Environment | 47 | 129 | 6066 | 1 | 0.034619 | 0.00026823 | MED
2013-01-08 |  | - | Jackie Howe | Urban | Weather | 24 | 147 | 3528 | 1 | 0.020135 | 0.00013697 | MED
2013-01-08 |  | - | Ashley | Urban | Weather | 18 | 240 | 4320 | 1 | 0.024655 | 0.00010273 | MED
2013-01-08 |  | - | Forster | Urban | Environment | 8 | 155 | 1242 | 1 | 0.0070882 | 4.5657e-05 | MED
2013-01-08 |  | - | Gaunson | Urban | Weather | 44 | 212 | 9330 | 1 | 0.053247 | 0.00025111 | MED
2013-01-08 |  | - | Hilder | Urban | General | 36 | 185 | 6660 | 1 | 0.038009 | 0.00020545 | MED
2013-01-08 |  | - | Weston East | Urban | Weather | 30 | 142 | 4260 | 1 | 0.024312 | 0.00017121 | MED
2013-01-08 |  | - | Lyons West | Urban | Environment | 37 | 27 | 996 | 1 | 0.0056843 | 0.00021116 | MED
2013-01-08 |  | - | Fielder | Urban | Weather | 18 | 48 | 864 | 1 | 0.0049309 | 0.00010273 | MED
2013-01-08 |  | - | O'Loghlen | Urban | Environment | 35 | 72 | 2520 | 1 | 0.014382 | 0.00019975 | MED
2013-01-08 |  | - | Power House | Urban | Equipment | 340 | 24 | 8160 | 1 | 0.04657 | 0.0019404 | MED
2013-01-08 |  | - | Bunbury | Urban | Environment | 46 | 77 | 3540 | 1 | 0.020203 | 0.00026253 | MED
2013-01-08 |  | - | Yarralumla | Urban | Environment | 42 | 124 | 5208 | 1 | 0.029722 | 0.0002397 | MED
2013-01-08 |  | - | Carruthers | Urban | Equipment | 29 | 131 | 3654 | 1 | 0.020854 | 0.00016551 | MED
2013-01-08 |  | - | Pridham | Urban | Environment | 52 | 15 | 780 | 1 | 0.0044515 | 0.00029677 | MED
2013-01-08 |  | - | Gaunson | Urban | Weather | 17 | 174 | 2958 | 1 | 0.016882 | 9.702e-05 | MED
2013-01-08 |  | - | Wolseley | Urban | Equipment | 18 | 143 | 2574 | 1 | 0.01469 | 0.00010273 | MED
2013-01-08 |  | - | Cunningham | Urban | Environment | 23 | 170 | 3912 | 1 | 0.022326 | 0.00013126 | MED
2013-01-08 |  | - | Homann | Urban | Environment | 28 | 102 | 2856 | 1 | 0.016299 | 0.0001598 | MED
2013-01-08 |  | - | Homann | Urban | Environment | 10 | 100 | 1002 | 1 | 0.0057185 | 5.7071e-05 | MED
2013-01-08 |  | - | Hawker | Urban | Environment | 24 | 15 | 360 | 1 | 0.0020545 | 0.00013697 | MED
2013-01-08 |  | - | Strzelecki | Urban | Environment | 36 | 28 | 1008 | 1 | 0.0057527 | 0.00020545 | MED
2013-01-08 |  | - | Bowley | Urban | Environment | 43 | 42 | 1806 | 1 | 0.010307 | 0.0002454 | MED
2013-01-26 |  | - | Langdon | Urban | Equipment | 1521 | 29.8 | 45456 | 1 | 0.25942 | 0.0086805 | MED
2013-01-26 |  | - | Belconnen Way North | Urban | Equipment | 4 | 6 | 24 | 1 | 0.00013697 | 2.2828e-05 | MED
2013-01-26 |  | - | Florey | Urban | Weather | 13 | 30 | 390 | 1 | 0.0022258 | 7.4192e-05 | MED
2013-01-26 |  | - | Melba | Urban | Weather | 72 | 986 | 70992 | 1 | 0.40516 | 0.00041091 | MED
2013-01-26 |  | - | Melba | Urban | Weather | 855 | 41 | 35058 | 1 | 0.20008 | 0.0048796 | MED
2013-01-26 |  | - | Haydon | Urban | Equipment | 1420 | 90.1 | 127950 | 1 | 0.73022 | 0.0081041 | MED
2013-01-26 |  | - | McGuiness | Urban | Weather | 22 | 906 | 19932 | 1 | 0.11375 | 0.00012556 | MED
2013-01-26 |  | - | Laurie | Urban | Weather | 32 | 454 | 14526 | 1 | 0.082901 | 0.00018263 | MED
2013-01-26 |  | - | Daplyn | Urban | Weather | 1043 | 379 | 395808 | 1 | 2.2589 | 0.0059525 | MED
2013-01-26 |  | - | Florey | Urban | Weather | 1078 | 379 | 408558 | 1 | 2.3317 | 0.0061522 | MED
2013-01-26 |  | - | Curtin North | Urban | Weather | 1170 | 151.33 | 177066 | 1 | 1.0105 | 0.0066773 | MED
2013-01-26 |  | - | Monaro | Urban | Weather | 130 | 75 | 9750 | 1 | 0.055644 | 0.00074192 | MED
2013-01-26 |  | - | Kelliher | Urban | Weather | 2 | 85 | 168 | 1 | 0.00095879 | 1.1414e-05 | MED
2013-01-26 |  | - | Strzelecki | Urban | Equipment | 1578 | 427.75 | 675000 | 1 | 3.8523 | 0.0090058 | MED
2013-01-26 |  | - | Meacham | Urban | Weather | 42 | 746 | 31332 | 1 | 0.17881 | 0.0002397 | MED
2013-01-26 |  | - | Verbrugghen | Urban | Weather | 49 | 434 | 21264 | 1 | 0.12136 | 0.00027965 | MED
2013-01-26 |  | - | Macrossan | Urban | Weather | 2157 | 162 | 378546 | 1 | 2.1604 | 0.01231 | MED
2013-01-26 |  | - | Wilson | Urban | Weather | 1164 | 150.8 | 175542 | 1 | 1.0018 | 0.006643 | MED
2013-01-26 |  | - | O'Loghlen | Urban | Equipment | 1217 | 118.21 | 143868 | 1 | 0.82107 | 0.0069455 | MED
2013-01-26 |  | - | Black Mountain | Urban | Weather | 29 | 104 | 3018 | 1 | 0.017224 | 0.00016551 | MED
2013-01-26 |  | - | Macrossan | Urban | Weather | 64 | 332 | 21246 | 1 | 0.12125 | 0.00036525 | MED
2013-01-26 |  | - | O'Loghlen | Urban | Weather | 42 | 815 | 34230 | 1 | 0.19535 | 0.0002397 | MED
2013-01-26 |  | - | Hilder | Urban | Weather | 24 | 105 | 2520 | 1 | 0.014382 | 0.00013697 | MED
Contents

## 1f. STPIS GSL
ActewAGL
STPIS Data Reporting |  | .
2012-13
Guaranteed Service Level
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Did the AER's GSL Scheme apply at any time during the regulatory year? | No
If the AER's GSL scheme applied at any time during the regulatory year, table 1 must be completed. Do not complete table 1 if the AER's GSL scheme did not apply during the regulatory year.
Table 1: Guaranteed service levels - AER GSL scheme
Reliability of supply
Frequency of interruptions CBD feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Urban feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Rural (short and long) feeders – 15 interruptions
Low reliability payments - 15 interruptions - ($)
Duration of interruptions CBD feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions urban feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions Rural (short and long) feeders – 18 hours
Low reliability payments - 18 hours - ($)
Total duration of interruptions Level 1 – 20 hours
Low reliability payments - 20 hours - ($)
Total duration of interruptions Level 2 – 30 hours
Low reliability payments - 30 hours - ($)
Total duration of interruptions Level 3 – 60 hours
Low reliability payments - 60 hours - ($)
Street lights
Streetlight repair 5 days - GSL payments - number
Street lights - GSL payments - ($)
New connections
Connections made
Connection not made on or before the day agreed - number
Connection not made on or before the day agreed - ($)
Connections - GSL payments - 1-6 day delay - number
Connections - GSL payments - 1-6 day delay - ($)
Connections - GSL payments - 7+ day delay - number
Connections - GSL payments - 7+ day delay - ($)
Planned interruptions
Notice of planned interruptions - 4 days not given - number
Notice of planned interruptions - 4 days not given - ($)
Total GSL payments payable under the AER's GSL scheme ($) | 0
Contents

## 2. Demand
ActewAGL
Demand
2012-13
The information is required to assess forecasts against outturn demand, and will inform the AER’s review of demand forecasts in future regulatory proposals. The information may be used in performance reports.
Note: a) Forecasts should be the demand forecasts for the relevant regulatory year that were made at the time of the regulatory proposal
b) t+1 forecasts should be the latest updates to the demand forecasts for the regulatory year t+1.
c) The PoE level only applies to the forecasts
Table 1: Maximum coincident demand at the network level |  |  | Source : REG Database (metering data)
Network coincident maximum demand | Forecast | Actual - raw | Actual - weather normalised | Variation % | t+1 forecast
90% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA) | 642 |  |  | -100% | 643
50% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA) | 660 |  |  | -100% | 661
10% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA) | 697 |  |  | -100% | 710
Table 2: Summer and winter non-coincident maximum demand by zone substation
Summer and winter maximum demand - ZS | [12 empty] | t+1 forecast |  |  |  | nameplate rating (MVA)
POE level = 50% | Forecast |  |  |  | Actual - raw |  |  |  | Actual - weather normalised
Location | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF
Angle Crossing - summer maximum demand |  | 3 |  | 0 |  | 5.16 |  | 0 |  |  |  | #DIV/0! |  | 3 |  |  | 15
Angle Crossing - winter maximum demand |  | 3 |  | 0 |  | 2.11 |  | 0 |  |  |  | #DIV/0! |  | 3 |  |  | 15
Belconnen - Summer maximum demand |  | 57 |  | 0 |  | 57.28 |  | 0 |  |  |  | #DIV/0! |  | 58 |  |  | 60
Belconnen - Winter maximum demand |  | 51 |  | 0 |  | 53.86 |  | 0 |  |  |  | #DIV/0! |  | 51 |  |  | 60
City East - Summer maximum demand |  | 88 |  | 0 |  | 75.48 |  | 0 |  |  |  | #DIV/0! |  | 90 |  |  | 100
City East - Winter maximum demand |  | 73 |  | 0 |  | 69.51 |  | 0 |  |  |  | #DIV/0! |  | 73 |  |  | 100
Civic - Summer maximum demand |  | 67 |  | 0 |  | 34.54 |  | 0 |  |  |  | #DIV/0! |  | 69 |  |  | 60
Civic - Winter maximum demand |  | 61 |  | 0 |  | 52.78 |  | 0 |  |  |  | #DIV/0! |  | 63 |  |  | 60
Fyshwick - Summer maximum demand |  | 47 |  | 0 |  | 34.99 |  | 0 |  |  |  | #DIV/0! |  | 45 |  |  | 47
Fyshwick - Winter maximum demand |  | 44 |  | 0 |  | 29.98 |  | 0 |  |  |  | #DIV/0! |  | 42 |  |  | 47
Gilmore - Summer maximum demand |  | 20 |  | 0 |  | 22.69 |  | 0 |  |  |  | #DIV/0! |  | 21 |  |  | 60
Gilmore - Winter maximum demand |  | 25 |  | 0 |  | 26.23 |  | 0 |  |  |  | #DIV/0! |  | 26 |  |  | 60
Gold Creek - Summer maximum demand |  | 43 |  | 0 |  | 48.48 |  | 0 |  |  |  | #DIV/0! |  | 46 |  |  | 69
Gold Creek - Winter maximum demand |  | 48 |  | 0 |  | 52.49 |  | 0 |  |  |  | #DIV/0! |  | 51 |  |  | 69
Latham - Summer maximum demand |  | 49 |  | 0 |  | 52.58 |  | 0 |  |  |  | #DIV/0! |  | 50 |  |  | 90
Latham - Winter maximum demand |  | 69 |  | 0 |  | 69.04 |  | 0 |  |  |  | #DIV/0! |  | 68 |  |  | 90
Telopea Park - Summer maximum demand |  | 91 |  | 0 |  | 103.91 |  | 0 |  |  |  | #DIV/0! |  | 90 |  |  | 90
Telopea Park - Winter maximum demand |  | 87 |  | 0 |  | 94.6 |  | 0 |  |  |  | #DIV/0! |  | 85 |  |  | 90
Theodore - Summer maximum demand |  | 24 |  | 0 |  | 25.76 |  | 0 |  |  |  | #DIV/0! |  | 24 |  |  | 60
Theodore - Winter maximum demand |  | 29 |  | 0 |  | 28.76 |  | 0 |  |  |  | #DIV/0! |  | 29 |  |  | 60
Wanniassa - Summer maximum demand |  | 72 |  | 0 |  | 71.11 |  | 0 |  |  |  | #DIV/0! |  | 74 |  |  | 90
Wanniassa - Winter maximum demand |  | 84 |  | 0 |  | 80.5 |  | 0 |  |  |  | #DIV/0! |  | 85 |  |  | 90
Woden - Summer maximum demand |  | 90 |  | 0 |  | 78.8 |  | 0 |  |  |  | #DIV/0! |  | 93 |  |  | 90
Woden - Winter maximum demand |  | 89 |  | 0 |  | 76.55 |  | 0 |  |  |  | #DIV/0! |  | 91 |  |  | 90
Please Note: ActewAGL does not measure power factor at its zone substations therefore this data is not available.
Maximum coincident demand at the network level - calculated using REG Database and converting into a spreadsheet to gain the maximum figures.
REG Database available at \\jeeves\nemprograms\production\NEM Network Production
In NMI field type NTTT% - select - double click on one of the meters - go to meters tab - right click on meter - select view meter data (this opens the meter data viewer) - click add - sort by NMI - select all the NTT meters (by double clicking) - select the date range of interest (31 days max) - Export to Excel for analysis
Summer and Winter non-coincident maximum demand by zone substation - Forecasts calculated using actuals because calculated at end of Summer
Actuals are calculated using TrendSCADA peak calculations and limiting the calculations to per zone substation and then multiplying by 11,000 (voltage) to convert the figures to MVA
To calculate figures from TrendSCADA - select date range - select 'normal point' - select data group (zone substation) - select data points in group - click OK
Data is extracted from TrendSCADA to an excel spreadsheet for analysis.
Note on S31: l_degville: Obtained through Asset Management System
Contents

## 3. Outcomes customer service
ActewAGL
Customer Service
2012-13
This information is used to monitor the service performance of the DNSP, and assist the AER understand service outcomes for customers. The information will inform the AER’s assessment of future service improvement expenditure proposals by the DNSP. The information may be used in performance reports.
Table 1: Quality of supply
2012-13
Over voltage events - due to high voltage injection
Customers receiving over-voltage - due to high voltage injection
Over voltage events - due to lightning
Customers receiving over-voltage - due to lightning
Over voltage events - due to voltage regulation or other cause
Customers receiving over-voltage - due to voltage regulation or other cause
Voltage variations - steady state (zone sub)
Voltage variations - one minute (zone sub)
Voltage variations - 10 seconds (zone sub) Min<0.7
Voltage variations - 10 seconds (zone sub) Min<0.8
Voltage variations - 10 seconds (zone sub) Min<0.9
Voltage variations - steady state (feeder)
Voltage variations - % zone subs monitored
Voltage variations - % feeders monitored
Customers - quality of supply improvement
Table 2: Complaints - technical quality of supply
2012-13
Complaints - technical quality of supply - number | 43 | *** New requirement for data - not required in the last reporting template
Complaints by category (%)
Low voltage supply
Voltage dips
Voltage swell
Voltage spike (impulsive transient)
Waveform distortion
TV or radio interference
Noise from appliances
Other
Complaints by Likely Cause (%)
Network equipment faulty
Network interference by NSP equipment
Network interference by another customer
Network limitation
Customer internal problem
No problem identified
Environmental
Other
Table 3: Customer service
2012-13
Timely provision of services
Connections made | 7559 | All requests for a basic connection completed
Connections not made on agreed date | 363 | Breaches
Timely repair of faulty streetlights
Streetlights - average monthly number "out"
Streetlights - not repaired by "fix by" date
Streetlights - average number of days to repair
Total streetlights
Call Centre Performance (number, unless stated)
Calls to call centre fault line | 36523
Calls to fault line not answered within 30 seconds | 5570
Calls to fault line - average waiting time before call answered | 61 seconds
Calls abandoned - percentage | 14.64%
Call centre - number of overload events | 1
Customer complaints (number)
Complaint - reliability of supply
Complaint - technical quality of supply
Complaint - administrative process or customer service
Complaint - connection or augmentation
Complaint - other
Total complaints | 342
Note on H58: Rob Walker: Calls to call centre fault line = Calls presented (excluding MEDs calls presented) = 39709 – 1344 – 1842 = 36523
Note on H59: Rob Walker:5/11/13 Calls to fault line not answered within 30 seconds = Calls handled – calls handled <SL (Excluding MEDs) = (32205 – 626 – 413) – (25876 – 186 – 94) = 31166 – 25596 = 5570
Note on H60: Rob Walker: Data obtained from Contact Service Queue Activty Report. This data cannot be filtered to excluded MED's.
Note on H61: Rob Walker: 5/11/13 Calls abandoned – percentage = Calls abandoned / Calls presented (excluding MEDs) =(7494 – 716 – 1429) / (39709 – 1344 – 1842) = 5349 / 36523 = 0.1464 *100% = 14.64%
Note on H62: Rob Walker:5/11/13 Call Centre – number of overload events = report from BSD advising of times the phone queue incidents = one incident where phones were intermittently impacted over a three day period between 22/08/12 – 24/08/12
Contents

## 4. General information
ActewAGL
General information
2012-13
The information will enable the AER to better understand the network and service performance outcomes reported by the DNSP. Network characteristics will be used to normalise other information, to assist in any benchmarking or other comparisons between DNSP financial and service performance outcomes.
Table 1: Metered supply points
| Total no. | By type of customer |  | By supply voltage
Number of metered supply points |  | Domestic | Non-domestic | Subtransmission | HV | LV
CBD | 0
Urban | 177255 | 160773 | 16482 | 0 | 24 | 177231
Rural Short | 0 | 0 | 0 | 0 | 0 | 0
Rural Long | 0
Total | 177255 | 160773 | 16482 | 0 | 24 | 177231
Table 2: Energy delivered
| Total GWh | By type of customer |  | By supply voltage
Energy delivered (GWh) |  | Domestic | Non-domestic | Subtransmission | HV | LV - residential | LV - non residential
CBD | 0
Urban | 0
Rural Short | 0
Rural Long | 0
Total | 2875
Table 3: Line length
Note: where a line supplies more than one feeder type, the line length should be proportionately allocated according to the number of feeders in each category. For example if a line supplied one each of a CBD and Urban feeder, 50% of the line length would be allocated to CBD and 50% to urban.
| Total km | Underground lines |  |  | Overhead lines
Line Length (km) |  | Subtransmission | HV | LV | Subtransmission | HV | LV
CBD | 0
Urban | 5131 | 3 | 1479 | 1255 | 196 | 1014 | 1184
Rural Short | 381 | 0 | 62 | 0 | 0 | 319
Rural Long | 0
Total | 5512 | 3 | 1541 | 1255 | 196 | 1333 | 1184
Table 4: Customer numbers
| Total no. | By type of customer |  | By supply voltage
Customer numbers |  | Domestic | Non-domestic | Subtransmission | HV | LV - residential | LV - non residential
Customer numbers start of period | 173186 | 156926 | 16260 | 0 | 23 | 158641 | 14522
Customer numbers end of period | 177255 | 160773 | 16482 | 0 | 24 | 162453 | 14778
Controlled load customers | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total New Customer Connections | 4070
Customer disconnections | 1787
Table 5: Number and capacity of transformers
Number & total capacity of transformers | Total no. | Capacity (MVA)
Distribution | 4985
Zone substation | 30 | 1423
Table 6: Unmetered supply points
Number of unmetered supply points | 2012-13
CBD
Urban | 23
Rural Short | 0
Rural Long
Total | 23
Table 7: Poles and substations
Number of poles and substations | 2012-13
Subtransmission poles | 1469
Distribution poles | 51375
Subtransmission and zone substations | 14
Distribution substations | 4506
Table 8: Other information
Other information | 2012-13
Distribution losses (% of purchases) | 4.5
Network Service area (sq.km) | 2358
Network Coincident Maximum Demand (MW) | 0
FTE employees | 497 | *Please note this is the total of all permanent employees employed by ActewAGL Distribution Network Services Division and Asset Management Division. This does not include staff employed by corporate services which may support these divisions.
Note on C69: m_sivasane: Mobile Zone Belconnen Zone Bruce Switching Station Causeway Switching Station City East Zone Civic Zone Fyshwick Zone Gilmore Zone Gold Creek Zone Latham Zone Telopea Park Zone Theodore Zone Wanniassa Zone Woden Zone
Note on D53: m_sivasane: 1 x 15 MVA : Mobile Zone 2 x 55 MVA : Belconnen Zone 2x57 + 1x55 MVA : City East Zone 3 x 55 MVA : Civic Zone 1x20 + 2x25 MVA : Fyshwick Zone 2 x 45 MVA : Gilmore Zone 2 x 57 MVA : Gold Creek Zone 3 x 50 MVA : Latham Zone 3 x 50 MVA : Telopea Park Zone 2 x 45 MVA : Theodore Zone 3 x 50 MVA : Wanniassa Zone 3 x 50 MVA : Woden Zone
Contents

## 5a. Network data outage
ActewAGL
Nework data - outages
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Unplanned Outages
AAD Note: The data below represents the 10 individual outages with the highest saidi (Unplanned & Planned ) in the network - excluding MED
Date (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Cause of event | Number of customers interrupted | Duration of interruption (Mins) | Unplanned customer minutes off supply (Mins) | Unplanned SAIDI impact | Unplanned SAIFI impact | Date (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Cause of event | Number of customers interrupted | Duration of interruption (Mins) - Average | Unplanned customer minutes off supply (Mins) | Unplanned SAIDI impact | Unplanned SAIFI impact
2013-06-16 |  | Nona | Urban | Weather | 2035 | 100.9 | 205381.8 | 1.1721 | 1.1614 | 41441 |  | Nona | Urban | Weather | 2035 | 100.9 | 205381.8 | 1.1721 | 1.1614
2013-02-08 |  | Duffy | Urban | Weather | 988 | 164 | 162030 | 0.92472 | 0.56386 | 41313 |  | Duffy | Urban | Weather | 988 | 164 | 162030 | 0.92472 | 0.56386
2013-06-23 |  | Meacham | Urban | Weather | 2665 | 41.49 | 110460 | 0.6304 | 1.5209 | 41448 |  | Meacham | Urban | Weather | 2665 | 41.49 | 110460 | 0.6304 | 1.5209
2012-08-09 |  | Stott | Urban | Equipment failure | 1755 | 53.59 | 94050 | 0.53675 | 1.0016 | 41130 |  | Stott | Urban | Equipment failure | 1755 | 53.59 | 94050 | 0.53675 | 1.0016
2013-02-08 |  | Baldwin | Urban | Equipment failure | 1015 | 91.61 | 92988 | 0.53069 | 0.57927 | 41313 |  | Baldwin | Urban | Equipment failure | 1015 | 91.61 | 92988 | 0.53069 | 0.57927
2013-05-14 |  | Cunningham | Urban | Equipment failure | 1770 | 51.64 | 91398 | 0.52162 | 1.0102 | 41408 |  | Cunningham | Urban | Equipment failure | 1770 | 51.64 | 91398 | 0.52162 | 1.0102
2012-11-25 |  | Longmore | Urban | Equipment failure | 1393 | 60 | 83580 | 0.477 | 0.795 | 41238 |  | Longmore | Urban | Equipment failure | 1393 | 60 | 83580 | 0.477 | 0.795
2013-01-18 |  | Wilson | Urban | Vegetation | 1164 | 71.49 | 83220 | 0.47494 | 0.6643 | 41292 |  | Wilson | Urban | Vegetation | 1164 | 71.49 | 83220 | 0.47494 | 0.6643
2012-10-19 |  | Macrossan | Urban | Third party impacts | 2296 | 36 | 82656 | 0.47172 | 1.3103 | 41201 |  | Macrossan | Urban | Third party impacts | 2296 | 36 | 82656 | 0.47172 | 1.3103
2012-10-16 |  | Deakin No 1 | Urban | Weather | 940 | 87 | 81798 | 0.46683 | 0.53647 | 41198 |  | Deakin No 1 | Urban | Weather | 940 | 87 | 81798 | 0.46683 | 0.53647
Table 2: Planned Outages |  |  | *** New requirement for data - not required in the last reporting template
Date (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Reason for planned outage | Number of customers interrupted | Duration of interruption (Mins) | Planned customer minutes off supply (Mins) | Planned SAIDI impact | Planned SAIFI impact | Date (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Reason for planned outage | Number of customers interrupted | Duration of interruption (Mins) - Average | Planned customer minutes off supply (Mins) | Planned SAIDI impact | Planned SAIFI impact
2013-02-12 |  | Nona | Urban | HV isolation Underground maintenance | 221 | 474 | 474 | 0.59784 | 0.12613 | 41317 |  | Nona | Urban | HV isolation Underground maintenance | 221 | 474 | 474 | 0.59784 | 0.12613
2013-01-17 |  | Langdon | Urban | HV isolation to establish new sub 9916 and change switchgear | 242 | 427 | 427 | 0.58972 | 0.13811 | 41291 |  | Langdon | Urban | HV isolation to establish new sub 9916 and change switchgear | 242 | 427 | 427 | 0.58972 | 0.13811
2012-12-11 |  | Cotter 11kV | Rural short | HV change pole Planned job L6194 all D/Stream of rec 9568 | 147 | 397 | 397 | 0.33304 | 0.083894 | 41254 |  | Cotter 11kV | Rural short | HV change pole Planned job L6194 all D/Stream of rec 9568 | 147 | 397 | 397 | 0.33304 | 0.083894
2012-08-31 |  | Miller | Urban | HV change poles | 92 | 445 | 445 | 0.23364 | 0.052505 | 41152 |  | Miller | Urban | HV change poles | 92 | 445 | 445 | 0.23364 | 0.052505
2012-08-31 |  | Miller | Urban | HV change poles | 91 | 434 | 434 | 0.22538 | 0.051934 | 41152 |  | Miller | Urban | HV change poles | 91 | 434 | 434 | 0.22538 | 0.051934
2013-03-29 |  | Barrier | Urban | LV isolation LV isolation for switchboard Modifications customer requested | 50 | 760 | 760 | 0.21686 | 0.028535 | 41362 |  | Barrier | Urban | LV isolation LV isolation for switchboard Modifications customer requested | 50 | 760 | 760 | 0.21686 | 0.028535
2012-10-30 |  | Ijong | Urban | LV change pole | 109 | 343 | 343 | 0.21336 | 0.062207 | 41212 |  | Ijong | Urban | LV change pole | 109 | 343 | 343 | 0.21336 | 0.062207
2013-06-06 |  | MacKenzie | Urban | HV change pole 2 Pole SUB | 72 | 497 | 497 | 0.20422 | 0.041091 | 41431 |  | MacKenzie | Urban | HV change pole 2 Pole SUB | 72 | 497 | 497 | 0.20422 | 0.041091
2013-01-24 |  | Hawker | Urban | HV isolation To rebuild SUB | 83 | 383 | 383 | 0.18142 | 0.047369 | 41298 |  | Hawker | Urban | HV isolation To rebuild SUB | 83 | 383 | 383 | 0.18142 | 0.047369
2013-01-17 |  | Wakefield | Urban | HV isolation To rebuild SUB 526 and replace LV poles | 76 | 401 | 401 | 0.17392 | 0.043374 | 41291 |  | Wakefield | Urban | HV isolation To rebuild SUB 526 and replace LV poles | 76 | 401 | 401 | 0.17392 | 0.043374
Formulas:
Date (DD/MM/YYYY) = [Date (DD/MM/YYYY)]
Contents

## 5b. Network data feeder
ActewAGL
Annual Feeder Reliability
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Annual Feeder Reliability Data |  | *** New requirement for data - not required in the last reporting template
Feeder ID / name | Outage ID | Geographical description of feeder | Feeder classification | Cause of event | Length of distribution lines - high voltage - overhead | Length of distribution lines - high voltage - underground | Unplanned customer minutes off supply (Mins) | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh) | Number of unplanned outages | Unplanned customer minutes off-supply (including excluded events and MEDs) | Unplanned customer minutes off-supply (after removing excluded events and MED) | Unplanned interruptions (SAIFI) (including excluded events and MEDs) | Unplanned interruptions (SAIFI) (after removing excluded events and MEDs) | Number of planned outages | Planned customer minutes off-supply | Planned interruptions (SAIFI)
Strzelecki |  |  | Urban | various |  |  | 696156 |  |  | 14 | 696156 | 20148 | 0.010715 | 0.0012802 | 21 | 157368 | 0.0035367
Macrossan |  |  | Urban | various |  |  | 636720 |  |  | 26 | 636720 | 230526 | 0.040851 | 0.027709 | 17 | 55152 | 0.0024611
Miller |  |  | Urban | various |  |  | 83196 |  |  | 7 | 83196 | 83196 | 0.013703 | 0.013703 | 36 | 499182 | 0.009102
Dryandra |  |  | Urban | various |  |  | 46242 |  |  | 12 | 46242 | 46242 | 0.0024553 | 0.0024553 | 46 | 474258 | 0.0089091
Daplyn |  |  | Urban | various |  |  | 452802 |  |  | 13 | 452802 | 56994 | 0.013241 | 0.0071436 | 6 | 35700 | 0.00081842
Florey |  |  | Urban | various |  |  | 473172 |  |  | 9 | 473172 | 64224 | 0.014077 | 0.007699 | 4 | 6276 | 0.00046182
Black Mountain |  |  | Urban | various |  |  | 96114 |  |  | 15 | 96114 | 93096 | 0.0089675 | 0.008798 | 49 | 359154 | 0.0074125
Baldwin |  |  | Urban | various |  |  | 165510 |  |  | 22 | 165510 | 165510 | 0.0095112 | 0.0095112 | 27 | 255282 | 0.0054425
Cowper |  |  | Urban | various |  |  | 25176 |  |  | 11 | 25176 | 25176 | 0.0015784 | 0.0015784 | 31 | 331344 | 0.0071846
Nona |  |  | Urban | various |  |  | 210481.8 |  |  | 4 | 210481.8 | 210481.8 | 0.012387 | 0.012387 | 5 | 141570 | 0.002122
Wakefield |  |  | Urban | various |  |  | 13164 |  |  | 9 | 13164 | 13164 | 0.0010815 | 0.0010815 | 32 | 320394 | 0.0063369
Wilson |  |  | Urban | various |  |  | 282066 |  |  | 8 | 282066 | 105420 | 0.014527 | 0.0076113 | 9 | 45528 | 0.001251
Chuculba |  |  | Urban | various |  |  | 67428 |  |  | 11 | 67428 | 67428 | 0.01306 | 0.01306 | 28 | 244488 | 0.0053665
O'Loghlen |  |  | Urban | various |  |  | 253830 |  |  | 10 | 253830 | 70074 | 0.015614 | 0.0078568 | 4 | 32982 | 0.00095287
Cunningham |  |  | Urban | various |  |  | 111852 |  |  | 10 | 111852 | 107940 | 0.011908 | 0.011774 | 22 | 169704 | 0.0037647
Curtin North |  |  | Urban | various |  |  | 206958 |  |  | 10 | 206958 | 25962 | 0.014398 | 0.007471 | 8 | 57168 | 0.0016719
Meacham |  |  | Urban | various |  |  | 206166 |  |  | 17 | 206166 | 171294 | 0.029118 | 0.028604 | 12 | 51384 | 0.0020285
Stott |  |  | Urban | various |  |  | 202242 |  |  | 7 | 202242 | 142608 | 0.031252 | 0.020992 | 6 | 47454 | 0.0013913
Duffy |  |  | Urban | various |  |  | 176496 |  |  | 10 | 176496 | 176496 | 0.0073775 | 0.0073775 | 9 | 51150 | 0.0014205
"Integrated" Names | Sumif Cust hrs Lost Largest to smallest | Interruptions Sustained | Interruptions Momentary | Customers Affected - Planned | SAIFI - Planned | Customers Affected - UnPlanned | SAIFI - Un Planned | Feeder Category |  | Name of feeder | Feeder identifer | Geographical description of feeder | Feeder categorisation | Number of customers | Maximum demand (MW) | Total number of sustained interruptions | Total number of unplanned sustained interruptions | Total number of sustained planned interruptions | Total number of momentary interruptions | Total minutes off supply (SAIDI) | Total unplanned minutes off supply (SAIDI) | Total planned minutes off supply (SAIDI) | Customers Affected - UnPlanned | SAIFI - Un Planned | Total number of sustained interruptions | Total number of unplanned sustained interruptions | Total number of sustained planned interruptions | Total number of momentary interruptions | Total minutes off supply (SAIDI) | Total unplanned minutes off supply (SAIDI) | Total planned minutes off supply (SAIDI)
Strzelecki | 14226.1 | 35 | 1 | 605 | 0.0035367 | 1833 | 0.010715 | U |  | Strzelecki |  |  | U | 1584 |  | 35 | 14 | 21 | 1 | 4.8711 | 3.973 | 0.89811 | 219 | 0.0012802 | 33 | 12 | 21 | 1 | 1.0131 | 0.11499 | 0.89811
Macrossan | 11531.6 | 43 | 1 | 421 | 0.0024611 | 6988 | 0.040851 | U |  | Macrossan |  |  | U | 2403 |  | 43 | 26 | 17 | 1 | 3.9486 | 3.6338 | 0.31476 | 4740 | 0.027709 | 40 | 23 | 17 | 0 | 1.6304 | 1.3156 | 0.31476
Miller | 9706.3 | 43 | 0 | 1557 | 0.009102 | 2344 | 0.013703 | U |  | Miller |  |  | U | 2214 |  | 43 | 7 | 36 | 0 | 3.3237 | 0.47481 | 2.8489 | 2344 | 0.013703 | 43 | 7 | 36 | 0 | 3.3237 | 0.47481 | 2.8489
Dryandra | 8675.7 | 58 | 1 | 1524 | 0.0089091 | 420 | 0.0024553 | U |  | Dryandra |  |  | U | 1058 |  | 58 | 12 | 46 | 1 | 2.9705 | 0.26391 | 2.7066 | 420 | 0.0024553 | 58 | 12 | 46 | 1 | 2.9705 | 0.26391 | 2.7066
Daplyn | 8142.1 | 19 | 1 | 140 | 0.00081842 | 2265 | 0.013241 | U |  | Daplyn |  |  | U | 1056 |  | 19 | 13 | 6 | 1 | 2.7879 | 2.5842 | 0.20374 | 1222 | 0.0071436 | 18 | 12 | 6 | 1 | 0.52901 | 0.32527 | 0.20374
Florey | 7990.8 | 13 | 3 | 79 | 0.00046182 | 2408 | 0.014077 | U |  | Florey |  |  | U | 1078 |  | 13 | 9 | 4 | 3 | 2.7362 | 2.7004 | 0.035818 | 1317 | 0.007699 | 11 | 7 | 4 | 1 | 0.40235 | 0.36653 | 0.035818
Black Mountain | 7588.9 | 64 | 1 | 1268 | 0.0074125 | 1534 | 0.0089675 | U |  | Black Mountain |  |  | U | 703 |  | 64 | 15 | 49 | 1 | 2.5983 | 0.54853 | 2.0497 | 1505 | 0.008798 | 63 | 14 | 49 | 1 | 2.581 | 0.53131 | 2.0497
Baldwin | 7013.2 | 49 | 0 | 931 | 0.0054425 | 1627 | 0.0095112 | U |  | Baldwin |  |  | U | 1027 |  | 49 | 22 | 27 | 0 | 2.4015 | 0.94458 | 1.4569 | 1627 | 0.0095112 | 49 | 22 | 27 | 0 | 2.4015 | 0.94458 | 1.4569
Cowper | 5943.8 | 42 | 2 | 1229 | 0.0071846 | 270 | 0.0015784 | U |  | Cowper |  |  | U | 1516 |  | 42 | 11 | 31 | 2 | 2.0347 | 0.14368 | 1.891 | 270 | 0.0015784 | 42 | 11 | 31 | 2 | 2.0347 | 0.14368 | 1.891
Nona | 5867.53 | 9 | 0 | 363 | 0.002122 | 2119 | 0.012387 | U |  | Nona |  |  | U | 2075 |  | 9 | 4 | 5 | 0 | 2.0092 | 1.2012 | 0.80795 | 2119 | 0.012387 | 9 | 4 | 5 | 0 | 2.0092 | 1.2012 | 0.80795
Wakefield | 5559.3 | 41 | 3 | 1084 | 0.0063369 | 185 | 0.0010815 | U |  | Wakefield |  |  | U | 1194 |  | 41 | 9 | 32 | 3 | 1.9036 | 0.075128 | 1.8285 | 185 | 0.0010815 | 41 | 9 | 32 | 2 | 1.9036 | 0.075128 | 1.8285
Wilson | 5459.9 | 17 | 2 | 214 | 0.001251 | 2485 | 0.014527 | U |  | Wilson |  |  | U | 1232 |  | 17 | 8 | 9 | 2 | 1.8696 | 1.6098 | 0.25983 | 1302 | 0.0076113 | 15 | 6 | 9 | 2 | 0.86147 | 0.60164 | 0.25983
Chuculba | 5199.3 | 39 | 0 | 918 | 0.0053665 | 2234 | 0.01306 | U |  | Chuculba |  |  | U | 1044 |  | 39 | 11 | 28 | 0 | 1.7801 | 0.38482 | 1.3953 | 2234 | 0.01306 | 39 | 11 | 28 | 0 | 1.7801 | 0.38482 | 1.3953
O'Loghlen | 4780.8 | 14 | 2 | 163 | 0.00095287 | 2671 | 0.015614 | U |  | O'Loghlen |  |  | U | 1245 |  | 14 | 10 | 4 | 2 | 1.6369 | 1.4486 | 0.18823 | 1344 | 0.0078568 | 10 | 6 | 4 | 1 | 0.58815 | 0.39992 | 0.18823
Cunningham | 4693.9 | 32 | 0 | 644 | 0.0037647 | 2037 | 0.011908 | U |  | Cunningham |  |  | U | 1603 |  | 32 | 10 | 22 | 0 | 1.6069 | 0.63835 | 0.96851 | 2014 | 0.011774 | 31 | 9 | 22 | 0 | 1.5845 | 0.61602 | 0.96851
Curtin North | 4402.1 | 18 | 1 | 286 | 0.0016719 | 2463 | 0.014398 | U |  | Curtin North |  |  | U | 1158 |  | 18 | 10 | 8 | 1 | 1.5074 | 1.1811 | 0.32626 | 1278 | 0.007471 | 16 | 8 | 8 | 1 | 0.47443 | 0.14817 | 0.32626
Meacham | 4293.1 | 29 | 0 | 347 | 0.0020285 | 4981 | 0.029118 | U |  | Meacham |  |  | U | 2232 |  | 29 | 17 | 12 | 0 | 1.4699 | 1.1766 | 0.29325 | 4893 | 0.028604 | 27 | 15 | 12 | 0 | 1.2708 | 0.97759 | 0.29325
Stott | 4162.5 | 13 | 2 | 238 | 0.0013913 | 5346 | 0.031252 | U |  | Stott |  |  | U | 1760 |  | 13 | 7 | 6 | 2 | 1.425 | 1.1542 | 0.27082 | 3591 | 0.020992 | 12 | 6 | 6 | 2 | 1.0847 | 0.81388 | 0.27082
Duffy | 3795.6 | 19 | 1 | 243 | 0.0014205 | 1262 | 0.0073775 | U |  | Duffy |  |  | U | 1004 |  | 19 | 10 | 9 | 1 | 1.2992 | 1.0073 | 0.29192 | 1262 | 0.0073775 | 19 | 10 | 9 | 1 | 1.2992 | 1.0073 | 0.29192
Contents

## 5c. Network data outages
ActewAGL
Cause of Outages
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Causes of unplanned sustained outages
Cause of outage | Number of outages
Weather | 4
Equipment failure | 4
Operational error | 0
Vegetation | 1
Animals | 0
Third party impacts | 1
Transmission failure | 0
Load shedding | 0
Inter-distributor connection failure | 0
Other | 0
Contents

## 5d. Network data planned outage
ActewAGL
Planned Outages
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Planned outages
Network categorisation
Planned outages | CBD | Urban | Rural short | Rural long | Whole network
SAIDI - after removing excluded events |  | 42.3203 | 69.2443 |  | 43.0289
SAIFI - after removing excluded events |  | 18.1473 | 26.5214 |  | 18.3677
2013 Report Tab 5d
Table 1: Planned outages
Network categorisation
Planned outages | CBD | Urban | Rural short | Rural long | Whole network
SAIDI - after removing excluded events |  | 42.3203 | 69.2443 |  | 43.0289
SAIFI - after removing excluded events |  | 18.1473 | 26.5214 |  | 18.3677
Contents

## 6. Weighted av cost of debt
ActewAGL
Weighted average cost of debt
2012-13
This information will be used to compare the DBs cost against the benchmark cost of debt. There is no intention to set the regulated cost of debt for a business based on its actual cost of debt.
Notes: the specific method of calculating the weighted average cost of debt for the financial year is ActewAGL's choice but must be fully described. If the description of the methodology cannot fit in this worksheet, ActewAGL can provide details as a separate attachment.
Table 1: Cost of debt
Weighted average cost of debt (%) | 2012-13 | Explanation of calculation method
0
Contents

## 7. Asset installation
ActewAGL
Asset Installation
2012-13
This information is used in the AER’s replacement capex model. The model is used by the AER to assess forecast replacement capex proposals. It may also be used to monitor the asset age profile of the business over time. This will be used as a tool to mon
Table 1: Asset age profile for distribution system assets
Asset group/categories | Replacement life (years) |  | Actual replacement volumes (number of assets replaced) | Replacement unit cost | Asset failures | Total quantity | Year commissioned (number of assets commissioned in each year)
| Mean | Standard deviation |  |  |  |  | 1910 | 1911 | 1912 | 1913 | 1914 | 1915 | 1916 | 1917 | 1918 | 1919 | 1920 | 1921 | 1922 | 1923 | 1924 | 1925 | 1926 | 1927 | 1928 | 1929 | 1930 | 1931 | 1932 | 1933 | 1934 | 1935 | 1936 | 1937 | 1938 | 1939 | 1940 | 1941 | 1942 | 1943 | 1944 | 1945 | 1946 | 1947 | 1948 | 1949 | 1950 | 1951 | 1952 | 1953 | 1954 | 1955 | 1956 | 1957 | 1958 | 1959 | 1960 | 1961 | 1962 | 1963 | 1964 | 1965 | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | Quantity of Unknown Age | NOTES:
Poles
All towers (steel) |  |  | 0 | No data | Nil | 201 | Year commissioned (number of assets commissioned in each year) 2012: 0; Year commissioned (number of assets commissioned in each year) 2013: 0
Subtransmission poles |  |  |  | 19332 | Nil | 1268 | Year commissioned (number of assets commissioned in each year) 2009: 22; Year commissioned (number of assets commissioned in each year) 2011: 8; Year commissioned (number of assets commissioned in each year) 2012: 150; Year commissioned (number of assets commissioned in each year) 2013: 0 |  | Based on project files
Distribution poles |  |  | 793 | 12660 | Nil | 49500 | [21 empty] | 6 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 403.2 | 403.2 | 403.2 | 403.2 | 403.2 | 600 | 600 | 600 | 600 | 600 | 1190 | 1190 | 1190 | 1190 | 1190 | 790 | 790 | 790 | 790 | 790 | 890 | 890 | 900 | 900 | 900 | 800 | 800 | 800 | 800 | 800 | 640 | 640 | 640 | 640 | 640 | 780 | 780 | 780 | 780 | 780 | 600 | 600 | 600 | 600 | 600 | 584 | 584 | 584 | 584 | 584 | 900 | 900 | 900 | 900 | 900 | 1040 | 1040 | 1040 | 1227 | 977 | 934 | 928 | 825 | 793 |  |  | This year provided data does not include private poles or ACT Government owned streetlight poles. 49500 are ActewAGL owned Poles; The total quantity column is the summation of all pole substation commissioned between 1910 to 2013; This template/table did not look at all the pole substation removed from the network over the same period. i.e. the net increment or reduction of pole substation. ActewAGL expect to see distribution poles net reduction is 150 poles every year. ActewAGL suggests that the template should be amended by the AER to improve the quality of data.
Pole top structures
Air Break Switches |  |  | 16 | 12291 |  | 1597 | Year commissioned (number of assets commissioned in each year) 2013: 16
Gas Switches |  |  |  | 14540 |  | 47 | Year commissioned (number of assets commissioned in each year) 2012: 4; Year commissioned (number of assets commissioned in each year) 2013: 4
HV Load Break Switch |  |  | 0 | 36221 |  | 4 | bar: Year commissioned (number of assets commissioned in each year) 2009
HV Links |  |  |  | 12291 |  | 1486 | Year commissioned (number of assets commissioned in each year) 2013: 10
Reclosers |  |  |  | 36221 |  | 31 | Year commissioned (number of assets commissioned in each year) 2012: 0; Year commissioned (number of assets commissioned in each year) 2013: 0
Pole Substations |  |  |  | 57885 |  | 1415 | [37 empty] | 2 | 1 | 1 | 6 | 0 | 19 | 8 | 1 | 11 | 6 | 6 | 13 | 5 | 6 | 17 | 8 | 12 | 20 | 13 | 20 | 54 | 45 | 86 | 32 | 49 | 65 | 43 | 52 | 41 | 35 | 54 | 41 | 39 | 34 | 25 | 17 | 26 | 22 | 16 | 13 | 17 | 24 | 20 | 24 | 18 | 17 | 13 | 9 | 8 | 6 | 5 | 2 | 1 | 1 | 10 | 16 | 10 | 33 | 50 | 32 | 44 | 38 | 35 | 37 | 28 | 24 | 34 |  |  | The total quantity column is the summation of all pole substation commissioned between 1910 to 2013; This template/table did not look at all the pole substation removed from the network over the same period. i.e. the net increment or reduction of pole substation. ActewAGL expects pole substation to reduce by very small amount every year due to undergrounding from land development. ActewAGL suggests that the template should be amended by the AER to improve the quality of data.
Conductors
Overhead 22kV & 11kV (km) |  |  | 0 | 88621 |  | 1014 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 1 | 5 | 5 | 5 | 7 | 12 | 15 | 17 | 19 | 10 | 21 | 22 | 27 | 41 | 37 | 27 | 26 | 35 | 49 | 39 | 31 | 29 | 47 | 52 | 48 | 20 | 36 | 32 | 35 | 45 | 28 | 28 | 17 | 5 | 7 | 7 | 2 | 9 | 12 | 14 | 15 | 19 | 20 | 30 | 12 | 0 | 0 | 0 | 0 | 187 | 4 |  |  | Prior to 2006-7, asset information was sourced from modelling conducted by SKM as submittted to the AER in 2008. Post 2007 figures are as per ActewAGL annual reports / GIS. Negative growth in O/H lines due to growth in underground cable in last 4 years.
Overhead LV (km) |  |  | 2 | 351067 |  | 1186 | [10 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 13 | 5 | 5 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1 | 5 | 3 | 0 | 5 | 8 | 1 | 5 | 20 | 23 | 12 | 12 | 14 | 32 | 62 | 36 | 14 | 15 | 0 | 13 | 23 | 26 | 12 | 30 | 0 | 10 | 7 | 29 | 95 | 0 | 11 | 83 | 124 | 118 | 0 | 38 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 46 | 39 | 45 | 38 | 18 | 30 | 0 | 0 | 0 | 0 | 0 | 2 |  |  | Prior to 2006-7, asset information was sourced from modelling conducted by SKM as submittted to the AER in 2008. Post 2007 figures are as per ActewAGL annual reports / GIS. Does not include LV Service cables. Negative growth in O/H lines due to growth in underground in last 4 yeras.
<asset type 3> | [5 empty] | 0
Underground cables | [112 empty] | Prior to 2006-7, asset information was sourced from modelling conducted by SKM as submittted to the AER in 2008. Post 2007 figures are as per ActewAGL annual reports / GIS.
HV (km) |  |  | 0 | 428674 |  | 1478 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 2 | 1 | 1 | 7 | 7 | 7 | 9 | 15 | 19 | 21 | 24 | 13 | 27 | 28 | 33 | 49 | 45 | 33 | 32 | 43 | 59 | 49 | 38 | 36 | 57 | 65 | 58 | 26 | 44 | 40 | 43 | 55 | 34 | 34 | 22 | 7 | 9 | 9 | 3 | 12 | 15 | 18 | 19 | 24 | 25 | 37 | 14 | 25 | 24 | 31 | 32 | 60 | 30 |  |  | Prior to 2006-7, asset information was sourced from modelling conducted by SKM as submittted to the AER in 2008. Post 2007 figures are as per ActewAGL annual reports / GIS. Does not include LV Service cables.
LV (km) |  |  | 2 | 285257 |  | 1242 | [10 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 4 | 4 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 4 | 3 | 0 | 4 | 7 | 1 | 4 | 17 | 20 | 10 | 10 | 12 | 28 | 54 | 31 | 12 | 12 | 0 | 11 | 20 | 23 | 10 | 26 | 0 | 8 | 6 | 25 | 82 | 0 | 9 | 72 | 108 | 103 | 0 | 33 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 40 | 34 | 39 | 33 | 16 | 26 | 24 | 44 | 37 | 51 | 56 | 26
<asset type 3> | [5 empty] | 0
Services (incl. LV pillars and LV service pits)
LV pillars (Nos.) |  |  |  | 6742 |  | 14488 | [10 empty] | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 13 | 0 | 0 | 0 | 117 | 40 | 42 | 0 | 22 | 12 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 14 | 40 | 32 | 0 | 43 | 75 | 8 | 40 | 176 | 206 | 106 | 104 | 119 | 291 | 561 | 322 | 119 | 124 | 0 | 115 | 203 | 236 | 107 | 270 | 3 | 78 | 59 | 255 | 845 | 0 | 94 | 739 | 1109 | 1062 | 0 | 341 | 0 | 0 | 0 | 0 | 71 | 1 | 0 | 412 | 346 | 403 | 342 | 163 | 270 | 395 | 394 | 395 | 396 | 2095 | 0 |  |  | Prior to 2006-7, asset information was sourced from modelling conducted by SKM as submittted to the AER in 2008. Post 2007 figures are the avarage no of units commissioned over 4 years.
LV service pits (Nos.) |  |  | 0 |  |  | 0 | Year commissioned (number of assets commissioned in each year) 2012: 0; Year commissioned (number of assets commissioned in each year) 2013: 0
<asset type 3> | [5 empty] | 0
Distribution transformers
All distribution Transformers |  |  | 80% | 63424 |  | 4978 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 2 | 1 | 3 | 1 | 2 | 4 | 2 | 12 | 8 | 8 | 13 | 29 | 12 | 21 | 18 | 38 | 45 | 62 | 59 | 35 | 65 | 72 | 72 | 118 | 98 | 83 | 64 | 98 | 134 | 122 | 100 | 103 | 134 | 153 | 137 | 76 | 125 | 94 | 95 | 120 | 81 | 106 | 53 | 20 | 29 | 26 | 13 | 26 | 32 | 44 | 44 | 59 | 71 | 106 | 30 | 345 | 345 | 345 | 345 | 63 | 53 |  |  | Prior to 2006-7, asset information was sourced from modelling conducted by SKM as submittted to the AER in 2008. Post 2007 figures are the average no of units commissioned over 4 years.
<asset type 2> | [5 empty] | 0
<asset type 3> | [5 empty] | 0
Distribution switchgear
HV Cast Resin Switchgear |  |  | 0 | 34044 |  | 1163 | Year commissioned (number of assets commissioned in each year) 2012: 45; Year commissioned (number of assets commissioned in each year) 2013: 0
All other switchgear units |  |  | 0 | 34044 |  | 2365 | Year commissioned (number of assets commissioned in each year) 2012: 22; Year commissioned (number of assets commissioned in each year) 2013: 0
<asset type 3> | [5 empty] | 0
Distribution 'other assets'
<asset type 1> | [5 empty] | 0 | Year commissioned (number of assets commissioned in each year) 2013: 0
<asset type 2> | [5 empty] | 0
<asset type 3> | [5 empty] | 0
Zone transformers
132kV Power Transformer |  |  | 0 | 2015796.003 |  | 27 | Year commissioned (number of assets commissioned in each year) 1967: 5; Year commissioned (number of assets commissioned in each year) 1971: 2; Year commissioned (number of assets commissioned in each year) 1975: 1; Year commissioned (number of assets commissioned in each year) 1976: 1; Year commissioned (number of assets commissioned in each year) 1978: 2; Year commissioned (number of assets commissioned in each year) 1979: 2; Year commissioned (number of assets commissioned in each year) 1980: 1; Year commissioned (number of assets commissioned in each year) 1981: 1; Year commissioned (number of assets commissioned in each year) 1982: 1; Year commissioned (number of assets commissioned in each year) 1983: 1; Year commissioned (number of assets commissioned in each year) 1984: 1; Year commissioned (number of assets commissioned in each year) 1985: 2; Year commissioned (number of assets commissioned in each year) 1987: 3; Year commissioned (number of assets commissioned in each year) 1989: 2; Year commissioned (number of assets commissioned in each year) 1994: 1; Year commissioned (number of assets commissioned in each year) 1995: 1; Year commissioned (number of assets commissioned in each year) 2013: 0 |  | Total "In service" units should be 27 including MoSS Tx in 2011 & Civic Tx in 2012. | WASP - Power transformer report - year made is taken as date of installation
66kV Power Transformer |  |  | 1 | 1265796.003 |  | 4 | [106 empty] | Fyshwick TX3 commissioned in Jul 2013. | WASP - Power transformer report - year made is taken as date of installation | bar: Year commissioned (number of assets commissioned in each year) 2001; Year commissioned (number of assets commissioned in each year) 2006; Year commissioned (number of assets commissioned in each year) 2008; Year commissioned (number of assets commissioned in each year) 2013
ZS Auxiliary Transformer |  |  | 0 | 112556.861 |  | 23 | Year commissioned (number of assets commissioned in each year) 1966: 2; Year commissioned (number of assets commissioned in each year) 1971: 4; Year commissioned (number of assets commissioned in each year) 1977: 2; Year commissioned (number of assets commissioned in each year) 1979: 2; Year commissioned (number of assets commissioned in each year) 1982: 2; Year commissioned (number of assets commissioned in each year) 1985: 2; Year commissioned (number of assets commissioned in each year) 1986: 2; Year commissioned (number of assets commissioned in each year) 1989: 2; Year commissioned (number of assets commissioned in each year) 1994: 2; Year commissioned (number of assets commissioned in each year) 2002: 2; Year commissioned (number of assets commissioned in each year) 2013: 0 |  | 1 unit was installed at MoSS. | WASP - Auxillary Transformers Report - year made is taken as date of installation
ZS Earthing Transformer |  |  | 0 | 163056.861 |  | 27 | Year commissioned (number of assets commissioned in each year) 1966: 4; Year commissioned (number of assets commissioned in each year) 1971: 2; Year commissioned (number of assets commissioned in each year) 1975: 2; Year commissioned (number of assets commissioned in each year) 1977: 2; Year commissioned (number of assets commissioned in each year) 1979: 2; Year commissioned (number of assets commissioned in each year) 1980: 1; Year commissioned (number of assets commissioned in each year) 1982: 1; Year commissioned (number of assets commissioned in each year) 1983: 4; Year commissioned (number of assets commissioned in each year) 1985: 2; Year commissioned (number of assets commissioned in each year) 1986: 3; Year commissioned (number of assets commissioned in each year) 1993: 1; Year commissioned (number of assets commissioned in each year) 1994: 2; Year commissioned (number of assets commissioned in each year) 2013: 0 |  | Total "In service" units should be 27 including MoSS Tx in 2011 & Civic Tx in 2012. 1 unit is system spare | WASP - Zone Substation Earthing Transformers Report - Year made is taken as date of installation
Zone switchgear
132kV Circuit Breaker |  |  | 1 | 231512.0819 |  | 63 | Year commissioned (number of assets commissioned in each year) 1966: 8; Year commissioned (number of assets commissioned in each year) 1967: 8; Year commissioned (number of assets commissioned in each year) 1971: 22; Year commissioned (number of assets commissioned in each year) 1977: 1; Year commissioned (number of assets commissioned in each year) 1978: 24; Year commissioned (number of assets commissioned in each year) 1981: 13; Year commissioned (number of assets commissioned in each year) 1983: 4; Year commissioned (number of assets commissioned in each year) 1986: 25; Year commissioned (number of assets commissioned in each year) 1988: 11; Year commissioned (number of assets commissioned in each year) 1993: 11; Year commissioned (number of assets commissioned in each year) 2004: 7; Year commissioned (number of assets commissioned in each year) 2013: 1 |  | 139 units are "In Service" and exclude System Spare. RG - Added Isolator for MoSS | WASP - Isolator Report - year of manufacture taken as installation date - Sort by Isolator type eg 66kv / 132 kv
132kV Isolator |  |  | 0 | 54398.028 |  | 141 | Year commissioned (number of assets commissioned in each year) 1973: 4; Year commissioned (number of assets commissioned in each year) 1975: 1; Year commissioned (number of assets commissioned in each year) 1977: 4; Year commissioned (number of assets commissioned in each year) 1979: 11; Year commissioned (number of assets commissioned in each year) 1981: 4; Year commissioned (number of assets commissioned in each year) 1982: 1; Year commissioned (number of assets commissioned in each year) 1983: 7; Year commissioned (number of assets commissioned in each year) 1985: 7; Year commissioned (number of assets commissioned in each year) 1986: 8; Year commissioned (number of assets commissioned in each year) 1989: 4; Year commissioned (number of assets commissioned in each year) 1992: 3; Year commissioned (number of assets commissioned in each year) 1994: 4; Year commissioned (number of assets commissioned in each year) 1995: 1; Year commissioned (number of assets commissioned in each year) 1996: 1; Year commissioned (number of assets commissioned in each year) 2013: 0 |  | Replacement: 1xWanniassa (2010), 1xCity East (2012), 1xWanniassa (2012) Additions: 1xMoSS (2011), 3x Civic (2012) | WASP - Cicuit Breaker Report provides the number of circuit breakers - year of manufacture in that report can be taken as installation date. Lifecycle of circuit breaker has been estimated at 50 yrs.
132kV Isolator with Earth Switch |  |  | 0 | 59765.628 |  | 37 | Year commissioned (number of assets commissioned in each year) 1971: 6; Year commissioned (number of assets commissioned in each year) 2013: 0 |  | 5 units are in service having 1 unit as System Spare. | WASP - Cicuit Breaker Report provides the number of circuit breakers - year of manufacture in that report can be taken as installation date. Lifecycle of circuit breaker has been estimated at 50 yrs.
66kV Circuit Breaker |  |  | 0 | 189712.0819 |  | 5 | Year commissioned (number of assets commissioned in each year) 1971: 4; Year commissioned (number of assets commissioned in each year) 2013: 0 |  | 4ZA was installed in 1985 hence total no. of "In Service" units are 5. | WASP - Isolator Report - year of manufacture taken as installation date - Sort by Isolator type eg 66kv / 132 kv
66kV Isolator |  |  | 0 | 52298.028 |  | 5 | Year commissioned (number of assets commissioned in each year) 1966: 2; Year commissioned (number of assets commissioned in each year) 1967: 2; Year commissioned (number of assets commissioned in each year) 1971: 5; Year commissioned (number of assets commissioned in each year) 1978: 7; Year commissioned (number of assets commissioned in each year) 1981: 3; Year commissioned (number of assets commissioned in each year) 1983: 1; Year commissioned (number of assets commissioned in each year) 1986: 10; Year commissioned (number of assets commissioned in each year) 1988: 2; Year commissioned (number of assets commissioned in each year) 1993: 2; Year commissioned (number of assets commissioned in each year) 2004: 2; Year commissioned (number of assets commissioned in each year) 2013: 0 |  | 35 units are "In Service" and exclude System Spare. RG - Added 1 ESW for the MoSS | WASP - Earth Switch - year of manufacture taken as installation date
11kV Circuit Breaker |  |  | 0 | 39399.074 |  | 388 | Year commissioned (number of assets commissioned in each year) 1966: 22; Year commissioned (number of assets commissioned in each year) 1971: 35; Year commissioned (number of assets commissioned in each year) 1974: 22; Year commissioned (number of assets commissioned in each year) 1977: 22; Year commissioned (number of assets commissioned in each year) 1979: 20; Year commissioned (number of assets commissioned in each year) 1981: 16; Year commissioned (number of assets commissioned in each year) 1982: 11; Year commissioned (number of assets commissioned in each year) 1983: 11; Year commissioned (number of assets commissioned in each year) 1986: 72; Year commissioned (number of assets commissioned in each year) 1987: 8; Year commissioned (number of assets commissioned in each year) 1988: 15; Year commissioned (number of assets commissioned in each year) 1989: 27; Year commissioned (number of assets commissioned in each year) 1993: 24; Year commissioned (number of assets commissioned in each year) 1994: 63; Year commissioned (number of assets commissioned in each year) 1995: 11; Year commissioned (number of assets commissioned in each year) 2001: 15; Year commissioned (number of assets commissioned in each year) 2013: 13 |  | 336 units are "In Service" and exclude System Spare & Earth Truck. Additions: 2 at the MoSS & 13 new at Civic ZS | WASP - Cicuit Breaker Report provides the number of circuit breakers - year of manufacture in that report can be taken as installation date. Sort by Circuit Breaker type eg 66 kv / 132kv Lifecycle of circuit breaker has been estimated at 50 yrs.
SF6 Modular Switchgear |  |  | 0 | 516187.1226 |  | 0 | Year commissioned (number of assets commissioned in each year) 2013: 0
Zone 'other assets'
ZS 132kV Voltage Transformer |  |  | 6 | 40492.5624 |  | 96 | Year commissioned (number of assets commissioned in each year) 1967: 14; Year commissioned (number of assets commissioned in each year) 1974: 11; Year commissioned (number of assets commissioned in each year) 1977: 5; Year commissioned (number of assets commissioned in each year) 1979: 21; Year commissioned (number of assets commissioned in each year) 1981: 6; Year commissioned (number of assets commissioned in each year) 1985: 9; Year commissioned (number of assets commissioned in each year) 1986: 12; Year commissioned (number of assets commissioned in each year) 1988: 6; Year commissioned (number of assets commissioned in each year) 1994: 5; Year commissioned (number of assets commissioned in each year) 2008: 8; Year commissioned (number of assets commissioned in each year) 2010: 12; Year commissioned (number of assets commissioned in each year) 2013: 6 |  | Note 90 includes top and bottom units | WASP - Voltage Transformer Report - year of manufacture taken as installation date. Sort by transformer type
ZS 132kV Current Transformer |  |  | 1 | 45278.6521 |  | 147 | Year commissioned (number of assets commissioned in each year) 1967: 19; Year commissioned (number of assets commissioned in each year) 1971: 3; Year commissioned (number of assets commissioned in each year) 1974: 6; Year commissioned (number of assets commissioned in each year) 1975: 6; Year commissioned (number of assets commissioned in each year) 1976: 6; Year commissioned (number of assets commissioned in each year) 1982: 7; Year commissioned (number of assets commissioned in each year) 1985: 25; Year commissioned (number of assets commissioned in each year) 1986: 18; Year commissioned (number of assets commissioned in each year) 1987: 6; Year commissioned (number of assets commissioned in each year) 1988: 15; Year commissioned (number of assets commissioned in each year) 1993: 1; Year commissioned (number of assets commissioned in each year) 1994: 12; Year commissioned (number of assets commissioned in each year) 2009: 27; Year commissioned (number of assets commissioned in each year) 2010: 1; Year commissioned (number of assets commissioned in each year) 2013: 1 |  |  | WASP - Current Transformer Report - year of manufacure taken as installation date. Sort by transformer type
ZS 66kV Voltage Transformer |  |  |  | 38392.5624 |  | 2 | Year commissioned (number of assets commissioned in each year) 1967: 2; Year commissioned (number of assets commissioned in each year) 2013: 0 |  | Units reported as single phase units | WASP - Voltage Transformer Report - year of manufacture taken as installation date. Sort by transformer type
ZS 66kV Current Transformer |  |  |  | 41078.6521 |  | 15 | Year commissioned (number of assets commissioned in each year) 1971: 18; Year commissioned (number of assets commissioned in each year) 2013: 0 |  | 15 units are "In Service" keeping 3 units as System Spare. | WASP - Current Transformer Report - year of manufacure taken as installation date. Sort by transformer type
SCADA and protection
<asset type 1> | [5 empty] | 0
<asset type 2> | [5 empty] | 0
<asset type 3> | [5 empty] | 0
Other
<asset type 1> | [5 empty] | 0
<asset type 2> | [5 empty] | 0
<asset type 3> | [5 empty] | 0
Notes:
* Replacement unit costs are in FY12/13 dollars
* Zone asset estimates includes preliminary costs e.g. tender set up costs which is only incurred once if multiple units are being replaced at the same time
* A new category "SF6 Modular Switchgear" created. This asset is currently only used in the new East Lake ZS
Note on DF13: 66 kV line only
Contents