#R000500_016_RAMP_F | 2009-02-10 | 1 | Hard Ramping constraint for constraint T>T_LIPM_220_3, Effective Date: 10/02/2009, Version: 1
#R000500_016_RAMP_V | 2009-02-10 | 1 | Soft Ramping constraint for constraint T>T_LIPM_220_3, Effective Date: 10/02/2009, Version: 1
#R000500_017_RAMP_F | 2009-02-10 | 1 | Hard Ramping constraint for constraint T^T_LIPM_1, Effective Date: 10/02/2009, Version: 1
#R000500_017_RAMP_V | 2009-02-10 | 1 | Soft Ramping constraint for constraint T^T_LIPM_1, Effective Date: 10/02/2009, Version: 1
#R000500_018_RAMP_F | 2009-02-10 | 1 | Hard Ramping constraint for constraint T^T_LIPM_2, Effective Date: 10/02/2009, Version: 1
#R000500_018_RAMP_V | 2009-02-10 | 1 | Soft Ramping constraint for constraint T^T_LIPM_2, Effective Date: 10/02/2009, Version: 1
#R000500_019_RAMP_F | 2009-02-10 | 1 | Hard Ramping constraint for constraint T^T_LIPM_3, Effective Date: 10/02/2009, Version: 1
#R000500_019_RAMP_V | 2009-02-10 | 1 | Soft Ramping constraint for constraint T^T_LIPM_3, Effective Date: 10/02/2009, Version: 1
#R000500_020_RAMP_F | 2009-02-10 | 1 | Hard Ramping constraint for constraint T^T_LIPM_4, Effective Date: 10/02/2009, Version: 1
#R000500_020_RAMP_V | 2009-02-10 | 1 | Soft Ramping constraint for constraint T^T_LIPM_4, Effective Date: 10/02/2009, Version: 1
#R000500_021_RAMP_F | 2009-02-10 | 1 | Hard Ramping constraint for constraint T^T_LIPM_5, Effective Date: 10/02/2009, Version: 1
#R000500_021_RAMP_V | 2009-02-10 | 1 | Soft Ramping constraint for constraint T^T_LIPM_5, Effective Date: 10/02/2009, Version: 1
#R000500_022_RAMP_F | 2009-02-10 | 1 | Hard Ramping constraint for constraint T^T_LIPM_6, Effective Date: 10/02/2009, Version: 1
#R000500_022_RAMP_V | 2009-02-10 | 1 | Soft Ramping constraint for constraint T^T_LIPM_6, Effective Date: 10/02/2009, Version: 1
#R000501_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N::N_BWMP_1, Effective Date: 11/02/2009, Version: 1
#R000501_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N::N_BWMP_1, Effective Date: 11/02/2009, Version: 1
#R000501_002_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N::Q_BWMP_1, Effective Date: 11/02/2009, Version: 1
#R000501_002_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N::Q_BWMP_1, Effective Date: 11/02/2009, Version: 1
#R000501_003_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N::V_BWMP, Effective Date: 11/02/2009, Version: 1
#R000501_003_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N::V_BWMP, Effective Date: 11/02/2009, Version: 1
#R000501_004_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>N-BWMP_01, Effective Date: 11/02/2009, Version: 1
#R000501_004_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>N-BWMP_01, Effective Date: 11/02/2009, Version: 1
#R000501_005_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>N-BWMP_02, Effective Date: 11/02/2009, Version: 1
#R000501_005_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>N-BWMP_02, Effective Date: 11/02/2009, Version: 1
#R000501_006_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>N-BWMP_03, Effective Date: 11/02/2009, Version: 1
#R000501_006_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>N-BWMP_03, Effective Date: 11/02/2009, Version: 1
#R000501_007_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>N-BWMP_04, Effective Date: 11/02/2009, Version: 1
#R000501_007_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>N-BWMP_04, Effective Date: 11/02/2009, Version: 1
#R000501_008_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>N-BWMP_05, Effective Date: 11/02/2009, Version: 1
#R000501_008_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>N-BWMP_05, Effective Date: 11/02/2009, Version: 1
#R000501_009_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>N-BWMP_06, Effective Date: 11/02/2009, Version: 1
#R000501_009_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>N-BWMP_06, Effective Date: 11/02/2009, Version: 1
#R000501_010_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>N-BWMP_07, Effective Date: 11/02/2009, Version: 1
#R000501_010_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>N-BWMP_07, Effective Date: 11/02/2009, Version: 1
#R000502_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>N-KSNB_01, Effective Date: 11/02/2009, Version: 1
#R000502_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>N-KSNB_01, Effective Date: 11/02/2009, Version: 1
#R000502_002_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>N-KSNB_02, Effective Date: 11/02/2009, Version: 1
#R000502_002_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>N-KSNB_02, Effective Date: 11/02/2009, Version: 1
#R000502_003_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>N-KSNB_TE_1, Effective Date: 11/02/2009, Version: 1
#R000502_003_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>N-KSNB_TE_1, Effective Date: 11/02/2009, Version: 1
#R000503_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^Q_AR_VCA, Effective Date: 11/02/2009, Version: 1
#R000503_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^Q_AR_VCA, Effective Date: 11/02/2009, Version: 1
#R000503_002_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^Q_AR_VCB, Effective Date: 11/02/2009, Version: 1
#R000503_002_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^Q_AR_VCB, Effective Date: 11/02/2009, Version: 1
#R000503_003_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 11/02/2009, Version: 1
#R000503_003_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 11/02/2009, Version: 1
#R000503_004_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^^Q_AR_VC_B2, Effective Date: 11/02/2009, Version: 1
#R000503_004_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^^Q_AR_VC_B2, Effective Date: 11/02/2009, Version: 1
#R000503_005_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^^Q_AR_VC_B3, Effective Date: 11/02/2009, Version: 1
#R000503_005_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^^Q_AR_VC_B3, Effective Date: 11/02/2009, Version: 1
#R000503_006_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^^Q_AR_VC_B4, Effective Date: 11/02/2009, Version: 1
#R000503_006_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^^Q_AR_VC_B4, Effective Date: 11/02/2009, Version: 1
#R000503_007_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^^Q_AR_VC_B5, Effective Date: 11/02/2009, Version: 1
#R000503_007_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^^Q_AR_VC_B5, Effective Date: 11/02/2009, Version: 1
#R000503_008_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^^Q_AR_VC_B6, Effective Date: 11/02/2009, Version: 1
#R000503_008_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^^Q_AR_VC_B6, Effective Date: 11/02/2009, Version: 1
#R000504_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>N-ERVP_A, Effective Date: 11/02/2009, Version: 1
#R000504_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>N-ERVP_A, Effective Date: 11/02/2009, Version: 1
#R000504_002_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>N-ERVP_B, Effective Date: 11/02/2009, Version: 1
#R000504_002_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>N-ERVP_B, Effective Date: 11/02/2009, Version: 1
#R000505_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint #V-S-MNSP1_I_E, Effective Date: 11/02/2009, Version: 1
#R000505_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint #V-S-MNSP1_I_E, Effective Date: 11/02/2009, Version: 1
#R000506_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint CA_SPS_38A2048F_01, Effective Date: 11/02/2009, Version: 1
#R000506_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint CA_SPS_38A2048F_01, Effective Date: 11/02/2009, Version: 1
#R000506_002_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint CA_SPS_38A2048F_02, Effective Date: 11/02/2009, Version: 1
#R000506_002_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint CA_SPS_38A2048F_02, Effective Date: 11/02/2009, Version: 1
#R000507_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N_V_HV0300, Effective Date: 11/02/2009, Version: 1
#R000507_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N_V_HV0300, Effective Date: 11/02/2009, Version: 1
#R000508_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N_V_HV0300, Effective Date: 11/02/2009, Version: 1
#R000508_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N_V_HV0300, Effective Date: 11/02/2009, Version: 1
#R000509_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint #V-S-MNSP1_I_E, Effective Date: 11/02/2009, Version: 1
#R000509_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint #V-S-MNSP1_I_E, Effective Date: 11/02/2009, Version: 1
#R000510_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint CA_SPS_38A2048F_01, Effective Date: 11/02/2009, Version: 1
#R000510_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint CA_SPS_38A2048F_01, Effective Date: 11/02/2009, Version: 1
#R000510_002_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint CA_SPS_38A2048F_02, Effective Date: 11/02/2009, Version: 1
#R000510_002_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint CA_SPS_38A2048F_02, Effective Date: 11/02/2009, Version: 1
#R000511_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>V_SMTXH1, Effective Date: 11/02/2009, Version: 1
#R000511_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>V_SMTXH1, Effective Date: 11/02/2009, Version: 1
#R000511_002_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>V_SMTXH1_2, Effective Date: 11/02/2009, Version: 1
#R000511_002_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>V_SMTXH1_2, Effective Date: 11/02/2009, Version: 1
#R000511_003_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>V_SMTXH1_3, Effective Date: 11/02/2009, Version: 1
#R000511_003_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>V_SMTXH1_3, Effective Date: 11/02/2009, Version: 1
#R000511_004_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^^V_SMTXH1_2, Effective Date: 11/02/2009, Version: 1
#R000511_004_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^^V_SMTXH1_2, Effective Date: 11/02/2009, Version: 1
#R000511_005_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^^V_SMTXH1_R, Effective Date: 11/02/2009, Version: 1
#R000511_005_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^^V_SMTXH1_R, Effective Date: 11/02/2009, Version: 1
#R000511_006_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint V>>N_SMTXH1, Effective Date: 11/02/2009, Version: 1
#R000511_006_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint V>>N_SMTXH1, Effective Date: 11/02/2009, Version: 1
#R000511_007_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint V>>V_SMTS_TX_H1_2A_R, Effective Date: 11/02/2009, Version: 1
#R000511_007_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint V>>V_SMTS_TX_H1_2A_R, Effective Date: 11/02/2009, Version: 1
#R000511_008_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint V>>V_SMTS_TX_H1_2B_R, Effective Date: 11/02/2009, Version: 1
#R000511_008_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint V>>V_SMTS_TX_H1_2B_R, Effective Date: 11/02/2009, Version: 1
#R000512_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>V_SMTXH1, Effective Date: 11/02/2009, Version: 1
#R000512_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>V_SMTXH1, Effective Date: 11/02/2009, Version: 1
#R000512_002_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>V_SMTXH1_2, Effective Date: 11/02/2009, Version: 1
#R000512_002_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>V_SMTXH1_2, Effective Date: 11/02/2009, Version: 1
#R000512_003_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>V_SMTXH1_3, Effective Date: 11/02/2009, Version: 1
#R000512_003_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>V_SMTXH1_3, Effective Date: 11/02/2009, Version: 1
#R000512_004_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^^V_SMTXH1_2, Effective Date: 11/02/2009, Version: 1
#R000512_004_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^^V_SMTXH1_2, Effective Date: 11/02/2009, Version: 1
#R000512_005_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^^V_SMTXH1_R, Effective Date: 11/02/2009, Version: 1
#R000512_005_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^^V_SMTXH1_R, Effective Date: 11/02/2009, Version: 1
#R000512_006_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint V>>N_SMTXH1, Effective Date: 11/02/2009, Version: 1
#R000512_006_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint V>>N_SMTXH1, Effective Date: 11/02/2009, Version: 1
#R000512_007_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint V>>V_SMTS_TX_H1_2A_R, Effective Date: 11/02/2009, Version: 1
#R000512_007_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint V>>V_SMTS_TX_H1_2A_R, Effective Date: 11/02/2009, Version: 1
#R000512_008_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint V>>V_SMTS_TX_H1_2B_R, Effective Date: 11/02/2009, Version: 1
#R000512_008_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint V>>V_SMTS_TX_H1_2B_R, Effective Date: 11/02/2009, Version: 1
#R000513_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint #V-S-MNSP1_I_E, Effective Date: 11/02/2009, Version: 1
#R000513_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint #V-S-MNSP1_I_E, Effective Date: 11/02/2009, Version: 1
#R000514_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint CA_SPS_38A2048F_01, Effective Date: 11/02/2009, Version: 1
#R000514_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint CA_SPS_38A2048F_01, Effective Date: 11/02/2009, Version: 1
#R000514_002_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint CA_SPS_38A2048F_02, Effective Date: 11/02/2009, Version: 1
#R000514_002_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint CA_SPS_38A2048F_02, Effective Date: 11/02/2009, Version: 1
#R000515_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N_V_HV0300, Effective Date: 11/02/2009, Version: 1
#R000515_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N_V_HV0300, Effective Date: 11/02/2009, Version: 1
#R000516_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>V_SMTXH1, Effective Date: 11/02/2009, Version: 1
#R000516_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>V_SMTXH1, Effective Date: 11/02/2009, Version: 1
#R000516_002_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>V_SMTXH1_2, Effective Date: 11/02/2009, Version: 1
#R000516_002_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>V_SMTXH1_2, Effective Date: 11/02/2009, Version: 1
#R000516_003_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N>>V_SMTXH1_3, Effective Date: 11/02/2009, Version: 1
#R000516_003_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N>>V_SMTXH1_3, Effective Date: 11/02/2009, Version: 1
#R000516_004_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^^V_SMTXH1_2, Effective Date: 11/02/2009, Version: 1
#R000516_004_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^^V_SMTXH1_2, Effective Date: 11/02/2009, Version: 1
#R000516_005_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N^^V_SMTXH1_R, Effective Date: 11/02/2009, Version: 1
#R000516_005_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N^^V_SMTXH1_R, Effective Date: 11/02/2009, Version: 1
#R000516_006_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint V>>N_SMTXH1, Effective Date: 11/02/2009, Version: 1
#R000516_006_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint V>>N_SMTXH1, Effective Date: 11/02/2009, Version: 1
#R000516_007_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint V>>V_SMTS_TX_H1_2A_R, Effective Date: 11/02/2009, Version: 1
#R000516_007_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint V>>V_SMTS_TX_H1_2A_R, Effective Date: 11/02/2009, Version: 1
#R000516_008_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint V>>V_SMTS_TX_H1_2B_R, Effective Date: 11/02/2009, Version: 1
#R000516_008_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint V>>V_SMTS_TX_H1_2B_R, Effective Date: 11/02/2009, Version: 1
#R000517_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint #V-S-MNSP1_I_E, Effective Date: 11/02/2009, Version: 1
#R000517_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint #V-S-MNSP1_I_E, Effective Date: 11/02/2009, Version: 1
#R000518_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint CA_SPS_38A2048F_01, Effective Date: 11/02/2009, Version: 1
#R000518_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint CA_SPS_38A2048F_01, Effective Date: 11/02/2009, Version: 1
#R000518_002_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint CA_SPS_38A2048F_02, Effective Date: 11/02/2009, Version: 1
#R000518_002_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint CA_SPS_38A2048F_02, Effective Date: 11/02/2009, Version: 1
#R000519_001_RAMP_F | 2009-02-11 | 1 | Hard Ramping constraint for constraint N_V_HV0300, Effective Date: 11/02/2009, Version: 1
#R000519_001_RAMP_V | 2009-02-11 | 1 | Soft Ramping constraint for constraint N_V_HV0300, Effective Date: 11/02/2009, Version: 1
#R000520_001_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint N>N-ARKS_TE_A1, Effective Date: 12/02/2009, Version: 1
#R000520_001_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint N>N-ARKS_TE_A1, Effective Date: 12/02/2009, Version: 1
#R000521_001_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint N>>N-ERVP_A, Effective Date: 12/02/2009, Version: 1
#R000521_001_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint N>>N-ERVP_A, Effective Date: 12/02/2009, Version: 1
#R000521_002_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint N>>N-ERVP_B, Effective Date: 12/02/2009, Version: 1
#R000521_002_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint N>>N-ERVP_B, Effective Date: 12/02/2009, Version: 1
#R000522_001_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint N^^V_X_DDSM_TWO, Effective Date: 12/02/2009, Version: 1
#R000522_001_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint N^^V_X_DDSM_TWO, Effective Date: 12/02/2009, Version: 1
#R000522_002_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint N_V_HV0750, Effective Date: 12/02/2009, Version: 1
#R000522_002_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint N_V_HV0750, Effective Date: 12/02/2009, Version: 1
#R000522_003_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint V>>V_X_DDSM_TWO, Effective Date: 12/02/2009, Version: 1
#R000522_003_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint V>>V_X_DDSM_TWO, Effective Date: 12/02/2009, Version: 1
#R000523_001_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint N>>V_SMTXH1, Effective Date: 12/02/2009, Version: 1
#R000523_001_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint N>>V_SMTXH1, Effective Date: 12/02/2009, Version: 1
#R000523_002_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint N>>V_SMTXH1_2, Effective Date: 12/02/2009, Version: 1
#R000523_002_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint N>>V_SMTXH1_2, Effective Date: 12/02/2009, Version: 1
#R000523_003_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint N>>V_SMTXH1_3, Effective Date: 12/02/2009, Version: 1
#R000523_003_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint N>>V_SMTXH1_3, Effective Date: 12/02/2009, Version: 1
#R000523_004_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint N^^V_SMTXH1_2, Effective Date: 12/02/2009, Version: 1
#R000523_004_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint N^^V_SMTXH1_2, Effective Date: 12/02/2009, Version: 1
#R000523_005_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint N^^V_SMTXH1_R, Effective Date: 12/02/2009, Version: 1
#R000523_005_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint N^^V_SMTXH1_R, Effective Date: 12/02/2009, Version: 1
#R000523_006_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint V>>N_SMTXH1, Effective Date: 12/02/2009, Version: 1
#R000523_006_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint V>>N_SMTXH1, Effective Date: 12/02/2009, Version: 1
#R000523_007_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint V>>V_SMTS_TX_H1_2A_R, Effective Date: 12/02/2009, Version: 1
#R000523_007_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint V>>V_SMTS_TX_H1_2A_R, Effective Date: 12/02/2009, Version: 1
#R000523_008_RAMP_F | 2009-02-12 | 1 | Hard Ramping constraint for constraint V>>V_SMTS_TX_H1_2B_R, Effective Date: 12/02/2009, Version: 1
#R000523_008_RAMP_V | 2009-02-12 | 1 | Soft Ramping constraint for constraint V>>V_SMTS_TX_H1_2B_R, Effective Date: 12/02/2009, Version: 1
#R6_20081010115605 | 2008-10-10 | 1 | (TAS1).RAISE6SEC >= 50 (Wt = 5)
#REDBANK1_E | 2004-07-31 | 1 | NMRK1.ENERGY * 1 <= 0 (Wt = 20)
#REECE2_E | 2006-01-25 | 1 | TRCB1.ENERGY * 1 = 0 (Wt = 360)
#REECE2_L5 | 2006-01-25 | 1 | TRCB1.LOWER5MIN * 1 = 0 (Wt = 360)
#REECE2_L6 | 2006-01-25 | 1 | TRCB1.LOWER6SEC * 1 = 0 (Wt = 360)
#REECE2_L60 | 2006-01-25 | 1 | TRCB1.LOWER60SEC * 1 = 0 (Wt = 360)
#REECE2_LR | 2006-01-25 | 1 | TRCB1.LOWERREG * 1 = 0 (Wt = 360)
#REECE2_R5 | 2006-01-25 | 1 | TRCB1.RAISE5MIN * 1 = 0 (Wt = 360)
#REECE2_R6 | 2006-01-25 | 1 | TRCB1.RAISE6SEC * 1 = 0 (Wt = 360)
#REECE2_R60 | 2006-01-25 | 1 | TRCB1.RAISE60SEC * 1 = 0 (Wt = 360)
#REECE2_RR | 2006-01-25 | 1 | TRCB1.RAISEREG * 1 = 0 (Wt = 360)
#ROMA_7_E | 2003-08-17 | 1 | QRMA7.ENERGY * 1 = 34 (Wt = 360)
#ROMA_8_E | 2003-08-17 | 1 | QRMA8.ENERGY * 1 = 34 (Wt = 360)
#RR_20050905072959 | 2005-09-05 | 1 | (QLD1).RAISEREG = 0 (Wt = 20)
#RR_20050905104639 | 2005-09-05 | 1 | (QLD1).RAISEREG = 0 (Wt = 20)
#RR_20050905114634 | 2005-09-05 | 1 | (QLD1).RAISEREG = 0 (Wt = 20)
#RR_20051201144055 | 2005-12-01 | 3 | (TAS1).RAISEREG >= 100 (Wt = 2)
#RR_20051202064654 | 2005-12-02 | 1 | (TAS1).RAISEREG >= 100 (Wt = 2)
#RR_20051203203152 | 2005-12-05 | 2 | (TAS1).RAISEREG >= 100 (Wt = 2)
#RR_20051205235806 | 2005-12-05 | 1 | (TAS1).RAISEREG >= 100 (Wt = 2)
#RR_20051206125021 | 2005-12-06 | 1 | (TAS1).RAISEREG >= 100 (Wt = 2)
#RR_20051206164533 | 2005-12-06 | 1 | (TAS1).RAISEREG >= 100 (Wt = 2)
#RR_20051208044413 | 2005-12-08 | 1 | (TAS1).RAISEREG >= 100 (Wt = 2)
#RR_20051215092403 | 2005-12-15 | 1 | (TAS1).RAISEREG >= 100 (Wt = 2)
#RR_20051216092721 | 2005-12-16 | 1 | (TAS1).RAISEREG >= 100 (Wt = 2)
#RR_20060315133544 | 2006-03-15 | 1 | (TAS1).RAISEREG >= 100 (Wt = 2)
#RR_20060328072013 | 2006-03-28 | 1 | (TAS1).RAISEREG >= 100 (Wt = 2)
#RR_20060610011350 | 2006-06-10 | 1 | (TAS1).RAISEREG >= 50 (Wt = 2)
#RR_20070116161854 | 2007-01-16 | 1 | (SA1 + VIC1).RAISEREG >= 100 (Wt = 2)
#RR_20070210095614 | 2007-02-10 | 1 | (QLD1).RAISEREG = 0 (Wt = 2)
#RR_20070210102251 | 2007-02-10 | 1 | (QLD1).RAISEREG = 0 (Wt = 2)
#RR_20070211082212 | 2007-02-11 | 1 | (TAS1).RAISEREG = 0 (Wt = 2)
#RR_20080101231258 | 2008-01-01 | 1 | (TAS1).RAISEREG >= 75 (Wt = 2)
#SA1_E_20080726 | 2008-07-26 | 1 | Multiple SA1 LHS <= 0 (Wt = 20)
#SHGEN_E | 2005-10-31 | 1 | NSHL.ENERGY * 1 >= 240 (Wt = 20)
#SHPUMP_E | 2007-07-12 | 2 | NSHP1.ENERGY * -1 = 0 (Wt = 20)
#SITHE01 | 2002-10-09 | 1 | ENERGY = 58 ; Eff = 09/10/2002 ; Wt = 360
#SNOWY6 | 2001-03-17 | 1 | Eff = 17/03/2001 ; RHS = 29 ; Op = "=" ; Wt = 320
#SNOWYP | 2007-07-12 | 2 | RHS = 390 ; Op = "=" ; Wt = 320 ; Type = INFLEXIBLE ; Int = N
#SNUG1 | 1999-04-18 | 1 | RHS = 18 ; Op = "=" ; Wt = 3 ; Type = INFLEXIBLE ; Int = N
#SNUG1_E | 2007-08-18 | 3 | SSGA1.ENERGY * 1 = 20 (Wt = 360)
#STAN-1 | 2002-08-23 | 1 | ENERGY = 160 ; Eff = 23/08/2002 ; Wt = 360
#STAN-2 | 2000-04-03 | 1 | RHS = 310 ; Op = "<=" ; Wt = 3 ; Type = AS_FC ; Int = N
#STAN-3 | 1998-12-25 | 1 | RHS = 185 ; Op = ">=" ; Wt = 50 ; Type = ANCILLARY ; Int = N
#STAN-4 | 2001-01-28 | 1 | No rebid received.
#SWAN_B_1 | 2001-01-05 | 1 | Eff = 05/01/2001 ; RHS = 90 ; Op = ">=" ; Wt = 3
#SWAN_B_2 | 2001-01-07 | 1 | Eff = 07/01/2001 ; RHS = 90 ; Op = ">=" ; Wt = 3
#SWAN_B_2_E | 2007-05-31 | 1 | QSWB2.ENERGY * 1 = 0 (Wt = 360)
#SWAN_B_3 | 2001-01-07 | 1 | Eff = 07/01/2001 ; RHS = 90 ; Op = ">=" ; Wt = 3
#SWAN_B_4 | 1998-12-16 | 1 | @QSB4>=60
#T-V-MNSP1_E | 2007-01-16 | 3 | T-V-MNSP1 * 1 >= 350 (Wt = 20)
#T-V-MNSP1_E_E | 2009-01-29 | 3 | T-V-MNSP1.ENERGY * 1 <= 300 (Wt = 20)
#T-V-MNSP1_I | 2007-01-19 | 1 | T-V-MNSP1 * -1 <= 235 (Wt = 20)
#T-V-MNSP1_RAMP_E_F | 2007-09-05 | 1 | T-V-MNSP1 <= MAX(200, InitialFlow - 200) (Wt=20)
#T-V-MNSP1_RAMP_E_V | 2007-09-05 | 1 | T-V-MNSP1 <= 200 (Wt=0.0002850)
#T-V-MNSP1_RAMP_I_F | 2008-09-16 | 1 | T-V-MNSP1 >= MIN(-160, InitialFlow + 200) (Wt=20)
#T-V-MNSP1_RAMP_I_V | 2007-11-01 | 1 | T-V-MNSP1 >= -291 (Wt=0.0002010)
#TALWA1_E | 2009-01-29 | 1 | NDT13T.ENERGY * 1 <= 340 (Wt = 360)
#TARONG#1 | 1998-12-25 | 1 | RHS = 330 ; Op = "<=" ; Wt = 50 ; Type = ANCILLARY ; Int = N
#TARONG#1_E | 2007-05-31 | 2 | QTRN1.ENERGY * 1 = 0 (Wt = 360)
#TARONG#2 | 1998-12-25 | 1 | RHS = 320 ; Op = "<=" ; Wt = 50 ; Type = ANCILLARY ; Int = N
#TARONG#3 | 2001-03-21 | 1 | Eff = 21/03/2001 ; RHS = 0 ; Op = "=" ; Wt = 320
#TARONG#3_E | 2007-04-08 | 1 | QTRN3.ENERGY * 1 <= 0 (Wt = 360)
#TARONG#3_L5 | 2006-08-04 | 1 | QTRN3.LOWER5MIN * 1 = 0 (Wt = 3)
#TARONG#3_L6 | 2006-08-04 | 1 | QTRN3.LOWER6SEC * 1 = 0 (Wt = 5)
#TARONG#3_L60 | 2006-08-04 | 1 | QTRN3.LOWER60SEC * 1 = 0 (Wt = 4)
#TARONG#3_LR | 2006-08-04 | 1 | QTRN3.LOWERREG * 1 = 0 (Wt = 2)
#TARONG#3_R6 | 2006-08-04 | 1 | QTRN3.RAISE6SEC * 1 = 0 (Wt = 5)
#TARONG#3_R60 | 2006-08-04 | 1 | QTRN3.RAISE60SEC * 1 = 0 (Wt = 4)
#TARONG#3_RR | 2006-08-04 | 1 | QTRN3.RAISEREG * 1 = 0 (Wt = 2)
#TARONG#4 | 1999-01-03 | 1 | FCAS 6sec Raise
#TAS1_E_20080626 | 2008-06-26 | 1 | Multiple TAS1 LHS <= 144 (Wt = 20)
#TNPS1_E | 2008-09-21 | 2 | QTNT. * 1 <= 0 (Wt = 360)
#TORRA1 | 2000-03-31 | 1 | RHS = 0 ; Op = "=" ; Wt = 90 ; Type = INFLEXIBLE ; Int = N
#TORRA2 | 2000-02-06 | 1 | RHS = 30 ; Op = "=" ; Wt = 20 ; Type = INFLEXIBLE ; Int = N
#TORRA2_I_E | 2004-02-13 | 1 | STSA2.ENERGY * 1 >= 50 (Wt = 55)
#TORRA2_W_E | 2004-02-13 | 1 | STSA2.ENERGY * 1 = 0 (Wt = 50)
#TORRA3 | 2000-07-25 | 2 | RHS = 0 ; Op = "=" ; Wt = 320 ; Type = INFLEXIBLE ; Int = N
#TORRA4 | 2000-06-26 | 1 | RHS = 0 ; Op = "=" ; Wt = 320 ; Type = INFLEXIBLE ; Int = N
#TORRB1 | 2000-07-08 | 1 | RHS = 64 ; Op = "=" ; Wt = 320 ; Type = INFLEXIBLE ; Int = N
#TORRB2_E | 2006-04-27 | 1 | STSB2.ENERGY * 1 <= 0 (Wt = 20)
#TORRB2_L5 | 2006-04-27 | 1 | STSB2.LOWER5MIN * 1 <= 0 (Wt = 3)
#TORRB2_L6 | 2006-04-27 | 1 | STSB2.LOWER6SEC * 1 <= 0 (Wt = 5)
#TORRB2_L60 | 2006-04-27 | 1 | STSB2.LOWER60SEC * 1 <= 0 (Wt = 4)
#TORRB2_LR | 2006-04-27 | 1 | STSB2.LOWERREG * 1 <= 0 (Wt = 2)
#TORRB2_R5 | 2006-04-27 | 1 | STSB2.RAISE5MIN * 1 <= 0 (Wt = 3)
#TORRB2_R6 | 2006-04-27 | 1 | STSB2.RAISE6SEC * 1 <= 0 (Wt = 5)
#TORRB2_R60 | 2006-04-27 | 1 | STSB2.RAISE60SEC * 1 <= 0 (Wt = 4)
#TORRB2_RR | 2006-04-27 | 1 | STSB2.RAISEREG * 1 <= 0 (Wt = 2)
#TORRB3 | 2000-06-24 | 1 | RHS = 0 ; Op = "=" ; Wt = 320 ; Type = INFLEXIBLE ; Int = N
#TORRB3_E | 2006-04-28 | 1 | STSB3.ENERGY * 1 <= 0 (Wt = 360)
#TORRB3_L5 | 2006-04-28 | 1 | STSB3.LOWER5MIN * 1 <= 0 (Wt = 360)
#TORRB3_L6 | 2006-04-28 | 1 | STSB3.LOWER6SEC * 1 <= 0 (Wt = 360)
#TORRB3_L60 | 2006-04-28 | 1 | STSB3.LOWER60SEC * 1 <= 0 (Wt = 360)
#TORRB3_LR | 2006-04-28 | 1 | STSB3.LOWERREG * 1 <= 0 (Wt = 360)
#TORRB3_R5 | 2006-04-28 | 1 | STSB3.RAISE5MIN * 1 <= 0 (Wt = 360)
#TORRB3_R6 | 2006-04-28 | 1 | STSB3.RAISE6SEC * 1 <= 0 (Wt = 360)
#TORRB3_R60 | 2006-04-28 | 1 | STSB3.RAISE60SEC * 1 <= 0 (Wt = 360)
#TORRB3_RR | 2006-04-28 | 1 | STSB3.RAISEREG * 1 <= 0 (Wt = 360)
#TORRB4 | 2001-08-06 | 1 | Eff = 06/08/2001 ; RHS = 0 ; Op = "=" ; Wt = 320
#TORRB4_S_E | 2004-02-13 | 1 | STSB4.ENERGY * 1 <= 140 (Wt = 48)
#TUMUT3_E | 2003-10-10 | 8 | NLTS8.ENERGY * 1 <= 500 (Wt = 20)
#TUNGATIN_E | 2006-06-25 | 3 | TTU11.ENERGY * 1 >= 20 (Wt = 20)
#UPPTUMUT_E | 2003-11-06 | 6 | NUTS8.ENERGY * 1 <= 500 (Wt = 20)
#V-S-MNSP1_E | 2006-12-01 | 1 | V-S-MNSP1 * 1 >= 20 (Wt = 20)
#V-S-MNSP1_I | 2008-01-26 | 3 | V-S-MNSP1 * -1 <= 95 (Wt = 360)
#V-S-MNSP1_I_E | 2009-02-11 | 1 | V-S-MNSP1. * -1 >= 120 (Wt = 20)
#V-S-MNSP1_RAMP_E_F | 2008-06-03 | 1 | V-S-MNSP1 >= MIN(0, InitialFlow + 40) (Wt=20)
#V-S-MNSP1_RAMP_E_V | 2007-09-06 | 3 | V-S-MNSP1 >= 0 (Wt=0.0012919)
#V-S-MNSP1_RAMP_I_F | 2008-11-14 | 1 | V-S-MNSP1 >= MIN(-60, InitialFlow + 40) (Wt=20)
#V-S-MNSP1_RAMP_I_V | 2007-05-11 | 1 | V-S-MNSP1 >= -36 (Wt=0.0020915)
#V-SA_E | 2006-05-12 | 1 | V-SA * 1 = 109 (Wt = 20)
#V-SA_I | 2007-01-16 | 5 | V-SA * -1 >= 250 (Wt = 20)
#V-SA_I_E | 2009-02-08 | 2 | V-SA. * -1 >= 50 (Wt = 20)
#V-SA_RAMP_E_F | 2008-12-24 | 1 | V-SA <= MAX(250, InitialFlow - 30) (Wt=20)
#V-SA_RAMP_E_V | 2007-12-27 | 1 | V-SA <= 89 (Wt=0.0005642)
#V-SA_RAMP_I_F | 2008-11-06 | 2 | V-SA >= MIN(-59, InitialFlow + 50) (Wt=20)
#V-SA_RAMP_I_V | 2008-09-09 | 1 | V-SA <= -50 (Wt=0.0006886)
#V-SN_RAMP_E_V | 2007-05-17 | 1 | V-SN <= 400 (Wt=0.0012588)
#V-SN_RAMP_I_V | 2007-02-17 | 2 | V-SN >= -200 (Wt=0.0000941)
#VIC1-NSW1_I_E | 2009-02-09 | 8 | VIC1-NSW1. * -1 >= 0 (Wt = 20)
#VIC1_E_20090130 | 2009-01-30 | 2 | Multiple VIC1 LHS <= 0 (Wt = 360)
#VIC1_E_20090209 | 2009-02-11 | 1 | Multiple VIC1 LHS <= 300 (Wt = 20)
#VP5 | 1999-06-07 | 1 | RHS = 590 ; Op = "<=" ; Wt = 20 ; Type = AS_FC ; Int = N
#VP6_E | 2003-09-25 | 1 | NVPP6.ENERGY * 1 = 55 (Wt = 360)
#W/HOE#1 | 2001-10-01 | 2 | ENERGY = 0 ; Eff = 01/10/2001 ; Wt = 320
#W/HOE#2 | 2002-02-06 | 1 | ENERGY = 50 ; Eff = 06/02/2002 ; Wt = 360
#WKIEWA1 | 2002-12-16 | 1 | ENERGY <= 10 ; Eff = 16/12/2002 ; Wt = 360
#WKIEWA2 | 2002-12-16 | 1 | ENERGY <= 10 ; Eff = 16/12/2002 ; Wt = 360
#WW7 | 2002-01-15 | 1 | ENERGY = 0 ; Eff = 15/01/2002 ; Wt = 360
#WW8 | 2000-06-04 | 1 | RHS = 0 ; Op = "=" ; Wt = 120 ; Type = INFLEXIBLE ; Int = N
#WW8_E | 2008-11-16 | 2 | NWW28.ENERGY * 1 <= 240 (Wt = 20)
#YABULU_E | 2008-07-12 | 1 | QTYP.ENERGY * 1 <= 85 (Wt = 20)
#YWPS1_E | 2004-12-05 | 1 | VYP21.ENERGY * 1 <= 340 (Wt = 20)
#YWPS2 | 2000-09-21 | 1 | RHS = 350 ; Op = "=" ; Wt = 320 ; Type = INFLEXIBLE ; Int = N
#YWPS2_E | 2004-12-05 | 1 | VYP22.ENERGY * 1 <= 320 (Wt = 20)
#YWPS3 | 2001-02-27 | 3 | Eff = 27/02/2001 ; RHS = 315 ; Op = "=" ; Wt = 320
#YWPS3_E | 2004-12-05 | 1 | VYP23.ENERGY * 1 <= 320 (Wt = 20)
#YWPS4_E | 2004-12-05 | 1 | VYP24.ENERGY * 1 <= 320 (Wt = 20)
@HW1-5, JLGS B <=540 | 2008-10-24 | 1 | @HW1-5, JLGS B <=540 MW
@JLB>=50 | 2007-02-27 | 1 | Eff = 27/02/2007 ; RHS = 50 ; Op = ">=" ; Wt = 20
@NPS+PLAY | 2005-06-10 | 1 | Eff = 10/06/2005 ; RHS = 525 ; Op = "<=" ; Wt = 20
@NSA_Q_COLNSV_158 | 2007-12-09 | 1 | NSA (Powerlink) for C-N limit Collinsville #2 to #5 only
@NSA_Q_COLNSV_22 | 2008-02-13 | 2 | Eff = 13/02/2008 ; RHS = 22 ; Op = ">=" ; Wt = 20
@NSA_V_BDL01_25 | 2007-02-07 | 1 | Eff = 07/02/2007 ; RHS = 25 ; Op = ">=" ; Wt = 20
@NSA_V_BDL02_25 | 2007-01-02 | 1 | Eff = 02/01/2007 ; RHS = 25 ; Op = ">=" ; Wt = 20
@N_LD1_>=50 | 2008-08-20 | 1 | Eff = 20/08/2008 ; RHS = 50 ; Op = ">=" ; Wt = 20
@N_TALWA1_400 | 2009-01-23 | 1 | Eff = 23/01/2009 ; RHS = 400 ; Op = "<=" ; Wt = 360
@QNI_GENBLOCK | 2007-10-15 | 1 | Eff = 15/10/2007 ; RHS = 1100 ; Op = "<=" ; Wt = 20
@QNI_GENBLOCK290907 | 2007-10-15 | 1 | Eff = 15/10/2007 ; RHS = 1550 ; Op = "<=" ; Wt = 20
@Q_CN_MTSTUART1_NSA | 2007-01-09 | 2 | Eff = 09/01/2007 ; RHS = 45 ; Op = ">=" ; Wt = 20
@Q_CN_QCVL_185 | 2005-12-13 | 1 | Eff = 13/12/2005 ; RHS = 185 ; Op = ">=" ; Wt = 20
@Q_CN_QCVL_NSA | 2007-02-16 | 1 | Eff = 16/02/2007 ; RHS = 114 ; Op = ">=" ; Wt = 20
@Q_SW_QLD_1350 | 2007-11-04 | 1 | Discretionary SW QLD Gen <= 1350MW
@Q_SW_QLD_1400 | 2007-11-04 | 1 | Discretionary SW QLD Gen <= 1400MW
@Q_SW_QLD_1500 | 2007-11-04 | 1 | Discretionary SW QLD Gen <= 1500MW
@Q_SW_QLD_1600 | 2007-11-04 | 1 | Discretionary SW QLD Gen <= 1600MW
@Q_SW_QLD_1700 | 2007-11-04 | 1 | Discretionary SW QLD Gen <= 1700MW
@Q_SW_QLD_1800 | 2007-12-16 | 1 | Discretionary SW QLD Gen <= 1800MW
@R4_CBS_OUT | 2007-03-02 | 1 | Eff = 02/03/2007 ; RHS = 850 ; Op = "<=" ; Wt = 360
@S-MTM1_0 | 2007-02-15 | 1 | Eff = 15/02/2007 ; RHS = 0 ; Op = "<=" ; Wt = 360
@SANTHGEN<450 | 2008-01-12 | 1 | Eff = 12/01/2008 ; RHS = 450 ; Op = "<=" ; Wt = 20
@SANTHGEN<475 | 2008-01-12 | 1 | Eff = 12/01/2008 ; RHS = 475 ; Op = "<=" ; Wt = 20
@SANTHGEN<500 | 2008-01-12 | 1 | Eff = 12/01/2008 ; RHS = 500 ; Op = "<=" ; Wt = 20
@SANTHGEN<525 | 2008-01-12 | 1 | Eff = 12/01/2008 ; RHS = 525 ; Op = "<=" ; Wt = 20
@SANTHGEN<550 | 2008-01-12 | 1 | SANorthern generation <550MW
@SANTHGEN<575 | 2008-01-12 | 1 | Eff = 12/01/2008 ; RHS = 575 ; Op = "<=" ; Wt = 20
@SANTHGEN<600 | 2008-01-12 | 1 | Eff = 12/01/2008 ; RHS = 600 ; Op = "<=" ; Wt = 20
@STANWELL650 | 2008-07-28 | 1 | Eff = 28/07/2008 ; RHS = 650 ; Op = "<=" ; Wt = 20
@S_PPT210 | 2007-10-28 | 1 | SA Pelican Pt. PS <=210, Out=PGW-CB6579
@T-STH_GEN | 2007-04-18 | 1 | Eff = 18/04/2007 ; RHS = 450 ; Op = "<=" ; Wt = 20
@T>T_LIPM_110_2A | 2008-03-14 | 3 | Eff = 14/03/2008 ; RHS = 520 ; Op = "<=" ; Wt = 20
@TARONG600 | 2008-07-28 | 1 | Eff = 28/07/2008 ; RHS = 600 ; Op = "<=" ; Wt = 20
@TA_TU | 2007-02-16 | 2 | Eff = 16/02/2007 ; RHS = 90 ; Op = "<=" ; Wt = 20
@T_T_RC1+2_TI_250 | 2007-01-14 | 2 | Discretionary 250 MW upper limit on, Reece 1+2 and Tribute
@V>V-500XLV | 2007-09-05 | 1 | Eff = 05/09/2007 ; RHS = 4100 ; Op = "<=" ; Wt = 20
@V_LV_BL_4300 | 2007-09-05 | 1 | Discretionary Latrobe Valley & Basslink <= 4300
@V_LV_BL_4500 | 2007-09-05 | 1 | Discretionary Latrobe Valley Gen & Basslink <= 4500
@V_LV_BL_4700 | 2007-09-05 | 1 | Discretionary Latrobe Valley Gen & Basslink <= 4700
@V_LV_BL_4900 | 2007-09-05 | 1 | Discretionary Latrobe Valley Gen & Basslink <= 4900
@V_LV_BL_5100 | 2007-09-05 | 1 | Discretionary Latrobe Valley Gen & Basslink <= 5100
@WW8<=240 | 2008-11-17 | 1 | Eff = 17/11/2008 ; RHS = 240 ; Op = "<=" ; Wt = 20
@_QNTE_130 | 2008-03-13 | 1 | Eff = 13/03/2008 ; RHS = 130 ; Op = "<=" ; Wt = 20
@_QNTE_140 | 2008-03-13 | 1 | Eff = 13/03/2008 ; RHS = 140 ; Op = "<=" ; Wt = 20
CA_BPS_36FED54A_01 | 2008-03-28 | 1 | Constraint Automation, O/L 275KV_871 @H24_CALV for CTG LQIK on trip of 848 H10_BCMB-H29_STAN 275KV LINE. Generated by STNET[MANFR] Host MANEEMP4(BP)
CA_BPS_370923EE_01 | 2008-04-05 | 1 | Constraint Automation, O/L ROBNWB_1 @R_TOWN for CTG LS5M on trip of N_W_B-MONASH-BERRI 132KV 1 LINE. Generated by STNET[MANFR] Host MANEEMP4(BP)
CA_BPS_37111A13_01 | 2008-04-11 | 1 | Constraint Automation, O/L TU_TA2 @TUNGATIN for CTG LTBA on trip of TARRALEAH_TUNGATINAH #1 110KV LINE. Generated by STNET[MANFR] Host MANEEMP3(BP)
CA_BPS_37111A13_02 | 2008-04-11 | 1 | Constraint Automation, O/L TU_TA1 @TUNGATIN for CTG LTBB on trip of TARRALEAH_TUNGATINAH #2 110KV LINE. Generated by STNET[MANFR] Host MANEEMP3(BP)
CA_BPS_373D77DD_01 | 2008-05-14 | 1 | Constraint Automation, O/L CANROB_1 @CANOWI for CTG LSHF on trip of DAVENP-R_TOWN 275KV 2 LINE. Generated by STNET[MANFR] Host MANEEMP4(BP)
CA_BPS_373D77DD_02 | 2008-05-14 | 1 | Constraint Automation, O/L DVPROB_2 @DAVENP for CTG LSIF on trip of R_TOWN - CANOWI 275KV 1 LINE. Generated by STNET[MANFR] Host MANEEMP4(BP)
CA_BPS_373D7DA1_01 | 2008-05-14 | 1 | Constraint Automation, O/L CANROB_1 @CANOWI for CTG LSHF on trip of DAVENP-R_TOWN 275KV 2 LINE. Generated by STNET[MANFR] Host MANEEMP4(BP)
CA_BPS_373D7DA1_02 | 2008-05-14 | 1 | Constraint Automation, O/L DVPROB_2 @DAVENP for CTG LSIF on trip of R_TOWN - CANOWI 275KV 1 LINE. Generated by STNET[MANFR] Host MANEEMP4(BP)
CA_BPS_373D7DA1_03 | 2008-05-14 | 1 | Constraint Automation, O/L DVPROB_2 @DAVENP for CTG LSHE on trip of DAVENP-CANOWI 275KV 1 LINE. Generated by STNET[MANFR] Host MANEEMP4(BP)
CA_BPS_374BECD7_01 | 2008-05-25 | 1 | Constraint Automation, O/L 132KV_7146 @T5_GLAD for CTG LQ9B on trip of 7145 T5_GLAD-H8_BOYNE 132KV LINE. Generated by STNET[MANFR] Host MANEEMP4(BP)
CA_BPS_374BECD7_02 | 2008-05-25 | 1 | Constraint Automation, O/L 132KV_7145 @T5_GLAD for CTG LQ9C on trip of 7146 T5_GLAD-H8_BOYNE 132KV LINE. Generated by STNET[MANFR] Host MANEEMP4(BP)
CA_BPS_3751CD0E_01 | 2008-05-30 | 1 | Constraint Automation, O/L ROBMW3_2 @R_TOWN for Nil Trip Base Case. Generated by STNET[MANFR] Host MANEEMP3(BP)
CA_BPS_3797DF11_01 | 2008-07-22 | 1 | Constraint Automation, O/L MINWAT_1 @MINTAR for CTG LSHJ on trip of BRINKW-PARA 275KV LINE. Generated by STNET[OFFLIN03] Host MANEEMP4(BP)
CA_BPS_3797DF11_02 | 2008-07-22 | 1 | Constraint Automation, O/L MINWAT_1 @MINTAR for CTG TSHF on trip of BRINKW 3 275/132KV TX. Generated by STNET[OFFLIN03] Host MANEEMP4(BP)
CA_BPS_3797DF11_03 | 2008-07-22 | 1 | Constraint Automation, O/L MINWAT_1 @MINTAR for CTG LS5Q on trip of BRINKW-MINTAR 132KV LINE. Generated by STNET[OFFLIN03] Host MANEEMP4(BP)
CA_BPS_37D0B7D6_01 | 2008-09-03 | 1 | Constraint Automation, O/L 275KV_871 @H24_CALV for CTG LQJB on trip of 8810 H18_TRNG-H24_CALV 275KV LINE. Generated by STNET[MANBL] Host MANEEMP4(BP)
CA_BPS_37E31B72_01 | 2008-09-17 | 1 | Constraint Automation, O/L MA3MAN_T @ANG_CK for CTG LSIM on trip of TUNKIL - T_BEND #1 275KV LINE. Generated by STNET[OFFLIN06] Host MANEEMP4(BP)
CA_BPS_37E31B72_02 | 2008-09-17 | 1 | Constraint Automation, O/L MIKANC_T @PARA for CTG LSIM on trip of TUNKIL - T_BEND #1 275KV LINE. Generated by STNET[OFFLIN06] Host MANEEMP4(BP)
CA_BPS_37E31B72_03 | 2008-09-17 | 1 | Constraint Automation, O/L PARA TRANSF T_8 for CTG LSIM on trip of TUNKIL - T_BEND #1 275KV LINE. Generated by STNET[OFFLIN06] Host MANEEMP4(BP)
CA_BPS_37E9983E_01 | 2008-09-22 | 1 | Constraint Automation, O/L S_EAST TRANSF T_1 for CTG LS6J on trip of KINCRAIG-PENO_W 132KV LINE. Generated by STNET[OFFLIN07] Host MANEEMP3(BP)
CA_BPS_37E9983E_02 | 2008-09-22 | 1 | Constraint Automation, O/L S_EAST TRANSF T_1 for CTG LS5Y on trip of KEITH-SNUGGY 132KV LINE. Generated by STNET[OFFLIN07] Host MANEEMP3(BP)
CA_BPS_37F5418D_01 | 2008-10-01 | 1 | Constraint Automation, O/L HUMWAT_1 @HUMMOC for CTG LSIL on trip of PARA-BUNGAM 275KV LINE. Generated by STNET[OFFLIN05] Host MANEEMP3(BP)
CA_BPS_37F5418D_02 | 2008-10-01 | 1 | Constraint Automation, O/L HUMWAT_1 @HUMMOC for CTG LSHF on trip of DAVENP-R_TOWN 275KV 2 LINE. Generated by STNET[OFFLIN05] Host MANEEMP3(BP)
CA_BPS_38123334_01 | 2008-10-23 | 1 | Constraint Automation, O/L SNUGGY TRANSF T_4 for CTG TS6B on trip of SNUGGY 1 132/33KV TX, #1 & 1A CAPS. Generated by STNET[OFFLIN08] Host MANEEMP4(BP)
CA_BPS_38259BE6_01 | 2008-11-07 | 1 | Constraint Automation, O/L MOBTAB_1 @MOBILO for CTG MSHR on trip of T_BEND-CH_GDN & TUNKIL 275KV LINES. Generated by STNET[MANFL] Host MANEEMP4(BP)
CA_BPS_383C8FE0_01 | 2008-11-24 | 1 | Constraint Automation, O/L S_EAST TRANSF T_2 for CTG TSHZ on trip of S_EAST 1 275/132KV TX. Generated by STNET[OFFLIN07] Host MANEEMP4(BP)
CA_BPS_383CBCF0_01 | 2008-11-24 | 1 | Constraint Automation, O/L S_EAST TRANSF T_2 for CTG TSHZ on trip of S_EAST 1 275/132KV TX. Generated by STNET[OFFLIN07] Host MANEEMP4(BP)
CA_BPS_385B10D7_01 | 2008-12-17 | 1 | Constraint Automation, O/L S_EAST TRANSF T_1 for Nil Trip Base Case. Generated by STNET[MANFR] Host MANEEMP3(BP)
CA_BPS_3865C035_01 | 2008-12-25 | 1 | Constraint Automation, O/L 275KV_855 @H24_CALV for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by STNET[MANFR] Host MANEEMP4(BP)
CA_BPS_387FA347_01 | 2009-01-14 | 1 | Constraint Automation, O/L TABKEI_1 @KEITH for CTG LS5W on trip of T_BEND-KEITH 132KV 2 LINE. Generated by STNET[OFFLIN07] Host MANEEMP3(BP)
CA_BPS_389351C3_01 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVCB on trip of ROTS-YPS7 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_02 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVCB on trip of ROTS-YPS7 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_03 | 2009-01-29 | 1 | Constraint Automation, O/L HWPS_ROTS1_220@HWPS for CTG LVCE on trip of HWPS-ROTS2 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_04 | 2009-01-29 | 1 | Constraint Automation, O/L HWPS_ROTS1_220@HWPS for CTG LVCE on trip of HWPS-ROTS2 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_05 | 2009-01-29 | 1 | Constraint Automation, O/L HWPS_ROTS2_220@HWPS for CTG LVCD on trip of HWPS-ROTS1 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_06 | 2009-01-29 | 1 | Constraint Automation, O/L HWPS_ROTS2_220@HWPS for CTG LVCD on trip of HWPS-ROTS1 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_07 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_08 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_09 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVCC on trip of ROTS-YPS8 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_10 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVCC on trip of ROTS-YPS8 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_11 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_12 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_13 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS6_220 @YPS for CTG LVCB on trip of ROTS-YPS7 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_14 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS6_220 @YPS for CTG LVCB on trip of ROTS-YPS7 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_15 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS6_220 @YPS for CTG LVCC on trip of ROTS-YPS8 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_16 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS6_220 @YPS for CTG LVCC on trip of ROTS-YPS8 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_17 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_18 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_19 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_20 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_21 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS6_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_22 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS6_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_23 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS5_220 @YPS for CTG LVCB on trip of ROTS-YPS7 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_24 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS5_220 @YPS for CTG LVCB on trip of ROTS-YPS7 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_25 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS5_220 @YPS for CTG LVCC on trip of ROTS-YPS8 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_26 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS5_220 @YPS for CTG LVCC on trip of ROTS-YPS8 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_27 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS5_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389351C3_28 | 2009-01-29 | 1 | Constraint Automation, O/L ROTS_YPS5_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[MANFL] Host MANEEMP3(BP)
CA_BPS_389CBC17_01 | 2009-02-05 | 1 | Constraint Automation, O/L 132KV_7276 @T145_TVL for CTG LQ6% on trip of 7277 T145_TVL - T150_ASH 132KV LN. Generated by STNET[OFFLIN00] Host MANEEMP4(BP)
CA_SPS_36E74606_01 | 2008-03-10 | 1 | Constraint Automation, O/L 96C @ARMIDALE for CTG LN8K on trip of ARMIDALE-KEMPSEY 965 132KV LINE. Generated by STNET[OFFLIN08] Host NOREEMP2(SP)
CA_SPS_37F7E408_01 | 2008-10-03 | 1 | Constraint Automation, O/L ERARING TRANSF 2TL for CTG LNPQ on trip of VALES_PT-SYD_NTH 22 330KV LINE. Generated by STNET[OFFLIN04] Host NOREEMP2(SP)
CA_SPS_37F7E636_01 | 2008-10-03 | 1 | Constraint Automation, O/L 65 @TUMUT1_2 for CTG LHPA on trip of LTSS-MSS 330KV LINE. Generated by STNET[OFFLIN05] Host NOREEMP2(SP)
CA_SPS_37F7E69C_01 | 2008-10-03 | 1 | Constraint Automation, O/L 65 @TUMUT1_2 for CTG LHPA on trip of LTSS-MSS 330KV LINE. Generated by STNET[OFFLIN05] Host NOREEMP2(SP)
CA_SPS_37F7EF63_01 | 2008-10-03 | 1 | Constraint Automation, O/L 22 @VALES_PT for CTG LNVA on trip of ERARING-KEMPS_CK 5A1 500KV LINE. Generated by STNET[OFFLIN04] Host NOREEMP2(SP)
CA_SPS_37F7F610_01 | 2008-10-03 | 1 | Constraint Automation, O/L ERARING TRANSF 2TL for CTG LNPM on trip of ERARING-NEWCSTLE 93 330KV LINE. Generated by STNET[OFFLIN04] Host NOREEMP2(SP)
CA_SPS_37F7F6C9_01 | 2008-10-03 | 1 | Constraint Automation, O/L 65 @MURRAY for CTG LHPA on trip of LTSS-MSS 330KV LINE. Generated by STNET[OFFLIN05] Host NOREEMP2(SP)
CA_SPS_37F7F95D_01 | 2008-10-03 | 1 | Constraint Automation, O/L DDTS TRANSF H1TR for CTG LVPD on trip of DDTS-SMTS1 330KV LINE. Generated by STNET[OFFLIN01] Host NOREEMP2(SP)
CA_SPS_37F7F95D_02 | 2008-10-03 | 1 | Constraint Automation, O/L DDTS TRANSF H1TR for CTG LVPD on trip of DDTS-SMTS1 330KV LINE. Generated by STNET[OFFLIN01] Host NOREEMP2(SP)
CA_SPS_37F7F95D_03 | 2008-10-03 | 1 | Constraint Automation, O/L 9U9 @LISM132 for CTG LN9C on trip of LISMORE - LISM132 9U8 132KV LINE. Generated by STNET[OFFLIN01] Host NOREEMP2(SP)
CA_SPS_37F7F9AD_01 | 2008-10-03 | 1 | Constraint Automation, O/L 8 @MARULAN for CTG LNQX on trip of AVON-MARULAN 16 330KV LINE. Generated by STNET[OFFLIN05] Host NOREEMP2(SP)
CA_SPS_382208F6_01 | 2008-11-04 | 1 | Constraint Automation, O/L 96L/1 @TENTFLD for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[CARFL] Host NOREEMP2(SP)
CA_SPS_38222DC6_01 | 2008-11-04 | 1 | Constraint Automation, O/L 96L/1 @TENTFLD for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[CARFL] Host NOREEMP2(SP)
CA_SPS_38262A8A_01 | 2008-11-07 | 1 | Constraint Automation, O/L HWTS TRANSF A2TR_500 for CTG TVVK on trip of HWTS A1 TRANS. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38262A8A_02 | 2008-11-07 | 1 | Constraint Automation, O/L HWTS TRANSF A2TR_500 for CTG TVVK on trip of HWTS A1 TRANS. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38262A8A_03 | 2008-11-07 | 1 | Constraint Automation, O/L HWTS TRANSF A1TR_500 for CTG TVVL on trip of HWTS A2 TRANS. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38262A8A_04 | 2008-11-07 | 1 | Constraint Automation, O/L HWTS TRANSF A1TR_500 for CTG TVVL on trip of HWTS A2 TRANS. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38262A8A_05 | 2008-11-07 | 1 | Constraint Automation, O/L HWTS TRANSF A3TR_500 for CTG TVVN on trip of HWTS A4 TRANS. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38262A8A_06 | 2008-11-07 | 1 | Constraint Automation, O/L HWTS TRANSF A3TR_500 for CTG TVVN on trip of HWTS A4 TRANS. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38262A8A_07 | 2008-11-07 | 1 | Constraint Automation, O/L HWTS TRANSF A4TR_500 for CTG TVVM on trip of HWTS A3 TRANS. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38262A8A_08 | 2008-11-07 | 1 | Constraint Automation, O/L HWTS TRANSF A4TR_500 for CTG TVVM on trip of HWTS A3 TRANS. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38332D6B_01 | 2008-11-17 | 1 | Constraint Automation, O/L 81 @LIDDELL for CTG LNPG on trip of LIDDELL-TOMAGO 82 330KV LINE. Generated by STNET[OFFLIN04] Host NOREEMP1(SP)
CA_SPS_38332D6B_02 | 2008-11-17 | 1 | Constraint Automation, O/L KEMPS_CK TRANSF 3L for CTG TNVB on trip of KEMPS_CK 2 500/330KV TX. Generated by STNET[OFFLIN04] Host NOREEMP1(SP)
CA_SPS_38332D6B_03 | 2008-11-17 | 1 | Constraint Automation, O/L KEMPS_CK TRANSF 2L for CTG TNVC on trip of KEMPS_CK 3 500/330KV TX. Generated by STNET[OFFLIN04] Host NOREEMP1(SP)
CA_SPS_38332D6B_04 | 2008-11-17 | 1 | Constraint Automation, O/L 82 @LIDDELL for CTG LNPH on trip of LIDDELL-NEWCSTLE 81 330KV LINE. Generated by STNET[OFFLIN04] Host NOREEMP1(SP)
CA_SPS_38332D6B_05 | 2008-11-17 | 1 | Constraint Automation, O/L 13 @KEMPS_CK for CTG LNQO on trip of SYD_WEST-LIVERPL 30 330KV LINE. Generated by STNET[OFFLIN04] Host NOREEMP1(SP)
CA_SPS_38332D6B_06 | 2008-11-17 | 1 | Constraint Automation, O/L 13 @KEMPS_CK for CTG LNQM on trip of WWANG-SYD_STH 76 330KV LINE. Generated by STNET[OFFLIN04] Host NOREEMP1(SP)
CA_SPS_38332D6B_07 | 2008-11-17 | 1 | Constraint Automation, O/L 8 @MARULAN for CTG LNPZ on trip of KEMPS_CK-AVON 37 330KV LINE. Generated by STNET[OFFLIN04] Host NOREEMP1(SP)
CA_SPS_3833359A_01 | 2008-11-17 | 1 | Constraint Automation, O/L 967 @KOOLKHAN for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38405792_01 | 2008-11-27 | 1 | Constraint Automation, O/L 967 @KOOLKHAN for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_3841AB0F_01 | 2008-11-28 | 1 | Constraint Automation, O/L 967 @KOOLKHAN for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[OFFLIN10] Host NOREEMP1(SP)
CA_SPS_3841B2EE_01 | 2008-11-28 | 1 | Constraint Automation, O/L 967 @KOOLKHAN for CTG LNPD on trip of COFFS-LISMORE 89 330KV LINE. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_3848745D_01 | 2008-12-03 | 1 | Constraint Automation, O/L 96C @ARMIDALE for CTG LNOZ on trip of ARMIDALE-COFFS 87 330KV LINE. Generated by STNET[OFFLIN10] Host NOREEMP1(SP)
CA_SPS_3849A8DA_01 | 2008-12-04 | 1 | Constraint Automation, O/L 96C @ARMIDALE for CTG LNOZ on trip of ARMIDALE-COFFS 87 330KV LINE. Generated by STNET[OFFLIN10] Host NOREEMP1(SP)
CA_SPS_3873FD74_01 | 2009-01-05 | 1 | Constraint Automation, O/L 96C @ARMIDALE for CTG LNOZ on trip of ARMIDALE-COFFS 87 330KV LINE. Generated by STNET[OFFLIN05] Host NOREEMP2(SP)
CA_SPS_38801279_01 | 2009-01-14 | 1 | Constraint Automation, O/L 66 @MURRAY for CTG LHPB on trip of MSS-UTSS 330KV LINE. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38801279_02 | 2009-01-14 | 1 | Constraint Automation, O/L 65 @MURRAY for CTG LHPA on trip of LTSS-MSS 330KV LINE. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38801279_03 | 2009-01-14 | 1 | Constraint Automation, O/L 65 @MURRAY for CTG LXPD on trip of LOWER TUMUT-CANBERRA 07 330KV LINE. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38801279_04 | 2009-01-14 | 1 | Constraint Automation, O/L 65 @MURRAY for CTG LXPC on trip of LOWER TUMUT-YASS 03 330KV LINE. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38869137_01 | 2009-01-19 | 1 | Constraint Automation, O/L DARL_PT TRANSF 3H for CTG TNRE on trip of DARL_PT 4 330/220KV TX. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38869137_02 | 2009-01-19 | 1 | Constraint Automation, O/L DARL_PT TRANSF 3H for CTG TNRE on trip of DARL_PT 4 330/220KV TX. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38869137_03 | 2009-01-19 | 1 | Constraint Automation, O/L DARL_PT TRANSF 4H for CTG TNRD on trip of DARL_PT 3 330/220KV TX. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_38869137_04 | 2009-01-19 | 1 | Constraint Automation, O/L DARL_PT TRANSF 4H for CTG TNRD on trip of DARL_PT 3 330/220KV TX. Generated by STNET[CARFL] Host NOREEMP1(SP)
CA_SPS_3893391F_01 | 2009-01-29 | 2 | Constraint Automation, O/L HWPS_ROTS2_220@HWPS for CTG LVCD on trip of HWPS-ROTS1 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_02 | 2009-01-29 | 2 | Constraint Automation, O/L HWPS_ROTS2_220@HWPS for CTG LVCD on trip of HWPS-ROTS1 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_03 | 2009-01-29 | 2 | Constraint Automation, O/L HWPS_ROTS1_220@HWPS for CTG LVCE on trip of HWPS-ROTS2 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_04 | 2009-01-29 | 2 | Constraint Automation, O/L HWPS_ROTS1_220@HWPS for CTG LVCE on trip of HWPS-ROTS2 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_05 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVCB on trip of ROTS-YPS7 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_06 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVCB on trip of ROTS-YPS7 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_07 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVCC on trip of ROTS-YPS8 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_08 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVCC on trip of ROTS-YPS8 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_09 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_10 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_11 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_12 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_13 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS6_220 @YPS for CTG LVCB on trip of ROTS-YPS7 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_14 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS6_220 @YPS for CTG LVCB on trip of ROTS-YPS7 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_15 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS6_220 @YPS for CTG LVCC on trip of ROTS-YPS8 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_16 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS6_220 @YPS for CTG LVCC on trip of ROTS-YPS8 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_17 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_18 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_19 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_20 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_21 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS6_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_3893391F_22 | 2009-01-29 | 2 | Constraint Automation, O/L ROTS_YPS6_220 @YPS for CTG LVBZ on trip of ROTS-YPS5 220KV LINE. Generated by STNET[OFFLIN02] Host NOREEMP1(SP)
CA_SPS_38952569_01 | 2009-01-30 | 1 | Constraint Automation, O/L SMTS_SYTS2_500@SMTS for CTG LVVF on trip of SMTS-SYTS1 500KV LINE. Generated by STNET[OFFLIN10] Host NOREEMP1(SP)
CA_SPS_38952569_02 | 2009-01-30 | 1 | Constraint Automation, O/L SMTS_SYTS2_500@SMTS for CTG LVVF on trip of SMTS-SYTS1 500KV LINE. Generated by STNET[OFFLIN10] Host NOREEMP1(SP)
CA_SPS_3895345D_01 | 2009-01-30 | 1 | Constraint Automation, O/L SMTS_SYTS1_500@SMTS for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[OFFLIN10] Host NOREEMP1(SP)
CA_SPS_3895345D_02 | 2009-01-30 | 1 | Constraint Automation, O/L SMTS_SYTS1_500@SMTS for CTG TVVP on trip of ROTS A1 500/220KV TRANS. Generated by STNET[OFFLIN10] Host NOREEMP1(SP)
CA_SPS_389BABB9_01 | 2009-02-04 | 1 | Constraint Automation, O/L DDTS_MSS2_330 @MURRAY for CTG LXPG on trip of DDTS-MSS1 330KV LINE. Generated by STNET[OFFLIN08] Host NOREEMP2(SP)
CA_SPS_389BABB9_02 | 2009-02-04 | 1 | Constraint Automation, O/L 965 @ARMIDALE for CTG LN8M on trip of COFFS-NAMBUCCA 9W3 132KV LINE. Generated by STNET[OFFLIN08] Host NOREEMP2(SP)
CA_SPS_38A2048F_01 | 2009-02-09 | 1 | Constraint Automation, O/L HOTS_RCTS_220 @HOTS for CTG LVDH on trip of BATS-BETS 220KV LINE. Generated by STNET[OFFLIN10] Host NOREEMP1(SP)
CA_SPS_38A2048F_02 | 2009-02-09 | 1 | Constraint Automation, O/L BATS_HOTS_220 @BATS for CTG LVDH on trip of BATS-BETS 220KV LINE. Generated by STNET[OFFLIN10] Host NOREEMP1(SP)
CA_SPS_38A3495E_01 | 2009-02-10 | 1 | Constraint Automation, O/L ROBMW3_2 @R_TOWN for Nil Trip Base Case. Generated by STNET[OFFLIN09] Host NOREEMP1(SP)
CA_SPS_38A3495E_02 | 2009-02-10 | 1 | Constraint Automation, O/L ROBNWB_1 @R_TOWN for Nil Trip Base Case. Generated by STNET[OFFLIN09] Host NOREEMP1(SP)
CA_SPS_38A3495E_03 | 2009-02-10 | 1 | Constraint Automation, O/L ROBNWB_1 @R_TOWN for CTG LS5K on trip of R_TOWN-N_W_B132KV 2LN VIA1,2,3MWPS. Generated by STNET[OFFLIN09] Host NOREEMP1(SP)
DATASNAP | 2009-01-19 | 2 | DATASNAP for Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Feedback, TG formulation in PD/ST
DATASNAP3 | 2007-01-23 | 1 | Reference Constraint to check Measurement/RHS; never to bind.
DATASNAP4 | 2007-12-14 | 2 | Reference Constraint to check measurement; never to bind.
DATASNAP5 | 2007-12-14 | 1 | Reference Constraint to check measurement; never to bind.
DATASNAP_B | 2007-12-14 | 1 | Reference Constraint to check measurement; never to bind.
DATA_MMS_ALERT1 | 2007-07-31 | 1 | MMS End to End Data Alerting Constraint - never to bind.
ESTN_HYSE | 2008-07-01 | 1 | SA / ESTN separation between Heywood and South East Sub, limit Vic to Snowy to ensure transient stability for a Hazelwood to South Morang 500kV line fault, system normal limit less 240 MW
ESTN_PATB | 2008-07-01 | 1 | SA / ESTN separation between Para and Tailem Bend, limit Vic to Snowy to ensure transient stability for a Hazelwood to South Morang 500kV line fault, system normal limit less Sth East SA+Tailem Bend net load term less 240 MW
ESTN_TBSE | 2008-07-01 | 1 | SA / ESTN separation between South East Sub and Tailem Bend, limit Vic to Snowy to ensure transient stability for a Hazelwood to South Morang 500kV line fault, system normal limit less Sth East SA net load term less 240 MW
F_ESTN++HYML_L5 | 2009-01-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Eastern Lower 5 min Requirement
F_ESTN++HYML_L6 | 2008-07-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Eastern Lower 6 sec Requirement
F_ESTN++HYML_L60 | 2008-07-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Eastern Lower 60 sec Requirement
F_ESTN++HYML_R5 | 2009-01-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Eastern Raise 5 min Requirement
F_ESTN++HYML_R6 | 2008-07-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Eastern Raise 6 sec Requirement
F_ESTN++HYML_R60 | 2008-07-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Eastern Raise 60 sec Requirement
F_ESTN++HYSE_L5 | 2009-01-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Eastern Lower 5 min Requirement
F_ESTN++HYSE_L6 | 2008-07-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Eastern Lower 6 sec Requirement
F_ESTN++HYSE_L60 | 2008-07-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Eastern Lower 60 sec Requirement
F_ESTN++HYSE_R5 | 2009-01-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Eastern Raise 5 min Requirement
F_ESTN++HYSE_R6 | 2008-07-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Eastern Raise 6 sec Requirement
F_ESTN++HYSE_R60 | 2008-07-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Eastern Raise 60 sec Requirement
F_ESTN+LG_ISLE_L5 | 2006-01-06 | 1 | SA/ Eastern separation between Para and South East, Snuggery + Ladbroke Grove Lower 5 min Requirement = 0
F_ESTN+LG_ISLE_L6 | 2006-01-06 | 1 | SA/ Eastern separation between Para and South East, Snuggery + Ladbroke Grove Lower 6 sec Requirement = 0
F_ESTN+LG_ISLE_L60 | 2006-01-06 | 1 | SA/ Eastern separation between Para and South East, Snuggery + Ladbroke Grove Lower 60 sec Requirement = 0
F_ESTN+LG_ISLE_LREG | 2006-01-06 | 1 | SA/ Eastern separation between Para and South East, Snuggery + Ladbroke Grove Lower Regulation Requirement = 0
F_ESTN+LREG_0100 | 2008-07-01 | 1 | Eastern Lower Regulation Requirement greater than 100 MW
F_ESTN+LREG_0120 | 2008-07-01 | 1 | Eastern Lower Regulation Requirement greater than 120 MW
F_ESTN+LREG_0200 | 2008-07-01 | 1 | Eastern Lower Regulation Requirement greater than 200 MW
F_ESTN+LREG_0250 | 2008-07-01 | 1 | Eastern Lower Regulation Requirement greater than 250 MW
F_ESTN+MG_R5 | 2009-01-01 | 1 | Raise 5 min Service Requirement for Eastern Generation Event
F_ESTN+MG_R6 | 2008-07-01 | 2 | Raise 6 sec Service Requirement for Eastern Generation Event
F_ESTN+MG_R60 | 2008-07-01 | 2 | Raise 60 sec Service Requirement for Eastern Generation Event
F_ESTN+ML_L5_0370 | 2009-01-01 | 1 | Lower 5 min requirement for a Eastern Load Event, ML = 370
F_ESTN+ML_L5_0400 | 2009-01-01 | 1 | Lower 5 min requirement for a Eastern Load Event, ML = 400
F_ESTN+ML_L60_0370 | 2008-07-01 | 1 | Lower 60 sec requirement for a Eastern Load Event, ML = 370
F_ESTN+ML_L60_0400 | 2008-07-01 | 1 | Lower 60 sec requirement for a Eastern Load Event, ML = 400
F_ESTN+ML_L6_0370 | 2008-07-01 | 1 | Lower 6 sec requirement for a Eastern Load Event, ML = 370
F_ESTN+ML_L6_0400 | 2008-07-01 | 1 | Lower 6 sec requirement for a Eastern Load Event, ML = 400
F_ESTN+RREG_0100 | 2008-07-01 | 1 | Eastern Raise Regulation Requirement greater than 100 MW
F_ESTN+RREG_0130 | 2008-07-01 | 1 | Eastern Raise Regulation Requirement greater than 130 MW
F_ESTN+RREG_0200 | 2008-07-01 | 1 | Eastern Raise Regulation Requirement greater than 200 MW
F_ESTN+RREG_0250 | 2008-07-01 | 1 | Eastern Raise Regulation Requirement greater than 250 MW
F_ESTN+TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Eastern Network Event, TG = 500
F_ESTN+TG_R5_0700 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Eastern Network Event, TG = 700
F_ESTN+TG_R5_0850 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Eastern Network Event, TG = 850
F_ESTN+TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Eastern Network Event, TG = 1000
F_ESTN+TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Eastern Network Event, TG = 1400
F_ESTN+TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Eastern Network Event, TG = 1600
F_ESTN+TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Eastern Network Event, TG = 2000
F_ESTN+TG_R5_2800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Eastern Network Event, TG = 2800
F_ESTN+TG_R60_0500 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Eastern Network Event, TG = 500
F_ESTN+TG_R60_0700 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Eastern Network Event, TG = 700
F_ESTN+TG_R60_0850 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Eastern Network Event, TG = 850
F_ESTN+TG_R60_1000 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Eastern Network Event, TG = 1000
F_ESTN+TG_R60_1400 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Eastern Network Event, TG = 1400
F_ESTN+TG_R60_1600 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Eastern Network Event, TG = 1600
F_ESTN+TG_R60_2000 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Eastern Network Event, TG = 2000
F_ESTN+TG_R60_2800 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Eastern Network Event, TG = 2800
F_ESTN+TG_R6_0500 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Eastern Network Event, TG = 500
F_ESTN+TG_R6_0700 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Eastern Network Event, TG = 700
F_ESTN+TG_R6_0850 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Eastern Network Event, TG = 850
F_ESTN+TG_R6_1000 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Eastern Network Event, TG = 1000
F_ESTN+TG_R6_1400 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Eastern Network Event, TG = 1400
F_ESTN+TG_R6_1600 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Eastern Network Event, TG = 1600
F_ESTN+TG_R6_2000 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Eastern Network Event, TG = 2000
F_ESTN+TG_R6_2800 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Eastern Network Event, TG = 2800
F_ESTN+TL_L5_0600 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a Eastern Network Event, TL = 600
F_ESTN+TL_L5_0800 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a Eastern Network Event, TL = 800
F_ESTN+TL_L60_0600 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a Eastern Network Event, TL = 600
F_ESTN+TL_L60_0800 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a Eastern Network Event, TL = 800
F_ESTN+TL_L6_0600 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a Eastern Network Event, TL = 600
F_ESTN+TL_L6_0800 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a Eastern Network Event, TL = 800
F_I+BB_12_N-2_TG_R5 | 2009-01-01 | 1 | Out= Nil, loss of Bell Bay units 1 and 2 declared credible, Global Raise 5 min requirement
F_I+BB_12_N-2_TG_R60 | 2008-07-01 | 1 | Out = Nil, loss of Bell Bay units 1 and 2 declared credible, Global Raise 60 sec requirement
F_I+BB_N-2_TG_R5 | 2009-01-01 | 1 | Out= Nil, loss of all Bell Bay units declared credible, Global Raise 5 min requirement
F_I+BB_N-2_TG_R6 | 2008-07-01 | 1 | Out= Nil, loss of all Bell Bay units declared credible, Global Raise 6 sec requirement
F_I+BB_N-2_TG_R60 | 2008-07-01 | 1 | Out = Nil, loss of all Bell Bay units declared credible, Global Raise 60 sec requirement
F_I+COGT_BB_TL_L5 | 2009-01-01 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Global Lower 5 min requirement for the loss of the remaining Comalco to George Town line
F_I+COGT_BB_TL_L6 | 2008-07-01 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Global Lower 6 sec requirement for the loss of the remaining Comalco to George Town line
F_I+COGT_BB_TL_L60 | 2008-07-01 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Global Lower 60 sec requirement for the loss of the remaining Comalco to George Town line
F_I+COGT_TL_L5 | 2009-01-01 | 1 | Out = one Comalco to George Town line, Global Lower 5 min requirement for the loss of the remaining Comalco to George Town line
F_I+COGT_TL_L6 | 2008-07-01 | 1 | Out = one Comalco to George Town line, Global Lower 6 sec requirement for the loss of the remaining Comalco to George Town line
F_I+COGT_TL_L60 | 2008-07-01 | 1 | Out = one Comalco to George Town line, Global Lower 60 sec requirement for the loss of the remaining Comalco to George Town line
F_I+CSGO_TG_R5 | 2009-01-01 | 1 | Out = one Chapel St to Gordon line, Global Raise 5 min requirement for loss of the remaining Chapel St to Gordon line
F_I+CSGO_TG_R6 | 2008-07-01 | 1 | Out = one Chapel St to Gordon line, Global Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line
F_I+CSGO_TG_R60 | 2008-07-01 | 1 | Out = one Chapel St to Gordon line, Global Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line
F_I+FASH1_2B_TG_R5 | 2009-01-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with Tribute and Reece 1,2 supplying Sheffield, Global Raise 5 min requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_2B_TG_R6 | 2008-07-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with Tribute and Reece 1,2 supplying Sheffield, Global Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_2B_TG_R60 | 2008-07-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with Tribute and Reece 1,2 supplying Sheffield, Global Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_2C_TG_R5 | 2009-01-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Global Raise 5 min requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_2C_TG_R6 | 2008-07-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Global Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_2C_TG_R60 | 2008-07-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Global Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_2D_TG_R5 | 2009-01-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with Basttyan, John Butters, Tribute & Reece 2 supplying Sheffield, Global Raise 5 min requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_2D_TG_R6 | 2008-07-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with Bastyan, John Butters, Tribute & Reece 2 supplying Sheffield, Global Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_2D_TG_R60 | 2008-07-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with Bastyan, John Butters, Tribute & Reece 2 supplying Sheffield, Global Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_A_TG_R5 | 2009-01-01 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Global Raise 5 min requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_A_TG_R6 | 2008-07-01 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Global Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_A_TG_R60 | 2008-07-01 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield Global Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_B_TG_R5 | 2009-01-01 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + Reece 1 & 2 + Tribute supplying Sheffield, Global Raise 5 min requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_B_TG_R6 | 2008-07-01 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + Reece 1 & 2 + Tribute supplying Sheffield, Global Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH1_B_TG_R60 | 2008-07-01 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + Reece 1 & 2 + Tribute supplying Sheffield Global Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH2_A_TG_R5 | 2009-01-01 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Global Raise 5 min requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH2_A_TG_R6 | 2008-07-01 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Global Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH2_A_TG_R60 | 2008-07-01 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Global Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH_N-2_TG_R5 | 2009-01-01 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Global Raise 5 min requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH_N-2_TG_R6 | 2008-07-01 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Global Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+FASH_N-2_TG_R60 | 2008-07-01 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Global Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line
F_I+GO_A752_TG_R5 | 2009-01-01 | 1 | Out= Gordon CB A752, Global Raise 5 min requirement
F_I+GO_A752_TG_R6 | 2008-07-01 | 1 | Out= Gordon CB A752, Global Raise 6 sec requirement
F_I+GO_A752_TG_R60 | 2008-07-01 | 1 | Out= Gordon CB A752, Global Raise 60 sec requirement
F_I+GO_C752_TG_R5 | 2009-01-01 | 1 | Out= Gordon CB C752, Global Raise 5 min requirement
F_I+GO_C752_TG_R6 | 2008-07-01 | 1 | Out= Gordon CB C752, Global Raise 6 sec requirement
F_I+GO_C752_TG_R60 | 2008-07-01 | 1 | Out= Gordon CB C752, Global Raise 60 sec requirement
F_I+GT_TX_TG_R5 | 2009-01-01 | 1 | Out = one George Town 220/110kV transformer, Global Raise 5 min requirement for loss of the remaining George Town transformer
F_I+GT_TX_TG_R6 | 2008-07-01 | 1 | Out = one George Town 220/110kV transformer, Global Raise 6 sec requirement for loss of the remaining George Town transformer
F_I+GT_TX_TG_R60 | 2008-07-01 | 1 | Out = one George Town 220/110kV transformer, Global Raise 60 sec requirement for loss of the remaining George Town transformer
F_I+LREG_0100 | 2008-07-02 | 1 | NEM Lower Regulation Requirement greater than 100 MW
F_I+LREG_0120 | 2008-07-02 | 1 | NEM Lower Regulation Requirement greater than 120 MW
F_I+LREG_0200 | 2008-07-02 | 1 | NEM Lower Regulation Requirement greater than 200 MW
F_I+LREG_0250 | 2008-07-02 | 1 | NEM Lower Regulation Requirement greater than 250 MW
F_I+LREG_0400 | 2008-07-02 | 1 | NEM Lower Regulation Requirement greater than 400 MW
F_I+ML_L5_0370 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 370
F_I+ML_L5_0400 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 400
F_I+ML_L5_0500 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 500
F_I+ML_L5_0600 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 600
F_I+ML_L60_0370 | 2008-07-02 | 1 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 370
F_I+ML_L60_0400 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 400
F_I+ML_L60_0500 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 500
F_I+ML_L60_0600 | 2008-07-02 | 1 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 600
F_I+ML_L6_0370 | 2008-07-02 | 1 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 370
F_I+ML_L6_0400 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 400
F_I+ML_L6_0500 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 500
F_I+ML_L6_0600 | 2008-07-02 | 1 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 600
F_I+MPP_TG_R5_N-2 | 2009-01-01 | 1 | Out= Nil, loss of all Millmerran units declared credible, Global Raise 5 Min requirement
F_I+MPP_TG_R60_N-2 | 2008-07-01 | 1 | Out= Nil, loss of all Millmerran units declared credible, Global Raise 60 sec requirement
F_I+MPP_TG_R6_N-2 | 2008-07-01 | 1 | Out= Nil, loss of all Millmerran units declared credible, Global Raise 6 sec requirement
F_I+NIL_BB_TG_R5 | 2009-01-01 | 1 | Out= Nil, Global Raise 5 min requirement for loss of a Bell Bay to George Town line
F_I+NIL_BB_TG_R6 | 2008-07-01 | 1 | Out= Nil, Global Raise 6 sec requirement for loss of a Bell Bay to George Town line
F_I+NIL_BB_TG_R60 | 2008-07-01 | 1 | Out= Nil, Global Raise 60 sec requirement for loss of a Bell Bay to George Town line
F_I+NIL_DYN_LREG | 2008-07-01 | 1 | NEM Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s
F_I+NIL_DYN_RREG | 2008-07-01 | 1 | NEM Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s
F_I+NIL_HWPS_TG_R5 | 2009-01-01 | 1 | Out= Nil, Raise 5 min requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5
F_I+NIL_HWPS_TG_R6 | 2008-07-01 | 1 | Out= Nil, Raise 6 sec requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5
F_I+NIL_HWPS_TG_R60 | 2008-07-01 | 1 | Out= Nil, Raise 60 sec requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5
F_I+NIL_MG_R5 | 2009-01-01 | 1 | Out = Nil, Raise 5 min requirement for a NEM Generation Event
F_I+NIL_MG_R6 | 2008-07-01 | 1 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event
F_I+NIL_MG_R60 | 2008-07-01 | 1 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event
F_I+NIL_RREG | 2008-07-01 | 1 | Out=Nil, NEM Raise Regulation Requirement
F_I+NIL_WN_TG_R5 | 2009-01-01 | 1 | Out= Nil, Global Raise 5 min requirement for loss of a Smithton to Woolnorth line
F_I+NIL_WN_TG_R6 | 2008-12-01 | 1 | Out= Nil, Global Raise 6 sec requirement for loss of a Smithton to Woolnorth line
F_I+NIL_WN_TG_R60 | 2008-12-01 | 1 | Out= Nil, Global Raise 60 sec requirement for loss of a Smithton to Woolnorth line
F_I+RREG_0100 | 2008-07-02 | 1 | NEM Raise Regulation Requirement greater than 100 MW
F_I+RREG_0130 | 2008-07-02 | 1 | NEM Raise Regulation Requirement greater than 130 MW
F_I+RREG_0200 | 2008-07-02 | 1 | NEM Raise Regulation Requirement greater than 200 MW
F_I+RREG_0250 | 2008-07-02 | 1 | NEM Raise Regulation Requirement greater than 250 MW
F_I+RREG_0300 | 2008-07-02 | 1 | NEM Raise Regulation Requirement greater than 300 MW
F_I+RREG_0350 | 2008-07-02 | 1 | NEM Raise Regulation Requirement greater than 350 MW
F_I+RREG_0400 | 2008-07-02 | 1 | NEM Raise Regulation Requirement greater than 400 MW
F_I+RREG_0450 | 2008-07-02 | 1 | NEM Raise Regulation Requirement greater than 450 MW
F_I+RREG_0500 | 2008-07-02 | 1 | NEM Raise Regulation Requirement greater than 500 MW
F_I+RREG_0550 | 2008-07-02 | 1 | NEM Raise Regulation Requirement greater than 550 MW
F_I+RREG_0600 | 2008-07-02 | 1 | NEM Raise Regulation Requirement greater than 600 MW
F_I+SB_TG_R5 | 2009-01-01 | 1 | Out= one Swanbank B station auxiliary transformer, Global Raise 5 min Requirement for loss of the remaining transformer
F_I+SB_TG_R6 | 2008-07-01 | 1 | Out= one Swanbank B station auxiliary transformer, Global Raise 6 sec Requirement for loss of the remaining transformer
F_I+SB_TG_R60 | 2008-07-01 | 1 | Out= one Swanbank B station auxiliary transformer, Global Raise 60 sec Requirement for loss of the remaining transformer
F_I+ST_N-2_MG_R5 | 2009-01-01 | 1 | Out= Nil, loss of all Stanwell units declared credible, Global Raise 5 Min requirement
F_I+ST_N-2_MG_R6 | 2008-07-01 | 1 | Out= Nil, loss of all Stanwell units declared credible, Global Raise 6 sec requirement
F_I+ST_N-2_MG_R60 | 2008-07-01 | 1 | Out= Nil, loss of all Stanwell units declared credible, Global Raise 60 sec requirement
F_I+TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NEM Network Event, TG = 500
F_I+TG_R5_0700 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NEM Network Event, TG = 700
F_I+TG_R5_0850 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NEM Network Event, TG = 850
F_I+TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1000
F_I+TG_R5_1200 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1200
F_I+TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1400
F_I+TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1600
F_I+TG_R5_1800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NEM Network Event, TG = 1800
F_I+TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NEM Network Event, TG = 2000
F_I+TG_R5_2400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NEM Network Event, TG = 2400
F_I+TG_R5_2800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NEM Network Event, TG = 2800
F_I+TG_R60_0500 | 2008-07-24 | 1 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 500
F_I+TG_R60_0700 | 2008-07-24 | 1 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 700
F_I+TG_R60_0850 | 2008-07-24 | 1 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 850
F_I+TG_R60_1000 | 2008-07-24 | 1 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1000
F_I+TG_R60_1200 | 2008-07-24 | 1 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1200
F_I+TG_R60_1400 | 2008-07-24 | 1 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1400
F_I+TG_R60_1600 | 2008-07-24 | 1 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1600
F_I+TG_R60_1800 | 2008-07-24 | 1 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 1800
F_I+TG_R60_2000 | 2008-07-24 | 1 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 2000
F_I+TG_R60_2400 | 2008-07-24 | 1 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 2400
F_I+TG_R60_2800 | 2008-07-24 | 1 | Raise 60 sec Service Requirement for a NEM Network Event, TG = 2800
F_I+TG_R6_0500 | 2008-07-24 | 1 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 500
F_I+TG_R6_0700 | 2008-07-24 | 1 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 700
F_I+TG_R6_0850 | 2008-07-24 | 1 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 850
F_I+TG_R6_1000 | 2008-07-24 | 1 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1000
F_I+TG_R6_1200 | 2008-07-24 | 1 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1200
F_I+TG_R6_1400 | 2008-07-24 | 1 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1400
F_I+TG_R6_1600 | 2008-07-24 | 1 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1600
F_I+TG_R6_1800 | 2008-07-24 | 1 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 1800
F_I+TG_R6_2000 | 2008-07-24 | 1 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 2000
F_I+TG_R6_2400 | 2008-07-24 | 1 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 2400
F_I+TG_R6_2800 | 2008-07-24 | 1 | Raise 6 sec Service Requirement for a NEM Network Event, TG = 2800
F_I+TL_L5_0200 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a NEM Network Event, TL = 200
F_I+TL_L5_0400 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a NEM Network Event, TL = 400
F_I+TL_L5_0450 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a NEM Network Event, TL = 450
F_I+TL_L5_0500 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a NEM Network Event, TL = 500
F_I+TL_L5_0550 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a NEM Network Event, TL = 550
F_I+TL_L5_0600 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a NEM Network Event, TL = 600
F_I+TL_L5_0800 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a NEM Network Event, TL = 800
F_I+TL_L5_0900 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a NEM Network Event, TL = 900
F_I+TL_L60_0200 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a NEM Network Event, TL = 200
F_I+TL_L60_0400 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a NEM Network Event, TL = 400
F_I+TL_L60_0450 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a NEM Network Event, TL = 450
F_I+TL_L60_0500 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a NEM Network Event, TL = 500
F_I+TL_L60_0550 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a NEM Network Event, TL = 550
F_I+TL_L60_0600 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a NEM Network Event, TL = 600
F_I+TL_L60_0800 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a NEM Network Event, TL = 800
F_I+TL_L60_0900 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a NEM Network Event, TL = 900
F_I+TL_L6_0200 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a NEM Network Event, TL = 200
F_I+TL_L6_0400 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a NEM Network Event, TL = 400
F_I+TL_L6_0450 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a NEM Network Event, TL = 450
F_I+TL_L6_0500 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a NEM Network Event, TL = 500
F_I+TL_L6_0550 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a NEM Network Event, TL = 550
F_I+TL_L6_0600 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a NEM Network Event, TL = 600
F_I+TL_L6_0800 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a NEM Network Event, TL = 800
F_I+TL_L6_0900 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a NEM Network Event, TL = 900
F_I+X_TATUBG_TG_R5 | 2009-01-01 | 1 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible, Global Raise 5 min requirement for loss of the remaining Tungatinah to Waddamana line
F_I+X_TATUBG_TG_R6 | 2008-07-01 | 1 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible, Global Raise 6 sec requirement for loss of the remaining Tungatinah to Waddamana line
F_I+X_TATUBG_TG_R60 | 2008-07-01 | 1 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible, Global Raise 60 sec requirement for loss of the remaining Tungatinah to Waddamana line
F_MAIN++HWLY_TG_R5 | 2009-01-01 | 1 | Out = Two 500kV lines from Hazelwood to Loy Yang (HWTS-LYPS). Mainland Raise 5 min Service Requirement for risk of losing the remaining 500kV line.
F_MAIN++HWLY_TG_R6 | 2008-12-02 | 1 | Out = Two 500kV lines from Hazelwood to Loy Yang (HWTS-LYPS). Mainland Raise 6s Service Requirement for risk of losing the remaining 500kV line.
F_MAIN++HWLY_TG_R60 | 2008-12-02 | 1 | Out = Two 500kV lines from Hazelwood to Loy Yang (HWTS-LYPS). Mainland Raise 60s Service Requirement for risk of losing the remaining 500kV line.
F_MAIN++LREG_0100 | 2008-07-02 | 1 | Mainland Lower Regulation Requirement greater than 100 MW, Basslink able transfer FCAS
F_MAIN++LREG_0120 | 2008-07-02 | 1 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS
F_MAIN++LREG_0200 | 2008-07-02 | 1 | Mainland Lower Regulation Requirement greater than 200 MW, Basslink able transfer FCAS
F_MAIN++LREG_0250 | 2008-07-02 | 1 | Mainland Lower Regulation Requirement greater than 250 MW, Basslink able transfer FCAS
F_MAIN++LREG_0400 | 2008-07-02 | 1 | Mainland Lower Regulation Requirement greater than 350 MW, Basslink able transfer FCAS
F_MAIN++ML_L5_0370 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 370, Basslink able transfer FCAS
F_MAIN++ML_L5_0400 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS
F_MAIN++ML_L5_0500 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 500, Basslink able transfer FCAS
F_MAIN++ML_L5_0600 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 600, Basslink able transfer FCAS
F_MAIN++ML_L60_0370 | 2008-07-02 | 1 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 370, Basslink able transfer FCAS
F_MAIN++ML_L60_0400 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS
F_MAIN++ML_L60_0500 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 500, Basslink able transfer FCAS
F_MAIN++ML_L60_0600 | 2008-07-02 | 1 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 600, Basslink able transfer FCAS
F_MAIN++ML_L60_370 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 370, Basslink able transfer FCAS
F_MAIN++ML_L6_0370 | 2008-07-02 | 1 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 370, Basslink able transfer FCAS
F_MAIN++ML_L6_0400 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS
F_MAIN++ML_L6_0500 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 500, Basslink able transfer FCAS
F_MAIN++ML_L6_0600 | 2008-07-02 | 1 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 600, Basslink able transfer FCAS
F_MAIN++MPP_TGR5_N-2 | 2009-01-01 | 1 | Out= Nil, loss of all Millmerran units declared credible, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS
F_MAIN++MPP_TGR60N-2 | 2008-07-01 | 1 | Out= Nil, loss of all Millmerran units declared credible, Mainland Raise 60 sec requirement, Basslink able to transfer FCAS
F_MAIN++MPP_TGR6_N-2 | 2008-07-01 | 1 | Out= Nil, loss of all Millmerran units declared credible, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS
F_MAIN++NILHW_TG_R60 | 2008-07-01 | 1 | Out= Nil, Mainland Raise 60 sec requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5; Basslink able to transfer FCAS
F_MAIN++NIL_BL_L5 | 2009-01-01 | 1 | Mainland Lower 5 min Requirement for loss of Basslink, Basslink flow into Tas
F_MAIN++NIL_BL_L6 | 2008-07-01 | 1 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas
F_MAIN++NIL_BL_L60 | 2008-07-01 | 1 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas
F_MAIN++NIL_BL_R5 | 2009-01-01 | 1 | Mainland Raise 5 min Requirement for loss of Basslink, Basslink flow into Vic
F_MAIN++NIL_BL_R6 | 2008-07-01 | 1 | Mainland Raise 6 second Requirement for loss of Basslink, Basslink flow into Vic
F_MAIN++NIL_BL_R60 | 2008-07-01 | 1 | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic
F_MAIN++NIL_DYN_LREG | 2008-07-01 | 1 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s, Basslink able transfer FCAS
F_MAIN++NIL_DYN_RREG | 2008-07-01 | 1 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink able transfer FCAS
F_MAIN++NIL_HW_TG_R5 | 2009-01-01 | 1 | Out= Nil, Mainland Raise 5 min requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5; Basslink able to transfer FCAS
F_MAIN++NIL_HW_TG_R6 | 2008-07-01 | 1 | Out= Nil, Mainland Raise 6 sec requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5; Basslink able to transfer FCAS
F_MAIN++NIL_MG_R5 | 2009-01-01 | 1 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS
F_MAIN++NIL_MG_R6 | 2008-07-01 | 1 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS
F_MAIN++NIL_MG_R60 | 2008-07-01 | 1 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS
F_MAIN++NIL_RREG | 2008-07-01 | 1 | Out=Nil, Mainland Raise Regulation Requirement, Basslink able transfer FCAS
F_MAIN++RREG_0100 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 100 MW, Basslink able transfer FCAS
F_MAIN++RREG_0130 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 130 MW, Basslink able transfer FCAS
F_MAIN++RREG_0200 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS
F_MAIN++RREG_0250 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 250 MW, Basslink able transfer FCAS
F_MAIN++RREG_0300 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 300 MW, Basslink able transfer FCAS
F_MAIN++RREG_0350 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 350 MW, Basslink able transfer FCAS
F_MAIN++RREG_0400 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 400 MW, Basslink able transfer FCAS
F_MAIN++RREG_0450 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 450 MW, Basslink able transfer FCAS
F_MAIN++RREG_0500 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 500 MW, Basslink able transfer FCAS
F_MAIN++RREG_0550 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 550 MW, Basslink able transfer FCAS
F_MAIN++RREG_0600 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 600 MW, Basslink able transfer FCAS
F_MAIN++SB_TG_R5 | 2009-01-01 | 1 | Out= one Swanbank B station auxiliary transformer, Raise 5 min Requirement for loss of the remaining transformer, Basslink able to transfer FCAS
F_MAIN++SB_TG_R6 | 2008-07-01 | 1 | Out= one Swanbank B station auxiliary transformer, Raise 6 sec Requirement for loss of the remaining transformer, Basslink able to transfer FCAS
F_MAIN++SB_TG_R60 | 2008-07-01 | 1 | Out= one Swanbank B station auxiliary transformer, Raise 60 sec Requirement for loss of the remaining transformer, Basslink able to transfer FCAS
F_MAIN++ST_N-2_MGR60 | 2008-07-01 | 1 | Out= Nil, loss of all Stanwell units declared credible, Mainland Raise 60 sec requirement, Basslink able to transfer FCAS
F_MAIN++ST_N-2_MG_R5 | 2009-01-01 | 1 | Out= Nil, loss of all Stanwell units declared credible, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS
F_MAIN++ST_N-2_MG_R6 | 2008-07-01 | 1 | Out= Nil, loss of all Stanwell units declared credible, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS
F_MAIN++TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 500, Basslink able to transfer FCAS
F_MAIN++TG_R5_0700 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 700, Basslink able to transfer FCAS
F_MAIN++TG_R5_0850 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 850, Basslink able to transfer FCAS
F_MAIN++TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1000, Basslink able to transfer FCAS
F_MAIN++TG_R5_1200 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1200, Basslink able to transfer FCAS
F_MAIN++TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1400, Basslink able to transfer FCAS
F_MAIN++TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1600, Basslink able to transfer FCAS
F_MAIN++TG_R5_1800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1800, Basslink able to transfer FCAS
F_MAIN++TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 2000, Basslink able to transfer FCAS
F_MAIN++TG_R5_2400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 2400, Basslink able to transfer FCAS
F_MAIN++TG_R5_2800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 2800, Basslink able to transfer FCAS
F_MAIN++TG_R60_0500 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 500, Basslink able to transfer FCAS
F_MAIN++TG_R60_0700 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 700, Basslink able to transfer FCAS
F_MAIN++TG_R60_0850 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 850, Basslink able to transfer FCAS
F_MAIN++TG_R60_1000 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1000, Basslink able to transfer FCAS
F_MAIN++TG_R60_1200 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1200, Basslink able to transfer FCAS
F_MAIN++TG_R60_1400 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1400, Basslink able to transfer FCAS
F_MAIN++TG_R60_1600 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1600, Basslink able to transfer FCAS
F_MAIN++TG_R60_1800 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1800, Basslink able to transfer FCAS
F_MAIN++TG_R60_2000 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 2000, Basslink able to transfer FCAS
F_MAIN++TG_R60_2400 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 2400, Basslink able to transfer FCAS
F_MAIN++TG_R60_2800 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 2800, Basslink able to transfer FCAS
F_MAIN++TG_R6_0500 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 500, Basslink able to transfer FCAS
F_MAIN++TG_R6_0700 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 700, Basslink able to transfer FCAS
F_MAIN++TG_R6_0850 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 850, Basslink able to transfer FCAS
F_MAIN++TG_R6_1000 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 1000, Basslink able to transfer FCAS
F_MAIN++TG_R6_1200 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 1200, Basslink able to transfer FCAS
F_MAIN++TG_R6_1400 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 1400, Basslink able to transfer FCAS
F_MAIN++TG_R6_1600 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 1600, Basslink able to transfer FCAS
F_MAIN++TG_R6_1800 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 1800, Basslink able to transfer FCAS
F_MAIN++TG_R6_2000 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 2000, Basslink able to transfer FCAS
F_MAIN++TG_R6_2400 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 2400, Basslink able to transfer FCAS
F_MAIN++TG_R6_2800 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 2800, Basslink able to transfer FCAS
F_MAIN++TL_L5_0400 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 400, Basslink able to transfer FCAS
F_MAIN++TL_L5_0450 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 450, Basslink able to transfer FCAS
F_MAIN++TL_L5_0500 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 500, Basslink able to transfer FCAS
F_MAIN++TL_L5_0550 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 550, Basslink able to transfer FCAS
F_MAIN++TL_L5_0600 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 600, Basslink able to transfer FCAS
F_MAIN++TL_L5_0800 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 800, Basslink able to transfer FCAS
F_MAIN++TL_L5_0900 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 900, Basslink able to transfer FCAS
F_MAIN++TL_L60_0400 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 400, Basslink able to transfer FCAS
F_MAIN++TL_L60_0450 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 450, Basslink able to transfer FCAS
F_MAIN++TL_L60_0500 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 500, Basslink able to transfer FCAS
F_MAIN++TL_L60_0550 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 550, Basslink able to transfer FCAS
F_MAIN++TL_L60_0600 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 600, Basslink able to transfer FCAS
F_MAIN++TL_L60_0800 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 800, Basslink able to transfer FCAS
F_MAIN++TL_L60_0900 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 900, Basslink able to transfer FCAS
F_MAIN++TL_L6_0400 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 400, Basslink able to transfer FCAS
F_MAIN++TL_L6_0450 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 450, Basslink able to transfer FCAS
F_MAIN++TL_L6_0500 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 500, Basslink able to transfer FCAS
F_MAIN++TL_L6_0550 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 550, Basslink able to transfer FCAS
F_MAIN++TL_L6_0600 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 600, Basslink able to transfer FCAS
F_MAIN++TL_L6_0800 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 800, Basslink able to transfer FCAS
F_MAIN++TL_L6_0900 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 900, Basslink able to transfer FCAS
F_MAIN+LREG_0100 | 2008-07-02 | 1 | Mainland Lower Regulation Requirement greater than 100 MW, Basslink unable to transfer FCAS
F_MAIN+LREG_0120 | 2008-07-02 | 1 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS
F_MAIN+LREG_0200 | 2008-07-02 | 1 | Mainland Lower Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS
F_MAIN+LREG_0250 | 2008-07-02 | 1 | Mainland Lower Regulation Requirement greater than 250 MW, Basslink unable to transfer FCAS
F_MAIN+LREG_0400 | 2008-07-02 | 1 | Mainland Lower Regulation Requirement greater than 350 MW, Basslink unable to transfer FCAS
F_MAIN+ML_L5_0370 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 370, Basslink unable transfer FCAS
F_MAIN+ML_L5_0400 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS
F_MAIN+ML_L5_0500 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 500, Basslink unable transfer FCAS
F_MAIN+ML_L5_0600 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 600, Basslink unable transfer FCAS
F_MAIN+ML_L60_0370 | 2008-07-02 | 1 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 370, Basslink unable transfer FCAS
F_MAIN+ML_L60_0400 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS
F_MAIN+ML_L60_0500 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 500, Basslink unable transfer FCAS
F_MAIN+ML_L60_0600 | 2008-07-02 | 1 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 600, Basslink unable transfer FCAS
F_MAIN+ML_L6_0370 | 2008-07-02 | 1 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 370, Basslink unable transfer FCAS
F_MAIN+ML_L6_0400 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS
F_MAIN+ML_L6_0500 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 500, Basslink unable transfer FCAS
F_MAIN+ML_L6_0600 | 2008-07-02 | 1 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 600, Basslink unable transfer FCAS
F_MAIN+MPP_TG_R5_N-2 | 2009-01-01 | 1 | Out= Nil, loss of all Millmerran units declared credible, Mainland Raise 5 Min requirement, Basslink unable to transfer FCAS
F_MAIN+MPP_TG_R60N-2 | 2008-07-01 | 1 | Out= Nil, loss of all Millmerran units declared credible, Mainland Raise 60 sec requirement, Basslink unable to transfer FCAS
F_MAIN+MPP_TG_R6_N-2 | 2008-07-01 | 1 | Out= Nil, loss of all Millmerran units declared credible, Mainland Raise 6 sec requirement, Basslink unable to transfer FCAS
F_MAIN+NIL_DYN_LREG | 2008-07-01 | 1 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s, Basslink unable transfer FCAS
F_MAIN+NIL_DYN_RREG | 2008-07-01 | 1 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink unable transfer FCAS
F_MAIN+NIL_HW_TG_R5 | 2009-01-01 | 1 | Out= Nil, Mainland Raise 5 min requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5; Basslink unable to transfer FCAS
F_MAIN+NIL_HW_TG_R6 | 2008-07-01 | 1 | Out= Nil, Mainland Raise 6 sec requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5; Basslink unable to transfer FCAS
F_MAIN+NIL_HW_TG_R60 | 2008-07-01 | 1 | Out= Nil, Mainland Raise 60 sec requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5; Basslink unable to transfer FCAS
F_MAIN+NIL_MG_R5 | 2009-01-01 | 1 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS
F_MAIN+NIL_MG_R6 | 2008-07-01 | 1 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS
F_MAIN+NIL_MG_R60 | 2008-07-01 | 1 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS
F_MAIN+NIL_RREG | 2008-07-01 | 1 | Out=Nil, Mainland Raise Regulation Requirement, Basslink unable to transfer FCAS
F_MAIN+RREG_0100 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 100 MW, Basslink unable to transfer FCAS
F_MAIN+RREG_0130 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 130 MW, Basslink unable to transfer FCAS
F_MAIN+RREG_0200 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS
F_MAIN+RREG_0250 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 250 MW, Basslink unable to transfer FCAS
F_MAIN+RREG_0300 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 300 MW, Basslink unable to transfer FCAS
F_MAIN+RREG_0350 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 350 MW, Basslink unable to transfer FCAS
F_MAIN+RREG_0400 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 400 MW, Basslink unable to transfer FCAS
F_MAIN+RREG_0450 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 450 MW, Basslink unable to transfer FCAS
F_MAIN+RREG_0500 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 500 MW, Basslink unable to transfer FCAS
F_MAIN+RREG_0550 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 550 MW, Basslink unable to transfer FCAS
F_MAIN+RREG_0600 | 2008-07-02 | 1 | Mainland Raise Regulation Requirement greater than 600 MW, Basslink unable to transfer FCAS
F_MAIN+SB_TG_R5 | 2009-01-01 | 1 | Out= one Swanbank B station auxiliary transformer, Raise 5 min Requirement for loss of the remaining transformer, Basslink unable to transfer FCAS
F_MAIN+SB_TG_R6 | 2008-07-01 | 1 | Out= one Swanbank B station auxiliary transformer, Raise 6 sec Requirement for loss of the remaining transformer, Basslink unable to transfer FCAS
F_MAIN+SB_TG_R60 | 2008-07-01 | 1 | Out= one Swanbank B station auxiliary transformer, Raise 60 sec Requirement for loss of the remaining transformer, Basslink unable to transfer FCAS
F_MAIN+ST_N-2_MG_R5 | 2009-01-01 | 1 | Out= Nil, loss of all Stanwell units declared credible, Mainland Raise 5 Min requirement, Basslink unable to transfer FCAS
F_MAIN+ST_N-2_MG_R6 | 2008-07-01 | 1 | Out= Nil, loss of all Stanwell units declared credible, Mainland Raise 6 sec requirement, Basslink unable to transfer FCAS
F_MAIN+ST_N-2_MG_R60 | 2008-07-01 | 1 | Out= Nil, loss of all Stanwell units declared credible, Mainland Raise 60 sec requirement, Basslink unable to transfer FCAS
F_MAIN+TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 500, Basslink unable to transfer FCAS
F_MAIN+TG_R5_0700 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 700, Basslink unable to transfer FCAS
F_MAIN+TG_R5_0850 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 850, Basslink unable to transfer FCAS
F_MAIN+TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1000, Basslink unable to transfer FCAS
F_MAIN+TG_R5_1200 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1200, Basslink unable to transfer FCAS
F_MAIN+TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1400, Basslink unable to transfer FCAS
F_MAIN+TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1600, Basslink unable to transfer FCAS
F_MAIN+TG_R5_1800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 1800, Basslink unable to transfer FCAS
F_MAIN+TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 2000, Basslink unable to transfer FCAS
F_MAIN+TG_R5_2400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 2400, Basslink unable to transfer FCAS
F_MAIN+TG_R5_2800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Mainland Network Event, TG = 2800, Basslink unable to transfer FCAS
F_MAIN+TG_R60_0500 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 500, Basslink unable to transfer FCAS
F_MAIN+TG_R60_0700 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 700, Basslink unable to transfer FCAS
F_MAIN+TG_R60_0850 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 850, Basslink unable to transfer FCAS
F_MAIN+TG_R60_1000 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1000, Basslink unable to transfer FCAS
F_MAIN+TG_R60_1200 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1200, Basslink unable to transfer FCAS
F_MAIN+TG_R60_1400 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1400, Basslink unable to transfer FCAS
F_MAIN+TG_R60_1600 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1600, Basslink unable to transfer FCAS
F_MAIN+TG_R60_1800 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 1800, Basslink unable to transfer FCAS
F_MAIN+TG_R60_2000 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 2000, Basslink unable to transfer FCAS
F_MAIN+TG_R60_2400 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 2400, Basslink unable to transfer FCAS
F_MAIN+TG_R60_2800 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Mainland Network Event, TG = 2800, Basslink unable to transfer FCAS
F_MAIN+TG_R6_0500 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 500, Basslink unable to transfer FCAS
F_MAIN+TG_R6_0700 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 700, Basslink unable to transfer FCAS
F_MAIN+TG_R6_0850 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 850, Basslink unable to transfer FCAS
F_MAIN+TG_R6_1000 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 1000, Basslink unable to transfer FCAS
F_MAIN+TG_R6_1200 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 1200, Basslink unable to transfer FCAS
F_MAIN+TG_R6_1400 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 1400, Basslink unable to transfer FCAS
F_MAIN+TG_R6_1600 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 1600, Basslink unable to transfer FCAS
F_MAIN+TG_R6_1800 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 1800, Basslink unable to transfer FCAS
F_MAIN+TG_R6_2000 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 2000, Basslink unable to transfer FCAS
F_MAIN+TG_R6_2400 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 2400, Basslink unable to transfer FCAS
F_MAIN+TG_R6_2800 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Mainland Network Event, TG = 2800, Basslink unable to transfer FCAS
F_MAIN+TL_L5_0400 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 400, Basslink unable to transfer FCAS
F_MAIN+TL_L5_0450 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 450, Basslink unable to transfer FCAS
F_MAIN+TL_L5_0500 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 500, Basslink unable to transfer FCAS
F_MAIN+TL_L5_0550 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 550, Basslink unable to transfer FCAS
F_MAIN+TL_L5_0600 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 600, Basslink unable to transfer FCAS
F_MAIN+TL_L5_0800 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 800, Basslink unable to transfer FCAS
F_MAIN+TL_L5_0900 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 900, Basslink unable to transfer FCAS
F_MAIN+TL_L60_0400 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 400, Basslink unable to transfer FCAS
F_MAIN+TL_L60_0450 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 450, Basslink unable to transfer FCAS
F_MAIN+TL_L60_0500 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 500, Basslink unable to transfer FCAS
F_MAIN+TL_L60_0550 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 550, Basslink unable to transfer FCAS
F_MAIN+TL_L60_0600 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 600, Basslink unable to transfer FCAS
F_MAIN+TL_L60_0800 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 800, Basslink unable to transfer FCAS
F_MAIN+TL_L60_0900 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event, TL = 900, Basslink unable to transfer FCAS
F_MAIN+TL_L6_0400 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 400, Basslink unable to transfer FCAS
F_MAIN+TL_L6_0450 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 450, Basslink unable to transfer FCAS
F_MAIN+TL_L6_0500 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 500, Basslink unable to transfer FCAS
F_MAIN+TL_L6_0550 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 550, Basslink unable to transfer FCAS
F_MAIN+TL_L6_0600 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 600, Basslink unable to transfer FCAS
F_MAIN+TL_L6_0800 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 800, Basslink unable to transfer FCAS
F_MAIN+TL_L6_0900 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event, TL = 900, Basslink unable to transfer FCAS
F_NQ++65_051_0X1_L5 | 2009-01-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, NSW & Qld Lower 5 min requirement
F_NQ++65_051_0X1_L6 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, NSW & Qld Lower 6 sec requirement
F_NQ++65_051_0X1_L60 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, NSW & Qld Lower 60 sec requirement
F_NQ++65_051_0X1_R5 | 2009-01-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, NSW & Qld Raise 5 min requirement
F_NQ++65_051_0X1_R6 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, NSW & Qld Raise 6 sec requirement
F_NQ++65_051_0X1_R60 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, NSW & Qld Raise 60 sec requirement
F_NQ+LREG_0120 | 2006-06-27 | 1 | Separated NSW and Qld Lower Regulation Requirement greater than 120 MW
F_NQ+MG_R5 | 2009-01-01 | 1 | Raise 5 min Service Requirement for separated NSW and Qld Generation Event
F_NQ+MG_R6 | 2003-10-02 | 1 | Raise 6 sec Service Requirement for separated NSW and Qld Generation Event
F_NQ+MG_R60 | 2003-10-02 | 1 | Raise 60 sec Service Requirement for separated NSW and Qld Generation Event
F_NQ+ML_L5_0370 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a NSW and Qld Load Event, ML = 370
F_NQ+ML_L60_0370 | 2005-12-21 | 1 | Lower 60 sec Service Requirement for a NSW and Qld Load Event, ML = 370
F_NQ+ML_L6_0370 | 2005-12-21 | 1 | Lower 6 sec Service Requirement for a NSW and Qld Load Event, ML = 370
F_NQ+RREG_0130 | 2005-07-25 | 1 | Separated NSW and Qld Raise Regulation Requirement greater than 130 MW
F_NQ+TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW and Qld Network Event, TG = 500
F_NQ+TG_R5_0700 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW and Qld Network Event, TG = 700
F_NQ+TG_R5_0850 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW and Qld Network Event, TG = 850
F_NQ+TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW and Qld Network Event, TG = 1000
F_NQ+TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW and Qld Network Event, TG = 1400
F_NQ+TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW and Qld Network Event, TG = 1600
F_NQ+TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW and Qld Network Event, TG = 2000
F_NQ+TG_R5_2800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW and Qld Network Event, TG = 2800
F_NQ+TG_R60_0500 | 2003-08-01 | 1 | Raise 60 sec Service Requirement for a NSW and Qld Network Event, TG = 500
F_NQ+TG_R60_0700 | 2003-08-01 | 1 | Raise 60 sec Service Requirement for a NSW and Qld Network Event, TG = 700
F_NQ+TG_R60_0850 | 2005-09-12 | 1 | Raise 60 sec Service Requirement for a NSW and Qld Network Event, TG = 850
F_NQ+TG_R60_1000 | 2003-08-01 | 1 | Raise 60 sec Service Requirement for a NSW and Qld Network Event, TG = 1000
F_NQ+TG_R60_1400 | 2003-08-01 | 1 | Raise 60 sec Service Requirement for a NSW and Qld Network Event, TG = 1400
F_NQ+TG_R60_1600 | 2003-08-01 | 1 | Raise 60 sec Service Requirement for a NSW and Qld Network Event, TG = 1600
F_NQ+TG_R60_2000 | 2003-08-01 | 1 | Raise 60 sec Service Requirement for a NSW and Qld Network Event, TG = 2000
F_NQ+TG_R60_2800 | 2005-09-12 | 1 | Raise 60 sec Service Requirement for a NSW and Qld Network Event, TG = 2800
F_NQ+TG_R6_0500 | 2003-08-01 | 1 | Raise 6 sec Service Requirement for a NSW and Qld Network Event, TG = 500
F_NQ+TG_R6_0700 | 2003-08-01 | 1 | Raise 6 sec Service Requirement for a NSW and Qld Network Event, TG = 700
F_NQ+TG_R6_0850 | 2005-09-12 | 1 | Raise 6 sec Service Requirement for a NSW and Qld Network Event, TG = 850
F_NQ+TG_R6_1000 | 2003-08-01 | 1 | Raise 6 sec Service Requirement for a NSW and Qld Network Event, TG = 1000
F_NQ+TG_R6_1400 | 2003-08-01 | 1 | Raise 6 sec Service Requirement for a NSW and Qld Network Event, TG = 1400
F_NQ+TG_R6_1600 | 2003-08-01 | 1 | Raise 6 sec Service Requirement for a NSW and Qld Network Event, TG = 1600
F_NQ+TG_R6_2000 | 2003-08-01 | 1 | Raise 6 sec Service Requirement for a NSW and Qld Network Event, TG = 2000
F_NQ+TG_R6_2800 | 2005-09-12 | 1 | Raise 6 sec Service Requirement for a NSW and Qld Network Event, TG = 2800
F_NQ+TL_L5_0350 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a NSW and Qld Network Event, TL = 350
F_NQ+TL_L5_0800 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a NSW and Qld Network Event, TL = 800
F_NQ+TL_L60_0350 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a NSW and Qld Network Event, TL = 350
F_NQ+TL_L60_0800 | 2003-08-01 | 1 | Lower 60 sec Service Requirement for a NSW and Qld Network Event, TL = 800
F_NQ+TL_L6_0350 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a NSW and Qld Network Event, TL = 350
F_NQ+TL_L6_0800 | 2003-08-01 | 1 | Lower 6 sec Service Requirement for a NSW and Qld Network Event, TL = 800
F_NVS++ARDM_L5 | 2009-01-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, NSW, Snowy, Vic and SA Lower 5 min Requirement, Basslink able to transfer FCAS
F_NVS++ARDM_L6 | 2008-07-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, NSW, Snowy, Vic and SA Lower 6 sec Requirement, Basslink able to transfer FCAS
F_NVS++ARDM_L60 | 2008-07-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink able to transfer FCAS
F_NVS++ARDM_R5 | 2009-01-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, NSW, Snowy, Vic and SA Raise 5 min Requirement, Basslink able to transfer FCAS
F_NVS++ARDM_R6 | 2008-07-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, NSW, Snowy, Vic and SA Raise 6 sec Requirement, Basslink able to transfer FCAS
F_NVS++ARDM_R60 | 2008-07-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, NSW, Snowy, Vic and SA Raise 60 sec Requirement, Basslink able to transfer FCAS
F_NVS++ARTW_L5 | 2009-01-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 5 min Requirement, Basslink able to transfer FCAS
F_NVS++ARTW_L6 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 6 sec Requirement, Basslink able to transfer FCAS
F_NVS++ARTW_L60 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink able to transfer FCAS
F_NVS++ARTW_R5 | 2009-01-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Raise 5 min Requirement, Basslink able to transfer FCAS
F_NVS++ARTW_R6 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Raise 6 sec Requirement, Basslink able to transfer FCAS
F_NVS++ARTW_R60 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Raise 60 sec Requirement, Basslink able to transfer FCAS
F_NVS++LDMU_L5 | 2009-01-01 | 1 | Out = Liddell to Muswellbrook (83) line, NSW, Snowy, Vic and SA Lower 5 min Requirement, Basslink able to transfer FCAS
F_NVS++LDMU_L6 | 2008-07-01 | 1 | Out = Liddell to Muswellbrook (83) line, NSW, Snowy, Vic and SA Lower 6 sec Requirement, Basslink able to transfer FCAS
F_NVS++LDMU_L60 | 2008-07-01 | 1 | Out = Liddell to Muswellbrook (83) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink able to transfer FCAS
F_NVS++LDMU_R5 | 2009-01-01 | 1 | Out = Liddell to Muswellbrook (83) line, NSW, Snowy, Vic and SA Raise 5 min Requirement, Basslink able to transfer FCAS
F_NVS++LDMU_R6 | 2008-07-01 | 1 | Out = Liddell to Muswellbrook (83) line, NSW, Snowy, Vic and SA Raise 6 sec Requirement, Basslink able to transfer FCAS
F_NVS++LDMU_R60 | 2008-07-01 | 1 | Out = Liddell to Muswellbrook (83) line, NSW, Snowy, Vic and SA Raise 60 sec Requirement, Basslink able to transfer FCAS
F_NVS++LDTW_L5 | 2009-01-01 | 1 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Lower 5 min Requirement, Basslink able to transfer FCAS
F_NVS++LDTW_L6 | 2008-07-01 | 1 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Lower 6 sec Requirement, Basslink able to transfer FCAS
F_NVS++LDTW_L60 | 2008-07-01 | 1 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink able to transfer FCAS
F_NVS++LDTW_R5 | 2009-01-01 | 1 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Raise 5 min Requirement, Basslink able to transfer FCAS
F_NVS++LDTW_R6 | 2008-07-01 | 1 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Raise 6 sec Requirement, Basslink able to transfer FCAS
F_NVS++LDTW_R60 | 2008-07-01 | 1 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Raise 60 sec Requirement, Basslink able to transfer FCAS
F_NVS++LREG_0100 | 2008-07-01 | 1 | NSW, Vic and SA Lower Regulation Requirement greater than 100 MW, Basslink able transfer FCAS
F_NVS++LREG_0120 | 2008-07-01 | 1 | NSW, Vic and SA Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS
F_NVS++LREG_0200 | 2008-07-01 | 1 | NSW, Vic and SA Lower Regulation Requirement greater than 200 MW, Basslink able transfer FCAS
F_NVS++LREG_0250 | 2008-07-01 | 1 | NSW, Vic and SA Lower Regulation Requirement greater than 250 MW, Basslink able transfer FCAS
F_NVS++ML_L5_0300 | 2009-01-01 | 1 | Lower 5 min requirement for a NSW, Vic and SA Load Event, ML = 300, Basslink able transfer FCAS
F_NVS++ML_L60_0300 | 2008-07-01 | 1 | Lower 60 sec requirement for a NSW, Vic and SA Load Event, ML = 300, Basslink able transfer FCAS
F_NVS++ML_L6_0300 | 2008-07-01 | 1 | Lower 6 sec requirement for a NSW, Vic and SA Load Event, ML = 300, Basslink able transfer FCAS
F_NVS++MUTW_L5 | 2009-01-01 | 1 | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Lower 5 min Requirement, Basslink able to transfer FCAS
F_NVS++MUTW_L6 | 2008-07-01 | 1 | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Lower 6 sec Requirement, Basslink able to transfer FCAS
F_NVS++MUTW_L60 | 2008-07-01 | 1 | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink able to transfer FCAS
F_NVS++MUTW_R5 | 2009-01-01 | 1 | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Raise 5 min Requirement, Basslink able to transfer FCAS
F_NVS++MUTW_R6 | 2008-07-01 | 1 | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Raise 6 sec Requirement, Basslink able to transfer FCAS
F_NVS++MUTW_R60 | 2008-07-01 | 1 | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Raise 60 sec Requirement, Basslink able to transfer FCAS
F_NVS++RREG_0100 | 2008-07-01 | 1 | NSW, Vic and SA Raise Regulation Requirement greater than 100 MW, Basslink able transfer FCAS
F_NVS++RREG_0130 | 2008-07-01 | 1 | NSW, Vic and SA Raise Regulation Requirement greater than 130 MW, Basslink able transfer FCAS
F_NVS++RREG_0200 | 2008-07-01 | 1 | NSW, Vic and SA Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS
F_NVS++RREG_0250 | 2008-07-01 | 1 | NSW, Vic and SA Raise Regulation Requirement greater than 250 MW, Basslink able transfer FCAS
F_NVS++TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 500, Basslink able to transfer FCAS
F_NVS++TG_R5_0700 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 700, Basslink able to transfer FCAS
F_NVS++TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 1000, Basslink able to transfer FCAS
F_NVS++TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 1400, Basslink able to transfer FCAS
F_NVS++TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 1600, Basslink able to transfer FCAS
F_NVS++TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 2000, Basslink able to transfer FCAS
F_NVS++TG_R5_2800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 2800, Basslink able to transfer FCAS
F_NVS++TG_R60_0500 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 500, Basslink able to transfer FCAS
F_NVS++TG_R60_0700 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 700, Basslink able to transfer FCAS
F_NVS++TG_R60_1000 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 1000, Basslink able to transfer FCAS
F_NVS++TG_R60_1400 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 1400, Basslink able to transfer FCAS
F_NVS++TG_R60_1600 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 1600, Basslink able to transfer FCAS
F_NVS++TG_R60_2000 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 2000, Basslink able to transfer FCAS
F_NVS++TG_R60_2800 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 2800, Basslink able to transfer FCAS
F_NVS++TG_R6_0500 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 500, Basslink able to transfer FCAS
F_NVS++TG_R6_0700 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 700, Basslink able to transfer FCAS
F_NVS++TG_R6_1000 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 1000, Basslink able to transfer FCAS
F_NVS++TG_R6_1400 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 1400, Basslink able to transfer FCAS
F_NVS++TG_R6_1600 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 1600, Basslink able to transfer FCAS
F_NVS++TG_R6_2000 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 2000, Basslink able to transfer FCAS
F_NVS++TG_R6_2800 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 2800, Basslink able to transfer FCAS
F_NVS++TL_L5_0600 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a NSW, Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS
F_NVS++TL_L5_0800 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a NSW, Vic and SA Network Event, TL = 800, Basslink able to transfer FCAS
F_NVS++TL_L5_1000 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a NSW, Vic and SA Network Event, TL = 1000, Basslink able to transfer FCAS
F_NVS++TL_L60_0600 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a NSW, Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS
F_NVS++TL_L60_0800 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a NSW, Vic and SA Network Event, TL = 800, Basslink able to transfer FCAS
F_NVS++TL_L60_1000 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a NSW, Vic and SA Network Event, TL = 1000, Basslink able to transfer FCAS
F_NVS++TL_L6_0600 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a NSW, Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS
F_NVS++TL_L6_0800 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a NSW, Vic and SA Network Event, TL = 800, Basslink able to transfer FCAS
F_NVS++TL_L6_1000 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a NSW, Vic and SA Network Event, TL = 1000, Basslink able to transfer FCAS
F_NVS+ARDM_L5 | 2009-01-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, NSW, Snowy, Vic and SA Lower 5 min Requirement, Basslink unable to transfer FCAS
F_NVS+ARDM_L6 | 2008-07-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, NSW, Snowy, Vic and SA Lower 6 sec Requirement, Basslink unable to transfer FCAS
F_NVS+ARDM_L60 | 2008-07-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS
F_NVS+ARDM_R5 | 2009-01-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, NSW, Snowy, Vic and SA Raise 5 min Requirement, Basslink unable to transfer FCAS
F_NVS+ARDM_R6 | 2008-07-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, NSW, Snowy, Vic and SA Raise 6 sec Requirement, Basslink unable to transfer FCAS
F_NVS+ARDM_R60 | 2008-07-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, NSW, Snowy, Vic and SA Raise 60 sec Requirement, Basslink unable to transfer FCAS
F_NVS+ARTW_L5 | 2009-01-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 5 min Requirement, Basslink unable to transfer FCAS
F_NVS+ARTW_L6 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 6 sec Requirement, Basslink unable to transfer FCAS
F_NVS+ARTW_L60 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS
F_NVS+ARTW_R5 | 2009-01-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Raise 5 min Requirement, Basslink unable to transfer FCAS
F_NVS+ARTW_R6 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Raise 6 sec Requirement, Basslink unable to transfer FCAS
F_NVS+ARTW_R60 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Raise 60 sec Requirement, Basslink unable to transfer FCAS
F_NVS+LDMU_L5 | 2009-01-01 | 1 | Out = Liddell to Muswellbrook (83) line, NSW, Snowy, Vic and SA Lower 5 min Requirement, Basslink unable to transfer FCAS
F_NVS+LDMU_L6 | 2008-07-01 | 1 | Out = Liddell to Muswellbrook (83) line, NSW, Snowy, Vic and SA Lower 6 sec Requirement, Basslink unable to transfer FCAS
F_NVS+LDMU_L60 | 2008-07-01 | 1 | Out = Liddell to Muswellbrook (83) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS
F_NVS+LDMU_R5 | 2009-01-01 | 1 | Out = Liddell to Muswellbrook (83) line, NSW, Snowy, Vic and SA Raise 5 min Requirement, Basslink unable to transfer FCAS
F_NVS+LDMU_R6 | 2008-07-01 | 1 | Out = Liddell to Muswellbrook (83) line, NSW, Snowy, Vic and SA Raise 6 sec Requirement, Basslink unable to transfer FCAS
F_NVS+LDMU_R60 | 2008-07-01 | 1 | Out = Liddell to Muswellbrook (83) line, NSW, Snowy, Vic and SA Raise 60 sec Requirement, Basslink unable to transfer FCAS
F_NVS+LDTW_L5 | 2009-01-01 | 1 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Lower 5 min Requirement, Basslink unable to transfer FCAS
F_NVS+LDTW_L6 | 2008-07-01 | 1 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Lower 6 sec Requirement, Basslink unable to transfer FCAS
F_NVS+LDTW_L60 | 2008-07-01 | 1 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS
F_NVS+LDTW_R5 | 2009-01-01 | 1 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Raise 5 min Requirement, Basslink unable to transfer FCAS
F_NVS+LDTW_R6 | 2008-07-01 | 1 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Raise 6 sec Requirement, Basslink unable to transfer FCAS
F_NVS+LDTW_R60 | 2008-07-01 | 1 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Raise 60 sec Requirement, Basslink unable to transfer FCAS
F_NVS+LREG_0100 | 2008-07-01 | 1 | NSW, Vic and SA Lower Regulation Requirement greater than 100 MW, Basslink unable to transfer FCAS
F_NVS+LREG_0120 | 2008-07-01 | 1 | NSW, Vic and SA Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS
F_NVS+LREG_0200 | 2008-07-01 | 1 | NSW, Vic and SA Lower Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS
F_NVS+LREG_0250 | 2008-07-01 | 1 | NSW, Vic and SA Lower Regulation Requirement greater than 250 MW, Basslink unable to transfer FCAS
F_NVS+ML_L5_0300 | 2009-01-01 | 1 | Lower 5 min requirement for a NSW, Vic and SA Load Event, ML = 300, Basslink unable transfer FCAS
F_NVS+ML_L60_0300 | 2008-07-01 | 1 | Lower 60 sec requirement for a NSW, Vic and SA Load Event, ML = 300, Basslink unable transfer FCAS
F_NVS+ML_L6_0300 | 2008-07-01 | 1 | Lower 6 sec requirement for a NSW, Vic and SA Load Event, ML = 300, Basslink unable transfer FCAS
F_NVS+MUTW_L5 | 2009-01-01 | 1 | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Lower 5 min Requirement, Basslink unable to transfer FCAS
F_NVS+MUTW_L6 | 2008-07-01 | 1 | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Lower 6 sec Requirement, Basslink unable to transfer FCAS
F_NVS+MUTW_L60 | 2008-07-01 | 1 | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS
F_NVS+MUTW_R5 | 2009-01-01 | 1 | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Raise 5 min Requirement, Basslink unable to transfer FCAS
F_NVS+MUTW_R6 | 2008-07-01 | 1 | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Raise 6 sec Requirement, Basslink unable to transfer FCAS
F_NVS+MUTW_R60 | 2008-07-01 | 1 | Out = Muswellbrook to Tamworth (88) line, NSW, Snowy, Vic and SA Raise 60 sec Requirement, Basslink unable to transfer FCAS
F_NVS+RREG_0100 | 2008-07-01 | 1 | NSW, Vic and SA Raise Regulation Requirement greater than 100 MW, Basslink unable to transfer FCAS
F_NVS+RREG_0130 | 2008-07-01 | 1 | NSW, Vic and SA Raise Regulation Requirement greater than 130 MW, Basslink unable to transfer FCAS
F_NVS+RREG_0200 | 2008-07-01 | 1 | NSW, Vic and SA Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS
F_NVS+RREG_0250 | 2008-07-01 | 1 | NSW, Vic and SA Raise Regulation Requirement greater than 250 MW, Basslink unable to transfer FCAS
F_NVS+TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 500, Basslink unable to transfer FCAS
F_NVS+TG_R5_0700 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 700, Basslink unable to transfer FCAS
F_NVS+TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 1000, Basslink unable to transfer FCAS
F_NVS+TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 1400, Basslink unable to transfer FCAS
F_NVS+TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 1600, Basslink unable to transfer FCAS
F_NVS+TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 2000, Basslink unable to transfer FCAS
F_NVS+TG_R5_2800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a NSW, Vic and SA Network Event, TG = 2800, Basslink unable to transfer FCAS
F_NVS+TG_R60_0500 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 500, Basslink unable to transfer FCAS
F_NVS+TG_R60_0700 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 700, Basslink unable to transfer FCAS
F_NVS+TG_R60_1000 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 1000, Basslink unable to transfer FCAS
F_NVS+TG_R60_1400 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 1400, Basslink unable to transfer FCAS
F_NVS+TG_R60_1600 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 1600, Basslink unable to transfer FCAS
F_NVS+TG_R60_2000 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 2000, Basslink unable to transfer FCAS
F_NVS+TG_R60_2800 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 2800, Basslink unable to transfer FCAS
F_NVS+TG_R6_0500 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 500, Basslink unable to transfer FCAS
F_NVS+TG_R6_0700 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 700, Basslink unable to transfer FCAS
F_NVS+TG_R6_1000 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 1000, Basslink unable to transfer FCAS
F_NVS+TG_R6_1400 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 1400, Basslink unable to transfer FCAS
F_NVS+TG_R6_1600 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 1600, Basslink unable to transfer FCAS
F_NVS+TG_R6_2000 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 2000, Basslink unable to transfer FCAS
F_NVS+TG_R6_2800 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a NSW, Vic and SA Network Event, TG = 2800, Basslink unable to transfer FCAS
F_NVS+TL_L5_0600 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink unable to transfer FCAS
F_NVS+TL_L5_0800 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Qld, NSW and Vic Network Event, TL = 800, Basslink unable to transfer FCAS
F_NVS+TL_L5_1000 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Qld, NSW and Vic Network Event, TL = 1000, Basslink unable to transfer FCAS
F_NVS+TL_L60_0600 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink unable to transfer FCAS
F_NVS+TL_L60_0800 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 800, Basslink unable to transfer FCAS
F_NVS+TL_L60_1000 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 1000, Basslink unable to transfer FCAS
F_NVS+TL_L6_0600 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink unable to transfer FCAS
F_NVS+TL_L6_0800 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 800, Basslink unable to transfer FCAS
F_NVS+TL_L6_1000 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 1000, Basslink unable to transfer FCAS
F_NVS_MI++MG_R5 | 2009-01-01 | 1 | Raise 5 min Service Requirement for NSW, Snowy, Vic and SA plus Millmerran Generation Event, Basslink able to transfer FCAS
F_NVS_MI++MG_R6 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for NSW, Snowy, Vic and SA plus Millmerran Generation Event, Basslink able to transfer FCAS
F_NVS_MI++MG_R60 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for NSW, Snowy, Vic and SA plus Millmerran Generation Event, Basslink able to transfer FCAS
F_NVS_MI+MG_R5 | 2009-01-01 | 1 | Raise 5 min Service Requirement for NSW, Snowy, Vic and SA plus Millmerran Generation Event, Basslink unable to transfer FCAS
F_NVS_MI+MG_R6 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for NSW, Snowy, Vic and SA plus Millmerran Generation Event, Basslink unable to transfer FCAS
F_NVS_MI+MG_R60 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for NSW, Snowy, Vic and SA plus Millmerran Generation Event, Basslink unable to transfer FCAS
F_N_BW01_L5 | 2007-03-27 | 1 | Out= NIL, Bayswater 1 L5 Requirement <= 0MW
F_N_BW01_L6 | 2007-03-27 | 1 | Out= NIL, Bayswater 1 L6 Requirement <= 0MW
F_N_BW01_L60 | 2007-03-27 | 1 | Out= NIL, Bayswater 1 L60 Requirement <= 0MW
F_N_BW01_LREG | 2007-03-27 | 1 | Out= NIL, Bayswater 1 LREG Requirement <= 0MW
F_N_BW01_R5 | 2007-03-27 | 1 | Out= NIL, Bayswater 1 R5 Requirement <= 0MW
F_N_BW01_R6 | 2007-03-27 | 1 | Out= NIL, Bayswater 1 R6 Requirement <= 0MW
F_N_BW01_R60 | 2007-03-27 | 1 | Out= NIL, Bayswater 1 R60 Requirement <= 0MW
F_N_BW01_RREG | 2007-03-27 | 1 | Out= NIL, Bayswater 1 RREG Requirement <= 0MW
F_N_BW02_L5 | 2007-03-27 | 1 | Out= NIL, Bayswater 2 L5 Requirement <= 0MW
F_N_BW02_L6 | 2007-03-27 | 1 | Out= NIL, Bayswater 2 L6 Requirement <= 0MW
F_N_BW02_L60 | 2007-03-27 | 1 | Out= NIL, Bayswater 2 L60 Requirement <= 0MW
F_N_BW02_LREG | 2007-03-27 | 1 | Out= NIL, Bayswater 2 LREG Requirement <= 0MW
F_N_BW02_R5 | 2007-03-27 | 1 | Out= NIL, Bayswater 2 R5 Requirement <= 0MW
F_N_BW02_R6 | 2007-03-27 | 1 | Out= NIL, Bayswater 2 R6 Requirement <= 0MW
F_N_BW02_R60 | 2007-03-27 | 1 | Out= NIL, Bayswater 2 R60 Requirement <= 0MW
F_N_BW02_RREG | 2007-03-27 | 1 | Out= NIL, Bayswater 2 RREG Requirement <= 0MW
F_N_BW03_L5 | 2007-03-27 | 1 | Out= NIL, Bayswater 3 L5 Requirement <= 0MW
F_N_BW03_L6 | 2007-03-27 | 1 | Out= NIL, Bayswater 3 L6 Requirement <= 0MW
F_N_BW03_L60 | 2007-03-27 | 1 | Out= NIL, Bayswater 3 L60 Requirement <= 0MW
F_N_BW03_LREG | 2007-03-27 | 1 | Out= NIL, Bayswater 3 LREG Requirement <= 0MW
F_N_BW03_R5 | 2007-03-27 | 1 | Out= NIL, Bayswater 3 R5 Requirement <= 0MW
F_N_BW03_R6 | 2007-03-27 | 1 | Out= NIL, Bayswater 3 R6 Requirement <= 0MW
F_N_BW03_R60 | 2007-03-27 | 1 | Out= NIL, Bayswater 3 R60 Requirement <= 0MW
F_N_BW03_RREG | 2007-03-27 | 1 | Out= NIL, Bayswater 3 RREG Requirement <= 0MW
F_N_BW04_L5 | 2007-03-27 | 1 | Out= NIL, Bayswater 4 L5 Requirement <= 0MW
F_N_BW04_L6 | 2007-03-27 | 1 | Out= NIL, Bayswater 4 L6 Requirement <= 0MW
F_N_BW04_L60 | 2007-03-27 | 1 | Out= NIL, Bayswater 4 L60 Requirement <= 0MW
F_N_BW04_LREG | 2007-03-27 | 1 | Out= NIL, Bayswater 4 LREG Requirement <= 0MW
F_N_BW04_R5 | 2007-03-27 | 1 | Out= NIL, Bayswater 4 R5 Requirement <= 0MW
F_N_BW04_R6 | 2007-03-27 | 1 | Out= NIL, Bayswater 4 R6 Requirement <= 0MW
F_N_BW04_R60 | 2007-03-27 | 1 | Out= NIL, Bayswater 4 R60 Requirement <= 0MW
F_N_BW04_RREG | 2007-03-27 | 1 | Out= NIL, Bayswater 4 RREG Requirement <= 0MW
F_N_ER01_L5 | 2007-03-27 | 1 | Out= NIL, Eraring 1 L5 Requirement <= 0MW
F_N_ER01_L6 | 2007-03-27 | 1 | Out= NIL, Eraring 1 L6 Requirement <= 0MW
F_N_ER01_L60 | 2007-03-27 | 1 | Out= NIL, Eraring 1 L60 Requirement <= 0MW
F_N_ER01_LREG | 2007-03-27 | 1 | Out= NIL, Eraring 1 LREG Requirement <= 0MW
F_N_ER01_R5 | 2007-03-27 | 1 | Out= NIL, Eraring 1 R5 Requirement <= 0MW
F_N_ER01_R6 | 2007-03-27 | 1 | Out= NIL, Eraring 1 R6 Requirement <= 0MW
F_N_ER01_R60 | 2007-03-27 | 1 | Out= NIL, Eraring 1 R60 Requirement <= 0MW
F_N_ER01_RREG | 2007-03-27 | 1 | Out= NIL, Eraring 1 RREG Requirement <= 0MW
F_N_ER02_L5 | 2007-03-27 | 1 | Out= NIL, Eraring 2 L5 Requirement <= 0MW
F_N_ER02_L6 | 2007-03-27 | 1 | Out= NIL, Eraring 2 L6 Requirement <= 0MW
F_N_ER02_L60 | 2007-03-27 | 1 | Out= NIL, Eraring 2 L60 Requirement <= 0MW
F_N_ER02_LREG | 2007-03-27 | 1 | Out= NIL, Eraring 2 LREG Requirement <= 0MW
F_N_ER02_R5 | 2007-03-27 | 1 | Out= NIL, Eraring 2 R5 Requirement <= 0MW
F_N_ER02_R6 | 2007-03-27 | 1 | Out= NIL, Eraring 2 R6 Requirement <= 0MW
F_N_ER02_R60 | 2007-03-27 | 1 | Out= NIL, Eraring 2 R60 Requirement <= 0MW
F_N_ER02_RREG | 2007-03-27 | 1 | Out= NIL, Eraring 2 RREG Requirement <= 0MW
F_N_ER03_L5 | 2007-03-27 | 1 | Out= NIL, Eraring 3 L5 Requirement <= 0MW
F_N_ER03_L6 | 2007-03-27 | 1 | Out= NIL, Eraring 3 L6 Requirement <= 0MW
F_N_ER03_L60 | 2007-03-27 | 1 | Out= NIL, Eraring 3 L60 Requirement <= 0MW
F_N_ER03_LREG | 2007-03-27 | 1 | Out= NIL, Eraring 3 LREG Requirement <= 0MW
F_N_ER03_R5 | 2007-03-27 | 1 | Out= NIL, Eraring 3 R5 Requirement <= 0MW
F_N_ER03_R6 | 2007-03-27 | 1 | Out= NIL, Eraring 3 R6 Requirement <= 0MW
F_N_ER03_R60 | 2007-03-27 | 1 | Out= NIL, Eraring 3 R60 Requirement <= 0MW
F_N_ER03_RREG | 2007-03-27 | 1 | Out= NIL, Eraring 3 RREG Requirement <= 0MW
F_N_ER04_L5 | 2007-03-27 | 1 | Out= NIL, Eraring 4 L5 Requirement <= 0MW
F_N_ER04_L6 | 2007-03-27 | 1 | Out= NIL, Eraring 4 L6 Requirement <= 0MW
F_N_ER04_L60 | 2007-03-27 | 1 | Out= NIL, Eraring 4 L60 Requirement <= 0MW
F_N_ER04_LREG | 2007-03-27 | 1 | Out= NIL, Eraring 4 LREG Requirement <= 0MW
F_N_ER04_R5 | 2007-03-27 | 1 | Out= NIL, Eraring 4 R5 Requirement <= 0MW
F_N_ER04_R6 | 2007-03-27 | 1 | Out= NIL, Eraring 4 R6 Requirement <= 0MW
F_N_ER04_R60 | 2007-03-27 | 1 | Out= NIL, Eraring 4 R60 Requirement <= 0MW
F_N_ER04_RREG | 2007-03-27 | 1 | Out= NIL, Eraring 4 RREG Requirement <= 0MW
F_N_GUTHEGA_L5 | 2008-07-01 | 1 | Out= NIL, Guthega L5 Requirement <= 0MW
F_N_GUTHEGA_L60 | 2008-07-01 | 1 | Out= NIL, Guthega L60 Requirement <= 0MW
F_N_GUTHEGA_LREG | 2008-07-01 | 1 | Out= NIL, Guthega LREG Requirement <= 0MW
F_N_GUTHEGA_R5 | 2008-07-01 | 1 | Out= NIL, Guthega R5 Requirement <= 0MW
F_N_GUTHEGA_R60 | 2008-07-01 | 1 | Out= NIL, Guthega R60 Requirement <= 0MW
F_N_GUTHEGA_RREG | 2008-07-01 | 1 | Out= NIL, Guthega RREG Requirement <= 0MW
F_N_LD01_L5 | 2007-03-27 | 1 | Out= NIL, Liddell 1 L5 Requirement <= 0MW
F_N_LD01_L6 | 2007-03-27 | 1 | Out= NIL, Liddell 1 L6 Requirement <= 0MW
F_N_LD01_L60 | 2007-03-27 | 1 | Out= NIL, Liddell 1 L60 Requirement <= 0MW
F_N_LD01_LREG | 2007-03-27 | 1 | Out= NIL, Liddell 1 LREG Requirement <= 0MW
F_N_LD01_R5 | 2007-03-27 | 1 | Out= NIL, Liddell 1 R5 Requirement <= 0MW
F_N_LD01_R6 | 2007-03-27 | 1 | Out= NIL, Liddell 1 R6 Requirement <= 0MW
F_N_LD01_R60 | 2007-03-27 | 1 | Out= NIL, Liddell 1 R60 Requirement <= 0MW
F_N_LD01_RREG | 2007-03-27 | 1 | Out= NIL, Liddell 1 RREG Requirement <= 0MW
F_N_LD02_L5 | 2007-03-27 | 1 | Out= NIL, Liddell 2 L5 Requirement <= 0MW
F_N_LD02_L6 | 2007-03-27 | 1 | Out= NIL, Liddell 2 L6 Requirement <= 0MW
F_N_LD02_L60 | 2007-03-27 | 1 | Out= NIL, Liddell 2 L60 Requirement <= 0MW
F_N_LD02_LREG | 2007-03-27 | 1 | Out= NIL, Liddell 2 LREG Requirement <= 0MW
F_N_LD02_R5 | 2007-03-27 | 1 | Out= NIL, Liddell 2 R5 Requirement <= 0MW
F_N_LD02_R6 | 2007-03-27 | 1 | Out= NIL, Liddell 2 R6 Requirement <= 0MW
F_N_LD02_R60 | 2007-03-27 | 1 | Out= NIL, Liddell 2 R60 Requirement <= 0MW
F_N_LD02_RREG | 2007-03-27 | 1 | Out= NIL, Liddell 2 RREG Requirement <= 0MW
F_N_LD03_L5 | 2007-03-27 | 1 | Out= NIL, Liddell 3 L5 Requirement <= 0MW
F_N_LD03_L6 | 2007-03-27 | 1 | Out= NIL, Liddell 3 L6 Requirement <= 0MW
F_N_LD03_L60 | 2007-03-27 | 1 | Out= NIL, Liddell 3 L60 Requirement <= 0MW
F_N_LD03_LREG | 2007-03-27 | 1 | Out= NIL, Liddell 3 LREG Requirement <= 0MW
F_N_LD03_R5 | 2007-03-27 | 1 | Out= NIL, Liddell 3 R5 Requirement <= 0MW
F_N_LD03_R6 | 2007-03-27 | 1 | Out= NIL, Liddell 3 R6 Requirement <= 0MW
F_N_LD03_R60 | 2007-03-27 | 1 | Out= NIL, Liddell 3 R60 Requirement <= 0MW
F_N_LD03_RREG | 2007-03-27 | 1 | Out= NIL, Liddell 3 RREG Requirement <= 0MW
F_N_LD04_L5 | 2007-03-27 | 1 | Out= NIL, Liddell 4 L5 Requirement <= 0MW
F_N_LD04_L6 | 2007-03-27 | 1 | Out= NIL, Liddell 4 L6 Requirement <= 0MW
F_N_LD04_L60 | 2007-03-27 | 1 | Out= NIL, Liddell 4 L60 Requirement <= 0MW
F_N_LD04_LREG | 2007-03-27 | 1 | Out= NIL, Liddell 4 LREG Requirement <= 0MW
F_N_LD04_R5 | 2007-03-27 | 1 | Out= NIL, Liddell 4 R5 Requirement <= 0MW
F_N_LD04_R6 | 2007-03-27 | 1 | Out= NIL, Liddell 4 R6 Requirement <= 0MW
F_N_LD04_R60 | 2007-03-27 | 1 | Out= NIL, Liddell 4 R60 Requirement <= 0MW
F_N_LD04_RREG | 2007-03-27 | 1 | Out= NIL, Liddell 4 RREG Requirement <= 0MW
F_N_MM3_L5 | 2007-03-27 | 1 | Out= NIL, Munmorah 3 L5 Requirement <= 0MW
F_N_MM3_L6 | 2007-03-27 | 1 | Out= NIL, Munmorah 3 L6 Requirement <= 0MW
F_N_MM3_L60 | 2007-03-27 | 1 | Out= NIL, Munmorah 3 L60 Requirement <= 0MW
F_N_MM3_LREG | 2007-03-27 | 1 | Out= NIL, Munmorah 3 LREG Requirement <= 0MW
F_N_MM3_R5 | 2007-03-27 | 1 | Out= NIL, Munmorah 3 R5 Requirement <= 0MW
F_N_MM3_R6 | 2007-03-27 | 1 | Out= NIL, Munmorah 3 R6 Requirement <= 0MW
F_N_MM3_R60 | 2007-03-27 | 1 | Out= NIL, Munmorah 3 R60 Requirement <= 0MW
F_N_MM3_RREG | 2007-03-27 | 1 | Out= NIL, Munmorah 3 RREG Requirement <= 0MW
F_N_MM4_L5 | 2007-03-27 | 1 | Out= NIL, Munmorah 4 L5 Requirement <= 0MW
F_N_MM4_L6 | 2007-03-27 | 1 | Out= NIL, Munmorah 4 L6 Requirement <= 0MW
F_N_MM4_L60 | 2007-03-27 | 1 | Out= NIL, Munmorah 4 L60 Requirement <= 0MW
F_N_MM4_LREG | 2007-03-27 | 1 | Out= NIL, Munmorah 4 LREG Requirement <= 0MW
F_N_MM4_R5 | 2007-03-27 | 1 | Out= NIL, Munmorah 4 R5 Requirement <= 0MW
F_N_MM4_R6 | 2007-03-27 | 1 | Out= NIL, Munmorah 4 R6 Requirement <= 0MW
F_N_MM4_R60 | 2007-03-27 | 1 | Out= NIL, Munmorah 4 R60 Requirement <= 0MW
F_N_MM4_RREG | 2007-03-27 | 1 | Out= NIL, Munmorah 4 RREG Requirement <= 0MW
F_N_MP1_L5 | 2007-03-27 | 1 | Out= NIL, MT Piper 1 L5 Requirement <= 0MW
F_N_MP1_L6 | 2007-03-27 | 1 | Out= NIL, MT Piper 1 L6 Requirement <= 0MW
F_N_MP1_L60 | 2007-03-27 | 1 | Out= NIL, MT Piper 1 L60 Requirement <= 0MW
F_N_MP1_LREG | 2007-03-27 | 1 | Out= NIL, MT Piper 1 LREG Requirement <= 0MW
F_N_MP1_R5 | 2007-03-27 | 1 | Out= NIL, MT Piper 1 R5 Requirement <= 0MW
F_N_MP1_R6 | 2007-03-27 | 1 | Out= NIL, MT Piper 1 R6 Requirement <= 0MW
F_N_MP1_R60 | 2007-03-27 | 1 | Out= NIL, MT Piper 1 R60 Requirement <= 0MW
F_N_MP1_RREG | 2007-03-27 | 1 | Out= NIL, MT Piper 1 RREG Requirement <= 0MW
F_N_MP2_L5 | 2007-03-27 | 1 | Out= NIL, MT Piper 2 L5 Requirement <= 0MW
F_N_MP2_L6 | 2007-03-27 | 1 | Out= NIL, MT Piper 2 L6 Requirement <= 0MW
F_N_MP2_L60 | 2007-03-27 | 1 | Out= NIL, MT Piper 2 L60 Requirement <= 0MW
F_N_MP2_LREG | 2007-03-27 | 1 | Out= NIL, MT Piper 2 LREG Requirement <= 0MW
F_N_MP2_R5 | 2007-03-27 | 1 | Out= NIL, MT Piper 2 R5 Requirement <= 0MW
F_N_MP2_R6 | 2007-03-27 | 1 | Out= NIL, MT Piper 2 R6 Requirement <= 0MW
F_N_MP2_R60 | 2007-03-27 | 1 | Out= NIL, MT Piper 2 R60 Requirement <= 0MW
F_N_MP2_RREG | 2007-03-27 | 1 | Out= NIL, MT Piper 2 RREG Requirement <= 0MW
F_N_SNOWYP_L5 | 2008-07-01 | 1 | Out= NIL, Snowy (T3) Pump L5 Requirement <= 0MW
F_N_SNOWYP_R5 | 2008-07-01 | 1 | Out= NIL, Snowy (T3) Pump R5 Requirement <= 0MW
F_N_SNOWYP_R6 | 2008-07-01 | 1 | Out= NIL, Snowy (T3) Pump R6 Requirement <= 0MW
F_N_SNOWYP_R60 | 2008-07-01 | 1 | Out= NIL, Snowy (T3) Pump R60 Requirement <= 0MW
F_N_TUMUT3-1_R5 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3-1) R5 Requirement <= 0MW
F_N_TUMUT3-1_R60 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3-1) R60 Requirement <= 0MW
F_N_TUMUT3-2_R5 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3-2) R5 Requirement <= 0MW
F_N_TUMUT3-2_R60 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3-2) R60 Requirement <= 0MW
F_N_TUMUT3-3_R5 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3-3) R5 Requirement <= 0MW
F_N_TUMUT3-3_R60 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3-3) R60 Requirement <= 0MW
F_N_TUMUT3-4_R5 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3-4) R5 Requirement <= 0MW
F_N_TUMUT3-4_R60 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3-4) R60 Requirement <= 0MW
F_N_TUMUT3-5_R5 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3-5) R5 Requirement <= 0MW
F_N_TUMUT3-5_R60 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3-5) R60 Requirement <= 0MW
F_N_TUMUT3-6_R5 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3-6) R5 Requirement <= 0MW
F_N_TUMUT3-6_R60 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3-6) R60 Requirement <= 0MW
F_N_TUMUT3_L5 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3) L5 Requirement <= 0MW
F_N_TUMUT3_L6 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3) L6 Requirement <= 0MW
F_N_TUMUT3_L60 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3) L60 Requirement <= 0MW
F_N_TUMUT3_LREG | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3) LREG Requirement <= 0MW
F_N_TUMUT3_R5 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3) R5 Requirement <= 0MW
F_N_TUMUT3_R6 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3) R6 Requirement <= 0MW
F_N_TUMUT3_R60 | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3) R60 Requirement <= 0MW
F_N_TUMUT3_RREG | 2008-07-01 | 1 | Out= NIL, Lower Tumut (T3) RREG Requirement <= 0MW
F_N_UPPTUMUT_L5 | 2008-07-01 | 1 | Out= NIL, Upper Tumut L5 Requirement <= 0MW
F_N_UPPTUMUT_L6 | 2008-07-01 | 1 | Out= NIL, Upper Tumut L6 Requirement <= 0MW
F_N_UPPTUMUT_L60 | 2008-07-01 | 1 | Out= NIL, Upper Tumut L60 Requirement <= 0MW
F_N_UPPTUMUT_LREG | 2008-07-01 | 1 | Out= NIL, Upper Tumut LREG Requirement <= 0MW
F_N_UPPTUMUT_R5 | 2008-07-01 | 1 | Out= NIL, Upper Tumut R5 Requirement <= 0MW
F_N_UPPTUMUT_R6 | 2008-07-01 | 1 | Out= NIL, Upper Tumut R6 Requirement <= 0MW
F_N_UPPTUMUT_R60 | 2008-07-01 | 1 | Out= NIL, Upper Tumut R60 Requirement <= 0MW
F_N_UPPTUMUT_RREG | 2008-07-01 | 1 | Out= NIL, Upper Tumut RREG Requirement <= 0MW
F_N_VP5_L5 | 2007-03-27 | 1 | Out= NIL, Vales Point 5 L5 Requirement <= 0MW
F_N_VP5_L6 | 2007-03-27 | 1 | Out= NIL, Vales Point 5 L6 Requirement <= 0MW
F_N_VP5_L60 | 2007-03-27 | 1 | Out= NIL, Vales Point 5 L60 Requirement <= 0MW
F_N_VP5_LREG | 2007-03-27 | 1 | Out= NIL, Vales Point 5 LREG Requirement <= 0MW
F_N_VP5_R5 | 2007-03-27 | 1 | Out= NIL, Vales Point 5 R5 Requirement <= 0MW
F_N_VP5_R6 | 2007-03-27 | 1 | Out= NIL, Vales Point 5 R6 Requirement <= 0MW
F_N_VP5_R60 | 2007-03-27 | 1 | Out= NIL, Vales Point 5 R60 Requirement <= 0MW
F_N_VP5_RREG | 2007-03-27 | 1 | Out= NIL, Vales Point 5 RREG Requirement <= 0MW
F_N_VP6_L5 | 2007-03-27 | 1 | Out= NIL, Vales Point 6 L5 Requirement <= 0MW
F_N_VP6_L6 | 2007-03-27 | 1 | Out= NIL, Vales Point 6 L6 Requirement <= 0MW
F_N_VP6_L60 | 2007-03-27 | 1 | Out= NIL, Vales Point 6 L60 Requirement <= 0MW
F_N_VP6_LREG | 2007-03-27 | 1 | Out= NIL, Vales Point 6 LREG Requirement <= 0MW
F_N_VP6_R5 | 2007-03-27 | 1 | Out= NIL, Vales Point 6 R5 Requirement <= 0MW
F_N_VP6_R6 | 2007-03-27 | 1 | Out= NIL, Vales Point 6 R6 Requirement <= 0MW
F_N_VP6_R60 | 2007-03-27 | 1 | Out= NIL, Vales Point 6 R60 Requirement <= 0MW
F_N_VP6_RREG | 2007-03-27 | 1 | Out= NIL, Vales Point 6 RREG Requirement <= 0MW
F_N_WW7_L5 | 2007-03-27 | 1 | Out= NIL, Wallerawang 7 L5 Requirement <= 0MW
F_N_WW7_L6 | 2007-03-27 | 1 | Out= NIL, Wallerawang 7 L6 Requirement <= 0MW
F_N_WW7_L60 | 2007-03-27 | 1 | Out= NIL, Wallerawang 7 L60 Requirement <= 0MW
F_N_WW7_LREG | 2007-03-27 | 1 | Out= NIL, Wallerawang 7 LREG Requirement <= 0MW
F_N_WW7_R5 | 2007-03-27 | 1 | Out= NIL, Wallerawang 7 R5 Requirement <= 0MW
F_N_WW7_R6 | 2007-03-27 | 1 | Out= NIL, Wallerawang 7 R6 Requirement <= 0MW
F_N_WW7_R60 | 2007-03-27 | 1 | Out= NIL, Wallerawang 7 R60 Requirement <= 0MW
F_N_WW7_RREG | 2007-03-27 | 1 | Out= NIL, Wallerawang 7 RREG Requirement <= 0MW
F_N_WW8_L5 | 2007-03-27 | 1 | Out= NIL, Wallerawang 8 L5 Requirement <= 0MW
F_N_WW8_L6 | 2007-03-27 | 1 | Out= NIL, Wallerawang 8 L6 Requirement <= 0MW
F_N_WW8_L60 | 2007-03-27 | 1 | Out= NIL, Wallerawang 8 L60 Requirement <= 0MW
F_N_WW8_LREG | 2007-03-27 | 1 | Out= NIL, Wallerawang 8 LREG Requirement <= 0MW
F_N_WW8_R5 | 2007-03-27 | 1 | Out= NIL, Wallerawang 8 R5 Requirement <= 0MW
F_N_WW8_R6 | 2007-03-27 | 1 | Out= NIL, Wallerawang 8 R6 Requirement <= 0MW
F_N_WW8_R60 | 2007-03-27 | 1 | Out= NIL, Wallerawang 8 R60 Requirement <= 0MW
F_N_WW8_RREG | 2007-03-27 | 1 | Out= NIL, Wallerawang 8 RREG Requirement <= 0MW
F_Q++ARDM_L5 | 2009-01-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Lower 5 min Requirement
F_Q++ARDM_L6 | 2006-01-03 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Lower 6 sec Requirement
F_Q++ARDM_L60 | 2006-01-03 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Lower 60 sec Requirement
F_Q++ARDM_R5 | 2009-01-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Raise 5 min Requirement
F_Q++ARDM_R6 | 2006-01-03 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Raise 6 sec Requirement
F_Q++ARDM_R60 | 2006-01-03 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Raise 60 sec Requirement
F_Q++ARTW_L5 | 2009-01-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement
F_Q++ARTW_L6 | 2007-04-18 | 1 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement
F_Q++ARTW_L60 | 2007-04-18 | 1 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement
F_Q++ARTW_R5 | 2009-01-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement
F_Q++ARTW_R6 | 2007-04-18 | 1 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement
F_Q++ARTW_R60 | 2007-04-18 | 1 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement
F_Q++LDMU_L5 | 2009-01-01 | 1 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement
F_Q++LDMU_L6 | 2007-04-18 | 1 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement
F_Q++LDMU_L60 | 2007-04-18 | 1 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement
F_Q++LDMU_R5 | 2009-01-01 | 1 | Out = Liddell to Muswellbrook (83) line, Qld Raise 5 min Requirement
F_Q++LDMU_R6 | 2007-04-18 | 1 | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement
F_Q++LDMU_R60 | 2007-04-18 | 1 | Out = Liddell to Muswellbrook (83) line, Qld Raise 60 sec Requirement
F_Q++LDTW_L5 | 2009-01-01 | 1 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement
F_Q++LDTW_L6 | 2007-04-18 | 1 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement
F_Q++LDTW_L60 | 2007-04-18 | 1 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement
F_Q++LDTW_R5 | 2009-01-01 | 1 | Out = Liddell to Tamworth (84) line, Qld Raise 5 min Requirement
F_Q++LDTW_R6 | 2007-04-18 | 1 | Out = Liddell to Tamworth (84) line, Qld Raise 6 sec Requirement
F_Q++LDTW_R60 | 2007-04-18 | 1 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement
F_Q++MUTW_L5 | 2009-01-01 | 1 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement
F_Q++MUTW_L6 | 2007-04-18 | 1 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement
F_Q++MUTW_L60 | 2007-04-18 | 1 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement
F_Q++MUTW_R5 | 2009-01-01 | 1 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement
F_Q++MUTW_R6 | 2007-04-18 | 1 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement
F_Q++MUTW_R60 | 2007-04-18 | 1 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement
F_Q++NIL_R5 | 2009-01-01 | 1 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 660MW unit
F_Q++NIL_R6 | 2005-08-15 | 2 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 6 sec requirement for loss of a NSW 660MW unit
F_Q++NIL_R60 | 2005-08-15 | 1 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 60 sec requirement for loss of a NSW 660MW unit
F_Q+LREG_0050 | 2005-12-15 | 1 | Qld Lower Regulation Requirement greater than 50 MW
F_Q+LREG_0100 | 2005-12-15 | 1 | Qld Lower Regulation Requirement greater than 100 MW
F_Q+LREG_0110 | 2005-12-15 | 1 | Qld Lower Regulation Requirement greater than 110 MW
F_Q+LREG_0150 | 2005-12-15 | 1 | Qld Lower Regulation Requirement greater than 150 MW
F_Q+LREG_0200 | 2005-12-15 | 1 | Qld Lower Regulation Requirement greater than 200 MW
F_Q+MG_R5 | 2009-01-01 | 1 | Raise 5 min Service Requirement for Qld Generation Event
F_Q+MG_R6 | 2005-12-21 | 1 | Raise 6 sec Service Requirement for Qld Generation Event
F_Q+MG_R60 | 2005-12-21 | 1 | Raise 60 sec Service Requirement for Qld Generation Event
F_Q+ML_L5_0370 | 2009-01-01 | 1 | Lower 5 min Service Requirement for Qld Load Event, ML = 370
F_Q+ML_L5_0400 | 2009-01-01 | 1 | Lower 5 min Service Requirement for Qld Load Event, ML = 390
F_Q+ML_L60_0370 | 2005-12-15 | 1 | Lower 60 sec Service Requirement for Qld Load Event, ML = 370
F_Q+ML_L60_0400 | 2005-12-15 | 1 | Lower 60 sec Service Requirement for Qld Load Event, ML = 390
F_Q+ML_L6_0370 | 2005-12-15 | 1 | Lower 6 sec Service Requirement for Qld Load Event, ML = 370
F_Q+ML_L6_0400 | 2005-12-15 | 1 | Lower 6 sec Service Requirement for Qld Load Event, ML = 390
F_Q+RREG_0050 | 2005-12-15 | 1 | Qld Raise Regulation Requirement greater than 50 MW
F_Q+RREG_0100 | 2005-12-15 | 1 | Qld Raise Regulation Requirement greater than 100 MW
F_Q+RREG_0110 | 2005-12-15 | 1 | Qld Raise Regulation Requirement greater than 110 MW
F_Q+RREG_0150 | 2005-12-15 | 1 | Qld Raise Regulation Requirement greater than 150 MW
F_Q+RREG_0200 | 2005-12-15 | 1 | Qld Raise Regulation Requirement greater than 200 MW
F_Q+SB_TX_R5 | 2006-03-14 | 1 | Out= one Swanbank B station auxiliary transformer, Swanbank B Raise 5 min requirement = 0
F_Q+SB_TX_R6 | 2006-03-14 | 1 | Out= one Swanbank B station auxiliary transformer, Swanbank B Raise 6 sec requirement = 0
F_Q+SB_TX_R60 | 2006-03-14 | 1 | Out= one Swanbank B station auxiliary transformer, Swanbank B Raise 60 sec requirement = 0
F_Q+SB_TX_RREG | 2006-03-14 | 1 | Out= one Swanbank B station auxiliary transformer, Swanbank B Raise Regulation min requirement = 0
F_Q+ST_N-2_R6 | 2007-06-28 | 1 | Out= Nil, loss of all Stanwell units declared credible, Stanwell Raise 6 sec requirement = 0
F_Q+ST_N-2_R60 | 2007-06-28 | 1 | Out= Nil, loss of all Stanwell units declared credible, Stanwell Raise 60 sec requirement = 0
F_Q+ST_N-2_RREG | 2007-06-28 | 1 | Out= Nil, loss of all Stanwell units declared credible, Stanwell Raise Regulation requirement = 0
F_Q+TG_R5_0850 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld Network Event, TG = 850
F_Q+TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld Network Event, TG = 1400
F_Q+TG_R60_0850 | 2005-09-12 | 1 | Raise 60 sec Service Requirement for a Qld Network Event, TG = 850
F_Q+TG_R60_1400 | 2003-08-01 | 1 | Raise 60 sec Service Requirement for a Qld Network Event, TG = 1400
F_Q+TG_R6_0850 | 2005-09-12 | 1 | Raise 6 sec Service Requirement for a Qld Network Event, TG = 850
F_Q+TG_R6_1400 | 2003-08-01 | 1 | Raise 6 sec Service Requirement for a Qld Network Event, TG = 1400
F_Q+TL_L5_0900 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a QLD Network Event, TL = 900
F_Q+TL_L60_0900 | 2003-08-01 | 1 | Lower 60 sec Service Requirement for a QLD Network Event, TL = 900
F_Q+TL_L6_0900 | 2003-08-01 | 1 | Lower 6 sec Service Requirement for a QLD Network Event, TL = 900
F_QLD+RB_ISLE_L5 | 2006-01-06 | 1 | Qld / Southern separation between Liddell and Muswellbrook (84 and 83), Redbank Lower 5 min Requirement = 0
F_QLD+RB_ISLE_L6 | 2006-01-06 | 1 | Qld / Southern separation between Liddell and Muswellbrook (84 and 83), Redbank Lower 6 sec Requirement = 0
F_QLD+RB_ISLE_L60 | 2006-01-06 | 1 | Qld / Southern separation between Liddell and Muswellbrook (84 and 83), Redbank Lower 60 sec Requirement = 0
F_QLD+RB_ISLE_LREG | 2006-01-06 | 1 | Qld / Southern separation between Liddell and Muswellbrook (84 and 83), Redbank Lower Regulation Requirement = 0
F_QLD+RB_ISLE_R5 | 2006-01-06 | 1 | Qld / Southern separation between Liddell and Muswellbrook (84 and 83), Redbank Raise 5 min Requirement = 0
F_QLD+RB_ISLE_R6 | 2006-01-06 | 1 | Qld / Southern separation between Liddell and Muswellbrook (84 and 83), Redbank Raise 6 sec Requirement = 0
F_QLD+RB_ISLE_R60 | 2006-01-06 | 1 | Qld / Southern separation between Liddell and Muswellbrook (84 and 83), Redbank Raise 60 sec Requirement = 0
F_QLD+RB_ISLE_RREG | 2006-01-06 | 1 | Qld / Southern separation between Liddell and Muswellbrook (84 and 83), Redbank Raise Regulation Requirement = 0
F_QNV++HYML_L5 | 2009-01-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Qld, NSW, Snowy and Vic Lower 5 min Requirement, Basslink able to transfer FCAS
F_QNV++HYML_L6 | 2008-07-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Qld, NSW, Snowy and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS
F_QNV++HYML_L60 | 2008-07-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Qld, NSW, Snowy and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS
F_QNV++HYML_R5 | 2009-01-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Qld, NSW, Snowy and Vic Raise 5 min Requirement, Basslink able to transfer FCAS
F_QNV++HYML_R6 | 2008-07-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Qld, NSW, Snowy and Vic Raise 6 sec Requirement, Basslink able to transfer FCAS
F_QNV++HYML_R60 | 2008-07-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Qld, NSW, Snowy and Vic Raise 60 sec Requirement, Basslink able to transfer FCAS
F_QNV++HYSE_L5 | 2009-01-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Qld, NSW, Snowy and Vic Lower 5 min Requirement, Basslink able to transfer FCAS
F_QNV++HYSE_L6 | 2008-07-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Qld, NSW, Snowy and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS
F_QNV++HYSE_L60 | 2008-07-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Qld, NSW, Snowy and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS
F_QNV++HYSE_R5 | 2009-01-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Qld, NSW, Snowy and Vic Raise 5 min Requirement, Basslink able to transfer FCAS
F_QNV++HYSE_R6 | 2008-07-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Qld, NSW, Snowy and Vic Raise 6 sec Requirement, Basslink able to transfer FCAS
F_QNV++HYSE_R60 | 2008-07-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Qld, NSW, Snowy and Vic Raise 60 sec Requirement, Basslink able to transfer FCAS
F_QNV++LREG_0100 | 2008-07-01 | 1 | Qld, NSW and Vic Lower Regulation Requirement greater than 100 MW, Basslink able transfer FCAS
F_QNV++LREG_0120 | 2008-07-01 | 1 | Qld, NSW and Vic Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS
F_QNV++LREG_0200 | 2008-07-01 | 1 | Qld, NSW and Vic Lower Regulation Requirement greater than 200 MW, Basslink able transfer FCAS
F_QNV++LREG_0250 | 2008-07-01 | 1 | Qld, NSW and Vic Lower Regulation Requirement greater than 250 MW, Basslink able transfer FCAS
F_QNV++ML_L5_0370 | 2009-01-01 | 1 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 370, Basslink able transfer FCAS
F_QNV++ML_L5_0400 | 2009-01-01 | 1 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS
F_QNV++ML_L60_0370 | 2008-07-01 | 1 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 370, Basslink able transfer FCAS
F_QNV++ML_L60_0400 | 2008-07-01 | 1 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS
F_QNV++ML_L6_0370 | 2008-07-01 | 1 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 370, Basslink able transfer FCAS
F_QNV++ML_L6_0400 | 2008-07-01 | 1 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink able transfer FCAS
F_QNV++RREG_0100 | 2008-07-01 | 1 | Qld, NSW and Vic Raise Regulation Requirement greater than 100 MW, Basslink able transfer FCAS
F_QNV++RREG_0130 | 2008-07-01 | 1 | Qld, NSW and Vic Raise Regulation Requirement greater than 130 MW, Basslink able transfer FCAS
F_QNV++RREG_0200 | 2008-07-01 | 1 | Qld, NSW and Vic Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS
F_QNV++RREG_0250 | 2008-07-01 | 1 | Qld, NSW and Vic Raise Regulation Requirement greater than 250 MW, Basslink able transfer FCAS
F_QNV++TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 500, Basslink able to transfer FCAS
F_QNV++TG_R5_0700 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 700, Basslink able to transfer FCAS
F_QNV++TG_R5_0850 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 850, Basslink able to transfer FCAS
F_QNV++TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 1000, Basslink able to transfer FCAS
F_QNV++TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 1400, Basslink able to transfer FCAS
F_QNV++TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 1600, Basslink able to transfer FCAS
F_QNV++TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 2000, Basslink able to transfer FCAS
F_QNV++TG_R5_2800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 2800, Basslink able to transfer FCAS
F_QNV++TG_R60_0500 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 500, Basslink able to transfer FCAS
F_QNV++TG_R60_0700 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 700, Basslink able to transfer FCAS
F_QNV++TG_R60_0850 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 850, Basslink able to transfer FCAS
F_QNV++TG_R60_1000 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 1000, Basslink able to transfer FCAS
F_QNV++TG_R60_1400 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 1400, Basslink able to transfer FCAS
F_QNV++TG_R60_1600 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 1600, Basslink able to transfer FCAS
F_QNV++TG_R60_2000 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 2000, Basslink able to transfer FCAS
F_QNV++TG_R60_2800 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 2800, Basslink able to transfer FCAS
F_QNV++TG_R6_0500 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 500, Basslink able to transfer FCAS
F_QNV++TG_R6_0700 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 700, Basslink able to transfer FCAS
F_QNV++TG_R6_0850 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 850, Basslink able to transfer FCAS
F_QNV++TG_R6_1000 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 1000, Basslink able to transfer FCAS
F_QNV++TG_R6_1400 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 1400, Basslink able to transfer FCAS
F_QNV++TG_R6_1600 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 1600, Basslink able to transfer FCAS
F_QNV++TG_R6_2000 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 2000, Basslink able to transfer FCAS
F_QNV++TG_R6_2800 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 2800, Basslink able to transfer FCAS
F_QNV++TL_L5_0600 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink able to transfer FCAS
F_QNV++TL_L5_0800 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Qld, NSW and Vic Network Event, TL = 800, Basslink able to transfer FCAS
F_QNV++TL_L60_0600 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink able to transfer FCAS
F_QNV++TL_L60_0800 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 800, Basslink able to transfer FCAS
F_QNV++TL_L6_0600 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink able to transfer FCAS
F_QNV++TL_L6_0800 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 800, Basslink able to transfer FCAS
F_QNV+HYML_L5 | 2009-01-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Qld, NSW, Snowy and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS
F_QNV+HYML_L6 | 2008-07-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Qld, NSW, Snowy and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS
F_QNV+HYML_L60 | 2008-07-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Qld, NSW, Snowy and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS
F_QNV+HYML_R5 | 2009-01-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Qld, NSW, Snowy and Vic Raise 5 min Requirement, Basslink unable to transfer FCAS
F_QNV+HYML_R6 | 2008-07-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Qld, NSW, Snowy and Vic Raise 6 sec Requirement, Basslink unable to transfer FCAS
F_QNV+HYML_R60 | 2008-07-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) line or one Moorabool to Sydneham (MLTS-SYTS) line Qld, NSW, Snowy and Vic Raise 60 sec Requirement, Basslink unable to transfer FCAS
F_QNV+HYSE_L5 | 2009-01-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Qld, NSW, Snowy and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS
F_QNV+HYSE_L6 | 2008-07-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Qld, NSW, Snowy and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS
F_QNV+HYSE_L60 | 2008-07-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Qld, NSW, Snowy and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS
F_QNV+HYSE_R5 | 2009-01-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Qld, NSW, Snowy and Vic Raise 5 min Requirement, Basslink unable to transfer FCAS
F_QNV+HYSE_R6 | 2008-07-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Qld, NSW, Snowy and Vic Raise 6 sec Requirement, Basslink unable to transfer FCAS
F_QNV+HYSE_R60 | 2008-07-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, Qld, NSW, Snowy and Vic Raise 60 sec Requirement, Basslink unable to transfer FCAS
F_QNV+LREG_0100 | 2008-07-01 | 1 | Qld, NSW and Vic Lower Regulation Requirement greater than 100 MW, Basslink unable to transfer FCAS
F_QNV+LREG_0120 | 2008-07-01 | 1 | Qld, NSW and Vic Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS
F_QNV+LREG_0200 | 2008-07-01 | 1 | Qld, NSW and Vic Lower Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS
F_QNV+LREG_0250 | 2008-07-01 | 1 | Qld, NSW and Vic Lower Regulation Requirement greater than 250 MW, Basslink unable to transfer FCAS
F_QNV+ML_L5_0370 | 2009-01-01 | 1 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 370, Basslink unable transfer FCAS
F_QNV+ML_L5_0400 | 2009-01-01 | 1 | Lower 5 min requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS
F_QNV+ML_L60_0370 | 2008-07-01 | 1 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 370, Basslink unable transfer FCAS
F_QNV+ML_L60_0400 | 2008-07-01 | 1 | Lower 60 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS
F_QNV+ML_L6_0370 | 2008-07-01 | 1 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 370, Basslink unable transfer FCAS
F_QNV+ML_L6_0400 | 2008-07-01 | 1 | Lower 6 sec requirement for a Qld, NSW and Vic Load Event, ML = 400, Basslink unable transfer FCAS
F_QNV+RREG_0100 | 2008-07-01 | 1 | Qld, NSW and Vic Raise Regulation Requirement greater than 100 MW, Basslink unable to transfer FCAS
F_QNV+RREG_0130 | 2008-07-01 | 1 | Qld, NSW and Vic Raise Regulation Requirement greater than 130 MW, Basslink unable to transfer FCAS
F_QNV+RREG_0200 | 2008-07-01 | 1 | Qld, NSW and Vic Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS
F_QNV+RREG_0250 | 2008-07-01 | 1 | Qld, NSW and Vic Raise Regulation Requirement greater than 250 MW, Basslink unable to transfer FCAS
F_QNV+TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 500, Basslink unable to transfer FCAS
F_QNV+TG_R5_0700 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 700, Basslink unable to transfer FCAS
F_QNV+TG_R5_0850 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 850, Basslink unable to transfer FCAS
F_QNV+TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 1000, Basslink unable to transfer FCAS
F_QNV+TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 1400, Basslink unable to transfer FCAS
F_QNV+TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 1600, Basslink unable to transfer FCAS
F_QNV+TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 2000, Basslink unable to transfer FCAS
F_QNV+TG_R5_2800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Qld, NSW and Vic Network Event, TG = 2800, Basslink unable to transfer FCAS
F_QNV+TG_R60_0500 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 500, Basslink unable to transfer FCAS
F_QNV+TG_R60_0700 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 700, Basslink unable to transfer FCAS
F_QNV+TG_R60_0850 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 850, Basslink unable to transfer FCAS
F_QNV+TG_R60_1000 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 1000, Basslink unable to transfer FCAS
F_QNV+TG_R60_1400 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 1400, Basslink unable to transfer FCAS
F_QNV+TG_R60_1600 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 1600, Basslink unable to transfer FCAS
F_QNV+TG_R60_2000 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 2000, Basslink unable to transfer FCAS
F_QNV+TG_R60_2800 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 2800, Basslink unable to transfer FCAS
F_QNV+TG_R6_0500 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 500, Basslink unable to transfer FCAS
F_QNV+TG_R6_0700 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 700, Basslink unable to transfer FCAS
F_QNV+TG_R6_0850 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 850, Basslink unable to transfer FCAS
F_QNV+TG_R6_1000 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 1000, Basslink unable to transfer FCAS
F_QNV+TG_R6_1400 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 1400, Basslink unable to transfer FCAS
F_QNV+TG_R6_1600 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 1600, Basslink unable to transfer FCAS
F_QNV+TG_R6_2000 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 2000, Basslink unable to transfer FCAS
F_QNV+TG_R6_2800 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TG = 2800, Basslink unable to transfer FCAS
F_QNV+TL_L5_0600 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink unable to transfer FCAS
F_QNV+TL_L5_0800 | 2009-01-01 | 1 | Out = Nil, Lower 5 min Service Requirement for a Qld, NSW and Vic Network Event, TL = 800, Basslink unable to transfer FCAS
F_QNV+TL_L60_0600 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink unable to transfer FCAS
F_QNV+TL_L60_0800 | 2008-07-01 | 1 | Out = Nil, Lower 60 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 800, Basslink unable to transfer FCAS
F_QNV+TL_L6_0600 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 600, Basslink unable to transfer FCAS
F_QNV+TL_L6_0800 | 2008-07-01 | 1 | Out = Nil, Lower 6 sec Service Requirement for a Qld, NSW and Vic Network Event, TL = 800, Basslink unable to transfer FCAS
F_Q_BR1_0_L5 | 2007-03-01 | 1 | Braemar unit 1 = 0MW. L5 <= 0MW
F_Q_BR1_0_L6 | 2007-03-01 | 1 | Braemar unit 1 = 0MW. L6 <= 0MW
F_Q_BR1_0_L60 | 2007-03-01 | 1 | Braemar unit 1 = 0MW L60 <= 0MW
F_Q_BR1_0_LREG | 2007-03-01 | 1 | Braemar unit 1 = 0MW LREG <= 0MW
F_Q_BR1_0_R5 | 2007-03-01 | 1 | Braemar unit 1 = 0MW. R5 <= 0MW
F_Q_BR1_0_R6 | 2007-03-01 | 1 | Braemar unit 1 = 0MW. R6 <= 0MW
F_Q_BR1_0_R60 | 2007-03-01 | 1 | Braemar unit 1 = 0MW. R60 <= 0MW
F_Q_BR1_0_RREG | 2007-03-01 | 1 | Braemar unit 1 = 0MW. RREG <= 0MW
F_Q_BR2_0_L5 | 2007-03-01 | 1 | Braemar Unit 2 = 0MW. L5 <= 0MW
F_Q_BR2_0_L6 | 2007-03-01 | 1 | Braemar Unit 2 = 0MW. L6 <= 0MW
F_Q_BR2_0_L60 | 2007-03-01 | 1 | Braemar Unit 2 = 0MW L60 <= 0MW
F_Q_BR2_0_LREG | 2007-03-01 | 1 | Braemar Unit 2 = 0MW LREG <= 0MW
F_Q_BR2_0_R5 | 2007-03-01 | 1 | Braemar Unit 2 = 0MW. R5 <= 0MW
F_Q_BR2_0_R6 | 2007-03-01 | 1 | Braemar Unit 2 = 0MW. R6 <= 0MW
F_Q_BR2_0_R60 | 2007-03-01 | 1 | Braemar Unit 2 = 0MW. R60 <= 0MW
F_Q_BR2_0_RREG | 2007-03-01 | 1 | Braemar Unit 2 = 0MW. RREG <= 0MW
F_Q_BR3_0_L5 | 2007-03-01 | 1 | Braemar Unit 3 = 0MW. L5 <= 0MW
F_Q_BR3_0_L6 | 2007-03-01 | 1 | Braemar Unit 3 = 0MW. L6 <= 0MW
F_Q_BR3_0_L60 | 2007-03-01 | 1 | Braemar Unit 3 = 0MW L60 <= 0MW
F_Q_BR3_0_LREG | 2007-03-01 | 1 | Braemar Unit 3 = 0MW LREG <= 0MW
F_Q_BR3_0_R5 | 2007-03-01 | 1 | Braemar Unit 3 = 0MW. R5 <= 0MW
F_Q_BR3_0_R6 | 2007-03-01 | 1 | Braemar Unit 3 = 0MW. R6 <= 0MW
F_Q_BR3_0_R60 | 2007-03-01 | 1 | Braemar Unit 3 = 0MW. R60 <= 0MW
F_Q_BR3_0_RREG | 2007-03-01 | 1 | Braemar Unit 3 = 0MW. RREG <= 0MW
F_Q_BRAEMAR1_L5 | 2007-03-27 | 1 | Out= NIL, Braemar 1 L5 Requirement <= 0MW
F_Q_BRAEMAR1_L6 | 2007-03-27 | 1 | Out= NIL, Braemar 1 L6 Requirement <= 0MW
F_Q_BRAEMAR1_L60 | 2007-03-27 | 1 | Out= NIL, Braemar 1 L60 Requirement <= 0MW
F_Q_BRAEMAR1_LREG | 2007-03-27 | 1 | Out= NIL, Braemar 1 LREG Requirement <= 0MW
F_Q_BRAEMAR1_R5 | 2007-03-27 | 1 | Out= NIL, Braemar 1 R5 Requirement <= 0MW
F_Q_BRAEMAR1_R6 | 2007-03-27 | 1 | Out= NIL, Braemar 1 R6 Requirement <= 0MW
F_Q_BRAEMAR1_R60 | 2007-03-27 | 1 | Out= NIL, Braemar 1 R60 Requirement <= 0MW
F_Q_BRAEMAR1_RREG | 2007-03-27 | 1 | Out= NIL, Braemar 1 RREG Requirement <= 0MW
F_Q_BRAEMAR2_L5 | 2007-03-27 | 1 | Out= NIL, Braemar 2 L5 Requirement <= 0MW
F_Q_BRAEMAR2_L6 | 2007-03-27 | 1 | Out= NIL, Braemar 2 L6 Requirement <= 0MW
F_Q_BRAEMAR2_L60 | 2007-03-27 | 1 | Out= NIL, Braemar 2 L60 Requirement <= 0MW
F_Q_BRAEMAR2_LREG | 2007-03-27 | 1 | Out= NIL, Braemar 2 LREG Requirement <= 0MW
F_Q_BRAEMAR2_R5 | 2007-03-27 | 1 | Out= NIL, Braemar 2 R5 Requirement <= 0MW
F_Q_BRAEMAR2_R6 | 2007-03-27 | 1 | Out= NIL, Braemar 2 R6 Requirement <= 0MW
F_Q_BRAEMAR2_R60 | 2007-03-27 | 1 | Out= NIL, Braemar 2 R60 Requirement <= 0MW
F_Q_BRAEMAR2_RREG | 2007-03-27 | 1 | Out= NIL, Braemar 2 RREG Requirement <= 0MW
F_Q_BRAEMAR3_L5 | 2007-03-27 | 1 | Out= NIL, Braemar 3 L5 Requirement <= 0MW
F_Q_BRAEMAR3_L6 | 2007-03-27 | 1 | Out= NIL, Braemar 3 L6 Requirement <= 0MW
F_Q_BRAEMAR3_L60 | 2007-03-27 | 1 | Out= NIL, Braemar 3 L60 Requirement <= 0MW
F_Q_BRAEMAR3_LREG | 2007-03-27 | 1 | Out= NIL, Braemar 3 LREG Requirement <= 0MW
F_Q_BRAEMAR3_R5 | 2007-03-27 | 1 | Out= NIL, Braemar 3 R5 Requirement <= 0MW
F_Q_BRAEMAR3_R6 | 2007-03-27 | 1 | Out= NIL, Braemar 3 R6 Requirement <= 0MW
F_Q_BRAEMAR3_R60 | 2007-03-27 | 1 | Out= NIL, Braemar 3 R60 Requirement <= 0MW
F_Q_BRAEMAR3_RREG | 2007-03-27 | 1 | Out= NIL, Braemar 3 RREG Requirement <= 0MW
F_Q_BRBRA_8838_L5 | 2009-01-09 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8838 (L5<=0)
F_Q_BRBRA_8838_L6 | 2009-01-09 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8838 (L6<=0)
F_Q_BRBRA_8838_L60 | 2009-01-09 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8838 (L60<=0)
F_Q_BRBRA_8838_LREG | 2009-01-09 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8838 (LREG<=0)
F_Q_BRBRA_8838_R5 | 2009-01-09 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8838 (R5<=0)
F_Q_BRBRA_8838_R6 | 2009-01-09 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8838 (R6<=0)
F_Q_BRBRA_8838_R60 | 2009-01-09 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8838 (R60<=0)
F_Q_BRBRA_8838_RREG | 2009-01-09 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8838 (RREG<=0)
F_Q_BRBRA_8839_L5 | 2009-01-08 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8839 (L5<=0)
F_Q_BRBRA_8839_L6 | 2009-01-08 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8839 (L6<=0)
F_Q_BRBRA_8839_L60 | 2009-01-08 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8839 (L60<=0)
F_Q_BRBRA_8839_LREG | 2009-01-08 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8839 (LREG<=0)
F_Q_BRBRA_8839_R5 | 2009-01-08 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8839 (R5<=0)
F_Q_BRBRA_8839_R6 | 2009-01-08 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8839 (R6<=0)
F_Q_BRBRA_8839_R60 | 2009-01-08 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8839 (R60<=0)
F_Q_BRBRA_8839_RREG | 2009-01-08 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8839 (RREG<=0)
F_Q_CALL_A_1_R5 | 2007-03-27 | 1 | Out= NIL, Callide A1 R5 Requirement <= 0MW
F_Q_CALL_A_2_R5 | 2007-03-27 | 1 | Out= NIL, Callide A2 R5 Requirement <= 0MW
F_Q_CALL_A_3_R5 | 2007-03-27 | 1 | Out= NIL, Callide A3 R5 Requirement <= 0MW
F_Q_CALL_A_4_R5 | 2007-03-27 | 1 | Out= NIL, Callide A4 R5 Requirement <= 0MW
F_Q_CALL_B_1_L6 | 2007-03-27 | 1 | Out= NIL, Callide B1 L6 Requirement <= 0MW
F_Q_CALL_B_1_L60 | 2007-03-27 | 1 | Out= NIL, Callide B1 L60 Requirement <= 0MW
F_Q_CALL_B_1_LREG | 2007-03-27 | 1 | Out= NIL, Callide B1 LREG Requirement <= 0MW
F_Q_CALL_B_1_R5 | 2007-03-27 | 1 | Out= NIL, Callide B1 R5 Requirement <= 0MW
F_Q_CALL_B_1_R6 | 2007-03-27 | 1 | Out= NIL, Callide B1 R6 Requirement <= 0MW
F_Q_CALL_B_1_R60 | 2007-03-27 | 1 | Out= NIL, Callide B1 R60 Requirement <= 0MW
F_Q_CALL_B_1_RREG | 2007-03-27 | 1 | Out= NIL, Callide B1 RREG Requirement <= 0MW
F_Q_CALL_B_2_L6 | 2007-03-27 | 1 | Out= NIL, Callide B2 L6 Requirement <= 0MW
F_Q_CALL_B_2_L60 | 2007-03-27 | 1 | Out= NIL, Callide B2 L60 Requirement <= 0MW
F_Q_CALL_B_2_LREG | 2007-03-27 | 1 | Out= NIL, Callide B2 LREG Requirement <= 0MW
F_Q_CALL_B_2_R5 | 2007-03-27 | 1 | Out= NIL, Callide B2 R5 Requirement <= 0MW
F_Q_CALL_B_2_R6 | 2007-03-27 | 1 | Out= NIL, Callide B2 R6 Requirement <= 0MW
F_Q_CALL_B_2_R60 | 2007-03-27 | 1 | Out= NIL, Callide B2 R60 Requirement <= 0MW
F_Q_CALL_B_2_RREG | 2007-03-27 | 1 | Out= NIL, Callide B2 RREG Requirement <= 0MW
F_Q_GSTONE1_L5 | 2007-03-27 | 1 | Out= NIL, Gladstone 1 L5 Requirement <= 0MW
F_Q_GSTONE1_L6 | 2007-03-27 | 1 | Out= NIL, Gladstone 1 L6 Requirement <= 0MW
F_Q_GSTONE1_L60 | 2007-03-27 | 1 | Out= NIL, Gladstone 1 L60 Requirement <= 0MW
F_Q_GSTONE1_LREG | 2007-03-27 | 1 | Out= NIL, Gladstone 1 LREG Requirement <= 0MW
F_Q_GSTONE1_R5 | 2007-03-27 | 1 | Out= NIL, Gladstone 1 R5 Requirement <= 0MW
F_Q_GSTONE1_R6 | 2007-03-27 | 1 | Out= NIL, Gladstone 1 R6 Requirement <= 0MW
F_Q_GSTONE1_R60 | 2007-03-27 | 1 | Out= NIL, Gladstone 1 R60 Requirement <= 0MW
F_Q_GSTONE1_RREG | 2007-03-27 | 1 | Out= NIL, Gladstone 1 RREG Requirement <= 0MW
F_Q_GSTONE2_L5 | 2007-03-27 | 1 | Out= NIL, Gladstone 2 L5 Requirement <= 0MW
F_Q_GSTONE2_L6 | 2007-03-27 | 1 | Out= NIL, Gladstone 2 L6 Requirement <= 0MW
F_Q_GSTONE2_L60 | 2007-03-27 | 1 | Out= NIL, Gladstone 2 L60 Requirement <= 0MW
F_Q_GSTONE2_LREG | 2007-03-27 | 1 | Out= NIL, Gladstone 2 LREG Requirement <= 0MW
F_Q_GSTONE2_R5 | 2007-03-27 | 1 | Out= NIL, Gladstone 2 R5 Requirement <= 0MW
F_Q_GSTONE2_R6 | 2007-03-27 | 1 | Out= NIL, Gladstone 2 R6 Requirement <= 0MW
F_Q_GSTONE2_R60 | 2007-03-27 | 1 | Out= NIL, Gladstone 2 R60 Requirement <= 0MW
F_Q_GSTONE2_RREG | 2007-03-27 | 1 | Out= NIL, Gladstone 2 RREG Requirement <= 0MW
F_Q_GSTONE3_L5 | 2007-03-27 | 1 | Out= NIL, Gladstone 3 L5 Requirement <= 0MW
F_Q_GSTONE3_L6 | 2007-03-27 | 1 | Out= NIL, Gladstone 3 L6 Requirement <= 0MW
F_Q_GSTONE3_L60 | 2007-03-27 | 1 | Out= NIL, Gladstone 3 L60 Requirement <= 0MW
F_Q_GSTONE3_LREG | 2007-03-27 | 1 | Out= NIL, Gladstone 3 LREG Requirement <= 0MW
F_Q_GSTONE3_R5 | 2007-03-27 | 1 | Out= NIL, Gladstone 3 R5 Requirement <= 0MW
F_Q_GSTONE3_R6 | 2007-03-27 | 1 | Out= NIL, Gladstone 3 R6 Requirement <= 0MW
F_Q_GSTONE3_R60 | 2007-03-27 | 1 | Out= NIL, Gladstone 3 R60 Requirement <= 0MW
F_Q_GSTONE3_RREG | 2007-03-27 | 1 | Out= NIL, Gladstone 3 RREG Requirement <= 0MW
F_Q_GSTONE4_L5 | 2007-03-27 | 1 | Out= NIL, Gladstone 4 L5 Requirement <= 0MW
F_Q_GSTONE4_L6 | 2007-03-27 | 1 | Out= NIL, Gladstone 4 L6 Requirement <= 0MW
F_Q_GSTONE4_L60 | 2007-03-27 | 1 | Out= NIL, Gladstone 4 L60 Requirement <= 0MW
F_Q_GSTONE4_LREG | 2007-03-27 | 1 | Out= NIL, Gladstone 4 LREG Requirement <= 0MW
F_Q_GSTONE4_R5 | 2007-03-27 | 1 | Out= NIL, Gladstone 4 R5 Requirement <= 0MW
F_Q_GSTONE4_R6 | 2007-03-27 | 1 | Out= NIL, Gladstone 4 R6 Requirement <= 0MW
F_Q_GSTONE4_R60 | 2007-03-27 | 1 | Out= NIL, Gladstone 4 R60 Requirement <= 0MW
F_Q_GSTONE4_RREG | 2007-03-27 | 1 | Out= NIL, Gladstone 4 RREG Requirement <= 0MW
F_Q_GSTONE5_L5 | 2007-03-27 | 1 | Out= NIL, Gladstone 5 L5 Requirement <= 0MW
F_Q_GSTONE5_L6 | 2007-03-27 | 1 | Out= NIL, Gladstone 5 L6 Requirement <= 0MW
F_Q_GSTONE5_L60 | 2007-03-27 | 1 | Out= NIL, Gladstone 5 L60 Requirement <= 0MW
F_Q_GSTONE5_LREG | 2007-03-27 | 1 | Out= NIL, Gladstone 5 LREG Requirement <= 0MW
F_Q_GSTONE5_R5 | 2007-03-27 | 1 | Out= NIL, Gladstone 5 R5 Requirement <= 0MW
F_Q_GSTONE5_R6 | 2007-03-27 | 1 | Out= NIL, Gladstone 5 R6 Requirement <= 0MW
F_Q_GSTONE5_R60 | 2007-03-27 | 1 | Out= NIL, Gladstone 5 R60 Requirement <= 0MW
F_Q_GSTONE5_RREG | 2007-03-27 | 1 | Out= NIL, Gladstone 5 RREG Requirement <= 0MW
F_Q_GSTONE6_L5 | 2007-03-27 | 1 | Out= NIL, Gladstone 6 L5 Requirement <= 0MW
F_Q_GSTONE6_L6 | 2007-03-27 | 1 | Out= NIL, Gladstone 6 L6 Requirement <= 0MW
F_Q_GSTONE6_L60 | 2007-03-27 | 1 | Out= NIL, Gladstone 6 L60 Requirement <= 0MW
F_Q_GSTONE6_LREG | 2007-03-27 | 1 | Out= NIL, Gladstone 6 LREG Requirement <= 0MW
F_Q_GSTONE6_R5 | 2007-03-27 | 1 | Out= NIL, Gladstone 6 R5 Requirement <= 0MW
F_Q_GSTONE6_R6 | 2007-03-27 | 1 | Out= NIL, Gladstone 6 R6 Requirement <= 0MW
F_Q_GSTONE6_R60 | 2007-03-27 | 1 | Out= NIL, Gladstone 6 R60 Requirement <= 0MW
F_Q_GSTONE6_RREG | 2007-03-27 | 1 | Out= NIL, Gladstone 6 RREG Requirement <= 0MW
F_Q_MACKAYGT_R5 | 2007-03-27 | 1 | Out= NIL, Mackay GT R5 Requirement <= 0MW
F_Q_MEWV_823_R5 | 2007-03-01 | 1 | Out= Mt England to Wivenhoe (823) line, Raise 5 min requirement of zero for Wivenhoe #1
F_Q_MEWV_823_R60 | 2007-03-01 | 1 | Out= Mt England to Wivenhoe (823) line, Raise 60 sec requirement of zero for Wivenhoe #1
F_Q_MEWV_824_R5 | 2007-03-01 | 1 | Out= Mt England to Wivenhoe (824) line, Raise 5 min requirement of zero for Wivenhoe #2
F_Q_MEWV_824_R60 | 2007-03-01 | 1 | Out= Mt England to Wivenhoe (824) line, Raise 60 sec requirement of zero for Wivenhoe #2
F_Q_MI+MG_R5 | 2009-01-01 | 1 | Raise 5 min Service Requirement for Qld minus Millmerran Generation Event
F_Q_MI+MG_R6 | 2005-12-21 | 1 | Raise 6 sec Service Requirement for Qld minus Millmerran Generation Event
F_Q_MI+MG_R60 | 2005-12-21 | 1 | Raise 60 sec Service Requirement for Qld minus Millmerran Generation Event
F_Q_MK_33BUS_R5 | 2007-03-01 | 1 | Out=T38 Mackay 33kV C Bus (R5 Requirement)
F_Q_MSPTS_7242_LREG | 2007-03-01 | 1 | Out= 7242 Mt Stuart Power Station Townsville South 132kV line (LREG Requirement)
F_Q_MSPTS_7242_RREG | 2007-03-01 | 1 | Out= 7242 Mt Stuart Power Station Townsville South 132kV line (RREG Requirement)
F_Q_MSPTS_7243_LREG | 2007-03-01 | 1 | Out= 7243 Mt Stuart Power Station Townsville South 132kV line (LREG Requirement)
F_Q_MSPTS_7243_RREG | 2007-03-01 | 1 | Out= 7243 Mt Stuart Power Station Townsville South 132kV line (RREG Requirement)
F_Q_MSTUART1_LREG | 2007-03-27 | 1 | Out= NIL, MT Stuart 1 LREG Requirement <= 0MW
F_Q_MSTUART1_RREG | 2007-03-27 | 1 | Out= NIL, MT Stuart 1 RREG Requirement <= 0MW
F_Q_MSTUART2_LREG | 2007-03-27 | 1 | Out= NIL, MT Stuart 2 LREG Requirement <= 0MW
F_Q_MSTUART2_RREG | 2007-03-27 | 1 | Out= NIL, MT Stuart 2 RREG Requirement <= 0MW
F_Q_OAKEY1_L6 | 2007-03-27 | 1 | Out= NIL, Oakey 1 L6 Requirement <= 0MW
F_Q_OAKEY1_L60 | 2007-03-27 | 1 | Out= NIL, Oakey 1 L60 Requirement <= 0MW
F_Q_OAKEY1_LREG | 2007-03-27 | 1 | Out= NIL, Oakey 1 LREG Requirement <= 0MW
F_Q_OAKEY1_R6 | 2007-03-27 | 1 | Out= NIL, Oakey 1 R6 Requirement <= 0MW
F_Q_OAKEY1_R60 | 2007-03-27 | 1 | Out= NIL, Oakey 1 R60 Requirement <= 0MW
F_Q_OAKEY1_RREG | 2007-03-27 | 1 | Out= NIL, Oakey 1 RREG Requirement <= 0MW
F_Q_OAKEY2_L6 | 2007-03-27 | 1 | Out= NIL, Oakey 2 L6 Requirement <= 0MW
F_Q_OAKEY2_L60 | 2007-03-27 | 1 | Out= NIL, Oakey 2 L60 Requirement <= 0MW
F_Q_OAKEY2_LREG | 2007-03-27 | 1 | Out= NIL, Oakey 2 LREG Requirement <= 0MW
F_Q_OAKEY2_R6 | 2007-03-27 | 1 | Out= NIL, Oakey 2 R6 Requirement <= 0MW
F_Q_OAKEY2_R60 | 2007-03-27 | 1 | Out= NIL, Oakey 2 R60 Requirement <= 0MW
F_Q_OAKEY2_RREG | 2007-03-27 | 1 | Out= NIL, Oakey 2 RREG Requirement <= 0MW
F_Q_PUMP1_R5 | 2007-03-27 | 1 | Out= NIL, PUMP1 R5 Requirement <= 0MW
F_Q_PUMP1_R6 | 2007-03-27 | 1 | Out= NIL, PUMP1 R6 Requirement <= 0MW
F_Q_PUMP1_R60 | 2007-03-27 | 1 | Out= NIL, PUMP1 R60 Requirement <= 0MW
F_Q_PUMP2_R5 | 2007-03-27 | 1 | Out= NIL, PUMP2 R5 Requirement <= 0MW
F_Q_PUMP2_R6 | 2007-03-27 | 1 | Out= NIL, PUMP2 R6 Requirement <= 0MW
F_Q_PUMP2_R60 | 2007-03-27 | 1 | Out= NIL, PUMP2 R60 Requirement <= 0MW
F_Q_SB1_0_L5 | 2007-03-01 | 1 | Out = Swanbank B1 due to transmission outage SBK_B1_L5 <= 0MW
F_Q_SB1_0_L6 | 2007-03-01 | 1 | Out = Swanbank B1 due to transmission outage SBK_B1_L6 <= 0MW
F_Q_SB1_0_L60 | 2007-03-01 | 1 | Out = Swanbank B1 due to transmission outage SBK_B1_L60 <= 0MW
F_Q_SB1_0_LREG | 2007-03-01 | 1 | Out = Swanbank B1 due to transmission outage SBK_B1_LREG <= 0MW
F_Q_SB1_0_R5 | 2007-03-01 | 1 | Out = Swanbank B1 due to transmission outage SBK_B1_R5 <= 0MW
F_Q_SB1_0_R6 | 2007-03-01 | 1 | Out = Swanbank B1 due to transmission outage SBK_B1_R6 <= 0MW
F_Q_SB1_0_R60 | 2007-03-01 | 1 | Out = Swanbank B1 due to transmission outage SBK_B1_R60 <= 0MW
F_Q_SB1_0_RREG | 2007-03-01 | 1 | Out = Swanbank B1 due to transmission outage SBK_B1_RREG <= 0MW
F_Q_SB_5221_L5 | 2007-03-01 | 1 | Out = H1 Swnabank Isol 5221. SBK_B2_L5 <= 0MW
F_Q_SB_5221_L6 | 2007-03-01 | 1 | Out = H1 Swnabank Isol 5221. SBK_B2_L6 <= 0MW
F_Q_SB_5221_L60 | 2007-03-01 | 1 | Out = H1 Swnabank Isol 5221. SBK_B2_L60 <= 0MW
F_Q_SB_5221_LREG | 2007-03-01 | 1 | Out = H1 Swnabank Isol 5221. SBK_B2_LREG <= 0MW
F_Q_SB_5221_R5 | 2007-03-01 | 1 | Out = H1 Swnabank Isol 5221. SBK_B2_R5 <= 0MW
F_Q_SB_5221_R6 | 2007-03-01 | 1 | Out = H1 Swnabank Isol 5221. SBK_B2_R6 <= 0MW
F_Q_SB_5221_R60 | 2007-03-01 | 1 | Out = H1 Swnabank Isol 5221. SBK_B2_R60 <= 0MW
F_Q_SB_5221_RREG | 2007-03-01 | 1 | Out = H1 Swnabank Isol 5221. SBK_B2_RREG <= 0MW
F_Q_STAN1_L5_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 1 L5 Requirement <= 0MW
F_Q_STAN1_L60_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 1 L60 Requirement <= 0MW
F_Q_STAN1_L6_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 1 L6 Requirement <= 0MW
F_Q_STAN1_LREG_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 1 LREG Requirement <= 0MW
F_Q_STAN1_R60_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 1 R60 Requirement <= 0MW
F_Q_STAN1_R6_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 1 R6 Requirement <= 0MW
F_Q_STAN1_RREG_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 1 RREG Requirement <= 0MW
F_Q_STAN2_L5_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 2 L5 Requirement <= 0MW
F_Q_STAN2_L60_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 2 L60 Requirement <= 0MW
F_Q_STAN2_L6_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 2 L6 Requirement <= 0MW
F_Q_STAN2_LREG_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 2 LREG Requirement <= 0MW
F_Q_STAN2_R60_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 2 R60 Requirement <= 0MW
F_Q_STAN2_R6_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 2 R6 Requirement <= 0MW
F_Q_STAN2_RREG_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 2 RREG Requirement <= 0MW
F_Q_STAN3_L5_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 3 L5 Requirement <= 0MW
F_Q_STAN3_L60_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 3 L60 Requirement <= 0MW
F_Q_STAN3_L6_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 3 L6 Requirement <= 0MW
F_Q_STAN3_LREG_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 3 LREG Requirement <= 0MW
F_Q_STAN3_R60_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 3 R60 Requirement <= 0MW
F_Q_STAN3_R6_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 3 R6 Requirement <= 0MW
F_Q_STAN3_RREG_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 3 RREG Requirement <= 0MW
F_Q_STAN4_L5_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 4 L5 Requirement <= 0MW
F_Q_STAN4_L60_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 4 L60 Requirement <= 0MW
F_Q_STAN4_L6_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 4 L6 Requirement <= 0MW
F_Q_STAN4_LREG_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 4 LREG Requirement <= 0MW
F_Q_STAN4_R60_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 4 R60 Requirement <= 0MW
F_Q_STAN4_R6_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 4 R6 Requirement <= 0MW
F_Q_STAN4_RREG_ZERO | 2007-03-27 | 1 | Out= NIL, Stanwell 4 RREG Requirement <= 0MW
F_Q_STSTN_861_L5 | 2007-03-01 | 1 | Out= 861 Stanwell Stanwell Power Station 275kV line (L5 Requirement)
F_Q_STSTN_861_L6 | 2007-03-01 | 1 | Out= 861 Stanwell Stanwell Power Station 275kV line (L6 Requirement)
F_Q_STSTN_861_L60 | 2007-03-01 | 1 | Out= 861 Stanwell Stanwell Power Station 275kV line (L60 Requirement)
F_Q_STSTN_861_LREG | 2007-03-01 | 1 | Out= 861 Stanwell Stanwell Power Station 275kV line (LREG Requirement)
F_Q_STSTN_861_R6 | 2007-03-01 | 1 | Out= 861 Stanwell Stanwell Power Station 275kV line (R6 Requirement)
F_Q_STSTN_861_R60 | 2007-03-01 | 1 | Out= 861 Stanwell Stanwell Power Station 275kV line (R60 Requirement)
F_Q_STSTN_861_RREG | 2007-03-01 | 1 | Out= 861 Stanwell Stanwell Power Station 275kV line (RREG Requirement)
F_Q_STSTN_862_L5 | 2007-03-01 | 1 | Out= 862 Stanwell Stanwell Power Station 275kV line (L5 Requirement)
F_Q_STSTN_862_L6 | 2007-03-01 | 1 | Out= 862 Stanwell Stanwell Power Station 275kV line (L6 Requirement)
F_Q_STSTN_862_L60 | 2007-03-01 | 1 | Out= 862 Stanwell Stanwell Power Station 275kV line (L60 Requirement)
F_Q_STSTN_862_LREG | 2007-03-01 | 1 | Out= 862 Stanwell Stanwell Power Station 275kV line (LREG Requirement)
F_Q_STSTN_862_R6 | 2007-03-01 | 1 | Out= 862 Stanwell Stanwell Power Station 275kV line (R6 Requirement)
F_Q_STSTN_862_R60 | 2007-03-01 | 1 | Out= 862 Stanwell Stanwell Power Station 275kV line (R60 Requirement)
F_Q_STSTN_862_RREG | 2007-03-01 | 1 | Out= 862 Stanwell Stanwell Power Station 275kV line (RREG Requirement)
F_Q_STSTN_863_L5 | 2007-03-01 | 1 | Out= 863 Stanwell Stanwell Power Station 275kV line (L5 Requirement)
F_Q_STSTN_863_L6 | 2007-03-01 | 1 | Out= 863 Stanwell Stanwell Power Station 275kV line (L6 Requirement)
F_Q_STSTN_863_L60 | 2007-03-01 | 1 | Out= 863 Stanwell Stanwell Power Station 275kV line (L60 Requirement)
F_Q_STSTN_863_LREG | 2007-03-01 | 1 | Out= 863 Stanwell Stanwell Power Station 275kV line (LREG Requirement)
F_Q_STSTN_863_R6 | 2007-03-01 | 1 | Out= 863 Stanwell Stanwell Power Station 275kV line (R6 Requirement)
F_Q_STSTN_863_R60 | 2007-03-01 | 1 | Out= 863 Stanwell Stanwell Power Station 275kV line (R60 Requirement)
F_Q_STSTN_863_RREG | 2007-03-01 | 1 | Out= 863 Stanwell Stanwell Power Station 275kV line (RREG Requirement)
F_Q_STSTN_864_L5 | 2007-03-01 | 1 | Out= 864 Stanwell Stanwell Power Station 275kV line (L5 Requirement)
F_Q_STSTN_864_L6 | 2007-03-01 | 1 | Out= 864 Stanwell Stanwell Power Station 275kV line (L6 Requirement)
F_Q_STSTN_864_L60 | 2007-03-01 | 1 | Out= 864 Stanwell Stanwell Power Station 275kV line (L60 Requirement)
F_Q_STSTN_864_LREG | 2007-03-01 | 1 | Out= 864 Stanwell Stanwell Power Station 275kV line (LREG Requirement)
F_Q_STSTN_864_R6 | 2007-03-01 | 1 | Out= 864 Stanwell Stanwell Power Station 275kV line (R6 Requirement)
F_Q_STSTN_864_R60 | 2007-03-01 | 1 | Out= 864 Stanwell Stanwell Power Station 275kV line (R60 Requirement)
F_Q_STSTN_864_RREG | 2007-03-01 | 1 | Out= 864 Stanwell Stanwell Power Station 275kV line (RREG Requirement)
F_Q_SWAN_B_1_L5 | 2007-03-27 | 1 | Out= NIL, Swanbank B1 L5 Requirement <= 0MW
F_Q_SWAN_B_1_L6 | 2007-03-27 | 1 | Out= NIL, Swanbank B1 L6 Requirement <= 0MW
F_Q_SWAN_B_1_L60 | 2007-03-27 | 1 | Out= NIL, Swanbank B1 L60 Requirement <= 0MW
F_Q_SWAN_B_1_LREG | 2007-03-27 | 1 | Out= NIL, Swanbank B1 LREG Requirement <= 0MW
F_Q_SWAN_B_1_R5 | 2007-03-27 | 1 | Out= NIL, Swanbank B1 R5 Requirement <= 0MW
F_Q_SWAN_B_1_R6 | 2007-03-27 | 1 | Out= NIL, Swanbank B1 R6 Requirement <= 0MW
F_Q_SWAN_B_1_R60 | 2007-03-27 | 1 | Out= NIL, Swanbank B1 R60 Requirement <= 0MW
F_Q_SWAN_B_1_RREG | 2007-03-27 | 1 | Out= NIL, Swanbank B1 RREG Requirement <= 0MW
F_Q_SWAN_B_2_L5 | 2007-03-27 | 1 | Out= NIL, Swanbank B2 L5 Requirement <= 0MW
F_Q_SWAN_B_2_L6 | 2007-03-27 | 1 | Out= NIL, Swanbank B2 L6 Requirement <= 0MW
F_Q_SWAN_B_2_L60 | 2007-03-27 | 1 | Out= NIL, Swanbank B2 L60 Requirement <= 0MW
F_Q_SWAN_B_2_LREG | 2007-03-27 | 1 | Out= NIL, Swanbank B2 LREG Requirement <= 0MW
F_Q_SWAN_B_2_R5 | 2007-03-27 | 1 | Out= NIL, Swanbank B2 R5 Requirement <= 0MW
F_Q_SWAN_B_2_R6 | 2007-03-27 | 1 | Out= NIL, Swanbank B2 R6 Requirement <= 0MW
F_Q_SWAN_B_2_R60 | 2007-03-27 | 1 | Out= NIL, Swanbank B2 R60 Requirement <= 0MW
F_Q_SWAN_B_2_RREG | 2007-03-27 | 1 | Out= NIL, Swanbank B2 RREG Requirement <= 0MW
F_Q_SWAN_B_3_L5 | 2007-03-27 | 1 | Out= NIL, Swanbank B3 L5 Requirement <= 0MW
F_Q_SWAN_B_3_L6 | 2007-03-27 | 1 | Out= NIL, Swanbank B3 L6 Requirement <= 0MW
F_Q_SWAN_B_3_L60 | 2007-03-27 | 1 | Out= NIL, Swanbank B3 L60 Requirement <= 0MW
F_Q_SWAN_B_3_LREG | 2007-03-27 | 1 | Out= NIL, Swanbank B3 LREG Requirement <= 0MW
F_Q_SWAN_B_3_R5 | 2007-03-27 | 1 | Out= NIL, Swanbank B3 R5 Requirement <= 0MW
F_Q_SWAN_B_3_R6 | 2007-03-27 | 1 | Out= NIL, Swanbank B3 R6 Requirement <= 0MW
F_Q_SWAN_B_3_R60 | 2007-03-27 | 1 | Out= NIL, Swanbank B3 R60 Requirement <= 0MW
F_Q_SWAN_B_3_RREG | 2007-03-27 | 1 | Out= NIL, Swanbank B3 RREG Requirement <= 0MW
F_Q_SWAN_B_4_L5 | 2007-03-27 | 1 | Out= NIL, Swanbank B4 L5 Requirement <= 0MW
F_Q_SWAN_B_4_L6 | 2007-03-27 | 1 | Out= NIL, Swanbank B4 L6 Requirement <= 0MW
F_Q_SWAN_B_4_L60 | 2007-03-27 | 1 | Out= NIL, Swanbank B4 L60 Requirement <= 0MW
F_Q_SWAN_B_4_LREG | 2007-03-27 | 1 | Out= NIL, Swanbank B4 LREG Requirement <= 0MW
F_Q_SWAN_B_4_R5 | 2007-03-27 | 1 | Out= NIL, Swanbank B4 R5 Requirement <= 0MW
F_Q_SWAN_B_4_R6 | 2007-03-27 | 1 | Out= NIL, Swanbank B4 R6 Requirement <= 0MW
F_Q_SWAN_B_4_R60 | 2007-03-27 | 1 | Out= NIL, Swanbank B4 R60 Requirement <= 0MW
F_Q_SWAN_B_4_RREG | 2007-03-27 | 1 | Out= NIL, Swanbank B4 RREG Requirement <= 0MW
F_Q_SWAN_E_L60 | 2007-03-27 | 1 | Out= NIL, Swanbank E L60 Requirement <= 0MW
F_Q_SWAN_E_LREG | 2007-03-27 | 1 | Out= NIL, Swanbank E LREG Requirement <= 0MW
F_Q_SWAN_E_R60 | 2007-03-27 | 1 | Out= NIL, Swanbank E R60 Requirement <= 0MW
F_Q_SWAN_E_RREG | 2007-03-27 | 1 | Out= NIL, Swanbank E RREG Requirement <= 0MW
F_Q_SWE_8829_L5 | 2005-07-26 | 3 | Out=Swanbank E to Swanbank E PS Line 8829 Lower 5Min requirement of zero for Swanbank E
F_Q_SWE_8829_L6 | 2005-07-26 | 2 | Out=Swanbank E to Swanbank E PS Line 8829 Lower 6Sec requirement of zero for Swanbank E
F_Q_SWE_8829_L60 | 2005-07-26 | 2 | Out=Swanbank E to Swanbank E PS Line 8829 Lower 60Sec requirement of zero for Swanbank E
F_Q_SWE_8829_R5 | 2005-07-26 | 1 | Out=Swanbank E to Swanbank E PS Line 8829 Raise 5Min requirement of zero for Swanbank E
F_Q_SWE_8829_R6 | 2005-07-26 | 1 | Out=Swanbank E to Swanbank E PS Line 8829 Raise 6Sec requirement of zero for Swanbank E
F_Q_SWE_8829_R60 | 2005-07-26 | 1 | Out=Swanbank E to Swanbank E PS Line 8829 Raise 60Sec requirement of zero for Swanbank E
F_Q_TARONG#1_L5 | 2007-03-27 | 1 | Out= NIL, Tarong 1 L5 Requirement <= 0MW
F_Q_TARONG#1_L6 | 2007-03-27 | 1 | Out= NIL, Tarong 1 L6 Requirement <= 0MW
F_Q_TARONG#1_L60 | 2007-03-27 | 1 | Out= NIL, Tarong 1 L60 Requirement <= 0MW
F_Q_TARONG#1_LREG | 2007-03-27 | 1 | Out= NIL, Tarong 1 LREG Requirement <= 0MW
F_Q_TARONG#1_R6 | 2007-03-27 | 1 | Out= NIL, Tarong 1 R6 Requirement <= 0MW
F_Q_TARONG#1_R60 | 2007-03-27 | 1 | Out= NIL, Tarong 1 R60 Requirement <= 0MW
F_Q_TARONG#1_RREG | 2007-03-27 | 1 | Out= NIL, Tarong 1 RREG Requirement <= 0MW
F_Q_TARONG#2_L5 | 2007-03-27 | 1 | Out= NIL, Tarong 2 L5 Requirement <= 0MW
F_Q_TARONG#2_L6 | 2007-03-27 | 1 | Out= NIL, Tarong 2 L6 Requirement <= 0MW
F_Q_TARONG#2_L60 | 2007-03-27 | 1 | Out= NIL, Tarong 2 L60 Requirement <= 0MW
F_Q_TARONG#2_LREG | 2007-03-27 | 1 | Out= NIL, Tarong 2 LREG Requirement <= 0MW
F_Q_TARONG#2_R6 | 2007-03-27 | 1 | Out= NIL, Tarong 2 R6 Requirement <= 0MW
F_Q_TARONG#2_R60 | 2007-03-27 | 1 | Out= NIL, Tarong 2 R60 Requirement <= 0MW
F_Q_TARONG#2_RREG | 2007-03-27 | 1 | Out= NIL, Tarong 2 RREG Requirement <= 0MW
F_Q_TARONG#3_L5 | 2007-03-27 | 1 | Out= NIL, Tarong 3 L5 Requirement <= 0MW
F_Q_TARONG#3_L6 | 2007-03-27 | 1 | Out= NIL, Tarong 3 L6 Requirement <= 0MW
F_Q_TARONG#3_L60 | 2007-03-27 | 1 | Out= NIL, Tarong 3 L60 Requirement <= 0MW
F_Q_TARONG#3_LREG | 2007-03-27 | 1 | Out= NIL, Tarong 3 LREG Requirement <= 0MW
F_Q_TARONG#3_R6 | 2007-03-27 | 1 | Out= NIL, Tarong 3 R6 Requirement <= 0MW
F_Q_TARONG#3_R60 | 2007-03-27 | 1 | Out= NIL, Tarong 3 R60 Requirement <= 0MW
F_Q_TARONG#3_RREG | 2007-03-27 | 1 | Out= NIL, Tarong 3 RREG Requirement <= 0MW
F_Q_TARONG#4_L5 | 2007-03-27 | 1 | Out= NIL, Tarong 4 L5 Requirement <= 0MW
F_Q_TARONG#4_L6 | 2007-03-27 | 1 | Out= NIL, Tarong 4 L6 Requirement <= 0MW
F_Q_TARONG#4_L60 | 2007-03-27 | 1 | Out= NIL, Tarong 4 L60 Requirement <= 0MW
F_Q_TARONG#4_LREG | 2007-03-27 | 1 | Out= NIL, Tarong 4 LREG Requirement <= 0MW
F_Q_TARONG#4_R6 | 2007-03-27 | 1 | Out= NIL, Tarong 4 R6 Requirement <= 0MW
F_Q_TARONG#4_R60 | 2007-03-27 | 1 | Out= NIL, Tarong 4 R60 Requirement <= 0MW
F_Q_TARONG#4_RREG | 2007-03-27 | 1 | Out= NIL, Tarong 4 RREG Requirement <= 0MW
F_Q_W/HOE#1_R5 | 2007-03-27 | 1 | Out= NIL, W/HOE#1 R5 Requirement <= 0MW
F_Q_W/HOE#1_R60 | 2007-03-27 | 1 | Out= NIL, W/HOE#1 R60 Requirement <= 0MW
F_Q_W/HOE#2_R5 | 2007-03-27 | 1 | Out= NIL, W/HOE#2 R5 Requirement <= 0MW
F_Q_W/HOE#2_R60 | 2007-03-27 | 1 | Out= NIL, W/HOE#2 R60 Requirement <= 0MW
F_Q_YABULU_L6 | 2007-03-27 | 1 | Out= NIL, Yabulu L6 Requirement <= 0MW
F_Q_YABULU_L60 | 2007-03-27 | 1 | Out= NIL, Yabulu L60 Requirement <= 0MW
F_Q_YABULU_LREG | 2007-03-27 | 1 | Out= NIL, Yabulu LREG Requirement <= 0MW
F_Q_YABULU_R6 | 2007-03-27 | 1 | Out= NIL, Yabulu R6 Requirement <= 0MW
F_Q_YABULU_R60 | 2007-03-27 | 1 | Out= NIL, Yabulu R60 Requirement <= 0MW
F_Q_YABULU_RREG | 2007-03-27 | 1 | Out= NIL, Yabulu RREG Requirement <= 0MW
F_S++HYML_L5 | 2009-01-01 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) 500kV line or one Moorabool to Sydneham (MLTS-SYTS) 500kV line, SA Lower 5 min Requirement
F_S++HYML_L6 | 2006-01-06 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) 500kV line or one Moorabool to Sydneham (MLTS-SYTS) 500kV line, SA Lower 6 sec Requirement
F_S++HYML_L60 | 2006-01-06 | 1 | Out = one Heywood to Moorabool (HYTS-MLTS) 500kV line or one Moorabool to Sydneham (MLTS-SYTS) 500kV line, SA Lower 60 sec Requirement
F_S++HYSE_L5 | 2009-01-01 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, SA Lower 5 min Requirement
F_S++HYSE_L6 | 2006-01-03 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, SA Lower 6 sec Requirement
F_S++HYSE_L60 | 2006-01-03 | 1 | Out = one Heywood to South East (HYTS-SESS) or one Heywood (HYTS) 500/275kV (M1 or M2) transformer, SA Lower 60 sec Requirement
F_S++ML_L5 | 2009-01-01 | 1 | Lower 5 min Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA
F_S++ML_L6 | 2005-12-21 | 1 | Lower 6 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA
F_S++ML_L60 | 2005-12-21 | 1 | Lower 60 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA
F_S+LREG_0050 | 2005-12-15 | 1 | SA Lower Regulation Requirement greater than 50 MW
F_S+LREG_0070 | 2005-12-15 | 1 | SA Lower Regulation Requirement greater than 70 MW
F_S+LREG_0100 | 2005-12-15 | 1 | SA Lower Regulation Requirement greater than 100 MW
F_S+LREG_0150 | 2005-12-15 | 1 | SA Lower Regulation Requirement greater than 150 MW
F_S+MG_R5 | 2009-01-01 | 1 | Raise 5 min Service Requirement for SA Generation Event
F_S+MG_R6 | 2005-12-21 | 1 | Raise 6 sec Service Requirement for SA Generation Event
F_S+MG_R60 | 2005-12-21 | 1 | Raise 60 sec Service Requirement for SA Generation Event
F_S+ML_L5_0100 | 2009-01-01 | 1 | Lower 5 min Service Requirement for SA Load Event, ML = 100
F_S+ML_L60_0100 | 2005-12-15 | 1 | Lower 60 sec Service Requirement for SA Load Event, ML = 100
F_S+ML_L6_0100 | 2005-12-15 | 1 | Lower 6 sec Service Requirement for SA Load Event, ML = 100
F_S+RREG_0050 | 2005-12-15 | 1 | SA Raise Regulation Requirement greater than 50 MW
F_S+RREG_0070 | 2005-12-15 | 1 | SA Raise Regulation Requirement greater than 70 MW
F_S+RREG_0100 | 2005-12-15 | 1 | SA Raise Regulation Requirement greater than 100 MW
F_S+RREG_0150 | 2005-12-15 | 1 | SA Raise Regulation Requirement greater than 150 MW
F_S+TG_R5_0250 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a SA Network Event, TG = 250
F_S+TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a SA Network Event, TG = 500
F_S+TG_R60_0250 | 2003-08-01 | 1 | Raise 60 sec Service Requirement for a SA Network Event, TG = 250
F_S+TG_R60_0500 | 2003-08-01 | 1 | Raise 60 sec Service Requirement for a SA Network Event, TG = 500
F_S+TG_R6_0250 | 2003-08-01 | 1 | Raise 6 sec Service Requirement for a SA Network Event, TG = 250
F_S+TG_R6_0500 | 2003-08-01 | 1 | Raise 6 sec Service Requirement for a SA Network Event, TG = 500
F_S+TL_L5_0150 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a SA Network Event, TL = 150
F_S+TL_L60_0150 | 2003-08-01 | 1 | Lower 60 sec Service Requirement for a SA Network Event, TL = 150
F_S+TL_L6_0150 | 2003-08-01 | 1 | Lower 6 sec Service Requirement for a SA Network Event, TL = 150
F_STHN++ARDM_L5 | 2009-01-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Southern Lower 5 min Requirement
F_STHN++ARDM_L6 | 2008-07-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Southern Lower 6 sec Requirement
F_STHN++ARDM_L60 | 2008-07-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Southern Lower 60 sec Requirement
F_STHN++ARDM_R5 | 2009-01-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Southern Raise 5 min Requirement
F_STHN++ARDM_R6 | 2008-07-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Southern Raise 6 sec Requirement
F_STHN++ARDM_R60 | 2008-07-01 | 1 | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Southern Raise 60 sec Requirement
F_STHN++ARTW_L5 | 2009-01-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, Southern Lower 5 min Requirement
F_STHN++ARTW_L6 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, Southern Lower 6 sec Requirement
F_STHN++ARTW_L60 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, Southern Lower 60 sec Requirement
F_STHN++ARTW_R5 | 2009-01-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, Southern Raise 5 min Requirement
F_STHN++ARTW_R6 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, Southern Raise 6 sec Requirement
F_STHN++ARTW_R60 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86) line, Southern Raise 60 sec Requirement
F_STHN++LDMU_L5 | 2009-01-01 | 1 | Out = Liddell to Muswellbrook (83) line, Southern Lower 5 min Requirement
F_STHN++LDMU_L6 | 2008-07-01 | 1 | Out = Liddell to Muswellbrook (83) line, Southern Lower 6 sec Requirement
F_STHN++LDMU_L60 | 2008-07-01 | 1 | Out = Liddell to Muswellbrook (83) line, Southern Lower 60 sec Requirement
F_STHN++LDMU_R5 | 2009-01-01 | 1 | Out = Liddell to Muswellbrook (83) line, Southern Raise 5 min Requirement
F_STHN++LDMU_R6 | 2008-07-01 | 1 | Out = Liddell to Muswellbrook (83) line, Southern Raise 6 sec Requirement
F_STHN++LDMU_R60 | 2008-07-01 | 1 | Out = Liddell to Muswellbrook (83) line, Southern Raise 60 sec Requirement
F_STHN++LDTW_L5 | 2009-01-01 | 1 | Out = Liddell to Tamworth (84) line, Southern Lower 5 min Requirement
F_STHN++LDTW_L6 | 2008-07-01 | 1 | Out = Liddell to Tamworth (84) line, Southern Lower 6 sec Requirement
F_STHN++LDTW_L60 | 2008-07-01 | 1 | Out = Liddell to Tamworth (84) line, Southern Lower 60 sec Requirement
F_STHN++LDTW_R5 | 2009-01-01 | 1 | Out = Liddell to Tamworth (84) line, Southern Raise 5 min Requirement
F_STHN++LDTW_R6 | 2008-07-01 | 1 | Out = Liddell to Tamworth (84) line, Southern Raise 6 sec Requirement
F_STHN++LDTW_R60 | 2008-07-01 | 1 | Out = Liddell to Tamworth (84) line, Southern Raise 60 sec Requirement
F_STHN++MUTW_L5 | 2009-01-01 | 1 | Out = Muswellbrook to Tamworth (88) line, Southern Lower 5 min Requirement
F_STHN++MUTW_L6 | 2008-07-01 | 1 | Out = Muswellbrook to Tamworth (88) line, Southern Lower 6 sec Requirement
F_STHN++MUTW_L60 | 2008-07-01 | 1 | Out = Muswellbrook to Tamworth (88) line, Southern Lower 60 sec Requirement
F_STHN++MUTW_R5 | 2009-01-01 | 1 | Out = Muswellbrook to Tamworth (88) line, Southern Raise 5 min Requirement
F_STHN++MUTW_R6 | 2008-07-01 | 1 | Out = Muswellbrook to Tamworth (88) line, Southern Raise 6 sec Requirement
F_STHN++MUTW_R60 | 2008-07-01 | 1 | Out = Muswellbrook to Tamworth (88) line, Southern Raise 60 sec Requirement
F_STHN+LREG_0100 | 2008-07-01 | 1 | Southern Lower Regulation Requirement greater than 100 MW
F_STHN+LREG_0120 | 2008-07-01 | 1 | Southern Lower Regulation Requirement greater than 120 MW
F_STHN+LREG_0200 | 2008-07-01 | 1 | Southern Lower Regulation Requirement greater than 200 MW
F_STHN+LREG_0250 | 2008-07-01 | 1 | Southern Lower Regulation Requirement greater than 250 MW
F_STHN+MG_R5 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Southern Generation Event
F_STHN+MG_R6 | 2008-07-01 | 2 | Raise 6 sec Service Requirement for a Southern Generation Event
F_STHN+MG_R60 | 2008-07-01 | 2 | Raise 60 sec Service Requirement for a Southern Generation Event
F_STHN+MI_ISLE_L5 | 2006-01-06 | 1 | Qld / Southern separation between Bulli Creek and Tarong with 9908 AND (9901 and 9902 or both Braemar 330/275kV transformers or 8814 and 8815) Millmerran Lower 5 min Requirement = 0
F_STHN+MI_ISLE_L6 | 2006-01-06 | 1 | Qld / Southern separation between Bulli Creek and Tarong with 9908 AND (9901 and 9902 or both Braemar 330/275kV transformers or 8814 and 8815), Millmerran Lower 6 sec Requirement = 0
F_STHN+MI_ISLE_L60 | 2006-01-06 | 1 | Qld / Southern separation between Bulli Creek and Tarong with 9908 AND (9901 and 9902 or both Braemar 330/275kV transformers or 8814 and 8815), Millmerran Lower 60 sec Requirement = 0
F_STHN+MI_ISLE_LREG | 2006-01-06 | 1 | Qld / Southern separation between Bulli Creek and Tarong with 9908 AND (9901 and 9902 or both Braemar 330/275kV transformers or 8814 and 8815), Millmerran Lower Regulation Requirement = 0
F_STHN+MI_ISLE_R5 | 2006-01-06 | 1 | Qld / Southern separation between Bulli Creek and Tarong with 9908 AND (9901 and 9902 or both Braemar 330/275kV transformers or 8814 and 8815), Millmerran Raise 5 min Requirement = 0
F_STHN+MI_ISLE_R6 | 2006-01-06 | 1 | Qld / Southern separation between Bulli Creek and Tarong with 9908 AND (9901 and 9902 or both Braemar 330/275kV transformers or 8814 and 8815), Millmerran Raise 6 sec Requirement = 0
F_STHN+MI_ISLE_R60 | 2006-01-06 | 1 | Qld / Southern separation between Bulli Creek and Tarong with 9908 AND (9901 and 9902 or both Braemar 330/275kV transformers or 8814 and 8815), Millmerran Raise 60 sec Requirement = 0
F_STHN+MI_ISLE_RREG | 2006-01-06 | 1 | Qld / Southern separation between Bulli Creek and Tarong with 9908 AND (9901 and 9902 or both Braemar 330/275kV transformers or 8814 and 8815), Millmerran Raise Regulation Requirement = 0
F_STHN+ML_L5_0300 | 2009-01-01 | 1 | Lower 5 min requirement for a Southern Load Event, ML = 300
F_STHN+ML_L60_0300 | 2008-07-01 | 1 | Lower 60 sec requirement for a Southern Load Event, ML = 300
F_STHN+ML_L6_0300 | 2008-07-01 | 1 | Lower 6 sec requirement for a Southern Load Event, ML = 300
F_STHN+RREG_0100 | 2008-07-01 | 1 | Southern Raise Regulation Requirement greater than 100 MW
F_STHN+RREG_0130 | 2008-07-01 | 1 | Southern Raise Regulation Requirement greater than 130 MW
F_STHN+RREG_0200 | 2008-07-01 | 1 | Southern Raise Regulation Requirement greater than 200 MW
F_STHN+RREG_0250 | 2008-07-01 | 1 | Southern Raise Regulation Requirement greater than 250 MW
F_STHN+TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Southern Network Event, TG = 500
F_STHN+TG_R5_0700 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Southern Network Event, TG = 700
F_STHN+TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Southern Network Event, TG = 1000
F_STHN+TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Southern Network Event, TG = 1400
F_STHN+TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Southern Network Event, TG = 1600
F_STHN+TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Southern Network Event, TG = 2000
F_STHN+TG_R5_2800 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Southern Network Event, TG = 2800
F_STHN+TG_R60_0500 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Southern Network Event, TG = 500
F_STHN+TG_R60_0700 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Southern Network Event, TG = 700
F_STHN+TG_R60_1000 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Southern Network Event, TG = 1000
F_STHN+TG_R60_1400 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Southern Network Event, TG = 1400
F_STHN+TG_R60_1600 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Southern Network Event, TG = 1600
F_STHN+TG_R60_2000 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Southern Network Event, TG = 2000
F_STHN+TG_R60_2800 | 2008-08-22 | 1 | Raise 60 sec Service Requirement for a Southern Network Event, TG = 2800
F_STHN+TG_R6_0500 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Southern Network Event, TG = 500
F_STHN+TG_R6_0700 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Southern Network Event, TG = 700
F_STHN+TG_R6_1000 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Southern Network Event, TG = 1000
F_STHN+TG_R6_1400 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Southern Network Event, TG = 1400
F_STHN+TG_R6_1600 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Southern Network Event, TG = 1600
F_STHN+TG_R6_2000 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Southern Network Event, TG = 2000
F_STHN+TG_R6_2800 | 2008-08-22 | 1 | Raise 6 sec Service Requirement for a Southern Network Event, TG = 2800
F_STHN+TL_L5_0600 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a Southern Network Event, TL = 600
F_STHN+TL_L5_0800 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a Southern Network Event, TL = 800
F_STHN+TL_L5_1000 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a Southern Network Event, TL = 1000
F_STHN+TL_L60_0600 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a Southern Network Event, TL = 600
F_STHN+TL_L60_0800 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a Southern Network Event, TL = 800
F_STHN+TL_L60_1000 | 2008-07-01 | 1 | Lower 60 sec Service Requirement for a Southern Network Event, TL = 1000
F_STHN+TL_L6_0600 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a Southern Network Event, TL = 600
F_STHN+TL_L6_0800 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a Southern Network Event, TL = 800
F_STHN+TL_L6_1000 | 2008-07-01 | 1 | Lower 6 sec Service Requirement for a Southern Network Event, TL = 1000
F_STHN_MI+MG_R5 | 2009-01-01 | 1 | Raise 5 min Service Requirement for Southern plus Millmerran Generation Event
F_STHN_MI+MG_R6 | 2008-07-01 | 1 | Raise 6 sec Service Requirement for Southern plus Millmerran Generation Event
F_STHN_MI+MG_R60 | 2008-07-01 | 1 | Raise 60 sec Service Requirement for Southern plus Millmerran Generation Event
F_S_LG+MG_R5 | 2009-01-01 | 1 | Raise 5 min Service Requirement for SA minus Ladbroke Grove Generation Event, Separation between Para and South East
F_S_LG+MG_R6 | 2005-12-21 | 1 | Raise 6 sec Service Requirement for SA minus Ladbroke Grove Generation Event, Separation between Para and South East
F_S_LG+MG_R60 | 2005-12-21 | 1 | Raise 60 sec Service Requirement for SA minus Ladbroke Grove Generation Event, Separation between Para and South East
F_S_NPS1_L6 | 2007-03-27 | 1 | Out= NIL, Northern (NPS1) L6 Requirement <= 0MW
F_S_NPS1_L60 | 2007-03-27 | 1 | Out= NIL, Northern (NPS1) L60 Requirement <= 0MW
F_S_NPS1_LREG | 2007-03-27 | 1 | Out= NIL, Northern (NPS1) LREG Requirement <= 0MW
F_S_NPS1_RREG | 2007-03-27 | 1 | Out= NIL, Northern (NPS1) RREG Requirement <= 0MW
F_S_NPS2_L6 | 2007-03-27 | 1 | Out= NIL, Northern (NPS2) L6 Requirement <= 0MW
F_S_NPS2_L60 | 2007-03-27 | 1 | Out= NIL, Northern (NPS2) L60 Requirement <= 0MW
F_S_NPS2_LREG | 2007-03-27 | 1 | Out= NIL, Northern (NPS2) LREG Requirement <= 0MW
F_S_NPS2_RREG | 2007-03-27 | 1 | Out= NIL, Northern (NPS2) RREG Requirement <= 0MW
F_S_PPCCGT_L6 | 2007-03-27 | 1 | Out= NIL, Pelican Point L6 Requirement <= 0MW
F_S_PPCCGT_L60 | 2007-03-27 | 1 | Out= NIL, Pelican Point L60 Requirement <= 0MW
F_S_PPCCGT_LREG | 2007-03-27 | 1 | Out= NIL, Pelican Point LREG Requirement <= 0MW
F_S_PPCCGT_R6 | 2007-03-27 | 1 | Out= NIL, Pelican Point R6 Requirement <= 0MW
F_S_PPCCGT_R60 | 2007-03-27 | 1 | Out= NIL, Pelican Point R60 Requirement <= 0MW
F_S_PPCCGT_RREG | 2007-03-27 | 1 | Out= NIL, Pelican Point RREG Requirement <= 0MW
F_S_PPT_0_L6 | 2008-10-31 | 1 | Pelican Pt Power Station O/S; unit L6=0
F_S_PPT_0_L60 | 2008-10-31 | 1 | Pelican Pt Power Station O/S; unit L60=0
F_S_PPT_0_LREG | 2008-10-31 | 1 | Pelican Pt Power Station O/S; unit LR=0
F_S_PPT_0_R6 | 2008-10-31 | 1 | Pelican Pt Power Station O/S; unit R6=0
F_S_PPT_0_R60 | 2008-10-31 | 1 | Pelican Pt Power Station O/S; unit R60=0
F_S_PPT_0_RREG | 2008-10-31 | 1 | Pelican Pt Power Station O/S; unit RR=0
F_S_TB1_TX_L5 | 2007-03-01 | 1 | Torrens B 1 Transformer O/S; unit L5=0
F_S_TB1_TX_L6 | 2007-03-01 | 1 | Torrens B 1 Transformer O/S; unit L6=0
F_S_TB1_TX_L60 | 2007-03-01 | 1 | Torrens B 1 Transformer O/S; unit L60=0
F_S_TB1_TX_LREG | 2007-03-01 | 1 | Torrens B 1 Transformer O/S; unit LR=0
F_S_TB1_TX_R5 | 2007-03-01 | 1 | Torrens B 1 Transformer O/S; unit R5=0
F_S_TB1_TX_R6 | 2007-03-01 | 1 | Torrens B 1 Transformer O/S; unit R6=0
F_S_TB1_TX_R60 | 2007-03-01 | 1 | Torrens B 1 Transformer O/S; unit R60=0
F_S_TB1_TX_RREG | 2007-03-01 | 1 | Torrens B 1 Transformer O/S; unit RR=0
F_S_TB2_TX_L5 | 2007-03-01 | 1 | Torrens B 2 Transformer O/S; unit L5=0
F_S_TB2_TX_L6 | 2007-03-01 | 1 | Torrens B 2 Transformer O/S; unit L6=0
F_S_TB2_TX_L60 | 2007-03-01 | 1 | Torrens B 2 Transformer O/S; unit L60=0
F_S_TB2_TX_LREG | 2007-03-01 | 1 | Torrens B 2 Transformer O/S; unit LR=0
F_S_TB2_TX_R5 | 2007-03-01 | 1 | Torrens B 2 Transformer O/S; unit R5=0
F_S_TB2_TX_R6 | 2007-03-01 | 1 | Torrens B 2 Transformer O/S; unit R6=0
F_S_TB2_TX_R60 | 2007-03-01 | 1 | Torrens B 2 Transformer O/S; unit R60=0
F_S_TB2_TX_RREG | 2007-03-01 | 1 | Torrens B 2 Transformer O/S; unit RR=0
F_S_TB3_TX_L5 | 2007-03-01 | 1 | Torrens B 3 Transformer O/S; unit L5=0
F_S_TB3_TX_L6 | 2007-03-01 | 1 | Torrens B 3 Transformer O/S; unit L6=0
F_S_TB3_TX_L60 | 2007-03-01 | 1 | Torrens B 3 Transformer O/S; unit L60=0
F_S_TB3_TX_LREG | 2007-03-01 | 1 | Torrens B 3 Transformer O/S; unit LR=0
F_S_TB3_TX_R5 | 2007-03-01 | 1 | Torrens B 3 Transformer O/S; unit R5=0
F_S_TB3_TX_R6 | 2007-03-01 | 1 | Torrens B 3 Transformer O/S; unit R6=0
F_S_TB3_TX_R60 | 2007-03-01 | 1 | Torrens B 3 Transformer O/S; unit R60=0
F_S_TB3_TX_RREG | 2007-03-01 | 1 | Torrens B 3 Transformer O/S; unit RR=0
F_S_TB4_TX_L5 | 2007-03-01 | 1 | Torrens B 4 Transformer O/S; unit L5=0
F_S_TB4_TX_L6 | 2007-03-01 | 1 | Torrens B 4 Transformer O/S; unit L6=0
F_S_TB4_TX_L60 | 2007-03-01 | 1 | Torrens B 4 Transformer O/S; unit L60=0
F_S_TB4_TX_LREG | 2007-03-01 | 1 | Torrens B 4 Transformer O/S; unit LR=0
F_S_TB4_TX_R5 | 2007-03-01 | 1 | Torrens B 4 Transformer O/S; unit R5=0
F_S_TB4_TX_R6 | 2007-03-01 | 1 | Torrens B 4 Transformer O/S; unit R6=0
F_S_TB4_TX_R60 | 2007-03-01 | 1 | Torrens B 4 Transformer O/S; unit R60=0
F_S_TB4_TX_RREG | 2007-03-01 | 1 | Torrens B 4 Transformer O/S; unit RR=0
F_S_TORRB1_L5 | 2007-03-27 | 1 | Out= NIL, Torrens B1 L5 Requirement <= 0MW
F_S_TORRB1_L6 | 2007-03-27 | 1 | Out= NIL, Torrens B1 L6 Requirement <= 0MW
F_S_TORRB1_L60 | 2007-03-27 | 1 | Out= NIL, Torrens B1 L60 Requirement <= 0MW
F_S_TORRB1_LREG | 2007-03-27 | 1 | Out= NIL, Torrens B1 LREG Requirement <= 0MW
F_S_TORRB1_R5 | 2007-03-27 | 1 | Out= NIL, Torrens B1 R5 Requirement <= 0MW
F_S_TORRB1_R6 | 2007-03-27 | 1 | Out= NIL, Torrens B1 R6 Requirement <= 0MW
F_S_TORRB1_R60 | 2007-03-27 | 1 | Out= NIL, Torrens B1 R60 Requirement <= 0MW
F_S_TORRB1_RREG | 2007-03-27 | 1 | Out= NIL, Torrens B1 RREG Requirement <= 0MW
F_S_TORRB2_L5 | 2007-03-27 | 1 | Out= NIL, Torrens B2 L5 Requirement <= 0MW
F_S_TORRB2_L6 | 2007-03-27 | 1 | Out= NIL, Torrens B2 L6 Requirement <= 0MW
F_S_TORRB2_L60 | 2007-03-27 | 1 | Out= NIL, Torrens B2 L60 Requirement <= 0MW
F_S_TORRB2_LREG | 2007-03-27 | 1 | Out= NIL, Torrens B2 LREG Requirement <= 0MW
F_S_TORRB2_R5 | 2007-03-27 | 1 | Out= NIL, Torrens B2 R5 Requirement <= 0MW
F_S_TORRB2_R6 | 2007-03-27 | 1 | Out= NIL, Torrens B2 R6 Requirement <= 0MW
F_S_TORRB2_R60 | 2007-03-27 | 1 | Out= NIL, Torrens B2 R60 Requirement <= 0MW
F_S_TORRB2_RREG | 2007-03-27 | 1 | Out= NIL, Torrens B2 RREG Requirement <= 0MW
F_S_TORRB3_L5 | 2007-03-27 | 1 | Out= NIL, Torrens B3 L5 Requirement <= 0MW
F_S_TORRB3_L6 | 2007-03-27 | 1 | Out= NIL, Torrens B3 L6 Requirement <= 0MW
F_S_TORRB3_L60 | 2007-03-27 | 1 | Out= NIL, Torrens B3 L60 Requirement <= 0MW
F_S_TORRB3_LREG | 2007-03-27 | 1 | Out= NIL, Torrens B3 LREG Requirement <= 0MW
F_S_TORRB3_R5 | 2007-03-27 | 1 | Out= NIL, Torrens B3 R5 Requirement <= 0MW
F_S_TORRB3_R6 | 2007-03-27 | 1 | Out= NIL, Torrens B3 R6 Requirement <= 0MW
F_S_TORRB3_R60 | 2007-03-27 | 1 | Out= NIL, Torrens B3 R60 Requirement <= 0MW
F_S_TORRB3_RREG | 2007-03-27 | 1 | Out= NIL, Torrens B3 RREG Requirement <= 0MW
F_S_TORRB4_L5 | 2007-03-27 | 1 | Out= NIL, Torrens B4 L5 Requirement <= 0MW
F_S_TORRB4_L6 | 2007-03-27 | 1 | Out= NIL, Torrens B4 L6 Requirement <= 0MW
F_S_TORRB4_L60 | 2007-03-27 | 1 | Out= NIL, Torrens B4 L60 Requirement <= 0MW
F_S_TORRB4_LREG | 2007-03-27 | 1 | Out= NIL, Torrens B4 LREG Requirement <= 0MW
F_S_TORRB4_R5 | 2007-03-27 | 1 | Out= NIL, Torrens B4 R5 Requirement <= 0MW
F_S_TORRB4_R6 | 2007-03-27 | 1 | Out= NIL, Torrens B4 R6 Requirement <= 0MW
F_S_TORRB4_R60 | 2007-03-27 | 1 | Out= NIL, Torrens B4 R60 Requirement <= 0MW
F_S_TORRB4_RREG | 2007-03-27 | 1 | Out= NIL, Torrens B4 RREG Requirement <= 0MW
F_T++BB_12_N-2_TGR60 | 2007-08-02 | 1 | Out= Nil, loss of Bell Bay units 1 and 2 declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS
F_T++BB_12_N-2_TG_R5 | 2009-01-01 | 1 | Out= Nil, loss of Bell Bay units 1 and 2 declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS
F_T++BB_N-2_TG_R5 | 2009-01-01 | 1 | Out= Nil, loss of all Bell Bay units declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS
F_T++BB_N-2_TG_R6 | 2007-03-28 | 1 | Out= Nil, loss of all Bell Bay units declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS
F_T++BB_N-2_TG_R60 | 2007-03-28 | 1 | Out= Nil, loss of all Bell Bay units declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS
F_T++BL_CO_N-2_L5 | 2009-01-01 | 1 | Out= Nil, Tasmania Lower 5 min Requirement for loss of Basslink and a Comalco potline declared credible, FCSPS unavailable
F_T++BL_CO_N-2_L6 | 2006-03-01 | 1 | Out= Nil, Tasmania Lower 6 second Requirement for loss of Basslink and a Comalco potline declared credible, FCSPS unavailable
F_T++BL_CO_N-2_L60 | 2006-03-01 | 1 | Out= Nil, Tasmania Lower 60 second Requirement for loss of Basslink and a Comalco potline declared credible, FCSPS unavailable
F_T++COGT_BB_TL_L5 | 2009-01-01 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS
F_T++COGT_BB_TL_L6 | 2006-03-02 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS
F_T++COGT_BB_TL_L60 | 2006-03-02 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS
F_T++COGT_TL_L5 | 2009-01-01 | 1 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS
F_T++COGT_TL_L6 | 2006-01-30 | 1 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS
F_T++COGT_TL_L60 | 2006-01-30 | 1 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS
F_T++CSGO_TG_R5 | 2009-01-01 | 1 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS
F_T++CSGO_TG_R6 | 2006-01-30 | 1 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS
F_T++CSGO_TG_R60 | 2006-01-30 | 1 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS
F_T++FASH1_2B_TG_R5 | 2009-01-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with Tribute and Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_2B_TG_R6 | 2006-12-27 | 1 | Out =either Farrell to Sheffield (1 or 2) line with Tribute and Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_2B_TG_R60 | 2006-12-27 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_2C_TG_R5 | 2009-01-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_2C_TG_R6 | 2007-06-07 | 1 | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_2C_TG_R60 | 2007-06-07 | 1 | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_2D_TG_R5 | 2009-01-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with Bastyan, John Butters, Tribute & Reece 2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_2D_TG_R6 | 2007-11-19 | 2 | Out =either Farrell to Sheffield (1 or 2) line with Bastyan, John Butters, Tribute & Reece 2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_2D_TG_R60 | 2007-11-19 | 2 | Out =either Farrell to Sheffield (1 or 2) line with Bastyan, John Butters, Tribute & Reece 2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_A_TG_R5 | 2009-01-01 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_A_TG_R6 | 2006-01-30 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_A_TG_R60 | 2006-01-30 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_B_TG_R5 | 2009-01-01 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + Reece 1 & 2 + Tribute supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_B_TG_R6 | 2006-05-12 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + Reece 1 & 2 + Tribute supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH1_B_TG_R60 | 2006-05-12 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + Reece 1 & 2 + Tribute supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH2_A_TG_R5 | 2009-01-01 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH2_A_TG_R6 | 2006-01-30 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH2_A_TG_R60 | 2006-01-30 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH_N-2_TG_R5 | 2009-01-01 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH_N-2_TG_R6 | 2006-01-30 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FASH_N-2_TG_R60 | 2006-01-30 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS
F_T++FCSPS_BL_L5 | 2009-01-01 | 1 | Out = Basslink FCSPS, Tasmania Lower 5 min Requirement for loss of Basslink, Pre-Dispatch only
F_T++FCSPS_BL_L6 | 2006-03-22 | 1 | Out = Basslink FCSPS, Tasmania Lower 6 second Requirement for loss of Basslink, Pre-Dispatch only
F_T++FCSPS_BL_L60 | 2006-03-22 | 1 | Out = Basslink FCSPS, Tasmania Lower 60 second Requirement for loss of Basslink, Pre-Dispatch only
F_T++FCSPS_BL_R5 | 2009-01-01 | 1 | Out = Basslink FCSPS, Tasmania Raise 5 min Requirement for loss of Basslink, Pre-Dispatch only
F_T++FCSPS_BL_R6 | 2006-01-06 | 1 | Out = Basslink FCSPS, Tasmania Raise 6 second Requirement for loss of Basslink, Pre-Dispatch only
F_T++FCSPS_BL_R60 | 2006-01-06 | 1 | Out = Basslink FCSPS, Tasmania Raise 60 second Requirement for loss of Basslink, Pre-Dispatch only
F_T++GO_A752_TG_R5 | 2009-01-01 | 1 | Out= Gordon CB A752, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS
F_T++GO_A752_TG_R6 | 2007-03-20 | 1 | Out= Gordon CB A752, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS
F_T++GO_A752_TG_R60 | 2007-03-20 | 1 | Out= Gordon CB A752, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS
F_T++GO_C752_TG_R5 | 2009-01-01 | 1 | Out= Gordon CB C752, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS
F_T++GO_C752_TG_R6 | 2007-04-04 | 1 | Out= Gordon CB C752, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS
F_T++GO_C752_TG_R60 | 2007-04-04 | 1 | Out= Gordon CB C752, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS
F_T++GT_TX_TG_R5 | 2009-01-01 | 1 | Out = one George Town 220/110kV transformer, Tasmania Raise 5 min requirement for loss of the remaining George Town transformer, Basslink able to transfer FCAS
F_T++GT_TX_TG_R6 | 2006-03-27 | 1 | Out = one George Town 220/110kV transformer, Tasmania Raise 6 sec requirement for loss of the remaining George Town transformer, Basslink able to transfer FCAS
F_T++GT_TX_TG_R60 | 2006-03-27 | 1 | Out = one George Town 220/110kV transformer, Tasmania Raise 60 sec requirement for loss of the remaining George Town transformer, Basslink able to transfer FCAS
F_T++LREG_0025 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 25 MW, Basslink able transfer FCAS
F_T++LREG_0030 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 30 MW, Basslink able transfer FCAS
F_T++LREG_0035 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 35 MW, Basslink able transfer FCAS
F_T++LREG_0040 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 40 MW, Basslink able transfer FCAS
F_T++LREG_0050 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS
F_T++LREG_0060 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 60 MW, Basslink able transfer FCAS
F_T++LREG_0070 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 70 MW, Basslink able transfer FCAS
F_T++LREG_0080 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 80 MW, Basslink able transfer FCAS
F_T++LREG_0090 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 90 MW, Basslink able transfer FCAS
F_T++LREG_0100 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 100 MW, Basslink able transfer FCAS
F_T++NIL_BB_TG_R5 | 2009-01-01 | 1 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Bell Bay to George Town line, Basslink able to transfer FCAS
F_T++NIL_BB_TG_R6 | 2006-09-01 | 1 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink able to transfer FCAS
F_T++NIL_BB_TG_R60 | 2006-09-01 | 1 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink able to transfer FCAS
F_T++NIL_BL_L5 | 2009-01-01 | 1 | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable
F_T++NIL_BL_L6 | 2007-09-14 | 1 | Tasmania Lower 6 second Requirement for loss of Basslink, FCSPS unavailable
F_T++NIL_BL_L60 | 2007-09-14 | 1 | Tasmania Lower 60 second Requirement for loss of Basslink, FCSPS unavailable
F_T++NIL_BL_R5 | 2009-01-01 | 1 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS unavailable
F_T++NIL_BL_R6 | 2006-05-17 | 1 | Tasmania Raise 6 second Requirement for loss of Basslink, FCSPS unavailable
F_T++NIL_BL_R60 | 2006-05-17 | 1 | Tasmania Raise 60 second Requirement for loss of Basslink, FCSPS unavailable
F_T++NIL_MG_R5 | 2009-01-01 | 1 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS
F_T++NIL_MG_R6 | 2006-01-24 | 1 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS
F_T++NIL_MG_R60 | 2006-01-24 | 1 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS
F_T++NIL_ML_L5 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS
F_T++NIL_ML_L6 | 2006-01-24 | 1 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS
F_T++NIL_ML_L60 | 2006-01-24 | 1 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS
F_T++NIL_TL_L5 | 2009-01-01 | 1 | Out=Nil, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS
F_T++NIL_TL_L6 | 2006-01-24 | 1 | Out=Nil, Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS
F_T++NIL_TL_L60 | 2008-08-22 | 1 | Out=Nil, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS
F_T++NIL_WN_TG_R5 | 2009-01-01 | 1 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS
F_T++NIL_WN_TG_R6 | 2008-12-01 | 1 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS
F_T++NIL_WN_TG_R60 | 2008-12-01 | 1 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS
F_T++NTH_BB_TG_R5 | 2009-02-10 | 1 | Raise 5 min requirement for North Tasmania for loss of a Bell Bay to George Town line, Basslink able to transfer FCAS
F_T++NTH_BB_TG_R6 | 2009-02-10 | 1 | Raise 6 sec requirement for North Tasmania for loss of a Bell Bay to George Town line, Basslink able to transfer FCAS
F_T++NTH_BB_TG_R60 | 2009-02-10 | 1 | Raise 60 sec requirement for North Tasmania for loss of a Bell Bay to George Town line, Basslink able to transfer FCAS
F_T++NTH_LREG | 2009-02-10 | 1 | Lower Regulation requirement for Northern Tasmania, Basslink able to transfer FCAS
F_T++NTH_MG_R5 | 2009-02-10 | 1 | Raise 5 min requirement for a North Tasmania Generation Event, Basslink able to transfer FCAS
F_T++NTH_MG_R6 | 2009-02-10 | 1 | Raise 6 sec requirement for a North Tasmania Generation Event, Basslink able to transfer FCAS
F_T++NTH_MG_R60 | 2009-02-10 | 1 | Raise 60 sec requirement for a North Tasmania Generation Event, Basslink able to transfer FCAS
F_T++NTH_ML_L5 | 2009-02-10 | 1 | Lower 5 min requirement for a North Tasmania Load Event, Basslink able to transfer FCAS
F_T++NTH_ML_L6 | 2009-02-10 | 1 | Lower 6 sec requirement for a North Tasmania Load Event, Basslink able to transfer FCAS
F_T++NTH_ML_L60 | 2009-02-10 | 1 | Lower 60 sec requirement for a North Tasmania Load Event, Basslink able to transfer FCAS
F_T++NTH_RREG | 2009-02-10 | 1 | Raise Regulation requirement for Northern Tasmania, Basslink able to transfer FCAS
F_T++NTH_TL_L5 | 2009-02-10 | 1 | Lower 5 min requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS
F_T++NTH_TL_L6 | 2009-02-10 | 1 | Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS
F_T++NTH_TL_L60 | 2009-02-10 | 1 | Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS
F_T++NTH_WN_TG_R5 | 2009-02-10 | 1 | Raise 5 min requirement for North Tasmania for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS
F_T++NTH_WN_TG_R6 | 2009-02-10 | 1 | Raise 6 sec requirement for North Tasmania for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS
F_T++NTH_WN_TG_R60 | 2009-02-10 | 1 | Raise 60 sec requirement for North Tasmania for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS
F_T++RREG_0025 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 25 MW, Basslink able transfer FCAS
F_T++RREG_0030 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 30 MW, Basslink able transfer FCAS
F_T++RREG_0035 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 35 MW, Basslink able transfer FCAS
F_T++RREG_0040 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 40 MW, Basslink able transfer FCAS
F_T++RREG_0050 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS
F_T++RREG_0060 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 60 MW, Basslink able transfer FCAS
F_T++RREG_0070 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 70 MW, Basslink able transfer FCAS
F_T++RREG_0080 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 80 MW, Basslink able transfer FCAS
F_T++RREG_0090 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 90 MW, Basslink able transfer FCAS
F_T++RREG_0100 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 100 MW, Basslink able transfer FCAS
F_T++X_TATUBG_TG_R5 | 2009-01-01 | 1 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible, Tasmania Raise 5 min requirement for loss of the remaining Tungatinah to Waddamana line, Basslink able to transfer FCAS
F_T++X_TATUBG_TG_R6 | 2006-07-28 | 3 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible, Tasmania Raise 6 sec requirement for loss of the remaining Tungatinah to Waddamana line, Basslink able to transfer FCAS
F_T++X_TATUBG_TG_R60 | 2006-07-28 | 3 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible, Tasmania Raise 60 sec requirement for loss of the remaining Tungatinah to Waddamana line, Basslink able to transfer FCAS
F_T+BB_12_N-2_R5 | 2007-08-02 | 1 | Out = Nil, loss of Bell Bay units 1 and 2 declared credible, Bell Bay Raise 5 min Requirement = 0
F_T+BB_12_N-2_RREG | 2007-08-02 | 1 | Out = Nil, loss of Bell Bay units 1 and 2 declared credible, Bell Bay Raise Regulation Requirement = 0
F_T+BB_12_N-2_TG_R5 | 2009-01-01 | 1 | Out= Nil, loss of Bell Bay units 1 and 2 declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS
F_T+BB_12_N-2_TG_R60 | 2007-08-02 | 1 | Out= Nil, loss of Bell Bay units 1 and 2 declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS
F_T+BB_N-2_R5 | 2007-03-28 | 1 | Out = Nil, loss of all Bell Bay units declared credible, Bell Bay Raise 5 min Requirement = 0
F_T+BB_N-2_R6 | 2007-03-28 | 1 | Out = Nil, all Bell Bay units declared credible, Bell Bay Raise 6 second Requirement = 0
F_T+BB_N-2_RREG | 2007-03-28 | 1 | Out = Nil, all Bell Bay units declared credible, Bell Bay Raise Regulation Requirement = 0
F_T+BB_N-2_TG_R5 | 2009-01-01 | 1 | Out= Nil, all of both Bell Bay units declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS
F_T+BB_N-2_TG_R6 | 2007-03-28 | 1 | Out= Nil, all of both Bell Bay units declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS
F_T+BB_N-2_TG_R60 | 2007-03-28 | 1 | Out= Nil, all of both Bell Bay units declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS
F_T+BL_CO_N-2_L5 | 2009-01-01 | 1 | Out= Nil, Tasmania Lower 5 min Requirement for loss of Basslink and a Comalco potline declared credible, FCSPS available
F_T+BL_CO_N-2_L6 | 2006-03-01 | 1 | Out= Nil, Tasmania Lower 6 second Requirement for loss of Basslink and a Comalco potline declared credible FCSPS available
F_T+BL_CO_N-2_L60 | 2006-03-01 | 1 | Out= Nil, Tasmania Lower 60 second Requirement for loss of Basslink and a Comalco potline declared credible, FCSPS available
F_T+BUHM_LREG | 2006-11-09 | 2 | Out = Burnie-Hampshire 110 kV line and one Farrell-Sheffield 220 kV line or reclassification of the loss of both FA-SH lines as a credible contingency, West Coast generation Lower Regulation Requirement = 0
F_T+BUHM_RREG | 2006-11-09 | 2 | Out = Burnie-Hampshire 110 kV line and one Farrell-Sheffield 220 kV line or reclassification of the loss of both FA-SH lines as a credible contingency, West Coast generation Raise Regulation Requirement = 0
F_T+COGT_BB_TL_L5 | 2009-01-01 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS
F_T+COGT_BB_TL_L6 | 2006-03-02 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS
F_T+COGT_BB_TL_L60 | 2006-03-02 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS
F_T+COGT_TL_L5 | 2009-01-01 | 1 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS
F_T+COGT_TL_L6 | 2006-01-30 | 1 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS
F_T+COGT_TL_L60 | 2006-01-30 | 1 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS
F_T+CSGO_TG_R5 | 2009-01-01 | 1 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS
F_T+CSGO_TG_R6 | 2006-01-30 | 1 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS
F_T+CSGO_TG_R60 | 2006-01-30 | 1 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS
F_T+FASH1_1_2_B_LREG | 2006-12-27 | 1 | Out = Farrell to Sheffield No.1 or 2 line; Bastyan, John Butters and Mackintosh unavailable for lower FCAS
F_T+FASH1_1_2_B_R5 | 2006-12-22 | 1 | Out = Farrell to Sheffield No.1 or 2 line; Reece 1, 2 and Tribute unavailable for raise FCAS
F_T+FASH1_1_2_B_R6 | 2006-12-22 | 1 | Out = Farrell to Sheffield No.1 or 2 line; Reece 1, 2 and Tribute unavailable for raise FCAS
F_T+FASH1_1_2_B_R60 | 2006-12-22 | 1 | Out = Farrell to Sheffield No.1 or 2 line; Reece 1, 2 and Tribute unavailable for raise FCAS
F_T+FASH1_1_2_B_RREG | 2006-12-27 | 1 | Out = Farrell to Sheffield No.1 or 2 line; Reece 1, 2 and Tribute unavailable for raise FCAS
F_T+FASH1_2B_TG_R5 | 2009-01-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with Tribute and Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_2B_TG_R6 | 2006-12-27 | 1 | Out = either Farrell to Sheffield (1 or 2) line with Tribute and Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_2B_TG_R60 | 2006-12-27 | 1 | Out = either Farrell to Sheffield (1 or 2) line with Tribute and Reece 1,2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_2C_LREG | 2007-06-07 | 1 | Out = Farrell to Sheffield No.1 or 2 line; Bastyan and Mackintosh unavailable for lower FCAS
F_T+FASH1_2C_R5 | 2007-06-07 | 1 | Out = Farrell to Sheffield No.1 or 2 line; John Butters, Tribute and Reece 1, 2 unavailable for raise FCAS
F_T+FASH1_2C_R6 | 2007-06-07 | 1 | Out = Farrell to Sheffield No.1 or 2 line; John Butters, Tribute and Reece 1, 2 unavailable for raise FCAS
F_T+FASH1_2C_R60 | 2007-06-07 | 1 | Out = Farrell to Sheffield No.1 or 2 line; John Butters, Tribute and Reece 1, 2 unavailable for raise FCAS
F_T+FASH1_2C_RREG | 2007-06-07 | 1 | Out = Farrell to Sheffield No.1 or 2 line; John Butters, Tribute and Reece 1, 2 unavailable for raise FCAS
F_T+FASH1_2C_TG_R5 | 2009-01-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_2C_TG_R6 | 2007-06-07 | 1 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_2C_TG_R60 | 2007-06-07 | 1 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_2D_LREG | 2007-11-19 | 2 | Out = Farrell to Sheffield No.1 or 2 line; Reece 1 and Mackintosh unavailable for lower FCAS
F_T+FASH1_2D_R5 | 2007-11-19 | 2 | Out = Farrell to Sheffield No.1 or 2 line; Bastyan, John Butters, Tribute and Reece 2 unavailable for raise FCAS
F_T+FASH1_2D_R6 | 2007-11-19 | 2 | Out = Farrell to Sheffield No.1 or 2 line; Bastyan, John Butters, Tribute and Reece 2 unavailable for raise FCAS
F_T+FASH1_2D_R60 | 2007-11-19 | 2 | Out = Farrell to Sheffield No.1 or 2 line; Bastyan, John Butters, Tribute and Reece 2 unavailable for raise FCAS
F_T+FASH1_2D_RREG | 2007-11-19 | 3 | Out = Farrell to Sheffield No.1 or 2 line; Bastyan, John Butters, Tribute, Mackintosh and Reece 1,2 unavailable for raise FCAS
F_T+FASH1_2D_TG_R5 | 2009-01-01 | 1 | Out = either Farrell to Sheffield (1 or 2) line with Bastyan, John Butters, Tribute & Reece 2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_2D_TG_R6 | 2007-11-19 | 2 | Out = either Farrell to Sheffield (1 or 2) line with Bastyan, John Butters, Tribute & Reece 2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_2D_TG_R60 | 2007-11-19 | 2 | Out = either Farrell to Sheffield (1 or 2) line with Bastyan, John Butters, Tribute & Reece 2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_A_LREG | 2006-06-14 | 1 | Out = Farrell to Sheffield No.1 line, Reece 1, Mackintosh and Tribute Lower Regulation Requirement = 0, Note Farrell 220kV bus configured as per Limits advice 7 June 2006
F_T+FASH1_A_R5 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.1 line, Bastyan, Reece 2 and Tribute Raise 5 min Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH1_A_R6 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.1 line, Bastyan, Reece 2 and Tribute Raise 6 second Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH1_A_R60 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.1 line, Bastyan, Reece 2 and Tribute Raise 60 second Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH1_A_RREG | 2006-06-14 | 1 | Out = Farrell to Sheffield No.1 line, Bastyan, Reece 1& 2, John Butters, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as per Limits advice 7 June 2006
F_T+FASH1_A_TG_R5 | 2009-01-01 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_A_TG_R6 | 2006-01-30 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_A_TG_R60 | 2006-01-30 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_B_R5 | 2006-01-12 | 1 | Out = Farrell to Sheffield No.1 line, Bastyan, Reece 1 & 2 and Tribute Raise 5 min Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH1_B_R6 | 2006-01-12 | 1 | Out = Farrell to Sheffield No.1 line, Bastyan, Reece 1 & 2 and Tribute Raise 6 second Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH1_B_R60 | 2006-01-12 | 1 | Out = Farrell to Sheffield No.1 line, Bastyan, Reece 1 & 2 and Tribute Raise 60 second Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH1_B_RREG | 2006-01-12 | 1 | Out = Farrell to Sheffield No.1 line, Bastyan, Reece 1 & 2 and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH1_B_TG_R5 | 2009-01-01 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + Reece 1 & 2 + Tribute supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_B_TG_R6 | 2006-05-12 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + Reece 1 & 2 + Tribute supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH1_B_TG_R60 | 2006-05-12 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + Reece 1 & 2 + Tribute supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH2_A_LREG | 2006-06-14 | 1 | Out = Farrell to Sheffield No.2 line, Bastyan, Reece 2, John Butters and Mackintosh Lower Regulation Requirement = 0, Note Farrell 220kV bus configured as per Limits advice 7 June 2006
F_T+FASH2_A_R5 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Tribute and Reece 1 Raise 5 min Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH2_A_R6 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Tribute and Reece 1 Raise 6 second Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH2_A_R60 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Tribute and Reece 1 Raise 60 second Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH2_A_RREG | 2006-06-14 | 1 | Out = Farrell to Sheffield No.2 line, Bastyan, Reece 1& 2, John Butters, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as per Limits advice 7 June 2006
F_T+FASH2_A_TG_R5 | 2009-01-01 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH2_A_TG_R6 | 2006-01-30 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH2_A_TG_R60 | 2006-01-30 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH_N-2_LREG | 2006-06-14 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Reece 1, Mackintosh and Tribute Lower Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006
F_T+FASH_N-2_R5 | 2006-01-06 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters and Reece 2 Raise 5 min Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH_N-2_R6 | 2006-01-06 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters and Reece 2 Raise 6 sec Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH_N-2_R60 | 2006-01-06 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters and Reece 2 Raise 60 sec Requirement = 0, Note Farrell 220kV bus configured as per OAN 180
F_T+FASH_N-2_RREG | 2006-06-14 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006
F_T+FASH_N-2_TG_R5 | 2009-01-01 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH_N-2_TG_R6 | 2006-01-30 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+FASH_N-2_TG_R60 | 2006-01-30 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS
F_T+GO_A752_TG_R5 | 2009-01-01 | 1 | Out= Gordon CB A752, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS
F_T+GO_A752_TG_R6 | 2007-03-20 | 1 | Out= Gordon CB A752, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS
F_T+GO_A752_TG_R60 | 2007-03-20 | 1 | Out= Gordon CB A752, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS
F_T+GO_C752_TG_R5 | 2009-01-01 | 1 | Out= Gordon CB C752, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS
F_T+GO_C752_TG_R6 | 2007-04-04 | 1 | Out= Gordon CB C752, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS
F_T+GO_C752_TG_R60 | 2007-04-04 | 1 | Out= Gordon CB C752, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS
F_T+GT_TX_TG_R5 | 2009-01-01 | 1 | Out = one George Town 220/110kV transformer, Tasmania Raise 5 min requirement for loss of the remaining George Town transformer, Basslink unable to transfer FCAS
F_T+GT_TX_TG_R6 | 2006-03-27 | 1 | Out = one George Town 220/110kV transformer, Tasmania Raise 6 sec requirement for loss of the remaining George Town transformer, Basslink unable to transfer FCAS
F_T+GT_TX_TG_R60 | 2006-03-27 | 1 | Out = one George Town 220/110kV transformer, Tasmania Raise 60 sec requirement for loss of the remaining George Town transformer, Basslink unable to transfer FCAS
F_T+LREG_0025 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 25 MW, Basslink unable to transfer FCAS
F_T+LREG_0030 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 30 MW, Basslink unable to transfer FCAS
F_T+LREG_0035 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 35 MW, Basslink unable to transfer FCAS
F_T+LREG_0040 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 40 MW, Basslink unable to transfer FCAS
F_T+LREG_0050 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS
F_T+LREG_0060 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 60 MW, Basslink unable to transfer FCAS
F_T+LREG_0070 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 70 MW, Basslink unable to transfer FCAS
F_T+LREG_0080 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 80 MW, Basslink unable to transfer FCAS
F_T+LREG_0090 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 90 MW, Basslink unable to transfer FCAS
F_T+LREG_0100 | 2006-01-24 | 1 | Tasmania Lower Regulation Requirement greater than 100 MW, Basslink unable to transfer FCAS
F_T+NIL_BB_TG_R5 | 2009-01-01 | 1 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS
F_T+NIL_BB_TG_R6 | 2006-09-01 | 1 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS
F_T+NIL_BB_TG_R60 | 2006-09-01 | 1 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS
F_T+NIL_BL_L5 | 2009-01-01 | 1 | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS available
F_T+NIL_BL_L6 | 2007-09-14 | 1 | Tasmania Lower 6 second Requirement for loss of Basslink FCSPS available
F_T+NIL_BL_L60 | 2007-09-14 | 1 | Tasmania Lower 60 second Requirement for loss of Basslink, FCSPS available
F_T+NIL_BL_R5 | 2009-01-01 | 1 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS available
F_T+NIL_BL_R6 | 2006-05-17 | 1 | Tasmania Raise 6 second Requirement for loss of Basslink, FCSPS available
F_T+NIL_BL_R60 | 2006-05-17 | 1 | Tasmania Raise 60 second Requirement for loss of Basslink, FCSPS available
F_T+NIL_MG_R5 | 2009-01-01 | 1 | Out = Nil, Raise 5 min requirement for a Tasmania Generation, Basslink unable to transfer FCAS
F_T+NIL_MG_R6 | 2006-01-24 | 1 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink unable to transfer FCAS
F_T+NIL_MG_R60 | 2006-01-24 | 1 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink unable to transfer FCAS
F_T+NIL_ML_L5 | 2009-01-01 | 1 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS
F_T+NIL_ML_L6 | 2006-01-24 | 1 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS
F_T+NIL_ML_L60 | 2006-01-24 | 1 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS
F_T+NIL_TL_L5 | 2009-01-01 | 1 | Out=Nil, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS
F_T+NIL_TL_L6 | 2006-01-24 | 1 | Out=Nil ,Tasmania Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS
F_T+NIL_TL_L60 | 2006-01-24 | 1 | Out=Nil, Tasmania Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS
F_T+NIL_WN_TG_R5 | 2009-01-01 | 1 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth line, Basslink unable to transfer FCAS
F_T+NIL_WN_TG_R6 | 2008-12-01 | 1 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth line, Basslink unable to transfer FCAS
F_T+NIL_WN_TG_R60 | 2008-12-01 | 1 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth line, Basslink unable to transfer FCAS
F_T+NTH_BB_TG_R5 | 2009-02-10 | 1 | Raise 5 min requirement for North Tasmania for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS
F_T+NTH_BB_TG_R6 | 2009-02-10 | 1 | Raise 6 sec requirement for North Tasmania for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS
F_T+NTH_BB_TG_R60 | 2009-02-10 | 1 | Raise 60 sec requirement for North Tasmania for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS
F_T+NTH_LREG | 2009-02-10 | 1 | Lower Regulation requirement for Northern Tasmania, Basslink unable to transfer FCAS
F_T+NTH_MG_R5 | 2009-02-10 | 1 | Raise 5 min requirement for a North Tasmania Generation Event, Basslink unable to transfer FCAS
F_T+NTH_MG_R6 | 2009-02-10 | 1 | Raise 6 sec requirement for a North Tasmania Generation Event, Basslink unable to transfer FCAS
F_T+NTH_MG_R60 | 2009-02-10 | 1 | Raise 60 sec requirement for a North Tasmania Generation Event, Basslink unable to transfer FCAS
F_T+NTH_ML_L5 | 2009-02-10 | 1 | Lower 5 min requirement for a North Tasmania Load Event, Basslink unable to transfer FCAS
F_T+NTH_ML_L6 | 2009-02-10 | 1 | Lower 6 sec requirement for a North Tasmania Load Event, Basslink unable to transfer FCAS
F_T+NTH_ML_L60 | 2009-02-10 | 1 | Lower 60 sec requirement for a North Tasmania Load Event, Basslink unable to transfer FCAS
F_T+NTH_RREG | 2009-02-10 | 1 | Raise Regulation requirement for Northern Tasmania, Basslink unable to transfer FCAS
F_T+NTH_TL_L5 | 2009-02-10 | 1 | Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS
F_T+NTH_TL_L6 | 2009-02-10 | 1 | Lower 6 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS
F_T+NTH_TL_L60 | 2009-02-10 | 1 | Lower 60 sec requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS
F_T+NTH_WN_TG_R5 | 2009-02-10 | 1 | Raise 5 min requirement for North Tasmania for loss of a Smithton to Woolnorth line, Basslink unable to transfer FCAS
F_T+NTH_WN_TG_R6 | 2009-02-10 | 1 | Raise 6 sec requirement for North Tasmania for loss of a Smithton to Woolnorth line, Basslink unable to transfer FCAS
F_T+NTH_WN_TG_R60 | 2009-02-10 | 1 | Raise 60 sec requirement for North Tasmania for loss of a Smithton to Woolnorth line, Basslink unable to transfer FCAS
F_T+RREG_0025 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 25 MW, Basslink unable to transfer FCAS
F_T+RREG_0030 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 30 MW, Basslink unable to transfer FCAS
F_T+RREG_0035 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 35 MW, Basslink unable to transfer FCAS
F_T+RREG_0040 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 40 MW, Basslink unable to transfer FCAS
F_T+RREG_0050 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS
F_T+RREG_0060 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 60 MW, Basslink unable to transfer FCAS
F_T+RREG_0070 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 70 MW, Basslink unable to transfer FCAS
F_T+RREG_0080 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 80 MW, Basslink unable to transfer FCAS
F_T+RREG_0090 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 90 MW, Basslink unable to transfer FCAS
F_T+RREG_0100 | 2006-01-24 | 1 | Tasmania Raise Regulation Requirement greater than 100 MW, Basslink unable to transfer FCAS
F_T+STH_LREG | 2009-02-10 | 1 | Lower Regulation requirement for Southern Tasmania
F_T+STH_MG_R5 | 2009-02-10 | 1 | Raise 5 min requirement for a South Tasmania Generation Event
F_T+STH_MG_R6 | 2009-02-10 | 1 | Raise 6 sec requirement for a South Tasmania Generation Event
F_T+STH_MG_R60 | 2009-02-10 | 1 | Raise 60 sec requirement for a South Tasmania Generation Event
F_T+STH_ML_L5 | 2009-02-10 | 1 | Lower 5 min requirement for a South Tasmania Load Event
F_T+STH_ML_L6 | 2009-02-10 | 1 | Lower 6 sec requirement for a South Tasmania Load Event
F_T+STH_ML_L60 | 2009-02-10 | 1 | Lower 60 sec requirement for a South Tasmania Load Event
F_T+STH_RREG | 2009-02-10 | 1 | Raise Regulation requirement for Southern Tasmania
F_T+T_COGT_BB_L5 | 2006-03-02 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Bell Bay Lower 5 min requirement = 0
F_T+T_COGT_BB_L6 | 2006-03-02 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Bell Bay Lower 6 sec requirement = 0
F_T+T_COGT_BB_L60 | 2006-03-02 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Bell Bay Lower 60 sec requirement = 0
F_T+T_COGT_BB_LREG | 2006-03-02 | 1 | Out = one Comalco to George Town line, Bell Bay tripping scheme armed, Bell Bay Lower Regulation requirement = 0
F_T+T_CSGO_R5 | 2005-05-16 | 1 | Out = one Chapel St to Gordon line, Gordon Raise 5 min Requirement = 0
F_T+T_CSGO_R6 | 2005-05-16 | 1 | Out = one Chapel St to Gordon line, Gordon Raise 6 second Requirement = 0
F_T+T_CSGO_R60 | 2005-05-16 | 1 | Out = one Chapel St to Gordon line, Gordon Raise 60 second Requirement = 0
F_T+T_CSGO_RREG | 2005-05-16 | 1 | Out = one Chapel St to Gordon line, Gordon Raise Regulation Requirement = 0
F_T+T_GO_A752_R5 | 2007-03-20 | 1 | Out= Gordon CB A752, Gordon Raise 5 min Requirement = 0
F_T+T_GO_A752_R6 | 2007-03-20 | 1 | Out= Gordon CB A752, Gordon Raise 6 second Requirement = 0
F_T+T_GO_A752_R60 | 2007-03-20 | 1 | Out= Gordon CB A752, Gordon Raise 60 second Requirement = 0
F_T+T_GO_A752_RREG | 2007-03-20 | 1 | Out= Gordon CB A752, Gordon Raise Regulation Requirement = 0
F_T+T_GO_C752_R5 | 2007-04-04 | 1 | Out= Gordon CB C752, Gordon Raise 5 min Requirement = 0
F_T+T_GO_C752_R6 | 2007-04-04 | 1 | Out= Gordon CB C752, Gordon Raise 6 second Requirement = 0
F_T+T_GO_C752_R60 | 2007-04-04 | 1 | Out= Gordon CB C752, Gordon Raise 60 second Requirement = 0
F_T+T_GO_C752_RREG | 2007-04-04 | 1 | Out= Gordon CB C752, Gordon Raise Regulation Requirement = 0
F_T+T_GT_TX_R5 | 2006-03-27 | 1 | Out = one George Town 220/110kV transformer, Bell Bay Raise 5 min requirement = 0
F_T+T_GT_TX_R6 | 2006-03-27 | 1 | Out = one George Town 220/110kV transformer, Bell Bay Raise 6 sec requirement = 0
F_T+T_GT_TX_R60 | 2006-03-27 | 1 | Out = one George Town 220/110kV transformer, Bell Bay Raise 60 sec requirement = 0
F_T+T_GT_TX_RREG | 2006-03-27 | 1 | Out = one George Town 220/110kV transformer, Bell Bay Raise Regulation requirement = 0
F_T+T_X_TATUBG_R5 | 2006-07-28 | 3 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible,; Tungatinah and Lake Echo Raise 5 min Requirement = 0
F_T+T_X_TATUBG_R6 | 2006-07-28 | 3 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible,; Tungatinah and Lake Echo Raise 6 second Requirement = 0
F_T+T_X_TATUBG_R60 | 2006-07-28 | 3 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible,; Tungatinah and Lake Echo Raise 60 second Requirement = 0
F_T+T_X_TATUBG_RREG | 2006-07-28 | 3 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible,; Tungatinah and Lake Echo Raise Regulation Requirement = 0
F_T+X_TATUBG_TG_R5 | 2009-01-01 | 1 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible, Tasmania Raise 5 min requirement for loss of the remaining Tungatinah to Waddamana line, Basslink unable to transfer FCAS
F_T+X_TATUBG_TG_R6 | 2006-07-28 | 3 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible, Tasmania Raise 6 sec requirement for loss of the remaining Tungatinah to Waddamana line, Basslink unable to transfer FCAS
F_T+X_TATUBG_TG_R60 | 2006-07-28 | 3 | Out= Lake Echo PS, loss of Tarraleah + Tungatinah + Butlers Gorge credible, Tasmania Raise 60 sec requirement for loss of the remaining Tungatinah to Waddamana line, Basslink unable to transfer FCAS
F_T_BASTYAN_L5 | 2007-03-27 | 1 | Out= NIL, Bastyan L5 Requirement <= 0MW
F_T_BASTYAN_L6 | 2007-03-27 | 1 | Out= NIL, Bastyan L6 Requirement <= 0MW
F_T_BASTYAN_L60 | 2007-03-27 | 1 | Out= NIL, Bastyan L60 Requirement <= 0MW
F_T_BASTYAN_LREG | 2007-03-27 | 1 | Out= NIL, Bastyan LREG Requirement <= 0MW
F_T_BASTYAN_R5 | 2007-03-27 | 1 | Out= NIL, Bastyan R5 Requirement <= 0MW
F_T_BASTYAN_R6 | 2007-03-27 | 1 | Out= NIL, Bastyan R6 Requirement <= 0MW
F_T_BASTYAN_R60 | 2007-03-27 | 1 | Out= NIL, Bastyan R60 Requirement <= 0MW
F_T_BASTYAN_RREG | 2007-03-27 | 1 | Out= NIL, Bastyan RREG Requirement <= 0MW
F_T_BELLBAY1_L5 | 2007-03-27 | 1 | Out= NIL, Bell Bay 1 L5 Requirement <= 0MW
F_T_BELLBAY1_L6 | 2007-03-27 | 1 | Out= NIL, Bell Bay 1 L6 Requirement <= 0MW
F_T_BELLBAY1_L60 | 2007-03-27 | 1 | Out= NIL, Bell Bay 1 L60 Requirement <= 0MW
F_T_BELLBAY1_LREG | 2007-03-27 | 1 | Out= NIL, Bell Bay 1 LREG Requirement <= 0MW
F_T_BELLBAY1_R5 | 2007-03-27 | 1 | Out= NIL, Bell Bay 1 R5 Requirement <= 0MW
F_T_BELLBAY1_R6 | 2007-03-27 | 1 | Out= NIL, Bell Bay 1 R6 Requirement <= 0MW
F_T_BELLBAY1_RREG | 2007-03-27 | 1 | Out= NIL, Bell Bay 1 RREG Requirement <= 0MW
F_T_BELLBAY2_L5 | 2007-03-27 | 1 | Out= NIL, Bell Bay 2 L5 Requirement <= 0MW
F_T_BELLBAY2_L6 | 2007-03-27 | 1 | Out= NIL, Bell Bay 2 L6 Requirement <= 0MW
F_T_BELLBAY2_L60 | 2007-03-27 | 1 | Out= NIL, Bell Bay 2 L60 Requirement <= 0MW
F_T_BELLBAY2_LREG | 2007-03-27 | 1 | Out= NIL, Bell Bay 2 LREG Requirement <= 0MW
F_T_BELLBAY2_R5 | 2007-03-27 | 1 | Out= NIL, Bell Bay 2 R5 Requirement <= 0MW
F_T_BELLBAY2_R6 | 2007-03-27 | 1 | Out= NIL, Bell Bay 2 R6 Requirement <= 0MW
F_T_BELLBAY2_RREG | 2007-03-27 | 1 | Out= NIL, Bell Bay 2 RREG Requirement <= 0MW
F_T_CETHANA_L5 | 2007-03-27 | 1 | Out= NIL, Cethana L5 Requirement <= 0MW
F_T_CETHANA_L6 | 2007-03-27 | 1 | Out= NIL, Cethana L6 Requirement <= 0MW
F_T_CETHANA_L60 | 2007-03-27 | 1 | Out= NIL, Cethana L60 Requirement <= 0MW
F_T_CETHANA_LREG | 2007-03-27 | 1 | Out= NIL, Cethana LREG Requirement <= 0MW
F_T_CETHANA_R5 | 2007-03-27 | 1 | Out= NIL, Cethana R5 Requirement <= 0MW
F_T_CETHANA_R6 | 2007-03-27 | 1 | Out= NIL, Cethana R6 Requirement <= 0MW
F_T_CETHANA_R60 | 2007-03-27 | 1 | Out= NIL, Cethana R60 Requirement <= 0MW
F_T_CETHANA_RREG | 2007-03-27 | 1 | Out= NIL, Cethana RREG Requirement <= 0MW
F_T_DEVILS_G_L5 | 2007-03-27 | 1 | Out= NIL, Devils Gate L5 Requirement <= 0MW
F_T_DEVILS_G_L6 | 2007-03-27 | 1 | Out= NIL, Devils Gate L6 Requirement <= 0MW
F_T_DEVILS_G_L60 | 2007-03-27 | 1 | Out= NIL, Devils Gate L60 Requirement <= 0MW
F_T_DEVILS_G_LREG | 2007-03-27 | 1 | Out= NIL, Devils Gate LREG Requirement <= 0MW
F_T_DEVILS_G_R5 | 2007-03-27 | 1 | Out= NIL, Devils Gate R5 Requirement <= 0MW
F_T_DEVILS_G_R6 | 2007-03-27 | 1 | Out= NIL, Devils Gate R6 Requirement <= 0MW
F_T_DEVILS_G_R60 | 2007-03-27 | 1 | Out= NIL, Devils Gate R60 Requirement <= 0MW
F_T_DEVILS_G_RREG | 2007-03-27 | 1 | Out= NIL, Devils Gate RREG Requirement <= 0MW
F_T_DG_0_L5 | 2007-03-01 | 1 | Devils Gate = 0MW. L5 <= 0MW
F_T_DG_0_L6 | 2007-03-01 | 1 | Devils Gate = 0MW. L6 <= 0MW
F_T_DG_0_L60 | 2007-03-01 | 1 | Devils Gate = 0MW L60 <= 0MW
F_T_DG_0_LREG | 2007-03-01 | 1 | Devils Gate = 0MW LREG <= 0MW
F_T_DG_0_R5 | 2007-03-01 | 1 | Devils Gate = 0MW. R5 <= 0MW
F_T_DG_0_R6 | 2007-03-01 | 1 | Devils Gate = 0MW. R6 <= 0MW
F_T_DG_0_R60 | 2007-03-01 | 1 | Devils Gate = 0MW. R60 <= 0MW
F_T_DG_0_RREG | 2007-03-01 | 1 | Devils Gate = 0MW. RREG <= 0MW
F_T_FABA_L5 | 2007-03-01 | 1 | Out=Farrell-Bastyan 220KV line. L5 <= 0MW
F_T_FABA_L6 | 2007-03-01 | 1 | Out=Farrell-Bastyan 220KV line. L6 <= 0MW
F_T_FABA_L60 | 2007-03-01 | 1 | Out=Farrell-Bastyan 220KV line. L60 <= 0MW
F_T_FABA_LREG | 2007-03-01 | 1 | Out=Farrell-Bastyan 220KV line. LREG <= 0MW
F_T_FABA_R5 | 2007-03-01 | 1 | Out=Farrell-Bastyan 220KV line. R5 <= 0MW
F_T_FABA_R6 | 2007-03-01 | 1 | Out=Farrell-Bastyan 220KV line. R6 <= 0MW
F_T_FABA_R60 | 2007-03-01 | 1 | Out=Farrell-Bastyan 220KV line. R60 <= 0MW
F_T_FABA_RREG | 2007-03-01 | 1 | Out=Farrell-Bastyan 220KV line. RREG <= 0MW
F_T_FAJB_L5 | 2007-03-01 | 1 | Out=Farrell-John Butters 220KV line. L5 <= 0MW
F_T_FAJB_L6 | 2007-03-01 | 1 | Out=Farrell-John Butters 220KV line. L6 <= 0MW
F_T_FAJB_L60 | 2007-03-01 | 1 | Out=Farrell-John Butters 220KV line. L60 <= 0MW
F_T_FAJB_LREG | 2007-03-01 | 1 | Out=Farrell-John Butters 220KV line. LREG <= 0MW
F_T_FAJB_R5 | 2007-03-01 | 1 | Out=Farrell-John Butters 220KV line. R5 <= 0MW
F_T_FAJB_R6 | 2007-03-01 | 1 | Out=Farrell-John Butters 220KV line. R6 <= 0MW
F_T_FAJB_R60 | 2007-03-01 | 1 | Out=Farrell-John Butters 220KV line. R60 <= 0MW
F_T_FAJB_RREG | 2007-03-01 | 1 | Out=Farrell-John Butters 220KV line. RREG <= 0MW
F_T_FAMA_L5 | 2007-03-01 | 1 | Out=Farrell-Mackintosh 110KV line. L5 <= 0MW
F_T_FAMA_L6 | 2007-03-01 | 1 | Out=Farrell-Mackintosh 110KV line. L6 <= 0MW
F_T_FAMA_L60 | 2007-03-01 | 1 | Out=Farrell-Mackintosh 110KV line. L60 <= 0MW
F_T_FAMA_LREG | 2007-03-01 | 1 | Out=Farrell-Mackintosh 110KV line. LREG <= 0MW
F_T_FAMA_R5 | 2007-03-01 | 1 | Out=Farrell-Mackintosh 110KV line. R5 <= 0MW
F_T_FAMA_R6 | 2007-03-01 | 1 | Out=Farrell-Mackintosh 110KV line. R6 <= 0MW
F_T_FAMA_R60 | 2007-03-01 | 1 | Out=Farrell-Mackintosh 110KV line. R60 <= 0MW
F_T_FAMA_RREG | 2007-03-01 | 1 | Out=Farrell-Mackintosh 110KV line. RREG <= 0MW
F_T_FARC1_L5 | 2007-03-01 | 1 | Out=Farrell-Reece 1 220KV line. L5 <= 0MW
F_T_FARC1_L6 | 2007-03-01 | 1 | Out=Farrell-Reece 1 220KV line. L6 <= 0MW
F_T_FARC1_L60 | 2007-03-01 | 1 | Out=Farrell-Reece 1 220KV line. L60 <= 0MW
F_T_FARC1_LREG | 2007-03-01 | 1 | Out=Farrell-Reece 1 220KV line. LREG <= 0MW
F_T_FARC1_R5 | 2007-03-01 | 1 | Out=Farrell-Reece 1 220KV line. R5 <= 0MW
F_T_FARC1_R6 | 2007-03-01 | 1 | Out=Farrell-Reece 1 220KV line. R6 <= 0MW
F_T_FARC1_R60 | 2007-03-01 | 1 | Out=Farrell-Reece 1 220KV line. R60 <= 0MW
F_T_FARC1_RREG | 2007-03-01 | 1 | Out=Farrell-Reece 1 220KV line. RREG <= 0MW
F_T_FARC2_L5 | 2007-03-01 | 1 | Out=Farrell-Reece 2 220KV line. L5 <= 0MW
F_T_FARC2_L6 | 2007-03-01 | 1 | Out=Farrell-Reece 2 220KV line. L6 <= 0MW
F_T_FARC2_L60 | 2007-03-01 | 1 | Out=Farrell-Reece 2 220KV line. L60 <= 0MW
F_T_FARC2_LREG | 2007-03-01 | 1 | Out=Farrell-Reece 2 220KV line. LREG <= 0MW
F_T_FARC2_R5 | 2007-03-01 | 1 | Out=Farrell-Reece 2 220KV line. R5 <= 0MW
F_T_FARC2_R6 | 2007-03-01 | 1 | Out=Farrell-Reece 2 220KV line. R6 <= 0MW
F_T_FARC2_R60 | 2007-03-01 | 1 | Out=Farrell-Reece 2 220KV line. R60 <= 0MW
F_T_FARC2_RREG | 2007-03-01 | 1 | Out=Farrell-Reece 2 220KV line. RREG <= 0MW
F_T_FATI_L5 | 2007-03-01 | 1 | Out=Farrell-Tribute 220KV line. L5 <= 0MW
F_T_FATI_L6 | 2007-03-01 | 1 | Out=Farrell-Tribute 220KV line. L6 <= 0MW
F_T_FATI_L60 | 2007-03-01 | 1 | Out=Farrell-Tribute 220KV line. L60 <= 0MW
F_T_FATI_LREG | 2007-03-01 | 1 | Out=Farrell-Tribute 220KV line. LREG <= 0MW
F_T_FATI_R5 | 2007-03-01 | 1 | Out=Farrell-Tribute 220KV line. R5 <= 0MW
F_T_FATI_R6 | 2007-03-01 | 1 | Out=Farrell-Tribute 220KV line. R6 <= 0MW
F_T_FATI_R60 | 2007-03-01 | 1 | Out=Farrell-Tribute 220KV line. R60 <= 0MW
F_T_FATI_RREG | 2007-03-01 | 1 | Out=Farrell-Tribute 220KV line. RREG <= 0MW
F_T_FISHER_L5 | 2007-03-27 | 1 | Out= NIL, Fisher L5 Requirement <= 0MW
F_T_FISHER_L6 | 2007-03-27 | 1 | Out= NIL, Fisher L6 Requirement <= 0MW
F_T_FISHER_L60 | 2007-03-27 | 1 | Out= NIL, Fisher L60 Requirement <= 0MW
F_T_FISHER_LREG | 2007-03-27 | 1 | Out= NIL, Fisher LREG Requirement <= 0MW
F_T_FISHER_R5 | 2007-03-27 | 1 | Out= NIL, Fisher R5 Requirement <= 0MW
F_T_FISHER_R6 | 2007-03-27 | 1 | Out= NIL, Fisher R6 Requirement <= 0MW
F_T_FISHER_R60 | 2007-03-27 | 1 | Out= NIL, Fisher R60 Requirement <= 0MW
F_T_FISHER_RREG | 2007-03-27 | 1 | Out= NIL, Fisher RREG Requirement <= 0MW
F_T_GORDON_L5 | 2007-03-27 | 1 | Out= NIL, Gordon L5 Requirement <= 0MW
F_T_GORDON_L6 | 2007-03-27 | 1 | Out= NIL, Gordon L6 Requirement <= 0MW
F_T_GORDON_L60 | 2007-03-27 | 1 | Out= NIL, Gordon L60 Requirement <= 0MW
F_T_GORDON_LREG | 2007-03-27 | 1 | Out= NIL, Gordon LREG Requirement <= 0MW
F_T_GORDON_R5 | 2007-03-27 | 1 | Out= NIL, Gordon R5 Requirement <= 0MW
F_T_GORDON_R6 | 2007-03-27 | 1 | Out= NIL, Gordon R6 Requirement <= 0MW
F_T_GORDON_R60 | 2007-03-27 | 1 | Out= NIL, Gordon R60 Requirement <= 0MW
F_T_GORDON_RREG | 2007-03-27 | 1 | Out= NIL, Gordon RREG Requirement <= 0MW
F_T_GTBB1_L5 | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 1 110KV line. L5 <= 0MW
F_T_GTBB1_L6 | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 1 110KV line. L6 <= 0MW
F_T_GTBB1_L60 | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 1 110KV line. L60 <= 0MW
F_T_GTBB1_LREG | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 1 110KV line. LREG <= 0MW
F_T_GTBB1_R5 | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 1 110KV line. R5 <= 0MW
F_T_GTBB1_R6 | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 1 110KV line. R6 <= 0MW
F_T_GTBB1_RREG | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 1 110KV line. RREG <= 0MW
F_T_GTBB2_L5 | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 2 110KV line. L5 <= 0MW
F_T_GTBB2_L6 | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 2 110KV line. L6 <= 0MW
F_T_GTBB2_L60 | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 2 110KV line. L60 <= 0MW
F_T_GTBB2_LREG | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 2 110KV line. LREG <= 0MW
F_T_GTBB2_R5 | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 2 110KV line. R5 <= 0MW
F_T_GTBB2_R6 | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 2 110KV line. R6 <= 0MW
F_T_GTBB2_RREG | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 2 110KV line. RREG <= 0MW
F_T_JBUTTERS_L5 | 2007-03-27 | 1 | Out= NIL, John Butters L5 Requirement <= 0MW
F_T_JBUTTERS_L6 | 2007-03-27 | 1 | Out= NIL, John Butters L6 Requirement <= 0MW
F_T_JBUTTERS_L60 | 2007-03-27 | 1 | Out= NIL, John Butters L60 Requirement <= 0MW
F_T_JBUTTERS_LREG | 2007-03-27 | 1 | Out= NIL, John Butters LREG Requirement <= 0MW
F_T_JBUTTERS_R5 | 2007-03-27 | 1 | Out= NIL, John Butters R5 Requirement <= 0MW
F_T_JBUTTERS_R6 | 2007-03-27 | 1 | Out= NIL, John Butters R6 Requirement <= 0MW
F_T_JBUTTERS_R60 | 2007-03-27 | 1 | Out= NIL, John Butters R60 Requirement <= 0MW
F_T_JBUTTERS_RREG | 2007-03-27 | 1 | Out= NIL, John Butters RREG Requirement <= 0MW
F_T_LEM_WIL_L5 | 2007-03-27 | 1 | Out= NIL, Lemonthyme + Wilmont L5 Requirement <= 0MW
F_T_LEM_WIL_L6 | 2007-03-27 | 1 | Out= NIL, Lemonthyme + Wilmont L6 Requirement <= 0MW
F_T_LEM_WIL_L60 | 2007-03-27 | 1 | Out= NIL, Lemonthyme + Wilmont L60 Requirement <= 0MW
F_T_LEM_WIL_LREG | 2007-03-27 | 1 | Out= NIL, Lemonthyme + Wilmont LREG Requirement <= 0MW
F_T_LEM_WIL_R5 | 2007-03-27 | 1 | Out= NIL, Lemonthyme + Wilmont R5 Requirement <= 0MW
F_T_LEM_WIL_R6 | 2007-03-27 | 1 | Out= NIL, Lemonthyme + Wilmont R6 Requirement <= 0MW
F_T_LEM_WIL_R60 | 2007-03-27 | 1 | Out= NIL, Lemonthyme + Wilmont R60 Requirement <= 0MW
F_T_LEM_WIL_RREG | 2007-03-27 | 1 | Out= NIL, Lemonthyme + Wilmont RREG Requirement <= 0MW
F_T_LI_WY_CA_L5 | 2007-03-27 | 1 | Out= NIL, Liapootah + Wayatinah + Catagunya L5 Requirement <= 0MW
F_T_LI_WY_CA_L6 | 2007-03-27 | 1 | Out= NIL, Liapootah + Wayatinah + Catagunya L6 Requirement <= 0MW
F_T_LI_WY_CA_L60 | 2007-03-27 | 1 | Out= NIL, Liapootah + Wayatinah + Catagunya L60 Requirement <= 0MW
F_T_LI_WY_CA_LREG | 2007-03-27 | 1 | Out= NIL, Liapootah + Wayatinah + Catagunya LREG Requirement <= 0MW
F_T_LI_WY_CA_R5 | 2007-03-27 | 1 | Out= NIL, Liapootah + Wayatinah + Catagunya R5 Requirement <= 0MW
F_T_LI_WY_CA_R6 | 2007-03-27 | 1 | Out= NIL, Liapootah + Wayatinah + Catagunya R6 Requirement <= 0MW
F_T_LI_WY_CA_R60 | 2007-03-27 | 1 | Out= NIL, Liapootah + Wayatinah + Catagunya R60 Requirement <= 0MW
F_T_LI_WY_CA_RREG | 2007-03-27 | 1 | Out= NIL, Liapootah + Wayatinah + Catagunya RREG Requirement <= 0MW
F_T_MACKNTCH_L5 | 2007-03-27 | 1 | Out= NIL, Mackintosh L5 Requirement <= 0MW
F_T_MACKNTCH_L6 | 2007-03-27 | 1 | Out= NIL, Mackintosh L6 Requirement <= 0MW
F_T_MACKNTCH_L60 | 2007-03-27 | 1 | Out= NIL, Mackintosh L60 Requirement <= 0MW
F_T_MACKNTCH_LREG | 2007-03-27 | 1 | Out= NIL, Mackintosh LREG Requirement <= 0MW
F_T_MACKNTCH_R5 | 2007-03-27 | 1 | Out= NIL, Mackintosh R5 Requirement <= 0MW
F_T_MACKNTCH_R6 | 2007-03-27 | 1 | Out= NIL, Mackintosh R6 Requirement <= 0MW
F_T_MACKNTCH_R60 | 2007-03-27 | 1 | Out= NIL, Mackintosh R60 Requirement <= 0MW
F_T_MACKNTCH_RREG | 2007-03-27 | 1 | Out= NIL, Mackintosh RREG Requirement <= 0MW
F_T_MEADOWBK_L5 | 2007-03-27 | 1 | Out= NIL, Meadowbank L5 Requirement <= 0MW
F_T_MEADOWBK_L6 | 2007-03-27 | 1 | Out= NIL, Meadowbank L6 Requirement <= 0MW
F_T_MEADOWBK_L60 | 2007-03-27 | 1 | Out= NIL, Meadowbank L60 Requirement <= 0MW
F_T_MEADOWBK_LREG | 2007-03-27 | 1 | Out= NIL, Meadowbank LREG Requirement <= 0MW
F_T_MEADOWBK_R5 | 2007-03-27 | 1 | Out= NIL, Meadowbank R5 Requirement <= 0MW
F_T_MEADOWBK_R6 | 2007-03-27 | 1 | Out= NIL, Meadowbank R6 Requirement <= 0MW
F_T_MEADOWBK_R60 | 2007-03-27 | 1 | Out= NIL, Meadowbank R60 Requirement <= 0MW
F_T_MEADOWBK_RREG | 2007-03-27 | 1 | Out= NIL, Meadowbank RREG Requirement <= 0MW
F_T_ME_ZERO_L5 | 2007-03-01 | 1 | Meadowbank Lower 5 min requirement <= 0
F_T_ME_ZERO_L6 | 2007-03-01 | 1 | Meadowbank Lower 6 sec requirement <= 0
F_T_ME_ZERO_L60 | 2007-03-01 | 1 | Meadowbank Lower 60 sec requirement <= 0
F_T_ME_ZERO_LREG | 2007-03-01 | 1 | Meadowbank Lower Regulation requirement <= 0
F_T_ME_ZERO_R5 | 2007-03-01 | 1 | Meadowbank Raise 5 min requirement <= 0
F_T_ME_ZERO_R6 | 2007-03-01 | 1 | Meadowbank Raise 6 sec requirement <= 0
F_T_ME_ZERO_R60 | 2007-03-01 | 1 | Meadowbank Raise 60 sec requirement <= 0
F_T_ME_ZERO_RREG | 2007-03-01 | 1 | Meadowbank Raise Regulation requirement <= 0
F_T_PMPO_FOUR220LREG | 2007-03-01 | 1 | Out= All four Palmerston-Poatina 220kV lines. LREG <= 0MW
F_T_PMPO_FOUR220RREG | 2007-03-01 | 1 | Out= All four Palmerston-Poatina 220kV lines. RREG <= 0MW
F_T_PMPO_FOUR220_L5 | 2007-03-01 | 1 | Out= All four Palmerston-Poatina 220kV lines. L5 <= 0MW
F_T_PMPO_FOUR220_L6 | 2007-03-01 | 1 | Out= All four Palmerston-Poatina 220kV lines. L6 <= 0MW
F_T_PMPO_FOUR220_L60 | 2007-03-01 | 1 | Out= All four Palmerston-Poatina 220kV lines. L60 <= 0MW
F_T_PMPO_FOUR220_R5 | 2007-03-01 | 1 | Out= All four Palmerston-Poatina 220kV lines. R5 <= 0MW
F_T_PMPO_FOUR220_R6 | 2007-03-01 | 1 | Out= All four Palmerston-Poatina 220kV lines. R6 <= 0MW
F_T_PMPO_FOUR220_R60 | 2007-03-01 | 1 | Out= All four Palmerston-Poatina 220kV lines. R60 <= 0MW
F_T_PMPO_TWO110_LREG | 2007-03-01 | 1 | Out=Both Palmerston-Poatina 110KV lines. LREG <= 0MW
F_T_PMPO_TWO110_RREG | 2007-03-01 | 1 | Out=Both Palmerston-Poatina 110KV lines. RREG <= 0MW
F_T_PMPO_TWO_110_L5 | 2007-03-01 | 1 | Out=Both Palmerston-Poatina 110KV lines. L5 <= 0MW
F_T_PMPO_TWO_110_L6 | 2007-03-01 | 1 | Out=Both Palmerston-Poatina 110KV lines. L6 <= 0MW
F_T_PMPO_TWO_110_L60 | 2007-03-01 | 1 | Out=Both Palmerston-Poatina 110KV lines. L60 <= 0MW
F_T_PMPO_TWO_110_R5 | 2007-03-01 | 1 | Out=Both Palmerston-Poatina 110KV lines. R5 <= 0MW
F_T_PMPO_TWO_110_R6 | 2007-03-01 | 1 | Out=Both Palmerston-Poatina 110KV lines. R6 <= 0MW
F_T_PMPO_TWO_110_R60 | 2007-03-01 | 1 | Out=Both Palmerston-Poatina 110KV lines. R60 <= 0MW
F_T_POAT110_L5 | 2007-03-27 | 1 | Out= NIL, Poatina 110kV L5 Requirement <= 0MW
F_T_POAT110_L6 | 2007-03-27 | 1 | Out= NIL, Poatina 110kV L6 Requirement <= 0MW
F_T_POAT110_L60 | 2007-03-27 | 1 | Out= NIL, Poatina 110kV L60 Requirement <= 0MW
F_T_POAT110_LREG | 2007-03-27 | 1 | Out= NIL, Poatina 110kV LREG Requirement <= 0MW
F_T_POAT110_R5 | 2007-03-27 | 1 | Out= NIL, Poatina 110kV R5 Requirement <= 0MW
F_T_POAT110_R6 | 2007-03-27 | 1 | Out= NIL, Poatina 110kV R6 Requirement <= 0MW
F_T_POAT110_R60 | 2007-03-27 | 1 | Out= NIL, Poatina 110kV R60 Requirement <= 0MW
F_T_POAT110_RREG | 2007-03-27 | 1 | Out= NIL, Poatina 110kV RREG Requirement <= 0MW
F_T_POAT220_L5 | 2007-03-27 | 1 | Out= NIL, Poatina 220kV L5 Requirement <= 0MW
F_T_POAT220_L6 | 2007-03-27 | 1 | Out= NIL, Poatina 220kV L6 Requirement <= 0MW
F_T_POAT220_L60 | 2007-03-27 | 1 | Out= NIL, Poatina 220kV L60 Requirement <= 0MW
F_T_POAT220_LREG | 2007-03-27 | 1 | Out= NIL, Poatina 220kV LREG Requirement <= 0MW
F_T_POAT220_R5 | 2007-03-27 | 1 | Out= NIL, Poatina 220kV R5 Requirement <= 0MW
F_T_POAT220_R6 | 2007-03-27 | 1 | Out= NIL, Poatina 220kV R6 Requirement <= 0MW
F_T_POAT220_R60 | 2007-03-27 | 1 | Out= NIL, Poatina 220kV R60 Requirement <= 0MW
F_T_POAT220_RREG | 2007-03-27 | 1 | Out= NIL, Poatina 220kV RREG Requirement <= 0MW
F_T_REECE1_L5 | 2007-03-27 | 1 | Out= NIL, Reece 1 L5 Requirement <= 0MW
F_T_REECE1_L6 | 2007-03-27 | 1 | Out= NIL, Reece 1 L6 Requirement <= 0MW
F_T_REECE1_L60 | 2007-03-27 | 1 | Out= NIL, Reece 1 L60 Requirement <= 0MW
F_T_REECE1_LREG | 2007-03-27 | 1 | Out= NIL, Reece 1 LREG Requirement <= 0MW
F_T_REECE1_R5 | 2007-03-27 | 1 | Out= NIL, Reece 1 R5 Requirement <= 0MW
F_T_REECE1_R6 | 2007-03-27 | 1 | Out= NIL, Reece 1 R6 Requirement <= 0MW
F_T_REECE1_R60 | 2007-03-27 | 1 | Out= NIL, Reece 1 R60 Requirement <= 0MW
F_T_REECE1_RREG | 2007-03-27 | 1 | Out= NIL, Reece 1 RREG Requirement <= 0MW
F_T_REECE2_L5 | 2007-03-27 | 1 | Out= NIL, Reece 2 L5 Requirement <= 0MW
F_T_REECE2_L6 | 2007-03-27 | 1 | Out= NIL, Reece 2 L6 Requirement <= 0MW
F_T_REECE2_L60 | 2007-03-27 | 1 | Out= NIL, Reece 2 L60 Requirement <= 0MW
F_T_REECE2_LREG | 2007-03-27 | 1 | Out= NIL, Reece 2 LREG Requirement <= 0MW
F_T_REECE2_R5 | 2007-03-27 | 1 | Out= NIL, Reece 2 R5 Requirement <= 0MW
F_T_REECE2_R6 | 2007-03-27 | 1 | Out= NIL, Reece 2 R6 Requirement <= 0MW
F_T_REECE2_R60 | 2007-03-27 | 1 | Out= NIL, Reece 2 R60 Requirement <= 0MW
F_T_REECE2_RREG | 2007-03-27 | 1 | Out= NIL, Reece 2 RREG Requirement <= 0MW
F_T_SHCE_L5 | 2007-03-01 | 1 | Out=Sheffield-Cethana 220KV line. L5 <= 0MW
F_T_SHCE_L6 | 2007-03-01 | 1 | Out=Sheffield-Cethana 220KV line. L6 <= 0MW
F_T_SHCE_L60 | 2007-03-01 | 1 | Out=Sheffield-Cethana 220KV line. L60 <= 0MW
F_T_SHCE_LREG | 2007-03-01 | 1 | Out=Sheffield-Cethana 220KV line. LREG <= 0MW
F_T_SHCE_R5 | 2007-03-01 | 1 | Out=Sheffield-Cethana 220KV line. R5 <= 0MW
F_T_SHCE_R6 | 2007-03-01 | 1 | Out=Sheffield-Cethana 220KV line. R6 <= 0MW
F_T_SHCE_R60 | 2007-03-01 | 1 | Out=Sheffield-Cethana 220KV line. R60 <= 0MW
F_T_SHCE_RREG | 2007-03-01 | 1 | Out=Sheffield-Cethana 220KV line. RREG <= 0MW
F_T_SHDG_L5 | 2007-03-01 | 1 | Out=Sheffield-Devils Gate 110KV line. L5 <= 0MW
F_T_SHDG_L6 | 2007-03-01 | 1 | Out=Sheffield-Devils Gate 110KV line. L6 <= 0MW
F_T_SHDG_L60 | 2007-03-01 | 1 | Out=Sheffield-Devils Gate 110KV line L60 <= 0MW
F_T_SHDG_LREG | 2007-03-01 | 1 | Out=Sheffield-Devils Gate 110KV line LREG <= 0MW
F_T_SHDG_R5 | 2007-03-01 | 1 | Out=Sheffield-Devils Gate 110KV line. R5 <= 0MW
F_T_SHDG_R6 | 2007-03-01 | 1 | Out=Sheffield-Devils Gate 110KV line. R6 <= 0MW
F_T_SHDG_R60 | 2007-03-01 | 1 | Out=Sheffield-Devils Gate 110KV line. R60 <= 0MW
F_T_SHDG_RREG | 2007-03-01 | 1 | Out=Sheffield-Devils Gate 110KV line. RREG <= 0MW
F_T_SHFI_L5 | 2007-03-01 | 1 | Out=Sheffield-Fisher 220KV line. L5 <= 0MW
F_T_SHFI_L6 | 2007-03-01 | 1 | Out=Sheffield-Fisher 220KV line. L6 <= 0MW
F_T_SHFI_L60 | 2007-03-01 | 1 | Out=Sheffield-Fisher 220KV line. L60 <= 0MW
F_T_SHFI_LREG | 2007-03-01 | 1 | Out=Sheffield-Fisher 220KV line. LREG <= 0MW
F_T_SHFI_R5 | 2007-03-01 | 1 | Out=Sheffield-Fisher 220KV line. R5 <= 0MW
F_T_SHFI_R6 | 2007-03-01 | 1 | Out=Sheffield-Fisher 220KV line. R6 <= 0MW
F_T_SHFI_R60 | 2007-03-01 | 1 | Out=Sheffield-Fisher 220KV line. R60 <= 0MW
F_T_SHFI_RREG | 2007-03-01 | 1 | Out=Sheffield-Fisher 220KV line. RREG <= 0MW
F_T_TREVALLN_L5 | 2007-03-27 | 1 | Out= NIL, Trevallyn L5 Requirement <= 0MW
F_T_TREVALLN_L6 | 2007-03-27 | 1 | Out= NIL, Trevallyn L6 Requirement <= 0MW
F_T_TREVALLN_L60 | 2007-03-27 | 1 | Out= NIL, Trevallyn L60 Requirement <= 0MW
F_T_TREVALLN_LREG | 2007-03-27 | 1 | Out= NIL, Trevallyn LREG Requirement <= 0MW
F_T_TREVALLN_R5 | 2007-03-27 | 1 | Out= NIL, Trevallyn R5 Requirement <= 0MW
F_T_TREVALLN_R6 | 2007-03-27 | 1 | Out= NIL, Trevallyn R6 Requirement <= 0MW
F_T_TREVALLN_R60 | 2007-03-27 | 1 | Out= NIL, Trevallyn R60 Requirement <= 0MW
F_T_TREVALLN_RREG | 2007-03-27 | 1 | Out= NIL, Trevallyn RREG Requirement <= 0MW
F_T_TRIBUTE_L5 | 2007-03-27 | 1 | Out= NIL, Tribute L5 Requirement <= 0MW
F_T_TRIBUTE_L6 | 2007-03-27 | 1 | Out= NIL, Tribute L6 Requirement <= 0MW
F_T_TRIBUTE_L60 | 2007-03-27 | 1 | Out= NIL, Tribute L60 Requirement <= 0MW
F_T_TRIBUTE_LREG | 2007-03-27 | 1 | Out= NIL, Tribute LREG Requirement <= 0MW
F_T_TRIBUTE_R5 | 2007-03-27 | 1 | Out= NIL, Tribute R5 Requirement <= 0MW
F_T_TRIBUTE_R6 | 2007-03-27 | 1 | Out= NIL, Tribute R6 Requirement <= 0MW
F_T_TRIBUTE_R60 | 2007-03-27 | 1 | Out= NIL, Tribute R60 Requirement <= 0MW
F_T_TRIBUTE_RREG | 2007-03-27 | 1 | Out= NIL, Tribute RREG Requirement <= 0MW
F_T_TUNGATIN_L5 | 2007-03-27 | 1 | Out= NIL, Tungatinah L5 Requirement <= 0MW
F_T_TUNGATIN_L6 | 2007-03-27 | 1 | Out= NIL, Tungatinah L6 Requirement <= 0MW
F_T_TUNGATIN_L60 | 2007-03-27 | 1 | Out= NIL, Tungatinah L60 Requirement <= 0MW
F_T_TUNGATIN_LREG | 2007-03-27 | 1 | Out= NIL, Tungatinah LREG Requirement <= 0MW
F_T_TUNGATIN_R5 | 2007-03-27 | 1 | Out= NIL, Tungatinah R5 Requirement <= 0MW
F_T_TUNGATIN_R6 | 2007-03-27 | 1 | Out= NIL, Tungatinah R6 Requirement <= 0MW
F_T_TUNGATIN_R60 | 2007-03-27 | 1 | Out= NIL, Tungatinah R60 Requirement <= 0MW
F_T_TUNGATIN_RREG | 2007-03-27 | 1 | Out= NIL, Tungatinah RREG Requirement <= 0MW
F_T_X+FASH_L5 | 2006-02-07 | 1 | Out = both Farrell to Sheffield lines, loss of both Farrell to Sheffield lines declared credible, West Coast Lower 5 min Requirement = 0
F_T_X+FASH_L6 | 2006-02-07 | 1 | Out = both Farrell to Sheffield lines, loss of both Farrell to Sheffield lines declared credible, West Coast Lower 6 sec Requirement = 0
F_T_X+FASH_L60 | 2006-02-07 | 1 | Out = both Farrell to Sheffield lines, loss of both Farrell to Sheffield lines declared credible, West Coast Lower 60 sec Requirement = 0
F_T_X+FASH_LREG | 2006-02-07 | 1 | Out = both Farrell to Sheffield lines, loss of both Farrell to Sheffield lines declared credible, West Coast Lower Regulation Requirement = 0
F_T_X+FASH_R5 | 2006-02-07 | 1 | Out = both Farrell to Sheffield lines, loss of both Farrell to Sheffield lines declared credible, West Coast Raise 5 min Requirement = 0
F_T_X+FASH_R6 | 2006-02-07 | 1 | Out = both Farrell to Sheffield lines, loss of both Farrell to Sheffield lines declared credible, West Coast Raise 6 sec Requirement = 0
F_T_X+FASH_R60 | 2006-02-07 | 1 | Out = both Farrell to Sheffield lines, loss of both Farrell to Sheffield lines declared credible, West Coast Raise 60 sec Requirement = 0
F_T_X+FASH_RREG | 2006-02-07 | 1 | Out = both Farrell to Sheffield lines, loss of both Farrell to Sheffield lines declared credible, West Coast Raise Regulation Requirement = 0
F_V+NIL_APD01_L5 | 2007-09-12 | 1 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 5 Min service
F_V+NIL_APD01_L6 | 2007-09-12 | 1 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 6 sec service
F_V+NIL_APD01_L60 | 2007-09-12 | 1 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 60 sec service
F_V+NIL_APD01_R5 | 2007-09-12 | 1 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service
F_V+NIL_APD01_R6 | 2007-09-12 | 1 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service
F_V+NIL_APD01_R60 | 2007-09-12 | 1 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service
F_V+NIL_APD02_L5 | 2007-09-12 | 1 | Out=Nil, limit APD02 to zero MW when potline is tripped for Lower 5 Min service
F_V+NIL_APD02_L6 | 2007-09-12 | 1 | Out=Nil, limit APD02 to zero MW when potline is tripped for Lower 6 sec service
F_V+NIL_APD02_L60 | 2007-09-12 | 1 | Out=Nil, limit APD02 to zero MW when potline is tripped for Lower 60 sec service
F_V+NIL_APD02_R5 | 2007-09-12 | 1 | Out=Nil, limit APD02 to zero MW when potline is tripped for Raise 5 Min service
F_V+NIL_APD02_R6 | 2007-09-12 | 1 | Out=Nil, limit APD02 to zero MW when potline is tripped for Raise 6 sec service
F_V+NIL_APD02_R60 | 2007-09-12 | 1 | Out=Nil, limit APD02 to zero MW when potline is tripped for Raise 60 sec service
F_V+NIL_PTH01_L5 | 2007-09-12 | 1 | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 5 Min service
F_V+NIL_PTH01_L6 | 2007-09-12 | 1 | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 6 sec service
F_V+NIL_PTH01_L60 | 2007-09-12 | 1 | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 60 sec service
F_V+NIL_PTH01_R5 | 2007-09-12 | 1 | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 5 Min service
F_V+NIL_PTH01_R6 | 2007-09-12 | 1 | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 6 sec service
F_V+NIL_PTH01_R60 | 2007-09-12 | 1 | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 60 sec service
F_V+NIL_PTH02_L5 | 2007-09-12 | 1 | Out=Nil, limit PTH02 to zero MW when potline is tripped for Lower 5 Min service
F_V+NIL_PTH02_L6 | 2007-09-12 | 1 | Out=Nil, limit PTH02 to zero MW when potline is tripped for Lower 6 sec service
F_V+NIL_PTH02_L60 | 2007-09-12 | 1 | Out=Nil, limit PTH02 to zero MW when potline is tripped for Lower 60 sec service
F_V+NIL_PTH02_R5 | 2007-09-12 | 1 | Out=Nil, limit PTH02 to zero MW when potline is tripped for Raise 5 Min service
F_V+NIL_PTH02_R6 | 2007-09-12 | 1 | Out=Nil, limit PTH02 to zero MW when potline is tripped for Raise 6 sec service
F_V+NIL_PTH02_R60 | 2007-09-12 | 1 | Out=Nil, limit PTH02 to zero MW when potline is tripped for Raise 60 sec service
F_V+NIL_PTH03_L5 | 2007-09-12 | 1 | Out=Nil, limit PTH03 to zero MW when potline is tripped for Lower 5 Min service
F_V+NIL_PTH03_L6 | 2007-09-12 | 1 | Out=Nil, limit PTH03 to zero MW when potline is tripped for Lower 6 sec service
F_V+NIL_PTH03_L60 | 2007-09-12 | 1 | Out=Nil, limit PTH03 to zero MW when potline is tripped for Lower 60 sec service
F_V+NIL_PTH03_R5 | 2007-09-12 | 1 | Out=Nil, limit PTH03 to zero MW when potline is tripped for Raise 5 Min service
F_V+NIL_PTH03_R6 | 2007-09-12 | 1 | Out=Nil, limit PTH03 to zero MW when potline is tripped for Raise 6 sec service
F_V+NIL_PTH03_R60 | 2007-09-12 | 1 | Out=Nil, limit PTH03 to zero MW when potline is tripped for Raise 60 sec service
F_VS++65_051_0X1_L5 | 2009-01-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic & SA Lower 5 min requirement, Basslink able to transfer FCAS
F_VS++65_051_0X1_L6 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic & SA Lower 6 sec requirement, Basslink able to transfer FCAS
F_VS++65_051_0X1_L60 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic & SA Lower 60 sec requirement, Basslink able to transfer FCAS
F_VS++65_051_0X1_R5 | 2009-01-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic & SA Raise 5 min requirement, Basslink able to transfer FCAS
F_VS++65_051_0X1_R6 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic & SA Raise 6 sec requirement, Basslink able to transfer FCAS
F_VS++65_051_0X1_R60 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic & SA Raise 60 sec requirement, Basslink able to transfer FCAS
F_VS++HWPS_TG_R5 | 2009-01-01 | 1 | Vic and SA Raise 5 min requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5; Basslink able to transfer FCAS
F_VS++HWPS_TG_R6 | 2006-01-30 | 1 | Vic and SA Raise 6 sec requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5; Basslink able to transfer FCAS
F_VS++HWPS_TG_R60 | 2006-01-30 | 1 | Vic and SA Raise 60 sec requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5; Basslink able to transfer FCAS
F_VS++LREG_0120 | 2006-06-27 | 1 | Vic and SA Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS
F_VS++MG_R5 | 2009-01-01 | 1 | Raise 5 min requirement for a Vic and SA Generation Event, Basslink able to transfer FCAS
F_VS++MG_R6 | 2006-01-30 | 1 | Raise 6 sec requirement for a Vic and SA Generation Event, Basslink able to transfer FCAS
F_VS++MG_R60 | 2006-01-30 | 1 | Raise 60 sec requirement for a Vic and SA Generation Event, Basslink able to transfer FCAS
F_VS++ML_L5_0300 | 2009-01-01 | 1 | Lower 5 min requirement for a Vic and SA Load Event, Basslink able to transfer FCAS
F_VS++ML_L60_0300 | 2007-04-30 | 1 | Lower 60 sec requirement for a Vic and SA Load Event, Basslink able to transfer FCAS
F_VS++ML_L6_0300 | 2007-04-30 | 1 | Lower 6 sec requirement for a Vic and SA Load Event, Basslink able to transfer FCAS
F_VS++RREG_0130 | 2006-01-30 | 1 | Vic and SA Raise Regulation Requirement greater than 130 MW, Basslink unable to transfer FCAS
F_VS++TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic and SA Network Event, TG = 500, Basslink able to transfer FCAS
F_VS++TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic and SA Network Event, TG = 1000, Basslink able to transfer FCAS
F_VS++TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic and SA Network Event, TG = 1400, Basslink able to transfer FCAS
F_VS++TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic and SA Network Event, TG = 1600, Basslink able to transfer FCAS
F_VS++TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic and SA Network Event, TG = 2000, Basslink able to transfer FCAS
F_VS++TG_R60_0500 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic and SA Network Event, TG = 500, Basslink able to transfer FCAS
F_VS++TG_R60_1000 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic and SA Network Event, TG = 1000, Basslink able to transfer FCAS
F_VS++TG_R60_1400 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic and SA Network Event, TG = 1400, Basslink able to transfer FCAS
F_VS++TG_R60_1600 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic and SA Network Event, TG = 1600, Basslink able to transfer FCAS
F_VS++TG_R60_2000 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic and SA Network Event, TG = 2000, Basslink able to transfer FCAS
F_VS++TG_R6_0500 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic and SA Network Event, TG = 500, Basslink able to transfer FCAS
F_VS++TG_R6_1000 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic and SA Network Event, TG = 1000, Basslink able to transfer FCAS
F_VS++TG_R6_1400 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic and SA Network Event, TG = 1400, Basslink able to transfer FCAS
F_VS++TG_R6_1600 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic and SA Network Event, TG = 1600, Basslink able to transfer FCAS
F_VS++TG_R6_2000 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic and SA Network Event, TG = 2000, Basslink able to transfer FCAS
F_VS++TL_L5_0600 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS
F_VS++TL_L60_0600 | 2006-01-31 | 2 | Lower 60 sec Service Requirement for a Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS
F_VS++TL_L6_0600 | 2006-01-31 | 2 | Lower 6 sec Service Requirement for a Vic and SA Network Event, TL = 600, Basslink able to transfer FCAS
F_VS+65_051_0X1_L5 | 2009-01-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic & SA Lower 5 min requirement, Basslink unable to transfer FCAS
F_VS+65_051_0X1_L6 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic & SA Lower 6 sec requirement, Basslink unable to transfer FCAS
F_VS+65_051_0X1_L60 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic & SA Lower 60 sec requirement, Basslink unable to transfer FCAS
F_VS+65_051_0X1_R5 | 2009-01-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic & SA Raise 5 min requirement, Basslink unable to transfer FCAS
F_VS+65_051_0X1_R6 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic & SA Raise 6 sec requirement, Basslink unable to transfer FCAS
F_VS+65_051_0X1_R60 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic & SA Raise 60 sec requirement, Basslink unable to transfer FCAS
F_VS+HWPS_TG_R5 | 2009-01-01 | 1 | Vic and SA Raise 5 min requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5; Basslink unable to transfer FCAS
F_VS+HWPS_TG_R6 | 2006-01-30 | 1 | Vic and SA Raise 6 sec requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5; Basslink unable to transfer FCAS
F_VS+HWPS_TG_R60 | 2006-01-30 | 1 | Vic and SA Raise 60 sec requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5; Basslink unable to transfer FCAS
F_VS+LREG_0120 | 2006-06-27 | 1 | Vic and SA Lower Regulation Requirement greater than 120 MW, Basslink able to transfer FCAS
F_VS+MG_R5 | 2009-01-01 | 1 | Raise 5 min requirement for a Vic and SA Generation Event, Basslink unable to transfer FCAS
F_VS+MG_R6 | 2006-01-30 | 1 | Raise 6 sec requirement for a Vic and SA Generation Event, Basslink unable to transfer FCAS
F_VS+MG_R60 | 2006-01-30 | 1 | Raise 60 sec requirement for a Vic and SA Generation Event, Basslink unable to transfer FCAS
F_VS+ML_L5_0300 | 2009-01-01 | 1 | Lower 5 min requirement for a Vic and SA Load Event, Basslink unable to transfer FCAS
F_VS+ML_L60_0300 | 2007-04-30 | 1 | Lower 60 sec requirement for a Vic and SA Load Event, Basslink unable to transfer FCAS
F_VS+ML_L6_0300 | 2007-04-30 | 1 | Lower 6 sec requirement for a Vic and SA Load Event, Basslink unable to transfer FCAS
F_VS+RREG_0130 | 2006-01-30 | 1 | Vic and SA RaiseRegulation Requirement greater than 130 MW, Basslink able to transfer FCAS
F_VS+TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic and SA Network Event, TG = 500, Basslink unable to transfer FCAS
F_VS+TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic and SA Network Event, TG = 1000, Basslink unable to transfer FCAS
F_VS+TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic and SA Network Event, TG = 1400, Basslink unable to transfer FCAS
F_VS+TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic and SA Network Event, TG = 1600, Basslink unable to transfer FCAS
F_VS+TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic and SA Network Event, TG = 2000, Basslink unable to transfer FCAS
F_VS+TG_R60_0500 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic and SA Network Event, TG = 500, Basslink unable to transfer FCAS
F_VS+TG_R60_1000 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic and SA Network Event, TG = 1000, Basslink unable to transfer FCAS
F_VS+TG_R60_1400 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic and SA Network Event, TG = 1400, Basslink unable to transfer FCAS
F_VS+TG_R60_1600 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic and SA Network Event, TG = 1600, Basslink unable to transfer FCAS
F_VS+TG_R60_2000 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic and SA Network Event, TG = 2000, Basslink unable to transfer FCAS
F_VS+TG_R6_0500 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic and SA Network Event, TG = 500, Basslink unable to transfer FCAS
F_VS+TG_R6_1000 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic and SA Network Event, TG = 1000, Basslink unable to transfer FCAS
F_VS+TG_R6_1400 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic and SA Network Event, TG = 1400, Basslink unable to transfer FCAS
F_VS+TG_R6_1600 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic and SA Network Event, TG = 1600, Basslink unable to transfer FCAS
F_VS+TG_R6_2000 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic and SA Network Event, TG = 2000, Basslink unable to transfer FCAS
F_VS+TL_L5_0600 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a Vic and SA Network Event, TL = 600, Basslink unable to transfer FCAS
F_VS+TL_L60_0600 | 2006-01-31 | 2 | Lower 60 sec Service Requirement for a Vic and SA Network Event, TL = 600, Basslink unable to transfer FCAS
F_VS+TL_L6_0600 | 2006-01-31 | 2 | Lower 6 sec Service Requirement for a Vic and SA Network Event, TL = 600, Basslink unable to transfer FCAS
F_VST++65_051_0X1L60 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic, SA & Tas Lower 60 sec requirement
F_VST++65_051_0X1R60 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic, SA & Tas Raise 60 sec requirement
F_VST++65_051_0X1_L5 | 2009-01-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic, SA & Tas Lower 5 min requirement
F_VST++65_051_0X1_L6 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic, SA & Tas Lower 6 sec requirement
F_VST++65_051_0X1_R5 | 2009-01-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic, SA & Tas Raise 5 min requirement
F_VST++65_051_0X1_R6 | 2008-07-01 | 1 | Out = Murray to Upper Tumut (65), 060 and 0X1, Vic, SA & Tas Raise 6 sec requirement
F_VST+HWPS_TG_R5 | 2009-01-01 | 1 | Vic, SA and Tas Raise 5 min requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5
F_VST+HWPS_TG_R6 | 2005-12-21 | 1 | Vic, SA and Tas Raise 6 sec requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5
F_VST+HWPS_TG_R60 | 2005-12-21 | 1 | Vic, SA and Tas Raise 60 sec requirement for trip of HWTS-HWPS #1 line, TG = output of HWPS 3,4,5
F_VST+LREG_0120 | 2006-06-27 | 1 | Vic, SA and Tas Lower Regulation Requirement greater than 120 MW
F_VST+MG_R5 | 2009-01-01 | 1 | Raise 5 min requirement for a Vic, SA and Tas Generation Event
F_VST+MG_R6 | 2005-12-21 | 1 | Raise 6 sec requirement for a Vic, SA and Tas Generation Event
F_VST+MG_R60 | 2005-12-21 | 1 | Raise 60 sec requirement for a Vic, SA and Tas Generation Event
F_VST+ML_L5_0300 | 2009-01-01 | 1 | Lower 5 min requirement for a Vic, SA and Tas Load Event
F_VST+ML_L60_0300 | 2007-04-30 | 1 | Lower 60 sec requirement for a Vic, SA and Tas Load Event
F_VST+ML_L6_0300 | 2007-04-30 | 1 | Lower 6 sec requirement for a Vic, SA and Tas Load Event
F_VST+RREG_0130 | 2005-12-21 | 1 | Vic, SA and Tas Raise Regulation Requirement greater than 130 MW
F_VST+TG_R5_0500 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic, SA and Tas Network Event, TG = 500
F_VST+TG_R5_1000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic, SA and Tas Network Event, TG = 1000
F_VST+TG_R5_1400 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic, SA and Tas Network Event, TG = 1400
F_VST+TG_R5_1600 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic, SA and Tas Network Event, TG = 1600
F_VST+TG_R5_2000 | 2009-01-01 | 1 | Raise 5 min Service Requirement for a Vic, SA and Tas Network Event, TG = 2000
F_VST+TG_R60_0500 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic, SA and Tas Network Event, TG = 500
F_VST+TG_R60_1000 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic, SA and Tas Network Event, TG = 1000
F_VST+TG_R60_1400 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic, SA and Tas Network Event, TG = 1400
F_VST+TG_R60_1600 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic, SA and Tas Network Event, TG = 1600
F_VST+TG_R60_2000 | 2006-01-31 | 1 | Raise 60 sec Service Requirement for a Vic, SA and Tas Network Event, TG = 2000
F_VST+TG_R6_0500 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic, SA and Tas Network Event, TG = 500
F_VST+TG_R6_1000 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic, SA and Tas Network Event, TG = 1000
F_VST+TG_R6_1400 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic, SA and Tas Network Event, TG = 1400
F_VST+TG_R6_1600 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic, SA and Tas Network Event, TG = 1600
F_VST+TG_R6_2000 | 2006-01-31 | 1 | Raise 6 sec Service Requirement for a Vic, SA and Tas Network Event, TG = 2000
F_VST+TL_L5_0600 | 2009-01-01 | 1 | Lower 5 min Service Requirement for a Vic, SA and Tas Network Event, TL = 600
F_VST+TL_L60_0600 | 2006-01-31 | 2 | Lower 60 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 600
F_VST+TL_L6_0600 | 2006-01-31 | 2 | Lower 6 sec Service Requirement for a Vic, SA and Tas Network Event, TL = 600
F_VS_V+NIL_L5 | 2006-01-31 | 1 | Out=Nil, Vic System Normal, 5 min ratings, Vic and SA Lower 5 Min requirement = 0
F_VS_V+NIL_L6 | 2006-01-31 | 1 | Out=Nil, Vic System Normal, 5 min ratings, Vic and SA Lower 6 sec requirement = 0
F_VS_V+NIL_L60 | 2006-01-31 | 1 | Out=Nil, Vic System Normal, 5 min ratings, Vic and SA Lower 60 sec requirement = 0
F_VS_V+NIL_LREG | 2006-01-31 | 1 | Out=Nil, Vic System Normal, 5 min ratings, Vic and SA Lower Regulation requirement = 0
F_V_APD01_L5 | 2007-03-27 | 1 | Out= NIL, APD Potline 1 L5 Requirement <= 0MW
F_V_APD01_L6 | 2007-03-27 | 1 | Out= NIL, APD Potline 1 L6 Requirement <= 0MW
F_V_APD01_L60 | 2007-03-27 | 1 | Out= NIL, APD Potline 1 L60 Requirement <= 0MW
F_V_APD01_R5 | 2007-03-27 | 1 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW
F_V_APD01_R6 | 2007-03-27 | 1 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW
F_V_APD01_R60 | 2007-03-27 | 1 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW
F_V_APD02_L5 | 2007-03-27 | 1 | Out= NIL, APD Potline 2 L5 Requirement <= 0MW
F_V_APD02_L6 | 2007-03-27 | 1 | Out= NIL, APD Potline 2 L6 Requirement <= 0MW
F_V_APD02_L60 | 2007-03-27 | 1 | Out= NIL, APD Potline 2 L60 Requirement <= 0MW
F_V_APD02_R5 | 2007-03-27 | 1 | Out= NIL, APD Potline 2 R5 Requirement <= 0MW
F_V_APD02_R6 | 2007-03-27 | 1 | Out= NIL, APD Potline 2 R6 Requirement <= 0MW
F_V_APD02_R60 | 2007-03-27 | 1 | Out= NIL, APD Potline 2 R60 Requirement <= 0MW
F_V_APS_L5 | 2007-03-27 | 1 | Out= NIL, Angelsa L5 Requirement <= 0MW
F_V_DARTM1_L6 | 2007-03-27 | 1 | Out= NIL, Dartmouth L6 Requirement <= 0MW
F_V_DARTM1_L60 | 2007-03-27 | 1 | Out= NIL, Dartmouth L60 Requirement <= 0MW
F_V_DARTM1_LREG | 2007-03-27 | 1 | Out= NIL, Dartmouth LREG Requirement <= 0MW
F_V_DARTM1_R5 | 2007-03-27 | 1 | Out= NIL, Dartmouth R5 Requirement <= 0MW
F_V_DARTM1_R6 | 2007-03-27 | 1 | Out= NIL, Dartmouth R6 Requirement <= 0MW
F_V_DARTM1_R60 | 2007-03-27 | 1 | Out= NIL, Dartmouth R60 Requirement <= 0MW
F_V_DARTM1_RREG | 2007-03-27 | 1 | Out= NIL, Dartmouth RREG Requirement <= 0MW
F_V_EILDON1_L6 | 2007-03-27 | 1 | Out= NIL, Eildon 1 L6 Requirement <= 0MW
F_V_EILDON1_L60 | 2007-03-27 | 1 | Out= NIL, Eildon 1 L60 Requirement <= 0MW
F_V_EILDON1_LREG | 2007-03-27 | 1 | Out= NIL, Eildon 1 LREG Requirement <= 0MW
F_V_EILDON1_R5 | 2007-03-27 | 1 | Out= NIL, Eildon 1 R5 Requirement <= 0MW
F_V_EILDON1_R6 | 2007-03-27 | 1 | Out= NIL, Eildon 1 R6 Requirement <= 0MW
F_V_EILDON1_R60 | 2007-03-27 | 1 | Out= NIL, Eildon 1 R60 Requirement <= 0MW
F_V_EILDON1_RREG | 2007-03-27 | 1 | Out= NIL, Eildon 1 RREG Requirement <= 0MW
F_V_EILDON2_L6 | 2007-03-27 | 1 | Out= NIL, Eildon 2 L6 Requirement <= 0MW
F_V_EILDON2_L60 | 2007-03-27 | 1 | Out= NIL, Eildon 2 L60 Requirement <= 0MW
F_V_EILDON2_LREG | 2007-03-27 | 1 | Out= NIL, Eildon 2 LREG Requirement <= 0MW
F_V_EILDON2_R5 | 2007-03-27 | 1 | Out= NIL, Eildon 2 R5 Requirement <= 0MW
F_V_EILDON2_R6 | 2007-03-27 | 1 | Out= NIL, Eildon 2 R6 Requirement <= 0MW
F_V_EILDON2_R60 | 2007-03-27 | 1 | Out= NIL, Eildon 2 R60 Requirement <= 0MW
F_V_EILDON2_RREG | 2007-03-27 | 1 | Out= NIL, Eildon 2 RREG Requirement <= 0MW
F_V_LOYYB1_L5 | 2007-03-27 | 1 | Out= NIL, Loy Yang B1 L5 Requirement <= 0MW
F_V_LOYYB1_L6 | 2007-03-27 | 1 | Out= NIL, Loy Yang B1 L6 Requirement <= 0MW
F_V_LOYYB1_L60 | 2007-03-27 | 1 | Out= NIL, Loy Yang B1 L60 Requirement <= 0MW
F_V_LOYYB1_LREG | 2007-03-27 | 1 | Out= NIL, Loy Yang B1 LREG Requirement <= 0MW
F_V_LOYYB1_R5 | 2007-03-27 | 1 | Out= NIL, Loy Yang B1 R5 Requirement <= 0MW
F_V_LOYYB1_R6 | 2007-03-27 | 1 | Out= NIL, Loy Yang B1 R6 Requirement <= 0MW
F_V_LOYYB1_R60 | 2007-03-27 | 1 | Out= NIL, Loy Yang B1 R60 Requirement <= 0MW
F_V_LOYYB1_RREG | 2007-03-27 | 1 | Out= NIL, Loy Yang B1 RREG Requirement <= 0MW
F_V_LOYYB2_L5 | 2007-03-27 | 1 | Out= NIL, Loy Yang B2 L5 Requirement <= 0MW
F_V_LOYYB2_L6 | 2007-03-27 | 1 | Out= NIL, Loy Yang B2 L6 Requirement <= 0MW
F_V_LOYYB2_L60 | 2007-03-27 | 1 | Out= NIL, Loy Yang B2 L60 Requirement <= 0MW
F_V_LOYYB2_LREG | 2007-03-27 | 1 | Out= NIL, Loy Yang B2 LREG Requirement <= 0MW
F_V_LOYYB2_R5 | 2007-03-27 | 1 | Out= NIL, Loy Yang B2 R5 Requirement <= 0MW
F_V_LOYYB2_R6 | 2007-03-27 | 1 | Out= NIL, Loy Yang B2 R6 Requirement <= 0MW
F_V_LOYYB2_R60 | 2007-03-27 | 1 | Out= NIL, Loy Yang B2 R60 Requirement <= 0MW
F_V_LOYYB2_RREG | 2007-03-27 | 1 | Out= NIL, Loy Yang B2 RREG Requirement <= 0MW
F_V_LYA1_L6 | 2007-03-27 | 1 | Out= NIL, Loy Yang A1 L6 Requirement <= 0MW
F_V_LYA1_L60 | 2007-03-27 | 1 | Out= NIL, Loy Yang A1 L60 Requirement <= 0MW
F_V_LYA1_LREG | 2007-03-27 | 1 | Out= NIL, Loy Yang A1 LREG Requirement <= 0MW
F_V_LYA1_R6 | 2007-03-27 | 1 | Out= NIL, Loy Yang A1 R6 Requirement <= 0MW
F_V_LYA1_R60 | 2007-03-27 | 1 | Out= NIL, Loy Yang A1 R60 Requirement <= 0MW
F_V_LYA1_RREG | 2007-03-27 | 1 | Out= NIL, Loy Yang A1 RREG Requirement <= 0MW
F_V_LYA2_L6 | 2007-03-27 | 1 | Out= NIL, Loy Yang A2 L6 Requirement <= 0MW
F_V_LYA2_L60 | 2007-03-27 | 1 | Out= NIL, Loy Yang A2 L60 Requirement <= 0MW
F_V_LYA2_LREG | 2007-03-27 | 1 | Out= NIL, Loy Yang A2 LREG Requirement <= 0MW
F_V_LYA2_R6 | 2007-03-27 | 1 | Out= NIL, Loy Yang A2 R6 Requirement <= 0MW
F_V_LYA2_R60 | 2007-03-27 | 1 | Out= NIL, Loy Yang A2 R60 Requirement <= 0MW
F_V_LYA2_RREG | 2007-03-27 | 1 | Out= NIL, Loy Yang A2 RREG Requirement <= 0MW
F_V_LYA3_L6 | 2007-03-27 | 1 | Out= NIL, Loy Yang A3 L6 Requirement <= 0MW
F_V_LYA3_L60 | 2007-03-27 | 1 | Out= NIL, Loy Yang A3 L60 Requirement <= 0MW
F_V_LYA3_LREG | 2007-03-27 | 1 | Out= NIL, Loy Yang A3 LREG Requirement <= 0MW
F_V_LYA3_R6 | 2007-03-27 | 1 | Out= NIL, Loy Yang A3 R6 Requirement <= 0MW
F_V_LYA3_R60 | 2007-03-27 | 1 | Out= NIL, Loy Yang A3 R60 Requirement <= 0MW
F_V_LYA3_RREG | 2007-03-27 | 1 | Out= NIL, Loy Yang A3 RREG Requirement <= 0MW
F_V_LYA4_L6 | 2007-03-27 | 1 | Out= NIL, Loy Yang A4 L6 Requirement <= 0MW
F_V_LYA4_L60 | 2007-03-27 | 1 | Out= NIL, Loy Yang A4 L60 Requirement <= 0MW
F_V_LYA4_LREG | 2007-03-27 | 1 | Out= NIL, Loy Yang A4 LREG Requirement <= 0MW
F_V_LYA4_R6 | 2007-03-27 | 1 | Out= NIL, Loy Yang A4 R6 Requirement <= 0MW
F_V_LYA4_R60 | 2007-03-27 | 1 | Out= NIL, Loy Yang A4 R60 Requirement <= 0MW
F_V_LYA4_RREG | 2007-03-27 | 1 | Out= NIL, Loy Yang A4 RREG Requirement <= 0MW
F_V_MBMK_L6 | 2007-03-01 | 1 | Lower 6 sec Service Requirement for McKay Creek PS set to zero due to outage of Mt Beauty to Mackay 220 kV line
F_V_MBMK_L60 | 2007-03-01 | 1 | Lower 60 sec Service Requirement for McKay Creek PS set to zero due to outage of Mt Beauty to Mackay 220 kV line
F_V_MBMK_LREG | 2007-03-01 | 1 | Lower Regulation Service Requirement for McKay Creek PS set to zero due to outage of Mt Beauty to Mackay 220 kV line
F_V_MBMK_R5 | 2007-03-01 | 1 | Raise 5 min Service Requirement for McKay Creek PS set to zero due to outage of Mt Beauty to Mackay 220 kV line
F_V_MBMK_R6 | 2007-03-01 | 1 | Raise 6 sec Service Requirement for McKay Creek PS set to zero due to outage of Mt Beauty to Mackay 220 kV line
F_V_MBMK_R60 | 2007-03-01 | 1 | Raise 60 sec Service Requirement for McKay Creek PS set to zero due to outage of Mt Beauty to Mackay 220 kV line
F_V_MBMK_RREG | 2007-03-01 | 1 | Raise Regulation Service Requirement for McKay Creek PS set to zero due to outage of Mt Beauty to Mackay 220 kV line
F_V_MBWK_L6 | 2007-03-01 | 1 | Lower 6 sec Service Requirement for West Kiewa PS set to zero due to outage of Mt Beauty to West Kiewa 220 kV line
F_V_MBWK_L60 | 2007-03-01 | 1 | Lower 60 sec Service Requirement for West Kiewa PS set to zero due to outage of Mt Beauty to West Kiewa 220 kV line
F_V_MBWK_LREG | 2007-03-01 | 1 | Lower Regulation Service Requirement for West Kiewa PS set to zero due to outage of Mt Beauty to West Kiewa 220 kV line
F_V_MBWK_R6 | 2007-03-01 | 1 | Raise 6 sec Service Requirement for West Kiewa PS set to zero due to outage of Mt Beauty to West Kiewa 220 kV line
F_V_MBWK_R60 | 2007-03-01 | 1 | Raise 60 sec Service Requirement for West Kiewa PS set to zero due to outage of Mt Beauty to West Kiewa 220 kV line
F_V_MBWK_RREG | 2007-03-01 | 1 | Raise Regulation Service Requirement for West Kiewa PS set to zero due to outage of Mt Beauty to West Kiewa 220 kV line
F_V_MB_BUS1_L6 | 2007-06-13 | 2 | Lower 6 sec Service Requirement for McKay Creek and West Kiewa PSs set to zero due to outage of Mt Beauty No 1 220 kV Bus
F_V_MB_BUS1_L60 | 2007-06-13 | 2 | Lower 60 sec Service Requirement for McKay Creek and West Kiewa PSs set to zero due to outage of Mt Beauty No 1 220 kV Bus
F_V_MB_BUS1_LREG | 2007-06-13 | 2 | Lower Regulation Service Requirement for McKay Creek and West Kiewa PSs set to zero due to outage of Mt Beauty No 1 220 kV Bus
F_V_MB_BUS1_R5 | 2007-06-13 | 2 | Raise 5 min Service Requirement for McKay Creek and West Kiewa PSs set to zero due to outage of Mt Beauty No 1 220 kV Bus
F_V_MB_BUS1_R6 | 2007-06-13 | 2 | Raise 6 sec Service Requirement for McKay Creek and West Kiewa PSs set to zero due to outage of Mt Beauty No 1 220 kV Bus
F_V_MB_BUS1_R60 | 2007-06-13 | 2 | Raise 60 sec Service Requirement for McKay Creek and West Kiewa PSs set to zero due to outage of Mt Beauty No 1 220 kV Bus
F_V_MB_BUS1_RREG | 2007-06-13 | 2 | Raise Regulation Service Requirement for McKay Creek and West Kiewa PSs set to zero due to outage of Mt Beauty No 1 220 kV Bus
F_V_MB_BUS2_L6 | 2007-06-13 | 2 | Lower 6 sec Service Requirement for Dartmouth PS set to zero due to outage of Mt Beauty No 2 220 kV Bus
F_V_MB_BUS2_L60 | 2007-06-13 | 2 | Lower 60 sec Service Requirement for Dartmouth PS set to zero due to outage of Mt Beauty No 2 220 kV Bus
F_V_MB_BUS2_LREG | 2007-06-13 | 2 | Lower Regulation Service Requirement for Dartmouth PS set to zero due to outage of Mt Beauty No 2 220 kV Bus
F_V_MB_BUS2_R5 | 2007-06-13 | 2 | Raise 5 min Service Requirement for Dartmouth PS set to zero due to outage of Mt Beauty No 2 220 kV Bus
F_V_MB_BUS2_R6 | 2007-06-13 | 2 | Raise 6 sec Service Requirement for Dartmouth PS set to zero due to outage of Mt Beauty No 2 220 kV Bus
F_V_MB_BUS2_R60 | 2007-06-13 | 2 | Raise 60 sec Service Requirement for Dartmouth PS set to zero due to outage of Mt Beauty No 2 220 kV Bus
F_V_MB_BUS2_RREG | 2007-06-13 | 2 | Raise Regulation Service Requirement for Dartmouth PS set to zero due to outage of Mt Beauty No 2 220 kV Bus
F_V_MCKAY1_L6 | 2007-03-27 | 1 | Out= NIL, Mackay 1 L6 Requirement <= 0MW
F_V_MCKAY1_L60 | 2007-03-27 | 1 | Out= NIL, Mackay 1 L60 Requirement <= 0MW
F_V_MCKAY1_LREG | 2007-03-27 | 1 | Out= NIL, Mackay 1 LREG Requirement <= 0MW
F_V_MCKAY1_R5 | 2007-03-27 | 1 | Out= NIL, Mackay 1 R5 Requirement <= 0MW
F_V_MCKAY1_R6 | 2007-03-27 | 1 | Out= NIL, Mackay 1 R6 Requirement <= 0MW
F_V_MCKAY1_R60 | 2007-03-27 | 1 | Out= NIL, Mackay 1 R60 Requirement <= 0MW
F_V_MCKAY1_RREG | 2007-03-27 | 1 | Out= NIL, Mackay 1 RREG Requirement <= 0MW
F_V_MCKAY2_L6 | 2007-03-27 | 1 | Out= NIL, Mackay 2 L6 Requirement <= 0MW
F_V_MCKAY2_L60 | 2007-03-27 | 1 | Out= NIL, Mackay 2 L60 Requirement <= 0MW
F_V_MCKAY2_LREG | 2007-03-27 | 1 | Out= NIL, Mackay 2 LREG Requirement <= 0MW
F_V_MCKAY2_R5 | 2007-03-27 | 1 | Out= NIL, Mackay 2 R5 Requirement <= 0MW
F_V_MCKAY2_R6 | 2007-03-27 | 1 | Out= NIL, Mackay 2 R6 Requirement <= 0MW
F_V_MCKAY2_R60 | 2007-03-27 | 1 | Out= NIL, Mackay 2 R60 Requirement <= 0MW
F_V_MCKAY2_RREG | 2007-03-27 | 1 | Out= NIL, Mackay 2 RREG Requirement <= 0MW
F_V_MURRAY_L5 | 2008-07-01 | 1 | Out= NIL, Murray L5 Requirement <= 0MW
F_V_MURRAY_L6 | 2008-07-01 | 1 | Out= NIL, Murray L6 Requirement <= 0MW
F_V_MURRAY_L60 | 2008-07-01 | 1 | Out= NIL, Murray L60 Requirement <= 0MW
F_V_MURRAY_LREG | 2008-07-01 | 1 | Out= NIL, Murray LREG Requirement <= 0MW
F_V_MURRAY_R5 | 2008-07-01 | 1 | Out= NIL, Murray R5 Requirement <= 0MW
F_V_MURRAY_R6 | 2008-07-01 | 1 | Out= NIL, Murray R6 Requirement <= 0MW
F_V_MURRAY_R60 | 2008-07-01 | 1 | Out= NIL, Murray R60 Requirement <= 0MW
F_V_MURRAY_RREG | 2008-07-01 | 1 | Out= NIL, Murray RREG Requirement <= 0MW
F_V_NPS_L6 | 2007-03-27 | 1 | Out= NIL, Newport L6 Requirement <= 0MW
F_V_NPS_L60 | 2007-03-27 | 1 | Out= NIL, Newport L60 Requirement <= 0MW
F_V_NPS_LREG | 2007-03-27 | 1 | Out= NIL, Newport LREG Requirement <= 0MW
F_V_NPS_R6 | 2007-03-27 | 1 | Out= NIL, Newport R6 Requirement <= 0MW
F_V_NPS_R60 | 2007-03-27 | 1 | Out= NIL, Newport R60 Requirement <= 0MW
F_V_NPS_RREG | 2007-03-27 | 1 | Out= NIL, Newport RREG Requirement <= 0MW
F_V_PTH01_L5 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 1 L5 Requirement <= 0MW
F_V_PTH01_L6 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 1 L6 Requirement <= 0MW
F_V_PTH01_L60 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 1 L60 Requirement <= 0MW
F_V_PTH01_R5 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 1 R5 Requirement <= 0MW
F_V_PTH01_R6 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 1 R6 Requirement <= 0MW
F_V_PTH01_R60 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 1 R60 Requirement <= 0MW
F_V_PTH02_L5 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 2 L5 Requirement <= 0MW
F_V_PTH02_L6 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 2 L6 Requirement <= 0MW
F_V_PTH02_L60 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 2 L60 Requirement <= 0MW
F_V_PTH02_R5 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 2 R5 Requirement <= 0MW
F_V_PTH02_R6 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 2 R6 Requirement <= 0MW
F_V_PTH02_R60 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 2 R60 Requirement <= 0MW
F_V_PTH03_L5 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 3 L5 Requirement <= 0MW
F_V_PTH03_L6 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 3 L6 Requirement <= 0MW
F_V_PTH03_L60 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 3 L60 Requirement <= 0MW
F_V_PTH03_R5 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 3 R5 Requirement <= 0MW
F_V_PTH03_R6 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 3 R6 Requirement <= 0MW
F_V_PTH03_R60 | 2007-03-27 | 1 | Out= NIL, Point Henry Potline 3 R60 Requirement <= 0MW
F_V_SNOWYGJP_L5 | 2008-07-01 | 1 | Out= NIL, Jindabyne Pump L5 Requirement <= 0MW
F_V_SNOWYGJP_R5 | 2008-07-01 | 1 | Out= NIL, Jindabyne Pump R5 Requirement <= 0MW
F_V_SNOWYGJP_R6 | 2008-07-01 | 1 | Out= NIL, Jindabyne Pump R6 Requirement <= 0MW
F_V_SNOWYGJP_R60 | 2008-07-01 | 1 | Out= NIL, Jindabyne Pump R60 Requirement <= 0MW
F_V_WKIEWA1_L6 | 2007-03-27 | 1 | Out= NIL, West Kiewa 1 L6 Requirement <= 0MW
F_V_WKIEWA1_L60 | 2007-03-27 | 1 | Out= NIL, West Kiewa 1 L60 Requirement <= 0MW
F_V_WKIEWA1_LREG | 2007-03-27 | 1 | Out= NIL, West Kiewa 1 LREG Requirement <= 0MW
F_V_WKIEWA1_R6 | 2007-03-27 | 1 | Out= NIL, West Kiewa 1 R6 Requirement <= 0MW
F_V_WKIEWA1_R60 | 2007-03-27 | 1 | Out= NIL, West Kiewa 1 R60 Requirement <= 0MW
F_V_WKIEWA1_RREG | 2007-03-27 | 1 | Out= NIL, West Kiewa 1 RREG Requirement <= 0MW
F_V_WKIEWA2_L6 | 2007-03-27 | 1 | Out= NIL, West Kiewa 2 L6 Requirement <= 0MW
F_V_WKIEWA2_L60 | 2007-03-27 | 1 | Out= NIL, West Kiewa 2 L60 Requirement <= 0MW
F_V_WKIEWA2_LREG | 2007-03-27 | 1 | Out= NIL, West Kiewa 2 LREG Requirement <= 0MW
F_V_WKIEWA2_R6 | 2007-03-27 | 1 | Out= NIL, West Kiewa 2 R6 Requirement <= 0MW
F_V_WKIEWA2_R60 | 2007-03-27 | 1 | Out= NIL, West Kiewa 2 R60 Requirement <= 0MW
F_V_WKIEWA2_RREG | 2007-03-27 | 1 | Out= NIL, West Kiewa 2 RREG Requirement <= 0MW
F_V_YWPS1_L5 | 2007-03-27 | 1 | Out= NIL, Yallourn W1 L5 Requirement <= 0MW
F_V_YWPS1_L6 | 2007-03-27 | 1 | Out= NIL, Yallourn W1 L6 Requirement <= 0MW
F_V_YWPS1_L60 | 2007-03-27 | 1 | Out= NIL, Yallourn W1 L60 Requirement <= 0MW
F_V_YWPS1_LREG | 2007-03-27 | 1 | Out= NIL, Yallourn W1 LREG Requirement <= 0MW
F_V_YWPS1_R5 | 2007-03-27 | 1 | Out= NIL, Yallourn W1 R5 Requirement <= 0MW
F_V_YWPS1_R6 | 2007-03-27 | 1 | Out= NIL, Yallourn W1 R6 Requirement <= 0MW
F_V_YWPS1_R60 | 2007-03-27 | 1 | Out= NIL, Yallourn W1 R60 Requirement <= 0MW
F_V_YWPS1_RREG | 2007-03-27 | 1 | Out= NIL, Yallourn W1 RREG Requirement <= 0MW
F_V_YWPS2_L5 | 2007-03-27 | 1 | Out= NIL, Yallourn W2 L5 Requirement <= 0MW
F_V_YWPS2_L6 | 2007-03-27 | 1 | Out= NIL, Yallourn W2 L6 Requirement <= 0MW
F_V_YWPS2_L60 | 2007-03-27 | 1 | Out= NIL, Yallourn W2 L60 Requirement <= 0MW
F_V_YWPS2_LREG | 2007-03-27 | 1 | Out= NIL, Yallourn W2 LREG Requirement <= 0MW
F_V_YWPS2_R5 | 2007-03-27 | 1 | Out= NIL, Yallourn W2 R5 Requirement <= 0MW
F_V_YWPS2_R6 | 2007-03-27 | 1 | Out= NIL, Yallourn W2 R6 Requirement <= 0MW
F_V_YWPS2_R60 | 2007-03-27 | 1 | Out= NIL, Yallourn W2 R60 Requirement <= 0MW
F_V_YWPS2_RREG | 2007-03-27 | 1 | Out= NIL, Yallourn W2 RREG Requirement <= 0MW
F_V_YWPS3_L5 | 2007-03-27 | 1 | Out= NIL, Yallourn W3 L5 Requirement <= 0MW
F_V_YWPS3_L6 | 2007-03-27 | 1 | Out= NIL, Yallourn W3 L6 Requirement <= 0MW
F_V_YWPS3_L60 | 2007-03-27 | 1 | Out= NIL, Yallourn W3 L60 Requirement <= 0MW
F_V_YWPS3_LREG | 2007-03-27 | 1 | Out= NIL, Yallourn W3 LREG Requirement <= 0MW
F_V_YWPS3_R5 | 2007-03-27 | 1 | Out= NIL, Yallourn W3 R5 Requirement <= 0MW
F_V_YWPS3_R6 | 2007-03-27 | 1 | Out= NIL, Yallourn W3 R6 Requirement <= 0MW
F_V_YWPS3_R60 | 2007-03-27 | 1 | Out= NIL, Yallourn W3 R60 Requirement <= 0MW
F_V_YWPS3_RREG | 2007-03-27 | 1 | Out= NIL, Yallourn W3 RREG Requirement <= 0MW
F_V_YWPS4_L5 | 2007-03-27 | 1 | Out= NIL, Yallourn W4 L5 Requirement <= 0MW
F_V_YWPS4_L6 | 2007-03-27 | 1 | Out= NIL, Yallourn W4 L6 Requirement <= 0MW
F_V_YWPS4_L60 | 2007-03-27 | 1 | Out= NIL, Yallourn W4 L60 Requirement <= 0MW
F_V_YWPS4_LREG | 2007-03-27 | 1 | Out= NIL, Yallourn W4 LREG Requirement <= 0MW
F_V_YWPS4_R5 | 2007-03-27 | 1 | Out= NIL, Yallourn W4 R5 Requirement <= 0MW
F_V_YWPS4_R6 | 2007-03-27 | 1 | Out= NIL, Yallourn W4 R6 Requirement <= 0MW
F_V_YWPS4_R60 | 2007-03-27 | 1 | Out= NIL, Yallourn W4 R60 Requirement <= 0MW
F_V_YWPS4_RREG | 2007-03-27 | 1 | Out= NIL, Yallourn W4 RREG Requirement <= 0MW
I>VS-500 | 2004-02-12 | 1 | VIC-SA Export Limit Nil Outage
MT_F_N-Q_ARTW | 2004-09-23 | 1 | Outage = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330kV line
MT_F_Q-N_ARTW | 2004-09-23 | 1 | Outage = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on trip of the largest Qld Generator
MT_N>>N-5MRAS_A_15M | 2008-10-23 | 1 | Out= Snowy 5MRAS scheme, avoid LowerTumut to Canberra (07) O/L (15 min rating) on UpperTumut-Canberra(01) trip
MT_N>>N-5MRAS_B_15M | 2008-10-23 | 1 | Out= Snowy 5MRAS scheme, avoid UpperTumut to Canberra (01) O/L (15 min rating) on LowerTumut-Canberra(07) trip
MT_N>>N-5MRAS_C_15M | 2008-10-23 | 1 | Out= Snowy 5MRAS scheme, avoid LowerTumut to Yass (3) O/L (15 min rating) on LowerTumut-Canberra(07) trip
MT_N>>N-5MRAS_D_15M | 2008-10-23 | 1 | Out= Snowy 5MRAS scheme, avoid UpperTumut to Canberra (01) O/L (15 min rating) on LowerTumut-Yass(3) trip
MT_N>>N-5MRAS_E_15M | 2008-10-23 | 1 | Out= Snowy 5MRAS scheme, avoid UpperTumut to Canberra (01) O/L (15 min rating) on UpperTumut-Yass(2) trip
MT_N>>N-5MRAS_F_15M | 2008-10-23 | 1 | Out= Snowy 5MRAS scheme, avoid UpperTumut to Yass (2) O/L (15 min rating) on Canberra-UpperTumut(01) trip
MT_N>>N-5MRAS_G_15M | 2008-10-23 | 1 | Out= Snowy 5MRAS scheme, avoid UpperTumut to Yass (2) O/L (15 min rating) on LowerTumut-Yass(3) trip
MT_N>>N-5MRAS_H_15M | 2008-10-23 | 1 | Out= Snowy 5MRAS scheme, avoid LowerTumut to Canberra (07) O/L (15 min rating) on LowerTumut-Yass(3) trip
MT_NSW_HEADROOM | 2008-07-07 | 1 | NSW Import Constraint for LRC Assessment
MT_N_TALWA1_300 | 2009-01-23 | 1 | Tallawarra upper limit of 300MW
MT_N_TALWA1_ZERO | 2008-12-16 | 1 | Tallawarra upper limit of 0 MW
MT_Q^^NIL_TR_0708_B | 2007-10-03 | 1 | Out=Nil system normal ;MTPASA only, Single contingency on any one of the four following 275kV feeders: CLTR , TRBK,SBE, WV & WOPW. Summer 07/08 Offset = +340 MW
MT_Q^^NIL_TR_0708_C | 2007-11-29 | 1 | Out=Nil system normal ;MTPASA only, Single contingency on any one of the four following 275kV feeders: CLTR , TRBK,SBE, WV & WOPW. Summer 07/08 (delayed S3 Greenbank-H14 Middle Ridge line augmentation) Offset = +45 MW
MT_Q^^NIL_TR_0809 | 2007-07-02 | 1 | Out=Nil system normal ;MTPASA only, Single contingency on any one of the four following 275kV feeders: CLTR , TRBK,SBE, WV & WOPW. Summer 08/09 Offset = +520 MW
MT_Q_CS_1900 | 2007-07-02 | 1 | Qld Central to Qld South upper transfer limit of 1900 MW ( MTPASA ) Summer 07/08 limit implementation
MT_Q_CS_2000 | 2007-07-02 | 2 | Qld Central to Qld South upper transfer limit of 2000 MW ( MTPASA ) Summer 08/09 limit implementation
MT_S_HALLWF1 | 2008-12-08 | 1 | Out= Nil; Limit Hallet windfarm generation for MT PASA
MT_S_LB2 | 2007-06-18 | 2 | Out= Nil; Limit Lake Bonney 2 generation.
MT_S_SNOWTWN1 | 2008-12-08 | 1 | Out= Nil; Limit Snowtown windfarm generation for MT PASA
MT_VIC_HEADROOM | 2008-07-07 | 1 | VIC Import Constraint for LRC Assessment
N::N_BWMP_1 | 2008-10-23 | 1 | Out= Bayswater-Mt Piper (73) line, transient stability limit (Qld to NSW) for loss of Liddell-Newcastle (81) line
N::N_BWMP_BWWW | 2008-10-30 | 1 | Out= both Bayswater to MtPiper/Wallerawang (73 + 74), transient stability limit (Qld to NSW) for loss of Liddell-Newcastle (81) line
N::N_BWMP_BWWW_N-2 | 2008-11-19 | 2 | Out= Nil, Loss of both Bayswater-Mt.Piper(73) & Bayswater-Wallerawang (74) declared credible, transient stability limit
N::N_BWSW_BWRG_N-2 | 2008-11-18 | 1 | Out= Nil, Loss of both Bayswater-Regentville(31) & Bayswater-Sydney West (32) declared credible, transient stability limit
N::N_BWSW_RGSW_N-2 | 2008-11-18 | 1 | Out= Nil, Loss of Bayswater-Sydney West (32) & Regentville-Sydney West (38) declared credible, transient stability limit
N::N_BWWW_1 | 2006-04-18 | 1 | Out= Bayswater-Wallerawang(74), limit flow South from BW,LD to avoid instability on Liddell-Newcastle(81) fault
N::N_LDNC_1 | 2008-10-23 | 1 | Out= Liddell-Newcastle(81), transient stability limit (Qld to NSW) for loss of Liddell-Tomago (82) line
N::N_LDNC_LDTM_N-2 | 2008-12-09 | 1 | Out= Nil, Loss of both Liddell-Newcastle(81) & Liddell-Tomago (82) declared credible, transient stability limit (Qld to NSW)
N::N_LDTM_1 | 2008-07-01 | 1 | Out= Liddell-Tomago (82) line, transient stability limit (Qld to NSW) for loss of Liddell-Newcastle (81) line
N::Q_ARTW_A1 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA positive and 8 units in service at Bayswater and Liddell
N::Q_ARTW_A2 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_ARTW_A3 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 to 1220 MW, 8 units in service at Bayswater and Liddell
N::Q_ARTW_A4 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_ARTW_A5 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_ARTW_A7 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 to 1270MW, 7 or less units in service at Bayswater and Liddell
N::Q_ARTW_B2 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: V-SN flows of 500 to 1000 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_ARTW_B3 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: V-SN flows of 1000 to 1170 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_ARTW_B5 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability for: V-SN flows of 390 to 1000 MW,2, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_ARTW_B6 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: V-SN flows of 1000 to 1170 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_ARTW_B8 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: V-SN flows of 500 to 1000 MW, 7 or less units in service at Bayswater and Liddell
N::Q_ARTW_B9 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: V-SN flows of 1000 to 1170 MW, 7 or less units in service at Bayswater and Liddell
N::Q_ARTW_C_1A | 2006-03-24 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability for a trip of Callide C3
N::Q_ARTW_C_1B | 2006-03-24 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability for a trip of a Callide C4
N::Q_ARTW_C_2A | 2006-03-24 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability for a trip of a Millmerran #1, for 1 unit online at Millmerran
N::Q_ARTW_C_2B | 2006-03-24 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability for a trip of a Millmerran #2, for 1 unit online at Millmerran
N::Q_ARTW_D | 2006-03-24 | 1 | Out= Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for a Tarong to Braemar (8814 or 8815) Fault, 2 units in service at Millmerran
N::Q_ARTW_E | 2006-03-24 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for trip of a Tarong North unit
N::Q_ARTW_F | 2007-07-06 | 2 | Out= Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for trip of Kogan Creek
N::Q_BR_VC_A1 | 2008-07-01 | 1 | Out= Braemar SVC, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_BR_VC_A2 | 2008-07-01 | 1 | Out= Braemar SVC, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_BR_VC_A3 | 2008-07-01 | 1 | Out= Braemar SVC, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 MW to 1220MW, 8 units in service at Bayswater and Liddell
N::Q_BR_VC_A4 | 2008-07-01 | 1 | Out= Braemar SVC, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_BR_VC_A5 | 2008-07-01 | 1 | Out= Braemar SVC, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_BR_VC_A7 | 2008-07-01 | 1 | Out= Braemar SVC, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 to 1270 MW, 7 or less units in service at Bayswater and Liddell
N::Q_BR_VC_B2 | 2008-07-01 | 1 | Out= Braemar SVC, NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 500 to 100 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_BR_VC_B3 | 2008-07-01 | 1 | Out= Braemar SVC, NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_BR_VC_B5 | 2008-07-01 | 1 | Out= Braemar SVC, NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 390 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_BR_VC_B6 | 2008-07-01 | 1 | Out= Braemar SVC, NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_BR_VC_B8 | 2008-07-01 | 1 | Out= Braemar SVC, NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 500 to 1000 MW, 7 or less units in service at Bayswater and Liddell
N::Q_BR_VC_B9 | 2008-07-01 | 1 | Out = Braemar SVC, NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 1000 to 1170 MW, 7 or less units in service at Bayswater and Liddell
N::Q_BR_VC_C_1A | 2005-08-30 | 1 | Out = Braemar SVC, NSW to Qld Transient Stability for a trip of Callide C3
N::Q_BR_VC_C_1B | 2005-08-30 | 1 | Out = Braemar SVC, NSW to Qld Transient Stability for a trip of a Callide C4
N::Q_BR_VC_C_2A | 2005-08-30 | 1 | Out = Braemar SVC, NSW to Qld Transient Stability for a trip of a Millmerran #1, for 1 unit online at Millmerran
N::Q_BR_VC_C_2B | 2005-08-30 | 1 | Out = Braemar SVC, NSW to Qld Transient Stability for a trip of a Millmerran #2, for 1 unit online at Millmerran
N::Q_BR_VC_D | 2005-08-30 | 1 | Out = Braemar SVC, NSW to Qld Transient Stability Limit for a Tarong to Braemar (8814 or 8815) Fault, 2 units in service at Millmerran
N::Q_BR_VC_E | 2005-08-30 | 1 | Out = Braemar SVC, NSW to Qld Transient Stability Limit for trip of a Tarong North unit
N::Q_BR_VC_F | 2007-07-06 | 2 | Out= Braemar SVC, NSW to Qld Transient Stability Limit for trip of Kogan Creek
N::Q_BWLD_N-2 | 2008-12-10 | 1 | Out= Nil, Loss of Bayswater to Liddell (33 and 34) lines declared credible, avoid Synch.loss(N::Q).
N::Q_BWMP_1 | 2008-10-23 | 1 | Out= Bayswater-Mt Piper(73), limit flow to Queensland to avoid instability on Liddell-Newcastle(81) fault
N::Q_BWMP_BWWW | 2008-10-30 | 1 | Out= Bayswater-Mt Piper(73) + Bayswater to Wallerawang (74), limit flow to Queensland to avoid instability on Liddell-Newcastle(81) fault
N::Q_BWWW_1 | 2006-04-18 | 1 | Out= Bayswater-Wallerawang(74), limit flow to Queensland to avoid instability on Liddell-Newcastle(81) fault
N::Q_DDWO_A1 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_DDWO_A2 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_DDWO_A3 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 MW to 1220MW, 8 units in service at Bayswater and Liddell
N::Q_DDWO_A4 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_DDWO_A5 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_DDWO_A7 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 to 1270 MW, 7 or less units in service at Bayswater and Liddell
N::Q_DDWO_B2 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 500 to 100 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_DDWO_B3 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_DDWO_B5 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 390 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_DDWO_B6 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_DDWO_B8 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 500 to 1000 MW, 7 or less units in service at Bayswater and Liddell
N::Q_DDWO_B9 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 1000 to 1170 MW, 7 or less units in service at Bayswater and Liddell
N::Q_DDWO_C_1A | 2008-04-08 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability for a trip of Callide C3
N::Q_DDWO_C_1B | 2008-04-08 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability for a trip of a Callide C4
N::Q_DDWO_C_2A | 2008-04-08 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability for a trip of a Millmerran #1, for 1 unit online at Millmerran
N::Q_DDWO_C_2B | 2008-04-08 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability for a trip of a Millmerran #2, for 1 unit online at Millmerran
N::Q_DDWO_D | 2008-04-08 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for a Tarong to Braemar (8814 or 8815) Fault, 2 units in service at Millmerran
N::Q_DDWO_E | 2008-04-08 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for trip of a Tarong North unit
N::Q_DDWO_F | 2008-08-19 | 2 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for trip of a Kogan Creek unit
N::Q_JNWG_A1 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_JNWG_A2 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_JNWG_A3 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 MW to 1220MW, 8 units in service at Bayswater and Liddell
N::Q_JNWG_A4 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_JNWG_A5 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_JNWG_A7 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 to 1270 MW, 7 or less units in service at Bayswater and Liddell
N::Q_JNWG_B2 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 500 to 100 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_JNWG_B3 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_JNWG_B5 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 390 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_JNWG_B6 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_JNWG_B8 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 500 to 1000 MW, 7 or less units in service at Bayswater and Liddell
N::Q_JNWG_B9 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 1000 to 1170 MW, 7 or less units in service at Bayswater and Liddell
N::Q_JNWG_C_1A | 2006-04-12 | 1 | Out = Jindera - Wagga (62) line, NSW to Qld Transient Stability for a trip of Callide C3
N::Q_JNWG_C_1B | 2006-04-12 | 1 | Out = Jindera - Wagga (62) line, NSW to Qld Transient Stability for a trip of a Callide C4
N::Q_JNWG_C_2A | 2006-04-12 | 1 | Out = Jindera - Wagga (62) line, NSW to Qld Transient Stability for a trip of a Millmerran #1, for 1 unit online at Millmerran
N::Q_JNWG_C_2B | 2006-04-12 | 1 | Out = Jindera - Wagga (62) line, NSW to Qld Transient Stability for a trip of a Millmerran #2, for 1 unit online at Millmerran
N::Q_JNWG_D | 2006-04-12 | 1 | Out = Jindera - Wagga (62) line, NSW to Qld Transient Stability Limit for a Tarong to Braemar (8814 or 8815) Fault, 2 units in service at Millmerran
N::Q_JNWG_E | 2006-04-12 | 1 | Out = Jindera - Wagga (62) line, NSW to Qld Transient Stability Limit for trip of a Tarong North unit
N::Q_JNWG_F | 2007-07-06 | 2 | Out= Jindera - Wagga (62) line, NSW to Qld Transient Stability Limit for trip of Kogan Creek
N::Q_JNWO_A1 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_JNWO_A2 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_JNWO_A3 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 MW to 1220MW, 8 units in service at Bayswater and Liddell
N::Q_JNWO_A4 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_JNWO_A5 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_JNWO_A7 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 to 1270 MW, 7 or less units in service at Bayswater and Liddell
N::Q_JNWO_B2 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 500 to 100 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_JNWO_B3 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_JNWO_B5 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 390 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_JNWO_B6 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_JNWO_B8 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 500 to 1000 MW, 7 or less units in service at Bayswater and Liddell
N::Q_JNWO_B9 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 1000 to 1170 MW, 7 or less units in service at Bayswater and Liddell
N::Q_JNWO_C_1A | 2006-04-12 | 1 | Out = Jindera - Wodonga (060) line, NSW to Qld Transient Stability for a trip of Callide C3
N::Q_JNWO_C_1B | 2006-04-12 | 1 | Out = Jindera - Wodonga (060) line, NSW to Qld Transient Stability for a trip of a Callide C4
N::Q_JNWO_C_2A | 2006-04-12 | 1 | Out = Jindera - Wodonga (060) line, NSW to Qld Transient Stability for a trip of a Millmerran #1, for 1 unit online at Millmerran
N::Q_JNWO_C_2B | 2006-04-12 | 1 | Out = Jindera - Wodonga (060) line, NSW to Qld Transient Stability for a trip of a Millmerran #2, for 1 unit online at Millmerran
N::Q_JNWO_D | 2006-04-12 | 1 | Out = Jindera - Wodonga (060) line, NSW to Qld Transient Stability Limit for a Tarong to Braemar (8814 or 8815) Fault, 2 units in service at Millmerran
N::Q_JNWO_E | 2006-04-12 | 1 | Out = Jindera - Wodonga (060) line, NSW to Qld Transient Stability Limit for trip of a Tarong North unit
N::Q_JNWO_F | 2007-07-06 | 2 | Out= Jindera - Wodonga (060) line, NSW to Qld Transient Stability Limit for trip of Kogan Creek
N::Q_LDMU_A1 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_LDMU_A2 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_LDMU_A3 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 MW to 1220MW, 8 units in service at Bayswater and Liddell
N::Q_LDMU_A4 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_LDMU_A5 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_LDMU_A7 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 to 1270 MW, 7 or less units in service at Bayswater and Liddell
N::Q_LDMU_B2 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 500 to 100 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_LDMU_B3 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_LDMU_B5 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 390 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_LDMU_B6 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_LDMU_B8 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 500 to 1000 MW, 7 or less units in service at Bayswater and Liddell
N::Q_LDMU_B9 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 1000 to 1170 MW, 7 or less units in service at Bayswater and Liddell
N::Q_LDMU_C_1A | 2006-03-24 | 1 | Out = Liddell to Muswellbrook (83), NSW to Qld Transient Stability for a trip of Callide C3
N::Q_LDMU_C_1B | 2006-03-24 | 1 | Out = Liddell to Muswellbrook (83), NSW to Qld Transient Stability for a trip of a Callide C4
N::Q_LDMU_C_2A | 2006-03-24 | 1 | Out = Liddell to Muswellbrook (83), NSW to Qld Transient Stability for a trip of a Millmerran #1, for 1 unit online at Millmerran
N::Q_LDMU_C_2B | 2006-03-24 | 1 | Out = Liddell to Muswellbrook (83), NSW to Qld Transient Stability for a trip of a Millmerran #2, for 1 unit online at Millmerran
N::Q_LDMU_D | 2006-03-24 | 1 | Out = Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for a Tarong to Braemar (8814 or 8815) Fault, 2 units in service at Millmerran
N::Q_LDMU_E | 2006-03-24 | 1 | Out = Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for trip of a Tarong North unit
N::Q_LDMU_F | 2007-07-06 | 2 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for trip of Kogan Creek
N::Q_LDNC_1 | 2008-10-23 | 1 | Out= Liddell-Newcastle(81), avoid Synch.loss(N:Q) on Liddell-Tomago(82) fault
N::Q_LDNC_LDTM_N-2 | 2008-12-09 | 1 | Out= Nil, Loss of both Liddell-Newcastle(81) & Liddell-Tomago (82) declared credible, avoid Synch.loss(N::Q).
N::Q_LDTW_A1 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_LDTW_A2 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_LDTW_A3 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 MW to 1220MW, 8 units in service at Bayswater and Liddell
N::Q_LDTW_A4 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_LDTW_A5 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_LDTW_A7 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 to 1270 MW, 7 or less units in service at Bayswater and Liddell
N::Q_LDTW_B2 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 500 to 100 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_LDTW_B3 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_LDTW_B5 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 390 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_LDTW_B6 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_LDTW_B8 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 500 to 1000 MW, 7 or less units in service at Bayswater and Liddell
N::Q_LDTW_B9 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 1000 to 1170 MW, 7 or less units in service at Bayswater and Liddell
N::Q_LDTW_C_1A | 2006-03-24 | 1 | Out = Nil, NSW to Qld Transient Stability for a trip of Callide C3
N::Q_LDTW_C_1B | 2006-03-24 | 1 | Out = Nil, NSW to Qld Transient Stability for a trip of a Callide C4
N::Q_LDTW_C_2A | 2006-03-24 | 1 | Out = Nil, NSW to Qld Transient Stability for a trip of a Millmerran #1, for 1 unit online at Millmerran
N::Q_LDTW_C_2B | 2006-03-24 | 1 | Out = Nil, NSW to Qld Transient Stability for a trip of a Millmerran #2, for 1 unit online at Millmerran
N::Q_LDTW_D | 2006-03-24 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for a Tarong to Braemar (8814 or 8815) Fault, 2 units in service at Millmerran
N::Q_LDTW_E | 2006-03-24 | 1 | Out = Nil, NSW to Qld Transient Stability Limit for trip of a Tarong North unit
N::Q_LDTW_F | 2007-07-06 | 2 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for trip of Kogan Creek
N::Q_MNMP_A1 | 2008-07-01 | 2 | Out= Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_MNMP_A2 | 2008-07-01 | 2 | Out= Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_MNMP_A3 | 2008-07-01 | 2 | Out= Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 MW to 1220MW, 8 units in service at Bayswater and Liddell
N::Q_MNMP_A4 | 2008-07-01 | 2 | Out= Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_MNMP_A5 | 2008-07-01 | 2 | Out= Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_MNMP_B2 | 2008-07-01 | 2 | Out= Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 500 to 100 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_MNMP_B3 | 2008-07-01 | 2 | Out= Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_MNMP_B5 | 2008-07-01 | 2 | Out= Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 390 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_MNMP_B6 | 2008-07-01 | 2 | Out= Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_MNMP_C_1A | 2008-07-01 | 1 | Out = Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability for a trip of Callide C3
N::Q_MNMP_C_1B | 2008-07-01 | 1 | Out = Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability for a trip of a Callide C4
N::Q_MNMP_C_2A | 2008-07-01 | 1 | Out = Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability for a trip of a Millmerran #1, for 1 unit online at Millmerran
N::Q_MNMP_C_2B | 2008-07-01 | 1 | Out = Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability for a trip of a Millmerran #2, for 1 unit online at Millmerran
N::Q_MNMP_D | 2008-07-01 | 1 | Out = Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for a Tarong to Braemar (8814 or 8815) Fault, 2 units in service at Millmerran
N::Q_MNMP_E | 2008-07-01 | 1 | Out = Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for trip of a Tarong North unit
N::Q_MNMP_F | 2008-07-01 | 1 | Out= Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for trip of Kogan Creek
N::Q_MUTW_A1 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_MUTW_A2 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_MUTW_A3 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 MW to 1220MW, 8 units in service at Bayswater and Liddell
N::Q_MUTW_A4 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_MUTW_A5 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_MUTW_A7 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 to 1270 MW, 7 or less units in service at Bayswater and Liddell
N::Q_MUTW_B2 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 500 to 100 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_MUTW_B3 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_MUTW_B5 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 390 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_MUTW_B6 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_MUTW_B8 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 500 to 1000 MW, 7 or less units in service at Bayswater and Liddell
N::Q_MUTW_B9 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 1000 to 1170 MW, 7 or less units in service at Bayswater and Liddell
N::Q_MUTW_C_1A | 2006-03-24 | 1 | Out = Muswellbrook to Tamworth (88), NSW to Qld Transient Stability for a trip of Callide C3
N::Q_MUTW_C_1B | 2006-03-24 | 1 | Out = Muswellbrook to Tamworth (88), NSW to Qld Transient Stability for a trip of a Callide C4
N::Q_MUTW_C_2A | 2006-03-24 | 1 | Out = Muswellbrook to Tamworth (88), NSW to Qld Transient Stability for a trip of a Millmerran #1, for 1 unit online at Millmerran
N::Q_MUTW_C_2B | 2006-03-24 | 1 | Out = Muswellbrook to Tamworth (88), NSW to Qld Transient Stability for a trip of a Millmerran #2, for 1 unit online at Millmerran
N::Q_MUTW_D | 2006-03-24 | 1 | Out = Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for a Tarong to Braemar (8814 or 8815) Fault, 2 units in service at Millmerran
N::Q_MUTW_E | 2006-03-24 | 1 | Out = Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for trip of a Tarong North unit
N::Q_MUTW_F | 2007-07-06 | 2 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for trip of Kogan Creek
N::Q_NIL_A1 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_NIL_A2 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_NIL_A3 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 MW to 1220MW, 8 units in service at Bayswater and Liddell
N::Q_NIL_A4 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_NIL_A5 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_NIL_A7 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 to 1270 MW, 7 or less units in service at Bayswater and Liddell
N::Q_NIL_B2 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 500 to 100 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_NIL_B3 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_NIL_B5 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 390 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_NIL_B6 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_NIL_B8 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 500 to 1000 MW, 7 or less units in service at Bayswater and Liddell
N::Q_NIL_B9 | 2008-07-01 | 1 | Out = Nil, NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 1000 to 1170 MW, 7 or less units in service at Bayswater and Liddell
N::Q_NIL_C_1A | 2006-03-21 | 1 | Out = Nil, NSW to Qld Transient Stability for a trip of Callide C3
N::Q_NIL_C_1B | 2006-03-21 | 1 | Out = Nil, NSW to Qld Transient Stability for a trip of a Callide C4
N::Q_NIL_C_2A | 2006-03-21 | 1 | Out = Nil, NSW to Qld Transient Stability for a trip of a Millmerran #1, for 1 unit online at Millmerran
N::Q_NIL_C_2B | 2006-03-21 | 1 | Out = Nil, NSW to Qld Transient Stability for a trip of a Millmerran #2, for 1 unit online at Millmerran
N::Q_NIL_D | 2006-03-21 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for a Tarong to Braemar (8814 or 8815) Fault, 2 units in service at Millmerran
N::Q_NIL_E | 2006-03-21 | 1 | Out = Nil, NSW to Qld Transient Stability Limit for trip of a Tarong North unit
N::Q_NIL_F | 2009-10-08 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek
N::Q_SSWW_A1 | 2008-07-01 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_SSWW_A2 | 2008-07-01 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_SSWW_A3 | 2008-07-01 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1200 MW to 1220MW, 8 units in service at Bayswater and Liddell
N::Q_SSWW_A4 | 2008-07-01 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_SSWW_A5 | 2008-07-01 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 1000 to 1200 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_SSWW_B2 | 2008-07-01 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 500 to 100 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_SSWW_B3 | 2008-07-01 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N::Q_SSWW_B5 | 2008-07-01 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 390 to 1000 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_SSWW_B6 | 2008-07-01 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for:Vic to Snowy flows of 1000 to 1170 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N::Q_SSWW_C_1A | 2006-03-24 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability for a trip of Callide C3
N::Q_SSWW_C_1B | 2006-03-24 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability for a trip of a Callide C4
N::Q_SSWW_C_2A | 2006-03-24 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability for a trip of a Millmerran #1, for 1 unit online at Millmerran
N::Q_SSWW_C_2B | 2006-03-24 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability for a trip of a Millmerran #2, for 1 unit online at Millmerran
N::Q_SSWW_D | 2006-03-24 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for a Tarong to Braemar (8814 or 8815) Fault, 2 units in service at Millmerran
N::Q_SSWW_E | 2006-03-24 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for trip of a Tarong North unit
N::Q_SSWW_F | 2007-07-06 | 2 | Out= Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for trip of Kogan Creek
N::V_AVDT | 2008-07-01 | 1 | Out= Avon - Dapto (10), NSW to Snowy Transient Limit
N::V_AVKC | 2008-07-01 | 1 | Out= Avon - Kemps Creek (37), NSW to Snowy Transient Limit
N::V_AVMN | 2008-07-01 | 1 | Out= Avon - Marulan (16), NSW to Snowy Transient Limit
N::V_BAHO | 2008-07-01 | 1 | Out= Ballarat to Horsham line, NSW to Snowy Transient Limit
N::V_BWLD_N-2 | 2008-12-10 | 1 | Out= Nil, Loss of Bayswater to Liddell (33 and 34) lines declared credible, NSW to Snowy Transient Limit
N::V_BWMP | 2008-07-01 | 1 | Out= Bayswater - Mt.Piper (73) line, NSW to Snowy Transient Limit
N::V_BWMP_BWWW | 2008-10-30 | 1 | Out= both Bayswater to MtPiper/Wallerawang (73 + 74), NSW to Snowy Transient Limit
N::V_BWMP_BWWW_N-2 | 2009-02-09 | 1 | Out=Nil, Loss of both Bayswater-Mt.Piper(73) & Bayswater-Wallerawang (74) declared credible, NSW to Snowy (Horizontal segment),transient stability limit
N::V_BWMP_BWWW_N-2_B | 2009-02-10 | 1 | Out= Nil, Loss of both Bayswater-Mt. Piper (73) & Bayswater-Wallerawang (74) declared credible (slope segment with 7 or fewer Hunter units), transient stability limit
N::V_BWMP_BWWW_N-2_C | 2009-02-10 | 1 | Out= Nil, Loss of both Bayswater-Mt. Piper (73) & Bayswater-Wallerawang (74) declared credible (slope segment with 8 Hunter units), transient stability limit
N::V_BWRG | 2008-07-01 | 1 | Out= Bayswater - Regentville (31), NSW to Snowy Transient Limit
N::V_BWSW | 2008-07-01 | 1 | Out= Bayswater - Sydney West (32), NSW to Snowy Transient Limit
N::V_BWSW_BWRG_N-2_B | 2009-02-09 | 1 | Out= Nil, Loss of both Bayswater-Regentville(31) & Bayswater-Sydney West (32) declared credible, NSW to Snowy (Slope segment for 7 units), transient stability limit
N::V_BWSW_BWRG_N-2_C | 2009-02-09 | 1 | Out= Nil, Loss of both Bayswater-Regentville(31) & Bayswater-Sydney West (32) declared credible, (Slope segement for 8 units), transient stability limit
N::V_BWSW_BWRG_N-2_D | 2009-02-09 | 1 | Out= Nil, Loss of both Bayswater-Regentville(31) & Bayswater-Sydney West (32) declared credible, (Horizontal segment) transient stability limit
N::V_BWSW_RGSW_N-2_B | 2009-02-10 | 1 | Out= Nil, Loss of both Bayswater-Sydney West(32) & Regentville-Sydney West (38) declared credible (slope segment with 7 or fewer Hunter units), transient stability limit
N::V_BWSW_RGSW_N-2_C | 2009-02-10 | 1 | Out= Nil, Loss of both Bayswater-Sydney West(32) & Regentville-Sydney West (38) declared credible (slope segment with 8 Hunter units), transient stability limit
N::V_BWSW_RGSW_N-2_D | 2009-02-10 | 1 | Out= Nil, Loss of both Bayswater-Sydney West(32) & Regentville-Sydney West (38) declared credible (NSW to Snowy Upper limit for 8 or less BW LD units), transient stability limit
N::V_BWWW | 2008-07-01 | 1 | Out= Bayswater - Wallerawang (74) line, NSW to Snowy Transient Limit
N::V_CNKV | 2008-07-01 | 3 | Out= Canberra - Kangaroo Valley (6), NSW to Snowy Transient Limit
N::V_CNLT | 2008-07-01 | 1 | Out= Canberra - Lower Tumut (07), NSW to Snowy Transient Limit
N::V_CNUT | 2008-07-01 | 1 | Out= Canberra - Upper Tumut (01), NSW to Snowy Transient Limit
N::V_CNYS | 2008-07-01 | 1 | Out= Canberra - Yass (9), NSW to Snowy Transient Limit
N::V_CNYS+MNYS | 2008-07-01 | 2 | Out= Canberra - Yass (9) and Marulan - Yass (5), NSW to Snowy Transient Limit
N::V_CNYS+UTYS | 2008-07-01 | 2 | Out= Canberra - Yass (9) and Upper Tumut - Yass (02), NSW to Snowy Transient Limit
N::V_DDMS | 2008-07-01 | 1 | Out= Dederang - Murray (67 or 68) line, NSW to Snowy Transient Limit
N::V_DDSM | 2008-07-01 | 1 | Out= Dederang to South Morang line, NSW to Snowy Transient Limit
N::V_DDWO | 2008-07-01 | 1 | Out= Dederang to Wodonga line, NSW to Snowy Transient Limit
N::V_DTKV | 2008-07-01 | 1 | Out= Dapto - Kangaroo Valley (18), NSW to Snowy Transient Limit
N::V_DTMN | 2008-07-01 | 1 | Out= Dapto - Marulan (8), NSW to Snowy Transient Limit
N::V_DTSS | 2008-07-01 | 1 | Out= Dapto - Sydney South (11), NSW to Snowy Transient Limit
N::V_ERVY | 2008-07-01 | 2 | Out= Eraring - Vales Pt (25), NSW to Snowy Transient Limit
N::V_ERVY_MMSW | 2009-01-16 | 1 | Out = Eraring-Vineyard (25) + Munmorah-Sydney West (26), NSW to Snowy Transient Limit
N::V_ERVY_MNSW_N-2 | 2008-07-01 | 1 | Out=Nil, loss of Eraring to Vineyard (25) and Munmorah to Sydney West (26) lines declared credible, NSW to Snowy Transient Limit
N::V_ER_TX | 2008-07-01 | 2 | Out= Eraring 500/330kV transformer, NSW to Snowy Transient Limit
N::V_HORC | 2008-07-01 | 1 | Out= Horsham to Red Cliffs line, NSW to Snowy Transient Limit
N::V_JNWG | 2008-07-01 | 2 | Out= Jindera - Wagga (62) line, NSW to Snowy Transient Limit
N::V_JNWO | 2008-07-01 | 2 | Out= Jindera - Wodonga (060) line, NSW to Snowy Transient Limit
N::V_KCSS | 2008-07-01 | 2 | Out= Kemps Creek - Sydney South (13), NSW to Snowy Transient Limit
N::V_KC_VC1 | 2008-07-01 | 1 | Out= one Kemps Creek SVC, NSW to Snowy Transient Limit
N::V_KC_VC2 | 2008-07-01 | 1 | Out= both Kemps Creek SVCs, NSW to Snowy Transient Limit
N::V_LDNC+ERTX | 2008-10-20 | 1 | Out= Liddell-Newcastle (81) + Eraring Tie Tx, NSW to Snowy Transient Limit
N::V_LDNC_1 | 2008-07-01 | 2 | Out= Liddell to Newcastle (81), NSW to Snowy Transient Limit
N::V_LDTM_1 | 2008-07-01 | 2 | Out= Liddell to Tomago (82), NSW to Snowy Transient Limit
N::V_LPSS | 2008-07-01 | 1 | Out= Liverpool - Sydney South (12), NSW to Snowy Transient Limit
N::V_LPSW | 2008-07-01 | 1 | Out= Liverpool - Sydney West (30), NSW to Snowy Transient Limit
N::V_LTMS | 2008-07-01 | 2 | Out= Lower Tumut - Murray (66) line, NSW to Snowy Transient Limit
N::V_LTUT | 2008-07-01 | 2 | Out= Lower Tumut - Upper Tumut (64), NSW to Snowy Transient Limit
N::V_LTWG | 2008-07-01 | 2 | Out= Lower Tumut - Wagga (051) line, NSW to Snowy Transient Limit
N::V_LTYS | 2008-07-01 | 1 | Out= Lower Tumut - Yass (03), NSW to Snowy Transient Limit
N::V_MMSN | 2008-07-01 | 1 | Out= Munmorah - Sydney North (21), NSW to Snowy Transient Limit
N::V_MMSW | 2008-07-01 | 2 | Out= Munmorah - Sydney West (26), NSW to Snowy Transient Limit
N::V_MMTG | 2008-11-21 | 1 | Out= Munmorah - Tuggerah (2M), NSW to Snowy Transient Limit
N::V_MNMP | 2008-07-01 | 2 | Out= Marulan - Mt Piper (35 or 36), NSW to Snowy Transient Limit
N::V_MNSW_SWVY_N-2 | 2008-07-01 | 1 | Out=Nil, loss of Munmorah to Sydney West (26) and Sydney West to Vineyard (29) lines declared credible, NSW to Snowy Transient Limit
N::V_MNYS | 2008-07-01 | 1 | Out= Marulan - Yass (4 or 5), NSW to Snowy Transient Limit
N::V_MNYS_N-2 | 2008-07-01 | 1 | Out=Nil, loss of both Marulan to Yass (4 + 5) lines declared credible, NSW to Snowy Transient Limit
N::V_MPWL | 2008-07-01 | 1 | Out= Mt Piper to Wellington (72), NSW to Snowy Transient Limit
N::V_MPWW | 2008-07-01 | 1 | Out= Mt Piper - Wallerawang (71), NSW to Snowy Transient Limit
N::V_MSUT | 2008-07-01 | 2 | Out= Murray - Upper Tumut (65) line, NSW to Snowy Transient Limit
N::V_NIL | 2009-06-17 | 1 | Out= Nil, southerly flow on Snowy cut-set (01,2,3,07,051,060,0X1 and 979 line) transient stability limit
N::V_NIL_1150 | 2008-07-01 | 1 | Out= Nil, transient stability maxium transfer on NSW to Vic
N::V_RGSW | 2008-07-01 | 1 | Out= Regentville - Sydney West (38), NSW to Snowy Transient Limit
N::V_SNTG | 2008-11-21 | 1 | Out= Tuggerah - Sydney North (21), NSW to Snowy Transient Limit
N::V_SNVP | 2008-07-01 | 1 | Out= Sydney North - Vales Point (22), NSW to Snowy Transient Limit
N::V_SSWW_IGSS_N-2 | 2008-07-01 | 1 | Out= Nil, loss of Sydney South to Wallerawang (76) and Ingleburn to Sydney South (78) lines declared credible, NSW to Snowy Transient Limit
N::V_SWVY | 2008-07-01 | 2 | Out= Sydney West - Vineyard (29), NSW to Snowy Transient Limit
N::V_SWYS | 2008-07-01 | 1 | Out= Sydney West - Yass (39), NSW to Snowy Transient Limit
N::V_UTYS | 2008-07-01 | 1 | Out= Upper Tumut - Yass (02), NSW to Snowy Transient Limit
N::V_X_BWSW_TWO | 2008-07-01 | 1 | Out= Bayswater - Regentville (31) and Bayswater - Sydney West (32), NSW to Snowy Transient Limit
N::V_X_ERKC_TWO | 2008-07-01 | 1 | Out= both Eraring - Kemps Creek (5A1 and 5A2), NSW to Snowy Transient Limit
N::V_X_MNMP_TWO | 2008-07-01 | 1 | Out= both Marulan - Mt Piper (35 and 36), NSW to Snowy Transient Limit
N:Q_ARTW_A6 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1200 MW, 7 or less units in service at Bayswater and Liddell
N:Q_ARTW_B1 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: V-SN flows of 0 to 500MW, V-SA positive, 8 units in service at Bayswater and Liddell
N:Q_ARTW_B4 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: V-SN flows of 0 to 390 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N:Q_ARTW_B7 | 2008-07-01 | 1 | Out = Armidale to Tamworth (85 or 86), NSW to Qld Transient Stability Limit for: V-SN flows of 0 to 500 MW, 7 or less units in service at Bayswater and Liddell
N:Q_AR_330_BS1_OSC | 2007-11-26 | 1 | Out= Armidale No.1 330kV bus, NSW to Qld Oscillatory stability limit
N:Q_AR_330_BS5_OSC | 2007-09-14 | 1 | Out= Armidale No.5 330kV bus, NSW to Qld Oscillatory stability limit
N:Q_BR_VC_A6 | 2008-07-01 | 1 | Out = Braemar SVC, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1200 MW, 7 or less units in service at Bayswater and Liddell
N:Q_BR_VC_B1 | 2008-07-01 | 1 | Out = Braemar SVC, NSW to Qld Transient Stability Limit for: V-SN flows of 0 to 500MW, V-SA positive, 8 units in service at Bayswater and Liddell
N:Q_BR_VC_B4 | 2008-07-01 | 1 | Out = Braemar SVC, NSW to Qld Transient Stability Limit for: V-SN flows of 0 to 390 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N:Q_BR_VC_B7 | 2008-07-01 | 1 | Out = Braemar SVC, NSW to Qld Transient Stability Limit for: V-SN flows of 0 to 500 MW, 7 or less units in service at Bayswater and Liddell
N:Q_DDWO_A6 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1200 MW, 7 or less units in service at Bayswater and Liddell
N:Q_DDWO_B1 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N:Q_DDWO_B4 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for:,Vic to Snowy flows of 0 to 390 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N:Q_DDWO_B7 | 2008-07-01 | 1 | Out= Dederang to Wodonga, NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, 7 or less units in service at Bayswater and Liddell
N:Q_JNWG_A6 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1200 MW, 7 or less units in service at Bayswater and Liddell
N:Q_JNWG_B1 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N:Q_JNWG_B4 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for:,Vic to Snowy flows of 0 to 390 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N:Q_JNWG_B7 | 2008-07-01 | 1 | Out= Jindera to Wagga (62), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, 7 or less units in service at Bayswater and Liddell
N:Q_JNWO_A6 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1200 MW, 7 or less units in service at Bayswater and Liddell
N:Q_JNWO_B1 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N:Q_JNWO_B4 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for:,Vic to Snowy flows of 0 to 390 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N:Q_JNWO_B7 | 2008-07-01 | 1 | Out= Jindera to Wodonga (060), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, 7 or less units in service at Bayswater and Liddell
N:Q_LDMU_A6 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1200 MW, 7 or less units in service at Bayswater and Liddell
N:Q_LDMU_B1 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N:Q_LDMU_B4 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for:,Vic to Snowy flows of 0 to 390 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N:Q_LDMU_B7 | 2008-07-01 | 1 | Out= Liddell to Muswellbrook (83), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, 7 or less units in service at Bayswater and Liddell
N:Q_LDTM_1 | 2008-07-01 | 1 | Out= Liddell-Tomago(82), avoid Synch.loss(N:Q) on Liddell-Newcastle(81) fault
N:Q_LDTW_A6 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1200 MW, 7 or less units in service at Bayswater and Liddell
N:Q_LDTW_B1 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N:Q_LDTW_B4 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for:,Vic to Snowy flows of 0 to 390 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N:Q_LDTW_B7 | 2008-07-01 | 1 | Out= Liddell to Tamworth (84), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, 7 or less units in service at Bayswater and Liddell
N:Q_MNMP_B1 | 2008-07-01 | 2 | Out= Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N:Q_MNMP_B4 | 2008-07-01 | 2 | Out= Marulan to Mt Piper (35 or 36), NSW to Qld Transient Stability Limit for:,Vic to Snowy flows of 0 to 390 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N:Q_MUTW_A6 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1200 MW, 7 or less units in service at Bayswater and Liddell
N:Q_MUTW_B1 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N:Q_MUTW_B4 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for:,Vic to Snowy flows of 0 to 390 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N:Q_MUTW_B7 | 2008-07-01 | 1 | Out= Muswellbrook to Tamworth (88), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, 7 or less units in service at Bayswater and Liddell
N:Q_NIL_A6 | 2008-07-01 | 1 | Out = Nil, NSW to Qld Transient Stability Limit for: NSW to Snowy flows of 0 to 1200 MW, 7 or less units in service at Bayswater and Liddell
N:Q_NIL_B1 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N:Q_NIL_B4 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for:,Vic to Snowy flows of 0 to 390 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N:Q_NIL_B7 | 2008-07-01 | 1 | Out= Nil, NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, 7 or less units in service at Bayswater and Liddell
N:Q_RGSW | 2006-10-06 | 1 | Out= Regentville-SydneyWest(38), avoid loss of Synchronism on Liddell-Newcastle(81) fault
N:Q_SSWW_B1 | 2008-07-01 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for: Vic to Snowy flows of 0 to 500 MW, V-SA positive, 8 units in service at Bayswater and Liddell
N:Q_SSWW_B4 | 2008-07-01 | 1 | Out = Sydney South to Ingleburn/Wallerawang (76 or 77 or 78), NSW to Qld Transient Stability Limit for:,Vic to Snowy flows of 0 to 390 MW, V-SA negative, 8 units in service at Bayswater and Liddell
N:Q_TW_330_BUS1_OSC | 2008-05-21 | 1 | Out= Tamworth No.1 330kV bus, NSW to Qld Oscillatory stability limit
N:Q_TW_330_BUS3_OSC | 2008-06-26 | 1 | Out= Tamworth No.3 330kV bus, NSW to Qld Oscillatory stability limit
N:V_NQ_VST_ISLE | 2008-07-01 | 1 | NSW / Vic separation, transient stability limit
N>>MMTG_01 | 2008-11-21 | 1 | Out= Munmorah-Tuggerah(2M), avoid ValesPoint to SydneyNorth (22) O/L on Munmorah-SydneyWest(26) trip; Feedback
N>>N-13+14_01 | 2008-07-01 | 1 | Out= KempsCreek-SydneySouth(13)+KempsCreek-SydneyNorth(14), avoid Eraring to Newcastle (93) O/L on Eraring-Vineyard(25) trip; Feedback
N>>N-13+14_02 | 2008-07-01 | 1 | Out= KempsCreek-SydneySouth(13)+KempsCreek-SydneyNorth(14), avoid Eraring to Newcastle (93) O/L on KempsCreek-Avon(37) trip; Feedback
N>>N-5MRAS_A_15M | 2008-07-01 | 2 | Out= Snowy 5MRAS scheme, avoid LowerTumut to Canberra (07) O/L (15 min rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N-5MRAS_B_15M | 2008-07-01 | 2 | Out= Snowy 5MRAS scheme, avoid UpperTumut to Canberra (01) O/L (15 min rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-5MRAS_C_15M | 2008-07-01 | 2 | Out= Snowy 5MRAS scheme, avoid LowerTumut to Yass (3) O/L (15 min rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-5MRAS_D_15M | 2008-07-01 | 2 | Out= Snowy 5MRAS scheme, avoid UpperTumut to Canberra (01) O/L (15 min rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-5MRAS_E_15M | 2008-07-01 | 2 | Out= Snowy 5MRAS scheme, avoid UpperTumut to Canberra (01) O/L (15 min rating) on UpperTumut-Yass(2) trip; Feedback
N>>N-5MRAS_F_15M | 2008-07-01 | 2 | Out= Snowy 5MRAS scheme, avoid UpperTumut to Yass (2) O/L (15 min rating) on Canberra-UpperTumut(01) trip; Feedback
N>>N-5MRAS_G_15M | 2008-07-01 | 2 | Out= Snowy 5MRAS scheme, avoid UpperTumut to Yass (2) O/L (15 min rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-5MRAS_H_15M | 2008-07-01 | 2 | Out= Snowy 5MRAS scheme, avoid LowerTumut to Canberra (07) O/L (15 min rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-ARCH_87_A | 2008-07-01 | 1 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Kempsey (965) on trip of Nil, Feedback, TG formulation in PD/ST
N>>N-ARCH_87_B1 | 2007-01-10 | 1 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Kempsey (965) on trip of Nil, TG formulation, Port Macquarie + Taree load= 45 MW
N>>N-ARCH_87_B2 | 2007-01-10 | 1 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Kempsey (965) on trip of Nil, TG formulation, Port Macquarie + Taree load= 50 MW
N>>N-ARCH_87_B3 | 2007-01-10 | 1 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Kempsey (965) on trip of Nil, TG formulation, Port Macquarie + Taree load= 55 MW
N>>N-ARCH_87_B5 | 2007-10-22 | 1 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Kempsey (965) on trip of Nil, TG formulation, Port Macquarie + Taree load= 65 MW
N>>N-ARCH_87_B7 | 2007-10-22 | 1 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Kempsey (965) on trip of Nil, TG formulation, Port Macquarie + Taree load= 75 MW
N>>N-ARCH_87_B9 | 2007-10-22 | 1 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Kempsey (965) on trip of Nil, TG formulation, Port Macquarie + Taree load= 85 MW
N>>N-AR_PST_DF_DS | 2009-02-11 | 1 | Out= Armidale PST, avoid Armidale->Kempsey(965) OL(selected rating) on Coffs_Harbour-Nambucca(9W3) trip, NEMMCO_spec
N>>N-AR_PST_DF_PD | 2009-02-11 | 1 | Out= Armidale PST, avoid Armidale->Kempsey(965) OL(15m rat) on Coffs_Harbour-Nambucca(9W3) trip, both Raleigh and Sawtell loads supplied ex Coffs_H, TG_spec
N>>N-AVDT_A | 2008-07-01 | 1 | Out= Avon-Dapto(10), avoid KempsCreek to SydneySouth (13) O/L on SydneyWest-Liverpool(30) trip; Feedback
N>>N-AVDT_B | 2008-07-01 | 1 | Out= Avon-Dapto(10), avoid SydneyWest to Liverpool (30) O/L on KempsCreek-SydneySouth(13) trip; Feedback
N>>N-AVDT_C | 2008-07-01 | 1 | Out= Avon-Dapto(10), avoid KempsCreek to SydneySouth (13) O/L on Liverpool-SydneySouth(12) trip; Feedback
N>>N-AVDT_D | 2008-07-01 | 1 | Out= Avon-Dapto(10), avoid MtPiper to Wallerawang (71) O/L on Dapto-SydneySouth(11) trip; Feedback
N>>N-AVDT_F | 2008-11-12 | 1 | Out= Avon-Dapto(10), avoid Marulan to Dapto (8) O/L on SydneySouth-Dapto(11) trip; Feedback
N>>N-AVDT_G | 2008-07-01 | 1 | Out= Avon-Dapto(10), avoid Marulan to Dapto (8) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-AVDT_LPSW_A | 2008-07-01 | 1 | Out= Avon-Dapto(10) + Liverpool-SydneyWest(30), avoid KempsCreek to SydneySouth(13) O/L on Wallerawang-Ingleburn(77) trip; Feedback
N>>N-AVDT_LPSW_B | 2008-07-01 | 1 | Out= Avon-Dapto(10) + Liverpool-SydneyWest(30), avoid KempsCreek to SydneySouth(13) O/L on Dapto-SydneySouth(11) trip; Feedback
N>>N-AVDT_LPSW_C | 2008-07-01 | 1 | Out= Avon-Dapto(10) + Liverpool-SydneyWest(30), avoid KempsCreek to SydneySouth(13) O/L on Nil trip; Feedback
N>>N-AVKC_01 | 2008-07-01 | 1 | Out= Avon-KempsCreek(37), avoid MtPiper to Wallerawang (71) O/L on Dapto-SydneySth(11) trip; Feedback
N>>N-AVKC_02 | 2008-07-01 | 1 | Out= Avon-KempsCreek(37), avoid MtPiper to Wallerawang (71) O/L on Nil trip; Feedback
N>>N-AVKC_03 | 2008-07-01 | 1 | Out= Avon-KempsCreek(37), avoid MtPiper to Wallerawang (71) O/L on Yass-SydneyWest(39) trip; Feedback
N>>N-AVKC_04 | 2008-07-01 | 1 | Out= Avon-KempsCreek(37), avoid Wallerawang to MtPiper (71) O/L on Bayswater-MtPiper(73) trip; Feedback
N>>N-AVKC_05 | 2008-10-09 | 1 | Out= Avon-KempsCreek(37), avoid Kemps Creek to Sydney South (13) O/L on Sydney West to Liverpool (30) trip; Feedback
N>>N-AVKC_06 | 2008-10-09 | 1 | Out= Avon-KempsCreek(37), avoid Sydney West- Liverpool (30) O/L on Kemps Creek - Sydney South(13) trip; Feedback
N>>N-AVKC_19 | 2008-07-01 | 1 | Out= Avon-KempsCreek(37), avoid Yass to SydneyWest (39) O/L on Dapto-SydneySouth(11) trip; Feedback
N>>N-AVMN_A | 2008-07-01 | 1 | Out= Avon-Marulan(16), avoid Marulan to Dapto (8) O/L on Kangaroo-Dapto(18) trip; Feedback
N>>N-AVMN_B | 2008-07-01 | 1 | Out= Avon-Marulan(16), avoid MtPiper to Wallerawang (71) O/L on Dapto-Marulan(8) trip; Feedback
N>>N-AVMN_C | 2008-07-01 | 1 | Out= Avon-Marulan(16), avoid MtPiper to Wallerawang (71) O/L on Nil trip; Feedback
N>>N-AVMN_D | 2008-07-01 | 1 | Out= Avon-Marulan(16), avoid Marulan to Dapto (8) O/L on Canberra-KangarooValley(6) trip; Feedback
N>>N-AVMN_E | 2008-07-01 | 1 | Out= Avon-Marulan(16), avoid Marulan to Dapto (8) O/L on MtPiper-Wallerawang(71) trip; Feedback
N>>N-BWLD_ONE_A | 2008-07-01 | 1 | Out= Bayswater to Liddell (33 or 34), avoid O/L Bayswater to Liddell (34 or 33) on trip of Nil, Feedback
N>>N-BWLD_ONE_B | 2008-07-01 | 1 | Out= Bayswater to Liddell (33 or 34), avoid O/L Liddell to Bayswater (34 or 33) on trip of Nil, Feedback
N>>N-BWLD_ONE_C | 2008-07-03 | 1 | Out= Bayswater to Liddell (33 or 34), avoid O/L Bayswater to Liddell (34 or 33) on trip of Bayswater to Regentville (31), Feedback
N>>N-BWLD_ONE_D | 2008-07-01 | 1 | Out= Bayswater to Liddell (33 or 34), avoid O/L Liddell to Bayswater (34 or 33) on trip of Liddell to Newcastle (81), Feedback
N>>N-BWLD_ONE_E | 2008-07-01 | 1 | Out= Bayswater to Liddell (33 or 34), avoid O/L Liddell to Bayswater (34 or 33) on trip of Liddell to Tomago (82), Feedback
N>>N-BWLD_TWO_A | 2008-07-01 | 1 | Out= both Bayswater to Liddell (33 + 34), avoid O/L Vales Point to Munmorah (23) on trip of Vales Point to Sydney North (22), Feedback
N>>N-BWLD_TWO_B | 2008-07-01 | 1 | Out= both Bayswater to Liddell (33 + 34), avoid O/L Liddell to Newcastle (81) on trip of Liddell to Tomago (82), Feedback
N>>N-BWLD_TWO_C | 2008-07-01 | 1 | Out= both Bayswater to Liddell (33 + 34), avoid O/L Liddell to Tomago (82) on trip of Liddell to Newcastle (81), Feedback
N>>N-BWLD_TWO_D | 2008-07-01 | 1 | Out= both Bayswater to Liddell (33 + 34), avoid O/L Eraring to Newcastle (93) on trip of Nil, Feedback
N>>N-BWLD_TWO_DY | 2008-07-01 | 1 | Out= both Bayswater to Liddell (33 + 34), avoid O/L Armidale to Kempsey (965) on trip of Coffs Harbour to Nambucca (9W3), Feedback
N>>N-BWLD_TWO_E | 2008-07-01 | 1 | Out= both Bayswater to Liddell (33 + 34), avoid O/L Eraring to Newcastle (93) on trip of Eraring to Vineyard (25), Feedback
N>>N-BWMP_01 | 2008-09-25 | 1 | Out= Bayswater-MtPiper(73), avoid Liddell-Newcastle(81) OL on Liddell-Tomago(82) trip; Fb,CoOp
N>>N-BWMP_02 | 2008-07-03 | 1 | Out= Bayswater to Mt Piper (73), avoid O/L Mt Piper to Wallerawang (71) on trip of Yass to Sydney West (39), Feedback
N>>N-BWMP_03 | 2008-07-03 | 1 | Out= Bayswater to Mt Piper (73), avoid O/L Mt Piper to Wallerawang (71) on trip of Nil, Feedback
N>>N-BWMP_04 | 2008-07-03 | 1 | Out= Bayswater to Mt Piper (73), avoid O/L Mt Piper to Wallerawang (71) on trip of Dapto to Sydney South (11), Feedback
N>>N-BWMP_05 | 2008-07-01 | 1 | Out= Bayswater to Mt Piper (73), avoid O/L Liddell to Newcastle (81) on trip of Bayswater to Regentville (31), Feedback
N>>N-BWMP_06 | 2008-09-25 | 1 | Out= Bayswater to Mt Piper (73), avoid O/L Mt Piper to Wallerawang (71) on trip of Kemps Creek to Avon (37), Feedback
N>>N-BWMP_07 | 2008-09-25 | 1 | Out= Bayswater-MtPiper(73), avoid Liddell-Tomago(82) OL on Liddell-Newcastle(81) trip; Fb,CoOp
N>>N-BWMP_BWWW_01 | 2008-10-31 | 1 | Out= both Bayswater to MtPiper/Wallerawang (73 + 74), avoid O/L Liddell to Newcastle (81) on trip of Liddell to Tomago (82), Feedback
N>>N-BWMP_BWWW_02 | 2008-10-30 | 1 | Out= both Bayswater to MtPiper/Wallerawang (73 + 74), avoid O/L Liddell to Tomago (82) on trip of Liddell to Newcastle (81), Feedback
N>>N-BWMP_BWWW_04 | 2008-10-30 | 1 | Out= both Bayswater to MtPiper/Wallerawang (73 + 74), avoid O/L Mt Piper to Wallerawang (94E) on trip of Mt Piper to Wallerawang (71), Feedback
N>>N-BWMP_BWWW_05 | 2008-10-30 | 1 | Out= both Bayswater to MtPiper/Wallerawang (73 + 74), avoid O/L Mt Piper 330/132kV transformer on trip of Mt Piper to Wallerawang (71), Feedback
N>>N-BWRG_A | 2008-09-25 | 1 | Out= Bayswater to Regentville (31), avoid O/L Bayswater to Liddell (34) on trip of Bayswater to Liddell (33)
N>>N-BWRG_B | 2008-09-25 | 1 | Out= Bayswater to Regentville (31), avoid O/L Liddell to Newcastle (81) on trip of Bayswater to Sydney West (32)
N>>N-BWRG_C | 2008-09-25 | 1 | Out= Bayswater to Regentville (31), avoid O/L Liddell to Newcastle (81) on trip of Bayswater to Wallerawang (74)
N>>N-BWRG_D | 2008-09-25 | 1 | Out= Bayswater to Regentville (31), avoid O/L Liddell to Newcastle (81) on trip of Liddell to Tomago (82)
N>>N-BWRG_E | 2008-09-25 | 1 | Out= Bayswater to Regentville (31), avoid O/L Liddell to Newcastle (81) on trip of Nil
N>>N-BWRG_F | 2008-07-03 | 1 | Out= Bayswater to Regentville (31), avoid O/L Liddell to Tomago (82) on trip of Bayswater to Sydney West (32)
N>>N-BWRG_G | 2008-09-25 | 1 | Out= Bayswater to Regentville (31), avoid O/L Liddell to Tomago (82) on trip of Liddell to Newcastle (81)
N>>N-BWRG_H | 2008-09-25 | 1 | Out= Bayswater to Regentville (31), avoid O/L Liddell to Tomago (82) on trip of Nil
N>>N-BWRG_J | 2008-09-25 | 1 | Out= Bayswater to Regentville (31), avoid O/L Vales Point to Munmorah (23) on trip of Vales Point to Sydney North (22)
N>>N-BWRG_K | 2008-09-25 | 1 | Out= Bayswater to Regentville (31), avoid O/L Vales Point to Munmorah (23) on trip of Eraring to Vineyard (25)
N>>N-BWRG_L | 2008-09-25 | 1 | Out= Bayswater to Regentville (31), avoid O/L Vales Point to Munmorah (23) on trip of Bayswater to Sydney West (32)
N>>N-BWSW_A | 2008-09-25 | 1 | Out= Bayswater to Sydney West (32), avoid O/L Bayswater to Liddell (34) on trip of Bayswater to Liddell (33), Feedback
N>>N-BWSW_B | 2008-09-25 | 1 | Out= Bayswater to Sydney West (32), avoid O/L Liddell to Newcastle (81) on trip of Bayswater to Regentville (31), Feedback
N>>N-BWSW_BWRG_N-2_D | 2008-11-18 | 1 | Out=Nil, avoid O/L Liddell to Newcastle (81) on trip of Bayswater to Regentville (31) and Basywater to Sydney West (32) lines, Feedback
N>>N-BWSW_BWRG_N-2_F | 2008-11-18 | 1 | Out=Nil, avoid O/L Liddell to Tomago (82) on trip of Bayswater to Regentville (31) and Basywater to Sydney West (32) lines, Feedback
N>>N-BWSW_BWRG_N-2_K | 2008-11-18 | 1 | Out=Nil, avoid O/L Mt Piper to Wallerawang (71) on trip of Bayswater to Regentville (31) and Basywater to Sydney West (32) lines, Feedback
N>>N-BWSW_BWRG_N-2_O | 2008-11-18 | 1 | Out=Nil, avoid O/L Vales Point to Munmorah (23) on trip of Bayswater to Regentville (31) and Basywater to Sydney West (32) lines, Feedback
N>>N-BWSW_C | 2008-09-25 | 1 | Out= Bayswater to Sydney West (32), avoid O/L Liddell to Newcastle (81) on trip of Bayswater to Wallerawang (74), Feedback
N>>N-BWSW_D | 2008-09-25 | 1 | Out= Bayswater to Sydney West (32), avoid O/L Liddell to Newcastle (81) on trip of Liddell to Tomago (82), Feedback
N>>N-BWSW_E | 2008-09-25 | 1 | Out= Bayswater to Sydney West (32), avoid O/L Liddell to Newcastle (81) on trip of Nil, Feedback
N>>N-BWSW_F | 2008-09-25 | 1 | Out= Bayswater to Sydney West (32), avoid O/L Liddell to Tomago (82) on trip of Bayswater to Regentville (31), Feedback
N>>N-BWSW_G | 2008-09-25 | 1 | Out= Bayswater to Sydney West (32), avoid O/L Liddell to Tomago (82) on trip of Liddell to Newcastle (81), Feedback
N>>N-BWSW_H | 2008-09-25 | 1 | Out= Bayswater to Sydney West (32), avoid O/L Liddell to Tomago (82) on trip of Nil, Feedback
N>>N-BWSW_J | 2008-09-25 | 1 | Out= Bayswater to Sydney West (32), avoid O/L Vales Point to Munmorah (23) on trip of Vales Point to Sydney North (22), Feedback
N>>N-BWSW_K | 2008-09-25 | 1 | Out= Bayswater to Sydney West (32), avoid O/L Vales Point to Munmorah (23) on trip of Eraring to Vineyard (25), Feedback
N>>N-BWSW_L | 2008-09-25 | 1 | Out= Bayswater to Sydney West (32), avoid O/L Vales Point to Munmorah (23) on trip of Bayswater to Regentville (31), Feedback
N>>N-BWSW_TWO_A | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Bayswater to Liddell (34) on trip of Bayswater to Liddell (33), Feedback
N>>N-BWSW_TWO_B | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Liddell to Newcastle (81) on trip of Bayswater to Wallerawang (74), Feedback
N>>N-BWSW_TWO_C | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Liddell to Newcastle (81) on trip of Liddell to Tomago (82), Feedback
N>>N-BWSW_TWO_D | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Liddell to Newcastle (81) on trip of Nil, Feedback
N>>N-BWSW_TWO_E | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Liddell to Tomago (82) on trip of Liddell to Newcastle (81), Feedback
N>>N-BWSW_TWO_F | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Liddell to Tomago (82) on trip of Nil, Feedback
N>>N-BWSW_TWO_G | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Mt Piper to Wallerawang (71) on trip of Marulan to Dapto (8), Feedback
N>>N-BWSW_TWO_H | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Mt Piper to Wallerawang (71) on trip of Dapto to Sydney South (11), Feedback
N>>N-BWSW_TWO_I | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Mt Piper to Wallerawang (71) on trip of Yass to Sydney West (39), Feedback
N>>N-BWSW_TWO_J | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Mt Piper to Wallerawang (71) on trip of Bayswater to Wallerawang (74), Feedback
N>>N-BWSW_TWO_K | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Mt Piper to Wallerawang (71) on trip of Nil, Feedback
N>>N-BWSW_TWO_L | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Vales Point to Munmorah (23) on trip of Vales Point to Sydney North (22), Feedback
N>>N-BWSW_TWO_M | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Vales Point to Munmorah (23) on trip of Eraring to Vineyard (25), Feedback
N>>N-BWSW_TWO_N | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Vales Point to Munmorah (23) on trip of Bayswater to Wallerawang (74), Feedback
N>>N-BWSW_TWO_O | 2008-07-03 | 1 | Out= both Bayswater to Sydney West (32 + 31/38) lines, avoid O/L Vales Point to Munmorah (23) on trip of Nil, Feedback
N>>N-BWWW_01 | 2008-07-03 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Mt Piper to Wallerawang (71) on trip of Marulan to Dapto (8), Feedback
N>>N-BWWW_02 | 2008-07-03 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Mt Piper to Wallerawang (71) on trip of Dapto to Sydney South (11), Feedback
N>>N-BWWW_03 | 2008-07-03 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Mt Piper to Wallerawang (71) on trip of Kemps Creek to Sydney South (13), Feedback
N>>N-BWWW_04 | 2008-07-03 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Mt Piper to Wallerawang (71) on trip of Marulan to Avon (16), Feedback
N>>N-BWWW_05 | 2008-09-25 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Mt Piper to Wallerawang (71) on trip of Kemps Creek to Avon (37), Feedback
N>>N-BWWW_06 | 2008-07-03 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Mt Piper to Wallerawang (71) on trip of Liddell to Newcastle (81), Feedback
N>>N-BWWW_07 | 2008-07-03 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Mt Piper to Wallerawang (71) on trip of Liddell to Tomago (82), Feedback
N>>N-BWWW_08 | 2008-07-03 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Mt Piper to Wallerawang (71) on trip of Nil, Feedback
N>>N-BWWW_09 | 2008-07-03 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Mt Piper to Wallerawang (71) on trip of Mt Piper to Wellington (72), Feedback
N>>N-BWWW_10 | 2008-07-01 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Liddell to Newcastle (81) on trip of Liddell to Tomago (82), Feedback
N>>N-BWWW_11 | 2008-07-01 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Liddell to Newcastle (81) on trip of Bayswater to Regentville (31), Feedback
N>>N-BWWW_12 | 2008-07-01 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Liddell to Tomago (82) on trip of Liddell to Newcastle (81), Feedback
N>>N-BWWW_13 | 2008-09-25 | 1 | Out= Bayswater to Wallerawang (74), avoid O/L Vales Point to Mumorah (23) on trip of Vales point to Sydney North (22), Feedback
N>>N-CHNB_01 | 2008-07-01 | 1 | Out= Coffs Harbour - Nambucca (9W3), avoid O/L Armidale to Kempsey (965) on trip of Nil, Feedback
N>>N-CHNB_02 | 2008-07-01 | 1 | Out= Coffs Harbour to Nambucca (9W3), avoid O/L (15 min rating) Armidale to Kempsey (965) on trip of Kurri to Stroud (96F), considering Port Macquarie + Taree area load
N>>N-CNKV_1N | 2008-07-01 | 1 | Out= Canberra-KangarooValley(6), avoid Yass to Marulan(4) O/L on Yass-Marulan(5) trip; Feedback
N>>N-CNKV_1S | 2008-07-01 | 1 | Out= Canberra-KangarooValley(6), avoid Marulan to Yass(4) O/L on Marulan-Yass(5) trip; Feedback
N>>N-CNKV_2 | 2008-07-01 | 1 | Out= Canberra-KangarooValley(6), avoid MtPiper to Wallerawang (71) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-CNKV_3 | 2008-07-01 | 1 | Out= Canberra-KangarooValley(6), avoid MtPiper to Wallerawang (71) O/L on Yass-SydneyWest(39) trip; Feedback
N>>N-CNKV_4N | 2008-07-01 | 1 | Out= Canberra-KangarooValley(6), avoid Marulan to Dapto (8) O/L on Marulan-Avon(16) trip; Feedback
N>>N-CNKV_5N | 2008-07-01 | 1 | Out= Canberra-KangarooValley(6), avoid Yass to Marulan (4) O/L on Yass-SydneyWest(39) trip; Feedback
N>>N-CNKV_5S | 2008-07-01 | 1 | Out= Canberra-KangarooValley(6), avoid Marulan to Yass (4) O/L on SydneyWest-Yass(39) trip; Feedback
N>>N-CNKV_6 | 2008-07-01 | 1 | Out= Canberra-KangarooValley(6), avoid Yass to Canberra (9) O/L on Nil trip; Feedback
N>>N-CNLT+LTUT_1_15M | 2008-07-01 | 1 | Out= Canberra-LowerTumut(07)+LowerTumut-UpperTumut(64), avoid LowerTumut to Yass (3) O/L (15m rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N-CNLT+LTUT_2_15M | 2008-07-01 | 1 | Out= Canberra-LowerTumut(07)+LowerTumut-UpperTumut(64), avoid UpperTumut to Canberra (01) O/L (15m rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-CNLT_A_15M | 2008-07-01 | 1 | Out= Canberra-LowerTumut(07), avoid LowerTumut to Yass (3) O/L (15m rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N-CNLT_B_15M | 2008-07-01 | 1 | Out= Canberra-LowerTumut(07), avoid UpperTumut to Canberra (01) O/L (15m rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-CNUT_AH_15M | 2008-07-01 | 1 | Out= Canberra-UpperTumut(01), avoid LowerTumut to Canberra(07) O/L(15_min rating) on UpperTumut-Yass(2) trip; Feedback
N>>N-CNUT_BH_15M | 2008-07-01 | 1 | Out= Canberra-UpperTumut(01), avoid LowerTumut to Canberra(07) O/L(15_min rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-CNUT_HA_15M | 2008-07-01 | 1 | Out= Canberra-UpperTumut(01), avoid UpperTumut to LowerTumut(64) O/L (15 min rating) on UpperTumut-Yass(2) trip; Feedback
N>>N-CNUT_HC_15M | 2008-07-01 | 1 | Out= Canberra-UpperTumut(01), avoid LowerTumut to Yass(3) O/L(15-min rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-CNYS+MNYS_1 | 2008-07-01 | 1 | Out= Marulan-Yass(5)+Canberra-Yass(9), avoid Marulan to Yass (4) O/L on KangarooValley-Canberra(6) trip; Feedback
N>>N-CNYS+MNYS_A | 2008-07-01 | 1 | Out= Marulan-Yass(5)+Canberra-Yass(9), avoid Yass to Marulan(4) O/L on Canberra-KangarooValley(6) trip; Feedback
N>>N-CNYS+MNYS_B | 2009-01-21 | 1 | Out= Marulan-Yass(5)+Canberra-Yass(9), avoid Marulan to Yass(4) O/L on Dapto-KangarooValley(18)trip; Feedback
N>>N-CNYS+MNYS_C | 2009-01-21 | 1 | Out= Marulan-Yass(5)+Canberra-Yass(9), avoid SydneyWest-Yass (39) O/L on Marulan-Yass (4)trip; Feedback
N>>N-CNYS+MNYS_D | 2009-01-21 | 1 | Out= Marulan-Yass(5)+Canberra-Yass(9), avoid Yass to Marulan(4) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-CNYS+UTYS_1 | 2008-07-01 | 1 | Out= Canbera-Yass(9)+UpperTumut-Yass(2), avoid KangarooValley to Canberra (6) O/L on Yass-LowerTumut(3) trip; Feedback
N>>N-CNYS+UTYS_2 | 2008-07-01 | 1 | Out= Canbera-Yass(9)+UpperTumut-Yass(2)+LowerTumut-UpperTumut(64), avoid KangarooValley to Canberra (6) O/L on Yass-LowerTumut(3) trip; Feedback
N>>N-CNYS+UTYS_3 | 2008-07-01 | 1 | Out= Canbera-Yass(9)+UpperTumut-Yass(2), avoid Yass to LowerTumut (3) O/L on KangarooValley-Canberra(6) trip; Feedback
N>>N-CNYS+UTYS_4 | 2008-07-01 | 1 | Out= Canbera-Yass(9)+UpperTumut-Yass(2)+LowerTumut-UpperTumut(64), avoid Yass to LowerTumut (3) O/L on KangarooValley-Canberra(6) trip; Feedback
N>>N-CNYS+UTYS_A | 2008-07-01 | 1 | Out= Canbera-Yass(9)+UpperTumut-Yass(2), avoid Canberra to KangarooValley (6) O/L on LowerTumut-Yass(3) trip; Feedback
N>>N-CNYS+UTYS_B | 2008-07-01 | 1 | Out= Canbera-Yass(9)+UpperTumut-Yass(2)+LowerTumut-UpperTumut(64), avoid Canberra to KangarooValley(6) O/L on LowerTumut-Yass(3) trip; Feedback
N>>N-CNYS+UTYS_C | 2008-07-01 | 1 | Out= Canbera-Yass(9)+UpperTumut-Yass(2), avoid LowerTumut to Yass (3) O/L (15min/SE rating) on Canberra-KangarooValley(6) trip; Feedback
N>>N-CNYS+UTYS_D | 2008-07-01 | 1 | Out= Canbera-Yass(9)+UpperTumut-Yass(2)+LowerTumut-UpperTumut(64), avoid LowerTumut to Yass (3) O/L (15min/SE rating) on Canberra-KangarooValley(6) trip; Feedback
N>>N-CNYS_A1S_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9), avoid Yass to UpperTumut(2) O/L(15m rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-CNYS_A1_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9), avoid UpperTumut to Yass (2) O/L(15m rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-CNYS_A2S_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9) + LowerTumut-UpperTumut(64), avoid Yass to UpperTumut(2) O/L(15m rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-CNYS_A2_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9) + LowerTumut-UpperTumut(64), avoid UpperTumut to Yass (2) O/L(15m rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-CNYS_B1_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9), avoid UpperTumut to Canberra (01) O/L(15m rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-CNYS_B2_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9) + LowerTumut-UpperTumut(64), avoid UpperTumut to Canberra (01) O/L(15m rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-CNYS_C1_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9), avoid LowerTumut to Yass(3) O/L(15m rating) on UpperTumut-Yass(2) trip; Feedback
N>>N-CNYS_C2_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9) + LowerTumut-UpperTumut(64), avoid LowerTumut to Yass (3) O/L(15m rating) on UpperTumut-Yass(2) trip; Feedback
N>>N-CNYS_D1_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9), avoid LowerTumut to Canberra (07) O/L(15m rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N-CNYS_D2_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9) + LowerTumut-UpperTumut(64), avoid LowerTumut-Canberra(07) O/L(15m rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N-CNYS_E1_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9), avoid LowerTumut to Yass(3) O/L(15m rating) on Canberra-KangarooValley(6) trip; Feedback
N>>N-CNYS_E2_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9) + LowerTumut-UpperTumut(64), avoid LowerTumut to Yass(3) O/L(15m rating) on Canberra-KangarooValley(6) trip; Feedback
N>>N-CNYS_F1_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9), avoid LowerTumut to Yass (3) O/L(15m rating) on KangarooValley-Dapto(18) trip; Feedback
N>>N-CNYS_F2_15M | 2008-07-01 | 1 | Out= Canberra-Yass(9) + LowerTumut-UpperTumut(64), avoid LowerTumut to Yass (3) O/L(15m rating) on KangarooValley-Dapto(18) trip; Feedback
N>>N-CNYS_G1 | 2008-07-01 | 1 | Out= Canberra-Yass(9), avoid LowerTumut to Yass (3) O/L on Nil trip; Feedback
N>>N-DP_TIETX_A | 2008-07-01 | 1 | Out= DarlingtonPt tie Tx(#3 or #4), avoid the remaining tie Tx O/L (330 to 220 kV) on Shepparton-Bendigo trip; Feedback
N>>N-DP_TIETX_B | 2008-07-01 | 1 | Out= DarlingtonPt tie Tx(#3 or #4), avoid the remaining tie Tx O/L (330 to 220 kV) on Nil trip; Feedback
N>>N-DTKV_1N | 2008-07-01 | 1 | Out= Dapto-KangarooValley(18), avoid Yass to Marulan (4) O/L on Marulan-Yass(5) trip; Feedback
N>>N-DTKV_1S | 2008-07-01 | 1 | Out= Dapto-KangarooValley(18), avoid Marulan to Yass (4) O/L on Marulan-Yass(5) trip; Feedback
N>>N-DTKV_8N | 2008-07-01 | 1 | Out= Dapto-KangarooValley(18), avoid Marulan to Dapto (8) O/L on Marulan-Avon(16) trip; Feedback
N>>N-DTKV_A_15M | 2008-07-01 | 1 | Out= Dapto-KangarooValley(18), avoid LowerTumut to Yass (3) O/L on Canberra-Yass(9) trip; Feedback
N>>N-DTKV_B | 2008-07-01 | 1 | Out= Dapto-KangarooValley(18), avoid Yass to SydneyWest (39) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-DTKV_C | 2008-07-01 | 1 | Out= Dapto-KangarooValley(18), avoid Marulan to Avon (16) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-DTKV_D | 2008-07-01 | 1 | Out= Dapto-KangarooValley(18), avoid MtPiper to Wallerawang (71) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-DTKV_E | 2008-07-01 | 1 | Out= Dapto-KangarooValley(18), avoid Canberra to Yass (9) O/L on LowerTumut-Yass(3) trip; Feedback
N>>N-DTKV_F | 2008-07-01 | 1 | Out= Dapto-KangarooValley(18), avoid MtPiper to Wallerawang (71) O/L on Yass-SydneyWest(39) trip; Feedback
N>>N-DTMN_01 | 2008-07-01 | 1 | Out= Dapto-Marulan(8), avoid MtPiper to Wallerawang (71) O/L on Marulan-Avon(16) trip; Feedback
N>>N-DTMN_02 | 2008-07-01 | 1 | Out= Dapto-Marulan(8), avoid MtPiper to Wallerawang (71) O/L on Yass-SydneyWest(39) trip; Feedback
N>>N-DTMN_03 | 2008-07-01 | 1 | Out= Dapto-Marulan(8), avoid MtPiper to Wallerawang (71) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-DTMN_04 | 2008-07-01 | 1 | Out= Dapto-Marulan(8), avoid MtPiper to Wallerawang (71) O/L on Canberra-KangarooValley(6) trip; Feedback
N>>N-DTMN_05 | 2008-07-01 | 1 | Out= Dapto-Marulan(8), avoid Marulan to Avon (16) O/L on MtPiper-Wallerawang(71) trip; Feedback
N>>N-DTMN_06 | 2008-07-01 | 1 | Out= Dapto-Marulan(8), avoid Marulan to Avon (16) O/L on Yass-SydneyWest(39) trip; Feedback
N>>N-DTMN_07 | 2008-07-01 | 1 | Out= Dapto-Marulan(8), avoid Marulan to Avon (16) O/L on Canberra-KangarooValley(6) trip; Feedback
N>>N-DTMN_08 | 2008-07-01 | 1 | Out= Dapto-Marulan(8), avoid Marulan to Avon(16) O/L on Dapto-KangarooValley(18) trip; Feedback
N>>N-DTMN_09 | 2008-07-01 | 1 | Out= Dapto-Marulan(8), avoid Yass to SydneyWest (39) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-DTMN_10 | 2008-07-01 | 1 | Out= Dapto-Marulan(8), avoid Yass to Marulan (5) O/L on Yass-Marulan(4) trip; Feedback
N>>N-DTSS_01 | 2008-07-01 | 1 | Out= Dapto-SydneySouth(11), avoid MtPiper to Wallerawang (71) O/L on Avon-KempsCreek(37) trip; Feedback
N>>N-DTSS_02 | 2008-07-01 | 1 | Out= Dapto-SydneySouth(11), avoid MtPiper to Wallerawang (71) O/L on Yass-SydneyWest(39) trip; Feedback
N>>N-DTSS_03 | 2008-07-01 | 1 | Out= Dapto-SydneySouth(11), avoid MtPiper to Wallerawang (71) O/L on Nil trip; Feedback
N>>N-DTSS_04 | 2008-07-01 | 1 | Out= Dapto-SydneySouth(11), avoid MtPiper to Wallerawang (71) O/L on KempsCreek-SydneySouth(13) trip; Feedback
N>>N-DTSS_05 | 2008-08-29 | 1 | Out= Dapto-SydneySouth(11), avoid KempsCreek to SydneySouth (13) O/L on KempsCreek-SydneyNorth(14) trip; Feedback
N>>N-DTSS_20 | 2008-07-01 | 1 | Out= Dapto-SydneySouth(11), avoid Yass to SydneyWest(39) O/L on Avon-KempsCreek(37) trip; Feedback
N>>N-ERKC_01_15M | 2008-07-01 | 1 | Out= Eraring-KempsCreek(5A1 or 5A2), avoid Eraring to Newcastle (93) O/L (15 min rating) on Eraring-KempsCreek(5A2 or 5A1) trip; Feedback
N>>N-ERKC_02_15M | 2008-07-01 | 1 | Out= Eraring-KempsCreek(5A1 or 5A2), avoid Eraring to Newcastle (93) O/L (15 min rating) on Eraring-Vineyard(25) trip; Feedback
N>>N-ERKC_03 | 2008-09-25 | 1 | Out= Eraring-KempsCreek(5A1 or 5A2), avoid ValesPoint to Munmorah (23) O/L on ValesPoint-SydneyNorth(22) trip; Feedback
N>>N-ERKC_04 | 2008-09-25 | 1 | Out= Eraring-KempsCreek(5A1 or 5A2), avoid ValesPoint to Munmorah (23) O/L on Eraring-KempsCreek(5A2 or 5A1) trip; Feedback
N>>N-ERNC90_A | 2008-09-15 | 1 | Out = Eraring to Newcastle (90), O/L on Eraring to Newcastle (93) on trip of Eraring to Vales point (24), Feedback
N>>N-ERNC90_B | 2008-09-15 | 1 | Out = Eraring to Newcastle (90), avoid O/L on Eraring to Vales Point (24) for trip of Eraring to Newcastle (93), Feedback
N>>N-ERNC93_A | 2008-09-15 | 1 | Out = Eraring to Newcastle (93), avoid O/L on Eraring to Newcastle (90) on trip of Eraring to Vales Point (24), Feedback
N>>N-ERNC93_B | 2008-09-15 | 1 | Out = Eraring to Newcastle (93), avoid O/L Eraring to Vales Point (24) on trip of Eraring to Newcastle (90), Feedback
N>>N-ERNC93_C | 2008-09-29 | 1 | Out = Eraring to Newcastle (93), avoid O/L Vales Point to Eraring (24) on trip of Eraring to Newcastle (90), Feedback
N>>N-ERNC_DY | 2008-07-01 | 1 | Out= Eraring-Newcastle(93), avoid Armidale to Kempsey (965) O/L on CoffsHarbour-Nambucca(9W3) trip; Feedback
N>>N-ERNC_NCVP_A | 2008-07-01 | 1 | Out= Eraring-Newcastle(93)+Newcastle-ValesPt(92), avoid Liddell to Tomago (82) O/L on Liddell-Newcastle(81) trip; Feedback
N>>N-ERNC_NCVP_DY | 2008-07-01 | 1 | Out= Eraring-Newcastle(93)+Newcastle-ValesPt(92), avoid Armidale to Kempsey (965) O/L on CoffsHarbour-Nambucca(9W3) trip; Feedback
N>>N-ERTX_B | 2008-07-01 | 1 | Out= Eraring 500/330 kV TieTx (#2), avoid Liddell to Newcastle (81) O/L on Liddell-Tomago(82) trip; Feedback
N>>N-ERTX_C | 2008-07-01 | 1 | Out= Eraring 500/330 kV TieTx (#2), avoid Liddell to Tomago (82) O/L on Liddell-Newcastle(81) trip; Feedback
N>>N-ERTX_D | 2008-10-16 | 1 | Out= Eraring 500/330 kV TieTx (#2), avoid Vales Point-Munmorah(23) O/L on Vales Point-Sydney North (22) trip; Feedback
N>>N-ERVP_A | 2008-09-15 | 1 | Out = Eraring to Vales Point (24), avoid O/L Eraring to Newcastle (90) on trip of Eraring to Newcastle (93), Feedback
N>>N-ERVP_B | 2008-09-15 | 1 | Out = Eraring to Vales Point (24), avoid O/L Eraring to Newcastle (93) on trip of Eraring to Newcastle (90), Feedback
N>>N-ERVY_01 | 2008-09-25 | 1 | Out= Eraring-Vineyard(25), avoid ValesPoint to Munmorah (23) O/L on Bayswater-Regentville(31) trip; Feedback
N>>N-ERVY_02 | 2008-09-25 | 1 | Out= Eraring-Vineyard(25), avoid ValesPoint to Munmorah (23) O/L on ValesPoint-SydneyNorth(22) trip; Feedback
N>>N-IGSS_01 | 2008-09-25 | 1 | Out= Ingleburn-SydneySouth(78), avoid Liddell to Tomago (82) O/L on Bayswater-Regentville(31) trip; Feedback
N>>N-IGSS_02 | 2008-09-25 | 1 | Out= Ingleburn-SydneySouth(78), avoid Liddell to Newcastle (81) O/L on Liddell-Tomago(82) trip; Feedback
N>>N-IGSS_03 | 2008-09-25 | 1 | Out= Ingleburn-SydneySouth(78), avoid Dapto to Sydney South (11) O/L on Wallerawang-SydneySouth(76) trip; Feedback
N>>N-IGSS_04 | 2008-09-25 | 1 | Out= Ingleburn-SydneySouth(78), avoid Liddell to Tomago (82) O/L on Liddell-Newcastle(81) trip; Feedback
N>>N-IGSS_05 | 2008-09-25 | 1 | Out= Ingleburn-SydneySouth(78), avoid Liddell to Newcastle (81) O/L on Bayswater-Regentville(31) trip; Feedback
N>>N-IGSS_06 | 2008-07-01 | 1 | Out= Ingleburn-SydneySouth(78), avoid Marulan to Dapto (8) O/L on Marulan-Avon(16) trip; Feedback
N>>N-IGWW_01 | 2008-09-25 | 1 | Out= Ingleburn-Wallerawang(77), avoid Liddell to Tomago (82) O/L on Bayswater-Regentville(31) trip; Feedback
N>>N-IGWW_02 | 2008-09-25 | 1 | Out= Ingleburn-Wallerawang(77), avoid Liddell to Newcastle (81) O/L on Liddell-Tomago(82) trip; Feedback
N>>N-IGWW_03 | 2008-09-25 | 1 | Out= Ingleburn-Wallerawang(77), avoid Dapto to Sydney South (11) O/L on Wallerawang-SydneySouth(76) trip; Feedback
N>>N-IGWW_04 | 2008-09-25 | 1 | Out= Ingleburn-Wallerawang(77), avoid Liddell to Tomago (82) O/L on Liddell-Newcastle(81) trip; Feedback
N>>N-IGWW_05 | 2008-09-25 | 1 | Out= Ingleburn-Wallerawang(77), avoid Liddell to Newcastle (81) O/L on Bayswater-Regentville(31) trip; Feedback
N>>N-IGWW_17 | 2008-07-01 | 1 | Out= Ingleburn-Wallerawang(77), avoid Marulan to Dapto (8) O/L on Marulan-Avon(16) trip; Feedback
N>>N-KCSN_04 | 2008-09-29 | 1 | Out= KempsCreek-SydneyNorth(14), avoid MtPiper to Wallerawang (71) O/L on KempsCreek-SydneySouth (13) trip; Feedback
N>>N-KCSN_05 | 2008-07-01 | 1 | Out= KempsCreek-SydneyNorth(14), avoid KempsCreek to SydneySouth (13) O/L on Eraring-Newcastle(93) trip; Feedback
N>>N-KCSN_05_15M | 2008-07-01 | 1 | Out= KempsCreek-SydneyNorth(14), avoid KempsCreek to SydneySouth (13) O/L (15 min rating) on Eraring-Newcastle(93) trip; Feedback
N>>N-KCSN_06 | 2008-07-01 | 1 | Out= KempsCreek-SydneyNorth(14), avoid KempsCreek to SydneySouth (13) O/L on KempsCreek-Avon(37) trip; Feedback
N>>N-KCSN_06_15M | 2008-07-01 | 1 | Out= KempsCreek-SydneyNorth(14), avoid KempsCreek to SydneySouth (13) O/L (15 min rating) on KempsCreek-Avon(37) trip; Feedback
N>>N-KCSS_01_15M | 2008-07-01 | 1 | Out= KempsCreek-SydneySouth(13), avoid Eraring to Newcastle (93) O/L (15 min rating) on KempsCreek-SydneyNorth(14) trip; Feedback
N>>N-KCSS_02_15M | 2008-07-01 | 1 | Out= KempsCreek-SydneySouth(13), avoid Eraring to Newcastle (93) O/L (15 min rating) on Eraring-Vineyard(25) trip; Feedback
N>>N-KCSS_03 | 2008-09-29 | 1 | Out= KempsCreek-SydneySouth(13), avoid MtPiper to Wallerawang (71) O/L on Bayswater-Wallerawang(74) trip; Feedback
N>>N-KCSS_04 | 2008-09-29 | 1 | Out= KempsCreek-SydneySouth(13), avoid SydneyWest to Liverpool (30) O/L on KempsCreek-Avon(37) trip; Feedback
N>>N-KCSS_06 | 2008-09-29 | 1 | Out= KempsCreek-SydneySouth(13), avoid Bayswater to Liddell (33) O/L on Bayswater-Liddell(34) trip; Feedback
N>>N-KCSS_08 | 2008-09-29 | 1 | Out= KempsCreek-SydneySouth(13), avoid MtPiper to Wallerawang (71) O/L on Dapto-SydneySouth(11) trip; Feedback
N>>N-KCSS_09 | 2008-09-29 | 1 | Out= KempsCreek-SydneySouth(13), avoid SydneyWest to Liverpool (30) O/L on Bayswater-Wallerawang(74) trip; Feedback
N>>N-KCSS_KCSN_N-2 | 2008-11-07 | 1 | Out=Nil, avoid O/L on Mt.Piper-Wallerawang (71) on trip of both KempsCreek-Sydney South(13) & KempsCreek-Sydney North (14), Feedback
N>>N-KC_TX_01 | 2008-10-16 | 1 | Out= one of KempsCreek 500/330kV transformers, avoid the remaining transformer O/L on Nil trip; Feedback
N>>N-KC_TX_03 | 2008-10-16 | 1 | Out= one of KempsCreek 500/330kV transformers, avoid the remaining transformer O/L (2 Hour rating) on Eraring-Vineyard(25) trip; Feedback
N>>N-KC_TX_04 | 2008-10-16 | 1 | Out= one of KempsCreek 500/330kV transformers, avoid the remaining transformer O/L (2 Hour rating) on Eraring-Newcastle(93) trip; Feedback
N>>N-KC_TX_05 | 2008-10-16 | 1 | Out= one of KempsCreek 500/330kV transformers, avoid the remaining transformer O/L (2 Hour rating) on Vales Point-Sydney North(22) trip; Feedback
N>>N-KC_TX_05_15M | 2008-07-01 | 1 | Out= one of KempsCreek 500/330kV transformers, avoid Eraring to Newcastle (93) O/L (15 min rating) on the remaining transformer trip; Feedback
N>>N-KC_TX_06_15M | 2008-07-01 | 1 | Out= one of KempsCreek 500/330kV transformers, avoid Eraring to Newcastle (93) O/L (15 min rating) on Eraring-Vineyard(25) trip; Feedback
N>>N-KSNB_01 | 2008-07-01 | 1 | Out= Kempsey to Nambucca (9W2), avoid O/L Armidale to Kempsey (965) on trip of Nil, Feedback
N>>N-KSNB_02 | 2008-07-01 | 1 | Out= Kempsey to Nambucca (9W2), avoid O/L (15 min rating) Armidale to Kempsey (965) on trip of Kurri to Stroud (96F), considering Port Macquarie area load
N>>N-LDNC_02 | 2008-09-25 | 1 | Out= Liddell-Newcastle(81); avoid Liddell to Tomago (82) O/L on Eraring-Newcastle(93) trip; Feedback
N>>N-LDNC_14 | 2008-07-01 | 1 | Out= Liddell-Newcastle(81), avoid MtPiper to Wallerawang (71) O/L on Bayswater-Wallerawang(74) trip; Feedback
N>>N-LDNC_19 | 2008-07-01 | 1 | Out= Liddell-Newcastle(81), avoid Liddell to Tomago (82) O/L on Bayswater-SydneyWest(32) trip; Feedback
N>>N-LDNC_1T | 2008-09-25 | 1 | Out= Liddell-Newcastle(81), avoid Liddell to Tomago (82) O/L on Nil trip; Feedback
N>>N-LDNC_22 | 2008-07-01 | 1 | Out= Liddell-Newcastle(81), avoid Liddell to Tomago (82) O/L on Bayswater-Regentville(31) trip; Feedback
N>>N-LDNC_31 | 2008-09-25 | 1 | Out= Liddell-Newcastle(81); avoid Bayswater to Regentville (31) O/L on Liddell-Tomago(82) trip; Feedback
N>>N-LDNC_32 | 2008-09-25 | 1 | Out= Liddell-Newcastle(81), avoid Bayswater-SydneyWest(32) O/L on Liddell to Tomago (82) trip; Feedback
N>>N-LDNC_73 | 2008-09-25 | 1 | Out= Liddell-Newcastle(81), avoid Liddell to Tomago (82) O/L on Bayswater-Mt. Piper(73) or Bayswater-Wallerawang(74) trip; Feedback
N>>N-LDNC_77 | 2008-09-25 | 1 | Out= Liddell-Newcastle(81), avoid Liddell to Tomago (82) O/L on Wallerawang-Ingleburn(77) or Wallerawang-SydneySouth (76) or Ingleburn-SydneySouth(78) trip; Feedback
N>>N-LDNC_82 | 2008-09-25 | 1 | Out= Liddell-Newcastle(81), avoid Liddell to Tomago (82) O/L on Regentville-SydneyWest(38) trip; Feedback
N>>N-LDNC_DY | 2008-07-01 | 1 | Out= Liddell-Newcastle(81), avoid Armidale to Kempsey (965) O/L on CoffsHarbour-Nambucca(9W3) trip; Feedback
N>>N-LDNC_LDTM_N-2 | 2008-12-09 | 1 | Out= Nil, avoid O/L on Bayswater-Regentville (31)on trip of both Liddell-Newcastle(81) & Liddell-Tomago (82)
N>>N-LDTM_01 | 2008-07-01 | 1 | Out= Liddell-Tomago(82), avoid Bayswater to Regentville (31) O/L on Liddell-Newcastle(81) trip; Feedback
N>>N-LDTM_02 | 2008-07-01 | 1 | Out= Liddell-Tomago(82), avoid Bayswater to SydneyWest (32) O/L on Liddell-Newcastle(81) trip; Feedback
N>>N-LDTM_05 | 2008-09-25 | 1 | Out= Liddell-Tomago(82), avoid Liddell to Newcastle (81) O/L on Eraring-Newcastle(93) trip; Feedback
N>>N-LDTM_06 | 2008-09-25 | 1 | Out= Liddell-Tomago(82), avoid Liddell to Newcastle (81) O/L on Wallerawang to Ingleburn (77) or Wallerawang to Sydney West (76) or Ingleburn to Sydney West (78) trip; Feedback
N>>N-LDTM_07 | 2008-09-25 | 1 | Out= Liddell-Tomago(82), avoid Liddell to Newcastle (81) O/L on Nil trip; Feedback
N>>N-LDTM_09 | 2008-07-01 | 1 | Out= Liddell-Tomago(82), avoid MtPiper to Wallerawang (71) O/L on Bayswater-Wallerawang(74) trip; Feedback
N>>N-LDTM_10 | 2008-07-01 | 1 | Out= Liddell-Tomago(82), avoid Liddell to Newcastle (81) O/L on Bayswater-Wallerawang(74) trip; Feedback
N>>N-LDTM_11 | 2008-07-01 | 1 | Out= Liddell-Tomago(82), avoid Liddell to Newcastle (81) O/L on Bayswater-MtPiper(73) trip; Feedback
N>>N-LDTM_14 | 2008-07-01 | 1 | Out= Liddell-Tomago(82), avoid Liddell to Newcastle (81) O/L on Bayswater-Regentville(31) trip; Feedback
N>>N-LDTM_15 | 2008-07-01 | 1 | Out= Liddell-Tomago(82), avoid Liddell to Newcastle (81) O/L on Bayswater-SydneyWest(32) trip; Feedback
N>>N-LDTM_38 | 2008-09-25 | 1 | Out= Liddell-Tomago(82), avoid Liddell to Newcastle (81) O/L on Regentville-SydneyWest(38) trip; Feedback
N>>N-LDTM_DY | 2008-07-01 | 1 | Out= Liddell-Tomago(82), avoid Armidale to Kempsey (965) O/L on CoffsHarbour-Nambucca(9W3) trip; Feedback
N>>N-LPSS_03 | 2008-07-01 | 1 | Out= Liverpool-SydneySouth(12), avoid KempsCreek to SydneySouth (13) O/L on KempsCreek-Avon(37) trip; Feedback
N>>N-LPSS_04 | 2008-07-01 | 1 | Out= Liverpool-SydneySouth(12), avoid MtPiper to Wallerawang (71) O/L on KempsCreek-SydneySouth(13) trip; Feedback
N>>N-LPSW_01 | 2008-09-25 | 1 | Out= Liverpool-SydWest(30), avoid KempsCk->SydSouth(13) OL on KempsCk-Avon(37) trip; Fb,CoOp
N>>N-LPSW_04 | 2008-09-25 | 1 | Out= Liverpool to Sydney West (30), avoid O/L Mt Piper to Wallerawang (71) on trip of Bayswater to Wallerawang (74), Feedback
N>>N-LPSW_05 | 2008-09-25 | 1 | Out= Liverpool to Sydney West (30), avoid O/L Kemps Creek to Sydney South (13) on trip of Avon to Dapto (10), Feedback
N>>N-LPSW_06 | 2008-09-25 | 1 | Out= Liverpool to Sydney West (30), avoid O/L Mt Piper to Wallerawang (71) on trip of Kemps Creek to Sydney South (13), Feedback
N>>N-LTMS_2 | 2008-07-01 | 1 | Out= LowerTumut-Murray(66), avoid Wagga to LowerTumut (051) O/L on Murray-UpperTumut(65) trip; Feedback
N>>N-LTMS_3 | 2008-07-01 | 1 | Out= LowerTumut-Murray(66), avoid LowerTumut to Wagga (051) O/L on UpperTumut-Murray(65) trip; Feedback
N>>N-LTMS_4 | 2008-07-01 | 1 | Out= LowerTumut-Murray(66), avoid UpperTumut to Canberra (01) O/L(15_m rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-LTUT_A_15M | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid LowerTumut to Canberra (07) O/L (15m rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N-LTUT_A_SE | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid LowerTumut to Canberra (07) O/L (contingency rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N-LTUT_B_15M | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Canberra (01) O/L (15m rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-LTUT_B_SE | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Canberra (01) O/L (contingency rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-LTUT_C_15M | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid LowerTumut to Yass (3) O/L (15m rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-LTUT_C_SE | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid LowerTumut to Yass (3) O/L (contingency rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-LTUT_D_15M | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Canberra (01) O/L (15m rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-LTUT_D_SE | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Canberra (01) O/L (contingency rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-LTUT_E_15M | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Canberra (01) O/L (15m rating) on UpperTumut-Yass(2) trip; Feedback
N>>N-LTUT_E_SE | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Canberra (01) O/L (contingency rating) on UpperTumut-Yass(2) trip; Feedback
N>>N-LTUT_F_15M | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Yass (2) O/L (15m rating) on Canberra-UpperTumut(01) trip; Feedback
N>>N-LTUT_F_SE | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Yass (2) O/L (contingency rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N-LTUT_G_15M | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Yass (2) O/L (15m rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-LTUT_G_SE | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Yass (2) O/L (contingency rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-LTUT_H_15M | 2009-01-15 | 1 | Out= LowerTumut-UpperTumut(64), avoid LowerTumut to Canberra (07) O/L (15m rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-LTUT_H_SE | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid LowerTumut to Canberra (07) O/L (contingency rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-LTUT_I_15M | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Canberra (01) O/L (15m rating) on Wodonga-Jindera(060) trip; Feedback
N>>N-LTUT_I_SE | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Canberra (01) O/L (contingency rating) on Wodonga-Jindera(060) trip; Feedback
N>>N-LTUT_K_15M | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Yass (2) O/L (15m rating) on Canberra-Yass(9) trip; Feedback
N>>N-LTUT_K_SE | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Yass (2) O/L (contingency rating) on Canberra-Yass(9) trip; Feedback
N>>N-LTUT_U_15M | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Canberra (01) O/L (15m rating) on Jindera-Wagga(62) trip; Feedback
N>>N-LTUT_U_SE | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Canberra (01) O/L (contingency rating) on Jindera-Wagga(62) trip; Feedback
N>>N-LTYS_A | 2008-07-01 | 1 | Out= LowerTumut-Yass(3), avoid Yass to Canberra (9) O/L on Yass-UpperTumut(2) trip; Feedback
N>>N-LTYS_B | 2008-07-01 | 1 | Out= LowerTumut-Yass(3), avoid Canberra to Yass (9) O/L on UpperTumut-Yass(2) trip; Feedback
N>>N-LTYS_HA_15M | 2008-07-01 | 1 | Out= LowerTumut-Yass(3), avoid UpperTumut to Canberra (01) O/L (15 min rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-MMSN_01 | 2008-08-25 | 1 | Out= Munmorah-SydneyNorth(21), avoid ValesPoint to SydneyNorth (22) O/L on Munmorah-SydneyWest(26) trip; Feedback
N>>N-MMSW_01 | 2008-11-28 | 1 | Out= Munmorah-SydneyWest(26), avoid ValesPt to SydneyNorth (22) O/L on Munmorah-Tuggerah(2M) trip; Feedback
N>>N-MNMP_N-2_01 | 2008-07-01 | 1 | Out=Nil, avoid O/L Mt Piper to Wallerawang (71) on trip of both Marulan to Mt Piper (35 + 36) lines, Feedback
N>>N-MNMP_ONE_1 | 2008-07-01 | 1 | Out= Marulan-MtPiper(35 or 36), avoid MtPiper to Wallerawang (71) O/L on MtPiper-Marulan(36 or 35) trip; Feedback
N>>N-MNMP_ONE_4 | 2008-07-01 | 1 | Out= Marulan-MtPiper(35 or 36), avoid Wallerawang to Ingleburn (77) O/L on MtPiper-Marulan(36 or 35) trip; Feedback
N>>N-MNMP_ONE_5 | 2008-07-01 | 2 | Out= Marulan-MtPiper(35 or 36), avoid Wellington to Parkes (94K) O/L on MtPiper-Marulan(36 or 35) trip; Feedback
N>>N-MNMP_TWO_1 | 2008-07-01 | 1 | Out= both Marulan to Mt Piper (35 + 36), avoid O/L Mt Piper to Wallerawang (71) on trip of Nil, Feedback
N>>N-MNMP_TWO_2 | 2008-07-01 | 1 | Out= both Marulan to Mt Piper (35 + 36), avoid O/L Mt Piper to Wallerawang (71) on trip of Bayswater to Wallerawang (74), Feedback
N>>N-MNMP_TWO_3 | 2008-07-01 | 1 | Out= both Marulan to Mt Piper (35 + 36), avoid O/L Mt Piper to Wallerawang (71) on trip of Bayswater to Regentville (31), Feedback
N>>N-MNMP_TWO_4 | 2008-07-01 | 1 | Out= both Marulan to Mt Piper (35 + 36), avoid O/L Wallerawang to Sydney South (76) on trip of Wallerawang to Ingleburn (77), Feedback
N>>N-MNMP_TWO_5 | 2008-07-01 | 1 | Out= both Marulan to Mt Piper (35 + 36), avoid O/L Mt Piper to Wallerawang (94E) on trip of Mt Piper to Wallerawang (71), Feedback
N>>N-MNMP_TWO_6 | 2008-07-01 | 1 | Out= both Marulan to Mt Piper (35 + 36), avoid O/L Mt Piper330/132kV transformer on trip of Mt Piper to Wallerawang (71), Feedback
N>>N-MNYS4_01 | 2008-07-01 | 1 | Out= Marulan-Yass(4), avoid Marulan to Yass(5) O/L on SydneyWest-Yass(39) trip; Feedback
N>>N-MNYS4_02 | 2008-07-01 | 1 | Out= Marulan-Yass(4), avoid Marulan to Yass (5) O/L on Dapto-KangarooValley(18) trip; Feedback
N>>N-MNYS4_03 | 2008-07-01 | 1 | Out= Marulan-Yass(4), avoid Marulan to Yass(5) O/L on KangarooValley-Canberra(6) trip; Feedback
N>>N-MNYS4_04 | 2008-07-01 | 1 | Out= Marulan-Yass(4), avoid Marulan to Yass(5) O/L on NIL trip; Feedback
N>>N-MNYS4_05 | 2008-07-01 | 1 | Out= Marulan-Yass(4), avoid Dapto to KangarooValley(18) O/L on Marulan-Yass(5) trip; Feedback
N>>N-MNYS4_06 | 2008-07-01 | 1 | Out= Marulan-Yass(4), avoid SydneyWest to Yass(39) O/L on Marulan-Yass(5) trip; Feedback
N>>N-MNYS4_07 | 2008-07-01 | 1 | Out= Marulan-Yass(4), avoid Yass to Marulan(5) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-MNYS4_08 | 2008-07-01 | 1 | Out= Marulan-Yass(4), avoid Yass to Marulan(5) O/L on Canberra-KangarooValley(6) trip; Feedback
N>>N-MNYS4_09 | 2008-07-01 | 1 | Out= Marulan-Yass(4), avoid KangarooValley to Dapto(18) O/L on Yass-Marulan(5) trip; Feedback
N>>N-MNYS4_10 | 2008-07-01 | 1 | Out= Marulan-Yass(4), avoid Yass to Marulan(5) O/L on Yass-SydneyWest(39) trip; Feedback
N>>N-MNYS4_11 | 2008-07-01 | 1 | Out= Marulan-Yass(4), avoid Yass to SydneyWest(39) O/L on Yass-Marulan(5) trip; Feedback
N>>N-MNYS4_12 | 2008-07-01 | 1 | Out= Marulan-Yass(4), avoid Yass to Marulan(5) O/L on NIL trip; Feedback
N>>N-MNYS5_01 | 2008-07-01 | 1 | Out= Marulan-Yass(5), avoid Marulan to Yass(4) O/L on SydneyWest-Yass(39) trip; Feedback
N>>N-MNYS5_02 | 2008-07-01 | 1 | Out= Marulan-Yass(5), avoid Marulan to Yass(4) O/L on Dapto-KangarooValley(18) trip; Feedback
N>>N-MNYS5_03 | 2008-07-01 | 1 | Out= Marulan-Yass(5), avoid Marulan to Yass(4) O/L on KangarooValley-Canberra(6) trip; Feedback
N>>N-MNYS5_04 | 2008-07-01 | 1 | Out= Marulan-Yass(5), avoid Dapto to KangarooValley(18) O/L on Marulan-Yass(4) trip; Feedback
N>>N-MNYS5_05 | 2008-07-01 | 1 | Out= Marulan-Yass(5), avoid SydneyWest to Yass(39) O/L on Marulan-Yass(4) trip; Feedback
N>>N-MNYS5_06 | 2008-07-01 | 1 | Out= Marulan-Yass(5), avoid Yass to Marulan(4) O/L on Yass-SydneyWest(39) trip; Feedback
N>>N-MNYS5_07 | 2008-07-01 | 1 | Out= Marulan-Yass(5), avoid Yass to Marulan(4) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-MNYS5_08 | 2008-07-01 | 1 | Out= Marulan-Yass(5), avoid Yass to Marulan(4) O/L on Canberra-KangarooValley(6) trip; Feedback
N>>N-MNYS5_09 | 2008-07-01 | 1 | Out= Marulan-Yass(5), avoid KangarooValley to Dapto(18) O/L on Yass-Marulan(4) trip; Feedback
N>>N-MNYS5_10 | 2008-07-01 | 1 | Out= Marulan-Yass(5), avoid Yass to SydneyWest(39) O/L on Yass-Marulan(4) trip; Feedback
N>>N-MPWL_A | 2008-07-01 | 1 | Out= MtPiper-Wellington(72), avoid MtPiper to Wallerawang (71) O/L on Bayswater-Wallerawang(74) trip; Feedback
N>>N-MPWL_B | 2008-07-01 | 1 | Out= MtPiper-Wellington(72), avoid MtPiper to Wallerawang (71) O/L on Yass-SydneyWest(39) trip; Feedback
N>>N-MPWL_C | 2008-07-01 | 1 | Out= MtPiper-Wellington(72), avoid MtPiper to Wallerawang (71) O/L on Dapto-SydneySouth(11) trip; Feedback
N>>N-MPWL_D | 2008-07-01 | 1 | Out= MtPiper-Wellington(72), avoid MtPiper to Wallerawang (71) O/L on Nil trip; Feedback
N>>N-MPWL_E | 2008-07-01 | 1 | Out= MtPiper-Wellington(72), avoid MtPiper to Wallerawang (71) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-MPWW_01 | 2008-07-01 | 1 | Out= MtPiper-Wallerawang(71), avoid Marulan to Avon (16) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-MPWW_02 | 2008-07-01 | 1 | Out= MtPiper-Wallerawang(71), avoid Marulan to Dapto (8) O/L on Marulan-Avon(16) trip; Feedback
N>>N-MPWW_03 | 2008-07-01 | 1 | Out= MtPiper-Wallerawang(71), avoid MtPiper 330/132kV (3H) transformer O/L on Nil trip; Feedback
N>>N-MPWW_04 | 2008-07-01 | 1 | Out= MtPiper-Wallerawang(71), avoid MtPiper to Wallerawang (94E) O/L on Nil trip; Feedback
N>>N-MPWW_09 | 2008-07-01 | 1 | Out= MtPiper-Wallerawang(71), avoid Yass to SydneyWest (39) O/L on Nil trip; Feedback
N>>N-MPWW_10 | 2008-07-01 | 1 | Out= MtPiper-Wallerawang(71), avoid Yass to SydneyWest (39) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-MSUT_1 | 2008-07-01 | 1 | Out= Murray-UpperTumut(65), avoid LowerTumut to Wagga (051) O/L on LowerTumut-Murray(66) trip; Feedback
N>>N-MSUT_1E | 2008-07-01 | 1 | Out= Murray-UpperTumut(65), avoid Wagga to LowerTumut (051) O/L on Murray-LowerTumut(66) trip; Feedback
N>>N-MSUT_2 | 2008-07-01 | 1 | Out= Murray-UpperTumut(65), avoid LowerTumut to Canberra (07) O/L(15_m rating) on LowerTumut-UpperTumut(64) trip; Feedback
N>>N-MSUT_3 | 2008-07-01 | 1 | Out= Murray-UpperTumut(65), avoid LowerTumut to Canberra (07) O/L(15_m rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-NIL_01S | 2008-07-01 | 1 | Out= Nil, avoid O/L Yass to Canberra (9) on trip of Dapto to Kangaroo Valley (18), Feedback
N>>N-NIL_03 | 2008-07-01 | 1 | Out= Nil, avoid O/L Yass to Canberra (9) on trip of Kangaroo Valley to Canberra (6), Feedback
N>>N-NIL_17N | 2008-07-01 | 1 | Out= Nil, avoid O/L Yass to Marulan (4) on trip of Kangaroo Valley to Dapto (18), Feedback
N>>N-NIL_17S | 2008-07-01 | 1 | Out= Nil, avoid O/L Marulan to Yass (4) on trip of Dapto to Kangaroo Valley (18), Feedback
N>>N-NIL_1A | 2008-09-15 | 1 | Out=Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback
N>>N-NIL_1E | 2009-08-25 | 1 | Out=Nil, avoid Liddel to Newcastl (81) O/L on loss of Liddell to Tomago (82), Feedback
N>>N-NIL_1G | 2009-07-07 | 1 | Out=Nil, avoid Vales Pt to Munmorah (23) O/L on trip of Vales Pt to Sydney North(22), Feedback
N>>N-NIL_1N | 2008-09-15 | 1 | Out= NIL, avoid Liddell to Tomago(82) O/L on Liddell to Newcastle(81) trip; Feedback
N>>N-NIL_1O | 2008-07-01 | 1 | Out= Nil, avoid Liddell to Newcastle (81) O/L on Bayswater to Regentville (31) trip, Feedback
N>>N-NIL_1R | 2009-07-07 | 1 | Out= Nil, avoid O/L Vales Point to Munmorah (23) on trip of Eraring to Vineyard (25), Feedback
N>>N-NIL_1S | 2008-09-15 | 1 | Out= NIL, avoid Liddell to Newcastle (81) O/L on Nil trip; Feedback
N>>N-NIL_1T | 2008-09-15 | 1 | Out= NIL, avoid Liddell to Tomago (82) O/L on Nil trip; Feedback
N>>N-NIL_1U | 2008-07-01 | 1 | Out= Nil, avoid MtPiper 330/132kV transformer O/L on MtPiper-Wallerawang(71) trip, Feedback
N>>N-NIL_1V | 2008-07-01 | 1 | Out= Nil, avoid MtPiper to Wallerawang (94E) O/L on MtPiper-Wallerawang(71) trip, Feedback
N>>N-NIL_1WN | 2008-07-01 | 1 | Out= Nil, avoid Yass to Marulan (5) O/L on Yass-Marulan(4) trip, Feedback
N>>N-NIL_1WS | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Yass (5) O/L on Marulan-Yass(4) trip, Feedback
N>>N-NIL_1XN | 2008-07-01 | 1 | Out= Nil, avoid Yass to Marulan (4) O/L on Yass-Marulan(5) trip, Feedback
N>>N-NIL_1XS | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Yass (4) O/L on Marulan-Yass(5) trip, Feedback
N>>N-NIL_1Y | 2008-07-01 | 1 | Out= Nil, avoid Yass to Marulan (4) O/L on Canberra-KangarooValley(6) trip, Feedback
N>>N-NIL_1YS | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Yass (4) O/L on KangarooValley-Canberra(6) trip, Feedback
N>>N-NIL_1Z | 2008-07-01 | 1 | Out= Nil, avoid Yass to Marulan (5) O/L on Canberra-KangarooValley(6) trip, Feedback
N>>N-NIL_1ZS | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Yass (5) O/L on KangarooValley-Canberra(6) trip, Feedback
N>>N-NIL_23N | 2008-07-01 | 1 | Out= Nil, avoid Yass to Marulan (5) O/L on KangarooValley-Dapto(18) trip, Feedback
N>>N-NIL_23S | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Yass (5) O/L on Dapto-KangarooValley(18) trip, Feedback
N>>N-NIL_28 | 2008-07-01 | 1 | Out= NIL, avoid Marulan to Dapto (8) O/L on Marulan-Avon(16) trip; Feedback
N>>N-NIL_29N | 2008-07-01 | 1 | Out= Nil, avoid Yass to Marulan (4) O/L on trip of Yass-SydneyWest(39), Feedback
N>>N-NIL_29S | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Yass (4) O/L on trip of SydneyWest-Yass(39), Feedback
N>>N-NIL_31N | 2008-07-01 | 1 | Out= Nil, avoid Yass to Marulan (5) O/L on Yass-SydneyWest(39) trip, Feedback
N>>N-NIL_31S | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Yass (5) O/L on SydneyWest-Yass(39) trip, Feedback
N>>N-NIL_36 | 2009-09-22 | 1 | Out= Nil, avoid Wagga to Jindera (62) O/L on trip of Nil, Feedback
N>>N-NIL_45 | 2009-01-27 | 1 | Out= Nil, avoid Yass to SydneyWest (39) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-NIL_46 | 2008-07-01 | 1 | Out= Nil, avoid Dapto to KangarooValley (18) O/L on Marulan-Yass(4) trip; Feedback
N>>N-NIL_47 | 2008-07-01 | 1 | Out= Nil, avoid KangarooValley to Dapto (18) O/L on Yass-Marulan(5) trip; Feedback
N>>N-NIL_48 | 2008-07-01 | 1 | Out= Nil, avoid KangarooValley to Dapto (18) O/L on Yass-Marulan(4) trip; Feedback
N>>N-NIL_49 | 2008-07-01 | 1 | Out= Nil, avoid Dapto to KangarooValley (18) O/L on Marulan-Yass(5) trip; Feedback
N>>N-NIL_56 | 2009-01-27 | 1 | Out= Nil, avoid Yass to SydneyWest (39) O/L on Yass-Marulan(4) trip; Feedback
N>>N-NIL_57 | 2008-07-01 | 1 | Out= Nil, avoid Dapto to KangarooValley (18) O/L on SydneyWest-Yass(39) trip; Feedback
N>>N-NIL_58 | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Dapto (8) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-NIL_59 | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Dapto (8) O/L on Canberra-KangarooValley(6) trip; Feedback
N>>N-NIL_5H | 2008-07-01 | 1 | Out= Nil, avoid Lower Tumut to Upper Tumut (64) O/L (30 minute rating) on Murray-UpperTumut(65) trip; Feedback
N>>N-NIL_60 | 2008-07-01 | 1 | Out= Nil, avoid Yass to SydneyWest (39) O/L on Canberra-KangarooValley(6) trip; Feedback
N>>N-NIL_61 | 2009-01-27 | 1 | Out= Nil, avoid Yass to SydneyWest (39) O/L on Yass-Marulan(5) trip; Feedback
N>>N-NIL_62 | 2009-01-27 | 1 | Out= Nil, avoid KangarooValley to Dapto (18) O/L on Marulan-Avon(16) trip; Feedback
N>>N-NIL_63 | 2009-01-27 | 1 | Out= Nil, avoid KangarooValley to Dapto (18) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-NIL_68 | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Yass (4) O/L on Bayswater-Regentville(31) trip; Feedback
N>>N-NIL_6H | 2008-07-01 | 1 | Out= Nil, avoid Upper Tumut to Lower Tumut (64) O/L (30 minute rating) on Murray-LowerTumut(66) trip; Feedback
N>>N-NIL_70 | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Yass (4) O/L on Wallerawang-Ingleburn(77) trip; Feedback
N>>N-NIL_72 | 2008-07-01 | 1 | Out= Nil, avoid Yass to SydneyWest (39) O/L on Dapto-SydneySouth(11) trip; Feedback
N>>N-NIL_73 | 2008-07-01 | 1 | Out= Nil, avoid Yass to SydneyWest (39) O/L on Avon-KempsCk(37) trip; Feedback
N>>N-NIL_77 | 2009-07-07 | 1 | Out= Nil, avoid KangarooValley to Canberra (6) O/L on Yass-Canberra(9) trip; Feedback
N>>N-NIL_81 | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Yass (4) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-NIL_9W7 | 2009-07-23 | 1 | Out= Nil, avoid Raleigh-Nambucca (9W7) O/L on Armidale-Kempsey(965) trip; Feedback
N>>N-NIL_AH | 2008-07-01 | 1 | Out= Nil, avoid Lower Tumut to Canberra (07) O/L (contingency rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N-NIL_BH | 2008-07-01 | 1 | Out= Nil, avoid Upper Tumut to Canberra (01) O/L (contingency rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-NIL_CH | 2008-07-01 | 1 | Out= Nil, avoid Lower Tumut to Yass (3) O/L (contingency rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-NIL_DF_1 | 2007-10-22 | 1 | Out= Nil, avoid Armidale->Kempsey(965) OL(15m rat) on Coffs_Harbour-Nambucca(9W3) trip, both Raleigh and Sawtell loads supplied ex Coffs_H, TG_spec
N>>N-NIL_DF_DS | 2008-06-05 | 1 | Out= Nil, avoid Armidale->Kempsey(965) OL(selected rating) on Coffs_Harbour-Nambucca(9W3) trip, NEMMCO_spec
N>>N-NIL_DF_PD | 2008-06-05 | 3 | Out= Nil, avoid Armidale->Kempsey(965) OL(15m rat) on Coffs_Harbour-Nambucca(9W3) trip, both Raleigh and Sawtell loads supplied ex Coffs_H, TG_spec
N>>N-NIL_DH | 2008-07-01 | 1 | Out= Nil, avoid Upper Tumut to Canberra (01) O/L (contingency rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-NIL_DPTX | 2009-09-22 | 1 | Out=Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other
N>>N-NIL_DX_1 | 2006-12-18 | 1 | Out= Nil, avoid Armidale->Kempsey(965) OL(15m rat) on Coffs_Harbour-Nambucca(9W3) trip, one only of Raleigh, Sawtell loads supplied ex Coffs_H, TG_spec
N>>N-NIL_DY_1 | 2006-12-18 | 1 | Out= Nil, avoid Armidale->Kempsey(965) OL(15m rat) on Coffs_Harbour-Nambucca(9W3) trip, Raleigh & Sawtell not ex Coffs_H, TG_spec
N>>N-NIL_EH | 2008-07-01 | 1 | Out= Nil, avoid Upper Tumut to Canberra (01) O/L (contingency rating) on UpperTumut-Yass(2) trip; Feedback
N>>N-NIL_FH | 2008-07-01 | 1 | Out= Nil, avoid Upper Tumut to Yass (2) O/L (contingency rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N-NIL_GH | 2008-07-01 | 1 | Out= Nil, avoid Upper Tumut to Yass (2) O/L (contingency rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-NIL_H01 | 2009-09-22 | 1 | Out= Nil, avoid Upper Tumut to Canberra (01) O/L on Nil trip; Feedback
N>>N-NIL_H02 | 2009-09-22 | 1 | Out= Nil, avoid Upper Tumut to Yass (2) O/L on Nil trip; Feedback
N>>N-NIL_H03 | 2009-07-07 | 1 | Out= Nil, avoid Lower Tumut to Yass (3) O/L on Nil trip; Feedback
N>>N-NIL_H051 | 2009-09-22 | 1 | Out= Nil, avoid Lower Tumut to Wagga (051) O/L on Nil trip; Feedback
N>>N-NIL_H060 | 2009-09-22 | 1 | Out= Nil, avoid Wodonga to Jindera (060) O/L on Nil trip; Feedback
N>>N-NIL_H07 | 2009-07-07 | 1 | Out= Nil, avoid Lower Tumut to Canberra (07) O/L on Nil trip; Feedback
N>>N-NIL_HA_15M | 2008-07-01 | 1 | Out= Nil, avoid LowerTumut->Canberra(07) O/L(15_min/5MRAS rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N-NIL_HB_15M | 2008-07-01 | 1 | Out= Nil, avoid UpperTumut->Canberra(01) O/L(15_min/5MRAS rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-NIL_HC_15M | 2008-07-01 | 1 | Out= Nil, avoid LowerTumut->Yass(3) O/L(15_min/5MRAS rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N-NIL_HD_15M | 2008-07-01 | 1 | Out= Nil, avoid UpperTumut->Canberra(01) O/L(15_min/5MRAS rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-NIL_HE | 2008-07-01 | 1 | Out= Nil, avoid Lower Tumut to Upper Tumut (64) O/L on Murray-UpperTumut(65) trip; Feedback
N>>N-NIL_HE_15M | 2008-07-01 | 1 | Out= Nil, avoid UpperTumut->Canberra(01) O/L(15_min/5MRAS rating) on UpperTumut-Yass(2) trip; Feedback
N>>N-NIL_HF | 2009-09-22 | 1 | Out= Nil, avoid Upper Tumut to Lower Tumut (64) O/L on Murray-LowerTumut(66) Trip; Feedback
N>>N-NIL_HF_15M | 2008-07-01 | 1 | Out= Nil, avoid UpperTumut->Yass(2) O/L(15_min/5MRAS rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N-NIL_HG_15M | 2008-07-01 | 1 | Out= Nil, avoid UpperTumut->Yass(2) O/L(15_min/5MRAS rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-NIL_HH | 2008-07-01 | 1 | Out= Nil, avoid Lower Tumut to Canberra (07) O/L (contingency rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-NIL_HH_15M | 2008-07-01 | 1 | Out= Nil, avoid LowerTumut->Canberra(07) O/L(15_min/5MRAS rating) on LowerTumut-Yass(3) trip; Feedback
N>>N-NIL_HI_15M | 2009-09-22 | 1 | Out= Nil, avoid Upper Tumut to Canberra (01) O/L (15 min rating) on Jindera-Wodonga(060) trip; Feedback
N>>N-NIL_HK_15M | 2009-09-22 | 1 | Out= Nil, avoid Upper Tumut to Yass (2) O/L (15 min rating) on Canberra-Yass(9) trip; Feedback
N>>N-NIL_HL | 2009-09-22 | 1 | Out= Nil, avoid Lower Tumut to Upper Tumut (64) O/L on NIL trip; Feedback
N>>N-NIL_HM | 2009-09-22 | 1 | Out= Nil, avoid Upper Tumut to Lower Tumut (64) O/L on NIL trip; Feedback
N>>N-NIL_HU_15M | 2009-09-22 | 1 | Out= Nil, avoid Upper Tumut to Canberra (01) O/L (15 min rating) on Jindera-Wagga(62) trip; Feedback
N>>N-NIL_IH | 2008-07-01 | 1 | Out= Nil, avoid Upper Tumut to Canberra (01) O/L (contingency rating) on Wodonga-Jindera(060) trip; Feedback
N>>N-NIL_KH | 2008-07-01 | 1 | Out= Nil, avoid Upper Tumut to Yass (2) O/L (contingency rating) on Canberra-Yass(9) trip; Feedback
N>>N-NIL_LH | 2009-07-07 | 1 | Out= Nil, avoid Lower Tumut to Yass (3) O/L (contingency rating) on UpperTumut-Yass(2) trip; Feedback
N>>N-NIL_MH | 2008-07-01 | 1 | Out= Nil, avoid Lower Tumut to Canberra (07) O/L (contingency rating) on UpperTumut-Yass(2) trip; Feedback
N>>N-NIL_UH | 2008-07-01 | 1 | Out= Nil, avoid Upper Tumut to Canberra (01) O/L (contingency rating) on Jindera-Wagga(62) trip; Feedback
N>>N-NIL__A | 2008-07-01 | 1 | Out= Nil, avoid MtPiper to Wallerawang (71) O/L on Dapto-SydneySouth(11) trip; Feedback
N>>N-NIL__B | 2008-07-01 | 1 | Out= Nil, avoid MtPiper to Wallerawang (71) O/L on Yass-SydneyWest(39) trip; Feedback
N>>N-NIL__C | 2008-07-01 | 1 | Out= Nil, avoid MtPiper to Wallerawang (71) O/L on Avon-KempsCreek(37) trip; Feedback
N>>N-NIL__E | 2008-11-05 | 1 | Out= Nil, avoid MtPiper to Wallerawang (71) O/L on Bayswater-Wallerawang(74) trip; Feedback
N>>N-NIL__F | 2008-07-01 | 1 | Out= Nil, avoid MtPiper to Wallerawang (71) O/L on Marulan-Avon(16) trip; Feedback
N>>N-NIL__G | 2008-07-01 | 1 | Out= Nil, avoid MtPiper to Wallerawang (71) O/L on trip of Marulan-Dapto(8); Feedback
N>>N-NIL__H | 2008-07-01 | 1 | Out= Nil, avoid Wallerawang to MtPiper (71) O/L on Bayswater-MtPiper(73) trip; Feedback
N>>N-NIL__I | 2008-07-01 | 1 | Out= Nil, avoid MtPiper to Wallerawang (71) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-NIL__J | 2008-07-01 | 1 | Out= Nil, avoid MtPiper to Wallerawang (71) O/L on Nil trip; Feedback
N>>N-NIL__K | 2009-08-25 | 1 | Out= Nil, avoid Wallerawang to Ingleburn (77) O/L on Wallerawang-SydneySouth(76) trip, Feedback
N>>N-NIL__L | 2008-07-01 | 1 | Out= Nil, avoid Wallerawang to Sydney South (76) O/L on Wallerawang-Ingleburn(77) trip; Feedback
N>>N-NIL__M | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Avon (16) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-NIL__N | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Avon (16) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-NIL__O | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Avon (16) O/L on Canberra-KangarooValley(6) trip; Feedback
N>>N-NIL__P | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Avon (16) O/L on Yass-SydneyWest(39) trip; Feedback
N>>N-NIL__Q | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Avon (16) O/L on MtPiper-Wallerawang(71) trip; Feedback
N>>N-NIL__R | 2008-07-01 | 1 | Out= Nil, avoid Marulan to Avon (16) O/L on Wallerawang-SydneySouth(76) trip; Feedback
N>>N-NIL__S | 2009-08-25 | 1 | Out= Nil, avoid MtPiper to Wallerawang (70) O/L on MtPiper to Wallerawang (71) trip; Feedback
N>>N-RGSW_A | 2008-09-26 | 1 | Out= Regentville to Sydney West (38), avoid O/L Bayswater to Liddell (34) on trip of Bayswater to Liddell (33), Feedback
N>>N-RGSW_B | 2008-09-26 | 1 | Out= Regentville to Sydney West (38), avoid O/L Liddell to Newcastle (81) on trip of Bayswater to Sydney West (32), Feedback
N>>N-RGSW_C | 2008-09-26 | 1 | Out= Regentville to Sydney West (38), avoid O/L Liddell to Newcastle (81) on trip of Bayswater to Mt Piper (73), Feedback
N>>N-RGSW_D | 2008-09-26 | 1 | Out= Regentville to Sydney West (38), avoid O/L Liddell to Newcastle (81) on trip of Liddell to Tomago (82), Feedback
N>>N-RGSW_E | 2008-09-26 | 1 | Out= Regentville to Sydney West (38), avoid O/L Liddell to Newcastle (81) on trip of Nil, Feedback
N>>N-RGSW_F | 2008-09-26 | 1 | Out= Regentville to Sydney West (38), avoid O/L Liddell to Tomago (82) on trip of Bayswater to Sydney West (32), Feedback
N>>N-RGSW_G | 2008-09-26 | 1 | Out= Regentville to Sydney West (38), avoid O/L Liddell to Tomago (82) on trip of Liddell to Newcastle (81), Feedback
N>>N-RGSW_H | 2008-09-26 | 1 | Out= Regentville to Sydney West (38), avoid O/L Liddell to Tomago (82) on trip of Nil, Feedback
N>>N-RGSW_J | 2008-09-26 | 1 | Out= Regentville to Sydney West (38), avoid O/L Vales Point to Munmorah (23) on trip of Vales Point to Sydney North (22), Feedback
N>>N-RGSW_K | 2008-09-26 | 1 | Out= Regentville to Sydney West (38), avoid O/L Vales Point to Munmorah (23) on trip of Eraring to Vineyard (25), Feedback
N>>N-RGSW_L | 2008-09-26 | 1 | Out= Regentville to Sydney West (38), avoid O/L Vales Point to Munmorah (23) on trip of Bayswater to Sydney West (32), Feedback
N>>N-SNVP_03 | 2008-09-25 | 1 | Out= SydneyNorth-ValesPoint(22), avoid ValesPoint to Munmorah (23) O/L on Eraring-Vinyard(25) trip; Feedback
N>>N-SNVP_04 | 2008-09-25 | 1 | Out= SydneyNorth-ValesPoint(22), avoid ValesPoint to Munmorah (23) O/L on Bayswater-SydneyWest(32) trip; Feedback
N>>N-SSWW_01 | 2008-09-25 | 1 | Out= SydneySouth-Wallerawang(76), avoid Liddell to Tomago (82) O/L on Bayswater-Regentville(31) trip; Feedback
N>>N-SSWW_02 | 2008-09-25 | 1 | Out= SydneySouth-Wallerawang(76), avoid Liddell to Newcastle (81) O/L on Liddell-Tomago(82) trip; Feedback
N>>N-SSWW_03 | 2008-09-25 | 1 | Out= SydneySouth-Wallerawang(76), avoid Dapto to Sydnet South (11) O/L on Wallerawang-Ingleburn(77) trip; Feedback
N>>N-SSWW_04 | 2008-09-25 | 1 | Out= SydneySouth-Wallerawang(76), avoid Liddell to Tomago (82) O/L on Liddell-Newcastle(81) trip; Feedback
N>>N-SSWW_05 | 2008-09-25 | 1 | Out= SydneySouth-Wallerawang(76), avoid Liddell to Newcastle (81) O/L on Bayswater-Regentville(31) trip; Feedback
N>>N-SSWW_17 | 2008-07-01 | 1 | Out= SydneySouth-Wallerawang(76), avoid Marulan to Dapto (8) O/L on Marulan-Avon(16) trip; Feedback
N>>N-SWVY_07 | 2008-09-25 | 1 | Out= SydneyWest-Vineyard(29), avoid ValesPoint to Munmorah (23) O/L on ValesPoint-SydneyNorth(22) trip; Feedback
N>>N-SWYS_A1 | 2008-07-01 | 1 | Out= SydneyWest-Yass(39), avoid Yass to Marulan (4) O/L on Yass-Marulan(5) trip; Feedback
N>>N-SWYS_A2 | 2008-07-01 | 1 | Out= SydneyWest-Yass(39), avoid Marulan to Yass (4) O/L on Marulan-Yass(5) trip; Feedback
N>>N-SWYS_B | 2008-07-01 | 1 | Out= SydneyWest-Yass(39), avoid Marulan to Dapto (8) O/L on Marulan-Avon(16) trip; Feedback
N>>N-SWYS_C | 2008-07-01 | 1 | Out= SydneyWest-Yass(39), avoid MtPiper to Wallerawang (71) O/L on Avon-KempsCreek(37) trip; Feedback
N>>N-SWYS_D | 2008-07-01 | 1 | Out= SydneyWest-Yass(39), avoid MtPiper to Wallerawang (71) O/L on Marulan-Avon(16) trip; Feedback
N>>N-SWYS_E | 2008-07-01 | 1 | Out= SydneyWest-Yass(39), avoid MtPiper to Wallerawang (71) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-SWYS_F | 2008-07-01 | 1 | Out= SydneyWest-Yass(39), avoid MtPiper to Wallerawang (71) O/L on Dapto-SydneySouth(11) trip; Feedback
N>>N-SWYS_G1 | 2008-07-01 | 1 | Out= SydneyWest-Yass(39), avoid Yass to Marulan (4) O/L on Canberra-KangarooValley(6) trip; Feedback
N>>N-SWYS_G2 | 2008-07-01 | 1 | Out= SydneyWest-Yass(39), avoid Marulan to Yass (4) O/L on KangarooValley-Canberra(6) trip; Feedback
N>>N-SWYS_H | 2008-07-01 | 1 | Out= SydneyWest-Yass(39), avoid Yass to Marulan (4) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-SWYS_I | 2008-07-01 | 1 | Out= SydneyWest-Yass(39), avoid MtPiper to Wallerawang (71) O/L on Nil trip; Feedback
N>>N-SWYS_J | 2008-07-01 | 1 | Out= SydneyWest-Yass(39), avoid Marulan to Avon (16) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-UT_A2_1 | 2008-07-01 | 1 | Out= Nil/At_risk, avoid LowerTumut to Canberra (07) O/L (15_min rating) on trip of UpperTumut A2 Bus(=lines 2+64+65); Feedback
N>>N-WWSS+WWIG_1 | 2008-07-03 | 1 | Out= Sydney South to Wallerawang (76) and Ingleburn to Wallerawang (77), avoid O/L Kemps Creek to Sydney South (13) on trip of Dapto to Sydney South (11), Feedback
N>>N-WWSS+WWIG_2 | 2008-07-03 | 1 | Out= Sydney South to Wallerawang (76) and Ingleburn to Wallerawang (77), avoid O/L Kemps Creek to Sydney South (13) on trip of Sydney West to Liverpool (30), Feedback
N>>N-WWSS+WWIG_3 | 2008-07-03 | 1 | Out= Sydney South to Wallerawang (76) and Ingleburn to Wallerawang (77), avoid O/L Wallerawang 330/132kV transformer trip of Wallerawang to Mt Piper (71), Feedback
N>>N-WWSS+WWIG_7 | 2008-07-03 | 1 | Out= Sydney South to Wallerawang (76) and Ingleburn to Wallerawang (77), avoid O/L Wallerawang to Mt Piper (94E) on trip of Wallerawang to Mt Piper (71), Feedback
N>>N-WWSS+WWIG_8 | 2008-07-03 | 1 | Out= Sydney South to Wallerawang (76) and Ingleburn to Wallerawang (77), avoid O/L Liddell to Newcastle (81), on trip of Liddell to Tomago (82), Feedback
N>>N-WWSS+WWIG_9 | 2008-07-03 | 1 | Out= Sydney South to Wallerawang (76) and Ingleburn to Wallerawang (77), avoid O/L Liddell to Tomago (82), on trip of Liddell to Newcastle (81), Feedback
N>>N-WWSS+WWIG_A | 2008-07-03 | 1 | Out= SydSouth-Wwang(76) + Ingleburn-Wwang(77), avoid MtPiper->Marulan(35) OL on Marulan-MtPiper(36) trip; Fb,CoOp
N>>N-WWSS+WWIG_D | 2008-07-03 | 1 | Out= Sydney South to Wallerawang (76) and Ingleburn to Wallerawang (77), avoid O/L Marulan to Avon (16) on trip of Marulan to Dapto (8), Feedback
N>>N-WWSS+WWIG_E | 2008-07-03 | 1 | Out= SydSouth-Wwang(76) + Ingleburn-Wwang(77), avoid Marulan->Dapto(8) OL on Marulan-Avon(16) trip; Fb,CoOp
N>>N-WWSS+WWIG_H | 2008-07-03 | 1 | Out= Sydney South to Wallerawang (76) and Ingleburn to Wallerawang (77), avoid O/L Bayswater to Liddell (34) on trip of Bayswater to Liddell (33), Feedback
N>>N-WWSS+WWIG_N | 2008-07-03 | 1 | Out= Sydney South to Wallerawang (76) and Ingleburn to Wallerawang (77), avoid O/L Marulan to Dapto (8) on trip of Kangaroo Valley to Dapto (18), Feedback
N>>N-WWSS+WWIG_T | 2008-07-03 | 1 | Out= Sydney South to Wallerawang (76) and Ingleburn to Wallerawang (77), avoid O/L Marulan to Dapto (8) on trip of Avon to Dapto (10), Feedback
N>>N-X_4_5_A | 2008-07-03 | 1 | Out= both Marulan-Yass(4+5) lines, avoid Canberra->KangarooV(6) OL on SydWest-Yass(39) trip; Fb,CoOp
N>>N-X_4_5_B | 2008-07-03 | 1 | Out= both Marulan-Yass(4+5) lines, avoid Yass->SydWest(39) OL on Canberra-KangarooV(6) trip; Fb,CoOp
N>>N-X_4_5_C | 2008-07-03 | 1 | Out= both Marulan-Yass(4+5) lines, avoid KangarooV->Canberra(6) OL on SydWest-Yass(39) trip; Fb,CoOp
N>>N-X_4_5_D | 2008-07-03 | 1 | Out= both Marulan-Yass(4+5) lines, avoid SydWest->Yass(39) OL on Canberra-KangarooV(6) trip; Fb,CoOp
N>>N-X_4_5_E | 2008-07-03 | 1 | Out= both Marulan-Yass(4+5) lines, avoid KangarooV->Dapto(18) OL on SydWest-Yass(39) trip; Fb,CoOp
N>>N-X_4_5_F | 2008-07-03 | 1 | Out= both Marulan-Yass(4+5) lines, avoid Yass->SydWest(39) OL on Dapto-KangarooV(18) trip; Fb,CoOp
N>>N-X_4_5_G | 2008-07-03 | 1 | Out= both Marulan-Yass(4+5) lines, avoid Dapto->KangarooV(18) OL on SydWest-Yass(39) trip; Fb,CoOp
N>>N-X_4_5_H | 2008-07-03 | 1 | Out= both Marulan-Yass(4+5) lines, avoid SydWest->Yass(39) OL on Dapto-KangarooV(18) trip; Fb,CoOp
N>>N-X_AVDT_WWIG_A | 2008-11-17 | 1 | Out= Avon-Dapto(10)and Wallerawang-Ingleburn (77), avoid KempsCreek to SydneySouth (13) O/L on SydneyWest-Liverpool(30) trip; Feedback
N>>N-X_AVDT_WWIG_B | 2008-11-17 | 1 | Out= Avon-Dapto(10) and Wallerawang-Ingleburn (77), avoid Marulan to Dapto (8) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-X_AVDT_WWIG_C | 2008-11-17 | 1 | Out= Avon-Dapto(10) and Wallerawang-Ingleburn (77), avoid Marulan to Dapto (8) O/L on KempsCreek-Avon(37) trip; Feedback
N>>N-X_AVDT_WWIG_D | 2008-11-17 | 1 | Out= Avon-Dapto(10) and Wallerawang-Ingleburn (77), avoid Kemps Creek-Sydney South (13) O/L on Wallerawang-Sydney South(76) trip; Feedback
N>>N-X_AVDT_WWIG_E | 2008-11-17 | 1 | Out= Avon-Dapto(10) and Wallerawang-Ingleburn (77), avoid Liddell-Newcastle(81) OL on Liddell-Tomago(82) trip; Feedback
N>>N-X_AVDT_WWIG_F | 2008-11-17 | 1 | Out= Avon-Dapto(10) and Wallerawang-Ingleburn (77), avoid Liddell-Tomago(82) OL on Liddell-Newcastle(81) trip; Feedback
N>>N-X_AVDT_WWIG_G | 2008-11-17 | 1 | Out= Avon-Dapto(10) and Wallerawang-Ingleburn (77), avoid Liddell-Tomago (82) O/L on Bayswater Regentville(31) trip; Feedback
N>>N-X_AVDT_WWIG_H | 2008-11-17 | 1 | Out= Avon-Dapto(10) and Wallerawang-Ingleburn (77), avoid Liddell-Newcastle (81) O/L on Bayswater Regentville(31) trip; Feedback
N>>N-X_AVDT_WWIG_I | 2008-11-17 | 1 | Out= Avon-Dapto(10) and Wallerawang-Ingleburn (77), avoid O/L Kemps Creek Tx on trip of the other; Feedback
N>>N-X_ERNC_ERVP_A | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback
N>>N-X_ERNC_ERVP_B | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24),avoid O/L Eraring to Newcastle (93), on trip of Eraring to Vineyard (25), Feedback
N>>N-X_ERNC_ERVP_C | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid O/L Eraring to Newcastle (93), on trip of Vineyard to Sydney West (29), Feedback
N>>N-X_ERNC_ERVP_D | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid Liddel to Newcastl (81) O/L on loss of Liddell to Tomago (82), Feedback
N>>N-X_ERNC_ERVP_E | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid O/L Eraring to Newcastle (93) on trip of Kemps Creek to Sydney North (14), Feedback
N>>N-X_ERNC_ERVP_F | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid Vales Pt to Munmorah (23) O/L on loss of Sydney North to Vales Pt (22), Feedback
N>>N-X_ERNC_ERVP_G | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid O/L Eraring to Newcastle (93) on trip of Eraring to Kemps Creek (5A1), Feedback
N>>N-X_ERNC_ERVP_H | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid O/L Eraring to Newcastle (93) on trip of Liddell to Newcastle (81), Feedback
N>>N-X_ERNC_ERVP_I | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid O/L Eraring to Newcastle (93) on trip of Kemps Creek to Sydney South (13), Feedback
N>>N-X_ERNC_ERVP_J | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid O/L Eraring to Newcastle (93) on trip of Liddell to Tomago (82), Feedback
N>>N-X_ERNC_ERVP_K | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid O/L Eraring to Newcastle (93), on Nil trip
N>>N-X_ERNC_ERVP_L | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid Liddell to Tomago(82) O/L on Liddell to Newcastle(81) trip; Feedback
N>>N-X_ERNC_ERVP_M | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid Liddell to Newcastle (81) O/L on Nil trip; Feedback
N>>N-X_ERNC_ERVP_N | 2008-09-15 | 1 | Out=Eraring-Newcastle(90)+Eraring-Vales Point(24), avoid Liddell to Tomago (82) O/L on Nil trip; Feedback
N>>N-X_ERNC_SNVP_A | 2008-09-15 | 1 | Out = Eraring-Newcastle (24)+Sydney North-Vales Point (22), avoid O/L Eraring-Newcastle (90) on trip of Eraring-Newcastle(93), Feedback
N>>N-X_ERNC_SNVP_B | 2008-09-15 | 1 | Out = Eraring-Newcastle (24)+Sydney North-Vales Point (22), avoid O/L Eraring-Newcastle (93) on trip of Eraring-Newcastle(90), Feedback
N>>N-X_ERNC_SNVP_C | 2008-09-15 | 1 | Out = Eraring-Newcastle (24)+Sydney North-Vales Point (22), avoid O/L Liddell-Bayswater (33) on trip of Liddell-Bayswater (34),Feedback
N>>N-X_ERNC_SNVP_D | 2008-09-15 | 1 | Out = Eraring-Newcastle (24)+Sydney North-Vales Point (22), avoid O/L Liddell-Bayswater (34) on trip of Liddell-Bayswater(33), Feedback
N>>N-X_ERNC_SNVP_E | 2008-09-15 | 1 | Out = Eraring-Newcastle (24)+Sydney North-Vales Point (22), avoid O/L Vales Point-Munmorah(23)on trip of Eraring-Vinyard(25) trip; Feedback
N>>N-X_ERNC_SNVP_F | 2008-09-15 | 1 | Out = Eraring-Newcastle (24)+Sydney North-Vales Point (22), avoid O/L Kemps Creek Tx on trip of the other; Feedback
N>>N-X_ERVY_MMSW_A | 2009-01-16 | 1 | Out = Eraring-Vineyard (25) + Munmorah-Sydney West (26), avoid O/L Munmorah-Tuggerah(2M) on trip of Vales Point-Sydney North (22), Feedback
N>>N-X_ERVY_MMSW_B | 2009-01-16 | 1 | Out = Eraring-Vineyard (25) + Munmorah-Sydney West (26), avoid O/L Vales Point-Sydney North (22) on trip of Munmorah-Tuggerah(2M) , Feedback
N>>N-X_LDNC_ERTX_1 | 2008-10-20 | 1 | Out= Liddell-Newcastle(81)+ Eraring Tie Tx, avoid Liddell to Tomago (82) O/L on Nil trip; Feedback
N>>N-X_LDNC_ERTX_2 | 2008-10-20 | 1 | Out= Liddell-Newcastle(81)+ Eraring Tie Tx, avoid Liddell to Tomago (82) O/L on Bayswater-Regentville(31) trip; Feedback
N>>N_BWSW_RGSW_N-2_D | 2008-11-18 | 1 | Out=Nil, avoid O/L Liddell to Newcastle (81) on trip of Regentville to sydney West (38) and Basywater to Sydney West (32) lines, Feedback
N>>N_BWSW_RGSW_N-2_F | 2008-11-18 | 1 | Out=Nil, avoid O/L Liddell to Tomago (82) on trip of Regentville to sydney West (38) and Basywater to Sydney West (32) lines, Feedback
N>>N_BWSW_RGSW_N-2_K | 2008-11-18 | 1 | Out=Nil, avoid O/L Mt Piper to Wallerawang (71) on trip of Regentville to Sydney West (38) and Basywater to Sydney West (32) lines, Feedback
N>>N_BWSW_RGSW_N-2_O | 2008-11-18 | 1 | Out=Nil, avoid O/L Vales Point to Munmorah (23) on trip of Regentville to Sydney West(38) and Basywater to Sydney West (32) lines, Feedback
N>>N_ERKC_N-2_3 | 2008-10-13 | 1 | Out= Nil, avoid O/L Vales Point to Munmorah (23) on trip of both Eraring to Kemps Creek (5A1 + 5A2) lines, Feedback
N>>N_MNYS_N-2_1 | 2008-11-07 | 1 | Out=Nil, avoid O/L Canberra to Kangaroo Valley (6) on trip of both Yass to Marulan (4 + 5) lines, Feedback
N>>N_MNYS_N-2_2 | 2008-11-07 | 1 | Out=Nil, avoid O/L Kangaroo Valley to Canberra (6) on trip of both Marulan to Yass (4 + 5) lines, Feedback
N>>N_MNYS_N-2_3 | 2008-07-03 | 1 | Out=Nil, avoid O/L Kangaroo Valley to Dapto (18) on trip of both Yass to Marulan (4 + 5) lines, Feedback
N>>N_MNYS_N-2_4 | 2008-11-07 | 1 | Out=Nil, avoid O/L Sydney West to Yass (39) on trip of both Marulan to Yass (4 + 5) lines, Feedback
N>>N_MNYS_N-2_5 | 2008-11-07 | 1 | Out=Nil, avoid O/L Yass to Sydney West (39) on trip of both Yass to Marulan (4 + 5) lines, Feedback
N>>N_SSWW_IGSS_N-2_1 | 2008-07-03 | 1 | Out=Nil, avoid O/L Marulan to Dapto (8) on trip of Wallerawang to Sydney South (76) and Ingleburn to Sydney South (78) lines, Feedback
N>>N_SSWW_IGWW_N-2_1 | 2008-07-03 | 1 | Out=Nil, avoid O/L Marulan to Dapto (8) on trip of Wallerawang to Sydney South (76) and Wallerawang to Ingleburn (77) lines, Feedback
N>>N_UTYS_AH_15M | 2008-07-01 | 1 | Out= UpperTumut-Yass(2), avoid UpperTumut to LowerTumut(64) O/L (15 min rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N_UTYS_CH_15M | 2008-07-01 | 1 | Out= UpperTumut-Yass(2), avoid UpperTumut to Canberra(01) O/L (15 min rating) on LowerTumut-Canberra(07) trip; Feedback
N>>N_UTYS_DH_15M | 2008-07-01 | 1 | Out= UpperTumut-Yass(2), avoid UpperTumut to Canberra(01) O/L (15 min rating) on LowerTumut-Yass(3) trip; Feedback
N>>N_UTYS_EH_15M | 2008-07-01 | 1 | Out= UpperTumut-Yass(2), avoid LowerTumut to Canberra(07) O/L (15 min rating) on UpperTumut-Canberra(01) trip; Feedback
N>>N_UTYS_FH_15M | 2008-07-01 | 1 | Out= UpperTumut-Yass(2), avoid LowerTumut to Canberra(07) O/L (15 min rating) on LowerTumut-Yass(3) trip; Feedback
N>>N_UTYS_GH | 2008-07-01 | 1 | Out= UpperTumut-Yass(2), avoid Yass to Canberra(9) O/L on Yass-LowerTumut(3) trip; Feedback
N>>Q_LDMU_A | 2008-07-01 | 1 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on Nil trip; FBk
N>>Q_LDMU_B | 2008-07-01 | 1 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL(15 min) on big Qld unit trip; FBk
N>>SNTG_01 | 2008-11-21 | 1 | Out= Tuggerah-SydneyNorth(21), avoid ValesPoint to SydneyNorth (22) O/L on Munmorah-SydneyWest(26) trip; Feedback
N>>V-BUDP_1S | 2008-07-01 | 2 | Out= Buronga-DarlingtonPt(X5), avoid LowerTumut to Murray (66) O/L (15/30_min rating) on UpperTumut-Murray(65) trip; Feedback
N>>V-BUDP_2S | 2008-07-01 | 2 | Out= Buronga-DarlingtonPt(X5), avoid UpperTumut to Murray (65) O/L (15/30_min rating) on LowerTumut-Murray(66) trip; Feedback
N>>V-BURC_1S | 2008-07-01 | 2 | Out= Buronga-RedCliffs(0X1), avoid LowerTumut to Murray (66) O/L on UpperTumut-Murray(65) trip; Feedback
N>>V-BURC_2S | 2008-07-01 | 2 | Out= Buronga-RedCliffs(0X1), avoid UpperTumut to Murray (65) O/L on LowerTumut-Murray(66) trip; Feedback
N>>V-DDMS_A | 2008-07-01 | 1 | Out= one of Dederang-Murray(67 or 68), avoid the other Murray to Dederang (68 or 67) O/L on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback
N>>V-DDWO_C | 2008-07-01 | 2 | Out= Dederang-Wodonga, avoid UpperTumut to Murray (65) O/L (15/30_min rating) on LowerTumut-Murray(66) trip; Feedback
N>>V-DDWO_D | 2008-07-01 | 2 | Out= Dederang-Wodonga, avoid LowerTumut to Murray (66) O/L (15/30_min rating) on UpperTumut-Murray(65) trip; Feedback
N>>V-DPWG_C | 2008-07-01 | 1 | Out= DarlingtonPt-Wagga(63), avoid UpperTumut to Murray (65) O/L on LowerTumut-Murray(66) trip; Feedback
N>>V-DPWG_D | 2008-07-01 | 1 | Out= DarlingtonPt-Wagga(63), avoid LowerTumut to Murray (66) O/L on UpperTumut-Murray(65) trip; Feedback
N>>V-JNWG+X5_C | 2008-07-01 | 2 | Out= Jindera-Wagga(62)+X5+996, avoid UpperTumut to Murray (65) O/L on LowerTumut-Murray(66) trip; Feedback
N>>V-JNWG+X5_D | 2008-07-01 | 2 | Out= Jindera-Wagga(62)+X5+996, avoid LowerTumut to Murray (66) O/L on UpperTumut-Murray(65) trip; Feedback
N>>V-JNWO_A | 2008-07-01 | 1 | Out= Jindera-Wodonga(060), avoid UpperTumut to Murray (65) O/L on LowerTumut-Murray(66) trip; Feedback
N>>V-JNWO_B | 2008-07-01 | 1 | Out= Jindera-Wodonga(060), avoid LowerTumut to Murray (66) O/L on UpperTumut-Murray(65) trip; Feedback
N>>V-LTMS_2 | 2008-07-01 | 1 | Out= LowerTumut-Murray(66), avoid UpperTumut to Murray (65) O/L on Nil trip; Feedback
N>>V-LTMS_5 | 2008-07-01 | 1 | Out= LowerTumut-Murray(66), avoid UpperTumut to Murray (65) O/L(15m rating) on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback
N>>V-LTMS_B | 2008-07-01 | 1 | Out= LowerTumut-Murray(66), avoid UpperTumut to Murray (65) O/L on LowerTumut-Wagga(051) trip; Feedback
N>>V-LTMS_BX | 2008-07-01 | 1 | Out= LowerTumut-Murray(66)+ LowerTumut-UpperTumut(64), avoid UpperTumut to Murray (65) O/L on LowerTumut-Wagga(051) trip; Feedback
N>>V-LTUT_3_30 | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Murray (65) O/L (30_min rating) on LowerTumut-Murray(66) trip; Feedback
N>>V-LTUT_4_30 | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid LowerTumut to Murray (66) O/L (30_min rating) on UpperTumut-Murray(65) trip; Feedback
N>>V-LTUT_C | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Murray (65) O/L on LowerTumut-Murray(66) trip; Feedback
N>>V-LTUT_D | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid LowerTumut to Murray (66) O/L on Murray-UpperTumut(65) trip; Feedback
N>>V-LTUT_E | 2009-01-19 | 1 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Murray (65) O/L on LowerTumut-Wagga(051) + 970,990,99M ex_Yass lines trips; Feedback
N>>V-LTUT_J | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid UpperTumut to Murray (65) O/L on Nil trip; Feedback
N>>V-LTUT_K | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid LowerTumut to Murray (66) O/L on Nil trip; Feedback
N>>V-LTUT_L | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid LowerTumut to Murray (66) O/L on LowerTumut-Wagga(051) trip; Feedback
N>>V-LTWG+LTUT_D | 2008-07-01 | 1 | Out= LowerTumut-Wagga(051)+LowerTumut-UpperTumut(64), avoid LowerTumut to Murray (66) O/L on Murray-UpperTumut(65) trip; Feedback
N>>V-LTWG_D | 2008-07-01 | 1 | Out= LowerTumut-Wagga(051), avoid LowerTumut to Murray (66) O/L on UpperTumut-Murray(65) trip; Feedback
N>>V-LTWG_E | 2008-07-01 | 1 | Out= LowerTumut-Wagga(051), avoid UpperTumut to Murray (65) O/L on LowerTumut-Murray(66) + 970,990,99M trips; Feedback
N>>V-LTWG_F | 2008-07-01 | 1 | Out= LowerTumut-Wagga(051), avoid LowerTumut to Murray (66) O/L on UpperTumut-Murray(65) + 970,990,99M trips; Feedback
N>>V-LTYS+LTUT_A | 2008-07-01 | 1 | Out= LowerTumut-Yass(3)+LowerTumut-UpperTumut(64), avoid UpperTumut to Murray (65) O/L on Canberra-LowerTumut(07) trip; Feedback
N>>V-LTYS_AH | 2008-07-01 | 1 | Out= LowerTumut-Yass(3), avoid UpperTumut to Murray (65) O/L on Canberra-LowerTumut(07) trip; Feedback
N>>V-MSUT_1A | 2008-07-01 | 1 | Out= Murray-UpperTumut(65), avoid LowerTumut to Murray (66) O/L on LowerTumut-Wagga(051) trip; Feedback
N>>V-MSUT_3 | 2008-07-01 | 1 | Out= Murray-UpperTumut(65), avoid LowerTumut to Murray (66) O/L on Nil trip; Feedback
N>>V-MSUT_5 | 2008-07-01 | 1 | Out= Murray-UpperTumut(65), avoid LowerTumut to Murray (66) O/L on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback
N>>V-NIL_3H | 2008-07-01 | 1 | Out= Nil, avoid Upper Tumut to Murray (65) O/L (30 minute rating) on LowerTumut-Murray(66) trip; Feedback
N>>V-NIL_4H | 2008-07-01 | 1 | Out= Nil, avoid Lower Tumut to Murray (66) O/L (30 minute rating) on UpperTumut-Murray(65) trip; Feedback
N>>V-NIL_HC | 2009-09-22 | 1 | Out= Nil, avoid Upper Tumut to Murray (65) O/L on Murray-LowerTumut(66) trip; Feedback
N>>V-NIL_HD | 2009-09-22 | 1 | Out= Nil, avoid Lower Tumut to Murray (66) O/L on Murray-UpperTumut(65) trip; Feedback
N>>V-NIL_HJ | 2009-09-22 | 1 | Out= Nil, avoid Upper Tumut to Murray (65) O/L on NIL trip; Feedback
N>>V-NIL_HK | 2009-09-22 | 1 | Out= Nil, avoid Lower Tumut to Murray (66) O/L on NIL trip; Feedback
N>>V-NIL_N | 2008-07-01 | 1 | Out= Nil, avoid LowerTumut to Murray (66) O/L on LowerTumut-Wagga (051) + 970,990,99M ex_Yass lines trips; Feedback
N>>V-NIL_O | 2009-01-19 | 1 | Out= Nil, avoid UpperTumut to Murray (65) O/L on LowerTumut-Wagga(051) + 970,990,99M ex_Yass lines trips; Feedback
N>>V-UT_A2_A | 2008-07-01 | 1 | Out= Nil/At_risk, avoid LowerTumut to Murray (66) O/L(15_min rating) on trip of UpperTumut A2 Bus(=lines 2+64+65); Feedback
N>>V-X_DDTX+DDSM | 2008-07-02 | 1 | Out= Dederang H2 transformer and one DDTS - SMTS line, avoid O/L DDTS H1 transformer on trip of the remaining DDTS to SMTS line, Feedback
N>>V_BUDP_1A | 2008-07-01 | 2 | Outage = Buronga to Darlington Point (X5) 220kV line, limit Vic interconnectors and generators to avoid overloading Dederang to Murray No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings
N>>V_BUDP_1B | 2008-07-01 | 2 | Outage = Buronga to Darlington Point (X5) 220kV line, limit Vic interconnectors and generators to avoid overloading Dederang to Murray No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings
N>>V_BURC_1A | 2008-07-01 | 2 | Outage = Buronga to Redcliffs (0X1) 220kV line, limit Vic interconnectors and generators to avoid overloading Dederang to Murray No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings
N>>V_BURC_1B | 2008-07-01 | 2 | Outage = Buronga to Redcliffs (0X1) 220kV line, limit Vic interconnectors and generators to avoid overloading Dederang to Murray No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings
N>>V_DBUSS_1 | 2008-07-01 | 1 | Outage=Dederang DBUSS-line control scheme, limit NSW to VIC to avoid overload of a Dederang to Murray 330k line for trip of one of the two lines
N>>V_DBUSS_2 | 2008-07-01 | 1 | Outage = Dederang DBUSS-Transformer control scheme (System Normal and Prior Outage), limit Vic generation and interconnectors to avoid overloading Dederang No.1 330/220kV transformer for loss of Dederang No.2 or No.3 330/220kV transformers
N>>V_DDMS | 2008-07-01 | 1 | Out= one of Murray-Dederang (67 or 68), avoid LowerTumut to Wagga (051) O/L on the remaining Murray-Dederang (68 or 67) trip; Feedback
N>>V_DDWO_1A | 2008-07-01 | 2 | Outage = Dederang to Wodonga 330kV line, limit Vic interconnectors and generators to avoid overload Dederang to Murray No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings
N>>V_DDWO_1B | 2008-07-01 | 2 | Outage = Dederang to Wodonga 330kV line, limit Vic interconnectors and generators to avoid overload Dederang to Murray No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings
N>>V_JNWG_1A | 2008-07-01 | 2 | Outage = Jindera to Wagga 330kV line, limit Vic interconnectors and generators to avoid overload Dederang to Murray No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings
N>>V_JNWG_1B | 2008-07-01 | 2 | Outage = Jindera to Wagga 330kV line, limit Vic interconnectors and generators to avoid overload Dederang to Murray No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings
N>>V_JNWO_1A | 2008-07-03 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic interconnectors and generators to avoid overload Dederang to Murray No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings
N>>V_JNWO_1B | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic interconnectors and generators to avoid overload Dederang to Murray No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings
N>>V_LTMS_1A | 2008-07-01 | 1 | Outage = Lower Tumut - Murray (66) line, limit Vic interconnectors and Vic generation to avoid overloading Dederang to Murray No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings
N>>V_LTMS_1B | 2008-07-01 | 1 | Outage = Lower Tumut - Murray (66) line, limit Vic interconnectors and Vic generation to avoid overloading Dederang to Murray No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings
N>>V_LTWG_1A | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload Dederang to Murray No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings
N>>V_LTWG_1B | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Snowy to Vic interconnector to avoid overload Dederang to Murray No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings
N>>V_MSBT | 2008-07-01 | 1 | Out= MSS Bus tie CB, avoid 051 OL on other MSS Bus tie CB trip
N>>V_MSUT_1A | 2008-07-01 | 1 | Outage = Murray - Upper Tumut (65) line, limit Vic interconnectors and Vic generation to avoid overloading Dederang to Murray No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings
N>>V_MSUT_1B | 2008-07-01 | 1 | Outage = Murray - Upper Tumut (65) line, limit Vic interconnectors and Vic generation to avoid overloading Dederang to Murray No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings
N>>V_SMDD2 | 2008-07-01 | 1 | Outage = Dederang to South Morang 330kV line, limit loading on DDTS H1 330/220 kV transformer for loss of a SMTS-DDTS 330 kV line and DBUSS scheme disarmed, VENCorp TLM pg VI-C/3
N>>V_SMDD3 | 2008-07-01 | 1 | Outage = Dederang to South Morang 330kV line, limit loading on Eildon-Thomastown 220 kV line for loss of a SMTS-DDTS 330 kV line, VENCorp TLM pg VI-C/3
N>>V_SMDD4 | 2008-07-01 | 1 | Outage = Dederang to South Morang 330kV line, limit loading on Shepparton-Fosterville-Bendigo 220 kV line for loss of remaining Dederang to South Morang 330 kV line
N>>V_SMSCP | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit NSW to Vic to avoid overloading Dederang No.1 330/220kV transformer for loss of Dederang No.2 or No.3 330/220kV transformers
N>>V_SMTXF2 | 2009-01-07 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit Vic generators and interconnectors (Vic import) to avoid overload of South Morang H1 transformer for trip of the H2 transformer
N>>V_SMTXH1 | 2009-01-07 | 1 | Outage = South Morang 330/220kV (H1) transformer, limit Vic generators and interconnectors (Vic import) to avoid overload of South Morang H2 transformer for trip of the South Morang 500/330kV (F2) transformer
N>>V_SMTXH1_2 | 2008-07-01 | 1 | Outage = South Morang 330/220kV H1 transformer, limit NSW to Vic to avoid overload of a Dederang 330/220kV transformer for trip of one of the three transformers
N>>V_SMTXH1_3 | 2008-07-01 | 1 | Outage = South Morang 330/220kV H1 transformer, limit NSW to Vic to avoid overload of a Dederang to South Morang 330kV line for trip of one of the two parallel lines, 15 minute ratings
N>>V_SMTXH2 | 2009-01-07 | 1 | Outage = South Morang 330/220kV (H2) transformer, limit Vic generators and interconnectors (Vic import) to avoid overload of South Morang H1 transformer for trip of the South Morang 500/330kV (F2) transformer
N>>V_X_DDTX | 2008-07-01 | 1 | Out=All DD Tx's, avoid DD-SM cont O/L,on other DD-SM trip, VI-84
N>>X_ARCHLS_A | 2008-07-01 | 1 | Out= Armidale - Coffs Harbour (87) and Coffs Harbour - Lismore (89), avoid O/L Armidale to Kempsey (965) on trip of Nil, Feedback
N>>X_ARCHLS_B_DS | 2008-07-01 | 1 | Out= Armidale - Coffs Harbour (87) and Coffs Harbour - Lismore (89), avoid O/L Armidale to Kempsey (965) on trip of Armidale to Coffs Harbour (96C), Feedback
N>>X_ARCHLS_B_PD | 2008-07-01 | 1 | Out= Armidale - Coffs Harbour (87) and Coffs Harbour - Lismore (89), avoid O/L Armidale to Kempsey (965) on trip of 96C, TG Formulation
N>N+NIL_TE_D | 2008-02-22 | 2 | Out= Nil, avoid O/L Lismore to Lismore 132 (9U9) on trip of Lismore to Lismore 132 (9U8), Feedback
N>N-ARCB5122_A | 2007-03-13 | 1 | Out= Armidale 330kV CB(5122), avoid Armidale #3 Tx O/L (2hr rating) on Armidale-Dumaresq(8E) trip; Fb,CoOp
N>N-ARCH_87_B | 2008-07-01 | 1 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Kempsey (965) on trip of Armidale to Coffs Harbour (96C), Feedback
N>N-ARCH_87_TE_C1 | 2009-01-09 | 1 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Koolkhan (966), Feedback, TG formulation in PD/ST
N>N-ARCH_87_TE_C2 | 2007-01-10 | 1 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Koolkhan (966), TG Formulation
N>N-ARCH_DY_1 | 2008-07-01 | 1 | Out= Armidale to Coffs Harbour (96C), avoid O/L Armidale to Kempsey (965) on trip of Armidale to Coffs Harbour (87), Feedback
N>N-ARCH_TE_1 | 2008-10-09 | 1 | Out= Armidale to Coffs Harbour (96C), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (87), Feedback, TG formulation in PD/ST
N>N-ARGI_TE_B1 | 2008-09-29 | 1 | Out= Armidale to Glen Innes (96T), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Feedback, TG formulation in PD/ST
N>N-ARGI_TE_C1 | 2008-11-28 | 1 | Out= Armidale to Glen Innes (96T), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Feedback, TG formulation in PD/ST
N>N-ARKK_C | 2008-12-23 | 2 | Out= Armidale-Koolkhan(966), avoid Armidale->Kempsey(965) OL on Armidale-CoffsHarbour (87) 330kV line trip, Feedback
N>N-ARKK_CH_CB892A | 2008-12-23 | 1 | Out= Armidale to Koolkhan (966) and Coffs Harbour CB 892 opened, avoid O/L Armidale to Coffs Harbour (96C)132kV line, on trip of Armidale to Coffs Harbour (87) 330kV line, Feedback
N>N-ARKK_TE | 2008-12-23 | 1 | Out= Armidale to Koolkhan (966), avoid O/L Armidale to Coffs Harbour (96C)132kV line, on trip of Armidale to Coffs Harbour (87) 330kV line, Feedback
N>N-ARKS_TE_A1 | 2008-12-04 | 1 | Out= Armidale to Kempsey (965), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Feedback, TG formulation in PD/ST
N>N-AR_132BS3_1 | 2008-10-09 | 1 | Out= Armidale No.3 132kV bus, avoid Armidale - Coffs Harbour (96C) O/L on Armidale - Coffs Harbour (87) trip, TG advice
N>N-AR_132BUS1_A | 2008-07-01 | 1 | Out= Armidale No.1 132kV Bus, avoid O/L avoid O/L (2 Hour rating) #6 Armidale 330/132kV Tx on trip of Armidale to Coffs Harbour (87), Feedback
N>N-AR_132BUS5_A | 2008-07-01 | 1 | Out= Armidale No.5 132kV Bus, avoid O/L avoid O/L (2 Hour rating) #3 Armidale 330/132kV Tx on trip of Armidale to Coffs Harbour (87), Feedback
N>N-AR_BS5_A | 2009-01-13 | 2 | Out= Armidale 132kV Bus_Sect_5, avoid Armidale to Koolkhan (966) O/L on Armidale-CoffsHarb(87) trip; Fb, TG formulation in PD/ST
N>N-AR_TX | 2008-09-26 | 1 | Out= Armidale No.3 or No.6 330/132kV Tx, avoid O/L or remaining Armidale 330/132kV Tx on trip of Armidale to Coffs Harbour (87)
N>N-CHKK_TE_1 | 2009-01-13 | 1 | Out= Coffs Harbour to Koolkhan (96H), avoid O/L Armidale to Koolkhan (966) on trip of Coffs Harbour to Lismore (89), TG formulation for PD/ST
N>N-CHLS_TE_A1 | 2009-01-09 | 1 | Out= Coffs Harbour to Lismore (89), avoid O/L Tenterfield to Lismore (96L) on trip of Koolkhan to Lismore (967), Feedback, TG formulation in PD/ST
N>N-CHLS_TE_A2 | 2007-01-10 | 1 | Out= Coffs Harbour to Lismore (89), avoid O/L Tenterfield to Lismore (96L) on trip of Koolkhan to Lismore (967), TG formulation
N>N-CHLS_TE_B1 | 2009-01-09 | 1 | Out= Coffs Harbour to Lismore (89), avoid O/L Armidale to Coffs Harbour (966) on trip of Armidale to Coffs Harbour (87), Feedback, TG formulation in PD/ST
N>N-CHNB_TE_1 | 2008-10-09 | 1 | Out= Coffs Harbour to Nambucca (9W3), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Feedback, TG formulation in PD/ST
N>N-CH_TX_TE_C | 2009-01-13 | 1 | Out= Coffs Harbour 330/132kV transformer, avoid O/L Armidale to Koolkhan (966), on trip of Armidale to Coffs Harbour (87), Feedback
N>N-ERKC_01 | 2008-09-25 | 1 | Out= Eraring-KempsCreek(5A1 or 5A2), avoid Eraring Tie Tx2 O/L on Eraring-KempsCreek (5A2 or 5A1) trip; Feedback
N>N-ERKC_TWO_03 | 2007-05-10 | 1 | Out= both Eraring to Kemps Creek (5A1 + 5A2), avoid O/L Eraring 500/330kV transformer on Nil trip
N>N-ETSOS_TE_E1 | 2006-11-10 | 1 | Out= DirectLink Emergency Trip Scheme, avoid Armidale to CoffsHarbour(96C) O/L on Armidale-CoffsHarbour(87) trip; Fb
N>N-ETSOS_TE_E2 | 2006-11-10 | 1 | Out= DirectLink Emergency Trip Scheme, avoid Armidale to CoffsHarbour(96C) O/L on Armidale-CoffsHarbour(87) trip; TG spec
N>N-EWMB_TE_A | 2008-12-04 | 1 | Out=Ballina-Lennox Head 66kV line (8504), avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other Lismore132 to Dunoon 132kV line (9U7 or 9U6), feedback
N>N-EWMB_TE_B | 2008-12-04 | 1 | Out=Ballina-Lennox Head 66kV line (8504), avoid Mullumbimby to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other Mullumbimby to Dunoon 132kV line (9U7 or 9U6), feedback
N>N-GITN_TE_B1 | 2008-10-09 | 1 | Out= Glen Innes to Tenterfield (96R), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Feedback, TG formulation in PD/ST
N>N-GITN_TE_C1 | 2008-12-11 | 1 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Feedback, TG formulation in PD/ST
N>N-KC_TX_02 | 2008-11-14 | 1 | Out= one of KempsCreek 500/330kV transformers, avoid the remaining transformer O/L (2 Hour rating) on Eraring-Newcastle(93) trip; Feedback
N>N-KKLS_TE_1 | 2009-01-13 | 2 | Out= Koolkhan to Lismore (967), avoid O/L Tenterfield to Lismore (96L) on trip of Coffs Harbour to Lismore (89), Feedback, TG formulation on PD & ST
N>N-KK_CB_4122 | 2009-01-06 | 1 | Out= Koolkhan 132kV bus section 2 (CB4122), avoid Armidale->Coffs Harbour(96C) on Armidale-CoffsHarbour (87) 330kV line trip, Feedback. TG formulation in PD/ST
N>N-KSNB_TE_1 | 2008-12-03 | 1 | Out= Kempsey to Nambucca (9W2) avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Feedback, TG formulation in PD/ST
N>N-LDBB_1 | 2001-02-09 | 1 | Out= Liddell Main Bus; avoid 33/34 OL on trip of unit 3/2
N>N-LDNC_07_15M | 2008-07-01 | 1 | Out= Liddell-Newcastle(81), avoid Eraring to Newcastle (93) O/L (15 min rating) on Liddell-Tomago(82) trip; Feedback
N>N-LDTM_04 | 2008-07-01 | 1 | Out= Liddell-Tomago(82), avoid Eraring to Newcastle (93) O/L on Liddell-Newcastle(81) trip; Feedback
N>N-LDTM_04_15M | 2008-07-01 | 1 | Out= Liddell-Tomago(82), avoid Eraring to Newcastle (93) O/L (15 min rating) on Liddell-Newcastle(81) trip; Feedback
N>N-LSTN_TE_B1 | 2008-10-09 | 1 | Out= Lismore to Tenterfield (96L), avoid O/L Armidale to Coffs Harbour (96C) on trip of Armidale to Coffs Harbour (87), Feedback, TG formulation in PD/ST
N>N-LSTN_TE_C1 | 2008-10-09 | 1 | Out= Lismore to Tenterfield (96L), avoid O/L Koolkhan to Lismore (967), on trip of Coffs Harbour to Lismore (89), Feedback, TG formulation in PD/ST
N>N-LS_TX_TE_A | 2009-02-10 | 1 | Out= Lismore No.1 or No.2 330/132 Transformer, avoid O/L Koolkhan to Lismore (967) on trip of remaining Lismore 330/132kV transformer, Feedback. TG formulation for PD/ST
N>N-NIL_DC | 2009-03-17 | 1 | Out= Nil, avoid Armidale to Tamworth (86) O/L on Armidale-Tamworth(85) trip; Feedback
N>N-NIL_F7_15M | 2009-03-17 | 1 | Out=Nil, avoid O/L (15 min rating) of Armidale to Tamworth (86) on trip of other Armidale to Tamworth (85) line, Feedback
N>N-NIL_LSDU | 2008-12-08 | 1 | Out=nil, Avoid Lismore-Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other Lismore-Dunoon 132kV line (9U7 or 9U6), Feedback
N>N-NIL_MBDU | 2008-12-08 | 1 | Out=Nil, avoid Mullumbimby-Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other Mullumbimby-Dunoon 132kV line (9U7 or 9U6), feedback
N>N-NIL_PAR_987_983 | 2008-11-21 | 1 | Out = nil, limit Tallawara generation to avoid O/L Tallawara to Dapto (983) line on trip of Tallawara to Dapto (987) line
N>N-NIL_TE_C | 2008-07-01 | 1 | Out= Nil, avoid Armidale to Koolkhan (966) O/L on Armidale-CoffsHarbour(87) trip; Feedback
N>N-NIL_TE_D2 | 2008-12-04 | 1 | Out= Nil, avoid Lismore330->Lismore132 (9U9) OL on Lismore330-Lismore132 (9U8) trip
N>N-NIL_TE_E1 | 2009-01-05 | 1 | Out= Nil, avoid Armidale to CoffsHarbour (96C) O/L on Armidale-CoffsHarbour(87) trip; Feedback, TG formulation in PD/ST
N>N-NIL_TE_LOAD | 2008-09-22 | 1 | Out= NIL, limit Directlink flow south to 115MW if Terranora load was greater than or equal to 85MW
N>N-NIL_TLDT | 2008-11-19 | 1 | Out = nil, limit Tallawara generation to avoid O/L Tallawara to Dapto (987) line (only 987 line in service from Tallawara to Datpo)
N>N-NIL__4_15M | 2008-07-01 | 1 | Out= Nil, avoid Muswellbrook to Tamworth (88) O/L on Liddell-Tamworth(84) trip; Feedback
N>N-NIL__7 | 2009-06-01 | 1 | Out= NIL, avoid Tamworth to Armidale (86) O/L on Nil trip; Feedback
N>N_AR_330_BS5_TE | 2009-01-16 | 1 | Out= Armidale No.5 330kV bus, avoid overload of the Armidale to coffs Harbour (96C) for Armidale to Coffs Harbour (87) trip, Feedback
N>N_ERKC_N-2_1 | 2009-01-30 | 1 | Out= Nil, avoid O/L Eraring 500/330kV transformer on trip of both Eraring to Kemps Creek (5A1 + 5A2) lines, Feedback
N>N_ETSOS_TE_C | 2007-05-10 | 1 | Out= Directlink Emergency Trip Scheme at Lismore, avoid O/L Armidale to Koolkhan (966), on trip of Armidale to Coffs Harbour (87), Feedback
N>N_LOTA_7 | 2000-07-13 | 1 | Out=Dapto-Marulan(8)+Avon-Dapto(10);avoid OL 9(Not_WN)on 11 trip
N>N_RBSI | 2007-07-02 | 1 | Out = Redbank to Singleton (955) line, limit Redbank generation to avoid O/L Redbank to Rothbury (953) line
N>N_UR_CB4102_A | 2009-01-05 | 1 | Out=Uranquinty CB 4102, avoid O/L Uranquinty to Finley 99A/1 on trip of Uranquinty to Wagga 9R1
N>N_UR_CB4102_B | 2009-01-05 | 1 | Out=Uranquinty CB 4102, avoid O/L Uranquinty to Yanco 99F on trip of Uranquinty to Wagga 9R2
N>N_X_ARCH87_KSTA_TE | 2008-03-12 | 1 | Out= Armidale to Coffs Harbour (87) 330kV line + one line from Kempsey to Taree (96G or 964), avoid O/L Armidale - Coffs Harbour 132kV (96C) on trip of Armidale - Kempsey (965), Feedback
N>Q-ARCB5122 | 2005-09-12 | 1 | Out= Armidale CB5122, avoid Armidale Tx_3 OL (2Hr rating) on Armidale-Tamworth(85) line trip, Fb
N>Q-ARCB5142 | 2007-05-10 | 1 | Out= Armidale CB5142, avoid Armidale Tx_6 OL (2Hr rating) on Armidale-Dumaresq(8C) line trip, Fb
N>Q-ARTW1A | 2006-03-24 | 1 | Out= Tamworth-Armidale(85), avoid Tamworth->Armidale(86) OL on NIL trip; Fb
N>Q-ARTW1B | 2006-03-24 | 1 | Out= Tamworth-Armidale(85), avoid Tamworth->Armidale(86) OL (15_min) on Qld unit trip; Fb
N>Q-FDNA | 2006-03-21 | 1 | Out= Directlink Flow Direction Signalling Not Available, limit Directlink Qld to NSW flow
N>Q-MUTW_1 | 2006-03-24 | 1 | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on NIL trip; Fb
N>Q-MUTW_2 | 2006-03-24 | 1 | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL (15_min) on Qld unit trip; Fb
N>Q_LS132BB1_RISK | 2007-02-05 | 1 | Out= Nil,but Lismore330 132kV_BB_Sect_1 at risk; avoid Lismore330->Lismore132(9U8) O/L on bus trip
N>Q_LSLS_9U8 | 2008-12-08 | 1 | Out= One of Lismore330-Lismore132 (9U8,9U9,9W1), avoid OL the line remaining on loss of the 2nd
N>X_ARCHLS_TE_C2 | 2008-09-02 | 1 | Out= Armidale - Coffs Harbour (87) and Coffs Harbour - Lismore (89), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Glen Innes (96T), TG Formulation
N>X_CH_TX_ETSOS_TE_C | 2007-05-10 | 1 | Out= Coffs Harbour 330/132kV transformer and Directlink Emergency Trip Scheme at Lismore, avoid O/L Armidale to Koolkhan (966), on trip of Armidale to Coffs Harbour (87), Feedback
NC_N_BLOWERNG | 2008-07-09 | 1 | Non Conformance Constraint for Blowerng Power Station
NC_N_BW01 | 2008-07-09 | 1 | Non Conformance Constraint for Bayswater 1 Power Station
NC_N_BW02 | 2008-07-09 | 1 | Non Conformance Constraint for Bayswater 2 Power Station
NC_N_BW03 | 2008-07-09 | 1 | Non Conformance Constraint for Bayswater 3 Power Station
NC_N_BW04 | 2008-07-09 | 1 | Non Conformance Constraint for Bayswater 4 Power Station
NC_N_ER01 | 2008-07-09 | 1 | Non Conformance Constraint for Eraring ER01 Power Station
NC_N_ER02 | 2008-07-09 | 1 | Non Conformance Constraint for Eraring ER02 Power Station
NC_N_ER03 | 2008-07-09 | 1 | Non Conformance Constraint for Eraring ER03 Power Station
NC_N_ER04 | 2008-07-09 | 1 | Non Conformance Constraint for Eraring ER04 Power Station
NC_N_GUTHEGA | 2008-07-01 | 1 | Non Conformance Constraint for Guthega Power Station
NC_N_HUMENSW | 2008-07-09 | 1 | Non Conformance Constraint for Hume Hydro Power Station
NC_N_HVGTS | 2008-07-09 | 1 | Non Conformance Constraint for Hunter Valley Gas Turbine
NC_N_LD01 | 2008-07-09 | 1 | Non Conformance Constraint for Liddell LD01 Power Station
NC_N_LD02 | 2008-07-09 | 1 | Non Conformance Constraint for Liddell LD02 Power Station
NC_N_LD03 | 2008-07-09 | 1 | Non Conformance Constraint for Liddell LD03 Power Station
NC_N_LD04 | 2008-07-09 | 1 | Non Conformance Constraint for Liddell LD04 Power Station
NC_N_MM3 | 2008-07-09 | 1 | Non Conformance Constraint for Munmorah MM3 Power Station
NC_N_MM4 | 2008-07-09 | 1 | Non Conformance Constraint for Munmorah MM4 Power Station
NC_N_MP1 | 2008-07-09 | 1 | Non Conformance Constraint for Mt Piper 1 Power Station
NC_N_MP2 | 2008-07-09 | 1 | Non Conformance Constraint for Mt Piper 2 Power Station
NC_N_REDBANK1 | 2008-07-09 | 1 | Non Conformance Constraint for Redbank Power Station
NC_N_SHGEN | 2008-07-09 | 1 | Non Conformance Constraint for Shoalhaven Power Station
NC_N_SHPUMP | 2008-07-09 | 1 | Non Conformance Constraint for Shoalhaven Pump
NC_N_SITHE01 | 2008-07-09 | 1 | Non Conformance Constraint for Smithfield Energy Facility
NC_N_SNOWYP | 2008-07-01 | 1 | Non Conformance Constraint for Lower Tumut Pump
NC_N_TALWA1 | 2008-06-25 | 1 | Non Conformance Constraint for Tallawarra Power Station
NC_N_TUMUT3 | 2008-07-01 | 1 | Non Conformance Constraint for Lower Tumut Power Station
NC_N_UPPTUMUT | 2008-07-01 | 1 | Non Conformance Constraint for Upper Tumut Power Station
NC_N_URANQ11 | 2008-11-10 | 1 | Non Conformance Constraint for Uranquinty 1 Power Station
NC_N_URANQ12 | 2008-11-10 | 1 | Non Conformance Constraint for Uranquinty 2 Power Station
NC_N_URANQ13 | 2008-11-10 | 1 | Non Conformance Constraint for Uranquinty 3 Power Station
NC_N_URANQ14 | 2008-11-10 | 1 | Non Conformance Constraint for Uranquinty 4 Power Station
NC_N_VP5 | 2008-07-09 | 1 | Non Conformance Constraint for Vales Point VP5 Power Station
NC_N_VP6 | 2008-07-09 | 1 | Non Conformance Constraint for Vales Point VP6 Power Station
NC_N_WW7 | 2008-07-09 | 1 | Non Conformance Constraint for Wallerawang WW7 Power Station
NC_N_WW8 | 2008-07-09 | 1 | Non Conformance Constraint for Wallerawang WW8 Power Station
NC_Q_BARCALDN | 2008-07-09 | 1 | Non Conformance Constraint for Barcaldine Power Station
NC_Q_BARRON-1 | 2008-07-09 | 1 | Non Conformance Constraint for Barron Gorge 1 Power Station
NC_Q_BARRON-2 | 2008-07-09 | 1 | Non Conformance Constraint for Barron Gorge 2 Power Station
NC_Q_BRAEMAR1 | 2008-07-09 | 1 | Non Conformance Constraint for Braemar 1 Power Station
NC_Q_BRAEMAR2 | 2008-07-09 | 1 | Non Conformance Constraint for Braemar 2 Power Station
NC_Q_BRAEMAR3 | 2008-07-09 | 1 | Non Conformance Constraint for Braemar 3 Power Station
NC_Q_CALL_A_1 | 2008-07-09 | 1 | Non Conformance Constraint for Callide A_1
NC_Q_CALL_A_2 | 2008-07-09 | 1 | Non Conformance Constraint for Callide A_2
NC_Q_CALL_A_3 | 2008-07-09 | 1 | Non Conformance Constraint for Callide A_3
NC_Q_CALL_A_4 | 2008-07-09 | 1 | Non Conformance Constraint for Callide A_4
NC_Q_CALL_B_1 | 2008-07-09 | 1 | Non Conformance Constraint for Callide B_1
NC_Q_CALL_B_2 | 2008-07-09 | 1 | Non Conformance Constraint for Callide B_2
NC_Q_COLNSV_1 | 2008-07-09 | 1 | Non Conformance Constraint for Colinsville 1 Power Station
NC_Q_COLNSV_2 | 2008-07-09 | 1 | Non Conformance Constraint for Colinsville 2 Power Station
NC_Q_COLNSV_3 | 2008-07-09 | 1 | Non Conformance Constraint for Colinsville 3 Power Station
NC_Q_COLNSV_4 | 2008-07-09 | 1 | Non Conformance Constraint for Colinsville 4 Power Station
NC_Q_COLNSV_5 | 2008-07-09 | 1 | Non Conformance Constraint for Colinsville 5 Power Station
NC_Q_CPP_3 | 2008-07-09 | 1 | Non Conformance Constraint for Callide C CPP_3
NC_Q_CPP_4 | 2008-07-09 | 1 | Non Conformance Constraint for Callide C CPP_4
NC_Q_GSTONE1 | 2008-07-09 | 1 | Non Conformance Constraint for Gladstone 1 Power Station
NC_Q_GSTONE2 | 2008-07-09 | 1 | Non Conformance Constraint for Gladstone 2 Power Station
NC_Q_GSTONE3 | 2008-07-09 | 1 | Non Conformance Constraint for Gladstone 3 Power Station
NC_Q_GSTONE4 | 2008-07-09 | 1 | Non Conformance Constraint for Gladstone 4 Power Station
NC_Q_GSTONE5 | 2008-07-09 | 1 | Non Conformance Constraint for Gladstone 5 Power Station
NC_Q_GSTONE6 | 2008-07-09 | 1 | Non Conformance Constraint for Gladstone 6 Power Station
NC_Q_KAREEYA1 | 2008-07-09 | 1 | Non Conformance Constraint for Kareeya 1 Power Station
NC_Q_KAREEYA2 | 2008-07-09 | 1 | Non Conformance Constraint for Kareeya 2 Power Station
NC_Q_KAREEYA3 | 2008-07-09 | 1 | Non Conformance Constraint for Kareeya 3 Power Station
NC_Q_KAREEYA4 | 2008-07-09 | 1 | Non Conformance Constraint for Kareeya 4 Power Station
NC_Q_KPP_1 | 2008-07-09 | 1 | Non Conformance Constraint for Kogan Creek Power Station
NC_Q_MACKAYGT | 2008-07-09 | 1 | Non Conformance Constraint for Mackay Gas Turbine
NC_Q_MPP_1 | 2008-07-09 | 1 | Non Conformance Constraint for Millmerran 1 Power Station
NC_Q_MPP_2 | 2008-07-09 | 1 | Non Conformance Constraint for Millmerran 2 Power Station
NC_Q_MSTUART1 | 2008-07-09 | 1 | Non Conformance Constraint for Mt Stuart 1 Power Station
NC_Q_MSTUART2 | 2008-07-09 | 1 | Non Conformance Constraint for Mt Stuart 2 Power Station
NC_Q_OAKEY1 | 2008-07-09 | 1 | Non Conformance Constraint for Oakey 1 Power Station
NC_Q_OAKEY2 | 2008-07-09 | 1 | Non Conformance Constraint for Oakey 2 Power Station
NC_Q_PUMP1 | 2008-07-09 | 1 | Non Conformance Constraint for Wivenhoe No.1 Pump
NC_Q_PUMP2 | 2008-07-09 | 1 | Non Conformance Constraint for Wivenhoe No.2 Pump
NC_Q_ROMA_7 | 2008-07-09 | 1 | Non Conformance Constraint for Roma 7 Power Station
NC_Q_ROMA_8 | 2008-07-09 | 1 | Non Conformance Constraint for Roma 8 Power Station
NC_Q_STAN-1 | 2008-07-09 | 1 | Non Conformance Constraint for Stanwell STAN-1 Power Station
NC_Q_STAN-2 | 2008-07-09 | 1 | Non Conformance Constraint for Stanwell STAN-2 Power Station
NC_Q_STAN-3 | 2008-07-09 | 1 | Non Conformance Constraint for Stanwell STAN-3 Power Station
NC_Q_STAN-4 | 2008-07-09 | 1 | Non Conformance Constraint for Stanwell STAN-4 Power Station
NC_Q_SWAN_B_1 | 2008-07-09 | 1 | Non Conformance Constraint for Swanbank B1 Power Station
NC_Q_SWAN_B_2 | 2008-07-09 | 1 | Non Conformance Constraint for Swanbank B2 Power Station
NC_Q_SWAN_B_3 | 2008-07-09 | 1 | Non Conformance Constraint for Swanbank B3 Power Station
NC_Q_SWAN_B_4 | 2008-07-09 | 1 | Non Conformance Constraint for Swanbank B4 Power Station
NC_Q_SWAN_E | 2008-07-09 | 1 | Non Conformance Constraint for Swanbank E Power Station
NC_Q_TARONG#1 | 2008-07-09 | 1 | Non Conformance Constraint for Tarong 1 Power Station
NC_Q_TARONG#2 | 2008-07-09 | 1 | Non Conformance Constraint for Tarong 2 Power Station
NC_Q_TARONG#3 | 2008-07-09 | 1 | Non Conformance Constraint for Tarong 3 Power Station
NC_Q_TARONG#4 | 2008-07-09 | 1 | Non Conformance Constraint for Tarong 4 Power Station
NC_Q_TNPS1 | 2008-07-09 | 1 | Non Conformance Constraint for Tarong North Power Station
NC_Q_W/HOE#1 | 2008-07-09 | 1 | Non Conformance Constraint for Wivenhoe No 1 Power Station
NC_Q_W/HOE#2 | 2008-07-09 | 1 | Non Conformance Constraint for Wivenhoe No 2 Power Station
NC_Q_YABULU | 2008-07-09 | 1 | Non Conformance Constraint for Yabulu Power Station
NC_Q_YABULU2 | 2008-07-09 | 1 | Non Conformance Constraint for Yabulu 2 Power Station
NC_S_AGLHAL | 2008-07-09 | 1 | Non Conformance Constraint for AGL Hallet Power Station
NC_S_ANGAS1 | 2008-07-09 | 1 | Non Conformance Constraint for Angaston 1 Power Station
NC_S_ANGAS2 | 2008-07-09 | 1 | Non Conformance Constraint for Angaston 2 Power Station
NC_S_DRYCGT1 | 2008-07-09 | 1 | Non Conformance Constraint for Dry Creek 1 Power Station
NC_S_DRYCGT2 | 2008-07-09 | 1 | Non Conformance Constraint for Dry Creek 2 Power Station
NC_S_DRYCGT3 | 2008-07-09 | 1 | Non Conformance Constraint for Dry Creek 3 Power Station
NC_S_HALLWF1 | 2008-07-09 | 1 | Non Conformance Constraint for Hallet Wind Farm
NC_S_LADBROK1 | 2008-07-09 | 1 | Non Conformance Constraint for Ladbroke Grove 1 Power Station
NC_S_LADBROK2 | 2008-07-09 | 1 | Non Conformance Constraint for Ladbroke Grove 2 Power Station
NC_S_LKBONNY2 | 2008-07-09 | 1 | Non Conformance Constraint for Lake Bonney 2 Windfarm
NC_S_MINTARO | 2008-07-09 | 1 | Non Conformance Constraint for Mintaro Gas Turbine
NC_S_NPS1 | 2008-07-09 | 1 | Non Conformance Constraint for Northern NPS1 Power Station
NC_S_NPS2 | 2008-07-09 | 1 | Non Conformance Constraint for Northern NPS2 Power Station
NC_S_OSB-AG | 2008-07-09 | 1 | Non Conformance Constraint for Osborne Power Station
NC_S_PLAYB-AG | 2008-07-09 | 1 | Non Conformance Constraint for Playford Power Station
NC_S_POR01 | 2008-07-09 | 1 | Non Conformance Constraint for Port Lincoln Power Station
NC_S_PPCCGT | 2008-07-09 | 1 | Non Conformance Constraint for Pelican Point Power Station
NC_S_QPS1 | 2008-07-09 | 1 | Non Conformance Constraint for Quarantine QPS1 Power Station
NC_S_QPS2 | 2008-07-09 | 1 | Non Conformance Constraint for Quarantine QPS2 Power Station
NC_S_QPS3 | 2008-07-09 | 1 | Non Conformance Constraint for Quarantine QPS3 Power Station
NC_S_QPS4 | 2008-07-09 | 1 | Non Conformance Constraint for Quarantine QPS4 Power Station
NC_S_QPS5 | 2008-12-19 | 1 | Non Conformance Constraint for Quarantine QPS5 Power Station
NC_S_SNOWTWN1 | 2008-07-09 | 1 | Non Conformance Constraint for Snowtown Wind Farm
NC_S_SNUG1 | 2008-07-09 | 1 | Non Conformance Constraint for Snuggery 1 Power Station
NC_S_TORRA1 | 2008-07-09 | 1 | Non Conformance Constraint for Torrens A1 Power Station
NC_S_TORRA2 | 2008-07-09 | 1 | Non Conformance Constraint for Torrens A2 Power Station
NC_S_TORRA3 | 2008-07-09 | 1 | Non Conformance Constraint for Torrens A3 Power Station
NC_S_TORRA4 | 2008-07-09 | 1 | Non Conformance Constraint for Torrens A4 Power Station
NC_S_TORRB1 | 2008-07-09 | 1 | Non Conformance Constraint for Torrens B1 Power Station
NC_S_TORRB2 | 2008-07-09 | 1 | Non Conformance Constraint for Torrens B2 Power Station
NC_S_TORRB3 | 2008-07-09 | 1 | Non Conformance Constraint for Torrens B3 Power Station
NC_S_TORRB4 | 2008-07-09 | 1 | Non Conformance Constraint for Torrens B4 Power Station
NC_T_BASTYAN | 2008-07-09 | 1 | Non Conformance Constraint for Bastyan Power Station
NC_T_BBTHREE1 | 2008-07-09 | 1 | Non Conformance Constraint for Bell Bay Three Unit 1 Power Station
NC_T_BBTHREE2 | 2008-07-09 | 1 | Non Conformance Constraint for Bell Bay Three Unit 2 Power Station
NC_T_BBTHREE3 | 2008-07-09 | 1 | Non Conformance Constraint for Bell Bay Three Unit 3 Power Station
NC_T_BELLBAY1 | 2008-07-09 | 1 | Non Conformance Constraint for Bell Bay 1 Power Station
NC_T_BELLBAY2 | 2008-07-09 | 1 | Non Conformance Constraint for Bell Bay 2 Power Station
NC_T_BLNKTAS | 2008-07-09 | 1 | Non Conformance Constraint for Basslink from Tas to Vic
NC_T_CETHANA | 2008-07-09 | 1 | Non Conformance Constraint for Cethana Power Station
NC_T_DEVILS_G | 2008-07-09 | 1 | Non Conformance Constraint for Devils Gate Power Station
NC_T_FISHER | 2008-07-09 | 1 | Non Conformance Constraint for Fisher Power Station
NC_T_GORDON | 2008-07-09 | 1 | Non Conformance Constraint for Gordon Power Station
NC_T_JBUTTERS | 2008-07-09 | 1 | Non Conformance Constraint for John Butters Power Station
NC_T_LEM_WIL | 2008-07-09 | 1 | Non Conformance Constraint for Lemonthyme + Wilmont Power Stations
NC_T_LI_WY_CA | 2008-07-09 | 1 | Non Conformance Constraint for Liapootah + Wayatinah + Catagunya Power Stations
NC_T_LK_ECHO | 2008-07-09 | 1 | Non Conformance Constraint for Lake Echo Power Station
NC_T_MACKNTSH | 2008-07-09 | 1 | Non Conformance Constraint for Mackintosh Power Station
NC_T_MEADOWBK | 2008-07-09 | 1 | Non Conformance Constraint for Meadowbank Power Station
NC_T_POAT110 | 2008-07-09 | 1 | Non Conformance Constraint for Poatina 110kV Power Station
NC_T_POAT220 | 2008-07-09 | 1 | Non Conformance Constraint for Poatina 220kV Power Station
NC_T_REECE1 | 2008-07-09 | 1 | Non Conformance Constraint for Reece 1 Power Station
NC_T_REECE2 | 2008-07-09 | 1 | Non Conformance Constraint for Reece 2 Power Station
NC_T_TARRALEA | 2008-07-09 | 1 | Non Conformance Constraint for Tarraleah Power Station
NC_T_TREVALLN | 2008-07-09 | 1 | Non Conformance Constraint for Trevallyn Power Station
NC_T_TRIBUTE | 2008-07-09 | 1 | Non Conformance Constraint for Tribute Power Station
NC_T_TUNGATIN | 2008-07-09 | 1 | Non Conformance Constraint for Tungatinah Power Station
NC_V_AGLSOM | 2008-07-09 | 1 | Non Conformance Constraint for Somerton Power Station
NC_V_APS | 2008-07-09 | 1 | Non Conformance Constraint for Angelsa Power Station
NC_V_BDL01 | 2008-07-09 | 1 | Non Conformance Constraint for Bairnsdale 1 Power Station
NC_V_BDL02 | 2008-07-09 | 1 | Non Conformance Constraint for Bairnsdale 2 Power Station
NC_V_BLNKVIC | 2008-07-09 | 1 | Non Conformance Constraint for Basslink from Vic to Tas
NC_V_DARTM1 | 2008-07-09 | 1 | Non Conformance Constraint for Dartmouth Power Station
NC_V_EILDON1 | 2008-07-09 | 1 | Non Conformance Constraint for Eildon 1 Power Station
NC_V_EILDON2 | 2008-07-09 | 1 | Non Conformance Constraint for Eildon 2 Power Station
NC_V_HUMEV | 2008-07-09 | 1 | Non Conformance Constraint for Hume Power Station
NC_V_HWPS1 | 2008-07-09 | 1 | Non Conformance Constraint for Hazelwood HWPS 1 Power Station
NC_V_HWPS2 | 2008-07-09 | 1 | Non Conformance Constraint for Hazelwood HWPS 2 Power Station
NC_V_HWPS3 | 2008-07-09 | 1 | Non Conformance Constraint for Hazelwood HWPS 3 Power Station
NC_V_HWPS4 | 2008-07-09 | 1 | Non Conformance Constraint for Hazelwood HWPS 4 Power Station
NC_V_HWPS5 | 2008-07-09 | 1 | Non Conformance Constraint for Hazelwood HWPS 5 Power Station
NC_V_HWPS6 | 2008-07-09 | 1 | Non Conformance Constraint for Hazelwood HWPS 6 Power Station
NC_V_HWPS7 | 2008-07-09 | 1 | Non Conformance Constraint for Hazelwood HWPS 7 Power Station
NC_V_HWPS8 | 2008-07-09 | 1 | Non Conformance Constraint for Hazelwood HWPS 8 Power Station
NC_V_JLA01 | 2008-07-09 | 1 | Non Conformance Constraint for Jeeralang A - 01 Power Station
NC_V_JLA02 | 2008-07-09 | 1 | Non Conformance Constraint for Jeeralang A - 02 Power Station
NC_V_JLA03 | 2008-07-09 | 1 | Non Conformance Constraint for Jeeralang A - 03 Power Station
NC_V_JLA04 | 2008-07-09 | 1 | Non Conformance Constraint for Jeeralang A - 04 Power Station
NC_V_JLB01 | 2008-07-09 | 1 | Non Conformance Constraint for Jeeralang B - 01 Power Station
NC_V_JLB02 | 2008-07-09 | 1 | Non Conformance Constraint for Jeeralang B - 02 Power Station
NC_V_JLB03 | 2008-07-09 | 1 | Non Conformance Constraint for Jeeralang B - 03 Power Station
NC_V_LAVNORTH | 2008-07-09 | 1 | Non Conformance Constraint for Laverton North Power Station
NC_V_LOYYB1 | 2008-07-09 | 1 | Non Conformance Constraint for Loy Yang B1 Power Station
NC_V_LOYYB2 | 2008-07-09 | 1 | Non Conformance Constraint for Loy Yang B2 Power Station
NC_V_LYA1 | 2008-07-09 | 1 | Non Conformance Constraint for Loy Yang A1 Power Station
NC_V_LYA2 | 2008-07-09 | 1 | Non Conformance Constraint for Loy Yang A2 Power Station
NC_V_LYA3 | 2008-07-09 | 1 | Non Conformance Constraint for Loy Yang A3 Power Station
NC_V_LYA4 | 2008-07-09 | 1 | Non Conformance Constraint for Loy Yang A4 Power Station
NC_V_MCKAY1 | 2008-07-09 | 1 | Non Conformance Constraint for Mackay 1 Power Station
NC_V_MCKAY2 | 2008-07-09 | 1 | Non Conformance Constraint for Mackay 2 Power Station
NC_V_MOR1 | 2008-07-09 | 1 | Non Conformance Constraint for MOR1 Energy Brix Power Station
NC_V_MOR2 | 2008-07-09 | 1 | Non Conformance Constraint for MOR2 Energy Brix Power Station
NC_V_MOR3 | 2008-07-09 | 1 | Non Conformance Constraint for MOR3 Energy Brix Power Station
NC_V_MURRAY | 2008-07-01 | 1 | Non Conformance Constraint for Murray Power Station
NC_V_NPS | 2008-07-09 | 1 | Non Conformance Constraint for Newport Power Station
NC_V_VPGS | 2008-07-09 | 1 | Non Conformance Constraint for Valley Power Power Station
NC_V_WKIEWA1 | 2008-07-09 | 1 | Non Conformance Constraint for West Kiewa 1 Power Station
NC_V_WKIEWA2 | 2008-07-09 | 1 | Non Conformance Constraint for West Kiewa 2 Power Station
NC_V_YWPS1 | 2008-07-09 | 1 | Non Conformance Constraint for Yallourn 'W' 1 Power Station
NC_V_YWPS2 | 2008-07-09 | 1 | Non Conformance Constraint for Yallourn 'W' 2 Power Station
NC_V_YWPS3 | 2008-07-09 | 1 | Non Conformance Constraint for Yallourn 'W' 3 Power Station
NC_V_YWPS4 | 2008-07-09 | 1 | Non Conformance Constraint for Yallourn 'W' 4 Power Station
NQS_000 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 0 MW
NQS_0000 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 0 MW
NQS_0025 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 25MW
NQS_0050 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 50 MW
NQS_0075 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 75 MW
NQS_0100 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 100 MW
NQS_0125 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 125 MW
NQS_0150 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 150 MW
NQS_0175 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 175 MW
NQS_0180 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 180 MW
NQS_0200 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 200 MW
NQS_0225 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 225 MW
NQS_0250 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 250 MW
NQS_0275 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 275 MW
NQS_0300 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 300 MW
NQS_0325 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 325 MW
NQS_0350 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 350 MW
NQS_0375 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 375 MW
NQS_0400 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 400 MW
NQS_0425 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 425 MW
NQS_0450 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 450 MW
NQS_0475 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 475 MW
NQS_0500 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 500 MW
NQS_0525 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 525 MW
NQS_0550 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 550 MW
NQS_0575 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 575 MW
NQS_0600 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 600 MW
NQS_0625 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 625 MW
NQS_0650 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 650 MW
NQS_0675 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 675 MW
NQS_0700 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 700 MW
NQS_0725 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 725 MW
NQS_0750 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 750 MW
NQS_0775 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 775 MW
NQS_0800 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 800 MW
NQS_0825 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 825 MW
NQS_0850 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 850 MW
NQS_0875 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 875 MW
NQS_0900 | 2008-08-05 | 1 | NSW to Qld summated QNI + Terranora upper transfer limit of 900 MW
NQTE_-010 | 2008-08-05 | 1 | NSW to Qld on Terranora Interconnector upper transfer limit of -10 MW
NQTE_-020 | 2008-08-05 | 1 | NSW to Qld on Terranora Interconnector upper transfer limit of -20 MW
NQTE_-030 | 2008-08-05 | 1 | NSW to Qld on Terranora Interconnector upper transfer limit of -30 MW
NQTE_000 | 2008-08-05 | 1 | NSW to Qld on Terranora Interconnector upper transfer limit of 0 MW
NQTE_010 | 2008-08-05 | 1 | NSW to Qld on Terranora Interconnector upper transfer limit of 10 MW
NQTE_020 | 2008-08-05 | 1 | NSW to Qld on Terranora Interconnector upper transfer limit of 20 MW
NQTE_030 | 2008-08-05 | 1 | NSW to Qld on Terranora Interconnector upper transfer limit of 30 MW
NQTE_060 | 2008-08-05 | 1 | NSW to Qld on Terranora Interconnector upper transfer limit of 60 MW
NQTE_090 | 2008-08-05 | 1 | NSW to Qld on Terranora Interconnector upper transfer limit of 90 MW
NQTE_120 | 2008-08-05 | 1 | NSW to Qld on Terranora Interconnector upper transfer limit of 120 MW
NQTE_150 | 2008-08-05 | 1 | NSW to Qld on Terranora Interconnector upper transfer limit of 150 MW
NQTE_ROC | 2006-12-27 | 1 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector
NQ_000 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 0 MW
NQ_025 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 25MW
NQ_050 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 50 MW
NQ_075 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 75 MW
NQ_100 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 100 MW
NQ_125 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 125 MW
NQ_150 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 150 MW
NQ_175 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 175 MW
NQ_200 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 200 MW
NQ_225 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 225 MW
NQ_250 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 250 MW
NQ_275 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 275 MW
NQ_300 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 300 MW
NQ_325 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 325 MW
NQ_350 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 350 MW
NQ_375 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 375 MW
NQ_400 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 400 MW
NQ_425 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 425 MW
NQ_450 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 450 MW
NQ_475 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 475 MW
NQ_500 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 500 MW
NQ_525 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 525 MW
NQ_550 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 550 MW
NQ_575 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 575 MW
NQ_600 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 600 MW
NQ_625 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 625 MW
NQ_650 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 650 MW
NQ_675 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 675 MW
NQ_700 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 700 MW
NQ_725 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 725 MW
NQ_750 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 750 MW
NQ_775 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 775 MW
NQ_800 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 800 MW
NQ_825 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 825 MW
NQ_850 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 850 MW
NQ_875 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 875 MW
NQ_900 | 2008-08-05 | 1 | NSW to Qld on QNI upper transfer limit of 900 MW
NQ_VST_ISLE_A | 2008-07-01 | 1 | Separation between Vic and NSW, allow Vic-NSW to supply Wagga or Northern Victoria
NQ_VST_ISLE_B | 2008-07-01 | 1 | Separation between Vic and NSW, allow Vic-NSW to supply Wagga or Northern Victoria
NQ_ZERO | 2005-11-11 | 1 | NSW to Qld on QNI upper transfer limit of zero MW
NR_NQ_100 | 2007-04-23 | 1 | Negative Residue Management: NSW to Qld on QNI greater than or equal to 100MW
NR_NQ_125 | 2007-04-23 | 1 | Negative Residue Management: NSW to Qld on QNI greater than or equal to 125 MW
NR_NQ_150 | 2007-04-23 | 1 | Negative Residue Management: NSW to Qld on QNI greater than or equal to 150 MW
NR_NQ_25 | 2007-04-23 | 1 | Negative Residue Management: NSW to Qld on QNI greater than or equal to 25 MW
NR_NQ_50 | 2007-04-23 | 1 | Negative Residue Management: NSW to Qld on QNI greater than or equal to 50 MW
NR_NQ_75 | 2007-04-23 | 1 | Negative Residue Management: NSW to Qld on QNI greater than or equal to 75 MW
NSA_N_TALWA1_025 | 2009-01-30 | 1 | Tallawarra >=25MW for Network Support Agreement
NSA_N_TALWA1_050 | 2009-01-30 | 1 | Tallawarra >=50MW for Network Support Agreement
NSA_N_TALWA1_075 | 2009-01-30 | 1 | Tallawarra >=75MW for Network Support Agreement
NSA_N_TALWA1_100 | 2009-01-30 | 1 | Tallawarra >=100MW for Network Support Agreement
NSA_N_TALWA1_125 | 2009-01-30 | 1 | Tallawarra >=125MW for Network Support Agreement
NSA_N_TALWA1_150 | 2009-01-30 | 1 | Tallawarra >=150MW for Network Support Agreement
NSA_N_TALWA1_175 | 2009-01-30 | 1 | Tallawarra >=175MW for Network Support Agreement
NSA_N_TALWA1_200 | 2009-01-30 | 1 | Tallawarra >=200MW for Network Support Agreement
NSA_N_TALWA1_225 | 2009-01-30 | 1 | Tallawarra >=225MW for Network Support Agreement
NSA_N_TALWA1_250 | 2009-01-30 | 1 | Tallawarra >=250MW for Network Support Agreement
NSA_N_TALWA1_275 | 2009-01-30 | 1 | Tallawarra >=275MW for Network Support Agreement
NSA_N_TALWA1_300 | 2009-01-30 | 1 | Tallawarra >=300MW for Network Support Agreement
NSA_N_TALWA1_325 | 2009-01-30 | 1 | Tallawarra >=325MW for Network Support Agreement
NSA_N_TALWA1_350 | 2009-01-30 | 1 | Tallawarra >=350MW for Network Support Agreement
NSA_N_TALWA1_375 | 2009-01-30 | 1 | Tallawarra >=375MW for Network Support Agreement
NSA_N_TALWA1_400 | 2009-01-30 | 1 | Tallawarra >=400MW for Network Support Agreement
NSA_N_TALWA1_425 | 2009-01-30 | 1 | Tallawarra >=425MW for Network Support Agreement
NSA_N_TALWA1_435 | 2009-01-30 | 1 | Tallawarra >= 435MW for Network Support Agreement
NSA_Q_COLNSV_010 | 2008-02-15 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 10 MW
NSA_Q_COLNSV_015 | 2008-02-15 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 15 MW
NSA_Q_COLNSV_020 | 2008-02-15 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 20 MW
NSA_Q_COLNSV_025 | 2008-02-15 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 25 MW
NSA_Q_COLNSV_030 | 2008-02-15 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 30 MW
NSA_Q_COLNSV_035 | 2008-02-15 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 35 MW
NSA_Q_COLNSV_040 | 2008-02-15 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 40 MW
NSA_Q_COLNSV_045 | 2008-02-15 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 45 MW
NSA_Q_COLNSV_050 | 2008-01-04 | 2 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 50 MW
NSA_Q_COLNSV_055 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 55 MW
NSA_Q_COLNSV_060 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 60 MW
NSA_Q_COLNSV_065 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 65 MW
NSA_Q_COLNSV_070 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 70 MW
NSA_Q_COLNSV_075 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 75 MW
NSA_Q_COLNSV_080 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 80 MW
NSA_Q_COLNSV_085 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 85 MW
NSA_Q_COLNSV_090 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 90 MW
NSA_Q_COLNSV_095 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 95 MW
NSA_Q_COLNSV_100 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 100 MW
NSA_Q_COLNSV_105 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 105 MW
NSA_Q_COLNSV_110 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 110 MW
NSA_Q_COLNSV_115 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 115 MW
NSA_Q_COLNSV_120 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 120 MW
NSA_Q_COLNSV_125 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 125 MW
NSA_Q_COLNSV_130 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 130 MW
NSA_Q_COLNSV_135 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 135 MW
NSA_Q_COLNSV_140 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 140 MW
NSA_Q_COLNSV_145 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 145 MW
NSA_Q_COLNSV_150 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 150 MW
NSA_Q_COLNSV_155 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 155 MW
NSA_Q_COLNSV_160 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 160 MW
NSA_Q_COLNSV_165 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 165 MW
NSA_Q_COLNSV_170 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 170 MW
NSA_Q_COLNSV_175 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 175 MW
NSA_Q_COLNSV_180 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 180 MW
NSA_Q_COLNSV_185 | 2006-05-02 | 1 | Network Support Agreement (Powerlink) for Central - North limit control - Collinsville Generation >= 185 MW
NSA_Q_GSTONE34_200 | 2006-07-10 | 1 | Gladstone 3+4 >= 200 for Network Support Agreement
NSA_Q_GSTONE34_220 | 2006-10-02 | 1 | Gladstone 3+4 >= 220 for Network Support Agreement
NSA_Q_GSTONE34_250 | 2006-06-21 | 1 | Gladstone 3 + 4 >= 250 for Network Support Agreement
NSA_Q_GSTONE34_270 | 2006-06-21 | 1 | Gladstone 3 + 4 >= 270 for Network Support Agreement
NSA_Q_GSTONE34_290 | 2006-06-21 | 1 | Gladstone 3 + 4 >= 290 for Network Support Agreement
NSA_Q_GSTONE34_310 | 2006-06-21 | 1 | Gladstone 3 + 4 >= 310 for Network Support Agreement
NSA_Q_GSTONE34_330 | 2006-06-21 | 1 | Gladstone 3 + 4 >= 330 for Network Support Agreement
NSA_Q_GSTONE34_350 | 2006-06-21 | 1 | Gladstone 3 + 4 >= 350 for Network Support Agreement
NSA_Q_GSTONE34_370 | 2006-06-21 | 1 | Gladstone 3 + 4 >= 370 for Network Support Agreement
NSA_Q_GSTONE34_390 | 2006-06-21 | 1 | Gladstone 3 + 4 >= 390 for Network Support Agreement
NSA_Q_GSTONE34_410 | 2006-06-21 | 1 | Gladstone 3 + 4 >= 410 for Network Support Agreement
NSA_Q_GSTONE34_430 | 2006-06-21 | 1 | Gladstone 3 + 4 >= 430 for Network Support Agreement
NSA_Q_GSTONE34_450 | 2006-06-21 | 1 | Gladstone 3 + 4 >= 450 for Network Support Agreement
NSA_Q_GSTONE34_500 | 2006-06-21 | 1 | Gladstone 3 + 4 >= 500 for Network Support Agreement
NSA_Q_GSTONE_1000 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=1000MW
NSA_Q_GSTONE_1050 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=1050MW
NSA_Q_GSTONE_1100 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=1100MW
NSA_Q_GSTONE_1150 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=1150MW
NSA_Q_GSTONE_1200 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=1200MW
NSA_Q_GSTONE_1250 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=1250MW
NSA_Q_GSTONE_600 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=600MW
NSA_Q_GSTONE_650 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=650MW
NSA_Q_GSTONE_700 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=700MW
NSA_Q_GSTONE_750 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=750MW
NSA_Q_GSTONE_800 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=800MW
NSA_Q_GSTONE_850 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=850MW
NSA_Q_GSTONE_900 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=900MW
NSA_Q_GSTONE_950 | 2006-05-25 | 1 | Discretionary Network Support Gladstone Gen>=950MW
NSA_Q_MSTUART1_100 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 100 MW
NSA_Q_MSTUART1_105 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 105 MW
NSA_Q_MSTUART1_110 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 110 MW
NSA_Q_MSTUART1_115 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 115 MW
NSA_Q_MSTUART1_120 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 120 MW
NSA_Q_MSTUART1_125 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 125 MW
NSA_Q_MSTUART1_130 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 130 MW
NSA_Q_MSTUART1_135 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 135 MW
NSA_Q_MSTUART1_140 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 140 MW
NSA_Q_MSTUART1_45 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 45 MW
NSA_Q_MSTUART1_50 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 50 MW
NSA_Q_MSTUART1_55 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 55 MW
NSA_Q_MSTUART1_60 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 60 MW
NSA_Q_MSTUART1_65 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 65 MW
NSA_Q_MSTUART1_70 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 70 MW
NSA_Q_MSTUART1_75 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 75 MW
NSA_Q_MSTUART1_80 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 80 MW
NSA_Q_MSTUART1_85 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 85 MW
NSA_Q_MSTUART1_90 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 90 MW
NSA_Q_MSTUART1_95 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart1 >= 95 MW
NSA_Q_MSTUART2_100 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 100 MW
NSA_Q_MSTUART2_105 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 105 MW
NSA_Q_MSTUART2_110 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >=110 MW
NSA_Q_MSTUART2_115 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 115 MW
NSA_Q_MSTUART2_120 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 120 MW
NSA_Q_MSTUART2_125 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 125 MW
NSA_Q_MSTUART2_130 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 130 MW
NSA_Q_MSTUART2_135 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 135 MW
NSA_Q_MSTUART2_140 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 140 MW
NSA_Q_MSTUART2_45 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 45 MW
NSA_Q_MSTUART2_50 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 50 MW
NSA_Q_MSTUART2_55 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 55 MW
NSA_Q_MSTUART2_60 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 60 MW
NSA_Q_MSTUART2_65 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 65 MW
NSA_Q_MSTUART2_70 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 70 MW
NSA_Q_MSTUART2_75 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 75 MW
NSA_Q_MSTUART2_80 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 80 MW
NSA_Q_MSTUART2_85 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 85 MW
NSA_Q_MSTUART2_90 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 90 MW
NSA_Q_MSTUART2_95 | 2007-03-19 | 1 | Network Support Agreement for Mt Stuart2 >= 95 MW
NSA_S_MINTARO_30 | 2006-06-21 | 1 | Mintaro >= 30 MW for Network Support Agreement
NSA_S_MINTARO_35 | 2006-06-21 | 1 | Mintaro >= 35 MW for Network Support Agreement
NSA_S_MINTARO_40 | 2006-06-21 | 1 | Mintaro >= 40 MW for Network Support Agreement
NSA_S_MINTARO_45 | 2006-06-21 | 1 | Mintaro >= 45 MW for Network Support Agreement
NSA_S_MINTARO_50 | 2006-06-21 | 1 | Mintaro >= 50 MW for Network Support Agreement
NSA_S_MINTARO_55 | 2006-06-21 | 1 | Mintaro >= 55 MW for Network Support Agreement
NSA_S_MINTARO_60 | 2006-06-21 | 1 | Mintaro >= 60 MW for Network Support Agreement
NSA_S_MINTARO_65 | 2006-06-21 | 1 | Mintaro >= 65 MW for Network Support Agreement
NSA_S_MINTARO_70 | 2006-06-21 | 1 | Mintaro >= 70 MW for Network Support Agreement
NSA_S_MINTARO_75 | 2006-06-21 | 1 | Mintaro >= 75 MW for Network Support Agreement
NSA_S_MINTARO_80 | 2006-06-21 | 1 | Mintaro >= 80 MW for Network Support Agreement
NSA_S_MINTARO_85 | 2006-06-21 | 1 | Mintaro >= 85 MW for Network Support Agreement
NSA_S_POR01_05 | 2006-06-21 | 1 | Port Lincoln >= 5 MW for Network Support Agreement
NSA_S_POR01_10 | 2006-06-21 | 1 | Port Lincoln >= 10 MW for Network Support Agreement
NSA_S_POR01_15 | 2006-06-21 | 1 | Port Lincoln >= 15 MW for Network Support Agreement
NSA_S_POR01_20 | 2006-06-21 | 1 | Port Lincoln >= 20 MW for Network Support Agreement
NSA_S_POR01_25 | 2006-06-21 | 1 | Port Lincoln >= 25 MW for Network Support Agreement
NSA_S_POR01_30 | 2006-06-21 | 1 | Port Lincoln >= 30 MW for Network Support Agreement
NSA_S_POR01_35 | 2006-06-21 | 1 | Port Lincoln >= 35 MW for Network Support Agreement
NSA_S_POR01_40 | 2006-06-21 | 1 | Port Lincoln >= 40 MW for Network Support Agreement
NSA_S_POR01_45 | 2006-06-21 | 1 | Port Lincoln >= 45 MW for Network Support Agreement
NSA_S_SNUG1_05 | 2006-06-21 | 1 | Snuggery >= 5 MW for Network Support Agreement
NSA_S_SNUG1_10 | 2006-06-21 | 1 | Snuggery >= 10 MW for Network Support Agreement
NSA_S_SNUG1_15 | 2006-06-21 | 1 | Snuggery >= 15 MW for Network Support Agreement
NSA_S_SNUG1_20 | 2006-06-21 | 1 | Snuggery >= 20 MW for Network Support Agreement
NSA_S_SNUG1_25 | 2006-06-21 | 1 | Snuggery >= 25 MW for Network Support Agreement
NSA_S_SNUG1_30 | 2006-06-21 | 1 | Snuggery >= 30 MW for Network Support Agreement
NSA_S_SNUG1_35 | 2006-06-21 | 1 | Snuggery >= 35 MW for Network Support Agreement
NSA_S_SNUG1_40 | 2006-06-21 | 1 | Snuggery >= 40 MW for Network Support Agreement
NSA_S_SNUG1_45 | 2006-06-21 | 1 | Snuggery >= 45 MW for Network Support Agreement
NSA_S_SNUG1_50 | 2006-06-21 | 1 | Snuggery >= 50 MW for Network Support Agreement
NSA_S_SNUG1_55 | 2006-06-21 | 1 | Snuggery >= 55 MW for Network Support Agreement
NSA_S_SNUG1_60 | 2006-06-21 | 1 | Snuggery >= 60 MW for Network Support Agreement
NSA_T>T_NIL_220_7A | 2008-05-01 | 1 | Outage = Nil, Basslink in service, avoid overloading the Liapootah to Cluny Tee 220kV line (flow to South) for loss of Liapootah to Chapel Street 220kV line, feedback equation, swamp if Tas South demand <=547MW when NSA is effective
NSA_T>T_NIL_220_8A | 2008-05-01 | 1 | Outage = Nil, Basslink in service, avoid overloading the Liapootah to Chapel Street 220kV line (flow to South) for loss of Cluny to Chapel Street 220kV line, feedback equation, swamp if Tas South demand <=547MW when NSA is effective
NSA_T>T_NIL_220_9A | 2008-05-01 | 1 | Outage = Nil, Basslink in service, avoid overloading the Cluny Tee to Chapel Street 220kV line (flow to South) for loss of Liapootah to Chapel Street 220kV line, feedback equation, swamp if Tas South demand <=547MW when NSA is effective
NSA_T^T_NIL_5_DS | 2008-05-09 | 1 | Outage = Nil, avoid voltage instability or violations for loss of a Liapootah to Cluny Tee to Chapel St 220 kV line, dispatch equation only, swamp if Tas South demand <=547MW when NSA is effective
NSA_T_GORDON_050 | 2007-07-31 | 1 | Gordon generation >= 50 MW for Network Support Agreement
NSA_T_GORDON_060 | 2007-07-31 | 1 | Gordon generation >= 60 MW for Network Support Agreement
NSA_T_GORDON_070 | 2006-05-10 | 1 | Gordon generation >= 70 MW for Network Support Agreement
NSA_T_GORDON_080 | 2006-05-10 | 1 | Gordon generation >= 80 MW for Network Support Agreement
NSA_T_GORDON_090 | 2006-05-10 | 1 | Gordon generation >= 90 MW for Network Support Agreement
NSA_T_GORDON_100 | 2006-05-10 | 1 | Gordon generation >= 100 MW for Network Support Agreement
NSA_T_GORDON_110 | 2006-05-10 | 1 | Gordon generation >= 110 MW for Network Support Agreement
NSA_T_GORDON_120 | 2006-05-10 | 1 | Gordon generation >= 120 MW for Network Support Agreement
NSA_T_GORDON_130 | 2006-05-10 | 1 | Gordon generation >= 130 MW for Network Support Agreement
NSA_T_GORDON_140 | 2006-05-10 | 1 | Gordon generation >= 140 MW for Network Support Agreement
NSA_T_GORDON_150 | 2006-05-10 | 1 | Gordon generation >= 150 MW for Network Support Agreement
NSA_T_GORDON_160 | 2006-05-10 | 1 | Gordon generation >= 160 MW for Network Support Agreement
NSA_T_GORDON_170 | 2006-05-10 | 1 | Gordon generation >= 170 MW for Network Support Agreement
NSA_T_GORDON_180 | 2006-05-10 | 1 | Gordon generation >= 180 MW for Network Support Agreement
NSA_T_GORDON_190 | 2006-05-10 | 1 | Gordon generation >= 190 MW for Network Support Agreement
NSA_T_GORDON_200 | 2006-05-10 | 1 | Gordon generation >= 200 MW for Network Support Agreement
NSA_T_GORDON_210 | 2006-05-10 | 1 | Gordon generation >= 210 MW for Network Support Agreement
NSA_T_GORDON_220 | 2006-05-10 | 1 | Gordon generation >= 220 MW for Network Support Agreement
NSA_T_GORDON_230 | 2006-05-10 | 1 | Gordon generation >= 230 MW for Network Support Agreement
NSA_T_GORDON_240 | 2006-05-10 | 1 | Gordon generation >= 240 MW for Network Support Agreement
NSA_T_GORDON_250 | 2006-05-10 | 1 | Gordon generation >= 250 MW for Network Support Agreement
NSA_T_GORDON_260 | 2006-05-10 | 1 | Gordon generation >= 260 MW for Network Support Agreement
NSA_T_GORDON_270 | 2006-05-10 | 1 | Gordon generation >= 270 MW for Network Support Agreement
NSA_T_GORDON_280 | 2006-05-10 | 1 | Gordon generation >= 280 MW for Network Support Agreement
NSA_T_GORDON_290 | 2006-05-10 | 1 | Gordon generation >= 290 MW for Network Support Agreement
NSA_T_GORDON_300 | 2006-05-10 | 1 | Gordon generation >= 200 MW for Network Support Agreement
NSA_T_GORDON_310 | 2006-05-10 | 1 | Gordon generation >= 310 MW for Network Support Agreement
NSA_T_GORDON_320 | 2006-05-10 | 1 | Gordon generation >= 320 MW for Network Support Agreement
NSA_T_GORDON_330 | 2006-05-10 | 1 | Gordon generation >= 330 MW for Network Support Agreement
NSA_T_GORDON_340 | 2006-05-10 | 1 | Gordon generation >= 340 MW for Network Support Agreement
NSA_T_GORDON_350 | 2006-05-10 | 1 | Gordon generation >= 350 MW for Network Support Agreement
NSA_T_GORDON_360 | 2006-05-10 | 1 | Gordon generation >= 360 MW for Network Support Agreement
NSA_T_GORDON_370 | 2006-05-10 | 1 | Gordon generation >= 370 MW for Network Support Agreement
NSA_T_GORDON_380 | 2006-05-10 | 1 | Gordon generation >= 380 MW for Network Support Agreement
NSA_T_GORDON_390 | 2006-05-10 | 1 | Gordon generation >= 390 MW for Network Support Agreement
NSA_T_GORDON_400 | 2006-05-10 | 1 | Gordon generation >= 400 MW for Network Support Agreement
NSA_V_BDL01_20 | 2006-06-21 | 1 | Bairnsdale Unit 1 >= 20 MW for Network Support Agreement
NSA_V_BDL01_30 | 2006-06-21 | 1 | Bairnsdale Unit 1 >= 30 MW for Network Support Agreement
NSA_V_BDL01_35 | 2006-06-21 | 1 | Bairnsdale Unit 1 >= 35MW for Network Support Agreement
NSA_V_BDL01_40 | 2006-06-21 | 1 | Bairnsdale Unit 1 >= 40 MW for Network Support Agreement
NSA_V_BDL01_45 | 2006-08-15 | 1 | Bairnsdale Unit 1 >= 45 MW for Network Support Agreement
NSA_V_BDL02_20 | 2006-06-21 | 1 | Bairnsdale Unit 2 >= 20 MW for Network Support Agreement
NSA_V_BDL02_30 | 2006-06-21 | 1 | Bairnsdale Unit 2 >= 30 MW for Network Support Agreement
NSA_V_BDL02_35 | 2006-06-21 | 1 | Bairnsdale Unit 2 >= 35 MW for Network Support Agreement
NSA_V_BDL02_40 | 2006-06-21 | 1 | Bairnsdale Unit 2 >= 40 MW for Network Support Agreement
NSA_V_BDL02_45 | 2006-08-15 | 1 | Bairnsdale Unit 2 >= 45 MW for Network Support Agreement
NSA_V_BDL_20 | 2006-06-21 | 1 | Bairnsdale Unit 1 and Unit 2 >= 20 MW for Network Support Agreement
NSA_V_BDL_25 | 2007-03-09 | 1 | Bairnsdale Unit 1 and Unit 2 >= 25 MW for Network Support Agreement
NSA_V_BDL_30 | 2006-06-21 | 1 | Bairnsdale Unit 1 and Unit 2 >= 30 MW for Network Support Agreement
NSA_V_BDL_35 | 2006-06-21 | 1 | Bairnsdale Unit 1 and Unit 2 >= 35 MW for Network Support Agreement
NSA_V_BDL_40 | 2006-06-21 | 1 | Bairnsdale Unit 1 and Unit 2 >= 40 MW for Network Support Agreement
NSA_V_BDL_45 | 2006-08-15 | 1 | Bairnsdale Unit 1 and Unit 2 >= 45 MW for Network Support Agreement
NV_0000 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 0 MW
NV_0050 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 50 MW
NV_0100 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 100 MW
NV_0150 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 150 MW
NV_0200 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 200 MW
NV_0250 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 250 MW
NV_0300 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 300 MW
NV_0350 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 350 MW
NV_0400 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 400 MW
NV_0450 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 450 MW
NV_0500 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 500 MW
NV_0550 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 550 MW
NV_0600 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 600 MW
NV_0650 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 650 MW
NV_0700 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 700 MW
NV_0750 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 750 MW
NV_0800 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 800 MW
NV_0850 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 850 MW
NV_0900 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 900 MW
NV_0950 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 950 MW
NV_1000 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 1000 MW
NV_1050 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 1050 MW
NV_1100 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 1100 MW
NV_1150 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 1150 MW
NV_1200 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer upper limit of 1200 MW
NV_1300 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 1300 MW
NV_1400 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 1400 MW
NV_1500 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 1500 MW
NV_1550 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 1550 MW
NV_1600 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 1600 MW
NV_1650 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 1650 MW
NV_1700 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 1700 MW
NV_1750 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 1750 MW
NV_1800 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 1800 MW
NV_1900 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 1900 MW
NV_2000 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 2000 MW
NV_2100 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 2100 MW
NV_2200 | 2008-07-01 | 1 | Discretionary NSW to Vic transfer limit of 2200 MW
NV_ZERO | 2009-02-05 | 1 | NSW to VIC upper transfer limit of zero MW
N^QAR_1CPA | 2003-10-02 | 1 | Outage= Armidale 80 Mvar Cap Bank, avoid Voltage Collapse on loss of Liddell to Muswellbrook 330kV line
N^QAR_2CPA | 2003-10-02 | 1 | Outage= Armidale 120 Mvar Cap Bank, avoid Voltage Collapse on loss of Liddell to Muswellbrook 330kV line
N^Q_ARDM_B | 2008-01-03 | 1 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of the largest of Tarong, Stanwell, Callide B or Swanbank E generators
N^Q_ARTW_1 | 2006-03-24 | 1 | Out = Armidale to Tamworth (85 or 86), avoid Voltage collapse on loss of largest Qld unit
N^Q_AR_330_BS1_1 | 2007-11-26 | 1 | Out= Armidale No.1 330kV bus, NSW to Qld voltage stability limit for trip of the largest Qld generator
N^Q_AR_330_BS5_1 | 2007-09-14 | 1 | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of the largest Qld generator
N^Q_AR_VCA | 2003-10-02 | 1 | Outage= Armidale SVC, avoid Voltage Collapse on loss of Liddell to Muswellbrook 330kV line
N^Q_AR_VCB | 2008-01-03 | 1 | Out= Armidale SVC, avoid Voltage Collapse on loss of the largest of Tarong, Stanwell, Callide B or Swanbank E generators
N^Q_BCDM_B | 2008-01-03 | 1 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of the largest of Tarong, Stanwell, Callide B or Swanbank E generators
N^Q_BM_VCA | 2003-10-02 | 1 | Outage= Braemar SVC, avoid Voltage Collapse on loss of Liddell to Muswellbrook 330kV line
N^Q_BM_VCB | 2007-05-11 | 1 | Out= Braemar SVC, avoid Voltage Collapse on loss of largest Qld Generator
N^Q_LDMU_1 | 2006-03-24 | 1 | Out = Liddell to Muswellbrook (83), avoid Voltage collapse on loss of largest Qld unit
N^Q_LDTW_1 | 2006-03-24 | 1 | Out = Liddell to Tamworth (84), avoid Voltage vollapse on loss of largest Qld generator
N^Q_LS_VCA | 2003-10-02 | 1 | Outage= Lismore SVC, avoid Voltage Collapse on loss of Liddell to Muswellbrook 330kV line
N^Q_LS_VCB | 2008-01-03 | 1 | Out= Lismore SVC, avoid Voltage Collapse on loss of the largest of Tarong, Stanwell, Callide B or Swanbank E generators
N^Q_MIMR_B | 2008-12-09 | 1 | Out= Millmerran-Middle Ridge (9907,9908 or H14 Tx) line, avoid Voltage Collapse on loss of the largest of Tarong, Stanwell, Callide B or Swanbank E generators
N^Q_MUTW_1 | 2006-03-24 | 1 | Out = Muswellbrook to Tamworth (88), avoid Voltage vollapse on loss of largest Qld unit
N^Q_MU_CPA | 2003-10-02 | 1 | Outage= Muswellbrook 120 Mvar Cap Bank, avoid Voltage Collapse on loss of Liddell to Muswellbrook 330kV line
N^Q_NIL_A | 2005-07-15 | 1 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line
N^Q_NIL_B | 2007-12-28 | 1 | Out= Nil, avoid Voltage Collapse on loss of the largest of Tarong, Stanwell, Callide B or Swanbank E generators
N^Q_TW_330_BUS1_1 | 2008-05-21 | 1 | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of the largest Qld generator
N^Q_TW_330_BUS3_1 | 2008-06-26 | 1 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of the largest Qld generator
N^Q_TW_CPA | 2005-03-02 | 1 | Out = Tamworth 120 Mvar Cap Bank, avoid Voltage Collapse on loss of Liddell to Muswellbrook line
N^^N_CN_CAP1 | 2008-07-01 | 1 | Out= Canberra No.1 or No.2 132kV Cap Bank (80MVar), Snowy to NSW voltage stability limit
N^^N_CN_CAP3 | 2008-07-01 | 1 | Out= Canberra No.3 132kV Cap Bank (120MVar), Snowy to NSW voltage stability limit
N^^N_NIL_1 | 2009-06-17 | 1 | Out= Nil, northerly flow on line 01,2,3 and 07 cut-set voltage stability limit, Feedback
N^^Q_ARDM_B1 | 2008-01-03 | 1 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek
N^^Q_ARDM_B2 | 2008-01-03 | 1 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Millmerran 1
N^^Q_ARDM_B3 | 2008-01-03 | 1 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Millmerran 2
N^^Q_ARDM_B4 | 2008-01-03 | 1 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Tarong North
N^^Q_ARDM_B5 | 2008-01-03 | 2 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Callide C3
N^^Q_ARDM_B6 | 2008-01-03 | 2 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Callide C4
N^^Q_AR_VC_B1 | 2008-01-03 | 1 | Out= Armidale SVC, avoid Voltage Collapse on loss of Kogan Creek
N^^Q_AR_VC_B2 | 2008-01-03 | 1 | Out= Armidale SVC, avoid Voltage Collapse on loss of Millmerran 1
N^^Q_AR_VC_B3 | 2008-01-03 | 1 | Out= Armidale SVC, avoid Voltage Collapse on loss of Millmerran 2
N^^Q_AR_VC_B4 | 2008-01-03 | 1 | Out= Armidale SVC, avoid Voltage Collapse on loss of Tarong North
N^^Q_AR_VC_B5 | 2008-01-03 | 1 | Out= Armidale SVC, avoid Voltage Collapse on loss of Callide C3
N^^Q_AR_VC_B6 | 2008-01-03 | 1 | Out= Armidale SVC, avoid Voltage Collapse on loss of Callide C4
N^^Q_BCDM_B1 | 2008-01-03 | 1 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Kogan Creek
N^^Q_BCDM_B2 | 2008-01-03 | 1 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Millmerran 1
N^^Q_BCDM_B3 | 2008-01-03 | 1 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Millmerran 2
N^^Q_BCDM_B4 | 2008-01-03 | 1 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Tarong North
N^^Q_BCDM_B5 | 2008-01-03 | 2 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Callide C3
N^^Q_BCDM_B6 | 2008-01-03 | 2 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Callide C4
N^^Q_BR_VC_B1 | 2008-01-03 | 1 | Out= Braemar SVC, avoid Voltage Collapse on loss of Kogan Creek
N^^Q_BR_VC_B2 | 2008-01-03 | 1 | Out= Braemar SVC, avoid Voltage Collapse on loss of Millmerran 1
N^^Q_BR_VC_B3 | 2008-01-03 | 1 | Out= Braemar SVC, avoid Voltage Collapse on loss of Millmerran 2
N^^Q_BR_VC_B4 | 2008-01-03 | 1 | Out= Braemar SVC, avoid Voltage Collapse on loss of Tarong North
N^^Q_BR_VC_B5 | 2008-01-03 | 1 | Out= Braemar SVC, avoid Voltage Collapse on loss of Callide C3
N^^Q_BR_VC_B6 | 2008-01-03 | 1 | Out= Braemar SVC, avoid Voltage Collapse on loss of Callide C4
N^^Q_LS_VC_B1 | 2008-01-03 | 1 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek
N^^Q_LS_VC_B2 | 2008-01-03 | 1 | Out= Lismore SVC, avoid Voltage Collapse on loss of Millmerran 1
N^^Q_LS_VC_B3 | 2008-01-03 | 1 | Out= Lismore SVC, avoid Voltage Collapse on loss of Millmerran 2
N^^Q_LS_VC_B4 | 2008-01-03 | 1 | Out= Lismore SVC, avoid Voltage Collapse on loss of Tarong North
N^^Q_LS_VC_B5 | 2008-01-03 | 1 | Out= Lismore SVC, avoid Voltage Collapse on loss of Callide C3
N^^Q_LS_VC_B6 | 2008-01-03 | 1 | Out= Lismore SVC, avoid Voltage Collapse on loss of Callide C4
N^^Q_MIMR_B1 | 2008-12-09 | 1 | Out= Millmerran-Middle Ridge (9907,9908 or H14 Tx) line, avoid Voltage Collapse on loss of Kogan Creek
N^^Q_MIMR_B2 | 2008-12-09 | 1 | Out= Millmerran-Middle Ridge (9907,9908 or H14 Tx) line, avoid Voltage Collapse on loss of Millmerran 1
N^^Q_MIMR_B3 | 2008-12-09 | 1 | Out= Millmerran-Middle Ridge (9907,9908 or H14 Tx) line, avoid Voltage Collapse on loss of Millmerran 2
N^^Q_MIMR_B4 | 2008-12-09 | 1 | Out= Millmerran-Middle Ridge (9907,9908 or H14 Tx) line, avoid Voltage Collapse on loss of Tarong North
N^^Q_MIMR_B5 | 2008-12-09 | 1 | Out= Millmerran-Middle Ridge (9907,9908 or H14 Tx) line, avoid Voltage Collapse on loss of Callide C3
N^^Q_MIMR_B6 | 2008-12-09 | 1 | Out= Millmerran-Middle Ridge (9907,9908 or H14 Tx) line, avoid Voltage Collapse on loss of Callide C4
N^^Q_NIL_B1 | 2007-12-28 | 1 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek
N^^Q_NIL_B2 | 2007-12-28 | 1 | Out= Nil, avoid Voltage Collapse on loss of Millmerran 1
N^^Q_NIL_B3 | 2007-12-28 | 1 | Out= Nil, avoid Voltage Collapse on loss of Millmerran 2
N^^Q_NIL_B4 | 2007-12-28 | 1 | Out= Nil, avoid Voltage Collapse on loss of Tarong North
N^^Q_NIL_B5 | 2007-12-28 | 1 | Out= Nil, avoid Voltage Collapse on loss of Callide C3
N^^Q_NIL_B6 | 2007-12-28 | 1 | Out= Nil, avoid Voltage Collapse on loss of Callide C4
N^^V_BUDP_2 | 2008-07-23 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic interconnectors and Snowy generation to avoid voltage collapse for loss of a Dederang to Murray 330kV line
N^^V_BUDP_P | 2008-07-23 | 1 | Outage = Buronga to Darlington Point 220kV line, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_BUDP_R | 2008-07-23 | 1 | Outage = Buronga to Darlington Point 220kV line, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, radial mode
N^^V_DD1B2 | 2008-07-01 | 1 | Outage = Dederang No.1 or No.2 330kV bus or MSS-2B 330kV CB or SMTS-1B 330kV CB, limit Vic generators and interconnectors to avoid voltage collapse for loss of a Dederang to Sth Morang and Dederang to Murray 330kV line, trip of one offloads the other
N^^V_DDMB_2 | 2008-07-29 | 1 | Outage = Dederang to Mt Beauty 220kV line, limit Vic interconnectors and Snowy generation to avoid voltage collapse for loss of a Dederang to Murray 330kV line
N^^V_DDMB_P | 2008-07-29 | 1 | Outage = Dederang to Mt Beauty 220kV line, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_DDMB_R | 2008-07-29 | 1 | Outage = Dederang to Mt Beauty 220kV line, limit limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, radial mode
N^^V_DDSM1_P | 2008-07-01 | 1 | Outage = South Morang to Dederang 330kV line 1 or line 2, limit NSW to VIC and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit or Basslink,3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_DDSM1_R | 2008-07-01 | 1 | Outage = South Morang to Dederang 330kV line 1 or line 2, limit NSW to VIC and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit or Basslink,radial mode
N^^V_DDSM2_A | 2008-07-01 | 1 | Outage = South Morang to Dederang 330kV line, limit NSW to VIC and Snowy generation to avoid voltage collapse for trip of a South Morang to Dederang 330kV line, linear approximation first segment
N^^V_DDSM2_B | 2008-07-01 | 1 | Outage = South Morang to Dederang 330kV line, limit NSW to VIC and Snowy generation to avoid voltage collapse for trip of a South Morang to Dederang 330kV line, linear approximation second segment
N^^V_DDWO_P | 2008-07-01 | 2 | Outage = Dederang to Wodonga 330kV line, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_DDWO_R | 2008-07-01 | 2 | Outage = Dederang to Wodonga 330kV line, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, radial mode
N^^V_EPMB_2 | 2008-07-29 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic interconnectors and Snowy generation to avoid voltage collapse for loss of a Dederang to Murray 330kV line
N^^V_EPMB_P | 2008-07-29 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_EPMB_R | 2008-07-29 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, radial mode
N^^V_EPTT | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit NSW to Vic to avoid voltage collapse for trip of a Dederang to South Morang 330kV line
N^^V_EPTT_P | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_EPTT_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, radial mode
N^^V_JNWG_P | 2008-07-01 | 2 | Outage = Jindera to Wagga 330kV line, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_JNWG_R | 2008-07-01 | 2 | Outage = Jindera to Wagga 330kV line, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, radial mode
N^^V_JNWO_P | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_JNWO_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, radial mode
N^^V_LTMS_P | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit NSW to Vic and Snowy gen to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_LTMS_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit NSW to Vic and Snowy gen to avoid voltage collapse for trip of the largest Vic generating unit, radial mode
N^^V_LTUT | 2008-07-29 | 1 | Outage = Lower Tumut to Upper Tumut 330kV line, limit Vic interconnectors and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit
N^^V_LTUT_2 | 2008-07-29 | 1 | Outage = Lower Tumut to Upper Tumut 330kV line, limit Vic interconnectors and Snowy generation to avoid voltage collapse for loss of a Dederang to Murray 330kV line
N^^V_LTWG1_P | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga (051) line, limit NSW to VIC and Snowy generation to avoid voltage collapse for trip of the largest Vic generating or Basslink,3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_LTWG1_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga (051) line, limit NSW to VIC and Snowy generation to avoid voltage collapse for trip of the largest Vic generating or Basslink, radial mode
N^^V_LTWG2_A | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga (051) line, limit NSW to VIC and Snowy generation to avoid voltage collapse for trip of a Murray to Dederang 330kV line, for Snowy generation lower than 2400 MW
N^^V_LTWG2_B | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga (051) line, limit NSW to VIC and Snowy generation to avoid voltage collapse for trip of a Murray to Dederang 330kV line, for Snowy generation above 2400 MW
N^^V_MSBT_1 | 2008-07-01 | 1 | Outage = Murray 330kV bustie CB open, limit NSW to Vic and Vic generators to avoid voltage collapse for trip of the other Murray 330kV bustie CB
N^^V_MSDD1_P | 2008-07-01 | 1 | Outage = Murray to Dederang 330kV line 1 or line 2 limit NSW to VIC and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit or Basslink,3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_MSDD1_R | 2008-07-01 | 1 | Outage = Murray to Dederang 330kV line 1 or line 2 limit NSW to VIC and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit or Basslink,radial mode
N^^V_MSDD2 | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit NSW to VIC and Snowy generation to avoid voltage collapse for trip of a Dederang to Murray 330kV line
N^^V_MSUT_A | 2008-07-01 | 1 | Outage = Murray to Upper Tumut OR Murray to Lower Tumut 330kV line, limit NSW to Vic and Snowy gen to avoid voltage collapse for trip of Murray to Lower Tumut or Murray to Upper Tumut 330kV line, linear approx first segment
N^^V_MSUT_B | 2008-07-01 | 1 | Outage = Murray to Upper Tumut OR Murray to Lower Tumut 330kV line, limit NSW to Vic and Snowy gen to avoid voltage collapse for trip of Murray to Lower Tumut or Murray to Upper Tumut 330kV line, linear approx second segment
N^^V_MSUT_P | 2008-07-01 | 1 | Outage = Murray to Upper Tumut 330kV line, limit NSW to Vic and Snowy gen to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_MSUT_R | 2008-07-01 | 1 | Outage = Murray to Upper Tumut 330kV line, limit NSW to Vic and Snowy gen to avoid voltage collapse for trip of the largest Vic generating unit, radial mode
N^^V_NIL_1 | 2008-07-02 | 1 | Outage = Nil, limit NSW to Vic and Snowy generation to avoid voltage collapse for loss of the largest Vic generating unit, radial or 6/2 parallel modes
N^^V_NIL_1_P | 2009-02-05 | 1 | Outage = Nil, limit NSW to Vic and Snowy generation to avoid voltage collapse for loss of the largest Vic generating unit
N^^V_NIL_2 | 2008-07-02 | 1 | Outage = Nil, limit Vic interconnectors and Snowy generation to avoid voltage collapse for loss of a Dederang to Murray 330kV line
N^^V_SMTXF2_2 | 2008-07-23 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit Vic interconnectors and Snowy generation to avoid voltage collapse for loss of a Dederang to Murray 330kV line
N^^V_SMTXF2_P | 2008-07-23 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_SMTXF2_R | 2008-07-23 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, radial mode
N^^V_SMTXH1_2 | 2008-07-23 | 1 | Outage = South Morang 330/220kV H1 transformer, limit Vic interconnectors and Snowy generation to avoid voltage collapse for loss of a Dederang to Murray 330kV line
N^^V_SMTXH1_P | 2008-07-23 | 1 | Outage = South Morang 330/220kV H1 transformer, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_SMTXH1_R | 2008-07-23 | 1 | Outage = South Morang 330/220kV H1 transformer, limit limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, radial mode
N^^V_SMTXH2_2 | 2008-07-23 | 1 | Outage = South Morang 330/220kV H2 transformer, limit Vic interconnectors and Snowy generation to avoid voltage collapse for loss of a Dederang to Murray 330kV line
N^^V_SMTXH2_P | 2008-07-23 | 1 | Outage = South Morang 330/220kV H2 transformer, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_SMTXH2_R | 2008-07-23 | 1 | Outage = South Morang 330/220kV H2 transformer, limit limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, radial mode
N^^V_SM_SCAP_P | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit NSW to Vic and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_SM_SCAP_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit NSW to Vic and and Snowy generation to avoid voltage collapse for trip of the largest Vic generating unit, radial
N^^V_XDDTX1 | 2008-07-01 | 1 | Out=All DD Tx's, Volt Coll loss of 500 MW Vic unit, VI-84
N^^V_XDDTX2 | 2008-07-01 | 1 | Out=All DD Tx's, Volt Collapse, loss of DDTS-SMTS, VI-84
N^^V_X_DDSM_TWO | 2008-07-01 | 1 | Outage = Both Dederang to Sth Morang 330kV lines, limit Snowy to Vic and Snowy generation to avoid voltage collapse for loss of the largest Vic generating unit
N^^V_X_EPMB_1 | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty lines, limit Snowy to Vic and and Snowy generation to avoid voltage collapse for loss of the largest Vic generating unit, radial or 6/2 parallel modes
N^^V_X_EPMB_1_P | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty lines, limit Snowy to Vic and Snowy generation to avoid voltage collapse for loss of the largest Vic generating unit, 3/5 or 2-5 tied parallel modes or modified radial mode with 1-2 tied
N^^V_X_EPMB_2 | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty lines, limit Vic interconnectors and Snowy generation to avoid voltage collapse for loss of a Dederang to Murray 330kV line
N_BDKV | 2007-12-04 | 1 | Out= Bendeela - Kangaroo Valley (19) line
N_BLTU_97B | 2004-08-27 | 1 | Blowering PS upper limit set to zero due to outage of Blowering to Tumut 97B 132kV line.
N_BW_2000 | 2004-08-17 | 1 | Discretionary upper limit for Bayswater Generation of 2000 MW
N_BW_2100 | 2004-08-17 | 1 | Discretionary upper limit for Bayswater Generation of 2100 MW
N_BW_2200 | 2004-08-17 | 1 | Discretionary upper limit for Bayswater Generation of 2200 MW
N_DL_ETSOS | 2006-08-16 | 1 | Out= Directlink Emergency Trip Scheme, Limit Directlink (Mullumbimby to Terranora) to 0 MW
N_ER_1600 | 2006-03-14 | 1 | Discretionary upper limit for Eraring Generation of 1600 MW
N_ER_1700 | 2006-03-14 | 1 | Discretionary upper limit for Eraring Generation of 1700 MW
N_ER_1800 | 2006-03-14 | 1 | Discretionary upper limit for Eraring Generation of 1800 MW
N_ER_1900 | 2006-03-14 | 1 | Discretionary upper limit for Eraring Generation of 1900 MW
N_ER_2000 | 2006-03-14 | 1 | Discretionary upper limit for Eraring Generation of 2000 MW
N_KV_CB_5432 | 2009-01-13 | 1 | Out= Kangaroo Valley 330kV CB 5432 or CB 5442
N_LD_1700 | 2008-12-10 | 1 | Discretionary upper limit for Liddell Generation of 1700 MW
N_MBTE1_A | 2006-08-16 | 1 | Out= one Directlink cable, NSW to Qld limit
N_MBTE1_B | 2006-08-16 | 1 | Out= one Directlink cable, Qld to NSW limit
N_NIL_TE_A | 2008-03-04 | 1 | Out=Nil, Terranora Interconnector NSW to Qld flow overall limits
N_NIL_TE_B | 2008-03-04 | 1 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits
N_TALWA1_286 | 2009-01-23 | 1 | Tallawarra upper limit of 286MW
N_TALWA1_300 | 2008-12-12 | 1 | Tallawarra upper limit of 300MW
N_TALWA1_400 | 2009-01-23 | 1 | Tallawarra upper limit of 400MW
N_TALWA1_ZERO | 2008-06-17 | 1 | Tallawarra upper limit of 0 MW
N_URANQ11_ZERO | 2008-10-22 | 1 | Uranquinty unit 1 upper limit of 0 MW
N_URANQ12_ZERO | 2008-10-22 | 1 | Uranquinty unit 2 upper limit of 0 MW
N_URANQ13_ZERO | 2008-10-22 | 1 | Uranquinty unit 3 upper limit of 0 MW
N_URANQ14_ZERO | 2008-10-22 | 1 | Uranquinty unit 4 upper limit of 0 MW
N_URANQ_RBSOS_1 | 2008-10-22 | 1 | Uranquinty runback scheme O/S, Discretionary upper limit for Uranquinty Generation to 500 MW
N_V_HV0250 | 2009-02-11 | 1 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 250 MW
N_V_HV0300 | 2009-02-11 | 1 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 300 MW
N_V_HV0350 | 2009-02-11 | 1 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 350 MW
N_V_HV0400 | 2009-02-11 | 1 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 400 MW
N_V_HV0450 | 2009-02-11 | 1 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 450 MW
N_V_HV0500 | 2009-02-11 | 1 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 500 MW
N_V_HV0550 | 2009-02-11 | 1 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 550 MW
N_V_HV0600 | 2008-07-01 | 1 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 600 MW
N_V_HV0750 | 2008-07-01 | 1 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 750 MW
N_V_HV1075 | 2008-07-01 | 1 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 1075 MW
N_V_HV1700 | 2008-07-01 | 1 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 1700 MW
N_X_6_18 | 2007-03-01 | 1 | Bendeela and Kangaroo Valley PS upper limit set to zero due to multiple outage of Canberra to Kangaroo Valley (6) and Dapto to Kangaroo Valley (18) 330 kV lines
N_X_MBTE2_A | 2006-08-16 | 1 | Out= two Directlink cables, NSW to Qld limit
N_X_MBTE2_B | 2006-08-16 | 1 | Out= two Directlink cables, Qld to NSW limit
N_X_MBTE_3 | 2007-06-29 | 1 | Out= all three Directlink cables, Terranora_I/C_import = Terranora_Load
Q1CH40_FL1 | 2004-12-16 | 1 | CQ-SQ<=1680MW(floor for constraint Q^CS1CH40G<1680)
Q1CH40_FL2 | 2004-12-16 | 1 | CQ-SQ<=1680MW(floor for constraint Q^CS1CH40C<1680)
Q1CS_120CPH6GG_FL1 | 2004-12-14 | 1 | QldCQ-SQ<=1680MW(floor for constraint Q^CS_120CP_H6GG_G<1680), Limit offset = -70MW, Specified System Normal=0.0
Q1CS_120CPH6GG_FL2 | 2004-12-14 | 1 | QldCQ-SQ<=1680MW(floor for constraint Q^CS_120CP_H6GG_C<1680), Limit offset = -70MW, Specified System Normal=0.0
Q1CS_50CPH6GG_FL1 | 2004-12-14 | 1 | QldCQ-SQ<=1720MW(floor for constraint Q^CS_50MVARCP_H6GG_G<1720), Limit offset = -30MW, Specified System Normal=0.0
Q1CS_50CPH6GG_FL2 | 2004-12-14 | 1 | QldCQ-SQ<=1720MW(floor for constraint Q^CS_50MVARCP_H6GG_C<1720), Limit offset = -30MW, Specified System Normal=0.0
Q1CS_WU120GG50CP_FL1 | 2004-12-14 | 1 | QldCQ-SQ<=1650MW(floor for constraint Q^CS_WU120CP_GG50_G<1650), Limit offset = -100MW, Specified System Normal=0.0
Q1CS_WU120GG50CP_FL2 | 2004-12-14 | 1 | QldCQ-SQ<=1650MW(floor for constraint Q^CS_WU120CP_GG50_C<1650), Limit offset = -100MW, Specified System Normal=0.0
Q1_H5WO120CP_FL1 | 2004-12-14 | 1 | CQ-SQ<=1715MW(floor for constraint Q^CS_120CP_H5WO_G<1715)
Q1_H5WO120CP_FL2 | 2004-12-14 | 1 | CQ-SQ<=1715MW(floor for constraint Q^CS_120CP_H5WO_C<1715)
Q::CS_WO_VC | 2008-12-10 | 1 | Out= Woolooga SVC, limit Central -South Qld upper transfer limit to 1900MW
Q:BCBS_820 | 2006-05-08 | 1 | Outage= 820 H10 Bouldercombe - H20 Broadsound, Central Qld to North Qld transient stability limit for loss of either Nebo to Strathmore (822 or 840) 275kV line.Limit is a function of NQLD GTs on/off
Q:BCNE_821 | 2006-05-12 | 1 | Outage= 821 H10 Bouldercombe - H11 Nebo, Central Qld to North Qld transient stability limit for loss of either Nebo to Strathmore (822 or 840) 275kV line.Limit is a function of NQLD GTs on/off
Q:BSNE_834_OR_845 | 2006-04-27 | 1 | Outage=either 834 or 845 Broadsound to Nebo, Central Qld to North Qld transient stability limit for loss of either Nebo to Strathmore (822 or 840) 275kV line.Limit is a function of NQLD GTs on/off
Q:CN680 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 680 MW (discretionary)
Q:CN690 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 690 MW (discretionary)
Q:CN700 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 700 MW (discretionary)
Q:CN710 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 710 MW (discretionary)
Q:CN720 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 720 MW (discretionary)
Q:CN730 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 730 MW (discretionary)
Q:CN740 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 740 MW (discretionary)
Q:CN750 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 750 MW (discretionary)
Q:CN760 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 760 MW (discretionary)
Q:CN770 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 770 MW (discretionary)
Q:CN780 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 780 MW (discretionary)
Q:CN790 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 790 MW (discretionary)
Q:CN800 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 800 MW (discretionary)
Q:CN810 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 810 MW (discretionary)
Q:CN820 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 820 MW (discretionary)
Q:CN830 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 830 MW (discretionary)
Q:CN840 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 840 MW (discretionary)
Q:CN850 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 850 MW (discretionary)
Q:CN860 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 860 MW (discretionary)
Q:CN870 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 870 MW (discretionary)
Q:CN880 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 880 MW (discretionary)
Q:CN890 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 890 MW (discretionary)
Q:CN900 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 900 MW (discretionary)
Q:CN910 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 910 MW (discretionary)
Q:CN920 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 920 MW (discretionary)
Q:CN930 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 930 MW (discretionary)
Q:CN940 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 940 MW (discretionary)
Q:CN950 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 950 MW (discretionary)
Q:CN960 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 960 MW (discretionary)
Q:CN980 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 980 MW (discretionary)
Q:CN_SM_SVC_REDUCED | 2008-02-18 | 1 | Out=Nil, Strathmore SVC reduced in capability, (Offset -50 on No GT eqn), Central Qld to North Qld voltage stability and damping limit for loss of either Nebo to Strathmore (822 or 840) 275kV line.Limit is a function of NQLD GTs on/off. Interim limit
Q:CQNQ_H11SVC_PART | 2004-11-30 | 1 | QLD,Out=H11 SVC restriction,CQ-NQ T.Stab Lmt = ( 975 - f(# of NQhyd SCs))
Q:CR_BUS2_CN1 | 2007-07-17 | 1 | Outage=Clare 2 Bus, Central Qld to North Qld transient stability limit for loss of either Nebo to Strathmore (822 or 840) 275kV line.Limit is a function of NQLD GTs on/off
Q:DSMH7124 | 2004-11-09 | 1 | QLD, C-N Lmt <= 820MW (132kV feeder 7124 Dysart-Moranbah oos) Average flow
Q:H35SM_TX | 2007-06-05 | 1 | QLD,Out= TX at H35 Strathmore, No offset on GT online eqn, but ceiling = 840MW; -250MW offset on NoGT On equation, with ceiling of 740MW.
Q:N1BIBRTX | 2003-03-27 | 1 | QNI-Out=BR_Tx &NSW fdr,Tstab(BITrip375MW)Lmt,Trf Q-N,MMPSon/off
Q:N2L-GBVC | 2008-05-22 | 1 | Out= Braemar SVC, Tstab(2L-Gfault Tar)Trf Q-N,Millm PS offline
Q:NE_CB8342 | 2007-07-26 | 1 | Outage= H11 NEBO CB 8342 , Central Qld to North Qld transient stability limit for loss of Nebo to Strathmore 822 275kV line.Limit is a function of NQLD GTs on/off
Q:NE_CP_120MVAR | 2004-11-30 | 1 | QLD,Out=H11 Nebo 120MVAR CP,CQ-NQ T.Stab Lmt = 985 - f(# of NQhyd SCs)-20
Q:NE_SVC_SM_CB | 2005-12-08 | 1 | Out=H11Nebo SVC+H35 Strathmore 275kV CB, Central Qld to North Qld transient stability limit for contingencies in the CQ-NQ network.Limit is a function of NQLD GTs on/off
Q:NIL_CN1 | 2007-11-30 | 1 | Outage=Nil, Central Qld to North Qld voltage stability and damping limit for loss of either Nebo to Strathmore (822 or 840) 275kV line.Limit is a function of NQLD GTs on/off. Interim limit
Q::NIL_CS | 2009-11-18 | 2 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW), 2008/2009 implementation
Q:NIL_CQNQ | 2008-04-30 | 1 | Outage=Nil, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:N_30+38_N4 | 2008-07-01 | 1 | Out= Liverpool-SydW(30)+Regentville-SydW(38), limit Qld->NSW QNI flow to retain synchronism on Liddell-Newcastle(81) fault
Q:N_AR330BS3_BCK2L-G | 2007-03-09 | 1 | Out= Armidale 330kV Bus Section #3, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Bulli Creek
Q:N_AR330BS3_BI_POT | 2007-03-09 | 1 | Out= Armidale 330kV Bus Section #3, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, Millmerran in-service
Q:N_AR330BS3_N3 | 2008-07-01 | 1 | Out= Armidale 330kV Bus Section #3, Qld to NSW on QNI Transient Stability Limit, Fault on one Bayswater to Liddell (33 or 34) 330kV Line
Q:N_AR330BS3_N4 | 2008-07-01 | 1 | Out= Armidale 330kV Bus Section #3, Qld to NSW on QNI Transient Stability Limit, Fault on Liddell to Newcastle (81) 330kV line
Q:N_ARDM_A | 2008-02-28 | 1 | Outage= 8C or 8E; QNI+Directlink; QLD to NSW transient stability limit for a contingent trip of a potline in Queensland (Boyne Island potline trip).
Q:N_ARTW_1 | 2006-02-10 | 1 | Out = Armidale to Tamworth (85 or 86), Qld to NSW on QNI Transient Stability, 2 Line to Ground fault at Bulli Creek
Q:N_ARTW_2 | 2006-02-10 | 1 | Out = Armidale to Tamworth (85 or 86), Qld to NSW on QNI Transient Stability Limit, Loss of Boyne Islane 375MW potline, Millmerran in-service
Q:N_ARTW_3 | 2008-07-01 | 1 | Outage = Armidale to Tamworth (85 or 86), Qld to NSW on QNI Transient Stability Limit, Fault on one Bayswater to Liddell (33 or 34) 330kV line
Q:N_ARTW_4 | 2008-07-01 | 1 | Outage = Armidale to Tamworth (85 or 86), Qld to NSW on QNI Transient Stability Limit, Fault on Liddell to Newcastle (81) 330kV line
Q:N_AR_330_BS1_1 | 2007-11-26 | 1 | Out= Armidale No.1 330kV bus, Qld to NSW transient stability limit for trip of a Qld potline
Q:N_AR_330_BS1_OSC | 2007-11-26 | 1 | Out= Armidale No.1 330kV bus, Qld to NSW Oscillatory stability limit
Q:N_AR_330_BS5_1 | 2007-09-14 | 1 | Out= Armidale No.5 330kV bus, Qld to NSW transient stability limit for trip of a Qld potline
Q:N_AR_330_BS5_OSC | 2007-09-14 | 1 | Out= Armidale No.5 330kV bus, Qld to NSW Oscillatory stability limit
Q:N_AR_BUS5_N-2 | 2009-01-05 | 2 | Out=Nil, Armidale 330kV bus 5 declared credible
Q:N_AR_CP1_BCK2L-G | 2006-02-10 | 1 | Out = Armidale capacitor bank (80MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Bulli Creek
Q:N_AR_CP1_BI_POT | 2006-02-10 | 1 | Out = Armidale capacitor bank (80MVAr), limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, Millmerran in-service
Q:N_AR_CP1_N3 | 2008-07-01 | 1 | Out = Armidale capacitor bank (80MVAr), Qld to NSW on QNI Transient Stability Limit, Fault on one Bayswater to Liddell (33 or 34) 330kV line
Q:N_AR_CP1_N4 | 2008-07-01 | 1 | Outage = Armidale capacitor bank (80MVAr), Qld to NSW on QNI Transient Stability Limit, Fault on Liddell to Newcastle (81) 330kV line
Q:N_AR_CP2_1 | 2006-02-10 | 1 | Out = Armidale capacitor bank (120MVAr), Qld to NSW on QNI Transient Stability Limit, Loss of Boyne Island 375MW potline, 1 or 2 Millmerran units I/S
Q:N_AR_CP2_BCK2L-G | 2006-02-10 | 1 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Bulli Creek
Q:N_AR_CP2_N3 | 2008-07-01 | 1 | Outage = Armidale capacitor bank (120MVAr), Qld to NSW on QNI Transient Stability Limit, Fault on one Bayswater to Liddell (33 or 34) 330kV line
Q:N_AR_CP2_N4 | 2008-07-01 | 1 | Outage = Armidale capacitor bank (120MVAr), Qld to NSW on QNI Transient Stability Limit, Fault on Liddell to Newcastle (81) 330kV line
Q:N_BCDM_A | 2008-03-03 | 1 | Outage= 8L or 8M; QNI+Directlink; QLD to NSW transient stability limit for a contingent trip of a potline in Queensland (Boyne Island potline trip).
Q:N_BCK2L-G_-025 | 2009-02-11 | 1 | Nominated Offset -25MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Bulli Creek, 2008/2009 implementation
Q:N_BCK2L-G_-050 | 2009-02-11 | 1 | Nominated Offset -50MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Bulli Creek, 2008/2009 implementation
Q:N_BCK2L-G_-075 | 2009-02-11 | 1 | Nominated Offset -75MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Bulli Creek, 2008/2009 implementation
Q:N_BCK2L-G_-100 | 2009-02-11 | 1 | Nominated Offset -100MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Bulli Creek, 2008/2009 implementation
Q:N_BCK2L-G_-125 | 2009-02-11 | 1 | Nominated Offset -125MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Bulli Creek, 2008/2009 implementation
Q:N_BCK2L-G_-150 | 2009-02-11 | 1 | Nominated Offset -150MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Bulli Creek, 2008/2009 implementation
Q:N_BCK2L-G_-175 | 2009-02-11 | 1 | Nominated Offset -175MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Bulli Creek, 2008/2009 implementation
Q:N_BCK2L-G_-200 | 2009-02-11 | 1 | Nominated Offset -200MW, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Bulli Creek, 2008/2009 implementation
Q:N_BCKTR_BCK2L-G | 2006-02-17 | 1 | Outage=either 8814,or 8815, or 9901, or 9902, or a Braemar Tx, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Bulli Creek, ( Offset -100MW )
Q:N_BCKTR_BI_POT | 2006-02-17 | 1 | Outage=either 8814,or 8815, or 9901, or 9902, or a Braemar Tx, limit Qld to NSW on QNI to avoid transient instability on loss of Boyne Island Potline, ( Offset -100MW )
Q:N_BCKTR_N3 | 2008-07-01 | 1 | Outage=either 8814,or 8815, or 9901, or 9902, or a Braemar Tx, Qld to NSW on QNI Transient Stability Limit, Fault on one Bayswater to Liddell (33 or 34) 330kV Line. , ( Offset -100MW )
Q:N_BCKTR_N4 | 2008-07-01 | 1 | Outage=either 8814,or 8815, or 9901, or 9902, or a Braemar Tx, Qld to NSW on QNI Transient Stability Limit, Fault on Liddell to Newcastle (81) 330kV line ( Offset -100MW ),
Q:N_BIMBVC | 2008-05-22 | 2 | Out=Braemar SVC, Tstab( 375MWload loss) Trf Q-N,.Millm.PS.Offline
Q:N_BI_POT488 | 2003-12-16 | 1 | QNI-Trn.stab(BI PotLnTrip488MW)Lmt,Trf Q-N,Millmer.PSon-line.
Q:N_BI_POT_-025 | 2009-02-11 | 1 | Nominated Offset -25MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-050 | 2009-02-11 | 1 | Nominated Offset -50MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-075 | 2009-02-11 | 1 | Nominated Offset -75MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-100 | 2009-02-11 | 1 | Nominated Offset -100MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-1000 | 2009-02-11 | 1 | Nominated Offset -1000MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-125 | 2009-02-11 | 1 | Nominated Offset -125MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-150 | 2009-02-11 | 1 | Nominated Offset -150MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-175 | 2009-02-11 | 1 | Nominated Offset -175MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-200 | 2009-02-11 | 1 | Nominated Offset -200MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-300 | 2009-02-11 | 1 | Nominated Offset -300MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-400 | 2009-02-11 | 1 | Nominated Offset -400MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-500 | 2009-02-11 | 1 | Nominated Offset -500MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-550 | 2007-10-29 | 1 | Outage=Boyne Island load at risk upto 520MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline. Limit_advice Kogan Creek in service May 2007
Q:N_BI_POT_-600 | 2009-02-11 | 1 | Nominated Offset -600MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-700 | 2009-02-11 | 1 | Nominated Offset -700MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-800 | 2009-02-11 | 1 | Nominated Offset -800MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BI_POT_-900 | 2009-02-11 | 1 | Nominated Offset -900MW, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_BKVC_N3 | 2008-07-01 | 1 | Outage = Blackwall SVC, Qld to NSW on QNI Transient Stability Limit, Fault on one Bayswater to Liddell (33 or 34) 330kV line
Q:N_BKVC_N4 | 2008-07-01 | 1 | Outage = Blackwall SVC, Qld to NSW on QNI Transient Stability Limit, Fault on Liddell to Newcastle (81) 330kV line
Q:N_BK_VC_OSC | 2004-11-12 | 2 | Outage= Blackwall SVC, limit Qld to NSW on QNI to avoid Oscillatory Instability
Q:N_BK_VC_POD_A | 2004-01-07 | 1 | Blackwall SVC POD reduced in effectiveness, Oscillatory Stability for the loss of either 8C or 8E (Armidale to Dumaresq) 330kV and high Qld demand
Q:N_BK_VC_POD_B | 2004-01-07 | 1 | Blackwall SVC POD reduced in effectiveness, Oscillatory Stability for the loss of either 8C or 8E (Armidale to Dumaresq) 330kV and light Qld demand
Q:N_BK_VC_POD_C | 2004-01-07 | 1 | Blackwall SVC POD reduced in effectiveness, Oscillatory Stability for the loss of a Boyne Island Potline and high Qld demand, No Millmerran Units I/S
Q:N_BRTX_BI_POT | 2006-06-02 | 2 | Outage=Braemar Tx and Bus, ( offset -150MW for no Millmerran units on else offset -20 MW for 1 or 2 units on ) limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, Millmerran in-service
Q:N_BRVC_MPP_ON | 2003-06-20 | 1 | Out=Braemar SVC, Q->N Transient stability Max Limit, Millmerran in service, discrete limit for one unit 835 for two units1010
Q:N_BRVC_N3 | 2008-07-01 | 1 | Out=Braemar svc, Q->N Tstab, Liddell-Bayswater Fault,
Q:N_BRVC_N4 | 2008-07-01 | 1 | Out=Braemar svc, Q->N Tstab, Liddell-Newcastle Fault
Q:N_BR_VC_A | 2004-01-29 | 1 | Outage= Braemar SVC, Oscillatory Stability for the loss of either 8C or 8E (Armidale to Dumaresq) 330kV and high Qld demand
Q:N_BR_VC_B | 2004-01-29 | 1 | Outage= Braemar SVC, Oscillatory Stability for the loss of either 8C or 8E (Armidale to Dumaresq) 330kV and light Qld demand
Q:N_BR_VC_C | 2004-01-29 | 1 | Outage= Braemar SVC, Oscillatory Stability for the loss of a Boyne Island Potline and high Qld demand, No Millmerran Units I/S
Q:N_BWLD_N-2 | 2009-02-10 | 1 | Discretionary import from QLD to NSW limits <=730
Q:N_DM_CB | 2004-10-22 | 1 | Outage = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, Qld to NSW on QNI Transient Stability Limit for a fault on either the Armidale to Dumaresq (8C or 8E) or Bulli Creek to Dumaresq (8L or 8M) 330kV lines
Q:N_H36BK_VC | 2007-06-14 | 1 | QNI-Out=H36BKSVC and with H22LL 50MVAr Cap avail/not available ,T.stability(BI PotLTrip375MW)Lmt,TransferQ-N, with MillmerranPS covered for 0, 1 or 2 units in service.
Q:N_LDMU_1 | 2004-12-22 | 1 | Outage = Liddell to Muswellbrook (83) 330kV line, Qld to NSW on QNI Transient Stability Limit for loss of Boyne Islane 375MW potline
Q:N_LDTW_1 | 2004-09-21 | 1 | Outage = Liddell to Tamworth (84) 330kV line, Qld to NSW on QNI Transient Stability Limit for loss of Boyne Islane 375MW potline
Q:N_LS_VC1 | 2008-05-22 | 2 | Out=Lismore SVC, QNI Q-N Transfer stability limit , Millmerran PS on/off.
Q:N_MMBCK_BCK2L-G | 2005-12-01 | 1 | Outage=MMBCK either 9903 or 9904, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Bulli Creek
Q:N_MMBCK_BI_POT | 2005-12-01 | 1 | Outage=MMBCK either 9903 or 9904, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, Millmerran in-service
Q:N_MUTW_1 | 2004-04-19 | 1 | Outage = Muswellbrook to Tamworth (88), Qld to NSW on QNI Transient Stability Limit, Loss of Boyne Islane 375MW potline, Millmeran in service
Q:N_NIL_BCK2L-G | 2009-02-10 | 1 | Outage=Nil, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Bulli Creek, 2008/2009 implementation
Q:N_NIL_BI_POT | 2009-02-10 | 1 | Outage=Nil, limit Qld to NSW on QNI to avoid transient instability on trip of a Boyne Island potline, 2008/2009 implementation
Q:N_NIL_BI_POT_-1000 | 2008-09-24 | 1 | Outage=1000MW NQ load at risk,( Qld to NSW on QNI potline eqn limit Offset = -1000MW to avoid transient instability ). Limit_advice PQ 5 Sept 2008
Q:N_NIL_BI_POT_-200 | 2008-09-24 | 1 | Outage=600MW NQ load at risk,( Qld to NSW on QNI potline eqn limit Offset = -200MW to avoid transient instability ). Limit_advice PQ 5 Sept 2008
Q:N_NIL_BI_POT_-400 | 2008-09-24 | 1 | Outage=700MW NQ load at risk,( Qld to NSW on QNI potline eqn limit Offset = -400MW to avoid transient instability ). Limit_advice PQ 5 Sept 2008
Q:N_NIL_BI_POT_-600 | 2008-09-24 | 1 | Outage=800MW NQ load at risk,( Qld to NSW on QNI potline eqn limit Offset = -600MW to avoid transient instability ). Limit_advice PQ 5 Sept 2008
Q:N_NIL_BI_POT_-800 | 2008-09-24 | 1 | Outage=900MW NQ load at risk,( Qld to NSW on QNI potline eqn limit Offset = -800MW to avoid transient instability ). Limit_advice PQ 5 Sept 2008
Q:N_NIL_N3 | 2008-07-01 | 1 | Outage = Nil, Qld to NSW on QNI Transient Stability Limit, Fault on one Bayswater to Liddell (33 or 34) 330kV Line
Q:N_NIL_N4 | 2008-07-01 | 1 | Outage = Nil, Qld to NSW on QNI Transient Stability Limit, Fault on Liddell to Newcastle (81) 330kV line
Q:N_NIL_OSC | 2004-12-07 | 1 | Outage = Nil, limit Qld to NSW on QNI to avoid Oscillatory Instability
Q:N_TW_330_BUS1_1 | 2008-06-26 | 1 | Out= Tamworth No.1 330kV bus, Qld to NSW transient stability limit for trip of a Qld potline
Q:N_TW_330_BUS1_OSC | 2008-06-26 | 1 | Out= Tamworth No.1 330kV bus, Qld to NSW Oscillatory stability limit
Q:N_TW_330_BUS3_1 | 2008-06-26 | 1 | Out= Tamworth No.3 330kV bus, Qld to NSW transient stability limit for trip of a Qld potline
Q:N_TW_330_BUS3_OSC | 2008-06-26 | 1 | Out= Tamworth No.3 330kV bus, Qld to NSW Oscillatory stability limit
Q:QBCK650 | 2003-01-21 | 1 | Qld- Millmerran PS generation<= 650 MW for dynamic stability.
Q:QBCK700 | 2003-01-21 | 1 | Qld- Millmerran PS generation<= 700 MW for dynamic stability.
Q:QBCK750 | 2003-01-21 | 1 | Qld- Millmerran PS generation<= 750MW for dynamic stability.
Q:QBCK800 | 2003-02-06 | 1 | Qld-Millmerran PS generation = 800 MW for dynamic stability.
Q:QNISTB03_488 | 2008-05-22 | 2 | QNI-Lmt Trn stab( 488MWload loss) Qld-NSW,.Millm.PS.Offline
Q:SMRS | 2007-10-10 | 1 | Out = either 880 or 879 H35 Strathmore to H13 Ross,C-N (Transient, 2Ph to gnd on 880 or 879) Lmt 400 (including Dysart infeed) - Collinsville generation, including ceilings of 340 with and 300 without Collinsville generation.
Q:T_CQNQ-000 | 2008-08-18 | 1 | Nominated Offset = -0MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-030 | 2008-05-23 | 1 | Nominated Offset = -30MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-060 | 2008-05-23 | 1 | Nominated Offset = -60MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-090 | 2008-05-23 | 1 | Nominated Offset = -90MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-120 | 2008-05-23 | 1 | Nominated Offset = -120MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-150 | 2008-05-23 | 1 | Nominated Offset = -150MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-180 | 2008-05-23 | 1 | Nominated Offset = -180MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-210 | 2008-05-23 | 1 | Nominated Offset = -210MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-240 | 2008-05-23 | 1 | Nominated Offset = -240MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-270 | 2008-05-23 | 1 | Nominated Offset = -270MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-300 | 2008-05-23 | 1 | Nominated Offset = -300MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-350 | 2008-05-23 | 1 | Nominated Offset = -350MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-400 | 2008-05-23 | 1 | Nominated Offset = -400MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-450 | 2008-05-23 | 1 | Nominated Offset = -450MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:T_CQNQ-500 | 2008-05-23 | 1 | Nominated Offset = -500MW, Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:X_BSNE_2_CQNQ | 2008-04-30 | 1 | Out= H20 Broadsound - H11 Nebo ( any two lines oos during augmentation works ), Central Qld to North Qld transient stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q:X_BSNE_2_RSVC_CQNQ | 2008-04-30 | 1 | Out= H20 Broadsound - H11 Nebo ( any two lines oos during augmentation works )+ H13 ROSS oos, Central Qld to North Qld transient stability limit for loss of either H11 to H35 (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q<NQGTS_01 | 1999-11-29 | 1 | Discretionary North Queensland GTs limit <= 180MW
Q<NQGTS_02 | 1999-11-29 | 1 | System Normal North Queensland GTs Limit <=200
Q<NQGTS_03 | 1999-11-29 | 1 | Discretionary North Queensland GTs limit <=220MW
Q<NQGTS_04 | 1999-11-29 | 1 | Discretionary North Queensland GTs limit <=240MW
Q<Q-821CN4 | 2003-11-25 | 1 | QLD,Outage of One,275kV fdr 821,834, 845orDysart7124/2(CNtf 700)
Q<QBCG_01 | 2005-01-18 | 1 | Out = Clermont to Lilyvale (7153) line, Barcaldine PS islanded
Q<QBCG_02 | 2005-01-18 | 1 | Out = Barcaldine to Clermont (7154) line, Barcaldine PS islanded
Q<QRMA_01 | 2005-01-18 | 1 | Out = both Chinchilla to Tarong (7168 and 7183) lines, Roma PS islanded
Q<QRMA_02 | 2005-01-18 | 1 | Out = both Chinchilla to Roma (7164 and 7174) lines, Roma PS islanded
Q>7227_CI_WR | 2004-04-16 | 1 | Out = 7227 Woree - Cairns 132Kv line. Barron Gorge gen >=30MW, maintain 7225/7226 within thermal limits for loss of 7226/7225
Q>822_PARALLEL-OPEN | 2008-09-26 | 1 | Out= H11 Nebo - H35 Strathmore 822 275kV line to prevent thermal overload on remaining H11 Nebo - H35 Strathmore 840 275kV line, with 132kV parallel open.
Q>840_PARALLEL-OPEN | 2008-09-26 | 1 | Out= H11 Nebo - H35 Strathmore 840 275kV line to prevent thermal overload on remaining H11 Nebo - H35 Strathmore 822 275kV line, with 132kV parallel open
Q>879_PARALLEL-OPEN | 2008-09-26 | 1 | Out= H35 Strathmore - H13 Ross 879 275kV line to prevent thermal overload on remaining H35 Strathmore - H13 Ross 880 275kV line, with the 132kV parallel open.
Q>880_PARALLEL-OPEN | 2008-09-26 | 1 | Out= H35 Strathmore - H13 Ross 880 275kV line to prevent thermal overload on remaining H35 Strathmore - H13 Ross 879 275kV line, with 132kV parallel open.
Q>>BCGL1_BCGL2_CLWU | 2008-11-04 | 1 | Out= Bouldercombe to Gladstone (812 or 811) avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Gladstone (811 or 812), Feedback
Q>>NIL_855_871 | 2009-12-15 | 2 | To prevent thermal overload on Calvale to Wurdong 275kV fdr 871 on trip of Calvale to Stanwell (855), Feedback
Q>>NIL_MR_4TX | 2007-06-15 | 1 | Out= NIL, avoid O/L Middle Ridge No.4 Transformer on trip of Braemar to Tarong (8814), Feedback
Q>>QTR_1400 | 2007-05-03 | 1 | Tarong cutset discretionary limit 1400MW
Q>>QTR_1450 | 2007-05-03 | 1 | Tarong cutset discretionary limit 1450MW
Q>>QTR_1500 | 2007-05-03 | 1 | Tarong cutset discretionary limit 1500MW
Q>>QTR_1550 | 2007-05-03 | 1 | Tarong cutset discretionary limit 1550MW
Q>>QTR_1600 | 2007-05-03 | 1 | Tarong cutset discretionary limit 1600MW
Q>>QTR_1650 | 2007-05-03 | 1 | Tarong cutset discretionary limit 1650MW
Q>>QTR_1700 | 2007-05-03 | 1 | Tarong cutset discretionary limit 1700MW
Q>>QTR_1750 | 2007-05-03 | 1 | Tarong cutset discretionary limit 1750MW
Q>>QTR_1800 | 2007-05-03 | 1 | Tarong cutset discretionary limit 1800MW
Q>>QTR_1850 | 2007-05-03 | 1 | Tarong cutset discretionary limit 1850MW
Q>>QTR_1900 | 2007-05-03 | 1 | Tarong cutset discretionary limit 1900MW
Q>>QTR_1950 | 2007-05-03 | 1 | Tarong cutset discretionary limit 1950MW
Q>>QTR_2000 | 2007-04-30 | 1 | Tarong cutset discretionary limit 2000MW
Q>>QTR_2050 | 2007-04-30 | 1 | Tarong cutset discretionary limit 2050MW
Q>>QTR_2100 | 2007-04-30 | 1 | Tarong cutset discretionary limit 2100MW
Q>>QTR_2150 | 2007-04-30 | 1 | Tarong cutset discretionary limit 2150MW
Q>>QTR_2200 | 2007-04-30 | 1 | Tarong cutset discretionary limit 2200MW
Q>>QTR_2250 | 2007-04-30 | 1 | Tarong cutset discretionary limit 2250MW
Q>>QTR_2300 | 2007-04-30 | 1 | Tarong cutset discretionary limit 2300MW
Q>>QTR_2350 | 2007-04-30 | 1 | Tarong cutset discretionary limit 2350MW
Q>>QTR_2400 | 2007-04-30 | 1 | Tarong cutset discretionary limit 2400MW
Q>>QTR_2450 | 2007-04-30 | 1 | Tarong cutset discretionary limit 2450MW
Q>>QTR_2500 | 2007-04-30 | 1 | Tarong cutset discretionary limit 2500MW
Q>>QTR_2550 | 2007-04-30 | 1 | Tarong cutset discretionary limit 2550MW
Q>>QTR_2600 | 2007-04-26 | 1 | Tarong cutset discretionary limit 2600MW
Q>>QTR_2650 | 2007-04-26 | 1 | Tarong cutset discretionary limit 2650MW
Q>>QTR_2700 | 2007-04-26 | 1 | Tarong cutset discretionary limit 2700MW
Q>>QTR_2750 | 2007-04-26 | 1 | Tarong cutset discretionary limit 2750MW
Q>>QTR_2800 | 2007-04-26 | 1 | Tarong cutset discretionary limit 2800MW
Q>>QTR_2850 | 2007-04-26 | 1 | Tarong cutset discretionary limit 2850MW
Q>>QTR_2900 | 2007-04-26 | 1 | Tarong cutset discretionary limit 2900MW
Q>>QTR_2950 | 2007-04-26 | 1 | Tarong cutset discretionary limit 2950MW
Q>>QTR_3000 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3000MW
Q>>QTR_3050 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3050MW
Q>>QTR_3100 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3100MW
Q>>QTR_3150 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3150MW
Q>>QTR_3200 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3200MW
Q>>QTR_3250 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3250MW
Q>>QTR_3300 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3300MW
Q>>QTR_3350 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3350MW
Q>>QTR_3400 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3400MW
Q>>QTR_3450 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3450MW
Q>>QTR_3500 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3500MW
Q>>QTR_3550 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3550MW
Q>>QTR_3600 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3600MW
Q>>QTR_3650 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3650MW
Q>>QTR_3700 | 2007-04-26 | 1 | Tarong cutset discretionary limit 3700MW
Q>ASTV_TYPGEN | 2004-08-10 | 1 | Out= 7276 & 7277 Alan Sherriff Townsville 132kV lines
Q>BCGL1_BCGL2_STCL | 2007-08-10 | 1 | Out= Bouldercombe to Gladstone (811), avoid O/L Stanwell to Calvale (855) on trip of Bouldercombe to Gladstone (812), Feedback
Q>BCGL1_STCL_BCGL2 | 2007-08-10 | 1 | Out= Bouldercombe to Gladstone (811), avoid O/L Bouldercombe to Gladstone (812) on trip of Stanwell to Calvale (855), Feedback
Q>BCGL2_BCGL1_STCL | 2007-08-10 | 1 | Out= Bouldercombe to Gladstone (812), avoid O/L Stanwell to Calvale (855) on trip of Bouldercombe to Gladstone (811), Feedback
Q>BCGL2_STCL_BCGL1 | 2007-08-10 | 1 | Out= Bouldercombe to Gladstone (812), avoid O/L Bouldercombe to Gladstone (811) on trip of Stanwell to Calvale (855), Feedback
Q>BI_1TX_865_GD460 | 2005-01-12 | 1 | Out=H8 Boyne Island 1Tx or Fdr 865 H8 Boyne to H40 Wurdong. Gladstone units 3&4 generation >=460MW.
Q>BI_7146_GD200 | 2005-03-16 | 1 | Out=7146 or 7145 H7 Gladstone to H8 Boyne Is; Gladstone units 3&4 >=200
Q>BRTX1-2 | 2005-03-10 | 1 | Braemar330/275kV Tx combined load<=1125MVA(Lmt adjustment= -100; if MVAr shortfall in availability >1210MVAr in SEQ )
Q>BSNE_834_OR_845 | 2006-05-08 | 1 | Out = 834 or 845 275kV Broadsound - Nebo , Thermal 7150/1( bay rating ) or 7124/2 ( conductor ), Qld Central to North upper transfer limit of 470 MW
Q>CLSW855_871C | 2004-03-08 | 1 | Out=Calvale-Stanwell 275kV Fdr 855, Max MVA Transfer on Fdr 871, Cal PS calculated max. gen
Q>CLSW855_871GL_ST | 2004-03-08 | 1 | Out=Calvale-Stanwell 275kV Fdr 855Max MVA Transfer on Fdr 871, Gld PS and Stn PS summated calculated min gen.
Q>CN350 | 2008-09-26 | 1 | Qld Central to North upper transfer limit of 350 MW (discretionary)
Q>CN500 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 500 MW (discretionary)
Q>CN520 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 520 MW (discretionary)
Q>CN540 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 540 MW (discretionary)
Q>CN560 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 560 MW (discretionary)
Q>CN580 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 580 MW (discretionary)
Q>CN600 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 600 MW (discretionary)
Q>CN620 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 620 MW (discretionary)
Q>CN640 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 640 MW (discretionary)
Q>CN660 | 2005-12-08 | 1 | Qld Central to North upper transfer limit of 660 MW (discretionary)
Q>GD_BTXFMR_120 | 2006-02-22 | 2 | Out = H7 Glad.275kV BTTx . Constrain Pre-conting. flow on other BTTx to 120MW to prevent post contingent flow exceeding 2 hr rating 370MVA for next Contingency GLWU 818.
Q>GD_BT_XFMR | 2005-01-12 | 1 | Out = H7/T5 Bus Tie Transformer. Gladstone units 3&4 generation >=450MW to maintain remaining BTT within 2hour rating post contingent.
Q>GD_BT_XFMR_400 | 2005-01-12 | 1 | Out = H7/T5 Bus Tie Transformer. Gladstone units 3&4 generation >=400MW to maintain remaining BTT within 2hour rating post contingent.
Q>GLBC_811-812 | 2006-05-26 | 1 | Out= 275kV Gladstone -Bouldercombe Feeder 811or 812 , ( includes secure thermal limit calc to maintain flow within rating of 871 and 811 or 812)
Q>H4MU_TX+704_GC540 | 2004-10-14 | 1 | Out=H4 TR and 132kV Fdr 704 or 132kV Fdr 7193, Summated MW Lmt for 275kV fdrs( 805 + 806) Swanbank to Mudgeeraba/Molendinar for Gold Coast limit of 540MW.
Q>H4MU_TX245 | 2003-10-08 | 1 | Out=Two H4Mudgeeraba 275/110kV transformers( one planned and one unplanned), Directlink constrained to maintain remaining transformer loading <=245MW ( 250MVA)
Q>H4MU_TX_GC380 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=380MW
Q>H4MU_TX_GC390 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=390MW
Q>H4MU_TX_GC400 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=400MW
Q>H4MU_TX_GC410 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=410MW
Q>H4MU_TX_GC420 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=420MW
Q>H4MU_TX_GC430 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=430MW
Q>H4MU_TX_GC440 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=440MW
Q>H4MU_TX_GC450 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=450MW
Q>H4MU_TX_GC460 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=460MW
Q>H4MU_TX_GC470 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=470MW
Q>H4MU_TX_GC480 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=480MW
Q>H4MU_TX_GC490 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=490MW
Q>H4MU_TX_GC500 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=500MW
Q>H4MU_TX_GC510 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=510MW
Q>H4MU_TX_GC520 | 2006-07-17 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=520MW
Q>H4MU_TX_GC530 | 2006-07-12 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=530MW
Q>H4MU_TX_GC540 | 2006-07-12 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=540MW
Q>H4MU_TX_GC550 | 2006-07-12 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=550MW
Q>H4MU_TX_GC560 | 2006-07-12 | 1 | Out = Mudgeeraba 275/110kV transformer, limit Directlink flows to maintain Gold Coast cutset transfer <= 560MW
Q>H4MU_TX_GC570 | 2006-07-12 | 1 | Out = Mudgeeraba 275/110kV transformer, limit Directlink flows to maintain Gold Coast cutset transfer <= 570MW
Q>H4MU_TX_GC580 | 2006-07-12 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=580MW
Q>H4MU_TX_GC590 | 2006-07-12 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=590MW
Q>H4MU_TX_GC600 | 2006-07-12 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=600MW
Q>H4MU_TX_GC610 | 2006-07-17 | 1 | Out=275/110kV, H4 Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=610MW
Q>H4MU_TX_GC620 | 2006-07-17 | 1 | Out=275/110kV, H4 Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=620MW
Q>H4MU_TX_GC630 | 2006-07-17 | 1 | Out=275/110kV, H4 Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=630MW
Q>H4MU_TX_GC650 | 2006-07-18 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=650MW
Q>H4MU_TX_GC675 | 2006-07-18 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=675MW
Q>H4MU_TX_GC700 | 2006-07-19 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=700MW
Q>H4MU_TX_GC750 | 2007-07-02 | 1 | Out=275/110kV H4Mudgeeraba transformer,N-Q&Q-N Dirlink flows constrained to maintain GoldCoast cutset transfer<=750MW, Note! requires load shed scheme armed.
Q>KACH_7191_7192 | 2006-05-05 | 1 | Out=Kareeya - Chalumbin 132kV lines 7191 and 7192. Management of thermal limit on 132kV fdrs 7176 and 7277. ( Dispatch Only )
Q>MRTA | 2007-06-14 | 1 | Out = NIL, OakeyPS constrained for continous rating of Middle-Ridge-Tangkam 110kV lines
Q>MRTA_731 | 2004-02-23 | 1 | Out = Middle-Ridge-Tangkam 110kV line 731, OakeyPS constrained for continous rating of Line 732.
Q>MRTA_732 | 2004-02-23 | 1 | Out = Middle-Ridge-Tangkam 110kV line 732 OakeyPS constrained for continous rating of Line 731.
Q>MUTE757_758_A | 2007-09-18 | 1 | Out= Terranora to Mudgeeraba 110kV feeders 757 or 758 thermal limit for Terranora to Mudgeeraba (at Terranora) Transfers
Q>MUTE757_758_B | 2007-09-18 | 1 | Out= Terranora to Mudgeeraba 110kV feeders 757 or 758 thermal limit for Mudgeeraba to Terranora (at Mudgeeraba) Transfers
Q>N-CH_TX_DY | 2006-08-14 | 1 | Out= Coffs Harbour 330/132kV transformer, avoid O/L (conditional 15 min rating) Armidale to Kempsey (965) on trip of Coffs Harbour to Nambucca (9W3), Raleigh and Sawtell not fed from Coffs Harbour, Feedback
Q>NIL_757+758_A | 2006-08-24 | 1 | Out=Nil,Thermal limit for 110kV fdrs( 757 + 758) Terranora to Mudgeeraba (at Terranora) System Normal.
Q>NIL_757+758_B | 2008-02-21 | 1 | Out=Nil, Thermal limit for 110kV fdrs( 757 + 758) Mudgeeraba to Terranora (at Mudgeeraba) System Normal. Summer and Winter ECS ratings selected by status
Q>NIL_805+806 | 2006-03-22 | 1 | Out=Nil, Thermal limit Summated MW for 275kV fdrs( 805 + 806) Swanbank to Mudgeeraba system normal.Summer and Winter ECS ratings selected by status..
Q>NIL_SBMU | 2006-03-23 | 1 | Out = Nil. Control post contingent flow on Fdrs 8826, 805 and 806 to within entered rating.
Q>NIL_STAN_STN | 2007-06-28 | 1 | Out = Nil Stanwell Power Station as a single credible contingency
Q>NIL_TR_TX1_4 | 2009-07-02 | 1 | Out= Nil, avoid thermal O/L on remaining Tarong 275/132 kV Tx #1 or #4, on trip of either Tarong 275/132 kV Tx #1 or #4, (or either 7168 or 7183 Tarong - Chinchilla 132kV lines), Feedback
Q>NIL_TRCN_TRCN | 2009-11-09 | 1 | Out= Nil, Powerlink relay limit on Tarong to Chinchilla 132kV lines, for the contingent loss of a single Tarong to Chinchilla 132kV line, Feedback
Q>NIL_CNTR_CNTR | 2010-01-15 | 1 | Out= Nil, Ergon relay limit on Chinchilla to Tarong 132kV lines, for the contingent loss of a single Chinchilla to Tarong 132kV line, Feedback
Q>N_NIL_8L_8M | 2008-11-18 | 1 | Out= Nil, limit QNI flow to avoid overloading 8L or 8M on trip of the other
Q>PRE855_871CAL | 2007-05-23 | 1 | SystemNormal MVA Max precontingent Transfer on Fdr 871for fdr 855 contingency, Cal PS calculated max.
Q>PRE855_871GL_ST | 2007-05-23 | 1 | SystemNormal MVA Max precontingent Transfer on Fdr 871for fdr 855 contingency, Glad PS and Stn PS summated calculated min.
Q>PWSP_1350 | 2006-08-10 | 1 | Qld Central to Qld South upper transfer limit of 1350MW (discretionary), ( 5 of 5 equations )
Q>TVAS7276_77_120PRE | 2006-08-15 | 2 | Out=Various system conditions which require 120MW Max summated pre-contingent transfer Townsv PS-Alan Sheriff 132kV lines 7276-7277 to cover next contingency being either 7277 or 7276.
Q>TVAS7276_77_POST | 2006-01-25 | 2 | Out=Nil, Post contingent Townsville PS - Alan Sherriff 132kV line 7276 or Towns.PS -Alan Sh.132kV line 7277. Thermal limit for remaining inservice parallel line. Washout of +2000applied when 2 lines are in service(System Normal).
Q>TVAS7276_77_PRE | 2007-07-11 | 1 | Out=anyone of the lines 7133, 7134 and 7135 ; Post contingent Townsville PS - Alan Sherriff 132kV lines 7276 or 7277. Precontingent transfer for initial contingent value for remaining inservice parallel line. 10000 washout applied following contingency
Q>TVAS_RADIAL | 2007-07-19 | 1 | Out= 7192 + 7191 + 7136 ; Townsville PS - Alan Sherriff 132kV lines 7276 or 7277. Precontingent transfer for initial contingent value for remaining inservice parallel line. 10000 washout applied following contingency of 7276 or 7277
Q>TV_TYP | 2005-09-19 | 1 | Out = 7241 Townsville - Townsville PS 132KV line orT145 Townsville PS SW'YD 132kV 2 bus.
Q>WOPW_1350 | 2007-03-14 | 1 | Qld Central to Qld South upper transfer limit of 1350MW ( ceiling 1350 ),
Q>WOSP_1600 | 2006-08-23 | 1 | Qld Central to Qld South upper transfer limit of 1600MW
Q>X_7253_7135 | 2006-09-20 | 1 | Out=Kareeya - Tully/Cardwell 132kV lines 7253 and 7135/2. Management of thermal limit on 132kV fdrs7276 and 7277. ( Dispatch Only )
QLD_BCTR | 2003-04-04 | 1 | Qld / Southern separation between Bulli Creek and Tarong, allow Millmerran flows into NSW
QMSP<=100 | 1999-11-08 | 1 | Eff : 08/11/1999 ; RHS = 100 ; Op = "<=" ; Wt = 20 ; Dynamic = N
QNI_ISLE_A | 2003-04-04 | 1 | Qld / Southern separation, allow QNI to supply Northern NSW Load
QNI_ISLE_B | 2003-04-04 | 1 | Qld / Southern separation, allow QNI to supply Northern NSW Load
QNS_000 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 0 MW
QNS_0000 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 0 MW
QNS_0025 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 25 MW
QNS_0050 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 50 MW
QNS_0075 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 75 MW
QNS_0100 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 100 MW
QNS_0125 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 125 MW
QNS_0150 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 150 MW
QNS_0175 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 175 MW
QNS_0200 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 200 MW
QNS_0225 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 225 MW
QNS_0250 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 250 MW
QNS_0275 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 275 MW
QNS_0300 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 300 MW
QNS_0325 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 325 MW
QNS_0350 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 350 MW
QNS_0375 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 375 MW
QNS_0400 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 400 MW
QNS_0425 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 425 MW
QNS_0450 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 450 MW
QNS_0475 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 475 MW
QNS_0500 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 500 MW
QNS_0525 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 525 MW
QNS_0550 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 550 MW
QNS_0575 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 575 MW
QNS_0600 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 600 MW
QNS_0625 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 625 MW
QNS_0650 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 650 MW
QNS_0675 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 675 MW
QNS_0700 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 700 MW
QNS_0725 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 725 MW
QNS_0750 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 750 MW
QNS_0775 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 775 MW
QNS_0800 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 800 MW
QNS_0825 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 825 MW
QNS_0850 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 850 MW
QNS_0875 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 875 MW
QNS_0900 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 900 MW
QNS_0925 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 925 MW
QNS_0950 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 950 MW
QNS_0975 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 975 MW
QNS_1000 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 1000 MW
QNS_1050 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 1050 MW
QNS_1100 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 1100 MW
QNS_1150 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 1150 MW
QNS_1200 | 2008-08-05 | 1 | Qld to NSW summated QNI + Terranora upper transfer limit of 1200 MW
QNTE>=10 | 2008-03-03 | 1 | Qld to NSW Terranora minimum Interconnector flow >=10 MW
QNTE_000 | 2008-08-05 | 1 | Qld to NSW on Terranora Interconnector upper transfer limit of 0 MW
QNTE_030 | 2008-08-05 | 1 | Qld to NSW on Terranora Interconnector upper transfer limit of 30 MW
QNTE_050 | 2008-08-05 | 1 | Qld to NSW on Terranora Interconnector upper transfer limit of 50 MW
QNTE_060 | 2008-08-05 | 1 | Qld to NSW on Terranora Interconnector upper transfer limit of 60 MW
QNTE_090 | 2008-08-05 | 1 | Qld to NSW on Terranora Interconnector upper transfer limit of 90 MW
QNTE_100 | 2008-08-05 | 1 | Qld to NSW on Terranora Interconnector upper transfer limit of 100 MW
QNTE_110 | 2008-08-05 | 1 | Qld to NSW Terranora Interconnector upper tfr limit of 110 MW
QNTE_120 | 2008-08-05 | 1 | Qld to NSW on Terranora Interconnector upper transfer limit of 120 MW
QNTE_150 | 2008-08-05 | 1 | Qld to NSW on Terranora Interconnector upper transfer limit of 150 MW
QNTE_180 | 2008-08-05 | 1 | Qld to NSW on Terranora Interconnector upper transfer limit of 180 MW
QNTE_210 | 2008-08-05 | 1 | Qld to NSW on Terranora Interconnector upper transfer limit of 210 MW
QNTE_240 | 2008-08-05 | 1 | Qld to NSW on Terranora Interconnector upper transfer limit of 240 MW
QNTE_ROC | 2006-12-27 | 1 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector
QN_000 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 0 MW
QN_025 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 25 MW
QN_050 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 50 MW
QN_075 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 75 MW
QN_100 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 100 MW
QN_1000 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 1000 MW
QN_1025 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 1025 MW
QN_1050 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 1050 MW
QN_1080 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 1080 MW
QN_1100 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 1100 MW
QN_125 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 125 MW
QN_150 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 150 MW
QN_175 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 175 MW
QN_200 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 200 MW
QN_225 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 225 MW
QN_250 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 250 MW
QN_275 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 275 MW
QN_300 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 300 MW
QN_325 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 325 MW
QN_350 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 350 MW
QN_375 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 375 MW
QN_400 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 400 MW
QN_425 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 425 MW
QN_450 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 450 MW
QN_475 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 475 MW
QN_500 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 500 MW
QN_525 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 525 MW
QN_550 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 550 MW
QN_575 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 575 MW
QN_600 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 600 MW
QN_615 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 615 MW
QN_625 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 625 MW
QN_650 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 650 MW
QN_675 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 675 MW
QN_700 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 700 MW
QN_725 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 725 MW
QN_750 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 750 MW
QN_775 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 775 MW
QN_800 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 800 MW
QN_825 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 825 MW
QN_850 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 850 MW
QN_875 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 875 MW
QN_900 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 900 MW
QN_925 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 925 MW
QN_950 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 950 MW
QN_975 | 2008-08-05 | 1 | Qld to NSW on QNI upper transfer limit of 975 MW
QN_ZERO | 2005-11-11 | 1 | Qld to NSW on QNI upper transfer limit of 0 MW
Q^7135_7253_857_FNQ3 | 2005-06-16 | 1 | Out=275kV Ross-Chal.Fdr 857or 858+Ingham -Kareeya 7135+ Tully-Kareeya 7253. voltage collapseFNQ Lmt(contingency Chalumbin-Woree)<= Limit calc - 8MWoffset.
Q^7135_7253_857_FNQ4 | 2005-06-16 | 1 | Out=275kV Ross-Chal.Fdr 857or 858+Ingham-Kareeya 7135+ Tully-Kareeya 7253, voltage collapseFNQ Lmt(contingency Ross-Chalumbin)<= Limit calc - 28MWoffset,
Q^ASTV_FNQ3 | 2007-10-12 | 1 | Outage= (single) either 7266 or 7277 T150 Alan Sherriff -T145Townsville 132kV lines, Far North Qld Voltage Stability limit for loss of Chalumbin to Woree (877) 275kV line
Q^ASTYP7276_7VC_FNQ4 | 2004-07-21 | 1 | Qld,out=132KV AlanSherriff-Townsville GT PS Lines 7276& 7277+ Ross SVC; volt.collapseFNQ Lmt(contingency Ross-Chalumbin)
Q^ASTYP7276_7_FNQ3 | 2004-07-21 | 1 | Qld,out=132KV AlanSherriff-Townsville GT PS Lines 7276& 7277;volt.collapseFNQ Lmt(contingencyChalumbin - Woree)
Q^ASTYP7276_7_FNQ4 | 2004-07-21 | 1 | Qld,out=132KV AlanSherriff-Townsville GT PS Lines 7276& 7277; volt.collapseFNQ Lmt(contingency Ross-Chalumbin)
Q^BCBS_820 | 2006-05-08 | 1 | Outage= 820 H10 Bouldercombe - H20 Broadsound, Central Qld to North Qld voltage stability limit for loss of either Nebo to Strathmore (822 or 840) 275kV line.Limit is a function of NQLD GTs on/off
Q^BCNE_821 | 2006-05-12 | 1 | Outage= 821 H10 Bouldercombe - H11 Nebo, Central Qld to North Qld voltage stability limit for loss of either Nebo to Strathmore (822 or 840) 275kV line.Limit is a function of NQLD GTs on/off
Q^BK_VC_GC | 2008-12-01 | 1 | Out= Blackwall SVC 275kV, Gold Coast Voltage Stability limit, Offset = -15MW, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC), Summer 2008/09
Q^BSNE_834_OR_845 | 2006-04-27 | 1 | Outage=834 or 845 Broadsound to Nebo, Central Qld to North Qld voltage stability limit for loss of either Nebo to Strathmore (822 or 840) 275kV line.Limit is a function of NQLD GTs on/off
Q^CL_CB88102_1CS | 2005-08-25 | 1 | Out = Calvale CB 88102, CQ-SQ Limit<=voltage stability calc(1277.2 + f(units on;MW,kV) - 50 Calc Marg) -75 offset, calc below 1660, 2000 washout applied , Gladstone Q margin
Q^CL_CB88102_2CS | 2005-08-25 | 1 | Out = Calvale CB 88102, CQ-SQ Limit<=voltage stability calc(1267.2 + f(units on;MW,kV) -50 Calc Marg) -90 offset, calc below 1660, 2000 washout applied, Calvale Q margin
Q^CL_CB88102_CSFL1 | 2005-08-25 | 1 | Out = Calvale CB 88102, CQ-SQ<=1675MW (floor for Q^CL_CB88102_1CS to maintain limit >=1675), Gladstone MVAr margin
Q^CL_CB88102_CSFL2 | 2005-08-25 | 1 | Out = Calvale CB 88102, CQ-SQ<=1675MW (floor for Q^CL_CB88102_2CS to maintain limit >=1675), Calvale MVAr margin
Q^CS1CH40C | 2004-12-16 | 1 | Out=H40Wurdong 120MVAr cap bank, CQ-SQ uv stab Lmt<=1680<=Calvale Qmargin calc<=1900, Limit offset = -70MW, Specified System Normal=0.0
Q^CS1CH40G | 2004-12-16 | 1 | Out=H40Wurdong 120MVAr cap bank, CQ-SQ uv stab Lmt<=1680<=Gladstone Qmargin calc<=1900, Limit offset = -70MW, Specified System Normal=0.0
Q^CS_-040 | 2009-01-29 | 1 | Nominated Offset -40MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_-080 | 2009-01-29 | 1 | Nominated Offset -80MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_-120 | 2009-01-29 | 1 | Nominated Offset -120MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_-160 | 2009-01-29 | 1 | Nominated Offset -160MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_-200 | 2009-01-29 | 1 | Nominated Offset -200MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_-240 | 2009-01-29 | 1 | Nominated Offset -240MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_-280 | 2009-01-29 | 1 | Nominated Offset -280MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_-320 | 2009-01-29 | 1 | Nominated Offset -320MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_-360 | 2009-01-29 | 1 | Nominated Offset -360MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_-400 | 2009-01-29 | 1 | Nominated Offset -400MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_-440 | 2009-01-29 | 1 | Nominated Offset -440MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_-480 | 2009-01-29 | 1 | Nominated Offset -480MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_-520 | 2009-01-29 | 1 | Nominated Offset -520MW, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^CS_120CP_H5WO_C | 2004-12-16 | 1 | Out=120MVAr 275kV CapBank at H5 Woolooga, CQ-SQ uv stab Lmt=1715 <=Calvale Qmargin calc <=1900, Limit offset = -35MW, Specified System Normal=0.0
Q^CS_120CP_H5WO_G | 2004-12-16 | 1 | Out=120MVAr 275kV CapBank at H5 Woolooga, CQ-SQ uv stab Lmt=1715 <=Gladstone Qmargin calc <=1900, Limit offset = -35MW, Specified System Normal=0.0
Q^CS_120CP_H6GG_C | 2004-12-16 | 1 | Out=120MVAr 275kVkV CapBank at H6 Gin Gin, CQ-SQ uv stab Lmt <=1680<=Calvale Qmargin calc<=1900, limit offset= -70, Specified system normal =0.0
Q^CS_120CP_H6GG_G | 2004-12-16 | 1 | Out=120MVAr 275kV CapBank at H6 Gin Gin, CQ-SQ uv stab Lmt=1680 <=Gladstone Qmargin calc <=1900, Limit offset = -70MW, Specified System Normal=0.0
Q^CS_WU120CP_GG50_C | 2004-12-16 | 1 | Out=Wurdong120MVArCapBank + GinGin 132kV CapBank, CQ-SQ uv stab Lmt<=1650 <=Calvale Qmargin calc<=1900, limit offset= -100, Specified system normal =0.0
Q^CS_WU120CP_GG50_G | 2004-12-16 | 1 | Out=Wurdong120MVArCapBank + GinGin 132kV CapBank , CQ-SQ uv stab Lmt<=1650 <=Gladstone Qmargin calc<=1900, Limit offset = -100MW, Specified System Normal=0.0
Q^FNQ4-015 | 2008-06-26 | 1 | Nominated offset = -15MW, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line
Q^FNQ4-030 | 2008-06-26 | 1 | Nominated offset = -30MW, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line
Q^FNQ4-045 | 2008-06-26 | 1 | Nominated offset = -45MW, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line
Q^FNQ4-060 | 2008-06-26 | 1 | Nominated offset = -60MW, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line
Q^FNQ4-075 | 2008-06-26 | 1 | Nominated offset = -75MW, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line
Q^FNQ4-090 | 2008-06-26 | 1 | Nominated offset = -90MW, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line
Q^FNQ4-105 | 2008-06-26 | 1 | Nominated offset = -105MW, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line
Q^FNQ4-120 | 2008-06-26 | 1 | Nominated offset = -120MW, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line
Q^FNQ4-135 | 2008-06-26 | 1 | Nominated offset = -135MW, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line
Q^FNQ4-150 | 2008-06-26 | 1 | Nominated offset = -150MW, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line
Q^GBMO_8824_8825 | 2008-12-01 | 1 | Out= Greenbank to Molendinar 275kV feeder 8824 or 8825, Gold Coast Voltage Stability limit, Offset = -30MW, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC), Summer 2008/09
Q^GBMO_N-2 | 2008-12-01 | 1 | Out= Nil. Greenbank to Molendinar 275kV feeders 8824 and 8825 declared a credible contingency, Gold Coast Voltage Stability limit, Offset = -40MW, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC), Summer 2008/09
Q^GBMU_835_836 | 2008-12-01 | 1 | Out= Greenbank to Mudgeeraba 275kV feeder 835 or 836, Gold Coast Voltage Stability limit, Offset = -50MW, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC), Summer 2008/09
Q^GBMU_N-2 | 2008-12-01 | 1 | Out= Nil. Greenbank to Mudgeeraba 275kV feeders 835 and 836 declared a credibile contingency, Gold Coast Voltage Stability limit, Offset = -55MW, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC), Summer 2008/09
Q^GC_-100 | 2008-12-01 | 1 | Nominated Offset -100, Gold Coast Voltage Stability limit, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC), Summer 2008/09
Q^GC_-125 | 2008-12-01 | 1 | Nominated Offset -125, Gold Coast Voltage Stability limit, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC), Summer 2008/09
Q^GC_-25 | 2008-12-01 | 1 | Nominated Offset -25, Gold Coast Voltage Stability limit, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC), Summer 2008/09
Q^GC_-50 | 2008-12-01 | 1 | Nominated Offset -50, Gold Coast Voltage Stability limit, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC), Summer 2008/09
Q^GC_-75 | 2008-12-01 | 1 | Nominated Offset -75, Gold Coast Voltage Stability limit, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC), Summer 2008/09
Q^GGGLD_1CS | 2007-03-30 | 1 | Out= 275kV feeder 814 H6 Gin Gin to H7 Gladstone, CQ-SQ Cutset, Gladstone Qmargin ( Offset -200MW ) ( floor 1550 )
Q^GGGLD_2CS | 2007-03-30 | 1 | Out= 275kV feeder 814 H6 Gin Gin to H7 Gladstone, CQ-SQ Cutset, Calvale Qmargin ( Offset -250MW ) ( floor 1500 )
Q^GGWO_1CS | 2007-03-30 | 1 | Out= 275kV feeder 816 H6 Gin Gin to H5 Woolooga , CQ-SQ Transfer voltage stability limit, Gladstone Equation, ( Offset -120 MW, floor 1630 MW )
Q^GGWO_2CS | 2007-03-30 | 1 | Out= 275kV feeder 816 H6 Gin Gin to H5 Woolooga, CQ-SQ Cutset voltage stability limit, Calvale Qmargin ( Offset -180 MW, floor 1570 MW )
Q^GGWU_1CS | 2008-05-14 | 1 | Out= 275kV feeder 819 H6 Gin Gin to H40 Wurdong, CQ-SQ Cutset, Gladstone Qmargin ( Offset -200MW ) ( floor 1550 )
Q^GGWU_2CS | 2008-05-14 | 1 | Out= 275kV feeder 819 H6 Gin Gin to H40 Wurdong, CQ-SQ Cutset, Calvale Qmargin ( Offset -250MW ) ( floor 1500 )
Q^MU_TX | 2008-02-05 | 1 | Out = a single Mudgeeraba 275kV / 110kV transformer, Offset = -30MW to Gold Coast voltage stability limit, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC)
Q^NIL_1CS | 2006-11-16 | 1 | Out=Nil , CQ-SQ Transfer SystemNormal<=voltage stabilitycalc(1277.2+f(units on;MW,kV)- 50CalcMarg),calc below 1750, Limit set to 1750 (floor) ; Gladstone Qmargin
Q^NIL_2CS | 2006-11-16 | 1 | Out=Nil , CQ-SQ Transfer SystemNormal<=voltage stabilitycalc(1267.2+f(units on;MW,kV)-50CalcMarg;)),calc below 1750, Limit set to 1750 (floor);Calvale Qmargin
Q^NIL_CN_FDR | 2009-10-15 | 1 | Outage=Nil, Central Qld to North Qld voltage stability limit, Feeder trip equation, 2009/10 implementation.
Q^NIL_CN_GT | 2009-10-15 | 1 | Outage=Nil, Central Qld to North Qld voltage stability limit, GT trip equation, 2009/10 implementation.
Q^NIL_CQNQ | 2008-10-27 | 1 | Outage=Nil, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^NIL_CS | 2009-01-29 | 1 | Out = Nil, CQ-SQ voltage stability limit, 2008/2009 implementation
Q^NIL_FNQ4 | 2008-02-14 | 1 | Out=Nil, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line
Q^NIL_GC | 2008-12-01 | 1 | Out = Nil, Gold Coast Voltage Stability limit, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC), Summer 2008/09
Q^NIL_TR_CLTR | 2008-12-16 | 1 | Out = Nil, Tarong voltage stability limit, Calvale-Tarong contingency equation, 2008/09 Summer Season
Q^N_AR_330_BS3_1 | 2008-03-06 | 1 | Out= Armidale No.3 330kV bus, QLD to NSW voltage stability limit for trip of a Dumaresq to Armidale 330kV line 8E
Q^PWCP_1CS | 2003-07-11 | 1 | Out=Palmwoods cap bank,CQ-SQ Limit<=voltage stabilitycalc(1277.2+f(units on;MW,kV)- 50CalcMarg) -10 offset,calc below 1740, 2000 washout applied ; Gladstone Qmargin
Q^PWCP_2CS | 2003-07-11 | 1 | Out=Palmwoods cap bank,CQ-SQ Limit<=voltage stabilitycalc(1267.2+f(units on;MW,kV)-50CalcMarg) -10 offset,calc below 1740, 2000 washout applied;Calvale Qmargin
Q^PWCP_CSFL1 | 2003-07-11 | 1 | QldCQ-SQ<=1740MW;floor for constr Q^PWCP_1CS to maintain limit >=1740),GladstoneMVAr marg
Q^PWCP_CSFL2 | 2003-07-11 | 1 | QldCQ-SQ<=1740MW;floor for constr Q^PWCP_1CS to maintain limit >=1740)Calvale MVAr marg
Q^PWSP_C2CS | 2006-08-17 | 1 | Out=Palmwoods-SouthPine,Calvale Qmargin, Limit calc below 1100 Logic select for limit to be specified 1100 floor.
Q^PWSP_G1CS | 2006-08-17 | 1 | Out=Palmwoods-SouthPine, CQ-SQ Transfer, Gladstone Qmargin, Limit calc below 1100 Logic select for limit to be specified 1100 floor.
Q^PWSP_TRBUS_1CS | 2005-09-15 | 1 | Out=275kV fdr 808 Palmwoods-SthPine+275kV Bus H18Tarong, CQ-SQ Transfer SystemNormal<=voltage stabilitycalc(1277.2+f(units on;MW,kV)- 50CalcMarg),calc below 1550, 2000 washout applied ; Gladstone Qmargin
Q^PWSP_TRBUS_2CS | 2005-09-15 | 1 | Out=275kV fdr 808 Palmwoods-SthPine+275kV Bus H18Tarong, CQ-SQ Transfer SystemNormal<=voltage stabilitycalc(1267.2+f(units on;MW,kV)-50CalcMarg;)),calc below 1450, 2000 washout applied;Calvale Qmargin
Q^PWSP_TRBUS_FL1 | 2005-09-15 | 1 | Out=275kV fdr 808 Palmwoods-SthPine+275kV Bus H18Tarong, CQ-SQ<=1550MW(floor for constr Q^PWSP_TRBUS_1CS to maintain limit>=1550), Gladstone MVAr margin
Q^PWSP_TRBUS_FL2 | 2005-09-15 | 1 | Out=275kV fdr 808 Palmwoods-SthPine+275kV Bus H18Tarong,CQ-SQ<=1450MW(floor for constr Q^PWSP_TRBUS_2CS to maintain limit>=1450) Calvale MVAr margin
Q^RS550_VC | 2004-11-30 | 1 | Qld,Out=Ross_SVC, Ross(H13Ross+fdrs7128 & 7208)uvLmt<=550MW
Q^SB_CB88262_GC | 2008-02-05 | 1 | Outage = H1 Swanbank CB88262, Gold Coast voltage stability limit, Cutset= (275kV into GC at H4MU and H31MD) + (110kV into GC at T81CC), Limit Offset -45MW when Swanbank E online.
Q^SEMU805_SBMU806 | 2006-08-02 | 2 | Out = Swanbank-Mudgeeraba 275kV fdr 805 or 806. GCLmt=497.68+f( SWBE+WIV on-line + SEQ cap banks + DL MWs,DLMVArs), -50 MW offset on GC UV limit. Note: 7193 also switched out.
Q^TR_CB88102_1CS | 2007-07-19 | 1 | Out=H18 Tarong CB88102, Equation1 Gladstone Qmargin, Offset -400MW
Q^TR_CB88102_2CS | 2007-07-19 | 1 | Out= H18 Tarong CB88102, CQ-SQ Equation 2, Calvale Qmargin, Offset -450 MW
Q^TR_CB88282_1CS | 2006-11-14 | 1 | Out=Tarong CB88282, Offset -400MW to CQ-SQ Transfer Equation1 Gladstone Qmargin
Q^TR_CB88282_2CS | 2006-11-14 | 2 | Out= Tarong CB88282, Offset -450MW CQ-SQ Transfer Limit Equation 2, Calvale Qmargin
Q^TR_CB88282_CSFL1 | 2006-11-14 | 1 | CQ-SQ<=(1750-400 offset) 1350MW floor equation1, Gladstone MVAr margin
Q^TR_CB88282_CSFL2 | 2006-11-14 | 1 | CQ-SQ<=(1750 - 450) 1300MW floor for equation2 Calvale MVAr margin
Q^TR_CLTR_-050 | 2008-12-16 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Calvale-Tarong contingency equation, Summer 2008/09
Q^TR_CLTR_-100 | 2008-12-16 | 1 | Nominated Offset -100MW, Tarong voltage stability limit, Calvale-Tarong contingency equation, Summer 2008/09
Q^TR_CLTR_-150 | 2008-12-16 | 1 | Nominated Offset -150MW, Tarong voltage stability limit, Calvale-Tarong contingency equation, Summer 2008/09
Q^TR_CLTR_-200 | 2008-12-16 | 1 | Nominated Offset -200MW, Tarong voltage stability limit, Calvale-Tarong contingency equation, Summer 2008/09
Q^TR_CLTR_-250 | 2008-12-16 | 1 | Nominated Offset -250MW, Tarong voltage stability limit, Calvale-Tarong contingency equation, Summer 2008/09
Q^TR_CLTR_-300 | 2008-12-16 | 1 | Nominated Offset -300MW, Tarong voltage stability limit, Calvale-Tarong contingency equation, Summer 2008/09
Q^TR_CLTR_-350 | 2008-12-16 | 1 | Nominated Offset -350MW, Tarong voltage stability limit, Calvale-Tarong contingency equation, Summer 2008/09
Q^TR_CLTR_-400 | 2008-12-16 | 1 | Nominated Offset -400MW, Tarong voltage stability limit, Calvale-Tarong contingency equation, Summer 2008/09
Q^TR_CLTR_-450 | 2008-12-16 | 1 | Nominated Offset -450MW, Tarong voltage stability limit, Calvale-Tarong contingency equation, Summer 2008/09
Q^TR_CLTR_-500 | 2008-12-16 | 1 | Nominated Offset -500MW, Tarong voltage stability limit, Calvale-Tarong contingency equation, Summer 2008/09
Q^TVTU_7134_FNQ3 | 2005-05-25 | 2 | Outage = Townsville PS -Tully132kV line 7134 Far North Qld Voltage Stability limit for loss of Chalumbin to Woree (877) 275kV line,Lmt Offset 0.0
Q^TVTU_7134_FNQ4 | 2005-05-25 | 2 | Outage = Townsville PS -Tully132kV line 7134, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line, Lmt Offset -8
Q^V_CQNQ-000 | 2008-10-28 | 1 | Nominated Offset = -0MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-030 | 2008-10-28 | 1 | Nominated Offset = -30MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-060 | 2008-10-28 | 1 | Nominated Offset = -60MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-090 | 2008-10-28 | 1 | Nominated Offset = -90MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-120 | 2008-10-28 | 1 | Nominated Offset = -120MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-150 | 2008-10-28 | 1 | Nominated Offset = -150MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-180 | 2008-10-28 | 1 | Nominated Offset = -180MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-210 | 2008-10-28 | 1 | Nominated Offset = -210MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-240 | 2008-10-28 | 1 | Nominated Offset = -240MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-270 | 2008-10-28 | 1 | Nominated Offset = -270MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-300 | 2008-10-28 | 1 | Nominated Offset = -300MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-350 | 2008-10-28 | 1 | Nominated Offset = -350MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-400 | 2008-10-28 | 1 | Nominated Offset = -400MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-450 | 2008-10-28 | 1 | Nominated Offset = -450MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^V_CQNQ-500 | 2008-10-28 | 1 | Nominated Offset = -500MW, Central Qld to North Qld voltage stability limit for loss of either H11 Nebo to H35 Strathmore (822 or 840) or H35 Strathmore to H13 Ross (880 or 879 ) 275kV lines.
Q^WO3C_1CS | 2007-08-29 | 1 | Out=120MVAr cap at H5 Woolooga, CQ-SQ voltage stability; Gladstone Qmargin, Offset -35 on equation and floor
Q^WO3C_2CS | 2007-08-29 | 1 | Out=120MVAr cap at H5 Woolooga, CQ-SQ voltage stability;Calvale Qmargin, Offset -35 on equation and floor
Q^WOCP_CS1 | 2004-03-24 | 1 | out= H5 Woolooga 50 MVAr cap bank; CQ-SQ Trf<=UVcalc(1277.2+f(units on;MW,kV;);GldQmarg
Q^WOCP_CS2 | 2004-03-24 | 1 | out= H5 Woolooga 50 MVAr cap bank; CQ-SQ Trf<=UVcalc(1267.2+f(units on;MW,kV;);CalvQmarg
Q^WOCP_FL1 | 2004-03-24 | 1 | out= H5 Woolooga 50 MVAr cap bank; QldCQ-SQ<=1735MW(floor for constr Q^WOCP_CS1>=1735)
Q^WOCP_FL2 | 2004-03-24 | 1 | out= H5 Woolooga 50 MVAr cap bank; QldCQ-SQ<=1735MW(floor for constr Q^WOCP_CS2>=1735)
Q^WOPW_C2CS | 2007-04-12 | 1 | Out=Woolooga - Palmwoods, Calvale Qmargin, 1350 floor, Offset -400MW
Q^WOPW_G1CS | 2007-04-12 | 1 | Out=Woolooga - Palmwoods, CQ-SQ Transfer, Gladstone Qmargin, 1350 floor, Offset -400MW
Q^WOSP_C2CS | 2006-08-23 | 1 | Out=Palmwoods-SouthPine,Calvale Qmargin, offset -300 on equation and floor.
Q^WOSP_G1CS | 2006-08-23 | 1 | Out=Palmwoods-SouthPine, CQ-SQ Transfer, Gladstone Qmargin, offset -200 on equation and floor.
Q^X_ASTV_FNQ3 | 2007-10-12 | 1 | Outage= (double) Both 7266 and 7277 T150 Alan Sherriff -T145Townsville 132kV lines, Far North Qld Voltage Stability limit for loss of Chalumbin to Woree (877) 275kV line
Q^X_BSNE_2_CQNQ | 2008-10-28 | 1 | Out= H20 Broadsound - H11 Nebo ( any two lines oos during augmentation works ), Central Qld to North Qld voltage stability limit for loss largest GT trip in North Queensland.
Q^X_BSNE_2_RSVC_CQNQ | 2008-04-30 | 1 | Out= H20 Broadsound - H11 Nebo ( any two lines oos during augmentation works )+ H13 ROSS oos, Central Qld to North Qld voltage stability limit for loss largest GT trip in North Queensland.
Q^X_NEVC_LVDS | 2006-05-23 | 1 | Outage=Nebo SVC + 7150 Lilyvale - Dysart, Central Qld to North Qld voltage stability limit for loss of either Nebo to Strathmore (822 or 840) 275kV line.Limit is a function of NQLD GTs on/off
Q^X_RSVC_WRVC | 2008-04-16 | 1 | Out=ROSS SVC + WOREE SVC, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line
Q^^BKBM_817 | 2006-10-19 | 1 | DO NOT INVOKE_to be archived revised TNSP limit advice 18 Oct 2006
Q^^BKSB_8819 | 2006-10-19 | 1 | DO NOT INVOKE_to be archived TNSP limit advice 18 Oct 2006
Q^^BMSB_8822 | 2006-05-09 | 1 | out=Belmont-Swanbank275kVline 8822 ; (Qgen + QNI)TarLmt<=uvCalc. Tarong limit offsets: CLTR(-10) , TRBK(-10), MELL(-20) & WOPW(-10). Specified System Normal offset =zero
Q^^CLTR_TR_CLTR | 2007-02-13 | 1 | Out = either 8810 or 8811 275kV Calvale - Tarong feeders, Tarong voltage stability limit, 275kV line Calvale to Tarong contingency equation 2006/07( Offset = -380MW )
Q^^CLTR_TR_SBE | 2007-02-13 | 1 | Out = either 8810 or 8811 275kV Calvale - Tarong feeders, Tarong voltage stability limit, Swanbank E contingency equation 2006/07 , 10000 Washout applied when Swanbank E not in service. ( Offset = -270MW )
Q^^CLTR_TR_ST | 2007-02-13 | 2 | Out= either 8810 or 8811 275kV Calvale - Tarong feeders, STPASA only, (Qgen + QNI)TarLmt<=uvCalc. Single contingency on any one of the four following 275kV feeders: CLTR , TRBK, MELL & WOPW. ( Offset = -380MW )
Q^^CLTR_TR_TRBK | 2007-02-13 | 1 | Out = either 8810 or 8811 275kV Calvale - Tarong feeders , Tarong voltage stability limit, 275kV line Tarong to Blackwall contingency equation 2006/07, ( Offset = -250MW )
Q^^CLTR_TR_WOPW | 2007-02-13 | 1 | Out = either 8810 or 8811 275kV Calvale - Tarong feeders , Tarong voltage stability limit, 275kV line Woolooga to Palmwoods contingency equation 2006/07( Offset = -270MW )
Q^^CLTR_TR_WV | 2007-02-13 | 1 | Out = either 8810 or 8811 275kV Calvale - Tarong feeders, Tarong voltage stability limit, Wivenhoe contingency equation 2006/07, 10000 Washout applied when there are no wivenhoe units in service.( Offset = -270MW )
Q^^LL_BUS | 2006-05-02 | 1 | Out= Loganlea 275kV bus, Tarong voltage collapse limit, Tarong limit offsets: MELL (-60)
Q^^LL_TX | 2007-01-29 | 1 | DO NOT INVOKE TO BE ARCHIVED
Q^^METR_8812 | 2006-05-02 | 1 | out=Mt.England - Tarong 275kV line 8812 ; (Qgen + QNI) TarLmt<=uvCalc. Tarong limit offsets: CLTR(-105) , TRBK(-95), MELL(-125) & WOPW(-110). Specified System Normal offset =zero
Q^^MR5T_TR_CLTR_S_A | 2008-03-26 | 1 | Out = Middle Ridge No.5 transformer, 110kV loop H14 to T135 closed, ( offset -100 MW) Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer.( Equation 1 of 4 )
Q^^MR5T_TR_CLTR_S_B | 2008-03-26 | 1 | Out = Middle Ridge No.5 transformer, 110kV loop H14 to T135 OPEN Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer.( Equation 1 of 4 )
Q^^MR5T_TR_SBE_S_A | 2008-03-26 | 1 | Out = Middle Ridge No.5 transformer, 110kV loop H14 to T135 closed, ( offset -100 MW) Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer ( Equation 2 of 4 )
Q^^MR5T_TR_SBE_S_B | 2008-03-26 | 1 | Out = Middle Ridge No.5 transformer, 110kV loop H14 to T135 OPEN, Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer ( Equation 2 of 4 )
Q^^MR5T_TR_ST_S_A | 2008-03-26 | 1 | Out = Middle Ridge No.5 transformer, 110kV loop H14 to T135 closed, ( offset -100 MW) Tarong voltage stability limit;STPASA only, (Qgen + QNI)TarLmt<=uvCalc. Single contingency on any one following 275kV feeders: CLTR , TRBK, or SBE gen , WV gen.
Q^^MR5T_TR_ST_S_B | 2008-03-26 | 1 | Out = Middle Ridge No.5 transformer, 110kV loop H14 to T135 OPEN, Tarong voltage stability limit;STPASA only, (Qgen + QNI)TarLmt<=uvCalc. Single contingency on a 275kV feeder: CLTR or TRBK, or Swanbank E or Wivenhoe generation.
Q^^MR5T_TR_TRBK_S_A | 2008-03-26 | 1 | Out = Middle Ridge No.5 transformer, 110kV loop H14 to T135 closed, ( offset -260 MW) Tarong voltage stability limit, Tarong - Blackwall contingency equation 2007/08 Summer ( Equation 4 of 4 )
Q^^MR5T_TR_TRBK_S_B | 2008-03-26 | 1 | Out = Middle Ridge No.5 transformer, 110kV loop H14 to T135 OPEN, ( offset -160 MW) Tarong voltage stability limit, Tarong - Blackwall contingency equation 2007/08 Summer ( Equation 4 of 4 )
Q^^MR5T_TR_WV_S_A | 2008-03-26 | 1 | Out = Middle Ridge No.5 transformer, 110kV loop H14 to T135 closed, ( offset -100 MW) Tarong voltage stability limit, Wivenhoe generator contingency equation 2007/08 Summer. ( Equation 3 of 4 )
Q^^MR5T_TR_WV_S_B | 2008-03-26 | 1 | Out = Middle Ridge No.5 transformer, 110kV loop H14 to T135 OPEN, Tarong voltage stability limit, Wivenhoe generator contingency equation 2007/08 Summer. ( Equation 3 of 4 )
Q^^NIL_TR_CLTR_S | 2008-03-26 | 1 | Out = Nil, Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 )
Q^^NIL_TR_CLTR_SH | 2007-11-27 | 1 | Out = Nil , Tarong voltage stability limit, 275kV line Calvale to Tarong contingency equation 2006/07 Shoulder Season post SEQ reactive plant augmentation.
Q^^NIL_TR_CLTR_W | 2007-07-05 | 1 | Out = Nil , Tarong voltage stability limit, 275kV line Calvale to Tarong contingency equation 2006/07 winter implementation
Q^^NIL_TR_CLTR |  |  | Out = Nil, Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 ) and 275kV line Calvale to Tarong contingency equation 2006/07 winter implementation
Q^^NIL_TR_SBE | 2008-12-16 | 1 | Out = Nil, Tarong voltage stability limit, Swanbank E contingency equation, 2008/09 Summer Season
Q^^NIL_TR_SBE_S | 2008-03-26 | 1 | Out = Nil, Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation. ( Equation 2 of 4 )
Q^^NIL_TR_SBE_SH | 2007-11-27 | 1 | Out = Nil , Tarong voltage stability limit, Swanbank E contingency equation 2006/07 Shoulder Season post SEQ reactive plant augmentation, 10000 Washout applied when Swanbank E not in service.
Q^^NIL_TR_SBE_W | 2007-07-05 | 2 | Out = Nil , Tarong voltage stability limit, Swanbank E contingency equation 2006/07 winter 2007 implementation, 10000 Washout applied when Swanbank E not in service.
Q^^NIL_TR_ST | 2008-03-26 | 1 | out=Nil system normal ;STPASA only, (Qgen + QNI)TarLmt<=uvCalc. Single contingency on any one of the four following 275kV feeders: CLTR , TRBK, or SBE gen, WV Gen.
Q^^NIL_TR_TRBK | 2008-12-16 | 1 | Out = Nil, Tarong voltage stability limit, Tarong-Blackwall contingency equation, 2008/09 Summer Season
Q^^NIL_TR_TRBK_S | 2008-03-26 | 1 | Out = Nil, Tarong voltage stability limit, Tarong - Blackwall contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation. ( Equation 4 of 4 )
Q^^NIL_TR_TRBK_SH | 2007-11-27 | 1 | Out = Nil , Tarong voltage stability limit, 275kV line Tarong to Blackwall contingency equation 2007 (Shoulder Season post SEQ reactive plant augmentation )
Q^^NIL_TR_TRBK_W | 2007-07-05 | 1 | Out = Nil , Tarong voltage stability limit, 275kV line Tarong to Blackwall contingency equation 2007 (winter implementation )
Q^^NIL_TR_WOPW | 2009-11-17 | 2 | Out = Nil, Tarong voltage stability limit, Woolooga-Palmwoods contingency equation, 2009/10 version
Q^^NIL_TR_WOPW_SH | 2007-11-27 | 1 | Out = 275kV line 875 or 827 Tarong - Blackwall , Tarong voltage stability limit, 275kV line Woolooga to Palmwoods contingency equation 2006/07 (Shoulder Season post SEQ reactive plant augmentation)
Q^^NIL_TR_WOPW_W | 2007-07-05 | 1 | Out = 275kV line 875 or 827 Tarong - Blackwall , Tarong voltage stability limit, 275kV line Woolooga to Palmwoods contingency equation 2006/07 (winter implementation)
Q^^NIL_TR_WV | 2008-12-16 | 1 | Out = Nil, Tarong voltage stability limit, Wivenhoe contingency equation, 2008/09 Summer Season
Q^^NIL_TR_WV_S | 2008-03-26 | 1 | Out = Nil, Tarong voltage stability limit, Wivenhoe generator contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation. ( Equation 3 of 4 )
Q^^NIL_TR_WV_SH | 2007-11-27 | 1 | Out = 275kV line 875 or 827 Tarong - Blackwall , Tarong voltage stability limit, Wivenhoe contingency equation 2006/07, 10000 Washout applied when there are no wivenhoe units in service.( Shoulder Season post SEQ reactive plant augmentation )
Q^^NIL_TR_WV_W | 2007-07-05 | 1 | Out = 275kV line 875 or 827 Tarong - Blackwall , Tarong voltage stability limit, Wivenhoe contingency equation 2006/07, 10000 Washout applied when there are no wivenhoe units in service.( WINTER IMPLEMENTATION )
Q^^TR_CLTR_OFFSET-50 | 2007-02-20 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, 275kV line Calvale to Tarong contingency equation 2006/07
Q^^TR_CLTR_SH_-100 | 2007-09-20 | 1 | Nominated Offset -100MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Calvale - Tarong equation.
Q^^TR_CLTR_SH_-150 | 2007-09-20 | 1 | Nominated Offset -150MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Calvale - Tarong equation.
Q^^TR_CLTR_SH_-200 | 2007-09-20 | 1 | Nominated Offset -200MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Calvale - Tarong equation.
Q^^TR_CLTR_SH_-250 | 2007-09-20 | 1 | Nominated Offset -250MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Calvale - Tarong equation.
Q^^TR_CLTR_SH_-300 | 2007-09-20 | 1 | Nominated Offset -300MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Calvale - Tarong equation.
Q^^TR_CLTR_SH_-350 | 2007-09-20 | 1 | Nominated Offset -350MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Calvale - Tarong equation.
Q^^TR_CLTR_SH_-400 | 2007-09-20 | 1 | Nominated Offset -400MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Calvale - Tarong equation.
Q^^TR_CLTR_SH_-450 | 2007-09-20 | 1 | Nominated Offset -450MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Calvale - Tarong equation.
Q^^TR_CLTR_SH_-50 | 2007-09-20 | 1 | Nominated Offset -50MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Calvale - Tarong equation.
Q^^TR_CLTR_S_-100 | 2008-01-23 | 1 | Nominated Offset -100MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 )
Q^^TR_CLTR_S_-150 | 2008-01-23 | 1 | Nominated Offset -150MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 )
Q^^TR_CLTR_S_-200 | 2008-01-23 | 2 | Nominated Offset -200MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 )
Q^^TR_CLTR_S_-250 | 2008-01-23 | 1 | Nominated Offset -250MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 )
Q^^TR_CLTR_S_-300 | 2008-01-23 | 1 | Nominated Offset -300MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 )
Q^^TR_CLTR_S_-350 | 2008-01-23 | 1 | Nominated Offset -350MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 )
Q^^TR_CLTR_S_-400 | 2008-01-23 | 1 | Nominated Offset -400MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 )
Q^^TR_CLTR_S_-450 | 2008-01-23 | 1 | Nominated Offset -450MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 )
Q^^TR_CLTR_S_-50 | 2008-01-23 | 1 | Nominated Offset -50MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 )
Q^^TR_CLTR_S_-500 | 2008-01-23 | 1 | Nominated Offset -500MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 )
Q^^TR_CLTR_S_0 | 2008-06-25 | 1 | Nominated Offset -0MW, ( Summer 2007/08 implementation of Base Equation ), Tarong voltage stability limit, Calvale - Tarong contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 1 of 4 )
Q^^TR_CLTR_W_-100 | 2007-07-13 | 1 | Nominated Offset -100MW, Tarong voltage stability limit, Calvale-Tarong contingency equation ( Winter 2007 Implementation )
Q^^TR_CLTR_W_-150 | 2007-07-13 | 1 | Nominated Offset -150MW, Tarong voltage stability limit, Calvale-Tarong contingency equation ( Winter 2007 Implementation )
Q^^TR_CLTR_W_-200 | 2007-07-13 | 1 | Nominated Offset -200MW, Tarong voltage stability limit, Calvale-Tarong contingency equation ( Winter 2007 Implementation )
Q^^TR_CLTR_W_-250 | 2007-07-13 | 1 | Nominated Offset -250MW, Tarong voltage stability limit, Calvale-Tarong contingency equation ( Winter 2007 Implementation )
Q^^TR_CLTR_W_-300 | 2007-07-13 | 1 | Nominated Offset -300MW, Tarong voltage stability limit, Calvale-Tarong contingency equation ( Winter 2007 Implementation )
Q^^TR_CLTR_W_-350 | 2007-07-13 | 1 | Nominated Offset -350MW, Tarong voltage stability limit, Calvale-Tarong contingency equation ( Winter 2007 Implementation )
Q^^TR_CLTR_W_-400 | 2007-07-13 | 1 | Nominated Offset -400MW, Tarong voltage stability limit, Calvale-Tarong contingency equation ( Winter 2007 Implementation )
Q^^TR_CLTR_W_-450 | 2007-07-13 | 1 | Nominated Offset -450MW, Tarong voltage stability limit, Calvale-Tarong contingency equation ( Winter 2007 Implementation )
Q^^TR_CLTR_W_-50 | 2007-07-13 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Calvale-Tarong contingency equation ( Winter 2007 Implementation )
Q^^TR_SBE_-050 | 2008-12-16 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Swanbank E contingency equation, Summer 2008/09
Q^^TR_SBE_-100 | 2008-12-16 | 1 | Nominated Offset -100MW, Tarong voltage stability limit, Swanbank E contingency equation, Summer 2008/09
Q^^TR_SBE_-150 | 2008-12-16 | 1 | Nominated Offset -150MW, Tarong voltage stability limit, Swanbank E contingency equation, Summer 2008/09
Q^^TR_SBE_-200 | 2008-12-16 | 1 | Nominated Offset -200MW, Tarong voltage stability limit, Swanbank E contingency equation, Summer 2008/09
Q^^TR_SBE_-250 | 2008-12-16 | 1 | Nominated Offset -250MW, Tarong voltage stability limit, Swanbank E contingency equation, Summer 2008/09
Q^^TR_SBE_-300 | 2008-12-16 | 1 | Nominated Offset -300MW, Tarong voltage stability limit, Swanbank E contingency equation, Summer 2008/09
Q^^TR_SBE_-350 | 2008-12-16 | 1 | Nominated Offset -350MW, Tarong voltage stability limit, Swanbank E contingency equation, Summer 2008/09
Q^^TR_SBE_-400 | 2008-12-16 | 1 | Nominated Offset -400MW, Tarong voltage stability limit, Swanbank E contingency equation, Summer 2008/09
Q^^TR_SBE_-450 | 2008-12-16 | 1 | Nominated Offset -450MW, Tarong voltage stability limit, Swanbank E contingency equation, Summer 2008/09
Q^^TR_SBE_-500 | 2008-12-16 | 1 | Nominated Offset -500MW, Tarong voltage stability limit, Swanbank E contingency equation, Summer 2008/09
Q^^TR_SBE_OFSET-50 | 2007-04-11 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Swanbank E contingency equation. ( Version 2 06/07 ), 10000 Washout applied when Swanbank E not in service.
Q^^TR_SBE_SH_-100 | 2007-09-20 | 1 | Nominated Offset -100MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Swanbank E equation.
Q^^TR_SBE_SH_-150 | 2007-09-20 | 1 | Nominated Offset -150MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Swanbank E equation.
Q^^TR_SBE_SH_-200 | 2007-09-20 | 1 | Nominated Offset -200MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Swanbank E equation.
Q^^TR_SBE_SH_-250 | 2007-09-20 | 1 | Nominated Offset -250MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Swanbank E equation.
Q^^TR_SBE_SH_-300 | 2007-09-20 | 1 | Nominated Offset -300MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Swanbank E equation.
Q^^TR_SBE_SH_-350 | 2007-09-20 | 1 | Nominated Offset -350MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Swanbank E equation.
Q^^TR_SBE_SH_-400 | 2007-09-20 | 1 | Nominated Offset -400MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Swanbank E equation.
Q^^TR_SBE_SH_-450 | 2007-09-20 | 1 | Nominated Offset -450MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Swanbank E equation.
Q^^TR_SBE_SH_-50 | 2007-09-20 | 1 | Nominated Offset -50MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Swanbank E equation.
Q^^TR_SBE_S_-100 | 2008-01-23 | 1 | Nominated Offset -100MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 2 of 4 )
Q^^TR_SBE_S_-150 | 2008-01-23 | 1 | Nominated Offset -150MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 2 of 4 )
Q^^TR_SBE_S_-200 | 2008-01-23 | 2 | Nominated Offset -200MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 2 of 4 )
Q^^TR_SBE_S_-250 | 2008-01-23 | 1 | Nominated Offset -250MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 2 of 4 )
Q^^TR_SBE_S_-300 | 2008-01-23 | 1 | Nominated Offset -300MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 2 of 4 )
Q^^TR_SBE_S_-350 | 2008-01-23 | 1 | Nominated Offset -350MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 2 of 4 )
Q^^TR_SBE_S_-400 | 2008-01-23 | 1 | Nominated Offset -400MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 2 of 4 )
Q^^TR_SBE_S_-450 | 2008-01-23 | 1 | Nominated Offset -450MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 2 of 4 )
Q^^TR_SBE_S_-50 | 2008-01-23 | 1 | Nominated Offset -50MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 2 of 4 )
Q^^TR_SBE_S_-500 | 2008-01-23 | 1 | Nominated Offset -500MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 2 of 4 )
Q^^TR_SBE_S_0 | 2008-06-25 | 1 | Nominated Offset -0MW, ( Summer 2007/08 implementation of Base Equation ), Tarong voltage stability limit, Swanbank E contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 2 of 4 )
Q^^TR_SBE_W_-100 | 2007-07-13 | 1 | Nominated Offset -100MW, Tarong voltage stability limit, Swanbank E contingency equation ( Winter 2007 Implementation )
Q^^TR_SBE_W_-150 | 2007-07-13 | 1 | Nominated Offset -150MW, Tarong voltage stability limit, Swanbank E contingency equation ( Winter 2007 Implementation )
Q^^TR_SBE_W_-200 | 2007-07-13 | 1 | Nominated Offset -200MW, Tarong voltage stability limit, Swanbank E contingency equation ( Winter 2007 Implementation )
Q^^TR_SBE_W_-250 | 2007-07-13 | 1 | Nominated Offset -250MW, Tarong voltage stability limit, Swanbank E contingency equation ( Winter 2007 Implementation )
Q^^TR_SBE_W_-300 | 2007-07-13 | 1 | Nominated Offset -300MW, Tarong voltage stability limit, Swanbank E contingency equation ( Winter 2007 Implementation )
Q^^TR_SBE_W_-350 | 2007-07-13 | 1 | Nominated Offset -350MW, Tarong voltage stability limit, Swanbank E contingency equation ( Winter 2007 Implementation )
Q^^TR_SBE_W_-400 | 2007-07-13 | 1 | Nominated Offset -400MW, Tarong voltage stability limit, Swanbank E contingency equation ( Winter 2007 Implementation )
Q^^TR_SBE_W_-450 | 2007-07-13 | 1 | Nominated Offset -450MW, Tarong voltage stability limit, Swanbank E contingency equation ( Winter 2007 Implementation )
Q^^TR_SBE_W_-50 | 2007-07-13 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Swanbank E contingency equation ( Winter 2007 Implementation )
Q^^TR_ST_W_-100 | 2007-07-13 | 1 | Nominated Offset -100MW, ( WINTER Implementation ), Tarong voltage stability limit, 275kV line contingencies , Calv-Tar, Wool-PalmW , Tar-Blkw and generatotrs SWE and Wiv.
Q^^TR_ST_W_-150 | 2007-07-13 | 1 | STPASA Nominated Offset -150MW, ( WINTER Implementation ), Tarong voltage stability limit, 275kV line contingencies , Calv-Tar, Wool-PalmW , Tar-Blkw and generatotrs SWE and Wiv.
Q^^TR_ST_W_-200 | 2007-07-13 | 1 | Nominated Offset -200MW, ( WINTER Implementation ), Tarong voltage stability limit, 275kV line contingencies , Calv-Tar, Wool-PalmW , Tar-Blkw and generatotrs SWE and Wiv.
Q^^TR_ST_W_-250 | 2007-07-13 | 1 | Nominated Offset -250MW, ( WINTER Implementation ), Tarong voltage stability limit, 275kV line contingencies , Calv-Tar, Wool-PalmW , Tar-Blkw and generatotrs SWE and Wiv.
Q^^TR_ST_W_-300 | 2007-07-13 | 1 | Nominated Offset -300MW, ( WINTER Implementation ), Tarong voltage stability limit, 275kV line contingencies , Calv-Tar, Wool-PalmW , Tar-Blkw and generatotrs SWE and Wiv.
Q^^TR_ST_W_-350 | 2007-07-13 | 1 | Nominated Offset -350MW, ( WINTER Implementation ), Tarong voltage stability limit, 275kV line contingencies , Calv-Tar, Wool-PalmW , Tar-Blkw and generatotrs SWE and Wiv.
Q^^TR_ST_W_-400 | 2007-07-13 | 1 | Nominated Offset -400MW, ( WINTER Implementation ), Tarong voltage stability limit, 275kV line contingencies , Calv-Tar, Wool-PalmW , Tar-Blkw and generatotrs SWE and Wiv.
Q^^TR_ST_W_-450 | 2007-07-13 | 1 | Nominated Offset -450MW, ( WINTER Implementation ), Tarong voltage stability limit, 275kV line contingencies , Calv-Tar, Wool-PalmW , Tar-Blkw and generatotrs SWE and Wiv.
Q^^TR_ST_W_-50 | 2007-07-13 | 1 | STPASA Nominated Offset -50MW, ( WINTER Implementation ), Tarong voltage stability limit, 275kV line contingencies , Calv-Tar, Wool-PalmW , Tar-Blkw and generatotrs SWE and Wiv.
Q^^TR_TRBK_-050 | 2008-12-16 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Tarong-Blackwall contingency equation, Summer 2008/09
Q^^TR_TRBK_-100 | 2008-12-16 | 1 | Nominated Offset -100MW, Tarong voltage stability limit, Tarong-Blackwall contingency equation, Summer 2008/09
Q^^TR_TRBK_-150 | 2008-12-16 | 1 | Nominated Offset -150MW, Tarong voltage stability limit, Tarong-Blackwall contingency equation, Summer 2008/09
Q^^TR_TRBK_-200 | 2008-12-16 | 1 | Nominated Offset -200MW, Tarong voltage stability limit, Tarong-Blackwall contingency equation, Summer 2008/09
Q^^TR_TRBK_-250 | 2008-12-16 | 1 | Nominated Offset -250MW, Tarong voltage stability limit, Tarong-Blackwall contingency equation, Summer 2008/09
Q^^TR_TRBK_-300 | 2008-12-16 | 1 | Nominated Offset -300MW, Tarong voltage stability limit, Tarong-Blackwall contingency equation, Summer 2008/09
Q^^TR_TRBK_-350 | 2008-12-16 | 1 | Nominated Offset -350MW, Tarong voltage stability limit, Tarong-Blackwall contingency equation, Summer 2008/09
Q^^TR_TRBK_-400 | 2008-12-16 | 1 | Nominated Offset -400MW, Tarong voltage stability limit, Tarong-Blackwall contingency equation, Summer 2008/09
Q^^TR_TRBK_-450 | 2008-12-16 | 1 | Nominated Offset -450MW, Tarong voltage stability limit, Tarong-Blackwall contingency equation, Summer 2008/09
Q^^TR_TRBK_-500 | 2008-12-16 | 1 | Nominated Offset -500MW, Tarong voltage stability limit, Tarong-Blackwall contingency equation, Summer 2008/09
Q^^TR_TRBK_OFSET-50 | 2007-04-11 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Tarong - Blackwall contingency equation. ( Version 2 06/07 )
Q^^TR_TRBK_SH_-100 | 2007-09-20 | 1 | Nominated Offset -100MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Tarong - Blackwall equation.
Q^^TR_TRBK_SH_-150 | 2007-09-20 | 1 | Nominated Offset -150MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Tarong - Blackwall equation.
Q^^TR_TRBK_SH_-200 | 2007-09-20 | 1 | Nominated Offset -200MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Tarong - Blackwall equation.
Q^^TR_TRBK_SH_-250 | 2007-09-20 | 1 | Nominated Offset -250MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Tarong - Blackwall equation.
Q^^TR_TRBK_SH_-300 | 2007-09-20 | 1 | Nominated Offset -300MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Tarong - Blackwall equation.
Q^^TR_TRBK_SH_-350 | 2007-09-20 | 1 | Nominated Offset -350MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Tarong - Blackwall equation.
Q^^TR_TRBK_SH_-400 | 2007-09-20 | 1 | Nominated Offset -400MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Tarong - Blackwall equation.
Q^^TR_TRBK_SH_-450 | 2007-09-20 | 1 | Nominated Offset -450MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Tarong - Blackwall equation.
Q^^TR_TRBK_SH_-50 | 2007-09-20 | 1 | Nominated Offset -50MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Tarong - Blackwall equation.
Q^^TR_TRBK_S_-100 | 2008-06-25 | 1 | Nominated Offset -100MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Tarong - Blackwall contingency equation post 275kV Greenbank - Middle Ridge line augmentation.( Equation 4 of 4 )
Q^^TR_TRBK_S_-150 | 2008-06-25 | 1 | Nominated Offset -150MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Tarong - Blackwall contingency equation post 275kV Greenbank - Middle Ridge line augmentation.( Equation 4 of 4 )
Q^^TR_TRBK_S_-200 | 2008-06-25 | 1 | Nominated Offset -200MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Tarong - Blackwall contingency equation post 275kV Greenbank - Middle Ridge line augmentation.( Equation 4 of 4 )
Q^^TR_TRBK_S_-250 | 2008-06-25 | 1 | Nominated Offset -250MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Tarong - Blackwall contingency equation post 275kV Greenbank - Middle Ridge line augmentation.( Equation 4 of 4 )
Q^^TR_TRBK_S_-300 | 2008-06-25 | 1 | Nominated Offset -300MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Tarong - Blackwall contingency equation post 275kV Greenbank - Middle Ridge line augmentation.( Equation 4 of 4 )
Q^^TR_TRBK_S_-350 | 2008-06-25 | 1 | Nominated Offset -350MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Tarong - Blackwall contingency equation post 275kV Greenbank - Middle Ridge line augmentation.( Equation 4 of 4 )
Q^^TR_TRBK_S_-400 | 2008-06-25 | 1 | Nominated Offset -400MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Tarong - Blackwall contingency equation post 275kV Greenbank - Middle Ridge line augmentation.( Equation 4 of 4 )
Q^^TR_TRBK_S_-450 | 2008-06-25 | 1 | Nominated Offset -450MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Tarong - Blackwall contingency equation post 275kV Greenbank - Middle Ridge line augmentation.( Equation 4 of 4 )
Q^^TR_TRBK_S_-50 | 2008-06-25 | 1 | Nominated Offset -50MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Tarong - Blackwall contingency equation post 275kV Greenbank - Middle Ridge line augmentation.( Equation 4 of 4 )
Q^^TR_TRBK_S_-500 | 2008-06-25 | 1 | Nominated Offset -500MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Tarong - Blackwall contingency equation post 275kV Greenbank - Middle Ridge line augmentation.( Equation 4 of 4 )
Q^^TR_TRBK_S_0 | 2008-06-25 | 1 | Nominated Offset -0MW, ( Summer 2007/08 implementation of Base Equation ), Tarong voltage stability limit, Tarong - Blackwall contingency equation post 275kV Greenbank - Middle Ridge line augmentation.( Equation 4 of 4 )
Q^^TR_TRBK_W_-100 | 2007-07-13 | 1 | Nominated Offset -100MW, Tarong voltage stability limit, Tarong - Blackwall contingency equation ( Winter 2007 Implementation )
Q^^TR_TRBK_W_-150 | 2007-07-13 | 1 | Nominated Offset -150MW, Tarong voltage stability limit, Tarong - Blackwall contingency equation ( Winter 2007 Implementation )
Q^^TR_TRBK_W_-200 | 2007-07-13 | 1 | Nominated Offset -200MW, Tarong voltage stability limit, Tarong - Blackwall contingency equation ( Winter 2007 Implementation )
Q^^TR_TRBK_W_-250 | 2007-07-13 | 1 | Nominated Offset -250MW, Tarong voltage stability limit, Tarong - Blackwall contingency equation ( Winter 2007 Implementation )
Q^^TR_TRBK_W_-300 | 2007-07-13 | 1 | Nominated Offset -300MW, Tarong voltage stability limit, Tarong - Blackwall contingency equation ( Winter 2007 Implementation )
Q^^TR_TRBK_W_-350 | 2007-07-13 | 1 | Nominated Offset -350MW, Tarong voltage stability limit, Tarong - Blackwall contingency equation ( Winter 2007 Implementation )
Q^^TR_TRBK_W_-400 | 2007-07-13 | 1 | Nominated Offset -400MW, Tarong voltage stability limit, Tarong - Blackwall contingency equation ( Winter 2007 Implementation )
Q^^TR_TRBK_W_-450 | 2007-07-13 | 1 | Nominated Offset -450MW, Tarong voltage stability limit, Tarong - Blackwall contingency equation ( Winter 2007 Implementation )
Q^^TR_TRBK_W_-50 | 2007-07-13 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Tarong - Blackwall contingency equation ( Winter 2007 Implementation )
Q^^TR_WOPW_-050 | 2008-12-16 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Woolooga-Palmwoods contingency equation, Summer 2008/09
Q^^TR_WOPW_-100 | 2008-12-16 | 1 | Nominated Offset -100MW, Tarong voltage stability limit, Woolooga-Palmwoods contingency equation, Summer 2008/09
Q^^TR_WOPW_-150 | 2008-12-16 | 1 | Nominated Offset -150MW, Tarong voltage stability limit, Woolooga-Palmwoods contingency equation, Summer 2008/09
Q^^TR_WOPW_-200 | 2008-12-16 | 1 | Nominated Offset -200MW, Tarong voltage stability limit, Woolooga-Palmwoods contingency equation, Summer 2008/09
Q^^TR_WOPW_-250 | 2008-12-16 | 1 | Nominated Offset -250MW, Tarong voltage stability limit, Woolooga-Palmwoods contingency equation, Summer 2008/09
Q^^TR_WOPW_-300 | 2008-12-16 | 1 | Nominated Offset -300MW, Tarong voltage stability limit, Woolooga-Palmwoods contingency equation, Summer 2008/09
Q^^TR_WOPW_-350 | 2008-12-16 | 1 | Nominated Offset -350MW, Tarong voltage stability limit, Woolooga-Palmwoods contingency equation, Summer 2008/09
Q^^TR_WOPW_-400 | 2008-12-16 | 1 | Nominated Offset -400MW, Tarong voltage stability limit, Woolooga-Palmwoods contingency equation, Summer 2008/09
Q^^TR_WOPW_-450 | 2008-12-16 | 1 | Nominated Offset -450MW, Tarong voltage stability limit, Woolooga-Palmwoods contingency equation, Summer 2008/09
Q^^TR_WOPW_-500 | 2008-12-16 | 1 | Nominated Offset -500MW, Tarong voltage stability limit, Woolooga-Palmwoods contingency equation, Summer 2008/09
Q^^TR_WOPW_OFSET-130 | 2007-03-14 | 1 | Nominated Offset -130MW, Tarong voltage stability limit, Woolooga -palmwoods contingency equation. ( Version 2 06/07 )
Q^^TR_WOPW_OFSET-50 | 2007-04-11 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Woolooga -Palmwoods contingency equation. ( Version 2 06/07 )
Q^^TR_WOPW_SH_-100 | 2007-09-20 | 1 | Nominated Offset -100MW, ( 20007 Shoulder Season Implementation ), Tarong voltage stability limit, Woolooga - Palmwoods equation.
Q^^TR_WOPW_SH_-150 | 2007-09-20 | 1 | Nominated Offset -150MW, ( 20007 Shoulder Season Implementation ), Tarong voltage stability limit, Woolooga - Palmwoods equation.
Q^^TR_WOPW_SH_-200 | 2007-09-20 | 1 | Nominated Offset -200MW, ( 20007 Shoulder Season Implementation ), Tarong voltage stability limit, Woolooga - Palmwoods equation.
Q^^TR_WOPW_SH_-250 | 2007-09-20 | 1 | Nominated Offset -250MW, ( 20007 Shoulder Season Implementation ), Tarong voltage stability limit, Woolooga - Palmwoods equation.
Q^^TR_WOPW_SH_-300 | 2007-09-20 | 1 | Nominated Offset -300MW, ( 20007 Shoulder Season Implementation ), Tarong voltage stability limit, Woolooga - Palmwoods equation.
Q^^TR_WOPW_SH_-350 | 2007-09-20 | 1 | Nominated Offset -350MW, ( 20007 Shoulder Season Implementation ), Tarong voltage stability limit, Woolooga - Palmwoods equation.
Q^^TR_WOPW_SH_-400 | 2007-09-20 | 1 | Nominated Offset -400MW, ( 20007 Shoulder Season Implementation ), Tarong voltage stability limit, Woolooga - Palmwoods equation.
Q^^TR_WOPW_SH_-450 | 2007-09-20 | 1 | Nominated Offset -450MW, ( 20007 Shoulder Season Implementation ), Tarong voltage stability limit, Woolooga - Palmwoods equation.
Q^^TR_WOPW_SH_-50 | 2007-09-20 | 1 | Nominated Offset -50MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Woolooga - Palmwoods equation.
Q^^TR_WOPW_W_-100 | 2007-07-13 | 1 | Nominated Offset -100MW, Tarong voltage stability limit, Woolooga - Palmwoods contingency equation ( Winter 2007 Implementation )
Q^^TR_WOPW_W_-150 | 2007-07-13 | 1 | Nominated Offset -150MW, Tarong voltage stability limit, Woolooga - Palmwoods contingency equation ( Winter 2007 Implementation )
Q^^TR_WOPW_W_-200 | 2007-07-13 | 1 | Nominated Offset -200MW, Tarong voltage stability limit, Woolooga - Palmwoods contingency equation ( Winter 2007 Implementation )
Q^^TR_WOPW_W_-250 | 2007-07-13 | 1 | Nominated Offset -250MW, Tarong voltage stability limit, Woolooga - Palmwoods contingency equation ( Winter 2007 Implementation )
Q^^TR_WOPW_W_-300 | 2007-07-13 | 1 | Nominated Offset -300MW, Tarong voltage stability limit, Woolooga - Palmwoods contingency equation ( Winter 2007 Implementation )
Q^^TR_WOPW_W_-350 | 2007-07-13 | 1 | Nominated Offset -350MW, Tarong voltage stability limit, Woolooga - Palmwoods contingency equation ( Winter 2007 Implementation )
Q^^TR_WOPW_W_-400 | 2007-07-13 | 1 | Nominated Offset -400MW, Tarong voltage stability limit, Woolooga - Palmwoods contingency equation ( Winter 2007 Implementation )
Q^^TR_WOPW_W_-450 | 2007-07-13 | 1 | Nominated Offset -450MW, Tarong voltage stability limit, Woolooga - Palmwoods contingency equation ( Winter 2007 Implementation )
Q^^TR_WOPW_W_-50 | 2007-07-13 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Woolooga - Palmwoods contingency equation ( Winter 2007 Implementation )
Q^^TR_WV_-050 | 2008-12-16 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Wivenhoe contingency equation, Summer 2008/09
Q^^TR_WV_-100 | 2008-12-16 | 1 | Nominated Offset -100MW, Tarong voltage stability limit, Wivenhoe contingency equation, Summer 2008/09
Q^^TR_WV_-150 | 2008-12-16 | 1 | Nominated Offset -150MW, Tarong voltage stability limit, Wivenhoe contingency equation, Summer 2008/09
Q^^TR_WV_-200 | 2008-12-16 | 1 | Nominated Offset -200MW, Tarong voltage stability limit, Wivenhoe contingency equation, Summer 2008/09
Q^^TR_WV_-250 | 2008-12-16 | 1 | Nominated Offset -250MW, Tarong voltage stability limit, Wivenhoe contingency equation, Summer 2008/09
Q^^TR_WV_-300 | 2008-12-16 | 1 | Nominated Offset -300MW, Tarong voltage stability limit, Wivenhoe contingency equation, Summer 2008/09
Q^^TR_WV_-350 | 2008-12-16 | 1 | Nominated Offset -350MW, Tarong voltage stability limit, Wivenhoe contingency equation, Summer 2008/09
Q^^TR_WV_-400 | 2008-12-16 | 1 | Nominated Offset -400MW, Tarong voltage stability limit, Wivenhoe contingency equation, Summer 2008/09
Q^^TR_WV_-450 | 2008-12-16 | 1 | Nominated Offset -450MW, Tarong voltage stability limit, Wivenhoe contingency equation, Summer 2008/09
Q^^TR_WV_-500 | 2008-12-16 | 1 | Nominated Offset -500MW, Tarong voltage stability limit, Wivenhoe contingency equation, Summer 2008/09
Q^^TR_WV_OFFSET-50 | 2007-04-11 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Wivenhoe Generator contingency equation. ( Version 2 06/07 ), 10000 Washout applied when there are no wivenhoe units in service.
Q^^TR_WV_SH_-100 | 2007-09-20 | 1 | Nominated Offset -100MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Wivenhoe equation.
Q^^TR_WV_SH_-150 | 2007-09-20 | 1 | Nominated Offset -150MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Wivenhoe equation.
Q^^TR_WV_SH_-200 | 2007-09-20 | 1 | Nominated Offset -200MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Wivenhoe equation.
Q^^TR_WV_SH_-250 | 2007-09-20 | 1 | Nominated Offset -250MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Wivenhoe equation.
Q^^TR_WV_SH_-300 | 2007-09-20 | 1 | Nominated Offset -300MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Wivenhoe equation.
Q^^TR_WV_SH_-350 | 2007-09-20 | 1 | Nominated Offset -350MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Wivenhoe equation.
Q^^TR_WV_SH_-400 | 2007-09-20 | 1 | Nominated Offset -400MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Wivenhoe equation.
Q^^TR_WV_SH_-450 | 2007-09-20 | 1 | Nominated Offset -450MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Wivenhoe equation.
Q^^TR_WV_SH_-50 | 2007-09-20 | 1 | Nominated Offset -50MW, ( 2007 Shoulder Season Implementation ), Tarong voltage stability limit, Wivenhoe equation.
Q^^TR_WV_S_-100 | 2008-01-23 | 1 | Nominated Offset -100MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Wivenhoe contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 3 of 4 )
Q^^TR_WV_S_-150 | 2008-01-23 | 1 | Nominated Offset -150MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Wivenhoe contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 3 of 4 )
Q^^TR_WV_S_-200 | 2008-01-23 | 2 | Nominated Offset -200MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Wivenhoe contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 3 of 4 )
Q^^TR_WV_S_-250 | 2008-01-23 | 1 | Nominated Offset -250MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Wivenhoe contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 3 of 4 )
Q^^TR_WV_S_-300 | 2008-01-23 | 1 | Nominated Offset -300MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Wivenhoe contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 3 of 4 )
Q^^TR_WV_S_-350 | 2008-01-23 | 1 | Nominated Offset -350MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Wivenhoe contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 3 of 4 )
Q^^TR_WV_S_-400 | 2008-01-23 | 1 | Nominated Offset -400MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Wivenhoe contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 3 of 4 )
Q^^TR_WV_S_-450 | 2008-01-23 | 1 | Nominated Offset -450MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Wivenhoe contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 3 of 4 )
Q^^TR_WV_S_-50 | 2008-01-23 | 1 | Nominated Offset -50MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Wivenhoe contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 3 of 4 )
Q^^TR_WV_S_-500 | 2008-01-23 | 1 | Nominated Offset -500MW, ( 2007/08 Summer Implementation ), Tarong voltage stability limit, Wivenhoe contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 3 of 4 )
Q^^TR_WV_S_0 | 2008-06-25 | 1 | Nominated Offset -0MW, ( Summer 2007/08 implementation of Base Equation ), Tarong voltage stability limit, Wivenhoe contingency equation 2007/08 Summer Season post 275kV Greenbank - Middle Ridge line augmentation.( Equation 3 of 4 )
Q^^TR_WV_W_-100 | 2007-07-13 | 1 | Nominated Offset -100MW, Tarong voltage stability limit, Wivenhoe contingency equation ( Winter 2007 Implementation )
Q^^TR_WV_W_-150 | 2007-07-13 | 1 | Nominated Offset -150MW, Tarong voltage stability limit, Wivenhoe contingency equation ( Winter 2007 Implementation )
Q^^TR_WV_W_-200 | 2007-07-13 | 1 | Nominated Offset -200MW, Tarong voltage stability limit, Wivenhoe contingency equation ( Winter 2007 Implementation )
Q^^TR_WV_W_-250 | 2007-07-13 | 1 | Nominated Offset -250MW, Tarong voltage stability limit, Wivenhoe contingency equation ( Winter 2007 Implementation )
Q^^TR_WV_W_-300 | 2007-07-13 | 1 | Nominated Offset -300MW, Tarong voltage stability limit, Wivenhoe contingency equation ( Winter 2007 Implementation )
Q^^TR_WV_W_-350 | 2007-07-13 | 1 | Nominated Offset -350MW, Tarong voltage stability limit, Wivenhoe contingency equation ( Winter 2007 Implementation )
Q^^TR_WV_W_-400 | 2007-07-13 | 1 | Nominated Offset -400MW, Tarong voltage stability limit, Wivenhoe contingency equation ( Winter 2007 Implementation )
Q^^TR_WV_W_-450 | 2007-07-13 | 1 | Nominated Offset -450MW, Tarong voltage stability limit, Wivenhoe contingency equation ( Winter 2007 Implementation )
Q^^TR_WV_W_-50 | 2007-07-13 | 1 | Nominated Offset -50MW, Tarong voltage stability limit, Wivenhoe contingency equation ( Winter 2007 Implementation )
Q_0430 | 2002-02-27 | 1 | Qld C-S<=1150MW WestCorridor;Call.B&C PS.Fdr 871oos(855 cont)
Q_BP_40 | 2004-11-03 | 1 | Barcaldine Gen >= 40MW
Q_BRAEM1_0 | 2007-03-01 | 1 | Braemar unit 1 generation = 0MW. Energy <= 0MW
Q_BRAEM2_0 | 2007-03-01 | 1 | Braemar unit 2 generation = 0MW. Energy <= 0MW
Q_BRAEM3_0 | 2007-03-01 | 1 | Braemar unit 3 generation = 0MW. Energy <= 0MW
Q_BRBRA_8838 | 2009-01-09 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8838
Q_BRBRA_8839 | 2009-01-08 | 1 | Out = R2 Braemar to H47 Braemar PS 275kV line 8839
Q_BSLV | 2004-11-03 | 1 | Out=Broadsound Lilyvale 833 and 850 lines, 275kV flow into Nebo <= 700MW (132kV feeder 789 OOS)
Q_CALB_C_1 | 2003-03-11 | 1 | Qld, Callide B+C generation <=1000
Q_CALB_C_2 | 2003-03-11 | 1 | Qld, Callide B+C generation <= 900
Q_CALB_C_3 | 2003-03-11 | 1 | Qld, Callide B+C generation <= 800
Q_CLCAC_853 | 2007-07-25 | 1 | Out= 853 Calvale Callide C PS 275kV line
Q_CLCAC_854 | 2007-07-25 | 1 | Out= 854 Calvale Callide C PS 275kV line
Q_CLCB_851 | 2004-08-10 | 2 | Out= 851 Calvale Callide B PS 275kV line
Q_CLCB_852 | 2004-08-10 | 2 | Out= 852 Calvale Callide B PS 275kV line
Q_CN1060 | 2008-09-26 | 1 | Qld Central to North upper transfer limit of 1060 MW (discretionary)
Q_CN1120 | 2009-02-04 | 1 | Qld Central to North upper transfer limit of 1120 MW (discretionary)
Q_CN1450 | 2009-10-15 | 1 | Qld Central to North upper transfer limit of 1450 MW (discretionary)
Q_CNRM_7164 | 2004-08-05 | 1 | Out= 7164 Chinchilla Roma 132kV line
Q_CNRM_7174 | 2004-08-05 | 1 | Out= 7174 Chinchilla Roma 132kV line
Q_CS_0800 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 800MW (discretionary), 2008/2009 implementation
Q_CS_0900 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 900MW (discretionary), 2008/2009 implementation
Q_CS_1000 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1000MW (discretionary), 2008/2009 implementation
Q_CS_1050 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1050MW (discretionary), 2008/2009 implementation
Q_CS_1100 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1100MW (discretionary), 2008/2009 implementation
Q_CS_1150 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1150MW (discretionary), 2008/2009 implementation
Q_CS_1200 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1200MW (discretionary), 2008/2009 implementation
Q_CS_1225 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1225MW (discretionary), 2008/2009 implementation
Q_CS_1250 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1250MW (discretionary), 2008/2009 implementation
Q_CS_1275 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1275MW (discretionary), 2008/2009 implementation
Q_CS_1300 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1300MW (discretionary), 2008/2009 implementation
Q_CS_1325 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1325MW (discretionary), 2008/2009 implementation
Q_CS_1350 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1350MW (discretionary), 2008/2009 implementation
Q_CS_1375 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1375MW (discretionary), 2008/2009 implementation
Q_CS_1400 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1400MW (discretionary), 2008/2009 implementation
Q_CS_1425 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1425MW (discretionary), 2008/2009 implementation
Q_CS_1450 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1450MW (discretionary), 2008/2009 implementation
Q_CS_1475 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1475MW (discretionary), 2008/2009 implementation
Q_CS_1500 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1500MW (discretionary), 2008/2009 implementation
Q_CS_1525 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1525MW (discretionary), 2008/2009 implementation
Q_CS_1550 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1550MW (discretionary), 2008/2009 implementation
Q_CS_1575 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1575MW (discretionary), 2008/2009 implementation
Q_CS_1600 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1600MW (discretionary), 2008/2009 implementation
Q_CS_1650 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1650MW (discretionary), 2008/2009 implementation
Q_CS_1700 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1700MW (discretionary), 2008/2009 implementation
Q_CS_1750 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1750MW (discretionary), 2008/2009 implementation
Q_CS_1800 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1800MW (discretionary), 2008/2009 implementation
Q_CS_1850 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1850MW (discretionary), 2008/2009 implementation
Q_CS_1900 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1900MW (discretionary), 2008/2009 implementation
Q_CS_1950 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 1950MW (discretionary), 2008/2009 implementation
Q_CS_2000 | 2009-01-29 | 1 | Qld Central to Qld South upper transfer limit of 2000MW (discretionary), 2008/2009 implementation
Q_CVL_090 | 2003-12-15 | 1 | Discretionary Collinsville Gen >= 90MW
Q_CVL_120 | 2004-11-03 | 1 | Collinsville Gen >= 120MW
Q_CVL_150 | 2003-12-15 | 1 | Discretionary Collinsville Gen >= 150MW
Q_CV_1BUS | 2007-03-01 | 1 | Out=T37 Collinsville 1A and 1B 132kV Bus
Q_CV_2BUS | 2007-03-01 | 1 | Out=T37 Collinsville 2A and 2B 132kV Bus
Q_CV_CB4212 | 2004-08-06 | 1 | Out=Collinsville 132kV CB4212
Q_CV_CB4222 | 2004-08-06 | 1 | Out=Collinsville 132kV CB4222
Q_CV_CB4232 | 2004-08-06 | 1 | Out=Collinsville 132kV CB4232
Q_CV_CB4242 | 2004-08-06 | 1 | Out=Collinsville 132kV CB4242
Q_CV_CB4252 | 2004-08-06 | 1 | Out=Collinsville 132kV CB4252
Q_FNQ_100 | 2004-09-16 | 1 | Qld, FNQ limit of 100MW
Q_FNQ_110 | 2004-07-09 | 1 | Qld, FNQ limit of 110MW
Q_FNQ_120 | 2003-11-25 | 1 | Qld, FNQ limit of 120MW
Q_FNQ_130 | 2003-11-25 | 1 | Qld, FNQ limit of 130MW
Q_FNQ_140 | 2003-11-25 | 1 | Qld, FNQ limit of 140MW
Q_FNQ_145 | 2003-11-25 | 1 | Qld, FNQ limit of 145MW
Q_FNQ_165 | 2003-11-25 | 1 | Qld, FNQ limit of 165MW
Q_FNQ_170 | 2003-11-25 | 1 | Qld, FNQ limit of 170MW
Q_FNQ_175 | 2003-11-25 | 1 | Qld, FNQ limit of 175MW
Q_FNQ_195 | 2003-11-25 | 1 | Qld, FNQ limit of 195MW
Q_FNQ_200 | 2003-11-25 | 1 | Qld, FNQ limit of 200MW
Q_FNQ_210 | 2003-11-25 | 1 | Qld, FNQ limit of 210MW
Q_FNQ_220 | 2003-11-25 | 1 | Qld, FNQ limit of 220MW
Q_FNQ_230 | 2003-11-25 | 1 | Qld, FNQ limit of 230MW
Q_FNQ_240 | 2003-11-25 | 1 | Qld, FNQ limit of 240MW
Q_FNQ_255 | 2003-11-25 | 1 | Qld, FNQ limit of 255MW
Q_GC_380 | 2006-08-02 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 380MW
Q_GC_390 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 390MW
Q_GC_400 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 400MW
Q_GC_410 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 410MW
Q_GC_420 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 420MW
Q_GC_430 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 430MW
Q_GC_440 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 440MW
Q_GC_450 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 450MW
Q_GC_460 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 460MW
Q_GC_470 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 470MW
Q_GC_480 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 480MW
Q_GC_490 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 490MW
Q_GC_500 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 500MW
Q_GC_510 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 510MW
Q_GC_520 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 520MW
Q_GC_530 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 530MW
Q_GC_540 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 540MW
Q_GC_550 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 550MW
Q_GC_560 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 560MW
Q_GC_570 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 570MW
Q_GC_580 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 580MW
Q_GC_590 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 590MW
Q_GC_600 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 600MW
Q_GC_610 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 610MW
Q_GC_620 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <=620MW
Q_GC_630 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 630MW
Q_GC_640 | 2004-12-09 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <= 640MW
Q_GC_650 | 2006-08-02 | 1 | Discretionary (Q-N Dirlink) , GoldCoast Cutset <=650MW
Q_GLD1200 | 2003-12-02 | 1 | Discretionary Gladstone Gen>=1200MW
Q_GLD1_0 | 2007-06-19 | 1 | Discretionary,Gladstone Unit 1 =< 0MW
Q_GLD2_0 | 2007-06-19 | 1 | Discretionary,Gladstone Unit 2 =< 0MW
Q_GLD34_500 | 2006-01-12 | 1 | Gladstone 3 + 4 Units Generation >= 500
Q_GLD3_0 | 2007-06-19 | 1 | Discretionary,Gladstone Unit 3 =< 0MW
Q_GLD4_0 | 2007-06-19 | 1 | Discretionary,Gladstone Unit 4 =< 0MW
Q_GLD5_0 | 2007-06-19 | 1 | Discretionary,Gladstone Unit 5 =< 0MW
Q_GLD6_0 | 2007-06-19 | 1 | Discretionary,Gladstone Unit 6 =< 0MW
Q_GLD900 | 2004-02-11 | 1 | Eff = 11/02/2004 ; RHS = 900 ; Op = ">=" ; Wt = 20
Q_KA_1TX | 2007-03-01 | 1 | Out= Kareeya Power Station 1 132/11/11kV transformer
Q_KA_2TX | 2004-10-22 | 1 | Out= Kareeya Power Station 2 132/11/11kV transformer
Q_KCBR_8820 | 2008-10-14 | 2 | Out= Kogan Creek PS to R2 Braemar 8820 275kV line
Q_KMBG_7143 | 2004-08-23 | 1 | Out= 7143 Kamerunga Barron Gorge PS 132kV line
Q_KMBG_7184 | 2004-08-23 | 1 | Out= 7184 Kamerunga Barron Gorge PS 132kV line
Q_MEWV_823_WIP1 | 2007-07-12 | 2 | Out= Mt England to Wivenhoe (823) line, Wivenhoe Pump #1 <=0
Q_MEWV_823_WIV1 | 2007-03-01 | 1 | Out= Mt England to Wivenhoe (823) line, Wivenhoe #1 <=0
Q_MEWV_824_WIP2 | 2007-07-12 | 2 | Out= Mt England to Wivenhoe (824) line, Wivenhoe Pump #2 <=0
Q_MEWV_824_WIV2 | 2007-03-01 | 1 | Out= Mt England to Wivenhoe (824) line, Wivenhoe #2 <=0
Q_MIMPP_9905 | 2007-03-01 | 1 | Out= 9905 Millmerran Millmerran Power Station 330kV line
Q_MIMPP_9906 | 2007-03-01 | 1 | Out= 9906 Millmerran Millmerran Power Station 330kV line
Q_MK_33BUS | 2007-03-01 | 1 | Out=T38 Mackay 33kV C Bus
Q_MSP1_80 | 2004-01-05 | 1 | Discretionary upper limit on Mt Stuart #1 GT of 80 MW
Q_MSP2_80 | 2004-01-05 | 1 | Discretionary upper limit on Mt Stuart #2 GT of 80 MW
Q_MSPTS_7242 | 2007-03-01 | 1 | Out= 7242 Mt Stuart Power Station Townsville South 132kV line
Q_MSPTS_7243 | 2007-03-01 | 1 | Out= 7243 Mt Stuart Power Station Townsville South 132kV line
Q_NIL_TR_4500 | 2009-11-17 | 2 | Tarong upper transfer limit of 4500MW (ceiling), 2009/10 implementation
Q_OKTA_7246 | 2007-03-01 | 1 | Out= 7246 Oakey Tangkam 132kV line
Q_OKTA_7247 | 2007-03-01 | 1 | Out= 7247 Oakey Tangkam 132kV line
Q_QTYP_100 | 2005-05-05 | 1 | Qld, Townsville PS 1 <=100MW
Q_QTYP_130 | 2004-10-13 | 1 | Qld, Townsville PS <=130MW
Q_QTYP_90 | 2005-07-28 | 1 | Qld Townsville PS <= 90MW
Q_RM7_0 | 2006-05-24 | 1 | Out = ROMA 7 due to transmission outage RM_7 <= 0MW
Q_RM8_0 | 2008-09-29 | 1 | Out = ROMA87 due to transmission outage RM_8 <= 0MW
Q_RS_230 | 2007-01-10 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=230MW
Q_RS_240 | 2008-09-24 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=240MW
Q_RS_250 | 2007-01-10 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=250MW
Q_RS_275 | 2007-01-10 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=275MW
Q_RS_300 | 2007-01-10 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=300MW
Q_RS_350 | 2007-01-10 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=350MW
Q_RS_400 | 2007-01-10 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=400MW
Q_RS_450 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=450MW
Q_RS_460 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=460MW
Q_RS_470 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=470MW
Q_RS_480 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=480MW
Q_RS_490 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=490MW
Q_RS_500 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=500MW
Q_RS_510 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=510MW
Q_RS_520 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=520MW
Q_RS_530 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=530MW
Q_RS_540 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=540MW
Q_RS_550 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=550MW
Q_RS_560 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=560MW
Q_RS_570 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=570MW
Q_RS_580 | 2004-12-02 | 1 | Qld,DiscretionaryTransfer(H13Ross+fdrs7128/ 7208) Limit<=580MW
Q_SB1_0 | 2007-03-01 | 1 | Out = Swanbank B1 due to transmission outage SBK_B1 <= 0MW
Q_SB4_0 | 2006-05-19 | 1 | Out = Swanbank B4 due to transmission outage SBK_B4 <= 0MW
Q_SB_5221 | 2007-03-01 | 1 | Out = H1 Swnabank Isol 5221. SBK_B2 <= 0MW
Q_STSTN_861 | 2007-03-01 | 1 | Out=861 Stanwell Power Station 275kV line
Q_STSTN_862 | 2007-03-01 | 1 | Out= 862 Stanwell Power Station 275kV line
Q_STSTN_863 | 2007-03-01 | 1 | Out=863 Stanwell Power Station 275kV line
Q_STSTN_864 | 2007-03-01 | 1 | Out= 864 Stanwell Power Station 275kV line
Q_SWE_8829 | 2005-07-26 | 1 | Out=Swanbank E to Swanbank E PS 275kV Line 8829
Q_TRNTR_8828 | 2008-09-29 | 1 | Out = 8828 Tarong North Power Station to H18 Tarong 275kV line
Q_TR_2000 | 2008-12-16 | 1 | Tarong upper transfer limit of 2000MW (discretionary), Summer 2008/09
Q_TR_2100 | 2008-12-16 | 1 | Tarong upper transfer limit of 2100MW (discretionary), Summer 2008/09
Q_TR_2200 | 2008-12-16 | 1 | Tarong upper transfer limit of 2200MW (discretionary), Summer 2008/09
Q_TR_2300 | 2008-12-16 | 1 | Tarong upper transfer limit of 2300MW (discretionary), Summer 2008/09
Q_TR_2400 | 2008-12-16 | 1 | Tarong upper transfer limit of 2400MW (discretionary), Summer 2008/09
Q_TR_2500 | 2008-12-16 | 1 | Tarong upper transfer limit of 2500MW (discretionary), Summer 2008/09
Q_TR_2600 | 2008-12-16 | 1 | Tarong upper transfer limit of 2600MW (discretionary), Summer 2008/09
Q_TR_2700 | 2008-12-16 | 1 | Tarong upper transfer limit of 2700MW (discretionary), Summer 2008/09
Q_TR_2800 | 2008-12-16 | 1 | Tarong upper transfer limit of 2800MW (discretionary), Summer 2008/09
Q_TR_2900 | 2008-12-16 | 1 | Tarong upper transfer limit of 2900MW (discretionary), Summer 2008/09
Q_TR_3000 | 2008-12-16 | 1 | Tarong upper transfer limit of 3000MW (discretionary), Summer 2008/09
Q_TR_3100 | 2008-12-16 | 1 | Tarong upper transfer limit of 3100MW (discretionary), Summer 2008/09
Q_TR_3200 | 2008-12-16 | 1 | Tarong upper transfer limit of 3200MW (discretionary), Summer 2008/09
Q_TR_3250 | 2008-12-16 | 1 | Tarong upper transfer limit of 3250MW (discretionary), Summer 2008/09
Q_TR_3300 | 2008-12-16 | 1 | Tarong upper transfer limit of 3300MW (discretionary), Summer 2008/09
Q_TR_3350 | 2008-12-16 | 1 | Tarong upper transfer limit of 3350MW (discretionary), Summer 2008/09
Q_TR_3400 | 2008-12-16 | 1 | Tarong upper transfer limit of 3400MW (discretionary), Summer 2008/09
Q_TR_3450 | 2008-12-16 | 1 | Tarong upper transfer limit of 3450MW (discretionary), Summer 2008/09
Q_TR_3500 | 2008-12-16 | 1 | Tarong upper transfer limit of 3500MW (discretionary), Summer 2008/09
Q_TR_3550 | 2008-12-16 | 1 | Tarong upper transfer limit of 3550MW (discretionary), Summer 2008/09
Q_TR_3600 | 2008-12-16 | 1 | Tarong upper transfer limit of 3600MW (discretionary), Summer 2008/09
Q_TR_3650 | 2008-12-16 | 1 | Tarong upper transfer limit of 3650MW (discretionary), Summer 2008/09
Q_TR_3700 | 2008-12-16 | 1 | Tarong upper transfer limit of 3700MW (discretionary), Summer 2008/09
Q_TR_3750 | 2008-12-16 | 1 | Tarong upper transfer limit of 3750MW (discretionary), Summer 2008/09
Q_TR_3800 | 2008-12-16 | 1 | Tarong upper transfer limit of 3800MW (discretionary), Summer 2008/09
Q_TR_3850 | 2008-12-16 | 1 | Tarong upper transfer limit of 3850MW (discretionary), Summer 2008/09
Q_TR_3900 | 2008-12-16 | 1 | Tarong upper transfer limit of 3900MW (discretionary), Summer 2008/09
Q_TR_3950 | 2008-12-16 | 1 | Tarong upper transfer limit of 3950MW (discretionary), Summer 2008/09
Q_TR_4000 | 2008-12-16 | 1 | Tarong upper transfer limit of 4000MW (discretionary), Summer 2008/09
Q_TR_4050 | 2008-12-16 | 1 | Tarong upper transfer limit of 4050MW (discretionary), Summer 2008/09
Q_TR_4100 | 2008-12-16 | 1 | Tarong upper transfer limit of 4100MW (discretionary), Summer 2008/09
Q_TR_4150 | 2008-12-16 | 1 | Tarong upper transfer limit of 4150MW (discretionary), Summer 2008/09
Q_TR_4200 | 2008-12-16 | 1 | Tarong upper transfer limit of 4200MW (discretionary), Summer 2008/09
Q_TR_TG_841 | 2007-06-05 | 1 | Out = 841 Tarong - Tarong PS 275kv line
Q_TR_TG_842 | 2004-07-20 | 1 | Out = 842 Tarong - Tarong PS 275kv line
Q_TR_TG_843 | 2007-08-08 | 1 | Out = 843 Tarong - Tarong PS 275kv line
Q_TR_TG_844 | 2007-08-08 | 1 | Out = 844 Tarong - Tarong PS 275kv line
Q_TV_CB4112 | 2004-09-21 | 1 | Out=T145 Townsville 132kV CB 4112
S-LB2_0 | 2007-08-14 | 1 | Discretionary upper limit for Lake Bonney 2 generation of 0 MW
S-MN_0 | 2006-07-28 | 1 | Mintaro generator CB or transformer out of service.
S-MPS_0 | 2004-07-20 | 1 | Brinkworth - Mintaro and Mintaro - Waterloo 132KV lines out of service. Mintaro PS=0MW
S-SG_0 | 2006-06-21 | 1 | Snuggery 132KV Turbine Bus out of service.
S-SG_21 | 2006-04-07 | 1 | Limit Snuggery GT gen to less than 21 MW
S-SG_42 | 2006-04-07 | 1 | Limit Snuggery GT gen to less than 42 MW
S-SNWWF_0 | 2008-05-05 | 1 | Discretionary upper limit for Snowtown WF generation of 0 MW
S-X_HUWT_BGPA_MNWT | 2007-12-19 | 1 | Out= Brinkworth - Para and Hummock - Waterloo lines, avoid O/L Mintaro to Waterloo on trip of Bungama to Para line, Feedback
S::V_CGMB_KHTB12MAMO | 2007-11-23 | 1 | Out=Cher.Gd-Mt.Bar+Keith-Tailem Bend 1&2+Mannum-Mobilong; SA-Vic Stability Limit on Loss of either Tailem Bend -TUNG #2 275kV Line or one Tailem Bend -SEAS 275kV Line
S::V_CGMB_NPS | 2008-04-11 | 1 | Out=Cherry Gardens - Mt.Barker 132kV line; SA-Vic Stability Limit on Loss of either Tailem Bend -TUNG #2 275kV Line or one Tailem Bend -SEAS 275kV Line
S::V_CGTB_TUTB | 2008-09-26 | 1 | Out=Cherry Gardens -Tailem Bend 275kV line; trip the remaining Tungkillo - Tailem Bend line
S::V_PATB_PATB | 2007-10-08 | 1 | SA to VIC Stab Lmt,Out=Para-TailB275kV, trip remaining Para-TailB
S::V_SECB6606_SETB2 | 2007-12-11 | 1 | Out = South East CB6606 or CB6607; SA to Vic Stability Limit. Critical Contingency: Trip one South Eat - Tailem Bend line.
S:DCGEN104 | 2003-11-25 | 1 | Dry Creek PS summated generation <= 104MW
S:NPS_SINGL_CONT | 2005-03-14 | 1 | Transient Stabilty constraint for the loss of Northen PS. Northern PS max generation as a function of V-SA. NPS < 2units, 2000WO applied
S:NPS_SINGL_CONT_HY | 2005-05-05 | 1 | Transient Stabilty constraint for the loss of Northen PS. Northern PS max generation as a function of V-SA. NPS < 2units, 2000WO applied
S:PPT_720-VS | 2003-08-27 | 1 | SA PelPt<= 720 -( trf Vic-SA);PPT max generation as a function of V-SA for stability(for loss of PPT ). PPt<3units,2000WO applied
S>>V_ACMA_CGTX_TBTX | 2007-06-28 | 1 | Out = Angas Ck - Mannum 132kV line, limit SA to Vic and SA generation to avoid Tailem Bend 275/132 kV Transformer OL on trip Cherry Gardens transformer.
S>>V_ACMA_TBTX_CGTX | 2007-12-19 | 1 | Out = Angas Ck - Mannum 132kV line, limit SA to Vic and SA generation to avoid Cherry Gardens Transformer OL on trip Tailem Bend 275/132 kV transformer.
S>>V_ACPA_CGTX_TBTX | 2007-06-12 | 1 | Out = Angas Ck - Para 132kV line, limit SA to Vic and SA generation to avoid Tailem Bend 275/132 kV Transformer OL on trip Cherry Gardens transformer.
S>>V_ACPA_TBTX_CGTX | 2007-12-19 | 1 | Out = Angas Ck - Para 132kV line, limit SA to Vic and SA generation to avoid Cherry Gardens Transformer OL on trip Tailem Bend 275/132 kV transformer.
S>>V_BRDV_BRPA_MNWT | 2008-07-23 | 1 | Out = Brinkworth - Davenport 275 kV line, avoid O/L Mintaro - Waterloo 132 kV line on trip of Brinkwoth - Para line.
S>>V_CGMB_KHTB12MAMO | 2007-11-07 | 1 | Out=Cher.Gd-Mt.Bar+Keith-Tailem Bend 1&2+Mannum-Mobilong; SA to Vic Limit to avoid O/L the Tungkillo -Tailem Bend line on trip Cherry Gardens -Tailem Bend line
S>>V_CGTB_TUTB_ACMP3 | 2007-12-19 | 1 | Prior Outage = Cherry Gardens - Tailem Bend 275 kV line; Avoid O/L Angas Creek to Mannum P3 line on trip Tailem Bend - Tungkillo line.
S>>V_CGTB_TUTB_CGTX | 2007-12-19 | 1 | Prior Outage = Cherry Gardens - Tailem Bend 275 kV line; Limits to avoid O/L Cherry Gardens 275/132 kV transformer on trip Tailem Bend - Tungkillo line.
S>>V_CGTB_TUTB_MOTB | 2007-11-27 | 2 | Prior Outage= Cherry Gardens -Tailem Bend 275 line; Avoid O/L Mobilong - Tailem bend 132kv on trip Tailem Bend - Tungkillo 275 kV line
S>>V_CGTB_TUTB_PAAC | 2007-12-19 | 1 | Prior Outage = Cherry Gardens - Tailem Bend line; Limits to avoid O/L Para to Millbrook T/Angas Ck 132 kV line on trip Tailem Bend - Tungkillo 275kV line.
S>>V_CNDV_DVMK_WTMW4 | 2009-01-21 | 1 | Out = Davenport - Canowi line; Limit SA-V on ML and SA generation to avoid overloading Waterloo - MWP4 line for one Davenport - Mokota - Robtstown line trip.
S>>V_CNRB_DVMK_HUWT | 2009-01-21 | 1 | Out = Canowi - Robetstown 275kV line, Humock - waterloo line on trip of Davenport - Mokota - Robtstown line.
S>>V_CNRB_DVMK_WTMW4 | 2009-01-21 | 1 | Out = Canowi - Robertstown line; Limit SA-V on ML and SA generation to avoid overloading Waterloo - MWP4 line for Davenport - Mokota - Robtstown line trip.
S>>V_DVRB_CNRB_WTMW4 | 2007-12-19 | 1 | Out = Davenport - Robertstown line; Limit SA-V on ML and SA generation to avoid overloading Waterloo - MWP4 line for Davenport - Canowi -Robertstown line trip.
S>>V_KHKN_NIL_KHSG | 2008-01-25 | 1 | Out = Keith - Kincraig 132 kV line; South East generation & Vic-SA limit to avoid Keith - Snuggery line OL (continuous rating) on nil trip
S>>V_KHKN_SETX_SETX | 2008-11-24 | 1 | Out = Keith - Kincraig 132 kV line, avoid O/L the remaining South East 275/132 kV transformer on trip of one South East 275/132 kV transformer, Feedback
S>>V_KHKN_TBSE_KHSG | 2008-01-25 | 1 | Out = Keith - Kincraig 132 kV line; avoid Snuggery - Keith line OL on trip Tailem Bend - South East 275 kV line
S>>V_KHSG_SETX_SETX | 2008-11-24 | 1 | Out=Keith - Snuggery 132 kV line, avoid O/L the remaining South East 275/132 kV transformer on trip of one South East 275/132 kV transformer, Feedback
S>>V_KHTB1_TBSE_TBKH | 2007-12-19 | 1 | Out = Keith - Tailem bend #1 132 kV line; limit SA to VIC transfer on the AC link and SA generation to avoid Tailem Bend - Keith #2 line OL on trip Tailem Bend - South East 275 kV line.
S>>V_KHTB2_TBSE_TBKH | 2007-12-19 | 1 | Out = Keith - Tailem bend #2 132 kV line; limit SA to VIC transfer on the AC link and SA generation to avoid Tailem Bend - Keith #1 line OL on trip one of the Tailem Bend - South East 275 kV lines.
S>>V_KNPW_NIL_KHSG | 2008-01-30 | 1 | Out = Kincraig - Penola West 132 kV line; South East generation & Vic-SA limit to avoid Keith - Snuggery line OL (continuous rating) on nil trip
S>>V_KNPW_SETX_SETX | 2008-11-24 | 1 | Out= Kincraig - Penola West 132 kV line, avoid O/L the remaining South East 275/132 kV transformer on trip of one South East 275/132 kV transformer, Feedback
S>>V_KNPW_TBSE_KHSG | 2008-01-30 | 1 | Out = Kincraig - Penola West 132 kV line; avoid Snuggery - Keith line OL on trip Tailem Bend - South East 275 kV line
S>>V_MAMO_CGTX_TBTX | 2007-07-03 | 1 | Out = Mannum - Mobilong 132kV line, limit SA to Vic and SA generation to avoid Tailem Bend 275/132 kV Transformer OL on trip Cherry Gardens transformer.
S>>V_MAMO_TBTX_CGTX | 2007-12-19 | 1 | Out = Mannum - Mobilong 132kV line, limit SA to Vic and SA generation to avoid Cherry Gardens Transformer OL on trip Tailem Bend 275/132 kV transformer.
S>>V_MOTB_CGTB_TUTB | 2008-01-22 | 1 | Out=Mobilong - Tailem Bend; SA-Vic and SA generation Limit to avoid O/L Tungkillo -Tailem Bend line on trip Cherry Gardens -Tailem Bend line.
S>>V_MOTB_TUTB_CGTB | 2008-01-22 | 1 | Out=Mobilong - Tailem Bend; SA-Vic and SA generation Limit to avoid O/L Cherry Gardens -Tailem Bend line on trip Tungkillo -Tailem Bend line.
S>>V_NIL_BRPA_MNWT | 2008-03-07 | 1 | Out= Nil, avoid O/L Mintaro to Waterloo 132 kV line on trip of Brinkworth to Para 275kV line, Feedback
S>>V_NIL_CGTX_ACMP3 | 2008-06-04 | 1 | Out = Nil; Limit Interconnectors and generation to avoid O/L Angas Creek to Mannum P3 line for trip Cherry Garden 275/132kV transformer. Fb CoOp.
S>>V_NIL_CGTX_MP2MA | 2008-06-04 | 1 | Out = Nil; Limit Interconnectors and generation to avoid O/L Mannum P2 to Mannum 132 kV line for trip Cherry Garden 275/132kV transformer. Fb CoOp.
S>>V_NIL_CGTX_PAAC | 2008-06-04 | 1 | Out = Nil; Limit Interconnectors and generation to avoid O/L Para to Millbrook T/Angas Ck 132 kV line for trip Cherry Garden 275/132kV transformer. Fb CoOp.
S>>V_NIL_MNWT_PARS | 2007-12-19 | 1 | Outage=Nil; Limit SA to Vic on Murraylink and SA generation to avoid overloading Para to Roseworthy 132kV line on loss of Mintaro - Waterloo line.
S>>V_NIL_NIL_KHSGC | 2008-01-30 | 1 | Out= Nil, avoid O/L Keith to Snuggery 132 kV line on trip of Nil, Feedback
S>>V_NIL_NIL_KHSGC_P | 2008-01-30 | 1 | Out= Nil, avoid O/L Keith to Snuggery 132 kV line on trip of Nil, Feedback
S>>V_NIL_NIL_RBTX | 2008-01-30 | 1 | Out=Nil with Run Back ON: limit SA to Vic on Murraylink and SA generation to avoid overloading Robertstown transformers.
S>>V_NIL_NIL_RBTX_P | 2008-01-30 | 1 | Out=Nil with Run Back ON: limit SA to Vic on Murraylink and SA generation to avoid overloading Robertstown transformers.
S>>V_NIL_PWSE_KHSG | 2007-12-14 | 1 | Out= Nil, avoid O/L Keith - Snuggery 132 kV line on trip of Penola West to South East line, Feedback
S>>V_NIL_PWSE_KHSG_P | 2007-12-14 | 1 | Out= Nil, avoid O/L Keith - Snuggery 132 kV line on trip of Penola West to South East line, Feedback
S>>V_NIL_RBTX_PARS | 2007-12-19 | 1 | Outage=Nil; Limit SA to Vic on Murraylink and SA generation to avoid overloading Para to Roseworthy 132kV line on loss of a Roberstown 275/132kV transformer.
S>>V_NIL_RBTX_PARS_P | 2007-12-19 | 1 | Outage=Nil; Limit SA to Vic on Murraylink and SA generation to avoid overloading Para to Roseworthy 132kV line on loss of a Roberstown 275/132kV transformer.
S>>V_NIL_RBTX_WTMW4 | 2007-12-19 | 1 | Out=Nil; Limit SA-V on ML and SA generation to avoid overloading Waterloo - MWP4 line for one Robtstown Transformer trip.
S>>V_NIL_RBTX_WTMW4_P | 2007-12-19 | 1 | Out=Nil; Limit SA-V on ML and SA generation to avoid overloading Waterloo - MWP4 line for one Robtstown Transformer trip.
S>>V_NIL_SETX_SETX | 2007-12-14 | 1 | Out= Nil, avoid O/L the remaining South East 275/132 kV transformer on trip of one South East 275/132 kV transformer, Feedback
S>>V_NIL_SETX_SETX_P | 2007-12-14 | 1 | Out= Nil, avoid O/L the remaining South East 275/132 kV transformer on trip of one South East 275/132 kV transformer, Feedback
S>>V_NIL_TBSE_KHSG | 2007-12-14 | 1 | Out= Nil, avoid O/L Keith - Snuggery 132 kV line on trip of Tailem Bend - South East 275kV line, Feedback
S>>V_NIL_TBSE_KHSG_P | 2007-12-14 | 1 | Out= Nil, avoid O/L Keith - Snuggery 132 kV line on trip of Tailem Bend - South East 275kV line, Feedback
S>>V_NIL_BRPA_MNWT_P | 2008-03-07 | 1 | Out= Nil, avoid O/L Mintaro to Waterloo 132 kV line on trip of Brinkworth to Para 275kV line, Feedback
S>>V_NIL_CGTX_ACMP3_P | 2008-06-04 | 1 | Out = Nil; Limit Interconnectors and generation to avoid O/L Angas Creek to Mannum P3 line for trip Cherry Garden 275/132kV transformer. Fb CoOp.
S>>V_NIL_CGTX_MP2MA_P | 2008-06-04 | 1 | Out = Nil; Limit Interconnectors and generation to avoid O/L Mannum P2 to Mannum 132 kV line for trip Cherry Garden 275/132kV transformer. Fb CoOp.
S>>V_NIL_CGTX_PAAC_P | 2008-06-04 | 1 | Out = Nil; Limit Interconnectors and generation to avoid O/L Para to Millbrook T/Angas Ck 132 kV line for trip Cherry Garden 275/132kV transformer. Fb CoOp.
S>>V_NIL_MNWT_PARS | 2007-12-19 | 1 | Outage=Nil; Limit SA to Vic on Murraylink and SA generation to avoid overloading Para to Roseworthy 132kV line on loss of Mintaro - Waterloo line.
S>>V_NIL_MNWT_PARS_P | 2007-12-19 | 1 | Outage=Nil; Limit SA to Vic on Murraylink and SA generation to avoid overloading Para to Roseworthy 132kV line on loss of Mintaro - Waterloo line.
S>>V_NIL_NIL_KHSGC | 2008-01-30 | 1 | Out= Nil, avoid O/L Keith to Snuggery 132 kV line on trip of Nil, Feedback
S>>V_NIL_NIL_RBTX | 2008-01-30 | 1 | Out=Nil with Run Back ON: limit SA to Vic on Murraylink and SA generation to avoid overloading Robertstown transformers.
S>>V_NIL_PWSE_KHSG | 2007-12-14 | 1 | Out= Nil, avoid O/L Keith - Snuggery 132 kV line on trip of Penola West to South East line, Feedback
S>>V_NIL_RBTX_PARS | 2007-12-19 | 1 | Outage=Nil; Limit SA to Vic on Murraylink and SA generation to avoid overloading Para to Roseworthy 132kV line on loss of a Roberstown 275/132kV transformer.
S>>V_NIL_RBTX_WTMW4 | 2007-12-19 | 1 | Out=Nil; Limit SA-V on ML and SA generation to avoid overloading Waterloo - MWP4 line for one Robtstown Transformer trip.
S>>V_NIL_SETX_SETX | 2007-12-14 | 1 | Out= Nil, avoid O/L the remaining South East 275/132 kV transformer on trip of one South East 275/132 kV transformer, Feedback
S>>V_NIL_TBSE_KHSG | 2007-12-14 | 1 | Out= Nil, avoid O/L Keith - Snuggery 132 kV line on trip of Tailem Bend - South East 275kV line, Feedback
S>>V_NORB_RBTX_RBTX | 2007-12-19 | 1 | Out=Murraylink Run Back (SA): limit SA to Vic on Murraylink and SA generation to avoid OL the remaining Robertstown transformer for trip of one Robertstown transformer.
S>>V_PARS_X_RBTX | 2007-12-19 | 1 | Out=Para - Roseworthy or Dorrien - Roseworthy 132kV line: limit SA to Vic on Murraylink and SA generation to avoid overloading Robertstown transformers.
S>>V_PWSE_NIL_KHSG | 2008-10-10 | 1 | Out = Penola West - South East 132 kV line; avoid Keith - Snuggery line OL (continuous rating) on nil trip
S>>V_PWSE_TBSE_KHSG | 2008-10-10 | 1 | Out = Penola West - South East 132 kV line; avoid Snuggery - Keith line OL on trip Tailem Bend - South East 275 kV line
S>>V_RBCB6188_MNWT | 2007-12-19 | 1 | Out = Robertstown CB6188, Prevent OL Mintaro-Waterloo 132kV line for loss of Robertstown 275/132kV no.2 transformer.
S>>V_RBTX_RBTX_MNWT | 2007-12-19 | 1 | Out = One Robertstown transformer. Prevent Mintaro - Waterloo 132 kV line OL for loss of the remaining Robertstown transformer.
S>>V_RBTX_RBTX_WTMW4 | 2007-05-03 | 1 | Out=One Robertstown 275/132 kV transformer; Limit SA-V on ML to avoid OL Waterloo - MWP4 line for loss of the remaining Robtstown Transformer.
S>>V_SESGT_SETB_SGBL | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; limit SA to VIC transfer on AC link and SA generation to avoid Snuggery - Blanche 132 kV line OL on trip Tailem Bend - South East 275 kV line.
S>>V_SETB_N-2_TBKH1 | 2007-06-27 | 1 | Prior outage= Nil; avoid O/L Keith to Tailem Bend #1 on trip of both South East to Tailem Bend 275 kV lines.
S>>V_SETB_N-2_TBKH2 | 2007-06-27 | 1 | Prior outage= Nil; avoid O/L Keith to Tailem Bend #2 on trip of both South East to Tailem Bend 275 kV lines.
S>>V_SETB_N-2_TBTX4 | 2007-12-19 | 1 | Prior outage= Nil; avoid O/L Tailem Bend 275/132kV transformer #4 on trip of both South East to Tailem Bend 275 kV lines.
S>>V_SETB_SETB_PWSE | 2007-09-20 | 1 | Out= One South East to Tailem Bend 275 kV line; avoid O/L Penola West South East line on trip of the remaining South East to Tailem Bend 275 kV line.
S>>V_SETB_SETB_TBKH1 | 2007-07-10 | 1 | Out= one South East to Tailem Bend 275kV line, avoid O/L Keith to Tailem Bend #1 on trip of the remaining South East to Tailem Bend line.
S>>V_SETB_SETB_TBKH2 | 2008-09-29 | 1 | Out= one South East to Tailem Bend 275kV line, avoid O/L Keith to Tailem Bend #2 on trip of the remaining South East to Tailem Bend line.
S>>V_SETB_SETB_TBTX4 | 2007-12-19 | 1 | Out= one South East to Tailem Bend 275kV line, avoid O/L Tailem Bend 275/132kV transformer #4 on trip of the remaining South East to Tailem Bend line
S>>V_SETX_PWKN_SETX | 2008-09-24 | 1 | Out = South East one transformer; Prevent remaining South East transformer OL for Penola West - Kincraig line trip.
S>>V_SETX_SGKH_SETX | 2008-09-24 | 1 | Out = South East one transformer; Prevent remaining South East transformer OL for Snuggery - Keith line trip.
S>>V_TBEBX_CGTX_PAAC | 2008-09-09 | 1 | Out = Tailem Bend East bus. Avoid O/L Para to Millbrook T/Angas Ck 132 kV line for trip Cherry Garden 275/132kV transformer.
S>>V_TBEBX_PAAC_CGTX | 2008-09-09 | 1 | Out = Tailem Bend East bus. Avoid O/L Cherry Garden 275/132kV transformer for trip Para to Millbrook T/Angas Ck 132 kV line.
S>>V_TBSE_N-2_PWSE | 2007-09-20 | 1 | Prior outage= Nil; avoid O/L Penola West South East line on trip of the both South East to Tailem Bend 275 kV lines.
S>>V_TBTU_CGTB_ACMP3 | 2007-12-19 | 1 | Prior Outage = Tailem Bend - Tungkillo 275 kV line; Avoid O/L Angas Creek to Mannum P3 line on trip Cherry Gardens - Tailem Bend line.
S>>V_TBTU_CGTB_CGTX | 2007-12-19 | 1 | Prior Outage = Tailem Bend - Tungkillo 275 kV line; Limits to avoid O/L Cherry Gardens 275/132 kV transformer on trip Cherry Gardens - Tailem Bend line.
S>>V_TBTU_CGTB_MOTB | 2007-11-27 | 2 | Prior Outage= Tailem Bend - Tungkillo 275 line; Avoid O/L Mobilong - Tailem bend 132kv on trip Cherry Gardens -Tailem Bend 275 kV line
S>>V_TBTU_CGTB_PAAC | 2007-12-19 | 1 | Prior Outage = Tailem Bend - Tungkillo line; Limits to avoid O/L Para to Millbrook T/Angas Ck 132 kV line on trip Cherry Gardens - Tailem Bend 275kV line.
S>>V_TBTU_N-2_ACMP3 | 2008-11-21 | 1 | Prior Outage = Nil; Avoid O/L Angas Creek to Mannum P3 line on trip Tailem Bend - Tungkillo line and Cherry Gardens - Tailem Bend line.
S>>V_TBTU_N-2_CGTX | 2008-11-21 | 1 | Prior Outage = Nil; Limits to avoid O/L Cherry Gardens 275/132 kV transformer on trip Tailem Bend - Tungkillo 275 kV line and Cherry Gardens - Tailem Bend line.
S>>V_TBTU_N-2_MOTB | 2008-11-21 | 1 | Prior Outage= Nil; Avoid O/L Mobilong - Tailem bend 132kv line on trip Tailem Bend - Tungkillo line and Cherry Gardens -Tailem Bend line
S>>V_TBTU_N-2_PAAC | 2008-11-21 | 1 | Prior Outage = Nil; Limits to avoid O/L Para to Millbrook T/Angas Ck 132 kV line on trip Tailem Bend - Tungkillo line and Cherry Gardens - Tailem Bend line.
S>>V_TBTX_CGTX_PAAC | 2007-12-19 | 1 | Out=Tailem Bend 275/132 kV transformer; Prevent OL Para - Angas creek line for Cherry Gardens 275/132 kV transformer trip.
S>>V_TBTX_PAAC_CGTX | 2007-12-19 | 1 | Out=Tailem Bend 275/132 kV transformer; Prevent OL Cherry Gardens 275/132 kV transformer for Para - Angas Creek line trip.
S>>V_XCG_TUTB_PAAC | 2008-09-26 | 1 | Out= Cherry Gardens - Tailem Bend and Cherry Gardens - Tungkillo 275kV lines and Cherry Gardens - Mt barker 132 kV line, avoid O/L PARA to MBRTEE on trip of TUNKIL to T_BEND, Feedback
S>>V_XCG_TUTB_PATX | 2008-09-26 | 1 | Out= Cherry Gardens - Tailem Bend and Cherry Gardens - Tungkillo 275kV lines and Cherry Gardens - Mt barker 132 kV line, avoid O/L PARA 275/132kV transformer on trip of TUNKIL to T_BEND, Feedback
S>>V_XHUWT_CNRB_MNWT | 2007-12-19 | 1 | Out= Brinkworth - Para and Hummock - Waterloo lines, avoid O/L Mintaro to Waterloo on trip of Canowi to Robertstown line, Feedback
S>BGPA_BRPA_MNWT | 2007-12-19 | 1 | Out = Bungama - Para line; Limit SA generation to avoid OL Mintaro - Waterloo 132 kV line for trip Brinkworth - Para 275kV line.
S>CNRB_BGPA_HUWT | 2008-10-01 | 1 | Out = Canowi - Robetstown 275kV line, O/L Humock - Waterloo line on trip of PARA-BUNGAM 275KV line
S>DVPF | 2004-06-28 | 2 | Out = Davenport - Playford 275KV line
S>HUWT_STBG | 2008-07-17 | 1 | Out = Hummocks - Waterloo 132 kV line; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL.
S>KHSG_SGBN | 2008-01-29 | 1 | Out = Keith-Snuggery line; Snuggery bus generation limit to avoid Snuggery - Blanche line OL on nil trip.
S>KHSG_SGBN_SGTSE | 2008-01-29 | 1 | Out = Keith-Snuggery line; Snuggery bus generation limit to avoid Snuggery T - South East line OL on trip Snuggery - Blanche line.
S>LFTI_PGPP_NOTI | 2006-09-15 | 1 | Out = Lefevre - Torrens Island 275 kV line; Limit generation to avoid OL New Osborne to Torrens Island 66 kV lines for trip Parafield Gardens West - Pelican Pt 275 kV line.
S>MYTX_MYTX | 2008-06-24 | 1 | Out = Mayura one 132/33 kV transformer, avoid O/L the remaining Mayura 132/33 kV transformer.
S>NIL_DVBG_STBG | 2008-07-16 | 1 | Out = Nil; Limit SA generation to avoid Snowtown - Bungama line OL on loss of Davenport to Bungama line.
S>NIL_DVBG_STBG_P | 2008-07-16 | 1 | Out = Nil; Limit SA generation to avoid Snowtown - Bungama line OL on loss of Davenport to Bungama line.
S>NIL_DVPF_WYCL | 2007-06-01 | 1 | Outage=NIL; Limit SA generation to avoid OL Whyalla Terminal to Cultana 132 kV line on trip Playford - Davenport 275 kV line.
S>NIL_HUWT_STBG | 2008-06-10 | 1 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.
S>NIL_NIL_MNWT | 2009-01-30 | 1 | Out = Nil; Limit Mintaro generation to avoid Mintaro - Waterloo line OL (continuous rating).
S>NIL_NIL_MNWT_P | 2009-01-30 | 1 | Out = Nil; Limit Mintaro generation to avoid Mintaro - Waterloo line OL (continuous rating).
S>NIL_NIL_STBG | 2008-07-23 | 1 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown T - Bungama line section OL.
S>NIL_NIL_STST-T | 2008-07-18 | 1 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Snowtown T line section OL.
S>NIL_NOTI_NOTI | 2009-02-04 | 1 | Out = NIL; Limit generation to avoid OL Torrens Island to New Osborne 66 kV lines for trip one of the Torrens Island to New Osborne 66 kV line.
S>NIL_NOTI_NOTI_P | 2009-02-04 | 1 | Out = NIL; Limit generation to avoid OL Torrens Island to New Osborne 66 kV lines for trip one of the Torrens Island to New Osborne 66 kV line.
S>NIL_PL_GENMAX | 2007-06-01 | 1 | Out = Nil, Maximum generation at Port Lincoln Due to Port Lincoln-Yadinarie line rating.
S>NIL_PL_GENMAX_P | 2007-06-01 | 1 | Out = Nil, Maximum generation at Port Lincoln Due to Port Lincoln-Yadinarie line rating.
S>NIL_PL_GENMAX_YDMD | 2007-06-01 | 1 | Out = Nil, Maximum generation at Port Lincoln Due to Yadnarie - Middleback 132kV line rating.
S>>V_KHKN_NIL_KHSG_P | 2008-01-25 | 1 | Out = Keith - Kincraig 132 kV line; South East generation & Vic-SA limit to avoid Keith - Snuggery line OL (continuous rating) on nil trip
S>>V_KHKN_SETX_SETX_P | 2008-11-24 | 1 | Out = Keith - Kincraig 132 kV line, avoid O/L the remaining South East 275/132 kV transformer on trip of one South East 275/132 kV transformer, Feedback
S>>V_KHKN_TBSE_KHSG_P | 2008-01-25 | 1 | Out = Keith - Kincraig 132 kV line; avoid Snuggery - Keith line OL on trip Tailem Bend - South East 275 kV line
S>>V_KHSG_SETX_SETX_P | 2008-11-24 | 1 | Out=Keith - Snuggery 132 kV line, avoid O/L the remaining South East 275/132 kV transformer on trip of one South East 275/132 kV transformer, Feedback
S>>V_KHTB1_TBSE_TBKH_P | 2007-12-19 | 1 | Out = Keith - Tailem bend #1 132 kV line; limit SA to VIC transfer on the AC link and SA generation to avoid Tailem Bend - Keith #2 line OL on trip Tailem Bend - South East 275 kV line.
S>>V_KHTB2_TBSE_TBKH_P | 2007-12-19 | 1 | Out = Keith - Tailem bend #2 132 kV line; limit SA to VIC transfer on the AC link and SA generation to avoid Tailem Bend - Keith #1 line OL on trip one of the Tailem Bend - South East 275 kV lines.
S>>V_KNPW_NIL_KHSG_P | 2008-01-30 | 1 | Out = Kincraig - Penola West 132 kV line; South East generation & Vic-SA limit to avoid Keith - Snuggery line OL (continuous rating) on nil trip
S>>V_KNPW_SETX_SETX_P | 2008-11-24 | 1 | Out= Kincraig - Penola West 132 kV line, avoid O/L the remaining South East 275/132 kV transformer on trip of one South East 275/132 kV transformer, Feedback
S>>V_KNPW_TBSE_KHSG_P | 2008-01-30 | 1 | Out = Kincraig - Penola West 132 kV line; avoid Snuggery - Keith line OL on trip Tailem Bend - South East 275 kV line
S>>V_MAMO_CGTX_TBTX | 2007-07-03 | 1 | Out = Mannum - Mobilong 132kV line, limit SA to Vic and SA generation to avoid Tailem Bend 275/132 kV Transformer OL on trip Cherry Gardens transformer.
S>>V_MAMO_TBTX_CGTX | 2007-12-19 | 1 | Out = Mannum - Mobilong 132kV line, limit SA to Vic and SA generation to avoid Cherry Gardens Transformer OL on trip Tailem Bend 275/132 kV transformer.
S>>V_MOTB_CGTB_TUTB | 2008-01-22 | 1 | Out=Mobilong - Tailem Bend; SA-Vic and SA generation Limit to avoid O/L Tungkillo -Tailem Bend line on trip Cherry Gardens -Tailem Bend line.
S>>V_MOTB_TUTB_CGTB | 2008-01-22 | 1 | Out=Mobilong - Tailem Bend; SA-Vic and SA generation Limit to avoid O/L Cherry Gardens -Tailem Bend line on trip Tungkillo -Tailem Bend line.
S>>V_NIL_BRPA_MNWT | 2008-03-07 | 1 | Out= Nil, avoid O/L Mintaro to Waterloo 132 kV line on trip of Brinkworth to Para 275kV line, Feedback
S>>V_NIL_CGTX_ACMP3 | 2008-06-04 | 1 | Out = Nil; Limit Interconnectors and generation to avoid O/L Angas Creek to Mannum P3 line for trip Cherry Garden 275/132kV transformer. Fb CoOp.
S>>V_NIL_CGTX_MP2MA | 2008-06-04 | 1 | Out = Nil; Limit Interconnectors and generation to avoid O/L Mannum P2 to Mannum 132 kV line for trip Cherry Garden 275/132kV transformer. Fb CoOp.
S>>V_NIL_CGTX_PAAC | 2008-06-04 | 1 | Out = Nil; Limit Interconnectors and generation to avoid O/L Para to Millbrook T/Angas Ck 132 kV line for trip Cherry Garden 275/132kV transformer. Fb CoOp.
S>>V_NIL_MNWT_PARS | 2007-12-19 | 1 | Outage=Nil; Limit SA to Vic on Murraylink and SA generation to avoid overloading Para to Roseworthy 132kV line on loss of Mintaro - Waterloo line.
S>>V_NIL_NIL_KHSGC | 2008-01-30 | 1 | Out= Nil, avoid O/L Keith to Snuggery 132 kV line on trip of Nil, Feedback
S>>V_NIL_NIL_RBTX | 2008-01-30 | 1 | Out=Nil with Run Back ON: limit SA to Vic on Murraylink and SA generation to avoid overloading Robertstown transformers.
S>>V_NIL_PWSE_KHSG | 2007-12-14 | 1 | Out= Nil, avoid O/L Keith - Snuggery 132 kV line on trip of Penola West to South East line, Feedback
S>>V_NIL_RBTX_PARS | 2007-12-19 | 1 | Outage=Nil; Limit SA to Vic on Murraylink and SA generation to avoid overloading Para to Roseworthy 132kV line on loss of a Roberstown 275/132kV transformer.
S>>V_NIL_RBTX_WTMW4 | 2007-12-19 | 1 | Out=Nil; Limit SA-V on ML and SA generation to avoid overloading Waterloo - MWP4 line for one Robtstown Transformer trip.
S>>V_NIL_SETX_SETX | 2007-12-14 | 1 | Out= Nil, avoid O/L the remaining South East 275/132 kV transformer on trip of one South East 275/132 kV transformer, Feedback
S>>V_NIL_TBSE_KHSG | 2007-12-14 | 1 | Out= Nil, avoid O/L Keith - Snuggery 132 kV line on trip of Tailem Bend - South East 275kV line, Feedback
S>>V_NORB_RBTX_RBTX | 2007-12-19 | 1 | Out=Murraylink Run Back (SA): limit SA to Vic on Murraylink and SA generation to avoid OL the remaining Robertstown transformer for trip of one Robertstown transformer.
S>>V_PARS_X_RBTX | 2007-12-19 | 1 | Out=Para - Roseworthy or Dorrien - Roseworthy 132kV line: limit SA to Vic on Murraylink and SA generation to avoid overloading Robertstown transformers.
S>>V_PWSE_NIL_KHSG | 2008-10-10 | 1 | Out = Penola West - South East 132 kV line; avoid Keith - Snuggery line OL (continuous rating) on nil trip
S>>V_PWSE_TBSE_KHSG | 2008-10-10 | 1 | Out = Penola West - South East 132 kV line; avoid Snuggery - Keith line OL on trip Tailem Bend - South East 275 kV line
S>>V_RBCB6188_MNWT | 2007-12-19 | 1 | Out = Robertstown CB6188, Prevent OL Mintaro-Waterloo 132kV line for loss of Robertstown 275/132kV no.2 transformer.
S>>V_RBTX_RBTX_MNWT | 2007-12-19 | 1 | Out = One Robertstown transformer. Prevent Mintaro - Waterloo 132 kV line OL for loss of the remaining Robertstown transformer.
S>>V_RBTX_RBTX_WTMW4 | 2007-05-03 | 1 | Out=One Robertstown 275/132 kV transformer; Limit SA-V on ML to avoid OL Waterloo - MWP4 line for loss of the remaining Robtstown Transformer.
S>>V_SESGT_SETB_SGBL | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; limit SA to VIC transfer on AC link and SA generation to avoid Snuggery - Blanche 132 kV line OL on trip Tailem Bend - South East 275 kV line.
S>>V_SETB_N-2_TBKH1 | 2007-06-27 | 1 | Prior outage= Nil; avoid O/L Keith to Tailem Bend #1 on trip of both South East to Tailem Bend 275 kV lines.
S>>V_SETB_N-2_TBKH2 | 2007-06-27 | 1 | Prior outage= Nil; avoid O/L Keith to Tailem Bend #2 on trip of both South East to Tailem Bend 275 kV lines.
S>>V_SETB_N-2_TBTX4 | 2007-12-19 | 1 | Prior outage= Nil; avoid O/L Tailem Bend 275/132kV transformer #4 on trip of both South East to Tailem Bend 275 kV lines.
S>>V_SETB_SETB_PWSE | 2007-09-20 | 1 | Out= One South East to Tailem Bend 275 kV line; avoid O/L Penola West South East line on trip of the remaining South East to Tailem Bend 275 kV line.
S>>V_SETB_SETB_TBKH1 | 2007-07-10 | 1 | Out= one South East to Tailem Bend 275kV line, avoid O/L Keith to Tailem Bend #1 on trip of the remaining South East to Tailem Bend line.
S>>V_SETB_SETB_TBKH2 | 2008-09-29 | 1 | Out= one South East to Tailem Bend 275kV line, avoid O/L Keith to Tailem Bend #2 on trip of the remaining South East to Tailem Bend line.
S>>V_SETB_SETB_TBTX4 | 2007-12-19 | 1 | Out= one South East to Tailem Bend 275kV line, avoid O/L Tailem Bend 275/132kV transformer #4 on trip of the remaining South East to Tailem Bend line
S>>V_SETX_PWKN_SETX | 2008-09-24 | 1 | Out = South East one transformer; Prevent remaining South East transformer OL for Penola West - Kincraig line trip.
S>>V_SETX_SGKH_SETX | 2008-09-24 | 1 | Out = South East one transformer; Prevent remaining South East transformer OL for Snuggery - Keith line trip.
S>>V_TBEBX_CGTX_PAAC | 2008-09-09 | 1 | Out = Tailem Bend East bus. Avoid O/L Para to Millbrook T/Angas Ck 132 kV line for trip Cherry Garden 275/132kV transformer.
S>>V_TBEBX_PAAC_CGTX | 2008-09-09 | 1 | Out = Tailem Bend East bus. Avoid O/L Cherry Garden 275/132kV transformer for trip Para to Millbrook T/Angas Ck 132 kV line.
S>>V_TBSE_N-2_PWSE | 2007-09-20 | 1 | Prior outage= Nil; avoid O/L Penola West South East line on trip of the both South East to Tailem Bend 275 kV lines.
S>>V_TBTU_CGTB_ACMP3 | 2007-12-19 | 1 | Prior Outage = Tailem Bend - Tungkillo 275 kV line; Avoid O/L Angas Creek to Mannum P3 line on trip Cherry Gardens - Tailem Bend line.
S>>V_TBTU_CGTB_CGTX | 2007-12-19 | 1 | Prior Outage = Tailem Bend - Tungkillo 275 kV line; Limits to avoid O/L Cherry Gardens 275/132 kV transformer on trip Cherry Gardens - Tailem Bend line.
S>>V_TBTU_CGTB_MOTB | 2007-11-27 | 2 | Prior Outage= Tailem Bend - Tungkillo 275 line; Avoid O/L Mobilong - Tailem bend 132kv on trip Cherry Gardens -Tailem Bend 275 kV line
S>>V_TBTU_CGTB_PAAC | 2007-12-19 | 1 | Prior Outage = Tailem Bend - Tungkillo line; Limits to avoid O/L Para to Millbrook T/Angas Ck 132 kV line on trip Cherry Gardens - Tailem Bend 275kV line.
S>>V_TBTU_N-2_ACMP3 | 2008-11-21 | 1 | Prior Outage = Nil; Avoid O/L Angas Creek to Mannum P3 line on trip Tailem Bend - Tungkillo line and Cherry Gardens - Tailem Bend line.
S>>V_TBTU_N-2_CGTX | 2008-11-21 | 1 | Prior Outage = Nil; Limits to avoid O/L Cherry Gardens 275/132 kV transformer on trip Tailem Bend - Tungkillo 275 kV line and Cherry Gardens - Tailem Bend line.
S>>V_TBTU_N-2_MOTB | 2008-11-21 | 1 | Prior Outage= Nil; Avoid O/L Mobilong - Tailem bend 132kv line on trip Tailem Bend - Tungkillo line and Cherry Gardens -Tailem Bend line
S>>V_TBTU_N-2_PAAC | 2008-11-21 | 1 | Prior Outage = Nil; Limits to avoid O/L Para to Millbrook T/Angas Ck 132 kV line on trip Tailem Bend - Tungkillo line and Cherry Gardens - Tailem Bend line.
S>>V_TBTX_CGTX_PAAC | 2007-12-19 | 1 | Out=Tailem Bend 275/132 kV transformer; Prevent OL Para - Angas creek line for Cherry Gardens 275/132 kV transformer trip.
S>>V_TBTX_PAAC_CGTX | 2007-12-19 | 1 | Out=Tailem Bend 275/132 kV transformer; Prevent OL Cherry Gardens 275/132 kV transformer for Para - Angas Creek line trip.
S>>V_XCG_TUTB_PAAC | 2008-09-26 | 1 | Out= Cherry Gardens - Tailem Bend and Cherry Gardens - Tungkillo 275kV lines and Cherry Gardens - Mt barker 132 kV line, avoid O/L PARA to MBRTEE on trip of TUNKIL to T_BEND, Feedback
S>>V_XCG_TUTB_PATX | 2008-09-26 | 1 | Out= Cherry Gardens - Tailem Bend and Cherry Gardens - Tungkillo 275kV lines and Cherry Gardens - Mt barker 132 kV line, avoid O/L PARA 275/132kV transformer on trip of TUNKIL to T_BEND, Feedback
S>>V_XHUWT_CNRB_MNWT | 2007-12-19 | 1 | Out= Brinkworth - Para and Hummock - Waterloo lines, avoid O/L Mintaro to Waterloo on trip of Canowi to Robertstown line, Feedback
S>BGPA_BRPA_MNWT | 2007-12-19 | 1 | Out = Bungama - Para line; Limit SA generation to avoid OL Mintaro - Waterloo 132 kV line for trip Brinkworth - Para 275kV line.
S>CNRB_BGPA_HUWT | 2008-10-01 | 1 | Out = Canowi - Robetstown 275kV line, O/L Humock - Waterloo line on trip of PARA-BUNGAM 275KV line
S>DVPF | 2004-06-28 | 2 | Out = Davenport - Playford 275KV line
S>HUWT_STBG | 2008-07-17 | 1 | Out = Hummocks - Waterloo 132 kV line; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL.
S>KHSG_SGBN | 2008-01-29 | 1 | Out = Keith-Snuggery line; Snuggery bus generation limit to avoid Snuggery - Blanche line OL on nil trip.
S>KHSG_SGBN_SGTSE | 2008-01-29 | 1 | Out = Keith-Snuggery line; Snuggery bus generation limit to avoid Snuggery T - South East line OL on trip Snuggery - Blanche line.
S>LFTI_PGPP_NOTI | 2006-09-15 | 1 | Out = Lefevre - Torrens Island 275 kV line; Limit generation to avoid OL New Osborne to Torrens Island 66 kV lines for trip Parafield Gardens West - Pelican Pt 275 kV line.
S>MYTX_MYTX | 2008-06-24 | 1 | Out = Mayura one 132/33 kV transformer, avoid O/L the remaining Mayura 132/33 kV transformer.
S>NIL_DVBG_STBG | 2008-07-16 | 1 | Out = Nil; Limit SA generation to avoid Snowtown - Bungama line OL on loss of Davenport to Bungama line.
S>NIL_DVPF_WYCL | 2007-06-01 | 1 | Outage=NIL; Limit SA generation to avoid OL Whyalla Terminal to Cultana 132 kV line on trip Playford - Davenport 275 kV line.
S>NIL_HUWT_STBG | 2008-06-10 | 1 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.
S>NIL_NIL_MNWT | 2009-01-30 | 1 | Out = Nil; Limit Mintaro generation to avoid Mintaro - Waterloo line OL (continuous rating).
S>NIL_NIL_STBG | 2008-07-23 | 1 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown T - Bungama line section OL.
S>NIL_NIL_STST-T | 2008-07-18 | 1 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Snowtown T line section OL.
S>NIL_NOTI_NOTI | 2009-02-04 | 1 | Out = NIL; Limit generation to avoid OL Torrens Island to New Osborne 66 kV lines for trip one of the Torrens Island to New Osborne 66 kV line.
S>NIL_PL_GENMAX | 2007-06-01 | 1 | Out = Nil, Maximum generation at Port Lincoln Due to Port Lincoln-Yadinarie line rating.
S>NIL_PL_GENMAX_YDMD | 2007-06-01 | 1 | Out = Nil, Maximum generation at Port Lincoln Due to Yadnarie - Middleback 132kV line rating.
S>PFWH | 2006-06-23 | 1 | One Playford - Whyalla 132KV line out of service.Limit Playford PS to avoid OL the remaining Playford - Whyalla line for trip of Playford - Davenport 275 kV Line.
S>PF_TX | 2007-01-17 | 1 | Playford Bus Tie Transf T_NT or T_ST out of service.Playford PS <=152 MW (160*0.95)
S>PGPP_LFTI_NOTI | 2006-09-15 | 1 | Out = Parafield Gardens West - Pelican Pt line; Limit generation to avoid OL New Osborne to Torrens Island 66 kV lines for trip Lefevre - Torrens Island 275 kV line.
S>PLCB6214_PL_GENMAX | 2007-02-22 | 1 | Out = Port Lincoln CB6214, Maximum generation at Port Lincoln to avoid OL Port Lincoln transformer #1 for trip Port Lincoln transformer #2.
S>SE132BUS_NIL_SGKHC | 2008-03-03 | 1 | Out= one South East 132 kV bus (W or E bus), avoid O/L Snuggery to Keith 132 kV line above the continuous rating
S>SE132BUS_SETX_SGKH | 2008-03-03 | 1 | Out= one South East 132 kV bus (W or E bus), avoid O/L Snuggery to Keith 132 kV line on trip of South East 275/132 transformer connected to the in service 132 kV bus
S>SE132CB_NIL_SGKHC | 2008-08-14 | 1 | Out= South East 132 kV CB6160 or CB6162, avoid O/L Snuggery to Keith 132 kV line above the continuous rating
S>SE132CB_SETX_SGKH | 2008-08-14 | 1 | Out= South East 132 kV CB6160 or CB6162, avoid O/L Snuggery to Keith 132 kV line on trip of the South East 275/132 transformer providing 275kV link to the LB2 WF
S>SESGT_BLSN_KHSN | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; Snuggery generation limit to avoid Snuggery - Keith line OL (15 minutes rating) on Blanche - Snuggery line trip
S>SESGT_KHSG_C_SGMIN | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; Run Snuggery generation to maintain Keith to Snuggery line flow below the continuous rating.
S>SESGT_SEMT_KHSG | 2008-06-13 | 1 | Out = South East - Snuggery T 132kV line; Run Snuggery and LB2 generation to maintain Keith to Snuggery line flow within the 15 minutes rating on trip South East-MtGambier line.
S>SESGT_SGKH_C_SGMAX | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; Maximum Snuggery generation possible with Snuggery to Keith line flow below the continuous rating.
S>SG_CB6105 | 2008-10-23 | 1 | Out=Snuggery CB6105: prevent overload of 132/33 kV transformer #f2 or 4 on trip of Transformer #3 or 1
S>SG_TX2 | 2007-06-25 | 1 | Out=Snuggery Trans 2: prevent overload of 132/33 kV transformer #f3 or 4 on trip of Transformer # 1
S>SN_CB6028 | 2007-06-22 | 1 | Out=Snuggery CB6028, prevent overload of #4 132/33 kV transformer for trip of Snuggery T1 or T3 transformer.
S>SN_CB6131 | 2007-08-14 | 1 | Out=Snuggery CB6131, prevent overload of #4 132/33 kV transformer for trip of Snuggery T1 transformer.
S>S_SG_CB6029 | 2007-06-22 | 1 | Out=Snuggery CB6029; to prevent #4 132/33 kV transformer overload for trip of Snuggery-Blanche line
S>S_SG_CB6103 | 2007-06-22 | 1 | Out=Snuggery CB6103, to prevent #2 132/33 kV transformer overload for trip of Snuggery-Blanche line
S>S_SNTX1A | 2007-06-25 | 1 | Out=Snuggery #1 132/33 kV transformer, prevent overload of #4 132/33 kV transformer for trip of Snuggery-Blanche line
S>S_SNTX3A | 2007-06-25 | 1 | Out=Snuggery #3 132/33 kV transformer, prevent overload of #4 132/33 kV transformer for trip of Snuggery-Blanche line
S>S_SNTX3B | 2007-06-25 | 1 | Out=Snuggery #3 132/33 kV transformer, prevent overload of #2 132/33 kV transformer for trip of Snuggery-Blanche line
S>VMLM3RB2 | 2009-01-05 | 1 | Out=MWP3_RB, limit SA to Vic on ML to avoid over-load on Robertstown to Nth West Bend line
S>VMLMH2RB | 2007-04-30 | 1 | Out=NWB-MWP1_MWP2_MWP3,&other outages,SA-V Lmt onMLfor NWB-RB#1
S>VMLMHNW1 | 2004-12-21 | 1 | Outage=Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash to Nth West Bend # 2 132kV line
S>VMLMHNW2 | 2004-12-21 | 1 | Out=MNSH_NW # 2, SA-V on ML, avoid overload on Monash to North West Bend # 1
S>VML_MHCB6152+BETX | 2007-07-13 | 1 | Out = Monash CB6152 and one Berri 132/66 kV transformer T1 with Berri Isolator A6307 closed; limit SA to Victoria on Murraylink to prevent Berri remaining transformer O/L on trip North West Bend - Monash - Berri #2 lines.
S>VML_NWCB6021_NWMH2 | 2006-06-27 | 1 | Out= North West Bend_CB6021; limit SA to Victoria on Murraylink to avoid NWB - Monash #2 O/L on trip NWB transformer #3.
S>VML_NWCB6021_RBNW1 | 2007-04-30 | 1 | Out= North West Bend_CB6021 with Run Back OFF; limit SA to Victoria on Murraylink to avoid Robertstown - NWB #1 O/L on trip Robertstown - MWP #3.
S>VML_NWCB6022_NWTX2 | 2006-06-09 | 1 | Out= North West Bend_CB6022; limit SA to Victoria on Murraylink to avoid North West Bend TF2 O/L on trip North West Bend - Robertstown # 1.
S>VML_NWCB6023_TX2 | 2007-07-13 | 2 | Out= North West Bend_CB6023; limit SA to Victoria on Murraylink to avoid North West Bend transformer#2 O/L on trip NWB - Robertstown line.
S>VML_NWCB6024+25 | 2007-02-16 | 1 | Out= North West Bend_CBs 6024 and 6025; limit SA to Victoria on Murraylink to avoid North West Bend transformer#3 O/L on trip NWB - MONASH #1 line.
S>VML_NWCB6024_NWTX2 | 2006-08-28 | 1 | Out= North West Bend_CB6024; limit SA to Vic on Murraylink to avoid North West Bend transformer #2 O/L on trip North West Bend transformer #3.
S>VML_NWCB6024_RBNW1 | 2007-04-30 | 1 | Out= North West Bend_CB6024 with Run back OFF; limit SA to Vic on Murraylink to avoid Robertstown-North West Bend line #1 O/L on trip Robertstown - MWP3 line.
S>VML_NWCB6025_NWTX2 | 2006-08-28 | 1 | Out= North West Bend_CB6025; limit SA to Vic on Murraylink to avoid North West Bend transformer #2 O/L on trip North West Bend - Monash line #2.
S>VML_NWCB6025_RBNW1 | 2007-04-30 | 1 | Out= North West Bend_CB6025 with Run back OFF; limit SA to Vic on Murraylink to avoid Robertstown-North West Bend line #1 O/L on trip Robertstown - MWP3 line.
S>VML_NWCB6033_TX2 | 2007-02-14 | 1 | Out= North West Bend_CB6033; limit SA to Victoria on Murraylink to avoid North West Bend transformer#2 O/L on trip NWB - MONASH #2 line.
S>VML_NWCB6225X_TX2 | 2007-06-21 | 2 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225 and 66 kV circuit breaker CB5605; limit SA to Victoria on Murraylink to avoid North West Bend transformer#2 O/L on trip NWB - MWP #1 line.
S>VML_NWCB6225_TX1 | 2007-01-04 | 1 | Out= North West Bend_CB6225; limit SA to Victoria on Murraylink to avoid North West Bend transformer#1 O/L on trip NWB - MWP #1.
S>VML_NWTXCB23_NWMH2 | 2006-08-28 | 1 | Out= North West Bend_CB6023 and Transformer #2; limit SA to Vic on Murraylink to avoid North West Bend -Monash #2 line O/L on trip North West Bend transformer# 1.
S>VML_NWTXCB23_RBNW1 | 2007-04-30 | 1 | Out= North West Bend_CB6023 and Transformer #2 with Run back OFF; limit SA to Vic on Murraylink to avoid Robertstown-North West Bend line #1 O/L on trip MWP3 - Robertstown line.
S>V_HYSE | 2004-06-29 | 1 | SA-V, Heywood - South East Outage
S>V_MHNW1_RBNW_RBP3 | 2009-01-05 | 1 | Out=MH_NW1, RunBack OS, SA-V on ML, load on MWP3_RB, NW_RB cont
S>V_MHNW1_RBP3_NWMH2 | 2009-01-05 | 1 | Out=MH_NW1, RunBack OS, SA-V on ML, load on MH_NW2, MWP3_RB cont
S>V_MW4WT_NIL_RBTX1 | 2006-08-17 | 1 | Out=Waterloo_MorganWhyallaPump4_Robertstown 132kV Line with Murraylink Run Back ON: limit SA to Vic on Murraylink to avoid overloading Robertstown transformer#1.
S>V_MW4WT_NIL_RBTX2 | 2006-08-17 | 1 | Out=Waterloo_MorganWhyallaPump4_Robertstown 132kV Line with Murraylink Run Back ON: limit SA to Vic on Murraylink to avoid overloading Robertstown transformer#2.
S>V_MW4WT_RBTX_RBTX | 2006-08-17 | 1 | Out=Waterloo-MWP4_Robertstown (RB) 132kV line without Murraylink Run Back; SA to Vic Murraylink limit to avoid RB Transformer OL for trip the other RB Transformer.
S>V_NIL_NIL_RBNW | 2009-02-11 | 1 | Outage=Nil; limit SA to Vic on Murraylink to avoid overloading North West Bend to Robertstown 132kV line.
S>V_NIL_NIL_RBNW_P | 2009-02-11 | 1 | Outage=Nil; limit SA to Vic on Murraylink to avoid overloading North West Bend to Robertstown 132kV line.
S>V_NORB_MWRB_RBNW | 2007-04-30 | 1 | Outage=Murraylink Run Back (SA); limit SA to Vic on Murraylink to avoid overloading Robertstown-North West Bend#1 for trip Robertstown-Morgan Whyala-NWB line.
S>V_NWRB2_RBNW1 | 2008-11-21 | 1 | Out = North West Bend to Robertstown No2 line, limit SA-V on ML, to avoid OL Robertstown to NWB1 line
S>V_NWRB_RBMWP3 | 2008-11-21 | 1 | Out=NWB - Robertstown 132kV line, Limit Murraylink SA to Vic flow to avoid OL Robertstown to MWP3 line.
S>V_P3RB_NWMH1_RBNW | 2009-01-06 | 1 | Out=MWP3_RB, RunBack OS, Limit SA to Vic on ML to avoid O/L RB-NWB line on trip MH-NW1
S>WHCB6045_46 | 2006-12-01 | 2 | Whyalla CB6045 and CB6046 with Yadnar circuit transferred to Playford using Playford - Whyalla #1 line. Limit Port Lincoln and Playford PS to avoid OL #2 Playford to Whyalla line for trip of Playford - Davenport 275 kV Line.
S>WHCB6045_50 | 2006-12-01 | 2 | Whyalla CB6045 and CB6050 with Yadnar circuit transferred to Playford using Playford - Whyalla #2 line. Limit Port Lincoln and Playford PS to avoid OL #1 Playford to Whyalla line for trip of Playford - Davenport 275 kV Line.
S>X_DVRBCN_DVBG_DVBR | 2008-01-09 | 1 | Out = Davenport - Robertstown and Davenport - Canowi 275 kV lines. Limit SA generation to avoid Davenport - Brinkworth line OL on trip Davenport - Bungama 275 kV line.
S>X_DVRBCN_NIL_DVBR | 2008-01-09 | 1 | Out = Davenport - Robertstown and Davenport - Canowi 275 kV lines. Limit SA generation to avoid Davenport - Brinkworth line OL.
S>X_DVRB_CGRB_BRDV | 2007-04-30 | 1 | Out = Davenport - Robertstown & Cherry Garden - Robertstown; Limit NPS, Playf, and Pt Linc generation to avoid Davenport - Brinkworth line OL on Davenport - Canowi - Robertstown line trip. Fb
S>X_SG_TX1+2 | 2007-07-11 | 1 | Out=Snuggery Transformer 1 and 2, prevent overload of #3 132/33 kV transformer for trip of Snuggery-Blanche line
SA_HYSE1 | 2003-04-04 | 1 | SA / Eastern separation between Heywood and South East (HYTS - SESS), Victoria to SA on VicSA upper limit of 0 MW
SA_HYSE2 | 2003-04-04 | 1 | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW
SA_PATB1 | 2008-09-11 | 1 | SA / Eastern separation between Tungkillo to Tailem Bend (TUNG - TBSS) Vic-SA Flow = South East Area Load - LocalGen
SA_TBSE1 | 2008-09-11 | 1 | SA / Eastern separation between Tailem Bend and South East (TBSS - SESS) Vic-SA Flow = South East Area Load - LocalGen
ST_NSW_HEADROOM | 2008-07-09 | 1 | NSW Import Constraint for LRC Assessment
ST_QLD_0 | 2006-11-13 | 1 | Qld Import Constraint for LRC Assessment
ST_Q^^QTR_OFFSET-100 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 100 MW
ST_Q^^QTR_OFFSET-110 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 110 MW
ST_Q^^QTR_OFFSET-120 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 120 MW
ST_Q^^QTR_OFFSET-125 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 125 MW
ST_Q^^QTR_OFFSET-130 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 130 MW
ST_Q^^QTR_OFFSET-140 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 140 MW
ST_Q^^QTR_OFFSET-150 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 150 MW
ST_Q^^QTR_OFFSET-160 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 160 MW
ST_Q^^QTR_OFFSET-170 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 170 MW
ST_Q^^QTR_OFFSET-180 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 180 MW
ST_Q^^QTR_OFFSET-190 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 190 MW
ST_Q^^QTR_OFFSET-200 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 200 MW
ST_Q^^QTR_OFFSET-210 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 210 MW
ST_Q^^QTR_OFFSET-220 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 220 MW
ST_Q^^QTR_OFFSET-230 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 230 MW
ST_Q^^QTR_OFFSET-240 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 240 MW
ST_Q^^QTR_OFFSET-250 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 250 MW
ST_Q^^QTR_OFFSET-260 | 2006-05-03 | 1 | Tarong voltage stability limit for ST PASA, Offset of 260 MW
ST_Q^^QTR_OFFSET-270 | 2006-05-03 | 1 | Tarong voltage stability limit for ST PASA, Offset of 270 MW
ST_Q^^QTR_OFFSET-280 | 2006-05-03 | 1 | Tarong voltage stability limit for ST PASA, Offset of 280 MW
ST_Q^^QTR_OFFSET-290 | 2006-05-03 | 1 | Tarong voltage stability limit for ST PASA, Offset of 290 MW
ST_Q^^QTR_OFFSET-300 | 2006-05-03 | 1 | Tarong voltage stability limit for ST PASA, Offset of 300 MW
ST_Q^^QTR_OFFSET-310 | 2006-05-03 | 1 | Tarong voltage stability limit for ST PASA, Offset of 310 MW
ST_Q^^QTR_OFFSET-320 | 2006-05-03 | 1 | Tarong voltage stability limit for ST PASA, Offset of 320 MW
ST_Q^^QTR_OFFSET-330 | 2006-05-03 | 1 | Tarong voltage stability limit for ST PASA, Offset of 330 MW
ST_Q^^QTR_OFFSET-340 | 2006-05-03 | 1 | Tarong voltage stability limit for ST PASA, Offset of 340 MW
ST_Q^^QTR_OFFSET-350 | 2006-05-03 | 1 | Tarong voltage stability limit for ST PASA, Offset of 350 MW
ST_Q^^QTR_OFFSET_-30 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 30 MW
ST_Q^^QTR_OFFSET_-40 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 40 MW
ST_Q^^QTR_OFFSET_-50 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 50 MW
ST_Q^^QTR_OFFSET_-60 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 60 MW
ST_Q^^QTR_OFFSET_-70 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 70 MW
ST_Q^^QTR_OFFSET_-80 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 80 MW
ST_Q^^QTR_OFFSET_-90 | 2006-05-04 | 1 | Tarong voltage stability limit for ST PASA, Offset of 90 MW
ST_SA_0 | 2006-11-13 | 1 | SA Import Constraint for LRC Assessment
ST_VIC_HEADROOM | 2008-07-09 | 1 | VIC Import Constraint for LRC Assessment
SVML_000 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 0 MW
SVML_010 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 10 MW
SVML_020 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 20 MW
SVML_040 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 40 MW
SVML_060 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 60 MW
SVML_080 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 80 MW
SVML_100 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 100 MW
SVML_120 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 120 MW
SVML_140 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 140 MW
SVML_160 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 160 MW
SVML_180 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 180 MW
SVML_200 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 200 MW
SVML_210 | 2008-08-05 | 1 | SA to Vic on Murraylink upper transfer limit of 210 MW
SVML_220 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 220 MW
SVML_240 | 2008-08-05 | 1 | SA to Vic on ML upper transfer limit of 240 MW
SVS_-700MN | 2003-02-11 | 1 | SA to Vic on Vic-SA + ML Minimum transfer limit of -700MW
SVS_000 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 0 MW
SVS_020 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 20 MW
SVS_040 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 40 MW
SVS_060 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 60 MW
SVS_080 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 80 MW
SVS_100 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 100 MW
SVS_120 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 120 MW
SVS_140 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 140 MW
SVS_160 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 160 MW
SVS_180 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 180 MW
SVS_200 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 200 MW
SVS_220 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 220 MW
SVS_240 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 240 MW
SVS_260 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 260 MW
SVS_280 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 280 MW
SVS_300 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 300 MW
SVS_350 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 350 MW
SVS_400 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 400 MW
SVS_420 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 420 MW
SVS_450 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 450 MW
SVS_500 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 500 MW
SVS_520 | 2008-08-05 | 1 | SA to Vic on Vic-SA + ML upper transfer limit of 520 MW
SV_000 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 0 MW
SV_020 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 20 MW
SV_030 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 30 MW
SV_040 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 40 MW
SV_050 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 50 MW
SV_060 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 60 MW
SV_070 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 70 MW
SV_080 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 80 MW
SV_100 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 100 MW
SV_120 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 120 MW
SV_130 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 130 MW
SV_140 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 140 MW
SV_150 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 150 MW
SV_160 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 160 MW
SV_180 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 180 MW
SV_200 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 200 MW
SV_220 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 220 MW
SV_240 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 240 MW
SV_250 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 250 MW
SV_260 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 260 MW
SV_280 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 280 MW
SV_300 | 2008-08-05 | 1 | SA to Victoria on VicSA upper transfer limit of 300 MW
S^NIL_LB1+2MAX | 2007-07-26 | 1 | Out= Nil; Limit Lake Bonney 1 and 2 generation to maintain voltage stability.
S^NIL_SGBL_LB2MAX | 2007-08-22 | 1 | Out= Nil; Limit Lake Bonney 2 and Snuggery generation to maintain voltage stability on Snuggery end fault on the Snuggery - Blanche line.
S^NPS_SINGL_CONT | 2005-03-14 | 1 | SA Northern PS min gen dispatch >= 360 MW, NPS<2units,-2000appl
S^NPS_SINGL_CONT_HY | 2005-03-22 | 2 | SA Northern PS min gen dispatch >= 360 MW, NPS<2units,-2000appl
S^PPT340 | 2003-08-14 | 2 | SA Pel Point min gen dispatch >= 340MW,PP<3units,-2000appl
S^SESGT_LB1+2MAX | 2007-12-12 | 1 | Out= South East - Snuggery T 132kV line; Limit Lake Bonney 1 and 2 generation to maintain voltage stability.
S^SESGT_SGBL_LB2MAX | 2007-12-12 | 1 | Out= South East - Snuggery T 132kV line; Limit Lake Bonney 2 and Snuggery generation to maintain voltage stability on Snuggery end fault on the Snuggery - Blanche line.
S^^V_SETB_SETB | 2007-12-20 | 1 | Out = One South East -Tailem Bend 275 kV line; Limit SA to Vic and generation to prevent voltage collapse for trip the other South East - Tailem Bend line.
S_0102 | 2001-03-06 | 1 | SA Pelican Point gen dependant on Vic-SA transfer <=500MW
S_ANGA_1+2 | 2006-10-10 | 1 | Angaston <= 0
S_CNHL_HAL | 2004-10-15 | 1 | Outage of Canowie Hallett 275kV line
S_DCBUS_DC1 | 2006-03-14 | 1 | Outage of Dry Creek 66kV bus sectiion, DRYCGT1<=0
S_DCBUS_DC2 | 2006-03-14 | 1 | Outage of Dry Creek 66kV bus section, DRYCGT2<=0
S_DC_CBG3 | 2006-03-14 | 1 | Outage of Dry Creek 66kV CB G3, DRYCGT3<=0
S_DVAR_CONF | 2008-06-12 | 1 | Out= Nil; Limit Lake Bonney 2 generation based on DVAR availablity.
S_DVNP_NP1 | 2005-03-23 | 1 | Out=Davenport Northern U1 275kV line
S_DVNP_NP2 | 2005-03-23 | 1 | Out=Davenport Northern U2 275kV line
S_HALWF_0 | 2008-07-28 | 1 | Discretionary upper limit for Hallett Wind Farm generation of 0 MW
S_HALWF_5 | 2007-12-19 | 1 | Discretionary upper limit for Hallett Wind Farm generation of 5 MW
S_HLPS_0 | 2008-07-28 | 1 | Discretionary upper limit for Hallett power station generation of 0 MW
S_HLWF_CONF | 2008-06-12 | 1 | Out= Nil; Limit Hallett WF generation based on DVAR availablity.
S_NPS+PF+PL_450 | 2008-05-05 | 1 | Discretionary upper limit for Northern + Playford + Port Lincoln generation of 450 MW
S_NPS+PF+PL_475 | 2008-05-05 | 1 | Discretionary upper limit for Northern + Playford + Port Lincoln generation of 475 MW
S_NPS+PF+PL_500 | 2008-05-05 | 1 | Discretionary upper limit for Northern + Playford + Port Lincoln generation of 500 MW
S_NPS+PF+PL_525 | 2008-05-05 | 1 | Discretionary upper limit for Northern + Playford + Port Lincoln generation of 525 MW
S_NPS+PF+PL_550 | 2008-05-05 | 1 | Discretionary upper limit for Northern + Playford + Port Lincoln generation of 550 MW
S_NPS+PF+PL_575 | 2008-05-05 | 1 | Discretionary upper limit for Northern + Playford + Port Lincoln generation of 575 MW
S_NPS+PF+PL_600 | 2008-05-05 | 1 | Discretionary upper limit for Northern + Playford + Port Lincoln generation of 600 MW
S_NPS+PF+PL_625 | 2008-05-05 | 1 | Discretionary upper limit for Northern + Playford + Port Lincoln generation of 625 MW
S_NPS+PF+PL_650 | 2008-05-05 | 1 | Discretionary upper limit for Northern + Playford + Port Lincoln generation of 650 MW
S_NPS+PF+PL_675 | 2008-05-05 | 1 | Discretionary upper limit for Northern + Playford + Port Lincoln generation of 675 MW
S_NPS+PF+PL_700 | 2008-05-05 | 1 | Discretionary upper limit for Northern + Playford + Port Lincoln generation of 700 MW
S_NPS1=180 | 2005-06-28 | 1 | NPS Unit 1 = 180 MW
S_NPS1_200 | 2008-07-02 | 2 | Discretionary upper limit for Northern unit 1 generation of 200 MW
S_NPS1_220 | 2008-05-21 | 1 | Discretionary upper limit for Northern unit 1 generation of 220 MW
S_NPS1_260 | 2008-07-02 | 2 | Discretionary upper limit for Northern unit 1 generation of 260 MW
S_NPS2=180 | 2005-06-28 | 1 | NPS Unit 2 = 180 MW
S_NPS2_200 | 2008-07-02 | 2 | Discretionary upper limit for Northern unit 2 generation of 200 MW
S_NPS2_220 | 2008-05-21 | 1 | Discretionary upper limit for Northern unit 2 generation of 220 MW
S_NPS2_260 | 2008-07-02 | 2 | Discretionary upper limit for Northern unit 2 generation of 260 MW
S_NPS_390 | 2005-03-22 | 1 | Discretionary upper limit for Northern generation of 390 MW
S_NPS_410 | 2005-03-22 | 1 | Discretionary upper limit for Northern generation of 410 MW
S_NPS_430 | 2005-03-22 | 1 | Discretionary upper limit for Northern generation of 430 MW
S_NPS_450 | 2005-03-22 | 1 | Discretionary upper limit for Northern generation of 450 MW
S_NPS_470 | 2005-03-22 | 1 | Discretionary upper limit for Northern generation of 470 MW
S_NPS_490 | 2005-03-22 | 1 | Discretionary upper limit for Northern generation of 490 MW
S_NPS_510 | 2005-03-22 | 1 | Discretionary upper limit for Northern generation of 510 MW
S_NPS_530 | 2005-03-22 | 1 | Discretionary upper limit for Northern generation of 530 MW
S_OSNO_OCPL1 | 2004-10-18 | 1 | Outage of New Osborne-OCPL line 1
S_PF_1_UNIT | 2004-09-16 | 1 | Out = 1 Playford unit. Playford PS output <= 189MW
S_PF_2_UNITS | 2004-09-16 | 1 | Out = 2 Playford units. Playford PS output <= 126MW
S_PF_3_UNITS | 2004-09-16 | 1 | Out = 3 Playford units. Playford PS output <= 63MW
S_PF_4_UNITS | 2004-09-16 | 1 | Out = 4 Playford units. Playford PS output <= 0MW
S_PLN_CB6210 | 2005-05-17 | 1 | Out=Port Lincoln CB6210 ( Generator transformer CB)
S_PLN_ISL1 | 2005-01-18 | 1 | Out = Whyalla to Yadnarie line, Port Lincoln PS islanded
S_PLN_ISL2 | 2005-01-18 | 1 | Out = Yadnarie to Port Lincoln line, Port Lincoln PS islanded
S_PPT200 | 2008-08-28 | 1 | SA Pelican Point gen <= 200MW
S_PPT210 | 2006-02-21 | 1 | SA Pelican Point gen <= 210MW
S_PPT220 | 2008-08-28 | 1 | SA Pelican Point gen <= 220MW
S_PPT240 | 2008-08-28 | 1 | SA Pelican Point gen <= 240MW
S_PPT260 | 2003-11-21 | 1 | SA Pelican Point gen <= 260MW
S_PPT_0 | 2008-10-31 | 1 | Pelican Pt Power Station out of service
S_PWLG_LG1 | 2004-10-26 | 1 | Outage of Penola West to Ladbroke Grove 132kV circuit
S_PWLG_LG2 | 2004-10-26 | 1 | Outage of Penola West to Ladbroke Grove 132kV circuit
S_QPS5_0 | 2008-12-19 | 1 | Discretionary upper limit for Quarantine #5 generation of 0 MW
S_SG_10 | 2006-02-09 | 1 | Discretionary upper limit for Snuggery generation of 10 MW
S_SG_15 | 2006-02-09 | 1 | Discretionary upper limit for Snuggery generation of 15 MW
S_SG_20 | 2006-02-09 | 1 | Discretionary upper limit for Snuggery generation of 20 MW
S_SG_25 | 2006-02-09 | 1 | Discretionary upper limit for Snuggery generation of 25 MW
S_SG_30 | 2006-02-09 | 1 | Discretionary upper limit for Snuggery generation of 30 MW
S_SG_40 | 2006-02-09 | 1 | Discretionary upper limit for Snuggery generation of 40 MW
S_SNWWF_CONF | 2008-06-12 | 1 | Out= Nil; Limit Snowtown WF generation based on DVAR availablity.
S_TA1_TX | 2005-03-23 | 2 | Torrens A 1 Transformer O/S; unit=0
S_TA2_TX | 2005-03-23 | 2 | Torrens A 2 Transformer O/S; unit=0
S_TA3_TX | 2005-03-23 | 1 | Torrens A 3 Transformer O/S; unit=0
S_TA4_TX | 2005-03-23 | 1 | Torrens A 4 Transformer O/S; unit=0
S_TB1_TX | 2007-03-01 | 1 | Torrens B 1 Transformer O/S; unit=0
S_TB2_TX | 2007-03-01 | 1 | Torrens B 2 Transformer O/S; unit=0
S_TB3_TX | 2007-03-01 | 1 | Torrens B 3 Transformer O/S; unit=0
S_TB4_TX | 2007-03-01 | 1 | Torrens B 4 Transformer O/S; unit=0
S_TITN1 | 2009-01-27 | 1 | Out= Torrens Island to Torrens North #1 66kV line
S_TITN2 | 2009-01-27 | 1 | Out= Torrens Island to Torrens North #2 66kV line
S_TI_CB_AW3+AC3 | 2004-08-18 | 1 | Torrens Island CBs AW3 & AC3 out of service.
S_TI_CB_AW4+AC4 | 2004-08-03 | 1 | Torrens Island CBs AC4 & AW4 out of service.
S_TI_CB_BW4+BC4 | 2004-09-02 | 1 | Out = Torrens Island CBs BW4 and BC4
S_V_NIL-300 | 2008-10-24 | 1 | Out= Nil, limit SA to Vic to reduce time and amount exceeding 300 MW due to non-conformance or FCAS raise reg flows
S_X_TI_CB_BW3+BC3 | 2006-04-05 | 1 | Out = Torrens Island CBs BW3 and BC3
T::T_GT_BUSPROT_220 | 2008-01-22 | 1 | Out = Georgetown 220kV A and B bus protection, maintain system security for a Georgetown 220kV bus fault
T::T_NIL_3 | 2008-06-12 | 1 | Out = Nil, Basslink importing only, avoid transient instability for fault and trip of the Palmerston to Sheffield line
T::T_SH_BUSPROT | 2008-12-04 | 1 | Out = Sheffield A & B 220kV bus zone protection, maintain system security for a Sheffield 220kV bus fault
T::T_SH_BUSPROT_RAMP | 2008-12-04 | 1 | Out = Sheffield A & B 220kV bus zone protection, Ramp down (25 MW per DI) Tasmanian generators and Basslink to maintain system security for a Sheffield 220kV bus fault
T:T_COMMS_CSGO | 2008-05-01 | 1 | Out = Communications to Gordon and hence Chapel St to Gordon 220kV line fast protection (leaving only distance protection in service), limit Gordon generation to avoid transient instability for a fault on a Chapel St to Gordon 220 kV line close to Gordon
T:T_FA_BUSPROT_1 | 2008-12-04 | 1 | Out = Farrell A & B 220kV bus zone protection, maintain system security for a Farrell 220kV bus fault by limiting each Farrell generator below 70% max output (50% for Mackintosh)
T:T_FA_BUSPROT_2 | 2008-12-04 | 1 | Out = Farrell A & B 220kV bus zone protection, maintain system security for a Farrell 220kV bus fault by limiting each Farrell generator below 70% max output (50% for Mackintosh)
T:T_FA_BUSPROT_3 | 2008-12-04 | 1 | Out = Farrell A & B 220kV bus zone protection, maintain system security for a Farrell 220kV bus fault by limiting each Farrell generator below 70% max output (50% for Mackintosh)
T:T_FA_BUSPROT_4 | 2008-12-04 | 1 | Out = Farrell A & B 220kV bus zone protection, maintain system security for a Farrell 220kV bus fault by limiting each Farrell generator below 70% max output (50% for Mackintosh)
T:T_FA_BUSPROT_5 | 2008-12-04 | 1 | Out = Farrell A & B 220kV bus zone protection, maintain system security for a Farrell 220kV bus fault by limiting each Farrell generator below 70% max output (50% for Mackintosh)
T:T_FA_BUSPROT_6 | 2008-12-04 | 1 | Out = Farrell A & B 220kV bus zone protection, maintain system security for a Farrell 220kV bus fault by limiting each Farrell generator below 70% max output (50% for Mackintosh)
T:T_LIPM_1 | 2005-05-16 | 1 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South)
T:T_LIPM_2 | 2005-05-16 | 1 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to North)
T:T_NIL_1 | 2006-01-09 | 1 | Out = Nil, Basslink importing only, avoid transient instability for fault and trip of a Farrell to Sheffield line
T:T_PMWA_1 | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid transient instability for fault and trip of a Liapootah to Chapel St 220kV line
T:T_SH_BUSPROT | 2006-07-06 | 1 | Out = Sheffield A & B 220kV zone bus protection, maintain system security for a Sheffield 220kV bus fault
T:T_SH_BUSPROT_220 | 2008-01-16 | 1 | Out = Sheffield A & B 220kV bus zone protection, maintain system security for a Sheffield 220kV bus fault
T:T_SH_BUSPROT_RAMP | 2006-09-25 | 1 | Out = Sheffield A & B 220kV bus zone protection, Ramp down (25 MW per DI) Tasmanian generators feeding the Sheffield import to maintain system security for a Sheffield 220kV bus fault
T:T_SH_PROT_RAMP_220 | 2008-01-16 | 1 | Out = Sheffield A & B 220kV bus zone protection, Ramp down (25 MW per DI) Tasmanian generators feeding the Sheffield import to maintain system security for a Sheffield 220kV bus fault
T>>T_GTSH_110_2 | 2006-06-08 | 1 | Out = Georgetown to Sheffield 220kV line, avoid O/L a Palmerston to Hadspen (No.3 or No.4) 110kV line for loss of the remaining Sheffield to Georgetown 220kV line
T>>T_GTSH_220_1 | 2007-10-03 | 1 | Out = Georgetown to Sheffield 220kV line, avoid O/L the Sheffield to Palmerston line for loss of the other Georgetown to Sheffield line, Feedback
T>>T_GTSH_220_1_N-2 | 2006-06-08 | 1 | Out = Nil, Loss of both Georgetown to Sheffield 220kV lines declared credible, avoid O/L the Sheffield to Palmerston line for loss of both Georgetown to Sheffield lines, Feedback
T>>T_GTSH_220_2A | 2006-06-08 | 2 | Out = Georgetown to Sheffield 220kV line, avoid O/L Palmerston to Hadspen No.1 220kV line for loss of the Hadspen to Palmerston No.2 220kV line, Feedback
T>>T_GTSH_220_2B | 2006-06-08 | 2 | Out = Georgetown to Sheffield 220kV line, avoid O/L a Palmerston to Hadspen No.2 220kV line for loss of the other Hadspen to Palmerston No.1 220kV line, Feedback
T>>T_GTSH_220_3A | 2007-05-24 | 1 | Out = Georgetown to Sheffield 220kV line, avoid O/L the Hadspen to Georgetown No.1 line for loss of the Georgetown to Hadspen No.2 line, Feedback
T>>T_GTSH_220_3B | 2006-06-08 | 2 | Out = Georgetown to Sheffield 220kV line, avoid O/L the Hadspen to Georgetown No.2 line for loss of the Georgetown to Hadspen No.1 line, Feedback
T>>T_GTSH_220_4A | 2007-05-17 | 1 | Out = Georgetown to Sheffield 220kV line, avoid O/L Sheffield to Georgetown No.2 line for loss of the Sheffield to Palmerston line, Feedback
T>>T_GTSH_220_4B | 2007-05-17 | 1 | Out = Georgetown to Sheffield 220kV line, avoid O/L Sheffield to Georgetown No.1 line for loss of the Sheffield to Palmerston line, Feedback
T>>T_GTSH_220_5 | 2006-06-08 | 1 | Out = Georgetown to Sheffield 220kV line, avoid O/L a Palmerston to Hadspen 220kV line for loss of the remaining Georgetown to Sheffield 220kV line
T>>T_GTSH_220_6 | 2006-06-08 | 1 | Out = Georgetown to Sheffield 220kV line, avoid O/L a Hadspen to Georgetown 220kV line for loss of the remaining Georgetown to Sheffield 220kV line
T>>T_HAPM_110_1A | 2007-07-23 | 1 | Outage = Hadspen to Palmerston (No.3 or No.4) 110kV line, limit Tas generation and Basslink to avoid pre-contingent and post-contingent overloading the Hadspen to Palmerston No.1 220kV line (flow to North), feedback equation
T>>T_HAPM_110_1B | 2007-07-23 | 1 | Outage = Hadspen to Palmerston (No.3 or No.4) 110kV line, limit Tas generation and Basslink to avoid pre-contingent and post-contingent overloading the Hadspen to Palmerston No.2 220kV line (flow to North), feedback equation
T>>T_HAPM_110_2A | 2007-07-23 | 1 | Outage = Hadspen to Palmerston (No.3 or No.4) 110kV line, limit Tas generation to avoid O/L either Palmerston to Hadspen 220kV line for trip of other Palmerston to Hadspen 220kV line (outage id's=39,40,41,42) taking into account NCSPS generation reduction
T>>T_HAPM_110_5A | 2007-07-23 | 1 | Out = Hadspen to Palmerston 110kV line, avoid O/L Sheffield to Palmerston line (flow to North) for loss of a Sheffield to Georgetown line
T>>T_HAPM_110_5B | 2007-07-23 | 1 | Out = Hadspen to Palmerston 110kV line, avoid O/L Sheffield to Palmerston line (flow to South) for loss of a Sheffield to Georgetown line
T>>T_HAPM_110_EXP_3A | 2007-07-23 | 1 | Outage = Hadspen to Palmerston (No.3 or No.4) 110kV line, ensure sufficient Basslink export dispatched for NCSPS action to avoid O/L either Palmerston to Hadspen 220kV line for trip of the other Palmerston to Hadspen 220kV line (outage id's=39,40,41,42)
T>>T_HAPM_110_EXP_3B | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.3 110kV line, ensure sufficient Basslink export dispatched for NCSPS action to avoid O/L Palmerston to Hadspen No.1 220kV line for trip of Palmerston to Sheffield 220kV line (outage id=44)
T>>T_HAPM_110_EXP_3C | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.4 110kV line, ensure sufficient Basslink export dispatched for NCSPS action to avoid O/L Palmerston to Hadspen No.1 220kV line for trip of Palmerston to Sheffield 220kV line (outage id=45)
T>>T_HAPM_110_EXP_3P | 2007-07-23 | 1 | Outage = Hadspen to Palmerston (No.3 or No.4) 110kV line, ensure sufficient Basslink export dispatched for NCSPS action to avoid O/L either Palmerston to Hadspen 110kV line for trip of the Palmerston 220/110kV transformer (outage id's=55,56)
T>>T_HAPM_110_EXP_3Q | 2007-07-23 | 1 | Outage = Hadspen to Palmerston (No.3 or No.4) 110kV line, ensure sufficient Basslink export dispatched for NCSPS action to avoid O/L either Palmerston to Hadspen 110kV line for trip of a Palmerston to Hadspen 220kV line (outage id's=57,58,59,60)
T>>T_HAPM_110_IMP_4A | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.3 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the other Palmerston to Hadspen 220kV line with no SPS action, feedback equation
T>>T_HAPM_110_IMP_4B | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.4 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the other Palmerston to Hadspen 220kV line with no SPS action, feedback equation
T>>T_HAPM_110_IMP_4C | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.3 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.2 220kV line (flow to North) for trip of the other Palmerston to Hadspen 220kV line with no SPS action, feedback equation
T>>T_HAPM_110_IMP_4D | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.4 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.2 220kV line (flow to North) for trip of the other Palmerston to Hadspen 220kV line with no SPS action, feedback equation
T>>T_HAPM_220_1A | 2006-06-08 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L the Sheffield to Georgetown No.1 line for loss of the Georgetown to Sheffield No.2 line, Feedback
T>>T_HAPM_220_1B | 2006-06-08 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L the Sheffield to Georgetown No.2 line for loss of the Georgetown to Sheffield No.1 line, Feedback
T>>T_HAPM_220_2A | 2006-06-08 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L Hadspen to Georgetown No.1 line for loss of the Georgetown to Hadspen No.2 line, Feedback
T>>T_HAPM_220_2B | 2006-06-08 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L Hadspen to Georgetown No.2 line for loss of the Georgetown to Hadspen No.1 line, Feedback
T>>T_HAPM_220_2C | 2008-04-23 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L Georgetown to Hadspen No.1 line (flow to South) for loss of the Georgetown to Hadspen No.2 line, Feedback
T>>T_HAPM_220_2D | 2008-04-23 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L Georgetown to Hadspen No.2 line (flow to South) for loss of the Georgetown to Hadspen No.1 line, Feedback
T>>T_HAPM_220_4A | 2007-05-23 | 2 | Out = Hadspen to Palmerston 220kV line, avoid O/L the Sheffield to Palmerston line (flow to South) for loss of either Georgetown to Sheffield line
T>>T_HAPM_220_4B | 2007-05-23 | 2 | Out = Hadspen to Palmerston 220kV line, avoid O/L the Sheffield to Palmerston line (flow to North) for loss of either Georgetown to Sheffield line
T>>T_HAPM_220_5 | 2006-06-08 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L a Palmerston to Hadspen (No. 3 or No. 4) 110kV line for loss of the remaining Hadspen to Palmerston 220kV line, Feedback
T>>T_HAPM_220_5B | 2008-04-23 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L a Hadspen to Palmerston (No. 3 or No. 4) 110kV line (flow to South) for loss of the remaining Hadspen to Palmerston 220kV line, Feedback
T>>T_HAPM_220_6A | 2006-06-08 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L the Sheffield to Palmerston line (flow to North) for loss of the remaining Hadspen to Palmerston 220kV line
T>>T_HAPM_220_6B | 2006-06-08 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L the Sheffield to Palmerston line (flow to South) for loss of the remaining Hadspen to Palmerston 220kV line
T>>T_HA_GT_220_1 | 2006-06-08 | 1 | Out = Hadspen to Georgetown 220kV line, avoid O/L the Palmerston to Hadspen No.1 220kV line for loss of the Palmerston to Hadspen No.2 220kV line
T>>T_HA_GT_220_2 | 2006-06-08 | 1 | Out = Hadspen to Georgetown 220kV line, avoid O/L the Sheffield to Georgetown No.1 line for loss of the Sheffield to Georgetown No.2 line
T>>T_HA_GT_220_4A | 2006-06-08 | 1 | Out = Hadspen to Georgetown 220kV line, avoid O/L the Sheffield to Palmerston line (flow to North) for loss of the Sheffield to Georgetown No.2 line
T>>T_HA_GT_220_4B | 2006-06-08 | 1 | Out = Hadspen to Georgetown 220kV line, avoid O/L the Sheffield to Palmerston line (flow to South) for loss of the Sheffield to Georgetown No.2 line
T>>T_NIL_BL_220_6A | 2006-08-15 | 1 | Outage = Nil, Basslink in service, avoid overloading the Palmerston to Sheffield 220kV line (flow to North) for loss of a Sheffield to Georgetown 220kV line, feedback equation, swamp if Basslink exporting
T>>T_NIL_BL_220_6B | 2008-07-01 | 1 | Outage = Nil, Basslink in service, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation
T>>T_NIL_BL_3A | 2006-08-16 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Palmerston to Hadspen No.1 220kV line, feedback equation
T>>T_NIL_BL_3B | 2006-08-16 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Palmerston to Hadspen No.2 220kV line, feedback equation
T>>T_NIL_BL_3C | 2007-02-13 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Palmerston to Hadspen 220kV line for trip of the other Palmerston to Hadspen 220kV line (outage id's=31,32) taking into account NCSPS generation reduction
T>>T_NIL_BL_3E | 2007-06-21 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Palmerston to Hadspen 220kV line for trip of a Sheffield to Georgetown 220kV line (outage id's=34,35) taking into account NCSPS generation reduction
T>>T_NIL_BL_5+6_A | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tas gen to avoid post-contingent O/L on Hadspen to Georgetown, Sheffield to Georgetown for trip of Palmerston to Sheffield (outage id's=73,83) taking into account Basslink export available for SPS action
T>>T_NIL_BL_5+6_B | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tas gen to avoid post-contingent O/L on Hadspen to Georgetown, Sheffield to Georgetown for trip of Sheffield to Georgetown (outage id's=74,75,81,82) taking into account Basslink export available for SPS action
T>>T_NIL_BL_5A | 2006-08-16 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Hadspen to Georgetown No.1 220kV line, feedback equation
T>>T_NIL_BL_5B | 2006-08-16 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Hadspen to Georgetown No.2 220kV line, feedback equation
T>>T_NIL_BL_5C | 2007-02-13 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Hadspen to Georgetown 220kV line for trip of the other Hadspen to Georgetown 220kV line (outage id's=71,72) taking into account NCSPS generation reduction
T>>T_NIL_BL_5E | 2007-02-13 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Hadspen to Georgetown 220kV line for trip of a Sheffield to Georgetown 220kV line (outage id's=74,75) taking into account NCSPS generation reduction
T>>T_NIL_BL_6A | 2006-08-16 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Sheffield to Georgetown No.1 220kV line, feedback equation
T>>T_NIL_BL_6B | 2006-08-16 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Sheffield to Georgetown No.2 220kV line, feedback equation
T>>T_NIL_BL_6C | 2006-08-07 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Sheffield to Georgetown 220kV line for trip of the other Sheffield to Georgetown 220kV line (outage id's=81,82) taking into account NCSPS generation reduction
T>>T_NIL_BL_6D | 2006-08-07 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Sheffield to Georgetown 220kV line for trip of the Palmerston to Sheffield 220kV line (outage id=83) taking into account NCSPS generation reduction
T>>T_NIL_BL_EXP_1B | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Gordon to Chapel St 220kV line for trip of the other Gordon to Chapel St line (outage id's=1,2) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_2B | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Liapootah to Palmerston No.1 220kV line for trip of Liapootah to Palmerston No.2 line (outage id=21) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_3F | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Palmerston to Hadspen 220kV line for trip of other Palmerston to Hadspen 220kV line (outage id's=31,32) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_3G | 2007-06-21 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Palmerston to Hadspen 220kV line for trip of Palmerston to Sheffield 220kV line (outage id=33) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_4E | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Palmerston to Hadspen 110kV line for trip of other Palmerston to Hadspen 110kV line (outage id's=51,52) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_4F | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Palmerston to Hadspen 110kV line for trip of Palmerston 220/110kV transformer (outage id=53) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_5F | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Hadspen to Georgetown 220kV line for trip of Hadspen to Georgetown 220kV line (outage id's=71,72) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_5G | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Hadspen to Georgetown 220kV line for trip of Palmerston to Sheffield 220kV line (outage id=73) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_5H | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Hadspen to Georgetown 220kV line for trip of Sheffield to Georgetown 220kV line (outage id's=74,75) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_6E | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Sheffield to Georgetown 220kV line for trip of Sheffield to Georgetown line (outage id's=81,82) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_6F | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Sheffield to Georgetown 220kV line for trip of Palmerston to Sheffield 220kV line (outage id=83) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_7C | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, Hampshire link open, limit Tas gen to avoid post-contingent O/L of Farrell to Sheffield 220kV line for trip of Farrell to Sheffield line (outage id's=91,92) taking into account Basslink export available for SPS action
T>>T_NIL_BL_IMP_3F | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the other Palmerston to Hadspen 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_3FF | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.2 220kV line (flow to North) for trip of the other Palmerston to Hadspen 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_3H | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.1 220kV line (flow to North) for trip of a Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_3HH | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.2 220kV line (flow to North) for trip of a Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_3I | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.1 220kV line (flow to South) for trip of the other Palmerston to Hadspen 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_3II | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.2 220kV line (flow to South) for trip of the other Palmerston to Hadspen 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_3K | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen 220kV No.1 line (flow to South) for trip of a Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_3KK | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen 220kV No.2 line (flow to South) for trip of a Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_5F | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.1 220kV line (flow to North) for trip of the other Hadspen to Georgetown 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_5FF | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.2 220kV line (flow to North) for trip of the other Hadspen to Georgetown 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_5H | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.1 220kV line (flow to North) for trip of a Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_5HH | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.2 220kV line (flow to North) for trip of a Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_5I | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.1 220kV line (flow to South) for trip of the other Hadspen to Georgetown 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_5II | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.2 220kV line (flow to South) for trip of the other Hadspen to Georgetown 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_5K | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.1 220kV line (flow to South) for trip of a Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_5KK | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.2 220kV line (flow to South) for trip of a Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_6E | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.1 220kV line (flow to North) for trip of the other Sheffield to Georgetown line with no SPS action, fedback equation
T>>T_NIL_BL_IMP_6EE | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.2 220kV line (flow to North) for trip of the other Sheffield to Georgetown line with no SPS action, fedback equation
T>>T_NIL_BL_IMP_6F | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.1 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_6FF | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.2 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_6G | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.1 220kV line (flow to South) for trip of the other Sheffield to Georgetown line with no SPS action, eedback equation
T>>T_NIL_BL_IMP_6GG | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.2 220kV line (flow to South) for trip of the other Sheffield to Georgetown line with no SPS action, eedback equation
T>>T_NIL_BL_IMP_6H | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.1 220kV line (flow to South) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>>T_NIL_BL_IMP_6HH | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.2 220kV line (flow to South) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>>T_PMSH_220_1 | 2008-04-22 | 1 | Out = Palmerston to Sheffield 220kV line, avoid O/L Georgetown to Sheffield No.1 line for loss of a Georgetown to Sheffield No.2 line
T>>T_PMWA_1D | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tas generation and Basslink to avoid pre-contingent and post-contingent overloading the Hadspen to Palmerston No.1 220kV line (flow to North), feedback equation
T>>T_PMWA_1DD | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tas generation and Basslink to avoid pre-contingent and post-contingent overloading the Hadspen to Palmerston No.2 220kV line (flow to North), feedback equation
T>>T_PMWA_2D | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tas generation to avoid O/L either Palmerston to Hadspen 220kV line for trip of the other Palmerston to Hadspen 220kV line (outage id's=37,38) taking into account NCSPS generation reduction
T>>T_PMWA_EXP_3A | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, ensure sufficient Basslink export dispatched for NCSPS action to avoid O/L Cluny Tee to Liapootah No.1 220kV line (flow to North) for trip of Chapel St to Liapootah No.2 220kV line (outage id=11)
T>>T_PMWA_EXP_3B | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, ensure sufficient Basslink export dispatched for NCSPS action to avoid O/L Chapel St to Liapootah No.2 220kV line (flow to North) for trip of Chapel St to Cluny Tee to Liapootah No.1 220kV line (outage id=12)
T>>T_PMWA_EXP_3C | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, ensure sufficient Basslink export dispatched for NCSPS action to avoid O/L Liapootah to Palmerston No.1 220kV line (flow to North) for trip of Liapootah to Palmerston No.2 220kV line (outage id=23)
T>>T_PMWA_EXP_3CC | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, ensure sufficient Basslink export dispatched for NCSPS action to avoid O/L Liapootah to Palmerston No.2 220kV line (flow to North) for trip of Liapootah to Palmerston No.1 220kV line (outage id=24)
T>>T_PMWA_EXP_3D | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, ensure sufficient Basslink export dispatched for NCSPS action to avoid O/L either Palmerston to Hadspen 220kV line for trip of the other Palmerston to Hadspen 220kV line (outage id's=37,38)
T>>T_PMWA_EXP_3DDD | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, ensure sufficient Basslink export dispatched for NCSPS action to avoid O/L Palmerston to Hadspen No.1 220kV line for trip of Palmerston to Sheffield 220kV line (outage id=43)
T>>T_PMWA_IMP_4D | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the other Palmerston to Hadspen 220kV line with no SPS action, feedback equation
T>>T_PMWA_IMP_4DD | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.2 220kV line (flow to North) for trip of the other Palmerston to Hadspen 220kV line with no SPS action, feedback equation
T>>T_X_GTSH_1 | 2008-07-16 | 1 | Outage = Both Georgetown to Sheffield 220kV lines, avoid O/L of Georgetown to Hadspen line (in this direction) for trip of Hadspen to Georgetown line
T>>T_X_GTSH_2 | 2008-07-16 | 1 | Outage = Both Georgetown to Sheffield 220kV lines, avoid O/L of Hadspen to Georgetown line (in this direction) for trip of Hadspen to Georgetown line
T>>T_X_HAGT_1 | 2008-07-16 | 1 | Outage = Both Hadspen to Georgetown 220kV lines, avoid O/L of Georgetown to Sheffield line (in this direction) for trip of Georgetown to Sheffield line
T>>T_X_HAGT_2 | 2008-07-16 | 1 | Outage = Both Hadspen to Georgetown 220kV lines, avoid O/L of Sheffield to Georgetown line (in this direction) for trip of Georgetown to Sheffield line
T>CS_TX3_RI_TRIP | 2007-10-23 | 1 | Out = Chapel St No.3 220/110kV transformer, Chapel St Transformer overload guard armed, avoid overloading a Chapel St 220/110kV transformer for loss of a parallel transformer, Feedback
T>CS_TX4_RI_TRIP | 2007-10-23 | 1 | Out = Chapel St No.4 220/110kV transformer, Chapel St Transformer overload guard armed, avoid overloading a Chapel St 220/110kV transformer for loss of a parallel transformer, Feedback
T>CS_TX4_RI_TRIP_PM | 2005-06-30 | 1 | Out = Chapel St No.4 220/110kV transformer, Chapel St Transformer overload guard armed, Palmerston 110kV bus split, avoid overloading a Chapel St 220/110kV transformer for loss of a parallel transformer, Feedback
T>TR_TX | 2007-01-11 | 1 | Out= one Trevallyn 110/11 kV transformer, upper limit for Trevallyn generation of 40 MW
T>T_BELLBAYINTERTRIP | 2006-10-16 | 1 | Out = Bell Bay Intertrip scheme, avoid O/L a Georgetown 220/110kV transformer for loss of parallel transformer
T>T_BUSH1_220 | 2005-05-16 | 1 | Out = Burnie to Sheffield 220kV line, Hampshire link open, avoid O/L a Sheffield 220/110kV transformer for loss of the other Sheffield 220/110kV transformer
T>T_BUSH1_220_HM | 2005-06-21 | 1 | Out = Burnie to Sheffield 220kV line, Hampshire link closed, avoid O/L a Sheffield 220/110kV transformer for loss of the other Sheffield 220/110kV transformer
T>T_BUSH1_220_HM_B | 2007-05-10 | 1 | Out = Burnie to Sheffield 220kV line; Hampshire link closed and Burnie 110kV bus split; avoid O/L a Sheffield 220/110kV transformer for loss of the other Sheffield 220/110kV transformer
T>T_BWLF_110_1 | 2006-06-08 | 1 | Out = Bridgewater to Lindisfarne 110kV line, avoid O/L the Chapel Street to New Norfolk line for loss of New Norfolk to Creek Road line
T>T_BWLF_110_2 | 2006-06-08 | 1 | Out = Bridgewater to Lindisfarne 110kV line, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of the Meadowbank to New Norfolk line
T>T_BWLF_110_3 | 2006-06-08 | 1 | Out = Bridgewater to Lindisfarne 110kV line, avoid O/L the Tarraleah to Meadowbank line for loss of the Tarraleah to New Norfolk line
T>T_BWLF_110_4 | 2006-06-08 | 1 | Out = Bridgewater to Lindisfarne 110kV line, avoid O/L the New Norfolk to Creek Road line for loss of the New Norfolk to Chapel St line
T>T_BWWA_110_1 | 2006-06-08 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Waddamana to Lindisfarne line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split
T>T_BWWA_110_2A | 2006-06-08 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Palmerston to Waddamana line (flow to North) for loss of a Liapootah to Palmerston line
T>T_BWWA_110_2A_RED5 | 2005-06-22 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Palmerston to Waddamana line (flow to North) for loss of a Liapootah to Palmerston line, reduced by 5 MW for coincident outage
T>T_BWWA_110_2B | 2006-06-08 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Palmerston to Waddamana line (flow to South) for loss of a Liapootah to Palmerston line
T>T_BWWA_110_2B_RED5 | 2005-06-22 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Palmerston to Waddamana line (flow to South) for loss of a Liapootah to Palmerston line, reduced by 5 MW for coincident outage
T>T_BWWA_110_3 | 2006-06-08 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Tungatinah to Lake Echo Tee No.1 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.2 line
T>T_BWWA_110_4 | 2006-06-08 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Waddamana to Lake Echo Tee No.1 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.2 line
T>T_BWWA_110_5 | 2006-06-08 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Tarraleah to Meadowbank line for loss of the Tarraleah to New Norfolk No.2 line
T>T_BWWA_110_5_RED5 | 2006-06-22 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Tarraleah to Meadowbank line for loss of the Tarraleah to New Norfolk No.2 line, reduced by 5 MW for coincident outage
T>T_BWWA_110_6 | 2006-06-08 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Tarraleah to New Norfolk No.2 line for loss of the Meadowbank to New Norfolk line
T>T_BWWA_110_6_RED5 | 2006-06-22 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Tarraleah to New Norfolk No.2 line for loss of the Meadowbank to New Norfolk line, reduced by 5 MW for coincident outage
T>T_BWWA_110_7 | 2006-06-08 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L a Tungatinah to Tarraleah line for loss of the other Tungtainah to Tarraleah line
T>T_BWWA_110_7_RED5 | 2006-06-22 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L a Tungatinah to Tarraleah line for loss of the other Tungtainah to Tarraleah line, reduced by 5 MW for coincident outage
T>T_BWWA_110_8 | 2006-06-08 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Meadowbank to New Norfolk line for loss of the Tarraleah to New Norfolk No.2 line
T>T_BWWA_110_8_RED5 | 2006-06-22 | 1 | Out = Bridgewater to Waddamana 110kV line, avoid O/L the Meadowbank to New Norfolk line for loss of the Tarraleah to New Norfolk No.2 line, reduced by 5 MW for coincident outage
T>T_CRNN_1 | 2007-01-22 | 1 | Out = Creek Road to New Norfolk 110kV line, avoid O/L the Waddamana to Lake Echo Tee No.1 line for loss of Chapel St to New Norfolk 110kV line
T>T_CRNN_2 | 2007-01-22 | 1 | Out = Creek Road to New Norfolk 110kV line, avoid O/L the Chapel St to New Norfolk 110kV line for loss of Waddamana to Lake Echo Tee to Tungatinah No.1 line with Waddamana bus split
T>T_CRNN_3 | 2007-01-22 | 1 | Out = Creek Road to New Norfolk 110kV line, avoid O/L the Tungatinah to Lake Echo Tee No.1 line for loss of Chapel St to New Norfolk 110kV line
T>T_CSCL_T_11A | 2006-02-21 | 1 | Out = Chapel St to Cluny Tee 220kV line, avoid O/L the Liapootah to Palmerston No.1 line (flow to North) for loss of the other Liapootah to Palmerston line
T>T_CSCL_T_11B | 2006-02-21 | 1 | Out = Chapel St to Cluny Tee 220kV line, avoid O/L the Liapootah to Palmerston No.1 line (flow to South) for loss of the other Liapootah to Palmerston line
T>T_CSCL_T_9A | 2006-08-07 | 2 | Out = Chapel St to Cluny Tee 220kV line, avoid O/L the Palmerston to Waddamana line (flow to North) for loss of the Liapootah to Chapel St line
T>T_CSCL_T_9B | 2006-08-07 | 2 | Out = Chapel St to Cluny Tee 220kV line, avoid O/L the Palmerston to Waddamana line (flow to South) for loss of the Liapootah to Chapel St line
T>T_CSNN_1 | 2007-03-15 | 1 | Out = Chapel St to New Norfolk 110kV line, avoid O/L the Waddamana to Lake Echo Tee No.1 line for loss of Creek Rd to New Norfolk 110kV line, swamp if either LE-LETee is open
T>T_CSNN_1A | 2007-03-16 | 1 | Out = Chapel St to New Norfolk 110kV line, avoid O/L the Waddamana to Lake Echo Tee No.1 line for loss of Creek Rd to New Norfolk 110kV line, swamp if LE-LE1 open or LE-LE2 in service
T>T_CSNN_1B | 2007-03-16 | 1 | Out = Chapel St to New Norfolk 110kV line, avoid O/L the Waddamana to Lake Echo Tee No.2 line for loss of Creek Rd to New Norfolk 110kV line, swamp if LE-LE1 in service or LE-LE2 open
T>T_CSNN_2 | 2007-03-16 | 1 | Out = Chapel St to New Norfolk 110kV line, avoid O/L the Creek Rd to New Norfolk 110kV line for loss of Waddamana to Lake Echo Tee to Tungatinah No.1 line with Waddamana bus split, swamp if LE-LE2 open
T>T_CSNN_2A | 2007-03-15 | 1 | Out = Chapel St to New Norfolk 110kV line, avoid O/L Creek Rd to New Norfolk 110kV line for loss Waddamana to Lake Echo Tee to Tungatinah No.2 line radialising Bridgewater to Waddamana line from Bridgewater, swamp if LE-LE1 open or LE-LE2 in service
T>T_CSNN_3 | 2007-03-15 | 1 | Out = Chapel St to New Norfolk 110kV line, avoid O/L the Tungatinah to Lake Echo Tee No.1 line for loss of Creek Rd to New Norfolk 110kV line, swamp if either LE-LETee is open
T>T_CSNN_3A | 2007-03-16 | 1 | Out = Chapel St to New Norfolk 110kV line, avoid O/L the Tungatinah to Lake Echo Tee No.1 line for loss of Creek Rd to New Norfolk 110kV line, swamp if LE-LE1 open or LE-LE2 in service
T>T_CSNN_3B | 2007-03-16 | 1 | Out = Chapel St to New Norfolk 110kV line, avoid O/L the Tungatinah to Lake Echo Tee No.2 line for loss of Creek Rd to New Norfolk 110kV line, swamp if LE-LE1 in service or LE-LE2 open
T>T_CSRI_RI+LF_R_10A | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, avoid O/L the New Norfolk to Chapel St line (flow to North) for loss of the New Norfolk to Creek Rd line
T>T_CSRI_RI+LF_R_10B | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, avoid O/L the New Norfolk to Chapel St line (flow to South) for loss of the New Norfolk to Creek Rd line
T>T_CSRI_RI+LF_R_11A | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, avoid O/L the New Norfolk to Creek Rd line (flow to North) for loss of the New Norfolk to Chapel St line
T>T_CSRI_RI+LF_R_11B | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, avoid O/L the New Norfolk to Creek Rd line (flow to South) for loss of the New Norfolk to Chapel St line
T>T_CSRI_RI+LF_R_12 | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, avoid O/L the Meadowbank to New Norfolk line for loss of the Tarraleah to New Norfolk No.2 line
T>T_CSRI_RI+LF_R_4 | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, avoid O/L the Palmerston to Waddamana line for loss of Liapootah to Palmerston No.2 line
T>T_CSRI_RI+LF_R_5 | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, avoid O/L the Tarraleah to Meadowbank line for loss of Tarraleah to New Norfolk No.2 line
T>T_CSRI_RI+LF_R_6 | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of the Meadowbank to New Norfolk line
T>T_CSRI_RI+LF_R_7 | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, avoid O/L Waddamana to LETee No.1 line for loss of Tungatinah-LETee-Waddamana No.2 line and Bridgewater to Waddamana line
T>T_CSRI_RI+LF_R_7L | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, Lake Echo gen only on TU-LETee-WA No.2 line, avoid O/L Waddamana to LETee No.1 line for loss of TU-LETee-WA No.2 line and BW-WA line
T>T_CSRI_RI+LF_R_8A | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, avoid O/L a Tarraleah to Tungatinah line (flow to North) for loss of the other Tarraleah to Tungatinah line
T>T_CSRI_RI+LF_R_8B | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, avoid O/L a Tarraleah to Tungatinah line (flow to South) for loss of the other Tarraleah to Tungatinah line
T>T_CSRI_RI+LF_R_9 | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, avoid O/L Tungatinah to Lake Echo Tee No.1 line for loss of Tungatinah-LETee-Waddamana No.2 line and Bridgewater to Waddamana line
T>T_CSRI_RI+LF_R_9L | 2007-01-17 | 1 | Out = Chapel St to Risdon 110kV line with Lindisfarne radial from Waddamana & Bridgewater, Risdon radial from Chapel St, Lake Echo gen only on TU-LETee-WA No.2 line, avoid O/L Tungatinah to LETee No.1 line for loss of TU-LETee-WA No.2 line and BW-WA line
T>T_CS_TX1 | 2007-10-23 | 1 | Out = Chapel St No.1 220/110kV transformer, avoid overloading a Chapel St 220/110kV transformer for loss of a parallel transformer, Feedback
T>T_CS_TX1_PM_SPLIT | 2005-05-16 | 1 | Out = Chapel St No.1 220/110kV transformer, Palmerston 110kV bus split, avoid overloading a Chapel St 220/110kV transformer for loss of a parallel transformer, Feedback
T>T_CS_TX2 | 2007-10-23 | 1 | Out = Chapel St No.2 220/110kV transformer, avoid overloading a Chapel St 220/110kV transformer for loss of a parallel transformer, Feedback
T>T_CS_TX2_PM_SPLIT | 2005-05-16 | 1 | Out = Chapel St No.2 220/110kV transformer, Palmerston 110kV bus split, avoid overloading a Chapel St 220/110kV transformer for loss of a parallel transformer, Feedback
T>T_CS_TX3 | 2007-10-23 | 1 | Out = Chapel St No.3 220/110kV transformer, avoid overloading a Chapel St 220/110kV transformer for loss of a parallel transformer, Feedback
T>T_CS_TX3_PM_SPLIT | 2005-05-16 | 1 | Out = Chapel St No.3 220/110kV transformer, Palmerston 110kV bus split, avoid overloading a Chapel St 220/110kV transformer for loss of a parallel transformer, Feedback
T>T_CS_TX4 | 2007-10-23 | 1 | Out = Chapel St No.4 220/110kV transformer, avoid overloading a Chapel St 220/110kV transformer for loss of a parallel transformer, Feedback
T>T_FASH1_A_1 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Hampshire link closed, avoid O/L Hampshire to Waratah Tee line
T>T_FASH1_A_2 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Hampshire link closed, avoid O/L Paloona to Ulverstone line for loss of the Burnie to Sheffield No.1 line
T>T_FASH1_A_3 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Hampshire link closed, avoid O/L Sheffield to Burnie No.2 line for loss of the Burnie to Sheffield No.1 line
T>T_FASH1_A_4 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, avoid O/L Farrell to Sheffield No.2 line
T>T_FASH1_B_1 | 2006-01-10 | 1 | Out = Farrell to Sheffield No.2 line, Farrell 220kV bus split with JButters supplying 220/110kV transformers and other generators supplying the 220kV line to Sheffield, Hampshire link closed, avoid O/L Hampshire to Waratah Tee line
T>T_FASH1_B_2 | 2006-01-10 | 1 | Out = Farrell to Sheffield No.2 line, Farrell 220kV bus split JButters supplying transformers other generators supplying the 220kV line to Sheffield, Hampshire link closed, avoid O/L Paloona to Ulverstone line for loss of Burnie to Sheffield No.1 line
T>T_FASH1_B_3 | 2006-01-10 | 1 | Out = Farrell to Sheffield No.2 line, Farrell 220kV bus split JButters supplying transformers other generators supplying the 220kV line to Sheffield,Hampshire link closed, avoid O/L Sheffield to Burnie No.2 line for loss of Burnie to Sheffield No.1 line
T>T_FASH1_B_4 | 2006-01-10 | 1 | Out = Farrell to Sheffield No.2 line, Farrell 220kV bus split JButters supplying transformers other generators supplying the 220kV line to Sheffield, limit Tribute+Bastyan+Reece 1&2 to avoid O/L Farrell to Sheffield No.1 line
T>T_FASH2_A_1 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Hampshire link closed, avoid O/L Hampshire to Waratah Tee line
T>T_FASH2_A_2 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield Hampshire link closed, avoid O/L Paloona to Ulverstone line for loss of the Burnie to Sheffield No.1 line
T>T_FASH2_A_3 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Hampshire link closed, avoid O/L Sheffield to Burnie No.2 line for loss of the Burnie to Sheffield No.1 line
T>T_FASH2_A_4 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, avoid O/L Farrell to Sheffield No.1 line
T>T_FASH_1_2_A | 2006-02-06 | 1 | Out = one Farrell to Sheffield line with Mackintosh unavailable, Hampshire link closed, limit West Coast gen to avoid avoid O/L Hampshire to Waratah Tee line
T>T_FASH_1_2_B1 | 2006-12-22 | 1 | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, Hamp. link closed, JButters+Bastyan+Mack supplying transformers other generators supplying 220kV line to Sheffield, limit JButters, Bastyan and Mackintosh <= 110% of West Coast load
T>T_FASH_1_2_B2 | 2006-12-22 | 1 | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, Hamp. link closed, JButters+Bastyan+Mack supplying transformers other generators supplying 220kV line to Sheffield, limit JButters, Bastyan and Mackintosh >= 90% of West Coast load
T>T_FASH_1_2_C1 | 2007-06-07 | 1 | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, Hamp. link closed, Bastyan+Mack supplying transformers other generators supplying 220kV line to Sheffield, limit Bastyan and Mackintosh <= 110% of West Coast load
T>T_FASH_1_2_C2 | 2007-06-07 | 1 | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, Hamp. link closed, Bastyan+Mack supplying transformers other generators supplying 220kV line to Sheffield, limit Bastyan and Mackintosh >= 90% of West Coast load
T>T_FASH_1_2_D1 | 2007-11-19 | 2 | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, Hamp. link closed, Reece 1+ Mackintosh supplying transformers other generators supplying 220kV line to Sheffield, limit Reece 1 and Mackintosh <= 110% of West Coast load
T>T_FASH_1_2_D2 | 2007-11-19 | 2 | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, Hamp. link closed, Reece 1 + Mackintosh supplying transformers other generators supplying 220kV line to Sheffield, limit Reecce 1 and Mackintosh >= 90% of West Coast load
T>T_FASH_1_N-2 | 2006-01-06 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, avoid O/L Hampshire to Waratah Tee line
T>T_FASH_2_N-2 | 2008-08-27 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, avoid O/L Farrell 220/110kV No.2 transformer
T>T_GTSH_110_1 | 2006-06-08 | 2 | Out = Georgetown to Sheffield 220kV line, avoid O/L a Palmerston to Hadspen (No.3 or No.4) 110kV line for loss of the other Hadspen to Palmerston 110kV line
T>T_GT_BUSPROT_110_1 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 1 only
T>T_GT_BUSPROT_110_2 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 1 and BBThree unit 1
T>T_GT_BUSPROT_110_3 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 1 and BBThree unit 2
T>T_GT_BUSPROT_110_4 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 1 and BBThree unit 3
T>T_GT_BUSPROT_110_5 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 1 and BBThree units 1,2
T>T_GT_BUSPROT_110_6 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 1 and BBThree units 1,3
T>T_GT_BUSPROT_110_7 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 1 and BBThree units 2,3
T>T_GT_BUSPROT_110_8 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 1 and BBThree units 1,2,3
T>T_GT_BUSPRO_110_11 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 2 only
T>T_GT_BUSPRO_110_12 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 2 and BBThree unit 1
T>T_GT_BUSPRO_110_13 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 2 and BBThree unit 2
T>T_GT_BUSPRO_110_14 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 2 and BBThree unit 3
T>T_GT_BUSPRO_110_15 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 2 and BBThree units 1,2
T>T_GT_BUSPRO_110_16 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 2 and BBThree units 1,3
T>T_GT_BUSPRO_110_17 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 2 and BBThree units 2,3
T>T_GT_BUSPRO_110_18 | 2008-01-29 | 1 | Out = Georgetown 110kV A and B bus protection, limit flow on BB-GT 110kV #1 line to 120MW, limit BB unit 2 and BBThree units 1,2,3
T>T_GT_TX1 | 2008-07-31 | 1 | Out = Georgetown No.1 220/110kV transformer, avoid O/L Georgetown No.2 or No.3 220/110kV transformer
T>T_GT_TX1+3_TRIPARM | 2008-08-05 | 1 | Out = Georgetown No.1 and No.3 220/110kV transformers, Georgetown to Bell Bay contingency tripping scheme armed, avoid O/L Georgetown No.2 220/110kV transformer
T>T_GT_TX1+TX2 | 2008-02-22 | 1 | Out = Georgetown No.1 and no.2 220/110kV transformers, avoid O/L the Georgetown No.3 220/110kV transformer
T>T_GT_TX2 | 2008-07-31 | 1 | Out = Georgetown No.2 220/110kV transformer, avoid O/L Georgetown No.1 or No.3 220/110kV transformer
T>T_GT_TX2+3_TRIPARM | 2008-08-05 | 1 | Out = Georgetown No.2 and No.3 220/110kV transformers, Georgetown to Bell Bay contingency tripping scheme armed, avoid O/L Georgetown No.1 220/110kV transformer
T>T_GT_TX2+TX3 | 2008-02-22 | 1 | Out = Georgetown No.2 and no.3 220/110kV transformers, avoid O/L the Georgetown No.1 220/110kV transformer
T>T_GT_TX2_BBTRIP_OS | 2008-04-10 | 1 | Out = George Town No.2 220/110kV transformer, avoid O/L the remaining Georgetown No.1 and no.3 220/110kV transformers, assuming the George Town Auto-transformer Overload Protection Scheme not in service
T>T_GT_TX3 | 2008-07-31 | 1 | Out = Georgetown No.3 220/110kV transformer, avoid O/L Georgetown No.1 or No.2 220/110kV transformer
T>T_HAPM_110_1 | 2006-06-08 | 2 | Out = Hadspen to Palmerston 110kV line, avoid O/L a Hadspen to Palmerston 110kV line for loss of a Hadspen to Palmerston 220kV line
T>T_HAPM_110_1P | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.4 110kV line, limit Tas generation to avoid pre-contingent and post-contingent overloading the Hadspen to Palmerston No.3 110kV line (flow to North), feedback equation
T>T_HAPM_110_1Q | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.3 110kV line, limit Tas generation to avoid pre-contingent and post-contingent overloading the Hadspen to Palmerston No.4 110kV line (flow to North), feedback equation
T>T_HAPM_110_2B | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.3 110kV line, limit Tas generation to avoid O/L Palmerston to Hadspen No.1 220kV line for trip of Palmerston to Sheffield 220kV line (outage id=44) taking into account NCSPS generation reduction
T>T_HAPM_110_2C | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.4 110kV line, limit Tas generation to avoid O/L Palmerston to Hadspen No.1 220kV line for trip of Palmerston to Sheffield 220kV line (outage id=45) taking into account NCSPS generation reduction
T>T_HAPM_110_2P | 2007-07-23 | 1 | Outage = Hadspen to Palmerston (No.3 or No.4) 110kV line, limit Tas generation to avoid O/L Palmerston to Hadspen 110kV line for trip of Palmerston 220/110kV transformer (outage id's=55,56) taking into account NCSPS generation reduction
T>T_HAPM_110_2Q | 2007-07-23 | 1 | Outage = Hadspen to Palmerston (No.3 or No.4) 110kV line, limit Tas generation to avoid O/L Palmerston to Hadspen 110kV line for trip of Palmerston to Hadspen 220kV line (outage id's=57,58,59,60) taking into account NCSPS generation reduction
T>T_HAPM_110_IMP_4E | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.3 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_HAPM_110_IMP_4F | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.4 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_HAPM_110_IMP_4P | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.4 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.3 110kV line (flow to North) for trip of Palmerston 220/110kV transformer with no SPS action, feedback equation
T>T_HAPM_110_IMP_4Q | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.3 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.4 110kV line (flow to North) for trip of Palmerston 220/110kV transformer with no SPS action, feedback equation
T>T_HAPM_110_IMP_4R | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.4 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.3 110kV line (flow to North) for trip of Palmerston to Hadspen No.1 220kV line with no SPS action, feedback equation
T>T_HAPM_110_IMP_4S | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.4 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.3 110kV line (flow to North) for trip of Palmerston to Hadspen No.2 220kV line with no SPS action, feedback equation
T>T_HAPM_110_IMP_4T | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.3 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.4 110kV line (flow to North) for trip of Palmerston to Hadspen No.1 220kV line with no SPS action, feedback equation
T>T_HAPM_110_IMP_4U | 2007-07-23 | 1 | Outage = Hadspen to Palmerston No.3 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.4 110kV line (flow to North) for trip of Palmerston to Hadspen No.2 220kV line with no SPS action, feedback equation
T>T_HAPM_220_3A | 2007-05-17 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L the Palmerston to Hadspen No.2 220kV line for loss of the Palmerston to Sheffield line, Feedback
T>T_HAPM_220_3B | 2007-05-17 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L the Palmerston to Hadspen No.1 220kV line for loss of the Palmerston to Sheffield line, Feedback
T>T_HAPM_220_3C | 2008-04-23 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L the Hadspen to Palmerston No.2 220kV line (flow to South) for loss of the Palmerston to Sheffield line, Feedback
T>T_HAPM_220_3D | 2008-04-23 | 1 | Out = Hadspen to Palmerston 220kV line, avoid O/L the Hadspen to Palmerston No.1 220kV line (flow to South) for loss of the Palmerston to Sheffield line, Feedback
T>T_HA_GT_220_3A | 2005-11-29 | 1 | Out = Hadspen to Georgetown 220kV line, avoid O/L the Sheffield to Palmerston No.1 line (flow to North) for loss of the Hadspen to Georgetown No.2 line
T>T_HA_GT_220_3B | 2005-11-29 | 1 | Out = Hadspen to Georgetown 220kV line, avoid O/L the Sheffield to Palmerston No.1 line (flow to South) for loss of the Hadspen to Georgetown No.2 line
T>T_HA_TX | 2005-06-09 | 1 | Out = Hadspen 220/110kV transformer, avoid O/L Palmerston 220/110kV transformer for loss of the remaining Hadspen 220/110kV transformer
T>T_LE_T_WA_2_1 | 2005-05-16 | 1 | Out = Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Meadowbank to New Norfolk line for loss of a Tarraleah to New Norfolk line
T>T_LE_T_WA_2_10 | 2005-05-16 | 1 | Out = Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Meadowbank to New Norfolk line for loss of Lake Echo to Lake Echo Tee No.1 line
T>T_LE_T_WA_2_2 | 2005-05-16 | 1 | Out = Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Waddamana to Lake Echo No.1 line for loss of a Tarraleah to New Norfolk line
T>T_LE_T_WA_2_3 | 2005-05-16 | 1 | Out = Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Waddamana to Lake Echo No.1 line for loss of the Meadowbank to New Norfolk line
T>T_LE_T_WA_2_4 | 2005-05-16 | 1 | Out = Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L a Tarraleah to Tungatinah line for loss of the other Tarraleah to Tungatinah line
T>T_LE_T_WA_2_5 | 2005-05-16 | 1 | Out = Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of the other Tarraleah to New Norfolk line
T>T_LE_T_WA_2_6 | 2005-05-16 | 1 | Out = Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of Lake Echo to Lake Echo Tee No.1 line
T>T_LE_T_WA_2_7 | 2005-05-16 | 1 | Out = Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of the Meadowbank to New Norfolk line
T>T_LE_T_WA_2_8 | 2005-05-16 | 1 | Out = Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Chapel St to New Norfolk line for loss of the Creek Rd to New Norfolk line
T>T_LE_T_WA_2_9 | 2005-05-16 | 1 | Out = Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Creek Rd to New Norfolk line for loss of the Chapel St to New Norfolk line
T>T_LFWA_110_1A | 2006-01-10 | 1 | Out = Lindisfarne to Waddamana 110kV line, avoid O/L the Waddamana to Lake Echo Tee No.1 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.2 line with Waddamana bus split
T>T_LFWA_110_2A | 2005-11-29 | 1 | Out = Lindisfarne to Waddamana 110kV line, avoid O/L the Palmerston to Waddamana line (flow to North) for loss of a Liapootah to Palmerston line
T>T_LFWA_110_2B | 2005-11-29 | 1 | Out = Lindisfarne to Waddamana 110kV line, avoid O/L the Palmerston to Waddamana line (flow to South) for loss of a Liapootah to Palmerston line
T>T_LFWA_110_3 | 2005-11-29 | 1 | Out = Lindisfarne to Waddamana 110kV line, avoid O/L a Tungatinah to Tarraleah line for loss of the other Tungtainah to Tarraleah line
T>T_LFWA_110_4 | 2006-01-10 | 1 | Out = Lindisfarne to Waddamana 110kV line, avoid O/L the Waddamana to Lake Echo Tee No.2 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split
T>T_LFWA_110_5 | 2005-11-29 | 1 | Out = Lindisfarne to Waddamana 110kV line, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of the Meadowbank to New Norfolk line
T>T_LFWA_110_6 | 2006-01-10 | 1 | Out = Lindisfarne to Waddamana 110kV line, avoid O/L the Tungatinah to Lake Echo Tee No.2 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split
T>T_LFWA_110_7A | 2006-01-10 | 1 | Out = Lindisfarne to Waddamana 110kV line, avoid O/L the Tungatinah to Lake Echo Tee No.1 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.2 line with Waddamana bus split
T>T_LFWA_110_8 | 2005-11-29 | 1 | Out = Lindisfarne to Waddamana 110kV line, avoid O/L the Meadowbank to New Norfolk line for loss of the Tarraleah to New Norfolk No.1 line
T>T_LFWA_110_9 | 2005-11-29 | 1 | Out = Lindisfarne to Waddamana 110kV line, avoid O/L the Tarraleah to Meadowbank line for loss of a Tarraleah to New Norfolk No.2 line
T>T_LICL_CS_9B_SSSPS | 2006-12-14 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the Palmerston to Waddamana line (flow to South) for loss of the Liapootah to Chapel St line, SSSPS armed when all Gordon units O/S and Tas southern load above 420 MW
T>T_LICL_T_11A | 2005-11-23 | 1 | Out = Liapootah to Cluny Tee 220kV line, avoid O/L the Liapootah to Palmerston No.1 line (flow to North) for loss of the other Liapootah to Palmerston line
T>T_LICL_T_11B | 2005-11-23 | 1 | Out = Liapootah to Cluny Tee 220kV line, avoid O/L the Liapootah to Palmerston No.1 line (flow to South) for loss of the other Liapootah to Palmerston line
T>T_LICL_T_9A | 2005-11-24 | 1 | Out = Liapootah to Cluny Tee 220kV line, avoid O/L the Palmerston to Waddamana line (flow to North) for loss of the Liapootah to Chapel St line
T>T_LICL_T_9B | 2005-11-24 | 1 | Out = Liapootah to Cluny Tee 220kV line, avoid O/L the Palmerston to Waddamana line (flow to South) for loss of the Liapootah to Chapel St line
T>T_LICL_T_CS_1 | 2005-06-21 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the Waddamana to Lindisfarne line (flow to South) for loss of the Waddamana Tee to Bridgewater line
T>T_LICL_T_CS_11A | 2005-06-21 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the Liapootah to Palmerston No.1 line (flow to North) for loss of the other Liapootah to Palmerston line
T>T_LICL_T_CS_11B | 2005-06-21 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the Liapootah to Palmerston No.1 line (flow to South) for loss of the other Liapootah to Palmerston line
T>T_LICL_T_CS_12 | 2005-06-21 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the Meadowbank to New Norfolk line for loss of the Tarraleah to New Norfolk No.1 line
T>T_LICL_T_CS_2 | 2005-06-21 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the Waddamana to Bridgewater line (flow to South) for loss of the Waddamana to Lindisfarne line
T>T_LICL_T_CS_3 | 2005-05-16 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the Waddamana to Lake Echo Tee No.2 line (flow to North) for loss of the Liapootah to Chapel St line
T>T_LICL_T_CS_4 | 2005-06-21 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the Tarraleah to New Norfolk No.1 line (flow to South) for loss of the Meadowbank to New Norfolk line
T>T_LICL_T_CS_5 | 2005-06-21 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the Tungatinah to Tarraleah No.1 line (flow to South) for loss of the Tungatinah to Tarraleah No.2 line
T>T_LICL_T_CS_6 | 2005-05-16 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the Tungatinah to Lake Echo Tee No.2 line (flow to North) for loss of the Liapootah to Chapel St line
T>T_LICL_T_CS_7 | 2005-06-21 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the New Norfolk to Creek Rd line (flow to South) for loss of the New Norfolk to Chapel St line
T>T_LICL_T_CS_8 | 2005-06-21 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the New Norfolk to Chapel St line (flow to South) for loss of the New Norfolk to Creek Rd line
T>T_LICL_T_CS_9A | 2006-02-09 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the Palmerston to Waddamana line (flow to North) for loss of the Liapootah to Chapel St line
T>T_LICL_T_CS_9B | 2006-02-09 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, avoid O/L the Palmerston to Waddamana line (flow to South) for loss of the Liapootah to Chapel St line
T>T_LICS_110_1 | 2005-11-29 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the Waddamana to Lindisfarne line for loss of the Waddamana to Bridgewater line
T>T_LICS_110_10 | 2005-11-29 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the Tarraleah to Meadowbank line (flow to South) for loss of the Tarraleah to New Norfolk No.2 line
T>T_LICS_110_11 | 2005-11-29 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the New Norfolk to Creek Rd line (flow to South) for loss of the New Norfolk to Chapel St line
T>T_LICS_110_12 | 2005-11-29 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the New Norfolk to Chapel St line (flow to South) for loss of the New Norfolk to Creek Rd line
T>T_LICS_110_2 | 2005-11-29 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the Waddamana to Bridgewater line for loss of the Waddamana to Lindisfarne line
T>T_LICS_110_3 | 2005-11-29 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the Waddamana to Lindisfarne line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split
T>T_LICS_110_4 | 2006-01-10 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the Tungatinah to Lake Echo Tee No.2 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split
T>T_LICS_110_5 | 2006-01-10 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the Waddamana to Lake Echo Tee No.2 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split
T>T_LICS_110_6A | 2006-01-10 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the Waddamana to Lake Echo Tee No.1 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.2 line with Waddamana bus split
T>T_LICS_110_7 | 2006-04-28 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the Tungatinah to Tarraleah No.1 line for loss of the Tungatinah to Tarraleah No.2 line
T>T_LICS_110_8A | 2006-01-10 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the Tungatinah to Lake Echo Tee No.1 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.2 line with Waddamana bus split
T>T_LICS_110_9A | 2006-04-28 | 1 | Out = Liapootah to Chapel St line, avoid O/L the Palmerston to Waddamana line (flow to North) for loss of the Liapootah to Cluny Tee to Chapel St 220kV line
T>T_LICS_110_9B | 2006-04-28 | 1 | Out = Liapootah to Chapel St line, avoid O/L the Palmerston to Waddamana line (flow to South) for loss of the Liapootah to Cluny Tee to Chapel St 220kV line
T>T_LICS_220_1 | 2005-11-29 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the Liapootah to Palmerston No.1 line for loss of the Liapootah to Palmerston No.2 line
T>T_LICS_220_2 | 2005-11-29 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the Cluny Tee to Chapel St 220kV line for loss of the Palmerston to Waddamana line
T>T_LICS_220_3 | 2005-11-29 | 1 | Out = Liapootah to Chapel St 220kV line, avoid O/L the Liapootah to Cluny Tee line for loss of the Palmerston to Waddamana line
T>T_LICS_9B_SSSPS | 2006-12-14 | 1 | Out = Liapootah to Chapel St line, avoid O/L the Palmerston to Waddamana line (flow to South) for loss of the Liapootah to Cluny Tee to Chapel St 220kV line, SSSPS armed when all Gordon units O/S and Tas southern load above 420 MW
T>T_LIPM_110_10 | 2005-06-20 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Lindisfarne to Waddamana line for loss of the Waddamana to Bridgewater line
T>T_LIPM_110_2 | 2007-04-18 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Palmerston to Waddamana line (flow to South) for loss of the other Liapootah to Palmerston line
T>T_LIPM_110_2A | 2007-04-18 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Palmerston to Waddamana line (flow to North) for loss of the other Liapootah to Palmerston line
T>T_LIPM_110_3A | 2006-01-10 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Waddamana to Lake Echo Tee No.1 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.2 line with Waddamana bus split
T>T_LIPM_110_3B | 2006-01-10 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Waddamana to Lake Echo Tee No.2 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split
T>T_LIPM_110_4 | 2006-01-10 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Tungatinah to Lake Echo Tee to Tungatinah No.2 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split
T>T_LIPM_110_5 | 2006-05-30 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Bridgewater to Waddamana line for loss of the Lindisfarne to Waddamana line
T>T_LIPM_110_6 | 2005-05-16 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Creek Rd to New Norfolk line for loss of the Chapel St to New Norfolk line, 2005 system
T>T_LIPM_110_6_RED10 | 2005-06-22 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Creek Rd to New Norfolk line for loss of the Chapel St to New Norfolk line, 2005 system
T>T_LIPM_110_7 | 2005-05-16 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Chapel St to New Norfolk line for loss of the Creek Rd to New Norfolk line, 2005 system
T>T_LIPM_110_7_RED10 | 2005-06-22 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Chapel St to New Norfolk line for loss of the Creek Rd to New Norfolk line, 2005 system
T>T_LIPM_110_8 | 2006-01-10 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Tungatinah to Lake Echo Tee No.1 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.2 line with Waddamana bus split
T>T_LIPM_110_9 | 2005-06-20 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Lindisfarne to Waddamana line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split
T>T_LIPM_220_1 | 2005-09-08 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Liapootah to Chapel Street line for loss of the Chapel St to Cluny Tee to Liapootah line, Feedback
T>T_LIPM_220_2 | 2005-09-08 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Cluny Tee to Liapootah line for loss of the Chapel St to Liapootah line, Feedback
T>T_LIPM_220_3 | 2005-09-08 | 1 | Out = Liapootah to Palmerston line, avoid O/L the Chapel St to Cluny Tee line for loss of the Chapel St to Liapootah line, Feedback
T>T_MBNN_110A | 2006-11-20 | 1 | Out = Meadowbank to New Norfolk 110 kV line, avoid O/L the Tarraleah to New Norfolk No.1 or No. 2 line for loss of the Tarraleah to New Norfolk No. 1 or No. 2 line
T>T_MBNN_110B | 2006-11-20 | 1 | Out = Meadowbank to New Norfolk 110 kV line, avoid O/L the Tungatinah to Lake Echo No. 1 Tee for loss of the Tungatinah-Lake Echo-Waddamana No. 2 110 kV line and Waddamana-Bridgewater 110 kV line, flow to North
T>T_MBNN_110C | 2006-11-20 | 1 | Out = Meadowbank to New Norfolk 110 kV line, avoid O/L the Waddamana to Lake Echo No. 1 Tee for loss of the Tungatinah-Lake Echo tee-Waddamana No. 2 110 kV line and Waddamana-Bridgewater 110 kV line, flow to South
T>T_MBNN_110D | 2006-11-20 | 1 | Out = Meadowbank to New Norfolk 110 kV line, avoid O/L the Tungatinah to Lake Echo No. 2 Tee for loss of the Tungatinah-Lake Echo-Waddamana No. 1 110 kV line and Waddamana 110 kV bus split, flow to South
T>T_MBNN_110E | 2006-11-20 | 1 | Out = Meadowbank to New Norfolk 110 kV line, avoid O/L the Waddamana to Lake Echo No. 2 Tee for loss of the Tungatinah-Lake Echo-Waddamana No. 1 110 kV line and Waddamana 110 kV bus split, flow to North
T>T_MBTA_110A | 2006-11-20 | 1 | Out = Tarraleah to Meadowbank 110 kV line, avoid O/L the Tarraleah to New Norfolk No.1 or No. 2 line for loss of the Tarraleah to New Norfolk No. 1 or No. 2 line
T>T_MBTA_110B | 2007-03-16 | 1 | Out = Tarraleah to Meadowbank 110 kV line, avoid O/L Waddamana to Lake Echo No. 1 110 kV Tee for loss of Tungatinah-Lake Echo-Waddamana No. 2 110 kV line and Waddamana-Bridgewater 110 kV line, flow to South, swamp if LE-LE1 open and LE-LE2 in service
T>T_MBTA_110BX | 2007-03-16 | 1 | Out = Tarraleah to Meadowbank 110 kV line, avoid O/L Waddamana to Lake Echo No. 1 110 kV Tee for loss of Tungatinah-Lake Echo-Waddamana No. 2 110 kV line and Waddamana-Bridgewater 110 kV line, flow to South, swamp if LE-LE2 open or LE-LE1 in service
T>T_MBTA_110C | 2007-03-16 | 1 | Out = Tarraleah to Meadowbank 110 kV line, avoid O/L Tungatinah to Lake Echo No. 1 110 kV Tee for loss of Tungatinah-Lake Echo-Waddamana No. 2 110 kV line and Waddamana-Bridgewater 110 kV line, flow to North, swamp if LE-LE1 open and LE-LE2 in service
T>T_MBTA_110CX | 2007-03-16 | 1 | Out = Tarraleah to Meadowbank 110 kV line, avoid O/L Tungatinah to Lake Echo No. 1 110 kV Tee for loss of Tungatinah-Lake Echo-Waddamana No. 2 110 kV line and Waddamana-Bridgewater 110 kV line, flow to North, swamp if LE-LE2 open or LE-LE1 in service
T>T_MBTA_110D | 2007-03-16 | 1 | Out = Tarraleah to Meadowbank 110 kV line, avoid O/L Tungatinah to Lake Echo No. 2 110 kV Tee for loss of Tungatinah-Lake Echo-Waddamana No. 1 110 kV line and Waddamana 110 kV bus split, flow to North, swamp if LE-LE2 open and LE-LE1 in service
T>T_MBTA_110DX | 2007-03-16 | 1 | Out = Tarraleah to Meadowbank 110 kV line, avoid O/L Tungatinah to Lake Echo No. 2 110 kV Tee for loss of Tungatinah-Lake Echo-Waddamana No. 1 110 kV line and Waddamana 110 kV bus split, flow to North, swamp if LE-LE1 open or LE-LE2 in service
T>T_MBTA_110E | 2007-03-16 | 1 | Out = Tarraleah to Meadowbank 110 kV line, avoid O/L Waddamana to Lake Echo Tee No. 2 110 kV Tee for loss of Tungatinah-Lake Echo-Waddamana No. 1 110 kV line and Waddamana 110 kV bus split, flow to South, swamp if LE-LE2 open and LE-LE1 in service
T>T_MBTA_110EX | 2007-03-16 | 1 | Out = Tarraleah to Meadowbank 110 kV line, avoid O/L Waddamana to Lake Echo Tee No. 2 110 kV Tee for loss of Tungatinah-Lake Echo-Waddamana No. 1 110 kV line and Waddamana 110 kV bus split, flow to South, swamp if LE-LE1 open or LE-LE2 in service
T>T_NIL_110_26_HM | 2005-05-18 | 1 | Out = Nil, Hampshire link closed, avoid O/L the Hampshire to Waratah Tee line for loss of a Farrell to Sheffield line
T>T_NIL_110_27_HM | 2005-05-18 | 1 | Out = Nil, Hampshire link closed, avoid overloading the Paloona to Ulverstone line for loss of the Sheffield to Burnie 220kV line
T>T_NIL_110_28_HM | 2005-05-18 | 1 | Out = Nil, Hampshire link closed, avoid overloading the Sheffield to Burnie 110kV line for loss of the Sheffield to Burnie 220kV line
T>T_NIL_110_29_HM | 2005-05-18 | 1 | Out = Nil, Hampshire link closed, avoid overloading the Sheffield to Paloona line for loss of the Sheffield to Burnie 220kV line
T>T_NIL_220_10_HM | 2005-05-18 | 1 | Out = Nil, Hampshire link closed, avoid overloading the Sheffield to Burnie 220kV line for loss of a Sheffield 220/110kV transformer
T>T_NIL_220_14_HM | 2005-05-18 | 1 | Out = Nil, Hampshire link closed, avoid overloading a Farrell to Sheffield line for loss of the parallel line, feedback equation
T>T_NIL_BL_110_1 | 2007-01-18 | 1 | Outage = Nil, Basslink in service, avoid overloading the Chapel Street to New Norfolk 110kV line for loss of New Norfolk to Creek Road 110kV line, feedback
T>T_NIL_BL_110_11 | 2006-06-08 | 1 | Outage = Nil, Basslink in service, avoid overloading the Meadowbank to New Norfolk 110kV line for loss of the Tarraleah to New Norfolk 110kV line, feedback
T>T_NIL_BL_110_18 | 2007-03-14 | 1 | Outage = Nil, Basslink in service, avoid O/L Tungatinah to Lake Echo Tee No.1 line (flow to North) for loss of Waddamana to Lake Echo Tee to Tungatinah No.2 line radialising Bridgewater to Waddamana line from Bridgewater, swamped if LE-LE1 line open
T>T_NIL_BL_110_18B | 2007-03-14 | 1 | Outage = Nil, Basslink in service, avoid overloading the Tungatinah to Lake Echo Tee No.2 110kV line (flow to North) for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, swamped if LE-LE2 line open
T>T_NIL_BL_110_18BX | 2007-03-14 | 1 | Outage = Nil, Basslink in service, avoid overloading Tungatinah to Lake Echo Tee No.2 110kV line (flow to North) for loss of Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, swamped if LE-LE2 line in service
T>T_NIL_BL_110_18X | 2007-03-14 | 1 | Outage = Nil, Basslink in service, avoid O/L Tungatinah to Lake Echo Tee No.1 line (flow to North) for loss of Waddamana to Lake Echo Tee to Tungatinah No.2 line radialising Bridgewater to Waddamana line from Bridgewater, swamped if LE-LE1 line in service
T>T_NIL_BL_110_19 | 2007-03-14 | 1 | Outage = Nil, Basslink in service, avoid O/L Waddamana to Lake Echo Tee No.1 line (flow to North) for loss of Tungatinah to Lake Echo Tee to Waddamana No.2 line radialising Bridgewater to Waddamana line from Bridgewater, swamped if LE-LE1 line open
T>T_NIL_BL_110_19X | 2007-03-14 | 1 | Outage = Nil, Basslink in service, avoid O/L Waddamana to Lake Echo Tee No.1 line (flow to North) for loss of Tungatinah to Lake Echo Tee to Waddamana No.2 line radialising Bridgewater to Waddamana line from Bridgewater, swamped if LE-LE1 line in service
T>T_NIL_BL_110_2 | 2006-06-08 | 1 | Outage = Nil, Basslink in service, avoid overloading the Bridgewater to Lindisfarne 110kV line for loss of the Waddamana to Lindisfarne 110kV line, feedback
T>T_NIL_BL_110_20 | 2007-03-14 | 1 | Outage = Nil, Basslink in service, avoid overloading Waddamana to Lake Echo Tee No.2 110kV line (flow to North) for loss of Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, swamped if LE-LE2 line open
T>T_NIL_BL_110_20X | 2007-03-14 | 1 | Outage = Nil, Basslink in service, avoid overloading Waddamana to Lake Echo Tee No.2 110kV line (flow to North) for loss of Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, swamped if LE-LE2 line in service
T>T_NIL_BL_110_21 | 2007-01-18 | 1 | Outage = Nil, Basslink in service, avoid overloading the Waddamana to Bridgewater 110kV line for loss of the Waddamana to Lindisfarne 110kV line, feedback
T>T_NIL_BL_110_22A | 2007-01-18 | 1 | Outage = Nil, Basslink in service, avoid overloading the Waddamana to Palmerston 110kV line (flow to North) for loss of the Liapootah to Palmerston 220kV line, feedback
T>T_NIL_BL_110_22B | 2007-01-18 | 1 | Outage = Nil, Basslink in service, avoid overloading the Waddamana to Palmerston 110kV line (flow to South) for loss of the Liapootah to Palmerston 220kV line, feedback
T>T_NIL_BL_110_23 | 2006-10-04 | 1 | Outage = Nil, Basslink in service, avoid overloading the Waddamana to Palmerston 110kV line (flow to South) for loss of the Liapootah-Cluny Tee-Chapel St 220kV line, feedback
T>T_NIL_BL_110_24 | 2006-06-08 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid overloading Lindisfarne to Risdon No.1 110kV line for loss of the other Lindisfarne to Risdon 110kV line, feedback
T>T_NIL_BL_110_24B | 2006-03-02 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid overloading Lindisfarne to Risdon No.2 110kV line for loss of the other Lindisfarne to Risdon 110kV line, feedback
T>T_NIL_BL_110_25 | 2008-04-02 | 1 | Outage = Nil, Basslink in service, avoid overloading Waddamana to Lindisfarne 110kV line for loss of Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, swamped if LE-LE2 line open
T>T_NIL_BL_110_25X | 2008-04-02 | 1 | Outage = Nil, Basslink in service, avoid overloading Waddamana to Lindisfarne 110kV line for loss of Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, swamped if LE-LE2 line in service
T>T_NIL_BL_110_26 | 2007-01-18 | 1 | Outage = Nil, Basslink in service, avoid overloading the Waddamana to Lindisfarne 110kV line for loss of the Waddamana to Bridgewater 110kV line, feedback
T>T_NIL_BL_110_4 | 2006-08-07 | 1 | Out = Nil, Basslink in service, avoid O/L a Hadspen to Trevallyn line for loss of the other Hadspen to Trevallyn line
T>T_NIL_BL_110_6 | 2007-01-18 | 1 | Outage = Nil, Basslink in service, avoid overloading the Tarraleah to New Norfolk No.1 110kV line for loss of the Meadowbank to New Norfolk 110kV line, feedback
T>T_NIL_BL_110_7 | 2006-06-08 | 1 | Outage = Nil, Basslink in service, avoid overloading the Tarraleah to Meadowbank 110kV line for loss of the Tarraleah to New Norfolk 110kV line, feedback
T>T_NIL_BL_110_8 | 2007-01-18 | 1 | Outage = Nil, Basslink in service, avoid overloading the New Norfolk to Creek Road 110kV line for loss of the New Norfolk to Chapel St 110kV line, feedback
T>T_NIL_BL_110_9A | 2008-04-14 | 1 | Outage = Nil, Basslink in service, avoid overloading Tarraleah to Tungatinah No.1 110kV line (flow to South) for loss of the other Tarraleah to Tungatinah 110kV line, feedback
T>T_NIL_BL_110_9B | 2008-04-14 | 1 | Outage = Nil, Basslink in service, avoid overloading Tarraleah to Tungatinah No.2 110kV line (flow to South) for loss of the other Tarraleah to Tungatinah 110kV line, feedback
T>T_NIL_BL_1A | 2006-08-16 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Gordon to Chapel Street 220kV lines
T>T_NIL_BL_220_13 | 2007-01-18 | 1 | Outage = Nil, Basslink in service, avoid O/L a Chapel Street 220/110kV transformer for loss of a parallel transformer, Feedback
T>T_NIL_BL_220_7A | 2008-11-18 | 1 | Outage = Nil, avoid overloading the Liapootah to Cluny Tee 220kV line (flow to South) for loss of Liapootah to Chapel Street 220kV line, feedback equation, swamp if Tas South demand is between 547MW and 760 MW when NSA is effective
T>T_NIL_BL_220_7B | 2008-02-07 | 1 | Outage = Nil, Basslink in service, avoid overloading the Liapootah to Cluny Tee 220kV line (flow to North) for loss of Liapootah to Chapel Street 220kV line, feedback equation
T>T_NIL_BL_220_8A | 2008-11-18 | 1 | Outage = Nil, avoid overloading the Liapootah to Chapel Street 220kV line (flow to South) for loss of Cluny to Chapel Street 220kV line, feedback equation, swamp if Tas South demand is between 547MW and 760 MW when NSA is effective
T>T_NIL_BL_220_8B | 2008-02-07 | 1 | Outage = Nil, Basslink in service, avoid overloading the Liapootah to Chapel Street 220kV line (flow to North) for loss of Cluny to Chapel Street 220kV line, feedback equation
T>T_NIL_BL_220_9A | 2008-11-18 | 1 | Outage = Nil, avoid overloading the Cluny Tee to Chapel Street 220kV line (flow to South) for loss of Liapootah to Chapel Street 220kV line, feedback equation, swamp if Tas South demand is between 547MW and 760 MW when NSA is effective
T>T_NIL_BL_220_9B | 2008-02-07 | 1 | Outage = Nil, Basslink in service, avoid overloading the Cluny Tee to Chapel Street 220kV line (flow to North) for loss of Liapootah to Chapel Street 220kV line, feedback equation
T>T_NIL_BL_2A | 2006-08-16 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Liapootah to Palmerston No.1 220kV line, feedback equation
T>T_NIL_BL_3D | 2007-06-21 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent overloading either Palmerston to Hadspen 220kV line for trip of the Palmerston to Sheffield 220kV line (outage id=33) taking into account NCSPS generation reduction
T>T_NIL_BL_4A | 2006-08-16 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Palmerston to Hadspen No.3 110kV line, feedback equation
T>T_NIL_BL_4B | 2006-08-16 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Palmerston to Hadspen No.4 110kV line, feedback equation
T>T_NIL_BL_4C | 2007-01-18 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent overloading either Palmerston to Hadspen 110kV line for trip of the other Palmerston to Hadspen 110kV line taking into account NCSPS generation reduction
T>T_NIL_BL_4D | 2006-06-08 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent overloading either Palmerston to Hadspen 110kV line for trip of the Palmerston 220/110kV transformer taking into account NCSPS generation reduction
T>T_NIL_BL_5D | 2007-02-13 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent overloading either Hadspen to Georgetown 220kV line for trip of the Palmerston to Sheffield 220kV line taking into account NCSPS generation reduction
T>T_NIL_BL_7A | 2006-08-16 | 1 | Outage = Nil, Basslink in service, Hampshire link open, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Farrell to Sheffield 220kV lines
T>T_NIL_BL_7B | 2006-01-05 | 1 | Outage = Nil, Basslink exporting, Hampshire link open, limit Tasmanian generation to avoid post-contingent overloading of either Farrell to Sheffield 220kV lines for trip of the other Farrell to Sheffield line taking into account NCSPS gen reduction
T>T_NIL_BL_EXP_3H | 2007-06-21 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L a Palmerston to Hadspen 220kV line for trip of Sheffield to Georgetown 220kV line (outage id's=34,35) taking into account Basslink export available for SPS action
T>T_NIL_BL_IMP_1B | 2006-01-05 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading either Gordon to Chapel St 220kV line for trip of the other Gordon to Chapel St line with no SPS action
T>T_NIL_BL_IMP_2B | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading the Liapootah to Palmerston No.1 220kV line (flow to North) for trip of the Liapootah to Palmerston No.2 line with no SPS action, feedback equation
T>T_NIL_BL_IMP_2C | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading the Liapootah to Palmerston No.1 220kV line (flow to South) for trip of the Liapootah to Palmerston No.2 line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3G | 2006-01-12 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3GG | 2006-01-12 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.2 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3J | 2006-01-12 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.1 220kV line (flow to South) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3JJ | 2006-01-12 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.2 220kV line (flow to South) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_4E | 2007-01-18 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.3 110kV line (flow to North) for trip of the other Palmerston to Hadspen 110kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_4EE | 2007-01-18 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.4 110kV line (flow to North) for trip of the other Palmerston to Hadspen 110kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_4F | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading either Palmerston to Hadspen 110kV line (flow to North) for trip of the Palmerston 220/110kV transformer with no SPS action
T>T_NIL_BL_IMP_4G | 2007-01-18 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.3 110kV line (flow to South) for trip of the other Palmerston to Hadspen 110kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_4GG | 2007-01-18 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.4 110kV line (flow to South) for trip of the other Palmerston to Hadspen 110kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_4H | 2006-06-08 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading either Palmerston to Hadspen 110kV line (flow to South) for trip of the Palmerston 220/110kV transformer with no SPS action
T>T_NIL_BL_IMP_5G | 2006-01-12 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.1 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5GG | 2006-01-12 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.2 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5J | 2006-01-12 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.1 220kV line (flow to South) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5JJ | 2006-01-12 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.2 220kV line (flow to South) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_7C | 2006-11-09 | 1 | Outage = Nil, Basslink not exporting, Hampshire link open, limit Tas gen to avoid post-contingent overloading of a Farrell to Sheffield 220kV line for trip of the other Farrell to Sheffield line with no SPS action
T>T_NIL_POAT110 | 2007-03-06 | 1 | Outage = Nil, avoid overloading a Poatina to Palmerston 110 kV line
T>T_NIL_POAT220 | 2007-03-06 | 1 | Outage = Nil, avoid overloading a Poatina to Palmerston 220 kV line
T>T_PMSH_220_2 | 2005-11-29 | 1 | Out = Palmerston to Sheffield 220kV line, avoid O/L Hadspen to Georgetown No.1 line for loss of the Hadspen to Georgetown No.2 line
T>T_PMSH_220_2B | 2008-04-23 | 1 | Out = Palmerston to Sheffield 220kV line, avoid O/L Georgetown to Hadspen No.1 line for loss of the Hadspen to Georgetown No.2 line
T>T_PMSH_220_3 | 2005-11-29 | 1 | Out = Palmerston to Sheffield 220kV line, avoid O/L Hadspen to Palmerston No.1 220kV line for loss of the Hadspen to Palmerston No.2 220kV line
T>T_PMWA_110_10 | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of the Meadowbank to New Norfolk line
T>T_PMWA_110_11 | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Tungatinah to Tarraleah No.1 line for loss of the Tarraleah to Tungatinah No.2 line
T>T_PMWA_110_12 | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Waddamana to Bridgewater line for loss of the Lindisfarne to Waddamana line
T>T_PMWA_110_13 | 2006-01-10 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Tungatinah to Lake Echo Tee No.1 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.2 line with Waddamana bus split
T>T_PMWA_110_14 | 2006-01-10 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Waddamana to Lake Echo Tee No.1 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.2 line with Waddamana bus split
T>T_PMWA_110_15 | 2006-01-10 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Tungatinah to Lake Echo Tee No.2 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split
T>T_PMWA_110_16 | 2006-01-10 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Waddamana to Lake Echo Tee No.2 line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split
T>T_PMWA_110_2 | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Bridgewater to Lindisfarne line for loss of the Waddamana to Lindisfarne line
T>T_PMWA_110_4 | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L Chapel St 220/110kV transformer for loss of Chapel St 220/110kV transformer
T>T_PMWA_110_6 | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Meadowbank to New Norfolk line for loss of the New Norfolk to Tarraleah No.2 line
T>T_PMWA_110_7 | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the New Norfolk to Chapel St No.1 line for loss of the Creek Road to New Norfolk line
T>T_PMWA_110_8 | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the New Norfolk to Creek Road line for loss of the Chapel St to New Norfolk No.1 line
T>T_PMWA_110_9 | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Tarraleah to Meadowbank line for loss of the New Norfolk to Tarraleah No.2 line
T>T_PMWA_1A | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Cluny Tee to Liapootah No.1 220kV line (flow to North), feedback equation
T>T_PMWA_1B | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Chapel St to Liapootah No.2 220kV line (flow to North), feedback equation
T>T_PMWA_1C | 2007-11-27 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Liapootah to Palmerston No.1 220kV line (flow to North), feedback equation
T>T_PMWA_1CC | 2007-11-27 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Liapootah to Palmerston No.2 220kV line (flow to North), feedback equation
T>T_PMWA_220_1 | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Cluny Tee to Chapel St line for loss of the Chapel St to Liapootah No.2 line
T>T_PMWA_220_2 | 2007-01-25 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Liapootah to Cluny Tee to Chapel St line for loss of the Chapel St to Liapootah No.2 line
T>T_PMWA_220_3 | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Liapootah to Chapel St No.2 line for loss of the Chapel St to Cluny Tee to Liapootah line
T>T_PMWA_220_4A | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Liapootah to Palmerston No.1 line (flow to North) for loss of the Liapootah to Palmerston No.2 line
T>T_PMWA_220_4B | 2005-11-29 | 1 | Out = Palmerston to Waddamana 110kV line, avoid O/L the Liapootah to Palmerston No.1 line (flow to South) for loss of the Liapootah to Palmerston No.2 line
T>T_PMWA_2DDD | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tas generation to avoid O/L Palmerston to Hadspen No.1 220kV line for trip of Palmerston to Sheffield 220kV line (outage id=43) taking into account NCSPS generation reduction
T>T_PMWA_IMP_4A | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tasmanian generation to avoid O/L Cluny Tee to Liapootah No.1 220kV line (flow to North) for loss of the Chapel St to Liapootah No.2 220kV line without NCSPS action
T>T_PMWA_IMP_4B | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tasmanian generation to avoid O/L Chapel St to Liapootah No.2 220kV line (flow to North) for loss of the Chapel St to Cluny Tee to Liapootah No.1 220kV line without NCSPS action
T>T_PMWA_IMP_4C | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tasmanian generation to avoid O/L Liapootah to Palmerston No.1 220kV line (flow to North) for trip of Liapootah to Palmerston No.2 220kV line without NCSPS action
T>T_PMWA_IMP_4CC | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tasmanian generation to avoid O/L Liapootah to Palmerston No.2 220kV line (flow to North) for trip of Liapootah to Palmerston No.1 220kV line without NCSPS action
T>T_PMWA_IMP_4DDD | 2007-07-23 | 1 | Outage = Palmerston to Waddamana 110kV line, limit Tasmanian generation to avoid O/L Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_PM_TX_1A | 2006-04-10 | 1 | Outage = Palmerston 220/110kV transformer, limit Tasmanian generation to avoid overloading the Palmerston to Hadspen No.3 110kV line (flow to North) for trip of Palmerston to Hadspen No.4 line, feedback equation
T>T_PM_TX_1B | 2006-04-10 | 1 | Outage = Palmerston 220/110kV transformer, limit Tasmanian generation to avoid overloading the Palmerston to Hadspen No.4 110kV line (flow to North) for trip of Palmerston to Hadspen No.3 line, feedback equation
T>T_PM_TX_1C | 2008-05-21 | 1 | Outage = Palmerston 220/110kV transformer, limit Tasmanian generation to avoid overloading the Hadspen 220kV/110kV transformer no.1 or no.2 for trip of Hadspen 220kV/110kV transformer no.1 or no.2, feedback equation
T>T_SH_TX | 2005-05-16 | 1 | Out = Sheffield 220/110kV transformer, Hampshire link open, avoid O/L the Burnie to Sheffield 220kV line for loss of the remaining Sheffield 220/110kV transformer
T>T_SH_TX_2 | 2005-06-16 | 1 | Out = Sheffield 220/110kV transformer, Hampshire link open and Burnie 110kV bus NOT split, avoid O/L the remaining Sheffield 220/110kV transformer for loss of the Burnie to Sheffield 220kV line
T>T_SH_TX_HM | 2005-05-16 | 1 | Out = Sheffield 220/110kV transformer, Hampshire link closed, avoid O/L the Burnie to Sheffield 220kV line for loss of the remaining Sheffield 220/110kV transformer
T>T_TAMB_110_1 | 2006-04-12 | 1 | Out = Tarraleah - Meadowbank line 110kV line: To maximise capacity with opening up the two circuits between TU and TA.
T>T_TAMB_110_2 | 2006-04-12 | 1 | Out = Tarraleah - Meadowbank line 110kV line: To maximise capacity with opening up the two circuits between TU and TA.
T>T_TANN1_110_1 | 2005-06-21 | 1 | Out = Tarraleah to New Norfolk No.1 110kV line, avoid O/L the Tarraleah to New Norfolk No.2 line for loss of the Tarraleah to Meadowbank line
T>T_TANN1_110_2 | 2005-06-21 | 1 | Out = Tarraleah to New Norfolk No.1 110kV line, avoid O/L the Tarraleah to New Norfolk No.2 line for loss of the Meadowbank to New Norfolk line
T>T_TANN2_110_1 | 2005-06-21 | 1 | Out = Tarraleah to New Norfolk No.2 110kV line, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of the Tarraleah to Meadowbank line
T>T_TANN2_110_2 | 2005-06-21 | 1 | Out = Tarraleah to New Norfolk No.2 110kV line, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of the Meadowbank to New Norfolk line
T>T_TANN_110_1 | 2005-06-21 | 1 | Out = Tarraleah to New Norfolk No.1 or No.2 110kV line, avoid O/L the Tarraleah to Meadowbank line for loss of the remaining Tarraleah to New Norfolk line
T>T_TATU_110_1 | 2005-10-11 | 1 | Out = Tarraleah to Tungatinah 110kV line, avoid O/L the Tarraleah to New Norfolk No.2 line for loss of the Meadowbank to New Norfolk line
T>T_TATU_110_2 | 2005-06-21 | 1 | Out = Tarraleah to Tungatinah 110kV line, avoid O/L the Tarraleah to Meadowbank line for loss of a Tarraleah to New Norfolk No.2 line
T>T_TULE_T1_WA_1RED5 | 2005-06-22 | 1 | Out = Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, avoid O/L the Waddamana to Lake Echo No.2 line for loss of the New Norfolk to Tarraleah No.2 line, reduced by 5 MW for coincident outage
T>T_TULE_T1_WA_2RED5 | 2005-06-22 | 1 | Out = Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, avoid O/L the Waddamana to Lake Echo No.2 line for loss of the Meadowbank to New Norfolk line, reduced by 5 MW for coincident outage
T>T_TULE_T1_WA_3RED5 | 2005-06-22 | 1 | Out = Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, avoid O/L the Tungatinah to Lake Echo No.2 line for loss of the New Norfolk to Tarraleah No.2 line, reduced by 5 MW for coincident outage
T>T_TULE_T1_WA_4RED5 | 2005-06-22 | 1 | Out = Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, avoid O/L the Tungatinah to Lake Echo No.2 line for loss of the Meadowbank to New Norfolk line, reduced by 5 MW for coincident outage
T>T_TULE_T1_WA_SPLT1 | 2006-01-10 | 1 | Out = Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, avoid O/L the Waddamana to Lake Echo No.2 line for loss of the New Norfolk to Tarraleah No.2 line
T>T_TULE_T1_WA_SPLT2 | 2006-01-10 | 1 | Out = Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, avoid O/L the Waddamana to Lake Echo No.2 line for loss of the Meadowbank to New Norfolk line
T>T_TULE_T1_WA_SPLT3 | 2006-01-10 | 1 | Out = Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, avoid O/L the Tungatinah to Lake Echo No.2 line for loss of the New Norfolk to Tarraleah No.2 line
T>T_TULE_T1_WA_SPLT4 | 2006-01-10 | 1 | Out = Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line with Waddamana bus split, avoid O/L the Tungatinah to Lake Echo No.2 line for loss of the Meadowbank to New Norfolk line
T>T_TULE_T2_WA_1 | 2006-01-10 | 1 | Out = Tungatinah to Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Waddamana to Lake Echo No.1 line for loss of the Tarraleah to New Norfolk No.2 line
T>T_TULE_T2_WA_2 | 2006-01-10 | 1 | Out = Tungatinah to Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Waddamana to Lake Echo No.1 line for loss of the Meadowbank to New Norfolk line
T>T_TULE_T2_WA_3 | 2006-01-10 | 1 | Out = Tungatinah to Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Tungatinah to Lake Echo No.1 line for loss of the Tarraleah to New Norfolk No.2 line
T>T_TULE_T2_WA_4 | 2006-01-10 | 1 | Out = Tungatinah to Lake Echo Tee to Waddamana No.2 110kV line, avoid O/L the Tungatinah to Lake Echo No.1 line for loss of the Meadowbank to New Norfolk line
T>T_TU_110KVBUSPROT | 2007-06-13 | 1 | Outage = Tungatinah 110kV Bus Zone protection, avoid overloading the Tungatinah to Lake Echo Tee No.2 110kV line radially connecting Tungatinah and Butlers Gorge generators (both TA-TU lines and TU-LEtee-WA 1 line opened)
T>T_WESTCOAST+HM | 2006-02-15 | 1 | Limit West Coast generation to West Coast load + rating of Hampshire link
T>T_X_010705AM_CL_1 | 2005-06-22 | 1 | Out = Bridgewater to Waddamana line and Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus closed, avoid O/L the Waddamana to Lindisfarne line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.2 line
T>T_X_010705AM_SP_1 | 2005-06-22 | 1 | Out = Bridgewater to Waddamana line and Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split, avoid O/L the Meadowbank to New Norfolk line for loss of the Tarraleah to New Norfolk No.2 line
T>T_X_010705AM_SP_2 | 2005-06-22 | 1 | Out = Bridgewater to Waddamana line and Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split, avoid O/L the Tarraleaheah to Meadowbank line for loss of the Tarraleah to New Norfolk No.2 line
T>T_X_010705AM_SP_3 | 2005-06-22 | 1 | Out = Bridgewater to Waddamana line and Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split, avoid O/L the Tarraleah to New Norfolk No.2 line for loss of the Meadowbank to New Norfolk line
T>T_X_010705AM_SP_4 | 2005-06-22 | 1 | Out = Bridgewater to Waddamana line and Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split, avoid O/L a Tungatinah to Tarraleah line for loss of the other Tungtainah to Tarraleah line
T>T_X_010705AM_SP_5 | 2005-06-22 | 1 | Out = Bridgewater to Waddamana line and Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split, avoid O/L the Palmerston to Waddamana line (flow to North) for loss of a Liapootah to Palmerston line
T>T_X_010705AM_SP_6 | 2005-06-22 | 1 | Out = Bridgewater to Waddamana line and Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split, avoid O/L the Creek Rd to New Norfolk line for loss of Chapel St to New Norfolk line
T>T_X_010705AM_SP_7 | 2005-06-22 | 1 | Out = Bridgewater to Waddamana line and Tungatinah to Lake Echo Tee to Waddamana No.1 line with Waddamana bus split, avoid O/L the Chapel St to New Norfolk line for loss of Creek Rd to New Norfolk line
T>T_X_010705PM_1 | 2005-06-22 | 1 | Out = Bridgewater to Waddamana line and Tungatinah to LE Tee to Waddamana No.1 line with Waddamana bus closed and Liapootah to Palmerston line, avoid O/L the Waddamana to Lindisfarne line for loss of the Tungatinah to Lake Echo Tee to Waddamana No.2 line
T>T_X_CSNN_BWWA | 2005-10-25 | 1 | Out = Chapel St to New Norfolk line and Bridgewater to Waddamana line, avoid O/L New Norfolk to Creek Rd line for loss of Waddamana to Lake Echo Tee #1 line with Waddamana bus split ofloading Waddamana to Lake Echo Tee # 2 line
T>T_X_LFWA_BWWA_2A | 2005-11-02 | 1 | Out = Lindisfarne to Waddamana and Bridgewater to Waddamana 110kV lines, avoid O/L the Palmerston to Waddamana line (flow to North) for loss of a Liapootah to Palmerston line
T>T_X_LFWA_BWWA_2B | 2005-11-02 | 1 | Out = Lindisfarne to Waddamana and Bridgewater to Waddamana 110kV lines, avoid O/L the Palmerston to Waddamana line (flow to South) for loss of a Liapootah to Palmerston line
T>T_X_LFWA_BWWA_3 | 2005-11-02 | 1 | Out = Lindisfarne to Waddamana and Bridgewater to Waddamana 110kV lines, avoid O/L a Tungatinah to Tarraleah line for loss of the other Tungtainah to Tarraleah line
T>T_X_LFWA_BWWA_5 | 2005-11-02 | 1 | Out = Lindisfarne to Waddamana and Bridgewater to Waddamana 110kV lines, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of the Meadowbank to New Norfolk line
T>T_X_LFWA_BWWA_8 | 2005-11-02 | 1 | Out = Lindisfarne to Waddamana and Bridgewater to Waddamana 110kV lines, avoid O/L the Meadowbank to New Norfolk line for loss of the Tarraleah to New Norfolk No.1 line
T>T_X_LFWA_BWWA_9 | 2005-11-02 | 1 | Out = Lindisfarne to Waddamana and Bridgewater to Waddamana 110kV lines, avoid O/L the Tarraleah to Meadowbank line for loss of a Tarraleah to New Norfolk No.2 line
T>T_X_LIPM_CSRI | 2006-02-22 | 1 | Out = Liapootah to Palmerston line and Chapel St to Risdon line, avoid O/L Creek Rd to Risdon for loss of the other Liapootah to Palmerston line
T>T_X_MBNN_MBTA | 2006-01-06 | 2 | Out = Meadowbank to New Norfolk and Meadowbank to Tarraleah 110kV lines, avoid O/L Tarraleah to New Norfolk No.1 line for loss of the Tarraleah to New Norfolk No.2 line
T>T_X_MBNN_TATU1-2_1 | 2006-01-24 | 2 | Outage = Meadowbank to New Norfolk with both Tarraleah to Tungatinah 110kV lines opened, avoid O/L either Waddamana to Lake Echo Tee 110kV lines for loss of one of the two parallel circuits
T>T_X_MBNN_TATU1-2_2 | 2006-01-24 | 2 | Outage = Meadowbank to New Norfolk with both Tarraleah to Tungatinah 110kV lines opened, avoid O/L either Tarraleah to New Norfolk 110kV lines for loss of one of the two paralle circuits
T>T_X_PMSH+GTSH_1 | 2008-07-16 | 1 | Outage = Palmerston to Sheffield 220kV line and one Georgetown to Sheffield 220kV line, avoid O/L of Hadspen to Georgetown line (in this direction) for trip of Hadspen to Georgetown line
T>T_X_PMSH+GTSH_2 | 2008-07-16 | 1 | Outage = Palmerston to Sheffield 220kV line and one Georgetown to Sheffield 220kV line, avoid O/L of Georgetown to Hadspen line (in this direction) for trip of Hadspen to Georgetown line
T>T_X_PMSH+HAGT_1 | 2008-07-16 | 1 | Outage = Palmerston to Sheffield 220kV line and one Hadspen to Georgetown 220kV line, avoid O/L of Sheffield to Georgetown line (in this direction) for trip of Georgetown to Sheffield line
T>T_X_PMSH+HAGT_2 | 2008-07-16 | 1 | Outage = Palmerston to Sheffield 220kV line and one Hadspen to Georgetown 220kV line, avoid O/L of Georgetown to Sheffield line (in this direction) for trip of Georgetown to Sheffield line
T>T_X_PMSH_GTSH | 2007-08-07 | 1 | Out = Palmerston to Sheffield 220kV line and Georgetown to Sheffield 220kV line, limit Tasmanian generation to limit Sheffield to Georgetwon 220kV line flow to 150 MW
T>T_X_PMTX_PMWA | 2006-04-28 | 1 | Out = Palmerston 220/110kV transformer and Palmerston to Waddamana 110kV line, limit Tasmanian generation to avoid overloading Palmerston to Hadspen No.3 or No. 4 110kV line for trip of either parallel line
T>T_X_TANN_TATU_BWWA | 2005-10-25 | 1 | Out = Tarraleah to New Norfolk No.2 line & Tarraleah to Tungatinah No.2 line & Bridgewater to Waddamana line, avoid O/L Tarraleah to Tungatina No.1 line for loss of Tungatina to Lake Echo to Waddamana No.1 line with Waddamana bus split
T>T_X_TARRALEAH_B | 2005-10-25 | 1 | Out = Tarraleah to New Norfolk No.1 line & Tarraleah to Tungatinah No.1 line & Tarraleah to Meadowbank & Bridgewater to Waddamana line, avoid O/L Tarraleah to New Norfolk No.2 line for loss of Tungatina to Waddamana No.1 line & Waddamana bus split
T>T_X_TULE_T2_LE1_1 | 2005-05-16 | 1 | Out = Lake Echo Tee to Tungatina No.2 110kV line and Lake Echo to Lake Echo Tee No.1 line, avoid O/L the Meadowbank to New Norfolk line for loss of a Tarraleah to New Norfolk line
T>T_X_TULE_T2_LE1_10 | 2005-05-16 | 1 | Out = Lake Echo Tee to Tungatina No.2 110kV line and Lake Echo to Lake Echo Tee No.1 line, avoid O/L the Creek Rd to New Norfolk line for loss of the Meadowbank to New Norfolk line
T>T_X_TULE_T2_LE1_2 | 2005-05-16 | 1 | Out = Lake Echo Tee to Tungatina No.2 110kV line and Lake Echo to Lake Echo Tee No.1 line, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of the other Tarraleah to New Norfolk line
T>T_X_TULE_T2_LE1_3 | 2005-05-16 | 1 | Out = Lake Echo Tee to Tungatina No.2 110kV line and Lake Echo to Lake Echo Tee No.1 line, avoid O/L the Tungatina to Lake Echo Tee No.1 line for loss of a Tarraleah to New Norfolk line
T>T_X_TULE_T2_LE1_4 | 2005-05-16 | 1 | Out = Lake Echo Tee to Tungatina No.2 110kV line and Lake Echo to Lake Echo Tee No.1 line, avoid O/L the Meadowbank to New Norfolk line for loss of Tungatina to Lake Echo Tee to Waddamana No.1 line
T>T_X_TULE_T2_LE1_5 | 2005-05-16 | 1 | Out = Lake Echo Tee to Tungatina No.2 110kV line and Lake Echo to Lake Echo Tee No.1 line, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of Tungatina to Lake Echo Tee to Waddamana No.1 line
T>T_X_TULE_T2_LE1_6 | 2005-05-16 | 1 | Out = Lake Echo Tee to Tungatina No.2 110kV line and Lake Echo to Lake Echo Tee No.1 line, avoid O/L the Tarraleah to New Norfolk No.1 line for loss of the Meadowbank to New Norfolk line
T>T_X_TULE_T2_LE1_7 | 2005-05-16 | 1 | Out = Lake Echo Tee to Tungatina No.2 110kV line and Lake Echo to Lake Echo Tee No.1 line, avoid O/L the Tungatina to Lake Echo Tee No.1 line for loss of the Meadowbank to New Norfolk line
T>T_X_TULE_T2_LE1_8 | 2005-05-16 | 1 | Out = Lake Echo Tee to Tungatina No.2 110kV line and Lake Echo to Lake Echo Tee No.1 line, avoid O/L Waddamana to Lake Echo Tee No.1 line for loss of the Chapel St to New Norfolk line
T>T_X_TULE_T2_LE1_9 | 2005-05-16 | 1 | Out = Lake Echo Tee to Tungatina No.2 110kV line and Lake Echo to Lake Echo Tee No.1 line, avoid O/L the Creek Rd to New Norfolk line for loss of the Chapel St to New Norfolk line
T>T_X_TUWA_TWO_TUTA | 2006-07-31 | 2 | Out = Both Tungatinah to Lake Echo Tee to Waddamana 110kV lines, avoid O/L remaining Tungatinah to Tarralea line for loss of the parallel line
T>T_X_TU_LE_WA_TWO | 2006-03-30 | 1 | Out = Both Tungatinah to Lake Echo Tee to Waddamana 110kV lines, avoid O/L New Norfolk to Creek Rd line for loss of New Norfolk to Chapel St line
T>X_FA_TX_FASH_BUS | 2006-01-19 | 1 | Out= one Farrell 220/110kV transformer and one Farrell to Sheffield line with Farrell 220kV busses tied, Hampshire link closed, avoid O/L Hampshire to Waratah Tee line
TESTSHRI | 2006-03-17 | 1 | Eff = 17/03/2006 ; RHS = 200 ; Op = "<=" ; Wt = 20
TVBL_ROC | 2006-12-27 | 1 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink
TV_000 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 0 MW
TV_050 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 50 MW
TV_100 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 100 MW
TV_150 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 150 MW
TV_200 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 200 MW
TV_250 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 250 MW
TV_300 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 300 MW
TV_350 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 350 MW
TV_400 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 400 MW
TV_450 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 450 MW
TV_500 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 500 MW
TV_550 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 550 MW
TV_600 | 2008-08-05 | 1 | Tas to Vic on Basslink upper limit of 600 MW
T^T_CSGO_1_DS | 2007-08-16 | 2 | Out = one Chapel St to Gordon 220 kV line, avoid voltage instability or violations for loss of the other Chapel St to Gordon line, Dispatch only
T^T_CSGO_1_N-2 | 2006-06-27 | 1 | Out = Nil, Loss of both Chapel St to Gordon 220 kV lines declared credible, avoid voltage instability or violations on loss of both lines
T^T_CSGO_1_PD | 2007-08-16 | 2 | Out = one Chapel St to Gordon 220 kV line, avoid voltage instability or violations for loss of the other Chapel St to Gordon line, Pre-Dispatch only
T^T_CSGO_2_DS | 2007-08-16 | 2 | Out = one Chapel St to Gordon 220 kV line, avoid voltage instability or violations for loss of Chapel St to Cluny Tee to Liapootah line, Dispatch only
T^T_CSGO_2_PD | 2007-08-16 | 2 | Out = one Chapel St to Gordon 220 kV line, avoid voltage instability or violations for loss of Chapel St to Cluny Tee to Liapootah line, Pre-Dispatch only
T^T_LICL_CS_4_SSSPS | 2007-10-23 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, Palmerston 110kV bus not split, avoid voltage instability or violations for loss of a Gordon to Chapel St line, SSSPS armed due to all Gordon units O/S and Tas southern load above 420 MW
T^T_LICL_CS_5_SSSPS | 2007-10-23 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, Palmerston 110kV bus not split, avoid voltage instability or violations for loss of a Liapootah to Chapel St line, SSSPS armed when all Gordon units O/S and Tas southern load above 420 MW
T^T_LICL_T_CS_1 | 2007-10-23 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, Palmerston 110kV bus not split, one Gordon machine in service, avoid voltage instability or violations for loss of the Gordon machine
T^T_LICL_T_CS_2 | 2007-10-23 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, Palmerston 110kV bus not split, two Gordon machines in service, avoid voltage instability or violations for loss of a Gordon machine
T^T_LICL_T_CS_3 | 2007-10-23 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, Palmerston 110kV bus not split, three Gordon machines in service, avoid voltage instability or olations for loss of a Gordon machine
T^T_LICL_T_CS_4 | 2007-10-23 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, Palmerston 110kV bus not split, avoid voltage instability or violations for loss of a Gordon to Chapel St line
T^T_LICL_T_CS_5 | 2007-10-23 | 1 | Out = Liapootah to Cluny Tee to Chapel St 220kV line, Palmerston 110kV bus not split, avoid voltage instability or violations for loss of a Liapootah to Chapel St line
T^T_LICS_1 | 2007-10-23 | 1 | Out = Liapootah to Chapel St 220kV line, Palmerston 110kV bus not split, one Gordon machine in service, avoid voltage instability or violations for loss of the Gordon machine
T^T_LICS_2 | 2007-10-23 | 1 | Out = Liapootah to Chapel St 220kV line, Palmerston 110kV bus not split, two Gordon machines in service, avoid voltage instability or violations for loss of a Gordon machine
T^T_LICS_3 | 2007-10-23 | 1 | Out = Liapootah to Chapel St 220kV line, Palmerston 110kV bus not split, three Gordon machines in service, avoid voltage instability or olations for loss of a Gordon machine
T^T_LICS_4 | 2007-10-23 | 1 | Out = Liapootah to Chapel St 220kV line, Palmerston 110kV bus not split, avoid voltage instability or violations for loss of a Gordon to Chapel St line
T^T_LICS_4_SSSPS | 2007-10-23 | 1 | Out = Liapootah to Chapel St 220kV line, Palmerston 110kV bus not split, avoid voltage instability or violations for loss of a Gordon to Chapel St line, SSSPS armed when all Gordon units O/S and Tas southern load above 420 MW
T^T_LICS_5 | 2007-10-23 | 1 | Out = Liapootah to Chapel St 220kV line, Palmerston 110kV bus not split, avoid voltage instability or violations for loss of a Liapootah to Cluny Tee to Chapel St line
T^T_LICS_5_SSSPS | 2007-10-23 | 1 | Out = Liapootah to Chapel St 220kV line, Palmerston 110kV bus not split, avoid voltage instability or violations for loss of a Liapootah to Cluny Tee to Chapel St line, SSSPS armed when all Gordon units O/S and Tas southern load above 420 MW
T^T_LIPM_1 | 2007-08-16 | 1 | Out = Liapootah to Palmerston line, avoid voltage instability or violations for loss of the other Liapootah to Palmerston line
T^T_LIPM_2 | 2007-08-16 | 1 | Out = Liapootah to Palmerston line, avoid voltage instability or violations for loss of Chapel St to Cluny Tee to Liapootah line
T^T_LIPM_3 | 2007-08-16 | 1 | Out = Liapootah to Palmerston line, avoid voltage instability or violations for loss of Gordon to Chapel St line
T^T_LIPM_4 | 2007-08-16 | 1 | Out = Liapootah to Palmerston line, one Gordon machine in service, avoid voltage instability or violations for loss of the Gordon machine
T^T_LIPM_5 | 2007-08-16 | 1 | Out = Liapootah to Palmerston line, two Gordon machines in service, avoid voltage instability or violations for loss of a Gordon machine
T^T_LIPM_6 | 2007-08-16 | 1 | Out = Liapootah to Palmerston line, three Gordon machines in service, avoid voltage instability or violations for loss of a Gordon machine
T^T_NIL_1 | 2005-06-16 | 1 | Out = Nil, Palmerston 110kV bus not split, one Gordon machine in service, avoid voltage instability for loss of the Gordon machine
T^T_NIL_1_DS_GOTEST | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, one Gordon machine in service, avoid voltage instability for loss of the Gordon machine, dispatch equation only, SSSPS armed during Gordon black start test scheduled on 19 Sep 2007
T^T_NIL_1_DS_SSSPS | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, one Gordon machine in service, avoid voltage instability for loss of the Gordon machine, dispatch equation only, SSSPS armed when all Gordon units O/S and Tas southern load above 630 MW
T^T_NIL_2 | 2005-06-16 | 1 | Out = Nil, Palmerston 110kV bus not split, two Gordon machines in service, avoid voltage instability for loss of a Gordon machine
T^T_NIL_2_DS_GOTEST | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, two Gordon machines in service, avoid voltage instability for loss of a Gordon machine, dispatch equation only, SSSPS armed during Gordon black start test scheduled on 19 Sep 2007
T^T_NIL_2_DS_SSSPS | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, two Gordon machines in service, avoid voltage instability for loss of a Gordon machine, dispatch equation only, SSSPS armed when all Gordon units O/S and Tas southern load above 630 MW
T^T_NIL_2_PD_GOTEST | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, two Gordon machines in service, avoid voltage instability for loss of a Gordon machine, dispatch pre-equation only, SSSPS armed during Gordon black start test scheduled on 19 Sep 2007
T^T_NIL_2_PD_SSSPS | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, two Gordon machines in service, avoid voltage instability for loss of a Gordon machine, dispatch pre-equation only, SSSPS armed when all Gordon units O/S and Tas southern load above 630 MW
T^T_NIL_3 | 2005-06-16 | 1 | Out = Nil, Palmerston 110kV bus not split, three Gordon machines in service, avoid voltage instability for loss of a Gordon machine
T^T_NIL_3_DS_GOTEST | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, three Gordon machines in service, avoid voltage instability for loss of a Gordon machine, dispatch equation only, SSSPS armed during Gordon black start test scheduled on 19 Sep 2007
T^T_NIL_3_DS_SSSPS | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, three Gordon machines in service, avoid voltage instability for loss of a Gordon machine, dispatch equation only, SSSPS armed when all Gordon units O/S and Tas southern load above 630 MW
T^T_NIL_4_DS | 2005-05-18 | 1 | Out = Nil, Palmerston 110kV bus not split, avoid voltage instability for loss of a Gordon to Chapel St line, dispatch equation only
T^T_NIL_4_DS_GOTEST | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, avoid voltage instability for loss of a Gordon to Chapel St 220 kV line, dispatch equation only, SSSPS armed during Gordon black start test scheduled on 19 Sep 2007
T^T_NIL_4_DS_SSSPS | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, avoid voltage instability for loss of a Gordon to Chapel St 220 kV line, dispatch equation only, SSSPS armed when all Gordon units O/S and Tas southern load above 630 MW
T^T_NIL_4_PD | 2005-09-02 | 1 | Out = Nil, Palmerston 110kV bus not split, avoid voltage instability for loss of a Gordon to Chapel St line, pre-dispatch equation only
T^T_NIL_4_PD_GOTEST | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, avoid voltage instability for loss of a Gordon to Chapel St 220 kV line, pre-dispatch equation only, SSSPS armed during Gordon black start test scheduled on 19 Sep 2007
T^T_NIL_4_PD_SSSPS | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, avoid voltage instability for loss of a Gordon to Chapel St 220 kV line, pre-dispatch equation only, SSSPS armed when all Gordon units O/S and Tas southern load above 630 MW
T^T_NIL_5_DS | 2005-05-18 | 1 | Out = Nil, Palmerston 110kV bus not split, avoid voltage instability for loss of a Liapootah to Cluny Tee to Chapel St line, dispatch equation only
T^T_NIL_5_DS_GOTEST | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, avoid voltage instability for loss of a Liapootah to Cluny Tee to Chapel St 220 kV line, dispatch equation only, SSSPS armed during Gordon black start test scheduled on 19 Sep 2007
T^T_NIL_5_DS_SSSPS | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, avoid voltage instability for loss of a Liapootah to Cluny Tee to Chapel St 220 kV line, dispatch equation only, SSSPS armed when all Gordon units O/S and Tas southern load above 630 MW
T^T_NIL_5_PD | 2005-09-02 | 1 | Out = Nil, Palmerston 110kV bus not split, avoid voltage instability for loss of a Liapootah to Cluny Tee to Chapel St line, pre-dispatch equation only
T^T_NIL_5_PD_GOTEST | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, avoid voltage instability for loss of a Liapootah to Cluny Tee to Chapel St 220 kV line, pre-dispatch equation only, SSSPS armed during Gordon black start test scheduled on 19 Sep 2007
T^T_NIL_5_PD_SSSPS | 2007-10-23 | 1 | Outage = Nil, Palmerston 110kV bus not split, avoid voltage instability for loss of a Liapootah to Cluny Tee to Chapel St 220 kV line, pre-dispatch equation only, SSSPS armed when all Gordon units O/S and Tas southern load above 630 MW
T^T_PMWA_1 | 2007-10-23 | 1 | Out = Palmerston to Waddamana 110kV line, Palmerston 110kV bus not split, one Gordon machine in service, avoid voltage instability for loss of the Gordon machine
T^T_PMWA_2 | 2007-10-23 | 1 | Out = Palmerston to Waddamana 110kV line, Palmerston 110kV bus not split, two Gordon machines in service, avoid voltage instability for loss of the Gordon machine
T^T_PMWA_3 | 2007-10-23 | 1 | Out = Palmerston to Waddamana 110kV line, Palmerston 110kV bus not split, three Gordon machines in service, avoid voltage instability for loss of the Gordon machine
T^T_PMWA_4 | 2007-10-23 | 1 | Out = Palmerston to Waddamana 110kV line, Palmerston 110kV bus not split, avoid voltage instability for loss of a Gordon to Chapel St line
T^T_PMWA_5 | 2007-10-23 | 1 | Out = Palmerston to Waddamana 110kV line, Palmerston 110kV bus not split, avoid voltage instability for loss of a Liapootah to Cluny Tee to Chapel St line
T^V_HAGT_BL_6 | 2005-12-08 | 1 | Outage = Hadspen to Georgetown 220kV line, Basslink in service, limit Basslink flow to Victoria to avoid transient over-voltage (TOV) for loss of Basslink
T^V_HAPM_220_BL_6 | 2005-12-08 | 1 | Outage = Hadspen to Palmerston 220kV line, Basslink in service, limit Basslink flow to Victoria to avoid transient over-voltage (TOV) for loss of Basslink
T^V_NIL_BL_6 | 2005-11-23 | 1 | Outage = Nil, Basslink in service, limit Basslink flow to Victoria to avoid transient over-voltage (TOV) for loss of Basslink
T^V_RPC_Q_MAX | 2008-09-09 | 1 | Outage = Nil, Basslink reactive power controller (RPC) at Georgetown operating in VAR (Q) mode, limit increase in Basslink flow to Vic to avoid under-voltage at Georgetown
T^V_RPC_Q_MIN | 2008-09-09 | 1 | Outage = Nil, Basslink reactive power controller (RPC) at Georgetown operating in VAR (Q) mode, limit decrease in Basslink flow to Vic to avoid over-voltage at Georgetown
T_BA_JB_RC2_300_RD | 2006-12-22 | 1 | Discretionary ramp down (25 MW per DI) to 300 MW on Bastyan, John Butters and Reece 2
T_BA_RC1+2_TI_300_RD | 2006-12-22 | 1 | Discretionary ramp down (25 MW per DI) to 300 MW on Bastyan, Reece 1+2 and Tribute
T_BA_RC2_TIMC_300_RD | 2006-12-22 | 1 | Discretionary ramp down (25 MW per DI) to 300 MW on Bastyan, Reece 2, Tribute and Mackintosh
T_BA_RC2_TI_300_RD | 2006-12-22 | 1 | Discretionary ramp down (25 MW per DI) to 300 MW on Bastyan, Reece 2 and Tribute
T_BB12_BBGT123_ZERO | 2008-04-10 | 1 | Discretionary 0 MW upper limit on Bell Bay no.1 & no.2 and Bell bay GT's no.1, no.2 & no.3
T_BB12_MIN_50 | 2007-11-09 | 1 | Discretionary minimum 50 MW limit on Bell Bay 1 and 2
T_BELLBAY_180 | 2006-01-18 | 1 | Discretionary upper limit of 180 MW for total Bell Bay generation
T_BUHM_WC1 | 2006-11-09 | 1 | Out = Burnie-Hampshire 110 kV line and one Farrell-Sheffield 220 kV line or reclassification of the loss of both FA-SH lines as a credible contingency. West Coast generators to be greater than 0.9*West Coast Load.
T_BUHM_WC2 | 2006-11-09 | 1 | Out = Burnie-Hampshire 110 kV line and one Farrell-Sheffield 220 kV line or reclassification of the loss of both FA-SH lines as a credible contingency. West Coast generators to be less than 1.1*West Coast Load.
T_DG_0 | 2007-03-01 | 1 | Devils Gate = 0MW. Energy <= 0MW
T_FABA | 2007-03-01 | 1 | Out=Farrell-Bastyan 220KV line. Energy <= 0MW
T_FAJB | 2007-03-01 | 1 | Out=Farrell-John Butters 220KV line. Energy <= 0MW
T_FAMA | 2007-03-01 | 1 | Out=Farrell-Mackintosh 110KV line. Energy <= 0MW
T_FARC1 | 2007-03-01 | 1 | Out=Farrell-Reece 1 220KV line. Energy <= 0MW
T_FARC2 | 2007-03-01 | 1 | Out=Farrell-Reece 2 220KV line. Energy <= 0MW
T_FASH_1_2_A_RAMP | 2006-12-22 | 1 | Ramp down (25 MW per DI) Tas west coast units for outage of one Farrell to Sheffield line with Mackintosh unavailable, Farrell 220kV bus NOT split, Hampshire link closed
T_FASH_1_2_B_WC_RAMP | 2006-12-27 | 1 | Ramp down (25 MW per DI) Bastyan, John Butters and Mackintosh to 110% of West Coast load for an outage of either Farrell to Sheffield line with Reece 1,2 and Tribute supplying Sheffield
T_FASH_1_2_C_WC_RAMP | 2007-06-07 | 1 | Ramp down (25 MW per DI) Bastyan and Mackintosh to 110% of West Coast load for an outage of either Farrell to Sheffield line with JButters, Reece 1,2 and Tribute supplying Sheffield
T_FASH_1_2_D_WC_RAMP | 2007-11-19 | 2 | Ramp down (25 MW per DI) Reece 1 and Mackintosh to 110% of West Coast load for an outage of either Farrell to Sheffield line with Bastyan, John Butters, Reece 2 and Tribute supplying Sheffield
T_FASH_1_2_MINGEN | 2006-02-06 | 1 | Out = one Farrell to Sheffield line with Mackintosh unavailable, Hampshire link closed, Minimum limit on John Butters to allow PSS to be in service
T_FASH_1_A_WC_RAMP | 2006-12-22 | 1 | Ramp down (25 MW per DI) Mackintosh, Reece 1 and Tribute to 110% of West Coast load for an outage of Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield
T_FASH_1_B_WC_RAMP | 2006-12-22 | 1 | Ramp down (25 MW per DI) John Butters and to 110% of West Coast load for an outage of Farrell to Sheffield No.1 line with Bastyan, Reece 1+2 and Tribute supplying Sheffield
T_FASH_2_A_WC_RAMP | 2006-12-22 | 1 | Ramp down (25 MW per DI) Bastyan, John Butters, Mackintosh and Reece 2 to 110% of West Coast load for an outage of Farrell to Sheffield No.1 line with Reece 1 and Tribute supplying Sheffield
T_FASH_MIN_JB | 2006-01-12 | 1 | Minimum limit on John Butters for Farrell to Sheffield outages to allow PSS to be in service
T_FASH_MIN_RC1 | 2006-01-06 | 1 | Minimum limit on Reece 1 for Farrell to Sheffield outages to allow PSS to be in service
T_FASH_N-2_WC_RAMP | 2006-12-22 | 1 | Ramp down (25 MW per DI) Mackintosh, Reece 1 and Tribute for loss of both Farrell to Sheffield lines declared credible
T_FATI | 2007-03-01 | 1 | Out=Farrell-Tribute 220KV line. Energy <= 0MW
T_GO_160 | 2005-08-16 | 1 | Discretionary 160 MW upper limit on total Gordon generation
T_GO_180 | 2005-08-16 | 1 | Discretionary 180 MW upper limit on total Gordon generation
T_GO_200 | 2005-08-16 | 1 | Discretionary 200 MW upper limit on total Gordon generation
T_GO_BUS | 2005-08-23 | 1 | Out=Gordon 220kV bus, one bus and one generator out of service only
T_GO_ZERO | 2005-11-22 | 1 | Discretionary 0 MW upper limit on total Gordon generation
T_GTBB1 | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 1 110KV line. Energy <= 0MW
T_GTBB2 | 2007-03-01 | 1 | Out=Georgetown-Bell Bay 2 110KV line. Energy <= 0MW
T_JB_MC_300_RD | 2006-12-22 | 1 | Discretionary ramp down (25 MW per DI) to 300 MW on John Butters and Mackintosh
T_JB_RC1_300_RD | 2006-12-22 | 1 | Discretionary ramp down (25 MW per DI) to 300 MW on John Butters and Reece 1
T_JB_RC1_MC_300_RD | 2006-12-22 | 1 | Discretionary ramp down (25 MW per DI) to 300 MW on John Butters + Reece_1 + Mackintosh
T_LIPM_PMWA_1_N-3 | 2007-05-15 | 1 | Out=Nil, loss of both Liapootah to Palmerston and Palmerston to Waddamana lines classified credible, limit southern generators to <= southern load + 15 MW
T_LIPM_PMWA_2_N-3 | 2007-05-16 | 1 | Out=Nil, loss of both Liapootah to Palmerston and Palmerston to Waddamana lines classified credible, limit southern generators to >= southern load - 15 MW
T_LIWY | 2005-05-31 | 1 | Out=Liapootah-Wayatinah 220KV line
T_LI_GEN_CB | 2006-09-14 | 1 | Out=Liapootah single 220KV generator CB (A52 or B52 or C52)
T_MA_WESTCOAST_1 | 2006-01-25 | 1 | Limit Mackintosh to 110% of West Coast load
T_MA_WESTCOAST_2 | 2006-01-25 | 1 | Limit Mackintosh to 90% of West Coast load
T_MB_ZERO | 2007-03-01 | 1 | Limit Meadowbank to zero MW
T_PMPO_110 | 2005-05-31 | 1 | Out=A single Palmerston-Poatina 110KV line. One line out of service only
T_PMPO_220 | 2005-07-05 | 2 | Out=A single Palmerston-Poatina 220KV line. One line out of service only
T_PMPO_FOUR_220 | 2007-03-01 | 1 | Out= All four Palmerston-Poatina 220KV lines
T_PMPO_THREE_220 | 2005-08-30 | 1 | Out= three Palmerston to Poatina 220KV lines
T_PMPO_TWO_110 | 2007-03-01 | 1 | Out=Both Palmerston-Poatina 110KV lines.
T_PMPO_TWO_220 | 2005-07-05 | 1 | Out= two Palmerston to Poatina 220KV lines
T_PO110_MIN_60 | 2005-06-17 | 3 | Discretionary minimum 60 MW limit on Poatina 1 and 2 (110kV)
T_RC1_TI_300_RD | 2006-12-22 | 1 | Discretionary ramp down (25 MW per DI) to 300 MW on Reece 1 and Tribute
T_SHCE | 2007-03-01 | 1 | Out=Sheffield-Cethana 220KV line. Energy <= 0MW
T_SHDG | 2007-03-01 | 1 | Out=Sheffield-Devils Gate 110KV line. Energy <= 0MW
T_SHFI | 2007-03-01 | 1 | Out=Sheffield-Fisher 220KV line. Energy <= 0MW
T_SHLT | 2005-05-31 | 1 | Out=Sheffield-Lemonthyme 220KV line.
T_SHWI | 2005-05-31 | 1 | Out-Sheffield-Wilmot 220KV line
T_TR_30 | 2005-05-16 | 1 | Discretionary 30MW lower limit on Trevallyn
T_TR_MIN_36 | 2005-06-17 | 1 | Discretionary minimum 36MW limit on Trevallyn
T_TR_ZERO | 2005-11-22 | 1 | Discretionary 0 MW upper limit on Trevallyn
T_T_BA_JB_RC2_050 | 2006-01-10 | 1 | Discretionary 50 MW upper limit on Bastyan, John Butters and Reece 2
T_T_BA_JB_RC2_100 | 2006-01-10 | 1 | Discretionary 100 MW upper limit on Bastyan, John Butters and Reece 2
T_T_BA_JB_RC2_150 | 2006-01-10 | 1 | Discretionary 150 MW upper limit on Bastyan, John Butters and Reece 2
T_T_BA_JB_RC2_175 | 2006-01-10 | 1 | Discretionary 175 MW upper limit on Bastyan, John Butters and Reece 2
T_T_BA_JB_RC2_185 | 2006-01-10 | 1 | Discretionary 185 MW upper limit on Bastyan, John Butters and Reece 2
T_T_BA_JB_RC2_200 | 2006-01-10 | 1 | Discretionary 200 MW upper limit on Bastyan, John Butters and Reece 2
T_T_BA_JB_RC2_225 | 2006-01-10 | 1 | Discretionary 225 MW upper limit on Bastyan, John Butters and Reece 2
T_T_BA_JB_RC2_250 | 2006-01-10 | 1 | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2
T_T_BA_JB_RC2_275 | 2006-01-10 | 1 | Discretionary 275 MW upper limit on Bastyan, John Butters and Reece 2
T_T_BA_RC1+2_TI_050 | 2005-10-07 | 1 | Discretionary 50 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_100 | 2005-10-07 | 1 | Discretionary 100 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_145 | 2005-10-07 | 1 | Discretionary 145 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_155 | 2005-10-07 | 1 | Discretionary 155 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_165 | 2005-10-07 | 1 | Discretionary 165 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_175 | 2005-10-07 | 1 | Discretionary 175 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_185 | 2005-10-07 | 1 | Discretionary 185 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_200 | 2005-10-07 | 1 | Discretionary 200 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_225 | 2005-10-07 | 1 | Discretionary 225 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_250 | 2005-10-07 | 1 | Discretionary 250 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_275 | 2005-10-07 | 1 | Discretionary 275 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_300 | 2005-10-07 | 1 | Discretionary 300 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_325 | 2005-10-07 | 1 | Discretionary 325 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC1+2_TI_350 | 2005-10-07 | 1 | Discretionary 350 MW upper limit on Bastyan, Reece 1+2 and Tribute
T_T_BA_RC2_TI_050 | 2005-05-20 | 1 | Discretionary 50 MW upper limit on Bastyan, Reece 2 and Tribute
T_T_BA_RC2_TI_100 | 2005-05-20 | 1 | Discretionary 100 MW upper limit on Bastyan, Reece 2 and Tribute
T_T_BA_RC2_TI_145 | 2005-05-16 | 1 | Discretionary 145 MW upper limit on Bastyan, Reece 2 and Tribute
T_T_BA_RC2_TI_155 | 2005-05-16 | 1 | Discretionary 155 MW upper limit on Bastyan, Reece 2 and Tribute
T_T_BA_RC2_TI_165 | 2005-05-16 | 1 | Discretionary 165 MW upper limit on Bastyan, Reece 2 and Tribute
T_T_BA_RC2_TI_175 | 2005-05-16 | 1 | Discretionary 175 MW upper limit on Bastyan, Reece 2 and Tribute
T_T_BA_RC2_TI_185 | 2005-05-16 | 2 | Discretionary 185 MW upper limit on Bastyan, Reece 2 and Tribute
T_T_BA_RC2_TI_200 | 2005-10-12 | 1 | Discretionary 200 MW upper limit on Bastyan, Reece 2 and Tribute
T_T_BA_RC2_TI_225 | 2005-10-12 | 1 | Discretionary 225 MW upper limit on Bastyan, Reece 2 and Tribute
T_T_BA_RC2_TI_250 | 2005-10-12 | 1 | Discretionary 250 MW upper limit on Bastyan, Reece 2 and Tribute
T_T_BA_RC2_TI_JB_050 | 2007-11-19 | 1 | Discretionary 50 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_075 | 2007-11-19 | 1 | Discretionary 75 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_100 | 2007-11-19 | 1 | Discretionary 100 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_125 | 2007-11-19 | 1 | Discretionary 125 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_145 | 2007-11-19 | 1 | Discretionary 145 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_155 | 2007-11-19 | 1 | Discretionary 155 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_165 | 2007-11-19 | 1 | Discretionary 165 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_175 | 2007-11-19 | 1 | Discretionary 175 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_185 | 2007-11-19 | 1 | Discretionary 185 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_200 | 2007-11-19 | 1 | Discretionary 200 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_225 | 2007-11-19 | 1 | Discretionary 225 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_250 | 2007-11-19 | 1 | Discretionary 250 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_300 | 2007-11-19 | 1 | Discretionary 300 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_325 | 2007-11-19 | 1 | Discretionary 325 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_350 | 2007-11-19 | 1 | Discretionary 350 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_375 | 2007-11-19 | 1 | Discretionary 375 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_JB_400 | 2007-11-19 | 1 | Discretionary 400 MW upper limit on Bastyan, Reece 2, Tribute and John Butters
T_T_BA_RC2_TI_MC_050 | 2005-10-12 | 1 | Discretionary 50 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_BA_RC2_TI_MC_075 | 2005-10-12 | 1 | Discretionary 75 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_BA_RC2_TI_MC_100 | 2005-10-12 | 1 | Discretionary 100 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_BA_RC2_TI_MC_125 | 2005-10-12 | 1 | Discretionary 125 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_BA_RC2_TI_MC_145 | 2005-10-12 | 1 | Discretionary 145 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_BA_RC2_TI_MC_155 | 2005-10-12 | 1 | Discretionary 155 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_BA_RC2_TI_MC_165 | 2005-10-12 | 1 | Discretionary 165 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_BA_RC2_TI_MC_175 | 2005-10-12 | 1 | Discretionary 175 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_BA_RC2_TI_MC_185 | 2005-10-12 | 1 | Discretionary 185 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_BA_RC2_TI_MC_200 | 2005-10-12 | 1 | Discretionary 200 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_BA_RC2_TI_MC_225 | 2005-10-12 | 1 | Discretionary 225 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_BA_RC2_TI_MC_250 | 2005-10-12 | 1 | Discretionary 250 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_BA_RC2_TI_MC_300 | 2005-10-12 | 1 | Discretionary 300 MW upper limit on Bastyan, Reece 2, Tribute and Mackintosh
T_T_FASH1_A_1 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Hampshire link closed, limit Reece 1 + Tribute + Mackintosh <= 110% of West Coast load
T_T_FASH1_A_2 | 2007-01-02 | 1 | Out = Farrell to Sheffield No.1 line with Bastyan + John Butters + Reece 2 supplying Sheffield, Hampshire link closed, limit Reece 1 + Tribute + Mackintosh >= 90% of West Coast load
T_T_FASH1_B_1 | 2006-01-10 | 1 | Out = Farrell to Sheffield No.2 line, Farrell 220kV bus split JButters supplying transformers other generators supplying the 220kV line to Sheffield, Hampshire link closed, limit John Butters + Mackintosh <= 110% of West Coast load
T_T_FASH1_B_2 | 2006-01-10 | 1 | Out = Farrell to Sheffield No.2 line, Farrell 220kV bus split JButters supplying transformers other generators supplying the 220kV line to Sheffield, Hampshire link closed, limit John Butters + Mackintosh >= 90% of West Coast load
T_T_FASH2_A_1 | 2006-01-06 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Hampshire link closed, limit Bastyan + Reece 2 + John Butters + Mackintosh <= 110% of West Coast load
T_T_FASH2_A_2 | 2007-01-02 | 1 | Out = Farrell to Sheffield No.2 line with Tribute and Reece 1 supplying Sheffield, Hampshire link closed, limit Bastyan + Reece 2 + John Butters + Mackintosh >= 90% of West Coast load
T_T_FASH_1_N-2 | 2006-01-30 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Hampshire link open, limit Tribute, Reece 1 + Mackintosh <= 110% of West Coast load
T_T_FASH_2_N-2 | 2006-01-30 | 1 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Hampshire link open, limit Tribute + Reece 1 + Mackintosh >= 90% of West Coast load
T_T_FA_TX_1 | 2007-10-04 | 1 | Out = Farrell 220/110kV transformer, limit Mackintosh <= 110% of West Coast load
T_T_FA_TX_2 | 2007-10-04 | 1 | Out = Farrell 220/110kV transformer, limit Mackintosh >= 90% of West Coast load
T_T_JB_MC_050 | 2005-10-07 | 1 | Discretionary 50 MW upper limit on John Butters and Mackintosh
T_T_JB_MC_075 | 2005-10-13 | 1 | Discretionary 75 MW upper limit on John Butters and Mackintosh
T_T_JB_MC_100 | 2005-10-07 | 1 | Discretionary 100 MW upper limit on John Butters and Mackintosh
T_T_JB_MC_145 | 2005-10-07 | 1 | Discretionary 145 MW upper limit on John Butters and Mackintosh
T_T_JB_MC_155 | 2005-10-07 | 1 | Discretionary 155 MW upper limit on John Butters and Mackintosh
T_T_JB_MC_165 | 2005-10-07 | 1 | Discretionary 165 MW upper limit on John Butters and Mackintosh
T_T_JB_MC_175 | 2005-10-07 | 1 | Discretionary 175 MW upper limit on John Butters and Mackintosh
T_T_JB_MC_185 | 2005-10-07 | 1 | Discretionary 185 MW upper limit on John Butters and Mackintosh
T_T_JB_MC_200 | 2005-10-07 | 1 | Discretionary 200 MW upper limit on John Butters and Mackintosh
T_T_JB_RC1_050 | 2005-05-20 | 1 | Discretionary 50 MW upper limit on John Butters and Reece 1
T_T_JB_RC1_100 | 2005-05-20 | 1 | Discretionary 100 MW upper limit on John Butters and Reece 1
T_T_JB_RC1_145 | 2005-05-16 | 1 | Discretionary 145 MW upper limit on John Butters and Reece 1
T_T_JB_RC1_155 | 2005-05-16 | 1 | Discretionary 155 MW upper limit on John Butters and Reece 1
T_T_JB_RC1_165 | 2005-05-16 | 1 | Discretionary 165 MW upper limit on John Butters and Reece 1
T_T_JB_RC1_175 | 2005-05-16 | 1 | Discretionary 175 MW upper limit on John Butters and Reece 1
T_T_JB_RC1_185 | 2005-05-16 | 2 | Discretionary 185 MW upper limit on John Butters and Reece 1
T_T_JB_RC1_200 | 2005-10-12 | 1 | Discretionary 200 MW upper limit on John Butters and Reece 1
T_T_JB_RC1_225 | 2005-10-12 | 1 | Discretionary 225 MW upper limit on John Butters and Reece 1
T_T_JB_RC1_MC_050 | 2005-10-12 | 1 | Discretionary limit 50 MW >(John Butters + Reece_1 + Mackintosh)
T_T_JB_RC1_MC_075 | 2005-10-12 | 1 | Discretionary limit 75 MW >(John Butters + Reece_1 + Mackintosh)
T_T_JB_RC1_MC_100 | 2005-08-04 | 1 | Discretionary limit 100 MW >(John Butters + Reece_1 + Mackintosh)
T_T_JB_RC1_MC_125 | 2005-10-12 | 1 | Discretionary limit 125 MW >(John Butters + Reece_1 + Mackintosh)
T_T_JB_RC1_MC_145 | 2005-08-04 | 1 | Discretionary limit 145 MW >(John Butters + Reece_1 + Mackintosh)
T_T_JB_RC1_MC_155 | 2005-08-04 | 1 | Discretionary limit 155 MW >(John Butters + Reece_1 + Mackintosh)
T_T_JB_RC1_MC_165 | 2005-08-04 | 1 | Discretionary limit 165 MW >(John Butters + Reece_1 + Mackintosh)
T_T_JB_RC1_MC_175 | 2005-08-04 | 1 | Discretionary limit 175 MW >(John Butters + Reece_1 + Mackintosh)
T_T_JB_RC1_MC_185 | 2005-08-04 | 1 | Discretionary limit 185 MW >(John Butters + Reece_1 + Mackintosh)
T_T_JB_RC1_MC_200 | 2005-08-04 | 1 | Discretionary limit 200 MW >(John Butters + Reece_1 + Mackintosh)
T_T_JB_RC1_MC_225 | 2005-08-04 | 1 | Discretionary limit 225 MW >(John Butters + Reece_1 + Mackintosh)
T_T_JB_RC1_MC_250 | 2005-10-12 | 1 | Discretionary limit 250 MW >(John Butters + Reece_1 + Mackintosh)
T_T_JB_RC1_MC_300 | 2005-10-12 | 1 | Discretionary limit 300 MW >(John Butters + Reece_1 + Mackintosh)
T_T_TA_TU_105 | 2006-08-01 | 1 | Discretionary 105 MW upper limit on Tarraleah and Tungatinah
T_T_TA_TU_115 | 2006-08-01 | 1 | Discretionary 115 MW upper limit on Tarraleah and Tungatinah
T_T_TA_TU_125 | 2006-08-01 | 1 | Discretionary 125 MW upper limit on Tarraleah and Tungatinah
T_T_TA_TU_135 | 2006-08-01 | 1 | Discretionary 135 MW upper limit on Tarraleah and Tungatinah
T_T_TA_TU_145 | 2006-08-01 | 1 | Discretionary 145 MW upper limit on Tarraleah and Tungatinah
T_T_TA_TU_155 | 2006-08-01 | 1 | Discretionary 155 MW upper limit on Tarraleah and Tungatinah
T_T_TA_TU_165 | 2006-08-01 | 1 | Discretionary 165 MW upper limit on Tarraleah and Tungatinah
T_T_TA_TU_175 | 2006-08-01 | 1 | Discretionary 175 MW upper limit on Tarraleah and Tungatinah
T_T_TA_TU_185 | 2006-08-01 | 1 | Discretionary 185 MW upper limit on Tarraleah and Tungatinah
T_T_TA_TU_195 | 2006-08-01 | 1 | Discretionary 195 MW upper limit on Tarraleah and Tungatinah
T_T_TA_TU_205 | 2006-08-01 | 1 | Discretionary 205 MW upper limit on Tarraleah and Tungatinah
T_T_TA_TU_215 | 2006-08-01 | 1 | Discretionary 215 MW upper limit on Tarraleah and Tungatinah
T_T_TA_TU_BG_205 | 2006-08-07 | 1 | 205 MW upper limit on Tarraleah, Tungatinah and Butlers Gorge generation
T_T_TU_75 | 2007-05-07 | 1 | Discretionary 75 MW (60% of registered capacity) upper limit on Tungatinah
T_T_TU_BG_80 | 2007-05-17 | 1 | 80 MW upper limit on Tungatinah and Butlers Gorge generation
T_T_X_FASH_A | 2006-05-11 | 1 | Out = both Farrell to Sheffield lines, limit West Coast gen <= 110% of West Coast load
T_T_X_FASH_B | 2006-05-11 | 1 | Out = both Farrell to Sheffield lines, limit West Coast gen >= 90% of West Coast load
T_V_FCSPS_RAMP | 2007-02-06 | 1 | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS
T_V_NIL_BL1 | 2008-05-26 | 1 | Out=Nil, Basslink no go zone limits Tas to Vic
T_V_NIL_FCSPS | 2007-02-06 | 1 | Basslink limit from Tas to Vic for generation enabled for FCSPS
T_WESTCOAST+HM_RAMP | 2006-12-22 | 1 | Ramp down (25 MW per DI) Tas west coast generation to West Coast load + rating of Hampshire link
T_WESTCOAST_075 | 2006-05-16 | 1 | West Coast Generation limited to <= 75 MW
T_WESTCOAST_150 | 2006-05-16 | 1 | West Coast Generation limited to <= 150 MW
T_WESTCOAST_225 | 2006-05-16 | 1 | West Coast Generation limited to <= 225 MW
T_WESTCOAST_300 | 2006-05-16 | 1 | West Coast Generation limited to <= 300 MW
T_WESTCOAST_360 | 2005-05-16 | 1 | West Coast Generation limited to <= 360MW
T_WESTCOAST_375 | 2006-05-16 | 1 | West Coast Generation limited to <= 375 MW
T_WESTCOAST_450 | 2006-05-16 | 1 | West Coast Generation limited to <= 450 MW
T_WESTCOAST_475 | 2008-05-12 | 1 | West coast generation <=475 MW
T_WESTCOAST_525 | 2006-05-16 | 1 | West Coast Generation limited to <= 525 MW
T_WESTCOAST_RD | 2006-12-22 | 1 | Ramp down (25 MW per DI) TAS west coast generation to West Coast load
T_WYCA | 2005-05-31 | 1 | Out=Wayatinah-Catagunya 220KV line
T_X_GTSH_1 | 2008-07-16 | 1 | Outage = Both Georgetown to Sheffield 220kV lines, limit West Coast + Sheffield generation <= West Coast + North West load + 10MW, limiting SH-PM line flow to 10 MW
T_X_GTSH_2 | 2008-07-16 | 1 | Outage = Both Georgetown to Sheffield 220kV lines, limit West Coast + Sheffield generation => West Coast + North West load - 10MW, limiting PM-SH line flow to 10 MW
T_X_HAGT_1 | 2008-07-16 | 1 | Outage = Both Hadspen to Georgetown 220kV lines, limit Southern + Poatina + Trevallyn generation <= South + North load + 10MW, limiting PM-SH line flow to 10 MW
T_X_HAGT_2 | 2008-07-16 | 1 | Outage = Both Hadspen to Georgetown 220kV lines, limit Southern + Poatina + Trevallyn generation => South + North load - 10MW, limiting SH-PM line flow to 10 MW
T_X_PMSH+GTSH_1 | 2008-07-16 | 1 | Outage = Palmerston to Sheffield 220kV line and one Georgetown to Sheffield 220kV line, limit West Coast + Sheffield generation <= West Coast + North West load + 10MW, limiting SH-GT line flow to 10 MW
T_X_PMSH+GTSH_2 | 2008-07-16 | 1 | Outage = Palmerston to Sheffield 220kV line and one Georgetown to Sheffield 220kV line, limit West Coast + Sheffield generation => West Coast + North West load - 10MW, limiting GT-SH line flow to 10 MW
T_X_PMSH+HAGT_1 | 2008-07-16 | 1 | Outage = Palmerston to Sheffield 220kV line and one Hadspen to Georgetown 220kV line, limit Southern + Poatina + Trevallyn generation <= South + North load + 10MW, limiting HA-GT line flow to 10 MW
T_X_PMSH+HAGT_2 | 2008-07-16 | 1 | Outage = Palmerston to Sheffield 220kV line and one Hadspen to Georgetown 220kV line, limit Southern + Poatina + Trevallyn generation => South + North load - 10MW, limiting GT-HA line flow to 10 MW
V::N_2RPQA_R | 2008-07-01 | 1 | Outage = 2 dynamic reactive plant from Vic metro or SESS SVC's, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_2RPQB_R | 2008-07-01 | 1 | Outage = 2 dynamic reactive plant from Vic metro or SESS SVC's, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_2RPQC_R | 2008-07-01 | 1 | Outage = 2 dynamic reactive plant from Vic metro or SESS SVC's, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_2RPQD_R | 2008-07-01 | 1 | Outage = 2 dynamic reactive plant from Vic metro or SESS SVC's, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_2RPQE_R | 2008-07-01 | 1 | Outage = 2 dynamic reactive plant from Vic metro or SESS SVC's, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_2RPQF_R | 2008-07-01 | 1 | Outage = 2 dynamic reactive plant from Vic metro or SESS SVC's, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_2RPVA_R | 2008-07-01 | 1 | Outage = 2 dynamic reactive plant from Vic metro or SESS SVC's, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_2RPVB_R | 2008-07-01 | 1 | Outage = 2 dynamic reactive plant from Vic metro or SESS SVC's, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_2RPVC_R | 2008-07-01 | 1 | Outage = 2 dynamic reactive plant from Vic metro or SESS SVC's, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_2RPVD_R | 2008-07-01 | 1 | Outage = 2 dynamic reactive plant from Vic metro or SESS SVC's, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_2RPVE_R | 2008-07-01 | 1 | Outage = 2 dynamic reactive plant from Vic metro or SESS SVC's, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_2RPVF_R | 2008-07-01 | 1 | Outage = 2 dynamic reactive plant from Vic metro or SESS SVC's, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BABEQA_R | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BABEQB_R | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BABEQC_R | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BABEQD_R | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BABEQE_R | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BABEQF_R | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BABEVA_R | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BABEVB_R | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BABEVC_R | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BABEVD_R | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BABEVE_R | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BABEVF_R | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BAHOQA_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BAHOQB_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BAHOQC_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BAHOQD_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BAHOQE_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BAHOQF_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BAHOVA_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BAHOVB_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BAHOVC_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BAHOVD_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BAHOVE_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BAHOVF_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BUDPQA_R | 2008-07-01 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BUDPQB_R | 2008-07-01 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BUDPQC_R | 2008-07-01 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BUDPQD_R | 2008-07-01 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BUDPQE_R | 2008-07-01 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BUDPQF_R | 2008-07-01 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BUDPVA_R | 2008-07-01 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BUDPVB_R | 2008-07-01 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BUDPVC_R | 2008-07-01 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BUDPVD_R | 2008-07-01 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BUDPVE_R | 2008-07-01 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BUDPVF_R | 2008-07-01 | 1 | Outage = Buronga to Darlington Point 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BURCQA_R | 2008-07-01 | 1 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BURCQB_R | 2008-07-01 | 1 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BURCQC_R | 2008-07-01 | 1 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BURCQD_R | 2008-07-01 | 1 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BURCQE_R | 2008-07-01 | 1 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BURCQF_R | 2008-07-01 | 1 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BURCVA_R | 2008-07-01 | 1 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BURCVB_R | 2008-07-01 | 1 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BURCVC_R | 2008-07-01 | 1 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BURCVD_R | 2008-07-01 | 1 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BURCVE_R | 2008-07-01 | 1 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BURCVF_R | 2008-07-01 | 1 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_BYPASS_HW_SY_QA | 2008-07-01 | 1 | Outage = All three SMTS 500kV CB's for HWTS and SYTS line (No.1 or No.2) with temporary bypass for a direct HWTS to SYTS line, limit Vic gens and interconnectors to avoid transient instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line
V::N_BYPASS_HW_SY_QB | 2008-07-01 | 1 | Outage = All three SMTS 500kV CB's for HWTS and SYTS line (No.1 or No.2) with temporary bypass for a direct HWTS to SYTS line, limit Vic gens and interconnectors to avoid transient instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line
V::N_BYPASS_HW_SY_QC | 2008-07-01 | 1 | Outage = All three SMTS 500kV CB's for HWTS and SYTS line (No.1 or No.2) with temporary bypass for a direct HWTS to SYTS line, limit Vic gens and interconnectors to avoid transient instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line
V::N_BYPASS_HW_SY_QD | 2008-07-01 | 1 | Outage = All three SMTS 500kV CB's for HWTS and SYTS line (No.1 or No.2) with temporary bypass for a direct HWTS to SYTS line, limit Vic gens and interconnectors to avoid transient instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line
V::N_BYPASS_HW_SY_QE | 2008-07-01 | 1 | Outage = All three SMTS 500kV CB's for HWTS and SYTS line (No.1 or No.2) with temporary bypass for a direct HWTS to SYTS line, limit Vic gens and interconnectors to avoid transient instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line
V::N_BYPASS_HW_SY_QF | 2008-07-01 | 1 | Outage = All three SMTS 500kV CB's for HWTS and SYTS line (No.1 or No.2) with temporary bypass for a direct HWTS to SYTS line, limit Vic gens and interconnectors to avoid transient instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line
V::N_BYPASS_HW_SY_VA | 2008-07-01 | 1 | Outage = All three SMTS 500kV CB's for HWTS and SYTS line (No.1 or No.2) with temporary bypass for a direct HWTS to SYTS line, limit Vic gens and interconnectors to avoid transient instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line
V::N_BYPASS_HW_SY_VB | 2008-07-01 | 1 | Outage = All three SMTS 500kV CB's for HWTS and SYTS line (No.1 or No.2) with temporary bypass for a direct HWTS to SYTS line, limit Vic gens and interconnectors to avoid transient instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line
V::N_BYPASS_HW_SY_VC | 2008-07-01 | 1 | Outage = All three SMTS 500kV CB's for HWTS and SYTS line (No.1 or No.2) with temporary bypass for a direct HWTS to SYTS line, limit Vic gens and interconnectors to avoid transient instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line
V::N_BYPASS_HW_SY_VD | 2008-07-01 | 1 | Outage = All three SMTS 500kV CB's for HWTS and SYTS line (No.1 or No.2) with temporary bypass for a direct HWTS to SYTS line, limit Vic gens and interconnectors to avoid transient instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line
V::N_BYPASS_HW_SY_VE | 2008-07-01 | 1 | Outage = All three SMTS 500kV CB's for HWTS and SYTS line (No.1 or No.2) with temporary bypass for a direct HWTS to SYTS line, limit Vic gens and interconnectors to avoid transient instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line
V::N_BYPASS_HW_SY_VF | 2008-07-01 | 1 | Outage = All three SMTS 500kV CB's for HWTS and SYTS line (No.1 or No.2) with temporary bypass for a direct HWTS to SYTS line, limit Vic gens and interconnectors to avoid transient instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line
V::N_DDMS2 | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit NSW to VIC to avoid transient instability for fault and trip of a Dederang to South Morang 330kV line, equation 1.2 from TLM-D minus 105MW
V::N_DDMSQA_R | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit Vic generators and interconnectors to avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDMSQB_R | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit Vic generators and interconnectors to avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDMSQC_R | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit Vic generators and interconnectors to avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDMSQD_R | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit Vic generators and interconnectors to avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDMSQE_R | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit Vic generators and interconnectors to avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDMSQF_R | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit Vic generators and interconnectors to avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDMSVA_R | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit Vic generators and interconnectors to avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDMSVB_R | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit Vic generators and interconnectors to avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDMSVC_R | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit Vic generators and interconnectors to avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDMSVD_R | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit Vic generators and interconnectors to avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDMSVE_R | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit Vic generators and interconnectors to avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDMSVF_R | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit Vic generators and interconnectors to avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDSM2 | 2008-07-01 | 1 | Outage = Dederang to South Morang 330kV line, limit VIC to NSW to avoid transient instability for fault and trip of a Dederang to South Morang 330kV line, equation 3.2q from TLM-Q
V::N_DDWOQA_R | 2008-07-01 | 1 | Outage = Dederang to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDWOQB_R | 2008-07-01 | 1 | Outage = Dederang to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDWOQC_R | 2008-07-01 | 1 | Outage = Dederang to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDWOQD_R | 2008-07-01 | 1 | Outage = Dederang to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDWOQE_R | 2008-07-01 | 1 | Outage = Dederang to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDWOQF_R | 2008-07-01 | 1 | Outage = Dederang to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDWOVA_R | 2008-07-01 | 1 | Outage = Dederang to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDWOVB_R | 2008-07-01 | 1 | Outage = Dederang to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDWOVC_R | 2008-07-01 | 1 | Outage = Dederang to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDWOVD_R | 2008-07-01 | 1 | Outage = Dederang to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDWOVE_R | 2008-07-01 | 1 | Outage = Dederang to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_DDWOVF_R | 2008-07-01 | 1 | Outage = Dederang to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPMBQA_R | 2008-07-01 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPMBQB_R | 2008-07-01 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPMBQC_R | 2008-07-01 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPMBQD_R | 2008-07-01 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPMBQE_R | 2008-07-01 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPMBQF_R | 2008-07-01 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPMBVA_R | 2008-07-01 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPMBVB_R | 2008-07-01 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPMBVC_R | 2008-07-01 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPMBVD_R | 2008-07-01 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPMBVE_R | 2008-07-01 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPMBVF_R | 2008-07-01 | 1 | Outage = Eildon to Mt Beauty 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPTTQA_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPTTQB_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPTTQC_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPTTQD_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPTTQE_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPTTQF_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPTTVA_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPTTVB_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPTTVC_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPTTVD_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPTTVE_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_EPTTVF_R | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HORCQA_R | 2008-07-01 | 1 | Outage = Horsham to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HORCQB_R | 2008-07-01 | 1 | Outage = Horsham to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HORCQC_R | 2008-07-01 | 1 | Outage = Horsham to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HORCQD_R | 2008-07-01 | 1 | Outage = Horsham to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HORCQE_R | 2008-07-01 | 1 | Outage = Horsham to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HORCQF_R | 2008-07-01 | 1 | Outage = Horsham to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HORCVA_R | 2008-07-01 | 1 | Outage = Horsham to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HORCVB_R | 2008-07-01 | 1 | Outage = Horsham to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HORCVC_R | 2008-07-01 | 1 | Outage = Horsham to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HORCVD_R | 2008-07-01 | 1 | Outage = Horsham to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HORCVE_R | 2008-07-01 | 1 | Outage = Horsham to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HORCVF_R | 2008-07-01 | 1 | Outage = Horsham to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HWSMQA_R | 2008-07-01 | 1 | Outage = Hazelwood to South Morang 500 kV line, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_HWSMQB_R | 2008-07-01 | 1 | Outage = Hazelwood to South Morang 500 kV line, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_HWSMQC_R | 2008-07-01 | 1 | Outage = Hazelwood to South Morang 500 kV line, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_HWSMQD_R | 2008-07-01 | 1 | Outage = Hazelwood to South Morang 500 kV line, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_HWSMQE_R | 2008-07-01 | 1 | Outage = Hazelwood to South Morang 500 kV line, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_HWSMQF_R | 2008-07-01 | 1 | Outage = Hazelwood to South Morang 500 kV line, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_HWSMVA_R | 2008-07-01 | 1 | Outage = Hazelwood to South Morang 500 kV line, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_HWSMVB_R | 2008-07-01 | 1 | Outage = Hazelwood to South Morang 500 kV line, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_HWSMVC_R | 2008-07-01 | 1 | Outage = Hazelwood to South Morang 500 kV line, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_HWSMVD_R | 2008-07-01 | 1 | Outage = Hazelwood to South Morang 500 kV line, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_HWSMVE_R | 2008-07-01 | 1 | Outage = Hazelwood to South Morang 500 kV line, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_HWSMVF_R | 2008-07-01 | 1 | Outage = Hazelwood to South Morang 500 kV line, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_HYMLQA_R | 2008-07-01 | 1 | Outage = Heywood to Moorabool 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYMLQB_R | 2008-07-01 | 1 | Outage = Heywood to Moorabool 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYMLQC_R | 2008-07-01 | 1 | Outage = Heywood to Moorabool 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYMLQD_R | 2008-07-01 | 1 | Outage = Heywood to Moorabool 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYMLQE_R | 2008-07-01 | 1 | Outage = Heywood to Moorabool 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYMLQF_R | 2008-07-01 | 1 | Outage = Heywood to Moorabool 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYMLVA_R | 2008-07-01 | 1 | Outage = Heywood to Moorabool 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYMLVB_R | 2008-07-01 | 1 | Outage = Heywood to Moorabool 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYMLVC_R | 2008-07-01 | 1 | Outage = Heywood to Moorabool 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYMLVD_R | 2008-07-01 | 1 | Outage = Heywood to Moorabool 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYMLVE_R | 2008-07-01 | 1 | Outage = Heywood to Moorabool 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYMLVF_R | 2008-07-01 | 1 | Outage = Heywood to Moorabool 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYSEA_P | 2008-07-01 | 1 | Vic, HY-SE Out,Trans Lim A,Eqn1-Eqn74.1,Parallel
V::N_HYSEA_R | 2008-07-01 | 1 | Vic, HY-SE Out,Trans Lim A,Eqn1-Eqn74.1,Radial
V::N_HYSEB_P | 2008-07-01 | 1 | Vic, HY-SE Out,Trans Lim B,Eqn1-Eqn74.1,Parallel
V::N_HYSEB_R | 2008-07-01 | 1 | Vic, HY-SE Out,Trans Lim B,Eqn1-Eqn74.1,Radial
V::N_HYSEC_P | 2008-07-01 | 1 | Vic, HY-SE Out,Trans Lim C,Eqn1-Eqn74.1,Parallel
V::N_HYSEC_R | 2008-07-01 | 1 | Vic, HY-SE Out,Trans Lim C,Eqn1-Eqn74.1,Radial
V::N_HYSEQA_R | 2008-07-01 | 1 | Outage = Heywood to South East 275kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYSEQB_R | 2008-07-01 | 1 | Outage = Heywood to South East 275kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYSEQC_R | 2008-07-01 | 1 | Outage = Heywood to South East 275kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYSEQD_R | 2008-07-01 | 1 | Outage = Heywood to South East 275kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYSEQE_R | 2008-07-01 | 1 | Outage = Heywood to South East 275kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYSEQF_R | 2008-07-01 | 1 | Outage = Heywood to South East 275kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYSEVA_R | 2008-07-01 | 1 | Outage = Heywood to South East 275kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYSEVB_R | 2008-07-01 | 1 | Outage = Heywood to South East 275kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYSEVC_R | 2008-07-01 | 1 | Outage = Heywood to South East 275kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYSEVD_R | 2008-07-01 | 1 | Outage = Heywood to South East 275kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYSEVE_R | 2008-07-01 | 1 | Outage = Heywood to South East 275kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_HYSEVF_R | 2008-07-01 | 1 | Outage = Heywood to South East 275kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWGQA_R | 2008-07-01 | 1 | Outage = Jindera to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWGQB_R | 2008-07-01 | 1 | Outage = Jindera to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWGQC_R | 2008-07-01 | 1 | Outage = Jindera to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWGQD_R | 2008-07-01 | 1 | Outage = Jindera to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWGQE_R | 2008-07-01 | 1 | Outage = Jindera to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWGQF_R | 2008-07-01 | 1 | Outage = Jindera to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWGVA_R | 2008-07-01 | 1 | Outage = Jindera to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWGVB_R | 2008-07-01 | 1 | Outage = Jindera to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWGVC_R | 2008-07-01 | 1 | Outage = Jindera to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWGVD_R | 2008-07-01 | 1 | Outage = Jindera to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWGVE_R | 2008-07-01 | 1 | Outage = Jindera to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWGVF_R | 2008-07-01 | 1 | Outage = Jindera to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWOQA_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWOQB_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWOQC_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWOQD_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWOQE_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWOQF_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWOVA_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWOVB_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWOVC_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWOVD_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWOVE_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_JNWOVF_R | 2008-07-01 | 1 | Outage = Jindera to Wodonga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTMSQA_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTMSQB_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTMSQC_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTMSQD_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTMSQE_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTMSQF_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTMSVA_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTMSVB_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTMSVC_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTMSVD_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTMSVE_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTMSVF_R | 2008-07-01 | 1 | Outage = Lower Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTWGQA_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTWGQB_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTWGQC_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTWGQD_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTWGQE_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTWGQF_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTWGVA_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTWGVB_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTWGVC_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTWGVD_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTWGVE_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_LTWGVF_R | 2008-07-01 | 1 | Outage = Lower Tumut to Wagga 330kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MLTXQA_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MLTXQB_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MLTXQC_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MLTXQD_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MLTXQE_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MLTXQF_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MLTXVA_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MLTXVB_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MLTXVC_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MLTXVD_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MLTXVE_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MLTXVF_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MSUTQA_R | 2008-07-01 | 1 | Outage = Upper Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MSUTQB_R | 2008-07-01 | 1 | Outage = Upper Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MSUTQC_R | 2008-07-01 | 1 | Outage = Upper Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MSUTQD_R | 2008-07-01 | 1 | Outage = Upper Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MSUTQE_R | 2008-07-01 | 1 | Outage = Upper Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MSUTQF_R | 2008-07-01 | 1 | Outage = Upper Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MSUTVA_R | 2008-07-01 | 1 | Outage = Upper Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MSUTVB_R | 2008-07-01 | 1 | Outage = Upper Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MSUTVC_R | 2008-07-01 | 1 | Outage = Upper Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MSUTVD_R | 2008-07-01 | 1 | Outage = Upper Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MSUTVE_R | 2008-07-01 | 1 | Outage = Upper Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_MSUTVF_R | 2008-07-01 | 1 | Outage = Upper Tumut to Murray 330kV line, limit Vic generators and interconnectors avoid avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NIL-OFFSET_QA_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NIL-OFFSET_QB_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NIL-OFFSET_QC_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NIL-OFFSET_QD_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NIL-OFFSET_QE_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NIL-OFFSET_QF_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NIL-OFFSET_VA_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NIL-OFFSET_VB_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NIL-OFFSET_VC_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NIL-OFFSET_VD_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NIL-OFFSET_VE_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NIL-OFFSET_VF_R | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_NILQA_BL_R | 2008-09-17 | 1 | Outage = Nil, Basslink import from Tas, limit Vic interconnectors, Qld to NSW on QNI and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_NILQB_BL_R | 2008-09-17 | 1 | Outage = Nil, Basslink import from Tas, limit Vic interconnectors, Qld to NSW on QNI and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_NILQC_BL_R | 2008-09-17 | 1 | Outage = Nil, Basslink import from Tas, limit Vic interconnectors, Qld to NSW on QNI and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_NILQD_BL_R | 2008-09-17 | 1 | Outage = Nil, Basslink export to Tas, limit Vic interconnectors, Qld to NSW on QNI and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_NILQE_BL_R | 2008-09-17 | 1 | Outage = Nil, Basslink export to Tas, limit Vic interconnectors, Qld to NSW on QNI and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_NILQF_BL_R | 2008-09-17 | 1 | Outage = Nil, Basslink export to Tas, limit Vic interconnectors, Qld to NSW on QNI and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_NILVA_BL_R | 2008-07-02 | 1 | Outage = Nil, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_NILVB_BL_R | 2008-07-02 | 1 | Outage = Nil, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_NILVC_BL_R | 2008-07-02 | 1 | Outage = Nil, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_NILVD_BL_R | 2008-09-17 | 1 | Outage = Nil, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_NILVE_BL_R | 2008-09-17 | 1 | Outage = Nil, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_NILVF_BL_R | 2008-09-17 | 1 | Outage = Nil, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode at Hazelwood
V::N_NIL_SH | 2008-07-01 | 1 | Vic-Snowy Trans Lim Nil EGR Cap Sn>1001
V::N_NIL_SL | 2008-07-01 | 1 | Vic-Snowy Trans Lim Nil EGR Cap Sn<1000
V::N_ROSMQA_P | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Parallel
V::N_ROSMQA_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_ROSMQA_SMBYPS_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500 kV line, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode
V::N_ROSMQB_P | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Parallel
V::N_ROSMQB_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_ROSMQB_SMBYPS_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500 kV line, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode
V::N_ROSMQC_P | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Parallel
V::N_ROSMQC_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_ROSMQC_SMBYPS_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500 kV line, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode
V::N_ROSMQD_P | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Parallel
V::N_ROSMQD_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_ROSMQD_SMBYPS_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500 kV line, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode
V::N_ROSMQE_P | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Parallel
V::N_ROSMQE_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_ROSMQE_SMBYPS_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500 kV line, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode
V::N_ROSMQF_P | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Parallel
V::N_ROSMQF_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_ROSMQF_SMBYPS_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500 kV line, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode
V::N_ROSMVA_P | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Parallel
V::N_ROSMVA_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_ROSMVA_SMBYPS_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500 kV line, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode
V::N_ROSMVB_P | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Parallel
V::N_ROSMVB_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_ROSMVB_SMBYPS_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500 kV line, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode
V::N_ROSMVC_P | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Parallel
V::N_ROSMVC_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_ROSMVC_SMBYPS_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500 kV line, Basslink import from Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode
V::N_ROSMVD_P | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Parallel
V::N_ROSMVD_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_ROSMVD_SMBYPS_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500 kV line, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode
V::N_ROSMVE_P | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Parallel
V::N_ROSMVE_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_ROSMVE_SMBYPS_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500 kV line, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode
V::N_ROSMVF_P | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Parallel
V::N_ROSMVF_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500kV line, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_ROSMVF_SMBYPS_R | 2008-07-01 | 1 | Outage = Rowville to South Morang 500 kV line, Basslink export to Tas, limit Vic interconnectors and Vic generation to avoid transient instability for fault and trip of a Hazelwood to Sth Morang 500kV line, radial mode
V::N_SM330_2B | 2008-07-01 | 1 | Vic-NSW Trans Lim SM 330kV No 2 Bus Out, Eqn 3.1q - 75MW
V::N_SMCSQA_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Radial
V::N_SMCSQB_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Radial
V::N_SMCSQC_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Radial
V::N_SMCSQD_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Radial
V::N_SMCSQE_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Radial
V::N_SMCSQF_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Radial
V::N_SMCSVA_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Radial
V::N_SMCSVB_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Radial
V::N_SMCSVC_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Radial
V::N_SMCSVD_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Radial
V::N_SMCSVE_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Radial
V::N_SMCSVF_R | 2008-07-01 | 1 | Outage = South Morang 330kV series capacitor, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV, Radial
V::N_SMF2QA_R | 2008-07-01 | 1 | Out = South Morang F2 500/330 kV transformer, limit Vic interconnectors, NSW to Qld on QNI and Vic generation to avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, first linear segment, Radial
V::N_SMF2QB_R | 2008-07-01 | 1 | Out = South Morang F2 500/330 kV transformer, limit Vic interconnectors, NSW to Qld on QNI and Vic generation to avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, second linear segment, Radial
V::N_SMF2QC_R | 2008-07-01 | 1 | Out = South Morang F2 500/330 kV transformer, limit Vic interconnectors, NSW to Qld on QNI and Vic generation to avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, third linear segment, Radial
V::N_SMF2VA_R | 2008-07-01 | 1 | Outage=South Morang 500/330 kV F2 transformer, limit Vic interconnectors and generators, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, first linear segment, Radial
V::N_SMF2VB_R | 2008-07-01 | 1 | Outage=South Morang 500/330 kV F2 transformer, limit Vic interconnectors and generators, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, second linear segment, Radial
V::N_SMF2VC_R | 2008-07-01 | 1 | Outage=South Morang 500/330 kV F2 transformer, limit Vic interconnectors and generators, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, third linear segment, Radial
V::N_X_DDMB | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic to Snowy and Vic to SA on Murraylink to avoid transient instability for fault and trip of a Dederang to South Morang 330kV line, equation 52.2 from TLM-D
V::N_X_DDMBQA_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_DDMBQB_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_DDMBQC_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_DDMBQD_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_DDMBQE_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_DDMBQF_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_DDMBVA_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_DDMBVB_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_DDMBVC_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_DDMBVD_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_DDMBVE_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_DDMBVF_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_DDTX | 2008-07-01 | 1 | Out=All DD Tx's, Tstab lim, Eq 52.2 - 10, VE-52, SMTS-DDTS fault
V::N_X_DTXA_P | 2008-07-01 | 1 | Out=All DD Tx's, Tstab lim A, Eq 1-Eq 52.1, VE-52, Parallel Mode
V::N_X_DTXA_R | 2008-07-01 | 1 | Out=All DD Tx's, Tstab lim A, Eq 1 - Eq 52.1, VE-52, Radial Mode
V::N_X_DTXB_P | 2008-07-01 | 1 | Out=All DD Tx's, Tstab lim B, Eq 1-Eq 52.1, VE-52, Parallel Mode
V::N_X_DTXB_R | 2008-07-01 | 1 | Out=All DD Tx's, Tstab lim B, Eq 1 - Eq 52.1, VE-52, Radial Mode
V::N_X_DTXC_P | 2008-07-01 | 1 | Out=All DD Tx's, Tstab lim C, Eq 1-Eq 52.1, VE-52, Parallel Mode
V::N_X_DTXC_R | 2008-07-01 | 1 | Out=All DD Tx's, Tstab lim C, Eq 1 - Eq 52.1, VE-52, Radial Mode
V::N_X_EPMBQA_R | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_EPMBQB_R | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_EPMBQC_R | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_EPMBQD_R | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_EPMBQE_R | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_EPMBQF_R | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_EPMBVA_R | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_EPMBVB_R | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_EPMBVC_R | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_EPMBVD_R | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_EPMBVE_R | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_EPMBVF_R | 2008-07-01 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Vic generators and interconnectors to avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Radial
V::N_X_SM_HW-SY_QA_R | 2008-07-01 | 1 | Out = South Morang 500kV bus, one Hazelwood - South Morang 500kV line and one South Morang - Sydneham 500kV line, Basslink import from Tas, transient stability limit, Radial mode
V::N_X_SM_HW-SY_QB_R | 2008-07-01 | 1 | Out = South Morang 500kV bus, one Hazelwood - South Morang 500kV line and one South Morang - Sydneham 500kV line, Basslink import from Tas, transient stability limit, Radial mode
V::N_X_SM_HW-SY_QC_R | 2008-07-01 | 1 | Out = South Morang 500kV bus, one Hazelwood - South Morang 500kV line and one South Morang - Sydneham 500kV line, Basslink import from Tas, transient stability limit, Radial mode
V::N_X_SM_HW-SY_QD_R | 2008-07-01 | 1 | Out = South Morang 500kV bus, one Hazelwood - South Morang 500kV line and one South Morang - Sydneham 500kV line, Basslink export to Tas, transient stability limit, Radial mode
V::N_X_SM_HW-SY_QE_R | 2008-07-01 | 1 | Out = South Morang 500kV bus, one Hazelwood - South Morang 500kV line and one South Morang - Sydneham 500kV line, Basslink export to Tas, transient stability limit, Radial mode
V::N_X_SM_HW-SY_QF_R | 2008-07-01 | 1 | Out = South Morang 500kV bus, one Hazelwood - South Morang 500kV line and one South Morang - Sydneham 500kV line, Basslink export to Tas, transient stability limit, Radial mode
V::N_X_SM_HW-SY_VA_R | 2008-07-01 | 1 | Out = South Morang 500kV bus, one Hazelwood - South Morang 500kV line and one South Morang - Sydneham 500kV line, Basslink import from Tas, transient stability limit, Radial mode
V::N_X_SM_HW-SY_VB_R | 2008-07-01 | 1 | Out = South Morang 500kV bus, one Hazelwood - South Morang 500kV line and one South Morang - Sydneham 500kV line, Basslink import from Tas, transient stability limit, Radial mode
V::N_X_SM_HW-SY_VC_R | 2008-07-01 | 1 | Out = South Morang 500kV bus, one Hazelwood - South Morang 500kV line and one South Morang - Sydneham 500kV line, Basslink import from Tas, transient stability limit, Radial mode
V::N_X_SM_HW-SY_VD_R | 2008-07-01 | 1 | Out = South Morang 500kV bus, one Hazelwood - South Morang 500kV line and one South Morang - Sydneham 500kV line, Basslink export to Tas, transient stability limit, Radial mode
V::N_X_SM_HW-SY_VE_R | 2008-07-01 | 1 | Out = South Morang 500kV bus, one Hazelwood - South Morang 500kV line and one South Morang - Sydneham 500kV line, Basslink export to Tas, transient stability limit, Radial mode
V::N_X_SM_HW-SY_VF_R | 2008-07-01 | 1 | Out = South Morang 500kV bus, one Hazelwood - South Morang 500kV line and one South Morang - Sydneham 500kV line, Basslink export to Tas, transient stability limit, Radial mode
V::S-X_MTSE+SETX_NPS | 2007-12-28 | 1 | Out = Mt Gambier - South East line and one South East transformer; Vic to SA Stability limit for loss of one NPS generator following a 2ph to ground fault.
V::S_ACMA | 2008-02-13 | 1 | Out=AngasCk-Mannum 132kV line; Vic-SA Stability limit for NPS trip
V::S_CGMB_KHTB12MAMO | 2008-02-04 | 1 | Out=Cher.Gd North Bus+Keith-Tailem Bend 1&2+Mannum-Mobilong; Vic to SA Stability Limit on trip NPS.
V::S_CGMB_NPS | 2008-04-11 | 1 | Out=Cherry Gardens - Mt.Barker 132kV line; Vic to SA Stability Limit on trip NPS.
V::S_CGRB | 2007-10-11 | 1 | Out = One Cherry Gardens - Robertstown 275 kV line: Vic-SA Stability Limit. Critical Contingency: Trip one NPS generator.
V::S_CGTB_TUTB | 2008-09-26 | 1 | Out=Cherry Gardens -Tailem Bend 275kV line; trip the remaining Tungkillo - Tailem Bend line
V::S_DVRB | 2006-02-22 | 1 | Out=Davenport-Robertstown 275kV line: Vic-SA Stability Limit on NPS trip.
V::S_KHSG | 2008-06-03 | 1 | Out=Keith-Snuggery line; Victoria to South Australia import Voltage Stability limit on loss of one NPS unit.
V::S_KNPW | 2008-06-03 | 2 | Out= Kincraig - Penola West 132kV line; Vic to SA stability limit for loss of one NPS unit or one South East - Tailem Bend 275kV line
V::S_LEPP | 2006-02-22 | 1 | Out=LeFev-PelPt 275kV line: Vic-SA Stability Limit on NPS trip.
V::S_MAMO | 2008-05-09 | 1 | Vic-SA Stab LmtOut=Mannum-Mobilong 132kV trip on NPS
V::S_MBMO | 2008-06-06 | 2 | Out= Mt Barker - Mobilong 132 kV line (or any section of this line); Vic to SA stability limit for loss of one NPS unit.
V::S_MOTB | 2008-05-09 | 1 | Vic-SA Stab LmtOut=Mobilong-TailemBend 132kV trip on NPS
V::S_NIL | 2008-02-13 | 1 | Out = Nil; Vic to SA Stability limit for loss of one NPS generator due to a 2ph to ground fault close to the generator.
V::S_NPS_SINCON_TIMG | 2006-07-21 | 1 | Vic-SA Stability limit for Magill - Tips outage with NPS declared single credible contingency.
V::S_PAAC | 2008-08-05 | 1 | Out = Para to Angas Ck 132kV line, limit Vic to SA to avoid transient instability for one NPS unit trip
V::S_PATB_PATB | 2007-10-08 | 1 | Vic-SA Stab Lmt,Out=Para-TailB275kV, trip remaining Para-TailB
V::S_PATU | 2008-03-26 | 1 | Out = Para to Tungkillo 275 kV line; Vic to SA Stability limit for loss of one NPS generator due to a 2ph to ground fault close to the generator.
V::S_PA_VC | 2008-03-04 | 1 | Out= one Para SVC, Vic-SA transient stability limit for loss of a Northern unit
V::S_PWSE_NPS | 2007-08-10 | 1 | Out= Penola West - South East 132kV line, Vic-SA Voltage stability limit for loss of one NPS unit or one South East - Tailem Bend 275kV line
V::S_RBTU_NPS | 2008-04-11 | 1 | Out= Robertstown - Tungkillo 275kV line; Vic-SA Stability limit for NPS trip
V::S_SESGT_NPS | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; Vic to SA Stability limit for loss of one NPS generator following a 2ph to ground fault.
V::S_SETX_NPS | 2007-08-10 | 1 | Out= One South East 275/132kV transformer, Vic-SA Voltage stability limit for loss of one NPS unit or one South East - Tailem Bend 275kV line
V::S_SETX_SEVC_NPS | 2007-09-27 | 1 | Prior outage = one South East 275/32 kV transformer and one SVC; Vic-SA Stability Limit for loss of one NPS unit following 2PhG fault on the Davenport - NPS line.
V::S_SE_VC | 2007-12-19 | 1 | Out = one South East SVC; Vic-SA Stability Limit for loss of one NPS unit following 2PhG fault on the Davenport - NPS line.
V::S_TB_1TX | 2006-07-21 | 1 | Vic-SA Stab Lmt,Out=TailemBend 275/132kV Tx, trip on NPS
V::S_X_MBMO+PAAC | 2008-08-05 | 1 | Out= Mt Barker - Mobilong 132 kV line (or any section of this line); Vic to SA stability limit for loss of one NPS unit.
V::V_1900 | 2008-07-02 | 1 | Out=Nil, upper limit into Vic of 1900 MW
V::V_DDSM | 2008-07-01 | 1 | Outage = Dederang to South Morang 330kV line, limit VIC to NSW to avoid transient instability for fault and trip of a Dederang to South Morang 330kV line, equation 3.1q from TLM-Q
V::V_EPTT | 2008-07-01 | 2 | Outage = Eildon to Thomastown 220kV line, limit Vic to NSW and Vic to SA on Murraylink to avoid transient instability for fault and trip of a Dederang to South Morang 330kV line, equation 18.1 from TLM-D
V:N_MSUT_1 | 2008-07-01 | 1 | Outage = Murray to Upper Tumut OR Murray to Lower Tumut 330kV line, limit Vic to NSW to avoid transient instability for fault and trip of a Murray to Lower Tumut or Murray to Upper Tumut 330kV line, equation 9.1 from TLM-D
V:S_200 | 2008-09-08 | 1 | Out = Tailem Bend 275kV Ebus, Cherry Gdn -Tailem Bend line and Tailem Bend - Mobilong line. Vic-SA stability limit
V:S_380PPT | 2003-08-14 | 1 | V-SAtransf Lmt<=380MW, PPt<3units,2000WO applied,
V:S_HYBT | 2004-01-14 | 1 | Outage = Nil, limit Vic to SA to avoid transient instability for fault and trip of a Moorabool to Heywood 500 kV line with automatic allowance for Heywood bustie status based on Heywood 275 kV capacitor bank status
V:S_KHKN | 2005-06-27 | 1 | Vic-SA Stab LmtOut=Keith-Kincraig 132kV trip on TB-SE275kV lineor NPS
V:S_KHTB_1 | 2005-06-27 | 1 | Vic-SA Stab LmtOut=Keith-TailemBend#1 132kV trip on TB-SE275kV lineor NPS
V:S_KHTB_2 | 2005-06-27 | 1 | Vic-SA Stab LmtOut=Keith-TailemBend#2 132kV trip on NPS
V:S_LETI | 2005-06-27 | 1 | Vic-SA Stab LmtOut=Lefv-TIPS275kV trip on NPS
V:S_NPS_SINGL_CONT_1 | 2005-05-23 | 1 | V-SA transf Lmt<=360MW (175 for PASA), NPS<2units,2000WO applied,
V:S_NPS_SIN_CON_HYSE | 2005-05-10 | 1 | Stab limit; Out = Heywood - Sth Est line; trip both Northern PS units.
V:S_NPS_SIN_CON_SECP | 2005-05-09 | 2 | Out = 275KV cap bank 62 with loss of two Northern PS units as single credible contingency.
V:S_NPS_SIN_CON_SEVC | 2005-05-09 | 1 | Stab limit; Out = Sth Est SVC; trip both Northern PS units.
V:S_NPS_SIN_COT_1_HY | 2005-05-05 | 1 | V-SA transf Lmt<=130MW NPS<2units2000WO applied
V:S_PATB | 2007-01-23 | 1 | Vic-SA Stab Lmt,Out=Para-TailB275kV, trip remaining Para-TailB
V:S_PA_VC | 2005-03-21 | 1 | Out= one Para SVC, Vic-SA transient stability limit for loss of a Northern unit
V:S_PPT_1 | 2003-08-21 | 1 | Vic-SA Stab Lmt,SingleCredible Contingency=PelicanPt PS trip
V:S_SE_CP | 2003-04-15 | 1 | Vic-SA Stab Lmt,Out=Sth East 100MVAr capbank, trip on NPS
V:S_TB_CP | 2005-01-25 | 2 | Out= Tailem Bend 100MVAr Cap Bank, Vic-SA transient stability for trip of Northern PS
V:T_NIL_BL_1 | 2006-07-05 | 1 | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability
V>>N-BUDP_1N | 2008-07-01 | 2 | Out= Buronga-DarlingtonPt(X5), avoid Murray to LowerTumut (66) O/L (15/30_min rating) on Murray-UpperTumut(65) trip; Feedback
V>>N-BUDP_2N | 2008-07-01 | 2 | Out= Buronga-DarlingtonPt(X5), avoid Murray to UpperTumut (65) O/L (15/30_min rating) on Murray-LowerTumut(66) trip; Feedback
V>>N-BURC_1N | 2008-07-01 | 2 | Out= Buronga-RedCliffs(0X1), avoid Murray to Lower Tumut (66) O/L on Murray-UpperTumut(65)trip; Feedback
V>>N-BURC_2N | 2008-07-01 | 2 | Out= Buronga-RedCliffs(0X1), avoid Murray to UpperTumut (65) O/L on Murray-LowerTumut(66) trip; Feedback
V>>N-CNLT+LTUT_A_15M | 2008-07-01 | 1 | Out= Canberra-LowerTumut(07)+LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut (65) O/L (15m rating) on LowerTumut-Yass(3) trip; Feedback
V>>N-CNUT_HB_15M | 2008-07-01 | 1 | Out= Canberra-UpperTumut(01), avoid Murray to LowerTumut(66) O/L(15 min rating) on Murray-UpperTumut(65) trip; Feedback
V>>N-DDWO_A | 2008-07-01 | 2 | Out= Dederang-Wodonga, avoid Murray to UpperTumut (65) O/L (15/30_min rating) on Murray-LowerTumut(66) trip; Feedback
V>>N-DDWO_B | 2008-07-01 | 2 | Out= Dederang-Wodonga, avoid Murray to LowerTumut (66) O/L (15/30_min rating) on Murray-UpperTumut(65) trip; Feedback
V>>N-DPWG_A | 2008-07-01 | 1 | Out= DarlingtonPt-Wagga(63), avoid Murray to UpperTumut (65) O/L on Murray-LowerTumut(66) trip; Feedback
V>>N-DPWG_B | 2008-07-01 | 1 | Out= DarlingtonPt-Wagga(63), avoid Murray to LowerTumut (66) O/L on Murray-UpperTumut(65) trip; Feedback
V>>N-DPWG_J | 2008-07-01 | 1 | Out= DarlingtonPt-Wagga(63), avoid Murray to UpperTumut (65) O/L on Dederang-Wodonga(DDWO) trip; Feedback
V>>N-DPWG_K | 2008-07-01 | 1 | Out= DarlingtonPt-Wagga(63), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback
V>>N-JNWG+X5_A | 2008-07-01 | 2 | Out= Jindera-Wagga(62)+X5+996, avoid Murray to UpperTumut (65) O/L on Murray-LowerTumut(66) trip; Feedback
V>>N-JNWG+X5_B | 2008-07-01 | 2 | Out= Jindera-Wagga(62)+X5+996, avoid Murray to LowerTumut (66) O/L on Murray-UpperTumut(65) trip; Feedback
V>>N-JNWO_C | 2008-07-01 | 1 | Out= Jindera-Wodonga(060), avoid Murray to UpperTumut (65) O/L on Murray-LowerTumut(66) trip; Feedback
V>>N-JNWO_D | 2008-07-01 | 1 | Out= Jindera-Wodonga(060), avoid Murray to LowerTumut (66) O/L on Murray-UpperTumut(65) trip; Feedback
V>>N-LTMS_1 | 2008-07-01 | 1 | Out= LowerTumut-Murray(66), avoid Murray to UpperTumut (65) O/L on Nil trip; Feedback
V>>N-LTMS_1C | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(66), avoid Wodonga to Jindera (060) O/L on Murray-UpperTumut(65) trip; Feedback
V>>N-LTMS_3 | 2008-07-01 | 1 | Out= LowerTumut-Murray(66), avoid Murray to UpperTumut (65) O/L(15m rating) on LowerTumut-Canberra(07) trip; Feedback
V>>N-LTMS_4 | 2008-07-01 | 1 | Out= LowerTumut-Murray(66), avoid Murray to UpperTumut (65) O/L(15m rating) on Dederang-Wodonga(DDWO) trip; Feedback
V>>N-LTMS_A | 2008-07-01 | 1 | Out= LowerTumut-Murray(66), avoid Murray to UpperTumut (65) O/L(15m rating) on Jindera-Wodonga(060) trip; Feedback
V>>N-LTMS_AX | 2008-07-01 | 1 | Out= LowerTumut-Murray(66)+ LowerTumut-UpperTumut(64), avoid Murray to UpperTumut (65) O/L(15m rating) on Jindera-Wodonga(060) trip; Feedback
V>>N-LTUT_1_30 | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid Murray to UpperTumut (65) O/L (30_min rating) on Murray-LowerTumut(66) trip; Feedback
V>>N-LTUT_2_30 | 2008-07-01 | 1 | Out= LowerTumut-UpperTumut(64), avoid Murray to LowerTumut (66) O/L (30_min rating) on Murray-UpperTumut(65) trip; Feedback
V>>N-LTUT_A | 2009-01-15 | 1 | Out= LowerTumut-UpperTumut(64), avoid Murray to UpperTumut (65) O/L on Murray-LowerTumut(66) trip; Feedback
V>>N-LTUT_B | 2009-01-15 | 1 | Out= LowerTumut-UpperTumut(64), avoid Murray to LowerTumut (66) O/L on Murray-UpperTumut(65) trip; Feedback
V>>N-LTUT_G | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid Murray to UpperTumut (65) O/L on Nil trip; Feedback
V>>N-LTUT_H | 2008-07-01 | 2 | Out= LowerTumut-UpperTumut(64), avoid Murray to LowerTumut (66) O/L on Nil trip; Feedback
V>>N-LTUT_L_15M | 2009-01-15 | 2 | Out= LowerTumut-UpperTumut(64), avoid Murray to UpperTumut (65) O/L on LowerTumut to Yass(03) trip; Feedback
V>>N-LTUT_M_15M | 2009-01-15 | 2 | Out= LowerTumut-UpperTumut(64), avoid Murray to UpperTumut (65) O/L on LowerTumut to Canberra(07) trip; Feedback
V>>N-LTUT_N_15M | 2009-01-15 | 3 | Out= LowerTumut-UpperTumut(64), avoid Murray to LowerTumut (66) O/L on UpperTumut to Canberra(01) trip; Feedback
V>>N-LTYS+LTUT_B | 2008-07-01 | 1 | Out= LowerTumut-Yass(3)+LowerTumut-UpperTumut(64), avoid Murray to UpperTumut (65) O/L on LowerTumut-Canberra(07) trip; Feedback
V>>N-LTYS_BH | 2008-08-14 | 1 | Out= LowerTumut-Yass(3), avoid Murray to UpperTumut (65) O/L on LowerTumut-Canberra(07) trip; Feedback
V>>N-MSUT_1 | 2008-07-01 | 1 | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on LowerTumut-Wagga(051) trip; Feedback
V>>N-MSUT_2 | 2008-07-01 | 1 | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Nil trip; Feedback
V>>N-MSUT_4 | 2008-07-01 | 1 | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback
V>>N-NIL_1H | 2008-07-01 | 1 | Out= Nil, avoid Murray to Upper Tumut (65) O/L (30 minute rating) on Murray-LowerTumut(66) trip; Feedback
V>>N-NIL_2H | 2008-07-01 | 1 | Out= Nil, avoid Murray to Lower Tumut (66) O/L (30 minute rating) on Murray-UpperTumut(65) trip; Feedback
V>>N-NIL_HA | 2008-07-01 | 1 | Out= Nil, avoid Murray to Upper Tumut (65) O/L on Murray-LowerTumut(66) trip; Feedback
V>>N-NIL_HB | 2008-07-01 | 1 | Out= Nil, avoid Murray to Lower Tumut (66) O/L on Murray-UpperTumut(65) trip; Feedback
V>>N-NIL_HG | 2008-07-01 | 1 | Out= Nil, avoid Murray to Upper Tumut (65) O/L on NIL trip; Feedback
V>>N-NIL_HH | 2008-07-01 | 1 | Out= Nil, avoid Murray to Lower Tumut (66) O/L on NIL trip; Feedback
V>>N-UT_A2_B | 2008-07-01 | 1 | Out= Nil/At_risk, avoid Murray to LowerTumut (66) O/L(15_min rating) on trip of UpperTumut A2 Bus(=lines 2+64+65); Feedback
V>>N_67+OX1 | 2008-07-01 | 1 | Out=DD-MS(67)+BU-RC(OX1), avoid WO-JN(060) OL on DD-MS(68) trip
V>>N_67+X5 | 2008-07-01 | 1 | Out=DD-MS(67)+DP-BU(X5), avoid WO-JN(060) OL on DD-MS(68) trip
V>>N_DDMS | 2008-07-01 | 1 | Out= one Murray to Dederang, avoid O/L Wodonga to Jindera (060) on trip of Dederang to Murray, Feedback
V>>N_MSBT | 2008-07-01 | 1 | Out= MSS bus section CB; avoid 060 OL (W->J) on other BS CB trip
V>>N_SMTXF2 | 2009-01-07 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit Vic generators and interconnectors (Vic export) to avoid overload of South Morang H1 transformer for trip of the H2 transformer
V>>N_SMTXF2_2 | 2008-07-01 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit Vic to NSW transfer to avoid overloading Ballarat to Bendigo 220 kV line for loss of Ballarat to Horsham 220kV line with Murraylink fast runback to zero operating
V>>N_SMTXH1 | 2009-01-07 | 1 | Outage = South Morang 330/220kV (H1) transformer, limit Vic generators and interconnectors (Vic export) to avoid overload of South Morang H2 transformer for trip of the South Morang 500/330kV (F2) transformer
V>>N_SMTXH2 | 2009-01-07 | 1 | Outage = South Morang 330/220kV (H2) transformer, limit Vic generators and interconnectors (Vic export) to avoid overload of South Morang H1 transformer for trip of the South Morang 500/330kV (F2) transformer
V>>N_UTYS_BH_15M | 2008-07-01 | 1 | Out= UpperTumut-Yass(2), avoid Murray to LowerTumut(66) O/L (15 min rating) on UpperTumut-Canberra(01) trip; Feedback
V>>S-SETX_SETB_KHTB | 2007-06-27 | 1 | Prior Outage = South East one transformer; Prevent Keith - Tailem Bend #1 OL for South East - Tailem Bend trip. Fb CoOp.
V>>S-SETX_SETB_SETX | 2007-08-28 | 1 | Out = South East one transformer; Prevent remaining South East transformer OL for South East - Tailem Bend trip.
V>>S-SEVCC_SETB_KHTB | 2007-06-15 | 1 | Prior Outage = South East one SVC and CBs; Prevent Keith - Tailem Bend #1 OL for South East - Tailem Bend trip. Fb CoOp.
V>>S-SEVCC_SETB_MTBL | 2007-06-15 | 1 | Prior Outage = South East SVC with CBs. Prevent Mt Gambier - Blanche OL for South East - Tailem Bend trip. Fb CoOp.
V>>S-SEVC_SETB_SETX | 2007-06-15 | 1 | Prior Outage = South East SVC with bus tie CB; Prevent South East transformer#2 OL for South East - Tailem Bend or the remaining SVC trip. Fb CoOp.
V>>SML_BABE_2 | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Vic generators and interconnectors to avoid pre-contingent O/L Bendigo to Shepparton 220 kV line, Murraylink VFRB enabled for RCTS-Buronga line contingency and Murraylink > 25MW
V>>SML_BAHO_2 | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid pre-contingent O/L Bendigo to Shepparton 220 kV line, Murraylink VFRB enabled for RCTS-Buronga line contingency and Murraylink > 25MW
V>>SML_BAHO_3 | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid O/L Bendigo to Shepparton 220 kV line for trip of Redcliffs to Buronga 220kV line, swamped if Murraylink VFRB enabled for this contingency and Murraylink > 25MW
V>>SML_BAHO_4 | 2008-07-01 | 1 | Outage = Ballarat to Horsham 220kV line, limit Vic generators and interconnectors to avoid O/L Bendigo to Shepparton 220 kV line for trip of Moorabool 500/220kV transformer, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_BAML | 2008-07-01 | 1 | Out = Ballarat to Moorabool (No.1 or No.2) line, limit Vic generators and interconnectors to avoid overloading Moorabool to Terang line on loss of Ballarat to Moorabool (No.2 or No.1) line
V>>SML_BAML1 | 2008-07-01 | 1 | Out = Ballarat to Moorabool No.1 line, limit Vic generators and interconnectors to avoid O/L Ballarat to Moorabool No.2 line on loss of Moorabool to Terang line
V>>SML_BAML1_2 | 2008-07-01 | 1 | Outage = Ballarat to Moorabool No.1 220kV line, limit Vic generators and interconnectors to avoid pre-contingent O/L Bendigo to Shepparton 220 kV line, Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_BAML2 | 2008-07-01 | 1 | Out = Ballarat to Moorabool No.2 line, limit Vic generators and interconnectors to avoid O/L Ballarat to Moorabool No.1 line on loss of Moorabool to Terang line
V>>SML_BAML2_2 | 2008-07-01 | 1 | Outage = Ballarat to Moorabool No.2 220kV line, limit Vic generators and interconnectors to avoid pre-contingent O/L Bendigo to Shepparton 220 kV line, Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_BAML_3 | 2008-07-01 | 1 | Outage = Ballarat to Moorabool #1 or #2 220kV line, limit Vic generators and Murraylink to avoid O/L Bendigo to Shepparton 220 kV line for trip of Ballarat to Moorabool #1 or #2 220kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_BATG2 | 2008-07-01 | 1 | Outage = Ballarat to Terang 220kV line, limit Murraylink from Vic to SA to avoid overloading Ballarat to Moorabool No.2 220kV line for loss of Ballarat to Moorabool No.1 220kV line
V>>SML_BATG_1 | 2008-07-01 | 1 | Outage = Ballarat to Terang 220kV line, limit Murraylink from Vic to SA to avoid overloading Ballarat to Moorabool No.1 220kV line for loss of Ballarat to Moorabool No.2 220kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_BATG_2 | 2008-07-01 | 1 | Outage = Ballarat to Terang 220kV line, limit Vic generators and interconnectors to avoid pre-contingent O/L Bendigo to Shepparton 220 kV line, Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_BATG_3 | 2008-07-01 | 1 | Outage = Ballarat to Terang 220kV line, limit Vic generators and interconnectors avoid O/L Bendigo to Shepparton 220 kV line for trip of Moorabool 500/220kV transformer, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_BUDP_2 | 2008-07-01 | 2 | Outage = Buronga to Darlington Pt 220kV line, limit Vic generators and interconnectors to avoid pre-contingent O/L Bendigo to Shepparton 220 kV line, Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_BUDP_3 | 2008-07-01 | 2 | Outage = Buronga to Darlington Pt 220kV line, limit Vic generators and interconnectors avoid O/L Bendigo to Shepparton 220 kV line for trip of Moorabool 500/220kV transformer, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_BURC_2 | 2008-07-01 | 2 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors to avoid pre-contingent O/L Bendigo to Shepparton 220 kV line, Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_BURC_3 | 2008-07-01 | 2 | Outage = Buronga to Redcliffs 220kV line, limit Vic generators and interconnectors avoid O/L Bendigo to Shepparton 220 kV line for trip of Moorabool 500/220kV transformer, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_DDGN | 2008-07-01 | 1 | Outage = Dederang to Glenrowan No.1 or No.3 220kV line, limit Vic generators and interconnectors to avoid overloading Dederang to Shepparton 220kV line on loss of Dederang to Glenrowan No.3 or No.1 220kV line
V>>SML_DDSH_1 | 2008-07-01 | 1 | Out = Dederang to Shepparton 220kV line, limit Vic generators and interconnectors to avoid O/L Dederang to Glenrowan No.1 line on loss of Dederang to Glenrowan No.3 line
V>>SML_DDSH_2 | 2008-07-01 | 1 | Out = Dederang to Shepparton 220kV line, limit Vic generators and interconnectors to avoid O/L Dederang to Glenrowan No.3 line on loss of Dederang to Glenrowan No.1 line
V>>SML_GNSH | 2008-07-01 | 1 | Outage = Glenrowan to Shepparton No.1 or No.3 220kV line, limit Vic generators and interconnectors to avoid overloading Dederang to Shepparton 220kV line on loss of Glenrowan to Shepparton No.3 or No.1 220kV line
V>>SML_MLTG2 | 2008-07-01 | 1 | Out = Moorabool to Terang line, avoid O/L Ballarat to Moorabool No.2 line on loss of Ballarat to Moorabool No.1
V>>SML_MLTG_1 | 2008-07-01 | 1 | Out = Moorabool to Terang or Ballarat to Moorabool No.2 line, avoid O/L Ballarat to Moorabool No.1 line on loss of Ballarat to Moorabool No.2 or Moorabool to Terang line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_MLTG_2 | 2008-07-01 | 1 | Outage = Moorabool to Terang 220kV line, limit Vic generators and interconnectors to avoid pre-contingent O/L Bendigo to Shepparton 220 kV line, Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_MLTG_3 | 2008-07-01 | 1 | Outage = Moorabool to Terang 220kV line, limit Vic generators and interconnectors avoid O/L Bendigo to Shepparton 220 kV line for trip of Moorabool 500/220kV transformer, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_NIL_1 | 2008-07-02 | 1 | Outage = Nil, limit Vic generators and interconnectors to avoid overloading Ballarat to Moorabool No.1 220 kV line for loss of Ballarat to Moorabool No.2 220 kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_NIL_2 | 2008-07-02 | 1 | Outage = Nil, limit Vic generators and interconnectors to avoid pre-contingent overloading of the Bendigo to Fosterville to Shepparton 220 kV line, Murraylink VFRB enabled for RCTS-Buronga line contingency and Murraylink > 25MW
V>>SML_NIL_3 | 2008-07-02 | 1 | Outage = Nil, limit Vic generators and interconnectors to avoid overloading the Bendigo to Fosterville to Shepparton 220 kV line for trip of Redcliffs to Buronga 220kV line, swamped if Murraylink VFRB enabled for this contingency and Murraylink > 25MW
V>>SML_NIL_4 | 2008-07-02 | 1 | Outage = Nil, limit Vic generators and interconnectors to avoid overloading Ballarat to Moorabool No.2 220 kV line for loss of Ballarat to Moorabool No.1 220 kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_NIL_6 | 2008-07-02 | 1 | Outage = Nil, limit Vic generators and interconnectors to avoid overloading the Bendigo to Fosterville to Shepparton 220 kV line for trip of Moorabool 500/220kV transformer, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_NIL_7A | 2008-07-03 | 1 | Outage = Nil, limit Vic to SA on Murraylink to avoid overload on the Ballarat North to Buangor 66kV line for loss of the Ballarat to Horsham 220kV line
V>>SML_NIL_7B | 2008-07-03 | 1 | Outage = Nil, limit Vic to SA on Murraylink to avoid overload on the Buangor to Arrarat 66kV line for loss of the Ballarat to Horsham 220kV line
V>>SML_NIL_7C | 2008-07-03 | 1 | Outage = Nil, limit Vic to SA on Murraylink to avoid overload on the Arrarat to Stawell 66kV line for loss of the Ballarat to Horsham 220kV line
V>>SML_SMTXF2_1 | 2008-07-01 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit Vic generation and interconnectors to avoid O/L Ballarat to Bendigo 220 kV line for loss of a South Morang 330kV line
V>>SML_SMTXF2_2 | 2008-07-01 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit Vic generation and interconnectors to avoid O/L Ballarat to Moorabool No.1 220 kV line for loss of Ballarat to Moorabool No.2 220 kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_SMTXF2_3 | 2008-07-01 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit Vic generation and interconnectors to avoid O/L Ballarat to Moorabool No.2 220 kV line for loss of Ballarat to Moorabool No.1 220 kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_SMTXF2_5A | 2008-07-01 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit Vic generation and interconnectors to avoid overload on Geelong to Keilor No.1 220kV line for loss of the Moorabool 500/220kV transformer, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_SMTXF2_5B | 2008-07-01 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit Vic generation and interconnectors to avoid overload on Geelong to Keilor No.2 220kV line for loss of the Moorabool 500/220kV transformer, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_SMTXF2_5C | 2008-07-01 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit Vic generation and interconnectors to avoid overload on Geelong to Keilor No.3 220kV line for loss of the Moorabool 500/220kV transformer, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_VFRB_7A-PD | 2008-07-08 | 1 | Outage = Murraylink VFRB scheme, limit Vic to SA on Murraylink to avoid overload on the Ballarat North to Buangor 66kV line for loss of the Ballarat to Horsham 220kV line, BATS-HOTS 66kV tie closed, pre-dispatch only
V>>SML_VFRB_7B-PD | 2008-07-08 | 1 | Outage = Murraylink VFRB scheme, limit Vic to SA on Murraylink to avoid overload on the Buangor to Arrarat 66kV line for loss of the Ballarat to Horsham 220kV line, BATS-HOTS 66kV tie closed, pre-dispatch only
V>>SML_VFRB_7C-PD | 2008-07-08 | 1 | Outage = Murraylink VFRB scheme, limit Vic to SA on Murraylink to avoid overload on the Arrarat to Stawell 66kV line for loss of the Ballarat to Horsham 220kV line, BATS-HOTS 66kV tie closed, pre-dispatch only
V>>S_6106_SGBL_SGTX4 | 2008-08-13 | 1 | Out= Snuggery CB6106, avoid O/L Snuggery T4 on trip of Snuggery - Blanche line.
V>>S_BGDV_CNRB_BRPA | 2007-12-19 | 1 | Out = Bungama - Davenport line; Limit Murraylink and SA generation to avoid OL Brinkworth to Para 275 kV line for trip Canowi - Robertstown line.
V>>S_BGDV_CNRB_DVBR | 2007-12-19 | 1 | Out = Bungama - Davenport line; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line for trip Canowi - Robertstown line.
V>>S_BGDV_DVMK_BRPA | 2009-01-21 | 1 | Out = Davenport to Bungama line; Limit Murraylink and SA generation to avoid OL Brinkworth to Para 275 kV line for trip Davenport - Mokota - Robtstown line.
V>>S_BGDV_DVMK_DVBR | 2009-01-21 | 1 | Out = Davenport to Bungama line; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line for trip Davenport - Mokota - Robtstown line .
V>>S_BGDV_NIL_BRPA | 2007-12-19 | 1 | Out = Davenport to Bungama line; Limit Murraylink and SA generation to maintain Brinkworth to Para 275 kV line flow below the continuous rating after Davenport - Robertstown line trip.
V>>S_BGDV_NIL_DVBR | 2007-12-19 | 1 | Out = Davenport to Bungama line; Limit Murraylink and SA generation to maintain Davenport to Brinkworth 275 kV line flow below the continuous rating after Davenport - Robertstown line trip.
V>>S_BGPA_DVBG_DVBR | 2007-12-19 | 1 | Out = Bungama - Para line; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line for trip Davenport - Bungama line.
V>>S_BGPA_DVMK_BRPA | 2009-01-21 | 1 | Out = Bungama - Para line; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line for trip Davenport - Mokota - Robtstown 275kV line.
V>>S_CGRB_NIL_DVBR | 2007-12-19 | 1 | Out = Cherry Gardens - Robertstown line; maintain Davenport to Brinkworth line flow below the continuous rating.
V>>S_CGRB_RBCG_DVBR | 2007-12-19 | 1 | Out = Cherry Gardens - Robertstown line; maintain Davenport to Brinkworth line post contingency flow below the 15 minutes rating followng loss of the other Cherry Gardens to Robertstown line.
V>>S_CGTB_TBTU_TBMO | 2007-11-27 | 2 | Prior Outage = Cherry Gardens - Tailem Bend 275 kV line; Limit to avoid O/L Tailem Bend - Mobilong 132kV line on trip Tailem Bend - Tungkillo line.
V>>S_CNDV_DVBG_BRPA | 2007-12-19 | 1 | Out = Davenport - Canowi line; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line on trip Davenport to Bungama line.
V>>S_CNDV_DVBG_DVBR | 2007-12-19 | 1 | Out = Davenport - Canowi line; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line on trip Davenport to Bungama line.
V>>S_CNDV_NIL_BRPA | 2007-12-19 | 1 | Out = Davenport - Canowi line; Limit Murraylink and SA generation to maintain Brinkworth-Para 275 kV line flow below the continuous rating following trip Davenport to Bungama line.
V>>S_CNDV_NIL_DVBR | 2007-12-19 | 1 | Out = Davenport - Canowi line; Limit Murraylink and SA generation to maintain Davenport to Brinkworth 275 kV line flow below the continuous rating following trip Davenport to Bungama line.
V>>S_CNRB_BGPA_BRPA | 2007-12-19 | 1 | Out = Canowi - Robertstown line; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line for trip Bungama to Para 275kV line.
V>>S_CNRB_DVBG_DVBR | 2007-12-19 | 1 | Out = Canowi - Robertstown line; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line on trip Davenport to Bungama line.
V>>S_DVRB_BGPA_BRPA | 2007-12-19 | 1 | Out = Davenport - Robertstown line; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line for trip Bungama to Para 275kV line.
V>>S_DVRB_DVBG_DVBR | 2008-10-28 | 1 | Out = Davenport - Robertstown line; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line for trip Davenport - bungama line.
V>>S_KHKN_NIL_SGKH | 2008-01-25 | 1 | Out = Keith - Kincraig 132 kV line; avoid Snuggery - Keith line (continuous rating) OL on nil trip.
V>>S_KHKN_SETB_SGKH | 2008-01-25 | 1 | Out = Keith - Kincraig 132 kV line; avoid Snuggery - Keith line OL on trip of South East - Tailem Bend 275 kV line
V>>S_KHSG_SETB_PWKN | 2007-12-19 | 1 | Prior Outage = Snuggery-Keith line; Limit Interconnectors and generation to avoid O/L Penola West to Kincraig line for trip one South East - Tailem Bend line.
V>>S_KHTB1_SETB_KHTB | 2007-06-08 | 1 | Out = Keith - Tailem Bend #1 132 kV line. Prevent Keith - Tailem Bend #2 line OL for South East - Tailem Bend line trip.
V>>S_KHTB2_SETB_KHTB | 2007-06-08 | 1 | Out = Keith - Tailem Bend #2 132 kV line. Prevent Keith - Tailem Bend #1 line OL on trip one of the South East - Tailem Bend lines.
V>>S_KH_X_SETB_SETB | 2007-07-10 | 1 | Out = Keith - Tailem Bend lines 1 and 2; limit Vic to SA, Ladbroke Grove gen and Snuggery gen to avoid South East - Tailem Bend 275 kV line OL on trip the other South East - Tailem Bend 275 kV line.
V>>S_KNPW_NIL_SGKH | 2008-01-30 | 1 | Out = Kincraig - Penola West 132 kV line; avoid Snuggery - Keith line (continuous rating) OL on nil trip.
V>>S_KNPW_SETB_SGKH | 2008-01-30 | 1 | Out = Kincraig - Penola West 132 kV line; avoid Snuggery - Keith line OL on trip of South East - Tailem Bend 275 kV line
V>>S_MGPA_CGTI_TIMG | 2007-12-19 | 1 | Out = Magill - Para 275 kV line; Limit Torrens Island generation to avoid Torrens Island to Magill line OL on Torrens Island - Cherry Gardens line trip. FbCoOp
V>>S_MGPA_MGTI_TICG | 2007-12-19 | 1 | Out = Magill - Para 275 kV line; Limit Torrens Island generation to avoid Torrens Island to Cherry Garden line OL on Torrens Island - Magill line trip. FbCoOp
V>>S_MOTB | 2008-08-05 | 1 | Out=Mobilong-Tailem Bend 132 kV line; limit to avoid Tailem Bend - Tungkillo 275kV line O/L on trip Talem Bend - Cherry Gardens 275kV line.
V>>S_NIL_BGPA_BRPA | 2007-12-19 | 1 | Out = Nil; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line for trip Bungama to Para 275kV line.
V>>S_NIL_DVBG_BRPA | 2008-07-08 | 1 | Out = Nil; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line for trip Davenport to Bungama line.
V>>S_NIL_DVBG_DVBR | 2008-07-08 | 1 | Out = Nil; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line for trip Davenport to Bungama line.
V>>S_NIL_KHTB1_KHTB2 | 2008-05-08 | 1 | Out = Nil. Prevent Keith - Tailem Bend #2 line OL for Keith - Tailem Bend #1 line trip.
V>>S_NIL_KHTB2_KHTB1 | 2009-01-14 | 1 | Out = Nil. Prevent Keith - Tailem Bend #1 line OL for Keith - Tailem Bend #2 line trip.
V>>S_NIL_NIL_BRPA | 2008-07-08 | 1 | Out = Nil; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line above the continuous rating following Davenport to Bungama line trip.
V>>S_NIL_NIL_DVBR | 2008-07-08 | 1 | Out = Nil; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line above the continuous rating for trip Davenport to Bungama line.
V>>S_NIL_NIL_DVBR_P | 2008-07-08 | 1 | Out = Nil; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line above the continuous rating for trip Davenport to Bungama line.
V>>S_NIL_NIL_SGKHC | 2008-02-19 | 1 | Out= Nil, avoid O/L Snugg to Keith 132 kV line above the continuous rating on trip of Nil, Feedback
V>>S_NIL_NPS_MAMA2 | 2008-06-04 | 1 | Out = Nil; Mannum to Mannum pump 2 line OL for one Northern PS trip. Fb CoOp.
V>>S_NIL_PWKN_SGKH | 2007-12-14 | 1 | Out= Nil, avoid O/L Snuggery - Keith 132 kV line on trip of Penola West - Kincraig line, Feedback
V>>S_NIL_SETB_KHTB | 2008-06-04 | 1 | Out = Nil; Prevent Keith - Tailem Bend #1 line OL for South East - Tailem Bend trip.
V>>S_NIL_SETB_PWKN | 2008-06-04 | 1 | Out = Nil; Prevent Penola West - Kincraig OL for South East - Tailem Bend trip. Fb CoOp.
V>>S_NIL_SETB_SGKH | 2007-12-14 | 1 | Out= Nil, avoid O/L Snuggery - Keith 132 kV line on trip of South East - Tailem Bend one 275kV line, Feedback
V>>S_NIL_SGBL_SGKH | 2007-12-14 | 1 | Out= Nil, avoid O/L Snuggery Keith 132 kV line on trip of Snuggery - Blanche line
V>>S_PTIMG_PAPG_MOTB | 2007-07-10 | 1 | Prior Outage = Para-Torrens Island and Para-Magill lines & Para West B2. Prevent TB-Mobilong OL for Para-Parafield trip. Fb CoOp.
V>>S_PWSE_NIL_SGKH | 2008-10-10 | 1 | Out = Penola West - South East 132 kV line; avoid Snuggery - Keith line (continuous rating) OL on nil trip.
V>>S_PWSE_SETB_SGKH | 2008-10-10 | 1 | Out = Penola West - South East 132 kV line; avoid Snuggery - Keith line OL on trip of South East - Tailem Bend 275 kV line
V>>S_RBPA_RBTU_BRPA | 2009-01-19 | 1 | Out= Robertstown - Para 275 kV line, avoid O/L Brinkworth to Para 275kV line on trip of Robertstown to Tungkillo 275kV line
V>>S_RBTU_N-2_BRPA | 2009-01-20 | 1 | Out= Nil; avoid O/L Brinkworth to Para 275kV line on trip of Robertstown - Para and Robertstown - Tungkillo 275kV lines
V>>S_RBTU_RBPA_BRPA | 2009-01-19 | 1 | Out= Robertstown - Tungkillo 275 kV line, avoid O/L Brinkworth to Para 275kV line on trip of Robertstown to Para 275kV line
V>>S_SESGT_KHSN | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; South East generation & Vic-SA limit to avoid Snuggery - Keith line OL (continuous rating). System normal.
V>>S_SESGT_PWKN_SGKH | 2007-12-19 | 1 | Out = South East - Snuggery T 132kV line; Prevent Snuggery - Keith 132 kV line OL for Penola West - Kincraig line trip.
V>>S_SESGT_SETB_BLSG | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; Prevent Blanche - Snuggery OL for South East - Tailem Bend trip. Fb CoOp.
V>>S_SESGT_SETB_KHTB | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; Prevent Keith - Tailem Bend #1 line OL for South East - Tailem Bend trip. Fb CoOp.
V>>S_SESGT_SETB_MGBL | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line;. Prevent Mt Gambier - Blanche OL for South East - Tailem Bend trip. Fb CoOp.
V>>S_SESGT_SETB_PWKN | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; Prevent Penola West - Kincraig OL for South East - Tailem Bend trip. Fb CoOp.
V>>S_SETB_N-2_KHTB1 | 2007-06-27 | 1 | Prior outage= Nil; avoid O/L Keith to Tailem Bend #1 132kV line on trip of both South East to Tailem Bend 275 kV lines.
V>>S_SETB_N-2_KHTB2 | 2007-06-27 | 1 | Prior outage= Nil; avoid O/L Keith to Tailem Bend #2 132kV line on trip of both South East to Tailem Bend 275 kV lines.
V>>S_SETB_N-2_PWKN | 2007-06-27 | 1 | Prior outage= Nil; avoid O/L Penola West to Kincraig line on trip of both South East to Tailem Bend 275 kV lines.
V>>S_SETB_N-2_SGKH | 2007-06-27 | 1 | Prior outage= Nil; avoid O/L Snuggery to Keith line on trip of both South East to Tailem Bend 275 kV lines.
V>>S_SETB_SETB_KHTB1 | 2007-06-27 | 2 | Out= one South East to Tailem Bend 275kV line, avoid O/L Keith to Tailem Bend #1 132kV line on trip of the remaining South East to Tailem Bend line.
V>>S_SETB_SETB_KHTB2 | 2007-06-27 | 2 | Out= one South East to Tailem Bend 275kV line, avoid O/L Keith to Tailem Bend #2 132kV line on trip of the remaining South East to Tailem Bend line.
V>>S_SETB_SETB_PWKN | 2007-06-27 | 2 | Out= one South East to Tailem Bend 275kV line, avoid O/L Penola West to Kincraig line on trip of the remaining South East to Tailem Bend line.
V>>S_SETB_SETB_SGKH | 2007-06-27 | 2 | Out= one South East to Tailem Bend 275kV line, avoid O/L Snuggery to Keith line on trip of the remaining South East to Tailem Bend line.
V>>S_SETX_NPS_SETX | 2007-12-19 | 1 | Out = One South East Transformer. Prevent remaining transformer OL for one Northern PS trip.
V>>S_TB6125+28_KHTB1 | 2007-07-03 | 1 | Out = Tailem Bend CBs 6125 and 6128; Limit SE generation and Vic-SA to avoid OL Keith-Tailem Bend #1 line for loss of Tailem Bend transformer #4.
V>>S_TBEBX_SEPA_KHTB | 2008-09-09 | 1 | Out = Tailem Bend East bus. Prevent Keith - Tailem Bend #1 line OL for South East - Tailem Bend 275 kV line trip. Fb CoOp.
V>>S_TBEBX_SEPA_PWKN | 2008-09-09 | 1 | Out = Tailem Bend East bus. Prevent Penola West - Kincraig OL for South East - Tailem Bend 275 kV lines trip. Fb CoOp.
V>>S_BGDV_CNRB_BRPA_P | 2007-12-19 | 1 | Out = Bungama - Davenport line; Limit Murraylink and SA generation to avoid OL Brinkworth to Para 275 kV line for trip Canowi - Robertstown line.
V>>S_BGDV_CNRB_DVBR_P | 2007-12-19 | 1 | Out = Bungama - Davenport line; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line for trip Canowi - Robertstown line.
V>>S_BGDV_DVMK_BRPA_P | 2009-01-21 | 1 | Out = Davenport to Bungama line; Limit Murraylink and SA generation to avoid OL Brinkworth to Para 275 kV line for trip Davenport - Mokota - Robtstown line.
V>>S_BGDV_DVMK_DVBR_P | 2009-01-21 | 1 | Out = Davenport to Bungama line; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line for trip Davenport - Mokota - Robtstown line .
V>>S_BGDV_NIL_BRPA_P | 2007-12-19 | 1 | Out = Davenport to Bungama line; Limit Murraylink and SA generation to maintain Brinkworth to Para 275 kV line flow below the continuous rating after Davenport - Robertstown line trip.
V>>S_BGDV_NIL_DVBR_P | 2007-12-19 | 1 | Out = Davenport to Bungama line; Limit Murraylink and SA generation to maintain Davenport to Brinkworth 275 kV line flow below the continuous rating after Davenport - Robertstown line trip.
V>>S_BGPA_DVBG_DVBR_P | 2007-12-19 | 1 | Out = Bungama - Para line; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line for trip Davenport - Bungama line.
V>>S_BGPA_DVMK_BRPA_P | 2009-01-21 | 1 | Out = Bungama - Para line; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line for trip Davenport - Mokota - Robtstown 275kV line.
V>>S_CGRB_NIL_DVBR_P | 2007-12-19 | 1 | Out = Cherry Gardens - Robertstown line; maintain Davenport to Brinkworth line flow below the continuous rating.
V>>S_CGRB_RBCG_DVBR_P | 2007-12-19 | 1 | Out = Cherry Gardens - Robertstown line; maintain Davenport to Brinkworth line post contingency flow below the 15 minutes rating followng loss of the other Cherry Gardens to Robertstown line.
V>>S_CGTB_TBTU_TBMO_P | 2007-11-27 | 2 | Prior Outage = Cherry Gardens - Tailem Bend 275 kV line; Limit to avoid O/L Tailem Bend - Mobilong 132kV line on trip Tailem Bend - Tungkillo line.
V>>S_CNDV_DVBG_BRPA_P | 2007-12-19 | 1 | Out = Davenport - Canowi line; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line on trip Davenport to Bungama line.
V>>S_CNDV_DVBG_DVBR_P | 2007-12-19 | 1 | Out = Davenport - Canowi line; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line on trip Davenport to Bungama line.
V>>S_CNDV_NIL_BRPA_P | 2007-12-19 | 1 | Out = Davenport - Canowi line; Limit Murraylink and SA generation to maintain Brinkworth-Para 275 kV line flow below the continuous rating following trip Davenport to Bungama line.
V>>S_CNDV_NIL_DVBR_P | 2007-12-19 | 1 | Out = Davenport - Canowi line; Limit Murraylink and SA generation to maintain Davenport to Brinkworth 275 kV line flow below the continuous rating following trip Davenport to Bungama line.
V>>S_CNRB_BGPA_BRPA_P | 2007-12-19 | 1 | Out = Canowi - Robertstown line; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line for trip Bungama to Para 275kV line.
V>>S_CNRB_DVBG_DVBR_P | 2007-12-19 | 1 | Out = Canowi - Robertstown line; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line on trip Davenport to Bungama line.
V>>S_DVRB_BGPA_BRPA_P | 2007-12-19 | 1 | Out = Davenport - Robertstown line; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line for trip Bungama to Para 275kV line.
V>>S_DVRB_DVBG_DVBR_P | 2008-10-28 | 1 | Out = Davenport - Robertstown line; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line for trip Davenport - bungama line.
V>>S_KHKN_NIL_SGKH_P | 2008-01-25 | 1 | Out = Keith - Kincraig 132 kV line; avoid Snuggery - Keith line (continuous rating) OL on nil trip.
V>>S_KHKN_SETB_SGKH_P | 2008-01-25 | 1 | Out = Keith - Kincraig 132 kV line; avoid Snuggery - Keith line OL on trip of South East - Tailem Bend 275 kV line
V>>S_KHSG_SETB_PWKN_P | 2007-12-19 | 1 | Prior Outage = Snuggery-Keith line; Limit Interconnectors and generation to avoid O/L Penola West to Kincraig line for trip one South East - Tailem Bend line.
V>>S_KHTB1_SETB_KHTB_P | 2007-06-08 | 1 | Out = Keith - Tailem Bend #1 132 kV line. Prevent Keith - Tailem Bend #2 line OL for South East - Tailem Bend line trip.
V>>S_KHTB2_SETB_KHTB_P | 2007-06-08 | 1 | Out = Keith - Tailem Bend #2 132 kV line. Prevent Keith - Tailem Bend #1 line OL on trip one of the South East - Tailem Bend lines.
V>>S_KH_X_SETB_SETB_P | 2007-07-10 | 1 | Out = Keith - Tailem Bend lines 1 and 2; limit Vic to SA, Ladbroke Grove gen and Snuggery gen to avoid South East - Tailem Bend 275 kV line OL on trip the other South East - Tailem Bend 275 kV line.
V>>S_KNPW_NIL_SGKH_P | 2008-01-30 | 1 | Out = Kincraig - Penola West 132 kV line; avoid Snuggery - Keith line (continuous rating) OL on nil trip.
V>>S_KNPW_SETB_SGKH_P | 2008-01-30 | 1 | Out = Kincraig - Penola West 132 kV line; avoid Snuggery - Keith line OL on trip of South East - Tailem Bend 275 kV line
V>>S_MGPA_CGTI_TIMG_P | 2007-12-19 | 1 | Out = Magill - Para 275 kV line; Limit Torrens Island generation to avoid Torrens Island to Magill line OL on Torrens Island - Cherry Gardens line trip. FbCoOp
V>>S_MGPA_MGTI_TICG_P | 2007-12-19 | 1 | Out = Magill - Para 275 kV line; Limit Torrens Island generation to avoid Torrens Island to Cherry Garden line OL on Torrens Island - Magill line trip. FbCoOp
V>>S_MOTB_P | 2008-08-05 | 1 | Out=Mobilong-Tailem Bend 132 kV line; limit to avoid Tailem Bend - Tungkillo 275kV line O/L on trip Talem Bend - Cherry Gardens 275kV line.
V>>S_NIL_BGPA_BRPA_P | 2007-12-19 | 1 | Out = Nil; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line for trip Bungama to Para 275kV line.
V>>S_NIL_DVBG_BRPA_P | 2008-07-08 | 1 | Out = Nil; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line for trip Davenport to Bungama line.
V>>S_NIL_DVBG_DVBR_P | 2008-07-08 | 1 | Out = Nil; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line for trip Davenport to Bungama line.
V>>S_NIL_KHTB1_KHTB2_P | 2008-05-08 | 1 | Out = Nil. Prevent Keith - Tailem Bend #2 line OL for Keith - Tailem Bend #1 line trip.
V>>S_NIL_KHTB2_KHTB1_P | 2009-01-14 | 1 | Out = Nil. Prevent Keith - Tailem Bend #1 line OL for Keith - Tailem Bend #2 line trip.
V>>S_NIL_NIL_BRPA_P | 2008-07-08 | 1 | Out = Nil; Limit Murraylink and SA generation to avoid OL Brinkworth-Para 275 kV line above the continuous rating following Davenport to Bungama line trip.
V>>S_NIL_NIL_DVBR_P | 2008-07-08 | 1 | Out = Nil; Limit Murraylink and SA generation to avoid OL Davenport to Brinkworth 275 kV line above the continuous rating for trip Davenport to Bungama line.
V>>S_NIL_NIL_SGKHC_P | 2008-02-19 | 1 | Out= Nil, avoid O/L Snugg to Keith 132 kV line above the continuous rating on trip of Nil, Feedback
V>>S_NIL_NPS_MAMA2_P | 2008-06-04 | 1 | Out = Nil; Mannum to Mannum pump 2 line OL for one Northern PS trip. Fb CoOp.
V>>S_NIL_PWKN_SGKH_P | 2007-12-14 | 1 | Out= Nil, avoid O/L Snuggery - Keith 132 kV line on trip of Penola West - Kincraig line, Feedback
V>>S_NIL_SETB_KHTB_P | 2008-06-04 | 1 | Out = Nil; Prevent Keith - Tailem Bend #1 line OL for South East - Tailem Bend trip.
V>>S_NIL_SETB_PWKN_P | 2008-06-04 | 1 | Out = Nil; Prevent Penola West - Kincraig OL for South East - Tailem Bend trip. Fb CoOp.
V>>S_NIL_SETB_SGKH_P | 2007-12-14 | 1 | Out= Nil, avoid O/L Snuggery - Keith 132 kV line on trip of South East - Tailem Bend one 275kV line, Feedback
V>>S_NIL_SGBL_SGKH_P | 2007-12-14 | 1 | Out= Nil, avoid O/L Snuggery Keith 132 kV line on trip of Snuggery - Blanche line
V>>S_PTIMG_PAPG_MOTB_P | 2007-07-10 | 1 | Prior Outage = Para-Torrens Island and Para-Magill lines & Para West B2. Prevent TB-Mobilong OL for Para-Parafield trip. Fb CoOp.
V>>S_PWSE_NIL_SGKH_P | 2008-10-10 | 1 | Out = Penola West - South East 132 kV line; avoid Snuggery - Keith line (continuous rating) OL on nil trip.
V>>S_PWSE_SETB_SGKH_P | 2008-10-10 | 1 | Out = Penola West - South East 132 kV line; avoid Snuggery - Keith line OL on trip of South East - Tailem Bend 275 kV line
V>>S_RBPA_RBTU_BRPA_P | 2009-01-19 | 1 | Out= Robertstown - Para 275 kV line, avoid O/L Brinkworth to Para 275kV line on trip of Robertstown to Tungkillo 275kV line
V>>S_RBTU_N-2_BRPA | 2009-01-20 | 1 | Out= Nil; avoid O/L Brinkworth to Para 275kV line on trip of Robertstown - Para and Robertstown - Tungkillo 275kV lines
V>>S_RBTU_RBPA_BRPA | 2009-01-19 | 1 | Out= Robertstown - Tungkillo 275 kV line, avoid O/L Brinkworth to Para 275kV line on trip of Robertstown to Para 275kV line
V>>S_SESGT_KHSN | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; South East generation & Vic-SA limit to avoid Snuggery - Keith line OL (continuous rating). System normal.
V>>S_SESGT_PWKN_SGKH | 2007-12-19 | 1 | Out = South East - Snuggery T 132kV line; Prevent Snuggery - Keith 132 kV line OL for Penola West - Kincraig line trip.
V>>S_SESGT_SETB_BLSG | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; Prevent Blanche - Snuggery OL for South East - Tailem Bend trip. Fb CoOp.
V>>S_SESGT_SETB_KHTB | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; Prevent Keith - Tailem Bend #1 line OL for South East - Tailem Bend trip. Fb CoOp.
V>>S_SESGT_SETB_MGBL | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line;. Prevent Mt Gambier - Blanche OL for South East - Tailem Bend trip. Fb CoOp.
V>>S_SESGT_SETB_PWKN | 2007-12-12 | 1 | Out = South East - Snuggery T 132kV line; Prevent Penola West - Kincraig OL for South East - Tailem Bend trip. Fb CoOp.
V>>S_SETB_N-2_KHTB1 | 2007-06-27 | 1 | Prior outage= Nil; avoid O/L Keith to Tailem Bend #1 132kV line on trip of both South East to Tailem Bend 275 kV lines.
V>>S_SETB_N-2_KHTB2 | 2007-06-27 | 1 | Prior outage= Nil; avoid O/L Keith to Tailem Bend #2 132kV line on trip of both South East to Tailem Bend 275 kV lines.
V>>S_SETB_N-2_PWKN | 2007-06-27 | 1 | Prior outage= Nil; avoid O/L Penola West to Kincraig line on trip of both South East to Tailem Bend 275 kV lines.
V>>S_SETB_N-2_SGKH | 2007-06-27 | 1 | Prior outage= Nil; avoid O/L Snuggery to Keith line on trip of both South East to Tailem Bend 275 kV lines.
V>>S_SETB_SETB_KHTB1_P | 2007-06-27 | 2 | Out= one South East to Tailem Bend 275kV line, avoid O/L Keith to Tailem Bend #1 132kV line on trip of the remaining South East to Tailem Bend line.
V>>S_SETB_SETB_KHTB2_P | 2007-06-27 | 2 | Out= one South East to Tailem Bend 275kV line, avoid O/L Keith to Tailem Bend #2 132kV line on trip of the remaining South East to Tailem Bend line.
V>>S_SETB_SETB_PWKN_P | 2007-06-27 | 2 | Out= one South East to Tailem Bend 275kV line, avoid O/L Penola West to Kincraig line on trip of the remaining South East to Tailem Bend line.
V>>S_SETB_SETB_SGKH_P | 2007-06-27 | 2 | Out= one South East to Tailem Bend 275kV line, avoid O/L Snuggery to Keith line on trip of the remaining South East to Tailem Bend line.
V>>S_SETX_NPS_SETX | 2007-12-19 | 1 | Out = One South East Transformer. Prevent remaining transformer OL for one Northern PS trip.
V>>S_TB6125+28_KHTB1 | 2007-07-03 | 1 | Out = Tailem Bend CBs 6125 and 6128; Limit SE generation and Vic-SA to avoid OL Keith-Tailem Bend #1 line for loss of Tailem Bend transformer #4.
V>>S_TBEBX_SEPA_KHTB | 2008-09-09 | 1 | Out = Tailem Bend East bus. Prevent Keith - Tailem Bend #1 line OL for South East - Tailem Bend 275 kV line trip. Fb CoOp.
V>>S_TBEBX_SEPA_PWKN | 2008-09-09 | 1 | Out = Tailem Bend East bus. Prevent Penola West - Kincraig OL for South East - Tailem Bend 275 kV lines trip. Fb CoOp.
V>>S_TBTU_N-2_TBMO | 2008-11-21 | 1 | Prior Outage = Nil; Limit to avoid O/L Tailem Bend - Mobilong 132kV line on trip Tailem Bend - Tungkillo line and Tailem Bend - Cherry Gardens line.
V>>S_TBTU_TBCG_TBMO | 2007-11-27 | 2 | Prior Outage = Tailem Bend - Tungkillo 275 kV line; Limit to avoid O/L Tailem Bend - Mobilong 132kV line on trip Tailem Bend - Cherry Gardens line.
V>>S_TX1_SGBL_SGTX4 | 2008-04-03 | 1 | Out= Snuggery T1 transformer , avoid O/L Snuggery T4 on trip of Snuggery - Blanche line.
V>>S_X_RBCG_WTTP | 2007-12-19 | 1 | Out= Rob Town - Ch Gar + Bri - Para and Para - Tailem Bend , avoid O/L Waterloo to Templers line on trip of Robertstown to Cherry Gardens.
V>>V-DPWG_01 | 2008-07-01 | 1 | Out= DarlingtonPt-Wagga(63), avoid Murray to Dederang (67) O/L on Murray-Dederang(68) trip + DBUSS_L operated; Feedback
V>>V-DPWG_01X | 2008-07-01 | 1 | Out= DarlingtonPt-Wagga(63), avoid Murray to Dederang (67) O/L on Murray-Dederang(68) trip with DBUSS_L non-auto; Feedback
V>>V-DPWG_02 | 2008-07-01 | 1 | Out= DarlingtonPt-Wagga(63), avoid Murray to Dederang (68) O/L on Murray-Dederang(67) trip + DBUSS_L operated; Feedback
V>>V-DPWG_02X | 2008-07-01 | 1 | Out= DarlingtonPt-Wagga(63), avoid Murray to Dederang (68) O/L on Murray-Dederang(67) trip with DBUSS_L non-auto; Feedback
V>>V-HWLY_1 | 2007-10-19 | 1 | Outage = Hazlewood to Loy Yang (HWTS-LYPS) No.1 500kV line, avoid overloading Hazelwood to Loy Yang No.2 or No.3 500kV line on trip of any of the remaining Hazelwood to Loy Yang 500 kV line
V>>V-HWLY_2 | 2007-10-19 | 1 | Outage = Hazlewood to Loy Yang (HWTS-LYPS) No.2 500kV line, avoid overloading Hazelwood to Loy Yang No.1 or No.3 500kV line on trip of any of the remaining Hazelwood to Loy Yang 500kV line
V>>V-HWLY_3 | 2007-10-19 | 1 | Outage = Hazlewood to Loy Yang (HWTS-LYPS) No.3 500kV line, avoid overloading Hazelwood to Loy Yang No.1 or No.2 500kV line on trip of any of the remaining Hazelwood to Loy Yang 500kV line
V>>V-MSUT_1 | 2008-07-01 | 1 | Out= Murray-UpperTumut(65), avoid Dederang to Wodonga (DDWO) O/L on Murray-LowerTumut(66) trip; Feedback
V>>V_CBTS_TX_2A_R | 2008-07-01 | 1 | Outage = Cranbourne 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood
V>>V_CBTS_TX_2B_R | 2008-07-01 | 1 | Outage = Cranbourne 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood
V>>V_CBTS_TX_2_P | 2008-07-01 | 1 | Outage = Cranbourne 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, parallel mode at Hazelwood
V>>V_CBTS_TX_3A_R | 2008-07-01 | 1 | Outage = Cranbourne 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 500kV mode, radial mode
V>>V_CBTS_TX_3B_R | 2008-07-01 | 1 | Outage = Cranbourne 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 220kV mode, radial mode
V>>V_CBTS_TX_3_P | 2008-07-01 | 1 | Outage = Cranbourne 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 220kV mode, parallel mode
V>>V_DDTX_A | 2008-07-01 | 1 | Outage = Dederang No.2 or No.3 330/220kV transformer, limit Vic generation and interconnectors to avoid pre-contingent overload of the Dederang No.1 transformer
V>>V_DDTX_B | 2008-07-01 | 1 | Outage = Dederang No.1 or No.3 330/220kV transformer, limit Vic generation and interconnectors to avoid pre-contingent overload of the Dederang No.2 transformer
V>>V_DDTX_C | 2008-07-01 | 1 | Outage = Dederang No.1 or No.2 330/220kV transformer, limit Vic generation and interconnectors to avoid pre-contingent overload of the Dederang No.3 transformer
V>>V_EPMB_1A | 2008-07-01 | 1 | Out = Eildon to Mt Beauty 220kV line, Mt Beauty 220kV Bustie CB closed, limit Vic interconnectors and Southern Hydro generation to avoid O/L of Dederang to Mt Beauty No.1 220kV line for loss of Dederang to Mt Beauty No.2 220kV line
V>>V_EPMB_1B | 2008-07-01 | 1 | Out = Eildon to Mt Beauty 220kV line, Mt Beauty 220kV Bustie CB closed, limit Vic interconnectors and Southern Hydro generation to avoid O/L of Dederang to Mt Beauty No.2 220kV line for loss of Dederang to Mt Beauty No.1 220kV line
V>>V_EPTT_1A | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic interconnectors and Vic generation to avoid overloading Dederang to Sth Morang No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings
V>>V_EPTT_1B | 2008-07-01 | 1 | Outage = Eildon to Thomastown 220kV line, limit Vic interconnectors and Vic generation to avoid overloading Dederang to Sth Morang No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings
V>>V_EPTT_2A_R | 2008-07-01 | 2 | Outage = Eildon to Thomastown 220kV line, limit Vic interconnectors and Vic generation to avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial
V>>V_EPTT_2B_R | 2008-07-01 | 2 | Outage = Eildon to Thomastown 220kV line, limit Vic interconnectors and Vic generation to avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial
V>>V_EPTT_2_P | 2008-07-01 | 2 | Outage = Eildon to Thomastown 220kV line, limit Vic interconnectors and Vic generation to avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, parallel
V>>V_EPTT_3A_R | 2008-07-01 | 2 | Outage = Eildon to Thomastown 220kV line, limit Vic interconnectors and generation to avoid post-contingent O/L the South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 500kV mode, radial
V>>V_EPTT_3B_R | 2008-07-01 | 2 | Outage = Eildon to Thomastown 220kV line, limit Vic interconnectors and generation to avoid post-contingent O/L the South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 220kV mode, radial
V>>V_EPTT_3_P | 2008-07-01 | 2 | Outage = Eildon to Thomastown 220kV line, limit Vic interconnectors and generation to avoid post-contingent O/L the South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 220kV mode, parallel
V>>V_GTKT_1 | 2008-07-01 | 1 | Out = Geelong to Keilor No.2 or No.3 220kV line, limit Vic generation and interconnectors to avoid O/L the Geelong to Keilor No.1 220kV line for trip of the Moorabool 500/220kV transformer
V>>V_GTKT_2 | 2008-07-01 | 1 | Out = Geelong to Keilor No.1 or No.3 220kV line, limit Vic generation and interconnectors to avoid O/L the Geelong to Keilor No.2 220kV line for trip of the Moorabool 500/220kV transformer
V>>V_GTKT_3 | 2008-07-01 | 1 | Out = Geelong to Keilor No.1 or No.2 220kV line, limit Vic generation and interconnectors to avoid O/L the Geelong to Keilor No.3 220kV line for trip of the Moorabool 500/220kV transformer
V>>V_HWPS-RO1_3-5_1 | 2008-10-22 | 2 | Out = Hazelwood to Rowville No.1 220kV line, 3-5 Parallel, Jeeralang split with JLGS B connected to Hazelwood #1 or #2 220kV bus, avoid O/L Hazelwood to Rowville No.2 220kV line for loss of Hazelwood #1 or #2 500/220kV transformer
V>>V_HWPS-RO1_3-5_2 | 2008-10-22 | 2 | Out = Hazelwood to Rowville No.1 220kV line, 3-5 Parallel, Jeeralang split with JLGS A connected to Hazelwood #1 or #2 220kV bus, avoid O/L Hazelwood to Rowville No.2 220kV line for loss of Hazelwood #1 or #2 500/220kV transformer
V>>V_HWPS-RO2_3-5_1 | 2008-10-22 | 2 | Out = Hazelwood to Rowville No.2 220kV line, 3-5 Parallel, Jeeralang split with JLGS B connected to Hazelwood #1 or #2 220kV bus, avoid O/L Hazelwood to Rowville No.1 220kV line for loss of Hazelwood #1 or #2 500/220kV transformer
V>>V_HWPS-RO2_3-5_2 | 2008-10-22 | 2 | Out = Hazelwood to Rowville No.2 220kV line, 3-5 Parallel, Jeeralang split with JLGS A connected to Hazelwood #1 or #2 220kV bus, avoid O/L Hazelwood to Rowville No.1 220kV line for loss of Hazelwood #1 or #2 500/220kV transformer
V>>V_HWPS-RO_3-5_3 | 2008-10-22 | 1 | Out = Hazelwood to Rowville No.1 or No.2 220kV line, 3-5 Parallel, Jeeralang split with JLGS B connected to Hazelwood #1 or #2 220kV bus, avoid O/L Hazelwood #1 or #2 500/220kV transformer for loss of either transformer
V>>V_HWPS-RO_3-5_4 | 2008-10-22 | 1 | Out = Hazelwood to Rowville No.1 or No.2 220kV line, 3-5 Parallel, Jeeralang split with JLGS A connected to Hazelwood #1 or #2 220kV bus, void O/L Hazelwood #1 or #2 500/220kV transformer for loss of either transformer
V>>V_HWTS_TX3_3-5MOD | 2008-10-22 | 1 | Out = Hazelwood #3 or #4 500/220kV transformer, 3-5 Parallel, Jeeralang split with JLGS A connected to Hazelwood #3 or #4 220kV bus, avoid O/L Hazelwood #4 or #3 500/220kV transformer for loss of Rowville to Yallourn #5 220kV line
V>>V_HWTS_TX3_PAR3-5 | 2008-10-22 | 1 | Out = Hazelwood #3 or #4 500/220kV transformer, 3-5 Parallel, Jeeralang split with JLGS B connected to Hazelwood #3 or #4 220kV bus, avoid O/L Hazelwood #4 or #3 500/220kV transformer for loss of Rowville to Yallourn #5 220kV line
V>>V_KTSM_1_R | 2008-07-01 | 1 | Outage = Keilor to South Morang 500kV line, avoid O/L South Morang 500/330kV (F2) transformer for trip of Keilor to Sydenham 500kV line, Yallourn unit 1 in 500kV mode, radial mode
V>>V_KTSM_2_R | 2008-07-01 | 1 | Outage = Keilor to South Morang 500kV line, avoid O/L South Morang 500/330kV (F2) transformer for trip of Keilor to Sydenham 500kV line, Yallourn unit 1 in 220kV mode, radial mode
V>>V_KTSY_1_R | 2008-07-01 | 1 | Outage = Keilor to Sydenham 500kV line, avoid O/L South Morang 500/330kV (F2) transformer for trip of Keilor to South Morang 500kV line, Yallourn unit 1 in 500kV mode, radial mode
V>>V_KTSY_2_R | 2008-07-01 | 1 | Outage = Keilor to Sydenham 500kV line, avoid O/L South Morang 500/330kV (F2) transformer for trip of Keilor to South Morang 500kV line, Yallourn unit 1 in 220kV mode, radial mode
V>>V_KTS_TX_A2_2A_R | 2008-07-01 | 1 | Outage = Keilor A2 or A4 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood
V>>V_KTS_TX_A2_2B_R | 2008-07-01 | 1 | Outage = Keilor A2 or A4 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood
V>>V_KTS_TX_A2_2_P | 2008-07-01 | 1 | Outage = Keilor A2 or A4 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, parallel mode at Hazelwood
V>>V_KTS_TX_A2_3A_R | 2008-07-01 | 1 | Outage = Keilor A2 or A4 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 500kV mode, radial mode
V>>V_KTS_TX_A2_3B_R | 2008-07-01 | 1 | Outage = Keilor A2 or A4 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 220kV mode, radial mode
V>>V_KTS_TX_A2_3_P | 2008-07-01 | 1 | Outage = Keilor A2 or A4 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 220kV mode, parallel mode
V>>V_KTS_TX_A3_2A_R | 2008-07-01 | 1 | Outage = Keilor A3 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood
V>>V_KTS_TX_A3_2B_R | 2008-07-01 | 1 | Outage = Keilor A3 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood
V>>V_KTS_TX_A3_2_P | 2008-07-01 | 1 | Outage = Keilor A3 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, parallel mode at Hazelwood
V>>V_KTS_TX_A3_3A_R | 2008-07-01 | 1 | Outage = Keilor A3 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 500kV mode, radial mode
V>>V_KTS_TX_A3_3B_R | 2008-07-01 | 1 | Outage = Keilor A3 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 220kV mode, radial mode
V>>V_KTS_TX_A3_3_P | 2008-07-01 | 1 | Outage = Keilor A3 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 220kV mode, parallel mode
V>>V_LTMS_1 | 2008-07-01 | 1 | Out= LowerTumut-Murray(66), avoid Dederang to Wodonga (DDWO) O/L on Murray-UpperTumut(65) trip; Feedback
V>>V_MLTS_TX_2A_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood
V>>V_MLTS_TX_2B_R | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood
V>>V_MLTS_TX_2_P | 2008-07-01 | 1 | Outage = Moorabool 500/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, parallel mode at Hazelwood
V>>V_MLTX_1 | 2008-07-01 | 1 | Out = Moorabool 500/220kV transformer, limit Vic generation and interconnectors to avoid O/L the Geelong to Keilor No.1 220kV line for loss of the remaining Moorabool transformer
V>>V_MLTX_2 | 2008-07-01 | 1 | Out = Moorabool 500/220kV transformer, limit Vic generation and interconnectors to avoid O/L the Geelong to Keilor No.2 220kV line for loss of the remaining Moorabool transformer
V>>V_MLTX_3 | 2008-07-01 | 1 | Out = Moorabool 500/220kV transformer, limit Vic generation and interconnectors to avoid O/L the Geelong to Keilor No.3 220kV line for loss of the remaining Moorabool transformer
V>>V_NIL1A_R | 2008-07-02 | 1 | Outage=Nil, limit Victorian interconnectors and Vic generators to avoid thermal overload on South Morang to Dederang 330 kV line for loss of the parallel line, Radial
V>>V_NIL_10 | 2008-07-02 | 1 | Out = Mt Beauty 220kV Bustie CB open, limit Vic generators and interconnectors to avoid O/L Dederang to Mt Beauty No.2 220kV line for loss of Dederang to Mt Beauty No.1 220kV line
V>>V_NIL_11 | 2008-07-02 | 1 | Out = Mt Beauty 220kV Bustie CB open, limit Vic generators and interconnectors to avoid O/L Dederang to Mt Beauty No.1 220kV line for loss of Dederang to Mt Beauty No.2 220kV line
V>>V_NIL_1A | 2008-07-02 | 1 | Outage = Nil, limit Vic interconnectors and Vic generation to avoid overloading Dederang to Murray No.1 330kV line for loss of the parallel No.2 line, 15 min line ratings
V>>V_NIL_1B | 2008-07-02 | 1 | Outage = Nil, limit Vic interconnectors and Vic generation to avoid overloading Dederang to Murray No.2 330kV line for loss of the parallel No.1 line, 15 min line ratings
V>>V_NIL_1C | 2008-07-02 | 1 | Outage = Nil, limit Vic interconnectors and Vic generation to avoid overloading Dederang to Murray No.1 330kV line for loss of the parallel No.2 line, 5 min line ratings
V>>V_NIL_1D | 2008-07-02 | 1 | Outage = Nil, limit Vic interconnectors and Vic generation to avoid overloading Dederang to Murray No.2 330kV line for loss of the parallel No.1 line, 5 min line ratings
V>>V_NIL_2A_R | 2008-07-02 | 1 | Outage = Nil, limit Vic interconnectors and generation to avoid pre-contingent overloading the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood
V>>V_NIL_2B_R | 2008-07-02 | 1 | Outage = Nil, limit Vic interconnectors and generation to avoid pre-contingent overloading the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood
V>>V_NIL_2_P | 2008-07-02 | 1 | Outage = Nil, limit Vic interconnectors and generation to avoid pre-contingent overloading the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, parallel mode at Hazelwood
V>>V_NIL_3 | 2008-07-02 | 1 | Outage = Nil, limit Vic interconnectors and Vic generation to avoid overloading a Dederang to South Morang 330kV line for loss of one of the two parallel lines
V>>V_NIL_4A | 2008-07-02 | 1 | Outage = Nil, limit Vic interconnectors and Vic generation to avoid exceeding the continuous rating of the No.1 Dederang 330/220kV transformer with the DBUSS-Transformer control scheme armed
V>>V_NIL_4B | 2008-07-02 | 1 | Outage = Nil, limit Vic interconnectors and Vic generation to avoid exceeding the continuous rating of the No.2 Dederang 330/220kV transformer with the DBUSS-Transformer control scheme armed
V>>V_NIL_4C | 2008-07-02 | 1 | Outage = Nil, limit Vic interconnectors and Vic generation to avoid exceeding the continuous rating of the No.3 Dederang 330/220kV transformer with the DBUSS-Transformer control scheme armed
V>>V_ROTS_TX_2A_R | 2008-07-01 | 1 | Outage = Rowville 500/220kV transformer, limit Vic interconnectors and generation to avoid pre-contingent overloading the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood
V>>V_ROTS_TX_2B_R | 2008-07-01 | 1 | Outage = Rowville 500/220kV transformer, limit Vic interconnectors and generation to avoid pre-contingent overloading the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood
V>>V_ROTS_TX_2_P | 2008-07-01 | 1 | Outage = Rowville 500/220kV transformer, limit Vic interconnectors and generation to avoid pre-contingent overloading the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, parallel mode at Hazelwood
V>>V_ROTS_TX_3A_R | 2008-07-01 | 1 | Outage = Rowville 500/220kV transformer, limit Vic interconnectors and gen to avoid post-contingent O/L South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood
V>>V_ROTS_TX_3B_R | 2008-07-01 | 1 | Outage = Rowville 500/220kV transformer, limit Vic interconnectors and gen to avoid post-contingent O/L South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood
V>>V_ROTS_TX_3_P | 2008-07-01 | 1 | Outage = Rowville 500/220kV transformer, limit Vic interconnectors and gen to avoid post-contingent O/L South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 220kV mode, parallel mode at Hazelwood
V>>V_SMSY_KTSM | 2008-07-01 | 1 | Prior Outage = South Morang-Sydenham line; Prevent OL remaining South Morang - Keilor line for South Morang - Sydenham line trip. Fb CoOp.
V>>V_SMSY_SMSY1 | 2008-07-01 | 1 | Prior Outage = South Morang-Sydenham line; Prevent OL remaining South Morang - Sydenham line for South Morang - Keilor line trip. Fb CoOp.
V>>V_SMTS_TX_H1_2A_R | 2008-07-01 | 1 | Outage = Sth Morang H1 330/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L Sth Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood
V>>V_SMTS_TX_H1_2B_R | 2008-07-01 | 1 | Outage = Sth Morang H1 330/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L Sth Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood
V>>V_SMTS_TX_H1_2_P | 2008-07-01 | 1 | Outage = Sth Morang H1 330/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L Sth Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, parallel mode at Hazelwood
V>>V_SMTS_TX_H2_2A_R | 2008-07-01 | 1 | Outage = Sth Morang H2 330/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L Sth Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood
V>>V_SMTS_TX_H2_2B_R | 2008-07-01 | 1 | Outage = Sth Morang H2 330/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L Sth Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode at Hazelwood
V>>V_SMTS_TX_H2_2_P | 2008-07-01 | 1 | Outage = Sth Morang H2 330/220kV transformer, limit Vic interconnectors and Vic generation to avoid O/L Sth Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, parallel mode at Hazelwood
V>>V_X_DDMB_2A_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic interconnectors and Vic generation to avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 500kV mode, radial
V>>V_X_DDMB_2B_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic interconnectors and Vic generation to avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial
V>>V_X_DDMB_2_P | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic interconnectors and Vic generation to avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, parallel
V>>V_X_DDMB_3A_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic interconnectors and generation to avoid post-contingent O/L the South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 500kV mode, radial
V>>V_X_DDMB_3B_R | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic interconnectors and generation to avoid post-contingent O/L the South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 220kV mode, radial
V>>V_X_DDMB_3_P | 2008-07-01 | 1 | Outage = Both Dederang to Mt Beauty 220kV lines, limit Vic interconnectors and generation to avoid post-contingent O/L the South Morang 500/330kV (F2) transformer for trip of Rowville 500/220kV transformer, Yallourn unit 1 in 220kV mode, parallel
V>>V_X_DDSM_TWO | 2008-07-01 | 1 | Outage = Both Dederang to Sth Morang 330kV lines, limit Vic generators and interconnectors to avoid O/L the Ballarat to Bendigo 220 kV line for trip of Eildon to Thomastown 220kV line
V>>V_X_DDTX1_DBUSS_A | 2008-07-01 | 1 | Outage = Dederang No.1 330/220kV transformer and DBUSS transformer control scheme, limit Vic generation and interconnectors to avoid overloading the Dederang No.2 transformer for loss of the Dederang No.3 transformer
V>>V_X_DDTX1_DBUSS_B | 2008-07-01 | 1 | Outage = Dederang No.1 330/220kV transformer and DBUSS transformer control scheme, limit Vic generation and interconnectors to avoid overloading the Dederang No.3 transformer for loss of the Dederang No.2 transformer
V>>V_X_DDTX2_3_DBUSS | 2008-07-01 | 1 | Outage = Dederang No.2 or No.3 330/220kV transformer and DBUSS transformer control scheme, limit Vic generation and interconnectors to avoid overloading the Dederang No.1 transformer for loss of the other Dederang transformer
V>>V_X_GTKT+MLTX_1 | 2008-07-01 | 1 | Out = One Geelong to Keilor No.2 or No.3 220kV line and a Moorabool 500/220kV transformer, limit Vic gen and interconnectors to avoid O/L the Geelong to Keilor No.1 220kV line for trip of Moorabool 500/220kV transformer
V>>V_X_GTKT+MLTX_2 | 2008-07-01 | 1 | Out = One Geelong to Keilor No.1 or No.3 220kV line and a Moorabool 500/220kV transformer, limit Vic gen and interconnectors to avoid O/L the Geelong to Keilor No.2 220kV line for trip of Moorabool 500/220kV transformer
V>>V_X_GTKT+MLTX_3 | 2008-07-01 | 1 | Out = One Geelong to Keilor No.1 or No.2 220kV line and a Moorabool 500/220kV transformer, limit Vic gen and interconnectors to avoid O/L the Geelong to Keilor No.3 220kV line for trip of Moorabool 500/220kV transformer
V>>V_X_MLTX+RO-KT_1R | 2008-07-03 | 1 | Outage = Moorabool transformer and Rowville to Sth Morang and Sth Morang to Keilor 500kV lines, avoid O/L South Morang 500/330kV (F2) transformer for trip of Keilor to Sydenham 500kV line, Yallourn unit 1 in 500kV mode, radial mode
V>>V_X_MLTX+RO-KT_2R | 2008-07-03 | 1 | Outage = Moorabool transformer and Rowville to Sth Morang and Sth Morang to Keilor 500kV lines, avoid O/L South Morang 500/330kV (F2) transformer for trip of Keilor to Sydenham 500kV line, Yallourn unit 1 in 220kV mode, radial mode
V>>V_X_SMTXH1+EPTT_A | 2009-01-07 | 1 | Outage = South Morang 330/220kV (H1) transformer and Eildon to Thomastown 220kV line, limit Vic generators and interconnectors (Vic import) to avoid overload of South Morang H2 transformer for trip of the South Morang 500/330kV (F2) transformer
V>>V_X_SMTXH1+EPTT_B | 2009-01-07 | 1 | Outage = South Morang 330/220kV (H1) transformer and Eildon to Thomastown 220kV line, limit Vic generators and interconnectors (Vic export) to avoid overload of South Morang H2 transformer for trip of the South Morang 500/330kV (F2) transformer
V>D2800-LY | 2000-09-08 | 1 | Discretionary Loy Yang Gneration Limit = 2800MW
V>EPTT | 2007-04-30 | 1 | Outage =Eildon to Thomastown 220kV line, limit Southern Hydro generation to avoid overloading either Dederang to Mt Beauty 220kV line for trip of one the lines
V>HWPSBUS2 | 2004-10-12 | 1 | Outage = Hazelwood No.2 220 kV bus, limit generation of Hazelwood units 1,2,3,4 to avoid overloading the Hazelwood No.2 500/220 kV transformer for loss of the Hazelwood to Rowville No.2 220 kV line, 6/2 parallel
V>LV2_1500 | 2002-11-12 | 1 | 1500MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_1550 | 2002-11-12 | 1 | 1550MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_1600 | 2002-11-12 | 1 | 1600MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_1650 | 2002-11-12 | 1 | 1650MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_1700 | 2002-11-12 | 1 | 1700MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_1750 | 2002-11-12 | 1 | 1750MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_1800 | 2002-11-12 | 1 | 1800MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_1850 | 2002-11-12 | 1 | 1850MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_1900 | 2002-11-12 | 1 | 1900MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_1950 | 2002-11-12 | 1 | 1950MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_2000 | 2002-06-17 | 1 | 2000MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_2050 | 2002-06-17 | 1 | 2050MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_2100 | 2002-06-17 | 1 | 2100MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_2150 | 2002-06-17 | 1 | 2150MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_2200 | 2002-06-17 | 1 | 2200MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_2250 | 2002-06-17 | 1 | 2250MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_2300 | 2002-06-17 | 1 | 2300MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_2350 | 2002-06-17 | 1 | 2350MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_2400 | 2002-06-17 | 1 | 2400MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_2450 | 2002-06-17 | 1 | 2450MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV2_2500 | 2002-06-17 | 1 | 2500MW upper limit for HWPS 6,7,8 + YPS+JLGSB+MWPS+BDPS gen
V>LV3_1500 | 2004-04-15 | 2 | 1500MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_1550 | 2002-11-12 | 1 | 1550MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_1600 | 2002-11-12 | 1 | 1600MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_1650 | 2002-11-12 | 1 | 1650MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_1700 | 2002-11-12 | 1 | 1700MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_1750 | 2002-11-12 | 1 | 1750MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_1800 | 2002-11-12 | 1 | 1800MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_1850 | 2002-11-12 | 1 | 1850MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_1900 | 2002-11-11 | 1 | 1900MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_1950 | 2002-11-11 | 1 | 1950MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_2000 | 2002-11-11 | 1 | 2000MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_2050 | 2002-11-11 | 1 | 2050MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_2100 | 2002-11-11 | 1 | 2100MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_2150 | 2002-11-11 | 1 | 2150MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_2200 | 2002-11-11 | 1 | 2200MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_2250 | 2002-11-11 | 1 | 2250MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_2300 | 2002-11-11 | 1 | 2300MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_2350 | 2002-11-11 | 1 | 2350MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_2400 | 2002-11-11 | 1 | 2400MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_2450 | 2002-11-11 | 1 | 2450MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV3_2500 | 2002-11-11 | 1 | 2500MW upper limit for HWPS 6,7,8 + YPS+JLGSA+MWPS+BDPS gen
V>LV4_1500 | 2004-04-30 | 1 | 1500 MW upper limit on Hazlewood units 1,2,6,7,8 + Jeeralang + Bairnsdale + Morwell + Yallourn unit 1
V>LV4_1520 | 2004-04-30 | 1 | 1520 MW upper limit on Hazlewood units 1,2,6,7,8 + Jeeralang + Bairnsdale + Morwell + Yallourn unit 1
V>LV_2000 | 2007-09-06 | 1 | Discretionary Latrobe Valley Generation and Basslink Limit <= 2000 MW
V>LV_2250 | 2007-09-06 | 1 | Discretionary Latrobe Valley Generation and Basslink Limit <= 2250 MW
V>LV_2500 | 2007-09-06 | 1 | Discretionary Latrobe Valley Generation and Basslink Limit <= 2500 MW
V>LV_2750 | 2007-09-06 | 1 | Discretionary Latrobe Valley Generation and Basslink Limit <= 2750 MW
V>LV_3000 | 2007-09-06 | 1 | Discretionary Latrobe Valley Generation and Basslink Limit <= 3000 MW
V>LV_3250 | 2007-09-06 | 1 | Discretionary Latrobe Valley Generation and Basslink Limit <= 3250 MW
V>LY_1600 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 1600 MW
V>LY_1650 | 2008-07-24 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 1650 MW
V>LY_1700 | 2008-07-24 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 1700 MW
V>LY_1750 | 2008-07-24 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 1750 MW
V>LY_1800 | 2008-07-24 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 1800 MW
V>LY_1850 | 2008-07-24 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 1850 MW
V>LY_1900 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 1900 MW
V>LY_1950 | 2008-07-24 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 1950 MW
V>LY_2000 | 2008-07-24 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2000 MW
V>LY_2050 | 2008-07-24 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2050 MW
V>LY_2100 | 2008-07-24 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2100 MW
V>LY_2150 | 2008-07-24 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2150 MW
V>LY_2200 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2200 MW
V>LY_2250 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2250 MW
V>LY_2300 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2300 MW
V>LY_2350 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2350 MW
V>LY_2400 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2400 MW
V>LY_2450 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2450 MW
V>LY_2500 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2500 MW
V>LY_2550 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2550 MW
V>LY_2600 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2600 MW
V>LY_2650 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2650 MW
V>LY_2700 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2700 MW
V>LY_2750 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2750 MW
V>LY_2800 | 2007-09-06 | 1 | Discretionary Latrobe Loy Yang A, B and Loy Yang Gas Generation and Basslink Limit <= 2800 MW
V>NIL_RAD_1-2_3-4_1 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1&2 and 3&4 busses tied
V>NIL_RAD_1-2_3-4_2 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1&2 and 3&4 busses tied
V>NIL_RAD_1-2_3-4_3 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1&2 and 3&4 busses tied
V>NIL_RAD_1-2_3-4_4 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1&2 and 3&4 busses tied
V>NIL_RAD_1-2_3-4_5 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A3 transformer for trip of A4 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1&2 and 3&4 busses tied
V>NIL_RAD_1-2_3-4_6 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A3 transformer for trip of A4 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1&2 and 3&4 busses tied
V>NIL_RAD_1-2_3-4_7 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A4 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1&2 and 3&4 busses tied
V>NIL_RAD_1-2_3-4_8 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A4 transformer for trip of A3 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1&2 and 3&4 busses tied
V>SMLBAHO1 | 2007-02-21 | 1 | Out = Ballarat to Horsham or Bendigo to Kerang line, Murraylink limit to avoid O/L Buronga to Balranald to Darlington Point (X5) line or Buronga to Recliffs (OX1) line or voltage collapse on X5, for trip of Bendigo to Kerang or Ballarat to Horsham line
V>SMLBAHO2 | 2006-07-27 | 1 | Out = Ballarat to Horsham or Balranald to Darlington Pt (X5/1) line, limit Murraylink from Vic to SA to avoid O/L Bendigo to Kerang line on loss of Balranald to Darlington Point (X5/1) or Ballarat to Horsham line
V>SMLBAHO3 | 2006-07-27 | 1 | Out = Ballarat to Horsham or Balranald to Darlington Pt (X5/1) line, limit Murraylink from Vic to SA to avoid O/L Kerang to Red Cliffs line on loss of Balranald to Darlington Point (X5/1) or Ballarat to Horsham line
V>SMLBATG1 | 2008-07-01 | 1 | Outage = Ballarat to Terang 220kV line, limit Murraylink from Vic to SA to avoid overloading Ballarat to Moorabool No.1 220kV line for loss of Ballarat to Moorabool No.2 220kV line, Murraylink VFRB enabled and Murraylink > 25MW
V>SMLBEKG | 2006-07-27 | 1 | Outage = Bendigo to Kerang or Balranald to Darlington Pt (X5/1) line, limit Murraylink from Vic to SA to avoid overloading Ballarat to Horsham line on loss of Balranald to Darlington Point (X5/1) or Bendigo to Kerang line
V>SMLBESH1 | 2008-07-01 | 2 | Outage = Bendigo to Shepparton or Ballarat to Bendigo 220kV line, limit Murraylink from Vic to SA to avoid overloading Ballarat to Horsham 220kV line on loss of Ballarat to Bendigo or Bendigo to Shepparton 220kV line
V>SMLBESH2 | 2008-07-01 | 2 | Outage = Bendigo to Shepparton or Ballarat to Bendigo 220kV line, limit Murraylink from Vic to SA to avoid overloading Balranald to Darlington Pt (X5/1) 220kV line on loss of Ballarat to Bendigo or Bendigo to Shepparton 220kV line
V>SMLBESH3 | 2008-07-01 | 1 | Outage = Bendigo to Shepparton 220kV line, limit Murraylink from Vic to SA to avoid overloading Ballarat to Moorabool No.1 220kV line on loss of Ballarat to Moorabool No.2 220kV line, Murraylink VFRB enabled and Murraylink > 25MW
V>SMLBSRC1 | 2008-07-01 | 1 | Out = Buronga to Redcliffs 220kV line, limit Murraylink from Vic to SA to avoid overloading Bendigo to Kerang 220kV line for loss of Ballarat to Horsham 220kV line
V>SMLBSRC2 | 2008-07-01 | 1 | Out = Buronga to Redcliffs line, limit Murraylink from Vic to SA to avoid overloading Ballarat to Horsham 220kV line for loss of Bendigo to Kerang 220kV line
V>SMLBSRC3 | 2008-07-01 | 1 | Out = Buronga to Redcliffs 220kV line, limit Murraylink from Vic to SA to avoid overloading Kerang to Redcliffs 220kV line for loss of Ballarat to Horsham 220kV line
V>SMLDDGN1 | 2008-07-01 | 1 | Outage = Dederang to Glenrowan No.1 line or No.3 220kV line AND Dederang to Shepparton 220kV line, limit Murraylink from Vic to SA to avoid overloading Ballarat to Bendigo 220kV line on loss of Dederang to Glenrowan No.3 or No.1 220kV line
V>SMLDDGN2 | 2008-07-01 | 1 | Outage = one Dederang to Glenrowan 220kV line, limit Murraylink from Vic to SA to avoid overloading Balranald to Darlington Pt (X5/1) 220kV line
V>SMLGNSH1 | 2008-07-01 | 1 | Out = Glenrowen to Shepparton No.1 or No.3 220kV line AND Dederang to Shepparton 220kV line, limit Murraylink from Vic to SA to avoid overloading Ballarat to Bendigo 220kV line for loss of Glenrowen to Shepparton No.3 or No.1 220kV line
V>SMLGNSH2 | 2008-07-01 | 1 | Outage = one Glenrowan to Shepparton 220kV line, limit Murraylink from Vic to SA to avoid overloading Balranald to Darlington Pt (X5/1) 220kV line
V>SMLHORC1 | 2006-12-06 | 1 | Out = Horsham to Red Cliffs 220kV line, limit Murraylink from Vic to SA to avoid overloading Balranald to Darlington Pt (X5/1) 220kV line for trip of Bendigo to Kerang line
V>SMLHORC2 | 2006-12-06 | 1 | Out = Horsham to Redcliffs 220kV line, limit Murraylink from Vic to SA to avoid overloading Bendigo to Kerang 220kV line for trip of Balranald to Darlington Point (X5/1) 220kV line
V>SMLHORC3 | 2006-12-06 | 1 | Out = Horsham to Redcliffs 220kV line, limit Murraylink from Vic to SA to avoid overloading Kerang to Redcliffs 220kV line for trip of Balranald to Darlington Point (X5/1) 220kV line
V>SMLKGRC1 | 2006-07-27 | 1 | Outage = one Kerang to Red Cliffs 220kV line, limit Murraylink from Vic to SA to avoid overloading Balranald to Darlington Pt (X5/1) 220kV line for trip of Ballarat to Horsham line
V>SMLKGRC2 | 2006-12-20 | 1 | Out = Kerang to Redcliffs 220kV line, limit Murraylink from Vic to SA to avoid overloading Ballarat to Horsham 220kV line for loss of Balranald to Darlington Point (X5/1) 220kV line
V>SMLMH2RB | 2007-04-30 | 1 | Out=NWB-MWP1_MWP2_MWP3;&other outages,V-S Lmt onML for NWB-RB#1
V>SMLMHNW1 | 2004-12-21 | 1 | Outage=Monash to North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash to Nth West Bend # 2 132kV line
V>SMLMHNW2 | 2004-12-21 | 1 | Out=MH_NW2, V-SA on ML, avoid overload on Monash to North West Bend # 1
V>SMLMLTG1 | 2008-07-01 | 1 | Out = Moorabool to Terang or Ballarat to Moorabool No.2 line, avoid O/L Ballarat to Moorabool No.1 line on loss of Ballarat to Moorabool No.2 or Moorabool to Terang line, Murraylink VFRB enabled and Murraylink > 25MW
V>SMLMW1NW | 2007-04-30 | 1 | Out=MWP1_NW, V-SA on ML, load on Robertstown to Nth West Bend
V>SML_1NIL | 2007-04-30 | 1 | Out=MLrunback,V-SA_ML,O/LLmtNW-RB1/MH-RB2;tripMH-RB/NW-RB/MH-NW
V>SML_BABE_3 | 2008-07-01 | 1 | Outage = Ballarat to Bendigo 220kV line, limit Murraylink interconnector to avoid O/L Bendigo to Shepparton 220 kV line for trip of Redcliffs to Buronga 220kV line, swamped if Murraylink VFRB enabled for this contingency and Murraylink > 25MW
V>SML_BESH_3 | 2008-07-01 | 1 | Outage = Bendigo to Shepparton 220kV line, limit Murraylink from Vic to SA to avoid overloading Ballarat to Moorabool No.1 220kV line on loss of Ballarat to Moorabool No.2 220kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>SML_BUDP_1 | 2008-07-01 | 1 | Outage = Buronga to Balranald to Darlington Pt (X5) line, limit Murraylink from Vic to SA to avoid overloading Ballarat to Horsham line on loss of Bendigo to Kerang line
V>SML_BUDP_2 | 2008-07-01 | 1 | Out = Buronga to Balranald to Darlington Pt (X5) line, limit Murraylink from Vic to SA to avoid O/L Bendigo to Kerang line on loss of Ballarat to Horsham line
V>SML_BUDP_3 | 2008-07-01 | 1 | Out = Buronga to Balranald to Darlington Pt (X5) line, limit Murraylink from Vic to SA to avoid O/L Kerang to Red Cliffs line on loss of Ballarat to Horsham line
V>SML_MHCB6152+BETX | 2007-07-13 | 1 | Out = Monash CB6152 and one Berri 132/66 kV transformer T1 with Berri Isolator A6307 closed; limit Victoria to SA on Murraylink to prevent Monash transformer O/L on trip North West Bend - Monash - Berri #2 lines.
V>SML_NIL_1 | 2008-07-02 | 1 | Outage = Nil, limit Vic to SA on Murraylink to avoid overloading Ballarat to Moorabool No.1 220 kV line for loss of Ballarat to Moorabool No.2 220 kV line, Murraylink VFRB enabled and Murraylink > 25MW
V>SML_NIL_8 | 2008-07-02 | 1 | Outage = Nil, limit Vic to SA on Murraylink to avoid overloading Ballarat to Bendigo 220 kV line for loss of Bendigo to Shepparton 220 kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>SML_NSWRB_10 | 2008-07-02 | 1 | Outage = NSW Murraylink runback scheme, limit Vic to SA on Murraylink to avoid overloading Kerang to Redcliffs 220 kV line for loss of Balranand to Darlington Point (X5/1) 220 kV line
V>SML_NSWRB_9 | 2008-07-02 | 1 | Outage = NSW Murraylink runback scheme, limit Vic to SA on Murraylink to avoid overloading Bendigo to Kerang 220 kV line for loss of Balranand to Darlington Point (X5/1) 220 kV line
V>SML_NWCB6021_NWMH2 | 2006-06-27 | 1 | Out= North West Bend_CB6021 with Run back OFF; limit Victoria to SA on Murraylink to avoid Monash - North West Bend#2 O/L on trip Monash - North West Bend# 1.
V>SML_NWCB6021_TX1 | 2006-06-27 | 1 | Out= North West Bend_CB6021; limit Victoria to SA on Murraylink to avoid North West Bend transformer#1 O/L on trip NWB - MWP #1.
V>SML_NWCB6021_TX3 | 2006-06-27 | 1 | Out= North West Bend_CB6021; limit Victoria to SA on Murraylink to avoid NWB transformer#3 O/L on trip Robertstown - NWB # 1.
V>SML_NWCB6022_NWMH2 | 2006-06-09 | 1 | Out= North West Bend_CB6022 with Run back OFF; limit Victoria to SA on Murraylink to avoid Monash - North West Bend#2 O/L on trip Monash - North West Bend# 1.
V>SML_NWCB6022_TX1 | 2006-06-09 | 1 | Out= North West Bend_CB6022; limit Victoria to SA on Murraylink to avoid North West Bend transformer#1 O/L on trip North West Bend transformer# 3.
V>SML_NWCB6022_TX1_2 | 2006-06-09 | 1 | Out= North West Bend_CB6022; Minimum Victoria to SA on Murraylink to avoid North West Bend transformer#1 O/L on trip North West Bend transformer# 3.
V>SML_NWCB6023_TX2 | 2007-07-13 | 2 | Out= North West Bend_CB6023; limit Victoria to SA on Murraylink to avoid North West Bend transformer#2 O/L on trip NWB - Robertstown line.
V>SML_NWCB6024+25 | 2007-02-16 | 1 | Out= North West Bend_CBs 6024 and 6025; limit Victoria to SA on Murraylink to avoid North West Bend transformer#1 O/L on trip NWB - Monash #1 line.
V>SML_NWCB6024_MHNW2 | 2006-08-28 | 1 | Out= North West Bend_CB6024; limit Vic to SA on Murraylink to avoid Monash - North West Bend #2 line O/L on trip Monash - North West Bend line #1.
V>SML_NWCB6024_NWTX1 | 2006-08-28 | 1 | Out= North West Bend_CB6024 with Run back OFF; limit Victoria to SA on Murraylink to avoid North West Bend transformer #1 O/L on trip Monash - North West Bend line #1.
V>SML_NWCB6025_MHNW2 | 2007-04-30 | 1 | Out= North West Bend_CB6025 with Run back OFF; limit Victoria to SA on Murraylink to avoid Monash - North West Bend line #2 O/L on trip Monash - North West Bend line #1.
V>SML_NWCB6025_NWMP1 | 2006-08-28 | 1 | Out= North West Bend_CB6025; limit Vic to SA on Murraylink to avoid North West Bend-MWP1line O/L on trip North West Bend transformer # 3.
V>SML_NWCB6033_TX2 | 2007-02-14 | 1 | Out= North West Bend_CB6033; limit Victoria to SA on Murraylink to avoid North West Bend transformer#2 O/L on trip NWB - Monash #2 line.
V>SML_NWCB6225X_TX1 | 2007-06-21 | 2 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225 and 66 kV circuit breaker CB5605; limit Victoria to SA on Murraylink to avoid North West Bend transformer#1 O/L on trip NWB - MWP #1 line.
V>SML_NWCB6225_TX1 | 2007-01-04 | 1 | Out= North West Bend_CB6225; limit Victoria to SA on Murraylink to avoid North West Bend transformer#1 O/L on trip NWB - MWP #1.
V>SML_NWRB_NWMWP1 | 2007-04-30 | 1 | Out=NW_RB line, V-SA on ML to avoid OL NWB to MWP1 132 kV line.
V>SML_NWTXCB23_MHNW1 | 2006-08-28 | 1 | Out= North West Bend_CB6023 and Transformer #2; limit Vic to SA on Murraylink to avoid North West Bend-Monash#1 line O/L on trip North West Bend transformer # 1.
V>SML_NWTXCB23_NWRB1 | 2007-04-30 | 1 | Out= North West Bend_CB6023 and Transformer #2 with Run back OFF; limit Victoria to SA on Murraylink to avoid North West Bend-Robertstown line #1 O/L on trip North West Bend-MWP1 line.
V>SML_SMTXF2_4 | 2008-07-01 | 1 | Outage = South Morang 500/330kV (F2) transformer, limit Vic to SA on Murraylink to avoid O/L on Ballarat North to BGR (Buangor) 66 kV line for loss of Ballarat to Horsham 220 kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>SML_VFRB_7 | 2007-09-24 | 1 | Outage = Murraylink VFRB scheme, limit Vic to SA on Murraylink to avoid overload on the Ballarat North to BGR (Buangor) 66kV line for loss of the Ballarat to Horsham 220kV line
V>SSEPA2VC | 2005-06-28 | 1 | Out = SEVC+PAVC;Vic-SA Thermal(O/L) Tr Lmt(Trip.TB-SE275Fdr)
V>S_MHNW1_NWP1_NWMH2 | 2009-01-05 | 1 | Out=MH_NW1, RunBack OS, V-SA on ML, load on MH_NW2, MWP1_NW cont
V>S_MHNW1_NWRB_NWMH2 | 2009-01-05 | 1 | Out=MH_NW#1, RunBack OS, V-SA on ML, load on MH_NW2, NW_RB cont
V>S_NWP1_MHNW1_NWRB | 2009-01-06 | 1 | Out=MWP1_NW, RunBack OS, avoid O/L NW_RB line on trip MH_NW1 line.
V>S_NWRB2_NWRB1 | 2008-11-21 | 1 | Out = North West Bend to Robertstown No2 line, limit V-SA on ML, to avoid OL NWB to Robertstown No1 line
V>V1NIL | 2004-07-05 | 1 | Outage = Nil, limit Yallourn unit 1+Hazelwood units 1,2,6,7,8+Jeeralang+ Bairnsdale+Morwell to avoid overload on Hazelwood 500/220kV No.2,3,4 transformers for loss of one transformer, Yallourn unit 1 in 500kV mode, Hazelwood in radial mode.
V>V2NIL | 2004-07-05 | 1 | Outage = Nil, limit Hazelwood units 1,2,6,7,8, Jeeralang, Bairnsdale, Morwell generation to avoid overload on Hazelwood 500/220kV No.2,3,4 transformers for loss of one of these transformers, Yallourn unit 1 in 220kV mode and Hazelwood in radial mode.
V>V3NIL | 2002-03-14 | 1 | SYS NORM, HWTS TX LOAD-LOSS TX,YW1 220kV,6/2 PARALLEL
V>V_HWBUS2_1 | 2007-05-09 | 1 | Outage = Hazelwood No. 2 220 kV Bus, limit Yallourn unit 1+Hazelwood units 1,2,3,4,6,7,8+Jeeralang+ Bairnsdale+Morwell to avoid O/L on Hazelwood 500/220kV No.2,3,4 transformers for loss of a transformer, Yallourn unit 1 in 500kV mode, Radial
V>V_HWBUS2_2 | 2007-05-09 | 1 | Outage = Hazelwood No. 2 220 kV Bus, limit Hazelwood units 1,2,3,4,6,7,8+Jeeralang+ Bairnsdale+Morwell to avoid O/L on Hazelwood 500/220kV No.2,3,4 transformers for loss of a transformer, Yallourn unit 1 in 220kV mode, Radial
V>V_HWBUS2_PAR_3-5_A | 2007-05-09 | 2 | Outage = Hazelwood No. 2 220 kV Bus, limit Hazelwood units 1,2,3,4+JLGS A to avoid O/L on HWTS 500/220kV No.2 transformer for trip of HWPS-ROTS No.2 220kV line (also offloads No.1 line), 3-5 Parallel mode with Jeeralang A connected to HWPS #1 220kV bus
V>V_HWBUS2_PAR_3-5_B | 2007-05-09 | 2 | Outage = Hazelwood No. 2 220 kV Bus, limit Hazelwood units 1,2,3,4+JLGS B to avoid O/L on HWTS 500/220kV No.2 transformer for trip of HWPS-ROTS No.2 220kV line (also offloads No.1 line), 3-5 Parallel mode with Jeeralang B connected to HWPS #1 220kV bus
V>V_HWBUS2_PAR_6-2 | 2007-05-09 | 1 | Outage = Hazelwood No.2 220 kV bus, limit generation of Hazelwood units 1,2,3,4 to avoid overloading the Hazelwood No.2 500/220 kV transformer for loss of the Hazelwood to Rowville No.2 220 kV line, 6-2 Parallel
V>V_HWJL1-2_RAD_1 | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.1 or No.2 220kV line, limit Yallourn unit 1 +HWPS area gen to avoid O/L HWTS A3 Tx for trip of HWPS-JLTS No.2 or No.1 220kV line, Yallourn unit 1 in 500kV mode, Radial Mode with 1&2 busses tied (3&4 busses remain split)
V>V_HWJL1-2_RAD_2 | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.1 or No.2 220kV line, limit HWPS area gen to avoid O/L HWTS A3 Tx for trip of HWPS-JLTS No.2 or No.1 220kV line, Yallourn unit 1 in 220kV mode, Radial Mode with 1&2 busses tied (3&4 busses remain split)
V>V_HWJL1-2_RAD_3 | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.1 or No.2 220kV line, limit Yallourn unit 1 +HWPS area gen to avoid O/L HWTS A4 Tx for trip of HWPS-JLTS No.2 or No.1 220kV line, Yallourn unit 1 in 500kV mode, Radial Mode with 1&2 busses tied (3&4 busses remain split)
V>V_HWJL1-2_RAD_4 | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.1 or No.2 220kV line, limit HWPS area gen to avoid O/L HWTS A4 Tx for trip of HWPS-JLTS No.2 or No.1 220kV line, Yallourn unit 1 in 220kV mode, Radial Mode with 1&2 busses tied (3&4 busses remain split)
V>V_HWJL2_RADIAL_1 | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.2 220kV line, limit Yallourn unit 1 +Hazelwood area generation to avoid O/L Hazelwood A2 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_HWJL2_RADIAL_2 | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.2 220kV line, limit Hazelwood area generation to avoid O/L Hazelwood A2 transformer for trip of A3 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_HWJL2_RADIAL_3 | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.2 220kV line, limit Hazelwood units 3,4,5 to avoid overload of Hazelwood A1 transformer, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_HWJL2_RADIAL_5 | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.2 220kV line, limit Yallourn unit 1 +Hazelwood area generation to avoid O/L Hazelwood A3 transformer for trip of A4 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_HWJL2_RADIAL_6 | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.2 220kV line, limit Hazelwood area generation to avoid O/L Hazelwood A3 transformer for trip of A4 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_HWJL2_RADIAL_7 | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.2 220kV line, limit Yallourn unit 1 +Hazelwood area generation to avoid O/L Hazelwood A4 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_HWJL2_RADIAL_8 | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.2 220kV line, limit Hazelwood area generation to avoid O/L Hazelwood A4 transformer for trip of A3 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_HWJL3 | 2004-05-17 | 1 | Outage = Hazelwood to Jeeralang No.3 220kV line, limit Hazelwood units 1,2+Jeeralang+Bairnsdale+Morwell 1,2,3 to avoid overload on Hazelwood to Jeeralang No.4 220kV line for loss of the HWTS 500/220kV No.2 transformer, Hazelwood in radial mode.
V>V_HWJL3-4_RAD | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.3 or No.4 220kV line, limit HWPS units3,4,5 and Jeeralang A to avoid O/L HWTS A1 Tx for trip of HWPS-JLTS No.4 or No.3 220kV line, Radial Mode with 1&2 busses split and 3&4 busses split or tied
V>V_HWJL3-4_RAD_1-2 | 2009-02-11 | 1 | Outage = Hazelwood to Jeeralang No.3 or No.4 220kV line, limit HWPS units1,2,3,4,5 and Jeeralang A&B to avoid O/L HWTS A2 Tx for trip of HWPS-JLTS No.4 or No.3 220kV line, Radial Mode with 1&2 busses tied and 3&4 busses split or tied
V>V_HWJL4 | 2004-05-17 | 1 | Outage = Hazelwood to Jeeralang No.4 220kV line, limit Hazelwood units 1,2+Jeeralang+Bairnsdale+Morwell 1,2,3 to avoid overload on Hazelwood to Jeeralang No.3 220kV line for loss of the HWTS 500/220kV No.2 transformer, Hazelwood in radial mode.
V>V_HWTS_TX1_PAR_3-5 | 2006-09-06 | 1 | Out = Hazelwood #1 or #2 500/220kV transformer, 3-5 Parallel, Jeeralang split with JLGS B connected to Hazelwood #1 or #2 220kV bus, avoid O/L Hazelwood to Rowville #1 and #2 220kV lines for loss of Hazelwood #2 or #1 500/220kV transformer
V>V_HWTS_TX3_3-5_MOD | 2008-10-07 | 1 | Out = Hazelwood #3 or #4 500/220kV transformer, 3-5 Parallel, Jeeralang split with JLGS A connected to Hazelwood #3 or #4 220kV bus, avoid O/L Rowville to Yallourn #5, #6, #7or #8 220kV lines for loss of Hazelwood #4 or #3 500/220kV transformer
V>V_HWTS_TX3_PAR_3-5 | 2008-10-21 | 1 | Out = Hazelwood #3 or #4 500/220kV transformer, 3-5 Parallel, Jeeralang split with JLGS B connected to Hazelwood #3 or #4 220kV bus, avoid O/L Rowville to Yallourn #5, #6, #7or #8 220kV lines for loss of Hazelwood #4 or #3 500/220kV transformer
V>V_HWTX1_PAR_3-5_2 | 2006-10-05 | 1 | Out = Hazelwood #1 or #2 500/220kV transformer, 3-5 Parallel, Jeeralang split with JLGS A connected to Hazelwood #1 or #2 220kV bus, avoid O/L Hazelwood to Rowville #1 and #2 220kV lines for loss of Hazelwood #2 or #1 500/220kV transformer
V>V_HW_BUS3_RAD_1 | 2009-02-11 | 1 | Outage = Hazelwood No.3 220kV bus, limit Yallourn unit 1+Hazelwood area generation to avoid O/L Hazelwood A1 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,4 busses split
V>V_HW_BUS3_RAD_2 | 2009-02-11 | 1 | Outage = Hazelwood No.3 220kV bus, limit Hazelwood area generation to avoid O/L Hazelwood A1 transformer for trip of A3 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1,2,4 busses split
V>V_HW_BUS3_RAD_3 | 2009-02-11 | 1 | Outage = Hazelwood No.3 220kV bus, limit Yallourn unit 1 +Hazelwood area generation to avoid O/L Hazelwood A2 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,4 busses split
V>V_HW_BUS3_RAD_4 | 2009-02-11 | 1 | Outage = Hazelwood No.3 220kV bus, limit Hazelwood area generation to avoid O/L Hazelwood A2 transformer for trip of A3 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1,2,4 busses split
V>V_HW_BUS3_RAD_5 | 2009-02-11 | 1 | Outage = Hazelwood No.3 220kV bus, limit Yallourn unit 1 +Hazelwood area generation to avoid O/L Hazelwood A3 transformer for trip of A2 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,4 busses split
V>V_HW_BUS3_RAD_6 | 2009-02-11 | 1 | Outage = Hazelwood No.3 220kV bus, limit Hazelwood area generation to avoid O/L Hazelwood A3 transformer for trip of A2 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1,2,4 busses split
V>V_HW_BUS3_RAD_7 | 2009-02-11 | 1 | Outage = Hazelwood No.3 220kV bus, limit Yallourn unit 1 +Hazelwood area generation to avoid O/L Hazelwood A4 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,4 busses split
V>V_HW_BUS3_RAD_8 | 2009-02-11 | 1 | Outage = Hazelwood No.3 220kV bus, limit Hazelwood area generation to avoid O/L Hazelwood A4 transformer for trip of A3 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1,2,4 busses split
V>V_JLTS_CB_1 | 2007-02-20 | 1 | Outage = Jeeralang TS (JLTS) to Morwell TS (MWTS) line 1 or line 2 to bus 1 220kV CB, limit Hazelwood units 1,2+Jeeralang B to avoid overload of HWTS 500/220kV No.2 transformer for trip of JLTS-MWTS line 2 or line 1 to bus 1 220kV CB, Radial
V>V_NIL_4 | 2005-11-07 | 1 | Outage = Nil, limit Hazelwood units 3,4,5 to avoid overload on Hazelwood 500/220kV No.1 transformer, Hazelwood in radial mode.
V>V_NIL_HW3-BUS1_1 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 500kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 3 on HWPS #1 bus
V>V_NIL_HW3-BUS1_2 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 220kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 3 on HWPS #1 bus
V>V_NIL_HW3-BUS1_3 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 500kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 3 on HWPS #1 bus
V>V_NIL_HW3-BUS1_4 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 220kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 3 on HWPS #1 bus
V>V_NIL_HW4-BUS1_1 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 500kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 4 on HWPS #1 bus
V>V_NIL_HW4-BUS1_2 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 220kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 4 on HWPS #1 bus
V>V_NIL_HW4-BUS1_3 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 500kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 4 on HWPS #1 bus
V>V_NIL_HW4-BUS1_4 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 220kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 4 on HWPS #1 bus
V>V_NIL_RADIAL_1 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_NIL_RADIAL_1-2_1 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1&2 busses tied (3&4 busses remain split)
V>V_NIL_RADIAL_1-2_2 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1&2 busses tied (3&4 busses remain split)
V>V_NIL_RADIAL_1-2_3 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1&2 busses tied (3&4 busses remain split)
V>V_NIL_RADIAL_1-2_4 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1&2 busses tied (3&4 busses remain split)
V>V_NIL_RADIAL_1-2_5 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A3 transformer for trip of A4 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1&2 busses tied (3&4 busses remain split)
V>V_NIL_RADIAL_1-2_6 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A3 transformer for trip of A4 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1&2 busses tied (3&4 busses remain split)
V>V_NIL_RADIAL_1-2_7 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A4 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1&2 busses tied (3&4 busses remain split)
V>V_NIL_RADIAL_1-2_8 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A4 transformer for trip of A3 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1&2 busses tied (3&4 busses remain split)
V>V_NIL_RADIAL_2 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_NIL_RADIAL_3 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_NIL_RADIAL_3-4_1 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 3&4 busses tied (1&2 busses remain split)
V>V_NIL_RADIAL_3-4_2 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 3&4 busses tied (1&2 busses remain split)
V>V_NIL_RADIAL_3-4_3 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 3&4 busses tied (1&2 busses remain split)
V>V_NIL_RADIAL_3-4_4 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 3&4 busses tied (1&2 busses remain split)
V>V_NIL_RADIAL_3-4_5 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A3 transformer for trip of A4 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 3&4 busses tied (1&2 busses remain split)
V>V_NIL_RADIAL_3-4_6 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A3 transformer for trip of A4 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 3&4 busses tied (1&2 busses remain split)
V>V_NIL_RADIAL_3-4_7 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A4 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 3&4 busses tied (1&2 busses remain split)
V>V_NIL_RADIAL_3-4_8 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A4 transformer for trip of A3 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 3&4 busses tied (1&2 busses remain split)
V>V_NIL_RADIAL_4 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_NIL_RADIAL_5 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A3 transformer for trip of A4 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_NIL_RADIAL_6 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A3 transformer for trip of A4 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_NIL_RADIAL_7 | 2009-02-05 | 1 | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A4 transformer for trip of A3 transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_NIL_RADIAL_8 | 2009-02-05 | 1 | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A4 transformer for trip of A3 transformer, Yallourn unit 1 in 220kV mode, Hazelwood Radial Mode with 1,2,3,4 busses split
V>V_NIL_RADIAL_9 | 2009-09-06 |  | Outage = Nil, limit Yallourn unit 1 + Hazelwood G6 + Bairnsdale + Morwell to avoid O/L Hazelwood - Jeeralang No. 4 220 kV line for trip of Hazelwood A4 500/220 kV transformer, Yallourn unit 1 in 500kV mode, Hazelwood Radial Mode with 3,4 busses split.
V>V_XEPMB | 2007-04-30 | 1 | Outage = Both Eildon to Mt Beauty 220kV lines, limit Southern Hydro generation to avoid overloading either Dederang to Mt Beauty 220kV line for trip of one the lines
V>V_X_JLTS_CB | 2007-02-20 | 1 | Outage = Jeeralang TS (JLTS) to Morwell TS (MWTS) line 1 AND line 2 to bus 1 220kV CB's, limit Hazelwood units 1,2+Jeeralang B to avoid pre-contingent overload of HWTS 500/220kV No.2 transformer, Radial
VN::DDMS | 2008-07-01 | 1 | Outage = Dederang to Murray 330kV line, limit VIC to NSW to avoid transient instability for fault and trip of Dederang to Murray 330kV line, equation 2.1 from TLM-D
VN_0000 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 0 MW
VN_0050 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 50 MW
VN_0100 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 100 MW
VN_0150 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 150 MW
VN_0200 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 200 MW
VN_0250 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 250 MW
VN_0300 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 300 MW
VN_0350 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 350 MW
VN_0400 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 400 MW
VN_0450 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 450 MW
VN_0500 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 500 MW
VN_0550 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 550 MW
VN_0600 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 600 MW
VN_0650 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 650 MW
VN_0700 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 700 MW
VN_0750 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 750 MW
VN_0800 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 800 MW
VN_0850 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 850 MW
VN_0900 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 900 MW
VN_0950 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 950 MW
VN_1000 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 1000 MW
VN_1050 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 1050 MW
VN_1100 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 1100 MW
VN_1200 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer upper limit of 1200 MW
VN_1300 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 1300 MW
VN_1400 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 1400 MW
VN_1500 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 1500 MW
VN_1550 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 1550 MW
VN_1600 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 1600 MW
VN_1700 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 1700 MW
VN_1800 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 1800 MW
VN_1900 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 1900 MW
VN_2000 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 2000 MW
VN_2100 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 2100 MW
VN_2200 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 2200 MW
VN_2300 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 2300 MW
VN_2400 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 2400 MW
VN_2500 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 2500 MW
VN_2600 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 2600 MW
VN_2700 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 2700 MW
VN_2800 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 2800 MW
VN_2900 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 2900 MW
VN_3000 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 3000 MW
VN_3100 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 3100 MW
VN_3200 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 3200 MW
VN_3300 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 3300 MW
VN_3400 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 3400 MW
VN_3500 | 2008-07-01 | 1 | Discretionary Vic to NSW transfer limit of 3500 MW
VN_ZERO | 2009-02-05 | 1 | VIC to NSW upper transfer limit of zero MW
VS:HYBT | 2004-01-21 | 1 | Outage = Heywood 275kV bustie open, limit Vic to South Australia to avoid transient instability for fault and trip of a Heywood to Moorabool 500kV line
VSML_-010 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of -10 MW
VSML_-020 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of -20 MW
VSML_-030 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of -30 MW
VSML_-040 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of -40 MW
VSML_-050 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of -50 MW
VSML_-060 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of -60 MW
VSML_-070 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of -70 MW
VSML_-080 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of -80 MW
VSML_-090 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of -90 MW
VSML_-100 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of -100 MW
VSML_000 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 0 MW
VSML_010 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 10 MW
VSML_015 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 15 MW
VSML_020 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 20 MW
VSML_030 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 30 MW
VSML_040 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 40 MW
VSML_060 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 60 MW
VSML_080 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 80 MW
VSML_100 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 100 MW
VSML_120 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 120 MW
VSML_140 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 140 MW
VSML_160 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 160 MW
VSML_180 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 180 MW
VSML_200 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 200 MW
VSML_210 | 2008-08-05 | 1 | Vic to SA on Murraylink upper transfer limit of 210 MW
VSML_220 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 220 MW
VSML_240 | 2008-08-05 | 1 | Vic to SA on ML upper transfer limit of 240 MW
VSML_VFRB_OFF | 2008-09-10 | 1 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only
VSS_000 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 0 MW
VSS_020 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 20 MW
VSS_040 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 40 MW
VSS_060 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 60 MW
VSS_080 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 80 MW
VSS_100 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 100 MW
VSS_120 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 120 MW
VSS_140 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 140 MW
VSS_160 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 160 MW
VSS_180 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 180 MW
VSS_200 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 200 MW
VSS_220 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 220 MW
VSS_240 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 240 MW
VSS_260 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 260 MW
VSS_280 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 280 MW
VSS_300 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 300 MW
VSS_320 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 320 MW
VSS_340 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 340 MW
VSS_360 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 360 MW
VSS_380 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 380 MW
VSS_400 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 400 MW
VSS_420 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 420 MW
VSS_440 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 440 MW
VSS_460 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 460 MW
VSS_480 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 480 MW
VSS_500 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 500 MW
VSS_550 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 550 MW
VSS_600 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 600 MW
VSS_620 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 620MW
VSS_650 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 650 MW
VSS_700 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 700 MW
VSS_720 | 2008-08-05 | 1 | Vic to SA on Vic-SA + ML upper transfer limit of 720 MW
VS_000 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 0 MW
VS_020 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 20 MW
VS_020_MIN | 2002-07-11 | 1 | Victoria to SA on VicSA minmum transfer limit of 20 MW
VS_040 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 40 MW
VS_050 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 50 MW
VS_050_MIN | 2002-07-11 | 1 | Victoria to SA on VicSA minmum transfer limit of 50 MW
VS_060 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 60 MW
VS_080 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 80 MW
VS_100 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 100 MW
VS_110 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 110 MW
VS_120 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 120 MW
VS_130 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 130 MW
VS_140 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 140 MW
VS_150 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 150 MW
VS_160 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 160 MW
VS_170 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 170 MW
VS_180 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 180 MW
VS_190 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 190 MW
VS_200 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 200 MW
VS_210 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 210 MW
VS_220 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 220 MW
VS_230 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 230 MW
VS_240 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 240 MW
VS_250 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 250 MW
VS_260 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 260 MW
VS_280 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 280 MW
VS_290 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 290 MW
VS_300 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 300 MW
VS_320 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 320 MW
VS_330 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 330 MW
VS_340 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 340 MW
VS_350 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 350 MW
VS_360 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 360 MW
VS_370 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 370 MW
VS_380 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 380 MW
VS_385 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 385 MW
VS_400 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 400 MW
VS_410 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 410 MW
VS_420 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 420 MW
VS_430 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 430 MW
VS_435 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 435 MW
VS_440 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 440 MW
VS_450 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 450 MW
VS_460 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 460 MW
VS_470 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 470 MW
VS_480 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 480 MW
VS_485 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 485 MW
VS_490 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 490 MW
VS_495 | 2008-08-05 | 1 | Victoria to SA on VicSA upper transfer limit of 495 MW
VS_HYCPBT | 2004-01-21 | 1 | Outage = Heywood 275kV capacitor off and bustie open, limit Vic to South Australia to avoid voltage collapse for loss of a Heywood to Moorabool 500kV line
VTBL_ROC | 2006-12-27 | 1 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink
VT_000 | 2008-08-05 | 1 | Vic to Tas on Basslink upper limit of 0 MW
VT_050 | 2008-08-05 | 1 | Vic to Tas on Basslink upper limit of 50 MW
VT_100 | 2008-08-05 | 1 | Vic to Tas on Basslink upper limit of 100 MW
VT_150 | 2008-08-05 | 1 | Vic to Tas on Basslink upper limit of 150 MW
VT_200 | 2008-08-05 | 1 | Vic to Tas on Basslink upper limit of 200 MW
VT_250 | 2008-08-05 | 1 | Vic to Tas on Basslink upper limit of 250 MW
VT_300 | 2008-08-05 | 1 | Vic to Tas on Basslink upper limit of 300 MW
VT_350 | 2008-08-05 | 1 | Vic to Tas on Basslink upper limit of 350 MW
VT_400 | 2008-08-05 | 1 | Vic to Tas on Basslink upper limit of 400 MW
VT_450 | 2008-08-05 | 1 | Vic to Tas on Basslink upper limit of 450 MW
VT_480 | 2008-08-05 | 1 | Vic to Tas on Basslink upper limit of 480 MW
V^SML_NIL_3 | 2008-07-02 | 1 | Outage = Nil, limit Vic to SA on Murraylink to avoid voltage collapse for loss of Bendigo to Kerang 220kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V^SML_NSWRB_2 | 2007-07-12 | 1 | Outage = NSW Murraylink runback scheme, limit Vic to SA on Murraylink to avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line
V^SML_RCTS220CAPAUTO | 2006-01-12 | 1 | Outage = Nil with one Redcliffs 220kV capacitor bank unavailable for auto switching, limit Vic to SA on Murraylink to avoid voltage collapse for a range of contingencies
V^SML_RCTS220CAPSAUT | 2006-01-12 | 1 | Outage = Nil with both Redcliffs 220kV capacitor banks unavailable for auto switching, limit Vic to SA on Murraylink to avoid voltage collapse for a range of contingencies
V^S_HYCP | 2004-01-14 | 1 | Outage = Nil, limit Vic to SA to avoid voltage collapse for loss of a Moorabool to Heywood 500 kV line with automatic allowance for Heywood 275 kV capacitor bank status
V^S_SEVC12 | 2006-06-27 | 1 | Out= Both South East SVCs; limit Victoria to SA to control voltage change at South East 132 kV substation.
V^^N_MSBT | 2008-07-01 | 1 | Out= MSS Bus tie CB, volt dev at Jindera on MSS Bus tie CB trip
V^^S_KHTB1+2 | 2006-09-14 | 1 | Out = Keith -Thailem Bend 132 kV lines 1 and 2; Vic-SA limit for voltage stability Limit.
V^^S_SETB_SETB | 2007-12-20 | 1 | Out= one South East to Tailem Bend 275kV line, Vic-SA Voltage stability limit for loss of the remaining South East to Tailem Bend line
V^^S_XSE_VC+CP | 2007-05-15 | 1 | Out = South East one SVC and 100MVAr capacitor bank; Vic-SA Voltage Stability limit for loss of one NPS unit following 2PhG fault on the Davenport - NPS line.
V_APPT | 2004-08-27 | 1 | Anglesea PS upper limit set to zero due to outage of Anglesea PS to Port Henry 220 kV line
V_EILDON_000 | 2008-06-11 | 2 | Discretionary upper limit for Eildon generation of 0 MW
V_HWMW | 2004-08-27 | 1 | Morwell Units 4 & 5 upper limit set to zero due to outage of Hazelwood PS to Morwell PS 220 kV line
V_HWPS_BUS2 | 2007-05-09 | 1 | Hazelwood PS Unit 5 upper limit set to zero due to outage of Hazelwood No 2 220 kV Bus
V_HW_BUS1 | 2004-08-27 | 1 | Hazelwood PS Units 1 & 2 upper limit set to zero due to outage of Hazelwood No 1 220 kV Bus
V_HW_BUS2 | 2004-08-27 | 1 | Hazelwood PS Unit 5 upper limit set to zero due to outage of Hazelwood No 2 220 kV Bus
V_HW_BUS3 | 2004-08-27 | 1 | Hazelwood PS Units 7 & 8 upper limit set to zero due to outage of Hazelwood No 3 220 kV Bus
V_HW_BUS4 | 2004-08-27 | 1 | Hazelwood PS Unit 6 upper limit set to zero due to outage of Hazelwood No 4 220 kV Bus
V_JLGSB_160 | 2005-08-22 | 1 | Discretionary upper limit on Jeeralang B of 160 MW
V_JLGSB_165 | 2005-08-22 | 1 | Discretionary upper limit on Jeeralang B of 165 MW
V_JLGSB_185 | 2005-08-22 | 1 | Discretionary upper limit on Jeeralang B of 185 MW
V_JLGSB_200 | 2006-06-21 | 1 | Discretionary upper limit on Jeeralang B of 200 MW
V_JLGSB_220 | 2006-06-21 | 1 | Discretionary upper limit on Jeeralang B of 220 MW
V_JLGS_0 | 2005-09-09 | 1 | Discretionary upper limit on Jeeralang (A+B) of 0 MW
V_JLGS_160 | 2005-08-22 | 1 | Discretionary upper limit on Jeerlang (A+B) generation of 160 MW
V_JLGS_165 | 2005-08-22 | 1 | Discretionary upper limit on Jeerlang (A+B) generation of 165 MW
V_JLGS_180 | 2005-08-22 | 1 | Discretionary upper limit on Jeerlang (A+B) generation of 180 MW
V_JLGS_185 | 2005-08-22 | 1 | Discretionary upper limit on Jeerlang (A+B) generation of 185 MW
V_JLGS_200 | 2005-08-22 | 1 | Discretionary upper limit on Jeerlang (A+B) generation of 200 MW
V_JL_BUS1 | 2007-03-01 | 1 | Jeeralang B GS upper limit set to zero due to outage of Jeeralang TS No 1 220 kV Bus
V_JL_BUS2 | 2007-03-01 | 1 | Jeeralang A GS upper limit set to zero due to outage of Jeeralang TS No 2 220 kV Bus
V_JL_JLA | 2007-03-01 | 1 | Jeeralang A PS upper limit set to zero due to outage of Jeeralang TS to Jeeralang A GS 220 kV line
V_JL_JLB | 2007-03-01 | 1 | Jeeralang B PS upper limit set to zero due to outage of Jeeralang TS to Jeeralang B GS 220 kV line
V_KIEWA_000 | 2007-04-03 | 1 | Discretionary upper limit for Kiewa area Generation of 0 MW
V_KIEWA_040 | 2007-03-19 | 1 | Discretionary upper limit for Kiewa area Generation of 40 MW
V_KIEWA_045 | 2007-04-04 | 1 | Discretionary upper limit for Kiewa area Generation of 45 MW
V_LAVNTH_160 | 2007-12-17 | 1 | Out= Altona 220kV bus (either #2 or #3), limit Laverton Nth to output of one unit
V_LV5_3000 | 2007-09-12 | 1 | 3000MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3050 | 2007-09-12 | 1 | 3050MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3100 | 2007-09-12 | 1 | 3100MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3150 | 2007-09-12 | 1 | 3150MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3200 | 2007-09-12 | 1 | 3200MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3250 | 2007-09-12 | 1 | 3250MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3300 | 2007-09-12 | 1 | 3300MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3350 | 2007-09-12 | 1 | 3350MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3400 | 2007-09-12 | 1 | 3400MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3450 | 2007-09-12 | 1 | 3450MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3500 | 2007-09-12 | 1 | 3500MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3550 | 2007-09-12 | 1 | 3550MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3600 | 2007-09-12 | 1 | 3600MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3650 | 2007-09-12 | 1 | 3650MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3700 | 2007-09-12 | 1 | 3700MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3750 | 2007-09-12 | 1 | 3750MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3800 | 2007-09-12 | 1 | 3800MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3850 | 2007-09-12 | 1 | 3850MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3900 | 2007-09-12 | 1 | 3900MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_3950 | 2007-09-12 | 1 | 3950MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4000 | 2007-09-06 | 1 | 4000MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4050 | 2007-09-06 | 1 | 4050MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4100 | 2007-09-06 | 1 | 4100MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4150 | 2007-09-06 | 1 | 4150MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4200 | 2007-09-06 | 1 | 4200MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4250 | 2007-09-06 | 1 | 4250MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4300 | 2007-09-06 | 1 | 4300MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4350 | 2007-09-06 | 1 | 4350MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4400 | 2007-09-06 | 1 | 4400MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4450 | 2007-09-06 | 1 | 4450MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4500 | 2007-09-06 | 1 | 4500MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4550 | 2007-09-06 | 1 | 4550MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4600 | 2007-09-06 | 1 | 4600MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4650 | 2007-09-06 | 1 | 4650MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4700 | 2007-09-06 | 1 | 4700MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4750 | 2007-09-06 | 1 | 4750MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4800 | 2007-09-06 | 1 | 4800MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4850 | 2007-09-06 | 1 | 4850MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4900 | 2007-09-06 | 1 | 4900MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_4950 | 2007-09-06 | 1 | 4950MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_5000 | 2007-09-06 | 1 | 5000MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_5050 | 2007-09-06 | 1 | 5050MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_5100 | 2007-09-06 | 1 | 5100MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_5150 | 2007-09-06 | 1 | 5150MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_5200 | 2007-09-06 | 1 | 5200MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_5250 | 2007-09-06 | 1 | 5250MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_5300 | 2007-09-06 | 1 | 5300MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_5350 | 2007-09-06 | 1 | 5350MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_5400 | 2007-09-06 | 1 | 5400MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_5450 | 2007-09-06 | 1 | 5450MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV5_5500 | 2007-09-06 | 1 | 5500MW upper limit on Latrobe Valley generation excluding Yallourn units 2,3,4 and Basslink
V_LV6_3000 | 2007-09-12 | 1 | 3000 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3050 | 2007-09-12 | 1 | 3050 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3100 | 2007-09-12 | 1 | 3100 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3150 | 2007-09-12 | 1 | 3150 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3200 | 2007-09-12 | 1 | 3200 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3250 | 2007-09-12 | 1 | 3250 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3300 | 2007-09-12 | 1 | 3300 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3350 | 2007-09-12 | 1 | 3350 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3400 | 2007-09-12 | 1 | 3400 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3450 | 2007-09-12 | 1 | 3450 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3500 | 2007-09-12 | 1 | 3500 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3550 | 2007-09-12 | 1 | 3550 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3600 | 2007-09-12 | 1 | 3600 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3650 | 2007-09-12 | 1 | 3650 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3700 | 2007-09-12 | 1 | 3700 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3750 | 2007-09-12 | 1 | 3750 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3800 | 2007-09-12 | 1 | 3800 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3850 | 2007-09-12 | 1 | 3850 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3900 | 2007-09-12 | 1 | 3900 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_3950 | 2007-09-12 | 1 | 3950 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4000 | 2007-09-06 | 1 | 4000 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4050 | 2007-09-06 | 1 | 4050 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4100 | 2007-09-06 | 1 | 4100 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4150 | 2007-09-06 | 1 | 4150 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4200 | 2007-09-06 | 1 | 4200 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4250 | 2007-09-06 | 1 | 4250 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4300 | 2007-09-06 | 1 | 4300 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4350 | 2007-09-06 | 1 | 4350 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4400 | 2007-09-06 | 1 | 4400 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4450 | 2007-09-06 | 1 | 4450 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4500 | 2007-09-06 | 1 | 4500 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4550 | 2007-09-06 | 1 | 4550 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4600 | 2007-09-06 | 1 | 4600 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4650 | 2007-09-06 | 1 | 4650 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4700 | 2007-09-06 | 1 | 4700 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4750 | 2007-09-06 | 1 | 4750 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4800 | 2007-09-06 | 1 | 4800 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4850 | 2007-09-06 | 1 | 4850 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4900 | 2007-09-06 | 1 | 4900 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_4950 | 2007-09-06 | 1 | 4950 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV6_5000 | 2007-09-06 | 1 | 5000 MW upper limit on Latrobe Valley generation and Basslink excluding Yallourn units
V_LV_3500 | 2007-09-06 | 1 | 3500 MW upper limit on Latrobe Valley generation and Basslink
V_LV_3750 | 2007-09-06 | 1 | 3750 MW upper limit on Latrobe Valley generation and Basslink
V_LV_4000 | 2007-09-06 | 1 | 4000 MW upper limit on Latrobe Valley generation and Basslink
V_LV_4250 | 2006-01-31 | 1 | 4250 MW upper limit on Latrobe Valley generation
V_LV_4500 | 2007-09-06 | 1 | 4500 MW upper limit on Latrobe Valley generation and Basslink
V_LV_4750 | 2007-09-06 | 1 | 4750 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5000 | 2007-09-06 | 1 | 5000 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5050 | 2006-01-31 | 1 | 5050 MW upper limit on Latrobe Valley generation
V_LV_5100 | 2007-09-06 | 1 | 5100 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5150 | 2007-09-06 | 1 | 5150 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5200 | 2007-09-06 | 1 | 5200 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5250 | 2007-09-06 | 1 | 5250 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5300 | 2007-09-06 | 1 | 5300 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5350 | 2007-09-06 | 1 | 5350 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5400 | 2007-09-06 | 1 | 5400 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5450 | 2007-09-06 | 1 | 5450 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5500 | 2007-09-06 | 1 | 5500 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5550 | 2007-09-06 | 1 | 5550 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5600 | 2007-09-06 | 1 | 5600 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5650 | 2007-09-06 | 1 | 5650 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5700 | 2007-09-06 | 1 | 5700 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5750 | 2007-09-06 | 1 | 5750 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5800 | 2007-09-06 | 1 | 5800 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5850 | 2007-09-06 | 1 | 5850 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5900 | 2007-09-06 | 1 | 5900 MW upper limit on Latrobe Valley generation and Basslink
V_LV_5950 | 2007-09-06 | 1 | 5950 MW upper limit on Latrobe Valley generation and Basslink
V_LV_6000 | 2007-09-06 | 1 | 6000 MW upper limit on Latrobe Valley generation and Basslink
V_LY_BUS1 | 2005-04-28 | 1 | Loy Yang Unit A1 upper limit set to zero due to outage of Loy Yang No 1 500 kV Bus
V_LY_BUS2 | 2004-08-27 | 1 | Loy Yang Unit A4 upper limit set to zero due to outage of Loy Yang No 2 500 kV Bus
V_LY_BUS3 | 2006-01-31 | 1 | Loy Yang Gas PS upper limit set to zero due to outage of Loy Yang No 3 500 kV Bus
V_LY_BUS4 | 2004-08-27 | 1 | Loy Yang Unit B1 upper limit set to zero due to outage of Loy Yang No 4 500 kV Bus
V_LY_TX | 2007-03-01 | 1 | Valley Power GS upper limit set to zero due to outage of Loy Yang 500/220 kV Transformer
V_MBMK | 2007-03-01 | 1 | McKay Creek PS upper limit set to zero due to outage of Mt Beauty to Mackay 220 kV line
V_MBWK | 2007-03-01 | 1 | West Kiewa PS upper limit set to zero due to outage of Mt Beauty to West Kiewa 220 kV line
V_MB_BUS1 | 2007-06-13 | 2 | McKay Creek and West Kiewa PSs upper limit set to zero due to outage of Mt Beauty No 1 220 kV Bus
V_MB_BUS2 | 2007-06-13 | 2 | Dartmouth PS upper limit set to zero due to outage of Mt Beauty No 2 220 kV Bus
V_N_VH0700 | 2008-07-01 | 1 | Snowy abolition constraint for discretionary Victoria to Snowy transfer upper limit of 700 MW
V_N_VH0900 | 2008-07-01 | 1 | Snowy abolition constraint for discretionary Victoria to Snowy transfer upper limit of 900 MW
V_N_VH1000 | 2008-07-01 | 1 | Snowy abolition version of Discretionary Victoria to Snowy transfer upper limit of 1000 MW
V_STHN_HYDRO_000 | 2004-07-05 | 1 | Discretionary upper limit for Southern Hydro Generation of 0 MW
V_STHN_HYDRO_050 | 2004-07-05 | 1 | Discretionary upper limit for Southern Hydro Generation of 50 MW
V_STHN_HYDRO_100 | 2004-07-05 | 1 | Discretionary upper limit for Southern Hydro Generation of 100 MW
V_STHN_HYDRO_150 | 2004-07-05 | 1 | Discretionary upper limit for Southern Hydro Generation of 150 MW
V_STHN_HYDRO_200 | 2004-07-05 | 1 | Discretionary upper limit for Southern Hydro Generation of 200 MW
V_STHN_HYDRO_250 | 2004-07-05 | 1 | Discretionary upper limit for Southern Hydro Generation of 250 MW
V_STHN_HYDRO_300 | 2004-07-05 | 1 | Discretionary upper limit for Southern Hydro Generation of 300 MW
V_STHN_HYDRO_350 | 2004-07-05 | 1 | Discretionary upper limit for Southern Hydro Generation of 350 MW
V_T_FCSPS_RAMP | 2007-02-06 | 1 | Ramp down (200 MW per DI) Basslink (Vic to Tas) for outage of FCSPS
V_T_NIL_BL1 | 2008-05-26 | 1 | Out=Nil, Basslink no go zone limits Vic to Tas
V_T_NIL_FCSPS | 2008-04-22 | 1 | Basslink limit from Vic to Tas for load enabled for FCSPS
V_YP_BUS1 | 2004-08-27 | 1 | Yallourn W Unit 4 upper limit set to zero due to outage of Yallourn PS No 1 220 kV Bus
V_YP_BUS2 | 2004-08-27 | 1 | Yallourn W Unit 2 upper limit set to zero due to outage of Yallourn PS No 2 220 kV Bus
V_YW_1000 | 2008-09-10 | 1 | Discretionary Yallourn W generation limit 1000MW
V_YW_1050 | 2008-09-10 | 1 | Discretionary Yallourn W generation limit 1050MW
V_YW_1100 | 2008-09-10 | 1 | Discretionary Yallourn W generation limit 1100MW
V_YW_1150 | 2008-09-10 | 1 | Discretionary Yallourn W generation limit 1150MW
V_YW_1200 | 2008-09-10 | 1 | Discretionary Yallourn W generation limit 1200MW
V_YW_1250 | 2008-09-10 | 1 | Discretionary Yallourn W generation limit 1250MW
V_YW_1300 | 2008-09-10 | 1 | Discretionary Yallourn W generation limit 1300MW
V_YW_1350 | 2008-09-10 | 1 | Discretionary Yallourn W generation limit 1350MW
V_YW_1400 | 2008-09-10 | 1 | Discretionary Yallourn W generation limit 1400MW
V_YW_1450 | 2008-09-10 | 1 | Discretionary Yallourn W generation limit 1450MW
ZZZZZZ | 1998-12-13 | 1 | Constraint list out of bounds work-around
TV_594 |  |  | Thermal limit on Basslink used for market simulation
VT_478 |  |  | Thermal limit on Basslink used for market simulation
Q>N_1500 |  |  | Thermal limit on QNI for market simulation
Q_CS<2100 |  |  | New Central to South Queensland constraint including committed projects
SV_460 |  |  | SA to VIC on V-SA upper transfer limit to 460MW
Q>Q_SWQ |  |  | Notional South West Queensland Export Limit provided by Powerlink for the ANTS
N::Q_NIL_C_2CNew Entry |  |  | Out = Nil Volateg Stability for loss of the largest new entrant coal fired unit in SWQ
Q^^NIL_TR_WV_1 |  |  | Tarong Voltage Limitation for Wivenhoe 1 contingency
Q^^NIL_TR_WV_2 |  |  | Tarong Voltage Limitation for Wivenhoe 2 contingency
Q^^NIL_TR_WV_1_W |  |  | Tarong Voltage Limitation for Wivenhoe 1 contingency
Q^^NIL_TR_WV_2_W |  |  | Tarong Voltage Limitation for Wivenhoe 2 contingency
Q^^NIL_TR_WV_1_S |  |  | Tarong Voltage Limitation for Wivenhoe 1 contingency
Q^^NIL_TR_WV_2_S |  |  | Tarong Voltage Limitation for Wivenhoe 2 contingency
I:NH-1150 | 2004-02-12 | 1 | NSW-Snowy Export Limit 1150 MW
HV_1900 | 2007-09-12 | 1 | Discretionary Snowy to Vic transfer limit of 1900 MW
N>>N_FWN_BH_220_WIND |  | 1 | NSW Wind farm constraints for Far west Broken Hill, Limited by voltage control capability: 300 MW
N>>N_FWN_BUR_220_WIND |  | 1 | NSW Wind farm constraints for Far west Buronga, Limited by voltage control capability: 430 MW
N>>N_MUN_330_WIND |  | 1 | NSW Wind farm constraints for Murray Jindera, Limited by line rating: 1000MW
N>>N_MUN_132_WIND |  | 1 | NSW Wind farm constraints for Murray Deniliquin, Limited by line rating: 160MW
N>>N_SEN_132_WIND |  | 1 | NSW Wind farm constraints for South east Cooma, Limited by line rating: 160MW
N>>N_MRN_132_WIND |  | 1 | NSW Wind farm constraints for Marulan Marulan 132KV, Limited by line rating:150MW
N>>N_WEN_132_WIND |  | 1 | NSW Wind farm constraints for West Wallerawang 132KV, Limited by line rating:200MW
N>>N_NEN_132_WIND |  | 1 | NSW Wind farm constraints for New England Armidale 132KV, Limited :200MW
N>>N_MRN_330_BS_WIND |  | 1 | NSW Wind farm constraints for Marulan Bannaby 330KV, limited by line rating between Bannaby and Sydney
N>>N_MRN_330_SCS_WIND |  | 1 | NSW Wind farm constraints for Marulan Bannaby 330KV, limited by line rating between South coast and Sydney
N>>N_NEN_330_S_WIND |  | 1 | NSW Wind farm constraints for New England Armidale 330KV, limited by line rating for No.86 line for southward flow
N>>N_NEN_330_N_WIND |  | 1 | NSW Wind farm constraints for New England Armidale 330KV, limited by line rating for No.86 line for northward flow
V>>S_NIL_HOTS_RCTS_WIND_1 |  | 1 | VIC Wind farm constraints on HOTS-RCTS line based on the outage of RCTS-WETS line
V>>S_NIL_HOTS_RCTS_WIND_2 |  | 1 | VIC Wind farm constraints on HOTS-RCTS line based on the outage of BETS-KGTS line
V>>S_NIL_HOTS_RCTS_WIND_3 |  | 1 | VIC Wind farm constraints on HOTS-RCTS line based on the outage of RCTS-BSS line
S>>V_NIL_RCTS_WETS_WIND_1 |  |  | VIC Wind farm constraints on RCTS-WETS line based on the outage of RCTS-HOTS line
S>>V_NIL_RCTS_WETS_WIND_2 |  |  | VIC Wind farm constraints on RCTS-WETS line based on the outage of HOTS-WBTS line
S>>V_NIL_RCTS_WETS_WIND_3 |  |  | VIC Wind farm constraints on RCTS-WETS line based on the outage of RCTS-BSS line
V>>S_NIL_BATS_BETS_WIND_1 |  |  | VIC Wind farm constraints on BATS-BETS line based on the outage of HOTS-WBTS line
V>>S_NIL_BATS_BETS_WIND_2 |  |  | VIC Wind farm constraints on BATS-BETS line based on the outage of BATS-WBTS-HOTS line
V>>S_NIL_BATS_WBTS_WIND_1 |  |  | VIC Wind farm constraints on BATS-WBTS line based on the outage of BETS-KGTS line
V>>S_NIL_BATS_WBTS_WIND_2 |  |  | VIC Wind farm constraints on BATS-WBTS line based on the outage of BATS-BETS line
V>>S_NIL_BETS_KGTS_WIND |  |  | VIC Wind farm constraints on BETS-KGTS line based on the outage of RCTS-HOTS line
S>>V_NIL_HOTS_WBTS_WIND_1 |  |  | VIC Wind farm constraints on HOTS-WBTS line based on the outage of BETS-KGTS line
S>>V_NIL_HOTS_WBTS_WIND_2 |  |  | VIC Wind farm constraints on HOTS-WBTS line based on the outage of BATS-BETS line
V>>SML_NIL_3_A_WIND |  |  | VIC Wind farm constraints on BETS-FVTS-SHTS line based on the outage of EPS-TTS line
V>>SML_NIL_3_B_WIND |  |  | VIC Wind farm constraints on BETS-FVTS-SHTS line based on the outage of DDTS-SMTS line
V>>V_NIL_BATS_TGTS_WIND |  |  | VIC Wind farm constraints on BATS-TGTS line based on the outage of MLTS-TGTS line
V>>V_NIL_MLTS_TGTS_WIND |  |  | VIC Wind farm constraints on MLTS-TGTS line based on the outage of BATS-TGTS line
S>>V_NIL_MLTS_GTS_WIND |  |  | VIC Wind farm constraints on MLTS-GTS line 1 based on the outage of MLTS-GTS line 2
V>>V_NIL_MLTS_HYTS_WIND |  |  | VIC Wind farm constraints on MLTS-HYTS/APD line based on the outage the parallel line
V>>V_NIL_ROTS-YPS_HWPS_WIND |  |  | VIC Wind farm constraints Max flow on ROTS-YPS/HWPS 220 kv lines following an outage of a parallel line
V>>SML_NIL_1_WIND | 2008-07-02 | 1 | Outage = Nil, limit Vic generators and interconnectors to avoid overloading Ballarat to Moorabool No.1 220 kV line for loss of Ballarat to Moorabool No.2 220 kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>>SML_NIL_2_WIND | 2008-07-02 | 1 | Outage = Nil, limit Vic generators and interconnectors to avoid pre-contingent overloading of the Bendigo to Fosterville to Shepparton 220 kV line, Murraylink VFRB enabled for RCTS-Buronga line contingency and Murraylink > 25MW
V>>SML_NIL_3_WIND | 2008-07-02 | 1 | Outage = Nil, limit Vic generators and interconnectors to avoid overloading the Bendigo to Fosterville to Shepparton 220 kV line for trip of Redcliffs to Buronga 220kV line, swamped if Murraylink VFRB enabled for this contingency and Murraylink > 25MW
V>>SML_NIL_4_WIND | 2008-07-02 | 1 | Outage = Nil, limit Vic generators and interconnectors to avoid overloading Ballarat to Moorabool No.2 220 kV line for loss of Ballarat to Moorabool No.1 220 kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
V>SML_NIL_8_WIND | 2008-07-02 | 1 | Outage = Nil, limit Vic to SA on Murraylink to avoid overloading Ballarat to Bendigo 220 kV line for loss of Bendigo to Shepparton 220 kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW
S>>S_NIL_1_WIND |  |  | Overload of Cultana 275 kV/132 kV Transformer 1 for loss of Davenport to Playford 275 kV line 1 and 2
S>>S_NIL_2_WIND |  |  | Overload of Red Hill to Brinkworth 132 kV line 1 for loss of Davenport to Bungama 275 kV line 1
S>>S_NIL_3_WIND |  |  | Overload of Bungama 275 kV/132 kV Transformer 1 for loss of Davenport to Bungama 275 kV line 1
S>>S_NIL_4_WIND |  |  | Overload of Brinkworth to Para 275 kV line 1 for loss of Davenport to Brinkworth 275 kV line 1
S>>S_NIL_5_WIND |  |  | Overload of Davenport to Playford 275 kV line 2 for loss of Davenport to Playford 275 kV line 1
S>>S_NIL_6_WIND |  |  | Overload of Playford 275 kV / 132 kV Transformer South
S>>S_NIL_7_WIND |  |  | Overload of Playford 275 kV / 132 kV Transformer North
S>>S_NIL_8_WIND |  |  | Overload of Cultana to Whyalla 132 kV line 1
S>>S_NIL_9_WIND |  |  | Overload of Playford 132 kV line 1 for the loss of Cultana 275 kV / 132 kV Transformer 1
S>>S_NIL_11_WIND |  |  | Overload of Davenport to Bungama 275 kV line 1 for loss of Bungama to Para 275 kV line 1
S>>S_NIL_12_WIND |  |  | Overload of Bungama 275 kV / 132 kV Transfomer 1 for the loss of Bungama to Para 275 kV line 1
S>>S_NIL_13_WIND |  |  | Overload of Red Hill to Brinkworth 132 kV line 1 for loss of Bungama 275 kV / 132 kV Transformer 1
S>>S_NIL_14_WIND |  |  | Overload of Waterloo to Hummocks 132 kV line 1 for loss of Bungama 275 kV / 132 kV Transformer 1
S>>S_NIL_15_WIND |  |  | Overload of Davenport to Brinkworth 275 kV line 1 for loss of Brinkworth to Para 275 kV line 1
S>>S_NIL_16_WIND |  |  | Overload of Brinkworth 275 kV / 132 kV Transfomer 1 for the loss of Brinkworth to Para 275 kV line 1
S>>S_NIL_17_WIND |  |  | Overload of Mintaro to Waterloo 132 kV line 1 for loss of Brinkworth 275 kV / 132 kV Transformer 3
S>>S_NIL_18_WIND |  |  | Overload of Brinkworth to Clare North 132 kV line 1 for loss of Brinkworth 275 kV / 132 kV Transformer 3
S>>S_NIL_20_WIND |  |  | Overload of Robertstown to Tungkillo 275 kV line 2 for loss of Robertstown to Tungkillo 275 kV line 1
S>>V_NIL_23_WIND |  |  | Overload of Murray Bridge to Tailem Bend 275 kV line 1
S>>V_NIL_24_WIND |  |  | Overload of Myponga to Murray Bridge 275 kV line 2 for loss of Tungkillo to Tailem Bend 275 kV line 1
S>>V_NIL_25_WIND |  |  | Overload of Cherry Gardens to Tungkillo 275 kV line 1
V>>S_NIL_26_WIND |  |  | Overload of Tungkillo to Para 275 kV line 1 for loss of Tungkillo to Cherry Gardens 275 kV line 1
S>>V_NIL_27_WIND |  |  | Overload of Myponga to Murray Bridge 275 kV line 2
S>>V_NIL_28_WIND |  |  | Overload of Tungkillo to Tailem Bend 275 kV line 1 for loss of Tailem Bend to Cherry Gardens 275 kV line 2
S>>V_NIL_29_WIND |  |  | Overload of Murray Bridge to Tailem Bend 275 kV line 2
S>>V_NIL_30_WIND |  |  | Overload of Cherry Gardens to Cherry Gardens 275 kV line 2
V>>S_NIL_31_WIND |  |  | Overload of Parafield Gardens West to Pelican Point 275 kV line 1 for loss of Para to Parafield Gardens West 275 kV line 1
S>>V_NIL_34_WIND |  |  | Overload of Angas Creek to Map No 3 Pump 132 kV line 1 for loss of Para 275 kV / 132 kV Transformer 8
S>>S_NIL_35_WIND |  |  | Overload of Torrens to Lefevre 275 kV line 1 for loss of Parafield Gardens West to Pelican Point 275 kV line 1
S>>S_NIL_37_WIND |  |  | Overload of Torrens to Lefevre 275 kV line 1 for loss of Pelican Point to Lefevre 275 kV line 1
S>>S_NIL_38_WIND |  |  | Overload of Para to Parafield Gardens West 275 kV line 1 for loss of Torrens to Lefevre 275 kV line 1
S>>S_NIL_39_WIND |  |  | Overload of Parafield Gardens West to Pelican Point 275 kV line 1 for loss of Torrens to Lefevre 275 kV line 1
S>>S_NIL_40_WIND |  |  | Overload of Kilburn to Northfield 275 kV line 1 for loss of Torrens to Kilburn 275 kV line 1
S>>V_NIL_42_WIND |  |  | Overload of Kilburn to Northfield 275 kV line 1 for loss of Torrens to Northfield 275 kV line 1
S>>S_NIL_44_WIND |  |  | Overload of Torrens to Kilburn 275 kV line 1 for loss of Kilburn to Northfield 275 kV line 1
S>>V_NIL_45_WIND |  |  | Overload of Torrens to Northfield 275 kV line 1 for loss of Kilburn to Northfield 275 kV line 1
S>>S_NIL_46_WIND |  |  | Overload of Happy Valley to Cherry Gardens 275 kV line 1 for loss of Magill to Happy Valley 275 kV line 1
V>>S_NIL_47_WIND |  |  | Overload of Para to Magill 275 kV line 1 for loss of Magill to Happy Valley 275 kV line 1
S>>S_NIL_48_WIND |  |  | Overload of Morphett Vale East to Cherry Gardens 275 kV line 1 for loss of Happy Valley to Morphett Vale East 275 kV line 1
S>>V_NIL_49_WIND |  |  | Overload of Morphett Vale East to Cherry Gardens 275 kV line 1 for loss of Happy Valley to Cherry Gardens 275 kV line 1
S>>V_NIL_50_WIND |  |  | Overload of Happy Valley to Morphett Vale East 275 kV line 1 for loss of Happy Valley to Cherry Gardens 275 kV line 1
S>>S_NIL_51_WIND |  |  | Overload of Happy Valley to Morphett Vale East 275 kV line 1 for loss of Morphett Vale East to Cherry Gardens 275 kV line 1
S>>V_NIL_52_WIND |  |  | Overload of Happy Valley to Cherry Gardens 275 kV line 1 for loss of Morphett Vale East to Cherry Gardens 275 kV line 1
S>>V_NIL_53_WIND |  |  | Overload of Tailem Bend to Myponga 275 kV line 2
S>>V_NIL_54_WIND |  |  | Overload of Cherry Gardens to Mt Barker 132 kV line 1
V>>S_NIL_55_WIND |  |  | Overload of Tailem Bend to Cherry Gardens 275 kV line 2
S>>V_NIL_56_WIND |  |  | Overload of Tailem Bend to South East 275 kV line 2 for loss of Tailem Bend to South East 275 kV line 1
S>>V_NIL_57_WIND |  |  | Overload of Mobilong to Tailem Bend 132 kV line 1 for loss of Tailem Bend 275 kV / 132 kV Transformer 4
V>>S_NIL_58_WIND |  |  | Overload of South Eact 275 kV / 132 kV Transformer for loss of South East 275 kV / 132 kV Transformer 2
S>>S_NIL_59_WIND |  |  | Overload of Davenport to Cultana 2 275 kV line 1 for loss of Cultana 275 kV / 132 kV Transformer 1
S>>S_NIL_60_WIND |  |  | Overload of Cultana 275 kV / 132 kV Transformer 1
S>>S_NIL_61_WIND |  |  | Overload of Davenport to Davenport 275 kV line 1 for loss of Cultana to Whyalla 132 kV line 1
S>>S_NIL_63_WIND |  |  | Overload of Waterloo to Hummocks 132 kV line 1 for loss of Bungama to Snowtown Tee 132 kV line 1
S>>S_NIL_64_WIND |  |  | Overload of Mintaro to Waterloo 132 kV line 1 for loss of Brinkworth to Clare North 132 kV line 1
S>>S_NIL_65_WIND |  |  | Overload of Brinkworth to Clare North 132 kV line 1 for loss of Mintaro to Waterloo 132 kV line 1
S>>S_NIL_66_WIND |  |  | Overload of Morgan Whyalla Pipline 2 to Morgan Whyalla Pipline 1 132 kV line 1
S>>S_NIL_69_WIND |  |  | Overload of Morgan Whyalla Pipline 3 to Morgan Whyalla Pipline 2 132 kV line 1
S>>S_NIL_74_WIND |  |  | Overload of Templers to Dorrien 132 kV line 1 for loss of Waterloo to Templers 132 kV line 1
S>>S_NIL_75_WIND |  |  | Overload of Bungama to Snowtown Tee 132 kV line 1 for loss of Waterloo to Hummocks 132 kV line 1
S>>S_NIL_76_WIND |  |  | Overload of Templers to Roseworthy 132 kV line 1 for loss of Templers to Dorrien 132 kV line 1
S>>S_NIL_77_WIND |  |  | Overload of Waterloo to Templers 132 kV line 1 for loss of Templers to Dorrien 132 kV line 1
S>>S_NIL_78_WIND |  |  | Overload of Roseworthy to Para 132 kV line 1
S>>S_NIL_79_WIND |  |  | Overload of Templers to Dorrien 132 kV line 1 for loss of Templers to Roseworthy 132 kV line 1
S>>V_NIL_80_WIND |  |  | Overload of Angas Creek to MAP No 3 Pump 132 kV line 1
S>>V_NIL_81_WIND |  |  | Overload of MAP No 3 Pump to MAP No 2 Pump 132 kV line 1
S>>V_NIL_82_WIND |  |  | Overload of Cherry Gardens 275 kV / 132 kV Transformer 1
V>>S_NIL_83_WIND |  |  | Overload of Mobilong to MHP No 2 Pump 132 kV line 1
V>>S_NIL_84_WIND |  |  | Overload of Cherry Gardens 275 kV / 132 kV Transformer 1
S>>V_NIL_85_WIND |  |  | Overload of Para to Millbrook Tee 132 kV line 1
S>>S_NIL_86_WIND |  |  | Overload of Para 275 kV / 132 kV Transformer 8 for loss of Angas Creek to Map No 3 Pump 132 kV line 1
S>>V_NIL_87_WIND |  |  | Overload of Tailem Bend 275 kV / 132 kV Transformer 4 for loss of Mobilong to Tailem Bend 132 kV line 1
S>>S_NIL_88_WIND |  |  | Overload of South East to Penola West 132 kV line 1 for loss of Keith to Kincraig 132 kV line 1
S>>S_NIL_89_WIND |  |  | Overload of Keith to Kincraig 132 kV line 1 for loss of South East to Penola West 132 kV line 1
V>>S_NIL_90_WIND |  |  | Overload of South East to Snuggery 132 kV line 1 for loss of South East to Mt Gambier 132 kV line 1
S>>V_NIL_91_WIND |  |  | Overload of Snuggery to Snuggery 132 kV line 1 for loss of South East to Mt Gambier 132 kV line 1
V>>S_NIL_92_WIND |  |  | Overload of Blanche to Snuggery 132 kV line 1 for loss of South East to Snuggery 132 kV line 1
V>>S_NIL_93_WIND |  |  | Overload of Mt Gambier to Blanche 132 kV line 1 for loss of South East to Snuggery 132 kV line 1
V>>S_NIL_94_WIND |  |  | Overload of Blanche to Snuggery 132 kV line 1 for loss of Snuggery to Snuggery 132 kV line 1
V>>S_NIL_95_WIND |  |  | Overload of Mt Gambier to Blanche 132 kV line 1 for loss of Snuggery to Snuggery 132 kV line 1
S>>S_NIL_96_WIND |  |  | Overload of Whyalla to Middleback 132 kV line 1
S>>S_NIL_97_WIND |  |  | Overload of Middleback to Yadnarie 132 kV line 1
S>>S_NIL_98_WIND |  |  | Overload of Yadnarie to Pt Lincoln 132 kV line 1
S>>S_NIL_100_WIND |  |  | Overload of Hummocks to Ardrossan West 132 kV line 1
S>>S_NIL_128_WIND |  |  | Overload of Red Hill to Brinkworth 132 kV line 1 for loss of Davenport to Bungama 275 kV line 1
S>>S_NIL_130_WIND |  |  | Overload of Brinkworth to Para 275 kV line 1 for loss of Davenport to Brinkworth 275 kV line 1
S>>S_NIL_139_WIND |  |  | Overload of Red Hill to Brinkworth 132 kV line 1 for loss of Bungama 275 kV / 132 kV Transformer 1
S>>S_NIL_141_WIND |  |  | Overload of Davenport to Brinkworth 275 kV line 1 for loss of Brinkworth to Para 275 kV line 1
S>>S_NIL_146_WIND |  |  | Overload of Robertstown to Tungkillo 275 kV line 2 for loss of Robertstown to Tungkillo 275 kV line 1
S>>V_NIL_149_WIND |  |  | Overload of Murray Bridge to Tailem Bend 275 kV line 1
S>>V_NIL_151_WIND |  |  | Overload of Cherry Gardens to Tungkillo 275 kV line 1
V>>S_NIL_152_WIND |  |  | Overload of Tungkillo to Para 275 kV line 1 for loss of Tungkillo to Cherry Gardens 275 kV line 1
S>>V_NIL_154_WIND |  |  | Overload of Tungkillo to Tailem Bend 275 kV line 1 for loss of Tailem Bend to Cherry Gardens 275 kV line 2
V>>S_NIL_157_WIND |  |  | Overload of Parafield Gardens West to Pelican Point 275 kV line 1 for loss of Para to Parafield Gardens West 275 kV line 1
S>>S_NIL_165_WIND |  |  | Overload of Parafield Gardens West to Pelican Point 275 kV line 1 for loss of Torrens to Lefevre 275 kV line 1
S>>S_NIL_172_WIND |  |  | Overload of Happy Valley to Cherry Gardens 275 kV line 1 for loss of Magill to Happy Valley 275 kV line 1
V>>S_NIL_173_WIND |  |  | Overload of Para to Magill 275 kV line 1 for loss of Magill to Happy Valley 275 kV line 1
S>>S_NIL_174_WIND |  |  | Overload of Morphett Vale East to Cherry Gardens 275 kV line 1 for loss of Happy Valley to Morphett Vale East 275 kV line 1
S>>V_NIL_175_WIND |  |  | Overload of Morphett Vale East to Cherry Gardens 275 kV line 1 for loss of Happy Valley to Cherry Gardens 275 kV line 1
S>>V_NIL_176_WIND |  |  | Overload of Happy Valley to Morphett Vale East 275 kV line 1 for loss of Happy Valley to Cherry Gardens 275 kV line 1
S>>S_NIL_177_WIND |  |  | Overload of Happy Valley to Morphett Vale East 275 kV line 1 for loss of Morphett Vale East to Cherry Gardens 275 kV line 1
S>>V_NIL_178_WIND |  |  | Overload of Happy Valley to Cherry Gardens 275 kV line 1 for loss of Morphett Vale East to Cherry Gardens 275 kV line 1
S>>V_NIL_180_WIND |  |  | Overload of Cherry Gardens to Mt Barker 132 kV line 1
S>>S_NIL_200_WIND |  |  | Overload of Templers to Dorrien 132 kV line 1 for loss of Waterloo to Templers 132 kV line 1
S>>S_NIL_201_WIND |  |  | Overload of Bungama to Snowtown Tee 132 kV line 1 for loss of Waterloo to Hummocks 132 kV line 1
S>>S_NIL_202_WIND |  |  | Overload of Templers to Roseworthy 132 kV line 1 for loss of Templers to Dorrien 132 kV line 1
S>>S_NIL_204_WIND |  |  | Overload of Roseworthy to Para 132 kV line 1
S>>V_NIL_207_WIND |  |  | Overload of MAP No 3 Pump to MAP No 2 Pump 132 kV line 1
V>>S_NIL_209_WIND |  |  | Overload of Mobilong to MHP No 2 Pump 132 kV line 1
S>>V_NIL_211_WIND |  |  | Overload of Para to Millbrook Tee 132 kV line 1
S>>S_NIL_214_WIND |  |  | Overload of South East to Penola West 132 kV line 1 for loss of Keith to Kincraig 132 kV line 1
V>>S_NIL_216_WIND |  |  | Overload of South East to Snuggery 132 kV line 1 for loss of South East to Mt Gambier 132 kV line 1
V>>S_NIL_218_WIND |  |  | Overload of Blanche to Snuggery 132 kV line 1 for loss of South East to Snuggery 132 kV line 1
V>>S_NIL_219_WIND |  |  | Overload of Mt Gambier to Blanche 132 kV line 1 for loss of South East to Snuggery 132 kV line 1
V>>S_NIL_220_WIND |  |  | Overload of Blanche to Snuggery 132 kV line 1 for loss of Snuggery to Snuggery 132 kV line 1
V>>S_NIL_221_WIND |  |  | Overload of Mt Gambier to Blanche 132 kV line 1 for loss of Snuggery to Snuggery 132 kV line 1
S>>S_NIL_222_WIND |  |  | Overload of Whyalla to Middleback 132 kV line 1
S>>S_NIL_223_WIND |  |  | Overload of Middleback to Yadnarie 132 kV line 1
S>>S_NIL_224_WIND |  |  | Overload of Yadnarie to Pt Lincoln 132 kV line 1
S>>S_NIL_1_WIND_P |  |  | Overload of Davenport to Cultana 2 275 kV line 1 for loss of Cultana 275 kV / 132 kV Transformer 1
S>>S_NIL_2_WIND_P |  |  | Overload of Davenport to Cultana 275 kV line A
S>>S_NIL_3_WIND_P |  |  | Overload of Davenport to Bungama 275 kV line 1 for loss of Bungama to Para 275 kV line 1
S>>S_NIL_4_WIND_P |  |  | Overload of Davenport to Playford 275 kV line 1 for loss of Davenport to Playford 275 kV line 2
S>>S_NIL_5_WIND_P |  |  | Overload of Playford 275 kV / 132 kV Transformer North for loss of Playford 275 kV / 132 Transformer South
S>>S_NIL_6_WIND_P |  |  | Overload of Playford 275 kV / 132 kV Transformer South for loss of Playford 275 kV / 132 Transformer North
S>>S_NIL_7_WIND_P |  |  | Overload of Cultana 275 kV / 132 kV Transformer 1 for loss of Davenport to Cultana 275 kV line A
S>>S_NIL_8_WIND_P |  |  | Overload of Cultana 275 kV / 132 kV Transformer 1 for loss of Cultana 275 kV / 132 kV Transformer 2
S>>S_NIL_9_WIND_P |  |  | Overload of Cultana 275 kV / 132 kV Transformer 2 for loss of Davenport to Cultana 275 kV line A
S>>S_NIL_11_WIND_P |  |  | Overload of Bungama 275 kV / 132 kV Transformer 1 for loss of Davenport to Bungama 275 kV line 1
S>>S_NIL_12_WIND_P |  |  | Overload of Bungama 275 kV / 132 kV Transformer 1 for loss of Red Hill to Brinkworth 132 kV line 1
S>>S_NIL_13_WIND_P |  |  | Overload of Brinkworth to Templers 275 kV line 1 for loss of Davenport to Brinkworth 275 kV line 1
S>>S_NIL_16_WIND_P |  |  | Overload of Templers to Para 275 kV line 1 for loss of Brinkworth to Templers 275 kV line 1
S>>S_NIL_17_WIND_P |  |  | Overload of Templers to Para 275 kV line 1 for loss of Bungama to Para 275 kV line 1
S>>S_NIL_18_WIND_P |  |  | Overload of Templers 275 kV / 132 kV Transformer 1
S>>S_NIL_19_WIND_P |  |  | Overload of Templers 275 kV / 132 kV Transformer 1 for loss of Templers to Dorrien 132 kV line 1
V>>S_NIL_20_WIND_P |  |  | Overload of Tungkillo to Para 275 kV line 1 for loss of Tungkillo to Cherry Gardens 275 kV line 1
V>>S_NIL_21_WIND_P |  |  | Overload of Tungkillo to Para 275 kV line 1 for loss of Cherry Gardens to Tungkillo 275 kV line 1
S>>V_NIL_22_WIND_P |  |  | Overload of Tungkillo to Tailem Bend 275 kV line 1
S>>V_NIL_23_WIND_P |  |  | Overload of Tungkillo to Tailem Bend 275 kV line 1 for loss of Tailem Bend to Cherry Gardens 275 kV line 2
S>>V_NIL_24_WIND_P |  |  | Overload of Tungkillo to Cherry Gardens 275 kV line 1 for loss of Cherry Gardens to Tungkillo 275 kV line 1
V>>S_NIL_25_WIND_P |  |  | Overload of Tailem Bend to Cherry Gardens 275 kV line 2
V>>S_NIL_26_WIND_P |  |  | Overload of Tailem Bend to Cherry Gardens 275 kV line 2 for loss of Tailem Bend to Murray Bridge 275 kV line 1
S>>V_NIL_27_WIND_P |  |  | Overload of Tailem Bend to Myponga 275 kV line 2
S>>V_NIL_28_WIND_P |  |  | Overload of Tailem Bend to Myponga 275 kV line 2
S>>S_NIL_30_WIND_P |  |  | Overload of Para to Parafield Gardens West 275 kV line 1 for loss of Torrens to Lefevre 275 kV line 1
V>>S_NIL_31_WIND_P |  |  | Overload of Para to Magill 275 kV line 1 for loss of Magill to Happy Valley 275 kV line 1
S>>V_NIL_32_WIND_P |  |  | Overload of Para to Magill 275 kV line 1 for loss of Torrens to Magill 275 kV line 1
S>>V_NIL_33_WIND_P |  |  | Overload of Para 275 kV / 132 kV Transformer 8 for loss of Templers to Roseworthy 132 kV line 1
S>>S_NIL_34_WIND_P |  |  | Overload of Para 275 kV / 132 kV Transformer 8 for loss of Millbrooke Tee to Angas Creek 132 kV line 1
S>>S_NIL_35_WIND_P |  |  | Overload of Parafield Gardens West to Pelican Point 275 kV line 1 for loss of Torrens to Lefevre 275 kV line 1
V>>S_NIL_36_WIND_P |  |  | Overload of Parafield Gardens West to Pelican Point 275 kV line 1 for loss of Para to Parafield Gardens West 275 kV line 1
S>>S_NIL_38_WIND_P |  |  | Overload of Torrens to Lefevre 275 kV line 1 for loss of Pelican Point to Lefevre 275 kV line 1
S>>S_NIL_39_WIND_P |  |  | Overload of Torrens to Lefevre 275 kV line 1 for loss of Parafield Gardens West to Pelican Point 275 kV line 1
S>>S_NIL_40_WIND_P |  |  | Overload of Torrens to Kilburn 275 kV line 1 for loss of Kilburn to Northfield 275 kV line 1
S>>V_NIL_42_WIND_P |  |  | Overload of Torrens to Northfield 275 kV line 1 for loss of Kilburn to Northfield 275 kV line 1
S>>S_NIL_44_WIND_P |  |  | Overload of Kilburn to Northfield 275 kV line 1 for loss of Torrens to Kilburn 275 kV line 1
S>>V_NIL_45_WIND_P |  |  | Overload of Kilburn to Northfield 275 kV line 1 for loss of Torrens to Northfield 275 kV line 1
S>>V_NIL_46_WIND_P |  |  | Overload of Happy Valley to Morphett Vale East 275 kV line 1 for loss of Happy Valley to Cherry Gardens 275 kV line 1
S>>S_NIL_47_WIND_P |  |  | Overload of Happy Valley to Morphett Vale East 275 kV line 1 for loss of Morphett Vale East to Cherry Gardens 275 kV line 1
S>>S_NIL_48_WIND_P |  |  | Overload of Happy Valley to Cherry Gardens 275 kV line 1 for loss of Magill to Happy Valley 275 kV line 1
S>>V_NIL_49_WIND_P |  |  | Overload of Happy Valley to Cherry Gardens 275 kV line 1 for loss of Morphett Vale East to Cherry Gardens 275 kV line 1
S>>V_NIL_50_WIND_P |  |  | Overload of Morphett Vale East to Cherry Gardens 275 kV line 1 for loss of Happy Valley to Cherry Gardens 275 kV line 1
S>>S_NIL_51_WIND_P |  |  | Overload of Morphett Vale East to Cherry Gardens 275 kV line 1 for loss of Happy Valley to Morphett Vale East 275 kV line 1
S>>V_NIL_52_WIND_P |  |  | Overload of Cherry Gardens to Cherry Gardens 275 kV line 2
S>>V_NIL_53_WIND_P |  |  | Overload of Cherry Gardens to Tungkillo 275 kV line 1 for loss of Tungkillo to Cherry Gardens 275 kV line 1
S>>V_NIL_54_WIND_P |  |  | Overload of Cherry Gardens 275 kV / 132 kV Transformer 1
S>>V_NIL_55_WIND_P |  |  | Overload of Cherry Gardens 275 kV / 132 kV Transformer 1 for loss of MHP No 2 Pump to MHP No 3 Pump 132 kV line 1
S>>V_NIL_56_WIND_P |  |  | Overload of Myponga to Murray Bridge 275 kV line 2
S>>V_NIL_57_WIND_P |  |  | Overload of Tailem Bend 275 kV / 132 kV Transformer 4 for loss of Mobilong to Tailem Bend 132 kV line 1
V>>S_NIL_58_WIND_P |  |  | Overload of South East 275 kV / 132 kV Transformer 1 for loss of South East 275 kV / 132 kV Transformer 2
S>>S_NIL_59_WIND_P |  |  | Overload of Playford to Cultana 132 kV line 1 for loss of Davenport to Davenport 275 kV line 1
S>>S_NIL_60_WIND_P |  |  | Overload of Playford to Cultana 132 kV line 2 for loss of Davenport to Davenport 275 kV line 1
S>>S_NIL_61_WIND_P |  |  | Overload of Cultana 275 kV / 132 kV Transformer 1
S>>S_NIL_62_WIND_P |  |  | Overload of Cultana 275 kV / 132 kV Transformer 2
S>>S_NIL_66_WIND_P |  |  | Overload of Red Hill to Brinkworth 132 kV line 1 for loss of Bungama 275 kV / 132 kV Transformer 1
S>>S_NIL_67_WIND_P |  |  | Overload of Red Hill to Brinkworth 132 kV line 1 for loss of Davenport to Bungama 275 kV line 1
S>>S_NIL_68_WIND_P |  |  | Overload of Bungama to Snowtown Tee 132 kV line 1 for loss of Waterloo to Hummocks 132 kV line 1
S>>S_NIL_69_WIND_P |  |  | Overload of Brinkworth to Clare North 132 kV line 1 for loss of Mintaro to Waterloo 132 kV line 1
S>>S_NIL_70_WIND_P |  |  | Overload of Mintaro to Waterloo 132 kV line 1 for loss of Brinkworth to Clare North 132 kV line 1
S>>S_NIL_71_WIND_P |  |  | Overload of Mintaro to Waterloo 132 kV line for loss Brinkworth 275 kV / 132 kV Transformer 3
S>>S_NIL_74_WIND_P |  |  | Overload of Robertstown to Morgan Whyalla Pipline 3 132 kV line 1
S>>S_NIL_77_WIND_P |  |  | Overload of Morgan Whyalla Pipline 4 to Waterloo 132 kV line 1 for loss of Robertstown to Tungkillo 275 kV line 2
S>>S_NIL_79_WIND_P |  |  | Overload of Morgan Whyalla Pipline 1 to North West Bend 132 kV line 1
S>>S_NIL_84_WIND_P |  |  | Overload of Waterloo to Templers 132 kV line 1 for loss of Templers to Roseworthy 132 kV line 1
S>>S_NIL_85_WIND_P |  |  | Overload of Waterloo to Templers 132 kV line 1 for loss of Robertstown to Morgan Whyalla Pipline 4 132 kV line 1
S>>S_NIL_86_WIND_P |  |  | Overload of Waterloo to Hummocks 132 kV line 1 for loss of Bungama to Snowtown Tee 132 kV line 1
S>>S_NIL_87_WIND_P |  |  | Overload of Templers to Dorrien 132 kV line 1 for loss of Templers 275 kV / 132 kV Transformer 1
S>>S_NIL_88_WIND_P |  |  | Overload of Templers to Dorrien 132 kV line 1 for loss of Templers to Para 275 kV line 1
S>>S_NIL_89_WIND_P |  |  | Overload of Templers to Roseworthy 132 kV line 1 for loss of Templers 275 kV / 132 kV Transformer 1
S>>V_NIL_90_WIND_P |  |  | Overload of Templers to Roseworthy 132 kV line 1 for loss of Para 275 kV / 132 kV Transformer 8
S>>S_NIL_91_WIND_P |  |  | Overload of Templers to Dorrien 132 kV line 1
S>>S_NIL_92_WIND_P |  |  | Overload of Templers to Dorrien 132 kV line 1 for loss of Templers to Para 275 kV line 1
S>>V_NIL_93_WIND_P |  |  | Overload of Para to Millbrook Tee 132 kV line 1
S>>V_NIL_94_WIND_P |  |  | Overload of Para to Millbrook Tee 132 kV line 1
S>>V_NIL_95_WIND_P |  |  | Overload of Cherry Gardens to Mt Barker 132 kV line 1
S>>V_NIL_96_WIND_P |  |  | Overload of Mt Barker to MHP No 3 Pump 132 kV line 1
S>>V_NIL_97_WIND_P |  |  | Overload of Mt Barker to MHP No 3 Pump 132 kV line 1 for loss of Cherry Gardens to Mt Barker 132 kV line 1
S>>V_NIL_98_WIND_P |  |  | Overload of Angas Creek to MAP No 3 Pump 132 kV line 1
S>>V_NIL_99_WIND_P |  |  | Overload of Mobilong to Tailem Bend 132 kV line 1 for loss of Tailem Bend 275 kV / 132 kV Transformer 4
S>>V_NIL_100_WIND_P |  |  | Overload of Mobilong to Tailem Bend 132 kV line 1 for loss of Mt Barker to MHP No 3 Pump 132 kV line 1
S>>S_NIL_101_WIND_P |  |  | Overload of Keith to Kincraig 132 kV line 1 for loss of South East to Penola West 132 kV line 1
S>>S_NIL_102_WIND_P |  |  | Overload of South East to Penola West 132 kV line 1 for loss of Keith to Kincraig 132 kV line 1
V>>S_NIL_103_WIND_P |  |  | Overload of South East to Mt Gambier 132 kV line 1
V>>S_NIL_104_WIND_P |  |  | Overload of South East to Snuggery 132 kV line 1 for loss of South East to Mt Gambier 132 kV line 1
V>>S_NIL_105_WIND_P |  |  | Overload of Mt Gambier to Blanche 132 kV line 1 for loss of Snuggery to Snuggery 132 kV line 1
V>>S_NIL_106_WIND_P |  |  | Overload of Mt Gambier to Blanche 132 kV line 1 for loss of South East to Snuggery 132 kV line 1
V>>S_NIL_107_WIND_P |  |  | Overload of Blanche to Snuggery 132 kV line 1 for loss of Snuggery to Snuggery 132 kV line 1
V>>S_NIL_108_WIND_P |  |  | Overload of Blanche to Snuggery 132 kV line 1 for loss of South East to Snuggery 132 kV line 1
S>>S_NIL_109_WIND_P |  |  | Overload of Whyalla to Middleback 132 kV line 1
S>>S_NIL_110_WIND_P |  |  | Overload of Middleback to Yadnarie 132 kV line 1
S>>S_NIL_111_WIND_P |  |  | Overload of Yadnarie to Pt Lincoln 132 kV line 1
S>>S_NIL_113_WIND_P |  |  | Overload of Hummocks to Ardrossan West 132 kV line 1
S>>S_NIL_156_WIND_P |  |  | Overload of Brinkworth to Templers 275 kV line 1 for loss of Davenport to Brinkworth 275 kV line 1
S>>S_NIL_159_WIND_P |  |  | Overload of Templers to Para 275 kV line 1 for loss of Brinkworth to Templers 275 kV line 1
S>>S_NIL_160_WIND_P |  |  | Overload of Templers to Para 275 kV line 1 for loss of Bungama to Para 275 kV line 1
V>>S_NIL_163_WIND_P |  |  | Overload of Tungkillo to Para 275 kV line 1 for loss of Tungkillo to Cherry Gardens 275 kV line 1
V>>S_NIL_164_WIND_P |  |  | Overload of Tungkillo to Para 275 kV line 1 for loss of Cherry Gardens to Tungkillo 275 kV line 1
S>>V_NIL_165_WIND_P |  |  | Overload of Tungkillo to Tailem Bend 275 kV line 1
S>>V_NIL_166_WIND_P |  |  | Overload of Tungkillo to Tailem Bend 275 kV line 1 for loss of Tailem Bend to Cherry Gardens 275 kV line 2
S>>V_NIL_167_WIND_P |  |  | Overload of Tungkillo to Cherry Gardens 275 kV line 1 for loss of Cherry Gardens to Tungkillo 275 kV line 1
V>>S_NIL_174_WIND_P |  |  | Overload of Para to Magill 275 kV line 1 for loss of Magill to Happy Valley 275 kV line 1
S>>V_NIL_175_WIND_P |  |  | Overload of Para to Magill 275 kV line 1 for loss of Torrens to Magill 275 kV line 1
S>>S_NIL_178_WIND_P |  |  | Overload of Parafield Gardens West to Pelican Point 275 kV line 1 for loss of Torrens to Lefevre 275 kV line 1
V>>S_NIL_179_WIND_P |  |  | Overload of Parafield Gardens West to Pelican Point 275 kV line 1 for loss of Para to Parafield Gardens West 275 kV line 1
S>>V_NIL_189_WIND_P |  |  | Overload of Happy Valley to Morphett Vale East 275 kV line 1 for loss of Happy Valley to Cherry Gardens 275 kV line 1
S>>S_NIL_190_WIND_P |  |  | Overload of Happy Valley to Morphett Vale East 275 kV line 1 for loss of Morphett Vale East to Cherry Gardens 275 kV line 1
S>>S_NIL_191_WIND_P |  |  | Overload of Happy Valley to Cherry Gardens 275 kV line 1 for loss of Magill to Happy Valley 275 kV line 1
S>>V_NIL_192_WIND_P |  |  | Overload of Happy Valley to Cherry Gardens 275 kV line 1 for loss of Morphett Vale East to Cherry Gardens 275 kV line 1
S>>V_NIL_193_WIND_P |  |  | Overload of Morphett Vale East to Cherry Gardens 275 kV line 1 for loss of Happy Valley to Cherry Gardens 275 kV line 1
S>>S_NIL_194_WIND_P |  |  | Overload of Morphett Vale East to Cherry Gardens 275 kV line 1 for loss of Happy Valley to Morphett Vale East 275 kV line 1
S>>V_NIL_196_WIND_P |  |  | Overload of Cherry Gardens to Tungkillo 275 kV line 1 for loss of Tungkillo to Cherry Gardens 275 kV line 1
S>>S_NIL_209_WIND_P |  |  | Overload of Red Hill to Brinkworth 132 kV line 1 for loss of Bungama 275 kV / 132 kV Transformer 1
S>>S_NIL_210_WIND_P |  |  | Overload of Red Hill to Brinkworth 132 kV line 1 for loss of Davenport to Bungama 275 kV line 1
S>>S_NIL_211_WIND_P |  |  | Overload of Bungama to Snowtown Tee 132 kV line 1 for loss of Waterloo to Hummocks 132 kV line 1
S>>S_NIL_232_WIND_P |  |  | Overload of Templers to Roseworthy 132 kV line 1 for loss of Templers 275 kV / 132 kV Transformer 1
S>>V_NIL_233_WIND_P |  |  | Overload of Templers to Roseworthy 132 kV line 1 for loss of Para 275 kV / 132 kV Transformer 8
S>>S_NIL_234_WIND_P |  |  | Overload of Templers to Dorrien 132 kV line 1
S>>S_NIL_235_WIND_P |  |  | Overload of Templers to Dorrien 132 kV line 1 for loss of Templers to Para 275 kV line 1
S>>V_NIL_236_WIND_P |  |  | Overload of Para to Millbrook Tee 132 kV line 1
S>>V_NIL_237_WIND_P |  |  | Overload of Para to Millbrook Tee 132 kV line 1
S>>V_NIL_238_WIND_P |  |  | Overload of Cherry Gardens to Mt Barker 132 kV line 1
S>>V_NIL_239_WIND_P |  |  | Overload of Mt Barker to MHP No 3 Pump 132 kV line 1
S>>V_NIL_240_WIND_P |  |  | Overload of Mt Barker to MHP No 3 Pump 132 kV line 1 for loss of Cherry Gardens to Mt Barker 132 kV line 1
S>>S_NIL_244_WIND_P |  |  | Overload of Keith to Kincraig 132 kV line 1 for loss of South East to Penola West 132 kV line 1
V>>S_NIL_246_WIND_P |  |  | Overload of South East to Mt Gambier 132 kV line 1
V>>S_NIL_247_WIND_P |  |  | Overload of South East to Snuggery 132 kV line 1 for loss of South East to Mt Gambier 132 kV line 1
V>>S_NIL_248_WIND_P |  |  | Overload of Mt Gambier to Blanche 132 kV line 1 for loss of Snuggery to Snuggery 132 kV line 1
V>>S_NIL_249_WIND_P |  |  | Overload of Mt Gambier to Blanche 132 kV line 1 for loss of South East to Snuggery 132 kV line 1
V>>S_NIL_250_WIND_P |  |  | Overload of Blanche to Snuggery 132 kV line 1 for loss of Snuggery to Snuggery 132 kV line 1
V>>S_NIL_251_WIND_P |  |  | Overload of Blanche to Snuggery 132 kV line 1 for loss of South East to Snuggery 132 kV line 1
S>>S_NIL_252_WIND_P |  |  | Overload of Whyalla to Middleback 132 kV line 1
S>>S_NIL_253_WIND_P |  |  | Overload of Middleback to Yadnarie 132 kV line 1
S>>S_NIL_254_WIND_P |  |  | Overload of Yadnarie to Pt Lincoln 132 kV line 1
S>NIL_NIL_MYTX | 2009-09-11 | 1 | Outage=NIL; Limit LB2 generation to avoid OL Mayura 132/33 kV transformer #1.
S>NIL_DVPF_CLTX | 2009-10-14 | 1 | Out = NIL; Minimum SA generation to avoid OL Cultana 275/132 kV transformer on trip Playford - Davenport 275 kV line.
S>NIL_DVPF_CLWY | 2009-09-18 | 1 | Out = NIL; Minimum SA generation to avoid OL Cultana to Whyalla Terminal 132 kV line on trip Playford - Davenport 275 kV line.
N>>N-NIL_500_01S | 2010-01-07 | 1 | Out= Nil, avoid O/L Yass to Canberra (9) on trip of Dapto to Kangaroo Valley (18), Feedback
N>>N-NIL_500_03 | 2010-01-07 | 1 | Out= Nil, avoid O/L Yass to Canberra (9) on trip of Kangaroo Valley to Capital (3W), Feedback
N>>N-NIL_500_17N | 2010-01-07 | 1 | Out= Nil, avoid O/L Yass to Marulan (4) on trip of Kangaroo Valley to Dapto (18), Feedback
N>>N-NIL_500_17S | 2010-01-07 | 1 | Out= Nil, avoid O/L Marulan to Yass (4) on trip of Dapto to Kangaroo Valley (18), Feedback
N>>N-NIL_500_1A | 2010-01-07 | 1 | Out=Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback
N>>N-NIL_500_1E | 2010-01-07 | 1 | Out=Nil, avoid Liddel to Newcastl (81) O/L on loss of Liddell to Tomago (82), Feedback
N>>N-NIL_500_1G | 2010-01-07 | 1 | Out=Nil, avoid Vales Pt to Munmorah (23) O/L on trip of Vales Pt to Sydney North(22), Feedback
N>>N-NIL_500_1N | 2010-01-07 | 1 | Out= NIL, avoid Liddell to Tomago(82) O/L on Liddell to Newcastle(81) trip; Feedback
N>>N-NIL_500_1O | 2010-01-07 | 1 | Out= Nil, avoid Liddell to Newcastle (81) O/L on Bayswater to Regentville (31) trip, Feedback
N>>N-NIL_500_1R | 2010-01-07 | 1 | Out= Nil, avoid O/L Vales Point to Munmorah (23) on trip of Eraring to Vineyard (25), Feedback
N>>N-NIL_500_1S | 2010-01-07 | 1 | Out= NIL, avoid Liddell to Newcastle (81) O/L on Nil trip; Feedback
N>>N-NIL_500_1T | 2010-01-07 | 1 | Out= NIL, avoid Liddell to Tomago (82) O/L on Nil trip; Feedback
N>>N-NIL_500_1WN | 2010-01-07 | 1 | Out= Nil, avoid Yass to Marulan (5) O/L on Yass-Marulan(4) trip, Feedback
N>>N-NIL_500_1WS | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Yass (5) O/L on Marulan-Yass(4) trip, Feedback
N>>N-NIL_500_1XN | 2010-01-07 | 1 | Out= Nil, avoid Yass to Marulan (4) O/L on Yass-Marulan(5) trip, Feedback
N>>N-NIL_500_1XS | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Yass (4) O/L on Marulan-Yass(5) trip, Feedback
N>>N-NIL_500_1Y | 2010-01-07 | 1 | Out= Nil, avoid Yass to Marulan (4) O/L on Canberra-Capital(6) trip, Feedback
N>>N-NIL_500_1YS | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Yass (4) O/L on KangarooValley-Capital(3W) trip, Feedback
N>>N-NIL_500_1Z | 2010-01-07 | 1 | Out= Nil, avoid Yass to Marulan (5) O/L on Canberra-Capital(6) trip, Feedback
N>>N-NIL_500_1ZS | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Yass (5) O/L on KangarooValley-Capital(3W) trip, Feedback
N>>N-NIL_500_23N | 2010-01-07 | 1 | Out= Nil, avoid Yass to Marulan (5) O/L on KangarooValley-Dapto(18) trip, Feedback
N>>N-NIL_500_23S | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Yass (5) O/L on Dapto-KangarooValley(18) trip, Feedback
N>>N-NIL_500_28 | 2010-01-07 | 1 | Out= NIL, avoid Marulan to Dapto (8) O/L on Marulan-Avon(16) trip; Feedback
N>>N-NIL_500_29N | 2010-01-07 | 1 | Out= Nil, avoid Yass to Marulan (4) O/L on trip of Yass-Bannaby (61), Feedback
N>>N-NIL_500_29S | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Yass (4) O/L on trip of SydneyWest-Bannaby(39), Feedback
N>>N-NIL_500_31N | 2010-01-07 | 1 | Out= Nil, avoid Yass to Marulan (5) O/L on Yass-Bannaby(61) trip, Feedback
N>>N-NIL_500_31S | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Yass (5) O/L on trip of SydneyWest-Bannaby(39), Feedback
N>>N-NIL_500_36 | 2010-01-07 | 1 | Out= Nil, avoid Wagga to Jindera (62) O/L on trip of Nil, Feedback
N>>N-NIL_500_45 | 2010-01-07 | 1 | Out= Nil, avoid Yass to Bannaby (61) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-NIL_500_46 | 2010-01-07 | 1 | Out= Nil, avoid Dapto to KangarooValley (18) O/L on Marulan-Yass(4) trip; Feedback
N>>N-NIL_500_47 | 2010-01-07 | 1 | Out= Nil, avoid KangarooValley to Dapto (18) O/L on Yass-Marulan(5) trip; Feedback
N>>N-NIL_500_48 | 2010-01-07 | 1 | Out= Nil, avoid KangarooValley to Dapto (18) O/L on Yass-Marulan(4) trip; Feedback
N>>N-NIL_500_49 | 2010-01-07 | 1 | Out= Nil, avoid Dapto to KangarooValley (18) O/L on Marulan-Yass(5) trip; Feedback
N>>N-NIL_500_56 | 2010-01-07 | 1 | Out= Nil, avoid Yass to Bannaby (61) O/L on Yass-Marulan(4) trip; Feedback
N>>N-NIL_500_57 | 2010-01-07 | 1 | Out= Nil, avoid Dapto to KangarooValley (18) O/L on SydneyWest-Bannaby (39) trip; Feedback
N>>N-NIL_500_58 | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Dapto (8) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-NIL_500_59 | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Dapto (8) O/L on Canberra- Capital(6) trip; Feedback
N>>N-NIL_500_60 | 2010-01-07 | 1 | Out= Nil, avoid Yass to Bannaby (61) O/L on Canberra-Capital (6) trip; Feedback
N>>N-NIL_500_61 | 2010-01-07 | 1 | Out= Nil, avoid Yass to Bannaby (61) O/L on Yass-Marulan(5) trip; Feedback
N>>N-NIL_500_62 | 2010-01-07 | 1 | Out= Nil, avoid KangarooValley to Dapto (18) O/L on Marulan-Avon(16) trip; Feedback
N>>N-NIL_500_63 | 2010-01-07 | 1 | Out= Nil, avoid KangarooValley to Dapto (18) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-NIL_500_72 | 2010-01-07 | 1 | Out= Nil, avoid Yass to Bannaby (61) O/L on Dapto-SydneySouth(11) trip; Feedback
N>>N-NIL_500_73 | 2010-01-07 | 1 | Out= Nil, avoid Yass to Bannaby (61) O/L on Avon-Macarthur(17) trip; Feedback
N>>N-NIL_500_77 | 2010-01-07 | 1 | Out= Nil, avoid KangarooValley-Capital (3W) O/L on Yass-Canberra(9) trip; Feedback
N>>N-NIL_500_81 | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Yass (4) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-NIL_500_H01 | 2010-01-07 | 1 | Out = Nil, avoid Upper Tumut to Canberra(1) O/L on Nil trip; Feedback
N>>N-NIL_500_H02 | 2010-01-07 | 1 | Out = Nil, avoid Upper Tumut to Yass(2) O/L on Nil trip; Feedback
N>>N-NIL_500_H03 | 2010-01-07 | 1 | Out = Nil, avoid Lower Tumut to Yass(3) O/L on Nil trip; Feedback
N>>N-NIL_500_H051 | 2010-01-07 | 1 | Out = Nil, avoid Lower Tumut to Wagga(051) O/L on Nil trip; Feedback
N>>N-NIL_500_H060 | 2010-01-07 | 1 | Out = Nil, avoid Wodonga to Jindera(060) O/L on Nil trip; Feedback
N>>N-NIL_500_H07 | 2010-01-07 | 1 | Out = Nil, avoid Lower Tumut to Canberra (7) O/L on Nil trip; Feedback
N>>N-NIL_500_HA_15M | 2010-01-07 | 1 | Out = Nil, avoid Lower Tumut to Canberra (15 mins/5MRAS rating)(7) O/L on Upper Tumut to Canberra(1) trip; Feedback
N>>N-NIL_500_HB_15M | 2010-01-07 | 1 | Out = Nil, avoid Upper Tumut to Canberra (15 mins/5MRAS rating)(1) O/L on Lower Tumut to Canberra (7) trip; Feedback
N>>N-NIL_500_HC_15M | 2010-01-07 | 1 | Out = Nil, avoid Lower Tumut to Yass (15 mins/5MRAS rating)(3) O/L on Lower Tumut to Canberra (7) trip; Feedback
N>>N-NIL_500_HD_15M | 2010-01-07 | 1 | Out = Nil, avoid Upper Tumut to Canberra (15 mins/5MRAS rating)(1) O/L on Lower Tumut to Yass(3) trip; Feedback
N>>N-NIL_500_HE | 2010-01-07 | 1 | Out = Nil, avoid Lower Tumut to Upper Tumut(64) O/L on Murray to Upper Tumut(65) trip; Feedback
N>>N-NIL_500_HE_15M | 2010-01-07 | 1 | Out = Nil, avoid Upper Tumut to Canberra (15 mins)(1) O/L on Upper Tumut to Yass(2) trip; Feedback
N>>N-NIL_500_HF | 2010-01-07 | 1 | Out= Nil, avoid Upper Tumut to Lower Tumut (64) O/L on Murray-LowerTumut(66) Trip; Feedback
N>>N-NIL_500_HF_15M | 2010-01-07 | 1 | Out = Nil, avoid Upper Tumut to Yass (15mins)(2) O/L on Upper Tumut to Canberra(1) trip; Feedback
N>>N-NIL_500_HG_15M | 2010-01-07 | 1 | Out = Nil, avoid Upper Tumut to Yass (15mins)(2) O/L on Lower Tumut to Yass(3) trip; Feedback
N>>N-NIL_500_HH_15M | 2010-01-07 | 1 | Out = Nil, avoid Lower Tumut to Canberra (15 mins)(7) O/L on Lower Tumut to Yass(3) trip; Feedback
N>>N-NIL_500_HI_15M | 2010-01-07 | 1 | Out = Nil, avoid Upper Tumut to Canberra (15 mins)(1) O/L on Jindera to Wodonga(060) trip; Feedback
N>>N-NIL_500_HK_15M | 2010-01-07 | 1 | Out = Nil, avoid Upper Tumut to Yass(2) O/L on Canberra to Yass(9) trip; Feedback
N>>N-NIL_500_HL | 2010-01-07 | 1 | Out = Nil, avoid Lower Tumut to Upper Tumut(64) O/L on Nil trip; Feedback
N>>N-NIL_500_HM | 2010-01-07 | 1 | Out = Nil, avoid Upper Tumut to Lower Tumut(64) O/L on Nil trip; Feedback
N>>N-NIL_500_HU_15M | 2010-01-07 | 1 | Out = Nil, avoid Upper Tumut to Canberra (15 mins/5MRAS rating)(1) O/L on Jindera to Wagga(62) trip; Feedback
N>>N-NIL_500__K | 2010-01-07 | 1 | Out= Nil, avoid Wallerawang to Ingleburn (77) O/L on Wallerawang-SydneySouth(76) trip, Feedback
N>>N-NIL_500__L | 2010-01-07 | 1 | Out= Nil, avoid Wallerawang to Sydney South (76) O/L on Wallerawang-Ingleburn(77) trip; Feedback
N>>N-NIL_500__M | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Avon (16) O/L on Marulan-Dapto(8) trip; Feedback
N>>N-NIL_500__N | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Avon (16) O/L on KangarooValley-Dapto(18) trip; Feedback
N>>N-NIL_500__O | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Avon (16) O/L on Canberra-Capital(6) trip; Feedback
N>>N-NIL_500__P | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Avon (16) O/L on Yass-Bannaby (61) trip; Feedback
N>>N-NIL_500__R | 2010-01-07 | 1 | Out= Nil, avoid Marulan to Avon (16) O/L on Wallerawang-SydneySouth(76) trip; Feedback
N>>N-NIL_500__S | 2010-01-07 | 1 | Out= Nil, avoid MtPiper to Wallerawang (70) O/L on MtPiper to Wallerawang (71) trip; Feedback
N>N-NIL_500_DC | 2010-01-07 | 1 | Out = Nil, avoid Armidale to Tamowrth(86) O/L on Armidale to Tamowrth(85) trip; Feedback
N>N-NIL_500_F7_15M | 2010-01-07 | 1 | Out = Nil, avoid Tamworth to Armidale (15 mins rating)(86) O/L on Tamorth to Armidale(85) trip; Feedback
N>N-NIL_500__4_15M | 2010-01-07 | 1 | Out = Nil, avoid Muswellbrook to Tamworth (15 mins rating)(88) O/L on Liddell to Tamworth(84) trip; Feedback
N>N-NIL_500__7 | 2010-01-07 | 1 | Out = Nil, avoid Tamworth to Armidale(86) O/L on Nil trip; Feedback
N>N-NIL_TE_E2 | 2009-12-11 | 2 | Out= Nil, avoid Koolkhan to Lismore (967) O/L on CoffsHarbour - Lismore (89) trip; Feedback, TG formulation in PD/ST
V>>N-NIL_500_HA | 2010-01-07 | 1 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback
V>>N-NIL_500_HB | 2010-01-07 | 1 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback
V>>N-NIL_500_HG | 2010-01-07 | 1 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback
V>>N-NIL_500_HH | 2010-01-07 | 1 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback
Q^NIL_FNQ | 2009-12-17 | 1 | Out=Nil, Far North Qld Voltage Stability limit for loss of either Chalumbin to Ross (857 or 858) 275kV line.
T>T_NIL_BL_110_18 |  |  | Outage = Nil, Basslink in service, avoid overloading Tungatinah to Lake Echo Tee No.2 110kV line (flow to North) for loss of Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line, Waddamana bus split by line loss, swamped if LE-LE2 line in service
T::T_NIL_1 | 2009-11-05 | 1 | Out = Nil, Basslink importing only, avoid transient instability for fault and trip of a Farrell to Sheffield line.
T::T_NIL_3 | 2008-06-12 | 1 | Out = Nil, Basslink importing only, avoid transient instability for fault and trip of the Palmerston to Sheffield line
T>>T_NIL_BL_3C | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Palmerston to Hadspen 220kV line for trip of the other Palmerston to Hadspen 220kV line (outage id's=31,32) taking into account NCSPS generation reduction
T>>T_NIL_BL_3E | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Palmerston to Hadspen 220kV line for trip of a Sheffield to Georgetown 220kV line (outage id's=34,35) taking into account NCSPS generation reduction
T>>T_NIL_BL_5+6_A | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tas gen to avoid post-contingent O/L on Hadspen to Georgetown, Sheffield to Georgetown for trip of Palmerston to Sheffield (outage id's=73,83) taking into account Basslink export available for SPS action
T>>T_NIL_BL_5+6_B | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tas gen to avoid post-contingent O/L on Hadspen to Georgetown, Sheffield to Georgetown for trip of Sheffield to Georgetown (outage id's=74,75,81,82) taking into account Basslink export available for SPS action
T>>T_NIL_BL_5C | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Hadspen to Georgetown 220kV line for trip of the other Hadspen to Georgetown 220kV line (outage id's=71,72) taking into account NCSPS generation reduction
T>>T_NIL_BL_5E | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Hadspen to Georgetown 220kV line for trip of a Sheffield to Georgetown 220kV line (outage id's=74,75) taking into account NCSPS generation reduction
T>>T_NIL_BL_6C | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Sheffield to Georgetown 220kV line for trip of the other Sheffield to Georgetown 220kV line (outage id's=81,82) taking into account NCSPS generation reduction
T>>T_NIL_BL_6D | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Sheffield to Georgetown 220kV line for trip of the Palmerston to Sheffield 220kV line (outage id=83) taking into account NCSPS generation reduction
T>>T_NIL_BL_EXP_1B | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Gordon to Chapel St 220kV line for trip of the other Gordon to Chapel St line (outage id's=1,2) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_2B | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Liapootah to Palmerston No.1 220kV line for trip of Liapootah to Palmerston No.2 line (outage id=21) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_3F | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Palmerston to Hadspen 220kV line for trip of other Palmerston to Hadspen 220kV line (outage id's=31,32) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_3G | 2007-06-21 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L either Palmerston to Hadspen 220kV line for trip of Palmerston to Sheffield 220kV line (outage id=33) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_4E | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Palmerston to Hadspen 110kV line for trip of other Palmerston to Hadspen 110kV line (outage id's=51,52) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_4F | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Palmerston to Hadspen 110kV line for trip of Palmerston 220/110kV transformer (outage id=53) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_5F | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Hadspen to Georgetown 220kV line for trip of Hadspen to Georgetown 220kV line (outage id's=71,72) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_5G | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Hadspen to Georgetown 220kV line for trip of Palmerston to Sheffield 220kV line (outage id=73) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_5H | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Hadspen to Georgetown 220kV line for trip of Sheffield to Georgetown 220kV line (outage id's=74,75) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_6E | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Sheffield to Georgetown 220kV line for trip of Sheffield to Georgetown line (outage id's=81,82) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_6F | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L Sheffield to Georgetown 220kV line for trip of Palmerston to Sheffield 220kV line (outage id=83) taking into account Basslink export available for SPS action
T>>T_NIL_BL_EXP_7C | 2007-02-27 | 1 | Outage = Nil, Basslink exporting, Hampshire link open, limit Tas gen to avoid post-contingent O/L of Farrell to Sheffield 220kV line for trip of Farrell to Sheffield line (outage id's=91,92) taking into account Basslink export available for SPS action
T>T_NIL_BL_110_1 | 2009-08-05 | 1 | Outage = Nil, Basslink in service, avoid overloading the Chapel Street to New Norfolk 110kV line (flow to south) for loss of New Norfolk to Creek Road 110kV line, feedback
T>T_NIL_BL_110_11 | 2009-08-05 | 1 | Outage = Nil, Basslink in service, avoid overloading the Meadowbank to New Norfolk (flow to south) 110kV line for loss of the Tarraleah to New Norfolk 110kV line, feedback
T>T_NIL_BL_110_18 | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid O/L Tungatinah to Lake Echo Tee No.1 line (flow to North) for loss of Waddamana to Lake Echo Tee to Tungatinah No.2 line radialising Bridgewater to Waddamana line from Bridgewater, swamped if LE-LE1 line open
T>T_NIL_BL_110_18B | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid overloading the Tungatinah to Lake Echo Tee No.2 110kV line (flow to North) for loss of the Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line, Waddamana bus split by line loss, swamped if LE-LE2 line open
T>T_NIL_BL_110_18BX | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid overloading Tungatinah to Lake Echo Tee No.2 110kV line (flow to North) for loss of Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line, Waddamana bus split by line loss, swamped if LE-LE2 line in service
T>T_NIL_BL_110_18X | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid O/L Tungatinah to Lake Echo Tee No.1 line (flow to North) for loss of Waddamana to Lake Echo Tee to Tungatinah No.2 line radialising Bridgewater to Waddamana line from Bridgewater, swamped if LE-LE1 line in service
T>T_NIL_BL_110_19 | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid O/L Waddamana to Lake Echo Tee No.1 line (flow to North) for loss of Tungatinah to Lake Echo Tee to Waddamana No.2 line, offloading Bridgewater to Waddamana line from Bridgewater, swamped if LE-LE1 line open
T>T_NIL_BL_110_19X | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid O/L Waddamana to Lake Echo Tee No.1 line (flow to North) for loss of Tungatinah to Lake Echo Tee to Waddamana No.2 line, offloading Bridgewater to Waddamana line from Bridgewater, swamped if LE-LE1 line in service
T>T_NIL_BL_110_2 | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid overloading the Bridgewater to Lindisfarne 110kV line for loss of the Meadowbank to New Norfolk 110kV line, feedback
T>T_NIL_BL_110_20 | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid overloading Waddamana to Lake Echo Tee No.2 110kV line (flow to North) for loss of Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line, Waddamana bus split by line loss, swamped if LE-LE2 line open
T>T_NIL_BL_110_20X | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid overloading Waddamana to Lake Echo Tee No.2 110kV line (flow to North) for loss of Tungatinah to Lake Echo Tee to Waddamana No.1 110kV line, Waddamana bus split by line loss, swamped if LE-LE2 line in service
T>T_NIL_BL_110_21 | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid overloading the Waddamana to Bridgewater 110kV line for loss of the Meadowbank to New Norfolk 110kV line, feedback
T>T_NIL_BL_110_22A | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid overloading the Waddamana to Palmerston 110kV line (flow to North) for loss of the Liapootah to Palmerston 220kV line, feedback
T>T_NIL_BL_110_22B | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid overloading the Waddamana to Palmerston 110kV line (flow to South) for loss of the Liapootah to Palmerston 220kV line, feedback
T>T_NIL_BL_110_23 | 2009-08-05 | 1 | Out= Nil, avoid overloading the Palmerston to Waddamana 110 kV line (flow to south) on trip of Liapootah to Cluny Tee to Chapel St 220 kV line, Feedback
T>T_NIL_BL_110_24 | 2009-08-05 | 1 | Outage = Nil, avoid overloading Lindisfarne to Risdon No.1 110kV line (flow from Risdon to Lindisfarne) for loss of the Lindisfarne to Risdon No. 2 110kV line, feedback
T>T_NIL_BL_110_24B | 2009-08-05 | 1 | Outage = Nil, avoid overloading Lindisfarne to Risdon No.2 110kV line (flow from Risdon to Lindisfarne) for loss of the Lindisfarne to Risdon No. 1 110kV line, feedback
T>T_NIL_BL_110_25 | 2010-01-13 | 2 | Out = Nil, avoid O/L Lake Echo No. 1 or No. 2 Tee line, feeback.
T>T_NIL_BL_110_4 | 2006-08-07 | 1 | Out = Nil, Basslink in service, avoid O/L a Hadspen to Trevallyn line for loss of the other Hadspen to Trevallyn line
T>T_NIL_BL_110_6 | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid overloading the Tarraleah to New Norfolk No.1 110kV line for loss of the Meadowbank to New Norfolk 110kV line, feedback
T>T_NIL_BL_110_7 | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid overloading the Tarraleah to Meadowbank 110kV line for loss of the Tarraleah to New Norfolk No. 2 110kV line, feedback
T>T_NIL_BL_110_8 | 2009-08-05 | 1 | Outage = Nil, avoid overloading the New Norfolk to Creek Road 110kV line (flow to south) for loss of the New Norfolk to Chapel St 110kV line, feedback
T>T_NIL_BL_110_9A | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid overloading Tarraleah to Tungatinah No.1 110kV line (flow to South) for loss of the other Tarraleah to Tungatinah 110kV line, feedback
T>T_NIL_BL_110_9B | 2009-05-12 | 1 | Outage = Nil, Basslink in service, avoid overloading Tarraleah to Tungatinah No.2 110kV line (flow to South) for loss of the other Tarraleah to Tungatinah 110kV line, feedback
T>T_NIL_BL_1A | 2006-08-16 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Gordon to Chapel Street 220kV lines
T>T_NIL_BL_220_13 | 2009-11-09 | 1 | Outage = Nil, Basslink in service, avoid O/L a Chapel Street 220/110kV transformer for loss of a parallel transformer, Feedback
T>T_NIL_BL_220_6A | 2009-10-07 | 1 | Outage = Nil, Basslink in service, avoid overloading the Palmerston to Sheffield 220kV line (flow to North) for loss of a Sheffield to Georgetown 220kV line, feedback equation, swamp if Basslink exporting
T>T_NIL_BL_220_6B | 2009-07-03 | 1 | Outage = Nil, Basslink in service, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation
T>T_NIL_BL_220_7A | 2009-10-15 | 1 | Outage = Nil, avoid overloading the Liapootah to Cluny Tee 220kV line section (flow to South) for loss of Liapootah to Chapel Street No. 2 220kV line, feedback equation.
T>T_NIL_BL_220_7B | 2009-07-23 | 2 | Outage = Nil, avoid overloading the Liapootah to Cluny Tee 220kV line section (flow to North) for loss of Liapootah to Chapel Street No. 2 220kV line, feedback equation.
T>T_NIL_BL_220_8A | 2009-10-15 | 1 | Outage = Nil, avoid overloading the Liapootah to Chapel St No. 2 220kV line (flow to South) for loss of Liapootah to Cluny Tee to Chapel Street 220kV line, feedback equation.
T>T_NIL_BL_220_8B | 2009-08-05 | 1 | Outage = Nil, avoid overloading the Liapootah to Chapel St No. 2 220kV line (flow to North) for loss of Liapootah to Cluny Tee to Chapel Street 220kV line, feedback equation.
T>T_NIL_BL_220_9A | 2009-10-15 | 1 | Outage = Nil, avoid overloading the Cluny Tee to Chapel St 220kV line section (flow to South) for loss of Liapootah to Chapel Street No. 2 220kV line, feedback equation.
T>T_NIL_BL_220_9B | 2009-07-24 | 1 | Outage = Nil, avoid overloading the Cluny Tee to Chapel St 220kV line section (flow to North) for loss of Liapootah to Chapel Street No. 2 220kV line, feedback equation.
T>T_NIL_BL_2A | 2009-06-15 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Liapootah to Palmerston No.1 220kV line, feedback equation
T>T_NIL_BL_3A | 2010-01-13 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent overloading the Palmerston to Hadspen No.1 220kV line (flow to North), feedback equation
T>T_NIL_BL_3B | 2010-01-13 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent overloading the Palmerston to Hadspen No.2 220kV line (flow to North), feedback equation
T>T_NIL_BL_3D | 2007-06-21 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent overloading either Palmerston to Hadspen 220kV line for trip of the Palmerston to Sheffield 220kV line (outage id=33) taking into account NCSPS generation reduction
T>T_NIL_BL_4A | 2009-06-15 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Palmerston to Hadspen No.3 110kV line, feedback equation
T>T_NIL_BL_4B | 2009-06-15 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Palmerston to Hadspen No.4 110kV line, feedback equation
T>T_NIL_BL_4C | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent overloading either Palmerston to Hadspen 110kV line for trip of the other Palmerston to Hadspen 110kV line taking into account NCSPS generation reduction
T>T_NIL_BL_4D | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent overloading either Palmerston to Hadspen 110kV line for trip of the Palmerston 220/110kV transformer taking into account NCSPS generation reduction
T>T_NIL_BL_5A | 2010-01-13 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent overloading the Hadspen to Georgetown No.1 220kV line (flow to North), feedback equation
T>T_NIL_BL_5B | 2010-01-13 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent overloading the Hadspen to Georgetown No.2 220kV line (flow to North), feedback equation
T>T_NIL_BL_5D | 2007-02-13 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent overloading either Hadspen to Georgetown 220kV line for trip of the Palmerston to Sheffield 220kV line taking into account NCSPS generation reduction
T>T_NIL_BL_6A | 2010-01-13 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent overloading the Sheffield to Georgetown No.1 220kV line (flow to North), feedback equation
T>T_NIL_BL_6B | 2010-01-13 | 1 | Outage = Nil, Basslink in service, limit Tasmanian generation to avoid pre-contingent overloading the Sheffield to Georgetown No.2 220kV line (flow to North), feedback equation
T>T_NIL_BL_7A | 2006-08-16 | 1 | Outage = Nil, Basslink in service, Hampshire link open, limit Tasmanian generation to avoid pre-contingent and post-contingent overloading the Farrell to Sheffield 220kV lines
T>T_NIL_BL_7B | 2006-01-05 | 1 | Outage = Nil, Basslink exporting, Hampshire link open, limit Tasmanian generation to avoid post-contingent overloading of either Farrell to Sheffield 220kV lines for trip of the other Farrell to Sheffield line taking into account NCSPS gen reduction
T>T_NIL_BL_EXP_3H | 2009-06-15 | 1 | Outage = Nil, Basslink exporting, limit Tasmanian generation to avoid post-contingent O/L a Palmerston to Hadspen 220kV line for trip of Sheffield to Georgetown 220kV line (outage id's=34,35) taking into account Basslink export available for SPS action
T>T_NIL_BL_IMP_1B | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading either Gordon to Chapel St 220kV line for trip of the other Gordon to Chapel St line with no SPS action
T>T_NIL_BL_IMP_2B | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading the Liapootah to Palmerston No.1 220kV line (flow to North) for trip of the Liapootah to Palmerston No.2 line with no SPS action, feedback equation
T>T_NIL_BL_IMP_2C | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading the Liapootah to Palmerston No.1 220kV line (flow to South) for trip of the Liapootah to Palmerston No.2 line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3F | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3FF | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.2 220kV line (flow to North) for trip of the Palmerston to Hadspen No. 1 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3G | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3GG | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.2 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3H | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.1 220kV line (flow to North) for trip of either Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3HH | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.2 220kV line (flow to North) for trip of either Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3I | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.1 220kV line (flow to South) for trip of the Palmerston to Hadspen No. 2 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3II | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.2 220kV line (flow to South) for trip of the Palmerston to Hadspen No. 1 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3J | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.1 220kV line (flow to South) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3JJ | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.2 220kV line (flow to South) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3K | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen 220kV No.1 line (flow to South) for trip of either Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_3KK | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen 220kV No.2 line (flow to South) for trip of either Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_4E | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.3 110kV line (flow to North) for trip of the other Palmerston to Hadspen 110kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_4EE | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.4 110kV line (flow to North) for trip of the other Palmerston to Hadspen 110kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_4F | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading either Palmerston to Hadspen 110kV line (flow to North) for trip of the Palmerston 220/110kV transformer with no SPS action
T>T_NIL_BL_IMP_4G | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.3 110kV line (flow to South) for trip of the other Palmerston to Hadspen 110kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_4GG | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Palmerston to Hadspen No.4 110kV line (flow to South) for trip of the other Palmerston to Hadspen 110kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_4H | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading either Palmerston to Hadspen 110kV line (flow to South) for trip of the Palmerston 220/110kV transformer with no SPS action
T>T_NIL_BL_IMP_5F | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.1 220kV line (flow to North) for trip of the Hadspen to Georgetown No. 2 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5FF | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.2 220kV line (flow to North) for trip of the Hadspen to Georgetown No. 1 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5G | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.1 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5GG | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.2 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5H | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.1 220kV line (flow to North) for trip of either Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5HH | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.2 220kV line (flow to North) for trip of either Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5I | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.1 220kV line (flow to South) for trip of the Hadspen to Georgetown No. 2 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5II | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.2 220kV line (flow to South) for trip of the Hadspen to Georgetown No. 1 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5J | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.1 220kV line (flow to South) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5JJ | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.2 220kV line (flow to South) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5K | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.1 220kV line (flow to South) for trip of either Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_5KK | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Hadspen to Georgetown No.2 220kV line (flow to South) for trip of either Sheffield to Georgetown 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_6E | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.1 220kV line (flow to North) for trip of the other Sheffield to Georgetown line with no SPS action, fedback equation
T>T_NIL_BL_IMP_6EE | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.2 220kV line (flow to North) for trip of the other Sheffield to Georgetown line with no SPS action, fedback equation
T>T_NIL_BL_IMP_6F | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.1 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_6FF | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.2 220kV line (flow to North) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_6G | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.1 220kV line (flow to South) for trip of the Sheffield to Georgetown No. 2 220 kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_6GG | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.2 220kV line (flow to South) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_6H | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.1 220kV line (flow to South) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_6HH | 2010-01-07 | 1 | Outage = Nil, Basslink not exporting, limit Tasmanian generation to avoid post-contingent overloading Sheffield to Georgetown No.2 220kV line (flow to South) for trip of the Palmerston to Sheffield 220kV line with no SPS action, feedback equation
T>T_NIL_BL_IMP_7C | 2009-10-07 | 1 | Outage = Nil, Basslink not exporting, Hampshire link open, limit Tas gen to avoid post-contingent overloading of a Farrell to Sheffield 220kV line for trip of the other Farrell to Sheffield line with no SPS action
T>T_NIL_POAT110 | 2007-03-06 | 1 | Outage = Nil, avoid overloading a Poatina to Palmerston 110 kV line
T>T_NIL_POAT220 | 2007-03-06 | 1 | Outage = Nil, avoid overloading a Poatina to Palmerston 220 kV line
TVBL_ROC | 2006-12-27 | 1 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink
T^T_NIL_BL_1_DS | 2009-06-04 | 1 | Outage = Nil, Basslink in service, Palmerston 110kV bus not split, one Gordon machine in service, avoid voltage instability or violations for loss of the Gordon machine, dispatch equation only
T^T_NIL_BL_2_DS | 2009-06-04 | 1 | Outage = Nil, Basslink in service, Palmerston 110kV bus not split, two Gordon machines in service, avoid voltage instability or violations for loss of a Gordon machine, dispatch equation only
T^T_NIL_BL_2_PD | 2009-06-04 | 1 | Outage = Nil, Basslink in service, Palmerston 110kV bus not split, two Gordon machines in service, avoid voltage instability or violations for loss of a Gordon machine, dispatch pre-equation only
T^T_NIL_BL_3_DS | 2009-06-04 | 1 | Outage = Nil, Basslink in service, Palmerston 110kV bus not split, three Gordon machines in service, avoid voltage instability or violations for loss of a Gordon machine, dispatch equation only
T^T_NIL_BL_4_DS | 2009-06-04 | 1 | Outage = Nil, Basslink in service, Palmerston 110kV bus not split, avoid voltage instability or violations for loss of a Gordon to Chapel St 220 kV line, dispatch equation only
T^T_NIL_BL_4_PD | 2009-06-04 | 1 | Outage = Nil, Basslink in service, Palmerston 110kV bus not split, avoid voltage instability or violations for loss of a Gordon to Chapel St 220 kV line, pre-dispatch equation only
T^T_NIL_BL_5_DS | 2009-10-15 | 1 | Outage = Nil, Palmerston 110kV bus not split, avoid voltage instability or violations for loss of a Liapootah to Cluny Tee to Chapel St 220 kV line, dispatch equation only.
T^T_NIL_BL_5_PD | 2009-06-29 | 1 | Outage = Nil, Basslink in service, Palmerston 110kV bus not split, avoid voltage instability or violations for loss of a Liapootah to Cluny Tee to Chapel St 220 kV line, pre-dispatch equation only
T^V_NIL_BL_6 | 2009-06-24 | 1 | Outage = Nil, Basslink in service, limit Basslink flow to Victoria to avoid transient over-voltage (TOV) for loss of Basslink
T_TAMARCCGT_GCS | 2009-08-11 | 1 | Tamar Valley 220 kV CCGT Generation Control Scheme (GCS) constraint to manage effective size of generation constingencyfor loss of Tamar CCGT. Limit output of Tamar CCGT based on load available for shedding by Tamar GCS.
T_V_NIL_BL1 | 2008-05-26 | 1 | Out=Nil, Basslink no go zone limits Tas to Vic
T_V_NIL_FCSPS | 2007-02-06 | 1 | Basslink limit from Tas to Vic for generation enabled for FCSPS
V:T_NIL_BL_1 | 2009-06-15 | 1 | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability

## All Outages
Hash | WONUM | PARENT | W/O Type | Has child | Equipment Name | LT8 | LT9 | WO20 | Equipment No | Outage Reason | Work Description | Requesting Organisation | Project ID | Project Description | Equipment Type | Work Group | Voltage | ACCC_TYPE | ACCC_PLANT | ACCC_CRITICALITY | Exclusion Code | Comments
_1022880138337.4930555556 | 10228801 |  | Parent | FALSE | NO.6 GEN TRANS NO.3 BUS 220KV CB AT HWPS | 38337.4931 | 39001.5757 | CONT | [12 empty] | 0
_Z41758B438606.6458333333 | Z41758B4 |  | Parent | FALSE | LNGS NO.1 GEN TRANS 220KV CB AT ATS | 38606.6458 | 38784.3438 | CONT | [12 empty] | 0
_Z41758B538609.6229166667 | Z41758B5 |  | Parent | FALSE | LNGS NO.2 GEN TRANS 220KV CB AT ATS | 38609.6229 | 38784.3403 | CONT | [12 empty] | 0
_1023313738610.3333333333 | 10233137 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT HWTS | 38610.3333 | 39082.5472 | CONT | 00009792 | SPIMAINT | Repair 22kV cable | SPIPOWER |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_1023330838611.9576388889 | 10233308 |  | Parent | FALSE | EX - NO.1 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 38611.9576 | 39147.8974 | CONT | [12 empty] | 0
_1023345038616.2395833333 | 10233450 |  | Parent | FALSE | EX - RTS NO.4 LINE/YPS NO.5 LINE CB AT ROTS | 38616.2396 | 39147.8989 | CONT | [12 empty] | 0
_1023350938618.5590277778 | 10233509 |  | Parent | FALSE | EX - SMTS LINE/A2 TRANS 500KV CB AT KTS | 38618.559 | 39147.9 | DAILY | [12 empty] | 0
_1023324738624.7152777778 | 10233247 |  | Parent | FALSE | EX - SBY 66KV FDR CB AT KTS | 38624.7153 | 39147.9015 | CONT | [12 empty] | 0
_1023387138630.9256944445 | 10233871 |  | Parent | FALSE | HYTS NO.2/SYTS NO.2 LINE 500KV CB AT MLTS | 38630.9257 | 38799.6146 | CONT | [12 empty] | 0
_1023535738673.4243055556 | 10235357 |  | Parent | FALSE | NO.3 66KV BUS AT RCTS | 38673.4243 | 38874.4062 | CONT | 00357242 | DB_AUG | Isolated for future work on No3 22kV Bus | SPIPOWER |  |  | Bus | Alstom | 66 |  |  |  | 0
_1023535638673.4708333333 | 10235356 |  | Parent | FALSE | 2-3 66KV TIE BUS NO.2 BUS SIDE ISOL AT RCTS | 38673.4708 | 38834.3403 | CONT | [12 empty] | 0
_V52158A238692.6493055556 | V52158A2 |  | Parent | FALSE | FUTURE F1 TRANS 500KV CB AT SMTS | 38692.6493 | 39147.919 | CONT | [12 empty] | 0
_1023619738704.6458333333 | 10236197 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT ATS | 38704.6458 | 38737.5312 | CONT | 00350821 | SPIMAINT | Repair damaged ROI Blade | SPIPOWER |  |  | Capacitors | Western | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1023682638709.7395833333 | 10236826 |  | Parent | FALSE | EX - MWTS NO.1 220KV LINE NO.1 BUS CB AT JLTS | 38709.7396 | 38735.5569 | CONT | [12 empty] | 0
_1023687138717.6513888889 | 10236871 |  | Parent | FALSE | W3 GEN TRANS NO.2 BUS 220KV CB AT YPS | 38717.6514 | 38720.525 | CONT | [12 empty] | 0
_1023688538718.5673611111 | 10236885 |  | Parent | FALSE | KTS 500KV LINE AT SMTS | 38718.5674 | 38719.616 | CONT | 00012441 | FORCED | TYREE CVT Leaking oil bellows W P/H | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023688938719.2513888889 | 10236889 |  | Parent | FALSE | 2-4 500KV BUS TIE CB AT LYPS | 38719.2514 | 38719.2896 | CONT | [12 empty] | 0
_1009867038720.2729166667 | 10098670 |  | Parent | FALSE | NO.1 11/220KV TRANS BANK AT MPS | 38720.2729 | 38723.6069 | CONT | 00001082 | SPIMAINT | O/HAUL No1 & 2 Transformers without Div Sw (EH) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X34458C238721.2930555556 | X34458C2 |  | Parent | TRUE | NO.4 66KV BUS AT BETS | 38721.2931 | 38721.4549 | DAILY | 00016367 | SPICAPX | Out W/O No4 66kV bus for NEMMCO met proj | SPIPOWER | X344 | X344 - NEM METERING UPGRADE - STAGE 3 | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X34458C338721.2930555556 | X34458C3 | X34458C2 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT BETS | 38721.2931 | 38721.4549 | DAILY | 00350819 | SPICAPX | Rebate W/O No 2A cap bk during NEMMCO bus outage | SPIPOWER | X344 | X344 - NEM METERING UPGRADE - STAGE 3 | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X34458C438721.2930555556 | X34458C4 | X34458C2 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 38721.2931 | 38721.4549 | DAILY | 00016274 | SPICAPX | Rebate W/O No 2B cap bk during NEMMCO bus outage | SPIPOWER | X344 | X344 - NEM METERING UPGRADE - STAGE 3 | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X34458C538721.2930555556 | X34458C5 | X34458C2 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 38721.2931 | 38721.4549 | DAILY | 00016040 | SPICAPX | Perf calc W/O No2 Tr 66 during NEMMCO bus outage | SPIPOWER | X344 | X344 - NEM METERING UPGRADE - STAGE 3 | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023635638721.3770833333 | 10236356 |  | Parent | TRUE | B3 TRANS 66KV CB AT MWTS | 38721.3771 | 38721.5625 | DAILY | [12 empty] | 0
_1023635838721.3770833333 | 10236358 | 10236356 | Child | FALSE | B3 220/66KV TRANS AT MWTS | 38721.3771 | 38721.5625 | DAILY | 00010267 | SPIMAINT | Avail of Plant SFT on CB C.T's for accuracy tests | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023636038721.3770833333 | 10236360 | 10236356 | Child | FALSE | HWPS-MPS 220KV LINE AT MWTS | 38721.3771 | 38721.5625 | DAILY | 00016132 | SPIMAINT | Rebate for SFT on CB C.T's for accuracy tests | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X34458C138721.4659722222 | X34458C1 |  | Parent | FALSE | NO.2 22KV BUS VT AT BETS | 38721.466 | 38721.5687 | DAILY | [12 empty] | 0
_X34458C638722.2993055556 | X34458C6 |  | Parent | FALSE | NO.4 22KV BUS VT AT BETS | 38722.2993 | 38722.4007 | DAILY | [12 empty] | 0
_1023626338722.3052546296 | 10236263 |  | Parent | FALSE | NO.1 11/220KV TRANS 220KV ISOL AT MPS | 38722.3053 | 38723.5847 | CONT | [12 empty] | 0
_X34458C738722.4048611111 | X34458C7 |  | Parent | FALSE | EX - NO.3 66KV BUS VT AT BETS | 38722.4049 | 38722.5632 | DAILY | [12 empty] | 0
_1023701038722.8729166667 | 10237010 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 38722.8729 | 38725.625 | CONT | 00356086 | GENCO | Outage for Genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X25158G238723.3159722222 | X25158G2 |  | Parent | FALSE | AEMO METERING AT HWPS | 38723.316 | 38723.4826 | DAILY | [12 empty] | 0
_1023705938723.8791666667 | 10237059 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 38723.8792 | 38724.6903 | CONT | 00356084 | GENCO | HWPS No6 Gen Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1023703038725.1673611111 | 10237030 |  | Parent | FALSE | A1 TRANS NO.3 BUS 500KV CB TRANS SIDE ROI AT LYPS | 38725.1674 | 38725.7729 | DAILY | [12 empty] | 0
_1009788138725.2270833333 | 10097881 |  | Parent | FALSE | B2 GEN TRANS NO.3 BUS 500KV CB BUS SIDE ROI AT LYPS | 38725.2271 | 38725.4854 | DAILY | [12 empty] | 0
_1023693438727.2805555556 | 10236934 |  | Parent | FALSE | HWPS CONTROLS AT HWPS | 38727.2806 | 38727.4451 | DAILY | [12 empty] | 0
_1023636738727.2909722222 | 10236367 |  | Parent | FALSE | MLTS-HYTS 1 500KV W | 38727.291 | 38727.3007 | DAILY | 00022630 | SW_NEM | MLTS 500kV reactor switching | VENCORP |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1023714838727.9020833333 | 10237148 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.1 BUS CB AT LYPS | 38727.9021 | 38728.3694 | CONT | [12 empty] | 0
_1023714538728.0590277778 | 10237145 |  | Parent | FALSE | YWPS NO.4 220KV LINE AT YPS | 38728.059 | 38731.3931 | CONT | 00016428 | GENCO | SCAP for W4 isolation and earth | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X34458D238728.2722222222 | X34458D2 |  | Parent | FALSE | NO.1 66KV BUS VT AT HTS | 38728.2722 | 38728.5833 | DAILY | [12 empty] | 0
_1023636938728.2923611111 | 10236369 |  | Parent | FALSE | MLTS-HYTS 2 500KV W | 38728.2924 | 38728.2972 | DAILY | 00022633 | SW_NEM | MLTS 500kV reactor switching | VENCORP |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1023607938728.30625 | 10236079 |  | Parent | FALSE | R2 220/66/22KV TRANS AT KGTS | 38728.3063 | 38728.6354 | DAILY | 00017344 | SPIMAINT | Out W/O No2 trans oil/air leaks | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X34458D338729.2722222222 | X34458D3 |  | Parent | FALSE | NO.2 66KV BUS VT AT HTS | 38729.2722 | 38729.4069 | DAILY | [12 empty] | 0
_1023716238729.2909722222 | 10237162 |  | Parent | FALSE | BLLY 500KV LINE AT LYPS | 38729.291 | 38729.6278 | DAILY | 00360516 | 3RDPARTY | SCAP for BLLY | 3RDPARTY |  |  | Circuits | Eastern | 500 | CONNECTION ASSET | EXCLUDED |  | 3
_X34458D438729.4166666667 | X34458D4 |  | Parent | FALSE | NO.3 66KV BUS VT AT HTS | 38729.4167 | 38729.5722 | DAILY | [12 empty] | 0
_1023717338730.2013888889 | 10237173 |  | Parent | FALSE | AUX C 220KV TRANS LINE AT HWPS | 38730.2014 | 38730.6208 | DAILY | 00356088 | GENCO | SCAP 3122 for HWPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1023692938730.2555555556 | 10236929 |  | Parent | FALSE | EX - BLTS 220KV LINE NO.1 BUS CB AT KTS | 38730.2556 | 38730.5993 | DAILY | [12 empty] | 0
_1010410538730.2916666667 | 10104105 |  | Parent | FALSE | NO.2 22KV CAPACITOR BANK Y & Y BACKUP PROT AT RWTS | 38730.2917 | 38730.5118 | DAILY | [12 empty] | 0
_1023722338730.8194444444 | 10237223 |  | Parent | FALSE | NO.5 GEN TRANS 220KV CB BUS SIDE ROI AT HWPS | 38730.8194 | 38732.4292 | CONT | [12 empty] | 0
_Z50758A338731.2277777778 | Z50758A3 |  | Parent | FALSE | RWTS-TTS 220KV WT | 38731.2278 | 38732.6708 | CONT | 00119311 | VEN_AUG | erect new tower 458 | SPIPOWER | Z507 | Z507 - (TTS-RWTS, TTS-TSTS) 220KV LINE UPGRADES | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023773338731.6388888889 | 10237733 |  | Parent | FALSE | EX - NO.3 66KV CAPACITOR BANK CB AT BETS | 38731.6389 | 38731.734 | DAILY | [12 empty] | 0
_1023702038732.2652777778 | 10237020 |  | Parent | FALSE | EX - NO.1 AUX TRANS AT MTS | 38732.2653 | 38732.4444 | DAILY | 00004556 | DBPROX | VSCAP for Alinta | DISTCO |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_1009930038733.2368055556 | 10099300 |  | Parent | FALSE | B2 220/66KV TRANS AT WMTS | 38733.2368 | 38733.6236 | DAILY | 00003235 | SPIMAINT | O/HAUL Transformer Div Mechanism (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023721838733.2534722222 | 10237218 |  | Parent | FALSE | NO.3 66KV BUS AT ERTS | 38733.2535 | 38733.6292 | DAILY | 00004383 | FORCED | REPLACE DEFECTIVE BUS CVT | SPIPOWER |  |  | Bus | Eastern | 66 |  |  |  | 0
_1009930138734.23125 | 10099301 |  | Parent | FALSE | B3 220/66KV TRANS AT WMTS | 38734.2312 | 38735.6271 | CONT | 00003236 | SPIMAINT | O/HAUL Transformer Div Mechanism (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023451538736.2388888889 | 10234515 |  | Parent | FALSE | EX - O.O.S TRANS W/PH UNIT C AT TTS | 38736.2389 | 38736.7826 | DAILY | 00026067 | SPIMAINT | Bushing oil level low | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009934938736.3361111111 | 10099349 |  | Parent | FALSE | 2-3 220KV BUS TIE CB AT WMTS | 38736.3361 | 38736.5806 | DAILY | [12 empty] | 0
_1023634238736.3409722222 | 10236342 |  | Parent | TRUE | SYTS NO.2 500KV LINE NO.1 BUS CB AT MLTS | 38736.341 | 38736.3979 | DAILY | [12 empty] | 0
_1023635238736.3409722222 | 10236352 | 10236342 | Child | FALSE | SYTS NO.2 500KV LINE AT MLTS | 38736.341 | 38736.3979 | DAILY | 00022778 | SPIMAINT | Rebate W/O SYTS No2 Line for CB CT samples at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023636838736.3694444445 | 10236368 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT MLTS | 38736.3694 | 38736.4771 | DAILY | [12 empty] | 0
_1023727138737.2222222222 | 10237271 |  | Parent | FALSE | B2 220/66KV TRANS AT WMTS | 38737.2222 | 38737.5611 | DAILY | 00003235 | SPIMAINT | replace faulty cooling pump | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023432538737.2340277778 | 10234325 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 38737.234 | 38737.4444 | DAILY | 00001147 | SPIMAINT | Bushing oil level low | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009930238737.2673611111 | 10099302 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT WMTS | 38737.2674 | 38737.4444 | DAILY | 00003239 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X25158G338737.28125 | X25158G3 |  | Parent | FALSE | AEMO METERING AT HWPS | 38737.2812 | 38737.3299 | DAILY | [12 empty] | 0
_1023637438737.2923611111 | 10236374 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB AT MLTS | 38737.2924 | 38737.3694 | DAILY | [12 empty] | 0
_1023733238737.2958333333 | 10237332 |  | Parent | FALSE | BLLY 500KV LINE AT LYPS | 38737.2958 | 38740.691 | CONT | 00360516 | GENCO | SCAP to Siemens | GENCO |  |  | Circuits | Eastern | 500 | CONNECTION ASSET | EXCLUDED |  | 0
_1023772638737.7611111111 | 10237726 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 38737.7611 | 38737.7736 | DAILY | 00359891 | FAULT | RCTS: No1, No2 and 66kV BUSES and associated CB's | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1023772938737.7611111111 | 10237729 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 38737.7611 | 38737.7736 | DAILY | 00359892 | FAULT | RCTS: No1, No2 and 66kV BUSES and associated CB's | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1023773038737.7611111111 | 10237730 |  | Parent | FALSE | NO.1 66KV REACTOR AT RCTS | 38737.7611 | 38737.7736 | DAILY | 00016895 | FAULT | RCTS: No1, No2 and 66kV BUSES and associated CB's | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1023773138737.7611111111 | 10237731 |  | Parent | FALSE | NO.2 66KV REACTOR AT RCTS | 38737.7611 | 38737.7736 | DAILY | 00016897 | FAULT | RCTS: No1, No2 and 66kV BUSES and associated CB's | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z50758A438738.23125 | Z50758A4 |  | Parent | FALSE | RWTS-TTS 220KV WT | 38738.2312 | 38739.6201 | CONT | 00119311 | VEN_AUG | erect new tower 458 | SPIPOWER | Z507 | Z507 - (TTS-RWTS, TTS-TSTS) 220KV LINE UPGRADES | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V4D958A138738.2576388889 | V4D958A1 |  | Parent | FALSE | KTS -WMTS 1 220KV WT | 38738.2576 | 38738.6333 | DAILY | 00022718 | SPICAPX | replace suspension plates & defect repairs | SPIPOWER | V4D9 | V4D9 - (KTS-WMTS) REPLACE WORN ATTACHMENT PLATES T10 & T12 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V4D958A038739.2576388889 | V4D958A0 |  | Parent | FALSE | KTS -WMTS 2 220KV WT | 38739.2576 | 38739.5049 | DAILY | 00022719 | SPICAPX | replace suspension plates & defect repairs | SPIPOWER | V4D9 | V4D9 - (KTS-WMTS) REPLACE WORN ATTACHMENT PLATES T10 & T12 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858E238739.2895833333 | X2A858E2 |  | Parent | FALSE | EX - (O.O.S) NO.3 22KV CAPACITOR BANK ISOLATING CB AT BTS | 38739.2896 | 38739.5486 | DAILY | [12 empty] | 0
_1023743438739.9194444444 | 10237434 |  | Parent | FALSE | YPS -YWPS 1 220KV G | 38739.9194 | 38743.6694 | CONT | 00020517 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z43958A438740.2680555556 | Z43958A4 |  | Parent | FALSE | EX - GTS NO.1 220KV LINE AT KTS | 38740.2681 | 38740.5729 | DAILY | 00015985 | VEN_AUG | install tension monitor at tower 137 | SPIPOWER | Z439 | Z439 - (KTS,GTS) WIND MONITORING & RATING SCHEME 220KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z43958A538741.2298611111 | Z43958A5 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE AT KTS | 38741.2299 | 38741.6493 | DAILY | 00015986 | VEN_AUG | install tension monitor to tower 137 | SPIPOWER | Z439 | Z439 - (KTS,GTS) WIND MONITORING & RATING SCHEME 220KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023721338741.3159722222 | 10237213 |  | Parent | FALSE | NO.1 500KV BUS AT SYTS | 38741.316 | 38741.5979 | DAILY | 00001389 | SPIMAINT | investigate fitting of driers to bus | SPIPOWER |  |  | Bus | Western | 500 |  |  |  | 0
_1023746038741.3263888889 | 10237460 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT SVTS | 38741.3264 | 38741.3778 | DAILY | 00004824 | SPIMAINT | Blown Primary Fuse | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X23358B338742.2347222222 | X23358B3 |  | Parent | FALSE | B3 220/66KV TRANS AT FBTS | 38742.2347 | 38742.6813 | REPDAILY | 00002727 | SPICAPX | commission new wti, insert new temp probe | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023764538743.6555555556 | 10237645 |  | Parent | FALSE | DDTS-SMTS 2 330KV | 38743.6556 | 38743.6674 | DAILY | 00328507 | FAULT | Loss of DDTS-SMTS No 2 330kV Line | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023772238743.6708333333 | 10237722 |  | Parent | FALSE | EPS -TTS 1 220KV N | 38743.6708 | 38743.6778 | DAILY | 00331826 | FAULT | Loss of EPS-TTS 220kV Line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023764638743.6798611111 | 10237646 |  | Parent | FALSE | DDTS-SMTS 2 330KV | 38743.6799 | 38743.691 | DAILY | 00328507 | FAULT | Second loss of DDTS-SMTS No 2 330kV Line | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023755838744.9395833333 | 10237558 |  | Parent | FALSE | 2-4 500KV BUS TIE CB AT LYPS | 38744.9396 | 38744.9965 | DAILY | [12 empty] | 0
_Z50758A538745.2291666667 | Z50758A5 |  | Parent | FALSE | RWTS-TTS 220KV WT | 38745.2292 | 38745.6153 | REPDAILY | 00119311 | VEN_AUG | convert tower 424 from suspension to strain | SPIPOWER | Z507 | Z507 - (TTS-RWTS, TTS-TSTS) 220KV LINE UPGRADES | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z50758A538746.2319444444 | Z50758A5 |  | Parent | FALSE | RWTS-TTS 220KV WT | 38746.2319 | 38746.4924 | REPDAILY | 00119311 | VEN_AUG | convert tower 424 from suspension to strain | SPIPOWER | Z507 | Z507 - (TTS-RWTS, TTS-TSTS) 220KV LINE UPGRADES | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023725038746.4166666667 | 10237250 |  | Parent | FALSE | A 66/11KV S/S TRANS OLTC MECH AT LYPS | 38746.4167 | 38747.5472 | DAILY | [12 empty] | 0
_1023756438747.20625 | 10237564 |  | Parent | FALSE | AUX TRANS 'B' 220KV CB AT YPS | 38747.2063 | 38750.4667 | CONT | [12 empty] | 0
_1009924438747.2513888889 | 10099244 |  | Parent | FALSE | DDTS 330KV LINE NO.2 BUS CB AT WOTS | 38747.2514 | 38749.7292 | CONT | [12 empty] | 0
_1009961038747.2520833333 | 10099610 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 38747.2521 | 38751.5951 | CONT | [12 empty] | 0
_X23358B438748.2333333333 | X23358B4 |  | Parent | FALSE | B3 220/66KV TRANS AT FBTS | 38748.2333 | 38748.6389 | REPDAILY | 00002727 | SPICAPX | commission new wti, insert new temp probe | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023612138748.275 | 10236121 |  | Parent | FALSE | EX - B3 TRANS 220KV CB AT GTS | 38748.275 | 38748.3646 | DAILY | [12 empty] | 0
_1023761838748.525 | 10237618 |  | Parent | FALSE | NO.4 GEN TRANS 500KV LINE E/SW AT LYPS | 38748.525 | 38750.7292 | CONT | [12 empty] | 0
_Z50658A038748.5319444445 | Z50658A0 |  | Parent | FALSE | NO.4 22KV/415V S/S TRANS AT DDTS | 38748.5319 | 38750.5819 | CONT | 00003974 | SPICAPX | (PROJ X506) OUT W /O Relacement of S/S Trans | SPIPOWER | X506 | X506 - (DDTS) REPLACE NO.4 STATION SERVICE TRANSFORMER | Other Transformers | Alstom | 22 |  |  |  | 0
_1023735038748.5868055556 | 10237350 |  | Parent | FALSE | 2-4 500KV TIE BUS NO.4 BUS SIDE ROI AT HWTS | 38748.5868 | 38748.6049 | DAILY | [12 empty] | 0
_1009877538749.2638888889 | 10098775 |  | Parent | FALSE | NO.2 500KV BUS E/SW AT LYPS | 38749.2639 | 38750.5986 | CONT | [12 empty] | 0
_X23356B638750.2236111111 | X23356B6 |  | Parent | FALSE | B4 220/66KV TRANS AT FBTS | 38750.2236 | 38750.6146 | REPDAILY | 00002728 | SPICAPX | commission new wti, insert new probe & remove old | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023764238750.2381944445 | 10237642 |  | Parent | FALSE | A3 TRANS 500KV CB AT KTS | 38750.2382 | 38750.6111 | DAILY | [12 empty] | 0
_1009924638750.2479166667 | 10099246 |  | Parent | FALSE | HPS 66KV LINE CB AT WOTS | 38750.2479 | 38750.634 | DAILY | [12 empty] | 0
_1023761738750.2729166667 | 10237617 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT TSTS | 38750.2729 | 38750.4222 | DAILY | 00351937 | SPIMAINT | Investigate out of balance alarm | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1023759738750.59375 | 10237597 |  | Parent | FALSE | 2-4 500KV BUS TIE CB AT LYPS | 38750.5938 | 38751.4556 | CONT | [12 empty] | 0
_1023779738751.1944444444 | 10237797 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 38751.1944 | 38752.4194 | DAILY | 00003104 | FAULT | Cap Bank Trip failed cap cans | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1009929638752.2208333333 | 10099296 |  | Parent | FALSE | NO.3 22KV BUS AT WMTS | 38752.2208 | 38752.6681 | DAILY | 00003263 | SPIMAINT | O/HAUL - 22kv or below Indoor Bus (Generic) | SPIPOWER |  |  | Bus | Western | 22 |  |  |  | 0
_Z50358B138752.2541666667 | Z50358B1 |  | Parent | FALSE | RTS NO.4 220KV LINE AT ROTS | 38752.2542 | 38753.6167 | CONT | 00023969 | VEN_AUG | Replace RTS 4l horisontal section at ROTS | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2B458B238752.2805555556 | X2B458B2 |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 38752.2806 | 38752.6375 | REPDAILY | 00007452 | SPICAPX | Carry preliminary wiring for L3 prot replacement | SPIPOWER | X2B4 | X2B4 - (RWTS) REPLACE TRANSFMR FDR PROT DT2/L3WYS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023783038752.9444444444 | 10237830 |  | Parent | FALSE | NO.7 GEN TRANS LINE AT HWPS | 38752.9444 | 38754.4382 | CONT | 00356085 | GENCO | CB isolation for genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1009929538753.2381944445 | 10099295 |  | Parent | FALSE | NO.2 22KV BUS AT WMTS | 38753.2382 | 38753.6514 | DAILY | 00003262 | SPIMAINT | O/HAUL - 22kv or below Indoor Bus (Generic) | SPIPOWER |  |  | Bus | Western | 22 |  |  |  | 0
_1023775538753.2888888889 | 10237755 |  | Parent | FALSE | NO.2 66KV BUS AT WMTS | 38753.2889 | 38753.4042 | DAILY | 00003259 | SPIMAINT | repair hot spot on 66kv bus isolator | SPIPOWER |  |  | Bus | Western | 66 |  |  |  | 0
_Z50358B238753.5972222222 | Z50358B2 |  | Parent | FALSE | EX - RTS NO.4 LINE/YPS NO.5 LINE CB AT ROTS | 38753.5972 | 38772.5035 | CONT | [12 empty] | 0
_1009929838754.2722222222 | 10099298 |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT WMTS | 38754.2722 | 38754.6875 | DAILY | [12 empty] | 0
_1023783638754.5208333333 | 10237836 |  | Parent | FALSE | EX - KTS NO.3 220KV LINE NO.2 BUS CB AT GTS | 38754.5208 | 38754.6312 | DAILY | [12 empty] | 0
_1023766438755.2513888889 | 10237664 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 38755.2514 | 38756.5764 | CONT | [12 empty] | 0
_1023761738755.2680555556 | 10237617 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT TSTS | 38755.2681 | 38755.3528 | DAILY | 00351937 | SPIMAINT | Investigate out of balance alarm | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1023769738755.26875 | 10237697 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 38755.2688 | 38755.5451 | DAILY | 00022690 | HVCUST | Work at PTH | HVCUST |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z33458B938755.2944444444 | Z33458B9 |  | Parent | FALSE | EX - 3-4 220KV TIE BUS AT SVTS | 38755.2944 | 38758.5889 | CONT | 00082841 | VEN_AUG | Replace defective CB bushing & complete sec wiring | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Bus | Eastern | 220 |  |  |  | 0
_1023783138755.3868055556 | 10237831 |  | Parent | FALSE | CB CONTROL EQUIPMENT AT BATS | 38755.3868 | 38755.5681 | DAILY | [12 empty] | 0
_1023767738756.25625 | 10237677 |  | Parent | FALSE | B4 220/66KV TRANS AT TTS | 38756.2562 | 38756.2917 | DAILY | 00001543 | SPIMAINT | replace faulty cooling fans | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023768438757.2368055556 | 10237684 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT TTS | 38757.2368 | 38757.6444 | DAILY | 00001533 | SPIMAINT | replace faulty cooling fans | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023788438757.2548611111 | 10237884 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 38757.2549 | 38757.6299 | DAILY | [12 empty] | 0
_1023803438757.7395833333 | 10238034 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT GTS | 38757.7396 | 38758.5 | CONT | 00350421 | FORCED | Bus Side Isolator. latch broke when switching | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1009799638758.2388888889 | 10097996 |  | Parent | FALSE | B2 220/66KV TRANS AT ATS | 38758.2389 | 38758.5778 | DAILY | 00060871 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1007237538758.2506944445 | 10072375 |  | Parent | TRUE | YPS NO.1 220KV LINE NO.6 BUS CB AT HWPS | 38758.2507 | 38758.3535 | DAILY | [12 empty] | 0
_1023799938758.2506944445 | 10237999 | 10072375 | Child | FALSE | YPS NO.1 220KV LINE AT HWPS | 38758.2507 | 38758.3535 | DAILY | 00015795 | SPIMAINT | Rebate capture for bushing top up | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023788738758.2520833333 | 10237887 |  | Parent | FALSE | EX - A4 TRANS NO.1 BUS 500KV CB AT KTS | 38758.2521 | 38758.6035 | DAILY | [12 empty] | 0
_1010018938758.3111111111 | 10100189 |  | Parent | FALSE | HB 66KV FDR X PROT AT TSTS | 38758.3111 | 38758.5993 | DAILY | [12 empty] | 0
_1023734938758.4083333333 | 10237349 |  | Parent | FALSE | 1-3 500KV TIE BUS NO.3 BUS SIDE ROI AT HWTS | 38758.4083 | 38758.5563 | DAILY | [12 empty] | 0
_1023803738758.5 | 10238037 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT GTS | 38758.5 | 38758.5875 | DAILY | 00350421 | SPIMAINT | Fault No1 66kV Cap Bank W phase Bus Side Isolator | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1023808038758.9194444444 | 10238080 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 38758.9194 | 38758.9549 | DAILY | [12 empty] | 0
_1023808238759.1256944445 | 10238082 |  | Parent | FALSE | NO.6 GEN TRANS NO.4 BUS 220KV CB AT HWPS | 38759.1257 | 38759.8368 | CONT | [12 empty] | 0
_1023808338759.1256944445 | 10238083 |  | Parent | FALSE | NO.8 GEN TRANS 220KV CB AT HWPS | 38759.1257 | 38760.8069 | CONT | [12 empty] | 0
_X26858A738759.2333333333 | X26858A7 |  | Parent | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 38759.2333 | 38759.7451 | DAILY | 00017905 | SPICAPX | OUT W/O Replace strain insulators | SPIPOWER | X268 | X268 - (EPS-TTS) LINE INSULATOR REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023517738759.2555555556 | 10235177 |  | Parent | TRUE | EX - NO.1 220KV BUS AT MBTS | 38759.2556 | 38759.5312 | DAILY | 00004001 | SPIMAINT | Out W/O #1 220 Bus for repair of DDTS 1L CB BS ROI | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1023517838759.2555555556 | 10235178 | 10235177 | Child | FALSE | MBTS-DDTS 1 220KV NW | 38759.2556 | 38759.5312 | DAILY | 00060187 | SPIMAINT | Rebate W/O DDTS 1L during bus outage at MBTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023518038759.2555555556 | 10235180 | 10235177 | Child | FALSE | DPS -MBTS 220KV NW | 38759.2556 | 38759.5312 | DAILY | 00060195 | SPIMAINT | Rebate W/O DPS L during bus outage at MBTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023518138759.2555555556 | 10235181 | 10235177 | Child | FALSE | MBTS-EPS 1 220KV N | 38759.2556 | 38759.5312 | DAILY | 00055380 | SPIMAINT | Rebate W/O EPS 1L during bus outage at MBTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X2B458B438759.2777777778 | X2B458B4 |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 38759.2778 | 38760.6736 | CONT | 00007452 | SPICAPX | Cut over to new protection on L3 | SPIPOWER | X2B4 | X2B4 - (RWTS) REPLACE TRANSFMR FDR PROT DT2/L3WYS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023809238760.1284722222 | 10238092 |  | Parent | FALSE | NO.7 GEN TRANS 220KV CB AT HWPS | 38760.1285 | 38761.5451 | CONT | [12 empty] | 0
_1009961738761.2618055556 | 10099617 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 38761.2618 | 38768.6278 | CONT | [12 empty] | 0
_1023769538761.2680555556 | 10237695 |  | Parent | FALSE | NO.2 330KV CAPACITOR BANK AT WOTS | 38761.2681 | 38761.4549 | DAILY | 00354001 | TRANSGRD | Out W/O No2 330kV Cap bank- Spray weeds | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_1023809738761.4131944444 | 10238097 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 38761.4132 | 38761.4306 | DAILY | [12 empty] | 0
_1023813138761.4722222222 | 10238131 |  | Parent | FALSE | WMTS NO.2 220KV LINE CB AT FBTS | 38761.4722 | 38761.4819 | DAILY | [12 empty] | 0
_1024086238761.9479166667 | 10240862 |  | Parent | FALSE | L4 220/22KV TRANS AT RTS | 38761.9479 | 38762.0118 | CONT | 00007333 | FAULT | RTS: L4 220/22kV Trans Trip due to Possum | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009906138762.2881944444 | 10099061 |  | Parent | FALSE | DDTS NO.3 LINE/SHTS NO.3 LINE 220KV CB AT GNTS | 38762.2882 | 38764.5715 | CONT | [12 empty] | 0
_1023817338762.4340277778 | 10238173 |  | Parent | FALSE | BLLY 500KV LINE AT LYPS | 38762.434 | 38777.4236 | CONT | 00360516 | GENCO | BLLY-LYPS Line de energised for Bass Link | GENCO |  |  | Circuits | Eastern | 500 | CONNECTION ASSET | EXCLUDED |  | 0
_1023820638762.8451388889 | 10238206 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 38762.8451 | 38764.8486 | CONT | 00356082 | GENCO | HWPS No4 Gen Isolation for Powerstation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X2A958D938763.2326388889 | X2A958D9 |  | Parent | FALSE | SMTS-SYTS 2 500KV WT | 38763.2326 | 38763.6458 | DAILY | 00022643 | SPICAPX | make connections to new prot panel & commission | SPIPOWER | X2A9 | X2A9 - (MLTS,SYTS,KTS) REPLACE 500KV PROTECTION | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1022999138763.2611111111 | 10229991 |  | Parent | FALSE | B2 220/66KV TRANS AT RTS | 38763.2611 | 38763.5819 | DAILY | 00007331 | SPIMAINT | Repair Fan on B2 | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023764438763.5458333333 | 10237644 |  | Parent | FALSE | WBTS 220KV LINE NO.2 BUS CB AT HOTS | 38763.5458 | 38763.6049 | REPDAILY | [12 empty] | 0
_1023764438764.3416666667 | 10237644 |  | Parent | FALSE | WBTS 220KV LINE NO.2 BUS CB AT HOTS | 38764.3417 | 38764.6083 | REPDAILY | [12 empty] | 0
_X34358A338764.7423611111 | X34358A3 |  | Parent | FALSE | ROTS NO.8 220KV LINE AT YPS | 38764.7424 | 38765.2604 | CONT | 00016416 | SPICAPX | Cut over to new prot on YPS -ROTS 8 Lines | SPIPOWER | X343 | X343 - (ROTS,YPS,HWPS) UPGRADE PROT ON 6 OR 7 220KV LINES | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023860638765.6222222222 | 10238606 |  | Parent | FALSE | NO.4 GEN TRANS NO.2 BUS 220KV CB AT HWPS | 38765.6222 | 38766.3125 | CONT | [12 empty] | 0
_X46158B038766.2166666667 | X46158B0 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 38766.2167 | 38766.825 | CONT | 00006559 | SPICAPX | Out W/O No2 220 Bus to remove isol & tie bay J | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158B138766.2166666667 | X46158B1 | X46158B0 | Child | FALSE | EX - BATS-HOTS 220KV W | 38766.2167 | 38766.825 | REPDAILY | 00026089 | SPICAPX | Rebate W/O HOTS Line for removal of HOTS Tie | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158B238766.2166666667 | X46158B2 | X46158B0 | Child | FALSE | MLTS-BATS 2 220KV WY | 38766.2167 | 38766.825 | REPDAILY | 00022731 | SPICAPX | Rebate W/O MLTS 2 Line during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158B338766.2166666667 | X46158B3 | X46158B0 | Child | FALSE | BATS-TGTS 220KV WW | 38766.2167 | 38766.825 | REPDAILY | 00022665 | SPICAPX | Rebate W/O TGTS Line during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158B438766.2166666667 | X46158B4 | X46158B0 | Child | FALSE | B2 220/66KV TRANS AT BATS | 38766.2167 | 38766.825 | REPDAILY | 00006555 | SPICAPX | Perf calc W/O No2 Trans during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z50358A638766.2263888889 | Z50358A6 |  | Parent | TRUE | ROTS NO.4 220KV LINE AT RTS | 38766.2264 | 38767.5889 | CONT | 00021338 | VEN_AUG | Replace conections RTS & No 3 220kV Bus (1 day) | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z50358A738766.2263888889 | Z50358A7 | Z50358A6 | Child | FALSE | L4 220/22KV TRANS AT RTS | 38766.2264 | 38767.5889 | CONT | 00007333 | VEN_AUG | Avail of plant work order for No 3 bus outage | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z50358B338766.2263888889 | Z50358B3 | Z50358A6 | Child | FALSE | B3 220/66KV TRANS AT RTS | 38766.2264 | 38767.5889 | CONT | 00329288 | VEN_AUG | Avail of plant work order for No 3 bus outage | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X3F958A338766.2361111111 | X3F958A3 |  | Parent | FALSE | B4 220/66KV TRANS AT FBTS | 38766.2361 | 38770.6444 | CONT | 00002728 | SPICAPX | replace existing conservator with new one | SPIPOWER | X3F9 | X3F9 - (FBTS) REFURBISH B4 TRANSFORMER | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023822838766.2430555556 | 10238228 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT SMTS | 38766.2431 | 38766.6083 | DAILY | 00026101 | SPIMAINT | top up oil in bushings & replace repaired fan | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1023831938766.2611111111 | 10238319 |  | Parent | FALSE | EX - NO.1 22KV/415V S/S TRANS AT WMTS | 38766.2611 | 38766.3611 | DAILY | 00003238 | 3RDPARTY | VSCAP to Citipower | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 3
_1009929438766.2833333333 | 10099294 |  | Parent | FALSE | NO.1 22KV BUS AT WMTS | 38766.2833 | 38766.6431 | DAILY | 00003261 | SPIMAINT | O/HAUL - 22kv or below Indoor Bus (Generic) | SPIPOWER |  |  | Bus | Western | 22 |  |  |  | 0
_1023865838768.5034722222 | 10238658 |  | Parent | FALSE | SYN/COND AT FBTS | 38768.5035 | 38768.5958 | DAILY | 00002697 | FAULT | FBTS: Sync Cond Fault | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1022964738769.2381944445 | 10229647 |  | Parent | FALSE | EX - B3 220/66KV TRANS AT TTS | 38769.2382 | 38769.6264 | DAILY | 00001544 | SPIMAINT | contactor failure, replace T.I. & bushing top up | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023841238769.2680555556 | 10238412 |  | Parent | FALSE | S003 HWPS-HWTS 3 220KV | 38769.2681 | 38769.4424 | DAILY | [12 empty] | 0
_1009924538769.2930555556 | 10099245 |  | Parent | FALSE | JINDERA 330KV LINE NO.1 BUS CB AT WOTS | 38769.2931 | 38771.6556 | CONT | [12 empty] | 0
_1023922438769.3888888889 | 10239224 |  | Parent | FALSE | SYN/COND AT FBTS | 38769.3889 | 38769.4778 | DAILY | 00002697 | FAULT | Auto Operation of S/C | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V5D158A038770.2361111111 | V5D158A0 |  | Parent | FALSE | GTS NO.1 220KV LINE NO.2 BUS CB AT MLTS | 38770.2361 | 38770.8562 | DAILY | [12 empty] | 0
_1023922638770.5486111111 | 10239226 |  | Parent | FALSE | SYN/COND AT FBTS | 38770.5486 | 38770.5979 | DAILY | 00002697 | FAULT | Syn Cond auto Op | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1023880138771.5395833333 | 10238801 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK CB BUS SIDE ROI AT ATS | 38771.5396 | 38771.6285 | DAILY | [12 empty] | 0
_1023880638772.2513888889 | 10238806 |  | Parent | FALSE | T055 HWTS-CBTS 4 500KV | 38772.2514 | 38772.3854 | DAILY | [12 empty] | 0
_1022699138772.2666666667 | 10226991 |  | Parent | FALSE | B3 220/66KV TRANS AT FBTS | 38772.2667 | 38772.4326 | DAILY | 00002727 | SPIMAINT | Cooling fan failure | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158A738773.2138888889 | X46158A7 |  | Parent | TRUE | NO.1 220KV BUS AT BATS | 38773.2139 | 38774.6778 | CONT | 00006558 | SPICAPX | Out W/O No1 220 kV Bus to connect bay H & K Roi's | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158A838773.2138888889 | X46158A8 | X46158A7 | Child | FALSE | EX - BATS-HOTS 220KV W | 38773.2139 | 38774.6778 | CONT | 00026089 | SPICAPX | Rebate W/O BAT-HOTS Line during BATS Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158A938773.2138888889 | X46158A9 | X46158A7 | Child | FALSE | B1 220/66KV TRANS AT BATS | 38773.2139 | 38774.6778 | CONT | 00006554 | SPICAPX | Perf calc W/O No1 Trans during BATS Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023927538773.225 | 10239275 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 38773.225 | 38774.6806 | CONT | 00026089 | SPICAPX | Out W/O No1 220 kV Bus to connect bay H & K Roi's | SPIPOWER |  | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023859838773.2270833333 | 10238598 | Z50358B6 | Child | FALSE | L1 220/22KV TRANS AT RTS | 38773.2271 | 38774.5868 | CONT | 00007330 | VEN_AUG | Avail of plant work order for No 1 bus outage | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023859938773.2270833333 | 10238599 | Z50358B6 | Child | FALSE | B1 220/66KV TRANS AT RTS | 38773.2271 | 38774.5868 | CONT | 00007329 | VEN_AUG | Avail of plant work order for No 1 bus outage | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z50358B638773.2270833333 | Z50358B6 |  | Parent | TRUE | ROTS NO.1 220KV LINE AT RTS | 38773.2271 | 38774.5868 | CONT | 00021385 | VEN_AUG | Replace conections RTS & No 1 220kV Bus (1 day) | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009853638773.2416666667 | 10098536 |  | Parent | FALSE | 2B-4 220KV BUS TIE CB AT BLTS | 38773.2417 | 38774.5569 | CONT | [12 empty] | 0
_1023860538773.2743055556 | 10238605 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT WMTS | 38773.2743 | 38773.6792 | DAILY | 00003239 | 3RDPARTY | VSCAP for Citipower | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 3
_1023889638773.6701388889 | 10238896 |  | Parent | FALSE | NO.8 GEN TRANS 220KV CB BUS SIDE ROI AT HWPS | 38773.6701 | 38774.8021 | CONT | [12 empty] | 0
_X43458A238774.2611111111 | X43458A2 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MBTS | 38774.2611 | 38774.5556 | DAILY | 00004002 | SPICAPX | OUT W/O No2 220 Bus to remove MBY-CLPS fdr cond | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43458A338774.2611111111 | X43458A3 | X43458A2 | Child | FALSE | MBTS-DDTS 2 220KV NW | 38774.2611 | 38774.5556 | DAILY | 00060194 | SPICAPX | Rebate W/O MBTS-DDTS 2 Line during 220 bus outage | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43458A438774.2611111111 | X43458A4 | X43458A2 | Child | FALSE | B1 220/66KV TRANS AT MWTS | 38774.2611 | 38774.5556 | DAILY | 00351931 | SPICAPX | Perf calc W/O Tie Trans during 220 bus outage | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X43458A538774.2611111111 | X43458A5 | X43458A2 | Child | FALSE | MKPS-BOPS-MBTS 220KV NW | 38774.2611 | 38774.5556 | DAILY | 00060197 | SPICAPX | Rebate W/O MKPS-MBTS Line during 220 bus outage | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43458A638774.2611111111 | X43458A6 | X43458A2 | Child | FALSE | MBTS-EPS 2 220KV N | 38774.2611 | 38774.5556 | DAILY | 00055381 | SPICAPX | Rebate W/O MBTS-EPS 2 Line during 220 bus outage | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X43458A738774.2611111111 | X43458A7 | X43458A2 | Child | FALSE | WKPS-MBTS 220KV NW | 38774.2611 | 38774.5556 | DAILY | 00060196 | SPICAPX | Rebate W/O WKPS-MBTS Line during 220 bus outage | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023896238775.2430555556 | 10238962 |  | Parent | FALSE | SYN/COND AT BLTS | 38775.2431 | 38775.3257 | DAILY | 00002547 | FAULT | BLTS Sync Cond on manual | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1022969338775.2444444445 | 10229693 |  | Parent | FALSE | B1 220/66KV TRANS B/PH AT BLTS | 38775.2444 | 38775.5778 | DAILY | 00002602 | SPIMAINT | Bushing oil level low | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023846638775.2715277778 | 10238466 |  | Parent | FALSE | A2 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 38775.2715 | 38775.4965 | DAILY | [12 empty] | 0
_1023703338775.4111111111 | 10237033 |  | Parent | FALSE | EX - NO.2 REACTOR CB AT HOTS | 38775.4111 | 38775.4812 | DAILY | [12 empty] | 0
_X34358A538775.6708333333 | X34358A5 |  | Parent | FALSE | ROTS NO.7 220KV LINE AT YPS | 38775.6708 | 38776.0153 | CONT | 00016415 | SPICAPX | Cut over to new prot on YPS -ROTS 7 Lines | SPIPOWER | X343 | X343 - (ROTS,YPS,HWPS) UPGRADE PROT ON 6 OR 7 220KV LINES | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023879938776.2305555556 | 10238799 | Z50358B8 | Child | FALSE | L1 220/22KV TRANS AT RTS | 38776.2306 | 38778.5944 | CONT | 00007330 | VEN_AUG | Avail of plant work order for No 1 bus outage | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023880038776.2305555556 | 10238800 | Z50358B8 | Child | FALSE | B1 220/66KV TRANS AT RTS | 38776.2306 | 38778.5944 | CONT | 00007329 | VEN_AUG | Avail of plant work order for No 1 bus outage | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z50358B738776.2305555556 | Z50358B7 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 38776.2306 | 38778.5944 | CONT | 00004776 | VEN_AUG | Replace ROTS 5 L CB Bus Side isolator | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z50358B838776.2305555556 | Z50358B8 | Z50358B7 | Child | TRUE | NO.1 220KV CAPACITOR BANK AT ROTS | 38776.2306 | 38778.5944 | CONT | 00354024 | VEN_AUG | Rebate work order for No 1Bus outage | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1023063138776.2479166667 | 10230631 |  | Parent | FALSE | B3A 220/66KV TRANS B/PH AT BLTS | 38776.2479 | 38776.5861 | DAILY | 00002614 | SPIMAINT | Bushing oil level low & fan failure | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023894838776.2513888889 | 10238948 |  | Parent | FALSE | NO.3 66KV CAPACITOR BANK AT WMTS | 38776.2514 | 38776.3465 | DAILY | 00003191 | SPIMAINT | Out of balance alarm | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1009578038776.2722222222 | 10095780 |  | Parent | FALSE | EX - NO.1 TRANS 66KV CB AT HOTS | 38776.2722 | 38776.6535 | DAILY | [12 empty] | 0
_1010086938776.3034722222 | 10100869 |  | Parent | FALSE | NO.2 11/6.6KV AUXILARY TRANS PROT AT TSTS | 38776.3035 | 38776.3479 | DAILY | [12 empty] | 0
_1023822638776.3395833333 | 10238226 |  | Parent | FALSE | EX - RCTS 220KV LINE NO.2 TIE BUS AT HOTS | 38776.3396 | 38776.559 | DAILY | 00018947 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 |  |  |  | 0
_1010087038776.3541666667 | 10100870 |  | Parent | FALSE | NO.3 11/6.6KV AUXILARY TRANS PROT AT TSTS | 38776.3542 | 38776.3896 | DAILY | [12 empty] | 0
_1023726638776.5611111111 | 10237266 |  | Parent | FALSE | C 66/11KV S/S TRANS OLTC MECH AT LYPS | 38776.5611 | 38777.6264 | DAILY | [12 empty] | 0
_1023922738776.6569444445 | 10239227 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 38776.6569 | 38776.6993 | DAILY | 00019243 | FAULT | SVC Trip due S/S 415V supply fail to C/O | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1022699038777.2430555556 | 10226990 |  | Parent | FALSE | B1 220/66KV TRANS AT FBTS | 38777.2431 | 38777.5868 | DAILY | 00002726 | SPIMAINT | Cooling fan failure | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023909438777.7208333333 | 10239094 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 38777.7208 | 38778.4069 | CONT | [12 empty] | 0
_1023902438778.2590277778 | 10239024 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 38778.259 | 38778.4076 | DAILY | 00019243 | SPIMAINT | SVC Out Investigate S/S 415V supply failure to C/O | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1023908638778.3381944445 | 10239086 |  | Parent | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 38778.3382 | 38778.3674 | DAILY | 00003008 | SW_NEM | Reactor Sw on APD-HYTS-MLTS 2 Line | VENCORP |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 3
_1023909338778.3381944445 | 10239093 |  | Parent | FALSE | MAH012:REAC Y R/T (APD to HYTS/MLTS) [ APD-HYTS # 2 500KV LINE] | 38778.3382 | 38786.5944 | CONT | [12 empty] | 0
_1023910538778.4069444445 | 10239105 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 38778.4069 | 38811.5417 | CONT | [12 empty] | 0
_1023726438778.5944444445 | 10237264 |  | Parent | FALSE | B 66/11KV S/S TRANS OLTC MECH AT LYPS | 38778.5944 | 38779.6319 | DAILY | [12 empty] | 0
_1023895238779.2930555556 | 10238952 |  | Parent | FALSE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 38779.2931 | 38779.3354 | DAILY | [12 empty] | 0
_1023921938779.3243055556 | 10239219 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 38779.3243 | 38779.4382 | DAILY | 00019243 | SPIMAINT | Out W/O Investigate S/S 415V supply failure to C/O | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1023928538779.4666666667 | 10239285 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 38779.4667 | 38916.6104 | CONT | [12 empty] | 0
_1023924838779.5055555556 | 10239248 |  | Parent | FALSE | EX - NO.1 66KV BUS VT AT TGTS | 38779.5056 | 38779.6472 | CONT | [12 empty] | 0
_1023928238780.0006944445 | 10239282 |  | Parent | FALSE | YPS -YWPS 1 220KV G | 38780.0007 | 38780.6167 | CONT | 00020517 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1023928138780.0256944445 | 10239281 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 38780.0257 | 38782.2764 | CONT | 00356081 | GENCO | Power station request | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1009929938780.2409722222 | 10099299 |  | Parent | FALSE | L1 220/22KV TRANS AT WMTS | 38780.241 | 38780.6271 | REPDAILY | 00003234 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A958E138780.2416666667 | X2A958E1 |  | Parent | FALSE | SYTS-KTS 500KV WT | 38780.2417 | 38780.7049 | DAILY | 00022635 | SPICAPX | make connections to new prot panel & commission | SPIPOWER | X2A9 | X2A9 - (MLTS,SYTS,KTS) REPLACE 500KV PROTECTION | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X334581138780.2541666667 | X3345811 |  | Parent | FALSE | HWPS-MPS 220KV LINE AT MWTS | 38780.2542 | 38780.7792 | DAILY | 00016132 | SPICAPX | HWPS-MPS-MWTS220kV L cut in prot & line maintenanc | SPIPOWER | X334 | X334 - (HWPS,MPS,MWTS) REPLACE PROT ON TEED 220KV | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858E838781.2270833333 | X2A858E8 |  | Parent | FALSE | BTS -RTS 220KV W (BTS to Joint Bay 7) (CABLE) | 38781.2271 | 38781.6535 | DAILY | 00310401 | SPICAPX | install pole3 jumpers-connect rts line to new tr | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009929938781.2326388889 | 10099299 |  | Parent | FALSE | L1 220/22KV TRANS AT WMTS | 38781.2326 | 38781.6361 | REPDAILY | 00003234 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A858F038781.28125 | X2A858F0 |  | Parent | FALSE | EX - (O.O.S) NO.1 22KV CAPACITOR BANK ISOLATING CB AT BTS | 38781.2812 | 38782.7264 | CONT | [12 empty] | 0
_1023998938781.5 | 10239989 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK AT BTS | 38781.5 | 38782.4653 | CONT | 00337002 | SPICAPX | prepare cable end for termination | SPIPOWER |  | X2A8 - (BTS) STATION REBUILD | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X2A858F738781.5657291667 | X2A858F7 |  | Parent | FALSE | EX - (O.O.S) NO.3 TRANS 22KV CB AT BTS | 38781.5657 | 38783.5659 | CONT | [12 empty] | 0
_X2A858F638781.6111111111 | X2A858F6 |  | Parent | FALSE | EX - (O.O.S) NO.2 TRANS 22KV CB AT BTS | 38781.6111 | 38787.2292 | DAILY | [12 empty] | 0
_X2A858E938783.1270833333 | X2A858E9 |  | Parent | FALSE | EX - (O.O.S) NO.3 22KV CAPACITOR BANK ISOLATING CB AT BTS | 38783.1271 | 38783.6035 | DAILY | [12 empty] | 0
_1023998638783.1736111111 | 10239986 |  | Parent | FALSE | NO.3 22KV CAPACITOR BANK AT BTS | 38783.1736 | 38783.4479 | CONT | 00337011 | SPICAPX | prepare cable end for termination | SPIPOWER |  | X2A8 - (BTS) STATION REBUILD | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1023947538783.21875 | 10239475 |  | Parent | FALSE | MTS NO.1 220KV LINE AT ROTS | 38783.2188 | 38785.5528 | CONT | 00350667 | VEN_AUG | NO.4 220KV BUS AT ROTS | SPIPOWER |  | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z500589038783.21875 | Z5005890 |  | Parent | FALSE | NO.4 220KV BUS AT ROTS | 38783.2188 | 38785.5528 | CONT | 00329012 | VEN_AUG | NO.4 220KV BUS AT ROTS | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1023902038783.2388888889 | 10239020 |  | Parent | FALSE | B4 220/66KV TRANS AT TTS | 38783.2389 | 38783.5868 | DAILY | 00001543 | SPIMAINT | install new T.I. element | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023752538783.2548611111 | 10237525 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE NO.3 BUS CB AT KTS | 38783.2549 | 38783.616 | DAILY | [12 empty] | 0
_1023694138783.2805555556 | 10236941 |  | Parent | FALSE | EX - LY NO.1 66KV FDR CB CT B/PH AT MWTS | 38783.2806 | 38783.4028 | DAILY | [12 empty] | 0
_1023947238783.2805555556 | 10239472 |  | Parent | FALSE | LY NO.1 66KV FDR AT MWTS | 38783.2806 | 38783.4028 | DAILY | 00016140 | SPIMAINT | ADJUST BLUE PHASE CT OIL LEVEL | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023931838784.2131944445 | 10239318 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 38784.2132 | 38784.4285 | DAILY | 00017270 | SPIMAINT | Out W/O SVC balance cap bank | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1023716938784.2381944445 | 10237169 |  | Parent | FALSE | RWTS 220KV LINE NO.2 BUS CB AT TTS | 38784.2382 | 38784.5764 | DAILY | [12 empty] | 0
_1023867938784.25625 | 10238679 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB AT MLTS | 38784.2562 | 38786.4785 | CONT | [12 empty] | 0
_1008902738784.2694444445 | 10089027 |  | Parent | FALSE | VNSC SUPPLY TRANS CB AT RTS | 38784.2694 | 38784.5229 | DAILY | [12 empty] | 0
_X2A858G038784.3541666667 | X2A858G0 |  | Parent | FALSE | LNGS NO.2 GEN TRANS 220KV CB AT ATS | 38784.3542 | 38788.3021 | CONT | [12 empty] | 0
_X2A858F938784.3576388889 | X2A858F9 |  | Parent | FALSE | LNGS NO.1 GEN TRANS 220KV CB AT ATS | 38784.3576 | 38982.7681 | CONT | [12 empty] | 0
_1010066738784.5513888889 | 10100667 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT RTS | 38784.5514 | 38784.6486 | DAILY | 00007335 | SPIMAINT | O/HAUL Transformer without Div Sw (EM) | SPIPOWER |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_1022694438785.24375 | 10226944 |  | Parent | FALSE | KTS NO.1 220KV LINE NO.1 BUS CB AT TTS | 38785.2438 | 38785.5826 | DAILY | [12 empty] | 0
_1023942938785.3631944445 | 10239429 |  | Parent | FALSE | S024 KTS -WMTS 1 220KV | 38785.3632 | 38785.4819 | DAILY | [12 empty] | 0
_1023998538785.3631944445 | 10239985 |  | Parent | FALSE | KTS -WMTS 1 220KV WT | 38785.3632 | 38785.4819 | DAILY | 00022718 | FORCED | Kite wrapped around 3 Phases over Maribynong River | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023946538785.5590277778 | 10239465 |  | Parent | FALSE | EX - MTS NO.1 220KV LINE CB AT ROTS | 38785.559 | 38785.9993 | CONT | [12 empty] | 0
_1023999338785.5590277778 | 10239993 |  | Parent | FALSE | MTS NO.1 220KV LINE AT ROTS | 38785.559 | 38785.9993 | CONT | 00350667 | SPIMAINT | Repair CB | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023946438785.5590277778 | 10239464 |  | Parent | FALSE | RWTS 220KV LINE NO.4 BUS CB AT ROTS | 38785.559 | 38786.5188 | CONT | [12 empty] | 0
_X34358A638785.6930555556 | X34358A6 |  | Parent | FALSE | ROTS NO.6 220KV LINE AT YPS | 38785.6931 | 38786.0958 | CONT | 00016414 | SPICAPX | Cut over to new prot on YPS -ROTS 6 Lines | SPIPOWER | X343 | X343 - (ROTS,YPS,HWPS) UPGRADE PROT ON 6 OR 7 220KV LINES | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z500588038785.9548611111 | Z5005880 |  | Parent | FALSE | EX - SVTS NO.1 220KV LINE NO.4 BUS CB AT ROTS | 38785.9549 | 38803.2278 | CONT | [12 empty] | 0
_1023941338786.2722222222 | 10239413 |  | Parent | FALSE | B3 220/66KV TRANS OLTC MECH AT WMTS | 38786.2722 | 38786.4236 | DAILY | [12 empty] | 0
_1023940538786.3430555556 | 10239405 |  | Parent | FALSE | 2A 220/66/22KV TRANS BANK AT BETS | 38786.3431 | 38786.3625 | DAILY | 00331163 | DBPROX | Trans Sw for P/Cor parallel | DISTCO |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023942438786.5833333333 | 10239424 |  | Parent | FALSE | HYTS NO.2 500KV LINE AT APD | 38786.5833 | 38786.6049 | DAILY | 00005922 | 3RDPARTY | Restoration of HYTS 2 Line Reactor at APD | HVCUST |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X2A858G438787.1673611111 | X2A858G4 |  | Parent | FALSE | NO.2 220KV BUS AT BTS | 38787.1674 | 38788.7708 | CONT | 00000943 | SPICAPX | Remove Bus, Equipt and Structures Stn Rebuild | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1023932038787.2444444445 | 10239320 |  | Parent | FALSE | L1 220/22KV TRANS AT WMTS | 38787.2444 | 38787.6083 | DAILY | 00003234 | SPIMAINT | repair transformer bucs mechanism | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z41758C038787.2916666667 | Z41758C0 |  | Parent | FALSE | LNGS NO.1 GEN TRANS 220KV LINE AT ATS | 38787.2917 | 38789.4583 | DAILY | 00360128 | DB_AUG | carry out pre-commissioning tests | SPIPOWER | Z417 | Z417 - (ATS) CONNECTN FOR SNOWY HYDRO AT LAVERTON | Circuits | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1023951838787.3381944445 | 10239518 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 38787.3382 | 38788.5625 | CONT | 00356082 | GENCO | Genco isolations & earthing | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X2A858G038788.3020833333 | X2A858G0 |  | Parent | FALSE | LNGS NO.2 GEN TRANS 220KV CB AT ATS | 38788.3021 | 38982.8153 | CONT | [12 empty] | 0
_1023905838790.2333333333 | 10239058 |  | Parent | FALSE | EX - A4 TRANS/B2 TRANS 220KV CB AT KTS | 38790.2333 | 38790.4524 | DAILY | [12 empty] | 0
_1023905438790.2333333333 | 10239054 |  | Parent | FALSE | EX - A4 TRANS/B2 TRANS 220KV CB AT KTS | 38790.2333 | 38790.5875 | CONT | [12 empty] | 0
_1009906338790.2513888889 | 10099063 |  | Parent | FALSE | SHTS NO.1 220KV LINE NO.2 BUS CB AT GNTS | 38790.2514 | 38792.7014 | CONT | [12 empty] | 0
_1023948138790.2986111111 | 10239481 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS AT JLGB | 38790.2986 | 38828.6956 | CONT | 00009830 | GENCO | SCAP:JLGSB1 Isolation for Power Station | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1023868038791.2513888889 | 10238680 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT MLTS | 38791.2514 | 38792.5139 | CONT | [12 empty] | 0
_1022908138791.2638888889 | 10229081 |  | Parent | FALSE | ATS 220KV LINE NO.4 BUS CB CT R/PH AT BLTS | 38791.2639 | 38791.5403 | DAILY | [12 empty] | 0
_1024000038791.2638888889 | 10240000 |  | Parent | FALSE | ATS 220KV LINE AT BLTS | 38791.2639 | 38791.5403 | DAILY | 00024010 | SPIMAINT | Oil level low | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A958E338791.2708333333 | X2A958E3 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT SMTS | 38791.2708 | 38791.5708 | DAILY | 00012440 | SPICAPX | transfer prot panel from temp to final position | SPIPOWER | X2A9 | X2A9 - (MLTS,SYTS,KTS) REPLACE 500KV PROTECTION | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023959538791.9305555556 | 10239595 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 38791.9306 | 38793.0535 | CONT | 00356082 | GENCO | No 4 Gen | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1023906138792.2368055556 | 10239061 |  | Parent | FALSE | B3 220/66KV TRANS AT ATS | 38792.2368 | 38792.5701 | REPDAILY | 00354003 | SPIMAINT | replace 2 off neutral isolators | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X34358A838792.6729166667 | X34358A8 |  | Parent | FALSE | ROTS NO.5 220KV LINE AT YPS | 38792.6729 | 38793.016 | CONT | 00016413 | SPICAPX | Cut over to new prot on YPS -ROTS 5 Lines | SPIPOWER | X343 | X343 - (ROTS,YPS,HWPS) UPGRADE PROT ON 6 OR 7 220KV LINES | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1022824738793.2631944444 | 10228247 |  | Parent | FALSE | S000 HWTS-CBTS 4 500KV | 38793.2632 | 38793.4111 | DAILY | [12 empty] | 0
_1023963938793.3958333333 | 10239639 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT SMTS | 38793.3958 | 38793.4437 | DAILY | [12 empty] | 0
_1023965938793.8326388889 | 10239659 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 38793.8326 | 38794.6854 | CONT | 00356079 | GENCO | HWPS No1 Gen Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1023965838793.8368055556 | 10239658 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 38793.8368 | 38794.6389 | CONT | 00356082 | GENCO | HWPS No4 Gen SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158B538794.2125 | X46158B5 |  | Parent | FALSE | MLTS NO.2 220KV LINE AT BATS | 38794.2125 | 38795.9271 | CONT | 00012431 | SPICAPX | Out W/O MLTS 2L Connection of new equipment | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023913038794.2916666667 | 10239130 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT EPSY | 38794.2917 | 38794.3465 | DAILY | 00087035 | SPIMAINT | Out W/O MBTS 1 Line CB gas samp at EPSY | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1023913138794.3472222222 | 10239131 |  | Parent | FALSE | MBTS NO.2 220KV LINE AT EPSY | 38794.3472 | 38794.3771 | DAILY | 00087036 | SPIMAINT | Out W/O MBTS 2 Line CB gas samp at EPSY | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1023913238794.3777777778 | 10239132 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT EPSY | 38794.3778 | 38794.4076 | DAILY | [12 empty] | 0
_1023921338794.4069444445 | 10239213 |  | Parent | FALSE | TTS 220KV LINE NO.1 BUS CB AT EPSY | 38794.4069 | 38794.434 | DAILY | [12 empty] | 0
_1023921638794.4347222222 | 10239216 |  | Parent | FALSE | TTS 220KV LINE NO.2 BUS CB AT EPSY | 38794.4347 | 38794.4674 | DAILY | [12 empty] | 0
_1024006838795.2111111111 | 10240068 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 38795.2111 | 38795.6201 | CONT | 00352121 | SPICAPX | OUT W/O New CT's to be placed near JW419 cb's | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1023952238795.2131944445 | 10239522 |  | Parent | TRUE | NO.2 330KV BUS AT DDTS | 38795.2132 | 38795.7299 | CONT | 00003979 | SPICAPX | OUT W/O New CT's to be placed near JW419 cb's | SPIPOWER |  |  | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1023955538795.2131944445 | 10239555 | 10239522 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 38795.2132 | 38795.7299 | DAILY | 00352121 | FORCED | No2 Trans Stranded by 220kV CB Faulty CB Man Relay | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1023868138795.2506944445 | 10238681 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT MLTS | 38795.2507 | 38796.5451 | CONT | [12 empty] | 0
_1023991938795.3840277778 | 10239919 |  | Parent | FALSE | EX - HWPS NO.3 LINE/MWTS NO.2 LINE 220KV CB AT JLTS | 38795.384 | 38897.5472 | CONT | [12 empty] | 0
_1023967138795.7298611111 | 10239671 |  | Parent | FALSE | H2 TRANS 220KV CB AT DDTS | 38795.7299 | 38796.7778 | CONT | [12 empty] | 0
_1024006738795.7298611111 | 10240067 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 38795.7299 | 38796.7778 | CONT | 00352121 | FORCED | Transf stranded by CB Fault (CB Mmt Relay fail) | ALSTOM |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1023963738796.2291666667 | 10239637 |  | Parent | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB AT DDTS | 38796.2292 | 38798.7604 | CONT | [12 empty] | 0
_1023967238796.2916666667 | 10239672 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 38796.2917 | 38798.6333 | CONT | 00356082 | GENCO | GenCo Requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010025038797.2298611111 | 10100250 |  | Parent | FALSE | SYN/COND AT TSTS | 38797.2299 | 38800.3826 | CONT | 00007626 | SPIMAINT | 3 Monthly O/HAUL - TSTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z32158C338797.2736111111 | Z32158C3 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 38797.2736 | 38797.6104 | REPDAILY | 00337581 | DB_AUG | Out W/O No1 Trans OLTC funtional checks | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z44158B538797.3 | Z44158B5 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT MLTS | 38797.3 | 38797.3701 | DAILY | 00337580 | VEN_AUG | Out W/O A1 Trans for 220kV CB CT ratio changes | SPIPOWER | Z441 | Z441 - (MLTS) A1 TRANSFORMER 220KV CONNECTIONS UPRATE | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1023971838797.353599537 | 10239718 |  | Parent | FALSE | NO.7 GEN TRANS LINE AT HWPS | 38797.3536 | 38799.3903 | CONT | 00356085 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z44158B638797.3715277778 | Z44158B6 |  | Parent | FALSE | GTS NO.2 220KV LINE AT MLTS | 38797.3715 | 38797.4069 | DAILY | 00022499 | VEN_AUG | Out W/O GTS 2L for 220kV CB CT ratio changes | SPIPOWER | Z441 | Z441 - (MLTS) A1 TRANSFORMER 220KV CONNECTIONS UPRATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010035038797.3854166667 | 10100350 |  | Parent | FALSE | NO.1 220KV BUS E/SW AT TTS | 38797.3854 | 38797.625 | REPDAILY | [12 empty] | 0
_1009292838797.3958333333 | 10092928 |  | Parent | FALSE | SMTS NO.2 220KV LINE CB AT TTS | 38797.3958 | 38799.6153 | CONT | [12 empty] | 0
_1024007538797.3972222222 | 10240075 |  | Parent | FALSE | SMTS NO.2 220KV LINE AT TTS | 38797.3972 | 38799.6118 | CONT | 00015729 | SPIMAINT | Out W/O for CB O/H at TTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023964238797.4118055556 | 10239642 |  | Parent | FALSE | SYTS-KTS 500KV WT | 38797.4118 | 38797.6181 | REPDAILY | 00022635 | SPIMAINT | Line required for proximity for crane work | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023975238797.5513888889 | 10239752 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE AT HWTS | 38797.5514 | 38798.0382 | CONT | 00016238 | FORCED | Plessy Ducon CVT Crack in Base leaking Oil | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158B638798.2111111111 | X46158B6 |  | Parent | FALSE | TGTS 220KV LINE AT BATS | 38798.2111 | 38799.7118 | CONT | 00012435 | SPICAPX | Out W/O TGTS Line remove old CB & commiss new CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010035038798.2291666667 | 10100350 |  | Parent | FALSE | NO.1 220KV BUS E/SW AT TTS | 38798.2292 | 38798.6278 | REPDAILY | [12 empty] | 0
_1023940938798.25 | 10239409 |  | Parent | FALSE | HYTS NO.2/SYTS NO.2 LINE 500KV CB AT MLTS | 38798.25 | 38799.559 | CONT | [12 empty] | 0
_1023943938798.3083333333 | 10239439 |  | Parent | FALSE | EX - AUX C 220KV TRANS LINE CT R/PH AT HWPS | 38798.3083 | 38798.6396 | DAILY | [12 empty] | 0
_1023979838798.6333333333 | 10239798 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 38798.6333 | 38804.075 | CONT | 00356082 | GENCO | Genco requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024044438799.1020833333 | 10240444 |  | Parent | FALSE | WBTS 220KV LINE AT BATS | 38799.1021 | 38799.1076 | DAILY | 00012410 | FAULT | No 1 220kv Bus Trip | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024044738799.1020833333 | 10240447 |  | Parent | FALSE | MLTS NO.2 220KV LINE AT BATS | 38799.1021 | 38799.1076 | DAILY | 00012431 | FAULT | No 1 220kv Bus Trip | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A558C338799.25 | X2A558C3 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT ERTS | 38799.25 | 38799.5354 | DAILY | [12 empty] | 0
_X2A558C438799.25 | X2A558C4 | X2A558C3 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT ERTS | 38799.25 | 38799.5354 | DAILY | 00004345 | SPICAPX | Rebate - Modify CB Circuits for DC DUPLICATION | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X2A558C538799.25 | X2A558C5 | X2A558C3 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT ERTS | 38799.25 | 38799.5354 | DAILY | 00337043 | SPICAPX | Rebate - Modify CB Circuits for DC DUPLICATION | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1023963838799.25 | 10239638 |  | Parent | FALSE | MSS NO.2 330KV LINE NO.2 BUS CB AT DDTS | 38799.25 | 38800.7917 | CONT | [12 empty] | 0
_1009438438799.25625 | 10094384 | 10097897 | Child | FALSE | NO.1 220KV CAPACITOR BANK E/SW AT KTS | 38799.2562 | 38800.6188 | REPDAILY | [12 empty] | 0
_1009789738799.25625 | 10097897 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB AT KTS | 38799.2562 | 38800.6188 | CONT | [12 empty] | 0
_1009789838799.25625 | 10097898 | 10097897 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 38799.2562 | 38800.6188 | REPDAILY | 00119824 | SPIMAINT | O/Haul - Cap bank (incl ESW,CT,reactor) (W) | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024013138799.25625 | 10240131 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 38799.2562 | 38800.6188 | CONT | 00119824 | SPIMAINT | CL.1 O/HAUL - ASEA HPL245 220KV CB | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1010766638799.3041666667 | 10107666 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 38799.3042 | 38799.5687 | DAILY | 00017270 | SPIMAINT | Out works order for testing SVC Prot | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1023974938799.3097222222 | 10239749 |  | Parent | FALSE | NO.1 11KV/415V S/S TRANS 11KV VT AT CBTS | 38799.3097 | 38799.616 | DAILY | [12 empty] | 0
_1023940938799.5833333333 | 10239409 |  | Parent | FALSE | HYTS NO.2/SYTS NO.2 LINE 500KV CB AT MLTS | 38799.5833 | 38940.5354 | CONT | [12 empty] | 0
_1024095338800.3118055556 | 10240953 |  | Parent | FALSE | KGTS 220KV LINE AT RCTS | 38800.3118 | 38800.3201 | DAILY | 00016959 | FAULT | Line CB Auto Opened | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A558C638800.3381944445 | X2A558C6 |  | Parent | FALSE | 1-3 66KV BUS TIE CB AT ERTS | 38800.3382 | 38800.4583 | DAILY | [12 empty] | 0
_1023991038800.7097222222 | 10239910 |  | Parent | FALSE | EX - HWPS NO.3 LINE/MWTS NO.2 LINE 220KV CB AT JLTS | 38800.7097 | 38806.2667 | CONT | [12 empty] | 0
_X46158B738801.2194444445 | X46158B7 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 38801.2194 | 38802.641 | CONT | 00006559 | SPICAPX | Out W/O No2 220kV BUS to commiss new HOTS CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158B838801.2194444445 | X46158B8 | X46158B7 | Child | FALSE | WBTS 220KV LINE AT BATS | 38801.2194 | 38802.641 | REPDAILY | 00012410 | SPICAPX | Rebate W/O HOTS LINE to commiss new HOTS equip | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158B938801.2194444445 | X46158B9 | X46158B7 | Child | FALSE | B2 220/66KV TRANS AT BATS | 38801.2194 | 38802.641 | REPDAILY | 00006555 | SPICAPX | Perc calc W/O No2 Trans during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158C038801.2194444445 | X46158C0 | X46158B7 | Child | FALSE | MLTS NO.2 220KV LINE AT BATS | 38801.2194 | 38802.641 | REPDAILY | 00012431 | SPICAPX | Rebate W/O MLTS 2L remove OOC equip during bus EAP | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023926738801.3666666667 | 10239267 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 38801.3667 | 38801.4507 | DAILY | 00019243 | SPIMAINT | Investigate S/S 415V supply failure to C/O | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X46158C138801.6875 | X46158C1 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 38801.6875 | 38801.9313 | CONT | 00006559 | SPICAPX | Out W/O No2 220kV Bus unavailable O'night | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158C238801.6875 | X46158C2 | X46158C1 | Child | FALSE | WBTS 220KV LINE AT BATS | 38801.6875 | 38801.9313 | CONT | 00012410 | SPICAPX | Rebate W/O HOTS Line unavailable O'night | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158C338801.6875 | X46158C3 | X46158C1 | Child | FALSE | EX - NO.2 TRANS BANK AT HOTS | 38801.6875 | 38801.9313 | CONT | 00026246 | SPICAPX | Perf calc W/O No2 Trans during No2 220 bus unavail | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023960238802.2743055556 | 10239602 |  | Parent | FALSE | NO.6 66KV BUS AT HTS | 38802.2743 | 38802.6708 | DAILY | 00004460 | DBPROX | SCAP: No 6 66kV Bus at HTS | DISTCO |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1023991338802.6048611111 | 10239913 |  | Parent | FALSE | SYN/COND AT FBTS | 38802.6049 | 38802.6639 | CONT | 00002697 | FORCED | Repair Cooling Fan belt Fault | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43458B138803.2090277778 | X43458B1 |  | Parent | TRUE | EX - NO.1 220KV BUS AT MBTS | 38803.209 | 38804.0354 | CONT | 00004001 | SPICAPX | OUT W/O Prep FutTie Bus cb No1B isol connex 4 serv | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43458B738803.2090277778 | X43458B7 | X43458B1 | Child | FALSE | EX - DDTS NO.1 220KV LINE AT MBTS | 38803.209 | 38804.0354 | DAILY | 00011748 | SPICAPX | Rebate W/O DDTS 1L for No 1 220kV bus outage | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43458B838803.2090277778 | X43458B8 | X43458B1 | Child | FALSE | DPS 220KV LINE AT MBTS | 38803.209 | 38804.0354 | DAILY | 00011754 | SPICAPX | Rebate W/O EPS 1L for No 1 220kV bus outage | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43458B938803.2090277778 | X43458B9 | X43458B1 | Child | FALSE | EX - EPS NO.1 220KV LINE AT MBTS | 38803.209 | 38804.0354 | DAILY | 00011751 | SPICAPX | Rebate W/O EPS 1L for No 1 220kV bus outage | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_Z500589038803.2277777778 | Z5005890 |  | Parent | FALSE | NO.4 220KV BUS AT ROTS | 38803.2278 | 38806.4667 | CONT | 00329012 | VEN_AUG | NO.4 220KV BUS AT ROTS | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1009854338803.2291666667 | 10098543 |  | Parent | FALSE | SYN/COND AT BLTS | 38803.2292 | 38805.6278 | CONT | 00002547 | SPIMAINT | 3 Monthly O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1009683638803.2527777778 | 10096836 |  | Parent | FALSE | MLTS NO.2 500KV LINE CB AT HYTS | 38803.2528 | 38803.5729 | REPDAILY | [12 empty] | 0
_1009292638803.2604166667 | 10092926 |  | Parent | FALSE | KTS NO.2 220KV LINE CB AT TTS | 38803.2604 | 38804.5736 | CONT | [12 empty] | 0
_1024025738803.2604166667 | 10240257 |  | Parent | FALSE | KTS NO.2 220KV LINE AT TTS | 38803.2604 | 38804.5736 | CONT | 00015727 | SPIMAINT | CL.1 O/HAUL - CGE AT(VH) CB | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009952538803.3048611111 | 10099525 |  | Parent | FALSE | NO.2 22KV BUS AT KGTS | 38803.3049 | 38803.641 | DAILY | 00017415 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 22 |  |  |  | 0
_X2A558D338803.3368055556 | X2A558D3 |  | Parent | FALSE | 1-4 66KV BUS TIE CB AT ERTS | 38803.3368 | 38803.4111 | DAILY | [12 empty] | 0
_1024045338804.1819444445 | 10240453 |  | Parent | FALSE | EX - DDTS NO.1 220KV LINE AT MBTS | 38804.1819 | 38804.4521 | DAILY | 00011748 | FORCED | No 1 220kV bus unable to close CB's | SPIPOWER |  | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024045438804.1819444445 | 10240454 |  | Parent | FALSE | DPS 220KV LINE AT MBTS | 38804.1819 | 38804.4521 | DAILY | 00011754 | FAULT | No 1 220kV bus unable to close CB's | SPIPOWER |  | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024045538804.1819444445 | 10240455 |  | Parent | FALSE | EX - EPS NO.1 220KV LINE AT MBTS | 38804.1819 | 38804.4521 | DAILY | 00011751 | FAULT | No 1 220kV bus unable to close CB's | SPIPOWER |  | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X2A558D038804.2506944445 | X2A558D0 |  | Parent | FALSE | NO.3 66KV CAPACITOR BANK CB AT ERTS | 38804.2507 | 38804.3264 | DAILY | [12 empty] | 0
_1009952438804.2506944445 | 10099524 |  | Parent | FALSE | NO.1 22KV BUS AT KGTS | 38804.2507 | 38804.6312 | DAILY | 00017414 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 22 |  |  |  | 0
_1009683638804.2534722222 | 10096836 |  | Parent | FALSE | MLTS NO.2 500KV LINE CB AT HYTS | 38804.2535 | 38804.5729 | REPDAILY | [12 empty] | 0
_1023943338804.26875 | 10239433 |  | Parent | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 38804.2688 | 38804.566 | DAILY | 00017906 | HVCUST | SCAP:GTS-PTH No 2 220kV Line | HVCUST |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023995038804.3090277778 | 10239950 |  | Parent | FALSE | BLLY 500KV LINE AT LYPS | 38804.309 | 38804.7896 | CONT | 00360516 | 3RDPARTY | De-energised for BLLY requirements | 3RDPARTY |  |  | Circuits | Eastern | 500 | CONNECTION ASSET | EXCLUDED |  | 3
_1023996338804.4055555556 | 10239963 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 38804.4056 | 38804.4208 | DAILY | 00060187 | FORCED | PLC Blocking CB Close DDTS 1 Line at MBTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023997638804.9951388889 | 10239976 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 38804.9951 | 38805.4021 | CONT | 00016423 | GENCO | YWPS No1 Gen Isolations for Powerstation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43458A938805.2166666667 | X43458A9 |  | Parent | TRUE | B1 220/66KV TRANS AT MWTS | 38805.2167 | 38805.8764 | DAILY | 00351931 | SPICAPX | OUT W/O Remove tie trans from service | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X43458B338805.2166666667 | X43458B3 | X43458A9 | Child | FALSE | EX - DDTS NO.2 220KV LINE AT MBTS | 38805.2167 | 38805.8764 | DAILY | 00011750 | SPICAPX | Rebate W/O DDTS2 line to changeover trans | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43458B438805.2166666667 | X43458B4 | X43458A9 | Child | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 38805.2167 | 38805.8764 | DAILY | 00011755 | SPICAPX | Rebate W/O MKPS-MBTS line to changeover trans | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43458B538805.2166666667 | X43458B5 | X43458A9 | Child | FALSE | MBTS-EPS 2 220KV N | 38805.2167 | 38805.8764 | DAILY | 00055381 | SPICAPX | Rebate W/O EPS2 line for changeover of trans | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X43458B638805.2166666667 | X43458B6 | X43458A9 | Child | FALSE | WKPS 220KV LINE AT MBTS | 38805.2167 | 38805.8764 | DAILY | 00011756 | SPICAPX | Rebate W/O WKPS line for changeover of trans | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009683638805.2465277778 | 10096836 |  | Parent | FALSE | MLTS NO.2 500KV LINE CB AT HYTS | 38805.2465 | 38805.6868 | REPDAILY | [12 empty] | 0
_1009930838805.2527777778 | 10099308 |  | Parent | FALSE | FBTS NO.1 220KV LINE CB AT WMTS | 38805.2528 | 38806.5583 | CONT | [12 empty] | 0
_X2A958E938805.3166666667 | X2A958E9 |  | Parent | FALSE | SMTS-KTS 500KV WT | 38805.3167 | 38805.5993 | DAILY | 00022650 | SPICAPX | commission new kts x digital current diff prot | SPIPOWER | X2A9 | X2A9 - (MLTS,SYTS,KTS) REPLACE 500KV PROTECTION | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A558D238805.3618055556 | X2A558D2 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT ERTS | 38805.3618 | 38805.4674 | DAILY | [12 empty] | 0
_1009894138806.2319444444 | 10098941 |  | Parent | FALSE | SYN/COND AT FBTS | 38806.2319 | 38808.6194 | CONT | 00002697 | SPIMAINT | Annual O/HAUL - FBTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X2A558D438806.25 | X2A558D4 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK CB AT ERTS | 38806.25 | 38806.3472 | DAILY | [12 empty] | 0
_X46158C538806.2680555556 | X46158C5 |  | Parent | FALSE | WBTS 220KV LINE AT BATS | 38806.2681 | 38806.7132 | DAILY | 00012410 | SPICAPX | Out W/O decommiss old/commiss new HOTS CB at BATS | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009828838806.2729166667 | 10098288 |  | Parent | FALSE | NO.4 66KV BUS AT BETS | 38806.2729 | 38806.7063 | DAILY | 00016367 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z32158C438806.2895833333 | Z32158C4 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 38806.2896 | 38806.5257 | DAILY | 00337584 | DB_AUG | Out W/O No2 Trans OLTC funtional checks | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010012138806.2923611111 | 10100121 |  | Parent | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 38806.2924 | 38806.6757 | REPDAILY | 00331027 | SPIMAINT | O/Haul - Cap bank (incl ESW,CT,reactor) (N) | SPIPOWER |  |  | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1023995638806.3111111111 | 10239956 |  | Parent | FALSE | NO.1 11KV/415V S/S TRANS AT CBTS | 38806.3111 | 38806.6062 | DAILY | 00359515 | 3RDPARTY | CBTS: NO 2 S/S Trans de-energised | DISTCO |  |  | Other Transformers | Eastern | 11 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1024003738806.4631944445 | 10240037 |  | Parent | FALSE | BATS-BETS 220KV | 38806.4632 | 38806.6028 | DAILY | 00328505 | DBPROX | maximo testing only | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010012138807.25 | 10100121 |  | Parent | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 38807.25 | 38807.6049 | REPDAILY | 00331027 | SPIMAINT | O/Haul - Cap bank (incl ESW,CT,reactor) (N) | SPIPOWER |  |  | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1009968638807.2506944445 | 10099686 |  | Parent | FALSE | NO.1A 66KV CAPACITOR BANK CB AT KTS | 38807.2507 | 38807.5889 | DAILY | [12 empty] | 0
_1024004738807.2861111111 | 10240047 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 38807.2861 | 38846.8194 | CONT | 00356082 | GENCO | HWPS No4 Gen Isolations for Powerstation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1023993338807.2902777778 | 10239933 |  | Parent | FALSE | SYTS-KTS 500KV WT | 38807.2903 | 38807.3007 | DAILY | 00022635 | SPIMAINT | Line required for proximity for crane work | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43458C238807.2916666667 | X43458C2 |  | Parent | FALSE | EX - B1 TRANS NO.2 BUS 220KV CB AT MBTS | 38807.2917 | 38807.775 | CONT | [12 empty] | 0
_X43458C638807.3477430556 | X43458C6 |  | Parent | FALSE | EX - B1 TRANS NO.2 BUS 220KV CB AT MBTS | 38807.3477 | 38829.3895 | CONT | [12 empty] | 0
_1024008538807.6201388889 | 10240085 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 38807.6201 | 38808.7361 | CONT | 00356080 | GENCO | Power Station requirement 31/3/06 -1/4/06 | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024008738807.7347222222 | 10240087 |  | Parent | FALSE | NO.2 GEN TRANS 500KV LINE E/SW AT LYPS | 38807.7347 | 38808.2847 | CONT | [12 empty] | 0
_Z50058A638808.2375 | Z50058A6 |  | Parent | FALSE | SVTS NO.2 220KV LINE AT ROTS | 38808.2375 | 38809.6257 | CONT | 00023968 | VEN_AUG | Replace SVTS 2Line 4B CB Line side isol | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A558C738808.2472222222 | X2A558C7 |  | Parent | FALSE | NO.1 TRANS 66KV CB AT ERTS | 38808.2472 | 38808.3938 | DAILY | [12 empty] | 0
_1023999638808.3972222222 | 10239996 |  | Parent | FALSE | W2 GEN TRANS NO.2 BUS 220KV CB AT YPS | 38808.3972 | 38814.3479 | CONT | [12 empty] | 0
_X2A558C838808.4006944445 | X2A558C8 |  | Parent | FALSE | NO.3 TRANS 66KV CB AT ERTS | 38808.4007 | 38808.5181 | DAILY | [12 empty] | 0
_X2A558C938808.5229166667 | X2A558C9 |  | Parent | FALSE | NO.4 TRANS 66KV CB AT ERTS | 38808.5229 | 38808.6167 | DAILY | [12 empty] | 0
_1024009638808.7361111111 | 10240096 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 38808.7361 | 38809.8556 | CONT | [12 empty] | 0
_Z50058A838809.6263888889 | Z50058A8 |  | Parent | FALSE | SVTS NO.2 220KV LINE NO.4 BUS CB AT ROTS | 38809.6264 | 38815.3097 | CONT | [12 empty] | 0
_1024000138810.3722222222 | 10240001 |  | Parent | FALSE | W2 GEN TRANS NO.2 BUS 220KV CB AT YPS | 38810.3722 | 38810.6667 | DAILY | [12 empty] | 0
_1023998738810.4166666667 | 10239987 |  | Parent | FALSE | MLTS NO.1 500KV LINE AT HYTS | 38810.4167 | 38810.4215 | DAILY | 00021195 | SW_NEM | Outage of APD/HYTS/MLTS 1 Line/Restore MLTSReactor | VENCORP |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z33458D238811.2986111111 | Z33458D2 |  | Parent | FALSE | NO.4 220KV BUS AT SVTS | 38811.2986 | 38814.4215 | CONT | 00004859 | VEN_AUG | Install future B4 Trans ROI bus side connections | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010154638811.2993055556 | 10101546 |  | Parent | FALSE | SMTS NO.2 330KV LINE AT DDTS | 38811.2993 | 38811.6986 | REPDAILY | 00012356 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010212038811.3097222222 | 10102120 |  | Parent | FALSE | EX - GTS NO.1 220KV LINE AT KTS | 38811.3097 | 38811.6903 | DAILY | 00015985 | SPIMAINT | O/Haul - 220kV Line (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A958F038811.3368055556 | X2A958F0 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT SMTS | 38811.3368 | 38811.3667 | DAILY | [12 empty] | 0
_1024015038811.5333333333 | 10240150 |  | Parent | FALSE | WMTS-FBTS 2 220KV WY | 38811.5333 | 38811.5417 | DAILY | 00022787 | SPIMAINT | SF6 Top up WMTS 2 Line CB at FBTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1024011038811.5416666667 | 10240110 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 38811.5417 | 38820.5319 | CONT | [12 empty] | 0
_1010215538812.2819444445 | 10102155 |  | Parent | FALSE | NO.2 500KV BUS E/SW AT KTS | 38812.2819 | 38813.6576 | CONT | [12 empty] | 0
_1010154638812.29375 | 10101546 |  | Parent | FALSE | SMTS NO.2 330KV LINE AT DDTS | 38812.2937 | 38812.7653 | REPDAILY | 00012356 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X34358A938812.29375 | X34358A9 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT HWPS | 38812.2937 | 38813.0194 | CONT | 00015790 | SPICAPX | Cut over to new prot on HWPS -ROTS 1 Lines | SPIPOWER | X343 | X343 - (ROTS,YPS,HWPS) UPGRADE PROT ON 6 OR 7 220KV LINES | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009285038812.3104166667 | 10092850 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE CB AT GTS | 38812.3104 | 38812.7076 | REPDAILY | [12 empty] | 0
_1010197938812.3145833333 | 10101979 | 10239756 | Child | FALSE | EX - NO.2 66KV CAPACITOR BANK CB AT BETS | 38812.3146 | 38813.5625 | DAILY | [12 empty] | 0
_1023975638812.3145833333 | 10239756 |  | Parent | TRUE | EX - NO.2 66KV CAPACITOR BANK CB AT BETS | 38812.3146 | 38813.5625 | DAILY | [12 empty] | 0
_1023975838812.3145833333 | 10239758 | 10239756 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT BETS | 38812.3146 | 38813.5625 | DAILY | 00350819 | SPIMAINT | Rebate W/O 2A Cap bk during 2A CB Service ops O/H | SPIPOWER |  |  | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1023975938812.3145833333 | 10239759 | 10239756 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 38812.3146 | 38813.5625 | DAILY | 00016274 | SPIMAINT | Rebate W/O 2B Cap bk during 2A CB Service ops O/H | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V4S258A038812.3395833333 | V4S258A0 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 38812.3396 | 38820.6403 | CONT | 00001328 | SPIMAINT | CARRY OUT PREP WORK ON No1 500KV BUS | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1024000238812.3805555556 | 10240002 |  | Parent | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB AT DDTS | 38812.3806 | 38812.65 | DAILY | [12 empty] | 0
_1010450738813.2979166667 | 10104507 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT DDTS | 38813.2979 | 38813.7181 | DAILY | 00337558 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009285038813.3173611111 | 10092850 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE CB AT GTS | 38813.3174 | 38813.6799 | REPDAILY | [12 empty] | 0
_1024000338813.3881944444 | 10240003 |  | Parent | FALSE | MSS NO.2 330KV LINE NO.2 BUS CB AT DDTS | 38813.3882 | 38813.5896 | DAILY | [12 empty] | 0
_1024022538813.4381944445 | 10240225 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 38813.4382 | 38813.45 | DAILY | [12 empty] | 0
_1010187638813.5638888889 | 10101876 |  | Parent | TRUE | EX - NO.3 66KV CAPACITOR BANK CB AT BETS | 38813.5639 | 38813.7194 | DAILY | [12 empty] | 0
_1024000838813.5638888889 | 10240008 | 10101876 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT BETS | 38813.5639 | 38813.7194 | DAILY | 00350820 | SPIMAINT | Rebate W/O No3A Cap bank during 3A CB O-H | SPIPOWER |  |  | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024001138813.5638888889 | 10240011 | 10101876 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 38813.5639 | 38813.7194 | DAILY | 00016304 | SPIMAINT | Rebate W/O No3B Cap bank during 3A CB O-H | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1009444638814.2826388889 | 10094446 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 38814.2826 | 38814.7181 | DAILY | 00352121 | SPIMAINT | O/HAUL Transformer without Div Sw | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009276238814.2944444444 | 10092762 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 38814.2944 | 38814.6875 | DAILY | 00017900 | SPIMAINT | O/Haul - KTS 220kV No.1 LINE at GTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010196938814.3013888889 | 10101969 | 10101970 | Child | FALSE | NO.4 220KV CAPACITOR BANK E/SW AT BLTS | 38814.3014 | 38814.6403 | DAILY | [12 empty] | 0
_1010197038814.3013888889 | 10101970 |  | Parent | TRUE | NO.4 220KV CAPACITOR BANK CB AT BLTS | 38814.3014 | 38814.6403 | DAILY | [12 empty] | 0
_Z33458C638814.3305555556 | Z33458C6 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT SVTS | 38814.3306 | 38814.4931 | DAILY | [12 empty] | 0
_X25158G538814.3368055556 | X25158G5 |  | Parent | FALSE | AEMO METERING AT HWPS | 38814.3368 | 38814.4062 | DAILY | [12 empty] | 0
_1024031138814.5861111111 | 10240311 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 38814.5861 | 38816.6424 | CONT | 00356084 | GENCO | Isolation for Generator | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z50058A738815.2798611111 | Z50058A7 |  | Parent | FALSE | SVTS NO.2 220KV LINE AT ROTS | 38815.2799 | 38816.7708 | CONT | 00023968 | VEN_AUG | Replace SVTS 2Line 4B CB L/S isol | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010032738815.2930555556 | 10100327 |  | Parent | FALSE | NO.3 66KV BUS AT TTS | 38815.2931 | 38815.6875 | REPDAILY | 00001555 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Western | 66 |  |  |  | 0
_Z33458C738815.3180555556 | Z33458C7 |  | Parent | FALSE | B2 220/66KV TRANS AT SVTS | 38815.3181 | 38815.7625 | DAILY | 00004850 | VEN_AUG | Modify No 2 66 kv Bus prot & No2 Tran 66kV BT CB | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010032738816.2902777778 | 10100327 |  | Parent | FALSE | NO.3 66KV BUS AT TTS | 38816.2903 | 38816.5743 | REPDAILY | 00001555 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Western | 66 |  |  |  | 0
_Z33458D338816.2916666667 | Z33458D3 |  | Parent | FALSE | B3 220/66KV TRANS AT SVTS | 38816.2917 | 38816.5243 | DAILY | 00004851 | VEN_AUG | Install 66 kV Connections in Bay L | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009286338817.2861111111 | 10092863 |  | Parent | FALSE | BTS NO.3 220KV LINE CB AT TTS | 38817.2861 | 38818.6486 | CONT | [12 empty] | 0
_1024071838817.2861111111 | 10240718 |  | Parent | FALSE | BTS NO.3 220KV LINE AT TTS | 38817.2861 | 38818.6486 | CONT | 00015724 | SPIMAINT | CL.1 O/HAUL - BTH JW419 & JW420 CB | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010154838817.2916666667 | 10101548 |  | Parent | FALSE | NO.1 220KV BUS AT DDTS | 38817.2917 | 38817.7306 | REPDAILY | 00003976 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1009276338817.2979166667 | 10092763 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 38817.2979 | 38817.6875 | DAILY | 00017901 | SPIMAINT | O/Haul - KTS 220kV No.2 LINE at GTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024025138817.3263888889 | 10240251 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS OLTC DIV/SW AT JLGA | 38817.3264 | 38818.6292 | DAILY | [12 empty] | 0
_1023931838817.3784722222 | 10239318 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 38817.3785 | 38817.7035 | DAILY | 00017270 | SPIMAINT | Out W/O SVC balance cap bank | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024062438817.6694444444 | 10240624 |  | Parent | FALSE | EX - FVTS/BETS 220KV LINE AT SHTS | 38817.6694 | 38817.6722 | DAILY | 00000810 | FAULT | BETS-FVTS-SHTS 220kv Line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010154838818.2916666667 | 10101548 |  | Parent | FALSE | NO.1 220KV BUS AT DDTS | 38818.2917 | 38818.7528 | REPDAILY | 00003976 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010241638818.2972222222 | 10102416 |  | Parent | FALSE | NO.4A 66KV CAPACITOR BANK CB AT TTS | 38818.2972 | 38818.6493 | DAILY | [12 empty] | 0
_X34358B038818.2986111111 | X34358B0 |  | Parent | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 38818.2986 | 38818.9271 | CONT | 00015793 | SPICAPX | Cut over to new prot on HWPS -ROTS 2 Lines | SPIPOWER | X343 | X343 - (ROTS,YPS,HWPS) UPGRADE PROT ON 6 OR 7 220KV LINES | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009285138818.31875 | 10092851 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE CB AT GTS | 38818.3187 | 38818.6813 | REPDAILY | [12 empty] | 0
_1023931838818.3381944444 | 10239318 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 38818.3382 | 38818.4944 | DAILY | 00017270 | SPIMAINT | Out W/O SVC balance cap bank | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024030738818.3541666667 | 10240307 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT HTS | 38818.3542 | 38818.7229 | DAILY | 00004449 | 3RDPARTY | HTS: No 2 S/S Trans de-energised | DISTCO |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_1024036838818.4729166667 | 10240368 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 38818.4729 | 38829.375 | CONT | [12 empty] | 0
_1024041338818.9625 | 10240413 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 38818.9625 | 38819.3486 | CONT | 00017270 | FAULT | SVC TRIPPING | ALSTOM |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1010241138819.2895833333 | 10102411 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK CB AT TTS | 38819.2896 | 38820.5986 | CONT | [12 empty] | 0
_1010154838819.2916666667 | 10101548 |  | Parent | FALSE | NO.1 220KV BUS AT DDTS | 38819.2917 | 38819.7583 | REPDAILY | 00003976 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1009285138819.3118055556 | 10092851 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE CB AT GTS | 38819.3118 | 38819.6778 | REPDAILY | [12 empty] | 0
_1024030838819.3409722222 | 10240308 |  | Parent | FALSE | NO.2 UNIT 230/10.5KV TRANS OLTC DIV/SW AT JLGA | 38819.341 | 38820.6549 | DAILY | [12 empty] | 0
_1023931838819.3486111111 | 10239318 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 38819.3486 | 38819.7403 | DAILY | 00017270 | SPIMAINT | Out W/O SVC balance cap bank | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024064438819.775 | 10240644 |  | Parent | FALSE | GTS NO.2 220KV LINE AT PTH | 38819.775 | 38819.7993 | DAILY | 00005926 | HVCUST | PTH: No 2 220kV Bus at PTH OUTAGE | HVCUST |  |  | Circuits | Western | 220 |  |  |  | 0
_1010154838820.2861111111 | 10101548 |  | Parent | FALSE | NO.1 220KV BUS AT DDTS | 38820.2861 | 38820.7979 | REPDAILY | 00003976 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z33458D138820.3354166667 | Z33458D1 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT SVTS | 38820.3354 | 38820.5771 | DAILY | [12 empty] | 0
_1024012338820.3881944444 | 10240123 |  | Parent | FALSE | FBTS NO.1 220KV LINE CB AT WMTS | 38820.3882 | 38820.406 | DAILY | [12 empty] | 0
_1010241738820.4868055556 | 10102417 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT TTS | 38820.4868 | 38820.5792 | DAILY | 00001533 | SPIMAINT | O/HAUL Transformer Div Mechanism (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024069838820.8048611111 | 10240698 |  | Parent | FALSE | FBTS NO.2 220KV LINE AT WMTS | 38820.8049 | 38820.8222 | DAILY | 00025736 | SPIMAINT | Oil samples to be taken from CT's | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1024024538821.1402777778 | 10240245 |  | Parent | FALSE | B2 GEN. TRAN 500KV LINE E/SW AT LYPS | 38821.1403 | 38823.6083 | CONT | [12 empty] | 0
_1024048238822.0326388889 | 10240482 |  | Parent | FALSE | NO.3 11/6.6KV AUX TRANS AT TSTS | 38822.0326 | 38831.2965 | CONT | 00007662 | FAULT | No 3 Aux Trans | SPIPOWER |  |  | Other Transformers | Eastern | 11 |  |  |  | 0
_1024049438824.3805555556 | 10240494 |  | Parent | FALSE | H1 TRANS NO.1 BUS 330KV CB AT DDTS | 38824.3806 | 38824.4097 | DAILY | [12 empty] | 0
_V4S258B738824.5833333333 | V4S258B7 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 38824.5833 | 38833.6924 | CONT | 00001328 | SPIMAINT | CARRY OUT SILICONE INJECTION ON No1 500KV BUS | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1024047038825.3368055556 | 10240470 |  | Parent | FALSE | NO.3 UNIT 230/10.5KV TRANS OLTC DIV/SW AT JLGA | 38825.3368 | 38826.6396 | CONT | [12 empty] | 0
_1024075238825.5930555556 | 10240752 |  | Parent | FALSE | RTS 220KV LINE AT BTS | 38825.5931 | 38825.6646 | DAILY | 00015960 | FAULT | RTS 220kV Line stranded by L4 Transf Trip | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024075338825.5930555556 | 10240753 |  | Parent | FALSE | L1 220/22KV TRANS AT BTS | 38825.5931 | 38825.6646 | DAILY | 00360728 | FAULT | New L4 transf opened Auto. Spurios Relay operation | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024164138825.6881944445 | 10241641 |  | Parent | TRUE | NO.4B 66KV CAPACITOR BANK CB AT TTS | 38825.6882 | 38872.509 | CONT | [12 empty] | 0
_1024185438825.6881944445 | 10241854 | 10241641 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT TTS | 38825.6882 | 38872.509 | CONT | 00337509 | SPIMAINT | replace cb ct's | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024030938826.3145833333 | 10240309 |  | Parent | FALSE | WOTS 330KV LINE NO.2 BUS CB AT DDTS | 38826.3146 | 38826.6486 | DAILY | [12 empty] | 0
_1024032338827.3166666667 | 10240323 |  | Parent | FALSE | EX - NO.1 TRANS NO.2 BUS 330KV CB CT R/PH AT DDTS | 38827.3167 | 38828.8569 | CONT | [12 empty] | 0
_1024053738827.3416666667 | 10240537 |  | Parent | FALSE | JLGA NO.4 UNIT TRANS DISC CB AT JLGA | 38827.3417 | 38828.6403 | CONT | [12 empty] | 0
_X2A858H138827.75 | X2A858H1 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK CB AT BTS | 38827.75 | 38834.4424 | DAILY | [12 empty] | 0
_1024069338827.75 | 10240693 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK AT BTS | 38827.75 | 38834.859 | DAILY | 00337002 | SPICAPX | inspect cable terminations at cb | SPIPOWER |  | X2A8 - (BTS) STATION REBUILD | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024036538828.3805555556 | 10240365 |  | Parent | FALSE | KTS NO.2 220KV LINE CB AT WMTS | 38828.3806 | 38828.4451 | DAILY | [12 empty] | 0
_1024069738828.7972222222 | 10240697 |  | Parent | FALSE | KTS NO.2 220KV LINE AT WMTS | 38828.7972 | 38828.8618 | DAILY | 00025731 | SPIMAINT | oil sample to be taked from ct's | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49058A438829.3125 | X49058A4 |  | Parent | FALSE | WOTS 330KV LINE NO.2 BUS CB AT DDTS | 38829.3125 | 38829.4583 | DAILY | [12 empty] | 0
_Z50458A238830.3409722222 | Z50458A2 |  | Parent | FALSE | NO.4 22KV BUS AT BETS | 38830.341 | 38830.6056 | DAILY | 00016373 | DB_AUG | Out W/O No4 22kV Bus. Extend for fut BET 5 fdr | SPIPOWER | Z504 | Z504 - (BETS) 22KV BUS EXTENSIONS AND FDRS BET5 & BET6 | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1024059838830.4895833333 | 10240598 |  | Parent | TRUE | EX - NO.1 220KV BUS AT JLTS | 38830.4896 | 38830.5347 | DAILY | 00009889 | GENCO | JLTS: GENCO Tripped No1 220 kV BUS at JLTS | GENCO |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024061038830.4895833333 | 10240610 | 10240598 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 38830.4896 | 38830.5347 | DAILY | 00015936 | GENCO | No1 220kV Bus at JLTS Trip | GENCO |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024061138830.4895833333 | 10240611 | 10240598 | Child | FALSE | MWTS NO.2 220KV LINE AT JLTS | 38830.4896 | 38830.5347 | DAILY | 00015948 | GENCO | JLTS: GENCO Tripped No1 220 kV BUS at JLTS | GENCO |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024075638830.4895833333 | 10240756 | 10240598 | Child | FALSE | B2 220/66KV TRANS AT MWTS | 38830.4896 | 38830.5347 | DAILY | 00010266 | GENCO | Outage at JLTS due to JLGS | GENCO |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024059938830.5104166667 | 10240599 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS AT JLGB | 38830.5104 | 38834.6708 | CONT | 00009830 | GENCO | Power Station requirements | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1025248338830.6055555556 | 10252483 |  | Parent | FALSE | NO.4 22KV BUS AT BETS | 38830.6056 | 39074.625 | CONT | 00016373 | DB_AUG | Fut Bet 5 Isolators | 3RDPARTY |  |  | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1010347638831.2833333333 | 10103476 |  | Parent | FALSE | NO.1 CSC AT ROTS | 38831.2833 | 38835.6667 | CONT | 00004718 | SPIMAINT | 2 Yearly O/Haul - No.1 CSC & line isols at ROTS | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024048138831.2965277778 | 10240481 |  | Parent | FALSE | B3 220/66KV TRANS AT TSTS | 38831.2965 | 38831.6472 | DAILY | 00007659 | SPIMAINT | Repair 11 kv insulator | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024075438831.6423611111 | 10240754 |  | Parent | FALSE | WKPS-MBTS 220KV NW | 38831.6424 | 38831.6861 | DAILY | 00060196 | FAULT | Forced outage due to fault Comms I/F Relay at MBTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010191738833.2756944444 | 10101917 |  | Parent | FALSE | KTS 220KV LINE NO.3 BUS CB AT BLTS | 38833.2757 | 38834.6347 | CONT | [12 empty] | 0
_1009441038833.2923611111 | 10094410 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 38833.2924 | 38833.6382 | DAILY | 00351939 | SPIMAINT | O/Haul - 220kV CAP BANK (N) | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_Z32158C838833.3166666667 | Z32158C8 |  | Parent | FALSE | NO.3 22KV BUS AT RCTS | 38833.3167 | 38833.7335 | DAILY | 00357244 | SPICAPX | Out W/O Fut No 3 bus bipods install | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Bus | Alstom | 22 |  |  |  | 0
_X4C4581438833.3555555556 | X4C45814 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38833.3556 | 38833.6472 | REPDAILY | [12 empty] | 0
_1024062538833.4388888889 | 10240625 |  | Parent | FALSE | MLTS-HYTS 1 500KV W | 38833.4389 | 38833.5243 | DAILY | 00022630 | APDALCOA | Isolation for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z32158D538833.7409722222 | Z32158D5 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 38833.741 | 38833.8861 | DAILY | 00337581 | DB_AUG | Out W/O No 1A & 2A OLTC mech controls mods | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024061538834.2527777778 | 10240615 |  | Parent | FALSE | L1 220/22KV TRANS AT BTS | 38834.2528 | 38834.6715 | DAILY | 00360728 | SPICAPX | INVESTIGATE REASON FOR L4 TRANS TRIPPING | SPIPOWER |  | X2A8 - (BTS) STATION REBUILD | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024037238834.2854166667 | 10240372 |  | Parent | FALSE | DDTS 330KV LINE NO.2 BUS CB AT WOTS | 38834.2854 | 38834.5958 | DAILY | [12 empty] | 0
_Z32158C738834.2875 | Z32158C7 |  | Parent | FALSE | 2-3 66KV TIE BUS AT RCTS | 38834.2875 | 38834.6771 | DAILY | 00357243 | DB_AUG | Out W/O Instal bipods for 2-3 66kV Tie bus | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Bus | Alstom | 66 |  |  |  | 0
_Z32158D638834.3236111111 | Z32158D6 |  | Parent | FALSE | NO.1B TRANS OLTC MECH AT RCTS | 38834.3236 | 38834.8993 | DAILY | [12 empty] | 0
_1024067638834.4097222222 | 10240676 |  | Parent | FALSE | EX - DDTS NO.1 220KV LINE CB AT MBTS | 38834.4097 | 38834.4611 | DAILY | [12 empty] | 0
_X43458D038834.5972222222 | X43458D0 |  | Parent | FALSE | EX - B1 TRANS NO.2 BUS 220KV CB AT MBTS | 38834.5972 | 38834.6042 | DAILY | [12 empty] | 0
_Z32158D038835.2756944444 | Z32158D0 |  | Parent | TRUE | EX - NO.1 220KV BUS AT RCTS | 38835.2757 | 38835.6132 | DAILY | 00016901 | DB_AUG | Out W/O Complete No 1 220kV bus ext bay H | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z32158D138835.2756944444 | Z32158D1 | Z32158D0 | Child | FALSE | HOTS-RCTS 220KV | 38835.2757 | 38835.6132 | DAILY | 00328509 | SPICAPX | Out W/O HOTS L rebate calc for No 1 bus outage | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024053838835.2847222222 | 10240538 |  | Parent | FALSE | EX - GTS NO.1 220KV LINE AT KTS | 38835.2847 | 38835.6458 | DAILY | 00015985 | SPIMAINT | replace insulator stacks and replace 1 esw blade | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X4C4581438835.3201388889 | X4C45814 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38835.3201 | 38835.6438 | REPDAILY | [12 empty] | 0
_Z33458D638836.2680555556 | Z33458D6 |  | Parent | FALSE | NO.2 66KV BUS AT SVTS | 38836.2681 | 38837.6604 | CONT | 00004861 | VEN_AUG | Split No 2 Bus into No 2 & 3 66kv Buses | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Bus | Eastern | 66 |  |  |  | 0
_1024016238836.29375 | 10240162 |  | Parent | FALSE | L3 220/22KV TRANS AT WMTS | 38836.2937 | 38836.7757 | CONT | 00003237 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024073538837.6819444444 | 10240735 |  | Parent | FALSE | NO.2 22KV BUS AT BETS | 38837.6819 | 39081.625 | CONT | 00016376 | DB_AUG | Fut Bet 6 Isolators | 3RDPARTY |  |  | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X4C4581438838.3145833333 | X4C45814 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38838.3146 | 38838.6924 | REPDAILY | [12 empty] | 0
_X46158C638838.3166666667 | X46158C6 |  | Parent | TRUE | NO.1 66KV BUS AT BATS | 38838.3167 | 38838.784 | REPDAILY | 00006560 | SPICAPX | Out W/O No1 66kV Bus replace insulators etc | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158C738838.3166666667 | X46158C7 | X46158C6 | Child | FALSE | B1 220/66KV TRANS AT BATS | 38838.3167 | 38838.784 | REPDAILY | 00006554 | SPICAPX | Perf calc W/O No1 Trans during No1 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158C838838.3166666667 | X46158C8 | X46158C6 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 38838.3167 | 38838.784 | REPDAILY | 00331109 | SPICAPX | Rebate W/O No1 Cap bank during No1 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z32158C938838.3270833333 | Z32158C9 |  | Parent | TRUE | NO.2 220KV BUS-CAPBK EXTENSION AT RCTS | 38838.3271 | 38838.875 | DAILY | 00016916 | DB_AUG | Out W/O Complete No 2 220kV bus exten and bipods | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z32158D238838.3270833333 | Z32158D2 | Z32158C9 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 38838.3271 | 38838.875 | DAILY | 00337584 | DB_AUG | Out W/O No 2 Trans system perf calc | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z32158D338838.3270833333 | Z32158D3 | Z32158C9 | Child | FALSE | KGTS-RCTS 220KV NB | 38838.3271 | 38838.875 | DAILY | 00026223 | DB_AUG | Out W/O Rebate calc while No 2 220kV bus outage | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z32158D438838.3270833333 | Z32158D4 | Z32158C9 | Child | FALSE | BSS RCTS (0X1) 220KV (Non SPI circuit) | 38838.3271 | 38838.875 | DAILY | 00354016 | DB_AUG | Out W/O Rebate calc while bus outage | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Circuits | Alstom | 220 |  |  |  | 0
_V4S258C038838.3527777778 | V4S258C0 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 38838.3528 | 38842.441 | CONT | 00001328 | SPIMAINT | carry out prep drilling & tapping | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1024075938838.8159722222 | 10240759 |  | Parent | FALSE | EX - NO.2 220/66KV TRANS BANK NO.3 BUS 66KV CB AT MTS | 38838.816 | 38839.6799 | DAILY | [12 empty] | 0
_Z32158D038839.2638888889 | Z32158D0 |  | Parent | TRUE | EX - NO.1 220KV BUS AT RCTS | 38839.2639 | 38839.7083 | DAILY | 00016901 | DB_AUG | Out W/O Complete No 1 220kV bus ext bay H | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z32158D138839.2638888889 | Z32158D1 | Z32158D0 | Child | FALSE | HOTS-RCTS 220KV | 38839.2639 | 38839.7083 | DAILY | 00328509 | SPICAPX | Out W/O HOTS L rebate calc for No 1 bus outage | SPIPOWER | Z321 | Z321 - (RCTS) INSTALL NEW TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010297138839.2902777778 | 10102971 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT SMTS | 38839.2903 | 38842.6493 | CONT | 00026101 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X46158C638839.2923611111 | X46158C6 |  | Parent | TRUE | NO.1 66KV BUS AT BATS | 38839.2924 | 38839.7535 | REPDAILY | 00006560 | SPICAPX | Out W/O No1 66kV Bus replace insulators etc | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158C738839.2923611111 | X46158C7 | X46158C6 | Child | FALSE | B1 220/66KV TRANS AT BATS | 38839.2924 | 38839.7535 | REPDAILY | 00006554 | SPICAPX | Perf calc W/O No1 Trans during No1 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158C838839.2923611111 | X46158C8 | X46158C6 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 38839.2924 | 38839.7535 | REPDAILY | 00331109 | SPICAPX | Rebate W/O No1 Cap bank during No1 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1009276438839.3145833333 | 10092764 |  | Parent | FALSE | EX - MLTS NO.1 220KV LINE AT GTS | 38839.3146 | 38839.7035 | DAILY | 00017903 | SPIMAINT | O/Haul - MLTS 220kV No.1 LINE at GTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024071238839.3381944444 | 10240712 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 38839.3382 | 38839.3993 | DAILY | 00060938 | APDALCOA | SCAP: HYTS No 2 Line De-energ for APD | HVCUST |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1010211438839.375 | 10102114 |  | Parent | FALSE | NO.2 22KV CAPACITOR BANK AT KGTS | 38839.375 | 38839.6931 | DAILY | 00017394 | SPIMAINT | O/Haul - Cap Bank & E/Sw (N) | SPIPOWER |  |  | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010167538839.3840277778 | 10101675 |  | Parent | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 38839.384 | 38839.6062 | DAILY | 00329970 | SPIMAINT | O/HAUL Transformer Div Mechanism (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024071338839.45 | 10240713 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 38839.45 | 38839.4785 | DAILY | 00027386 | APDALCOA | SCAP: HYTS No 1 LIne de-energ for APD | HVCUST |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z50358C238839.5423611111 | Z50358C2 |  | Parent | FALSE | EX - YPS NO.8 220KV LINE NO.3 BUS CB AT ROTS | 38839.5424 | 38843.25 | CONT | [12 empty] | 0
_1024079438839.7083333333 | 10240794 |  | Parent | FALSE | EX - NO.1 220KV BUS AT RCTS | 38839.7083 | 38874.4062 | CONT | 00016901 | SPICAPX | RCTS No.3 Trans No.1 and No.2 Bus connections HVS. | 3RDPARTY |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z32158D738839.75 | Z32158D7 |  | Parent | FALSE | R3 TRANS X PROT AT RCTS | 38839.75 | 38874.3125 | CONT | [12 empty] | 0
_X46158C938840.2944444444 | X46158C9 |  | Parent | FALSE | NO.2 66KV BUS AT BATS | 38840.2944 | 38840.7396 | REPDAILY | 00006561 | SPICAPX | Out W/O No2 66kV Bus replace insulators etc | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010324538840.2979166667 | 10103245 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 38840.2979 | 38840.6451 | DAILY | 00112418 | SPIMAINT | O/Haul - Cap Bank & E/Sw (EM) | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1009972338840.3 | 10099723 |  | Parent | FALSE | GTS NO.1 220KV LINE AT MLTS | 38840.3 | 38840.7417 | DAILY | 00022489 | SPIMAINT | O/Haul - GTS No.1 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458C238840.3576388889 | X38458C2 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38840.3576 | 38840.691 | REPDAILY | 00023231 | SPICAPX | Out W/O New B1 Trans gantry foundations | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010360338841.2951388889 | 10103603 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 38841.2951 | 38841.6569 | DAILY | 00354024 | SPIMAINT | O/Haul - 220kV CAP BANK (EM) | SPIPOWER |  |  | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X46158C938841.3020833333 | X46158C9 |  | Parent | FALSE | NO.2 66KV BUS AT BATS | 38841.3021 | 38841.7438 | REPDAILY | 00006561 | SPICAPX | Out W/O No2 66kV Bus replace insulators etc | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458C238841.3375 | X38458C2 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38841.3375 | 38841.6979 | REPDAILY | 00023231 | SPICAPX | Out W/O New B1 Trans gantry foundations | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024092138841.6243055556 | 10240921 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 38841.6243 | 38841.6667 | CONT | [12 empty] | 0
_1010279338842.3180555556 | 10102793 |  | Parent | FALSE | NO.4 GEN TRANS 220KV E/SW AT HWPS | 38842.3181 | 38842.6333 | DAILY | [12 empty] | 0
_1010211538842.3340277778 | 10102115 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 38842.334 | 38842.6562 | CONT | 00017270 | SPIMAINT | 4 Yearly O/Haul - SVC at KGTS | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024080338842.4020833333 | 10240803 |  | Parent | FALSE | NO.3 GEN TRANS 500KV LINE E/SW AT LYPS | 38842.4021 | 38846.3674 | CONT | [12 empty] | 0
_1024093438842.4666666667 | 10240934 |  | Parent | FALSE | ERTS NO.1 220KV LINE NO.2 BUS CB AT CBTS | 38842.4667 | 38842.5451 | DAILY | [12 empty] | 0
_Z33458D938843.2590277778 | Z33458D9 |  | Parent | FALSE | NO.3 TRANS 66KV CB AT SVTS | 38843.259 | 38843.6993 | DAILY | [12 empty] | 0
_Z50358C338843.2652777778 | Z50358C3 |  | Parent | TRUE | NO.3 220KV BUS AT ROTS | 38843.2653 | 38860.6257 | CONT | 00329013 | VEN_AUG | Replace YPS No 8 Line No3 Bus CB B/S isol | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z50358C438843.2652777778 | Z50358C4 | Z50358C3 | Child | FALSE | MTS NO.3 220KV LINE AT ROTS | 38843.2653 | 38860.6257 | CONT | 00023099 | VEN_AUG | Rebate - No3 Bus YPS No 8 Line No3 Bus CB B/S isol | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023985438843.2916666667 | 10239854 |  | Parent | FALSE | EX - KTS NO.3 220KV LINE AT GTS | 38843.2917 | 38843.7 | DAILY | 00017902 | SPIMAINT | Out W/O KTS-GTS 3L line choke removal both ends | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024097838843.29375 | 10240978 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE NO.3 BUS CB AT KTS | 38843.2937 | 38844.7375 | CONT | [12 empty] | 0
_1024016038843.2951388889 | 10240160 |  | Parent | FALSE | L1 220/22KV TRANS AT WMTS | 38843.2951 | 38844.6146 | CONT | 00003234 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024130338843.3048611111 | 10241303 |  | Parent | FALSE | B3 220/66KV TRANS AT KTS | 38843.3049 | 38843.3111 | DAILY | 00350448 | FAULT | Outage to allow CB isolation | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024130838843.3048611111 | 10241308 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE AT KTS | 38843.3049 | 38843.3111 | DAILY | 00015986 | FAULT | Outage to allow CB isolation | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024066038844.2708333333 | 10240660 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE AT HWTS | 38844.2708 | 38844.6924 | DAILY | 00016238 | SPIMAINT | Replace faulty line CVT | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024062638844.2930555556 | 10240626 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 38844.2931 | 38844.7375 | DAILY | 00017900 | SPIMAINT | Out W/O KTS-GTS 1L line choke removal both ends | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024129138844.6201388889 | 10241291 |  | Parent | FALSE | WKPS 220KV LINE AT MBTS | 38844.6201 | 38844.7139 | DAILY | 00011756 | FAULT | Loss of controls and prot on CB at MBTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024129238844.6201388889 | 10241292 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 38844.6201 | 38844.7139 | DAILY | 00011755 | FAULT | Loss of controls and prot on CB at MBTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V4S258C138844.6965277778 | V4S258C1 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 38844.6965 | 38855.6667 | CONT | 00001328 | SPIMAINT | inject silicon & replace flanges | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1024099338844.9090277778 | 10240993 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 38844.909 | 38846.9146 | CONT | 00356084 | GENCO | HWPS No6 Gen Trans Isolation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010297238845.2569444444 | 10102972 |  | Parent | FALSE | H2 330/220KV TRANS BANK AT SMTS | 38845.2569 | 38848.641 | CONT | 00026102 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1010371738845.2631944444 | 10103717 |  | Parent | TRUE | HYTS NO.1 500KV LINE AT MLTS | 38845.2632 | 38845.8187 | REPDAILY | 00022695 | SPIMAINT | O/Haul - HYTS No.1 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024088838845.2631944444 | 10240888 | 10103717 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 38845.2632 | 38845.8187 | CONT | 00003007 | SPIMAINT | MLTS: HYTS No 1 Shunt reactor unavail | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024089038845.2631944444 | 10240890 | 10103717 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 38845.2632 | 38845.8187 | CONT | 00002863 | SPIMAINT | MLTS: HYTS No 1 Line Reactor Unavail | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024172238845.2631944444 | 10241722 | 10103717 | Child | FALSE | APD NO.1 500KV LINE AT HYTS | 38845.2632 | 38845.8187 | REPDAILY | 00027386 | SPIMAINT | MLTS: HYTS No 1 Line Reactor Unavail | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010154938845.2722222222 | 10101549 |  | Parent | TRUE | NO.2 220KV BUS AT DDTS | 38845.2722 | 38845.7236 | REPDAILY | 00003980 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 |  |  |  | 0
_1024014238845.2722222222 | 10240142 | 10101549 | Child | FALSE | SHTS 220KV LINE AT DDTS | 38845.2722 | 38845.7236 | REPDAILY | 00012371 | SPIMAINT | Rebate W/O DDTS-SHTS L during DDTS bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024014338845.2722222222 | 10240143 | 10101549 | Child | FALSE | MBTS NO.2 220KV LINE AT DDTS | 38845.2722 | 38845.7236 | REPDAILY | 00012363 | SPIMAINT | Rebate W/O DDTS-MBTS 2L during DDTS bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024062738845.2916666667 | 10240627 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 38845.2917 | 38845.7278 | DAILY | 00017901 | SPIMAINT | Out W/O KTS-GTS 2L line choke removal both ends | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010347338845.3645833333 | 10103473 |  | Parent | FALSE | NO.2 CSC AT ROTS | 38845.3646 | 38848.6264 | CONT | 00004716 | SPIMAINT | 2 Yearly O/Haul - No.2 CSC at ROTS | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024104738845.5881944444 | 10241047 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 38845.5882 | 38845.5965 | DAILY | [12 empty] | 0
_1024106138845.7236111111 | 10241061 |  | Parent | FALSE | H2 TRANS 220KV CB AT DDTS | 38845.7236 | 38846.2674 | CONT | [12 empty] | 0
_1024128938845.7236111111 | 10241289 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 38845.7236 | 38846.2674 | CONT | 00352121 | FAULT | No2 Trans 220KV CB Faulty Failed To Latch | ALSTOM |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024172638845.7236111111 | 10241726 |  | Parent | FALSE | HYTS-APD 1 500KV W | 38845.7236 | 38846.2674 | REPDAILY | 00319998 | APDALCOA | SCAP:APD-HYTS No 1 500kV Line to APD | HVCUST |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1010154938846.2673611111 | 10101549 |  | Parent | TRUE | NO.2 220KV BUS AT DDTS | 38846.2674 | 38846.7104 | REPDAILY | 00003980 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 |  |  |  | 0
_1024014238846.2673611111 | 10240142 | 10101549 | Child | FALSE | SHTS 220KV LINE AT DDTS | 38846.2674 | 38846.7104 | REPDAILY | 00012371 | SPIMAINT | Rebate W/O DDTS-SHTS L during DDTS bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024014338846.2673611111 | 10240143 | 10101549 | Child | FALSE | MBTS NO.2 220KV LINE AT DDTS | 38846.2674 | 38846.7104 | REPDAILY | 00012363 | SPIMAINT | Rebate W/O DDTS-MBTS 2L during DDTS bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010371738846.2729166667 | 10103717 |  | Parent | TRUE | HYTS NO.1 500KV LINE AT MLTS | 38846.2729 | 38846.8 | REPDAILY | 00022695 | SPIMAINT | O/Haul - HYTS No.1 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024088838846.2729166667 | 10240888 | 10103717 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 38846.2729 | 38846.8 | CONT | 00003007 | SPIMAINT | MLTS: HYTS No 1 Shunt reactor unavail | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024089038846.2729166667 | 10240890 | 10103717 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 38846.2729 | 38846.8 | CONT | 00002863 | SPIMAINT | MLTS: HYTS No 1 Line Reactor Unavail | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024172238846.2729166667 | 10241722 | 10103717 | Child | FALSE | APD NO.1 500KV LINE AT HYTS | 38846.2729 | 38846.8 | REPDAILY | 00027386 | SPIMAINT | MLTS: HYTS No 1 Line Reactor Unavail | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009277538846.3111111111 | 10092775 |  | Parent | FALSE | HWTS NO.1 220KV LINE AT HWPS | 38846.3111 | 38846.5979 | DAILY | 00015794 | SPIMAINT | O/Haul - 220KV LINE at HWPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024106838846.3875 | 10241068 |  | Parent | TRUE | EX - DPS LINE CB AT MBTS | 38846.3875 | 38849.5792 | CONT | [12 empty] | 0
_1024166738846.3875 | 10241667 | 10241068 | Child | FALSE | DPS 220KV LINE AT MBTS | 38846.3875 | 38849.5792 | CONT | 00011754 | STHHYDRO | Work by SHCC | SNOWY |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1024110038846.6597222222 | 10241100 |  | Parent | FALSE | A1 515/230KV TRANS AT HWTS | 38846.6597 | 38846.7847 | DAILY | 00009772 | FORCED | A1 Trans stranded by 500kV CB air leak | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024172638846.7104166667 | 10241726 |  | Parent | FALSE | HYTS-APD 1 500KV W | 38846.7104 | 38847.2729 | REPDAILY | 00319998 | APDALCOA | SCAP:APD-HYTS No 1 500kV Line to APD | HVCUST |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1024014538846.7138888889 | 10240145 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 38846.7139 | 38846.7292 | CONT | 00352121 | FORCED | H2 Trans stranded by 220kV CB Fault | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024172838846.8 | 10241728 |  | Parent | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 38846.8 | 38847.2688 | REPDAILY | 00003007 | SPIMAINT | MLTS: HYTS No 2 Line Reactor Disc/Isol & E'd | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010371738847.26875 | 10103717 |  | Parent | TRUE | HYTS NO.1 500KV LINE AT MLTS | 38847.2688 | 38847.7653 | REPDAILY | 00022695 | SPIMAINT | O/Haul - HYTS No.1 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024088838847.26875 | 10240888 | 10103717 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 38847.2688 | 38847.7653 | CONT | 00003007 | SPIMAINT | MLTS: HYTS No 1 Shunt reactor unavail | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024089038847.26875 | 10240890 | 10103717 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 38847.2688 | 38847.7653 | CONT | 00002863 | SPIMAINT | MLTS: HYTS No 1 Line Reactor Unavail | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024172238847.26875 | 10241722 | 10103717 | Child | FALSE | APD NO.1 500KV LINE AT HYTS | 38847.2688 | 38847.7653 | REPDAILY | 00027386 | SPIMAINT | MLTS: HYTS No 1 Line Reactor Unavail | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010154938847.2729166667 | 10101549 |  | Parent | TRUE | NO.2 220KV BUS AT DDTS | 38847.2729 | 38847.7139 | REPDAILY | 00003980 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 |  |  |  | 0
_1024014238847.2729166667 | 10240142 | 10101549 | Child | FALSE | SHTS 220KV LINE AT DDTS | 38847.2729 | 38847.7139 | REPDAILY | 00012371 | SPIMAINT | Rebate W/O DDTS-SHTS L during DDTS bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024014338847.2729166667 | 10240143 | 10101549 | Child | FALSE | MBTS NO.2 220KV LINE AT DDTS | 38847.2729 | 38847.7139 | REPDAILY | 00012363 | SPIMAINT | Rebate W/O DDTS-MBTS 2L during DDTS bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024107538847.3631944444 | 10241075 |  | Parent | FALSE | HPS 66KV LINE AT WOTS | 38847.3632 | 38847.6 | DAILY | 00012055 | 3RDPARTY | WOTS-HPS 66kV Line Isol only | TRANSGRD |  |  | Circuits | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 3
_1024107738847.3894097222 | 10241077 |  | Parent | FALSE | SMTS 500KV LINE Y PROT AT KTS | 38847.3894 | 38887.3895 | DAILY | [12 empty] | 0
_X4C4581438847.4006944444 | X4C45814 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38847.4007 | 38847.6653 | REPDAILY | [12 empty] | 0
_1024172638847.7138888889 | 10241726 |  | Parent | FALSE | HYTS-APD 1 500KV W | 38847.7139 | 38848.2646 | REPDAILY | 00319998 | APDALCOA | SCAP:APD-HYTS No 1 500kV Line to APD | HVCUST |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1024172838847.7652777778 | 10241728 |  | Parent | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 38847.7653 | 38848.2688 | REPDAILY | 00003007 | SPIMAINT | MLTS: HYTS No 2 Line Reactor Disc/Isol & E'd | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010154938848.2645833333 | 10101549 |  | Parent | TRUE | NO.2 220KV BUS AT DDTS | 38848.2646 | 38848.7292 | REPDAILY | 00003980 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 |  |  |  | 0
_1024014238848.2645833333 | 10240142 | 10101549 | Child | FALSE | SHTS 220KV LINE AT DDTS | 38848.2646 | 38848.7292 | REPDAILY | 00012371 | SPIMAINT | Rebate W/O DDTS-SHTS L during DDTS bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024014338848.2645833333 | 10240143 | 10101549 | Child | FALSE | MBTS NO.2 220KV LINE AT DDTS | 38848.2646 | 38848.7292 | REPDAILY | 00012363 | SPIMAINT | Rebate W/O DDTS-MBTS 2L during DDTS bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010371738848.26875 | 10103717 |  | Parent | TRUE | HYTS NO.1 500KV LINE AT MLTS | 38848.2688 | 38848.7743 | REPDAILY | 00022695 | SPIMAINT | O/Haul - HYTS No.1 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024088838848.26875 | 10240888 | 10103717 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 38848.2688 | 38848.7743 | CONT | 00003007 | SPIMAINT | MLTS: HYTS No 1 Shunt reactor unavail | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024089038848.26875 | 10240890 | 10103717 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 38848.2688 | 38848.7743 | CONT | 00002863 | SPIMAINT | MLTS: HYTS No 1 Line Reactor Unavail | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024172238848.26875 | 10241722 | 10103717 | Child | FALSE | APD NO.1 500KV LINE AT HYTS | 38848.2688 | 38848.7743 | REPDAILY | 00027386 | SPIMAINT | MLTS: HYTS No 1 Line Reactor Unavail | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009277238848.3201388889 | 10092772 |  | Parent | FALSE | HWTS NO.3 220KV LINE AT HWPS | 38848.3201 | 38848.6125 | DAILY | 00015782 | SPIMAINT | O/Haul - HWTS No.3 LINE at HWPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X4C4581638848.3243055556 | X4C45816 |  | Parent | FALSE | EX - MWTS NO.1 220KV LINE NO.1 BUS CB AT JLTS | 38848.3243 | 38848.6569 | CONT | [12 empty] | 0
_Z33458E438848.3402777778 | Z33458E4 |  | Parent | FALSE | NO.1 TRANS 66KV CB AT SVTS | 38848.3403 | 38848.3944 | DAILY | [12 empty] | 0
_1010371738849.2680555556 | 10103717 |  | Parent | TRUE | HYTS NO.1 500KV LINE AT MLTS | 38849.2681 | 38849.9243 | REPDAILY | 00022695 | SPIMAINT | O/Haul - HYTS No.1 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024088838849.2680555556 | 10240888 | 10103717 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 38849.2681 | 38849.9243 | CONT | 00003007 | SPIMAINT | MLTS: HYTS No 1 Shunt reactor unavail | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024089038849.2680555556 | 10240890 | 10103717 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 38849.2681 | 38849.9243 | CONT | 00002863 | SPIMAINT | MLTS: HYTS No 1 Line Reactor Unavail | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024172238849.2680555556 | 10241722 | 10103717 | Child | FALSE | APD NO.1 500KV LINE AT HYTS | 38849.2681 | 38849.9243 | REPDAILY | 00027386 | SPIMAINT | MLTS: HYTS No 1 Line Reactor Unavail | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024109438849.2923611111 | 10241094 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT SMTS | 38849.2924 | 38849.5986 | DAILY | 00026101 | SPIMAINT | repair/replace faulty upper fan | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009277338849.3138888889 | 10092773 |  | Parent | FALSE | HWTS NO.4 220KV LINE AT HWPS | 38849.3139 | 38849.5931 | DAILY | 00015783 | SPIMAINT | O/Haul - HWTS No.4 LINE at HWPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024077838849.3819444444 | 10240778 |  | Parent | FALSE | B2 220/66KV TRANS AT GNTS | 38849.3819 | 38849.5243 | DAILY | 00000743 | SPIMAINT | OUT W/O Top up No2 TR 220kV cb cts with nitrogen | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1022712038849.4618055556 | 10227120 |  | Parent | FALSE | SMTS NO.2 330KV LINE NO.1 BUS CB BUS SIDE ROI AT DDTS | 38849.4618 | 38849.5368 | DAILY | [12 empty] | 0
_1024128738849.5930555556 | 10241287 |  | Parent | FALSE | A4 515/230KV TRANS BANK AT HWTS | 38849.5931 | 38849.6819 | DAILY | 00337582 | FAULT | CB Trip at HWTS | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024123238849.9444444444 | 10241232 |  | Parent | FALSE | EX - NO.7 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 38849.9444 | 38851.8333 | CONT | [12 empty] | 0
_1010371638850.2847222222 | 10103716 |  | Parent | TRUE | HYTS NO.2 500KV LINE AT MLTS | 38850.2847 | 38850.6792 | REPDAILY | 00022754 | SPIMAINT | O/Haul - HYTS No.2 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024103038850.2847222222 | 10241030 | 10103716 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 38850.2847 | 38850.6792 | REPDAILY | 00003008 | SPIMAINT | MLTS: HYTS No 2 Line Reactor Disc/Isol & E'd | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024172438850.2847222222 | 10241724 | 10103716 | Child | FALSE | APD NO.2 500KV LINE AT HYTS | 38850.2847 | 38850.6792 | REPDAILY | 00060938 | SPIMAINT | wo to capture rebate | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024172538850.2847222222 | 10241725 | 10103716 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 38850.2847 | 38850.6792 | REPDAILY | 00002862 | SPIMAINT | wo to capture rebate | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024130938850.6395833333 | 10241309 |  | Parent | FALSE | HWPS NO.1 220KV LINE AT JLTS | 38850.6396 | 38850.6639 | DAILY | 00015936 | FAULT | JLGS: Loss of No 1 220 kV Bus | GENCO |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024086138850.6791666667 | 10240861 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 38850.6792 | 38851.2542 | REPDAILY | 00060938 | APDALCOA | SCAP:APD-HYTS No 2 500kV Line to APD | HVCUST |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1010371638851.2541666667 | 10103716 |  | Parent | TRUE | HYTS NO.2 500KV LINE AT MLTS | 38851.2542 | 38851.7486 | REPDAILY | 00022754 | SPIMAINT | O/Haul - HYTS No.2 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024103038851.2541666667 | 10241030 | 10103716 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 38851.2542 | 38851.7486 | REPDAILY | 00003008 | SPIMAINT | MLTS: HYTS No 2 Line Reactor Disc/Isol & E'd | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024172438851.2541666667 | 10241724 | 10103716 | Child | FALSE | APD NO.2 500KV LINE AT HYTS | 38851.2542 | 38851.7486 | REPDAILY | 00060938 | SPIMAINT | wo to capture rebate | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024172538851.2541666667 | 10241725 | 10103716 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 38851.2542 | 38851.7486 | REPDAILY | 00002862 | SPIMAINT | wo to capture rebate | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024086138851.7486111111 | 10240861 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 38851.7486 | 38852.2715 | REPDAILY | 00060938 | APDALCOA | SCAP:APD-HYTS No 2 500kV Line to APD | HVCUST |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1010371638852.2715277778 | 10103716 |  | Parent | TRUE | HYTS NO.2 500KV LINE AT MLTS | 38852.2715 | 38852.7597 | REPDAILY | 00022754 | SPIMAINT | O/Haul - HYTS No.2 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024103038852.2715277778 | 10241030 | 10103716 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 38852.2715 | 38852.7597 | REPDAILY | 00003008 | SPIMAINT | MLTS: HYTS No 2 Line Reactor Disc/Isol & E'd | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024172438852.2715277778 | 10241724 | 10103716 | Child | FALSE | APD NO.2 500KV LINE AT HYTS | 38852.2715 | 38852.7597 | REPDAILY | 00060938 | SPIMAINT | wo to capture rebate | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024172538852.2715277778 | 10241725 | 10103716 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 38852.2715 | 38852.7597 | REPDAILY | 00002862 | SPIMAINT | wo to capture rebate | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X46158D338852.2916666667 | X46158D3 |  | Parent | TRUE | NO.1 66KV BUS AT BATS | 38852.2917 | 38852.7764 | DAILY | 00006560 | SPICAPX | Out W/O No1 66kV Bus replace insulators etc. | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158D438852.2916666667 | X46158D4 | X46158D3 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 38852.2917 | 38852.7764 | DAILY | 00331109 | SPICAPX | Rebate W/O No1 66 Cap BK during No1 66 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X46158D538852.2916666667 | X46158D5 | X46158D3 | Child | FALSE | B1 220/66KV TRANS AT BATS | 38852.2917 | 38852.7764 | DAILY | 00006554 | SPICAPX | Perf calc W/O No1 Trans during No1 66 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X4C4581638852.3180555556 | X4C45816 |  | Parent | FALSE | EX - MWTS NO.1 220KV LINE NO.1 BUS CB AT JLTS | 38852.3181 | 38852.6729 | CONT | [12 empty] | 0
_1024086138852.7597222222 | 10240861 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 38852.7597 | 38853.2708 | REPDAILY | 00060938 | APDALCOA | SCAP:APD-HYTS No 2 500kV Line to APD | HVCUST |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1024172738852.7597222222 | 10241727 |  | Parent | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 38852.7597 | 38853.2708 | REPDAILY | 00003008 | SPIMAINT | MLTS: HYTS No 2 Line Reactor Disc/Isol & E'd | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010307838853.2631944444 | 10103078 |  | Parent | FALSE | NO.2 330KV BUS AT SMTS | 38853.2632 | 38853.6819 | REPDAILY | 00001331 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Western | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1010371638853.2708333333 | 10103716 |  | Parent | TRUE | HYTS NO.2 500KV LINE AT MLTS | 38853.2708 | 38853.7458 | REPDAILY | 00022754 | SPIMAINT | O/Haul - HYTS No.2 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024103038853.2708333333 | 10241030 | 10103716 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 38853.2708 | 38853.7458 | REPDAILY | 00003008 | SPIMAINT | MLTS: HYTS No 2 Line Reactor Disc/Isol & E'd | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024172438853.2708333333 | 10241724 | 10103716 | Child | FALSE | APD NO.2 500KV LINE AT HYTS | 38853.2708 | 38853.7458 | REPDAILY | 00060938 | SPIMAINT | wo to capture rebate | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024172538853.2708333333 | 10241725 | 10103716 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 38853.2708 | 38853.7458 | REPDAILY | 00002862 | SPIMAINT | wo to capture rebate | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X4C4581638853.2958333333 | X4C45816 |  | Parent | FALSE | EX - MWTS NO.1 220KV LINE NO.1 BUS CB AT JLTS | 38853.2958 | 38853.6243 | CONT | [12 empty] | 0
_X46158D638853.2979166667 | X46158D6 |  | Parent | TRUE | NO.2 66KV BUS AT BATS | 38853.2979 | 38853.7403 | DAILY | 00006561 | SPICAPX | Out W/O No2 66kV Bus to replace ins etc | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158D738853.2979166667 | X46158D7 | X46158D6 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 38853.2979 | 38853.7403 | DAILY | 00331118 | SPICAPX | Rebate W/O No2 66 Cap bk during No2 66 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X46158D838853.2979166667 | X46158D8 | X46158D6 | Child | FALSE | B2 220/66KV TRANS AT BATS | 38853.2979 | 38853.7403 | DAILY | 00006555 | SPICAPX | Perf calc W/O No2 Trans during No2 66 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024171538853.3 | 10241715 | X2A558D7 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 38853.3 | 38853.5097 | DAILY | 00327661 | SPICAPX | complete dc wiring mods & test cb | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X2A558D738853.3 | X2A558D7 |  | Parent | TRUE | NO.4 220KV CAPACITOR BANK CB AT FBTS | 38853.3 | 38853.5097 | DAILY | [12 empty] | 0
_1024097938853.3090277778 | 10240979 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 38853.309 | 38853.616 | DAILY | 00017270 | SPIMAINT | KGTS SVC Faulty Thyristor | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1009145738853.3125 | 10091457 |  | Parent | FALSE | ERTS NO.2 LINE/HWPS NO.1 LINE 220KV CB AT ROTS | 38853.3125 | 38853.6542 | DAILY | [12 empty] | 0
_1009277038853.3263888889 | 10092770 |  | Parent | FALSE | HWTS NO.2 500KV LINE AT LYPS | 38853.3264 | 38853.6062 | DAILY | 00016087 | SPIMAINT | O/Haul - Line SDs (EH) | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A558D838853.5111111111 | X2A558D8 |  | Parent | FALSE | 1-3 220KV BUS TIE CB AT FBTS | 38853.5111 | 38853.6625 | DAILY | [12 empty] | 0
_1024086138853.7458333333 | 10240861 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 38853.7458 | 38854.2708 | REPDAILY | 00060938 | APDALCOA | SCAP:APD-HYTS No 2 500kV Line to APD | HVCUST |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1024172738853.7458333333 | 10241727 |  | Parent | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 38853.7458 | 38854.2708 | REPDAILY | 00003008 | SPIMAINT | MLTS: HYTS No 2 Line Reactor Disc/Isol & E'd | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010307838854.2631944444 | 10103078 |  | Parent | FALSE | NO.2 330KV BUS AT SMTS | 38854.2632 | 38854.6681 | REPDAILY | 00001331 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Western | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1010371638854.2708333333 | 10103716 |  | Parent | TRUE | HYTS NO.2 500KV LINE AT MLTS | 38854.2708 | 38854.8056 | REPDAILY | 00022754 | SPIMAINT | O/Haul - HYTS No.2 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024103038854.2708333333 | 10241030 | 10103716 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 38854.2708 | 38854.8056 | REPDAILY | 00003008 | SPIMAINT | MLTS: HYTS No 2 Line Reactor Disc/Isol & E'd | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024172438854.2708333333 | 10241724 | 10103716 | Child | FALSE | APD NO.2 500KV LINE AT HYTS | 38854.2708 | 38854.8056 | REPDAILY | 00060938 | SPIMAINT | wo to capture rebate | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024172538854.2708333333 | 10241725 | 10103716 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 38854.2708 | 38854.8056 | REPDAILY | 00002862 | SPIMAINT | wo to capture rebate | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024171338854.2972222222 | 10241713 | X2A558E0 | Child | FALSE | WMTS NO.2 220KV LINE AT FBTS | 38854.2972 | 38854.4313 | DAILY | 00017157 | SPICAPX | complete dc wiring mods & test cb | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1024171438854.2972222222 | 10241714 | X2A558E0 | Child | FALSE | BLTS 220KV LINE AT FBTS | 38854.2972 | 38854.4313 | DAILY | 00002660 | SPICAPX | complete dc wiring mods & test cb | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X2A558E038854.2972222222 | X2A558E0 |  | Parent | TRUE | WMTS NO.1 220KV LINE CB AT FBTS | 38854.2972 | 38854.4313 | DAILY | [12 empty] | 0
_1009875938854.3076388889 | 10098759 |  | Parent | FALSE | LYGS A1 TRANS 500KV CB AT LYPS | 38854.3076 | 38854.6222 | DAILY | [12 empty] | 0
_1010156338854.3097222222 | 10101563 |  | Parent | FALSE | MSS NO.1 LINE/SMTS NO.1 LINE 330KV CB AT DDTS | 38854.3097 | 38854.6722 | REPDAILY | [12 empty] | 0
_X2A558D938854.4333333333 | X2A558D9 |  | Parent | FALSE | B1 TRANS 66KV CB AT FBTS | 38854.4333 | 38854.5451 | DAILY | [12 empty] | 0
_X2A558E138854.5458333333 | X2A558E1 |  | Parent | FALSE | 3-4 220KV BUS TIE CB AT FBTS | 38854.5458 | 38854.6597 | DAILY | [12 empty] | 0
_1024136238854.7618055556 | 10241362 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 38854.7618 | 38854.7903 | DAILY | [12 empty] | 0
_1010308338855.2722222222 | 10103083 |  | Parent | FALSE | NO.1 330KV BUS AT SMTS | 38855.2722 | 38856.6542 | CONT | 00001330 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Western | 330 |  |  |  | 0
_1024170938855.2861111111 | 10241709 | X2A558E2 | Child | FALSE | WMTS NO.2 220KV LINE AT FBTS | 38855.2861 | 38855.4313 | DAILY | 00017157 | SPICAPX | complete dc wiring mods & test cb | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X2A558E238855.2861111111 | X2A558E2 |  | Parent | TRUE | WMTS NO.2 220KV LINE CB AT FBTS | 38855.2861 | 38855.4313 | DAILY | [12 empty] | 0
_1024104938855.2923611111 | 10241049 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 38855.2924 | 38855.5687 | DAILY | 00002862 | SPIMAINT | Out W/O M2 Transformer to replace its 22kV VT | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024104338855.3034722222 | 10241043 |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 38855.3035 | 38856.6514 | CONT | 00007452 | SPIMAINT | Trans Tests by Tech services Charge to 10241443 | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010276538855.3111111111 | 10102765 |  | Parent | FALSE | LYPS NO.3 500KV LINE E/SW AT HWTS | 38855.3111 | 38856.6062 | CONT | [12 empty] | 0
_1010156338855.3138888889 | 10101563 |  | Parent | FALSE | MSS NO.1 LINE/SMTS NO.1 LINE 330KV CB AT DDTS | 38855.3139 | 38855.6521 | REPDAILY | [12 empty] | 0
_1010288738855.3541666667 | 10102887 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT HYTS | 38855.3542 | 38855.5833 | DAILY | 00331066 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X2A558E338855.4340277778 | X2A558E3 |  | Parent | FALSE | B3 TRANS 66KV CB AT FBTS | 38855.434 | 38855.5861 | DAILY | [12 empty] | 0
_1024140338855.5722222222 | 10241403 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 38855.5722 | 38855.8771 | DAILY | 00002862 | FORCED | Repair 22kV VT | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X2A558E438855.59375 | X2A558E4 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT FBTS | 38855.5938 | 38855.7035 | DAILY | [12 empty] | 0
_1024171238856.2909722222 | 10241712 | X2A558E5 | Child | FALSE | BLTS 220KV LINE AT FBTS | 38856.291 | 38856.4118 | DAILY | 00002660 | SPICAPX | complete dc wiring mods & test cb | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X2A558E538856.2909722222 | X2A558E5 |  | Parent | TRUE | BLTS 220KV LINE CB AT FBTS | 38856.291 | 38856.4118 | DAILY | [12 empty] | 0
_X38458C338856.3548611111 | X38458C3 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38856.3549 | 38856.7208 | REPDAILY | 00023231 | SPICAPX | Out W/O Finish gantry foundations and erection | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A558E638856.4152777778 | X2A558E6 |  | Parent | FALSE | B4 TRANS 66KV CB AT FBTS | 38856.4153 | 38856.534 | DAILY | [12 empty] | 0
_V4S258D038856.5277777778 | V4S258D0 |  | Parent | FALSE | KTS 500KV LINE AT SMTS | 38856.5278 | 38856.6646 | DAILY | 00012441 | SPIMAINT | install weather protection | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A558E738856.5333333333 | X2A558E7 |  | Parent | FALSE | 2EXT-4 66KV BUS TIE CB AT FBTS | 38856.5333 | 38856.6658 | DAILY | [12 empty] | 0
_1010278138856.91875 | 10102781 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 38856.9187 | 38863.6111 | CONT | [12 empty] | 0
_X38458C338857.3194444444 | X38458C3 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38857.3194 | 38857.5507 | REPDAILY | 00023231 | SPICAPX | Out W/O Finish gantry foundations and erection | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X3E658A538858.2777777778 | X3E658A5 |  | Parent | FALSE | NO.1 66KV BUS AT WMTS | 38858.2778 | 38858.5632 | DAILY | 00003258 | SPICAPX | install flicker blades on no.1 bus ext cable isol | SPIPOWER | X3E6 | X3E6 - (WMTS) INSTALL 2*DISCONNECT SWS NO.1 & NO.3 66KV BUS | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010299838859.2590277778 | 10102998 |  | Parent | FALSE | DDTS NO.1 330KV LINE AT SMTS | 38859.259 | 38863.6493 | CONT | 00012749 | SPIMAINT | O/Haul - 330kV Line-CVTs & L/Traps | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A558E838859.2902777778 | X2A558E8 |  | Parent | FALSE | NPSD 220KV LINE CB AT FBTS | 38859.2903 | 38859.4111 | DAILY | [12 empty] | 0
_1009276538859.2993055556 | 10092765 |  | Parent | FALSE | EX - MLTS NO.2 220KV LINE AT GTS | 38859.2993 | 38859.709 | DAILY | 00017904 | SPIMAINT | O/Haul - MLTS 220kV No.2 LINE at GTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1008688738859.3013888889 | 10086887 |  | Parent | FALSE | SHTS NO.3 220KV LINE AT GNTS | 38859.3014 | 38859.6771 | DAILY | 00021794 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024104438859.3104166667 | 10241044 |  | Parent | FALSE | L2 220/22KV TRANS BANK AT RWTS | 38859.3104 | 38860.6597 | CONT | 00007447 | SPIMAINT | Trans Tests by Tech services Charge to 10241441 | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V4S258C238859.3631944444 | V4S258C2 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 38859.3632 | 38863.6583 | CONT | 00001328 | SPIMAINT | carry out prep drilling & tapping | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_X2A558E938859.5291666667 | X2A558E9 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT FBTS | 38859.5292 | 38859.6632 | DAILY | [12 empty] | 0
_X41258A038860.2743055556 | X41258A0 |  | Parent | TRUE | EX - NO.2 220KV BUS AT SHTS | 38860.2743 | 38860.6924 | DAILY | 00000846 | SPICAPX | Out W/O No2 220kV Bus. Disconnect bays A & B | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X41258A138860.2743055556 | X41258A1 | X41258A0 | Child | FALSE | GNTS NO.3 220KV LINE AT SHTS | 38860.2743 | 38860.6924 | DAILY | 00352426 | SPICAPX | Rebate W/O GNTS-SHTS 3L during No2 220 Bus outage | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X41258A238860.2743055556 | X41258A2 | X41258A0 | Child | FALSE | B2 220/66KV TRANS AT SHTS | 38860.2743 | 38860.6924 | DAILY | 00000841 | SPICAPX | Perf calc W/O No2 Trans during No2 220 Bus outage | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V5A058B038860.3090277778 | V5A058B0 |  | Parent | FALSE | SPARE 66KV CB - STOCK ITEM 9003437 AT YARRA-ST | 38860.309 | 38860.5069 | CONT | [12 empty] | 0
_Z33458E538860.3131944445 | Z33458E5 |  | Parent | TRUE | NO.4A 66KV CAPACITOR BANK AT SVTS | 38860.3132 | 38860.5813 | DAILY | 00004825 | VEN_AUG | ModifyProt DC supplies & Trip check (CB isolated) | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z33458E638860.3131944445 | Z33458E6 | Z33458E5 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT SVTS | 38860.3132 | 38860.5813 | DAILY | 00329600 | VEN_AUG | Rebate ModifyProt DC supplies & Trip check | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1009285338860.3131944445 | 10092853 |  | Parent | FALSE | MLTS NO.2 220KV LINE CB AT GTS | 38860.3132 | 38860.6729 | REPDAILY | [12 empty] | 0
_1024028538860.3222222222 | 10240285 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 38860.3222 | 38860.675 | REPDAILY | 00019243 | SPIMAINT | Rebate Capture for Prot Work On the SVC | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X2A558F038860.4298611111 | X2A558F0 |  | Parent | FALSE | SYN/COND TRANS NO.3 BUS 66KV CB AT FBTS | 38860.4299 | 38860.6806 | DAILY | [12 empty] | 0
_Z50358C538860.6256944445 | Z50358C5 |  | Parent | FALSE | EX - YPS NO.8 220KV LINE NO.3 BUS CB AT ROTS | 38860.6257 | 38901.2743 | CONT | [12 empty] | 0
_X41258A338861.2534722222 | X41258A3 |  | Parent | TRUE | EX - FVTS/BETS 220KV LINE AT SHTS | 38861.2535 | 38866.6 | CONT | 00000810 | SPICAPX | Out W/O BETS-FVTS-SHTS Line inc. DDTS SHTS Line | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X41258A438861.2534722222 | X41258A4 | X41258A3 | Child | FALSE | EX - DDTS 220KV LINE AT SHTS | 38861.2535 | 38866.6 | CONT | 00000811 | SPICAPX | Rebate W/O DDTS-SHTS Line | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010622138861.2944444444 | 10106221 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 38861.2944 | 38869.7243 | CONT | 00354002 | SPIMAINT | O/HAUL Transformer Div Mechanism (EM) | SPIPOWER |  |  | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1009285338861.3173611111 | 10092853 |  | Parent | FALSE | MLTS NO.2 220KV LINE CB AT GTS | 38861.3174 | 38861.6451 | REPDAILY | [12 empty] | 0
_X2A858H838861.3381944444 | X2A858H8 |  | Parent | FALSE | NO.2 220KV BUS AT BTS | 38861.3382 | 38861.4812 | DAILY | 00000943 | SPICAPX | check operation of earth switches | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010170038861.3680555556 | 10101700 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT GNTS | 38861.3681 | 38861.6729 | DAILY | 00000745 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1024150238861.5423611111 | 10241502 |  | Parent | TRUE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 38861.5424 | 38861.566 | DAILY | [12 empty] | 0
_1024170838861.5423611111 | 10241708 | 10241502 | Child | FALSE | A2 500/220KV TRANS BANK AT KTS | 38861.5424 | 38861.566 | DAILY | 00026096 | SPIMAINT | repair leaking prv | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024028538861.54375 | 10240285 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 38861.5437 | 38861.6944 | REPDAILY | 00019243 | SPIMAINT | Rebate Capture for Prot Work On the SVC | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024147738862.3006944444 | 10241477 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS 220KV SD W/PH AT JLGB | 38862.3007 | 38862.6972 | DAILY | [12 empty] | 0
_1010167138862.3305555556 | 10101671 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 38862.3306 | 38862.6056 | DAILY | 00329879 | SPIMAINT | O/Haul - CAPACITOR BANK (N) | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024028538862.3326388889 | 10240285 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 38862.3326 | 38862.7042 | REPDAILY | 00019243 | SPIMAINT | Rebate Capture for Prot Work On the SVC | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024152738862.55625 | 10241527 |  | Parent | TRUE | WMTS NO.2 220KV LINE CB AT FBTS | 38862.5563 | 38862.5639 | DAILY | [12 empty] | 0
_1024170438862.55625 | 10241704 | 10241527 | Child | FALSE | WMTS NO.2 220KV LINE AT FBTS | 38862.5563 | 38862.5639 | DAILY | 00017157 | SPIMAINT | top up sf6 gas | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1024143038863.4888888889 | 10241430 |  | Parent | FALSE | B3 220/66KV TRANS AT TSTS | 38863.4889 | 38863.6083 | DAILY | 00007659 | SPIMAINT | Repair 11 kv insulator charge to 10240481 | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53258A038864.2361111111 | Z53258A0 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT HWPS | 38864.2361 | 38864.7743 | REPDAILY | 00015790 | VEN_AUG | HWPS -ROTS 1&2 Lines Erect Tower & cut over lines | SPIPOWER | Z532 | Z532 - (HWTS-ROTS) LINE 3 HW MINE EXTENSION - ST1 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158D938864.2972222222 | X46158D9 |  | Parent | FALSE | NO.1 66KV BUS AT BATS | 38864.2972 | 38865.6868 | CONT | 00006560 | SPICAPX | Out W/O No1 66kV Bus replace insulators etc. | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024146738864.7743055556 | 10241467 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT HWPS | 38864.7743 | 38865.2576 | CONT | 00015790 | GEN_AUG | HVS: HWPS-ROTS No 1 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53258A038865.2576388889 | Z53258A0 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT HWPS | 38865.2576 | 38865.641 | REPDAILY | 00015790 | VEN_AUG | HWPS -ROTS 1&2 Lines Erect Tower & cut over lines | SPIPOWER | Z532 | Z532 - (HWTS-ROTS) LINE 3 HW MINE EXTENSION - ST1 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010064638865.3194444444 | 10100646 |  | Parent | FALSE | NO.2 22KV BUS AT RWTS | 38865.3194 | 38865.6354 | DAILY | 00007483 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_V4S258C338866.2125 | V4S258C3 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 38866.2125 | 38876.6618 | CONT | 00001328 | SPIMAINT | inject silicon & replace flanges | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1009903238866.2708333333 | 10099032 |  | Parent | FALSE | NO.2 220KV BUS AT GTS | 38866.2708 | 38866.7361 | REPDAILY | 00002834 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024128438866.2722222222 | 10241284 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 38866.2722 | 38866.7444 | REPDAILY | 00060191 | SPIMAINT | Out W/O MSS-DDTS No2 Line Xray conductor | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158E038866.2930555556 | X46158E0 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 38866.2931 | 38866.6924 | DAILY | 00006554 | SPICAPX | Out W/O No1 Trans to remove old 66kV CB foundation | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009903238867.2743055556 | 10099032 |  | Parent | FALSE | NO.2 220KV BUS AT GTS | 38867.2743 | 38867.7396 | REPDAILY | 00002834 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010147138867.2916666667 | 10101471 |  | Parent | FALSE | NO.4 220KV CAPACITOR BANK CB AT FBTS | 38867.2917 | 38868.6021 | CONT | [12 empty] | 0
_1010154738867.2930555556 | 10101547 |  | Parent | FALSE | H3 330/220KV TRANS AT DDTS | 38867.2931 | 38867.7146 | REPDAILY | 00003971 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1010096538867.2944444444 | 10100965 |  | Parent | TRUE | NO.2 220KV CAPACITOR BANK CB AT ATS | 38867.2944 | 38868.6424 | CONT | [12 empty] | 0
_1024173638867.2944444444 | 10241736 | 10100965 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ATS | 38867.2944 | 38868.6424 | CONT | 00350821 | SPIMAINT | CL.1 O/HAUL - ASEA HPL245 220KV CB | SPIPOWER |  |  | Capacitors | Western | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024128438867.5055555556 | 10241284 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 38867.5056 | 38867.734 | REPDAILY | 00060191 | SPIMAINT | Out W/O MSS-DDTS No2 Line Xray conductor | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024128538868.2722222222 | 10241285 |  | Parent | FALSE | MSS -DDTS 1 330KV NW | 38868.2722 | 38868.7424 | DAILY | 00060190 | SPIMAINT | Out W/O MSS-DDTS No1 Line Xray conductor | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009903238868.2770833333 | 10099032 |  | Parent | FALSE | NO.2 220KV BUS AT GTS | 38868.2771 | 38868.7736 | REPDAILY | 00002834 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010154738868.2951388889 | 10101547 |  | Parent | FALSE | H3 330/220KV TRANS AT DDTS | 38868.2951 | 38868.7236 | REPDAILY | 00003971 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1010222938869.2847222222 | 10102229 |  | Parent | FALSE | B3 220/66KV TRANS AT KTS | 38869.2847 | 38869.6646 | DAILY | 00350448 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010215038869.2916666667 | 10102150 |  | Parent | FALSE | EX - TTS NO.1 220KV LINE NO.2 BUS CB AT KTS | 38869.2917 | 38870.6042 | CONT | [12 empty] | 0
_1024191038869.4833333333 | 10241910 |  | Parent | FALSE | HWPS NO.1 220KV LINE AT JLTS | 38869.4833 | 38869.4861 | DAILY | 00015936 | FAULT | JLTS: 220kV CB Blocked Alarm Low Oil Pressure | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024190838869.4833333333 | 10241908 |  | Parent | FALSE | MWTS NO.2 220KV LINE AT JLTS | 38869.4833 | 38869.4868 | DAILY | 00015948 | FAULT | JLTS: 220kV CB Blocked Alarm Low Oil Pressure | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024191138869.4833333333 | 10241911 |  | Parent | FALSE | MWTS NO.1 220KV LINE AT JLTS | 38869.4833 | 38869.4889 | DAILY | 00015947 | FAULT | JLTS: 220kV CB Blocked Alarm Low Oil Pressure | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024190538869.4833333333 | 10241905 |  | Parent | FALSE | EX - MWTS NO.1 220KV LINE NO.1 BUS CB AT JLTS | 38869.4833 | 38869.6542 | DAILY | [12 empty] | 0
_1024177338870.0430555556 | 10241773 |  | Parent | FALSE | NO.3 GEN 220/16.5KV TRANS AT HWPS | 38870.0431 | 38873.3708 | CONT | 00009644 | GENCO | Power Station Requirement | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1024162738870.2819444445 | 10241627 |  | Parent | FALSE | A4 500/220KV TRANS BANK AT KTS | 38870.2819 | 38870.5542 | DAILY | 00026098 | SPIMAINT | top up red & white phase 220kv bushings | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024164038871.2701388889 | 10241640 |  | Parent | FALSE | DDTS-SHTS 220KV NW | 38871.2701 | 38871.6681 | REPDAILY | 00352425 | SPIMAINT | Out W/O repair hot joints on 8 towers | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024036338871.2881944444 | 10240363 |  | Parent | FALSE | B3 220/66KV TRANS AT FBTS | 38871.2882 | 38871.5792 | DAILY | 00002727 | SPIMAINT | Cooling fan failure - replace repaired fan | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158E138871.2916666667 | X46158E1 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 38871.2917 | 38871.7681 | DAILY | 00006559 | SPICAPX | Out W/O No2 220kV Bus connect Fut ROIs bays H&D | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158E238871.2916666667 | X46158E2 | X46158E1 | Child | FALSE | WBTS 220KV LINE AT BATS | 38871.2917 | 38871.7681 | DAILY | 00012410 | SPICAPX | Rebate W/O HOTS Line during No2 220kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158E338871.2916666667 | X46158E3 | X46158E1 | Child | FALSE | MLTS NO.2 220KV LINE AT BATS | 38871.2917 | 38871.7681 | DAILY | 00012431 | SPICAPX | Rebate W/O MLTS 2L prox for No2 220kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158E438871.2916666667 | X46158E4 | X46158E1 | Child | FALSE | B2 220/66KV TRANS AT BATS | 38871.2917 | 38871.7681 | DAILY | 00006555 | SPICAPX | Perf calc W/O No2 Trans for No2 220kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009438138871.3111111111 | 10094381 |  | Parent | FALSE | NO.4 66KV BUS AT TTS | 38871.3111 | 38871.6882 | DAILY | 00001556 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Western | 66 |  |  |  | 0
_1024164038872.2680555556 | 10241640 |  | Parent | FALSE | DDTS-SHTS 220KV NW | 38872.2681 | 38872.5847 | REPDAILY | 00352425 | SPIMAINT | Out W/O repair hot joints on 8 towers | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X3E658A638872.2715277778 | X3E658A6 |  | Parent | FALSE | NO.3 66KV BUS AT WMTS | 38872.2715 | 38872.5312 | DAILY | 00003260 | SPICAPX | install flicker blades on no.3 bus ext cable isol | SPIPOWER | X3E6 | X3E6 - (WMTS) INSTALL 2*DISCONNECT SWS NO.1 & NO.3 66KV BUS | Bus | Western | 66 |  |  |  | 0
_1024145138872.2958333333 | 10241451 | X46158E5 | Child | FALSE | WBTS 220KV LINE AT BATS | 38872.2958 | 38872.6667 | DAILY | 00012410 | SPICAPX | Rebate W/O HOTS Line during No2 220kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024145238872.2958333333 | 10241452 | X46158E5 | Child | FALSE | TGTS 220KV LINE AT BATS | 38872.2958 | 38872.6667 | DAILY | 00012435 | SPICAPX | Rebate W/O TGTS Line prox for No2 220kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024145338872.2958333333 | 10241453 | X46158E5 | Child | FALSE | B2 220/66KV TRANS AT BATS | 38872.2958 | 38872.6667 | DAILY | 00006555 | SPICAPX | Perf calc W/O No2 Trans for No2 220kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158E538872.2958333333 | X46158E5 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 38872.2958 | 38872.6667 | DAILY | 00006559 | SPICAPX | Out W/O No2 220kV Bus connect Fut ROIs bays K&D | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025248538872.6145833333 | 10252485 |  | Parent | FALSE | TGTS 220KV LINE NO.2 TIE BUS BUS SIDE ROI AT BATS | 38872.6146 | 39249.2507 | CONT | [12 empty] | 0
_1025248538872.65625 | 10252485 |  | Parent | FALSE | TGTS 220KV LINE NO.2 TIE BUS BUS SIDE ROI AT BATS | 38872.6562 | 39249.209 | CONT | [12 empty] | 0
_X46158E638873.28125 | X46158E6 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 38873.2812 | 38873.6799 | REPDAILY | 00006554 | SPICAPX | Out W/O No1 Trans to prelim install new 66kV CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010191338873.2861111111 | 10101913 |  | Parent | FALSE | 1-4 66KV BUS TIE CB AT BLTS | 38873.2861 | 38873.6354 | DAILY | [12 empty] | 0
_1010215138873.2993055556 | 10102151 |  | Parent | FALSE | EX - TTS NO.2 220KV LINE NO.2 BUS CB AT KTS | 38873.2993 | 38874.6444 | CONT | [12 empty] | 0
_1024165638873.3166666667 | 10241656 |  | Parent | FALSE | LY NO.4 66KV FDR NO.4 BUS CB FDR SIDE ISOL AT MWTS | 38873.3167 | 38873.6167 | DAILY | [12 empty] | 0
_1010154538873.3215277778 | 10101545 |  | Parent | FALSE | GNTS NO.3 220KV LINE AT DDTS | 38873.3215 | 38873.7562 | REPDAILY | 00012373 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z52058A138873.3409722222 | Z52058A1 |  | Parent | FALSE | MLTS-BATS 1 220KV WY | 38873.341 | 38873.6771 | DAILY | 00022728 | VEN_AUG | Out W/O MLTS-BATS 1L weather monitor | SPIPOWER | Z520 | Z520 - (ROTS-YPS,ROTS-HWTS) 220KV LINE WIND MONITORING | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024184238873.8083333333 | 10241842 |  | Parent | FALSE | NO.1 CSC AT ROTS | 38873.8083 | 38875.5708 | CONT | 00004718 | FAULT | Investigate/Repair after fault | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1010191838874.2805555556 | 10101918 |  | Parent | FALSE | 4-5 220KV BUS TIE CB AT BLTS | 38874.2806 | 38875.6292 | CONT | [12 empty] | 0
_1010343638874.3006944444 | 10103436 |  | Parent | FALSE | B1 TRANS NO.1 BUS 220KV CB AT RWTS | 38874.3007 | 38875.6611 | CONT | [12 empty] | 0
_1010154538874.3159722222 | 10101545 |  | Parent | FALSE | GNTS NO.3 220KV LINE AT DDTS | 38874.316 | 38874.7069 | REPDAILY | 00012373 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024094238874.4270833333 | 10240942 |  | Parent | FALSE | HOTS-RCTS 220KV | 38874.4271 | 38874.4396 | DAILY | 00328509 | DB_AUG | RCTS: No 1 220kV Bus de-nergised for 3Tr comm | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z32158D938874.43125 | Z32158D9 |  | Parent | FALSE | R3 TRANS X PROT AT RCTS | 38874.4313 | 38875.5938 | CONT | [12 empty] | 0
_Z52058A238874.4513888889 | Z52058A2 |  | Parent | FALSE | MLTS-BATS 2 220KV WY | 38874.4514 | 38874.6458 | DAILY | 00022731 | VEN_AUG | Out W/O MLTS-BATS 2L install weather monitor | SPIPOWER | Z520 | Z520 - (ROTS-YPS,ROTS-HWTS) 220KV LINE WIND MONITORING | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010215238875.2986111111 | 10102152 |  | Parent | FALSE | EX - WMTS NO.1 220KV LINE NO.1 BUS CB AT KTS | 38875.2986 | 38876.6438 | CONT | [12 empty] | 0
_1024164938875.3069444444 | 10241649 |  | Parent | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 38875.3069 | 38875.6736 | REPDAILY | 00015793 | SPIMAINT | Replace insulators charge to 10234674 | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010405638875.3145833333 | 10104056 |  | Parent | FALSE | B2 220/66KV TRANS AT SHTS | 38875.3146 | 38875.7639 | REPDAILY | 00000841 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024094438875.3819444444 | 10240944 |  | Parent | TRUE | NO.2 22KV BUS AT RCTS | 38875.3819 | 38875.5938 | DAILY | 00016998 | DB_AUG | RCTS: No 2 66 & 22kV Bus de-ener-3Tr comm | SPIPOWER |  |  | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1024193438875.3819444444 | 10241934 | 10240944 | Child | FALSE | NO.2 22KV CAPACITOR BANK AT RCTS | 38875.3819 | 38875.5938 | DAILY | 00016713 | DB_AUG | RCTS: No 2 66 & 22kV Bus de-ener-3Tr comm | SPIPOWER |  |  | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V55358A038875.4270833333 | V55358A0 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT EPSY | 38875.4271 | 38875.8049 | DAILY | 00087035 | SPICAPX | Out W/O RF noise measurements MBTS 1L CB L/S ROI | SPIPOWER | V553 | V553 - (EPSY) INVESTIGATE POSSIBLE EXCESSIVE RF | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1024189438875.6875 | 10241894 |  | Parent | FALSE | EX - 1-2 22KV BUS TIE CB AT MTS | 38875.6875 | 38875.7174 | DAILY | [12 empty] | 0
_1010191438876.2743055556 | 10101914 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT BLTS | 38876.2743 | 38876.6444 | DAILY | [12 empty] | 0
_1010343538876.2923611111 | 10103435 |  | Parent | FALSE | B1 TRANS NO.2 BUS 220KV CB AT RWTS | 38876.2924 | 38877.6194 | CONT | [12 empty] | 0
_1024178938876.29375 | 10241789 |  | Parent | FALSE | EX - SYTS LINE/A4 TRANS 500KV CB AT KTS | 38876.2937 | 38876.6493 | DAILY | [12 empty] | 0
_1010405638876.3083333333 | 10104056 |  | Parent | FALSE | B2 220/66KV TRANS AT SHTS | 38876.3083 | 38876.6736 | REPDAILY | 00000841 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024164938876.3111111111 | 10241649 |  | Parent | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 38876.3111 | 38876.6479 | REPDAILY | 00015793 | SPIMAINT | Replace insulators charge to 10234674 | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024188438876.3520833333 | 10241884 |  | Parent | FALSE | W4 GEN TRANS 220KV CB AT YPS | 38876.3521 | 38881.7021 | CONT | [12 empty] | 0
_1024130138876.375 | 10241301 |  | Parent | FALSE | EX - NO.1 66KV BUS VT AT TGTS | 38876.375 | 38876.4889 | DAILY | [12 empty] | 0
_1009728838876.5284722222 | 10097288 |  | Parent | FALSE | EX - NO.2 66KV BUS VT AT TGTS | 38876.5285 | 38876.6062 | DAILY | [12 empty] | 0
_1010191538877.2784722222 | 10101915 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT BLTS | 38877.2785 | 38877.5972 | DAILY | [12 empty] | 0
_1024179038877.2888888889 | 10241790 |  | Parent | FALSE | EX - A4 TRANS NO.1 BUS 500KV CB AT KTS | 38877.2889 | 38877.6458 | DAILY | [12 empty] | 0
_1024165038877.3138888889 | 10241650 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT HWPS | 38877.3139 | 38877.591 | DAILY | 00015790 | SPIMAINT | Replace insulators charge to 10234674 | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024060938877.3375 | 10240609 |  | Parent | FALSE | EX - NO.1B TRANS W/PH AT TGTS | 38877.3375 | 38877.6896 | DAILY | 00003125 | SPIMAINT | Top Up 220 Kv Bushing | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024187238877.3465277778 | 10241872 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 38877.3465 | 38877.5167 | DAILY | 00354002 | SPIMAINT | Replace A1 Trans | SPIPOWER |  |  | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1024180238878.3006944444 | 10241802 |  | Parent | FALSE | EPS -TTS 1 220KV N | 38878.3007 | 38878.7153 | REPDAILY | 00331826 | SPIMAINT | Out W/O EPS-TTS Line repair hot joints along line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V4S258D138878.3236111111 | V4S258D1 |  | Parent | FALSE | KTS 500KV LINE AT SMTS | 38878.3236 | 38878.3868 | DAILY | 00012441 | SPIMAINT | install weather protection | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V4S258D238878.4305555556 | V4S258D2 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT SMTS | 38878.4306 | 38878.5312 | DAILY | 00012440 | SPIMAINT | install weather protection | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024196338878.5541666667 | 10241963 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB LINE SIDE ISOL AT SMTS | 38878.5542 | 38878.6431 | DAILY | [12 empty] | 0
_1024193138879.2951388889 | 10241931 |  | Parent | TRUE | S360 HWTS-SMTS 1 500KV | 38879.2951 | 38879.6472 | DAILY | [12 empty] | 0
_1024254738879.2951388889 | 10242547 | 10241931 | Child | FALSE | HWTS-SMTS 1 500KV WT | 38879.2951 | 38879.6472 | DAILY | 00119314 | SPIMAINT | socket clevis pin 1/4 out T360 | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024180238879.3055555556 | 10241802 |  | Parent | FALSE | EPS -TTS 1 220KV N | 38879.3056 | 38879.4868 | REPDAILY | 00331826 | SPIMAINT | Out W/O EPS-TTS Line repair hot joints along line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024197838880.9625 | 10241978 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 38880.9625 | 38881.2493 | CONT | 00356079 | GENCO | Isolation of HWPS Unit 1 | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024198938881.4548611111 | 10241989 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT HTS | 38881.4549 | 38884.6569 | CONT | [12 empty] | 0
_1024250638881.4548611111 | 10242506 | 10241989 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT HTS | 38881.4549 | 38884.6569 | CONT | 00004426 | FORCED | Out for rebate on Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024250838881.4548611111 | 10242508 | 10241989 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HTS | 38881.4549 | 38884.6569 | CONT | 00331019 | FORCED | Rebate calc for Cap Bank on CB failure | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010343438882.2930555556 | 10103434 |  | Parent | FALSE | ROTS 220KV LINE NO.2 BUS CB AT RWTS | 38882.2931 | 38883.6556 | DAILY | [12 empty] | 0
_1010215338882.2951388889 | 10102153 |  | Parent | FALSE | EX - WMTS NO.2 220KV LINE NO.1 BUS CB AT KTS | 38882.2951 | 38883.6389 | CONT | [12 empty] | 0
_1024164638882.3152777778 | 10241646 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 38882.3153 | 38883.6306 | CONT | 00003011 | SPIMAINT | Out W/O 220kV Shunt react for HV testing | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X4C458A538882.325 | X4C458A5 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38882.325 | 38882.6465 | REPDAILY | [12 empty] | 0
_1024043538883.1770833333 | 10240435 |  | Parent | FALSE | NO.2 330KV BUS AT DDTS | 38883.1771 | 38883.3896 | DAILY | 00003979 | SPICAPX | Out W/O Removing CT's from with-in sw/yard | SPIPOWER |  | X490 - (DDTS) 220KV REDEVELOPMENT | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024204138883.1791666667 | 10242041 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT KTS | 38883.1792 | 38883.1944 | CONT | 00026096 | FORCED | De-energise A2 Trans due to CB lockout fault | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024204338883.1909722222 | 10242043 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 38883.191 | 38883.3896 | CONT | [12 empty] | 0
_X4C458A538883.3152777778 | X4C458A5 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38883.3153 | 38883.6465 | REPDAILY | [12 empty] | 0
_X2A558F938883.5458333333 | X2A558F9 |  | Parent | TRUE | NO.1 TRANS 66KV CB AT SVTS | 38883.5458 | 38883.6542 | DAILY | [12 empty] | 0
_X2A558H138883.5458333333 | X2A558H1 | X2A558F9 | Child | FALSE | B1 220/66KV TRANS AT SVTS | 38883.5458 | 38883.6542 | DAILY | 00004849 | SPICAPX | Avail of plant Modify CB wiring for DC duplication | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A558F638884.2930555556 | X2A558F6 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT SVTS | 38884.2931 | 38884.4062 | DAILY | [12 empty] | 0
_X2A558F738884.2930555556 | X2A558F7 | X2A558F6 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT SVTS | 38884.2931 | 38884.4062 | DAILY | 00004824 | SPICAPX | Rebate Install duplicated battery system | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024204938884.2944444444 | 10242049 |  | Parent | FALSE | EX - SMTS LINE/A2 TRANS 500KV CB AT KTS | 38884.2944 | 38884.6361 | DAILY | [12 empty] | 0
_1010343138884.2958333333 | 10103431 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT RWTS | 38884.2958 | 38884.5903 | DAILY | [12 empty] | 0
_X2A858I138884.3215277778 | X2A858I1 |  | Parent | FALSE | TTS NO.3 220KV LINE NO.3 BUS ROI AT BTS | 38884.3215 | 38884.6882 | DAILY | [12 empty] | 0
_X2A558G038884.5125 | X2A558G0 |  | Parent | TRUE | NO.2 TRANS 66KV CB AT SVTS | 38884.5125 | 38884.6535 | DAILY | [12 empty] | 0
_X2A558H238884.5125 | X2A558H2 | X2A558G0 | Child | FALSE | B2 220/66KV TRANS AT SVTS | 38884.5125 | 38884.6535 | DAILY | 00004850 | SPICAPX | Avail of plant Modify CB wiring for DC duplication | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024213938884.98125 | 10242139 |  | Parent | FALSE | NO.7 GEN TRANS LINE AT HWPS | 38884.9812 | 38887.3472 | CONT | 00356085 | GENCO | HWPS No7 Gen Tran Isol SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X2A558F538885.2805555556 | X2A558F5 |  | Parent | TRUE | HTS NO.1 220KV LINE CB AT SVTS | 38885.2806 | 38885.4299 | DAILY | [12 empty] | 0
_X2A558G938885.2805555556 | X2A558G9 | X2A558F5 | Child | FALSE | HTS NO.1 220KV LINE AT SVTS | 38885.2806 | 38885.4299 | DAILY | 00351703 | SPICAPX | Rebate Modify CB wiring for DC duplication | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024157438885.3111111111 | 10241574 | X46158E7 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 38885.3111 | 38886.4507 | CONT | 00331118 | SPICAPX | Rebate W/O No2 66 Cap bk during No2 66 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024157538885.3111111111 | 10241575 | X46158E7 | Child | FALSE | B2 220/66KV TRANS AT BATS | 38885.3111 | 38886.4507 | CONT | 00006555 | SPICAPX | Perf calc W/O No2 Trans during No2 66 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158E738885.3111111111 | X46158E7 |  | Parent | TRUE | NO.2 66KV BUS AT BATS | 38885.3111 | 38886.4507 | CONT | 00006561 | SPICAPX | Out W/O No2 66kV Bus to replace ins/move Tr 66 cb | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1002328138885.3159722222 | 10023281 |  | Parent | TRUE | S015 HWTS-SMTS 1 500KV | 38885.316 | 38885.7063 | REPDAILY | [12 empty] | 0
_1024254838885.3159722222 | 10242548 | 10023281 | Child | FALSE | HWTS-SMTS 1 500KV G | 38885.316 | 38885.7063 | REPDAILY | 00020191 | SPIMAINT | INSUL BROKEN REPL SU pC stL q1(29)P BN 36000 NGK 1 | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A558F838885.43125 | X2A558F8 |  | Parent | TRUE | HTS NO.2 220KV LINE CB AT SVTS | 38885.4313 | 38885.5403 | DAILY | [12 empty] | 0
_X2A558H038885.43125 | X2A558H0 | X2A558F8 | Child | FALSE | HTS NO.2 220KV LINE AT SVTS | 38885.4313 | 38885.5403 | DAILY | 00351702 | SPICAPX | Rebate Modify CB wiring for DC duplication | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010343938886.2815625 | 10103439 |  | Parent | FALSE | B1 TRANS NO.1 BUS 220KV CB TRANS SIDE ISOL AT RWTS | 38886.2816 | 38886.6153 | DAILY | [12 empty] | 0
_X4C458A538886.2916666667 | X4C458A5 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38886.2917 | 38886.5653 | REPDAILY | [12 empty] | 0
_1002328138886.3131944445 | 10023281 |  | Parent | TRUE | S015 HWTS-SMTS 1 500KV | 38886.3132 | 38886.6611 | REPDAILY | [12 empty] | 0
_1024254838886.3131944445 | 10242548 | 10023281 | Child | FALSE | HWTS-SMTS 1 500KV G | 38886.3132 | 38886.6611 | REPDAILY | 00020191 | SPIMAINT | INSUL BROKEN REPL SU pC stL q1(29)P BN 36000 NGK 1 | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158A138887.2854166667 | Z53158A1 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 38887.2854 | 38887.7188 | DAILY | 00004776 | VEN_AUG | Decommission old HWPS No3 Line Bus side isol | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158A238887.2854166667 | Z53158A2 | Z53158A1 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 38887.2854 | 38887.7188 | DAILY | 00354024 | VEN_AUG | Rebate for Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X46158E838887.2881944444 | X46158E8 |  | Parent | FALSE | B2 220/66KV TRANS AT BATS | 38887.2882 | 38887.7174 | DAILY | 00006555 | SPICAPX | Out W/O No2 Trans to remove old 66kV CB foundation | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010188338887.3 | 10101883 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 38887.3 | 38887.6944 | REPDAILY | 00016040 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A858I238887.3034722222 | X2A858I2 |  | Parent | FALSE | 2-3 220KV BUS TIE CB NO.2 BUS SIDE ROI AT BTS | 38887.3035 | 38887.5653 | DAILY | [12 empty] | 0
_X4C458A538887.3403703704 | X4C458A5 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38887.3404 | 38887.6501 | REPDAILY | [12 empty] | 0
_1024200838887.3777777778 | 10242008 |  | Parent | FALSE | EX - B3 220/66KV TRANS AT TTS | 38887.3778 | 38887.6639 | DAILY | 00001544 | SPIMAINT | red ph low bush, control box mounts, faulty pump | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A558G138887.4166666667 | X2A558G1 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT SVTS | 38887.4167 | 38887.5535 | DAILY | [12 empty] | 0
_1024215638887.5444444444 | 10242156 |  | Parent | FALSE | MWTS NO.1 220KV LINE AT JLTS | 38887.5444 | 38887.6424 | DAILY | 00015947 | SPIMAINT | Fix isol at JLTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A558G238887.5541666667 | X2A558G2 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT SVTS | 38887.5542 | 38887.6562 | DAILY | [12 empty] | 0
_X38458C438887.5986111111 | X38458C4 |  | Parent | FALSE | B2 220/66KV TRANS AT TGTS | 38887.5986 | 38887.6319 | DAILY | 00003127 | SPICAPX | OUT W/O for de-energisation of No2 TX | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158A338888.2763888889 | Z53158A3 | Z53158A4 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 38888.2764 | 38888.6944 | DAILY | 00112418 | VEN_AUG | Rebate for Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z53158A438888.2763888889 | Z53158A4 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 38888.2764 | 38888.6944 | DAILY | 00004778 | VEN_AUG | Decommission old HWPS No3 Line Bus side isol | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010188338888.2979166667 | 10101883 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 38888.2979 | 38888.6944 | REPDAILY | 00016040 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A858I338888.3097222222 | X2A858I3 |  | Parent | FALSE | 1-2 220KV BUS TIE CB NO.2 BUS SIDE ROI AT BTS | 38888.3097 | 38888.6167 | DAILY | [12 empty] | 0
_X4C458A538888.3264814815 | X4C458A5 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38888.3265 | 38888.6405 | REPDAILY | [12 empty] | 0
_X38458C538888.3645833333 | X38458C5 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38888.3646 | 38888.7042 | REPDAILY | 00023231 | SPICAPX | OUT W/O for isolation of No1 TX | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A558G338888.4125 | X2A558G3 |  | Parent | FALSE | 4-5 66KV BUS TIE CB AT SVTS | 38888.4125 | 38888.541 | DAILY | [12 empty] | 0
_X2A558G438888.5423611111 | X2A558G4 |  | Parent | FALSE | 2-4 220KV BUS TIE CB AT SVTS | 38888.5424 | 38888.6569 | DAILY | [12 empty] | 0
_1024221338888.6118055556 | 10242213 |  | Parent | FALSE | EX - NO.1 TRANS GROUP NO.2 BUS 220KV CB AT RCTS | 38888.6118 | 38889.5871 | CONT | [12 empty] | 0
_1024255438889.2569444444 | 10242554 | X2A858I4 | Child | FALSE | RTS 220KV LINE AT BTS | 38889.2569 | 38889.7882 | DAILY | 00015960 | SPICAPX | CONNECT BUS TO L2 TRANS ROI | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858I438889.2569444444 | X2A858I4 |  | Parent | TRUE | RTS 220KV LINE NO.2 BUS ROI AT BTS | 38889.2569 | 38889.7882 | DAILY | [12 empty] | 0
_1010241838889.2881944444 | 10102418 |  | Parent | FALSE | 2-3 220KV BUS TIE CB AT TTS | 38889.2882 | 38890.7396 | CONT | [12 empty] | 0
_1024223138889.2923611111 | 10242231 |  | Parent | FALSE | SYN/COND AT BLTS | 38889.2924 | 38889.3792 | DAILY | 00002547 | FAULT | Protection trip of BLTS S/Con | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010188338889.2986111111 | 10101883 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 38889.2986 | 38889.7122 | REPDAILY | 00016040 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X4C458A538889.3604166667 | X4C458A5 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38889.3604 | 38889.6639 | REPDAILY | [12 empty] | 0
_X38458C538889.3618055556 | X38458C5 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38889.3618 | 38889.6424 | REPDAILY | 00023231 | SPICAPX | OUT W/O for isolation of No1 TX | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A558G538889.4104166667 | X2A558G5 |  | Parent | FALSE | 1-6 66KV BUS TIE CB AT SVTS | 38889.4104 | 38889.5312 | DAILY | [12 empty] | 0
_V4S258D738889.5041666667 | V4S258D7 |  | Parent | FALSE | NO.2 500KV BUS AT SMTS | 38889.5042 | 38988.6354 | CONT | 00001329 | SPIMAINT | inject silicone to prepare flanges & replace seals | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Bus | Western | 500 |  |  |  | 0
_X2A558G738889.5326388889 | X2A558G7 |  | Parent | FALSE | 1-3 220KV BUS TIE CB AT SVTS | 38889.5326 | 38889.6764 | DAILY | [12 empty] | 0
_X2A858I838889.7465277778 | X2A858I8 |  | Parent | FALSE | L2 TRANS NO.2 220KV BUS ROI AT BTS | 38889.7465 | 38919.3958 | DAILY | [12 empty] | 0
_X43258A238890.2729166667 | X43258A2 |  | Parent | TRUE | BSS 220KV LINE AT RCTS | 38890.2729 | 38890.7458 | REPDAILY | 00016966 | SPICAPX | Out W/O BSS L and No 1 220kV Bus in Bay H | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258A338890.2729166667 | X43258A3 | X43258A2 | Child | FALSE | HOTS 220KV LINE AT RCTS | 38890.2729 | 38890.7458 | DAILY | 00016954 | SPICAPX | Out W/O Rebate calc while No 1 220kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010146238890.2895833333 | 10101462 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT FBTS | 38890.2896 | 38890.6264 | DAILY | [12 empty] | 0
_1010188338890.2958333333 | 10101883 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 38890.2958 | 38890.691 | REPDAILY | 00016040 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z33458E338890.2979166667 | Z33458E3 |  | Parent | FALSE | NO.4 220KV BUS AT SVTS | 38890.2979 | 38892.3111 | CONT | 00004859 | VEN_AUG | Modify 3-4 BT CB 4 Bus side ROI | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024255538890.3006944444 | 10242555 | X2A858I5 | Child | FALSE | TTS NO.1 220KV LINE AT BTS | 38890.3007 | 38890.809 | DAILY | 00015958 | SPICAPX | remove existing isol operating switch | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858I538890.3006944444 | X2A858I5 |  | Parent | TRUE | TTS NO.1 220KV LINE NO.1 BUS ROI AT BTS | 38890.3007 | 38890.809 | DAILY | [12 empty] | 0
_X4C458A538890.3166666667 | X4C458A5 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38890.3167 | 38890.6361 | REPDAILY | [12 empty] | 0
_1024232838890.3548611111 | 10242328 |  | Parent | FALSE | MLRC 220KV LINE AT RCTS | 38890.3549 | 38890.7458 | DAILY | 00352130 | SPIMAINT | RCTS-MLRC de-energised (linked to X43258A2) | SPIPOWER |  |  | Circuits | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 4
_X38458C538890.3590277778 | X38458C5 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38890.359 | 38890.6972 | REPDAILY | 00023231 | SPICAPX | OUT W/O for isolation of No1 TX | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A558F238891.2895833333 | X2A558F2 |  | Parent | TRUE | NO.4 66KV CAPACITOR BANK CB AT SVTS | 38891.2896 | 38891.5479 | DAILY | [12 empty] | 0
_X2A558F338891.2895833333 | X2A558F3 | X2A558F2 | Child | FALSE | NO.4A 66KV CAPACITOR BANK AT SVTS | 38891.2896 | 38891.5479 | DAILY | 00004825 | SPICAPX | Rebate - Install duplicated battery system | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X2A558F438891.2895833333 | X2A558F4 | X2A558F2 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT SVTS | 38891.2896 | 38891.5479 | DAILY | 00329600 | SPICAPX | Rebate - Install duplicated battery system | SPIPOWER | X2A5 | X2A5 - (ERTS,FBTS,MWTS,SVTS) BATTERY DUPLICATIONS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010146338891.2916666667 | 10101463 |  | Parent | FALSE | 2EXT-4 66KV BUS TIE CB AT FBTS | 38891.2917 | 38891.6215 | DAILY | [12 empty] | 0
_X43258B438891.2930555556 | X43258B4 |  | Parent | FALSE | BSS 220KV LINE AT RCTS | 38891.2931 | 38891.591 | DAILY | 00016966 | SPICAPX | Out W/O Modify BSS LINE Tie Bus Line side isol | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010188338891.2930555556 | 10101883 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 38891.2931 | 38891.6743 | REPDAILY | 00016040 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024207338891.3083333333 | 10242073 |  | Parent | FALSE | TTS 220KV LINE NO.1 BUS CB AT RWTS | 38891.3083 | 38891.6799 | DAILY | [12 empty] | 0
_X4C458A538891.3125 | X4C458A5 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38891.3125 | 38891.6062 | REPDAILY | [12 empty] | 0
_X2A858I638891.3430555556 | X2A858I6 |  | Parent | FALSE | 1-2 220KV BUS TIE CB NO.1 BUS SIDE ROI AT BTS | 38891.3431 | 38891.6188 | DAILY | [12 empty] | 0
_X38458C738891.3659722222 | X38458C7 |  | Parent | FALSE | B2 220/66KV TRANS AT TGTS | 38891.366 | 38891.4437 | DAILY | 00003127 | SPICAPX | OUT W/O for de-energisation of No2 TX | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024229038891.4291666667 | 10242290 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 38891.4292 | 38891.4743 | DAILY | [12 empty] | 0
_1024231838891.7465277778 | 10242318 |  | Parent | FALSE | NO.5 GEN 220/16.5KV TRANS AT HWPS | 38891.7465 | 38895.4701 | CONT | 00009646 | GENCO | Power Station requirements | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1024188838892.2979166667 | 10241888 |  | Parent | FALSE | L1 220/22KV TRANS AT RTS | 38892.2979 | 38893.7222 | CONT | 00007330 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area(W) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z33458E138892.3111111111 | Z33458E1 |  | Parent | TRUE | NO.3 220KV BUS AT SVTS | 38892.3111 | 38892.6875 | DAILY | 00004858 | VEN_AUG | Modify N03-4 BT CB No3 Bus Side isol | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z33458E238892.3111111111 | Z33458E2 | Z33458E1 | Child | FALSE | B3 220/66KV TRANS AT SVTS | 38892.3111 | 38892.6875 | DAILY | 00004851 | VEN_AUG | Avail of plant Modify BT CB No3 &4 Bus side ROIS | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024087338892.3145833333 | 10240873 |  | Parent | TRUE | S199 HWTS-SMTS 2 500KV | 38892.3146 | 38892.6625 | REPDAILY | [12 empty] | 0
_1024256738892.3145833333 | 10242567 | 10240873 | Child | FALSE | HWTS-SMTS 2 500KV G | 38892.3146 | 38892.6625 | REPDAILY | 00020242 | SPIMAINT | Repair hot joints | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024225738892.3201388889 | 10242257 |  | Parent | FALSE | EX - B3 TRANS 220KV CB AT GTS | 38892.3201 | 38892.375 | DAILY | [12 empty] | 0
_Z33458F338892.3333333333 | Z33458F3 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 38892.3333 | 38898.6833 | CONT | 00352791 | VEN_AUG | Commisioning work on new No4 Tranformer | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024256738893.31875 | 10242567 | 10240873 | Child | FALSE | HWTS-SMTS 2 500KV G | 38893.3187 | 38893.6708 | REPDAILY | 00020242 | SPIMAINT | Repair hot joints | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024087338893.31875 | 10240873 |  | Parent | TRUE | S199 HWTS-SMTS 2 500KV | 38893.3187 | 38893.6715 | REPDAILY | [12 empty] | 0
_V4S258C538894.2111111111 | V4S258C5 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 38894.2111 | 38904.3229 | CONT | 00001328 | SPIMAINT | inject silicon & replace seals | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158E938894.2847222222 | X46158E9 |  | Parent | FALSE | B2 220/66KV TRANS AT BATS | 38894.2847 | 38894.566 | DAILY | 00006555 | SPICAPX | Out W/O No2 Trans to prelim install new 66kV CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258A838895.29375 | X43258A8 |  | Parent | FALSE | HOTS 220KV LINE AT RCTS | 38895.2937 | 38895.6194 | DAILY | 00016954 | SPICAPX | Out W/O HOTS Line and Tie Bus -line side isol | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024422538895.29375 | 10244225 | X49058A9 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 38895.2937 | 38987.6861 | CONT | 00352121 | SPICAPX | Out W/O Replace CT's marshalling box and conductor | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X49058A938895.29375 | X49058A9 |  | Parent | TRUE | H2 TRANS 330KV CB AT DDTS | 38895.2937 | 38987.6861 | REPDAILY | [12 empty] | 0
_1010113838895.2972222222 | 10101138 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT WMTS | 38895.2972 | 38895.6257 | DAILY | [12 empty] | 0
_1010242938895.2986111111 | 10102429 |  | Parent | FALSE | B5 TRANS NO.3 BUS 220KV CB AT TTS | 38895.2986 | 38895.6278 | DAILY | [12 empty] | 0
_1024187038895.3034722222 | 10241870 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT MLTS | 38895.3035 | 38895.7319 | REPDAILY | 00022778 | SPIMAINT | OUT W/O For SYTS No2 Line Side ROI Repair Work | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058A338895.3152777778 | X32058A3 |  | Parent | FALSE | EX - NO.1 AUX TRANS AT MTS | 38895.3153 | 38895.6743 | DAILY | 00004556 | SPICAPX | De commission No 1 Aux Transformer | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Other Transformers | Eastern | 22 |  |  |  | 0
_1024238138895.7243055556 | 10242381 |  | Parent | FALSE | NO.4 GEN TRANS NO.2 BUS 220KV CB AT HWPS | 38895.7243 | 38897.1736 | CONT | [12 empty] | 0
_X43258A138896.2972222222 | X43258A1 |  | Parent | TRUE | NO.2 220KV BUS-CAPBK EXTENSION AT RCTS | 38896.2972 | 38896.7917 | DAILY | 00016916 | SPICAPX | Out W/O No 2 220 Bus in bays A&B & HOTS L tie bus | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258A438896.2972222222 | X43258A4 | X43258A1 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RCTS | 38896.2972 | 38896.7917 | DAILY | 00360383 | SPICAPX | Out W/O Rebate calc for No 2 220kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258A538896.2972222222 | X43258A5 | X43258A1 | Child | FALSE | KGTS 220KV LINE AT RCTS | 38896.2972 | 38896.7917 | DAILY | 00016959 | SPICAPX | Out W/O Rebate calc for No 2 220kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258A638896.2972222222 | X43258A6 | X43258A1 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 38896.2972 | 38896.7917 | DAILY | 00337584 | SPICAPX | Out W/O Perf calc for No 2 220kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258A738896.2972222222 | X43258A7 | X43258A1 | Child | FALSE | BSS 220KV LINE AT RCTS | 38896.2972 | 38896.7917 | DAILY | 00016966 | SPICAPX | Out W/O Rebate calc for No 2 220kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010243038896.3020833333 | 10102430 |  | Parent | FALSE | B5 TRANS NO.3 BUS 66KV CB AT TTS | 38896.3021 | 38896.6215 | DAILY | [12 empty] | 0
_1024238638896.3965277778 | 10242386 |  | Parent | TRUE | EX - B3 TRANS 220KV CB AT GTS | 38896.3965 | 38896.6944 | DAILY | [12 empty] | 0
_1024238838896.3965277778 | 10242388 | 10242386 | Child | FALSE | B3 220/66KV TRANS AT GTS | 38896.3965 | 38896.6944 | DAILY | 00002829 | SPIMAINT | Perf calc W/O No3 Trans for 220 CB air leak repair | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X4C458A538897 | X4C458A5 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38897 | 38897.7537 | REPDAILY | [12 empty] | 0
_1010166538897.2861111111 | 10101665 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 38897.2861 | 38897.7375 | REPDAILY | 00002830 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024182038897.2916666667 | 10241820 |  | Parent | FALSE | EX - 2-3 66KV BUS TIE CB AT KTS | 38897.2917 | 38897.6319 | DAILY | [12 empty] | 0
_1010243138897.2916666667 | 10102431 |  | Parent | FALSE | B5 TRANS NO.1 BUS 66KV CB AT TTS | 38897.2917 | 38897.6417 | DAILY | [12 empty] | 0
_X43458D638897.2916666667 | X43458D6 |  | Parent | FALSE | EX - DDTS NO.1 220KV LINE AT MBTS | 38897.2917 | 38897.7549 | DAILY | 00011748 | SPICAPX | Out W/O DDTS No1 line, prox erecting Fut B1rack | SPIPOWER | X434 | X434 - (MBTS) TRANSFORMER REPLACEMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258B338897.3159722222 | X43258B3 |  | Parent | FALSE | KGTS 220KV LINE AT RCTS | 38897.316 | 38897.5736 | DAILY | 00016959 | SPICAPX | Out W/O KGTS LINE & Tie Bus Line side isol | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024238938897.3958333333 | 10242389 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 38897.3958 | 38897.4194 | DAILY | [12 empty] | 0
_1024225538898.2715277778 | 10242255 | X43258B2 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 38898.2715 | 38898.5993 | DAILY | 00337581 | SPICAPX | Out W/O Perf calc for No 1 220kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258B038898.2715277778 | X43258B0 |  | Parent | TRUE | EX - NO.1 220KV BUS AT RCTS | 38898.2715 | 38898.5993 | DAILY | 00016901 | SPICAPX | Out W/O No 1 220kV Bus & KGTS LINE Tie Bus | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258B138898.2715277778 | X43258B1 | X43258B0 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 38898.2715 | 38898.5993 | DAILY | 00337581 | SPICAPX | Out W/O Perf calc for No 1 220kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258B238898.2715277778 | X43258B2 | X43258B0 | Child | TRUE | HOTS 220KV LINE AT RCTS | 38898.2715 | 38898.5993 | DAILY | 00016954 | SPICAPX | Out W/O Rebate calc for No 1 220kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010113738898.3638888889 | 10101137 |  | Parent | FALSE | B1 TRANS 66KV CB AT WMTS | 38898.3639 | 38898.6215 | DAILY | [12 empty] | 0
_1024230438898.4618055556 | 10242304 |  | Parent | TRUE | L2 TRANS 22KV CB AT RWTS | 38898.4618 | 38898.6549 | DAILY | [12 empty] | 0
_1024230538898.4618055556 | 10242305 | 10242304 | Child | FALSE | L2 220/22KV TRANS BANK AT RWTS | 38898.4618 | 38898.6549 | DAILY | 00007447 | SPIMAINT | Avail plant Replace faulty Auxilary switch on CB | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024016438899.2847222222 | 10240164 |  | Parent | FALSE | B3 220/66KV TRANS AT HTS | 38899.2847 | 38900.7354 | CONT | 00004447 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area(W) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z500581038901.2805555556 | Z5005810 |  | Parent | FALSE | YPS NO.8 220KV LINE AT ROTS | 38901.2806 | 38912.6799 | CONT | 00024015 | VEN_AUG | YPS NO.8 220KV LINE &MTS3L& CB's to replace isol | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024334438901.28125 | 10243344 |  | Parent | FALSE | MTS NO.3 220KV LINE AT ROTS | 38901.2812 | 38905.5979 | CONT | 00023099 | VEN_AUG | Line out for proximity- Z500 | SPIPOWER |  | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024021738901.3006944444 | 10240217 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 38901.3007 | 38901.6764 | REPDAILY | 00002829 | SPIMAINT | Out W/O No3 Trans for its 66kV & 220kV CB O-H | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010312638901.3159722222 | 10103126 |  | Parent | FALSE | B3 220/66KV TRANS AT SHTS | 38901.316 | 38901.6792 | REPDAILY | 00000842 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024254138901.3215277778 | 10242541 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 38901.3215 | 38902.6042 | CONT | 00112417 | FAULT | Pending repairs to No 3 220 kV Cap Bank after auto | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024255038901.5472222222 | 10242550 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 38901.5472 | 38901.7056 | DAILY | 00351939 | SPIMAINT | Investigate possible faulty CB CT or cable | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024331338901.5472222222 | 10243313 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 38901.5472 | 38901.7056 | DAILY | 00351939 | FORCED | DDTS - No 1 220 kV Cap Bank Not Available | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024255238901.8402777778 | 10242552 |  | Parent | TRUE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 38901.8403 | 38901.8792 | DAILY | [12 empty] | 0
_1024256038901.8402777778 | 10242560 | 10242552 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 38901.8403 | 38901.8792 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during 275CB de-energ | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024237538902.28125 | 10242375 |  | Parent | FALSE | S045 TTS -KTS 1N220KV | 38902.2812 | 38902.6799 | REPDAILY | [12 empty] | 0
_1010312638902.3041666667 | 10103126 |  | Parent | FALSE | B3 220/66KV TRANS AT SHTS | 38902.3042 | 38902.7028 | REPDAILY | 00000842 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024021738902.3069444444 | 10240217 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 38902.3069 | 38902.6965 | REPDAILY | 00002829 | SPIMAINT | Out W/O No3 Trans for its 66kV & 220kV CB O-H | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024245138902.4131944444 | 10242451 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT SHTS | 38902.4132 | 38902.4618 | DAILY | [12 empty] | 0
_1024245238902.4131944444 | 10242452 | 10242451 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT SHTS | 38902.4132 | 38902.4618 | DAILY | 00350862 | SPIMAINT | Rebate W/O No2A 66kV Cap bank to top up cb gas | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024245338902.4131944444 | 10242453 | 10242451 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT SHTS | 38902.4132 | 38902.4618 | DAILY | 00330829 | SPIMAINT | Rebate W/O No2B 66kV Cap bank to top up 2A cb gas | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z33458F438903.2673611111 | Z33458F4 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 38903.2674 | 38913.2642 | CONT | 00352791 | VEN_AUG | Commisioning work on new No4 Tranformer | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024237538903.2791666667 | 10242375 |  | Parent | FALSE | S045 TTS -KTS 1N220KV | 38903.2792 | 38903.6167 | REPDAILY | [12 empty] | 0
_1024021738903.29375 | 10240217 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 38903.2937 | 38903.7257 | REPDAILY | 00002829 | SPIMAINT | Out W/O No3 Trans for its 66kV & 220kV CB O-H | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010145838903.29375 | 10101458 |  | Parent | FALSE | NO.1 6.6KV/415V S/S TRANS AT FBTS | 38903.2937 | 38904.5625 | DAILY | 00002731 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Other Transformers | Western | 6.6 |  |  |  | 0
_1010344238903.2965277778 | 10103442 |  | Parent | FALSE | VNSC 22KV/415V SUPPLY TRANS AT RTS | 38903.2965 | 38903.5972 | DAILY | 00007334 | SPIMAINT | O/HAUL Transformer without Div Sw (EM) | SPIPOWER |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_1024236738903.3069444444 | 10242367 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT TTS | 38903.3069 | 38903.684 | DAILY | 00001533 | SPIMAINT | invest 2 off fans not working & clean radiators | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X4C458A738903.3208333333 | X4C458A7 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38903.3208 | 38903.6347 | REPDAILY | [12 empty] | 0
_1010404138903.3215277778 | 10104041 |  | Parent | FALSE | B3 TRANS 66KV CB AT SHTS | 38903.3215 | 38903.7285 | DAILY | [12 empty] | 0
_V63158A138903.3701388889 | V63158A1 |  | Parent | FALSE | 1-4 66KV BUS TIE CB AT TTS | 38903.3701 | 38903.6368 | DAILY | [12 empty] | 0
_1024021738904.2958333333 | 10240217 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 38904.2958 | 38904.6521 | REPDAILY | 00002829 | SPIMAINT | Out W/O No3 Trans for its 66kV & 220kV CB O-H | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010167638904.2972222222 | 10101676 |  | Parent | FALSE | NO.1 220KV BUS AT GNTS | 38904.2972 | 38904.7507 | REPDAILY | 00000746 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010357238904.3006944444 | 10103572 |  | Parent | FALSE | B3 TRANS 66KV CB AT RTS | 38904.3007 | 38904.6604 | DAILY | [12 empty] | 0
_1024236538904.3013888889 | 10242365 |  | Parent | FALSE | EX - BLTS 220KV LINE NO.1 BUS CB AT KTS | 38904.3014 | 38904.5854 | DAILY | [12 empty] | 0
_V4S258C738904.3229166667 | V4S258C7 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 38904.3229 | 38904.6667 | CONT | 00001328 | SPIMAINT | install refurbed interrupter to fut f1 tr 500kv cb | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_X2A858J038904.5902777778 | X2A858J0 |  | Parent | FALSE | L3 TRANS 22KV CB AT BTS | 38904.5903 | 38971.5833 | DAILY | [12 empty] | 0
_1010167638905.2923611111 | 10101676 |  | Parent | FALSE | NO.1 220KV BUS AT GNTS | 38905.2924 | 38905.734 | REPDAILY | 00000746 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024203938905.2951388889 | 10242039 |  | Parent | FALSE | S047 TTS -KTS 2 220KV | 38905.2951 | 38905.5104 | DAILY | [12 empty] | 0
_1010345338905.2958333333 | 10103453 |  | Parent | FALSE | 2B-4 220KV BUS TIE CB AT RTS | 38905.2958 | 38905.6771 | DAILY | [12 empty] | 0
_1010191138906.2597222222 | 10101911 |  | Parent | FALSE | NO.1A 220KV BUS AT BLTS | 38906.2597 | 38906.6535 | REPDAILY | 00002642 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_1024261538906.2986111111 | 10242615 |  | Parent | FALSE | B1 220/66KV TRANS AT HTS | 38906.2986 | 38906.5146 | DAILY | 00004445 | SPIMAINT | Inspect B1 Trans Gas Relay (charge to 10242568) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V4S258D438906.3409722222 | V4S258D4 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT SMTS | 38906.341 | 38906.4493 | DAILY | 00012440 | SPIMAINT | dismantle weather protection | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024261638906.5472222222 | 10242616 |  | Parent | FALSE | B2 220/66KV TRANS AT HTS | 38906.5472 | 38906.6417 | DAILY | 00004446 | SPIMAINT | Inspect B2 Trans Gas Relay (charge to 10242569) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024331638906.9527777778 | 10243316 |  | Parent | FALSE | ROTS NO.4 220KV LINE AT RTS | 38906.9528 | 38907.0167 | CONT | 00021338 | FAULT | Trans fault | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024339938906.9527777778 | 10243399 |  | Parent | FALSE | L4 220/22KV TRANS AT RTS | 38906.9528 | 38907.0167 | CONT | 00007333 | FAULT | Trans fault | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024285538906.9527777778 | 10242855 |  | Parent | FALSE | B3 220/66KV TRANS AT RTS | 38906.9528 | 38907.6569 | CONT | 00329288 | FAULT | Trans fault | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010191138907.2625 | 10101911 |  | Parent | FALSE | NO.1A 220KV BUS AT BLTS | 38907.2625 | 38907.6847 | REPDAILY | 00002642 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_X43258B538908.2881944444 | X43258B5 |  | Parent | TRUE | NO.1 66KV BUS AT RCTS | 38908.2882 | 38908.7514 | REPDAILY | 00016976 | SPICAPX | Out W/O 66kV Bus side isol & isulator replacement | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258B738908.2881944444 | X43258B7 | X43258B5 | Child | FALSE | NO.1B 220/66/22KV TRANS AT RCTS | 38908.2882 | 38908.7514 | DAILY | 00016758 | SPICAPX | Out W/O Perf calc for 66kV only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258B838908.2881944444 | X43258B8 | X43258B5 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 38908.2882 | 38908.7514 | DAILY | 00016895 | SPICAPX | Out W/O Perf calc for No 1 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258B938908.2881944444 | X43258B9 | X43258B5 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 38908.2882 | 38908.7514 | DAILY | 00359891 | SPICAPX | Out W/O Perf calc for No 1 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024331738908.6027777778 | 10243317 |  | Parent | FALSE | SYN/COND AT BLTS | 38908.6028 | 38908.6562 | DAILY | 00002547 | FAULT | Protection trip of synchronous condenser | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024289838909.1784722222 | 10242898 |  | Parent | FALSE | 220KV SHUNT REACTOR CB AT MLTS | 38909.1785 | 38910.384 | CONT | [12 empty] | 0
_1010237638909.2847222222 | 10102376 |  | Parent | FALSE | SYN/COND AT TSTS | 38909.2847 | 38912.6937 | CONT | 00007626 | SPIMAINT | 3 Monthly O/HAUL - TSTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258B538909.2895833333 | X43258B5 |  | Parent | TRUE | NO.1 66KV BUS AT RCTS | 38909.2896 | 38909.7583 | REPDAILY | 00016976 | SPICAPX | Out W/O 66kV Bus side isol & isulator replacement | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258B738909.2895833333 | X43258B7 | X43258B5 | Child | FALSE | NO.1B 220/66/22KV TRANS AT RCTS | 38909.2896 | 38909.7583 | DAILY | 00016758 | SPICAPX | Out W/O Perf calc for 66kV only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258B838909.2895833333 | X43258B8 | X43258B5 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 38909.2896 | 38909.7583 | DAILY | 00016895 | SPICAPX | Out W/O Perf calc for No 1 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258B938909.2895833333 | X43258B9 | X43258B5 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 38909.2896 | 38909.7583 | DAILY | 00359891 | SPICAPX | Out W/O Perf calc for No 1 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010112938909.2916666667 | 10101129 |  | Parent | FALSE | 2-3 22KV BUS TIE CB AT WMTS | 38909.2917 | 38909.6208 | DAILY | [12 empty] | 0
_1024226138909.3027777778 | 10242261 | X41258A9 | Child | FALSE | GNTS NO.3 220KV LINE AT SHTS | 38909.3028 | 38909.625 | DAILY | 00352426 | SPICAPX | Rebate W/O GNTS-SHTS 3L during No2 220 Bus outage | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024226238909.3027777778 | 10242262 | X41258A9 | Child | FALSE | B2 220/66KV TRANS AT SHTS | 38909.3028 | 38909.625 | DAILY | 00000841 | SPICAPX | Perf calc W/O No2 Trans during No2 220 Bus outage | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X41258A938909.3027777778 | X41258A9 |  | Parent | TRUE | EX - NO.2 220KV BUS AT SHTS | 38909.3028 | 38909.625 | DAILY | 00000846 | SPICAPX | Out W/O No2 220kV Bus. Disconnect bay C | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X4C458A238909.3222222222 | X4C458A2 |  | Parent | FALSE | EX - HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 38909.3222 | 38932.4896 | CONT | [12 empty] | 0
_1010449238909.3638888889 | 10104492 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK CB AT DDTS | 38909.3639 | 38911.6292 | CONT | [12 empty] | 0
_1024331838909.4902777778 | 10243318 |  | Parent | FALSE | RTS 220KV LINE AT BTS | 38909.4903 | 38909.6354 | DAILY | 00015960 | FORCED | RTS-BTS Cable and L4 Transfo | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024331938909.4902777778 | 10243319 |  | Parent | FALSE | L1 220/22KV TRANS AT BTS | 38909.4903 | 38909.6354 | DAILY | 00360728 | FORCED | RTS-BTS Cable and L4 Transfo | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024332138909.6208333333 | 10243321 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 38909.6208 | 38911.5757 | CONT | 00017270 | FAULT | Capacitor - Cable Broken | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258B538910.2847222222 | X43258B5 |  | Parent | TRUE | NO.1 66KV BUS AT RCTS | 38910.2847 | 38910.7701 | REPDAILY | 00016976 | SPICAPX | Out W/O 66kV Bus side isol & isulator replacement | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258B738910.2847222222 | X43258B7 | X43258B5 | Child | FALSE | NO.1B 220/66/22KV TRANS AT RCTS | 38910.2847 | 38910.7701 | DAILY | 00016758 | SPICAPX | Out W/O Perf calc for 66kV only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258B838910.2847222222 | X43258B8 | X43258B5 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 38910.2847 | 38910.7701 | DAILY | 00016895 | SPICAPX | Out W/O Perf calc for No 1 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258B938910.2847222222 | X43258B9 | X43258B5 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 38910.2847 | 38910.7701 | DAILY | 00359891 | SPICAPX | Out W/O Perf calc for No 1 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1008878738910.2951388889 | 10088787 |  | Parent | FALSE | EX - NO.1 2.2KV/415V S/S TRANS AT BTS | 38910.2951 | 38910.7125 | DAILY | 00000937 | SPIMAINT | O/HAUL Transformer without Div Sw | SPIPOWER |  |  | Other Transformers | Western | 2.2 |  |  |  | 0
_X41258B038910.2979166667 | X41258B0 |  | Parent | FALSE | EX - GNTS NO.1 220KV LINE AT SHTS | 38910.2979 | 38912.7611 | CONT | 00000812 | SPICAPX | Out W/O GNTS No1 Line - decomm 2 bus equip | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010113338910.3034722222 | 10101133 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 38910.3035 | 38910.6222 | DAILY | [12 empty] | 0
_1010423438910.3805555556 | 10104234 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 38910.3806 | 38910.7542 | REPDAILY | 00337581 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024289738910.3840277778 | 10242897 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 38910.384 | 38910.6528 | DAILY | 00003011 | FORCED | Out W/O 220kV shunt reactor for CB oil leak repair | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X32058A438911.2527777778 | X32058A4 |  | Parent | FALSE | EX - NO.3 220/22KV TRANS BANK AT MTS | 38911.2528 | 38911.5451 | DAILY | 00026903 | SPICAPX | Proximity for crane work | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258B538911.2618055556 | X43258B5 |  | Parent | TRUE | NO.1 66KV BUS AT RCTS | 38911.2618 | 38911.7743 | REPDAILY | 00016976 | SPICAPX | Out W/O 66kV Bus side isol & isulator replacement | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258B738911.2618055556 | X43258B7 | X43258B5 | Child | FALSE | NO.1B 220/66/22KV TRANS AT RCTS | 38911.2618 | 38911.7743 | DAILY | 00016758 | SPICAPX | Out W/O Perf calc for 66kV only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258B838911.2618055556 | X43258B8 | X43258B5 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 38911.2618 | 38911.7743 | DAILY | 00016895 | SPICAPX | Out W/O Perf calc for No 1 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258B938911.2618055556 | X43258B9 | X43258B5 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 38911.2618 | 38911.7743 | DAILY | 00359891 | SPICAPX | Out W/O Perf calc for No 1 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1008878838911.2916666667 | 10088788 |  | Parent | FALSE | EX - NO.3 S/S TRANS AT BTS | 38911.2917 | 38911.6465 | DAILY | 00000938 | SPIMAINT | O/HAUL Transformer without Div Sw | SPIPOWER |  |  | Other Transformers | Western | 2.2 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1010423438911.3131944445 | 10104234 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 38911.3132 | 38911.7549 | REPDAILY | 00337581 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010145938911.3548611111 | 10101459 |  | Parent | FALSE | NO.2 6.6KV/415V S/S TRANS AT FBTS | 38911.3549 | 38911.6062 | DAILY | 00002732 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Other Transformers | Western | 6.6 |  |  |  | 0
_Z500587038911.3791666667 | Z5005870 |  | Parent | FALSE | EX - SVTS NO.1 LINE/YPS NO.8 LINE CB AT ROTS | 38911.3792 | 38920.2667 | CONT | [12 empty] | 0
_X32058A638911.5388888889 | X32058A6 |  | Parent | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 38911.5389 | 38911.7167 | DAILY | 00026900 | SPICAPX | Proximity for crane work B3 Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024291038911.7222222222 | 10242910 |  | Parent | FALSE | NO.1 GEN 220/16.5KV TRANS AT HWPS | 38911.7222 | 38914.8694 | CONT | 00009642 | GENCO | Power Station Requirements | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1024263238912.2527777778 | 10242632 | X32058A9 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 38912.2528 | 38912.7347 | DAILY | 00026900 | SPICAPX | Proximity for crane work B3 & ROTS No 3 Line | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058A738912.2527777778 | X32058A7 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 38912.2528 | 38912.7347 | DAILY | 00004569 | SPICAPX | Remove OOS equipment from No 3 66 kv Bus | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058A938912.2527777778 | X32058A9 | X32058A7 | Child | TRUE | EX - NO.3 220/66KV TRANS BANK AT MTS | 38912.2528 | 38912.7347 | DAILY | 00026900 | SPICAPX | Avail plant outage No3 66 kv Bus | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258B538912.2625 | X43258B5 |  | Parent | TRUE | NO.1 66KV BUS AT RCTS | 38912.2625 | 38912.7799 | REPDAILY | 00016976 | SPICAPX | Out W/O 66kV Bus side isol & isulator replacement | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258B738912.2625 | X43258B7 | X43258B5 | Child | FALSE | NO.1B 220/66/22KV TRANS AT RCTS | 38912.2625 | 38912.7799 | DAILY | 00016758 | SPICAPX | Out W/O Perf calc for 66kV only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258B838912.2625 | X43258B8 | X43258B5 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 38912.2625 | 38912.7799 | DAILY | 00016895 | SPICAPX | Out W/O Perf calc for No 1 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258B938912.2625 | X43258B9 | X43258B5 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 38912.2625 | 38912.7799 | DAILY | 00359891 | SPICAPX | Out W/O Perf calc for No 1 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010423438912.3470486111 | 10104234 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 38912.347 | 38912.7792 | REPDAILY | 00337581 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010113138912.4256944444 | 10101131 |  | Parent | FALSE | EX - NO.1 22KV/415V S/S TRANS AT WMTS | 38912.4257 | 38912.5792 | DAILY | 00003238 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1024292438912.4326388889 | 10242924 |  | Parent | FALSE | EX - MWTS NO.2 220KV LINE NO.1 BUS CB AT JLTS | 38912.4326 | 38912.4417 | DAILY | [12 empty] | 0
_Z33458F038913.2611111111 | Z33458F0 |  | Parent | TRUE | NO.3 220KV BUS AT SVTS | 38913.2611 | 38915.5931 | CONT | 00004858 | VEN_AUG | Commission No 4 tran protection (see long descript | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z33458F138913.2611111111 | Z33458F1 | Z33458F0 | Child | FALSE | B3 220/66KV TRANS AT SVTS | 38913.2611 | 38915.5931 | CONT | 00004851 | VEN_AUG | Avail of plant commision B4 tran prot | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X51358A038913.2805555556 | X51358A0 |  | Parent | FALSE | EX - 66/22KV TIE TRANS AT BLTS | 38913.2806 | 38937.6389 | CONT | 00002623 | SPICAPX | dismantle & remove 66kv rack structure | SPIPOWER | X513 | X513 - (BLTS) REPLACE 66/22KV TIE TRANSFORMER | Connection Transformers | Western | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010340738913.3145833333 | 10103407 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK CB AT RCTS | 38913.3146 | 38913.6965 | DAILY | [12 empty] | 0
_V63158A338914.2118055556 | V63158A3 |  | Parent | FALSE | O.O.S BAY L 66KV FDR CB AT TTS (WAS DRN) | 38914.2118 | 38914.6708 | DAILY | [12 empty] | 0
_X38458C938914.3541666667 | X38458C9 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38914.3542 | 38914.675 | DAILY | 00023231 | SPICAPX | Out W/O Steel work on Fut B1 gantry and buswork | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024316538914.4520833333 | 10243165 |  | Parent | FALSE | HWTS NO.3 500KV LINE AT LYPS | 38914.4521 | 38914.4729 | DAILY | 00016088 | FORCED | HWTS No 3 Line stranded by outage to top up SF6 | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024295438914.5875 | 10242954 |  | Parent | FALSE | NO.8 GEN TRANS 220KV CB AT HWPS | 38914.5875 | 38927.0729 | CONT | [12 empty] | 0
_V63158A438914.6701388889 | V63158A4 |  | Parent | FALSE | O.O.S BAY L 66KV FDR CB AT TTS (WAS DRN) | 38914.6701 | 38921.5007 | CONT | [12 empty] | 0
_X43258B638915.2694444444 | X43258B6 |  | Parent | TRUE | NO.2 66KV BUS AT RCTS | 38915.2694 | 38915.7722 | REPDAILY | 00016977 | SPICAPX | Out W/O 66kV Bus side isol & insulator replacement | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258C038915.2694444444 | X43258C0 | X43258B6 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 38915.2694 | 38915.7722 | DAILY | 00337584 | SPICAPX | Out W/O 66kV Perf calc for 66kV only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258C138915.2694444444 | X43258C1 | X43258B6 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 38915.2694 | 38915.7722 | DAILY | 00016897 | SPICAPX | Out W/O Perf calc for No 2 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C238915.2694444444 | X43258C2 | X43258B6 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 38915.2694 | 38915.7722 | DAILY | 00359892 | SPICAPX | Out W/O Perf calc for No 2 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C338915.2694444444 | X43258C3 | X43258B6 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 38915.2694 | 38915.7722 | DAILY | 00357254 | SPICAPX | Out W/O Perf calc for No 2 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C438915.2694444444 | X43258C4 | X43258B6 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 38915.2694 | 38915.7722 | DAILY | 00361128 | SPICAPX | Out W/O Perf calc for 66kV outage only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1010192738915.2805555556 | 10101927 |  | Parent | FALSE | SYN/COND AT BLTS | 38915.2806 | 38919.6153 | CONT | 00002547 | SPIMAINT | 12 monthly O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024238238915.3090277778 | 10242382 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 38915.309 | 38916.6104 | CONT | 00337579 | SPIMAINT | Replace C.T on SMTS 1 L / No 3 Main tran CB | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X38458D038915.3770833333 | X38458D0 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38915.3771 | 38915.7569 | REPDAILY | 00023231 | SPICAPX | Out W/O Remove buswork install temp conductors | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010236638915.4708333333 | 10102366 |  | Parent | FALSE | 2-4 66KV BUS TIE CB AT TSTS | 38915.4708 | 38915.6625 | DAILY | [12 empty] | 0
_X43258B638916.2590277778 | X43258B6 |  | Parent | TRUE | NO.2 66KV BUS AT RCTS | 38916.259 | 38916.766 | REPDAILY | 00016977 | SPICAPX | Out W/O 66kV Bus side isol & insulator replacement | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258C038916.2590277778 | X43258C0 | X43258B6 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 38916.259 | 38916.766 | DAILY | 00337584 | SPICAPX | Out W/O 66kV Perf calc for 66kV only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258C138916.2590277778 | X43258C1 | X43258B6 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 38916.259 | 38916.766 | DAILY | 00016897 | SPICAPX | Out W/O Perf calc for No 2 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C238916.2590277778 | X43258C2 | X43258B6 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 38916.259 | 38916.766 | DAILY | 00359892 | SPICAPX | Out W/O Perf calc for No 2 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C338916.2590277778 | X43258C3 | X43258B6 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 38916.259 | 38916.766 | DAILY | 00357254 | SPICAPX | Out W/O Perf calc for No 2 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C438916.2590277778 | X43258C4 | X43258B6 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 38916.259 | 38916.766 | DAILY | 00361128 | SPICAPX | Out W/O Perf calc for 66kV outage only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1010236438916.2965277778 | 10102364 |  | Parent | FALSE | SYN/COND TRANS NO.1 BUS 66KV CB AT TSTS | 38916.2965 | 38916.5618 | DAILY | [12 empty] | 0
_X46158F138916.3125 | X46158F1 |  | Parent | FALSE | EX - 1-2 66KV BUS TIE CB AT BATS | 38916.3125 | 38916.684 | DAILY | [12 empty] | 0
_X38458D038916.3243055556 | X38458D0 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38916.3243 | 38916.5861 | REPDAILY | 00023231 | SPICAPX | Out W/O Remove buswork install temp conductors | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X34458F538916.3819444444 | X34458F5 |  | Parent | TRUE | NO.1 66KV BUS AT GNTS | 38916.3819 | 38916.5729 | DAILY | 00000748 | SPICAPX | Out W/O No1 66kV Bus VT de-energ- NEMMCO cutover | SPIPOWER | X344 | X344 - NEM METERING UPGRADE - STAGE 3 | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X34458F738916.3819444444 | X34458F7 | X34458F5 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT GNTS | 38916.3819 | 38916.5729 | DAILY | 00329962 | SPICAPX | Rebate W/O No1 Cap bank during No1 66 Bus deenerg | SPIPOWER | X344 | X344 - NEM METERING UPGRADE - STAGE 3 | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X34458F838916.3819444444 | X34458F8 | X34458F5 | Child | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 38916.3819 | 38916.5729 | DAILY | 00329970 | SPICAPX | Perf calc W/O #1Trans during No1 66 Bus deenerg | SPIPOWER | X344 | X344 - NEM METERING UPGRADE - STAGE 3 | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010236538916.5625 | 10102365 |  | Parent | FALSE | SYN/COND TRANS NO.2 BUS 66KV CB AT TSTS | 38916.5625 | 38916.6361 | DAILY | [12 empty] | 0
_X34458F638916.5833333333 | X34458F6 |  | Parent | TRUE | NO.2 66KV BUS AT GNTS | 38916.5833 | 38916.6715 | REPDAILY | 00000749 | SPICAPX | Out W/O No2 66kV Bus VT de-energ- NEMMCO cutover | SPIPOWER | X344 | X344 - NEM METERING UPGRADE - STAGE 3 | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X34458F938916.5833333333 | X34458F9 | X34458F6 | Child | FALSE | NO.2 66KV BUS AT GNTS | 38916.5833 | 38916.6715 | DAILY | 00000749 | SPICAPX | Perf calc W/O #2 Trans during No2 66 bus deenerg | SPIPOWER | X344 | X344 - NEM METERING UPGRADE - STAGE 3 | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258B638917.2631944444 | X43258B6 |  | Parent | TRUE | NO.2 66KV BUS AT RCTS | 38917.2632 | 38917.7722 | REPDAILY | 00016977 | SPICAPX | Out W/O 66kV Bus side isol & insulator replacement | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258C038917.2631944444 | X43258C0 | X43258B6 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 38917.2632 | 38917.7722 | DAILY | 00337584 | SPICAPX | Out W/O 66kV Perf calc for 66kV only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258C138917.2631944444 | X43258C1 | X43258B6 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 38917.2632 | 38917.7722 | DAILY | 00016897 | SPICAPX | Out W/O Perf calc for No 2 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C238917.2631944444 | X43258C2 | X43258B6 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 38917.2632 | 38917.7722 | DAILY | 00359892 | SPICAPX | Out W/O Perf calc for No 2 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C338917.2631944444 | X43258C3 | X43258B6 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 38917.2632 | 38917.7722 | DAILY | 00357254 | SPICAPX | Out W/O Perf calc for No 2 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C438917.2631944444 | X43258C4 | X43258B6 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 38917.2632 | 38917.7722 | DAILY | 00361128 | SPICAPX | Out W/O Perf calc for 66kV outage only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1023697138917.2777777778 | 10236971 |  | Parent | TRUE | EX - NO.2 MAIN TRANS 500KV CB AT HWTS | 38917.2778 | 38917.584 | DAILY | [12 empty] | 0
_1024301138917.2777777778 | 10243011 | 10236971 | Child | FALSE | A2 515/230KV TRANS BANK AT HWTS | 38917.2778 | 38917.584 | DAILY | 00337572 | SPIMAINT | REPAIR CB AIR LEAK. | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1010247638917.2951388889 | 10102476 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT TSTS | 38917.2951 | 38917.6674 | DAILY | 00351937 | SPIMAINT | O/Haul - Cap Bank & E/Sw (EM) & CB | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X43258B638918.2597222222 | X43258B6 |  | Parent | TRUE | NO.2 66KV BUS AT RCTS | 38918.2597 | 38918.7729 | REPDAILY | 00016977 | SPICAPX | Out W/O 66kV Bus side isol & insulator replacement | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258C038918.2597222222 | X43258C0 | X43258B6 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 38918.2597 | 38918.7729 | DAILY | 00337584 | SPICAPX | Out W/O 66kV Perf calc for 66kV only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258C138918.2597222222 | X43258C1 | X43258B6 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 38918.2597 | 38918.7729 | DAILY | 00016897 | SPICAPX | Out W/O Perf calc for No 2 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C238918.2597222222 | X43258C2 | X43258B6 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 38918.2597 | 38918.7729 | DAILY | 00359892 | SPICAPX | Out W/O Perf calc for No 2 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C338918.2597222222 | X43258C3 | X43258B6 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 38918.2597 | 38918.7729 | DAILY | 00357254 | SPICAPX | Out W/O Perf calc for No 2 66kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C438918.2597222222 | X43258C4 | X43258B6 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 38918.2597 | 38918.7729 | DAILY | 00361128 | SPICAPX | Out W/O Perf calc for 66kV outage only | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X46158F238918.2694444444 | X46158F2 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 38918.2694 | 38918.7785 | DAILY | 00006554 | SPICAPX | Out W/O No1 Trans install 66kV neutral CT's etc. | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z33458F638918.3666666667 | Z33458F6 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 38918.3667 | 38918.6472 | REPDAILY | 00352791 | VEN_AUG | No4 Tranformer isol daily for work on OLTC | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158F338919.2673611111 | X46158F3 |  | Parent | FALSE | B2 220/66KV TRANS AT BATS | 38919.2674 | 38919.7743 | DAILY | 00006555 | SPICAPX | Out W/O No2 Trans install 66kV neutral CT's etc. | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024294238919.2979166667 | 10242942 |  | Parent | FALSE | B3 220/66KV TRANS AT RTS | 38919.2979 | 38919.6681 | DAILY | 00329288 | SPIMAINT | SFT for injections tests on leakage prot | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A858K238919.35 | X2A858K2 |  | Parent | FALSE | L2 220/22KV TRANS AT BTS | 38919.35 | 38929.2569 | CONT | 00360870 | SPICAPX | connect l2 transformer | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X4C458A838919.3611111111 | X4C458A8 |  | Parent | FALSE | HWPS NO.4 220KV LINE AT JLTS | 38919.3611 | 38919.6493 | DAILY | 00015940 | SPICAPX | HWPS 4 LINE / MWTS #1 CB LINE CONNECTIONS | SPIPOWER | X4C4 | X4C4 - (JLTS) REPLACE 3AS2 220KV CBS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024306738919.5027777778 | 10243067 |  | Parent | TRUE | WMTS NO.2 220KV LINE CB AT FBTS | 38919.5028 | 38919.509 | DAILY | [12 empty] | 0
_1024306938919.5027777778 | 10243069 | 10243067 | Child | FALSE | WMTS NO.2 220KV LINE AT FBTS | 38919.5028 | 38919.509 | DAILY | 00017157 | SPIMAINT | top up sf6 gas | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1024307638919.95625 | 10243076 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 38919.9563 | 38929.2299 | CONT | [12 empty] | 0
_Z50058B038920.2736111111 | Z50058B0 |  | Parent | FALSE | SVTS NO.1 220KV LINE AT ROTS | 38920.2736 | 38920.6653 | CONT | 00350027 | VEN_AUG | Remove Line connection SVTS NO.1 L/YPS NO.8 LCB | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024308738920.7840277778 | 10243087 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 38920.784 | 38923.8194 | CONT | 00016423 | GENCO | Power Station Requirements | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V4D958A338921.2979166667 | V4D958A3 |  | Parent | FALSE | KTS -WMTS 2 220KV WT | 38921.2979 | 38921.6847 | DAILY | 00022719 | SPICAPX | suspension plate change | SPIPOWER | V4D9 | V4D9 - (KTS-WMTS) REPLACE WORN ATTACHMENT PLATES T10 & T12 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V63158A538921.3868055556 | V63158A5 |  | Parent | FALSE | O.O.S BAY L 66KV FDR AT TTS (WAS DRN) | 38921.3868 | 38921.6188 | DAILY | 00015493 | SPIMAINT | remove temp connections | SPIPOWER | V631 | V631 - (TTS) REPLACE KLK-MDI-RUBA FDR 66KV POST CTS | Circuits | Western | 66 |  |  |  | 0
_1024308538921.4111111111 | 10243085 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 38921.4111 | 38921.4806 | DAILY | 00003104 | SPIMAINT | Cap Bank Auto | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V4S258C938921.6041666667 | V4S258C9 |  | Parent | FALSE | FUTURE F1 TRANS 500KV CB AT SMTS | 38921.6042 | 38948.5639 | CONT | [12 empty] | 0
_X43258C538922.28125 | X43258C5 |  | Parent | TRUE | EX - NO.1 220KV BUS AT RCTS | 38922.2812 | 38922.7278 | REPDAILY | 00016901 | SPICAPX | Out W/O Replace No 1 220kV bus support insulators | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258C738922.28125 | X43258C7 | X43258C5 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT RCTS | 38922.2812 | 38922.7278 | DAILY | 00360382 | SPICAPX | Out W/O Perf calc for No 1 220kV CAP BANK | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258C838922.28125 | X43258C8 | X43258C5 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 38922.2812 | 38922.7278 | DAILY | 00337581 | SPICAPX | Out W/O Perf calc for No 1TRANSFORMER 220kV | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258C938922.28125 | X43258C9 | X43258C5 | Child | FALSE | HOTS 220KV LINE AT RCTS | 38922.2812 | 38922.7278 | DAILY | 00016954 | SPICAPX | Out W/O Rebate calc for HOTS LINE | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009894338923.2680555556 | 10098943 |  | Parent | FALSE | SYN/COND AT FBTS | 38923.2681 | 38925.2125 | CONT | 00002697 | SPIMAINT | 3 Monthly O/HAUL - FBTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258C538923.2722222222 | X43258C5 |  | Parent | TRUE | EX - NO.1 220KV BUS AT RCTS | 38923.2722 | 38923.7125 | REPDAILY | 00016901 | SPICAPX | Out W/O Replace No 1 220kV bus support insulators | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258C738923.2722222222 | X43258C7 | X43258C5 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT RCTS | 38923.2722 | 38923.7125 | DAILY | 00360382 | SPICAPX | Out W/O Perf calc for No 1 220kV CAP BANK | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258C838923.2722222222 | X43258C8 | X43258C5 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 38923.2722 | 38923.7125 | DAILY | 00337581 | SPICAPX | Out W/O Perf calc for No 1TRANSFORMER 220kV | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258C938923.2722222222 | X43258C9 | X43258C5 | Child | FALSE | HOTS 220KV LINE AT RCTS | 38923.2722 | 38923.7125 | DAILY | 00016954 | SPICAPX | Out W/O Rebate calc for HOTS LINE | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010341738923.3444444445 | 10103417 |  | Parent | FALSE | NO.1 66KV REACTOR AT RCTS | 38923.3444 | 38923.6667 | DAILY | 00016895 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024300838923.3527777778 | 10243008 |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 38923.3528 | 38923.4875 | DAILY | [12 empty] | 0
_1024300738923.5381944444 | 10243007 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT GTS | 38923.5382 | 38923.5687 | DAILY | [12 empty] | 0
_1024304438924.2861111111 | 10243044 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 38924.2861 | 38924.6076 | DAILY | [12 empty] | 0
_1024298738924.5013888889 | 10242987 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 38924.5014 | 38924.6931 | DAILY | 00002862 | SPIMAINT | Replace B Ph Tertiary VT | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024320838924.6555555556 | 10243208 |  | Parent | FALSE | HWTS NO.3 500KV LINE AT LYPS | 38924.6556 | 38924.6771 | DAILY | 00016088 | FORCED | Low SF6 on W phase on HWTS No3 Line No4 Bus CB | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024324138924.7395833333 | 10243241 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 38924.7396 | 38925.4 | CONT | [12 empty] | 0
_1024332238924.75 | 10243322 |  | Parent | FALSE | SYN/COND AT TSTS | 38924.75 | 38930.5 | CONT | 00007626 | FORCED | S/C Bearing Temp alarm Oil Pump Failure | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010214938925.3444444445 | 10102149 |  | Parent | FALSE | EX - GTS NO.1 220KV LINE NO.3 BUS CB AT KTS | 38925.3444 | 38926.6431 | CONT | [12 empty] | 0
_1024332338925.59375 | 10243323 | X38458D3 | Child | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 38925.5938 | 38925.6382 | DAILY | 00003104 | SPICAPX | Out W/O Isolation for access of concrete truck | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X38458D338925.59375 | X38458D3 |  | Parent | TRUE | EX - 66KV CAPACITOR BANK CB AT TGTS | 38925.5938 | 38925.6382 | DAILY | [12 empty] | 0
_Z33458F638925.7473726852 | Z33458F6 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 38925.7474 | 38925.7485 | REPDAILY | 00352791 | VEN_AUG | No4 Tranformer isol daily for work on OLTC | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024314838926.4416666667 | 10243148 |  | Parent | FALSE | AUX TRANS 'C' NO.1 BUS 220KV CB AT YPS | 38926.4417 | 38926.4611 | DAILY | [12 empty] | 0
_1023583838927.2916666667 | 10235838 |  | Parent | FALSE | S006 SMTS-KTS 500KV | 38927.2917 | 38927.6937 | REPDAILY | [12 empty] | 0
_1024332538927.2916666667 | 10243325 |  | Parent | FALSE | SMTS-KTS 500KV WT | 38927.2917 | 38927.6937 | REPDAILY | 00022650 | SPIMAINT | Hot joint | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024329038927.3034722222 | 10243290 |  | Parent | FALSE | NO.1 11/220KV TRANS W/PH AT MPS | 38927.3035 | 38927.5472 | DAILY | 00350226 | SPIMAINT | Top white phase bushing oil level | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024332938928.2569444444 | 10243329 |  | Parent | FALSE | TTS NO.3 220KV LINE AT BTS | 38928.2569 | 38928.6222 | DAILY | 00015959 | SPICAPX | replace droppers | SPIPOWER |  | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858J838928.2569444444 | X2A858J8 |  | Parent | FALSE | 2-3 220KV BUS TIE CB NO.3 BUS SIDE ROI AT BTS | 38928.2569 | 38928.6222 | DAILY | [12 empty] | 0
_1023583838928.2986111111 | 10235838 |  | Parent | FALSE | S006 SMTS-KTS 500KV | 38928.2986 | 38928.6785 | REPDAILY | [12 empty] | 0
_1024332538928.2986111111 | 10243325 |  | Parent | FALSE | SMTS-KTS 500KV WT | 38928.2986 | 38928.6785 | REPDAILY | 00022650 | SPIMAINT | Hot joint | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024332738928.6270833333 | 10243327 |  | Parent | FALSE | TTS NO.1 220KV LINE AT BTS | 38928.6271 | 38928.8569 | DAILY | 00015958 | SPICAPX | replace droppers | SPIPOWER |  | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858J938928.6270833333 | X2A858J9 |  | Parent | FALSE | 1-2 220KV BUS TIE CB NO.1 BUS SIDE ROI AT BTS | 38928.6271 | 38928.8569 | DAILY | [12 empty] | 0
_1024017638929.2930555556 | 10240176 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 38929.2931 | 38933.6111 | CONT | 00007456 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024331538929.5069444444 | 10243315 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 38929.5069 | 38939.3249 | CONT | 00016424 | GENCO | Outage for generator | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010207338930.34375 | 10102073 |  | Parent | FALSE | FIRE HYDRANT SYSTEM AT KTS | 38930.3438 | 38930.6382 | DAILY | [12 empty] | 0
_1024306338930.6472222222 | 10243063 |  | Parent | TRUE | NO.2 330KV BUS AT DDTS | 38930.6472 | 38930.6514 | REPDAILY | 00003979 | SPICAPX | Out W/O Remove old and bring in new 330 CT's | SPIPOWER |  |  | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024337838930.6472222222 | 10243378 | 10243063 | Child | FALSE | NO.2 330KV CAPACITOR BANK AT DDTS | 38930.6472 | 38930.6514 | REPDAILY | 00352093 | SPICAPX | Out W/O Sys perf calc for No 2 330kV bus outage | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_1024337938930.6472222222 | 10243379 | 10243063 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 38930.6472 | 38930.6514 | REPDAILY | 00352121 | SPICAPX | Out W/O Sys perf calc for No 2 330kV bus outage | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1010329538931.2736111111 | 10103295 |  | Parent | FALSE | NO.2 66KV BUS AT RTS | 38931.2736 | 38931.6347 | DAILY | 00022328 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus | SPIPOWER |  |  | Bus | Eastern | 66 |  |  |  | 0
_1023644238931.2895833333 | 10236442 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE NO.1 BUS CB AT KTS | 38931.2896 | 38932.6297 | CONT | [12 empty] | 0
_1010215638931.3541666667 | 10102156 |  | Parent | FALSE | STANDBY DIESEL GENERATOR AT KTS | 38931.3542 | 38932.5708 | REPDAILY | [12 empty] | 0
_X38458D438932.5444444444 | X38458D4 |  | Parent | FALSE | B2 220/66KV TRANS AT TGTS | 38932.5444 | 38932.6111 | DAILY | 00003127 | SPICAPX | Out W/O De-energisation of trans for truck access | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024340138933.48125 | 10243401 |  | Parent | TRUE | MBTS NO.1 220KV LINE CB AT EPSY | 38933.4812 | 38933.6104 | DAILY | [12 empty] | 0
_1024340738933.48125 | 10243407 | 10243401 | Child | FALSE | MBTS-EPS 1 220KV N | 38933.4812 | 38933.6104 | DAILY | 00055380 | SPIMAINT | Rebate W/O MBTS-EPS No1 Line for CB outage at EPSY | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1024358138934.2833333333 | 10243581 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 38934.2833 | 38934.5799 | CONT | [12 empty] | 0
_1024336438934.3138888889 | 10243364 |  | Parent | FALSE | ROTS NO.3 500KV LINE AT HWTS | 38934.3139 | 38934.7354 | REPDAILY | 00016239 | SPIMAINT | Line outage for Lines OMU charge to 10228244 | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X51358A238935.3034722222 | X51358A2 |  | Parent | FALSE | NO.2 66KV BUS AT BLTS | 38935.3035 | 38935.5319 | DAILY | 00002650 | SPICAPX | NO.2 66KV BUS DE-ENERGIZED FOR PROXIMITY | SPIPOWER | X513 | X513 - (BLTS) REPLACE 66/22KV TIE TRANSFORMER | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024359738935.8125 | 10243597 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT BTS | 38935.8125 | 38940.7847 | CONT | [12 empty] | 0
_1024360038935.9319444444 | 10243600 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 38935.9319 | 38936.9326 | CONT | 00356082 | GENCO | For genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258D438936.275 | X43258D4 |  | Parent | TRUE | NO.1 66KV BUS AT RCTS | 38936.275 | 38936.8056 | DAILY | 00016976 | SPICAPX | Out W/O Change insulators and u/slungs No 1 66kV b | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258D638936.275 | X43258D6 | X43258D4 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 38936.275 | 38936.8056 | DAILY | 00016895 | SPICAPX | Out W/O Sys perf calc for No 1 66kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258D738936.275 | X43258D7 | X43258D4 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 38936.275 | 38936.8056 | DAILY | 00359891 | SPICAPX | Out W/O Rebate calc for No 1 66kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258D838936.275 | X43258D8 | X43258D4 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 38936.275 | 38936.8056 | DAILY | 00337581 | SPICAPX | Out W/O Sys perf calc on 66 for No 1 66kV bus out | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024360938936.5833333333 | 10243609 |  | Parent | FALSE | KTS -GTS 2 220KV WY | 38936.5833 | 38936.5924 | DAILY | 00022705 | FORCED | KTS-GTS No 2 Line | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024363938936.9326388889 | 10243639 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 38936.9326 | 38939.8472 | CONT | 00356082 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258D538937.2625 | X43258D5 |  | Parent | TRUE | NO.2 66KV BUS AT RCTS | 38937.2625 | 38937.7569 | DAILY | 00016977 | SPICAPX | Out W/O Replace BT 2 side & trans u/slungs on 2bus | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258D938937.2625 | X43258D9 | X43258D5 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 38937.2625 | 38937.7569 | DAILY | 00359892 | SPICAPX | Out W/O Sys perf calc for No 2 66kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258E038937.2625 | X43258E0 | X43258D5 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 38937.2625 | 38937.7569 | DAILY | 00016897 | SPICAPX | Out W/O Sys perf calc for No 2 66kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258E138937.2625 | X43258E1 | X43258D5 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 38937.2625 | 38937.7569 | DAILY | 00337584 | SPICAPX | Out W/O Sys perf calc for No 2 66kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258E238937.2625 | X43258E2 | X43258D5 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 38937.2625 | 38937.7569 | DAILY | 00357254 | SPICAPX | Out W/O Sys perf calc for No 2 66kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258E338937.2625 | X43258E3 | X43258D5 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 38937.2625 | 38937.7569 | DAILY | 00361128 | SPICAPX | Out W/O Sys perf calc for No 2 66kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_Z52058A338937.3194444444 | Z52058A3 |  | Parent | FALSE | ROTS NO.5 220KV LINE AT YPS | 38937.3194 | 38937.7562 | DAILY | 00016413 | VEN_AUG | Installation of line strain monitors. | SPIPOWER | Z520 | Z520 - (ROTS-YPS,ROTS-HWTS) 220KV LINE WIND MONITORING | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023861538937.3583333333 | 10238615 |  | Parent | FALSE | EX - BLTS 220KV LINE NO.2 BUS CB AT KTS | 38937.3583 | 38937.6535 | DAILY | [12 empty] | 0
_Z54758A138937.36875 | Z54758A1 |  | Parent | FALSE | BETS-FVTS-SHTS 220KV NB | 38937.3688 | 38937.5278 | DAILY | 00026225 | VEN_AUG | Out W/O BETS/FVTS/SHTSline-load meter installation | SPIPOWER | Z547 | Z547 - (BETS-FVTS-SHTS) WIND MONITORING SCHEME | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024410438937.375 | 10244104 | X38458D1 | Child | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 38937.375 | 38937.7083 | REPDAILY | 00003104 | SPICAPX | Out W/O Upgrade insulators on bus & bus tie cb iso | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X38458D138937.375 | X38458D1 |  | Parent | TRUE | EX - NO.1 66KV BUS AT TGTS | 38937.375 | 38937.7083 | REPDAILY | 00003132 | SPICAPX | Out W/O Upgrade insulators on bus & bus tie cb iso | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024369938937.5777777778 | 10243699 |  | Parent | FALSE | EX - NO.3 22KV BUS AT MTS | 38937.5778 | 38937.6347 | DAILY | 00004570 | FAULT | No 3 Bus Trip due to VR Gardiner Fdr 126 dug up | SPIPOWER |  |  | Bus | Eastern | 22 |  |  |  | 0
_1024410238938.1972222222 | 10244102 | X2A858K6 | Child | FALSE | TTS NO.1 220KV LINE AT BTS | 38938.1972 | 38940.7847 | CONT | 00015958 | SPICAPX | No 1 220KV BUS AT BTS | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858K638938.1972222222 | X2A858K6 |  | Parent | TRUE | NO.1 220KV BUS AT BTS | 38938.1972 | 38940.7847 | CONT | 00000942 | SPICAPX | No 1 220KV BUS AT BTS | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Bus | Western | 220 |  |  |  | 0
_V5A458A038938.2722222222 | V5A458A0 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT MLTS | 38938.2722 | 38938.9042 | DAILY | 00022778 | SPIMAINT | Out W/O SYTS-MLTS 2L for CVT replacement at MLTS | SPIPOWER | V5A4 | V5A4 - (MLTS) INVESTIGATE & REPAIR AFTER 500KV CT FAILURE | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z52058A438938.3145833333 | Z52058A4 |  | Parent | FALSE | ROTS NO.6 220KV LINE AT YPS | 38938.3146 | 38938.6458 | DAILY | 00016414 | VEN_AUG | Installation of line strain monitors. | SPIPOWER | Z520 | Z520 - (ROTS-YPS,ROTS-HWTS) 220KV LINE WIND MONITORING | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024410438938.3736111111 | 10244104 | X38458D1 | Child | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 38938.3736 | 38938.7021 | REPDAILY | 00003104 | SPICAPX | Out W/O Upgrade insulators on bus & bus tie cb iso | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X38458D138938.3736111111 | X38458D1 |  | Parent | TRUE | EX - NO.1 66KV BUS AT TGTS | 38938.3736 | 38938.7021 | REPDAILY | 00003132 | SPICAPX | Out W/O Upgrade insulators on bus & bus tie cb iso | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024369438938.3819444444 | 10243694 |  | Parent | FALSE | B3 220/66KV TRANS AT SHTS | 38938.3819 | 38938.6326 | DAILY | 00000842 | SPIMAINT | Out W/O No3 Trans for operator training | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258E438939.25625 | X43258E4 |  | Parent | TRUE | NO.2 220KV BUS-CAPBK EXTENSION AT RCTS | 38939.2562 | 38939.7597 | DAILY | 00016916 | SPICAPX | Out W/O Replace insulators & include BSS line work | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258E538939.25625 | X43258E5 | X43258E4 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RCTS | 38939.2562 | 38939.7597 | DAILY | 00360383 | SPICAPX | Out W/O Sys perf calc for No 2 220kV BUS outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258E638939.25625 | X43258E6 | X43258E4 | Child | FALSE | KGTS 220KV LINE AT RCTS | 38939.2562 | 38939.7597 | DAILY | 00016959 | SPICAPX | Out W/O Rebate calc for No 2 220kV BUS outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258E738939.25625 | X43258E7 | X43258E4 | Child | FALSE | BSS 220KV LINE AT RCTS | 38939.2562 | 38939.7597 | DAILY | 00016966 | SPICAPX | Out W/O Rebate calc for No 2 220kV BUS outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024370138939.2611111111 | 10243701 |  | Parent | FALSE | MLRC 220KV LINE AT RCTS | 38939.2611 | 38939.7583 | DAILY | 00352130 | SPIMAINT | HVS: RCTS-MLRC 220kV Line | SPIPOWER |  |  | Circuits | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 4
_X46158F638939.2833333333 | X46158F6 |  | Parent | TRUE | NO.1 66KV BUS AT BATS | 38939.2833 | 38940.9417 | CONT | 00006560 | SPICAPX | Out W/O No1 66 Bus to Commiss No1 TR Fut 66&220CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158F738939.2833333333 | X46158F7 | X46158F6 | Child | FALSE | B1 220/66KV TRANS AT BATS | 38939.2833 | 38940.9417 | CONT | 00006554 | SPICAPX | Perf calc W/O No1 TR t o Commiss its Fut 66&220CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158F838939.2833333333 | X46158F8 | X46158F6 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 38939.2833 | 38940.9417 | CONT | 00331109 | SPICAPX | Rebate W/O No1 66 Cap bk during No1 66 bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z52058A538939.3041666667 | Z52058A5 |  | Parent | FALSE | ROTS NO.7 220KV LINE AT YPS | 38939.3042 | 38939.6042 | DAILY | 00016415 | VEN_AUG | Installation of line strain monitors. | SPIPOWER | Z520 | Z520 - (ROTS-YPS,ROTS-HWTS) 220KV LINE WIND MONITORING | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V5A458A138939.3361111111 | V5A458A1 |  | Parent | FALSE | HYTS NO.2 500KV LINE AT MLTS | 38939.3361 | 38939.709 | DAILY | 00022754 | SPIMAINT | Out W/O MLTS-HYTS 2L for ROI repair at MLTS | SPIPOWER | V5A4 | V5A4 - (MLTS) INVESTIGATE & REPAIR AFTER 500KV CT FAILURE | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023985638939.3451388889 | 10239856 |  | Parent | FALSE | EX - ATS LINE/A2 TRANS 220KV CB AT KTS | 38939.3451 | 38939.4965 | DAILY | [12 empty] | 0
_1024410438939.3791666667 | 10244104 | X38458D1 | Child | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 38939.3792 | 38939.6917 | REPDAILY | 00003104 | SPICAPX | Out W/O Upgrade insulators on bus & bus tie cb iso | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X38458D138939.3791666667 | X38458D1 |  | Parent | TRUE | EX - NO.1 66KV BUS AT TGTS | 38939.3792 | 38939.6917 | REPDAILY | 00003132 | SPICAPX | Out W/O Upgrade insulators on bus & bus tie cb iso | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024334638939.4972222222 | 10243346 |  | Parent | FALSE | EX - TTS NO.1 220KV LINE NO.2 BUS CB AT KTS | 38939.4972 | 38939.6451 | DAILY | [12 empty] | 0
_1024324738939.5444444444 | 10243247 |  | Parent | FALSE | EX - FVTS/SHTS 220KV LINE NO.1 BUS CB AT BETS | 38939.5444 | 38939.6562 | DAILY | [12 empty] | 0
_X2A858L038940.0317708333 | X2A858L0 |  | Parent | FALSE | L1 220/22KV TRANS AT BTS | 38940.0318 | 38940.7847 | CONT | 00360728 | SPICAPX | L1 TRANSFORMER AT BTS | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024357738940.2916666667 | 10243577 |  | Parent | TRUE | S018 KTS -GTS 2 220KV | 38940.2917 | 38940.6271 | REPDAILY | [12 empty] | 0
_1024410338940.2916666667 | 10244103 | 10243577 | Child | FALSE | KTS -GTS 2 220KV WY | 38940.2917 | 38940.6271 | REPDAILY | 00022705 | SPIMAINT | Insulator replacement program | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49058A538940.2916666667 | X49058A5 |  | Parent | FALSE | H1 TRANS NO.2 BUS 330KV CB AT DDTS | 38940.2917 | 38940.7931 | DAILY | [12 empty] | 0
_1024410438940.3868055556 | 10244104 | X38458D1 | Child | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 38940.3868 | 38940.6562 | REPDAILY | 00003104 | SPICAPX | Out W/O Upgrade insulators on bus & bus tie cb iso | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X38458D138940.3868055556 | X38458D1 |  | Parent | TRUE | EX - NO.1 66KV BUS AT TGTS | 38940.3868 | 38940.6562 | REPDAILY | 00003132 | SPICAPX | Out W/O Upgrade insulators on bus & bus tie cb iso | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024375938940.8743055556 | 10243759 |  | Parent | FALSE | W1 GEN TRANS NO.2 BUS 220KV CB LINE SIDE ISOL AT YPS | 38940.8743 | 38943.3625 | CONT | [12 empty] | 0
_1024375838941.0555555556 | 10243758 |  | Parent | FALSE | HWTS NO.3 500KV LINE CB AT LYPS | 38941.0556 | 38941.0792 | DAILY | [12 empty] | 0
_1024388338941.0555555556 | 10243883 |  | Parent | FALSE | HWTS NO.3 500KV LINE AT LYPS | 38941.0556 | 38941.0792 | DAILY | 00016088 | FORCED | Rebate for CB top up of SF6 | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024417638941.2131944444 | 10244176 | X2A858K7 | Child | FALSE | TTS NO.3 220KV LINE AT BTS | 38941.2132 | 38942.5472 | CONT | 00015959 | SPICAPX | Rebate for work on No 3 220KV BUS AT BTS | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858K738941.2131944444 | X2A858K7 |  | Parent | TRUE | NO.3 220KV BUS AT BTS | 38941.2132 | 38942.5472 | CONT | 00000944 | SPICAPX | No 3 220KV BUS AT BTS | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Bus | Western | 220 |  |  |  | 0
_Z50058B638941.2715277778 | Z50058B6 |  | Parent | FALSE | SVTS NO.1 220KV LINE AT ROTS | 38941.2715 | 38942.6382 | CONT | 00350027 | VEN_AUG | Replace Line connection SVTS NO.1 L/YPS NO.8 LCB | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158F938941.2923611111 | X46158F9 |  | Parent | TRUE | NO.1 220KV BUS AT BATS | 38941.2924 | 38941.8083 | DAILY | 00006558 | SPICAPX | Out W/O No1 220 Bus to Connect Fut 2TR220CB BS ROI | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158G038941.2923611111 | X46158G0 | X46158F9 | Child | FALSE | TGTS 220KV LINE AT BATS | 38941.2924 | 38941.8083 | DAILY | 00012435 | SPICAPX | Rebate W/O TGTS Line during No1 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158G138941.2923611111 | X46158G1 | X46158F9 | Child | FALSE | MLTS NO.2 220KV LINE AT BATS | 38941.2924 | 38941.8083 | DAILY | 00012431 | SPICAPX | Rebate W/O MLTS 2 Line during No1 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158G238941.2923611111 | X46158G2 | X46158F9 | Child | FALSE | B1 220/66KV TRANS AT BATS | 38941.2924 | 38941.8083 | DAILY | 00006554 | SPICAPX | Perf calc W/O No1 Trans for 220 O'head proximity | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024423838941.29375 | 10244238 |  | Parent | FALSE | B2 220/66KV TRANS AT BATS | 38941.2937 | 38941.2965 | DAILY | 00006555 | FAULT | Unexplained out of BATS No2 TRANS | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49058A638941.2972222222 | X49058A6 |  | Parent | FALSE | MSS -DDTS 1 330KV NW | 38941.2972 | 38941.8236 | DAILY | 00060190 | SPICAPX | Out W/O Replace marshalling box & o/h conductor | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458D238941.3555555556 | X38458D2 |  | Parent | FALSE | EX - NO.2 66KV BUS AT TGTS | 38941.3556 | 38941.6465 | REPDAILY | 00003133 | SPICAPX | Out W/O Upgrade insulators No 2 BUS & B/T CB isol | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024377438941.8236111111 | 10243774 |  | Parent | FALSE | NO.2 330KV BUS AT DDTS | 38941.8236 | 38941.8326 | DAILY | 00003979 | FAULT | DDTS No 2 330kV Bus | SPIPOWER |  |  | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024377538941.8236111111 | 10243775 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 38941.8236 | 38941.8326 | DAILY | 00352121 | FAULT | No 2 Trans off due to bus trip | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X46158G338942.29375 | X46158G3 |  | Parent | TRUE | NO.1 220KV BUS AT BATS | 38942.2937 | 38942.7306 | DAILY | 00006558 | SPICAPX | Out W/O No1 220 Bus to Connect Fut 2TR220CB BS ROI | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158G438942.29375 | X46158G4 | X46158G3 | Child | FALSE | B2 220/66KV TRANS AT BATS | 38942.2937 | 38942.7306 | DAILY | 00006555 | SPICAPX | Perf calc W/O No2 Trans for 220 O'head proximity | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158G538942.29375 | X46158G5 | X46158G3 | Child | FALSE | TGTS 220KV LINE AT BATS | 38942.2937 | 38942.7306 | DAILY | 00012435 | SPICAPX | Rebate W/O TGTS Line during No1 220kV BUS outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158G638942.29375 | X46158G6 | X46158G3 | Child | FALSE | MLTS NO.2 220KV LINE AT BATS | 38942.2937 | 38942.7306 | DAILY | 00012431 | SPICAPX | Rebate W/O MLTS 2 Line during No1 220kV BUS outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458D238942.3173611111 | X38458D2 |  | Parent | FALSE | EX - NO.2 66KV BUS AT TGTS | 38942.3174 | 38942.5972 | REPDAILY | 00003133 | SPICAPX | Out W/O Upgrade insulators No 2 BUS & B/T CB isol | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X2A858K838943.2111111111 | X2A858K8 |  | Parent | FALSE | TTS NO.1 220KV LINE AT BTS | 38943.2111 | 38943.8583 | REPDAILY | 00015958 | SPICAPX | TTS NO.1 220KV LINE AT BTS | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024325338943.2701388889 | 10243253 | X46158G7 | Child | FALSE | B2 220/66KV TRANS AT BATS | 38943.2701 | 38944.7708 | CONT | 00006555 | SPICAPX | Perf calc W/O No2 TR to Commiss its Fut 66&220CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024325438943.2701388889 | 10243254 | X46158G7 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 38943.2701 | 38944.7708 | CONT | 00331118 | SPICAPX | Rebate W/O No2 66 Cap bk during No2 66 bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X46158G738943.2701388889 | X46158G7 |  | Parent | TRUE | NO.2 66KV BUS AT BATS | 38943.2701 | 38944.7708 | CONT | 00006561 | SPICAPX | Out W/O No2 66 Bus to Commiss No2 TR Fut 66&220CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058B038943.2784722222 | X32058B0 |  | Parent | FALSE | EX - 1-3 66KV BUS TIE CB AT MTS | 38943.2785 | 38943.8347 | DAILY | [12 empty] | 0
_1024216938943.2986111111 | 10242169 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT TTS | 38943.2986 | 38943.4021 | DAILY | 00119178 | SPIMAINT | sample cap bank cb ct's | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1010386538943.2986111111 | 10103865 |  | Parent | FALSE | NO.1 500KV BUS E/SW AT MLTS | 38943.2986 | 38943.7208 | REPDAILY | [12 empty] | 0
_1024364238943.3006944444 | 10243642 |  | Parent | FALSE | EX - BLTS 220KV LINE NO.1 BUS CB AT KTS | 38943.3007 | 38943.6174 | DAILY | [12 empty] | 0
_X4C4581638943.3041666667 | X4C45816 |  | Parent | FALSE | EX - MWTS NO.1 220KV LINE NO.1 BUS CB AT JLTS | 38943.3042 | 38947.6368 | CONT | [12 empty] | 0
_1024341238943.3104166667 | 10243412 |  | Parent | FALSE | R2 220/66/22KV TRANS AT KGTS | 38943.3104 | 38944.7042 | CONT | 00017344 | SPIMAINT | Out W/O No2 Trans HV testing by tech services | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010278238943.31875 | 10102782 |  | Parent | FALSE | 4-6 220KV BUS TIE CB AT HWPS | 38943.3187 | 38943.6042 | DAILY | [12 empty] | 0
_1024371038943.4409722222 | 10243710 |  | Parent | FALSE | NO.2 330KV CAPACITOR BANK AT WOTS | 38943.441 | 38943.6465 | DAILY | 00354001 | TRANSGRD | Investigate sec wiring between REF relay and CB | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_X2A858L538943.5 | X2A858L5 |  | Parent | FALSE | L3 TRANS 22KV CB AT BTS | 38943.5 | 38992.3438 | CONT | [12 empty] | 0
_1024399938943.7590277778 | 10243999 |  | Parent | TRUE | B1 220/66KV TRANS AT BATS | 38943.759 | 38943.7667 | DAILY | 00006554 | FAULT | W/O to capture TRANS out from BUS trip | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024423338943.7590277778 | 10244233 | 10243999 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 38943.759 | 38943.7667 | DAILY | 00331109 | FAULT | W/O to capture TRANS out from BUS trip | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X2A858K838944.2319444444 | X2A858K8 |  | Parent | FALSE | TTS NO.1 220KV LINE AT BTS | 38944.2319 | 38944.7743 | REPDAILY | 00015958 | SPICAPX | TTS NO.1 220KV LINE AT BTS | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1023962238944.2916666667 | 10239622 |  | Parent | FALSE | EX - A2 TRANS NO.2 BUS 220KV CB AT KTS | 38944.2917 | 38944.6771 | DAILY | [12 empty] | 0
_X43258F238944.2972222222 | X43258F2 |  | Parent | FALSE | NO.2 66KV REACTOR AT RCTS | 38944.2972 | 38944.5674 | DAILY | 00016897 | SPICAPX | Out W/O For construction work next to reactor & cb | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024422538944.2979166667 | 10244225 | X49058A9 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 38944.2979 | 38946.7722 | CONT | 00352121 | SPICAPX | Out W/O Replace CT's marshalling box and conductor | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X49058A938944.2979166667 | X49058A9 |  | Parent | TRUE | H2 TRANS 330KV CB AT DDTS | 38944.2979 | 38946.7722 | REPDAILY | [12 empty] | 0
_X32058B238944.2986111111 | X32058B2 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 38944.2986 | 38944.6125 | CONT | 00004569 | SPICAPX | Install new pole adjacent to No 3 Bus | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058B338944.2986111111 | X32058B3 | X32058B2 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 38944.2986 | 38944.6125 | CONT | 00026900 | SPICAPX | Avail of plant B3 Trans for No3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010386538944.3097222222 | 10103865 |  | Parent | FALSE | NO.1 500KV BUS E/SW AT MLTS | 38944.3097 | 38944.7049 | REPDAILY | [12 empty] | 0
_1024373938944.4451388889 | 10243739 |  | Parent | TRUE | SPARE 66KV CB - STOCK ITEM 9003437 AT YARRA-ST | 38944.4451 | 38944.5687 | DAILY | [12 empty] | 0
_1024374038944.4451388889 | 10243740 | 10243739 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT SHTS | 38944.4451 | 38944.5687 | DAILY | 00350863 | SPIMAINT | Rebate W/O No3A Cap bank during 3A/B CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024374138944.4451388889 | 10243741 | 10243739 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT SHTS | 38944.4451 | 38944.5687 | DAILY | 00330780 | SPIMAINT | Rebate W/O No3B Cap bank during 3A/B CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024341338944.725 | 10243413 |  | Parent | FALSE | R3 220/66/22KV TRANS AT KGTS | 38944.725 | 38946.7257 | CONT | 00017375 | SPIMAINT | Out W/O No3 Trans HV testing by tech services | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A858K838945.2486111111 | X2A858K8 |  | Parent | FALSE | TTS NO.1 220KV LINE AT BTS | 38945.2486 | 38945.5826 | REPDAILY | 00015958 | SPICAPX | TTS NO.1 220KV LINE AT BTS | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058B438945.275 | X32058B4 |  | Parent | TRUE | EX - NO.1 66KV BUS AT MTS | 38945.275 | 38945.8326 | DAILY | 00004566 | SPICAPX | Relocate No1 Bus V.T | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058B538945.275 | X32058B5 | X32058B4 | Child | FALSE | EX - NO.1 220/66KV TRANS BANK AT MTS | 38945.275 | 38945.8326 | DAILY | 00026898 | SPICAPX | Avail of plant work order for No 1 66 Bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024357738945.2993055556 | 10243577 |  | Parent | TRUE | S018 KTS -GTS 2 220KV | 38945.2993 | 38945.6 | REPDAILY | [12 empty] | 0
_1024410338945.2993055556 | 10244103 | 10243577 | Child | FALSE | KTS -GTS 2 220KV WY | 38945.2993 | 38945.6 | REPDAILY | 00022705 | SPIMAINT | Insulator replacement program | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024364438945.3027777778 | 10243644 |  | Parent | FALSE | EX - B1 TRANS 220KV CB AT KTS | 38945.3028 | 38945.6813 | DAILY | [12 empty] | 0
_1010386538945.3263888889 | 10103865 |  | Parent | FALSE | NO.1 500KV BUS E/SW AT MLTS | 38945.3264 | 38945.6708 | REPDAILY | [12 empty] | 0
_1024389038945.4166666667 | 10243890 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB LINE SIDE ROI AT MLTS | 38945.4167 | 38945.6361 | DAILY | [12 empty] | 0
_1024390438945.5083333333 | 10243904 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 38945.5083 | 38947.2937 | CONT | [12 empty] | 0
_X38458D638945.5708333333 | X38458D6 |  | Parent | FALSE | B2 220/66KV TRANS AT TGTS | 38945.5708 | 38945.659 | DAILY | 00003127 | SPICAPX | Out W/O De-energisation of trans for truck access | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058B638946.2861111111 | X32058B6 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 38946.2861 | 38946.8403 | DAILY | 00004569 | SPICAPX | Reconnect 1-3 66kV B.T CB | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058B738946.2861111111 | X32058B7 | X32058B6 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 38946.2861 | 38946.8403 | DAILY | 00026900 | SPICAPX | Avail of plant for No 3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024357738946.2916666667 | 10243577 |  | Parent | TRUE | S018 KTS -GTS 2 220KV | 38946.2917 | 38946.6632 | REPDAILY | [12 empty] | 0
_1024410338946.2916666667 | 10244103 | 10243577 | Child | FALSE | KTS -GTS 2 220KV WY | 38946.2917 | 38946.6632 | REPDAILY | 00022705 | SPIMAINT | Insulator replacement program | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010301238946.2944444444 | 10103012 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT SVTS | 38946.2944 | 38946.6257 | DAILY | [12 empty] | 0
_1010385938946.3166666667 | 10103859 |  | Parent | FALSE | HYTS NO.1 LINE/SYTS NO.1 LINE 500KV CB AT MLTS | 38946.3167 | 38946.6951 | REPDAILY | [12 empty] | 0
_1024366138946.3402777778 | 10243661 |  | Parent | FALSE | EX - BLTS 220KV LINE NO.2 BUS CB AT KTS | 38946.3403 | 38947.6403 | CONT | [12 empty] | 0
_1024324438946.3770833333 | 10243244 |  | Parent | TRUE | HWTS NO.3 500KV LINE CB AT LYPS | 38946.3771 | 38946.3979 | DAILY | [12 empty] | 0
_1024396438946.3770833333 | 10243964 | 10243244 | Child | FALSE | HWTS NO.3 500KV LINE AT LYPS | 38946.3771 | 38946.3979 | DAILY | 00016088 | FORCED | ADJUST SF6 GAS PRESSURE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z33458F838946.5493055556 | Z33458F8 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 38946.5493 | 38947.5924 | CONT | 00352791 | VEN_AUG | Test Trans cooling controls and tap indications | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010301438947.2944444444 | 10103014 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT SVTS | 38947.2944 | 38947.5806 | DAILY | [12 empty] | 0
_X49758A038947.2965277778 | X49758A0 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 38947.2965 | 38947.7861 | DAILY | 00016040 | SPICAPX | Out W/O No2 Trans grp relocate 66kV conn support | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024387838947.2979166667 | 10243878 |  | Parent | TRUE | 5-6 220KV BUS TIE CB NO.5 BUS SIDE ISOL AT HWPS | 38947.2979 | 38947.6097 | DAILY | [12 empty] | 0
_1024388038947.2979166667 | 10243880 | 10243878 | Child | FALSE | ROTS NO.1 220KV LINE AT HWPS | 38947.2979 | 38947.6097 | DAILY | 00015790 | SPIMAINT | Repair frozen isolator.on No 5 Bus | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010385938947.3173611111 | 10103859 |  | Parent | FALSE | HYTS NO.1 LINE/SYTS NO.1 LINE 500KV CB AT MLTS | 38947.3174 | 38947.6542 | REPDAILY | [12 empty] | 0
_1024396138947.3354166667 | 10243961 |  | Parent | FALSE | BLLY 500KV LINE AT LYPS | 38947.3354 | 38947.3569 | DAILY | 00360516 | FAULT | BLLY trip | SPIPOWER |  |  | Circuits | Eastern | 500 | CONNECTION ASSET | EXCLUDED |  | 0
_1024365538947.4256944444 | 10243655 |  | Parent | FALSE | B1 220/66KV TRANS AT FBTS | 38947.4257 | 38947.634 | DAILY | 00002726 | SPIMAINT | 1 fan to be installed & 1 to be removed for repair | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024396938947.4597222222 | 10243969 |  | Parent | TRUE | NO.2 66KV BUS AT MWTS | 38947.4597 | 38947.4681 | DAILY | 00010279 | FAULT | No 2 66kV Bus Trip | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024397038947.4597222222 | 10243970 | 10243969 | Child | FALSE | B2 220/66KV TRANS AT MWTS | 38947.4597 | 38947.4681 | DAILY | 00010266 | FAULT | B2 220/66KV TRANS No2 66kV Bus Trip | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024397138947.4597222222 | 10243971 | 10243969 | Child | FALSE | MWTS-LY 2 66KV G | 38947.4597 | 38947.4681 | DAILY | 00020536 | FAULT | No 2 66kV Bus Trip | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024422938947.4597222222 | 10244229 | 10243969 | Child | FALSE | JLTS NO.2 220KV LINE AT MWTS | 38947.4597 | 38947.4681 | DAILY | 00016131 | FAULT | JLTS NO2 220KV LINE, No 2 66kV Bus Trip | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z50058B738948.2659722222 | Z50058B7 |  | Parent | FALSE | SVTS NO.1 220KV LINE AT ROTS | 38948.266 | 38948.6549 | REPDAILY | 00350027 | VEN_AUG | Replace Line connection SVTS NO.1 L/YPS NO.8 LCB | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V4S258E138948.2743055556 | V4S258E1 |  | Parent | FALSE | BAY F 500KV LINE AT SMTS (O.O.S) | 38948.2743 | 38948.5458 | CONT | 00012398 | SPIMAINT | erect hypotronics | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Circuits | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1024385838948.3958333333 | 10243858 |  | Parent | FALSE | YPS -YWPS 4 220KV G | 38948.3958 | 38989.7689 | CONT | 00020523 | GENCO | YWPS Unit 4 SCAP isolation and earth | GENCO |  |  | Circuits | Eastern | 220 |  |  |  | 0
_Z50058B738949.2666666667 | Z50058B7 |  | Parent | FALSE | SVTS NO.1 220KV LINE AT ROTS | 38949.2667 | 38949.5889 | REPDAILY | 00350027 | VEN_AUG | Replace Line connection SVTS NO.1 L/YPS NO.8 LCB | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024398038949.3354166667 | 10243980 |  | Parent | FALSE | NO.2 GEN 500/21KV TRANS AT LYPA | 38949.3354 | 38955.5201 | CONT | 00010007 | GENCO | LYPSA No2 SCAP on Isolations and Earths | GENCO |  |  | Main Transformers | Eastern | 500 |  |  |  | 0
_Z500580038949.5444444444 | Z5005800 |  | Parent | FALSE | EX - SVTS NO.1 LINE/YPS NO.8 LINE CB AT ROTS | 38949.5444 | 38953.2764 | CONT | [12 empty] | 0
_1024398438949.6381944444 | 10243984 |  | Parent | FALSE | NO.7 GEN TRANS LINE AT HWPS | 38949.6382 | 38952.3701 | CONT | 00356085 | GENCO | HWPS No7 Gen Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53458A138950.2756944444 | Z53458A1 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 38950.2757 | 38952.2674 | CONT | [12 empty] | 0
_1024380138951.2979166667 | 10243801 |  | Parent | FALSE | EX - TTS NO.1 LINE/WMTS NO.1 LINE 220KV CB AT KTS | 38951.2979 | 38954.6083 | CONT | [12 empty] | 0
_1010301338951.3006944444 | 10103013 |  | Parent | FALSE | 1-6 66KV BUS TIE CB AT SVTS | 38951.3007 | 38951.6049 | DAILY | [12 empty] | 0
_1016118138951.3131944445 | 10161181 | 10087419 | Child | FALSE | NO.2 GEN TRANS 500KV LINE E/SW AT LYPS | 38951.3132 | 38954.6146 | DAILY | [12 empty] | 0
_1010278838951.3180555556 | 10102788 |  | Parent | FALSE | HWTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 38951.3181 | 38951.3743 | CONT | [12 empty] | 0
_1010278338951.3958333333 | 10102783 |  | Parent | FALSE | 5-6 220KV BUS TIE CB AT HWPS | 38951.3958 | 38955.4799 | CONT | [12 empty] | 0
_1024400338951.4152777778 | 10244003 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 38951.4153 | 38954.525 | CONT | 00356082 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024401738951.8173611111 | 10244017 |  | Parent | FALSE | EX - MWTS NO.2 220KV LINE NO.1 BUS CB AT JLTS | 38951.8174 | 38954.4201 | CONT | [12 empty] | 0
_Z53458A738952.2645833333 | Z53458A7 |  | Parent | FALSE | CBTS NO.4 500KV LINE AT ROTS (RTF) | 38952.2646 | 38952.7944 | DAILY | 00356730 | VEN_AUG | Construction work assoc with A2 Tran install | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49058B238952.2930555556 | X49058B2 |  | Parent | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB AT DDTS | 38952.2931 | 38952.7306 | DAILY | [12 empty] | 0
_X46158F038952.3104166667 | X46158F0 |  | Parent | FALSE | EX - 1-2 66KV BUS TIE CB AT BATS | 38952.3104 | 38952.6965 | DAILY | [12 empty] | 0
_1009613838952.3152777778 | 10096138 |  | Parent | TRUE | EX - JLTS NO.2 220KV LINE E/SW AT MWTS | 38952.3153 | 38952.5847 | DAILY | [12 empty] | 0
_1024469638952.3152777778 | 10244696 | 10096138 | Child | FALSE | JLTS NO.2 220KV LINE AT MWTS | 38952.3153 | 38952.5847 | DAILY | 00016131 | SPIMAINT | CL.2 O/HAUL - Stanger TTR 220kv E/Switch | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024402938952.3645833333 | 10244029 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 38952.3646 | 38952.3889 | DAILY | [12 empty] | 0
_1010301538952.4375 | 10103015 |  | Parent | FALSE | 4-5 66KV BUS TIE CB AT SVTS | 38952.4375 | 38952.6014 | DAILY | [12 empty] | 0
_Z53458A238952.7763888889 | Z53458A2 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 38952.7764 | 38993.5806 | CONT | [12 empty] | 0
_Z50058B838953.2791666667 | Z50058B8 |  | Parent | FALSE | YPS NO.8 220KV LINE AT ROTS | 38953.2792 | 38953.7208 | REPDAILY | 00024015 | VEN_AUG | Replace Line connection SVTS NO.1 L/YPS NO.8 LCB | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49058B338953.2916666667 | X49058B3 |  | Parent | FALSE | SMTS NO.2 330KV LINE NO.1 BUS CB AT DDTS | 38953.2917 | 38955.3389 | CONT | [12 empty] | 0
_1024379838953.34375 | 10243798 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 38953.3438 | 38953.4111 | DAILY | 00002863 | SPIMAINT | Out W/O M1 Trans to Top Up 500 & 275 CB SF 6 | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024385738953.3451388889 | 10243857 |  | Parent | TRUE | EX - JLTS NO.1 220KV LINE E/SW AT MWTS | 38953.3451 | 38953.6306 | DAILY | [12 empty] | 0
_1024469938953.3451388889 | 10244699 | 10243857 | Child | FALSE | JLTS NO.1 220KV LINE AT MWTS | 38953.3451 | 38953.6306 | DAILY | 00016130 | SPIMAINT | repair broken e/sw & o/h trans side isol & e/sw | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024175038953.3541666667 | 10241750 |  | Parent | FALSE | W4 GEN TRANS 220KV CB AT YPS | 38953.3542 | 38953.6993 | DAILY | [12 empty] | 0
_Z50058B938953.7256944444 | Z50058B9 |  | Parent | FALSE | EX - SVTS NO.1 LINE/YPS NO.8 LINE CB AT ROTS | 38953.7257 | 38961.6681 | CONT | [12 empty] | 0
_Z50058B838954.2715277778 | Z50058B8 |  | Parent | FALSE | YPS NO.8 220KV LINE AT ROTS | 38954.2715 | 38954.6333 | REPDAILY | 00024015 | VEN_AUG | Replace Line connection SVTS NO.1 L/YPS NO.8 LCB | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158H038954.2979166667 | X46158H0 |  | Parent | FALSE | WBTS 220KV LINE AT BATS | 38954.2979 | 38954.6562 | DAILY | 00012410 | SPICAPX | Out W/O HOTS Line to Fit tie droppers to tie isol | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024380038954.3347222222 | 10243800 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 38954.3347 | 38954.3896 | DAILY | 00002862 | SPIMAINT | Out W/O M2 Trans to Top Up 500 & 275 CB SF 6 | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024417838954.4006944444 | 10244178 |  | Parent | TRUE | NO.1 220KV BUS AT DDTS | 38954.4007 | 38954.4583 | CONT | 00003976 | FAULT | No1 220kV Bus Outage | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024417738954.4006944444 | 10244177 | 10244178 | Child | FALSE | MBTS NO.1 220KV LINE AT DDTS | 38954.4007 | 38954.4597 | CONT | 00012361 | FAULT | Outage MBTS1 Line due to No1 220kV Bus Trip | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024418438954.4006944444 | 10244184 | 10244178 | Child | FALSE | GNTS NO.1 220KV LINE AT DDTS | 38954.4007 | 38954.4597 | CONT | 00352475 | FAULT | Outage GNTS1 Line due to No1 220kV Bus Trip | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024421438954.4006944444 | 10244214 | 10244178 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 38954.4007 | 38954.4597 | CONT | 00351939 | FAULT | Outage 220 Cap due to trip of No1 220kV Bus | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024417538954.4006944444 | 10244175 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT DDTS | 38954.4007 | 38957.6861 | CONT | 00337558 | FAULT | H1 Trans Bank stranded by 220 CB Internal Flashove | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X4C4581838954.4201388889 | X4C45818 |  | Parent | FALSE | EX - MWTS NO.2 220KV LINE NO.1 BUS CB AT JLTS | 38954.4201 | 38989.4806 | CONT | [12 empty] | 0
_1010190738955.2680555556 | 10101907 |  | Parent | TRUE | NO.3 220KV BUS AT BLTS | 38955.2681 | 38955.6507 | REPDAILY | 00002645 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010192338955.2680555556 | 10101923 | 10101907 | Child | FALSE | NO.3 220KV BUS E/SW AT BLTS | 38955.2681 | 38955.6507 | REPDAILY | [12 empty] | 0
_1010193138955.2680555556 | 10101931 | 10101907 | Child | FALSE | KTS 220KV LINE NO.3 BUS CB BUS SIDE E/SW AT BLTS | 38955.2681 | 38955.6507 | REPDAILY | [12 empty] | 0
_1010193238955.2680555556 | 10101932 | 10101907 | Child | FALSE | FBTS 220KV LINE CB BUS SIDE E/SW AT BLTS | 38955.2681 | 38955.6507 | REPDAILY | [12 empty] | 0
_1010194338955.2680555556 | 10101943 | 10101907 | Child | FALSE | 3-5 220KV BUS TIE CB NO.3 BUS SIDE ISOL AT BLTS | 38955.2681 | 38955.6507 | REPDAILY | [12 empty] | 0
_1010194438955.2680555556 | 10101944 | 10101907 | Child | FALSE | NO.3A 220/66KV TRANS BANK 220KV ISOL AT BLTS | 38955.2681 | 38955.6507 | REPDAILY | [12 empty] | 0
_1010195038955.2680555556 | 10101950 | 10101907 | Child | FALSE | 1B-3 220KV BUS TIE CB NO.3 BUS SIDE ISOL AT BLTS | 38955.2681 | 38955.6507 | REPDAILY | [12 empty] | 0
_1024474338955.2680555556 | 10244743 | 10101907 | Child | FALSE | B3A 220/66KV TRANS BANK AT BLTS | 38955.2681 | 38955.6507 | REPDAILY | 00018491 | SPIMAINT | O/Haul - 220kV SWITCHGEAR HPV ISOLATOR (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024474538955.2680555556 | 10244745 | 10101907 | Child | FALSE | FBTS 220KV LINE AT BLTS | 38955.2681 | 38955.6507 | REPDAILY | 00024012 | SPIMAINT | O/Haul - 220kV SWITCHGEAR HPV ISOLATOR (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1024474738955.2680555556 | 10244747 | 10101907 | Child | FALSE | KTS 220KV LINE AT BLTS | 38955.2681 | 38955.6507 | REPDAILY | 00024011 | SPIMAINT | O/Haul - 220kV SWITCHGEAR HPV ISOLATOR (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158H138955.2902777778 | X46158H1 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 38955.2903 | 38955.5896 | DAILY | 00006559 | SPICAPX | Out W/O No2 220kV BUS decomm old #2TR CB BS ROI | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158H238955.2902777778 | X46158H2 | X46158H1 | Child | FALSE | WBTS 220KV LINE AT BATS | 38955.2903 | 38955.5896 | DAILY | 00012410 | SPICAPX | Rebate W/O HOTS Line for No2 220 bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158H338955.2902777778 | X46158H3 | X46158H1 | Child | FALSE | B1 220/66KV TRANS AT BATS | 38955.2903 | 38955.5896 | DAILY | 00006554 | SPICAPX | Perf calc W/O No1 Trans during No2 220 bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49058B438955.3479166667 | X49058B4 |  | Parent | FALSE | SMTS NO.2 330KV LINE AT DDTS | 38955.3479 | 38955.9514 | DAILY | 00012356 | SPICAPX | Out W/O Replace conductor between cb & L/S/isol | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024424638955.9875 | 10244246 |  | Parent | FALSE | SMTS NO.2 330KV LINE NO.1 BUS CB AT DDTS | 38955.9875 | 38957.4618 | CONT | [12 empty] | 0
_1010190738956.2756944444 | 10101907 |  | Parent | TRUE | NO.3 220KV BUS AT BLTS | 38956.2757 | 38956.6368 | REPDAILY | 00002645 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010192338956.2756944444 | 10101923 | 10101907 | Child | FALSE | NO.3 220KV BUS E/SW AT BLTS | 38956.2757 | 38956.6368 | REPDAILY | [12 empty] | 0
_1010193138956.2756944444 | 10101931 | 10101907 | Child | FALSE | KTS 220KV LINE NO.3 BUS CB BUS SIDE E/SW AT BLTS | 38956.2757 | 38956.6368 | REPDAILY | [12 empty] | 0
_1010193238956.2756944444 | 10101932 | 10101907 | Child | FALSE | FBTS 220KV LINE CB BUS SIDE E/SW AT BLTS | 38956.2757 | 38956.6368 | REPDAILY | [12 empty] | 0
_1010194338956.2756944444 | 10101943 | 10101907 | Child | FALSE | 3-5 220KV BUS TIE CB NO.3 BUS SIDE ISOL AT BLTS | 38956.2757 | 38956.6368 | REPDAILY | [12 empty] | 0
_1010194438956.2756944444 | 10101944 | 10101907 | Child | FALSE | NO.3A 220/66KV TRANS BANK 220KV ISOL AT BLTS | 38956.2757 | 38956.6368 | REPDAILY | [12 empty] | 0
_1010195038956.2756944444 | 10101950 | 10101907 | Child | FALSE | 1B-3 220KV BUS TIE CB NO.3 BUS SIDE ISOL AT BLTS | 38956.2757 | 38956.6368 | REPDAILY | [12 empty] | 0
_1024474338956.2756944444 | 10244743 | 10101907 | Child | FALSE | B3A 220/66KV TRANS BANK AT BLTS | 38956.2757 | 38956.6368 | REPDAILY | 00018491 | SPIMAINT | O/Haul - 220kV SWITCHGEAR HPV ISOLATOR (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024474538956.2756944444 | 10244745 | 10101907 | Child | FALSE | FBTS 220KV LINE AT BLTS | 38956.2757 | 38956.6368 | REPDAILY | 00024012 | SPIMAINT | O/Haul - 220kV SWITCHGEAR HPV ISOLATOR (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1024474738956.2756944444 | 10244747 | 10101907 | Child | FALSE | KTS 220KV LINE AT BLTS | 38956.2757 | 38956.6368 | REPDAILY | 00024011 | SPIMAINT | O/Haul - 220kV SWITCHGEAR HPV ISOLATOR (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024424138956.5208333333 | 10244241 |  | Parent | TRUE | NO.1 220KV BUS AT DDTS | 38956.5208 | 38957.6861 | CONT | 00003976 | SPIMAINT | No1 220kV Bus outage for H1 Trans connection | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024424238956.5208333333 | 10244242 | 10244241 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 38956.5208 | 38957.6861 | CONT | 00351939 | SPIMAINT | Child of No1 220kV Bus | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024424338956.5208333333 | 10244243 | 10244241 | Child | FALSE | MBTS NO.1 220KV LINE AT DDTS | 38956.5208 | 38957.6861 | CONT | 00012361 | SPIMAINT | Child of No1 220kV Bus | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024424438956.5208333333 | 10244244 | 10244241 | Child | FALSE | DDTS-GNTS 1 220KV NW | 38956.5208 | 38957.6861 | CONT | 00060184 | SPIMAINT | Child of No1 220kV Bus | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010176638957.2979166667 | 10101766 |  | Parent | FALSE | NO.1 220KV BUS AT YPS | 38957.2979 | 38958.6076 | CONT | 00010588 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_Z33458F638957.3229166667 | Z33458F6 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 38957.3229 | 38968.6715 | REPDAILY | 00352791 | VEN_AUG | No4 Tranformer isol daily for work on OLTC | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024425038957.3333333333 | 10244250 |  | Parent | FALSE | B4 220/66KV TRANS AT BLTS | 38957.3333 | 38957.616 | DAILY | 00002615 | DBPROX | VSCAP for Agility | DISTCO |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024427938957.4909722222 | 10244279 |  | Parent | TRUE | TTS -BTS 3 220KV WT | 38957.491 | 38957.5243 | DAILY | 00023086 | FAULT | TTS -BTS 3 220KV Line BTS-RTS Cable Trip | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024428038957.4909722222 | 10244280 | 10244279 | Child | FALSE | L2 220/22KV TRANS AT BTS | 38957.491 | 38957.5243 | DAILY | 00360870 | FAULT | L2 TRANSF BTS-RTS Cable Trip | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024428138957.4909722222 | 10244281 |  | Parent | FALSE | BTS -RTS 220KV W (BTS to Joint Bay 7) (CABLE) | 38957.491 | 39032.3208 | DAILY | 00310401 | FAULT | RTS-BTS 220kV LINE (Under Ground Cable) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024428438957.7083333333 | 10244284 |  | Parent | TRUE | NO.1 220KV BUS AT DDTS | 38957.7083 | 38957.7375 | DAILY | 00003976 | FORCED | DDTS 220kV Cap Bank Fault | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024428538957.7083333333 | 10244285 | 10244284 | Child | TRUE | NO.1 220KV CAPACITOR BANK AT DDTS | 38957.7083 | 38957.7375 | CONT | 00351939 | FORCED | Child of No1 220kV Bus | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024428838957.7083333333 | 10244288 | 10244285 | Child | FALSE | H3 330/220KV TRANS AT DDTS | 38957.7083 | 38957.7375 | DAILY | 00003971 | FAULT | H3 Transf, DDTS 220kV Cap Bank CB Fault trips Bus | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024428938957.7083333333 | 10244289 | 10244284 | Child | FALSE | H1 330/220KV TRANS BANK AT DDTS | 38957.7083 | 38957.7375 | DAILY | 00337558 | FAULT | H1Transf, DDTS 220kV Cap Bank CB Fault trips Bus | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024429038957.7083333333 | 10244290 | 10244284 | Child | FALSE | GNTS NO.1 220KV LINE AT DDTS | 38957.7083 | 38957.7375 | DAILY | 00352475 | FAULT | GNTS NO.1 220KV LINE, DDTS Cap CB Fault | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024429138957.7083333333 | 10244291 | 10244284 | Child | FALSE | MBTS NO.1 220KV LINE AT DDTS | 38957.7083 | 38957.7375 | DAILY | 00012361 | FAULT | MBTS NO1 220KV LINE, DDTS Cap CB Fault | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024424938957.7083333333 | 10244249 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK CB AT DDTS | 38957.7083 | 38980.7222 | CONT | [12 empty] | 0
_1024429338957.7375 | 10244293 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 38957.7375 | 38989.4847 | DAILY | 00351939 | SPIMAINT | 220kV Cap Bank, DDTS Cap CB fault Unregulated Asse | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 3
_X38458D738958.3006944444 | X38458D7 |  | Parent | FALSE | EX - NO.1 66KV BUS VT AT TGTS | 38958.3007 | 38958.5303 | DAILY | [12 empty] | 0
_1010166638958.3097222222 | 10101666 |  | Parent | FALSE | EX - B1 TRANS NO.2 BUS 220KV CB AT GTS | 38958.3097 | 38960.4498 | CONT | [12 empty] | 0
_1010176538959.3013888889 | 10101765 |  | Parent | FALSE | 5 GRP 220/11KV TRANS AT YPS | 38959.3014 | 38959.6889 | DAILY | 00010550 | SPIMAINT | O/HAUL Transformer without Div Sw (EH) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024434638959.4784722222 | 10244346 | X32058B8 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 38959.4785 | 38959.534 | DAILY | 00026900 | SPICAPX | Avail of plant B3 Trans for No3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058B838959.4784722222 | X32058B8 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 38959.4785 | 38959.534 | DAILY | 00004569 | SPICAPX | Proximity for 20 tonne crane | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458D838959.5451388889 | X38458D8 |  | Parent | FALSE | B2 220/66KV TRANS AT TGTS | 38959.5451 | 38959.6035 | DAILY | 00003127 | SPICAPX | Out W/O De-energisation to allow access for truck | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258G038960.2979166667 | X43258G0 |  | Parent | FALSE | HOTS-RCTS 220KV | 38960.2979 | 38960.6271 | DAILY | 00328509 | SPICAPX | Out W/O Changeover prot panel to new location | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024434238960.3159722222 | 10244342 |  | Parent | FALSE | H2 TRANS 220KV CB AT DDTS | 38960.316 | 38960.7083 | DAILY | [12 empty] | 0
_1024431338960.3944444444 | 10244313 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT MWTS | 38960.3944 | 38960.4431 | DAILY | [12 empty] | 0
_1010343238961.2708333333 | 10103432 |  | Parent | FALSE | U1 TRANS 22KV CB AT RWTS | 38961.2708 | 38963.566 | DAILY | [12 empty] | 0
_X41258B338961.2923611111 | X41258B3 |  | Parent | FALSE | B2 220/66KV TRANS AT SHTS | 38961.2924 | 38961.5444 | DAILY | 00000841 | SPICAPX | Out W/O No2 Trans disconnect 220kV connections | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024393938961.2979166667 | 10243939 |  | Parent | FALSE | H3 330/220KV TRANS AT DDTS | 38961.2979 | 38961.7292 | DAILY | 00003971 | SPIMAINT | Out W/O No3 Trans to replace 22 CT & O/H 330 ROI | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1010799238961.3083333333 | 10107992 |  | Parent | FALSE | EX - KTS NO.3 220KV LINE NO.2 BUS CB AT GTS | 38961.3083 | 38961.6417 | DAILY | [12 empty] | 0
_Z50058C038961.5902777778 | Z50058C0 |  | Parent | FALSE | YPS NO.8 220KV LINE AT ROTS | 38961.5903 | 38961.6604 | DAILY | 00024015 | VEN_AUG | De-energise the line for Commission CB | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024425338962.2743055556 | 10244253 |  | Parent | TRUE | NO.3 220KV BUS AT BLTS | 38962.2743 | 38962.6757 | DAILY | 00002645 | SPIMAINT | finish the bus overhaul | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024508338962.2743055556 | 10245083 | 10244253 | Child | FALSE | KTS 220KV LINE AT BLTS | 38962.2743 | 38962.6757 | DAILY | 00024011 | SPIMAINT | O/H No3 22kV Bus - out on line | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024436038962.3020833333 | 10244360 |  | Parent | FALSE | SHTS 220KV LINE CB AT DDTS | 38962.3021 | 38962.6576 | DAILY | [12 empty] | 0
_1024476738963.0006944445 | 10244767 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 38963.0007 | 38963.2438 | DAILY | 00011755 | FAULT | Prot Trip of MBTS-MKPS 220kV Line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024508538964.2923611111 | 10245085 | X43258F9 | Child | FALSE | BSS 220KV LINE AT RCTS | 38964.2924 | 38964.4431 | DAILY | 00016966 | SPICAPX | Out W/O Install temp termination strip for cb cont | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258F938964.2923611111 | X43258F9 |  | Parent | TRUE | EX - BSS 220KV LINE NO.2 BUS CB AT RCTS | 38964.2924 | 38964.4431 | DAILY | [12 empty] | 0
_1024412238964.3125 | 10244122 | X41258B4 | Child | FALSE | GNTS NO.3 220KV LINE AT SHTS | 38964.3125 | 38986.6639 | CONT | 00352426 | SPICAPX | Rebate W/O GNTS-SHTS 3L during No2 220 Bus outage | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024412338964.3125 | 10244123 | X41258B4 | Child | FALSE | B2 220/66KV TRANS AT SHTS | 38964.3125 | 38986.6639 | CONT | 00000841 | SPICAPX | Perf calc W/O No2 Trans- 220kV disconnected | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X41258B438964.3125 | X41258B4 |  | Parent | TRUE | EX - NO.2 220KV BUS AT SHTS | 38964.3125 | 38986.6639 | CONT | 00000846 | SPICAPX | Out W/O No2 220kV Bus. Complete bus replacement | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158C038964.3541666667 | Z53158C0 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 38964.3542 | 38964.6993 | DAILY | 00004778 | VEN_AUG | Bus outage to rem bus bi pods & TTS Line conection | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158C338964.3541666667 | Z53158C3 | Z53158C0 | Child | FALSE | TTS 220KV LINE AT ROTS | 38964.3542 | 38964.6993 | DAILY | 00023972 | VEN_AUG | Line outage to diconnect CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1024477738964.6192476852 | 10244777 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 38964.6192 | 38964.6687 | DAILY | 00060938 | APDALCOA | Requsted by Alcoa for SF6 Top up at APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X32058B938965.2388888889 | X32058B9 |  | Parent | FALSE | EX - NO.3 220/22KV TRANS BANK AT MTS | 38965.2389 | 38971.3569 | CONT | 00026903 | SPICAPX | Proximity outage of L3 Tr for scaffhold build | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010346538965.2604166667 | 10103465 |  | Parent | TRUE | NO.4 220KV BUS AT ROTS | 38965.2604 | 38966.6479 | CONT | 00329012 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024433538965.2604166667 | 10244335 | 10103465 | Child | FALSE | MTS NO.1 220KV LINE AT ROTS | 38965.2604 | 38966.6479 | CONT | 00350667 | SPIMAINT | rebate for bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010211938965.2743055556 | 10102119 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 38965.2743 | 38965.6674 | REPDAILY | 00015976 | SPIMAINT | O/Haul - 220kV Line (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009278938965.3305555556 | 10092789 |  | Parent | TRUE | ROTS NO.1 220KV LINE CB AT HWPS | 38965.3306 | 38968.5694 | CONT | [12 empty] | 0
_1024508838965.3305555556 | 10245088 | 10092789 | Child | FALSE | ROTS NO.1 220KV LINE AT HWPS | 38965.3306 | 38968.5694 | CONT | 00015790 | SPIMAINT | Out for CB O/H at HWPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024474938965.375 | 10244749 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT TBTS | 38965.375 | 38965.6667 | DAILY | 00351938 | SPIMAINT | Investigate cap bank controls POW Alm | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024441638965.4243055556 | 10244416 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 38965.4243 | 38965.6951 | DAILY | 00017270 | SPIMAINT | SVC - Replace faulty Thyristor & investigate cause | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1010211938966.2708333333 | 10102119 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 38966.2708 | 38966.5771 | REPDAILY | 00015976 | SPIMAINT | O/Haul - 220kV Line (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024509238966.3541666667 | 10245092 | X38458D9 | Child | FALSE | MLTS-TGTS 220KV W | 38966.3542 | 38966.6729 | REPDAILY | 00022740 | SPICAPX | Out for No2 220kV Bus/ calc line rebate | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458D938966.3541666667 | X38458D9 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 38966.3542 | 38966.6729 | REPDAILY | 00003131 | SPICAPX | Out W/O Replace bus insulators and retire bus VT | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458E038966.3541666667 | X38458E0 | X38458D9 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 38966.3542 | 38966.6729 | REPDAILY | 00003127 | SPICAPX | Out W/O Perf calc for bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X4C4581638966.5194444444 | X4C45816 |  | Parent | FALSE | EX - MWTS NO.1 220KV LINE NO.1 BUS CB AT JLTS | 38966.5194 | 38989.568 | CONT | [12 empty] | 0
_1010222538967.2729166667 | 10102225 |  | Parent | FALSE | EX - WMTS NO.2 220KV LINE AT KTS | 38967.2729 | 38967.6604 | REPDAILY | 00015982 | SPIMAINT | INSPECT LINE (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009283638967.2854166667 | 10092836 | 10092839 | Child | FALSE | HTS NO.1 220KV LINE CB AT SVTS | 38967.2854 | 38967.6854 | DAILY | [12 empty] | 0
_1009283938967.2854166667 | 10092839 |  | Parent | TRUE | HTS NO.1 220KV LINE E/SW AT SVTS | 38967.2854 | 38967.6854 | DAILY | [12 empty] | 0
_1009284038967.2854166667 | 10092840 | 10092839 | Child | FALSE | HTS NO.1 220KV LINE CB LINE SIDE ISOL AT SVTS | 38967.2854 | 38967.6854 | DAILY | [12 empty] | 0
_1024509438967.2854166667 | 10245094 | 10092839 | Child | FALSE | HTS NO.2 220KV LINE AT SVTS | 38967.2854 | 38967.6854 | DAILY | 00351702 | SPIMAINT | O/Haul - Sw/gear 220kV HPV Isol | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024509238967.3694444444 | 10245092 | X38458D9 | Child | FALSE | MLTS-TGTS 220KV W | 38967.3694 | 38967.6813 | REPDAILY | 00022740 | SPICAPX | Out for No2 220kV Bus/ calc line rebate | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458D938967.3694444444 | X38458D9 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 38967.3694 | 38967.6813 | REPDAILY | 00003131 | SPICAPX | Out W/O Replace bus insulators and retire bus VT | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458E038967.3694444444 | X38458E0 | X38458D9 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 38967.3694 | 38967.6813 | REPDAILY | 00003127 | SPICAPX | Out W/O Perf calc for bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024494038967.625 | 10244940 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 38967.625 | 38971.3993 | CONT | 00356082 | GENCO | Isolation for Generator | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024475938968.2680555556 | 10244759 |  | Parent | TRUE | H1 330/220KV TRANS BANK AT DDTS | 38968.2681 | 38968.7944 | REPDAILY | 00337558 | SPICAPX | Out W/O No 1Trans, and No 1 220 Bus outage | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024493638968.2680555556 | 10244936 | 10244759 | Child | FALSE | DDTS-GNTS 1 220KV NW | 38968.2681 | 38968.7944 | REPDAILY | 00060184 | SPICAPX | Out W/O Rebate calc for 220kV bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024493738968.2680555556 | 10244937 | 10244759 | Child | FALSE | MBTS-DDTS 1 220KV NW | 38968.2681 | 38968.7944 | REPDAILY | 00060187 | SPICAPX | Out W/O Rebate calc for 220kV bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010222538968.2722222222 | 10102225 |  | Parent | FALSE | EX - WMTS NO.2 220KV LINE AT KTS | 38968.2722 | 38968.6208 | REPDAILY | 00015982 | SPIMAINT | INSPECT LINE (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009283538968.2888888889 | 10092835 | 10092837 | Child | FALSE | HTS NO.2 220KV LINE CB AT SVTS | 38968.2889 | 38968.6299 | DAILY | [12 empty] | 0
_1009283738968.2888888889 | 10092837 |  | Parent | TRUE | HTS NO.2 220KV LINE E/SW AT SVTS | 38968.2889 | 38968.6299 | DAILY | [12 empty] | 0
_1009283838968.2888888889 | 10092838 | 10092837 | Child | FALSE | HTS NO.2 220KV LINE CB LINE SIDE ISOL AT SVTS | 38968.2889 | 38968.6299 | DAILY | [12 empty] | 0
_1024510538968.2888888889 | 10245105 | 10092837 | Child | FALSE | HTS NO.2 220KV LINE AT SVTS | 38968.2889 | 38968.6299 | DAILY | 00351702 | SPIMAINT | O/Haul - Sw/gear 220kV HPV Isol | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024509238968.3590277778 | 10245092 | X38458D9 | Child | FALSE | MLTS-TGTS 220KV W | 38968.359 | 38968.6757 | REPDAILY | 00022740 | SPICAPX | Out for No2 220kV Bus/ calc line rebate | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458D938968.3590277778 | X38458D9 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 38968.359 | 38968.6757 | REPDAILY | 00003131 | SPICAPX | Out W/O Replace bus insulators and retire bus VT | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458E038968.3590277778 | X38458E0 | X38458D9 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 38968.359 | 38968.6757 | REPDAILY | 00003127 | SPICAPX | Out W/O Perf calc for bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024400638968.55625 | 10244006 |  | Parent | FALSE | DDTS NO.3 220KV LINE NO.1 BUS CB AT GNTS | 38968.5563 | 38968.5972 | DAILY | [12 empty] | 0
_1024503238968.8777777778 | 10245032 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 38968.8778 | 39018.9722 | CONT | 00356084 | GENCO | No6 Gen Trans Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025257038969.0152777778 | 10252570 |  | Parent | FALSE | HWTS NO.3 500KV LINE AT LYPS | 38969.0153 | 38969.1132 | DAILY | 00016088 | FORCED | Low SF6 in line CB | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010301638969.25 | 10103016 |  | Parent | TRUE | NO.1 220KV BUS AT SVTS | 38969.25 | 38969.6701 | DAILY | 00004856 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1024433138969.25 | 10244331 | 10103016 | Child | FALSE | ROTS NO.1 220KV LINE AT SVTS | 38969.25 | 38969.6701 | DAILY | 00351700 | SPIMAINT | Rebate work order for bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024433238969.25 | 10244332 | 10103016 | Child | FALSE | HTS NO.1 220KV LINE AT SVTS | 38969.25 | 38969.6701 | DAILY | 00351703 | SPIMAINT | Rebate work order for bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024475938969.2694444444 | 10244759 |  | Parent | TRUE | H1 330/220KV TRANS BANK AT DDTS | 38969.2694 | 38969.5889 | REPDAILY | 00337558 | SPICAPX | Out W/O No 1Trans, and No 1 220 Bus outage | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024493638969.2694444444 | 10244936 | 10244759 | Child | FALSE | DDTS-GNTS 1 220KV NW | 38969.2694 | 38969.5889 | REPDAILY | 00060184 | SPICAPX | Out W/O Rebate calc for 220kV bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024493738969.2694444444 | 10244937 | 10244759 | Child | FALSE | MBTS-DDTS 1 220KV NW | 38969.2694 | 38969.5889 | REPDAILY | 00060187 | SPICAPX | Out W/O Rebate calc for 220kV bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858M138969.2763888889 | X2A858M1 |  | Parent | FALSE | TTS -BTS 1 220KV WT | 38969.2764 | 38969.6604 | REPDAILY | 00023081 | SPICAPX | erect new L3 Transformer enclosure | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024509238969.3138888889 | 10245092 | X38458D9 | Child | FALSE | MLTS-TGTS 220KV W | 38969.3139 | 38969.6521 | REPDAILY | 00022740 | SPICAPX | Out for No2 220kV Bus/ calc line rebate | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458D938969.3138888889 | X38458D9 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 38969.3139 | 38969.6521 | REPDAILY | 00003131 | SPICAPX | Out W/O Replace bus insulators and retire bus VT | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458E038969.3138888889 | X38458E0 | X38458D9 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 38969.3139 | 38969.6521 | REPDAILY | 00003127 | SPICAPX | Out W/O Perf calc for bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010301738970.2493055556 | 10103017 |  | Parent | TRUE | NO.2 220KV BUS AT SVTS | 38970.2493 | 38970.5903 | DAILY | 00004857 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1010302138970.2493055556 | 10103021 | 10103017 | Child | FALSE | 2-4 220KV BUS TIE CB NO.2 BUS SIDE E/SW AT SVTS | 38970.2493 | 38970.5903 | DAILY | [12 empty] | 0
_1010302238970.2493055556 | 10103022 | 10103017 | Child | FALSE | NO.2 TRANS 220KV E/SW AT SVTS | 38970.2493 | 38970.5903 | DAILY | [12 empty] | 0
_1010303238970.2493055556 | 10103032 | 10103017 | Child | FALSE | NO.2 TRANS 220KV ISOL AT SVTS | 38970.2493 | 38970.5903 | DAILY | [12 empty] | 0
_1010303338970.2493055556 | 10103033 | 10103017 | Child | FALSE | 2-4 220KV BUS TIE CB NO.2 BUS SIDE ISOL AT SVTS | 38970.2493 | 38970.5903 | DAILY | [12 empty] | 0
_1010303538970.2493055556 | 10103035 | 10103017 | Child | FALSE | HTS NO.2 220KV LINE CB BUS SIDE E/SW AT SVTS | 38970.2493 | 38970.5903 | DAILY | [12 empty] | 0
_1024478738970.2493055556 | 10244787 | 10103017 | Child | FALSE | HTS NO.2 220KV LINE AT SVTS | 38970.2493 | 38970.5903 | DAILY | 00351702 | SPIMAINT | Rebate work order for bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024478838970.2493055556 | 10244788 | 10103017 | Child | FALSE | ROTS NO.2 220KV LINE AT SVTS | 38970.2493 | 38970.5903 | DAILY | 00351701 | SPIMAINT | Rebate work order for bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858M138970.2666666667 | X2A858M1 |  | Parent | FALSE | TTS -BTS 1 220KV WT | 38970.2667 | 38970.5382 | REPDAILY | 00023081 | SPICAPX | erect new L3 Transformer enclosure | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024509238970.3236111111 | 10245092 | X38458D9 | Child | FALSE | MLTS-TGTS 220KV W | 38970.3236 | 38970.6431 | REPDAILY | 00022740 | SPICAPX | Out for No2 220kV Bus/ calc line rebate | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458D938970.3236111111 | X38458D9 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 38970.3236 | 38970.6431 | REPDAILY | 00003131 | SPICAPX | Out W/O Replace bus insulators and retire bus VT | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458E038970.3236111111 | X38458E0 | X38458D9 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 38970.3236 | 38970.6431 | REPDAILY | 00003127 | SPICAPX | Out W/O Perf calc for bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z50058C138970.3527777778 | Z50058C1 |  | Parent | FALSE | NO.4 220KV BUS AT ROTS | 38970.3528 | 38970.4792 | DAILY | 00329012 | VEN_AUG | NO.4 220KV BUS & SVTS 2 Line Isolated only | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z50058C238970.4881944444 | Z50058C2 |  | Parent | FALSE | SVTS NO.2 220KV LINE AT ROTS | 38970.4882 | 38970.5431 | DAILY | 00023968 | VEN_AUG | SVTS 2 Line Isolated only | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024504538970.9701388889 | 10245045 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 38970.9701 | 38971.4236 | CONT | 00017270 | FAULT | KGTS SVC Tripped | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1010299938971.2743055556 | 10102999 |  | Parent | FALSE | DDTS NO.2 330KV LINE AT SMTS | 38971.2743 | 38975.6854 | CONT | 00012750 | SPIMAINT | O/Haul - 330kV Line | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024409138971.2951388889 | 10244091 |  | Parent | FALSE | EX - 66/22KV TIE TRANS AT BLTS | 38971.2951 | 39017.5174 | CONT | 00002623 | SPICAPX | REPLACE 66/22KV TIE TRANSFORMER | SPIPOWER |  | X513 - (BLTS) REPLACE 66/22KV TIE TRANSFORMER | Connection Transformers | Western | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_X4C4581238971.3111111111 | X4C45812 |  | Parent | FALSE | EX - HWPS NO.4 220KV LINE NO.2 BUS CB AT JLTS | 38971.3111 | 38975.6625 | CONT | [12 empty] | 0
_1009279038971.3180555556 | 10092790 |  | Parent | FALSE | HWTS NO.1 220KV LINE CB AT HWPS | 38971.3181 | 38975.5875 | CONT | [12 empty] | 0
_X38458E338971.3465277778 | X38458E3 |  | Parent | TRUE | EX - NO.1 220KV BUS AT TGTS | 38971.3465 | 38971.6819 | REPDAILY | 00003130 | SPICAPX | Out W/O Replace bus support insulators & remove VT | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458E438971.3465277778 | X38458E4 | X38458E3 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38971.3465 | 38971.6819 | REPDAILY | 00023231 | SPICAPX | Out W/O Perf calc for No 1 trans while bus out | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024507538971.3541666667 | 10245075 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 38971.3542 | 38971.366 | DAILY | 00012436 | FAULT | HWTS-SMTS No1 Line off-loaded at SMTS | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058C038971.3597222222 | X32058C0 |  | Parent | FALSE | EX - NO.2 220/22KV TRANS BANK AT MTS | 38971.3597 | 38986.3979 | CONT | 00026902 | SPICAPX | EAP outage of L2 Tr for scaffhold build | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024504438971.4236111111 | 10245044 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 38971.4236 | 38971.6958 | CONT | 00017270 | SPIMAINT | KGTS SVC Tripped - Investigate/repair | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z33458G038971.4583333333 | Z33458G0 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 38971.4583 | 38990.2951 | REPDAILY | 00352791 | VEN_AUG | No4 Tranformer isol daily for work on OLTC | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024018238971.4972222222 | 10240182 |  | Parent | FALSE | NO.1A TRANS AT RCTS | 38971.4972 | 38973.6222 | CONT | 00016722 | SPIMAINT | Condition Monitoring Country Trans 2day North Area | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024508738971.5159722222 | 10245087 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 38971.516 | 38976.759 | CONT | 00356080 | GENCO | Isolated for GenCo | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024509338971.5972222222 | 10245093 |  | Parent | FALSE | YPS -YWPS 2 220KV G | 38971.5972 | 38973.5632 | CONT | 00020518 | GENCO | Genco Work | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158I138972.2638888889 | X46158I1 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 38972.2639 | 38972.7132 | DAILY | 00006554 | SPICAPX | Out W/O No1 Trans isolated for SCIMS testing | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010343338972.2784722222 | 10103433 |  | Parent | FALSE | L3 TRANS 22KV CB AT RWTS | 38972.2785 | 38972.6326 | DAILY | [12 empty] | 0
_1010267938972.2909722222 | 10102679 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 38972.291 | 38972.709 | DAILY | 00019243 | SPIMAINT | 1 Yearly O/Haul - SVC at HOTS | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X46158I338972.3763888889 | X46158I3 |  | Parent | TRUE | NO.1 66KV BUS AT BATS | 38972.3764 | 38972.7028 | DAILY | 00006560 | SPICAPX | Out W/O No1 66kV Bus to remove bus VT | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158I438972.3763888889 | X46158I4 | X46158I3 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 38972.3764 | 38972.7028 | DAILY | 00331109 | SPICAPX | Rebate W/O No1 Cap bank during 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024502738972.4069444445 | 10245027 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS AT JLGB | 38972.4069 | 38996.6701 | CONT | 00009830 | GENCO | SCAP:JLGSB1 Isolation & Earthed for Power Station | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_X38458E338972.4409722222 | X38458E3 |  | Parent | TRUE | EX - NO.1 220KV BUS AT TGTS | 38972.441 | 38972.7007 | REPDAILY | 00003130 | SPICAPX | Out W/O Replace bus support insulators & remove VT | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458E438972.4409722222 | X38458E4 | X38458E3 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38972.441 | 38972.7007 | REPDAILY | 00023231 | SPICAPX | Out W/O Perf calc for No 1 trans while bus out | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024508038972.4979166667 | 10245080 |  | Parent | TRUE | WMTS NO.2 220KV LINE CB AT FBTS | 38972.4979 | 38972.5076 | DAILY | [12 empty] | 0
_1025257138972.4979166667 | 10252571 | 10245080 | Child | FALSE | WMTS NO.2 220KV LINE AT FBTS | 38972.4979 | 38972.5076 | DAILY | 00017157 | SPIMAINT | OUT FOR LOW SF6 ALARM | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X46158I238973.2729166667 | X46158I2 |  | Parent | FALSE | B2 220/66KV TRANS AT BATS | 38973.2729 | 38973.7271 | DAILY | 00006555 | SPICAPX | Out W/O No2 Trans isolated for SCIMS testing | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49758A238973.2923611111 | X49758A2 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 38973.2924 | 38974.6914 | CONT | 00016040 | SPICAPX | Out W/O No2 Trans grp relocate 66kV conn support | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A858M238973.3013888889 | X2A858M2 |  | Parent | FALSE | RTS 220KV LINE E/SW AT BTS | 38973.3014 | 38973.6146 | DAILY | [12 empty] | 0
_1023797038973.3097222222 | 10237970 |  | Parent | TRUE | EX - NO.2 66KV CAPACITOR BANK CB AT HOTS | 38973.3097 | 38973.6819 | DAILY | [12 empty] | 0
_1024483438973.3097222222 | 10244834 | 10237970 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 38973.3097 | 38973.6819 | DAILY | 00359897 | SPIMAINT | Rebate W/O No2 Cap bank during CB O/H | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024484438973.3180555556 | 10244844 |  | Parent | FALSE | NO.6 GEN TRANS NO.4 BUS 220KV CB AT HWPS | 38973.3181 | 38973.6181 | DAILY | [12 empty] | 0
_X38458E338973.3576388889 | X38458E3 |  | Parent | TRUE | EX - NO.1 220KV BUS AT TGTS | 38973.3576 | 38973.6944 | REPDAILY | 00003130 | SPICAPX | Out W/O Replace bus support insulators & remove VT | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458E438973.3576388889 | X38458E4 | X38458E3 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38973.3576 | 38973.6944 | REPDAILY | 00023231 | SPICAPX | Out W/O Perf calc for No 1 trans while bus out | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024483938974.2930555556 | 10244839 |  | Parent | TRUE | NO.3 220KV CAPACITOR BANK CB AT ROTS | 38974.2931 | 38974.5118 | DAILY | [12 empty] | 0
_1025275038974.2930555556 | 10252750 | 10244839 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 38974.2931 | 38974.5118 | DAILY | 00112417 | SPIMAINT | Ductor CB with high current ductor | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024303338974.3020833333 | 10243033 |  | Parent | TRUE | EX - NO.1 220KV BUS AT JLTS | 38974.3021 | 38974.591 | DAILY | 00009889 | SPIMAINT | Accuracy testing of Bus CVT | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024479538974.3020833333 | 10244795 | 10243033 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 38974.3021 | 38974.591 | DAILY | 00015936 | SPIMAINT | Rebate for Accuracy testing of Bus CVT | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458E338974.4 | X38458E3 |  | Parent | TRUE | EX - NO.1 220KV BUS AT TGTS | 38974.4 | 38974.6458 | REPDAILY | 00003130 | SPICAPX | Out W/O Replace bus support insulators & remove VT | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458E438974.4 | X38458E4 | X38458E3 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38974.4 | 38974.6458 | REPDAILY | 00023231 | SPICAPX | Out W/O Perf calc for No 1 trans while bus out | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X4C458B038974.4291666667 | X4C458B0 |  | Parent | FALSE | MWTS NO.2 220KV LINE AT JLTS | 38974.4292 | 38974.616 | DAILY | 00015948 | SPICAPX | HWPS 4 LINE / MWTS #1 CB LINE CONNECTIONS | SPIPOWER | X4C4 | X4C4 - (JLTS) REPLACE 3AS2 220KV CBS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024303238975.3194444444 | 10243032 |  | Parent | TRUE | EX - NO.2 220KV BUS AT JLTS | 38975.3194 | 38975.5319 | DAILY | 00009890 | SPIMAINT | Accuracy testing of Bus CVT | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024479638975.3194444444 | 10244796 | 10243032 | Child | FALSE | HWPS-JLTS 2 220KV G | 38975.3194 | 38975.5319 | DAILY | 00020443 | SPIMAINT | Rebate wo for Accuracy testing of Bus CVT | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024314338975.3361111111 | 10243143 |  | Parent | FALSE | RCTS 220KV LINE NO.1 BUS CB AT HOTS | 38975.3361 | 38975.509 | DAILY | [12 empty] | 0
_1025207438975.4465277778 | 10252074 |  | Parent | FALSE | EX - ATS 220KV LINE AT KTS | 38975.4465 | 38975.4653 | DAILY | 00015978 | FORCED | Remove foreign object | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025207238975.5527777778 | 10252072 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 38975.5528 | 38975.6017 | DAILY | [12 empty] | 0
_1010325038976.2722222222 | 10103250 | 10103443 | Child | FALSE | NO.2A 220KV BUS E/SW AT RTS | 38976.2722 | 38976.6243 | REPDAILY | [12 empty] | 0
_1010337938976.2722222222 | 10103379 | 10103443 | Child | FALSE | NO.2B 220KV BUS AT RTS | 38976.2722 | 38976.6243 | REPDAILY | 00021391 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1010338038976.2722222222 | 10103380 | 10103443 | Child | FALSE | BTS 220KV LINE CB BUS SIDE ROI AT RTS | 38976.2722 | 38976.6243 | REPDAILY | [12 empty] | 0
_1010344338976.2722222222 | 10103443 |  | Parent | TRUE | NO.2A 220KV BUS AT RTS | 38976.2722 | 38976.6243 | REPDAILY | 00007348 | SPIMAINT | O/HAUL - 220kv Bus 2A & 2B | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1010345038976.2722222222 | 10103450 | 10103443 | Child | FALSE | 1-2A 220KV BUS TIE CB NO.2A BUS SIDE E/SW AT RTS | 38976.2722 | 38976.6243 | REPDAILY | [12 empty] | 0
_1010345138976.2722222222 | 10103451 | 10103443 | Child | FALSE | B2 TRANS 220KV E/SW AT RTS | 38976.2722 | 38976.6243 | REPDAILY | [12 empty] | 0
_1010345238976.2722222222 | 10103452 | 10103443 | Child | FALSE | NO.2B 220KV BUS E/SW AT RTS | 38976.2722 | 38976.6243 | REPDAILY | [12 empty] | 0
_1010345738976.2722222222 | 10103457 | 10103443 | Child | FALSE | 2B-4 220KV BUS TIE CB NO.2B BUS SIDE ISOL AT RTS | 38976.2722 | 38976.6243 | REPDAILY | [12 empty] | 0
_1010345838976.2722222222 | 10103458 | 10103443 | Child | FALSE | 1-2A 220KV BUS TIE CB NO.2A BUS SIDE ISOL AT RTS | 38976.2722 | 38976.6243 | REPDAILY | [12 empty] | 0
_1010345938976.2722222222 | 10103459 | 10103443 | Child | FALSE | B2 TRANS 220KV ISOL AT RTS | 38976.2722 | 38976.6243 | REPDAILY | [12 empty] | 0
_1010346038976.2722222222 | 10103460 | 10103443 | Child | FALSE | 2A-2B 220KV BUS TIE ISOL AT RTS | 38976.2722 | 38976.6243 | REPDAILY | [12 empty] | 0
_1024484538976.2722222222 | 10244845 | 10103443 | Child | FALSE | B2 220/66KV TRANS AT RTS | 38976.2722 | 38976.6243 | REPDAILY | 00007331 | SPIMAINT | Avail of plant work order for Bus O/H | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024188538976.2951388889 | 10241885 |  | Parent | FALSE | B1 220/66KV TRANS AT FBTS | 38976.2951 | 38977.6854 | CONT | 00002726 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010325038977.275 | 10103250 | 10103443 | Child | FALSE | NO.2A 220KV BUS E/SW AT RTS | 38977.275 | 38977.6431 | REPDAILY | [12 empty] | 0
_1010337938977.275 | 10103379 | 10103443 | Child | FALSE | NO.2B 220KV BUS AT RTS | 38977.275 | 38977.6431 | REPDAILY | 00021391 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1010338038977.275 | 10103380 | 10103443 | Child | FALSE | BTS 220KV LINE CB BUS SIDE ROI AT RTS | 38977.275 | 38977.6431 | REPDAILY | [12 empty] | 0
_1010344338977.275 | 10103443 |  | Parent | TRUE | NO.2A 220KV BUS AT RTS | 38977.275 | 38977.6431 | REPDAILY | 00007348 | SPIMAINT | O/HAUL - 220kv Bus 2A & 2B | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1010345038977.275 | 10103450 | 10103443 | Child | FALSE | 1-2A 220KV BUS TIE CB NO.2A BUS SIDE E/SW AT RTS | 38977.275 | 38977.6431 | REPDAILY | [12 empty] | 0
_1010345138977.275 | 10103451 | 10103443 | Child | FALSE | B2 TRANS 220KV E/SW AT RTS | 38977.275 | 38977.6431 | REPDAILY | [12 empty] | 0
_1010345238977.275 | 10103452 | 10103443 | Child | FALSE | NO.2B 220KV BUS E/SW AT RTS | 38977.275 | 38977.6431 | REPDAILY | [12 empty] | 0
_1010345738977.275 | 10103457 | 10103443 | Child | FALSE | 2B-4 220KV BUS TIE CB NO.2B BUS SIDE ISOL AT RTS | 38977.275 | 38977.6431 | REPDAILY | [12 empty] | 0
_1010345838977.275 | 10103458 | 10103443 | Child | FALSE | 1-2A 220KV BUS TIE CB NO.2A BUS SIDE ISOL AT RTS | 38977.275 | 38977.6431 | REPDAILY | [12 empty] | 0
_1010345938977.275 | 10103459 | 10103443 | Child | FALSE | B2 TRANS 220KV ISOL AT RTS | 38977.275 | 38977.6431 | REPDAILY | [12 empty] | 0
_1010346038977.275 | 10103460 | 10103443 | Child | FALSE | 2A-2B 220KV BUS TIE ISOL AT RTS | 38977.275 | 38977.6431 | REPDAILY | [12 empty] | 0
_1024484538977.275 | 10244845 | 10103443 | Child | FALSE | B2 220/66KV TRANS AT RTS | 38977.275 | 38977.6431 | REPDAILY | 00007331 | SPIMAINT | Avail of plant work order for Bus O/H | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024516038977.9125 | 10245160 |  | Parent | FALSE | A1 GEN TRANS 500KV CB AT LYPS | 38977.9125 | 38982.7739 | CONT | [12 empty] | 0
_1009286238979.2958333333 | 10092862 |  | Parent | FALSE | KTS NO.1 220KV LINE CB AT WMTS | 38979.2958 | 38979.641 | REPDAILY | [12 empty] | 0
_1025222638979.2986111111 | 10252226 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.2 BUS CB AT HWTS | 38979.2986 | 38979.6285 | DAILY | [12 empty] | 0
_1003692038979.2986111111 | 10036920 |  | Parent | FALSE | S180 HWTS-SMTS 1 500KV | 38979.2986 | 38979.6306 | REPDAILY | [12 empty] | 0
_1025222338979.2986111111 | 10252223 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 38979.2986 | 38979.6306 | DAILY | [12 empty] | 0
_1009276138979.3104166667 | 10092761 |  | Parent | FALSE | JLA NO.1 220KV LINE AT TBTS | 38979.3104 | 38979.6778 | DAILY | 00018301 | SPIMAINT | O/Haul - JLA 1 Line CVTs at TBTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458E638979.3881944444 | X38458E6 |  | Parent | FALSE | EX - 1-2 220KV BUS TIE CB AT TGTS | 38979.3882 | 38988.5993 | CONT | [12 empty] | 0
_1010240938979.4243055556 | 10102409 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT TGTS | 38979.4243 | 38979.6174 | DAILY | 00003129 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1025223438979.6284722222 | 10252234 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.2 BUS CB AT HWTS | 38979.6285 | 38979.7694 | CONT | [12 empty] | 0
_1025199738980.25 | 10251997 |  | Parent | TRUE | H1 330/220KV TRANS BANK AT DDTS | 38980.25 | 38980.7222 | CONT | 00337558 | SPICAPX | Out W/O No 1 220 bus & No 1 Trans outage | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025214338980.25 | 10252143 | 10251997 | Child | FALSE | DDTS-GNTS 1 220KV NW | 38980.25 | 38980.7222 | CONT | 00060184 | SPICAPX | Out W/O Rebate calc for No 1 220kV Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025214438980.25 | 10252144 | 10251997 | Child | FALSE | MBTS-DDTS 1 220KV NW | 38980.25 | 38980.7222 | CONT | 00060187 | SPICAPX | Out W/O Rebate calc for No 1 220kV Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025214538980.25 | 10252145 | 10251997 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 38980.25 | 38980.7222 | CONT | 00351939 | SPICAPX | Out W/O Perf calc for No 1 220kV Bus outage | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1010239938980.2951388889 | 10102399 |  | Parent | FALSE | B2 TRANS 220KV CB AT TBTS | 38980.2951 | 38980.6535 | CONT | [12 empty] | 0
_Z53158C438980.3027777778 | Z53158C4 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 38980.3028 | 38982.7194 | CONT | 00004778 | VEN_AUG | Outage to replace Bus and stands in bay M,N,Q,R | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158C538980.3027777778 | Z53158C5 | Z53158C4 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 38980.3028 | 38982.7194 | CONT | 00112418 | VEN_AUG | Bus outage to remove bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1009286238980.3069444444 | 10092862 |  | Parent | FALSE | KTS NO.1 220KV LINE CB AT WMTS | 38980.3069 | 38980.6132 | REPDAILY | [12 empty] | 0
_1024428338980.3104166667 | 10244283 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK CB AT TGTS | 38980.3104 | 38980.6562 | DAILY | [12 empty] | 0
_1003692038980.3229166667 | 10036920 |  | Parent | FALSE | S180 HWTS-SMTS 1 500KV | 38980.3229 | 38980.6479 | REPDAILY | [12 empty] | 0
_X38458E738980.3548611111 | X38458E7 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38980.3549 | 38980.7132 | REPDAILY | 00023231 | SPICAPX | Out W/O De-energisation for safety purposes | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025224038980.3791666667 | 10252240 |  | Parent | FALSE | JLGB NO.2 UNIT TRANS DISC CB AT JLGB | 38980.3792 | 38980.6438 | DAILY | [12 empty] | 0
_1025226138980.5416666667 | 10252261 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 38980.5417 | 38980.566 | DAILY | [12 empty] | 0
_1025227638980.6736111111 | 10252276 |  | Parent | TRUE | HWTS NO.3 500KV LINE CB AT LYPS | 38980.6736 | 38980.7069 | DAILY | [12 empty] | 0
_1025275438980.6736111111 | 10252754 | 10252276 | Child | FALSE | HWTS NO.3 500KV LINE AT LYPS | 38980.6736 | 38980.7069 | DAILY | 00016088 | SPIMAINT | SF6 top up | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025208238980.7222222222 | 10252082 |  | Parent | FALSE | EX - NO.1 TRANS 220KV CB AT DDTS | 38980.7222 | 38983.7229 | CONT | [12 empty] | 0
_1024483138981.2729166667 | 10244831 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 38981.2729 | 38981.6743 | REPDAILY | 00026099 | SPIMAINT | investigate/repair leaking transformer | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1003692038981.2916666667 | 10036920 |  | Parent | FALSE | S180 HWTS-SMTS 1 500KV | 38981.2917 | 38981.6097 | REPDAILY | [12 empty] | 0
_1009441138981.3027777778 | 10094411 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT TBTS | 38981.3028 | 38981.6035 | DAILY | 00351938 | SPIMAINT | O/Haul - Cap Bank & E/Sw (EM) | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024484338981.3076388889 | 10244843 |  | Parent | FALSE | A1 GEN TRANS 500KV CB AT LYPS | 38981.3076 | 38981.5896 | DAILY | [12 empty] | 0
_X38458E738981.3729166667 | X38458E7 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38981.3729 | 38981.6847 | REPDAILY | 00023231 | SPICAPX | Out W/O De-energisation for safety purposes | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024483138982.2722222222 | 10244831 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 38982.2722 | 38982.6785 | REPDAILY | 00026099 | SPIMAINT | investigate/repair leaking transformer | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024482938982.3020833333 | 10244829 |  | Parent | TRUE | NO.1 500KV BUS AT LYPS | 38982.3021 | 38982.525 | DAILY | 00010023 | SPIMAINT | No 1 & 3 Bus outage to o/haul 1-3 TIE ROI | SPIPOWER |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1024483038982.3020833333 | 10244830 | 10244829 | Child | FALSE | HWTS NO.2 500KV LINE AT LYPS | 38982.3021 | 38982.525 | DAILY | 00016087 | SPIMAINT | Rebate for No 1&3 Bus outage to o/haul 1-3 TIE ROI | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X460581038982.3020833333 | X4605810 |  | Parent | FALSE | LYGS A1 TRANS 500KV CB AT LYPS | 38982.3021 | 38982.6493 | DAILY | [12 empty] | 0
_1010405538982.3916666667 | 10104055 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT TBTS | 38982.3917 | 38982.4619 | DAILY | 00004903 | SPIMAINT | O/HAUL Transformer without Div Sw (EM) | SPIPOWER |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_1025274838982.6763888889 | 10252748 |  | Parent | FALSE | EX - NO.3 220/22KV TRANS BANK AT MTS | 38982.6764 | 38982.6958 | DAILY | 00026903 | FORCED | Out for L3 TRANS to isolate B3 | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025274938982.6763888889 | 10252749 |  | Parent | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 38982.6764 | 38982.8243 | DAILY | 00026900 | FORCED | Out for B3 due to control cable damage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025247638982.8631944444 | 10252476 |  | Parent | FALSE | NO.3 GEN 220/16.5KV TRANS OLTC MECH AT HWPS | 38982.8632 | 38985.7375 | CONT | [12 empty] | 0
_Z53158D138983.2833333333 | Z53158D1 |  | Parent | FALSE | TTS 220KV LINE AT ROTS | 38983.2833 | 38983.6382 | DAILY | 00023972 | VEN_AUG | Line outage to diconnect CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1024483138983.2840277778 | 10244831 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 38983.284 | 38983.6153 | REPDAILY | 00026099 | SPIMAINT | investigate/repair leaking transformer | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025248138983.7229166667 | 10252481 |  | Parent | FALSE | H1 TRANS NO.2 BUS 330KV CB AT DDTS | 38983.7229 | 38986.5042 | CONT | [12 empty] | 0
_X51358A438984.3131944445 | X51358A4 |  | Parent | FALSE | NO.2 66KV BUS AT BLTS | 38984.3132 | 38984.6035 | DAILY | 00002650 | SPICAPX | bus o.o.s. to install new tie tr connections | SPIPOWER | X513 | X513 - (BLTS) REPLACE 66/22KV TIE TRANSFORMER | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010239638985.2840277778 | 10102396 |  | Parent | FALSE | NO.1 66KV BUS AT TBTS | 38985.284 | 38985.6257 | DAILY | 00004907 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1005569838985.2923611111 | 10055698 |  | Parent | TRUE | S216 HWTS-SMTS 2 500KV | 38985.2924 | 38985.6556 | REPDAILY | [12 empty] | 0
_1025275738985.2923611111 | 10252757 | 10055698 | Child | FALSE | HWTS-SMTS 2 500KV G | 38985.2924 | 38985.6556 | REPDAILY | 00020242 | SPIMAINT | out for line defect repairs | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024510438985.2923611111 | 10245104 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB AT HWTS | 38985.2924 | 38989.6222 | CONT | [12 empty] | 0
_1025222138985.2930555556 | 10252221 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT TTS | 38985.2931 | 38985.5069 | DAILY | 00001485 | SPIMAINT | re-balance cap bank | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X33458C438985.3097222222 | X33458C4 |  | Parent | FALSE | B3 TRANS 66KV CB AT MWTS | 38985.3097 | 38985.4507 | DAILY | [12 empty] | 0
_1025255238985.5222222222 | 10252552 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 38985.5222 | 38985.5326 | DAILY | [12 empty] | 0
_1025258638986.2618055556 | 10252586 |  | Parent | TRUE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 38986.2618 | 38987.5097 | DAILY | 00007399 | FAULT | No2 66kV cap bank tripping | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024422538986.2847222222 | 10244225 | X49058A9 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 38986.2847 | 38986.7528 | CONT | 00352121 | SPICAPX | Out W/O Replace CT's marshalling box and conductor | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X49058A938986.2847222222 | X49058A9 |  | Parent | TRUE | H2 TRANS 330KV CB AT DDTS | 38986.2847 | 38986.7528 | REPDAILY | [12 empty] | 0
_1010239838986.2854166667 | 10102398 |  | Parent | FALSE | B1 TRANS 220KV CB AT TBTS | 38986.2854 | 38986.6306 | DAILY | [12 empty] | 0
_1005569838986.2951388889 | 10055698 |  | Parent | TRUE | S216 HWTS-SMTS 2 500KV | 38986.2951 | 38986.6806 | REPDAILY | [12 empty] | 0
_1025275738986.2951388889 | 10252757 | 10055698 | Child | FALSE | HWTS-SMTS 2 500KV G | 38986.2951 | 38986.6806 | REPDAILY | 00020242 | SPIMAINT | out for line defect repairs | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858M538986.2965277778 | X2A858M5 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK AT BTS | 38986.2965 | 38986.484 | DAILY | 00337002 | SPICAPX | prep work for decommission & relocation | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025222538986.3104166667 | 10252225 |  | Parent | FALSE | TSTS 220KV LINE NO.1 BUS CB AT TTS | 38986.3104 | 38986.4292 | DAILY | [12 empty] | 0
_1025250238986.3131944445 | 10252502 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB AT HWTS | 38986.3132 | 38989.6222 | CONT | [12 empty] | 0
_1010277338986.3166666667 | 10102773 |  | Parent | FALSE | NO.4 220KV BUS AT HWPS | 38986.3167 | 38986.4583 | CONT | 00009661 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1025222838986.4298611111 | 10252228 |  | Parent | TRUE | EX - SMTS NO.1 220KV LINE CB AT TTS | 38986.4299 | 38986.5938 | DAILY | [12 empty] | 0
_1025275838986.4298611111 | 10252758 | 10252228 | Child | FALSE | SMTS NO.1 220KV LINE AT TTS | 38986.4299 | 38986.5938 | DAILY | 00015732 | SPIMAINT | reclose lockout relay leaking | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025276038986.4298611111 | 10252760 | 10252228 | Child | FALSE | H1 330/220KV TRANS BANK AT SMTS | 38986.4299 | 38986.5938 | DAILY | 00026101 | SPIMAINT | reclose lockout relay leaking | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X2A858M638986.4840277778 | X2A858M6 |  | Parent | FALSE | NO.3 22KV CAPACITOR BANK AT BTS | 38986.484 | 38986.6069 | DAILY | 00337011 | SPICAPX | prep work for decommission & relocation | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025259138986.5083333333 | 10252591 |  | Parent | TRUE | 4-6 220KV BUS TIE CB NO.6 BUS SIDE ISOL AT HWPS | 38986.5083 | 38986.6118 | DAILY | [12 empty] | 0
_1025259238986.5083333333 | 10252592 | 10252591 | Child | FALSE | YPS NO.1 220KV LINE AT HWPS | 38986.5083 | 38986.6118 | DAILY | 00015795 | SPIMAINT | Rebate for No 6 Bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024516938987.2604166667 | 10245169 | X46158I5 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 38987.2604 | 38987.6743 | DAILY | 00331109 | SPICAPX | Rebate W/O No1 Cap bank during 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X46158I538987.2604166667 | X46158I5 |  | Parent | TRUE | NO.1 66KV BUS AT BATS | 38987.2604 | 38987.6743 | DAILY | 00006560 | SPICAPX | Out W/O No1 66kV Bus to install new bus VT | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010239738987.2895833333 | 10102397 |  | Parent | TRUE | NO.2 66KV BUS AT TBTS | 38987.2896 | 38987.6146 | DAILY | 00004908 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024510238987.2895833333 | 10245102 | 10102397 | Child | FALSE | B2 220/66KV TRANS AT TBTS | 38987.2896 | 38987.6146 | DAILY | 00004902 | SPIMAINT | Avail of plant for No2 66 bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1005569838987.2923611111 | 10055698 |  | Parent | TRUE | S216 HWTS-SMTS 2 500KV | 38987.2924 | 38987.6354 | REPDAILY | [12 empty] | 0
_1025275738987.2923611111 | 10252757 | 10055698 | Child | FALSE | HWTS-SMTS 2 500KV G | 38987.2924 | 38987.6354 | REPDAILY | 00020242 | SPIMAINT | out for line defect repairs | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025258838987.3131944445 | 10252588 | 10252586 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 38987.3132 | 38987.5097 | DAILY | 00331179 | SPIMAINT | Reabte while fixing No2 66kV cap bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010277338987.3166666667 | 10102773 |  | Parent | FALSE | NO.4 220KV BUS AT HWPS | 38987.3167 | 38989.5792 | CONT | 00009661 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1025264538987.5722222222 | 10252645 |  | Parent | FALSE | EX - A4 TRANS NO.1 BUS 500KV CB AT KTS | 38987.5722 | 38987.6056 | DAILY | [12 empty] | 0
_X49058B038988.2930555556 | X49058B0 |  | Parent | FALSE | MSS NO.2 330KV LINE NO.2 BUS CB AT DDTS | 38988.2931 | 38989.65 | CONT | [12 empty] | 0
_1005569838988.2958333333 | 10055698 |  | Parent | TRUE | S216 HWTS-SMTS 2 500KV | 38988.2958 | 38988.6403 | REPDAILY | [12 empty] | 0
_1025275738988.2958333333 | 10252757 | 10055698 | Child | FALSE | HWTS-SMTS 2 500KV G | 38988.2958 | 38988.6403 | REPDAILY | 00020242 | SPIMAINT | out for line defect repairs | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010386038988.3083333333 | 10103860 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 38988.3083 | 38988.6694 | REPDAILY | [12 empty] | 0
_X2A858M438988.3361111111 | X2A858M4 |  | Parent | FALSE | EX - 1-2 22KV BUS TIE CB AT BTS | 38988.3361 | 38988.6872 | DAILY | [12 empty] | 0
_V4S258E038988.6354166667 | V4S258E0 |  | Parent | FALSE | NO.2 500KV BUS AT SMTS | 38988.6354 | 39002.5972 | CONT | 00001329 | SPIMAINT | inject silicone to prepare flanges & replace seals | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Bus | Western | 500 |  |  |  | 0
_1025270938989.2916666667 | 10252709 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 38989.2917 | 38989.316 | CONT | [12 empty] | 0
_1005569838989.2916666667 | 10055698 |  | Parent | TRUE | S216 HWTS-SMTS 2 500KV | 38989.2917 | 38989.5389 | REPDAILY | [12 empty] | 0
_1025275738989.2916666667 | 10252757 | 10055698 | Child | FALSE | HWTS-SMTS 2 500KV G | 38989.2917 | 38989.5389 | REPDAILY | 00020242 | SPIMAINT | out for line defect repairs | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010386038989.3180555556 | 10103860 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 38989.3181 | 38989.6806 | REPDAILY | [12 empty] | 0
_Z33458G138990.3020833333 | Z33458G1 |  | Parent | TRUE | B4 220/66KV TRANS AT SVTS | 38990.3021 | 38990.5917 | DAILY | 00352791 | VEN_AUG | VRR commissioning on B4 & B3 B2 & B1 Transformer | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z33458G338990.3020833333 | Z33458G3 | Z33458G1 | Child | FALSE | B3 220/66KV TRANS AT SVTS | 38990.3021 | 38990.5917 | DAILY | 00004851 | VEN_AUG | VRR commissioning on B3 & B4 Transformer | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V4S258E338990.4375 | V4S258E3 |  | Parent | FALSE | ROTS NO.3 500KV LINE AT SMTS | 38990.4375 | 38990.4743 | DAILY | 00012438 | SPIMAINT | erect weather protection over no.2 500kv bus | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025242138990.6673611111 | 10252421 |  | Parent | FALSE | LYBPS NO.1 500KV LINE AT LYPS | 38990.6674 | 39025.7797 | CONT | 00023074 | GENCO | Genco work. | GENCO |  |  | Circuits | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_Z33458G238991.3090277778 | Z33458G2 |  | Parent | TRUE | B1 220/66KV TRANS AT SVTS | 38991.309 | 38991.5917 | DAILY | 00004849 | VEN_AUG | VRR commissioning on B2 & B1 Transformer | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z33458G438991.3090277778 | Z33458G4 | Z33458G2 | Child | FALSE | B2 220/66KV TRANS AT SVTS | 38991.309 | 38991.5917 | DAILY | 00004850 | VEN_AUG | VRR commissioning on B2 & B1 Transformer | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025275638991.5409722222 | 10252756 |  | Parent | TRUE | EX - KTS NO.1 220KV LINE CB AT GTS | 38991.541 | 38991.5472 | DAILY | [12 empty] | 0
_1025276738991.5409722222 | 10252767 | 10252756 | Child | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 38991.541 | 38991.5472 | DAILY | 00017900 | FORCED | GTS-KTS 220kv Line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025276438991.6347222222 | 10252764 |  | Parent | FALSE | SYN/COND AT BLTS | 38991.6347 | 38991.6667 | DAILY | 00002547 | FAULT | S/C AVR | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X2A858N338992.5034722222 | X2A858N3 |  | Parent | FALSE | L3 220/22KV TRANS 22KV CABLE AT BTS | 38992.5035 | 38997.6875 | DAILY | 00361092 | SPICAPX | hipot the new L3 Trans 220kv cables | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1025276938992.68125 | 10252769 |  | Parent | FALSE | NO.2 UNIT 230/10.5KV TRANS OLTC DIV/SW AT JLGB | 38992.6813 | 38996.8 | CONT | [12 empty] | 0
_X46158H438993.2701388889 | X46158H4 |  | Parent | FALSE | MLTS NO.2 220KV LINE AT BATS | 38993.2701 | 38996.2708 | CONT | 00012431 | SPICAPX | Out W/O MLTS 2 Line. Reposition h/string droppers | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010299238993.2715277778 | 10102992 |  | Parent | FALSE | MLTS NO.1 500KV LINE AT SYTS | 38993.2715 | 38993.7278 | REPDAILY | 00016969 | SPIMAINT | O/Haul - 500kV SYTS-MLTS 1 Line at SYTS | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53458A838993.2798611111 | Z53458A8 |  | Parent | FALSE | CBTS NO.4 500KV LINE AT ROTS (RTF) | 38993.2799 | 38993.5806 | DAILY | 00356730 | VEN_AUG | Adjust Line side isolator & E/SW | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010288938993.3152777778 | 10102889 |  | Parent | FALSE | A2 515/230KV TRANS BANK AT HWTS | 38993.3153 | 38996.6312 | CONT | 00337572 | SPIMAINT | O/HAUL Transformer & Line equipment | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009275838993.3180555556 | 10092758 |  | Parent | TRUE | JLA NO.2 220KV LINE AT TBTS | 38993.3181 | 38993.6965 | DAILY | 00026919 | SPIMAINT | O/Haul - JLA 2 Line CVTs at TBTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009282738993.3180555556 | 10092827 | 10092758 | Child | FALSE | JLA NO.2 220KV LINE CB LINE SIDE E/SW AT TBTS | 38993.3181 | 38993.6965 | DAILY | [12 empty] | 0
_1009283038993.3180555556 | 10092830 | 10092758 | Child | FALSE | JLA NO.2 220KV LINE E/SW AT TBTS | 38993.3181 | 38993.6965 | DAILY | [12 empty] | 0
_1009283238993.3180555556 | 10092832 | 10092758 | Child | FALSE | JLA NO.2 220KV LINE CB AT TBTS | 38993.3181 | 38993.6965 | DAILY | [12 empty] | 0
_1009283438993.3180555556 | 10092834 | 10092758 | Child | FALSE | JLA NO.2 220KV LINE CB LINE SIDE ISOL AT TBTS | 38993.3181 | 38993.6965 | DAILY | [12 empty] | 0
_X2A858N238993.3381944444 | X2A858N2 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK AT BTS | 38993.3382 | 38993.6465 | DAILY | 00337002 | SPICAPX | decommission no.1 22kv cao bank, cb esw & cable | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X41258B638993.4465277778 | X41258B6 |  | Parent | FALSE | GNTS NO.1 220KV LINE NO.2 BUS CB AT SHTS | 38993.4465 | 38999.4458 | CONT | [12 empty] | 0
_1025277538993.4618055556 | 10252775 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 38993.4618 | 38993.5757 | DAILY | 00003104 | SPIMAINT | Replace blown fuse | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X41258B938993.5131944444 | X41258B9 |  | Parent | FALSE | B3 TR 220 CB CONTROL/MONITOR RELAY T2E AT SHTS | 38993.5132 | 39006.3542 | CONT | [12 empty] | 0
_1025278138993.5784722222 | 10252781 |  | Parent | FALSE | HWTS NO.3 500KV LINE CB AT LYPS | 38993.5785 | 38993.6236 | REPDAILY | [12 empty] | 0
_X41258B738993.6118055556 | X41258B7 |  | Parent | FALSE | EX - DDTS 220KV LINE NO.2 BUS TIE LINE SIDE ISOL AT SHTS | 38993.6118 | 39013.3229 | CONT | [12 empty] | 0
_X41258B838993.6326388889 | X41258B8 |  | Parent | FALSE | FVTS/BETS 220KV LINE NO.2 BUS CB AT SHTS | 38993.6326 | 39021.2576 | CONT | [12 empty] | 0
_1010299238994.2708333333 | 10102992 |  | Parent | FALSE | MLTS NO.1 500KV LINE AT SYTS | 38994.2708 | 38994.6701 | REPDAILY | 00016969 | SPIMAINT | O/Haul - 500kV SYTS-MLTS 1 Line at SYTS | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z52958A038994.2916666667 | Z52958A0 |  | Parent | TRUE | NO.1 66KV BUS AT RTS | 38994.2917 | 38994.659 | DAILY | 00022323 | DB_AUG | No1 Bus & TK FDR for fdr upgrade | SPIPOWER | Z529 | Z529 - (RTS) UPRATE SUB TK 66KV FDR CONNECTION TO 1200A | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z52958A138994.2916666667 | Z52958A1 | Z52958A0 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RTS | 38994.2917 | 38994.659 | DAILY | 00007279 | DB_AUG | Rebate for No1 Bus & TK FDR for fdr upgrade | SPIPOWER | Z529 | Z529 - (RTS) UPRATE SUB TK 66KV FDR CONNECTION TO 1200A | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z52958A238994.2916666667 | Z52958A2 | Z52958A0 | Child | FALSE | B1 220/66KV TRANS AT RTS | 38994.2917 | 38994.659 | DAILY | 00007329 | DB_AUG | Avail of plant No1 Bus & TK FDR for fdr upgrade | SPIPOWER | Z529 | Z529 - (RTS) UPRATE SUB TK 66KV FDR CONNECTION TO 1200A | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A858N138994.3888888889 | X2A858N1 |  | Parent | FALSE | NO.3 22KV CAPACITOR BANK AT BTS | 38994.3889 | 38994.6729 | DAILY | 00337011 | SPICAPX | decommission no.3 22kv cao bank, cb esw & cable | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025219338995.2666666667 | 10252193 |  | Parent | FALSE | MLRC 220KV LINE AT RCTS | 38995.2667 | 38995.8042 | REPDAILY | 00352130 | 3RDPARTY | MLRC-RCTS Line | HVCUST |  |  | Circuits | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 3
_1025232738995.2680555556 | 10252327 |  | Parent | FALSE | EX - O.O.S 220/66KV TRANS BANK (9 SINGLE PHASE UNITS) AT TTS | 38995.2681 | 38996.6028 | CONT | 00026062 | SPIMAINT | top up trans bushings | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER | Out of Service | 0
_X49858A038995.2756944444 | X49858A0 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MBTS | 38995.2757 | 38995.7549 | REPDAILY | 00004002 | SPICAPX | Out W/O No2 220kV bus erect new ROI's etc | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49858A138995.2756944444 | X49858A1 | X49858A0 | Child | FALSE | B2 220/66KV TRANS AT MBTS | 38995.2757 | 38995.7549 | DAILY | 00362372 | SPICAPX | Perf calc W/O B2 Trans during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49858A238995.2756944444 | X49858A2 | X49858A0 | Child | FALSE | EX - DDTS NO.2 220KV LINE AT MBTS | 38995.2757 | 38995.7549 | DAILY | 00011750 | SPICAPX | Rebate W/O DDTS 2 Line during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858A338995.2756944444 | X49858A3 | X49858A0 | Child | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 38995.2757 | 38995.7549 | DAILY | 00011755 | SPICAPX | Rebate W/O MKPS Line during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858A438995.2756944444 | X49858A4 | X49858A0 | Child | FALSE | EX - EPS NO.2 220KV LINE AT MBTS | 38995.2757 | 38995.7549 | DAILY | 00011752 | SPICAPX | Rebate W/O EPS 2 Line during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49858A538995.2756944444 | X49858A5 | X49858A0 | Child | FALSE | WKPS 220KV LINE AT MBTS | 38995.2757 | 38995.7549 | DAILY | 00011756 | SPICAPX | Rebate W/O WKPS Line during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010371538995.2923611111 | 10103715 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT MLTS | 38995.2924 | 38995.7389 | DAILY | 00022778 | SPIMAINT | O/Haul - SYTS No.2 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458E938995.3590277778 | X38458E9 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38995.359 | 38995.6576 | DAILY | 00023231 | SPICAPX | Out W/O For work on Future No 1 Trans | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025282038995.3791666667 | 10252820 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 38995.3792 | 38995.4167 | DAILY | [12 empty] | 0
_X46158H538996.2708333333 | X46158H5 |  | Parent | FALSE | MLTS NO.2 220KV LINE AT BATS | 38996.2708 | 38996.9604 | DAILY | 00012431 | SPICAPX | Out W/O MLTS 2 Line. Commission its fut 2 Bus CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858A038996.2729166667 | X49858A0 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MBTS | 38996.2729 | 38996.6097 | REPDAILY | 00004002 | SPICAPX | Out W/O No2 220kV bus erect new ROI's etc | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49858A138996.2729166667 | X49858A1 | X49858A0 | Child | FALSE | B2 220/66KV TRANS AT MBTS | 38996.2729 | 38996.6097 | DAILY | 00362372 | SPICAPX | Perf calc W/O B2 Trans during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49858A238996.2729166667 | X49858A2 | X49858A0 | Child | FALSE | EX - DDTS NO.2 220KV LINE AT MBTS | 38996.2729 | 38996.6097 | DAILY | 00011750 | SPICAPX | Rebate W/O DDTS 2 Line during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858A338996.2729166667 | X49858A3 | X49858A0 | Child | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 38996.2729 | 38996.6097 | DAILY | 00011755 | SPICAPX | Rebate W/O MKPS Line during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858A438996.2729166667 | X49858A4 | X49858A0 | Child | FALSE | EX - EPS NO.2 220KV LINE AT MBTS | 38996.2729 | 38996.6097 | DAILY | 00011752 | SPICAPX | Rebate W/O EPS 2 Line during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49858A538996.2729166667 | X49858A5 | X49858A0 | Child | FALSE | WKPS 220KV LINE AT MBTS | 38996.2729 | 38996.6097 | DAILY | 00011756 | SPICAPX | Rebate W/O WKPS Line during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010216738996.2736111111 | 10102167 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE E/SW AT KTS | 38996.2736 | 38996.6757 | DAILY | [12 empty] | 0
_X43258G238996.2965277778 | X43258G2 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 38996.2965 | 39015.7806 | CONT | 00337581 | SPICAPX | Out W/O Replace No 1B TRANS 66kV CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X41258C138996.4541666667 | X41258C1 |  | Parent | FALSE | EX - NO.2 TRANS 220KV CB AT SHTS | 38996.4542 | 38996.7257 | DAILY | [12 empty] | 0
_1025287938996.6909722222 | 10252879 |  | Parent | FALSE | LNGS NO.1 GEN TRANS 220KV CB TRANS SIDE ROI AT ATS | 38996.691 | 39004.538 | CONT | [12 empty] | 0
_1025285638996.8020833333 | 10252856 |  | Parent | FALSE | NO.3 UNIT 230/10.5KV TRANS AT JLGB | 38996.8021 | 39001.3514 | CONT | 00009832 | GENCO | SCAP JLGS B3 Unit Trans Isol'd & earthed | GENCO |  |  | Connection Transformers | Eastern | 220 |  |  |  | 0
_1025291538997.2506944445 | 10252915 |  | Parent | FALSE | TTS NO.3 220KV LINE AT BTS | 38997.2507 | 38997.7132 | CONT | 00015959 | SPICAPX | TTS No3 220kV Line Outage | SPIPOWER |  | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858N638997.2506944445 | X2A858N6 |  | Parent | FALSE | NO.3 220KV BUS AT BTS | 38997.2507 | 38997.7132 | REPDAILY | 00000944 | SPICAPX | Connect L3 Trans to No2 220kv bus. | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Bus | Western | 220 |  |  |  | 0
_X46158I638997.2743055556 | X46158I6 |  | Parent | FALSE | BETS 220KV LINE AT BATS | 38997.2743 | 38997.6958 | CONT | 00012434 | SPICAPX | Out W/O BETS Line to decomm its 2B CB & equip | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158H638997.2819444445 | X46158H6 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 38997.2819 | 38997.6993 | DAILY | 00006559 | SPICAPX | Out W/O No2 220kV Bus. Decomm BETS L 2B equip | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158H738997.2819444445 | X46158H7 | X46158H6 | Child | FALSE | BETS 220KV LINE AT BATS | 38997.2819 | 38997.6993 | DAILY | 00012434 | SPICAPX | Rebate W/O BETS Line to decomm its 2B CB & equip | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158H838997.2819444445 | X46158H8 | X46158H6 | Child | FALSE | WBTS 220KV LINE AT BATS | 38997.2819 | 38997.6993 | DAILY | 00012410 | SPICAPX | Rebate W/O HOTS Line during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158H938997.2819444445 | X46158H9 | X46158H6 | Child | FALSE | B1 220/66KV TRANS AT BATS | 38997.2819 | 38997.6993 | DAILY | 00006554 | SPICAPX | Perf calc W/O No1 Trans during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458F038997.3458333333 | X38458F0 |  | Parent | TRUE | EX - NO.1 66KV BUS AT TGTS | 38997.3458 | 38997.7278 | REPDAILY | 00003132 | SPICAPX | x4615816 | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458F138997.3458333333 | X38458F1 | X38458F0 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38997.3458 | 38997.7278 | REPDAILY | 00023231 | SPICAPX | Out W/O Perf calc for 66 bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009733938997.5256944444 | 10097339 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 38997.5257 | 38997.7424 | REPDAILY | 00002863 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X2A858N538997.6875 | X2A858N5 |  | Parent | FALSE | L3 220/22KV TRANS AT BTS | 38997.6875 | 39004.2556 | CONT | 00360871 | SPICAPX | connect L3 Transformer | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009733938998.2708333333 | 10097339 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 38998.2708 | 38998.7014 | REPDAILY | 00002863 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X2A858N838998.2840277778 | X2A858N8 |  | Parent | FALSE | TTS NO.3 220KV LINE AT BTS | 38998.284 | 38998.5021 | REPDAILY | 00015959 | SPICAPX | decommission old TTS3 Line Prot | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458F038998.3159722222 | X38458F0 |  | Parent | TRUE | EX - NO.1 66KV BUS AT TGTS | 38998.316 | 38998.659 | REPDAILY | 00003132 | SPICAPX | x4615816 | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458F138998.3159722222 | X38458F1 | X38458F0 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 38998.316 | 38998.659 | REPDAILY | 00023231 | SPICAPX | Out W/O Perf calc for 66 bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009733938999.2701388889 | 10097339 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 38999.2701 | 38999.7076 | REPDAILY | 00002863 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025207838999.2736111111 | 10252078 |  | Parent | FALSE | DDTS NO.2 330KV LINE AT SMTS | 38999.2736 | 39001.6431 | CONT | 00012750 | SPIMAINT | complete o/h on the ddts no.2 330kv line equip | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X41258C238999.2784722222 | X41258C2 |  | Parent | FALSE | EX - GNTS NO.1 220KV LINE AT SHTS | 38999.2785 | 39003.5049 | CONT | 00000812 | SPICAPX | OUT W/O GNTS 1 Line. Commiss 2B CB | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010227438999.3027777778 | 10102274 | 10102362 | Child | FALSE | NO.1 220KV CAPACITOR BANK CB BUS SIDE E/SW AT TSTS | 38999.3028 | 39000.6236 | CONT | [12 empty] | 0
_1010227538999.3027777778 | 10102275 | 10102362 | Child | FALSE | NO.1 220KV CAPACITOR BANK CB BUS SIDE ROI AT TSTS | 38999.3028 | 39000.6236 | CONT | [12 empty] | 0
_1010236238999.3027777778 | 10102362 |  | Parent | TRUE | NO.1 220KV BUS AT TSTS | 38999.3028 | 39000.6236 | CONT | 00007670 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010237038999.3027777778 | 10102370 | 10102362 | Child | FALSE | NO.1 TRANS NO.1 BUS 220KV CB BUS SIDE E/SW AT TSTS | 38999.3028 | 39000.6236 | CONT | [12 empty] | 0
_1010237138999.3027777778 | 10102371 | 10102362 | Child | FALSE | NO.1 220KV BUS E/SW AT TSTS | 38999.3028 | 39000.6236 | CONT | [12 empty] | 0
_1010237238999.3027777778 | 10102372 | 10102362 | Child | FALSE | NO.2 TRANS 220KV E/SW AT TSTS | 38999.3028 | 39000.6236 | CONT | [12 empty] | 0
_1010238538999.3027777778 | 10102385 | 10102362 | Child | FALSE | NO.1 TRANS NO.1 BUS 220KV CB BUS SIDE ROI AT TSTS | 38999.3028 | 39000.6236 | CONT | [12 empty] | 0
_1010238638999.3027777778 | 10102386 | 10102362 | Child | FALSE | NO.2 TRANS 220KV ROI AT TSTS | 38999.3028 | 39000.6236 | CONT | [12 empty] | 0
_1010238838999.3027777778 | 10102388 | 10102362 | Child | FALSE | ROTS 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT TSTS | 38999.3028 | 39000.6236 | CONT | [12 empty] | 0
_1010239438999.3027777778 | 10102394 | 10102362 | Child | FALSE | ROTS LINE NO.1 BUS CB BUS SIDE ROI AT TSTS | 38999.3028 | 39000.6236 | CONT | [12 empty] | 0
_1025209038999.3027777778 | 10252090 | 10102362 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT TSTS | 38999.3028 | 39000.6236 | CONT | 00329164 | SPIMAINT | Rebate for bus outage | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025209238999.3027777778 | 10252092 | 10102362 | Child | FALSE | B2 220/66KV TRANS AT TSTS | 38999.3028 | 39000.6236 | CONT | 00007658 | SPIMAINT | Avail of plsnt for bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010289038999.3034722222 | 10102890 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 38999.3035 | 39000.6319 | CONT | 00337579 | SPIMAINT | O/HAUL Transformer without Div Sw (EH) | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_P70358A938999.31875 | P70358A9 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 38999.3187 | 39001.4604 | CONT | 00354024 | VEN_AUG | Modify Cap bank Auto Voltage Controls | SPIPOWER | P703 | P703 - (ATS,BETS,DDTS,MLTS,ROTS,TBTS,TSTS) SHUNT CAP BANKS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49758A338999.3284722222 | X49758A3 |  | Parent | TRUE | NO.4 66KV BUS EXTENSION AT BETS | 38999.3285 | 39017.6292 | CONT | 00016369 | SPICAPX | Out W/O No4 66kV bus ext & 2AB Cap CB reposition | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 66 |  |  |  | 0
_X49758A438999.3284722222 | X49758A4 | X49758A3 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT BETS | 38999.3285 | 39017.6292 | CONT | 00350819 | SPICAPX | Rebate W/O 2A Cap bank for 2AB Cap CB reposition | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49758A538999.3284722222 | X49758A5 | X49758A3 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 38999.3285 | 39017.6292 | CONT | 00016274 | SPICAPX | Rebate W/O 2B Cap bank for 2AB Cap CB reposition | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258E838999.3423611111 | X43258E8 |  | Parent | TRUE | NO.2 22KV BUS AT RCTS | 38999.3424 | 38999.7694 | REPDAILY | 00016998 | SPICAPX | Out W/O To replace copper bus on No 2 22kV Bus | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258E938999.3423611111 | X43258E9 | X43258E8 | Child | FALSE | NO.2 22KV CAPACITOR BANK AT RCTS | 38999.3424 | 38999.7694 | REPDAILY | 00016713 | SPICAPX | Out W/O Perf calc for No 2 22kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258F038999.3423611111 | X43258F0 | X43258E8 | Child | FALSE | NO.2A TRANS AT RCTS | 38999.3424 | 38999.7694 | REPDAILY | 00016759 | SPICAPX | Out W/O Perf calc for 22kV only No 2 22 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258F138999.3423611111 | X43258F1 | X43258E8 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 38999.3424 | 38999.7694 | REPDAILY | 00361128 | SPICAPX | Out W/O Perf calc for 22kV only No 2 22 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1025288538999.3555555556 | 10252885 |  | Parent | FALSE | EX - NO.2 MAIN TRANS 500KV CB AT HWTS | 38999.3556 | 38999.5896 | DAILY | [12 empty] | 0
_1025179338999.4576388889 | 10251793 |  | Parent | FALSE | BTS -RTS 220KV W (BTS to Joint Bay 7) (CABLE) | 38999.4576 | 39003.5799 | CONT | 00310401 | EXCLUDE | BTS - RTS 220kV Cable Out of Commission | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025294839000.0076388889 | 10252948 |  | Parent | TRUE | NO.3 66KV BUS AT ERTS | 39000.0076 | 39000.0764 | DAILY | 00004383 | FAULT | No 3 66kV Bus Trip | SPIPOWER |  |  | Bus | Eastern | 66 |  |  |  | 0
_1025294939000.0076388889 | 10252949 | 10252948 | Child | FALSE | B3 220/66KV TRANS AT ERTS | 39000.0076 | 39000.0764 | DAILY | 00004371 | FAULT | No 3 66kV Bus Trip (Cap Bank CB explosive Failure) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025295039000.0076388889 | 10252950 |  | Parent | TRUE | NO.3 66KV CAPACITOR BANK CB AT ERTS | 39000.0076 | 39034.609 | CONT | [12 empty] | 0
_1025425539000.0076388889 | 10254255 | 10252950 | Child | FALSE | NO.3 66KV CAPACITOR BANK AT ERTS | 39000.0076 | 39034.609 | CONT | 00087144 | FAULT | Cap CB Failure | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1009733939000.2722222222 | 10097339 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39000.2722 | 39000.7083 | REPDAILY | 00002863 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X49058C039000.2729166667 | X49058C0 |  | Parent | FALSE | DDTS-GNTS 3 220KV NW | 39000.2729 | 39000.7104 | DAILY | 00060186 | SPICAPX | Out W/O Replace CT's and conductor on CB | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258E839000.3013888889 | X43258E8 |  | Parent | TRUE | NO.2 22KV BUS AT RCTS | 39000.3014 | 39000.8347 | REPDAILY | 00016998 | SPICAPX | Out W/O To replace copper bus on No 2 22kV Bus | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258E939000.3013888889 | X43258E9 | X43258E8 | Child | FALSE | NO.2 22KV CAPACITOR BANK AT RCTS | 39000.3014 | 39000.8347 | REPDAILY | 00016713 | SPICAPX | Out W/O Perf calc for No 2 22kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258F039000.3013888889 | X43258F0 | X43258E8 | Child | FALSE | NO.2A TRANS AT RCTS | 39000.3014 | 39000.8347 | REPDAILY | 00016759 | SPICAPX | Out W/O Perf calc for 22kV only No 2 22 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258F139000.3013888889 | X43258F1 | X43258E8 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 39000.3014 | 39000.8347 | REPDAILY | 00361128 | SPICAPX | Out W/O Perf calc for 22kV only No 2 22 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X49058C339000.7104166667 | X49058C3 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.1 BUS CB AT DDTS | 39000.7104 | 39001.291 | CONT | [12 empty] | 0
_1009733939001.2743055556 | 10097339 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39001.2743 | 39001.6882 | REPDAILY | 00002863 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1010236339001.2875 | 10102363 |  | Parent | TRUE | NO.2 220KV BUS AT TSTS | 39001.2875 | 39001.6229 | DAILY | 00007671 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010236939001.2875 | 10102369 | 10102363 | Child | FALSE | TTS 220KV LINE NO.2 BUS CB BUS SIDE E/SW AT TSTS | 39001.2875 | 39001.6229 | DAILY | [12 empty] | 0
_1010237339001.2875 | 10102373 | 10102363 | Child | FALSE | NO.2 220KV BUS E/SW AT TSTS | 39001.2875 | 39001.6229 | DAILY | [12 empty] | 0
_1010237439001.2875 | 10102374 | 10102363 | Child | FALSE | NO.3 TRANS 220KV E/SW AT TSTS | 39001.2875 | 39001.6229 | DAILY | [12 empty] | 0
_1010238139001.2875 | 10102381 | 10102363 | Child | FALSE | ROTS LINE NO.2 BUS CB BUS SIDE ROI AT TSTS | 39001.2875 | 39001.6229 | DAILY | [12 empty] | 0
_1010238439001.2875 | 10102384 | 10102363 | Child | FALSE | TTS LINE NO.2 BUS CB BUS SIDE ROI AT TSTS | 39001.2875 | 39001.6229 | DAILY | [12 empty] | 0
_1010238739001.2875 | 10102387 | 10102363 | Child | FALSE | NO.3 TRANS 220KV ROI AT TSTS | 39001.2875 | 39001.6229 | DAILY | [12 empty] | 0
_1010239239001.2875 | 10102392 | 10102363 | Child | FALSE | ROTS 220KV LINE NO.2 BUS CB BUS SIDE E/SW AT TSTS | 39001.2875 | 39001.6229 | DAILY | [12 empty] | 0
_1025209939001.2875 | 10252099 | 10102363 | Child | FALSE | B3 220/66KV TRANS AT TSTS | 39001.2875 | 39001.6229 | DAILY | 00007659 | SPIMAINT | Avail of plsnt for bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49058B539001.2909722222 | X49058B5 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.1 BUS CB AT DDTS | 39001.291 | 39002.709 | CONT | [12 empty] | 0
_X43258E839001.3083333333 | X43258E8 |  | Parent | TRUE | NO.2 22KV BUS AT RCTS | 39001.3083 | 39001.7486 | REPDAILY | 00016998 | SPICAPX | Out W/O To replace copper bus on No 2 22kV Bus | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258E939001.3083333333 | X43258E9 | X43258E8 | Child | FALSE | NO.2 22KV CAPACITOR BANK AT RCTS | 39001.3083 | 39001.7486 | REPDAILY | 00016713 | SPICAPX | Out W/O Perf calc for No 2 22kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258F039001.3083333333 | X43258F0 | X43258E8 | Child | FALSE | NO.2A TRANS AT RCTS | 39001.3083 | 39001.7486 | REPDAILY | 00016759 | SPICAPX | Out W/O Perf calc for 22kV only No 2 22 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258F139001.3083333333 | X43258F1 | X43258E8 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 39001.3083 | 39001.7486 | REPDAILY | 00361128 | SPICAPX | Out W/O Perf calc for 22kV only No 2 22 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1025297839001.3861111111 | 10252978 |  | Parent | FALSE | JLGA NO.2 UNIT TRANS DISC CB AT JLGA | 39001.3861 | 39002.6042 | CONT | [12 empty] | 0
_1025301139001.5354166667 | 10253011 |  | Parent | FALSE | A1 515/230KV TRANS AT HWTS | 39001.5354 | 39001.7889 | CONT | 00009772 | FAULT | Investigate Hot spot B Ph 220 Bushing connect's | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1010281939001.5784722222 | 10102819 |  | Parent | FALSE | NO.6 GEN TRANS NO.4 BUS 220KV CB TRANS SIDE ROI AT HWPS | 39001.5785 | 39018.3438 | DAILY | [12 empty] | 0
_Z53158C139002.2888888889 | Z53158C1 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 39002.2889 | 39003.3132 | CONT | 00004778 | VEN_AUG | Replace TTS Line CB Bus side isols | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158C939002.2888888889 | Z53158C9 | Z53158C1 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39002.2889 | 39003.3132 | CONT | 00112418 | VEN_AUG | Rebate work order for bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1009736039002.2930555556 | 10097360 |  | Parent | FALSE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39002.2931 | 39002.6986 | REPDAILY | [12 empty] | 0
_1025311139002.6055555556 | 10253111 |  | Parent | FALSE | ROTS NO.3 500KV LINE AT SMTS | 39002.6056 | 39002.6194 | DAILY | 00012438 | FORCED | ROTS-SMTS No 3 500kv Line | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025316639003.0097222222 | 10253166 |  | Parent | FALSE | NO.5 GEN 220/16.5KV TRANS AT HWPS | 39003.0097 | 39006.9042 | CONT | 00009646 | GENCO | Power Station requirement | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1025317439003.2833333333 | 10253174 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39003.2833 | 39008.8243 | CONT | 00356082 | GENCO | Generator 4 maintenance by Genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1009736039003.2944444444 | 10097360 |  | Parent | FALSE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39003.2944 | 39003.641 | REPDAILY | [12 empty] | 0
_Z53158C839003.3118055556 | Z53158C8 | Z53158E1 | Child | FALSE | TTS 220KV LINE AT ROTS | 39003.3118 | 39003.7806 | DAILY | 00023972 | VEN_AUG | Line outage to Reconnect No 2 CB diconnect 1 busCB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025297339003.5798611111 | 10252973 |  | Parent | FALSE | BTS -RTS 220KV W (BTS to Joint Bay 7) (CABLE) | 39003.5799 | 39003.6694 | DAILY | 00310401 | EXCLUDE | RTS-BTS 220kV LINE (Under Ground Cable) | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025321039003.6694444444 | 10253210 |  | Parent | FALSE | RTS 220KV LINE AT BTS | 39003.6694 | 39007.4028 | CONT | 00015960 | SPIMAINT | BTS Cable soaking | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858N739004.2555555556 | X2A858N7 |  | Parent | FALSE | L3 220/22KV TRANS AT BTS | 39004.2556 | 39004.6132 | REPDAILY | 00360871 | SPICAPX | commission new L3 Trans including on-loads | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009733839004.2902777778 | 10097338 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39004.2903 | 39004.6771 | REPDAILY | 00002862 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_V4S258E439004.3166666667 | V4S258E4 |  | Parent | FALSE | ROTS NO.3 500KV LINE AT SMTS | 39004.3167 | 39004.3854 | DAILY | 00012438 | SPIMAINT | dismantle weather protection over no.2 500kv bus | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009733839005.2722222222 | 10097338 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39005.2722 | 39005.6986 | REPDAILY | 00002862 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X516586039005.2826388889 | X5165860 |  | Parent | FALSE | B3 220/66KV TRANS AT RWTS | 39005.2826 | 39005.6083 | REPDAILY | 00007455 | SPICAPX | NO. 3 220/66KV TRANS REPLACE SD'S | SPIPOWER | X516 | X516 -(ATS,BLTS,ERTS,MWTS,RWTS) REPL 66KV EMP CMP60 SUR ARRS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009733839006.2694444444 | 10097338 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39006.2694 | 39006.7083 | REPDAILY | 00002862 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X41258C339006.2965277778 | X41258C3 |  | Parent | FALSE | B3 220/66KV TRANS AT SHTS | 39006.2965 | 39010.5153 | CONT | 00000842 | SPICAPX | OUT W/O No3 Trans to commiss its Fut 220kV 2B CB | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025282839006.3465277778 | 10252828 | X46158I7 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39006.3465 | 39006.6979 | DAILY | 00331118 | SPICAPX | Rebate W/O No2 Cap bank during 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025285739006.3465277778 | 10252857 | X46158I7 | Child | TRUE | B2 220/66KV TRANS AT BATS | 39006.3465 | 39006.6979 | DAILY | 00006555 | SPICAPX | Perf calc W/O No2 Trans 66 only during bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025285839006.3465277778 | 10252858 | 10252857 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39006.3465 | 39006.6979 | DAILY | 00331118 | SPICAPX | Rebate W/O No2 Cap bank during 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X46158I739006.3465277778 | X46158I7 |  | Parent | TRUE | NO.2 66KV BUS AT BATS | 39006.3465 | 39006.6979 | DAILY | 00006561 | SPICAPX | Out W/O No2 66kV Bus to remove bus VT | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025333439006.8118055556 | 10253334 |  | Parent | TRUE | L3 220/22KV TRANS AT WMTS | 39006.8118 | 39006.8708 | DAILY | 00003237 | FORCED | No 3 220/22kV Trans de-energised | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025333539006.8118055556 | 10253335 | 10253334 | Child | FALSE | B3 220/66KV TRANS AT WMTS | 39006.8118 | 39006.8708 | DAILY | 00003236 | FORCED | No 3 220/22kV Trans de-energised | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009733839007.2708333333 | 10097338 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39007.2708 | 39007.7118 | REPDAILY | 00002862 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025298739007.2743055556 | 10252987 |  | Parent | FALSE | B1 220/66KV TRANS AT WMTS | 39007.2743 | 39007.6299 | DAILY | 00003233 | SPIMAINT | low oil in w & b phase busshings & faulty fan | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010192639007.2791666667 | 10101926 |  | Parent | FALSE | SYN/COND AT BLTS | 39007.2792 | 39010.6042 | CONT | 00002547 | SPIMAINT | 3 Monthly O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010289039007.3104166667 | 10102890 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 39007.3104 | 39012.6111 | CONT | 00337579 | SPIMAINT | O/HAUL Transformer without Div Sw (EH) | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025297439007.3486111111 | 10252974 |  | Parent | FALSE | BTS -RTS 220KV W (BTS to Joint Bay 7) (CABLE) | 39007.3486 | 39032.3208 | DAILY | 00310401 | FAULT | Disconnect RTS-BTS 220kV LINE (Under Ground Cable) | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025334739007.4527777778 | 10253347 |  | Parent | FALSE | JLGA NO.3 UNIT TRANS DISC CB AT JLGA | 39007.4528 | 39009.597 | CONT | [12 empty] | 0
_V67758A939007.5076388889 | V67758A9 |  | Parent | FALSE | WMTS-FBTS 1 220KV WY | 39007.5076 | 39007.6556 | DAILY | 00022785 | SPIMAINT | Conductor Corrosion Survey | SPIPOWER | V677 | V677 - CORROSION MONITORING OF ACSR CONDUCTORS USING CORMON | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025337639007.975 | 10253376 |  | Parent | TRUE | NO.1 66KV BUS PROT AT HOTS | 39007.975 | 39008.0167 | DAILY | [12 empty] | 0
_1025422939007.975 | 10254229 | 10253376 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT HOTS | 39007.975 | 39008.0167 | DAILY | 00359898 | FAULT | HOTS No 1 66kV Bus trip | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025423039007.975 | 10254230 | 10253376 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HOTS | 39007.975 | 39008.0167 | DAILY | 00359901 | FAULT | HOTS No 1 66kV Bus trip | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025472739007.975 | 10254727 | 10253376 | Child | FALSE | EX - NO.1 TRANS BANK AT HOTS | 39007.975 | 39008.0167 | DAILY | 00026245 | FAULT | HOTS No 1 66kV Bus trip | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009733839008.2708333333 | 10097338 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39008.2708 | 39008.7063 | REPDAILY | 00002862 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X49058C139008.2715277778 | X49058C1 |  | Parent | FALSE | DDTS-GNTS 3 220KV NW | 39008.2715 | 39008.7417 | DAILY | 00060186 | SPICAPX | Out W/O Change CT's and reconductor CT to L/S isol | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025273339008.3138888889 | 10252733 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT HTS | 39008.3139 | 39008.5021 | DAILY | 00004426 | SPIMAINT | HTS: Cap Fault Alarm | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025280039008.3138888889 | 10252800 | 10252733 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT HTS | 39008.3139 | 39008.5021 | DAILY | 00004426 | SPIMAINT | Rebate due to 1A Cap Bank outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X38458F339008.35625 | X38458F3 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39008.3562 | 39008.4257 | DAILY | 00023231 | SPICAPX | Out W/O Install future Bph ROI in Bay A | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025295639008.4180555556 | 10252956 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39008.4181 | 39008.6444 | DAILY | 00017270 | SPIMAINT | SVC Inspection | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X38458F439008.4631944444 | X38458F4 |  | Parent | FALSE | EX - MLTS 220KV LINE NO.2 BUS CB AT TGTS | 39008.4632 | 39008.6062 | DAILY | [12 empty] | 0
_1025337839008.5041666667 | 10253378 |  | Parent | FALSE | EX - HWPS NO.3 220KV LINE NO.2 BUS CB AT JLTS | 39008.5042 | 39010.4924 | CONT | [12 empty] | 0
_1025423139008.6194444444 | 10254231 |  | Parent | FALSE | MPS-MWTS 220KV LINE AT HWPS | 39008.6194 | 39008.6264 | DAILY | 00015789 | FAULT | Trip of MWTS/MPS Line CB @ HWPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49058C539008.7416666667 | X49058C5 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.2 BUS CB AT DDTS | 39008.7417 | 39010.5764 | CONT | [12 empty] | 0
_Z53158E239009.2868055556 | Z53158E2 |  | Parent | FALSE | TTS 220KV LINE AT ROTS | 39009.2868 | 39009.9361 | DAILY | 00023972 | VEN_AUG | Line outage to Reconnect No 2 CB diconnect 1 busCB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025289539009.2958333333 | 10252895 |  | Parent | FALSE | EX - A3 TRANS 220KV CB AT KTS | 39009.2958 | 39009.6264 | DAILY | [12 empty] | 0
_1025305539009.3152777778 | 10253055 |  | Parent | FALSE | B2 220/66KV TRANS AT TBTS | 39009.3153 | 39009.6021 | DAILY | 00004902 | SPIMAINT | Temp indication problem Charge to 10228876 | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009735039009.3166666667 | 10097350 |  | Parent | FALSE | SESS NO.2 275KV LINE/M2 TRANS CB AT HYTS | 39009.3167 | 39009.6208 | REPDAILY | [12 empty] | 0
_X38458F739009.5416666667 | X38458F7 |  | Parent | FALSE | BATS 220KV LINE AT TGTS | 39009.5417 | 39009.5964 | DAILY | 00023130 | SPICAPX | Out W/O Close both Ties for on load tests | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49058B639009.7395833333 | X49058B6 |  | Parent | TRUE | GNTS NO.3 220KV LINE NO.2 BUS CB AT DDTS | 39009.7396 | 39010.5764 | CONT | [12 empty] | 0
_X49058B739009.7395833333 | X49058B7 | X49058B6 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 39009.7396 | 39010.5764 | DAILY | 00352121 | SPICAPX | Out W/O Perf calc for GNTS 3 L No 2 B CB outage | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025345039009.8993402778 | 10253450 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39009.8993 | 39012.4535 | CONT | 00356082 | GENCO | Isol for GENCO | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158A839010.2694444444 | Z53158A8 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39010.2694 | 39010.6944 | DAILY | 00004776 | VEN_AUG | Bus outage to remove bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158D039010.2694444444 | Z53158D0 | Z53158A8 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39010.2694 | 39010.6944 | DAILY | 00354024 | VEN_AUG | Rebate work order for bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49058C639011.2944444444 | X49058C6 |  | Parent | FALSE | MSS -DDTS 1 330KV NW | 39011.2944 | 39011.7194 | DAILY | 00060190 | SPICAPX | Out W/O Prepare founds for new SD's | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V67758B039011.3020833333 | V67758B0 |  | Parent | FALSE | KTS -BLTS 220KV WY | 39011.3021 | 39011.4646 | DAILY | 00022716 | SPIMAINT | Conductor Corrosion Survey | SPIPOWER | V677 | V677 - CORROSION MONITORING OF ACSR CONDUCTORS USING CORMON | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V67758B139011.4666666667 | V67758B1 |  | Parent | FALSE | KTS -GTS 2 220KV WY | 39011.4667 | 39011.6236 | DAILY | 00022705 | SPIMAINT | Conductor Corrosion Survey | SPIPOWER | V677 | V677 - CORROSION MONITORING OF ACSR CONDUCTORS USING CORMON | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025271439012.2826388889 | 10252714 |  | Parent | TRUE | NO.1 22KV BUS AT RWTS | 39012.2826 | 39012.6681 | DAILY | 00007482 | SPIMAINT | Protection work Trans & Bus No1 Bus isolated | SPIPOWER |  |  | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1025281139012.2826388889 | 10252811 | 10252714 | Child | FALSE | NO.1 22KV CAPACITOR BANK AT RWTS | 39012.2826 | 39012.6681 | DAILY | 00356999 | SPIMAINT | Rebate for Bus No1 Bus isolated | SPIPOWER |  |  | Capacitors | Eastern | 22 | CONNECTION ASSET | EXCLUDED |  | 0
_1025281339012.2826388889 | 10252813 | 10252714 | Child | FALSE | L2 220/22KV TRANS BANK AT RWTS | 39012.2826 | 39012.6681 | DAILY | 00007447 | SPIMAINT | Avail of plant for Bus No1 Bus isolated | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49058C739012.2965277778 | X49058C7 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39012.2965 | 39012.7125 | DAILY | 00060191 | SPICAPX | Out W/O Prepare founds for new SD's | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025348039012.9666666667 | 10253480 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39012.9667 | 39015.8917 | CONT | 00356082 | GENCO | No4 Gen Tran Line Isolated for HWPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49058B839013.25625 | X49058B8 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 39013.2562 | 39015.6868 | CONT | 00060194 | SPICAPX | Out W/O Replace MBTS No 2 LINE CB CT's | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010024839013.2708333333 | 10100248 |  | Parent | FALSE | SYN/COND AT TSTS | 39013.2708 | 39029.4826 | CONT | 00007626 | SPIMAINT | 5 Yearly O/HAUL - TSTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X41258C439013.2743055556 | X41258C4 |  | Parent | FALSE | EX - DDTS 220KV LINE AT SHTS | 39013.2743 | 39016.4486 | CONT | 00000811 | SPICAPX | OUT W/O DDTS Line to commiss its Fut 2B CB | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158I839013.2916666667 | X46158I8 |  | Parent | FALSE | WBTS 220KV LINE AT BATS | 39013.2917 | 39017.725 | CONT | 00012410 | SPICAPX | Out W/O HOTS Line to commiss its No1 Tie | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024016639013.2965277778 | 10240166 |  | Parent | FALSE | B3 220/66KV TRANS AT SVTS | 39013.2965 | 39014.6778 | CONT | 00004851 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area(W) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010276739013.3125 | 10102767 |  | Parent | TRUE | LYPS NO.2 500KV LINE E/SW AT HWTS | 39013.3125 | 39013.6382 | CONT | [12 empty] | 0
_1010277639013.3125 | 10102776 | 10102767 | Child | FALSE | LYPS NO.2 LINE/ROTS NO.3 LINE CB LYPS NO.2 LINE SIDE 500KV ROI AT HWTS | 39013.3125 | 39013.6382 | CONT | [12 empty] | 0
_V67758A039013.31875 | V67758A0 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT HWPS | 39013.3187 | 39013.5681 | DAILY | 00015790 | SPIMAINT | Corrosion Survey HWPS-ROTS 1 | SPIPOWER | V677 | V677 - CORROSION MONITORING OF ACSR CONDUCTORS USING CORMON | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025387039013.4909722222 | 10253870 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39013.491 | 39013.5868 | DAILY | 00003104 | FAULT | 1-2 220KV B/T CB fault | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025424539013.4909722222 | 10254245 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39013.491 | 39013.591 | DAILY | 00003104 | FAULT | TGTS 220kV Bus Tie Fault | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025424639013.4909722222 | 10254246 |  | Parent | FALSE | B2 220/66KV TRANS AT TGTS | 39013.491 | 39013.6764 | DAILY | 00003127 | FAULT | TGTS 220kV Bus Tie Fault | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025356639013.4909722222 | 10253566 |  | Parent | FALSE | MLTS-TGTS 220KV W | 39013.491 | 39013.6778 | DAILY | 00022740 | FAULT | MLTS Line outage due to TGTS Bus Tie Fault | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025424739013.4909722222 | 10254247 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39013.491 | 39013.7618 | DAILY | 00023231 | FAULT | TGTS 220kV Bus Tie Fault | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025431639013.4909722222 | 10254316 |  | Parent | FALSE | BATS-TGTS 220KV WW | 39013.491 | 39014.3764 | CONT | 00022665 | FAULT | 220kV B/t fault outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025347639013.5152777778 | 10253476 |  | Parent | FALSE | LNGS NO.1 GEN TRANS 220KV CB AT ATS | 39013.5153 | 39017.584 | CONT | [12 empty] | 0
_1025350939013.7097222222 | 10253509 |  | Parent | FALSE | EX - NO.1 220KV BUS AT TGTS | 39013.7097 | 39014.7625 | DAILY | 00003130 | SPIMAINT | Remove Damage Section or Clean | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025424939013.8895833333 | 10254249 |  | Parent | FALSE | HWTS NO.3 500KV LINE AT LYPS | 39013.8896 | 39014.3153 | CONT | 00016088 | FORCED | CB SF6 Low Alarm | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V64358A039014.2805555556 | V64358A0 |  | Parent | FALSE | KTS 500KV LINE AT SYTS | 39014.2806 | 39014.6743 | REPDAILY | 00016967 | SPIMAINT | fit new isolator switch mech & motors | SPIPOWER | V673 | V673 - (SYTS) REPLC ISOL & E/SW MOTORS & CAMS (6 MECH TRIAL) | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V67758A139014.2930555556 | V67758A1 |  | Parent | FALSE | YPS NO.1 220KV LINE AT HWPS | 39014.2931 | 39014.4646 | DAILY | 00015795 | SPIMAINT | Corrosion Survey HWPS-YPS 1 | SPIPOWER | V677 | V677 - CORROSION MONITORING OF ACSR CONDUCTORS USING CORMON | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025274639014.3090277778 | 10252746 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39014.309 | 39014.6903 | REPDAILY | [12 empty] | 0
_1025342839014.3131944445 | 10253428 |  | Parent | FALSE | B3 220/66KV TRANS AT WMTS | 39014.3132 | 39014.5687 | DAILY | 00003236 | SPIMAINT | repair faulty fan | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009274939014.3152777778 | 10092749 |  | Parent | FALSE | HWTS NO.3 500KV LINE AT LYPS | 39014.3153 | 39015.6382 | CONT | 00016088 | SPIMAINT | O/Haul - Line SDs (EH) Replace seals in CB | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025356539014.3763888889 | 10253565 |  | Parent | FALSE | BATS-TGTS 220KV WW | 39014.3764 | 39014.7618 | CONT | 00022665 | FAULT | BATS Line outage due to TGTS Bus Tie Fault | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025357339014.7236111111 | 10253573 |  | Parent | FALSE | EX - 1-2 220KV BUS TIE CB AT TGTS | 39014.7236 | 39021.5447 | CONT | [12 empty] | 0
_V64358A039015.2791666667 | V64358A0 |  | Parent | FALSE | KTS 500KV LINE AT SYTS | 39015.2792 | 39015.6743 | REPDAILY | 00016967 | SPIMAINT | fit new isolator switch mech & motors | SPIPOWER | V673 | V673 - (SYTS) REPLC ISOL & E/SW MOTORS & CAMS (6 MECH TRIAL) | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V67758A239015.2944444444 | V67758A2 |  | Parent | FALSE | ROTS NO.5 220KV LINE AT YPS | 39015.2944 | 39015.5625 | DAILY | 00016413 | SPIMAINT | Corrosion Survey YPS-ROTS 5 | SPIPOWER | V677 | V677 - CORROSION MONITORING OF ACSR CONDUCTORS USING CORMON | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025274639015.3138888889 | 10252746 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39015.3139 | 39015.6882 | REPDAILY | [12 empty] | 0
_V65558A039015.3277777778 | V65558A0 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB AT HWTS | 39015.3278 | 39015.5319 | DAILY | [12 empty] | 0
_1025335339015.3277777778 | 10253353 |  | Parent | FALSE | EX - SYTS LINE/A4 TRANS 500KV CB AT KTS | 39015.3278 | 39015.6014 | DAILY | [12 empty] | 0
_V65558A139015.3479166667 | V65558A1 |  | Parent | FALSE | A2 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39015.3479 | 39015.5958 | DAILY | [12 empty] | 0
_1025357439015.3923611111 | 10253574 |  | Parent | FALSE | EX - 1-2 220KV BUS TIE CB AT TGTS | 39015.3924 | 39017.4167 | DAILY | [12 empty] | 0
_X43258G839015.5833333333 | X43258G8 |  | Parent | FALSE | EX - NO.1A/1B 220/66/22KV TRANS X PROT AT RCTS | 39015.5833 | 39015.7806 | DAILY | [12 empty] | 0
_1009281339016.2256944444 | 10092813 |  | Parent | FALSE | JLTS NO.3 220KV LINE LINE ROI AT HWPS | 39016.2257 | 39017.6806 | DAILY | [12 empty] | 0
_V64358A139016.2722222222 | V64358A1 |  | Parent | FALSE | SMTS NO.1 500KV LINE AT SYTS | 39016.2722 | 39016.6514 | REPDAILY | 00016971 | SPIMAINT | fit new isolator & earth switch motors | SPIPOWER | V673 | V673 - (SYTS) REPLC ISOL & E/SW MOTORS & CAMS (6 MECH TRIAL) | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158A939016.2722222222 | Z53158A9 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39016.2722 | 39016.6535 | CONT | 00004776 | VEN_AUG | Bus outage to remove bus bi pods HWPS No1 Line CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158G039016.2722222222 | Z53158G0 | Z53158A9 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39016.2722 | 39016.6535 | CONT | 00354024 | VEN_AUG | Rebate to remove bus bi pods HWPS No1 Line CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1025274639016.3256944444 | 10252746 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39016.3257 | 39016.5958 | REPDAILY | [12 empty] | 0
_1025335139016.3326388889 | 10253351 |  | Parent | FALSE | EX - A4 TRANS NO.1 BUS 500KV CB AT KTS | 39016.3326 | 39016.625 | DAILY | [12 empty] | 0
_V67758A439016.4166666667 | V67758A4 |  | Parent | FALSE | HTS NO.1 220KV LINE AT SVTS | 39016.4167 | 39016.6958 | DAILY | 00351703 | SPIMAINT | Corrosion Survey SVTS-HTS | SPIPOWER | V677 | V677 - CORROSION MONITORING OF ACSR CONDUCTORS USING CORMON | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49058D039016.5347222222 | X49058D0 |  | Parent | FALSE | DDTS-GNTS 3 220KV NW | 39016.5347 | 39018.6007 | CONT | 00060186 | SPICAPX | Out W/O Remove redundant line traps and structures | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025339639016.5527777778 | 10253396 |  | Parent | FALSE | LY NO.4 66KV FDR NO.3 BUS CB AT MWTS | 39016.5528 | 39016.6139 | DAILY | [12 empty] | 0
_1025361339016.6340277778 | 10253613 |  | Parent | TRUE | H2 TRANS 220KV CB AT DDTS | 39016.634 | 39016.7299 | DAILY | [12 empty] | 0
_1025362039016.6340277778 | 10253620 | 10253613 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 39016.634 | 39016.7299 | DAILY | 00352121 | SPIMAINT | Rebate W/O No2 Trans for 220kV CB bushing top up | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025387639017.0347222222 | 10253876 |  | Parent | FALSE | SYN/COND AT BLTS | 39017.0347 | 39017.0618 | DAILY | 00002547 | FAULT | Syn Con AVR to manual | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V64358A139017.2729166667 | V64358A1 |  | Parent | FALSE | SMTS NO.1 500KV LINE AT SYTS | 39017.2729 | 39017.6472 | REPDAILY | 00016971 | SPIMAINT | fit new isolator & earth switch motors | SPIPOWER | V673 | V673 - (SYTS) REPLC ISOL & E/SW MOTORS & CAMS (6 MECH TRIAL) | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025334239017.3229166667 | 10253342 |  | Parent | FALSE | NO.1 330KV CAPACITOR BANK AT DDTS | 39017.3229 | 39017.4201 | DAILY | 00352085 | SPICAPX | Out W/o Spray weeds of cap bank enclosure | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_1025361239017.3625 | 10253612 |  | Parent | TRUE | EX - NO.1 220KV BUS AT TGTS | 39017.3625 | 39017.6493 | DAILY | 00003130 | SPIMAINT | Out W/O No1 220kV BUS - CT oil samples | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025361439017.3625 | 10253614 | 10253612 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39017.3625 | 39017.6493 | DAILY | 00023231 | SPIMAINT | Perf calc W/O No1 Trans during #1 220kV bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025334339017.4333333333 | 10253343 |  | Parent | FALSE | NO.2 330KV CAPACITOR BANK AT DDTS | 39017.4333 | 39017.4861 | DAILY | 00352093 | SPICAPX | Out W/O Spray weeds in cap bank enclosure | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_V67758A639017.4736111111 | V67758A6 |  | Parent | FALSE | EX - ROTS NO.1 220KV LINE AT MTS | 39017.4736 | 39017.6389 | DAILY | 00351696 | SPIMAINT | Corrosion Survey ROTS-MTS 1 | SPIPOWER | V677 | V677 - CORROSION MONITORING OF ACSR CONDUCTORS USING CORMON | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49758A639017.5520833333 | X49758A6 |  | Parent | TRUE | NO.4 66KV BUS AT BETS | 39017.5521 | 39017.6292 | DAILY | 00016367 | SPICAPX | W/O No4 66kV Bus de-energ to commiss new equip | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758A739017.5520833333 | X49758A7 | X49758A6 | Child | FALSE | R4 220/66/22KV TRANS AT BETS | 39017.5521 | 39017.6292 | DAILY | 00016220 | SPICAPX | Perf calc W/O No4 Trans for No4 66kV Bus de-energ | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158F039018.2722222222 | Z53158F0 |  | Parent | FALSE | B4 220/66KV TRANS AT ERTS | 39018.2722 | 39019.609 | CONT | 00004372 | VEN_AUG | Replace Tran 220 kV ISOLS & O/H Trans | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025292439018.2743055556 | 10252924 | X46158I9 | Child | FALSE | WBTS 220KV LINE AT BATS | 39018.2743 | 39018.7424 | DAILY | 00012410 | SPICAPX | Rebate W/O HOTS Line during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025292839018.2743055556 | 10252928 | X46158I9 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39018.2743 | 39018.7424 | DAILY | 00006554 | SPICAPX | Perf calc W/O #1 TR during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158I939018.2743055556 | X46158I9 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 39018.2743 | 39018.7424 | REPDAILY | 00006559 | SPICAPX | Out W/O No2 220kV Bus to connect BETS 2B ROI | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z50058C439019.2479166667 | Z50058C4 |  | Parent | FALSE | NO.3 220KV BUS AT ROTS | 39019.2479 | 39019.5972 | DAILY | 00329013 | VEN_AUG | No3 Bus & YPS 8 L & SVTS 1 LTesting of interlocks | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025292439019.2777777778 | 10252924 | X46158I9 | Child | FALSE | WBTS 220KV LINE AT BATS | 39019.2778 | 39019.4681 | DAILY | 00012410 | SPICAPX | Rebate W/O HOTS Line during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025292839019.2777777778 | 10252928 | X46158I9 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39019.2778 | 39019.4681 | DAILY | 00006554 | SPICAPX | Perf calc W/O #1 TR during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158I939019.2777777778 | X46158I9 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 39019.2778 | 39019.4681 | REPDAILY | 00006559 | SPICAPX | Out W/O No2 220kV Bus to connect BETS 2B ROI | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158J639019.4736111111 | X46158J6 |  | Parent | FALSE | B2 220/66KV TRANS AT BATS | 39019.4736 | 39019.6076 | DAILY | 00006555 | SPICAPX | Out W/O No2 Trans to repair 220 H'string insulator | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258G439020.2645833333 | X43258G4 |  | Parent | FALSE | NO.1 66KV REACTOR AT RCTS | 39020.2646 | 39020.5111 | DAILY | 00016895 | SPICAPX | Out W/O Include No 1 TR. To bore holes 4 CT founds | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025361539020.3013888889 | 10253615 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 39020.3014 | 39020.6417 | DAILY | 00003131 | SPIMAINT | Out W/O No2 220kV BUS - CT oil samples | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025361639020.3013888889 | 10253616 | 10253615 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39020.3014 | 39020.6417 | DAILY | 00003127 | SPIMAINT | Perf calc W/O No2 Trans during #2 220kV bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49658A239020.3034722222 | X49658A2 |  | Parent | FALSE | NO.2 66KV BUS AT HOTS | 39020.3035 | 39020.5694 | DAILY | 00006941 | SPICAPX | Out W/O Stand future B3 trans isol structure | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258H239020.4097222222 | X43258H2 |  | Parent | FALSE | KGTS-RCTS 220KV NB | 39020.4097 | 39020.4583 | DAILY | 00026223 | SPICAPX | Out W/O Temp installation of terminal strip | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258H139020.5506944445 | X43258H1 |  | Parent | FALSE | HOTS-RCTS 220KV | 39020.5507 | 39020.6222 | DAILY | 00328509 | SPICAPX | Out W/O Install temp termination strip | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258G539020.5666666667 | X43258G5 |  | Parent | FALSE | NO.2 66KV REACTOR AT RCTS | 39020.5667 | 39020.7167 | DAILY | 00016897 | SPICAPX | Out W/O To bore for foundations for new CTs | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z53458A339021.2083333333 | Z53458A3 |  | Parent | FALSE | HWTS NO.3 500KV LINE AT ROTS (RTF) | 39021.2083 | 39022.7792 | DAILY | 00359383 | VEN_AUG | Construction work assoc with A2 Tran install | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V67358A239021.2520833333 | V67358A2 |  | Parent | FALSE | SMTS NO.2 500KV LINE NO.1 BUS CB AT SYTS | 39021.2521 | 39021.5701 | REPDAILY | [12 empty] | 0
_X41258C539021.2569444444 | X41258C5 |  | Parent | FALSE | EX - FVTS/BETS 220KV LINE AT SHTS | 39021.2569 | 39021.3583 | CONT | 00000810 | SPICAPX | OUT W/O FVTS/BETS Line to commiss its Fut 2B CB | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010289139021.2604166667 | 10102891 |  | Parent | FALSE | A4 515/230KV TRANS BANK AT HWTS | 39021.2604 | 39026.5493 | CONT | 00337582 | SPIMAINT | O/HAUL Transformer without Div Sw (EH) | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009285439021.2694444445 | 10092854 |  | Parent | FALSE | PT. HENRY NO.2 220KV LINE CB AT GTS | 39021.2694 | 39021.6326 | DAILY | [12 empty] | 0
_1025321939021.2833333333 | 10253219 |  | Parent | FALSE | NO.1 66KV BUS VT AT RCTS | 39021.2833 | 39021.5535 | DAILY | [12 empty] | 0
_1024056339021.2868055556 | 10240563 |  | Parent | FALSE | EX - NO.1 TRANS BANK AT HOTS | 39021.2868 | 39021.4812 | DAILY | 00026245 | SPIMAINT | Repair Cooling Fans | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023751239021.3027777778 | 10237512 |  | Parent | FALSE | A2 TRANS NO.1 BUS 220KV CB AT MLTS | 39021.3028 | 39021.5854 | REPDAILY | [12 empty] | 0
_1025339739021.3736111111 | 10253397 |  | Parent | FALSE | LY NO.4 66KV FDR NO.3 BUS CB AT MWTS | 39021.3736 | 39021.4674 | DAILY | [12 empty] | 0
_X4C4581239021.3972222222 | X4C45812 |  | Parent | FALSE | EX - HWPS NO.4 220KV LINE NO.2 BUS CB AT JLTS | 39021.3972 | 39052.5667 | CONT | [12 empty] | 0
_X49758A839021.4208333333 | X49758A8 |  | Parent | TRUE | NO.1 220KV BUS AT BETS | 39021.4208 | 39021.6847 | DAILY | 00016305 | SPICAPX | Out W/O No1 220kV Bus to decommiss bays C & D | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758A939021.4208333333 | X49758A9 | X49758A8 | Child | FALSE | R4 220/66/22KV TRANS AT BETS | 39021.4208 | 39021.6847 | DAILY | 00016220 | SPICAPX | Perf calc W/O No4 Trans during #1 220 bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025341339021.5111111111 | 10253413 |  | Parent | FALSE | EX - HWPS NO.3 220KV LINE NO.2 BUS CB AT JLTS | 39021.5111 | 39021.5188 | DAILY | [12 empty] | 0
_1025328139021.5534722222 | 10253281 |  | Parent | FALSE | NO.2 66KV BUS VT AT RCTS | 39021.5535 | 39021.6931 | DAILY | [12 empty] | 0
_X2A858P839021.6631944444 | X2A858P8 |  | Parent | FALSE | EX - NO.3 S/S TRANS AT BTS | 39021.6632 | 39038.3681 | CONT | 00000938 | SPICAPX | disconnect & remove for factory repairs | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Other Transformers | Western | 2.2 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1025377939021.6770833333 | 10253779 |  | Parent | FALSE | EX - KGTS 220KV LINE NO.1 BUS CB AT BETS | 39021.6771 | 39156.2292 | CONT | [12 empty] | 0
_1025451839022.2055555556 | 10254518 | X46158J0 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39022.2056 | 39022.6708 | DAILY | 00331118 | SPICAPX | Out W/O No2 66kV BUS for new VT install | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X46158J039022.2055555556 | X46158J0 |  | Parent | TRUE | NO.2 66KV BUS AT BATS | 39022.2056 | 39022.6708 | DAILY | 00006561 | SPICAPX | Out W/O No2 66kV BUS for new VT install | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_V67358A239022.2472222222 | V67358A2 |  | Parent | FALSE | SMTS NO.2 500KV LINE NO.1 BUS CB AT SYTS | 39022.2472 | 39022.584 | REPDAILY | [12 empty] | 0
_1009276639022.25625 | 10092766 |  | Parent | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39022.2562 | 39022.6472 | REPDAILY | 00017905 | SPIMAINT | O/Haul - PT.HENRY 220kV No.1 LINE at GTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025331439022.2736111111 | 10253314 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK AT RCTS | 39022.2736 | 39022.5563 | DAILY | 00016710 | SPIMAINT | Out W/O No1 22kV Cap bank for its CB's CT tests | SPIPOWER |  |  | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1023751239022.3347222222 | 10237512 |  | Parent | FALSE | A2 TRANS NO.1 BUS 220KV CB AT MLTS | 39022.3347 | 39022.3889 | REPDAILY | [12 empty] | 0
_1025331739022.55625 | 10253317 |  | Parent | FALSE | NO.2 22KV CAPACITOR BANK AT RCTS | 39022.5563 | 39022.7271 | DAILY | 00016713 | SPIMAINT | Out W/O No2 22kV Cap bank for its CB's CT tests | SPIPOWER |  |  | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025381439022.5763888889 | 10253814 |  | Parent | FALSE | JLTS-JLGS A 220KV G | 39022.5764 | 39024.6549 | DAILY | 00020463 | GENCO | Genco Transformer washing | GENCO |  |  | Circuits | Eastern | 220 |  |  |  | 0
_Z53158B839023.2076388889 | Z53158B8 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 39023.2076 | 39023.4646 | DAILY | 00004778 | VEN_AUG | No 2 Bus outage to remove Future A2 b/s ROI | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158D239023.2076388889 | Z53158D2 | Z53158B8 | Child | FALSE | TTS 220KV LINE AT ROTS | 39023.2076 | 39023.4646 | DAILY | 00023972 | VEN_AUG | Rebate for No2 Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_Z53158E939023.2076388889 | Z53158E9 | Z53158B8 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39023.2076 | 39023.4646 | DAILY | 00112418 | VEN_AUG | Rebate for No 2 Bus Outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1009276639023.2576388889 | 10092766 |  | Parent | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39023.2576 | 39023.6243 | REPDAILY | 00017905 | SPIMAINT | O/Haul - PT.HENRY 220kV No.1 LINE at GTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V67358A339023.2604166667 | V67358A3 |  | Parent | FALSE | SMTS NO.2 500KV LINE NO.1 BUS CB AT SYTS | 39023.2604 | 39023.6014 | REPDAILY | [12 empty] | 0
_1025328739023.2722222222 | 10253287 |  | Parent | FALSE | NO.1 22KV BUS VT AT RCTS | 39023.2722 | 39023.4667 | DAILY | [12 empty] | 0
_1024483639023.2895833333 | 10244836 |  | Parent | FALSE | B2 220/66KV TRANS AT GNTS | 39023.2896 | 39023.6222 | DAILY | 00000743 | SPIMAINT | Out W/O No2 Trans for 220kV CB BS ROI repair | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025386539023.3506944444 | 10253865 |  | Parent | FALSE | LNGS NO.2 GEN TRANS 220KV CB AT ATS | 39023.3507 | 39027.3264 | CONT | [12 empty] | 0
_1025329239023.5069444444 | 10253292 |  | Parent | FALSE | NO.2 22KV BUS VT AT RCTS | 39023.5069 | 39023.6479 | DAILY | [12 empty] | 0
_1025393339023.9861111111 | 10253933 |  | Parent | FALSE | EX - NO.7 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 39023.9861 | 39025.6982 | CONT | [12 empty] | 0
_1025393439024.0118055556 | 10253934 |  | Parent | FALSE | YPS NO.3 220KV LINE AT YWPS | 39024.0118 | 39027.2917 | CONT | 00016403 | GENCO | W3 Gen Trans Isolation | GENCO |  |  | Circuits | Eastern | 220 |  |  |  | 0
_V67358A339024.2916666667 | V67358A3 |  | Parent | FALSE | SMTS NO.2 500KV LINE NO.1 BUS CB AT SYTS | 39024.2917 | 39024.5271 | REPDAILY | [12 empty] | 0
_X38458F639024.3277777778 | X38458F6 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39024.3278 | 39024.6062 | DAILY | 00023231 | SPICAPX | Out W/O Building bund walls around future trans | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025278139024.5326388889 | 10252781 |  | Parent | FALSE | HWTS NO.3 500KV LINE CB AT LYPS | 39024.5326 | 39024.5743 | REPDAILY | [12 empty] | 0
_1025399039024.6555555556 | 10253990 |  | Parent | FALSE | NO.2 UNIT 230/10.5KV TRANS AT JLGA | 39024.6556 | 39029.3354 | CONT | 00009821 | GENCO | Scap for power station | GENCO |  |  | Connection Transformers | Eastern | 220 |  |  |  | 0
_Z53158F439025.2347222222 | Z53158F4 |  | Parent | FALSE | B3 220/66KV TRANS AT ERTS | 39025.2347 | 39026.566 | CONT | 00004371 | VEN_AUG | Replace Tran 220 kV ISOLS & O/H Trans | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49058C839025.2506944445 | X49058C8 |  | Parent | FALSE | MSS -DDTS 1 330KV NW | 39025.2507 | 39026.4986 | CONT | 00060190 | SPICAPX | Out W/O Install new SD's into position | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025399939025.6979166667 | 10253999 |  | Parent | FALSE | NO.7 GEN TRANS LINE AT HWPS | 39025.6979 | 39026.8042 | CONT | 00356085 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025400939026.2270833333 | 10254009 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB AT MLTS | 39026.2271 | 39027.5361 | CONT | [12 empty] | 0
_1025386839027.2152777778 | 10253868 | X43258G7 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT RCTS | 39027.2153 | 39027.3208 | DAILY | 00360382 | SPICAPX | Rebate W/O No1 220 Cap bk during bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025386939027.2152777778 | 10253869 | X43258G7 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39027.2153 | 39027.3208 | DAILY | 00337581 | SPICAPX | Perf calc W/O No1 trans grp during bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258G739027.2152777778 | X43258G7 |  | Parent | TRUE | EX - NO.1 220KV BUS AT RCTS | 39027.2153 | 39027.3208 | CONT | 00016901 | SPICAPX | Out W/O Remove 220kV Bus from Bays H & J | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025386039027.3138888889 | 10253860 |  | Parent | FALSE | B1 GEN TRANS 500KV CB AT LYPS | 39027.3139 | 39027.4139 | DAILY | [12 empty] | 0
_X41258C739029.2340277778 | X41258C7 |  | Parent | FALSE | EX - NO.1 220KV BUS AT SHTS | 39029.234 | 39092.2875 | CONT | 00000845 | SPICAPX | Out W/O No1 220kV BUS - remove/replace | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49058D239029.2472222222 | X49058D2 |  | Parent | FALSE | H3 TRANS NO.1 BUS 220KV CB AT DDTS | 39029.2472 | 39029.4187 | DAILY | [12 empty] | 0
_1010278039029.2736111111 | 10102780 |  | Parent | TRUE | YPS NO.1 220KV LINE NO.6 BUS CB AT HWPS | 39029.2736 | 39031.525 | CONT | [12 empty] | 0
_1025292039029.2736111111 | 10252920 | 10102780 | Child | FALSE | YPS NO.1 220KV LINE AT HWPS | 39029.2736 | 39031.525 | CONT | 00015795 | SPIMAINT | Rebate for CL.1 O/HAUL - BTH JW419 & JW420 CB | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158J139029.2833333333 | X46158J1 |  | Parent | FALSE | BETS 220KV LINE AT BATS | 39029.2833 | 39033.5625 | CONT | 00012434 | SPICAPX | Out W/O BETS Line to commiss 2B CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025406939029.8125 | 10254069 |  | Parent | FALSE | EX - NO.2 220/66KV TRANS BANK NO.3 BUS 66KV CB AT MTS | 39029.8125 | 39030.7754 | CONT | [12 empty] | 0
_V67358A439030.2354166667 | V67358A4 |  | Parent | FALSE | MLTS NO.1 LINE/SMTS NO.1 LINE 500KV CB AT SYTS | 39030.2354 | 39030.6549 | REPDAILY | [12 empty] | 0
_1025381639030.2708333333 | 10253816 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT RTS | 39030.2708 | 39031.4278 | CONT | [12 empty] | 0
_1025452039030.2708333333 | 10254520 | 10253816 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RTS | 39030.2708 | 39031.4278 | CONT | 00007279 | SPIMAINT | REBALANCE CAP BANK | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1009276739030.2715277778 | 10092767 |  | Parent | FALSE | LY NO.3 66KV FDR AT MWTS | 39030.2715 | 39030.5576 | DAILY | 00016142 | SPIMAINT | O/Haul - LY No.3 66kV Line at MWTS | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49758B039030.3229166667 | X49758B0 |  | Parent | FALSE | EX - KGTS 220KV LINE NO.1 BUS CB AT BETS | 39030.3229 | 39030.5854 | DAILY | [12 empty] | 0
_X43258H439030.6020833333 | X43258H4 |  | Parent | FALSE | NO.2 66KV BUS AT RCTS | 39030.6021 | 39030.7007 | DAILY | 00016977 | SPICAPX | Out W/O Bus de-energisation for commiss MDA Fdr CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_V67358A439031.2305555556 | V67358A4 |  | Parent | FALSE | MLTS NO.1 LINE/SMTS NO.1 LINE 500KV CB AT SYTS | 39031.2306 | 39031.5889 | REPDAILY | [12 empty] | 0
_1007869839032.2111111111 | 10078698 |  | Parent | FALSE | NO.1 220KV TRANS BUS CB AT WMTS | 39032.2111 | 39032.6521 | REPDAILY | [12 empty] | 0
_X46158J239032.2270833333 | X46158J2 |  | Parent | TRUE | NO.1 220KV BUS AT BATS | 39032.2271 | 39032.7097 | REPDAILY | 00006558 | SPICAPX | Out W/O No1 220 bus & BETS L to decomm 1B CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158J439032.2270833333 | X46158J4 | X46158J2 | Child | FALSE | TGTS 220KV LINE AT BATS | 39032.2271 | 39032.7097 | REPDAILY | 00012435 | SPICAPX | Rebate W/O TGTS Line during No1 220kV bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158J539032.2270833333 | X46158J5 | X46158J2 | Child | FALSE | B2 220/66KV TRANS AT BATS | 39032.2271 | 39032.7097 | REPDAILY | 00006555 | SPICAPX | Perf calc W/O #2 Trans during No1 220kV bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025404839032.2291666667 | 10254048 |  | Parent | TRUE | A4 TRANS NO.1 BUS 500KV CB BUS SIDE ROI AT HWTS | 39032.2292 | 39032.5479 | DAILY | [12 empty] | 0
_1025405139032.2291666667 | 10254051 | 10254048 | Child | FALSE | A1 515/230KV TRANS AT HWTS | 39032.2292 | 39032.5479 | DAILY | 00009772 | SPIMAINT | Rebate - No 1 Bus outage to repair isolator. | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z53158F839032.2534722222 | Z53158F8 |  | Parent | FALSE | TTS 220KV LINE AT ROTS | 39032.2535 | 39032.6924 | REPDAILY | 00023972 | VEN_AUG | Reconfigure TTS Line connection | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025411939032.2930555556 | 10254119 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 39032.2931 | 39033.9896 | CONT | 00356086 | GENCO | SCAP No8 Gen Trans Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025408739032.3215277778 | 10254087 |  | Parent | FALSE | RTS 220KV LINE AT BTS | 39032.3215 | 39034.3812 | DAILY | 00015960 | SPIMAINT | reconnect line | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158G739033.2451388889 | Z53158G7 |  | Parent | TRUE | HWPS NO.1 220KV LINE AT ROTS | 39033.2451 | 39033.7458 | DAILY | 00023990 | VEN_AUG | HWPS 1L & ERTS 2 LProximity for rack stringing | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158G839033.2451388889 | Z53158G8 | Z53158G7 | Child | FALSE | ERTS NO.2 220KV LINE AT ROTS | 39033.2451 | 39033.7458 | DAILY | 00023971 | VEN_AUG | Line outage to string rack | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158F839033.25 | Z53158F8 |  | Parent | FALSE | TTS 220KV LINE AT ROTS | 39033.25 | 39033.741 | REPDAILY | 00023972 | VEN_AUG | Reconfigure TTS Line connection | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025386839034.21875 | 10253868 | X43258G7 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT RCTS | 39034.2188 | 39040.7208 | DAILY | 00360382 | SPICAPX | Rebate W/O No1 220 Cap bk during bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025386939034.21875 | 10253869 | X43258G7 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39034.2188 | 39040.7208 | DAILY | 00337581 | SPICAPX | Perf calc W/O No1 trans grp during bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258G739034.21875 | X43258G7 |  | Parent | TRUE | EX - NO.1 220KV BUS AT RCTS | 39034.2188 | 39040.7208 | CONT | 00016901 | SPICAPX | Out W/O Remove 220kV Bus from Bays H & J | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058C139034.2465277778 | X32058C1 | X32058C2 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39034.2465 | 39034.6444 | REPDAILY | 00026900 | SPICAPX | Avail of plant for No 3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058C239034.2465277778 | X32058C2 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39034.2465 | 39034.6444 | REPDAILY | 00004569 | SPICAPX | Projects work | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158B039034.25 | Z53158B0 |  | Parent | FALSE | HWPS NO.1 220KV LINE AT ROTS | 39034.25 | 39035.7757 | CONT | 00023990 | VEN_AUG | Reconfigure HWPS No Line connection | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858Q139034.3930555556 | X2A858Q1 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK AT BTS | 39034.3931 | 39034.6319 | DAILY | 00337002 | SPICAPX | Test No1 22kv Cap Bk | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025418839035.0729166667 | 10254188 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB AT MLTS | 39035.0729 | 39036.5604 | CONT | [12 empty] | 0
_1025460239035.2368055556 | 10254602 | X2A858P3 | Child | FALSE | NO.1 22KV CAPACITOR BANK AT BTS | 39035.2368 | 39035.6424 | DAILY | 00337002 | SPICAPX | connect no.1 cap bank to new cable | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X2A858P339035.2368055556 | X2A858P3 |  | Parent | TRUE | NO.1 22KV CAPACITOR BANK CB AT BTS | 39035.2368 | 39035.6424 | DAILY | [12 empty] | 0
_X32058C139035.2548611111 | X32058C1 | X32058C2 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39035.2549 | 39035.6354 | REPDAILY | 00026900 | SPICAPX | Avail of plant for No 3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058C239035.2548611111 | X32058C2 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39035.2549 | 39035.6354 | REPDAILY | 00004569 | SPICAPX | Projects work | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025335539035.3006944445 | 10253355 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 39035.3007 | 39035.5417 | DAILY | [12 empty] | 0
_1025739339035.3958333333 | 10257393 |  | Parent | FALSE | EX - NO.1 TRANS NO.1 BUS 220KV CB CT R/PH AT GTS | 39035.3958 | 39259.3264 | CONT | [12 empty] | 0
_1025739339035.3958333333 | 10257393 |  | Parent | FALSE | EX - NO.1 TRANS NO.1 BUS 220KV CB CT R/PH AT GTS | 39035.3958 | 39259.3681 | CONT | [12 empty] | 0
_1025421539035.4520833333 | 10254215 |  | Parent | TRUE | EX - PT. HENRY NO.1 220KV LINE CT W/PH AT GTS | 39035.4521 | 39037.409 | CONT | [12 empty] | 0
_1025421639035.4520833333 | 10254216 | 10254215 | Child | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39035.4521 | 39037.409 | CONT | 00017905 | FORCED | Outage W/O for GTS-PTH No1 Line CB CT Replacement | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49058D139036.2291666667 | X49058D1 |  | Parent | FALSE | DDTS-GNTS 3 220KV NW | 39036.2292 | 39037.7312 | CONT | 00060186 | SPICAPX | Install New SD's | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158B139036.2513888889 | Z53158B1 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39036.2514 | 39039.6326 | DAILY | 00004776 | VEN_AUG | Bus outage to remove bus bi pods & modifiy bus | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158G639036.2513888889 | Z53158G6 | Z53158B1 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39036.2514 | 39039.6326 | DAILY | 00354024 | VEN_AUG | Rebate Bus outage to remove bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X38458F839036.2861111111 | X38458F8 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT TGTS | 39036.2861 | 39036.4619 | DAILY | 00003128 | SPICAPX | OuT W/O No1 S/S Trans. Reterminate 415V cable | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1025407639036.3194444444 | 10254076 |  | Parent | FALSE | EX - SMTS LINE/A2 TRANS 500KV CB AT KTS | 39036.3194 | 39036.5681 | DAILY | [12 empty] | 0
_X2A858Q339036.3819444444 | X2A858Q3 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK AT BTS | 39036.3819 | 39036.5819 | DAILY | 00337002 | SPICAPX | commission no.1 cap bank, s/s & bus link cable cb | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X38458F939036.4631944445 | X38458F9 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT TGTS | 39036.4632 | 39036.6667 | DAILY | 00003129 | SPICAPX | Out W/O No2 S/S Trans. Reterminate 415V cable | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1025418939036.5167361111 | 10254189 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB AT MLTS | 39036.5167 | 39036.5611 | DAILY | [12 empty] | 0
_1025425639037.2083333333 | 10254256 |  | Parent | FALSE | SYN/COND AT TSTS | 39037.2083 | 39037.3868 | DAILY | 00007626 | SPIMAINT | Change over oil pump | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025425939037.2451388889 | 10254259 |  | Parent | FALSE | NO.7 GEN TRANS 220KV CB AT HWPS | 39037.2451 | 39042.3014 | CONT | [12 empty] | 0
_1025382439037.2520833333 | 10253824 |  | Parent | FALSE | EX - SYTS LINE/A4 TRANS 500KV CB AT KTS | 39037.2521 | 39038.5771 | CONT | [12 empty] | 0
_1025396439037.2583333333 | 10253964 | X49758B2 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39037.2583 | 39037.6174 | DAILY | 00016040 | SPICAPX | Perf calc W/O No2 Trans during #3 66kV BUS outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025396839037.2583333333 | 10253968 | X49758B2 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT BETS | 39037.2583 | 39037.6174 | DAILY | 00350820 | SPICAPX | Rebate W/O 3A Cap bk during #3 66kV BUS outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1025396939037.2583333333 | 10253969 | X49758B2 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 39037.2583 | 39037.6174 | DAILY | 00016304 | SPICAPX | Rebate W/O 3B Cap bk during #3 66kV BUS outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758B239037.2583333333 | X49758B2 |  | Parent | TRUE | NO.3 66KV BUS AT BETS | 39037.2583 | 39037.6174 | REPDAILY | 00016366 | SPICAPX | Out W/O No3 66kV BUS to connect new CTN STBY CB | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025405539037.3388888889 | 10254055 |  | Parent | FALSE | EX - NO.1 TRANS GROUP 220KV CB CT W/PH AT TGTS | 39037.3389 | 39037.5576 | DAILY | [12 empty] | 0
_1025428739037.4847222222 | 10254287 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 39037.4847 | 39037.5646 | DAILY | 00352121 | FORCED | Unable to close No 2 Trans 220kV CB at DDTS | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X2A858Q239038.2333333333 | X2A858Q2 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT BTS | 39038.2333 | 39038.325 | DAILY | [12 empty] | 0
_X32058C139038.2416666667 | X32058C1 | X32058C2 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39038.2417 | 39038.6653 | REPDAILY | 00026900 | SPICAPX | Avail of plant for No 3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058C239038.2416666667 | X32058C2 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39038.2417 | 39038.6653 | REPDAILY | 00004569 | SPICAPX | Projects work | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z50658A139038.2840277778 | Z50658A1 |  | Parent | FALSE | NO.6 66KV BUS AT HTS | 39038.284 | 39038.6097 | DAILY | 00004460 | SPIMAINT | Proximity work for CB foundations. | SPIPOWER | Z506 | Z506 - (HTS) OPTIMISING 66KV CBS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025407039038.2986111111 | 10254070 |  | Parent | FALSE | EX - B1 TRANS NO.2 BUS 220KV CB AT GTS | 39038.2986 | 39038.3743 | DAILY | [12 empty] | 0
_1023700739038.3229166667 | 10237007 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 39038.3229 | 39038.6201 | DAILY | 00352121 | SPIMAINT | Remove flow meter and replace gasket | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025431039038.3708333333 | 10254310 |  | Parent | TRUE | EX - NO.4 220KV BUS AT ERTS | 39038.3708 | 39038.4493 | DAILY | 00004380 | FORCED | No4 220kV Bus Faulty CVT | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025460539038.3708333333 | 10254605 | 10254310 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT ERTS | 39038.3708 | 39038.4493 | DAILY | 00004344 | FORCED | No4 220kV Bus Faulty CVT | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025472839038.3708333333 | 10254728 | 10254310 | Child | FALSE | B4 220/66KV TRANS AT ERTS | 39038.3708 | 39038.4493 | DAILY | 00004372 | FORCED | No4 220kV Bus Faulty CVT | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025430139038.5 | 10254301 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39038.5 | 39038.5333 | DAILY | [12 empty] | 0
_1025430339038.5381944444 | 10254303 |  | Parent | TRUE | HWTS NO.3 500KV LINE CB AT LYPS | 39038.5382 | 39038.5687 | DAILY | [12 empty] | 0
_1025430539038.5381944444 | 10254305 | 10254303 | Child | FALSE | HWTS NO.3 500KV LINE AT LYPS | 39038.5382 | 39038.5687 | DAILY | 00016088 | FORCED | ADJUST SF6 GAS PRESSURE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025431939038.975 | 10254319 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 39038.975 | 39041.4118 | CONT | 00356081 | GENCO | HWPS No 3 Gen Isol'd for Genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010386139039.2305555556 | 10103861 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT MLTS | 39039.2306 | 39039.6444 | REPDAILY | 00337580 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z53158F539039.2333333333 | Z53158F5 |  | Parent | FALSE | B1 220/66KV TRANS AT ERTS | 39039.2333 | 39040.5278 | CONT | 00004370 | VEN_AUG | Replace Tran 220 kV ISOLS & O/H Trans | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025419439039.2395833333 | 10254194 |  | Parent | FALSE | NO.1 220KV TRANS BUS CB AT WMTS | 39039.2396 | 39039.6549 | DAILY | [12 empty] | 0
_1010278539039.25 | 10102785 |  | Parent | FALSE | NO.7 GEN TRANS 220KV E/SW AT HWPS | 39039.25 | 39039.4264 | DAILY | [12 empty] | 0
_Z53158F939039.2506944445 | Z53158F9 |  | Parent | FALSE | TTS 220KV LINE AT ROTS | 39039.2507 | 39039.6368 | DAILY | 00023972 | VEN_AUG | Reconfigure TTS Line connection | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025472139039.7916666667 | 10254721 |  | Parent | FALSE | CBTS NO.1 66KV FDR AT FTS | 39039.7917 | 39039.8465 | DAILY | 00012275 | FAULT | Security breach at FTS, tripping of line | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158H239040.20625 | Z53158H2 |  | Parent | TRUE | SVTS NO.2 220KV LINE AT ROTS | 39040.2063 | 39040.8187 | DAILY | 00023968 | VEN_AUG | SVTS 2 Line & RTS 1 Line Const A2 Trans upgrade | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158H339040.20625 | Z53158H3 | Z53158H2 | Child | FALSE | RTS NO.1 220KV LINE AT ROTS | 39040.2063 | 39040.8187 | DAILY | 00023111 | VEN_AUG | Const for A2 Trans upgrade | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010386139040.2513888889 | 10103861 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT MLTS | 39040.2514 | 39040.6771 | REPDAILY | 00337580 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025271339040.25625 | 10252713 |  | Parent | TRUE | NO.2 22KV BUS AT RWTS | 39040.2562 | 39040.4424 | DAILY | 00007483 | SPIMAINT | Prot work Trans & Bus (No2 & No3 Bus isolated) | SPIPOWER |  |  | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1025280939040.25625 | 10252809 | 10252713 | Child | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39040.2562 | 39040.4424 | DAILY | 00007452 | SPIMAINT | Avail plant Bus (No2 & No3 Bus isolated) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025281039040.25625 | 10252810 | 10252713 | Child | FALSE | NO.2 22KV CAPACITOR BANK AT RWTS | 39040.2562 | 39040.4424 | DAILY | 00357000 | SPIMAINT | Rebate Bus (No2 & No3 Bus isolated) | SPIPOWER |  |  | Capacitors | Eastern | 22 | CONNECTION ASSET | EXCLUDED |  | 0
_1010422939040.2611111111 | 10104229 |  | Parent | FALSE | L3 220/22KV TRANS AT WMTS | 39040.2611 | 39040.5986 | DAILY | 00003237 | SPIMAINT | O/HAUL Transformer Div Mechanism & 22kv cb | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025433139040.4805555556 | 10254331 |  | Parent | FALSE | NO.8 GEN 220/16.5KV TRANS AT HWPS | 39040.4806 | 39043.8208 | CONT | 00009649 | GENCO | Power Station Requirements | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1025433239040.6672453704 | 10254332 |  | Parent | FALSE | BSS 220KV LINE NO.1 BUS CB AT RCTS | 39040.6672 | 39062.4653 | CONT | [12 empty] | 0
_Z53458A439041.2229166667 | Z53458A4 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39041.2229 | 39042.684 | CONT | [12 empty] | 0
_1025475439041.2236111111 | 10254754 |  | Parent | FALSE | B1 220/66KV TRANS AT CBTS | 39041.2236 | 39041.5104 | DAILY | 00353076 | FAULT | B1 trans trip due to No1 BUS fault | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1010155239041.2465277778 | 10101552 |  | Parent | FALSE | H3 TRANS NO.2 BUS 220KV CB AT DDTS | 39041.2465 | 39041.641 | REPDAILY | [12 empty] | 0
_1024956439041.2493055556 | 10249564 |  | Parent | FALSE | EX - SYTS LINE/A4 TRANS 500KV CB AT KTS | 39041.2493 | 39048.5569 | CONT | [12 empty] | 0
_X49858A739041.2513888889 | X49858A7 |  | Parent | FALSE | EX - EPS NO.2 220KV LINE AT MBTS | 39041.2514 | 39041.2917 | DAILY | 00011752 | SPICAPX | Out W/O EPS 2 Line to replace CVT's | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1010422539041.3034722222 | 10104225 |  | Parent | FALSE | B2 220/66KV TRANS AT MWTS | 39041.3035 | 39042.5701 | CONT | 00010266 | SPIMAINT | O/HAUL Transformer and Div Sw (EH) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025434739041.3111111111 | 10254347 |  | Parent | TRUE | B2 TRANS NO.1 BUS 220KV CB AT GTS | 39041.3111 | 39041.3333 | CONT | [12 empty] | 0
_1025472639041.3111111111 | 10254726 | 10254347 | Child | FALSE | GTS -PTH 2 220KV WY | 39041.3111 | 39041.3333 | CONT | 00022691 | FORCED | Replace broken/corroded studs | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025405039041.34375 | 10254050 |  | Parent | FALSE | EX - NO.2 TRANS 220KV CB AT TGTS | 39041.3438 | 39041.6625 | DAILY | [12 empty] | 0
_1025436539042.1291666667 | 10254365 |  | Parent | TRUE | 1-2 22KV BUS TIE CB AT RWTS | 39042.1292 | 39043.2937 | CONT | [12 empty] | 0
_1025473639042.1291666667 | 10254736 | 10254365 | Child | FALSE | U1 66/22KV TRANS AT RWTS | 39042.1292 | 39043.2937 | CONT | 00007456 | FAULT | 1-2 Bus Tie CB fault | SPIPOWER |  |  | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025473839042.1291666667 | 10254738 | 10254365 | Child | FALSE | L2 220/22KV TRANS BANK AT RWTS | 39042.1292 | 39043.2937 | CONT | 00007447 | FAULT | 1-2 Bus Tie CB fault | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025473939042.1291666667 | 10254739 | 10254365 | Child | FALSE | L3 220/22KV TRANS B/PH AT RWTS | 39042.1292 | 39043.2937 | CONT | 00007449 | FAULT | 1-2 Bus Tie CB fault | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025424839042.1965277778 | 10254248 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 39042.1965 | 39045.9875 | CONT | 00016423 | GENCO | isolated and earthed for Genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025402139042.2277777778 | 10254021 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 39042.2278 | 39042.809 | CONT | 00027386 | APDALCOA | APD request to isolate and earth HYTS No.1 500kV L | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X32058C139042.2444444445 | X32058C1 | X32058C2 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39042.2444 | 39042.5354 | REPDAILY | 00026900 | SPICAPX | Avail of plant for No 3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058C239042.2444444445 | X32058C2 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39042.2444 | 39042.5354 | REPDAILY | 00004569 | SPICAPX | Projects work | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010155239042.2486111111 | 10101552 |  | Parent | FALSE | H3 TRANS NO.2 BUS 220KV CB AT DDTS | 39042.2486 | 39042.5958 | REPDAILY | [12 empty] | 0
_1010142939042.3048611111 | 10101429 |  | Parent | FALSE | 22KV/415V S/S TRANS AT FTS | 39042.3049 | 39042.4618 | DAILY | 00004393 | SPIMAINT | O/HAUL Transformer without Div Sw (EM) | SPIPOWER |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1025435839042.8673611111 | 10254358 |  | Parent | FALSE | NO.4 GEN 500/21KV TRANS AT LYPA | 39042.8674 | 39046.5028 | CONT | 00010009 | GENCO | SCAP for LYPSA No4 Gen Trans Isols & Earths | GENCO |  |  | Main Transformers | Eastern | 500 |  |  |  | 0
_X32058C139043.2409722222 | X32058C1 | X32058C2 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39043.241 | 39043.6792 | REPDAILY | 00026900 | SPICAPX | Avail of plant for No 3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058C239043.2409722222 | X32058C2 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39043.241 | 39043.6792 | REPDAILY | 00004569 | SPICAPX | Projects work | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010143039043.2534722222 | 10101430 |  | Parent | FALSE | NO.2 66KV BUS AT FTS | 39043.2535 | 39043.55 | DAILY | 00004395 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 66 |  |  |  | 0
_1010155139043.2541666667 | 10101551 |  | Parent | FALSE | H3 TRANS NO.1 BUS 220KV CB AT DDTS | 39043.2542 | 39043.641 | REPDAILY | [12 empty] | 0
_X49858A739043.2652777778 | X49858A7 |  | Parent | FALSE | EX - EPS NO.2 220KV LINE AT MBTS | 39043.2653 | 39043.7667 | DAILY | 00011752 | SPICAPX | Out W/O EPS 2 Line to replace CVT's | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1010222239043.2729166667 | 10102222 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT KGTS | 39043.2729 | 39043.4292 | DAILY | 00017150 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Other Transformers | Alstom | 22 |  |  |  | 0
_1025439039043.29375 | 10254390 |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT RWTS | 39043.2937 | 39044.6021 | CONT | [12 empty] | 0
_1025406039043.2986111111 | 10254060 | X49858A6 | Child | FALSE | B2 220/66KV TRANS AT MBTS | 39043.2986 | 39043.5882 | DAILY | 00362372 | SPICAPX | Perf calc W/O B2 Trans during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025406139043.2986111111 | 10254061 | X49858A6 | Child | FALSE | EX - DDTS NO.2 220KV LINE AT MBTS | 39043.2986 | 39043.5882 | DAILY | 00011750 | SPICAPX | Rebate W/O DDTS 2 Line during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025406239043.2986111111 | 10254062 | X49858A6 | Child | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39043.2986 | 39043.5882 | DAILY | 00011755 | SPICAPX | Rebate W/O MKPS Line during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025406339043.2986111111 | 10254063 | X49858A6 | Child | FALSE | EX - EPS NO.2 220KV LINE AT MBTS | 39043.2986 | 39043.5882 | DAILY | 00011752 | SPICAPX | Rebate W/O EPS 2 Line during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025406439043.2986111111 | 10254064 | X49858A6 | Child | FALSE | WKPS 220KV LINE AT MBTS | 39043.2986 | 39043.5882 | DAILY | 00011756 | SPICAPX | Rebate W/O WKPS Line during No2 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858A639043.2986111111 | X49858A6 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MBTS | 39043.2986 | 39043.5882 | REPDAILY | 00004002 | SPICAPX | Out W/O No2 220kV bus de-energ for bus prot mods | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010379739043.3597222222 | 10103797 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT MWTS | 39043.3597 | 39044.5764 | CONT | 00010265 | SPIMAINT | O/HAUL Transformer and Div Sw (EH) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010222139043.4298611111 | 10102221 |  | Parent | TRUE | NO.2 22KV/415V S/S TRANS AT KGTS | 39043.4299 | 39043.6618 | DAILY | 00017126 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Other Transformers | Alstom | 22 |  |  |  | 0
_1010428539043.4298611111 | 10104285 | 10102221 | Child | FALSE | R3 220/66/22KV TRANS AT KGTS | 39043.4299 | 39043.6618 | DAILY | 00017375 | SPIMAINT | O/HAUL Transformer Div Mechanism (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158G339044.2006944444 | Z53158G3 |  | Parent | TRUE | NO.4 220KV BUS AT ROTS | 39044.2007 | 39044.6285 | DAILY | 00329012 | VEN_AUG | Construction for A2 Trans upgrade | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158G939044.2006944444 | Z53158G9 | Z53158G3 | Child | FALSE | MTS NO.1 220KV LINE AT ROTS | 39044.2007 | 39044.6285 | DAILY | 00350667 | VEN_AUG | Construction for A2 Trans upgrade | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025402239044.2333333333 | 10254022 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 39044.2333 | 39044.6458 | CONT | 00027386 | APDALCOA | APD request to isolate and earth HYTS No.1 500kV L | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1010155139044.2506944445 | 10101551 |  | Parent | FALSE | H3 TRANS NO.1 BUS 220KV CB AT DDTS | 39044.2507 | 39044.6056 | REPDAILY | [12 empty] | 0
_X49758B539044.2527777778 | X49758B5 |  | Parent | FALSE | EX - FVTS/SHTS 220KV LINE AT BETS | 39044.2528 | 39044.4611 | REPDAILY | 00016446 | SPICAPX | Out W/O BETS/FVTS/SHTS Line for work at BETS | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025431739044.3194444444 | 10254317 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT TGTS | 39044.3194 | 39044.4451 | DAILY | 00003129 | DBPROX | PowerCor work | DISTCO |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1025455139044.5888888889 | 10254551 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 39044.5889 | 39044.7556 | DAILY | [12 empty] | 0
_1025473539044.5888888889 | 10254735 |  | Parent | FALSE | A4 500/220KV TRANS BANK AT KTS | 39044.5889 | 39044.7556 | DAILY | 00026098 | FAULT | Spurious opening of A2 Trans No 1 Bus CB | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X32058C139045.2520833333 | X32058C1 | X32058C2 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39045.2521 | 39045.5153 | REPDAILY | 00026900 | SPICAPX | Avail of plant for No 3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058C239045.2520833333 | X32058C2 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39045.2521 | 39045.5153 | REPDAILY | 00004569 | SPICAPX | Projects work | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025451739045.2604166667 | 10254517 |  | Parent | FALSE | 5-6 220KV BUS TIE CB AT HWPS | 39045.2604 | 39045.5424 | DAILY | [12 empty] | 0
_1025451539045.2868055556 | 10254515 |  | Parent | TRUE | HWTS NO.3 500KV LINE CB AT LYPS | 39045.2868 | 39045.3382 | DAILY | [12 empty] | 0
_1025451639045.2868055556 | 10254516 | 10254515 | Child | FALSE | HWTS NO.3 500KV LINE AT LYPS | 39045.2868 | 39045.3382 | DAILY | 00016088 | FORCED | ADJUST SF6 GAS PRESSURE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025454839045.3416666667 | 10254548 |  | Parent | FALSE | B2 TRANS 220KV CB AT GNTS | 39045.3417 | 39045.591 | DAILY | [12 empty] | 0
_1025456139045.66875 | 10254561 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT SHTS | 39045.6687 | 39045.6903 | DAILY | [12 empty] | 0
_1025456639045.66875 | 10254566 | 10254561 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT SHTS | 39045.6687 | 39045.6903 | DAILY | 00330829 | SPIMAINT | Rebate W/O 2B Cap bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025456739045.66875 | 10254567 | 10254561 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT SHTS | 39045.6687 | 39045.6903 | DAILY | 00350862 | SPIMAINT | Rebate W/O 2A Cap bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025416239046.2527777778 | 10254162 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT MLTS | 39046.2528 | 39046.316 | REPDAILY | 00337580 | SPIMAINT | Complete O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025457639046.2701388889 | 10254576 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 39046.2701 | 39047.9354 | CONT | [12 empty] | 0
_X2A858Q839046.2833333333 | X2A858Q8 |  | Parent | FALSE | L1 220/22KV TRANS AT BTS | 39046.2833 | 39046.3542 | DAILY | 00360728 | SPICAPX | access to roof of trans enclosure for repairs | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158H039047.2083333333 | Z53158H0 | Z53158H1 | Child | FALSE | SVTS NO.2 220KV LINE AT ROTS | 39047.2083 | 39047.7792 | DAILY | 00023968 | VEN_AUG | Construction for A2 Trans upgrade | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158H139047.2083333333 | Z53158H1 |  | Parent | TRUE | RTS NO.4 220KV LINE AT ROTS | 39047.2083 | 39047.7792 | DAILY | 00023969 | VEN_AUG | RTS 4 Line & SVTS 2L Const for A2 Trans upgrade | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025454939047.3833333333 | 10254549 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 39047.3833 | 39047.5694 | DAILY | [12 empty] | 0
_1025461339048.1222222222 | 10254613 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB AT MLTS | 39048.1222 | 39049.4021 | CONT | [12 empty] | 0
_1025424039048.2111111111 | 10254240 | X46158K0 | Child | FALSE | B2 220/66KV TRANS AT BATS | 39048.2111 | 39048.7 | REPDAILY | 00006555 | SPICAPX | Perf calc W/O No2 Trans during No2 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025424139048.2111111111 | 10254241 | X46158K0 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39048.2111 | 39048.7 | REPDAILY | 00331118 | SPICAPX | Rebate W/O No2 Cap bank during No2 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X46158K039048.2111111111 | X46158K0 |  | Parent | TRUE | NO.2 66KV BUS AT BATS | 39048.2111 | 39048.7 | REPDAILY | 00006561 | SPICAPX | Out W/O No2 66kV Bus to replace BAN No2 FDR CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1009286839049.1763888889 | 10092868 |  | Parent | TRUE | FUTURE ROTS 220KV LINE NO.2 BUS CB AT TTS | 39049.1764 | 39049.6743 | DAILY | [12 empty] | 0
_1009287239049.1763888889 | 10092872 | 10092868 | Child | FALSE | BTS NO.1 220KV LINE AT TTS | 39049.1764 | 39049.6743 | DAILY | 00015723 | SPIMAINT | O/Haul - VT | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025424039049.2013888889 | 10254240 | X46158K0 | Child | FALSE | B2 220/66KV TRANS AT BATS | 39049.2014 | 39049.6458 | REPDAILY | 00006555 | SPICAPX | Perf calc W/O No2 Trans during No2 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025424139049.2013888889 | 10254241 | X46158K0 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39049.2014 | 39049.6458 | REPDAILY | 00331118 | SPICAPX | Rebate W/O No2 Cap bank during No2 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X46158K039049.2013888889 | X46158K0 |  | Parent | TRUE | NO.2 66KV BUS AT BATS | 39049.2014 | 39049.6458 | REPDAILY | 00006561 | SPICAPX | Out W/O No2 66kV Bus to replace BAN No2 FDR CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010158639049.2777777778 | 10101586 |  | Parent | FALSE | H1 TRANS NO.2 BUS 330KV CB AT DDTS | 39049.2778 | 39049.6139 | REPDAILY | [12 empty] | 0
_1010278839049.2902777778 | 10102788 |  | Parent | FALSE | HWTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 39049.2903 | 39049.5813 | CONT | [12 empty] | 0
_Z53158I239049.3118055556 | Z53158I2 |  | Parent | FALSE | RTS NO.4 LINE/YPS NO.5 LINE 220KV CB AT ROTS | 39049.3118 | 39049.7264 | DAILY | [12 empty] | 0
_1025462839049.5479166667 | 10254628 |  | Parent | FALSE | NO.2 330KV CAPACITOR BANK AT WOTS | 39049.5479 | 39049.584 | CONT | 00354001 | FORCED | Replace CB Mech box cover | ALSTOM |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_1025453239050.1770833333 | 10254532 |  | Parent | TRUE | FUTURE ROTS 220KV LINE NO.2 BUS CB AT TTS | 39050.1771 | 39050.5069 | DAILY | [12 empty] | 0
_1025454039050.1770833333 | 10254540 | 10254532 | Child | FALSE | BTS NO.1 220KV LINE AT TTS | 39050.1771 | 39050.5069 | DAILY | 00015723 | SPIMAINT | O/Haul - VT | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025460939050.25 | 10254609 |  | Parent | FALSE | EX - 2-3 66KV BUS TIE CB AT KTS | 39050.25 | 39050.5493 | DAILY | [12 empty] | 0
_1025383539050.2583333333 | 10253835 |  | Parent | FALSE | EX - SMTS LINE/A2 TRANS 500KV CB AT KTS | 39050.2583 | 39050.6208 | REPDAILY | [12 empty] | 0
_1010379639050.2701388889 | 10103796 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT MWTS | 39050.2701 | 39050.5292 | DAILY | [12 empty] | 0
_1024409239050.275 | 10244092 |  | Parent | FALSE | 1-2 22KV BUS TIE CB NO.2 BUS SIDE ISOL AT RCTS | 39050.275 | 39050.6972 | DAILY | [12 empty] | 0
_1010158639050.2777777778 | 10101586 |  | Parent | FALSE | H1 TRANS NO.2 BUS 330KV CB AT DDTS | 39050.2778 | 39050.5944 | REPDAILY | [12 empty] | 0
_X49758B539050.2854166667 | X49758B5 |  | Parent | FALSE | EX - FVTS/SHTS 220KV LINE AT BETS | 39050.2854 | 39050.441 | REPDAILY | 00016446 | SPICAPX | Out W/O BETS/FVTS/SHTS Line for work at BETS | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025466939050.6083333333 | 10254669 |  | Parent | FALSE | RTS NO.4 LINE/YPS NO.5 LINE 220KV CB AT ROTS | 39050.6083 | 39050.7389 | CONT | [12 empty] | 0
_X46158K139051.2041666667 | X46158K1 |  | Parent | FALSE | NO.1 66KV BUS AT BATS | 39051.2042 | 39051.5924 | DAILY | 00006560 | SPICAPX | Out W/O No1 66kV Bus to replace bus tie CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010380239051.2659722222 | 10103802 |  | Parent | FALSE | 1-4 66KV BUS TIE CB AT MWTS | 39051.266 | 39051.5125 | DAILY | [12 empty] | 0
_1010155039051.2715277778 | 10101550 |  | Parent | FALSE | H3 TRANS NO.1 BUS 330KV CB AT DDTS | 39051.2715 | 39051.6236 | REPDAILY | [12 empty] | 0
_1025434339051.2736111111 | 10254343 |  | Parent | TRUE | 66KV CAPACITOR BANK CB AT TGTS | 39051.2736 | 39051.4896 | DAILY | [12 empty] | 0
_1025471339051.2736111111 | 10254713 | 10254343 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT WMTS | 39051.2736 | 39051.4896 | DAILY | 00074391 | SPIMAINT | carry out drm tests on cb | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025466039051.5729166667 | 10254660 |  | Parent | FALSE | RTS NO.4 LINE/YPS NO.5 LINE 220KV CB AT ROTS | 39051.5729 | 39051.609 | DAILY | [12 empty] | 0
_X46158K239051.5777777778 | X46158K2 |  | Parent | FALSE | EX - 1-2 66KV BUS TIE CB AT BATS | 39051.5778 | 39056.6667 | CONT | [12 empty] | 0
_1025469739051.6965277778 | 10254697 |  | Parent | TRUE | EX - BAN NO.1 66KV FDR CB AT BATS | 39051.6965 | 39052.7083 | CONT | [12 empty] | 0
_1025474239051.6965277778 | 10254742 | 10254697 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 39051.6965 | 39052.7083 | CONT | 00331109 | FAULT | BAN No1 66kV CB Fault causing outage No1 66kV Bus | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025474339051.6965277778 | 10254743 | 10254697 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39051.6965 | 39052.7083 | CONT | 00006554 | FAULT | BAN No1 66kV CB Fault causing outage No1 66kV Bus | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025469539051.6965277778 | 10254695 |  | Parent | FALSE | EX - BAN NO.1 66KV FDR CB AT BATS | 39051.6965 | 39052.7125 | CONT | [12 empty] | 0
_1025470039052.1277777778 | 10254700 |  | Parent | FALSE | HPS 66KV LINE CB AT WOTS | 39052.1278 | 39052.4104 | CONT | [12 empty] | 0
_X43258H539052.2152777778 | X43258H5 |  | Parent | TRUE | EX - NO.1 220KV BUS AT RCTS | 39052.2153 | 39059.8215 | CONT | 00016901 | SPICAPX | Out W/O No 1 220kV bus upgrade. | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258H639052.2152777778 | X43258H6 | X43258H5 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39052.2153 | 39059.8215 | CONT | 00337581 | SPICAPX | Perf calc W/O No1 Trans while No 1 220 bus OOS | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258H739052.2152777778 | X43258H7 | X43258H5 | Child | FALSE | HOTS-RCTS 220KV | 39052.2153 | 39059.8215 | CONT | 00328509 | SPICAPX | Rebate W/O HOTS L while No 1 220 bus OOS | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258H839052.2152777778 | X43258H8 | X43258H5 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT RCTS | 39052.2153 | 39059.8215 | CONT | 00360382 | SPICAPX | Rebate W/O No1 220 Cap bk while No 1 220 bus OOS | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258J339052.2604166667 | X43258J3 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39052.2604 | 39052.6785 | REPDAILY | 00337584 | SPICAPX | Out W/O #2 Tr de-en daily during #1 220 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025383539052.2618055556 | 10253835 |  | Parent | FALSE | EX - SMTS LINE/A2 TRANS 500KV CB AT KTS | 39052.2618 | 39052.5778 | REPDAILY | [12 empty] | 0
_1010155039052.2701388889 | 10101550 |  | Parent | FALSE | H3 TRANS NO.1 BUS 330KV CB AT DDTS | 39052.2701 | 39052.5931 | REPDAILY | [12 empty] | 0
_1025434539052.3125 | 10254345 |  | Parent | TRUE | EX - NO.1B 66KV CAPACITOR BANK CB AT KTS | 39052.3125 | 39052.5813 | DAILY | [12 empty] | 0
_1025517139052.3125 | 10255171 | 10254345 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT KTS | 39052.3125 | 39052.5813 | DAILY | 00337022 | SPIMAINT | carry out drm tests on cb | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025476339052.6979166667 | 10254763 |  | Parent | FALSE | EX - BAN NO.1 66KV FDR CB AT BATS | 39052.6979 | 39053.6472 | CONT | [12 empty] | 0
_1010146539053.2069444445 | 10101465 |  | Parent | FALSE | SYN/COND AT FBTS | 39053.2069 | 39054.6222 | CONT | 00002697 | SPIMAINT | 3 Monthly O/H of Syn/Cond & Cooling system | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025475639053.2111111111 | 10254756 |  | Parent | FALSE | B1 GEN TRANS 500KV CB AT LYPS | 39053.2111 | 39053.6347 | DAILY | [12 empty] | 0
_Z53158H539053.2194444445 | Z53158H5 |  | Parent | FALSE | SVTS NO.2 220KV LINE AT ROTS | 39053.2194 | 39053.6764 | REPDAILY | 00023968 | VEN_AUG | Construction for A2 Trans upgrade Erect poles | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158F739053.2388888889 | Z53158F7 | Z53158I4 | Child | FALSE | B4 220/66KV TRANS AT ERTS | 39053.2389 | 39054.7125 | CONT | 00004372 | VEN_AUG | Avail of plant Replace 3-4 B.T No4 B 220 kV ISOLS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158I439053.2388888889 | Z53158I4 |  | Parent | TRUE | EX - NO.4 220KV BUS AT ERTS | 39053.2389 | 39054.7125 | CONT | 00004380 | VEN_AUG | Replace 3-4 B.T No4 B 220 kV ISOLS No4 Tr OOS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49058C939053.2534722222 | X49058C9 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39053.2535 | 39054.6333 | CONT | 00060191 | SPICAPX | Out W/O Install new SD's into position L2 | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258J339053.2555555556 | X43258J3 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39053.2556 | 39053.6799 | REPDAILY | 00337584 | SPICAPX | Out W/O #2 Tr de-en daily during #1 220 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025477439053.8284722222 | 10254774 |  | Parent | FALSE | DDTS-SMTS 1 330KV | 39053.8285 | 39053.9535 | CONT | 00328506 | BUSHFIRE | DDTS-SMTS No1 Line forced outage due to bushfire. | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM Event bushfire
_Z53158H539054.2229166667 | Z53158H5 |  | Parent | FALSE | SVTS NO.2 220KV LINE AT ROTS | 39054.2229 | 39054.7924 | REPDAILY | 00023968 | VEN_AUG | Construction for A2 Trans upgrade Erect poles | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z52958A339054.2326388889 | Z52958A3 | Z52958A5 | Child | FALSE | B1 220/66KV TRANS AT RTS | 39054.2326 | 39054.6847 | DAILY | 00007329 | DB_AUG | Avail of plant No1 Bus & TK FDR for fdr upgrade | SPIPOWER | Z529 | Z529 - (RTS) UPRATE SUB TK 66KV FDR CONNECTION TO 1200A | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z52958A439054.2326388889 | Z52958A4 | Z52958A5 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RTS | 39054.2326 | 39054.6847 | DAILY | 00007279 | DB_AUG | Rebate for No1 Bus & TK FDR for fdr upgrade | SPIPOWER | Z529 | Z529 - (RTS) UPRATE SUB TK 66KV FDR CONNECTION TO 1200A | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z52958A539054.2326388889 | Z52958A5 |  | Parent | TRUE | NO.1 66KV BUS AT RTS | 39054.2326 | 39054.6847 | DAILY | 00022323 | DB_AUG | Rebate for No1 & No6 Bus & TK FDR for fdr upgrade | SPIPOWER | Z529 | Z529 - (RTS) UPRATE SUB TK 66KV FDR CONNECTION TO 1200A | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025416239054.2520833333 | 10254162 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT MLTS | 39054.2521 | 39054.6951 | REPDAILY | 00337580 | SPIMAINT | Complete O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X49658A439055.2333333333 | X49658A4 |  | Parent | TRUE | NO.2 220KV BUS AT HOTS | 39055.2333 | 39055.6965 | REPDAILY | 00006939 | SPICAPX | Out W/O No 2 220kV bus extension | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49658A539055.2333333333 | X49658A5 | X49658A4 | Child | FALSE | EX - NO.2 TRANS BANK AT HOTS | 39055.2333 | 39055.6965 | DAILY | 00026246 | SPICAPX | Out W/O Perf calc for bus outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158B239055.2361111111 | Z53158B2 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39055.2361 | 39056.2771 | CONT | 00004776 | VEN_AUG | Bus outage to replace bus bi pods for TTS line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158H939055.2361111111 | Z53158H9 | Z53158B2 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39055.2361 | 39056.2771 | CONT | 00354024 | VEN_AUG | rebate Bus outage to remove bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024955439055.25625 | 10249554 |  | Parent | FALSE | EX - SMTS LINE/A2 TRANS 500KV CB AT KTS | 39055.2562 | 39059.6125 | CONT | [12 empty] | 0
_X43258J339055.2631944444 | X43258J3 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39055.2632 | 39055.6965 | REPDAILY | 00337584 | SPICAPX | Out W/O #2 Tr de-en daily during #1 220 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010278439055.2722222222 | 10102784 |  | Parent | FALSE | NO.6 GEN TRANS NO.4 BUS 220KV CB AT HWPS | 39055.2722 | 39059.5646 | CONT | [12 empty] | 0
_1025477739055.2916666667 | 10254777 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 39055.2917 | 39055.3431 | DAILY | 00331109 | SPIMAINT | Out W/O No1 66kV Cap bank for CT dga samples | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X38458G139055.3284722222 | X38458G1 |  | Parent | TRUE | EX - NO.2 66KV BUS AT TGTS | 39055.3285 | 39055.6687 | REPDAILY | 00003133 | SPICAPX | Out W/O Install bi-pods on bus in Bays K & M | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458G239055.3284722222 | X38458G2 | X38458G1 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39055.3285 | 39055.6687 | DAILY | 00003127 | SPICAPX | Out W/O Perf calc for No 2 66 bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025468339055.3368055556 | 10254683 |  | Parent | FALSE | B1 220/66KV TRANS AT TBTS | 39055.3368 | 39055.375 | DAILY | 00004901 | SPIMAINT | Take sample on B1 Tran CB C.T's De-energised only | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025477839055.3430555556 | 10254778 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39055.3431 | 39055.4049 | DAILY | 00331118 | SPIMAINT | Out W/O No2 66kV Cap bank for CT dga samples | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025441839055.3923611111 | 10254418 |  | Parent | TRUE | MBTS NO.1 220KV LINE CB AT DDTS | 39055.3924 | 39055.4375 | DAILY | [12 empty] | 0
_1025518039055.3923611111 | 10255180 | 10254418 | Child | FALSE | MBTS NO.1 220KV LINE AT DDTS | 39055.3924 | 39055.4375 | DAILY | 00012361 | SPIMAINT | Tyree CT Oil sample | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025468539055.4194444444 | 10254685 |  | Parent | FALSE | B2 220/66KV TRANS AT TBTS | 39055.4194 | 39055.4785 | DAILY | 00004902 | SPIMAINT | Take sample on B2 Tran CB C.T's De-energised only | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025477939055.4298611111 | 10254779 |  | Parent | FALSE | EX - MLTS NO.1 220KV LINE NO.1 BUS CB AT BATS (RESIDENT NOISE NOTIFICATION RE | 39055.4299 | 39055.5125 | DAILY | [12 empty] | 0
_1025436839055.4430555556 | 10254368 |  | Parent | FALSE | WOTS 330KV LINE NO.2 BUS CB AT DDTS | 39055.4431 | 39055.4736 | DAILY | [12 empty] | 0
_1025429639056.2145833333 | 10254296 | X46158K3 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39056.2146 | 39056.6667 | DAILY | 00331118 | SPICAPX | Rebate W/O No2 66 Cap bk during No2 66 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025429739056.2145833333 | 10254297 | X46158K3 | Child | FALSE | B2 220/66KV TRANS AT BATS | 39056.2146 | 39056.6667 | DAILY | 00006555 | SPICAPX | Perf calc W/O No2 Trans during No2 66 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158K339056.2145833333 | X46158K3 |  | Parent | TRUE | NO.2 66KV BUS AT BATS | 39056.2146 | 39056.6667 | DAILY | 00006561 | SPICAPX | Out W/O No2 66kV Bus to replace bus tie CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010158539056.2548611111 | 10101585 |  | Parent | FALSE | WOTS 330KV LINE/H3 TRANS CB AT DDTS | 39056.2549 | 39056.591 | REPDAILY | [12 empty] | 0
_X43258J339056.2583333333 | X43258J3 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39056.2583 | 39056.6875 | REPDAILY | 00337584 | SPICAPX | Out W/O #2 Tr de-en daily during #1 220 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158B339056.2770833333 | Z53158B3 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39056.2771 | 39056.9062 | DAILY | 00004776 | VEN_AUG | Reconnect TTS Line No 1 Bus CB No1 Bus & TTS Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158H639056.2770833333 | Z53158H6 | Z53158B3 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39056.2771 | 39056.9062 | DAILY | 00354024 | VEN_AUG | Rebate for No1 Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_Z53158H839056.2770833333 | Z53158H8 | Z53158B3 | Child | FALSE | TTS 220KV LINE AT ROTS | 39056.2771 | 39056.9062 | DAILY | 00023972 | VEN_AUG | Rebate for No1 Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025488439056.2847222222 | 10254884 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39056.2847 | 39058.8542 | CONT | 00356082 | GENCO | Isol for Gen Co: No 4 Gen CB isolated | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025495339056.2895833333 | 10254953 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB AT MLTS | 39056.2896 | 39056.3486 | DAILY | [12 empty] | 0
_X38458H039056.3256944444 | X38458H0 |  | Parent | FALSE | EX - NO.2 66KV BUS AT TGTS | 39056.3257 | 39056.7 | DAILY | 00003133 | SPICAPX | Out W/O No 2 66kV bus outage re-applied 5 Dec | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025495739057.0208333333 | 10254957 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 39057.0208 | 39063.5802 | CONT | [12 empty] | 0
_1010158539057.2506944445 | 10101585 |  | Parent | FALSE | WOTS 330KV LINE/H3 TRANS CB AT DDTS | 39057.2507 | 39057.5792 | REPDAILY | [12 empty] | 0
_X43258J339057.2576388889 | X43258J3 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39057.2576 | 39057.3708 | REPDAILY | 00337584 | SPICAPX | Out W/O #2 Tr de-en daily during #1 220 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z60358A239057.2722222222 | Z60358A2 |  | Parent | TRUE | NO.2 66KV BUS AT SVTS | 39057.2722 | 39057.6757 | DAILY | 00004861 | VEN_AUG | UPGRADE SV No1 FDR connections Bus & Line side | SPIPOWER | Z603 | Z603 - (SVTS) WORK ASSOC. WITH THE NEW ZONE SS SVW | Bus | Eastern | 66 |  |  |  | 0
_Z60358A339057.2722222222 | Z60358A3 | Z60358A2 | Child | FALSE | B2 220/66KV TRANS AT SVTS | 39057.2722 | 39057.6757 | DAILY | 00004850 | VEN_AUG | Avail of Plant UPGR SV No1 FDR Bus connections | SPIPOWER | Z603 | Z603 - (SVTS) WORK ASSOC. WITH THE NEW ZONE SS SVW | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158I739057.2798611111 | Z53158I7 |  | Parent | TRUE | ERTS NO.2 220KV LINE AT ROTS | 39057.2799 | 39057.3139 | DAILY | 00023971 | VEN_AUG | ERTS 2L & HWPS 1 de-energisation for pole erection | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158I839057.2798611111 | Z53158I8 | Z53158I7 | Child | FALSE | HWPS NO.1 220KV LINE AT ROTS | 39057.2799 | 39057.3139 | DAILY | 00023990 | VEN_AUG | ERTS 2L & HWPS 1 de-energisation for pole erection | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025469139057.3340277778 | 10254691 |  | Parent | FALSE | NO.4 GEN TRANS NO.1 BUS 220KV CB AT HWPS | 39057.334 | 39057.5833 | DAILY | [12 empty] | 0
_1025497339057.3722222222 | 10254973 |  | Parent | FALSE | R3 220/66/22KV TRANS AT RCTS | 39057.3722 | 39057.6375 | DAILY | 00361128 | FORCED | Out W/O No3 Trans to repair neut isol | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1025502139057.5854166667 | 10255021 |  | Parent | TRUE | MBTS-EPS 1 220KV N | 39057.5854 | 39060.1778 | CONT | 00055380 | BUSHFIRE | EPS 1 Line Trip due to Bushfire | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 1
_1025518839057.5854166667 | 10255188 | 10255021 | Child | FALSE | MBTS-EPS 2 220KV N | 39057.5854 | 39060.1778 | CONT | 00055381 | BUSHFIRE | EPS 2 Line Trip due to Bushfire | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 1 | FM Event bushfire
_1010346939058.2493055556 | 10103469 |  | Parent | FALSE | EX - SVTS NO.1 220KV LINE NO.4 BUS CB AT ROTS | 39058.2493 | 39059.6076 | CONT | [12 empty] | 0
_X43258J339058.2590277778 | X43258J3 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39058.259 | 39058.6597 | REPDAILY | 00337584 | SPICAPX | Out W/O #2 Tr de-en daily during #1 220 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025451139058.2673611111 | 10254511 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.4 MAIN TRANS CB AT HWTS | 39058.2674 | 39058.5972 | DAILY | [12 empty] | 0
_1025468639058.3201388889 | 10254686 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 39058.3201 | 39058.5521 | DAILY | [12 empty] | 0
_1025451639058.5277777778 | 10254516 | 10254515 | Child | FALSE | HWTS NO.3 500KV LINE AT LYPS | 39058.5278 | 39058.5507 | DAILY | 00016088 | FORCED | ADJUST SF6 GAS PRESSURE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025451539058.5277777778 | 10254515 |  | Parent | TRUE | HWTS NO.3 500KV LINE CB AT LYPS | 39058.5278 | 39058.5511 | DAILY | [12 empty] | 0
_1025507939058.6333333333 | 10255079 |  | Parent | FALSE | B4 TRANS 66KV CB AT FBTS | 39058.6333 | 39059.3354 | CONT | [12 empty] | 0
_1025508739058.6333333333 | 10255087 |  | Parent | FALSE | B4 TRANS 66KV CB AT FBTS | 39058.6333 | 39059.5479 | DAILY | [12 empty] | 0
_X43258J339059.2534722222 | X43258J3 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39059.2535 | 39059.4889 | REPDAILY | 00337584 | SPICAPX | Out W/O #2 Tr de-en daily during #1 220 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025507139059.2916666667 | 10255071 |  | Parent | FALSE | EX - EPS NO.2 220KV LINE CB AT MBTS | 39059.2917 | 39059.4319 | DAILY | [12 empty] | 0
_1025509539059.3354166667 | 10255095 |  | Parent | FALSE | SYN/COND AT FBTS | 39059.3354 | 39059.3597 | DAILY | 00002697 | FORCED | FBTS Syn Cond Trip | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025508339059.4319444445 | 10255083 |  | Parent | FALSE | EX - EPS NO.1 220KV LINE CB AT MBTS | 39059.4319 | 39059.5701 | DAILY | [12 empty] | 0
_1025557739059.7111111111 | 10255577 |  | Parent | FALSE | DDTS-SMTS 2 330KV | 39059.7111 | 39059.7465 | DAILY | 00328507 | BUSHFIRE | CFA requested outage | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025558439059.71875 | 10255584 |  | Parent | FALSE | BATS-BETS 220KV | 39059.7188 | 39059.8292 | DAILY | 00328505 | SW_NEM | Nemmco requested outage due to Bushfire outages | NEMMCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025557539059.7486111111 | 10255575 |  | Parent | FALSE | DDTS-SMTS 1 330KV | 39059.7486 | 39059.8104 | DAILY | 00328506 | BUSHFIRE | CFA requested outage | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025557839059.8118055556 | 10255578 |  | Parent | FALSE | DDTS-SMTS 2 330KV | 39059.8118 | 39059.8208 | DAILY | 00328507 | BUSHFIRE | CFA requested outage | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025557639059.8361111111 | 10255576 |  | Parent | FALSE | DDTS-SMTS 1 330KV | 39059.8361 | 39059.9194 | DAILY | 00328506 | BUSHFIRE | CFA requested outage | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025558339059.8395833333 | 10255583 |  | Parent | FALSE | BATS-BETS 220KV | 39059.8396 | 39059.9257 | DAILY | 00328505 | SW_NEM | Nemmco requested outage due to Bushfire outages | NEMMCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025558539059.8430555556 | 10255585 |  | Parent | FALSE | HOTS-RCTS 220KV | 39059.8431 | 39059.9278 | DAILY | 00328509 | SW_NEM | Nemmco requested outage due to Bushfire outages | NEMMCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z53158I939060.2298611111 | Z53158I9 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 39060.2299 | 39060.7382 | REPDAILY | 00004778 | VEN_AUG | No 2 Bus & TTS 220 kV Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158J039060.2298611111 | Z53158J0 | Z53158I9 | Child | FALSE | TTS 220KV LINE AT ROTS | 39060.2299 | 39060.7382 | REPDAILY | 00023972 | VEN_AUG | Rebate - No 2 Bus & TTS 220 kV Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_Z53158J139060.2298611111 | Z53158J1 | Z53158I9 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39060.2299 | 39060.7382 | REPDAILY | 00112418 | VEN_AUG | Rebate - No 2 Bus & TTS 220 kV Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X2A858R939060.5520833333 | X2A858R9 |  | Parent | FALSE | EX - NO.3 S/S TRANS AT BTS | 39060.5521 | 39104.2708 | DAILY | 00000938 | SPICAPX | disconnect cable from 3 s/s tr from isol sw | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Other Transformers | Western | 2.2 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_Z33458G639061.1861111111 | Z33458G6 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 39061.1861 | 39062.2382 | CONT | 00352791 | VEN_AUG | Replace No 1 Cooling Pump | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158I939061.2291666667 | Z53158I9 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 39061.2292 | 39061.5903 | REPDAILY | 00004778 | VEN_AUG | No 2 Bus & TTS 220 kV Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158J039061.2291666667 | Z53158J0 | Z53158I9 | Child | FALSE | TTS 220KV LINE AT ROTS | 39061.2292 | 39061.5903 | REPDAILY | 00023972 | VEN_AUG | Rebate - No 2 Bus & TTS 220 kV Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_Z53158J139061.2291666667 | Z53158J1 | Z53158I9 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39061.2292 | 39061.5903 | REPDAILY | 00112418 | VEN_AUG | Rebate - No 2 Bus & TTS 220 kV Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025513439061.6034722222 | 10255134 |  | Parent | FALSE | MBTS-EPS 1 220KV N | 39061.6035 | 39063.566 | CONT | 00055380 | BUSHFIRE | EPS 1 Line Trip due to bushfires | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 1 | FM Event bushfire
_1025513839061.6819444445 | 10255138 |  | Parent | FALSE | MBTS-EPS 2 220KV N | 39061.6819 | 39063.5694 | CONT | 00055381 | BUSHFIRE | EPS 2 Line Trip due to Bushfires | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 1 | FM Event bushfire
_Z53158B439062.2472222222 | Z53158B4 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39062.2472 | 39063.2292 | CONT | 00004776 | VEN_AUG | Bus outage to install bus bi pods HWPS No 1 L CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158H739062.2472222222 | Z53158H7 | Z53158B4 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39062.2472 | 39063.2292 | DAILY | 00354024 | VEN_AUG | Rebate for No1 Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1025450439062.3631944445 | 10254504 |  | Parent | FALSE | JLA NO.1 220KV LINE CB AT TBTS | 39062.3632 | 39062.3694 | DAILY | [12 empty] | 0
_1025515939062.4138888889 | 10255159 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB AT HWTS | 39062.4139 | 39062.4854 | DAILY | [12 empty] | 0
_Z53158B539063.2402777778 | Z53158B5 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39063.2403 | 39063.7618 | DAILY | 00004776 | VEN_AUG | No1 Bus outage & HWPS 1 L for reconnection | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158I039063.2402777778 | Z53158I0 | Z53158B5 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39063.2403 | 39063.7618 | DAILY | 00354024 | VEN_AUG | Rebate for No1 Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_Z53158I139063.2402777778 | Z53158I1 | Z53158B5 | Child | FALSE | HWPS NO.1 220KV LINE AT ROTS | 39063.2403 | 39063.7618 | CONT | 00023990 | VEN_AUG | Reconfigure HWPS No Line connection | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010347039063.2486111111 | 10103470 |  | Parent | FALSE | YPS NO.7 220KV LINE NO.3 BUS CB AT ROTS | 39063.2486 | 39064.5625 | CONT | [12 empty] | 0
_1025504339063.2958333333 | 10255043 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT BATS | 39063.2958 | 39063.3514 | DAILY | [12 empty] | 0
_1025521439063.2958333333 | 10255214 | 10255043 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 39063.2958 | 39063.3514 | DAILY | 00331109 | SPIMAINT | Oil sample from CB CT's | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025502539063.3 | 10255025 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT SMTS | 39063.3 | 39063.5778 | DAILY | [12 empty] | 0
_1025504439063.3486111111 | 10255044 |  | Parent | TRUE | EX - NO.2 66KV CAPACITOR BANK CB AT BATS | 39063.3486 | 39063.4229 | DAILY | [12 empty] | 0
_1025521339063.3486111111 | 10255213 | 10255044 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39063.3486 | 39063.4229 | DAILY | 00331118 | SPIMAINT | CT oil samples from CB | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025437139063.4506944444 | 10254371 |  | Parent | TRUE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39063.4507 | 39063.4736 | DAILY | [12 empty] | 0
_1025521239063.4506944444 | 10255212 | 10254371 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39063.4507 | 39063.4736 | DAILY | 00002863 | SPIMAINT | Tyree CT Oil sample | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025519439063.7618055556 | 10255194 |  | Parent | FALSE | EX - HWPS NO.1 220KV LINE NO.1 BUS CB AT ROTS | 39063.7618 | 39064.5826 | CONT | [12 empty] | 0
_1025452739064.2465277778 | 10254527 | X46158K5 | Child | FALSE | TGTS 220KV LINE AT BATS | 39064.2465 | 39064.7486 | DAILY | 00012435 | SPICAPX | Rebate W/O TGTS Line during No1 220kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025452839064.2465277778 | 10254528 | X46158K5 | Child | FALSE | B2 220/66KV TRANS AT BATS | 39064.2465 | 39064.7486 | DAILY | 00006555 | SPICAPX | Perf calc W/O #2 Trans during No1 220kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158K539064.2465277778 | X46158K5 |  | Parent | TRUE | NO.1 220KV BUS AT BATS | 39064.2465 | 39064.7486 | DAILY | 00006558 | SPICAPX | Out W/O #1 220 bus Connect BETS L fut 1B CB BS ROI | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025337439064.2590277778 | 10253374 |  | Parent | TRUE | EX - NO.4 66KV CAPACITOR BANK CB AT GTS | 39064.259 | 39064.6653 | DAILY | [12 empty] | 0
_1025339139064.2590277778 | 10253391 | 10253374 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39064.259 | 39064.6653 | DAILY | 00329879 | SPIMAINT | Rebate W/O No4 66 Cap BK for CB S-Ops O/H | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025517739064.2979166667 | 10255177 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39064.2979 | 39064.3194 | DAILY | [12 empty] | 0
_1025502739064.3069444445 | 10255027 |  | Parent | FALSE | HWTS NO.1 LINE/SYTS NO.1 LINE 500KV CB AT SMTS | 39064.3069 | 39064.6021 | DAILY | [12 empty] | 0
_1025437939064.3090277778 | 10254379 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 39064.309 | 39064.4382 | DAILY | [12 empty] | 0
_X38458G339064.33125 | X38458G3 |  | Parent | TRUE | EX - NO.1 220KV BUS AT TGTS | 39064.3313 | 39064.7069 | DAILY | 00003130 | SPICAPX | Out W/O Install bi-pods for future MLTS cb ROI | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458G439064.33125 | X38458G4 | X38458G3 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39064.3313 | 39064.7069 | DAILY | 00023231 | SPICAPX | Out W/O Perf calc for No 1 220kV bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025463439064.3326388889 | 10254634 |  | Parent | FALSE | APD NO.1/MLTS NO.1 LINE 500KV CB AT HYTS | 39064.3326 | 39064.4097 | DAILY | [12 empty] | 0
_1025463539064.4305555556 | 10254635 |  | Parent | FALSE | APD NO.2/MLTS NO.2 LINE 500KV CB AT HYTS | 39064.4306 | 39064.6194 | DAILY | [12 empty] | 0
_1025443139064.4395833333 | 10254431 |  | Parent | FALSE | DDTS 330KV LINE NO.2 BUS CB AT WOTS | 39064.4396 | 39064.534 | DAILY | [12 empty] | 0
_1025518239064.5416666667 | 10255182 |  | Parent | FALSE | EX - BETS 220KV LINE NO.1 BUS CB BUS SIDE ROI AT BATS | 39064.5417 | 39066.4049 | CONT | [12 empty] | 0
_1025397639064.5479166667 | 10253976 | X49758B3 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39064.5479 | 39064.7743 | DAILY | 00016040 | SPICAPX | Perf calc W/O No2 Trans during #3 66kV BUS outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025397739064.5479166667 | 10253977 | X49758B3 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT BETS | 39064.5479 | 39064.7743 | DAILY | 00350820 | SPICAPX | Rebate W/O 3A Cap bk during #3 66kV BUS outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1025397839064.5479166667 | 10253978 | X49758B3 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 39064.5479 | 39064.7743 | DAILY | 00016304 | SPICAPX | Rebate W/O 3B Cap bk during #3 66kV BUS outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758B339064.5479166667 | X49758B3 |  | Parent | TRUE | NO.3 66KV BUS AT BETS | 39064.5479 | 39064.7743 | DAILY | 00016366 | SPICAPX | Out W/O No3 66kV BUS to connect new MRO fdr CB | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025451539065.2083333333 | 10254515 |  | Parent | TRUE | HWTS NO.3 500KV LINE CB AT LYPS | 39065.2083 | 39065.3299 | DAILY | [12 empty] | 0
_1025451639065.2083333333 | 10254516 | 10254515 | Child | FALSE | HWTS NO.3 500KV LINE AT LYPS | 39065.2083 | 39065.3299 | DAILY | 00016088 | FORCED | ADJUST SF6 GAS PRESSURE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258H939065.2236111111 | X43258H9 |  | Parent | FALSE | BSS 220KV LINE AT RCTS | 39065.2236 | 39065.791 | DAILY | 00016966 | SPICAPX | Out W/O BSS Line to Commiss fut No 1 bus CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010348039065.2451388889 | 10103480 |  | Parent | FALSE | RWTS LINE/YPS NO.7 LINE 220KV CB AT ROTS | 39065.2451 | 39066.4618 | CONT | [12 empty] | 0
_X46158K839065.2597222222 | X46158K8 |  | Parent | FALSE | BETS 220KV LINE AT BATS | 39065.2597 | 39065.5479 | DAILY | 00012434 | SPICAPX | Out W/O BETS Line to commiss 1B CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025460039065.2777777778 | 10254600 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB AT MLTS | 39065.2778 | 39065.4736 | DAILY | [12 empty] | 0
_1025502939065.3013888889 | 10255029 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.2 BUS CB AT SMTS | 39065.3014 | 39065.5792 | DAILY | [12 empty] | 0
_1025443239065.3145833333 | 10254432 |  | Parent | FALSE | JINDERA 330KV LINE NO.1 BUS CB AT WOTS | 39065.3146 | 39065.4062 | DAILY | [12 empty] | 0
_1025443339065.4152777778 | 10254433 |  | Parent | FALSE | JINDERA 330KV LINE NO.2 BUS CB AT WOTS | 39065.4153 | 39065.5174 | DAILY | [12 empty] | 0
_X38458G539065.4201388889 | X38458G5 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 39065.4201 | 39065.6868 | DAILY | 00003131 | SPICAPX | Out W/O Bi-pods for No 2 220kV bus Bay A | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458G639065.4201388889 | X38458G6 | X38458G5 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39065.4201 | 39065.6868 | DAILY | 00003127 | SPICAPX | Out W/O Perf calc for bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025450539065.4388888889 | 10254505 |  | Parent | TRUE | JLA NO.1 220KV LINE CB AT TBTS | 39065.4389 | 39065.4424 | DAILY | [12 empty] | 0
_1025576339065.4388888889 | 10255763 | 10254505 | Child | FALSE | JLA NO.1 220KV LINE AT TBTS | 39065.4389 | 39065.4424 | DAILY | 00018301 | HVCUST | For JLA | HVCUST |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025528139065.6784722222 | 10255281 |  | Parent | FALSE | H2 330/220KV TRANS BANK AT SMTS | 39065.6785 | 39065.6847 | DAILY | 00026102 | BUSHFIRE | Off-loading of SMTS-H2 Trans (Bushfire) | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 1 | FM Event bushfire
_1025527639065.6784722222 | 10255276 |  | Parent | FALSE | SMTS NO.2 330KV LINE AT DDTS | 39065.6785 | 39065.7917 | DAILY | 00012356 | BUSHFIRE | Loss of DDTS-SMTS 2 Line (Bushfire) | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM Event bushfire
_1025527939065.6833333333 | 10255279 |  | Parent | FALSE | SMTS NO.1 330KV LINE AT DDTS | 39065.6833 | 39065.6847 | DAILY | 00012354 | BUSHFIRE | DDTS-SMTS 1 Line Trip due to Bushfires | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM Event bushfire
_1025528339065.6833333333 | 10255283 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT SMTS | 39065.6833 | 39065.6847 | DAILY | 00026101 | BUSHFIRE | Off-loading of SMTS-H1 Trans (Bushfire) | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 1 | FM Event bushfire
_1025528439065.6833333333 | 10255284 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 39065.6833 | 39065.6847 | DAILY | 00026099 | BUSHFIRE | Off-loading of SMTS-F2 Trans (Bushfire) | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 1 | FM Event bushfire
_1025523739065.6833333333 | 10255237 |  | Parent | FALSE | DDTS NO.1 330KV LINE SERIES CAPACITOR BANK AT SMTS | 39065.6833 | 39066.3479 | DAILY | 00327836 | BUSHFIRE | DDTS-SMTS 1 Line & Series Cap Trip due to Bushfire | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 1 | FM Event bushfire
_1025495939066.2548611111 | 10254959 |  | Parent | TRUE | EX - NO.2 MAIN TRANS 500KV CB AT HWTS | 39066.2549 | 39066.3264 | DAILY | [12 empty] | 0
_1025518539066.2548611111 | 10255185 | 10254959 | Child | FALSE | A2 515/230KV TRANS BANK AT HWTS | 39066.2549 | 39066.3264 | DAILY | 00337572 | SPIMAINT | Rebate - REPAIR CB AIR LEAK. | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025437239066.2715277778 | 10254372 |  | Parent | TRUE | SESS NO.2 275KV LINE/M2 TRANS CB AT HYTS | 39066.2715 | 39066.3222 | DAILY | [12 empty] | 0
_1025534739066.2715277778 | 10255347 | 10254372 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 39066.2715 | 39066.3222 | DAILY | 00002862 | SPIMAINT | Tyree CT Oil sample on CB, outage of Trans | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025522239066.3173611111 | 10255222 |  | Parent | FALSE | 415V AUTO CHANGEOVER EQUIPMENT AT BLTS | 39066.3174 | 39066.4889 | DAILY | [12 empty] | 0
_1010157239066.33125 | 10101572 |  | Parent | FALSE | NO.4 22KV/415V S/S TRANS AT DDTS | 39066.3313 | 39066.5424 | DAILY | 00003974 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Other Transformers | Alstom | 22 |  |  |  | 0
_1025499939066.3590277778 | 10254999 |  | Parent | FALSE | B5 220/66KV TRANS AT TTS | 39066.359 | 39066.5813 | DAILY | 00327874 | SPIMAINT | check "x" prot and ct's | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025503139066.3895833333 | 10255031 |  | Parent | FALSE | F2 TRANS NON AUTO 500KV CB AT SMTS | 39066.3896 | 39066.5868 | DAILY | [12 empty] | 0
_X46158K939066.4097222222 | X46158K9 |  | Parent | FALSE | BETS 220KV LINE X PROT AT BATS | 39066.4097 | 39066.6132 | REPDAILY | [12 empty] | 0
_1025530939066.6256944445 | 10255309 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE AT HWTS | 39066.6257 | 39066.6319 | DAILY | 00016237 | FORCED | Outage of HWTS-SMTS No 1 500kV Line | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025531039066.6256944445 | 10255310 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 39066.6257 | 39066.6319 | DAILY | 00337579 | FORCED | Outage of HWTS: No 3 Main Trans | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025531139066.6256944445 | 10255311 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 39066.6257 | 39070.5257 | CONT | [12 empty] | 0
_1025531339066.7847222222 | 10255313 |  | Parent | FALSE | DDTS NO.1 330KV LINE SERIES CAPACITOR BANK AT SMTS | 39066.7847 | 39070.6389 | DAILY | 00327836 | FAULT | SMTS: DDTS No 1 LIne Series cap bank | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_Z53158J239067.2291666667 | Z53158J2 |  | Parent | TRUE | EX - NO.1 220KV BUS AT ERTS | 39067.2292 | 39068.5722 | CONT | 00004378 | VEN_AUG | Replace 1-3 B.T CB No 1B/S 220 kV ISOLS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158J339067.2291666667 | Z53158J3 | Z53158J2 | Child | FALSE | B1 220/66KV TRANS AT ERTS | 39067.2292 | 39068.5722 | CONT | 00004370 | VEN_AUG | Avail of plant Replace 1-3 B.T No1 B 220 kV ISOLS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025496539067.2361111111 | 10254965 |  | Parent | TRUE | EX - NO.1 MAIN TRANS 500KV CB AT HWTS | 39067.2361 | 39067.5069 | DAILY | [12 empty] | 0
_1025518639067.2361111111 | 10255186 | 10254965 | Child | FALSE | A1 515/230KV TRANS AT HWTS | 39067.2361 | 39067.5069 | DAILY | 00009772 | SPIMAINT | Rebate-REPLACE LEAKING GRADING CAPACITOR. | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025459339067.25 | 10254593 | X46158L0 | Child | FALSE | MLTS NO.1 220KV LINE AT BATS | 39067.25 | 39067.75 | DAILY | 00012429 | SPICAPX | Rebate W/O MLTS No 1 Line to decommiss 2 Bus CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025459139067.25 | 10254591 | X46158L0 | Child | FALSE | WBTS 220KV LINE AT BATS | 39067.25 | 39067.7792 | DAILY | 00012410 | SPICAPX | Rebate W/O HOTS Line during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025459239067.25 | 10254592 | X46158L0 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39067.25 | 39067.7792 | DAILY | 00006554 | SPICAPX | Perf calc W/O #1 TR during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158L039067.25 | X46158L0 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 39067.25 | 39067.7792 | DAILY | 00006559 | SPICAPX | Out W/O No2 220kV Bus to disconnect MLTS 1L CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025518739067.2527777778 | 10255187 |  | Parent | FALSE | EX - ATS LINE/A2 TRANS 220KV CB LINE SIDE ISOL AT KTS | 39067.2528 | 39067.4396 | DAILY | [12 empty] | 0
_X2A858Q939067.3173611111 | X2A858Q9 |  | Parent | FALSE | EX - NO.1 22KV BUS AT BTS | 39067.3174 | 39067.4201 | DAILY | 00000945 | SPICAPX | commission & test all new cb's | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Bus | Western | 22 |  |  |  | 0
_X2A858R039067.4645833333 | X2A858R0 |  | Parent | FALSE | EX - NO.2 22KV BUS AT BTS | 39067.4646 | 39067.5181 | DAILY | 00000947 | SPICAPX | commission & test all new cb's | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Bus | Western | 22 |  |  |  | 0
_1025458139067.4895833333 | 10254581 | X49758B6 | Child | FALSE | R4 220/66/22KV TRANS AT BETS | 39067.4896 | 39067.7472 | DAILY | 00016220 | SPICAPX | Perf calc W/O No4 Trans during #4 66kV BUS outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025458239067.4895833333 | 10254582 | X49758B6 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT BETS | 39067.4896 | 39067.7472 | DAILY | 00350819 | SPICAPX | Rebate W/O 2A Cap bk during #4 66kV BUS outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1025458339067.4895833333 | 10254583 | X49758B6 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 39067.4896 | 39067.7472 | DAILY | 00016274 | SPICAPX | Rebate W/O 2B Cap bk during #4 66kV BUS outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758B639067.4895833333 | X49758B6 |  | Parent | TRUE | NO.4 66KV BUS AT BETS | 39067.4896 | 39067.7472 | DAILY | 00016367 | SPICAPX | Out W/O No4 66kV BUS to connect new CMN FDR CB | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X2A858R139067.5201388889 | X2A858R1 |  | Parent | FALSE | EX - NO.3 22KV BUS AT BTS | 39067.5201 | 39067.6236 | DAILY | 00000948 | SPICAPX | commission & test all new cb's | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Bus | Western | 22 |  |  |  | 0
_X46158L139067.75 | X46158L1 |  | Parent | FALSE | MLTS NO.1 220KV LINE AT BATS | 39067.75 | 39068.5153 | CONT | 00012429 | SPICAPX | Out W/O MLTS No 1 Line to decommiss its 2 Bus CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025468739068.2305555556 | 10254687 |  | Parent | FALSE | NO.2A 220KV BUS AT BLTS | 39068.2306 | 39068.6222 | DAILY | 00002644 | SPIMAINT | o/h bus & isol/esw, no.2 220/66kv & 22kv tr | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025281639068.25625 | 10252816 |  | Parent | FALSE | B3 220/66KV TRANS AT RTS | 39068.2562 | 39068.5687 | DAILY | 00329288 | SPIMAINT | B3 Tran checks charge to 10242819 | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025532739068.3729166667 | 10255327 |  | Parent | FALSE | ROTS 220KV LINE AT TTS | 39068.3729 | 39068.5799 | DAILY | 00015733 | DBPROX | AGLSCAP:ROTS-TTS 220kV Line | DISTCO |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025532839068.3743055556 | 10255328 |  | Parent | FALSE | SMTS NO.1 220KV LINE AT TTS | 39068.3743 | 39068.5799 | DAILY | 00015732 | DBPROX | AGLSCAP:SMTS-TTS No 1 220kV Line | DISTCO |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025533139068.5895833333 | 10255331 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39068.5896 | 39070.7049 | CONT | 00017270 | FAULT | SVC Tripped Cap Connection fault | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025533739068.9861111111 | 10255337 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB AT MLTS | 39068.9861 | 39071.2597 | CONT | [12 empty] | 0
_1025536639068.9861111111 | 10255366 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB AT MLTS | 39068.9861 | 39072.5972 | CONT | [12 empty] | 0
_Z53158G139069.2305555556 | Z53158G1 |  | Parent | TRUE | NO.4 220KV BUS AT ROTS | 39069.2306 | 39069.7215 | CONT | 00329012 | VEN_AUG | Relocate MTS 1L connection to Bay F | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158I539069.2305555556 | Z53158I5 | Z53158G1 | Child | FALSE | MTS NO.1 220KV LINE AT ROTS | 39069.2306 | 39069.7215 | CONT | 00350667 | VEN_AUG | Relocate MTS 1L connection to Bay F | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025517539069.2673611111 | 10255175 |  | Parent | TRUE | NO.2B 66KV CAPACITOR BANK CB AT RWTS | 39069.2674 | 39069.5875 | DAILY | [12 empty] | 0
_1025517639069.2673611111 | 10255176 | 10255175 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39069.2674 | 39069.5875 | DAILY | 00331179 | SPIMAINT | Rebate - Investigate contact resistance on CB | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025534839069.2715277778 | 10255348 |  | Parent | TRUE | SMTS-TTS 1 220KV WT | 39069.2715 | 39069.5868 | DAILY | 00022767 | DBPROX | Proximity for AGL Disco | DISTCO |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025534939069.2715277778 | 10255349 | 10255348 | Child | FALSE | ROTS-TTS 220KV E | 39069.2715 | 39069.5868 | DAILY | 00022762 | DBPROX | Proximity for AGL | DISTCO |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1010177239069.2791666667 | 10101772 |  | Parent | FALSE | AUX TRANS 'C' NO.2 BUS 220KV CB AT YPS | 39069.2792 | 39069.5431 | DAILY | [12 empty] | 0
_1025534639069.3694444445 | 10255346 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 39069.3694 | 39069.7278 | DAILY | 00007456 | FORCED | Burnt 66kV Cross arm | SPIPOWER |  |  | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025530239069.3993055556 | 10255302 |  | Parent | FALSE | NO.2 UNIT 230/10.5KV TRANS AT JLGB | 39069.3993 | 39069.5521 | CONT | 00009831 | GENCO | SCAP:JLGSB2 Isolation & Earthed for Power Station | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1025537739069.5381944444 | 10255377 |  | Parent | FALSE | EX - EPS NO.1 220KV LINE AT MBTS | 39069.5382 | 39070.1167 | CONT | 00011751 | BUSHFIRE | EPS 1 Line Trip due to bushfires | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 1 | FM Event bushfire
_1025538439069.5381944444 | 10255384 |  | Parent | FALSE | MBTS-EPS 2 220KV N | 39069.5382 | 39070.1167 | CONT | 00055381 | BUSHFIRE | EPS 2 Line Trip due to bushfires | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 1 | FM Event bushfire
_1025563639069.5493055556 | 10255636 |  | Parent | FALSE | NO.1B 220/66/22KV TRANS AT RCTS | 39069.5493 | 39069.625 | DAILY | 00016758 | FAULT | RCTS: Tripping No1 66kV Bus | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025530339069.5625 | 10255303 |  | Parent | FALSE | NO.4 UNIT 230/10.5KV TRANS AT JLGA | 39069.5625 | 39069.6222 | CONT | 00009819 | GENCO | SCAP:JLGSA4 Isolation & Earthed for Power Station | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1025562039069.6013888889 | 10255620 |  | Parent | TRUE | NO.2B TRANS AT RCTS | 39069.6014 | 39069.6104 | DAILY | 00016760 | FAULT | Fault on 2 & 3 66 kV BUSES | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025562439069.6013888889 | 10255624 | 10255620 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 39069.6014 | 39069.6104 | DAILY | 00361128 | FAULT | Fault on 2 & 3 66 kV BUSES | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1025562639069.6013888889 | 10255626 | 10255620 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 39069.6014 | 39069.6104 | DAILY | 00016897 | FAULT | Fault on 2 & 3 66 kV BUSES | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025562739069.6013888889 | 10255627 | 10255620 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 39069.6014 | 39069.6104 | DAILY | 00357254 | FAULT | Fault on 2 & 3 66 kV BUSES | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025562839069.6013888889 | 10255628 | 10255620 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 39069.6014 | 39069.6104 | DAILY | 00359892 | FAULT | Fault on 2 & 3 66 kV BUSES | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z53158G239070.2291666667 | Z53158G2 |  | Parent | TRUE | NO.4 220KV BUS AT ROTS | 39070.2292 | 39070.7632 | DAILY | 00329012 | VEN_AUG | Bus Outage & MTS No 1 Line & A1 Trans 220 Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158I639070.2291666667 | Z53158I6 | Z53158G2 | Child | FALSE | MTS NO.1 220KV LINE AT ROTS | 39070.2292 | 39070.7632 | CONT | 00350667 | VEN_AUG | Relocate MTS 1L connection to Bay F | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158J439070.2291666667 | Z53158J4 | Z53158G2 | Child | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39070.2292 | 39070.7632 | CONT | 00354002 | VEN_AUG | Rebate for Relocate MTS 1L connection to Bay F | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1010167839070.2527777778 | 10101678 |  | Parent | FALSE | SHTS NO.3 220KV LINE NO.2 BUS CB AT GNTS | 39070.2528 | 39070.6319 | REPDAILY | [12 empty] | 0
_X38458H139070.3159722222 | X38458H1 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39070.316 | 39070.6028 | DAILY | 00023231 | SPICAPX | Out W/O Replace cons bladder on Future B1 Trans | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025538139070.3541666667 | 10255381 |  | Parent | FALSE | JLGA NO.3 UNIT TRANS DISC CB AT JLGA | 39070.3542 | 39070.5521 | DAILY | [12 empty] | 0
_1025538239070.3541666667 | 10255382 |  | Parent | FALSE | JLGA NO.4 UNIT TRANS DISC CB AT JLGA | 39070.3542 | 39070.5521 | DAILY | [12 empty] | 0
_X32058C539070.3784722222 | X32058C5 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39070.3785 | 39070.6521 | REPDAILY | 00004569 | SPICAPX | Avail of plant B3 Trans for No3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058C639070.3784722222 | X32058C6 | X32058C5 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39070.3785 | 39070.6521 | REPDAILY | 00026900 | SPICAPX | Avail of plant B3 Trans for No3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025538339070.4166666667 | 10255383 |  | Parent | FALSE | JLGB NO.2 UNIT TRANS DISC CB AT JLGB | 39070.4167 | 39070.5208 | DAILY | [12 empty] | 0
_Z53158G539071.2263888889 | Z53158G5 |  | Parent | FALSE | NO.4 220KV BUS EXTENSION G AT ROTS | 39071.2264 | 39110.3333 | CONT | 00004779 | VEN_AUG | ROTS 4 Bus Ext Outage no longer supplying MTS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025461739071.2347222222 | 10254617 | X43258I0 | Child | FALSE | BSS 220KV LINE AT RCTS | 39071.2347 | 39071.7083 | DAILY | 00016966 | SPICAPX | Rebate W/O BSS Line to de-commiss BSS No 2 bus CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025461839071.2347222222 | 10254618 | X43258I0 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39071.2347 | 39071.7083 | DAILY | 00337584 | SPICAPX | Perf calc W/O No2 TR during No2 220kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025461939071.2347222222 | 10254619 | X43258I0 | Child | FALSE | KGTS 220KV LINE AT RCTS | 39071.2347 | 39071.7083 | DAILY | 00016959 | SPICAPX | Rebate W/O KGTS Line during No2 220kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025462039071.2347222222 | 10254620 | X43258I0 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RCTS | 39071.2347 | 39071.7083 | DAILY | 00360383 | SPICAPX | Rebate W/O #2 220 Cap during No2 220kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258I039071.2347222222 | X43258I0 |  | Parent | TRUE | NO.2 220KV BUS-CAPBK EXTENSION AT RCTS | 39071.2347 | 39071.7083 | DAILY | 00016916 | SPICAPX | Out W/O #2 220 BUS to de-commiss BSS No 2 bus CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53458A639071.2395833333 | Z53458A6 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39071.2396 | 39072.6076 | CONT | [12 empty] | 0
_X32058C539071.2625 | X32058C5 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39071.2625 | 39071.6451 | REPDAILY | 00004569 | SPICAPX | Avail of plant B3 Trans for No3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058C639071.2625 | X32058C6 | X32058C5 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39071.2625 | 39071.6451 | REPDAILY | 00026900 | SPICAPX | Avail of plant B3 Trans for No3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010167839071.2659722222 | 10101678 |  | Parent | FALSE | SHTS NO.3 220KV LINE NO.2 BUS CB AT GNTS | 39071.266 | 39071.6125 | REPDAILY | [12 empty] | 0
_1010177139071.26875 | 10101771 |  | Parent | FALSE | AUX TRANS 'C' NO.1 BUS 220KV CB AT YPS | 39071.2688 | 39071.5521 | DAILY | [12 empty] | 0
_1025509239071.2715277778 | 10255092 |  | Parent | TRUE | S431 RWTS-TTS L 220KV | 39071.2715 | 39071.4917 | DAILY | [12 empty] | 0
_1025563439071.2715277778 | 10255634 | 10255092 | Child | FALSE | RWTS-TTS 220KV WT | 39071.2715 | 39071.4917 | DAILY | 00119311 | SPIMAINT | Tree cutting | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025503739071.3020833333 | 10255037 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.2 BUS CB AT SMTS | 39071.3021 | 39071.5924 | DAILY | [12 empty] | 0
_X2A858S339071.4263888889 | X2A858S3 |  | Parent | FALSE | EX - 1-2 22KV BUS TIE CB AT BTS | 39071.4264 | 39071.5347 | DAILY | [12 empty] | 0
_X2A858S439071.4263888889 | X2A858S4 |  | Parent | FALSE | EX - 2-3 22KV BUS TIE CB AT BTS | 39071.4264 | 39071.5347 | DAILY | [12 empty] | 0
_1010178039071.7229166667 | 10101780 |  | Parent | FALSE | AUX TRANS 'B' 220KV E/SW AT YPS | 39071.7229 | 39072.5556 | CONT | [12 empty] | 0
_1025559039071.8534722222 | 10255590 |  | Parent | FALSE | B5 220/66KV TRANS AT TTS | 39071.8535 | 39072.3278 | CONT | 00327874 | FAULT | B5 Transformer trip SIR 10255588 | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010167839072.2555555556 | 10101678 |  | Parent | FALSE | SHTS NO.3 220KV LINE NO.2 BUS CB AT GNTS | 39072.2556 | 39072.5958 | REPDAILY | [12 empty] | 0
_1025503939072.2944444444 | 10255039 |  | Parent | FALSE | ROTS NO.3 LINE/KTS LINE 500KV CB AT SMTS | 39072.2944 | 39072.3729 | DAILY | [12 empty] | 0
_1025561039072.3958333333 | 10255610 |  | Parent | FALSE | EX - NO.4 66KV CAPACITOR BANK CB AT GTS | 39072.3958 | 39073.4313 | CONT | [12 empty] | 0
_1025572739072.3958333333 | 10255727 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39072.3958 | 39073.4313 | CONT | 00329879 | FAULT | CB Failed to close | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025563339072.53125 | 10255633 |  | Parent | FALSE | ROTS-MTS 1 220KV E | 39072.5312 | 39072.6146 | DAILY | 00022746 | FAULT | CB Opened at ROTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025567139073.6416666667 | 10255671 |  | Parent | FALSE | NO.3 66KV CAPACITOR BANK AT WMTS | 39073.6417 | 39080.5715 | CONT | 00003191 | FAULT | Burnt Connection No3 Cap Bank | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025564239074.0361111111 | 10255642 |  | Parent | FALSE | KTS -WMTS 1 220KV WT | 39074.0361 | 39074.5333 | CONT | 00022718 | FAULT | KTS-WMTS Unsuccessful ARC See SIR 10255643 | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025565239076.9201388889 | 10255652 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39076.9201 | 39077.3486 | CONT | 00019243 | FAULT | HOTS SVC Outage for Trip Investigation | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X2A858S239080.4180555556 | X2A858S2 |  | Parent | FALSE | EX - (O.O.S) NS 22KV FDR 176 CB AT BTS | 39080.4181 | 39080.459 | DAILY | [12 empty] | 0
_1025568539082.4861111111 | 10255685 |  | Parent | FALSE | SVC 220KV CB AT HOTS | 39082.4861 | 39082.5146 | CONT | [12 empty] | 0
_1025568939082.6340277778 | 10255689 |  | Parent | FALSE | LY NO.3 66KV FDR AT MWTS | 39082.634 | 39082.6722 | CONT | 00016142 | FAULT | MWTS LY No3 Line Tripped due to lightning | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025569239082.8819444444 | 10255692 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39082.8819 | 39082.9021 | DAILY | 00019243 | FAULT | Tripping of The SVC | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025569639082.9798611111 | 10255696 |  | Parent | FALSE | NO.4 66KV BUS AT BETS | 39082.9799 | 39083.0674 | CONT | [12 empty] | 0
_1025575239082.9798611111 | 10255752 |  | Parent | FALSE | NO.2A 66KV CAPACITOR BANK AT BETS | 39082.9799 | 39083.0674 | DAILY | [12 empty] | 0
_1025575639082.9798611111 | 10255756 |  | Parent | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 39082.9799 | 39083.0674 | DAILY | [12 empty] | 0
_1025796739082.9798611111 | 10257967 |  | Parent | FALSE | R4 220/66/22KV TRANS AT BETS | 39082.9799 | 39083.0674 | CONT | [12 empty] | 0
_1025569839083.0291666667 | 10255698 |  | Parent | FALSE | NO.2 500KV BUS AT LYPS | 39083.0292 | 39083.0785 | CONT | 00010024 | GENCO | Tripping of The No2 220kV BUS | GENCO |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1025528739084.2763888889 | 10255287 |  | Parent | FALSE | NO.1 11/220KV TRANS BANK AT MPS | 39084.2764 | 39092.6139 | CONT | 00001082 | SPIMAINT | No1 & 2 Trans for clean up & C.T Testing | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025572539084.5201388889 | 10255725 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39084.5201 | 39084.5806 | DAILY | 00019243 | SPIMAINT | SVC S/S Change Over Fault Investigation | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X2A858S539085.3958333333 | X2A858S5 |  | Parent | FALSE | EX - (O.O.S) NS 22KV FDR 176 CB AT BTS | 39085.3958 | 39085.4354 | DAILY | [12 empty] | 0
_1027775539086.9881944445 | 10277755 |  | Parent | FALSE | NO.7 GEN TRANS 220KV CB AT HWPS | 39086.9882 | 39455.6764 | CONT | [12 empty] | 0
_1025575739087.2180555556 | 10255757 |  | Parent | FALSE | NO.1 CSC AT ROTS | 39087.2181 | 39087.4042 | DAILY | 00004718 | SPIMAINT | REPLACE INSULATOR | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025585439087.8333333333 | 10255854 |  | Parent | FALSE | NO.3 GEN 220/16.5KV TRANS AT HWPS | 39087.8333 | 39090.8743 | CONT | 00009644 | GENCO | SCAP: No3 Gen Isolation requested by Power Station | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1025536139088.2125 | 10255361 | X49858A9 | Child | FALSE | EX - EPS NO.1 220KV LINE AT MBTS | 39088.2125 | 39089.841 | CONT | 00011751 | SPICAPX | Rebate W/O EPS #1 Line to Loop DDTS & EPS #1 Lines | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025536239088.2125 | 10255362 |  | Parent | FALSE | EX - DDTS NO.1 220KV LINE AT MBTS | 39088.2125 | 39089.841 | CONT | 00011748 | SPICAPX | RebateW/O DDTS #1 Line to Loop DDTS & EPS #1 Lines | SPIPOWER |  | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025586539088.2125 | 10255865 | X49858A9 | Child | FALSE | DPS 220KV LINE AT MBTS | 39088.2125 | 39089.841 | CONT | 00011754 | SPICAPX | Outage due to No1 Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858A939088.2125 | X49858A9 |  | Parent | TRUE | EX - NO.1 220KV BUS AT MBTS | 39088.2125 | 39089.841 | CONT | 00004001 | SPICAPX | Out W/O No1 220kV Bus to Loop DDTS & EPS #1 Lines | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158J839088.2298611111 | Z53158J8 |  | Parent | TRUE | EX - NO.3 220KV BUS AT ERTS | 39088.2299 | 39089.5007 | CONT | 00004379 | VEN_AUG | Replace 1-3 B.T No3 B 220 kV ISOLS-No3 Trans out | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158J939088.2298611111 | Z53158J9 | Z53158J8 | Child | FALSE | B3 220/66KV TRANS AT ERTS | 39088.2299 | 39089.5007 | CONT | 00004371 | VEN_AUG | Replace 1-3 B.T No3 B 220 kV ISOLS - No3 Trans out | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025469039088.2555555556 | 10254690 |  | Parent | FALSE | NO.3 GEN TRANS NO.1 BUS 220KV CB AT HWPS | 39088.2556 | 39088.6167 | DAILY | [12 empty] | 0
_1025469239088.2701388889 | 10254692 |  | Parent | FALSE | NO.3 GEN TRANS NO.2 BUS 220KV CB AT HWPS | 39088.2701 | 39088.6167 | DAILY | [12 empty] | 0
_1025585139088.4104166667 | 10255851 |  | Parent | FALSE | WMTS NO.2 220KV LINE AT FBTS | 39088.4104 | 39088.4174 | DAILY | 00017157 | FORCED | FBTS:WMTS No 2 Line CB SF6 Top Up | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025576239089.8409722222 | 10255762 |  | Parent | TRUE | EX - NO.1 220KV BUS AT MBTS | 39089.841 | 39090.3653 | CONT | 00004001 | VEN_AUG | Isolated | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025586439089.8409722222 | 10255864 | 10255762 | Child | FALSE | DPS 220KV LINE AT MBTS | 39089.841 | 39090.3653 | CONT | 00011754 | SPICAPX | Outage due to No1 Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025546239091.2513888889 | 10255462 |  | Parent | TRUE | TSTS 220KV LINE NO.1 BUS CB LINE SIDE ISOL AT TTS | 39091.2514 | 39091.4764 | DAILY | [12 empty] | 0
_1025589139091.2513888889 | 10255891 | 10255462 | Child | FALSE | TSTS 220KV LINE AT TTS | 39091.2514 | 39091.4764 | DAILY | 00015736 | SPIMAINT | repair hot spot on line side ISOL | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258J739091.2694444445 | X43258J7 |  | Parent | FALSE | R3 TRANS NO.2 BUS 220KV CB AT RCTS | 39091.2694 | 39091.2854 | DAILY | [12 empty] | 0
_1009278339091.2833333333 | 10092783 |  | Parent | TRUE | HWPS/MPS LINE 220KV E/SW AT MWTS | 39091.2833 | 39091.5951 | DAILY | [12 empty] | 0
_1025589339091.2833333333 | 10255893 | 10092783 | Child | FALSE | HWPS-MPS 220KV LINE AT MWTS | 39091.2833 | 39091.5951 | DAILY | 00016132 | SPIMAINT | 220kV E/SW O/Haul (EH) | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258J839091.4548611111 | X43258J8 |  | Parent | FALSE | R3 TRANS NO.2 BUS 220KV CB AT RCTS | 39091.4549 | 39091.4632 | DAILY | [12 empty] | 0
_Z53158C239092.2041666667 | Z53158C2 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 39092.2042 | 39092.6882 | DAILY | 00004778 | VEN_AUG | Bus outage to remove bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158J539092.2041666667 | Z53158J5 | Z53158C2 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39092.2042 | 39092.6882 | DAILY | 00112418 | VEN_AUG | Rebate -Cap bank Bus outage to remove bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1009277439092.2708333333 | 10092774 |  | Parent | FALSE | MPS-MWTS 220KV LINE AT HWPS | 39092.2708 | 39092.6139 | DAILY | 00015789 | SPIMAINT | O/Haul - MPS-MWTS LINE at HWPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025665039092.5506944445 | 10256650 |  | Parent | FALSE | SYN/COND AT TSTS | 39092.5507 | 39092.6722 | CONT | 00007626 | FAULT | TSTS Syn Cond shut down- water supply shut off | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025592939092.6138888889 | 10255929 |  | Parent | FALSE | LY NO.4 66KV FDR NO.3 BUS CB AT MWTS | 39092.6139 | 39191.35 | CONT | [12 empty] | 0
_1025666039092.6736111111 | 10256660 |  | Parent | FALSE | EX - NO.4A 66KV CAPACITOR BANK AT TTS | 39092.6736 | 39092.6931 | CONT | 00001486 | FAULT | TTS No4A Cap Bank 66kV CB Failed to close | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025666139092.6736111111 | 10256661 |  | Parent | FALSE | NO.4B 66KV CAPACITOR BANK AT TTS | 39092.6736 | 39092.6931 | CONT | 00337509 | FAULT | TTS No4A Cap Bank 66kV CB Failed to close | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025588739093.2708333333 | 10255887 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.4 MAIN TRANS CB AT HWTS | 39093.2708 | 39093.5771 | DAILY | [12 empty] | 0
_1025593839093.3958333333 | 10255938 |  | Parent | FALSE | YWPS NO.4 220KV LINE AT YPS | 39093.3958 | 39098.3243 | CONT | 00016428 | GENCO | Request for generator isolation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025597839093.8784722222 | 10255978 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 39093.8785 | 39097.834 | CONT | 00356083 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027795739093.9576388889 | 10277957 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 39093.9576 | 39460.4549 | CONT | [12 empty] | 0
_Z53458A539094.2263888889 | Z53458A5 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39094.2264 | 39094.7257 | DAILY | [12 empty] | 0
_X38458H839094.3104166667 | X38458H8 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39094.3104 | 39094.6681 | REPDAILY | 00023231 | SPICAPX | Fix Conservator Air Bag Assembly | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53458B339094.8152777778 | Z53458B3 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39094.8153 | 39096.7312 | CONT | [12 empty] | 0
_1025600239094.8680555556 | 10256002 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 39094.8681 | 39097.0013 | CONT | 00356086 | GENCO | SCAP on Isolations for HWPS No8 Gen | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158K039095.2402777778 | Z53158K0 |  | Parent | TRUE | EX - NO.3 220KV BUS AT ERTS | 39095.2403 | 39096.5444 | CONT | 00004379 | VEN_AUG | Replace 3-4 B.T No3 B 220 kV ISOLS - No3 Trans out | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158K139095.2402777778 | Z53158K1 | Z53158K0 | Child | FALSE | B3 220/66KV TRANS AT ERTS | 39095.2403 | 39096.5444 | CONT | 00004371 | VEN_AUG | Replace 3-4 B.T No3 B 220 kV ISOLS - No3 Trans out | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53458A939095.2673611111 | Z53458A9 |  | Parent | FALSE | HWTS NO.3 500KV LINE AT ROTS (RTF) | 39095.2674 | 39095.8396 | DAILY | 00359383 | VEN_AUG | Line de-energised for protection modification | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458G939095.3159722222 | X38458G9 |  | Parent | FALSE | MLTS-TGTS 220KV W | 39095.316 | 39095.8049 | DAILY | 00022740 | SPICAPX | Out W/O MLTS Line changeover & No 2 220kV BUS | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025600339095.3729166667 | 10256003 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39095.3729 | 39097.8333 | CONT | 00356084 | GENCO | Isolation on No6 Gen Trans | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458H239095.8048611111 | X38458H2 |  | Parent | FALSE | MLTS-TGTS 220KV W | 39095.8049 | 39096.484 | DAILY | 00022740 | SPICAPX | Out W/O To tune the Line Chokes | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z50658A239096.2256944444 | Z50658A2 |  | Parent | TRUE | NO.3 66KV BUS AT HTS | 39096.2257 | 39096.684 | DAILY | 00004458 | SPIMAINT | Erect future CBTS/MMC/FTN Emerg suply CB B/S isol | SPIPOWER | Z506 | Z506 - (HTS) OPTIMISING 66KV CBS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z50658A339096.2256944444 | Z50658A3 | Z50658A2 | Child | FALSE | B3 220/66KV TRANS AT HTS | 39096.2257 | 39096.684 | DAILY | 00004447 | SPIMAINT | Avail of plantCBTS/MMC/FTN Emerg suply CB B/S isol | SPIPOWER | Z506 | Z506 - (HTS) OPTIMISING 66KV CBS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53458B239096.2583333333 | Z53458B2 |  | Parent | FALSE | CBTS NO.4 500KV LINE AT ROTS (RTF) | 39096.2583 | 39096.7312 | DAILY | 00356730 | VEN_AUG | Line de-energised for Protection Mods | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025600839096.3659722222 | 10256008 |  | Parent | TRUE | NO.4A 66KV CAPACITOR BANK AT SVTS | 39096.366 | 39097.6021 | CONT | 00004825 | FAULT | No 4 66 kV Cap Bank isolated pending repairs | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025653939096.3659722222 | 10256539 | 10256008 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT SVTS | 39096.366 | 39097.6021 | CONT | 00329600 | FAULT | No 4 66 kV Cap Bank isolated pending repairs | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025535139096.3756944445 | 10255351 |  | Parent | FALSE | MLTS-HYTS 1 500KV W | 39096.3757 | 39096.3806 | DAILY | 00022630 | SW_NEM | To switch line reactor | NEMMCO |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025535239096.3826388889 | 10255352 |  | Parent | FALSE | MLTS-HYTS 2 500KV W | 39096.3826 | 39096.3917 | DAILY | 00022633 | SW_NEM | To switch line reactor | NEMMCO |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025601139096.4756944444 | 10256011 |  | Parent | FALSE | HWTS NO.3 500KV LINE AT ROTS (RTF) | 39096.4757 | 39096.4833 | DAILY | 00359383 | FAULT | HWTS-ROTS No 3 500kV Line Trip | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025666239096.7479166667 | 10256662 |  | Parent | FALSE | CBTS NO.4 500KV LINE AT ROTS (RTF) | 39096.7479 | 39096.7493 | CONT | 00356730 | FAULT | CBTS-ROTS No4 500kV Line Inadvertent Trip. | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025545339097.1368055556 | 10255453 | X32058C7 | Child | FALSE | EX - NO.2 220/66KV TRANS BANK AT MTS | 39097.1368 | 39097.4062 | CONT | 00026899 | SPICAPX | Proximity for crane work B3 & ROTS No 3 Line | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025546039097.1368055556 | 10255460 | X32058C8 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39097.1368 | 39097.4062 | CONT | 00026900 | SPICAPX | Proximity for crane work B3 & ROTS No 3 Line | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058C739097.1368055556 | X32058C7 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MTS | 39097.1368 | 39097.4062 | DAILY | 00004564 | SPICAPX | De-commission L2 tranformer | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058C839097.1368055556 | X32058C8 | X32058C7 | Child | TRUE | EX - NO.2 220/22KV TRANS BANK AT MTS | 39097.1368 | 39097.4062 | CONT | 00026902 | SPICAPX | Avail of plant Trans taken out of commision | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158B639097.25 | Z53158B6 |  | Parent | FALSE | NO.1 220KV BUS AT ROTS | 39097.25 | 39097.6653 | DAILY | 00004776 | VEN_AUG | Proximity to stand Future A2 Isolator in Bay Q | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X4C458A339097.2715277778 | X4C458A3 |  | Parent | FALSE | EX - HWPS NO.4 220KV LINE NO.2 BUS CB AT JLTS | 39097.2715 | 39115.4104 | CONT | [12 empty] | 0
_1009174039097.3041666667 | 10091740 |  | Parent | FALSE | KTS 500KV LINE NO.1 BUS CB AT SMTS | 39097.3042 | 39097.5882 | DAILY | [12 empty] | 0
_1025591439097.3166666667 | 10255914 |  | Parent | FALSE | EX - A4 TRANS NO.1 BUS 500KV CB AT KTS | 39097.3167 | 39097.4549 | DAILY | [12 empty] | 0
_X43258J939097.3576388889 | X43258J9 |  | Parent | TRUE | EX - NO.1 220KV BUS AT RCTS | 39097.3576 | 39097.6201 | DAILY | 00016901 | SPICAPX | Out W/O Commission B/S Isols of Future CB's | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258K439097.3576388889 | X43258K4 | X43258J9 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT RCTS | 39097.3576 | 39097.6201 | DAILY | 00360382 | SPICAPX | Out W/O Perf calc for No 1 220kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258K539097.3576388889 | X43258K5 | X43258J9 | Child | FALSE | HOTS-RCTS 220KV | 39097.3576 | 39097.6201 | DAILY | 00328509 | SPICAPX | Out W/O Perf calc for No 1 220kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458J139097.3868055556 | X38458J1 |  | Parent | FALSE | MLTS-TGTS 220KV W | 39097.3868 | 39097.6875 | DAILY | 00022740 | SPICAPX | Out W/O Commission MLTS LINE No 2 Bus 220kV CB | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025605839098.2347222222 | 10256058 |  | Parent | FALSE | YPS NO.1 220KV LINE AT HWPS | 39098.2347 | 39098.3083 | CONT | 00015795 | FAULT | Line Tripping | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025552239098.2923611111 | 10255522 |  | Parent | FALSE | HWTS NO.2 500KV LINE NO.2 BUS CB AT SMTS | 39098.2924 | 39098.4604 | DAILY | [12 empty] | 0
_1025442439098.3368055556 | 10254424 |  | Parent | FALSE | MLTS NO.1 500KV LINE AT HYTS | 39098.3368 | 39098.4826 | DAILY | 00021195 | SPIMAINT | Out W/O Tyree CT Oil sample | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025608839098.6263888889 | 10256088 |  | Parent | FALSE | SMTS NO.1 330KV LINE AT DDTS | 39098.6264 | 39098.9688 | CONT | 00012354 | BUSHFIRE | Loss of DDTS-SMTS No 1 330kV Line due to Bushfire | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM event as per SP AusNet Service Performance Incentive Scheme | Refer to NEMMCO Power System Incident Report "System Separation and load Shedding 16 January 2007" available on NEMMCO Public Website. Also refer VenCorp System Incident Report 16 January 2007" available on VenCorp website. VenCorp granted exemptions from the Rebate Scheme for these outages. Refer SP AusNet System Incident Report 10256082. Refer Joint media release DSSE and CFA dated 18 January 2007. refer SP-AusNet Internal Magazine "Connected" Dated 19 January 2007.
_1025609539098.6270833333 | 10256095 |  | Parent | FALSE | BETS-FVTS-SHTS 220KV NB | 39098.6271 | 39098.7604 | CONT | 00026225 | BUSHFIRE | BETS/FVTS/SHTS Line offloaded at SHTS due Bushfire | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM event as per SP AusNet Service Performance Incentive Scheme
_1025609339098.6270833333 | 10256093 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT SMTS | 39098.6271 | 39098.9688 | CONT | 00026101 | BUSHFIRE | SMTS: H1 Trans offloaded due to Bushfire | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 1 | FM event as per SP AusNet Service Performance Incentive Scheme | Refer to NEMMCO Power System Incident Report "System Separation and load Shedding 16 January 2007" available on NEMMCO Public Website. Also refer VenCorp System Incident Report 16 January 2007" available on VenCorp website. VenCorp granted exemptions from the Rebate Scheme for these outages. Refer SP AusNet System Incident Report 10256082. Refer Joint media release DSSE and CFA dated 18 January 2007. refer SP-AusNet Internal Magazine "Connected" Dated 19 January 2007.
_1025608939098.6270833333 | 10256089 |  | Parent | FALSE | SMTS NO.2 330KV LINE AT DDTS | 39098.6271 | 39098.9701 | CONT | 00012356 | BUSHFIRE | Loss of DDTS-SMTS No 2 330kV Line due to Bushfire | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM event as per SP AusNet Service Performance Incentive Scheme | Refer to NEMMCO Power System Incident Report "System Separation and load Shedding 16 January 2007" available on NEMMCO Public Website. Also refer VenCorp System Incident Report 16 January 2007" available on VenCorp website. VenCorp granted exemptions from the Rebate Scheme for these outages. Refer SP AusNet System Incident Report 10256082. Refer Joint media release DSSE and CFA dated 18 January 2007. refer SP-AusNet Internal Magazine "Connected" Dated 19 January 2007.
_1025609039098.6270833333 | 10256090 |  | Parent | FALSE | MBTS NO.2 220KV LINE AT EPSY | 39098.6271 | 39098.9729 | CONT | 00087036 | BUSHFIRE | Loss of EPS-MBTS No 2 330kV Line due to Bushfire | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 1 | FM event as per SP AusNet Service Performance Incentive Scheme | Refer to NEMMCO Power System Incident Report "System Separation and load Shedding 16 January 2007" available on NEMMCO Public Website. Also refer VenCorp System Incident Report 16 January 2007" available on VenCorp website. VenCorp granted exemptions from the Rebate Scheme for these outages. Refer SP AusNet System Incident Report 10256082. Refer Joint media release DSSE and CFA dated 18 January 2007. refer SP-AusNet Internal Magazine "Connected" Dated 19 January 2007.
_1025609139098.6270833333 | 10256091 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT EPSY | 39098.6271 | 39098.9743 | CONT | 00087035 | BUSHFIRE | Loss of EPS-MBTS No 1 330kV Line due to Bushfire | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 1 | FM event as per SP AusNet Service Performance Incentive Scheme | Refer to NEMMCO Power System Incident Report "System Separation and load Shedding 16 January 2007" available on NEMMCO Public Website. Also refer VenCorp System Incident Report 16 January 2007" available on VenCorp website. VenCorp granted exemptions from the Rebate Scheme for these outages. Refer SP AusNet System Incident Report 10256082. Refer Joint media release DSSE and CFA dated 18 January 2007. refer SP-AusNet Internal Magazine "Connected" Dated 19 January 2007.
_1025609239098.6270833333 | 10256092 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 39098.6271 | 39098.9743 | CONT | 00060187 | BUSHFIRE | Loss of EPS-MBTS No 1 330kV Line due to Bushfire | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM event as per SP AusNet Service Performance Incentive Scheme | Refer to NEMMCO Power System Incident Report "System Separation and load Shedding 16 January 2007" available on NEMMCO Public Website. Also refer VenCorp System Incident Report 16 January 2007" available on VenCorp website. VenCorp granted exemptions from the Rebate Scheme for these outages. Refer SP AusNet System Incident Report 10256082. Refer Joint media release DSSE and CFA dated 18 January 2007. refer SP-AusNet Internal Magazine "Connected" Dated 19 January 2007.
_1025577439099.2979166667 | 10255774 |  | Parent | FALSE | HWTS NO.2 LINE/SYTS NO.2 LINE 500KV CB AT SMTS | 39099.2979 | 39099.541 | DAILY | [12 empty] | 0
_1025610739099.5298611111 | 10256107 |  | Parent | FALSE | NO.2 TRANS NO.2 BUS 66KV CB AT KGTS | 39099.5299 | 39099.5972 | DAILY | [12 empty] | 0
_1025613939099.9472222222 | 10256139 |  | Parent | FALSE | NO.7 GEN 220/16.5KV TRANS AT HWPS | 39099.9472 | 39102.3306 | CONT | 00009648 | GENCO | Power Station requirement | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1025607239100.2618055556 | 10256072 |  | Parent | FALSE | HWPS NO.1 220KV LINE AT YPS | 39100.2618 | 39100.3958 | DAILY | 00016409 | SPIMAINT | Replace insulator after flash over | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258L239100.2777777778 | X43258L2 |  | Parent | FALSE | KGTS-RCTS 220KV NB | 39100.2778 | 39100.6576 | DAILY | 00026223 | SPICAPX | Out W/O Commission KGTS LINE No 1 BUS CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49658A639100.2895833333 | X49658A6 |  | Parent | FALSE | NO.1 66KV BUS AT HOTS | 39100.2896 | 39100.5417 | DAILY | 00006940 | SPICAPX | Out W/O No 1 66 Bus VT & No 1 Reactor founds | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025552639100.3020833333 | 10255526 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT SMTS | 39100.3021 | 39100.5764 | DAILY | [12 empty] | 0
_X32058E039100.3020833333 | X32058E0 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39100.3021 | 39100.6174 | DAILY | 00004569 | SPICAPX | N03 Bus 1-3 B.T & EL fdr intsall structures | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058E139100.3020833333 | X32058E1 | X32058E0 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39100.3021 | 39100.6174 | DAILY | 00026900 | SPICAPX | Avail of plant for No 3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025552839101.3090277778 | 10255528 |  | Parent | FALSE | F2 TRANS NO.2 BUS 500KV CB AT SMTS | 39101.309 | 39101.5458 | DAILY | [12 empty] | 0
_X49758B939101.3125 | X49758B9 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT BETS | 39101.3125 | 39101.375 | DAILY | 00016035 | SPICAPX | No 1 and 2 S/S Tr Connections in Turn | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758B839101.3784722222 | X49758B8 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT BETS | 39101.3785 | 39101.5181 | DAILY | 00016431 | SPICAPX | No 2 S/S Trans connection of new AC Supply cbles | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1010423339102.2763888889 | 10104233 |  | Parent | FALSE | B4 220/66KV TRANS AT BLTS | 39102.2764 | 39102.325 | DAILY | 00002615 | SPIMAINT | O/HAUL Transformer Div Mechanism (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010190839103.23125 | 10101908 |  | Parent | FALSE | NO.3 66KV BUS AT BLTS | 39103.2312 | 39103.5333 | DAILY | 00002651 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025621039103.2472222222 | 10256210 |  | Parent | FALSE | W2 GEN TRANS NO.2 BUS 220KV CB AT YPS | 39103.2472 | 39107.5904 | CONT | [12 empty] | 0
_Z53158K239103.2625 | Z53158K2 |  | Parent | FALSE | EX - 1-3 220KV BUS TIE CB AT ERTS | 39103.2625 | 39103.3812 | DAILY | [12 empty] | 0
_1025621139103.3076388889 | 10256211 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 39103.3076 | 39104.934 | CONT | 00356079 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X2A858S639104.1805555556 | X2A858S6 |  | Parent | FALSE | TTS NO.3 220KV LINE AT BTS | 39104.1806 | 39104.4771 | DAILY | 00015959 | SPICAPX | connect earthing sw aux switches & test interlocks | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258L539104.2340277778 | X43258L5 |  | Parent | TRUE | NO.2 220KV BUS-CAPBK EXTENSION AT RCTS | 39104.234 | 39104.6354 | DAILY | 00016916 | SPICAPX | Remove and make alterations to Bus in Bays H&J | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258L639104.2340277778 | X43258L6 | X43258L5 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39104.234 | 39104.6354 | DAILY | 00337584 | SPICAPX | Pref Calc W/O for No2 Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258L739104.2340277778 | X43258L7 | X43258L5 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RCTS | 39104.234 | 39104.6354 | DAILY | 00360383 | SPICAPX | Pref Calc W/O for No2 Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258L839104.2340277778 | X43258L8 | X43258L5 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 39104.234 | 39104.6354 | DAILY | 00361128 | SPICAPX | Pref Calc W/O for No2 Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X32058D839104.2479166667 | X32058D8 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39104.2479 | 39104.4785 | DAILY | 00004569 | SPICAPX | N03 Bus 1-3 B.T & EL fdr intsall structures | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058D939104.2479166667 | X32058D9 | X32058D8 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39104.2479 | 39104.4785 | DAILY | 00026900 | SPICAPX | Avail of plant for No 3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X2A858S939104.275 | X2A858S9 |  | Parent | FALSE | EX - (O.O.S) NO.1 AUX TRANS 2.2KV CB AT BTS | 39104.275 | 39112.2951 | CONT | [12 empty] | 0
_X2A858S739105.1708333333 | X2A858S7 |  | Parent | FALSE | RTS 220KV LINE AT BTS | 39105.1708 | 39105.4285 | DAILY | 00015960 | SPICAPX | connect earthing sw aux switches & test interlocks | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858B039105.2111111111 | X49858B0 |  | Parent | FALSE | EX - NO.1 220KV BUS AT MBTS | 39105.2111 | 39105.4667 | CONT | 00004001 | SPICAPX | Out W/O No1 220kV Bus- to dismantle/remove bus | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025576439105.2277777778 | 10255764 |  | Parent | FALSE | B1 220/66KV TRANS AT WMTS | 39105.2278 | 39105.5139 | DAILY | 00003233 | SPIMAINT | top up white & blue phase bushings | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025614339105.2527777778 | 10256143 |  | Parent | TRUE | AUX TRANS 'A' 220KV CB BUS SIDE ROI AT YPS | 39105.2528 | 39105.4917 | DAILY | [12 empty] | 0
_1025614439105.2527777778 | 10256144 | 10256143 | Child | FALSE | ROTS NO.8 220KV LINE AT YPS | 39105.2528 | 39105.4917 | DAILY | 00016416 | SPIMAINT | rebate for No2 Bus repair Isol | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025614539105.2527777778 | 10256145 | 10256143 | Child | FALSE | HWPS NO.2 220KV LINE AT YPS | 39105.2528 | 39105.4917 | DAILY | 00016412 | SPIMAINT | rebate for No2 Bus repair Isol | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010122139105.2770833333 | 10101221 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT ERTS | 39105.2771 | 39105.6104 | DAILY | 00004373 | SPIMAINT | O/HAUL Transformer without Div Sw (VSCAP Needed) | SPIPOWER |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1010178239105.4916666667 | 10101782 |  | Parent | FALSE | AUX TRANS 'A' 220KV LINE E/SW AT YPS | 39105.4917 | 39105.6278 | DAILY | [12 empty] | 0
_1025625539105.6145833333 | 10256255 |  | Parent | FALSE | CBTS NO.4 500KV LINE NO.3 BUS CB AT HWTS | 39105.6146 | 39107.2708 | CONT | [12 empty] | 0
_Z53158L039106.2097222222 | Z53158L0 |  | Parent | FALSE | ERTS NO.2 220KV LINE AT ROTS | 39106.2097 | 39107.6479 | CONT | 00023971 | VEN_AUG | Re configure line connections | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49658A739106.2722222222 | X49658A7 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 39106.2722 | 39106.4882 | DAILY | 00359897 | SPICAPX | Out W/O Excavating foundations | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X38458J439106.3180555556 | X38458J4 |  | Parent | FALSE | EX - NO.1 220KV BUS AT TGTS | 39106.3181 | 39106.6993 | DAILY | 00003130 | SPICAPX | Out W/O Install Fut B1 Trans 66kV bus supports | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49658A839106.4902777778 | X49658A8 |  | Parent | FALSE | NO.2 66KV REACTOR AT HOTS | 39106.4903 | 39106.6382 | DAILY | 00357255 | SPICAPX | Out W/O Founds for new CB | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X2A858T139106.5263888889 | X2A858T1 |  | Parent | FALSE | EX - (O.O.S) NS 22KV FDR 176 CB AT BTS | 39106.5264 | 39106.5875 | DAILY | [12 empty] | 0
_1025625739106.6881944445 | 10256257 |  | Parent | FALSE | AUX TRANS 'B' 220KV CB CT R/PH AT YPS | 39106.6882 | 39107.5896 | CONT | [12 empty] | 0
_1025630339106.6888888889 | 10256303 |  | Parent | FALSE | EX - BATS 220KV LINE NO.1 BUS CB AT TGTS | 39106.6889 | 39107.6667 | CONT | [12 empty] | 0
_1025625439107.2708333333 | 10256254 |  | Parent | FALSE | CBTS NO.4 500KV LINE NO.3 BUS CB CT B/PH AT HWTS | 39107.2708 | 39112.4646 | DAILY | [12 empty] | 0
_1025626039107.3145833333 | 10256260 |  | Parent | FALSE | DDTS NO.1 330KV LINE SERIES CAPACITOR BANK AT SMTS | 39107.3146 | 39107.4646 | DAILY | 00327836 | FAULT | investigate/repair battery earth faults | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49758C239107.4111111111 | X49758C2 |  | Parent | FALSE | EX - EHK 66KV FDR CB AT BETS | 39107.4111 | 39107.691 | DAILY | [12 empty] | 0
_1025637339107.8333333333 | 10256373 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 39107.8333 | 39109.3681 | CONT | [12 empty] | 0
_X2A858T639109.2930555556 | X2A858T6 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT BTS | 39109.2931 | 39109.3681 | DAILY | [12 empty] | 0
_1025638839110.0536342593 | 10256388 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39110.0536 | 39111.9972 | CONT | 00356084 | GENCO | Isolation for generator | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458J539110.3131944445 | X38458J5 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 39110.3132 | 39110.5528 | DAILY | 00003131 | SPICAPX | Out W/O Install bi-pods in Bay C of 220kV sw/yard | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458J739110.3131944445 | X38458J7 | X38458J5 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39110.3132 | 39110.5528 | DAILY | 00003127 | SPICAPX | Out W/O Perf calc for bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025619639111.2263888889 | 10256196 | X43258L9 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39111.2264 | 39122.7146 | CONT | 00337584 | SPICAPX | Pref Calc W/O for No2 Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025619739111.2263888889 | 10256197 | X43258L9 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RCTS | 39111.2264 | 39122.7146 | CONT | 00360383 | SPICAPX | Pref Calc W/O for No2 Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025619839111.2263888889 | 10256198 | X43258L9 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 39111.2264 | 39122.7146 | CONT | 00361128 | SPICAPX | Pref Calc W/O for No2 Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X43258L939111.2263888889 | X43258L9 |  | Parent | TRUE | NO.2 220KV BUS-CAPBK EXTENSION AT RCTS | 39111.2264 | 39122.7146 | CONT | 00016916 | SPICAPX | Replace No2 220kV BUS | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010306939111.2416666667 | 10103069 |  | Parent | FALSE | MLTS NO.1 500KV LINE NO.2 BUS CB AT SYTS | 39111.2417 | 39112.6167 | REPDAILY | [12 empty] | 0
_1025638739111.2506944445 | 10256387 |  | Parent | FALSE | KTS 500KV LINE AT SYTS | 39111.2507 | 39111.259 | REPDAILY | 00016967 | SPIMAINT | De en line to isol MLTS 1L 2B CB | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025638639111.2534722222 | 10256386 |  | Parent | FALSE | MLTS NO.1 500KV LINE AT SYTS | 39111.2535 | 39111.2604 | REPDAILY | 00016969 | SPIMAINT | De en line to isolate MLTS 1 L 2B CB | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025618439111.2708333333 | 10256184 | X4C458B1 | Child | FALSE | MWTS NO.1 220KV LINE AT JLTS | 39111.2708 | 39111.6021 | DAILY | 00015947 | SPICAPX | HWPS 4 LINE / MWTS #1 CB LINE CONNECTIONS | SPIPOWER | X4C4 | X4C4 - (JLTS) REPLACE 3AS2 220KV CBS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X4C458B139111.2708333333 | X4C458B1 |  | Parent | TRUE | HWPS NO.4 220KV LINE AT JLTS | 39111.2708 | 39111.6021 | DAILY | 00015940 | SPICAPX | HWPS 4 LINE No 2 Bus CB LINE CONNECTIONS | SPIPOWER | X4C4 | X4C4 - (JLTS) REPLACE 3AS2 220KV CBS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025664439112.2416666667 | 10256644 | X49658B1 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 39112.2417 | 39112.7493 | DAILY | 00359897 | SPICAPX | Out W/O Includes No 2 66 bus also, B3 trans commis | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025664539112.2416666667 | 10256645 | X49658B1 | Child | FALSE | NO.2 66KV REACTOR AT HOTS | 39112.2417 | 39112.7493 | DAILY | 00357255 | SPICAPX | Out W/O Includes No 2 66 bus also, B3 trans commis | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49658B139112.2416666667 | X49658B1 |  | Parent | TRUE | NO.2 220KV BUS AT HOTS | 39112.2417 | 39112.7493 | DAILY | 00006939 | SPICAPX | Out W/O Includes No 2 66 bus also, B3 trans commis | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010128139112.2625 | 10101281 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT LY | 39112.2625 | 39112.5326 | DAILY | 00009894 | SPIMAINT | O/Haul - No.2 Cap Bank at LY | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025651039112.2631944444 | 10256510 |  | Parent | TRUE | B2 220/66KV TRANS AT SVTS | 39112.2632 | 39112.3069 | DAILY | 00004850 | FAULT | Mid Phase drop at T11 on ROTS-SVTS 2 Line | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025651339112.2631944444 | 10256513 | 10256510 | Child | FALSE | B1 220/66KV TRANS AT HTS | 39112.2632 | 39112.3069 | DAILY | 00004445 | FAULT | Mid Phase drop at T11 on ROTS-SVTS 2 Line | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025651539112.2631944444 | 10256515 | 10256510 | Child | FALSE | SVTS-HTS 2 220KV E | 39112.2632 | 39112.3069 | DAILY | 00022773 | FAULT | Mid Phase drop at T11 on ROTS-SVTS 2 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025647739112.2631944444 | 10256477 |  | Parent | FALSE | ROTS-SVTS 2 220KV E | 39112.2632 | 39112.5771 | DAILY | 00022756 | FAULT | Mid Phase drop at T11 | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A858T539112.2861111111 | X2A858T5 |  | Parent | FALSE | EX - (O.O.S) NS 22KV FDR 193 CB AT BTS | 39112.2861 | 39116.5396 | CONT | [12 empty] | 0
_X2A858T339112.2861111111 | X2A858T3 |  | Parent | FALSE | EX - (O.O.S) NS 22KV FDR 176 CB AT BTS | 39112.2861 | 39116.7604 | CONT | [12 empty] | 0
_X2A858T439112.2861111111 | X2A858T4 |  | Parent | FALSE | EX - NS 22KV FDR 190 CB AT BTS | 39112.2861 | 39117.5972 | CONT | [12 empty] | 0
_X49658B839113.2118055556 | X49658B8 |  | Parent | FALSE | NO.2 220KV BUS X PROT AT HOTS | 39113.2118 | 39117.6677 | CONT | [12 empty] | 0
_1009276939113.2701388889 | 10092769 |  | Parent | FALSE | MWTS NO.4 66KV FDR AT LY | 39113.2701 | 39113.566 | DAILY | 00015997 | SPIMAINT | O/Haul - MWTS No.4 66kV LINE at LY | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025658639113.3722222222 | 10256586 |  | Parent | FALSE | EX - NO.2 TRANS BANK AT HOTS | 39113.3722 | 39113.3833 | DAILY | 00026246 | FAULT | No2 BUS trip | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025627039113.4159722222 | 10256270 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 39113.416 | 39113.5604 | DAILY | [12 empty] | 0
_1025371939114.2270833333 | 10253719 | X46158J7 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39114.2271 | 39114.6396 | REPDAILY | 00006554 | SPICAPX | Perf calc W/O No1 Trans during No1 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025372039114.2270833333 | 10253720 | X46158J7 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 39114.2271 | 39114.6396 | REPDAILY | 00331109 | SPICAPX | Rebate W/O No1 Cap bank during No1 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X46158J739114.2270833333 | X46158J7 |  | Parent | TRUE | NO.1 66KV BUS AT BATS | 39114.2271 | 39114.6396 | DAILY | 00006560 | SPICAPX | Out W/O No1 66kV Bus to replace BGL-BMH CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010131239114.2715277778 | 10101312 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.2 BUS CB AT LYPS | 39114.2715 | 39114.5347 | DAILY | [12 empty] | 0
_X49658C139114.2736111111 | X49658C1 |  | Parent | FALSE | NO.2 220KV BUS AT HOTS | 39114.2736 | 39117.2174 | DAILY | 00006939 | SPICAPX | Out W/O B3 Trans soak bus de-energisation only | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025622639114.2916666667 | 10256226 |  | Parent | FALSE | A4 500/220KV TRANS DELUGE SYSTEM AT KTS | 39114.2917 | 39114.3812 | DAILY | [12 empty] | 0
_1025661439114.3590277778 | 10256614 |  | Parent | FALSE | B5 220/66KV TRANS AT TTS | 39114.359 | 39114.6333 | DAILY | 00327874 | FAULT | B5 transformer trip. | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023293939114.3854166667 | 10232939 |  | Parent | FALSE | WOTS 330KV LINE NO.2 BUS CB AT DDTS | 39114.3854 | 39114.5389 | DAILY | [12 empty] | 0
_1025660639114.5631944445 | 10256606 |  | Parent | FALSE | WBTS 220KV LINE NO.2 BUS CB AT HOTS | 39114.5632 | 39119.5674 | DAILY | [12 empty] | 0
_1025661539114.5854166667 | 10256615 |  | Parent | FALSE | EX - NO.2 TRANS BANK AT HOTS | 39114.5854 | 39114.7097 | DAILY | 00026246 | FORCED | No.2 Transformer forced outage | ALSTOM |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025622839115.2451388889 | 10256228 |  | Parent | FALSE | B2 220/66KV TRANS AT KTS | 39115.2451 | 39115.6604 | DAILY | 00001148 | SPIMAINT | replace buckoltz relay & replace faulty lower fan | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010127939115.2694444445 | 10101279 |  | Parent | FALSE | 2-4 500KV BUS TIE CB AT LYPS | 39115.2694 | 39115.5188 | DAILY | [12 empty] | 0
_Z53458B739115.3548611111 | Z53458B7 |  | Parent | FALSE | NO.2 500KV BUS AT ROTS | 39115.3549 | 39115.5819 | DAILY | 00362955 | VEN_AUG | EAP No 2 500 Bus Check operation of E/SW's & ROIS | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1025670639115.375 | 10256706 |  | Parent | TRUE | NO.3 220KV CAPACITOR BANK CB AT ROTS | 39115.375 | 39115.4361 | CONT | [12 empty] | 0
_1025796139115.375 | 10257961 | 10256706 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39115.375 | 39115.4361 | CONT | 00112417 | FORCED | Investigate CB Trip (Phase discre) on energisation | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X46158L239115.5046180556 | X46158L2 |  | Parent | FALSE | NO.1 66KV BUS AT BATS | 39115.5046 | 39115.5326 | DAILY | 00006560 | SPICAPX | Out W/O No1 66kV Bus to commiss BGL-BMH CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025813339115.5104166667 | 10258133 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 39115.5104 | 39129.8056 | CONT | 00351939 | FORCED | Investigate No 1 220 kV Cap Bank Faulty Trip ccts | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1025665939115.5548611111 | 10256659 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 39115.5549 | 39115.6167 | DAILY | 00060938 | APDALCOA | HYTS-APD 2L de-energised for APD. | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025670439115.575 | 10256704 |  | Parent | FALSE | NO.1 220KV BUS AT DDTS | 39115.575 | 39115.616 | CONT | 00003976 | FORCED | Isolate No 1 220 kV Cap Bank - Faulty Trip CCTs | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025813039115.575 | 10258130 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT DDTS | 39115.575 | 39115.616 | CONT | 00012361 | FORCED | Investigate No 1 220 kV Cap Bank Faulty Trip ccts | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025813139115.575 | 10258131 |  | Parent | FALSE | GNTS NO.1 220KV LINE AT DDTS | 39115.575 | 39115.616 | CONT | 00352475 | FORCED | Investigate No 1 220 kV Cap Bank Faulty Trip ccts | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025813239115.575 | 10258132 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT DDTS | 39115.575 | 39115.616 | CONT | 00337558 | FORCED | Investigate No 1 220 kV Cap Bank Faulty Trip ccts | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025670539115.6159722222 | 10256705 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK CB AT DDTS | 39115.616 | 39115.8056 | CONT | [12 empty] | 0
_Z53158L539116.2055555556 | Z53158L5 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39116.2056 | 39117.6833 | CONT | 00354002 | VEN_AUG | Relocate A1 Tran 220kV Line to new poles E2,E4,E5 | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 3
_1025670239116.2319444444 | 10256702 |  | Parent | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39116.2319 | 39116.5625 | CONT | 00007399 | FAULT | Rebalance No 2A Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025661139116.2347222222 | 10256611 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT SVTS | 39116.2347 | 39116.4062 | DAILY | 00351700 | SPIMAINT | Replace insulators | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025637739116.2798611111 | 10256377 |  | Parent | FALSE | B4 220/66KV TRANS AT BLTS | 39116.2799 | 39116.5708 | DAILY | 00002615 | SPIMAINT | replace faulty bearings in trans mechanism | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025661739116.4090277778 | 10256617 |  | Parent | FALSE | ROTS NO.2 220KV LINE AT SVTS | 39116.409 | 39116.6583 | DAILY | 00351701 | SPIMAINT | Change insulators | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49658B739117.2173611111 | X49658B7 |  | Parent | FALSE | NO.2 220KV BUS AT HOTS | 39117.2174 | 39117.5444 | DAILY | 00006939 | SPICAPX | Out W/O Includes 66kV bus & de-commiss No 2 Trans | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058E539117.2590277778 | X32058E5 |  | Parent | FALSE | EX - NO.3 220/22KV TRANS BANK AT MTS | 39117.259 | 39117.3257 | DAILY | 00026903 | SPICAPX | Investiage cable trenching job | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X24258B039117.2861111111 | X24258B0 |  | Parent | FALSE | L1 220/22KV TRANS AT WMTS | 39117.2861 | 39117.5146 | DAILY | 00003234 | SPICAPX | commission new auto oltc panel | SPIPOWER | X242 | X242 - (WMTS) UPGRADE VOLTAGE REG OF 22KV BUSES | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058E639117.3638888889 | X32058E6 |  | Parent | FALSE | EX - NO.1 220/22KV TRANS BANK AT MTS | 39117.3639 | 39117.4285 | DAILY | 00026901 | SPICAPX | Investiage cable trenching job | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X24258B139117.5159722222 | X24258B1 |  | Parent | FALSE | L3 220/22KV TRANS AT WMTS | 39117.516 | 39117.6625 | DAILY | 00003237 | SPICAPX | commission new auto oltc panel | SPIPOWER | X242 | X242 - (WMTS) UPGRADE VOLTAGE REG OF 22KV BUSES | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158L339119.2319444444 | X46158L3 |  | Parent | FALSE | MLTS NO.1 220KV LINE AT BATS | 39119.2319 | 39119.6549 | REPDAILY | 00012429 | SPICAPX | Out W/O MLTS No1 Line for proximity clearance | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025639439119.2506944445 | 10256394 |  | Parent | FALSE | NO.3 66KV CAPACITOR BANK AT WMTS | 39119.2507 | 39119.5833 | DAILY | 00003191 | FAULT | re-balance cap bank | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V62258A039119.2541666667 | V62258A0 |  | Parent | FALSE | HWTS NO.1 LINE/SYTS NO.1 LINE 500KV CB AT SMTS | 39119.2542 | 39122.441 | CONT | [12 empty] | 0
_X4C458A439119.2611111111 | X4C458A4 |  | Parent | FALSE | EX - HWPS NO.3 220KV LINE NO.2 BUS CB AT JLTS | 39119.2611 | 39129.4514 | CONT | [12 empty] | 0
_1025442739119.2729166667 | 10254427 |  | Parent | FALSE | BATS NO.1 LINE/TGTS LINE 220KV CB AT MLTS | 39119.2729 | 39119.3535 | DAILY | [12 empty] | 0
_1025652439119.3236111111 | 10256524 |  | Parent | TRUE | EX - BATS 220KV LINE NO.1 BUS CB AT BETS | 39119.3236 | 39119.6951 | DAILY | [12 empty] | 0
_1025652539119.3236111111 | 10256525 | 10256524 | Child | FALSE | R4 220/66/22KV TRANS AT BETS | 39119.3236 | 39119.6951 | DAILY | 00016220 | SPIMAINT | Perf calc W/O No4 Trans during BATS L 1B CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025437539119.3541666667 | 10254375 |  | Parent | FALSE | BATS NO.1 220KV LINE NO.1 BUS CB AT MLTS | 39119.3542 | 39119.4514 | DAILY | [12 empty] | 0
_X46158L339120.2326388889 | X46158L3 |  | Parent | FALSE | MLTS NO.1 220KV LINE AT BATS | 39120.2326 | 39120.6861 | REPDAILY | 00012429 | SPICAPX | Out W/O MLTS No1 Line for proximity clearance | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158B739120.2333333333 | Z53158B7 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39120.2333 | 39122.6472 | CONT | 00004776 | VEN_AUG | Bus outage to INSTALL bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158KO39120.2333333333 | Z53158KO | Z53158B7 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39120.2333 | 39122.6472 | CONT | 00354024 | VEN_AUG | Rebate Bus outage to remove bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1025443039120.2986111111 | 10254430 |  | Parent | FALSE | 220KV SHUNT REACTOR CB AT MLTS | 39120.2986 | 39120.3271 | DAILY | [12 empty] | 0
_X38458H939120.3125 | X38458H9 |  | Parent | TRUE | EX - NO.2 66KV BUS AT TGTS | 39120.3125 | 39120.725 | DAILY | 00003133 | SPICAPX | Out W/O Commission CDN Fdr and CB | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458K339120.3125 | X38458K3 | X38458H9 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39120.3125 | 39120.725 | DAILY | 00003127 | SPICAPX | Out W/O Perf calc for 66kV bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z60358A439120.3993055556 | Z60358A4 | Z60358A5 | Child | FALSE | B1 220/66KV TRANS AT SVTS | 39120.3993 | 39120.5938 | DAILY | 00004849 | VEN_AUG | Avail of Plant UPGR SV No3 FDR Bus connections | SPIPOWER | Z603 | Z603 - (SVTS) WORK ASSOC. WITH THE NEW ZONE SS SVW | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z60358A539120.3993055556 | Z60358A5 |  | Parent | TRUE | NO.1 66KV BUS AT SVTS | 39120.3993 | 39120.5938 | DAILY | 00004860 | VEN_AUG | UPGR SV No3 FDR Bus side connections | SPIPOWER | Z603 | Z603 - (SVTS) WORK ASSOC. WITH THE NEW ZONE SS SVW | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z60358A639120.3993055556 | Z60358A6 | Z60358A5 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT SVTS | 39120.3993 | 39120.5938 | DAILY | 00004824 | VEN_AUG | Rebate UPGR SV No3 FDR Bus connections | SPIPOWER | Z603 | Z603 - (SVTS) WORK ASSOC. WITH THE NEW ZONE SS SVW | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X46158L339121.2256944444 | X46158L3 |  | Parent | FALSE | MLTS NO.1 220KV LINE AT BATS | 39121.2257 | 39121.6775 | REPDAILY | 00012429 | SPICAPX | Out W/O MLTS No1 Line for proximity clearance | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010177539121.2694444445 | 10101775 |  | Parent | FALSE | ROTS NO.6 220KV LINE NO.1 BUS CB AT YPS | 39121.2694 | 39121.5236 | DAILY | [12 empty] | 0
_1023586339121.2729166667 | 10235863 |  | Parent | TRUE | S001 KTS -WMTS 1 220KV | 39121.2729 | 39121.6042 | DAILY | [12 empty] | 0
_1025799239121.2729166667 | 10257992 | 10235863 | Child | FALSE | EX - WMTS NO.1 220KV LINE AT KTS | 39121.2729 | 39121.6042 | DAILY | 00015983 | SPIMAINT | Repair Hot joint T1 | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025685539121.2833333333 | 10256855 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.2 BUS CB AT HWTS | 39121.2833 | 39121.3556 | DAILY | [12 empty] | 0
_1025437339121.2916666667 | 10254373 |  | Parent | FALSE | A1 TRANS NO.1 BUS 220KV CB AT MLTS | 39121.2917 | 39121.3306 | DAILY | [12 empty] | 0
_X49058D539121.3131944445 | X49058D5 |  | Parent | FALSE | WOTS 330KV LINE NO.2 BUS CB AT DDTS | 39121.3132 | 39121.5847 | DAILY | [12 empty] | 0
_1025442939121.3513888889 | 10254429 |  | Parent | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB AT MLTS | 39121.3514 | 39121.3924 | DAILY | [12 empty] | 0
_X38458J039121.3638888889 | X38458J0 |  | Parent | TRUE | EX - NO.2 66KV BUS AT TGTS | 39121.3639 | 39121.7396 | DAILY | 00003133 | SPICAPX | Out W/O Commission KRT No 2 Fdr and CB | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458K439121.3638888889 | X38458K4 | X38458J0 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39121.3639 | 39121.7396 | DAILY | 00003127 | SPICAPX | Out W/O Perf calc for 66kV bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458K539121.5208333333 | X38458K5 |  | Parent | FALSE | MLTS 220KV LINE NO.2 BUS CB AT TGTS | 39121.5208 | 39121.5583 | DAILY | [12 empty] | 0
_X46158L339122.21875 | X46158L3 |  | Parent | FALSE | MLTS NO.1 220KV LINE AT BATS | 39122.2188 | 39122.6833 | REPDAILY | 00012429 | SPICAPX | Out W/O MLTS No1 Line for proximity clearance | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025690839122.2527777778 | 10256908 |  | Parent | FALSE | ROTS-SVTS 1 220KV E | 39122.2528 | 39122.55 | DAILY | 00022752 | SPIMAINT | Replace porcelain insulators | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058E739122.2576388889 | X32058E7 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39122.2576 | 39122.6958 | DAILY | 00004569 | SPICAPX | N03 Bus 1-3 B.T & EL fdr intsall structures | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058E839122.2576388889 | X32058E8 | X32058E7 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39122.2576 | 39122.6958 | DAILY | 00026900 | SPICAPX | Avail of plant for No 3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025660039122.2631944444 | 10256600 |  | Parent | TRUE | S027 KTS -WMTS 2 220KV | 39122.2632 | 39122.5757 | DAILY | [12 empty] | 0
_1025799339122.2631944444 | 10257993 | 10256600 | Child | FALSE | KTS -WMTS 2 220KV WT | 39122.2632 | 39122.5757 | DAILY | 00022719 | SPIMAINT | Replace Cracked insulator T27 | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010176339122.2895833333 | 10101763 |  | Parent | FALSE | HWPS NO.2 220KV LINE NO.2 BUS CB AT YPS | 39122.2896 | 39122.5437 | DAILY | [12 empty] | 0
_Z53158O339122.6 | Z53158O3 |  | Parent | FALSE | EX - HWPS NO.3 220KV LINE NO.1 BUS CB AT ROTS | 39122.6 | 39127.2715 | CONT | [12 empty] | 0
_Z53158O639123.2354166667 | Z53158O6 |  | Parent | TRUE | EX - NO.4 220KV BUS AT ERTS | 39123.2354 | 39123.4576 | DAILY | 00004380 | VEN_AUG | install temp bus pedastal 3-4 b.t CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158O739123.2354166667 | Z53158O7 | Z53158O6 | Child | FALSE | B4 220/66KV TRANS AT ERTS | 39123.2354 | 39123.4576 | CONT | 00004372 | VEN_AUG | Avail of plant Replace 3-4 B.T No4 B 220 kV ISOLS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010185839123.2361111111 | 10101858 |  | Parent | FALSE | B2 220/66KV TRANS BANK AT BLTS | 39123.2361 | 39123.5563 | DAILY | 00018641 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025662539123.2493055556 | 10256625 |  | Parent | FALSE | ROTS-SVTS 2 220KV E | 39123.2493 | 39123.6389 | DAILY | 00022756 | SPIMAINT | Replace porcelain insulators | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009277839123.25 | 10092778 |  | Parent | TRUE | HWPS NO.1 220KV LINE E/SW AT YPS | 39123.25 | 39123.4736 | DAILY | [12 empty] | 0
_1025640439123.25 | 10256404 | 10092778 | Child | FALSE | HWPS NO.1 220KV LINE AT YPS | 39123.25 | 39123.4736 | DAILY | 00016409 | SPIMAINT | Rebate HWPS No 1 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025701239123.9722222222 | 10257012 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 39123.9722 | 39125.4812 | CONT | 00356086 | GENCO | Scap for genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010428439124.2333333333 | 10104284 |  | Parent | FALSE | B4 220/66KV TRANS AT WMTS | 39124.2333 | 39124.5708 | DAILY | 00350829 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010134239124.2569444444 | 10101342 |  | Parent | FALSE | HWPS NO.3 220KV LINE AT JLTS | 39124.2569 | 39124.4674 | DAILY | 00015939 | SPIMAINT | O/Haul - HWPS No.3 220kV LINE at JLTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010324839124.2972222222 | 10103248 |  | Parent | TRUE | TTS 220KV LINE AT RWTS | 39124.2972 | 39124.6035 | DAILY | 00082880 | SPIMAINT | O/Haul - TTS Line & CVT at RWTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010343739124.2972222222 | 10103437 | 10103248 | Child | FALSE | TTS 220KV LINE NO.1 BUS CB LINE SIDE ISOL AT RWTS | 39124.2972 | 39124.6035 | DAILY | [12 empty] | 0
_1010343839124.2972222222 | 10103438 | 10103248 | Child | FALSE | TTS 220KV LINE NO.2 BUS CB LINE SIDE ISOL AT RWTS | 39124.2972 | 39124.6035 | DAILY | [12 empty] | 0
_1010344139124.2972222222 | 10103441 | 10103248 | Child | FALSE | TTS 220KV LINE E/SW AT RWTS | 39124.2972 | 39124.6035 | DAILY | [12 empty] | 0
_Z50058C839124.3 | Z50058C8 |  | Parent | TRUE | ROTS NO.2 220KV LINE AT SVTS | 39124.3 | 39124.4833 | CONT | 00351701 | VEN_AUG | No2busConvert to ROIS & work on line equip at ROTS | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z50058D039124.3 | Z50058D0 | Z50058C8 | Child | FALSE | HTS NO.2 220KV LINE AT SVTS | 39124.3 | 39124.4833 | CONT | 00351702 | VEN_AUG | RebateConvert to ROIS & work on line equip at ROTS | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z50058D139124.3 | Z50058D1 | Z50058C8 | Child | FALSE | B2 220/66KV TRANS AT SVTS | 39124.3 | 39124.4833 | CONT | 00004850 | VEN_AUG | AavailConvert to ROIS & work on line equip at ROTS | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z50058C939124.4708333333 | Z50058C9 |  | Parent | TRUE | ROTS NO.1 220KV LINE AT SVTS | 39124.4708 | 39124.5979 | CONT | 00351700 | VEN_AUG | No1 Bus outage Convert ROTS 1 line ISOL to ROI's | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z50058D239124.4708333333 | Z50058D2 | Z50058C9 | Child | FALSE | HTS NO.1 220KV LINE AT SVTS | 39124.4708 | 39124.5979 | CONT | 00351703 | VEN_AUG | Rebate No1 Bus outage ROTS 1 line ISOL to ROI's | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z50058D339124.4708333333 | Z50058D3 | Z50058C9 | Child | FALSE | B1 220/66KV TRANS AT SVTS | 39124.4708 | 39124.5979 | CONT | 00004849 | VEN_AUG | Avail No1 Bus outage ROTS 1 line ISOL to ROI's | SPIPOWER | Z500 | Z500 - (ROTS-SVTS) UPGRADE 220KV LINE TERMINATIONS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010346639125.2861111111 | 10103466 |  | Parent | FALSE | RTS NO.4 220KV LINE NO.4 BUS CB AT ROTS | 39125.2861 | 39129.5236 | CONT | [12 empty] | 0
_1025711239125.4006944445 | 10257112 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 39125.4007 | 39125.4535 | CONT | 00060938 | APDALCOA | APD requirement | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1010201839125.5152777778 | 10102018 | 10102016 | Child | FALSE | EX - NO.2 AIR COMPRESSOR AT BETS | 39125.5153 | 39126.2917 | DAILY | [12 empty] | 0
_1025604239126.2263888889 | 10256042 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39126.2264 | 39126.4313 | DAILY | 00019243 | SPIMAINT | Out W/O S/S Auto change over contactor | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025713339126.3284722222 | 10257133 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK CB AT ROTS | 39126.3285 | 39126.4472 | CONT | [12 empty] | 0
_1025690439126.3395833333 | 10256904 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT TTS | 39126.3396 | 39126.3958 | DAILY | [12 empty] | 0
_1025799439126.3395833333 | 10257994 | 10256904 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT TTS | 39126.3396 | 39126.3958 | DAILY | 00001485 | SPIMAINT | cb outage to be used for trainee operators | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025690239126.3958333333 | 10256902 |  | Parent | FALSE | 2-3 220KV BUS TIE CB AT TTS | 39126.3958 | 39126.5375 | REPDAILY | [12 empty] | 0
_1025378739127.2194444445 | 10253787 | X46158J8 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39127.2194 | 39127.6347 | DAILY | 00006554 | SPICAPX | Perf calc W/O No1 Trans during No1 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025378839127.2194444445 | 10253788 | X46158J8 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 39127.2194 | 39127.6347 | DAILY | 00331109 | SPICAPX | Rebate W/O No1 Cap bank during No1 66kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X46158J839127.2194444445 | X46158J8 |  | Parent | TRUE | NO.1 66KV BUS AT BATS | 39127.2194 | 39127.6347 | DAILY | 00006560 | SPICAPX | Out W/O No1 66kV Bus to replace BAS No1 FDR CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158D539127.2270833333 | Z53158D5 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 39127.2271 | 39129.5757 | CONT | 00004778 | VEN_AUG | Erect ERTS 2 Line CB B/S ROI | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158L739127.2270833333 | Z53158L7 | Z53158D5 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39127.2271 | 39129.5757 | CONT | 00112418 | VEN_AUG | Line outage to Reconnect No 2 CB diconnect 1 busCB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024056339127.2868055556 | 10240563 |  | Parent | FALSE | EX - NO.1 TRANS BANK AT HOTS | 39127.2868 | 39127.4889 | DAILY | 00026245 | SPIMAINT | Repair Cooling Fans | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025662739128.6513888889 | 10256627 | X43258M3 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39128.6514 | 39128.6583 | DAILY | 00359891 | SPICAPX | Rebate W/O No1 66kV Cap bk during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025662839128.6513888889 | 10256628 | X43258M3 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 39128.6514 | 39128.6583 | DAILY | 00016895 | SPICAPX | Rebate W/O No1 66kV React during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025662939128.6513888889 | 10256629 | X43258M3 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 39128.6514 | 39128.6583 | DAILY | 00016895 | SPICAPX | Perf calc W/O 1B Trans during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258M339128.6513888889 | X43258M3 |  | Parent | TRUE | NO.1 66KV BUS AT RCTS | 39128.6514 | 39128.6583 | DAILY | 00016976 | SPICAPX | Out W/O No1 66kV BUS de-energ for RVL CB commiss | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010113439129.3395833333 | 10101134 |  | Parent | FALSE | JA NO.3 66KV FDR NO.2 BUS CB AT WMTS | 39129.3396 | 39129.5299 | DAILY | [12 empty] | 0
_1025738239129.5451388889 | 10257382 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39129.5451 | 39129.55 | DAILY | [12 empty] | 0
_Z53158O539129.5993055556 | Z53158O5 |  | Parent | FALSE | EX - HWPS NO.3 220KV LINE NO.1 BUS CB AT ROTS | 39129.5993 | 39151.2083 | CONT | [12 empty] | 0
_1025741239129.8333333333 | 10257412 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 39129.8333 | 39131.4514 | CONT | 00356079 | GENCO | No1 gen 220kV CB / Gen-Co Isolations | GENCO |  |  | Circuits | 3rd Party | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025728339130.2361111111 | 10257283 |  | Parent | FALSE | B4 220/66KV TRANS AT WMTS | 39130.2361 | 39130.3083 | DAILY | 00350829 | SPIMAINT | replace diverter switch oil | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010135939130.2472222222 | 10101359 |  | Parent | TRUE | HWPS NO.2 220KV LINE E/SW AT JLTS | 39130.2472 | 39130.4701 | DAILY | [12 empty] | 0
_1025640939130.2472222222 | 10256409 | 10101359 | Child | FALSE | HWPS NO.2 220KV LINE AT JLTS | 39130.2472 | 39130.4701 | DAILY | 00015937 | SPIMAINT | Rebate for line equipment o/haul | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z33458G939131.1840277778 | Z33458G9 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 39131.184 | 39131.5535 | DAILY | 00352791 | VEN_AUG | Replace No 2 Cooling Pump | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025737539131.2131944445 | 10257375 |  | Parent | FALSE | ROTS-RTS 4 220KV E | 39131.2132 | 39131.3472 | DAILY | 00022750 | SPIMAINT | rots-rts 4 Line replace insulators | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010328639131.3576388889 | 10103286 |  | Parent | TRUE | TSTS 220KV LINE AT ROTS | 39131.3576 | 39131.6042 | DAILY | 00022678 | SPIMAINT | O/Haul - TSTS Line & CVT,s at ROTS & TSTS (M) | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010349739131.3576388889 | 10103497 | 10103286 | Child | FALSE | TSTS 220KV LINE E/SW AT ROTS | 39131.3576 | 39131.6042 | DAILY | [12 empty] | 0
_1010349839131.3576388889 | 10103498 | 10103286 | Child | FALSE | TSTS 220KV LINE NO.4 BUS CB LINE SIDE E/SW AT ROTS | 39131.3576 | 39131.6042 | DAILY | [12 empty] | 0
_1010349939131.3576388889 | 10103499 | 10103286 | Child | FALSE | TSTS 220KV LINE/YPS NO.6 LINE CB TSTS LINE SIDE E/SW AT ROTS | 39131.3576 | 39131.6042 | DAILY | [12 empty] | 0
_1010352539131.3576388889 | 10103525 | 10103286 | Child | FALSE | TSTS 220KV LINE NO.4 BUS CB LINE SIDE ISOL AT ROTS | 39131.3576 | 39131.6042 | DAILY | [12 empty] | 0
_1010353639131.3576388889 | 10103536 | 10103286 | Child | FALSE | TSTS LINE/YPS NO.6 LINE CB TSTS LINE SIDE ISOL AT ROTS | 39131.3576 | 39131.6042 | DAILY | [12 empty] | 0
_1025681439131.7180555556 | 10256814 | X46158L4 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 39131.7181 | 39131.7431 | DAILY | 00331109 | SPICAPX | Rebate W/O No1 66 Cap during No1 66 BUS de-energ | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025681739131.7180555556 | 10256817 | X46158L4 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39131.7181 | 39131.7431 | DAILY | 00006554 | SPICAPX | Perf calc W/O No1 Tran during No1 66 BUS de-energ | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158L439131.7180555556 | X46158L4 |  | Parent | TRUE | NO.1 66KV BUS AT BATS | 39131.7181 | 39131.7431 | DAILY | 00006560 | SPICAPX | Out W/O No1 66kV BUS for BAS No1 FDR CB commiss | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158M239132.2291666667 | Z53158M2 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39132.2292 | 39132.6632 | DAILY | 00004776 | VEN_AUG | Bus outage to remove bus bi pods HWPS 2 Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158M339132.2291666667 | Z53158M3 | Z53158M2 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39132.2292 | 39132.6632 | CONT | 00354024 | VEN_AUG | Rebate Bus outage to remove bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49658C639132.2770833333 | X49658C6 |  | Parent | FALSE | EX - NO.1 66KV REACTOR AT HOTS | 39132.2771 | 39141.7396 | CONT | 00006935 | SPICAPX | Out W/O No 1 66kV Reactor to replace its 66kV CB | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025603139132.3486111111 | 10256031 |  | Parent | FALSE | A2 515/220KV TRANS BANK AT ROTS | 39132.3486 | 39135.5396 | CONT | 00362994 | VEN_AUG | HV Tests ROTS A2 1000MVA 500kV transformer | SPIPOWER |  |  | Main Transformers | 3rd Party | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1025747739132.7736111111 | 10257477 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39132.7736 | 39133.5667 | DAILY | 00003104 | FAULT | Replace Blown Fuse on W Phase Can | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025758039133.1951388889 | 10257580 |  | Parent | FALSE | KTS -BLTS 220KV WY | 39133.1951 | 39133.6153 | CONT | 00022716 | FAULT | KTS - BTS 220kV Line Tripped | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025693339133.2618055556 | 10256933 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT SVTS | 39133.2618 | 39133.6007 | DAILY | [12 empty] | 0
_1025811139133.2618055556 | 10258111 | 10256933 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT SVTS | 39133.2618 | 39133.6007 | DAILY | 00004824 | SPIMAINT | Service Points Overhaul | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025554539133.2708333333 | 10255545 |  | Parent | FALSE | 3-5 220KV BUS TIE CB AT BLTS | 39133.2708 | 39133.5208 | DAILY | [12 empty] | 0
_V62258A139133.2965277778 | V62258A1 |  | Parent | FALSE | HWTS NO.1 LINE/SYTS NO.1 LINE 500KV CB AT SMTS | 39133.2965 | 39141.5194 | CONT | [12 empty] | 0
_1025748339133.4763888889 | 10257483 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 39133.4764 | 39133.5715 | DAILY | 00015976 | FAULT | replace flashed over insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025748039133.575 | 10257480 |  | Parent | FALSE | EX - GTS NO.1 220KV LINE AT KTS | 39133.575 | 39133.6833 | DAILY | 00015985 | FAULT | replace flashed over insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025684639134.2555555556 | 10256846 | X46158L6 | Child | FALSE | WBTS 220KV LINE AT BATS | 39134.2556 | 39134.541 | DAILY | 00012410 | SPICAPX | Rebate W/O HOTS Line during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025684739134.2555555556 | 10256847 | X46158L6 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39134.2556 | 39134.541 | DAILY | 00006554 | SPICAPX | Perf calc W/O #1 TR during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158L639134.2555555556 | X46158L6 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 39134.2556 | 39134.541 | DAILY | 00006559 | SPICAPX | Out W/O No2 220kV Bus to connect fut MLTS 1L ROI | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025739539134.2583333333 | 10257395 |  | Parent | FALSE | NO.2 CSC AT ROTS | 39134.2583 | 39134.359 | DAILY | 00004716 | SPIMAINT | REPLACE INSULATOR | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z53158P739134.26875 | Z53158P7 |  | Parent | FALSE | HWPS NO.2 220KV LINE NO.1 BUS CB AT ROTS | 39134.2688 | 39138.2604 | CONT | [12 empty] | 0
_1025554739134.2736111111 | 10255547 |  | Parent | FALSE | 1A-2A 220KV BUS TIE CB AT BLTS | 39134.2736 | 39134.4764 | DAILY | [12 empty] | 0
_X38458K939134.3395833333 | X38458K9 |  | Parent | TRUE | EX - NO.2 66KV BUS AT TGTS | 39134.3396 | 39134.7854 | DAILY | 00003133 | SPICAPX | Out W/O Changeover CDN fdr to final location | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458L039134.3395833333 | X38458L0 | X38458K9 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39134.3396 | 39134.7854 | DAILY | 00003127 | SPICAPX | Out W/O Perf calc while 66kV bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025437039135.2708333333 | 10254370 |  | Parent | FALSE | PT. HENRY NO.2 220KV LINE CB AT GTS | 39135.2708 | 39135.5813 | DAILY | [12 empty] | 0
_1025631539135.2708333333 | 10256315 |  | Parent | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39135.2708 | 39135.5813 | DAILY | 00017905 | APDALCOA | SCAP for PTH | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X4C458A139135.2770833333 | X4C458A1 |  | Parent | FALSE | EX - MWTS NO.1 220KV LINE NO.1 BUS CB AT JLTS | 39135.2771 | 39148.425 | CONT | [12 empty] | 0
_X38458L139135.3527777778 | X38458L1 |  | Parent | TRUE | EX - NO.1 66KV BUS AT TGTS | 39135.3528 | 39135.691 | DAILY | 00003132 | SPICAPX | Out W/O Commission HTN No 1 66kV CB | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458L239135.3527777778 | X38458L2 | X38458L1 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39135.3528 | 39135.691 | DAILY | 00023231 | SPICAPX | Out W/O Perf calc for 66kV bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025762539136.2979166667 | 10257625 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 39136.2979 | 39136.3889 | DAILY | [12 empty] | 0
_1025762839136.3888888889 | 10257628 |  | Parent | FALSE | EX - NO.4 MAIN TRANS NO.1 BUS 500KV CB AT HWTS | 39136.3889 | 39136.5125 | DAILY | [12 empty] | 0
_1025771939136.9201388889 | 10257719 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 39136.9201 | 39141.4799 | CONT | 00356080 | GENCO | SCAP: HWPS 2 Gen Isol'd & Earthed | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025763539137.1805555556 | 10257635 |  | Parent | TRUE | S361 ROTS-RTS 4 220KV | 39137.1806 | 39137.2896 | DAILY | [12 empty] | 0
_1025811539137.1805555556 | 10258115 | 10257635 | Child | FALSE | ROTS-RTS 4 220KV E | 39137.1806 | 39137.2896 | DAILY | 00022750 | SPIMAINT | Five flat insulators on middle phase. ins 1-5 | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025438039137.2118055556 | 10254380 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT MLTS | 39137.2118 | 39137.7438 | REPDAILY | 00337580 | SPIMAINT | Pref Calc W/O For 500Kv TX Switch Gear O/H | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z53158P039137.23125 | Z53158P0 |  | Parent | TRUE | EX - NO.1 220KV BUS AT ERTS | 39137.2312 | 39137.6167 | CONT | 00004378 | VEN_AUG | Make bus side connection to Replace 1-3 B.T CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158P139137.23125 | Z53158P1 | Z53158P0 | Child | FALSE | B1 220/66KV TRANS AT ERTS | 39137.2312 | 39137.6167 | CONT | 00004370 | VEN_AUG | Avail of plant Replace 1-3 B.T No1 B 220 kV ISOLS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X4C458A039137.2569444444 | X4C458A0 |  | Parent | FALSE | EX - MWTS NO.2 220KV LINE NO.1 BUS CB AT JLTS | 39137.2569 | 39137.5153 | REPDAILY | [12 empty] | 0
_1010191639137.2916666667 | 10101916 |  | Parent | FALSE | NO.2 TRANS 66KV CB AT BLTS | 39137.2917 | 39137.5569 | DAILY | [12 empty] | 0
_X38458K639137.3076388889 | X38458K6 |  | Parent | TRUE | EX - NO.1 220KV BUS AT TGTS | 39137.3076 | 39137.5979 | DAILY | 00003130 | SPICAPX | Out W/O Extend No 1 220kV bus & install bi-pods | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458K839137.3076388889 | X38458K8 | X38458K6 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39137.3076 | 39137.5979 | DAILY | 00023231 | SPICAPX | Out W/O Perf calc while bus is out | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025772739137.5854166667 | 10257727 |  | Parent | TRUE | B4 220/66KV TRANS AT BLTS | 39137.5854 | 39137.6931 | CONT | 00002615 | FAULT | B4 220/66kV Transf Trip on oil surge. | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025772839137.5854166667 | 10257728 | 10257727 | Child | FALSE | NO.4 220KV BUS AT BLTS | 39137.5854 | 39137.6931 | CONT | 00002646 | FAULT | No4 220kV Bus trip due to B4 Trans Trip | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025778239137.5854166667 | 10257782 | 10257727 | Child | FALSE | ATS 220KV LINE AT BLTS | 39137.5854 | 39137.6931 | CONT | 00024010 | FAULT | ATS 220kV Line Trip due to No4 220kV Bus trip | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025778439137.5854166667 | 10257784 | 10257727 | Child | FALSE | NPSD 220KV LINE AT BLTS | 39137.5854 | 39137.6931 | CONT | 00024014 | FAULT | NPSD 220kV Line Trip due to No4 220kV Bus trip | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025778539137.5854166667 | 10257785 | 10257727 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT BLTS | 39137.5854 | 39137.6931 | CONT | 00327921 | FAULT | No4 220kV Cap bank Trip due to No4 220kV Bus trip | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z53158P239137.6166666667 | Z53158P2 |  | Parent | FALSE | EX - 1-3 220KV BUS TIE CB AT ERTS | 39137.6167 | 39144.6493 | DAILY | [12 empty] | 0
_1025438039138.2208333333 | 10254380 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT MLTS | 39138.2208 | 39138.759 | REPDAILY | 00337580 | SPIMAINT | Pref Calc W/O For 500Kv TX Switch Gear O/H | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z53158N639138.2256944444 | Z53158N6 |  | Parent | FALSE | HWPS NO.2 220KV LINE AT ROTS | 39138.2257 | 39138.525 | DAILY | 00024004 | VEN_AUG | outage remove HWPS #2 line #1 bus cb line side iso | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010112839138.2347222222 | 10101128 |  | Parent | FALSE | NO.1 66KV BUS AT WMTS | 39138.2347 | 39138.6194 | DAILY | 00003258 | SPIMAINT | O/HAUL - 66kv Bus and replace bus vt | SPIPOWER |  |  | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X4C458A039138.2548611111 | X4C458A0 |  | Parent | FALSE | EX - MWTS NO.2 220KV LINE NO.1 BUS CB AT JLTS | 39138.2549 | 39138.4278 | REPDAILY | [12 empty] | 0
_1025773439138.45 | 10257734 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 39138.45 | 39140.3785 | CONT | 00356079 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z50358C839138.6340277778 | Z50358C8 |  | Parent | FALSE | RTS NO.4 220KV LINE AT ROTS | 39138.634 | 39138.8951 | DAILY | 00023969 | VEN_AUG | Line out for RTS NO.4 LINE/YPS NO.5 LINE CB | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49058E039139.1909722222 | X49058E0 |  | Parent | FALSE | NO.1 330KV BUS AT DDTS | 39139.191 | 39139.5722 | DAILY | 00003978 | SPICAPX | Out W/O Excavate for new founds under bus | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X41258C839139.2541666667 | X41258C8 |  | Parent | FALSE | EX - DDTS 220KV LINE AT SHTS | 39139.2542 | 39140.7736 | CONT | 00000811 | SPICAPX | Commission DDTS CB's & Equipment | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025770239139.2638888889 | 10257702 |  | Parent | TRUE | S009 KTS -WMTS 2 220KV | 39139.2639 | 39139.4042 | DAILY | [12 empty] | 0
_1025811639139.2638888889 | 10258116 | 10257702 | Child | FALSE | KTS -WMTS 2 220KV WT | 39139.2639 | 39139.4042 | DAILY | 00022719 | SPIMAINT | Flat insulators T9 | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025684639139.3368055556 | 10256846 | X46158L6 | Child | FALSE | WBTS 220KV LINE AT BATS | 39139.3368 | 39139.6229 | DAILY | 00012410 | SPICAPX | Rebate W/O HOTS Line during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025684739139.3368055556 | 10256847 | X46158L6 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39139.3368 | 39139.6229 | DAILY | 00006554 | SPICAPX | Perf calc W/O #1 TR during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158L639139.3368055556 | X46158L6 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 39139.3368 | 39139.6229 | DAILY | 00006559 | SPICAPX | Out W/O No2 220kV Bus to connect fut MLTS 1L ROI | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025555139139.4083333333 | 10255551 |  | Parent | FALSE | 3-4 220KV BUS TIE CB AT WMTS | 39139.4083 | 39139.5903 | DAILY | [12 empty] | 0
_1025772239139.4107638889 | 10257722 |  | Parent | FALSE | YWPS NO.3 220KV LINE AT YPS | 39139.4108 | 39145.4181 | CONT | 00016426 | GENCO | SCAP: W3 Gen is Isol'd & Earthed | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z50358C739140.2340277778 | Z50358C7 |  | Parent | FALSE | YPS NO.5 220KV LINE AT ROTS | 39140.234 | 39140.5069 | DAILY | 00024008 | VEN_AUG | Check Interlocking on Line side Isols | SPIPOWER | Z503 | Z503 - (ROTS,RTS) REPLACE 4 220KV CBS TO MATCH LINE RATING | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025555739140.2534722222 | 10255557 |  | Parent | TRUE | FBTS NO.2 220KV LINE CB AT WMTS | 39140.2535 | 39140.4153 | DAILY | [12 empty] | 0
_1025812339140.2534722222 | 10258123 | 10255557 | Child | FALSE | WMTS-FBTS 2 220KV WY | 39140.2535 | 39140.4153 | DAILY | 00022787 | SPIMAINT | ct oil sampling | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025785939141.2076388889 | 10257859 |  | Parent | FALSE | EX - NO.2 220KV BUS AT JLTS | 39141.2076 | 39141.2986 | DAILY | 00009890 | FAULT | Trip caused by JLGSA Unit 3 | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025778839141.2083333333 | 10257788 | Z53158P5 | Child | FALSE | A1 TRANS 220KV LINE AT ROTS (RTF) | 39141.2083 | 39141.5479 | DAILY | 00023965 | VEN_AUG | Child of No4 Bus at ROTS | SPIPOWER |  |  | Circuits | Eastern | 220 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 3
_1025713639141.2083333333 | 10257136 | Z53158P5 | Child | FALSE | MTS NO.1 220KV LINE AT ROTS | 39141.2083 | 39141.7812 | DAILY | 00350667 | VEN_AUG | Relocate MTS 1L connection to Bay F | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025797439141.2083333333 | 10257974 | Z53158P5 | Child | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39141.2083 | 39141.7812 | DAILY | 00354002 | VEN_AUG | Relocate MTS 1L connection to Bay F | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_Z53158P539141.2083333333 | Z53158P5 |  | Parent | TRUE | NO.4 220KV BUS AT ROTS | 39141.2083 | 39141.7812 | DAILY | 00329012 | VEN_AUG | Bus Outage & MTS No 1 Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X56558A139141.23125 | X56558A1 |  | Parent | FALSE | WOTS-DDTS 330KV NW | 39141.2312 | 39141.7417 | DAILY | 00060189 | SPICAPX | Out W/O WOTS-DDTS Line CT replace at DDTS | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025694139141.2611111111 | 10256941 | X43258M7 | Child | FALSE | HOTS 220KV LINE AT RCTS | 39141.2611 | 39141.8368 | DAILY | 00016954 | SPICAPX | Rebate W/O HOTS Line to commiss new 2B CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025694239141.2611111111 | 10256942 | X43258M7 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RCTS | 39141.2611 | 39141.8368 | DAILY | 00360383 | SPICAPX | Rebate W/O No2 220 Cap bk during #2 220 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025694439141.2611111111 | 10256944 | X43258M7 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39141.2611 | 39141.8368 | DAILY | 00337584 | SPICAPX | Perf calc W/O No2 TR during #2 220 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258M739141.2611111111 | X43258M7 |  | Parent | TRUE | NO.2 220KV BUS-CAPBK EXTENSION AT RCTS | 39141.2611 | 39141.8368 | DAILY | 00016916 | SPICAPX | Out W/O No2 220kV Bus & HOTS L to commiss new CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025713939141.2840277778 | 10257139 | X49658C7 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT HOTS | 39141.284 | 39141.7396 | DAILY | 00359898 | SPICAPX | Rebate W/O 1A Cap bk during No1 66kV bus outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025714039141.2840277778 | 10257140 | X49658C7 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HOTS | 39141.284 | 39141.7396 | DAILY | 00359901 | SPICAPX | Rebate W/O 1B Cap bk during No1 66kV bus outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025714239141.2840277778 | 10257142 | X49658C7 | Child | FALSE | EX - NO.1 TRANS BANK AT HOTS | 39141.284 | 39141.7396 | DAILY | 00026245 | SPICAPX | Perf calc W/O #1 Trans during No1 66kV bus outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49658C739141.2840277778 | X49658C7 |  | Parent | TRUE | NO.1 66KV BUS AT HOTS | 39141.284 | 39141.7396 | DAILY | 00006940 | SPICAPX | Out W/O No 1 66kV BUS to commiss new VT & react CB | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025786039141.2909722222 | 10257860 |  | Parent | FALSE | JLGA NO.3 UNIT TRANS DISC CB AT JLGA | 39141.291 | 39142.3403 | DAILY | [12 empty] | 0
_1025790239141.3305555556 | 10257902 |  | Parent | FALSE | EX - A3 TRANS 220KV CB AT KTS | 39141.3306 | 39141.5715 | DAILY | [12 empty] | 0
_1025812839141.3305555556 | 10258128 |  | Parent | FALSE | A3 500/220KV TRANS BANK AT KTS | 39141.3306 | 39141.5715 | DAILY | 00026097 | FAULT | red & white phase sf6 gas leaks | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025771739141.3347222222 | 10257717 |  | Parent | FALSE | HYTS NO.2 500KV LINE AT APD | 39141.3347 | 39141.3861 | DAILY | 00005922 | APDALCOA | APD ins washing | APDALCOA |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025771639141.4861111111 | 10257716 |  | Parent | FALSE | HYTS NO.1 500KV LINE AT APD | 39141.4861 | 39141.5271 | DAILY | 00005921 | APDALCOA | APD insulator washing | APDALCOA |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025778639141.5 | 10257786 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39141.5 | 39141.5389 | CONT | 00003104 | FAULT | Fault outage Blown Fuse (Note: SWACT in 10257787) | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025789739141.625 | 10257897 |  | Parent | FALSE | EX - NO.1 REACTOR CB AT HOTS | 39141.625 | 39142.388 | CONT | [12 empty] | 0
_X56558A339141.6909375 | X56558A3 |  | Parent | FALSE | WOTS 330KV LINE NO.2 BUS CB AT DDTS | 39141.6909 | 39143.6889 | CONT | [12 empty] | 0
_1025790139141.7104166667 | 10257901 |  | Parent | FALSE | MLRC 220KV LINE AT RCTS | 39141.7104 | 39141.7576 | DAILY | 00352130 | FAULT | MLRC line at RCTS | SPIPOWER |  |  | Circuits | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 4
_X32058D239142.1784722222 | X32058D2 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MTS | 39142.1785 | 39142.8528 | REPDAILY | 00004564 | SPICAPX | No2 220kv BUS & B2 trans stand new rack structure | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058D339142.1784722222 | X32058D3 | X32058D2 | Child | FALSE | EX - NO.2 220/66KV TRANS BANK AT MTS | 39142.1785 | 39142.8528 | DAILY | 00026899 | SPICAPX | No2 Bus & B2 Tran Isolated to stand up new rack | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025777939142.2416666667 | 10257779 |  | Parent | FALSE | B4 220/66KV TRANS AT BLTS | 39142.2417 | 39142.7333 | DAILY | 00002615 | SPIMAINT | condition monitoring test | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X41258C939142.2506944445 | X41258C9 |  | Parent | FALSE | EX - GNTS NO.1 220KV LINE AT SHTS | 39142.2507 | 39143.5819 | CONT | 00000812 | SPICAPX | Commission CB and Line Equipment | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V4S258E939142.2583333333 | V4S258E9 |  | Parent | FALSE | BAY F 500KV LINE AT SMTS (O.O.S) | 39142.2583 | 39142.5792 | CONT | 00012398 | SPIMAINT | Dismantle hypotronics | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Circuits | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1025790339142.3125 | 10257903 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 39142.3125 | 39148.5938 | CONT | [12 empty] | 0
_X32058D239143.19375 | X32058D2 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MTS | 39143.1937 | 39143.6896 | REPDAILY | 00004564 | SPICAPX | No2 220kv BUS & B2 trans stand new rack structure | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058D339143.19375 | X32058D3 | X32058D2 | Child | FALSE | EX - NO.2 220/66KV TRANS BANK AT MTS | 39143.1937 | 39143.6896 | DAILY | 00026899 | SPICAPX | No2 Bus & B2 Tran Isolated to stand up new rack | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025746239143.2305555556 | 10257462 |  | Parent | FALSE | EX - B3 220/66KV TRANS AT TTS | 39143.2306 | 39143.4292 | DAILY | 00001544 | SPIMAINT | top up blue phase bushing & conservator | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258N039143.2319444444 | X43258N0 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39143.2319 | 39143.5437 | DAILY | 00337581 | SPICAPX | Out W/O No1 TR GRP commiss Fut 2 Bus 220kV CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058D239144.2270833333 | X32058D2 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MTS | 39144.2271 | 39144.5903 | REPDAILY | 00004564 | SPICAPX | No2 220kv BUS & B2 trans stand new rack structure | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058D339144.2270833333 | X32058D3 | X32058D2 | Child | FALSE | EX - NO.2 220/66KV TRANS BANK AT MTS | 39144.2271 | 39144.5903 | DAILY | 00026899 | SPICAPX | No2 Bus & B2 Tran Isolated to stand up new rack | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158P339144.2298611111 | Z53158P3 |  | Parent | TRUE | EX - NO.3 220KV BUS AT ERTS | 39144.2299 | 39144.6479 | DAILY | 00004379 | VEN_AUG | Connect 1-3 B.T CB 3 B/S | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158P439144.2298611111 | Z53158P4 | Z53158P3 | Child | FALSE | B3 220/66KV TRANS AT ERTS | 39144.2299 | 39144.6479 | DAILY | 00004371 | VEN_AUG | Avail of plant Replace 1-3 B.T CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009826339144.2388888889 | 10098263 |  | Parent | FALSE | L2 220/22KV TRANS BANK AT BLTS | 39144.2389 | 39144.5701 | DAILY | 00018665 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X4C458B439144.2541666667 | X4C458B4 |  | Parent | FALSE | MWTS NO.1 220KV LINE AT JLTS | 39144.2542 | 39144.5014 | DAILY | 00015947 | SPICAPX | Install new line CVT | SPIPOWER | X4C4 | X4C4 - (JLTS) REPLACE 3AS2 220KV CBS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025840439144.4076388889 | 10258404 |  | Parent | FALSE | EX - TTS NO.2 220KV LINE AT KTS | 39144.4076 | 39144.4132 | CONT | 00015987 | FAULT | Trip of TTS-KTS 2 at KTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025840539144.4076388889 | 10258405 |  | Parent | FALSE | EX - WMTS NO.2 220KV LINE AT KTS | 39144.4076 | 39144.4132 | CONT | 00015982 | FAULT | Trip of TTS-KTS 2 at KTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025798139144.4125 | 10257981 |  | Parent | FALSE | EX - O.O.S 220/66KV TRANS BANK (9 SINGLE PHASE UNITS) AT TTS | 39144.4125 | 39145.7458 | CONT | 00026062 | FAULT | B2 Trans Winding failure B unit W/PH at TTS | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER | Out of Service | 0
_1025798239144.8951388889 | 10257982 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39144.8951 | 39145.8652 | CONT | 00356084 | GENCO | HWPS No6 Gen Tran Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X2A958G239145.2145833333 | X2A958G2 |  | Parent | FALSE | SYTS NO.1 500KV LINE Y PROT AT MLTS | 39145.2146 | 39145.6625 | DAILY | [12 empty] | 0
_X23358C539145.2291666667 | X23358C5 |  | Parent | FALSE | B3 220/66KV TRANS AT WMTS | 39145.2292 | 39145.591 | DAILY | 00003236 | SPICAPX | commission new wti, insert new probe & remove old | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010329639145.2326388889 | 10103296 |  | Parent | TRUE | NO.3 66KV BUS AT RTS | 39145.2326 | 39145.5708 | DAILY | 00022329 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus & SK FDR | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025728139145.2326388889 | 10257281 | 10103296 | Child | FALSE | B3 220/66KV TRANS AT RTS | 39145.2326 | 39145.5708 | DAILY | 00329288 | SPIMAINT | tran rebate | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010190939145.2402777778 | 10101909 |  | Parent | FALSE | NO.1 22KV BUS AT BLTS | 39145.2403 | 39145.6826 | DAILY | 00002654 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1025777739145.2402777778 | 10257777 |  | Parent | FALSE | NO.1B 220KV BUS AT BLTS | 39145.2403 | 39145.6826 | DAILY | 00002641 | SPIMAINT | Change defective insulators | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X41258D339146.2541666667 | X41258D3 |  | Parent | FALSE | BETS-FVTS-SHTS 220KV NB | 39146.2542 | 39150.4174 | DAILY | 00026225 | SPICAPX | DIS/ RECONNECT BRIDGES AT FIRST TOWER OUT | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X41258D439146.4166666667 | X41258D4 |  | Parent | FALSE | EX - NO.2 TRANS 220KV CB AT SHTS | 39146.4167 | 39148.434 | CONT | [12 empty] | 0
_1025798939146.4618055556 | 10257989 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 39146.4618 | 39146.5514 | DAILY | 00027386 | APDALCOA | APD requirement | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X32058D239147.2104166667 | X32058D2 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MTS | 39147.2104 | 39147.7382 | REPDAILY | 00004564 | SPICAPX | No2 220kv BUS & B2 trans stand new rack structure | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058D339147.2104166667 | X32058D3 | X32058D2 | Child | FALSE | EX - NO.2 220/66KV TRANS BANK AT MTS | 39147.2104 | 39147.7382 | DAILY | 00026899 | SPICAPX | No2 Bus & B2 Tran Isolated to stand up new rack | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158M039147.2194444445 | Z53158M0 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39147.2194 | 39148.6736 | CONT | 00004776 | VEN_AUG | Replace existing bus insulators | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158M139147.2194444445 | Z53158M1 | Z53158M0 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39147.2194 | 39148.6736 | CONT | 00354024 | VEN_AUG | Rebate Bus outage to remove bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_V62258A239147.2513888889 | V62258A2 |  | Parent | FALSE | F2 TRANS NON AUTO 500KV CB AT SMTS | 39147.2514 | 39155.4986 | CONT | [12 empty] | 0
_X41258D139148.25 | X41258D1 |  | Parent | FALSE | B2 220/66KV TRANS AT SHTS | 39148.25 | 39149.6667 | DAILY | 00000841 | SPICAPX | Commision No2 Trans No1 Bus CB | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025799639148.2715277778 | 10257996 |  | Parent | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39148.2715 | 39148.6014 | DAILY | 00017906 | APDALCOA | SCAP for Alcoa Point Henry | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025793739148.2743055556 | 10257937 |  | Parent | TRUE | AUTO RECLOSE CONTROL EQUIPMENT AT BLTS | 39148.2743 | 39148.3368 | DAILY | [12 empty] | 0
_1025811039148.2743055556 | 10258110 | 10257937 | Child | FALSE | KTS -BLTS 220KV WY | 39148.2743 | 39148.3368 | DAILY | 00022716 | SPIMAINT | child for work at BLTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025451539148.2916666667 | 10254515 |  | Parent | TRUE | HWTS NO.3 500KV LINE CB AT LYPS | 39148.2917 | 39148.3632 | DAILY | [12 empty] | 0
_1025451639148.2916666667 | 10254516 | 10254515 | Child | FALSE | HWTS NO.3 500KV LINE AT LYPS | 39148.2917 | 39148.3632 | DAILY | 00016088 | FORCED | ADJUST SF6 GAS PRESSURE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458L339148.3180555556 | X38458L3 |  | Parent | TRUE | EX - NO.1 66KV BUS AT TGTS | 39148.3181 | 39148.7097 | DAILY | 00003132 | SPICAPX | Out W/O Commission SUB COB FDR CB | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458L439148.3180555556 | X38458L4 | X38458L3 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39148.3181 | 39148.7097 | DAILY | 00023231 | SPICAPX | Out W/O Perf calc for No 1 66kV BUS outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49658D339148.4243055556 | X49658D3 |  | Parent | FALSE | NO.1 66KV BUS AT HOTS | 39148.4243 | 39148.6813 | DAILY | 00006940 | SPICAPX | Out W/O De-energise No 1 66kV BUS | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458M839148.4569444445 | X38458M8 |  | Parent | FALSE | MLTS 220KV LINE NO.2 BUS CB AT TGTS | 39148.4569 | 39148.5333 | DAILY | [12 empty] | 0
_1025812039148.9715277778 | 10258120 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 39148.9715 | 39152.4979 | CONT | 00356080 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358A039149.25 | Z51358A0 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 39149.25 | 39149.4118 | DAILY | 00007456 | SPICAPX | Proximty reasons No1 66/22kv trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025800739149.2611111111 | 10258007 |  | Parent | FALSE | S048 TTS -KTS 2 220KV | 39149.2611 | 39149.4896 | DAILY | [12 empty] | 0
_1025900439149.2611111111 | 10259004 |  | Parent | FALSE | TTS -KTS 2S220KV WT | 39149.2611 | 39149.4896 | DAILY | 00026989 | SPIMAINT | Flashed insulators - T Ph T48 | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025807139149.2791666667 | 10258071 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39149.2792 | 39149.3806 | DAILY | [12 empty] | 0
_X49658C839149.3236111111 | X49658C8 |  | Parent | FALSE | NO.2 66KV REACTOR AT HOTS | 39149.3236 | 39162.2486 | CONT | 00357255 | SPICAPX | Out W/O Replace No 2 REACTOR CB | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z56958B239149.8541666667 | Z56958B2 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 39149.8542 | 39150.2472 | DAILY | 00015976 | 3RDPARTY | insert exten links to insulators at tower 30 | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058F039150.2375 | X32058F0 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39150.2375 | 39150.7028 | DAILY | 00004569 | SPICAPX | No3 66kv Bus & 1-3 B.T CB | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058F139150.2375 | X32058F1 | X32058F0 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39150.2375 | 39150.7028 | DAILY | 00026900 | SPICAPX | Avail of plant for No 3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025806639150.2659722222 | 10258066 |  | Parent | FALSE | S017 TTS -BTS 1 220KV | 39150.266 | 39150.4861 | DAILY | [12 empty] | 0
_1025900539150.2659722222 | 10259005 |  | Parent | FALSE | TTS -BTS 1 220KV WT | 39150.266 | 39150.4861 | DAILY | 00023081 | SPIMAINT | Cracked bridging clamp T Ph T17 | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025768139150.2763888889 | 10257681 | 10257893 | Child | FALSE | B2 TRANS 220KV CB CT R/PH AT GNTS | 39150.2764 | 39150.4708 | DAILY | [12 empty] | 0
_1025789339150.2763888889 | 10257893 |  | Parent | TRUE | B2 TRANS 220KV CB AT GNTS | 39150.2764 | 39150.4708 | DAILY | [12 empty] | 0
_1025790939150.4763888889 | 10257909 |  | Parent | FALSE | SHTS NO.3 220KV LINE NO.2 BUS CB AT GNTS | 39150.4764 | 39150.6062 | DAILY | [12 empty] | 0
_Z53158P939151.2090277778 | Z53158P9 |  | Parent | TRUE | NO.4 220KV BUS AT ROTS | 39151.209 | 39151.8132 | DAILY | 00329012 | VEN_AUG | Bus Outage & MTS No 1 Line & A1 Trans | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158Q039151.2090277778 | Z53158Q0 | Z53158P9 | Child | FALSE | MTS NO.1 220KV LINE AT ROTS | 39151.209 | 39151.8132 | DAILY | 00350667 | VEN_AUG | Relocate MTS 1L connection to Bay F | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158Q139151.2090277778 | Z53158Q1 | Z53158P9 | Child | FALSE | A2 TRANS NO.4 BUS 220KV CB AT ROTS | 39151.209 | 39151.8132 | DAILY | [12 empty] | 0
_Z53158Q239151.2090277778 | Z53158Q2 | Z53158P9 | Child | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39151.209 | 39151.8132 | DAILY | 00354002 | VEN_AUG | Relocate MTS 1L connection to Bay F | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_Z56958A039151.25 | Z56958A0 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 39151.25 | 39151.8528 | DAILY | 00015976 | 3RDPARTY | erect new tower 29a | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010329739151.2972222222 | 10103297 |  | Parent | TRUE | NO.4 66KV BUS AT RTS | 39151.2972 | 39151.5896 | DAILY | 00022330 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025740639151.2972222222 | 10257406 | 10103297 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT RTS | 39151.2972 | 39151.5896 | CONT | 00055373 | SPIMAINT | cap bank rebate | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z53158O239151.7777777778 | Z53158O2 |  | Parent | FALSE | A2 TRANS NO.1 BUS 220KV CB AT ROTS | 39151.7778 | 39154.516 | CONT | [12 empty] | 0
_1025820139152.0138888889 | 10258201 |  | Parent | FALSE | W2 GEN TRANS 220KV CB BUS SIDE ISOL AT YPS | 39152.0139 | 39154.1285 | CONT | [12 empty] | 0
_Z56958A139152.23125 | Z56958A1 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 39152.2312 | 39152.6913 | DAILY | 00015976 | 3RDPARTY | erect new tower 29 | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009281939152.2506944445 | 10092819 |  | Parent | TRUE | ROTS NO.1 220KV LINE CB AT RTS | 39152.2507 | 39152.4785 | DAILY | [12 empty] | 0
_1025904339152.2506944445 | 10259043 | 10092819 | Child | FALSE | ROTS NO.1 220KV LINE AT RTS | 39152.2507 | 39152.4785 | DAILY | 00021385 | SPIMAINT | CL.1 O/HAUL - S&S HPF514P/6A CB | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025806739152.2805555556 | 10258067 |  | Parent | FALSE | NO.1 22KV BUS AT RWTS | 39152.2806 | 39152.5806 | DAILY | 00007482 | DBPROX | VSCAP's for discos | DISTCO |  |  | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1025808639153.125 | 10258086 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 39153.125 | 39211.3063 | CONT | 00016423 | GENCO | SCAP for Genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025768639153.25 | 10257686 | X43258N2 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39153.25 | 39153.6861 | DAILY | 00359891 | SPICAPX | Rebate W/O No1 66kV Cap bk during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025768739153.25 | 10257687 | X43258N2 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 39153.25 | 39153.6861 | DAILY | 00016895 | SPICAPX | Rebate W/O No1 66kV React during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258N239153.25 | X43258N2 |  | Parent | TRUE | NO.1 66KV BUS AT RCTS | 39153.25 | 39153.6861 | REPDAILY | 00016976 | SPICAPX | Out W/O No1 66kV BUS to replace CB bus droppers | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758C539154.2347222222 | X49758C5 |  | Parent | TRUE | NO.1 220KV BUS AT BETS | 39154.2347 | 39154.7042 | REPDAILY | 00016305 | SPICAPX | Out W/O Connect existing bus to new. | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758C639154.2347222222 | X49758C6 | X49758C5 | Child | FALSE | R4 220/66/22KV TRANS AT BETS | 39154.2347 | 39154.7042 | REPDAILY | 00016220 | SPICAPX | Out W/O Perf calc for bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025768639154.2381944445 | 10257686 | X43258N2 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39154.2382 | 39154.6847 | DAILY | 00359891 | SPICAPX | Rebate W/O No1 66kV Cap bk during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025768739154.2381944445 | 10257687 | X43258N2 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 39154.2382 | 39154.6847 | DAILY | 00016895 | SPICAPX | Rebate W/O No1 66kV React during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258N239154.2381944445 | X43258N2 |  | Parent | TRUE | NO.1 66KV BUS AT RCTS | 39154.2382 | 39154.6847 | REPDAILY | 00016976 | SPICAPX | Out W/O No1 66kV BUS to replace CB bus droppers | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1023672839154.2534722222 | 10236728 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT ROTS (RTF) | 39154.2535 | 39154.5278 | DAILY | [12 empty] | 0
_X46158L839154.2611111111 | X46158L8 |  | Parent | FALSE | MLTS NO.1 220KV LINE AT BATS | 39154.2611 | 39156.7771 | CONT | 00012429 | SPICAPX | Out W/O MLTS No1 Line to commiss its Fut 2B CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158M939154.4520833333 | Z53158M9 | Z53158M8 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39154.4521 | 39198.2708 | DAILY | 00112418 | VEN_AUG | Rebates Cap bank | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025824339154.7041666667 | 10258243 |  | Parent | FALSE | EX - KGTS 220KV LINE NO.1 BUS CB AT BETS | 39154.7042 | 39155.216 | CONT | [12 empty] | 0
_X49758C539155.2166666667 | X49758C5 |  | Parent | TRUE | NO.1 220KV BUS AT BETS | 39155.2167 | 39155.6757 | REPDAILY | 00016305 | SPICAPX | Out W/O Connect existing bus to new. | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758C639155.2166666667 | X49758C6 | X49758C5 | Child | FALSE | R4 220/66/22KV TRANS AT BETS | 39155.2167 | 39155.6757 | REPDAILY | 00016220 | SPICAPX | Out W/O Perf calc for bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025816039155.2256944444 | 10258160 | X49058E2 | Child | FALSE | NO.1 330KV CAPACITOR BANK AT DDTS | 39155.2257 | 39155.666 | DAILY | 00352085 | SPICAPX | Out W/O Perf calc for Bus outage | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_X49058E239155.2256944444 | X49058E2 |  | Parent | TRUE | NO.1 330KV BUS AT DDTS | 39155.2257 | 39155.666 | DAILY | 00003978 | SPICAPX | Out W/O Cut and remove Rph bus ext & support | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025768639155.23125 | 10257686 | X43258N2 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39155.2312 | 39155.6701 | DAILY | 00359891 | SPICAPX | Rebate W/O No1 66kV Cap bk during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025768739155.23125 | 10257687 | X43258N2 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 39155.2312 | 39155.6701 | DAILY | 00016895 | SPICAPX | Rebate W/O No1 66kV React during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258N239155.23125 | X43258N2 |  | Parent | TRUE | NO.1 66KV BUS AT RCTS | 39155.2312 | 39155.6701 | REPDAILY | 00016976 | SPICAPX | Out W/O No1 66kV BUS to replace CB bus droppers | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024263439155.2430555556 | 10242634 | X32058A8 | Child | FALSE | EX - NO.1 220/66KV TRANS BANK AT MTS | 39155.2431 | 39155.6062 | DAILY | 00026898 | SPICAPX | Avail plant for work on No1 66 kV Bus | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058A839155.2430555556 | X32058A8 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39155.2431 | 39155.6062 | DAILY | 00004569 | SPICAPX | Proximty work | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025814239155.2715277778 | 10258142 |  | Parent | TRUE | EX - HWPS NO.1 220KV LINE CB CT R/PH AT YPS | 39155.2715 | 39155.3222 | DAILY | [12 empty] | 0
_1025814339155.2715277778 | 10258143 | 10258142 | Child | FALSE | HWPS NO.1 220KV LINE AT YPS | 39155.2715 | 39155.3222 | DAILY | 00016409 | SPIMAINT | rebate C.T oil samples | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025805939155.3097222222 | 10258059 |  | Parent | TRUE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39155.3097 | 39155.3889 | DAILY | [12 empty] | 0
_1025806039155.3097222222 | 10258060 | 10258059 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39155.3097 | 39155.3889 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during 275CB de-energ | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025805439155.3826388889 | 10258054 |  | Parent | FALSE | EX - NO.2 TRANS 220KV CB AT TGTS | 39155.3826 | 39155.4285 | DAILY | [12 empty] | 0
_1025800839155.475 | 10258008 |  | Parent | FALSE | EX - NO.1 TRANS GROUP 220KV CB AT TGTS | 39155.475 | 39155.5396 | DAILY | [12 empty] | 0
_1025820439155.5 | 10258204 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 39155.5 | 39158.3507 | CONT | [12 empty] | 0
_X49758C539156.2131944445 | X49758C5 |  | Parent | TRUE | NO.1 220KV BUS AT BETS | 39156.2132 | 39156.8028 | REPDAILY | 00016305 | SPICAPX | Out W/O Connect existing bus to new. | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758C639156.2131944445 | X49758C6 | X49758C5 | Child | FALSE | R4 220/66/22KV TRANS AT BETS | 39156.2132 | 39156.8028 | REPDAILY | 00016220 | SPICAPX | Out W/O Perf calc for bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025816139156.2298611111 | 10258161 | X49058E3 | Child | FALSE | NO.2 330KV CAPACITOR BANK AT DDTS | 39156.2299 | 39156.5847 | DAILY | 00352093 | SPICAPX | Out W/O Rebate calc for bus outage | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_1025816439156.2298611111 | 10258164 | X49058E3 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 39156.2299 | 39156.5847 | DAILY | 00352121 | SPICAPX | Out W/O Rebate calc for bus outage | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X49058E339156.2298611111 | X49058E3 |  | Parent | TRUE | NO.2 330KV BUS AT DDTS | 39156.2299 | 39156.5847 | DAILY | 00003979 | SPICAPX | Out W/O Weld new flags onto bus | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025768639156.2326388889 | 10257686 | X43258N2 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39156.2326 | 39156.6861 | DAILY | 00359891 | SPICAPX | Rebate W/O No1 66kV Cap bk during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025768739156.2326388889 | 10257687 | X43258N2 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 39156.2326 | 39156.6861 | DAILY | 00016895 | SPICAPX | Rebate W/O No1 66kV React during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258N239156.2326388889 | X43258N2 |  | Parent | TRUE | NO.1 66KV BUS AT RCTS | 39156.2326 | 39156.6861 | REPDAILY | 00016976 | SPICAPX | Out W/O No1 66kV BUS to replace CB bus droppers | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025804139156.2597222222 | 10258041 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 39156.2597 | 39156.5632 | DAILY | 00001147 | SPIMAINT | no low oil in blue phase 220kv bushing | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025437539156.2805555556 | 10254375 |  | Parent | FALSE | BATS NO.1 220KV LINE NO.1 BUS CB AT MLTS | 39156.2806 | 39156.3396 | DAILY | [12 empty] | 0
_1025650839156.3423611111 | 10256508 |  | Parent | FALSE | HYTS NO.1 LINE/SYTS NO.1 LINE 500KV CB AT MLTS | 39156.3424 | 39156.5694 | DAILY | [12 empty] | 0
_1025831539156.6527777778 | 10258315 |  | Parent | FALSE | EX - NO.4 TRANS 220KV CB AT BETS | 39156.6528 | 39156.7653 | DAILY | [12 empty] | 0
_1025832639156.8027777778 | 10258326 |  | Parent | FALSE | EX - KGTS 220KV LINE NO.1 BUS CB AT BETS | 39156.8028 | 39249.2708 | CONT | [12 empty] | 0
_1025769239157.2328125 | 10257692 | X43258N3 | Child | FALSE | KGTS 220KV LINE AT RCTS | 39157.2328 | 39157.5201 | DAILY | 00016959 | SPICAPX | Rebate W/O KGTS Line for No1 220kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025769339157.2328125 | 10257693 | X43258N3 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT RCTS | 39157.2328 | 39157.5201 | DAILY | 00360382 | SPICAPX | Rebate W/O No1 220 Cap for No1 220kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025769539157.2328125 | 10257695 | X43258N3 | Child | FALSE | BSS 220KV LINE AT RCTS | 39157.2328 | 39157.5201 | DAILY | 00016966 | SPICAPX | Rebate W/O BSS Line for No1 220kV Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025769839157.2328125 | 10257698 | X43258N3 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39157.2328 | 39157.5201 | DAILY | 00337581 | SPICAPX | Perf calc W/O No1 TR for No1 220kV Bus proximity | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258N339157.2328125 | X43258N3 |  | Parent | TRUE | EX - NO.1 220KV BUS AT RCTS | 39157.2328 | 39157.5201 | DAILY | 00016901 | SPICAPX | Out W/O No1 220kV Bus to decommiss bays A & B | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025828939157.2361111111 | 10258289 |  | Parent | FALSE | MLRC 220KV LINE AT RCTS | 39157.2361 | 39157.5236 | DAILY | 00352130 | SPIMAINT | RCTS-MLRC Line Required De-energised | SPIPOWER |  |  | Circuits | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 3
_Z53158P839157.2444444445 | Z53158P8 |  | Parent | FALSE | HWPS NO.2 220KV LINE AT ROTS | 39157.2444 | 39157.6173 | DAILY | 00024004 | VEN_AUG | Erect New HWPS No2 LINE No1 BUS CB LINE SIDE ROI | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025809639157.2506944445 | 10258096 |  | Parent | TRUE | NO.1 220KV BUS AT DDTS | 39157.2507 | 39157.6694 | DAILY | 00003976 | SPIMAINT | NO.1 220KV BUS AT DDTS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025809839157.2506944445 | 10258098 | 10258096 | Child | FALSE | GNTS NO.1 220KV LINE AT DDTS | 39157.2507 | 39157.6694 | DAILY | 00352475 | SPIMAINT | GNTS NO.1 220KV LINE AT DDTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025809939157.2506944445 | 10258099 | 10258096 | Child | FALSE | MBTS NO.1 220KV LINE AT DDTS | 39157.2507 | 39157.6694 | DAILY | 00012361 | SPIMAINT | MBTS NO.1 220KV LINE AT DDTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025810039157.2506944445 | 10258100 | 10258096 | Child | FALSE | H1 330/220KV TRANS BANK AT DDTS | 39157.2507 | 39157.6694 | DAILY | 00337558 | SPIMAINT | NO.1 TRANS BANK AT DDTS | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025810139157.2506944445 | 10258101 | 10258096 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 39157.2507 | 39157.6694 | DAILY | 00351939 | SPIMAINT | NO.1 220KV CAPACITOR BANK AT DDTS | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1025437639157.2777777778 | 10254376 |  | Parent | FALSE | GTS NO.1 220KV LINE NO.2 BUS CB AT MLTS | 39157.2778 | 39157.3646 | DAILY | [12 empty] | 0
_1025804939157.3041666667 | 10258049 |  | Parent | FALSE | RWTS 220KV LINE NO.2 BUS CB AT TTS | 39157.3042 | 39157.4068 | DAILY | [12 empty] | 0
_1025437339157.3652777778 | 10254373 |  | Parent | FALSE | A1 TRANS NO.1 BUS 220KV CB AT MLTS | 39157.3653 | 39157.4167 | DAILY | [12 empty] | 0
_1025837839157.8951388889 | 10258378 |  | Parent | FALSE | NO.7 GEN TRANS 220KV CB AT HWPS | 39157.8951 | 39159.2076 | CONT | [12 empty] | 0
_1010191039158.2590277778 | 10101910 |  | Parent | FALSE | NO.3 22KV BUS AT BLTS | 39158.259 | 39158.5792 | DAILY | 00002656 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1025837939158.2604166667 | 10258379 | X2A958G3 | Child | FALSE | SYTS-MLTS 2 500KV WY | 39158.2604 | 39158.6424 | DAILY | 00022638 | SPICAPX | Rebate outage | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X2A958G339158.2604166667 | X2A958G3 |  | Parent | TRUE | SYTS NO.2 500KV LINE Y PROT AT MLTS | 39158.2604 | 39158.6424 | DAILY | [12 empty] | 0
_1010166839158.26875 | 10101668 |  | Parent | FALSE | B3 TRANS NO.2 BUS 220KV CB AT GTS | 39158.2688 | 39158.6 | REPDAILY | [12 empty] | 0
_1009282039159.2277777778 | 10092820 |  | Parent | TRUE | ROTS NO.4 220KV LINE CB AT RTS | 39159.2278 | 39159.5667 | DAILY | [12 empty] | 0
_1009282239159.2277777778 | 10092822 | 10092820 | Child | FALSE | ROTS NO.4 220KV LINE CB LINE SIDE ISOL AT RTS | 39159.2278 | 39159.5667 | DAILY | [12 empty] | 0
_1009282539159.2277777778 | 10092825 | 10092820 | Child | FALSE | ROTS NO.4 220KV LINE CB LINE SIDE E/SW AT RTS | 39159.2278 | 39159.5667 | DAILY | [12 empty] | 0
_1009282639159.2277777778 | 10092826 | 10092820 | Child | FALSE | ROTS NO.4 220KV LINE E/SW AT RTS | 39159.2278 | 39159.5667 | DAILY | [12 empty] | 0
_1025805539159.2277777778 | 10258055 | 10092820 | Child | FALSE | ROTS NO.4 220KV LINE AT RTS | 39159.2278 | 39159.5667 | DAILY | 00021338 | SPIMAINT | Line Rebate | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025775739159.2340277778 | 10257757 | X46158M3 | Child | FALSE | TGTS 220KV LINE AT BATS | 39159.234 | 39159.6993 | DAILY | 00012435 | SPICAPX | Rebate W/O TGTS Line during No1 220kV BUS outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025775839159.2340277778 | 10257758 | X46158M3 | Child | FALSE | B2 220/66KV TRANS AT BATS | 39159.234 | 39159.6993 | DAILY | 00006555 | SPICAPX | Perf calc W/O No2 Trans during No1 220 BUS outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158M339159.2340277778 | X46158M3 |  | Parent | TRUE | NO.1 220KV BUS AT BATS | 39159.234 | 39159.6993 | DAILY | 00006558 | SPICAPX | Out W/O No1 220kV BUS to decommiss bus VT | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X23358C639159.25625 | X23358C6 |  | Parent | FALSE | B2 220/66KV TRANS AT WMTS | 39159.2562 | 39159.5062 | DAILY | 00003235 | SPICAPX | commission new wti, insert new probe & remove old | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z56958A539159.2604166667 | Z56958A5 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 39159.2604 | 39159.6535 | DAILY | 00015976 | 3RDPARTY | dismantle old tower 29 | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010166839159.26875 | 10101668 |  | Parent | FALSE | B3 TRANS NO.2 BUS 220KV CB AT GTS | 39159.2688 | 39159.4799 | REPDAILY | [12 empty] | 0
_1025823339159.425 | 10258233 |  | Parent | FALSE | NO.2 22KV BUS AT RWTS | 39159.425 | 39159.5972 | DAILY | 00007483 | DBPROX | VSCAP for DOC | DISTCO |  |  | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X41258D639160.2305555556 | X41258D6 |  | Parent | TRUE | EX - NO.2 220KV BUS AT SHTS | 39160.2306 | 39160.691 | DAILY | 00000846 | SPICAPX | W/O for pref Calc to remove No2 TX Bi-pods etc | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X41258D739160.2305555556 | X41258D7 | X41258D6 | Child | FALSE | GNTS-SHTS 3 220KV NW | 39160.2306 | 39160.691 | CONT | 00055389 | SPICAPX | Pref Calc W/O for No2 220kVBus Outage | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025840239160.3520833333 | 10258402 |  | Parent | FALSE | B5 220/66KV TRANS GROUP AT BLTS | 39160.3521 | 39160.3757 | CONT | 00018452 | 3RDPARTY | Remote Trip1 NO5 TRANS GROUP by DistCo Contractor | DISTCO |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 3
_1025840339160.38125 | 10258403 |  | Parent | FALSE | B5 220/66KV TRANS GROUP AT BLTS | 39160.3812 | 39160.4 | CONT | 00018452 | 3RDPARTY | Remote Trip2 NO5 TRANS GROUP by DistCo Contractor | DISTCO |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 3
_1025840839161.0625 | 10258408 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT MLTS | 39161.0625 | 39161.3278 | CONT | [12 empty] | 0
_X49858B539161.2097222222 | X49858B5 |  | Parent | FALSE | TRANSFORMER 66KV BUS AT MBTS | 39161.2097 | 39164.7153 | DAILY | 00362419 | SPICAPX | Out W/O Trans 66kV ring bus to connect Fut B1 TR | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X49858B639161.2111111111 | X49858B6 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 39161.2111 | 39164.7833 | CONT | 00060194 | SPICAPX | Out W/O DDTS No2 Line to cutover to No1 220kV Bus | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010237739161.2270833333 | 10102377 |  | Parent | FALSE | SYN/COND AT TSTS | 39161.2271 | 39164.3688 | CONT | 00007626 | SPIMAINT | Take Bearing Oil | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010212239161.2555555556 | 10102122 |  | Parent | FALSE | SMTS 500KV LINE AT KTS | 39161.2556 | 39161.6312 | REPDAILY | 00015991 | SPIMAINT | O/Haul - 500kV Line (W) | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025831139161.2743055556 | 10258311 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.2 BUS CB AT HWTS | 39161.2743 | 39162.5097 | DAILY | [12 empty] | 0
_1025437439161.2847222222 | 10254374 |  | Parent | TRUE | BATS NO.2 220KV LINE CB AT MLTS | 39161.2847 | 39161.3556 | DAILY | [12 empty] | 0
_1025905639161.2847222222 | 10259056 | 10254374 | Child | FALSE | BATS NO.2 220KV LINE AT MLTS | 39161.2847 | 39161.3556 | DAILY | 00022969 | SPIMAINT | Tyree CT Oil sample | ALSTOM |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025906439161.5458333333 | 10259064 | X43258N7 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 39161.5458 | 39161.6111 | REPDAILY | 00016897 | SPICAPX | Out W/O No2 66kV Bus prot upgrade | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025906539161.5458333333 | 10259065 | X43258N7 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 39161.5458 | 39161.6111 | REPDAILY | 00357254 | SPICAPX | Out W/O No2 66kV Bus prot upgrade | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258N739161.5458333333 | X43258N7 |  | Parent | TRUE | NO.2 66KV BUS X PROT AT RCTS | 39161.5458 | 39161.6111 | REPDAILY | [12 empty] | 0
_X2A858T739162.2375 | X2A858T7 |  | Parent | FALSE | L1 220/22KV TRANS AT BTS | 39162.2375 | 39162.3653 | DAILY | 00360728 | SPICAPX | access to the lid of trans enclosure for repairs | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025906139162.2486111111 | 10259061 | X49658D4 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 39162.2486 | 39162.7181 | DAILY | 00359897 | SPICAPX | Out W/O Replace VT's Bay J to K, comm No 2 Rea CB | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025906239162.2486111111 | 10259062 | X49658D4 | Child | FALSE | NO.2 66KV REACTOR AT HOTS | 39162.2486 | 39162.7181 | DAILY | 00357255 | SPICAPX | Out W/O Replace VT's Bay J to K, comm No 2 Rea CB | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49658D439162.2486111111 | X49658D4 |  | Parent | TRUE | NO.2 66KV BUS AT HOTS | 39162.2486 | 39162.7184 | DAILY | 00006941 | SPICAPX | Out W/O Replace VT's Bay J to K, comm No 2 Rea CB | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010212239162.2569444444 | 10102122 |  | Parent | FALSE | SMTS 500KV LINE AT KTS | 39162.2569 | 39162.6729 | REPDAILY | 00015991 | SPIMAINT | O/Haul - 500kV Line (W) | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025437839162.2756944445 | 10254378 |  | Parent | FALSE | TGTS 220KV LINE NO.2 BUS CB AT MLTS | 39162.2757 | 39162.3361 | DAILY | [12 empty] | 0
_1025905939162.3 | 10259059 | X38458M9 | Child | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39162.3 | 39162.7528 | DAILY | 00003104 | SPICAPX | Out W/O Commission new TRG No 1 FDR CB | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X38458M939162.3 | X38458M9 |  | Parent | TRUE | EX - NO.1 66KV BUS AT TGTS | 39162.3 | 39162.7528 | DAILY | 00003132 | SPICAPX | Out W/O Commission new TRG No 1 FDR CB | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025442839162.3368055556 | 10254428 |  | Parent | FALSE | A2 TRANS NO.1 BUS 220KV CB AT MLTS | 39162.3368 | 39162.4118 | DAILY | [12 empty] | 0
_X38458L639162.3902777778 | X38458L6 |  | Parent | TRUE | EX - NO.1 220KV BUS AT TGTS | 39162.3903 | 39162.7326 | DAILY | 00003130 | SPICAPX | Out W/O Install bi-pods to Fut BATS L & No2 Tr ROI | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458L739162.3902777778 | X38458L7 | X38458L6 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39162.3903 | 39162.7326 | DAILY | 00023231 | SPICAPX | Out W/O Perf calc for BUS outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025906439162.5722222222 | 10259064 | X43258N7 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 39162.5722 | 39162.6694 | REPDAILY | 00016897 | SPICAPX | Out W/O No2 66kV Bus prot upgrade | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025906539162.5722222222 | 10259065 | X43258N7 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 39162.5722 | 39162.6694 | REPDAILY | 00357254 | SPICAPX | Out W/O No2 66kV Bus prot upgrade | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258N739162.5722222222 | X43258N7 |  | Parent | TRUE | NO.2 66KV BUS X PROT AT RCTS | 39162.5722 | 39162.6696 | REPDAILY | [12 empty] | 0
_Z56958A239162.8131944445 | Z56958A2 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 39162.8132 | 39163.3021 | DAILY | 00015976 | 3RDPARTY | transfer conductors to new towers 29 and 29a | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025748839163.2166666667 | 10257488 | X56558A0 | Child | FALSE | WOTS-DDTS 330KV NW | 39163.2167 | 39163.5271 | DAILY | 00060189 | SPICAPX | Out W/O Replace WOTS line No 2 BUS CB CT's | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558A039163.2166666667 | X56558A0 |  | Parent | TRUE | WOTS-DDTS 330KV NW | 39163.2167 | 39163.5271 | DAILY | 00060189 | SPICAPX | Out W/O WOTS-DDTS Line CT replace at WOTS | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158M439163.2569444444 | Z53158M4 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 39163.2569 | 39163.75 | DAILY | 00004778 | VEN_AUG | Bus install bus bi pods ERTS No2 LINE No2 BUS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158M539163.2569444444 | Z53158M5 | Z53158M4 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39163.2569 | 39163.75 | CONT | 00112418 | VEN_AUG | Rebate Bus outage to remove bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025841339163.2583333333 | 10258413 |  | Parent | FALSE | EX - O.O.S 220/66KV TRANS BANK (9 SINGLE PHASE UNITS) AT TTS | 39163.2583 | 39164.334 | REPDAILY | 00026062 | SPIMAINT | transformer testing | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER | Out of Service | 0
_1025442039163.2805555556 | 10254420 |  | Parent | TRUE | B2 TRANS NO.1 BUS 220KV CB AT GTS | 39163.2806 | 39163.3417 | DAILY | [12 empty] | 0
_1025911139163.2805555556 | 10259111 | 10254420 | Child | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39163.2806 | 39163.3417 | DAILY | 00017906 | SPIMAINT | Tyree CT Oil sample | ALSTOM |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025784139163.2833333333 | 10257841 | X43258N5 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39163.2833 | 39163.7986 | DAILY | 00359891 | SPICAPX | Rebate W/O No1 66kV Cap bk during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025784239163.2833333333 | 10257842 | X43258N5 | Child | FALSE | NO.1 66KV REACTOR AT RCTS | 39163.2833 | 39163.7986 | DAILY | 00016895 | SPICAPX | Rebate W/O No1 66kV React during bus de-energ | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258N539163.2833333333 | X43258N5 |  | Parent | TRUE | NO.1 66KV BUS AT RCTS | 39163.2833 | 39163.7986 | DAILY | 00016976 | SPICAPX | Out W/O No1 66kV BUS to replace 1-2 66kV BT CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025846739163.2965277778 | 10258467 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 39163.2965 | 39163.5563 | DAILY | [12 empty] | 0
_Z53458B439163.3090277778 | Z53458B4 |  | Parent | FALSE | NO.2 500KV BUS AT ROTS | 39163.309 | 39164.2757 | CONT | 00362955 | VEN_AUG | MODIFY EARTH SW's NO LINE OUTAGES CB'S ONLY | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458M039163.3201388889 | X38458M0 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 39163.3201 | 39163.6097 | DAILY | 00003131 | SPICAPX | Out W/O Install bus bi-pods to Fut BATS L No 2 CB | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458M139163.3201388889 | X38458M1 | X38458M0 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39163.3201 | 39163.6097 | DAILY | 00003127 | SPICAPX | Out W/O Perf calc for No 2 220kV bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025437739163.3715277778 | 10254377 |  | Parent | FALSE | GTS NO.2 LINE/A1 TRANS 220KV CB AT MLTS | 39163.3715 | 39163.4243 | DAILY | [12 empty] | 0
_1025848439163.4659722222 | 10258484 |  | Parent | FALSE | EX - NO.4A 66KV CAPACITOR BANK AT TTS | 39163.466 | 39164.4167 | DAILY | 00001486 | FORCED | re-balance white phase | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025902639163.4736111111 | 10259026 |  | Parent | FALSE | NO.4B 66KV CAPACITOR BANK AT TTS | 39163.4736 | 39164.4167 | CONT | 00337509 | FORCED | Trip of 4A Cap CB | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z53158T539163.75 | Z53158T5 |  | Parent | FALSE | ERTS NO.2 220KV LINE NO.2 BUS CB AT ROTS | 39163.75 | 39166.7444 | CONT | [12 empty] | 0
_Z56958A339163.8138888889 | Z56958A3 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 39163.8139 | 39164.234 | DAILY | 00015976 | 3RDPARTY | transfer conductors to new towers 29 and 29a | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025850539164.5416666667 | 10258505 |  | Parent | FALSE | JLGA NO.2 UNIT TRANS DISC CB AT JLGA | 39164.5417 | 39164.5424 | CONT | [12 empty] | 0
_1025851039164.8541666667 | 10258510 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39164.8542 | 39167.5868 | CONT | 00356084 | GENCO | HWPS No6 Gen Trans Isolations for SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53458B039165.2145833333 | Z53458B0 |  | Parent | TRUE | HWTS NO.3 500KV LINE AT ROTS (RTF) | 39165.2146 | 39166.8368 | CONT | 00359383 | VEN_AUG | No2 500kv bus & hwts 3 Line move Line to new spot | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53458B539165.2145833333 | Z53458B5 | Z53458B0 | Child | FALSE | NO.2 500KV BUS AT ROTS | 39165.2146 | 39166.8368 | CONT | 00362955 | VEN_AUG | BUS OUTAGE | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158Q739165.2236111111 | Z53158Q7 |  | Parent | TRUE | EX - NO.3 220KV BUS AT ERTS | 39165.2236 | 39165.6493 | DAILY | 00004379 | VEN_AUG | Disconnect 3-4 B.T CB 3 B/S, No3 tran 66 connect | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158Q839165.2236111111 | Z53158Q8 | Z53158Q7 | Child | FALSE | B3 220/66KV TRANS AT ERTS | 39165.2236 | 39165.6493 | DAILY | 00004371 | VEN_AUG | Avail of plant Replace 3-4 B.T CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025841339165.2458333333 | 10258413 |  | Parent | FALSE | EX - O.O.S 220/66KV TRANS BANK (9 SINGLE PHASE UNITS) AT TTS | 39165.2458 | 39165.8097 | REPDAILY | 00026062 | SPIMAINT | transformer testing | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER | Out of Service | 0
_Z56958A439165.2583333333 | Z56958A4 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 39165.2583 | 39165.7646 | DAILY | 00022702 | 3RDPARTY | gts no.1 & 3 lines under eap - erect new tower 29a | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158L939165.3368055556 | X46158L9 |  | Parent | FALSE | TGTS 220KV LINE AT BATS | 39165.3368 | 39165.75 | CONT | 00012435 | SPICAPX | Out W/O TGTS Line new CVT's & Fut 2 Bus TIE | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458N039165.75 | X38458N0 |  | Parent | FALSE | BATS-TGTS 220KV WW | 39165.75 | 39168.7236 | CONT | 00022665 | SPICAPX | Out W/O Future BATS LINE No 1 & 2 BUS CBs | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025853539166.2215277778 | 10258535 |  | Parent | FALSE | NO.2 66KV REACTOR AT HOTS | 39166.2215 | 39168.5729 | CONT | 00357255 | FAULT | No2 REACTOR TRIPPED FREE | ALSTOM |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z56958A639166.25625 | Z56958A6 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 39166.2562 | 39166.8146 | DAILY | 00022702 | 3RDPARTY | gts no.1 & 3 lines under eap - erect new tower 29 | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158L839166.2833333333 | Z53158L8 |  | Parent | FALSE | ERTS NO.2 220KV LINE AT ROTS | 39166.2833 | 39166.8097 | DAILY | 00023971 | VEN_AUG | ERTS No2 Line outage to Reconnect CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158Q939166.2833333333 | Z53158Q9 |  | Parent | FALSE | EX - 3-4 220KV BUS TIE CB AT ERTS | 39166.2833 | 39172.5083 | CONT | [12 empty] | 0
_Z53158O839166.2854166667 | Z53158O8 |  | Parent | TRUE | EX - NO.4 220KV BUS AT ERTS | 39166.2854 | 39166.6882 | DAILY | 00004380 | VEN_AUG | install future 3-4 b.t CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158O939166.2854166667 | Z53158O9 | Z53158O8 | Child | FALSE | B4 220/66KV TRANS AT ERTS | 39166.2854 | 39166.6882 | CONT | 00004372 | VEN_AUG | Avail of plant Replace 3-4 B.T CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025853239166.3159722222 | 10258532 |  | Parent | FALSE | B2 220/66KV TRANS AT SVTS | 39166.316 | 39166.6014 | CONT | 00004850 | FORCED | SVTS: Low Oil Trip B2 220/66kV Trans | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025853339166.3381944444 | 10258533 |  | Parent | FALSE | SVTS NO.2 220KV LINE AT ROTS | 39166.3382 | 39166.3528 | DAILY | 00023968 | FAULT | Trip on ROTS-SVTS No 2 220kV Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025853439166.3381944444 | 10258534 |  | Parent | FALSE | SVTS-HTS 2 220KV E | 39166.3382 | 39166.3528 | DAILY | 00022773 | FAULT | Trip on SVTS-HTS No 2 220kV Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858B739167.2534722222 | X49858B7 |  | Parent | FALSE | MBTS-EPS 2 220KV N | 39167.2535 | 39171.6299 | CONT | 00055381 | SPICAPX | Out W/O EPS 2 Line to cutover to new CB on No1 bus | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49058E439167.2680555556 | X49058E4 |  | Parent | FALSE | SMTS NO.1 330KV LINE AT DDTS | 39167.2681 | 39167.7153 | DAILY | 00012354 | SPICAPX | Out W/O Replace SMTS LINE No 1 BUS CB CT's | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158M639167.2715277778 | Z53158M6 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39167.2715 | 39167.6674 | DAILY | 00004776 | VEN_AUG | Bus outage to remove bus bi pods HWPS 2 Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158M739167.2715277778 | Z53158M7 | Z53158M6 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39167.2715 | 39167.6674 | CONT | 00354024 | VEN_AUG | Rebate Bus outage to remove bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1010192839167.2722222222 | 10101928 |  | Parent | FALSE | SYN/COND AT BLTS | 39167.2722 | 39169.6819 | CONT | 00002547 | SPIMAINT | 3 Monthly O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010236739167.3027777778 | 10102367 |  | Parent | TRUE | TTS 220KV LINE E/SW AT TSTS | 39167.3028 | 39167.5958 | DAILY | [12 empty] | 0
_1010236839167.3027777778 | 10102368 | 10102367 | Child | FALSE | TTS 220KV LINE/NO.2 BUS CB LINE SIDE E/SW AT TSTS | 39167.3028 | 39167.5958 | DAILY | [12 empty] | 0
_1010238239167.3027777778 | 10102382 | 10102367 | Child | FALSE | TTS 220KV LINE/B1 TRANS CB TTS LINE SIDE ROI AT TSTS | 39167.3028 | 39167.5958 | DAILY | [12 empty] | 0
_1010238339167.3027777778 | 10102383 | 10102367 | Child | FALSE | TTS 220KV LINE/NO.2 BUS CB LINE SIDE ISOL AT TSTS | 39167.3028 | 39167.5958 | DAILY | [12 empty] | 0
_1010239339167.3027777778 | 10102393 | 10102367 | Child | FALSE | TTS LINE/NO.1 TRANS 220KV CB TTS LINE S E/SW AT TSTS | 39167.3028 | 39167.5958 | DAILY | [12 empty] | 0
_1025912039167.3027777778 | 10259120 | 10102367 | Child | FALSE | TTS 220KV LINE AT TSTS | 39167.3028 | 39167.5958 | DAILY | 00020098 | SPIMAINT | REBATE FOR LINE MAINTENANCE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025831239167.3138888889 | 10258312 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB AT HWTS | 39167.3139 | 39167.5646 | DAILY | [12 empty] | 0
_1025850639167.3958333333 | 10258506 |  | Parent | FALSE | EX - JLGS 'B' 220KV LINE AT JLTS | 39167.3958 | 39217.4271 | CONT | 00015946 | GENCO | ISOL FOR POWER STATION | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025855339167.4770833333 | 10258553 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39167.4771 | 39167.4861 | DAILY | [12 empty] | 0
_1025856339167.6340277778 | 10258563 |  | Parent | FALSE | NO.4A 66KV CAPACITOR BANK CB AT TTS | 39167.634 | 39167.6521 | DAILY | [12 empty] | 0
_X49058E539167.7152777778 | X49058E5 |  | Parent | FALSE | SMTS NO.1 330KV LINE NO.1 BUS CB AT DDTS | 39167.7153 | 39169.7562 | CONT | [12 empty] | 0
_1025641339168.2805555556 | 10256413 | X43258M0 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 39168.2806 | 39168.6875 | DAILY | 00357254 | SPICAPX | Rebate W/O #3 React prox during 2B TR 66 CB remove | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258M039168.2805555556 | X43258M0 |  | Parent | TRUE | EX - NO.2B TRANS 66KV CB AT RCTS | 39168.2806 | 39168.6875 | DAILY | [12 empty] | 0
_V62258A439168.2958333333 | V62258A4 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.2 BUS CB AT SMTS | 39168.2958 | 39170.691 | CONT | [12 empty] | 0
_1010237939168.3 | 10102379 | 10102390 | Child | FALSE | ROTS 220KV LINE NO.1 BUS CB LINE SIDE ISOL AT TSTS | 39168.3 | 39168.5951 | DAILY | [12 empty] | 0
_1010238039168.3 | 10102380 | 10102390 | Child | FALSE | ROTS 220KV LINE NO.2 BUS CB LINE SIDE ISOL AT TSTS | 39168.3 | 39168.5951 | DAILY | [12 empty] | 0
_1010238939168.3 | 10102389 | 10102390 | Child | FALSE | ROTS 220KV LINE NO.1 BUS CB LINE SIDE E/SW AT TSTS | 39168.3 | 39168.5951 | DAILY | [12 empty] | 0
_1010239039168.3 | 10102390 |  | Parent | TRUE | ROTS 220KV LINE E/SW AT TSTS | 39168.3 | 39168.5951 | DAILY | [12 empty] | 0
_1010239139168.3 | 10102391 | 10102390 | Child | FALSE | ROTS 220KV LINE NO.2 BUS CB LINE SIDE E/SW AT TSTS | 39168.3 | 39168.5951 | DAILY | [12 empty] | 0
_1025912139168.3 | 10259121 | 10102390 | Child | FALSE | ROTS 220KV LINE AT TSTS | 39168.3 | 39168.5951 | DAILY | 00020107 | SPIMAINT | REBATE FOR LINE MAINTENANCE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025849239168.325 | 10258492 |  | Parent | FALSE | MLTS-HYTS 1 500KV W | 39168.325 | 39168.3333 | DAILY | 00022630 | SW_NEM | Restoring line shunt reactors to service | NEMMCO |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025846239168.325 | 10258462 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39168.325 | 39168.5542 | CONT | 00319998 | SPIMAINT | Wash V-String insulators at T628 | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025849339168.5555555556 | 10258493 |  | Parent | FALSE | MLTS-HYTS 2 500KV W | 39168.5556 | 39168.5604 | DAILY | 00022633 | SW_NEM | De-energise line to restore shunt reactors at MLTS | NEMMCO |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025846339168.5604166667 | 10258463 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39168.5604 | 39168.7951 | DAILY | 00319999 | SPIMAINT | Wash V-String insulators at T628 | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025646139168.69375 | 10256461 | X43258M1 | Child | FALSE | NO.2B TRANS AT RCTS | 39168.6937 | 39182.4486 | CONT | 00016760 | SPICAPX | Perf calc W/O 2B Trans during 66kV CB civil works | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258M139168.69375 | X43258M1 |  | Parent | TRUE | EX - NO.2B TRANS 66KV CB AT RCTS | 39168.6937 | 39182.4486 | CONT | [12 empty] | 0
_X38458N339168.7236111111 | X38458N3 |  | Parent | FALSE | BATS-TGTS 220KV WW | 39168.7236 | 39169.6111 | DAILY | 00022665 | SPICAPX | Out W/O Tune line chokes and commish CB's | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025889939168.9395833333 | 10258899 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39168.9396 | 39171.5618 | CONT | 00356084 | GENCO | HWPS No6 Gen Tran Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z56958A739168.9826388889 | Z56958A7 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 39168.9826 | 39169.266 | DAILY | 00022702 | 3RDPARTY | transfer conductors to new towers 29 & 29a | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025892839169.6354166667 | 10258928 |  | Parent | FALSE | EX - SMTS LINE/A2 TRANS 500KV CB AT KTS | 39169.6354 | 39170.6125 | DAILY | [12 empty] | 0
_X49058E639170.25 | X49058E6 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT DDTS | 39170.25 | 39170.7014 | DAILY | 00337558 | SPICAPX | Out W/O change CT's on No 1 TR No 1 bus CB | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X43258N639170.2590277778 | X43258N6 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39170.259 | 39176.6444 | DAILY | 00337584 | SPICAPX | Out W/O No2 Trans grp commiss on to new 1B CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010146639170.2729166667 | 10101466 |  | Parent | FALSE | SYN/COND AT FBTS | 39170.2729 | 39172.6028 | CONT | 00002697 | SPIMAINT | SYNCHRONOUS CONDENSER Overhaul | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010135739170.3152777778 | 10101357 |  | Parent | TRUE | HWPS NO.1 220KV LINE E/SW AT JLTS | 39170.3153 | 39170.5896 | DAILY | [12 empty] | 0
_1025640739170.3152777778 | 10256407 | 10101357 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 39170.3153 | 39170.5896 | DAILY | 00015936 | SPIMAINT | Rebate for line equipment o/haul | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458N739170.3368055556 | X38458N7 |  | Parent | FALSE | MLTS 220KV LINE NO.2 BUS CB AT TGTS | 39170.3368 | 39170.5701 | DAILY | [12 empty] | 0
_1025913339170.4076388889 | 10259133 |  | Parent | FALSE | BATS 220KV LINE AT TGTS | 39170.4076 | 39170.4132 | DAILY | 00023130 | SPICAPX | Rebate BATS-TGTS off loaded during BU prot checks | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49058E739170.7013888889 | X49058E7 |  | Parent | FALSE | H1 TRANS NO.1 BUS 330KV CB AT DDTS | 39170.7014 | 39172.5944 | CONT | [12 empty] | 0
_X49758D139170.7034722222 | X49758D1 |  | Parent | FALSE | EX - FVTS/SHTS 220KV LINE NO.1 BUS CB AT BETS | 39170.7035 | 39170.7451 | DAILY | [12 empty] | 0
_Z56958A939170.8597222222 | Z56958A9 |  | Parent | FALSE | KTS -GTS 3 220KV WY | 39170.8597 | 39171.2965 | DAILY | 00022709 | 3RDPARTY | transfer conductors to new towers 29 & 29a | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158O039171.2645833333 | Z53158O0 |  | Parent | FALSE | RTS NO.1 220KV LINE AT ROTS | 39171.2646 | 39171.4292 | DAILY | 00023111 | VEN_AUG | ROTS-RTS No1 Line outage to disconnect No 2 CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025896339171.3666666667 | 10258963 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 39171.3667 | 39171.5069 | DAILY | [12 empty] | 0
_1025914839171.44375 | 10259148 |  | Parent | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39171.4437 | 39171.4604 | CONT | 00351697 | 3RDPARTY | BWSH 22kV Feeder damaged by Alinta Tripped L3 Tran | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025914939171.44375 | 10259149 |  | Parent | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39171.4437 | 39171.4604 | CONT | 00026900 | 3RDPARTY | BWSH 22kV Feeder damaged by Alinta Tripped L3 Tran | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 3
_1025896839171.44375 | 10258968 |  | Parent | FALSE | EX - NO.3 220/22KV TRANS BANK AT MTS | 39171.4437 | 39171.6201 | CONT | 00026903 | 3RDPARTY | BWSH 22kV Feeder damaged by Alinta Tripped L3 Tran | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 3
_1025915039171.44375 | 10259150 |  | Parent | FALSE | EX - NO.1 220/22KV TRANS BANK AT MTS | 39171.4437 | 39171.6854 | CONT | 00026901 | 3RDPARTY | BWSH 22kV Feeder damaged by Alinta Tripped L3 Tran | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 3
_1025894339171.7402777778 | 10258943 |  | Parent | FALSE | AUX TRANS 'A' 220KV CB AT YPS | 39171.7403 | 39175.6354 | DAILY | [12 empty] | 0
_Z56958B339171.8583333333 | Z56958B3 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 39171.8583 | 39172.3056 | DAILY | 00015976 | 3RDPARTY | transfer bottom phase to new tower 29 | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025899339171.8958333333 | 10258993 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 39171.8958 | 39175.2882 | CONT | 00356081 | GENCO | Isolations for Unit 3 | GENCO |  |  | Circuits | 3rd Party | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025900239171.9152777778 | 10259002 |  | Parent | FALSE | HOTS 220KV LINE AT RCTS | 39171.9153 | 39171.9236 | CONT | 00016954 | FAULT | No2 220 kV BUS TRIP | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025900339171.9152777778 | 10259003 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT RCTS | 39171.9153 | 39171.9236 | CONT | 00360383 | FAULT | No2 220 kV BUS TRIP | SPIPOWER |  |  | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025899639172.2215277778 | 10258996 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39172.2215 | 39174.3527 | CONT | 00356084 | GENCO | Isolations on unit 6 | GENCO |  |  | Circuits | 3rd Party | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025718139172.2444444444 | 10257181 | X32058E9 | Child | FALSE | EX - NO.2 220/66KV TRANS BANK AT MTS | 39172.2444 | 39172.7819 | DAILY | 00026899 | SPICAPX | No2 Bus & B2 Tran Isolated to stand up new rack | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058E939172.2444444444 | X32058E9 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MTS | 39172.2444 | 39172.7819 | DAILY | 00004564 | SPICAPX | commision New B3 Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758C739172.2784722222 | X49758C7 |  | Parent | FALSE | BETS-KGTS 220KV NB | 39172.2785 | 39174.95 | CONT | 00026196 | SPICAPX | Out W/O Commission new KGTS No 1 BUS CB | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z56958B139173.3173611111 | Z56958B1 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 39173.3174 | 39173.5257 | DAILY | 00022702 | 3RDPARTY | gts no.1 & 3 lines on eap - dismantle old tower 29 | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058F339174.2534722222 | X32058F3 |  | Parent | FALSE | U1 66/22KV TRANS AT MTS | 39174.2535 | 39202.7361 | CONT | 00363343 | SPICAPX | Post commissioning check on U 1 66KV CB & 22KV BUS | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158R039174.2666666667 | Z53158R0 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39174.2667 | 39176.6458 | CONT | 00004776 | VEN_AUG | Bus outage to connect bus bi pods & HWPS 2 Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158R139174.2666666667 | Z53158R1 | Z53158R0 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39174.2667 | 39176.6458 | CONT | 00354024 | VEN_AUG | Rebate Bus outage to remove bus bi pods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_Z51358A239174.3138888889 | Z51358A2 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 39174.3139 | 39174.5667 | DAILY | 00007456 | SPICAPX | Proximty reasons No1 66/22kv trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49658D539174.3180555556 | X49658D5 |  | Parent | FALSE | NO.1 66KV BUS AT HOTS | 39174.3181 | 39174.7354 | DAILY | 00006940 | SPICAPX | Out W/O Commish No 1 66 BUS VT's | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026400539174.6048611111 | 10264005 |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT MTS | 39174.6049 | 39331.5792 | CONT | [12 empty] | 0
_1025901539174.9451388889 | 10259015 |  | Parent | FALSE | NO.2 66KV REACTOR AT HOTS | 39174.9451 | 39174.9583 | CONT | 00357255 | FAULT | HOTS No2 Reactor Tripped on Closing | ALSTOM |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758D039175.2666666667 | X49758D0 |  | Parent | FALSE | NO.2 220KV BUS AT BETS | 39175.2667 | 39175.7326 | DAILY | 00016335 | SPICAPX | Out W/O De-commish Bus side isols on No 2 BUS | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025081339175.2805555556 | 10250813 |  | Parent | FALSE | EX - BLTS 220KV LINE AT KTS | 39175.2806 | 39176.6271 | CONT | 00015980 | SPIMAINT | INSPECTION OF LINE (BLTS 220KV) AT KTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025891439175.3145833333 | 10258914 |  | Parent | FALSE | S000 YPS -YWPS A 220KV | 39175.3146 | 39175.6354 | DAILY | [12 empty] | 0
_1025993139175.3145833333 | 10259931 |  | Parent | FALSE | YPS -YWPS A 220KV G | 39175.3146 | 39175.6354 | DAILY | 00020496 | SPIMAINT | change flat insulators | SPIPOWER |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024826339175.3152777778 | 10248263 |  | Parent | FALSE | W1 GEN TRANS 220KV LINE E/SW AT YPS | 39175.3153 | 39177.6243 | CONT | [12 empty] | 0
_Z51358A139175.3208333333 | Z51358A1 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 39175.3208 | 39175.7604 | DAILY | 00007456 | SPICAPX | Proximty reasons No1 66/22kv trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025902239175.375 | 10259022 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 39175.375 | 39178.3875 | CONT | 00016424 | GENCO | W2 Isolations | GENCO |  |  | Circuits | 3rd Party | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058F639176.2583333333 | X32058F6 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MTS | 39176.2583 | 39176.5062 | DAILY | 00004564 | SPICAPX | remove 220kv droppers to b3 trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058F739176.2583333333 | X32058F7 | X32058F6 | Child | FALSE | B3 220/66KV TRANS AT MTS | 39176.2583 | 39176.5062 | DAILY | 00363305 | SPICAPX | No2 Bus & B2 Tran Isolated to stand up new rack | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025904939176.3173611111 | 10259049 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.4 MAIN TRANS CB AT HWTS | 39176.3174 | 39176.5417 | DAILY | [12 empty] | 0
_X38458N839176.3666666667 | X38458N8 |  | Parent | TRUE | EX - NO.1 66KV BUS AT TGTS | 39176.3667 | 39176.7569 | DAILY | 00003132 | SPICAPX | Out W/O Commish KRT No 1 Fdr CB into Bay F | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458N939176.3666666667 | X38458N9 | X38458N8 | Child | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39176.3667 | 39176.7569 | DAILY | 00023231 | SPICAPX | Out W/O Perf calc for 66kV bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458O039176.4333333333 | X38458O0 |  | Parent | FALSE | MLTS 220KV LINE NO.2 BUS CB AT TGTS | 39176.4333 | 39176.6861 | DAILY | [12 empty] | 0
_1025908739176.4847222222 | 10259087 |  | Parent | TRUE | HWPS NO.1 220KV LINE CB AT YPS | 39176.4847 | 39176.5194 | CONT | [12 empty] | 0
_1025913439176.4847222222 | 10259134 | 10259087 | Child | FALSE | HWPS NO.1 220KV LINE AT YPS | 39176.4847 | 39176.5194 | CONT | 00016409 | FORCED | RebateCT wiring problem on HWPS 1 Line CB at YPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058F839176.50625 | X32058F8 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39176.5062 | 39202.6146 | CONT | 00363305 | SPICAPX | B3 TRANS Mod neutral | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158U539176.6402777778 | Z53158U5 |  | Parent | FALSE | HWPS NO.2 220KV LINE NO.1 BUS CB AT ROTS | 39176.6403 | 39183.2861 | CONT | [12 empty] | 0
_1025912639176.7006944444 | 10259126 |  | Parent | FALSE | NO.2A TRANS AT RCTS | 39176.7007 | 39183.6667 | CONT | 00016759 | SPIMAINT | RCTS: No 2 Trans de-energised | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V5B858A039177.3118055556 | V5B858A0 |  | Parent | FALSE | BTS -RTS 220KV E (RTS to Joint Bay 7) (CABLE) | 39177.3118 | 39213.3264 | CONT | 00119369 | SPIMAINT | CIVIL WORKS - LINES bts/rts 220kv cable | SPIPOWER | V5B8 | V5B8 - (BTS-RTS) REPLACE CABLE JOINTS AT JOINT BAY 9 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025915139177.8923611111 | 10259151 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 39177.8924 | 39180.3789 | CONT | [12 empty] | 0
_1025908639178.1076388889 | 10259086 |  | Parent | FALSE | LYBPS NO.2 500KV LINE AT LYPS | 39178.1076 | 39180.9069 | CONT | 00023076 | GENCO | Isol & earth SCAP for LYPS B2 | GENCO |  |  | Circuits | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1024558739179.29375 | 10245587 |  | Parent | FALSE | B2 GEN TRANS NO.3 BUS 500KV CB LINE SIDE ROI AT LYPS | 39179.2937 | 39179.5778 | DAILY | [12 empty] | 0
_Z51058A339182.2895833333 | Z51058A3 |  | Parent | FALSE | B3 TRANS 220KV BUS AT ATS | 39182.2896 | 39182.6618 | DAILY | 00360125 | SPICAPX | outage to allow access for excavator | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024943939182.2951388889 | 10249439 |  | Parent | FALSE | 3-5 220KV BUS TIE CB AT BLTS | 39182.2951 | 39182.641 | CONT | [12 empty] | 0
_1024839939182.3097222222 | 10248399 |  | Parent | FALSE | YPS NO.2 220KV LINE NO.4 BUS CB AT HWPS | 39182.3097 | 39185.2917 | CONT | [12 empty] | 0
_1025914439182.3215277778 | 10259144 |  | Parent | FALSE | YPS NO.1 220KV LINE AT HWPS | 39182.3215 | 39182.5806 | DAILY | 00015795 | SPIMAINT | top oil level of YPS No1 Line No6 Bus CB | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158N439183.2708333333 | Z53158N4 |  | Parent | FALSE | HWPS NO.2 220KV LINE AT ROTS | 39183.2708 | 39184.7382 | CONT | 00024004 | VEN_AUG | Line outage to Reconnect CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010191239183.2888888889 | 10101912 |  | Parent | FALSE | SCI 66KV FDR CB AT BLTS | 39183.2889 | 39184.6514 | DAILY | [12 empty] | 0
_Z51058A439183.2916666667 | Z51058A4 |  | Parent | FALSE | B2 TRANS 220KV BUS AT ATS | 39183.2917 | 39183.6556 | DAILY | 00360124 | SPICAPX | outage to allow access for excavator | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758D239183.3340277778 | X49758D2 |  | Parent | FALSE | BETS-FVTS-SHTS 220KV NB | 39183.334 | 39183.4903 | DAILY | 00026225 | SPICAPX | Out W/O Decommish No 2 bus cb line side isol | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258M239183.4486111111 | X43258M2 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39183.4486 | 39185.7417 | DAILY | 00337584 | SPICAPX | Out W/O 2B Tr 66kV CB install/commiss. Inc#3React | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025892039183.8916666667 | 10258920 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 39183.8917 | 39184.2632 | DAILY | 00022702 | 3RDPARTY | transfer conductor to new tower 29 | SPIPOWER |  | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009273339184.2736111111 | 10092733 |  | Parent | FALSE | ATS 220KV LINE AT BLTS | 39184.2736 | 39185.5125 | CONT | 00024010 | SPIMAINT | INSPECT LINE (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025955139184.3416666667 | 10259551 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS AT JLGB | 39184.3417 | 39185.6208 | CONT | 00009830 | GENCO | SCAP JLGS B1 Isols & Earths | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1025974539184.4659722222 | 10259745 |  | Parent | FALSE | EX - BATS 220KV LINE NO.1 BUS CB AT BETS | 39184.466 | 39185.5375 | DAILY | 00015866 | SPIMAINT | BATS LINE NO 1 BUS CB DC EARTH FAULT | SPIPOWER |  |  | CB | Alstom | 220 |  |  |  | 0
_1025986439184.5826388889 | 10259864 |  | Parent | FALSE | WMTS NO.2 220KV LINE AT FBTS | 39184.5826 | 39184.5924 | DAILY | 00017157 | FORCED | Rebate work order for Top up of CB low SF6 | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_Z56958B539184.85625 | Z56958B5 |  | Parent | FALSE | KTS -GTS 3 220KV WY | 39184.8562 | 39185.2792 | DAILY | 00022709 | 3RDPARTY | transfer conductor to new tower 29 | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258O739185.2673611111 | X43258O7 | X43258O4 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39185.2674 | 39185.5333 | DAILY | 00337581 | SPICAPX | Perf calc W/O #1TR during No2 220 Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258O439185.2673611111 | X43258O4 |  | Parent | TRUE | NO.2 220KV BUS-CAPBK EXTENSION AT RCTS | 39185.2674 | 39185.5514 | DAILY | 00016916 | SPICAPX | Out W/O No2 220kV Bus to disconnect OOS TR ROI | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258O539185.2673611111 | X43258O5 | X43258O4 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RCTS | 39185.2674 | 39185.5514 | DAILY | 00360383 | SPICAPX | Rebate W/O No2 220kV Cap bk during 220 Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258O639185.2673611111 | X43258O6 | X43258O4 | Child | FALSE | HOTS 220KV LINE AT RCTS | 39185.2674 | 39185.5514 | DAILY | 00016954 | SPICAPX | Rebate W/O HOTS Line during No2 220 Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158N839185.2694444444 | Z53158N8 |  | Parent | FALSE | ERTS NO.1 220KV LINE AT ROTS | 39185.2694 | 39185.4903 | DAILY | 00350666 | VEN_AUG | Disconnect ERTS1L/HWPS 2L CB and change droppers | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025913139185.3118055556 | 10259131 | X49658D7 | Child | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39185.3118 | 39185.7083 | DAILY | 00019243 | SPICAPX | Rebate W/O SVC during No1 220 Bus outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X49658D739185.3118055556 | X49658D7 |  | Parent | TRUE | NO.1 220KV BUS AT HOTS | 39185.3118 | 39185.7083 | DAILY | 00006938 | SPICAPX | Out W/O No1 220kV Bus to connect Fut B2TR ROI | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1010268239185.31875 | 10102682 |  | Parent | TRUE | YPS NO.2 220KV LINE AT HWPS | 39185.3187 | 39185.5201 | DAILY | 00015796 | SPIMAINT | O/Haul - YPS No.2 LINE at HWPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010280239185.31875 | 10102802 | 10102682 | Child | FALSE | YPS NO.2 220KV LINE E/SW (NO.6 BUS) AT HWPS | 39185.3187 | 39185.5201 | DAILY | [12 empty] | 0
_1010281239185.31875 | 10102812 | 10102682 | Child | FALSE | YPS NO.2 220KV LINE NO.6 BUS CB LINE SIDE E/SW AT HWPS | 39185.3187 | 39185.5201 | DAILY | [12 empty] | 0
_1010282339185.31875 | 10102823 | 10102682 | Child | FALSE | YPS NO.2 220KV LINE NO.6 BUS CB LINE SIDE ISOL AT HWPS | 39185.3187 | 39185.5201 | DAILY | [12 empty] | 0
_X49658D939185.5333333333 | X49658D9 | X49658D7 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39185.5333 | 39185.7083 | DAILY | 00337581 | SPICAPX | Perf calc W/O #1 Trans during No1 220 Bus outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49658E039185.7194444445 | X49658E0 |  | Parent | FALSE | B2 220/66KV TRANS AT HOTS | 39185.7194 | 39267.3542 | CONT | 00363103 | SPICAPX | Out W/O Fut B2 Trans make connections to its CB's | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025984739185.9861111111 | 10259847 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 39185.9861 | 39187.2361 | CONT | 00356079 | GENCO | SCAP On HWPS No1 Gen Trans Isols | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158T639186.275 | Z53158T6 |  | Parent | TRUE | EX - NO.4 220KV BUS AT ERTS | 39186.275 | 39187.6097 | CONT | 00004380 | VEN_AUG | No 4 220kv BUS,No4 TRANS,CBTS No1,ROTS No2 LINE | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158T739186.275 | Z53158T7 | Z53158T6 | Child | FALSE | B4 220/66KV TRANS AT ERTS | 39186.275 | 39187.6097 | CONT | 00004372 | VEN_AUG | No4 TRANS AT ERTS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158T839186.275 | Z53158T8 | Z53158T6 | Child | FALSE | ROTS NO.2 220KV LINE AT ERTS | 39186.275 | 39187.6097 | CONT | 00012288 | VEN_AUG | ROTS No2 LINE | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158T939186.275 | Z53158T9 | Z53158T6 | Child | FALSE | CBTS NO.1 220KV LINE AT ERTS | 39186.275 | 39187.6097 | CONT | 00012286 | VEN_AUG | CBTS No1 LINE | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858B939186.3055555556 | X49858B9 |  | Parent | FALSE | WKPS 220KV LINE AT MBTS | 39186.3056 | 39192.7188 | CONT | 00011756 | SPICAPX | Out W/O WKPS Line to cutover to new CB on No1 bus | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458P039186.3125 | X38458P0 |  | Parent | FALSE | EX - NO.1 TRANS GROUP AT TGTS (O.O.S) | 39186.3125 | 39187.6965 | DAILY | 00023231 | SPICAPX | Out W/O Commission Future B 1 TRANS 66kV CB. | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025985039186.4916666667 | 10259850 |  | Parent | FALSE | JLA NO.1 220KV LINE AT TBTS | 39186.4917 | 39186.5028 | CONT | 00018301 | FORCED | Top up SF6 of JLA NO.1 220KV LINE CB AT TBTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025985639187.2597222222 | 10259856 |  | Parent | FALSE | W2 GEN TRANS 220KV CB BUS SIDE ISOL AT YPS | 39187.2597 | 39189.2778 | CONT | [12 empty] | 0
_X23358C739187.2965277778 | X23358C7 |  | Parent | FALSE | B1 220/66KV TRANS AT WMTS | 39187.2965 | 39187.5979 | DAILY | 00003233 | SPICAPX | commission new wti, insert new probe & remove old | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z56958B639187.4048611111 | Z56958B6 |  | Parent | FALSE | KTS -GTS 3 220KV WY | 39187.4049 | 39187.5715 | DAILY | 00022709 | 3RDPARTY | dismantle part of old tower 29 - 1 & 3 line outage | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49658E439188.2972222222 | X49658E4 |  | Parent | TRUE | NO.2 220KV BUS AT HOTS | 39188.2972 | 39188.6931 | DAILY | 00006939 | SPICAPX | Out W/O No2 220kV BUS disconnect RCTS tie | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49658E539188.2972222222 | X49658E5 | X49658E4 | Child | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39188.2972 | 39188.6931 | DAILY | 00019243 | SPICAPX | Rebate W/O SVC outage for proximity | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X49658E639188.2972222222 | X49658E6 | X49658E4 | Child | FALSE | B3 220/66KV TRANS AT HOTS | 39188.2972 | 39188.6931 | DAILY | 00363102 | SPICAPX | Perf calc W/O B3 Trans during #2 220 bus outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458P239188.3208333333 | X38458P2 |  | Parent | FALSE | EX - NO.1 220KV BUS AT TGTS | 39188.3208 | 39188.775 | DAILY | 00003130 | SPICAPX | Out W/O Includes MLTS -TGTS line | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258O839189.3013888889 | X43258O8 |  | Parent | TRUE | NO.2 220KV BUS-CAPBK EXTENSION AT RCTS | 39189.3014 | 39189.75 | DAILY | 00016916 | SPICAPX | Primary connections toBSS LineTie No2 bus equip | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258Z039189.3013888889 | X43258Z0 | X43258O8 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RCTS | 39189.3014 | 39189.75 | DAILY | 00360383 | SPICAPX | Primary connections toBSS LineTie No2 bus equip | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024841839189.3125 | 10248418 |  | Parent | FALSE | HWTS NO.4 220KV LINE NO.4 BUS CB AT HWPS | 39189.3125 | 39192.5528 | CONT | [12 empty] | 0
_1024958939189.3145833333 | 10249589 |  | Parent | FALSE | NO.1 500KV BUS E/SW AT KTS | 39189.3146 | 39191.65 | CONT | [12 empty] | 0
_X49658E739189.3430555556 | X49658E7 |  | Parent | FALSE | RCTS 220KV LINE AT HOTS | 39189.3431 | 39189.75 | DAILY | 00018715 | SPICAPX | Out W/O RCTS Line to decommiss RCTS tie | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X47758B239189.3555555556 | X47758B2 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 39189.3556 | 39189.7562 | REPDAILY | 00026099 | SPICAPX | install rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025982739189.4069444445 | 10259827 |  | Parent | FALSE | W1 GTG/HWPS NO.2 LINE 220KV CB AT YPS | 39189.4069 | 39189.6431 | DAILY | [12 empty] | 0
_Z56958B739189.8756944445 | Z56958B7 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 39189.8757 | 39190.2646 | DAILY | 00022702 | 3RDPARTY | transfer conductors to new tower 29 | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158U639190.2625 | Z53158U6 |  | Parent | TRUE | NO.3 220KV BUS AT ROTS | 39190.2625 | 39190.6799 | DAILY | 00329013 | VEN_AUG | Bus outage to erect new MTS No1 LINE No3 BUS ROI | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158U739190.2625 | Z53158U7 | Z53158U6 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39190.2625 | 39190.6799 | DAILY | 00112417 | VEN_AUG | REBATE OUTAGE No3 CAP BANK | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X47758B239190.2847222222 | X47758B2 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 39190.2847 | 39190.7597 | REPDAILY | 00026099 | SPICAPX | install rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X54758A139190.3006944444 | X54758A1 |  | Parent | FALSE | HWTS NO.4 L/ROTS NO.4 L 500KV CB AT CBTS | 39190.3007 | 39190.6 | DAILY | [12 empty] | 0
_1025982939190.3229166667 | 10259829 |  | Parent | FALSE | W1 GEN TRANS NO.1 BUS 220KV CB AT YPS | 39190.3229 | 39190.6326 | DAILY | [12 empty] | 0
_X43258P839190.3534722222 | X43258P8 |  | Parent | FALSE | NO.3 66KV REACTOR AT RCTS | 39190.3535 | 39192.775 | CONT | 00357254 | SPICAPX | Out W/O No3 66kv Reactor upgrade | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z56958B839190.8576388889 | Z56958B8 |  | Parent | FALSE | KTS -GTS 3 220KV WY | 39190.8576 | 39191.2722 | DAILY | 00022709 | 3RDPARTY | transfer conductors to new tower 29 | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X47758B239191.2493055556 | X47758B2 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 39191.2493 | 39191.7396 | REPDAILY | 00026099 | SPICAPX | install rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X54758A239191.2909722222 | X54758A2 |  | Parent | FALSE | A1 TRANS/HWTS NO.4 LINE 500KV CB AT CBTS | 39191.291 | 39191.6542 | DAILY | [12 empty] | 0
_X49058F139191.29375 | X49058F1 |  | Parent | TRUE | NO.1 330KV BUS AT DDTS | 39191.2937 | 39191.7312 | DAILY | 00003978 | SPICAPX | Install new CVT's on No1 330kv Bus | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X49058F239191.29375 | X49058F2 | X49058F1 | Child | FALSE | NO.1 330KV CAPACITOR BANK AT DDTS | 39191.2937 | 39191.7312 | DAILY | 00352085 | SPICAPX | rebate w/o for No1 cap bank | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_1025983539191.3194444444 | 10259835 |  | Parent | FALSE | W1 GEN TRANS NO.2 BUS 220KV CB AT YPS | 39191.3194 | 39191.6257 | DAILY | [12 empty] | 0
_1025988639191.35 | 10259886 |  | Parent | FALSE | LY NO.4 66KV FDR NO.3 BUS CB AT MWTS | 39191.35 | 39206.466 | DAILY | [12 empty] | 0
_1025994039191.7097222222 | 10259940 |  | Parent | FALSE | B1 220/66KV TRANS AT TGTS | 39191.7097 | 39191.7153 | CONT | 00363297 | FORCED | New B1 Trans de-energised to short out WTI CT | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X47758B239192.25 | X47758B2 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 39192.25 | 39192.7549 | REPDAILY | 00026099 | SPICAPX | install rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025822339192.2548611111 | 10258223 | X49858C0 | Child | FALSE | EX - DDTS NO.2 220KV LINE AT MBTS | 39192.2549 | 39192.7188 | DAILY | 00011750 | SPICAPX | Rebate W/O DDTS 2 Line during No1 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025822439192.2548611111 | 10258224 | X49858C0 | Child | FALSE | EX - EPS NO.2 220KV LINE AT MBTS | 39192.2549 | 39192.7188 | DAILY | 00011752 | SPICAPX | Rebate W/O EPS 2 Line during No1 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49858C039192.2548611111 | X49858C0 |  | Parent | TRUE | EX - NO.1 220KV BUS AT MBTS | 39192.2549 | 39192.7188 | DAILY | 00004001 | SPICAPX | Out W/O No1 220 bus to cutover to new WKPS CB | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53458B839192.2861111111 | Z53458B8 |  | Parent | FALSE | NO.2 500KV BUS AT ROTS | 39192.2861 | 39192.6743 | DAILY | 00362955 | VEN_AUG | EAP No 2 500 Bus Check operation of E/SW's & ROIS | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_X49058F339192.2972222222 | X49058F3 |  | Parent | TRUE | NO.2 330KV BUS AT DDTS | 39192.2972 | 39192.6125 | DAILY | 00003979 | SPICAPX | Install new CVT's on No2 330kv Bus | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X49058F439192.2972222222 | X49058F4 | X49058F3 | Child | FALSE | NO.2 330KV CAPACITOR BANK AT DDTS | 39192.2972 | 39192.6125 | DAILY | 00352093 | SPICAPX | rebate w/o for No2 330kv cap bank | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_X49058F539192.2972222222 | X49058F5 | X49058F3 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 39192.2972 | 39192.6125 | DAILY | 00352121 | SPICAPX | rebate w/o for No2 330/220kv Transformer | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024959139192.3138888889 | 10249591 | 10250493 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT KTS | 39192.3139 | 39192.6139 | DAILY | 00327947 | SPIMAINT | O/Haul - 'A' Cap Bank & E/Sw & 'B' Bank Isol (W) | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025049339192.3138888889 | 10250493 |  | Parent | TRUE | EX - NO.1B 66KV CAPACITOR BANK CB AT KTS | 39192.3139 | 39192.6139 | DAILY | [12 empty] | 0
_1025991239192.31875 | 10259912 |  | Parent | FALSE | AUX TRANS 'A' 220KV CB AT YPS | 39192.3187 | 39192.5681 | DAILY | [12 empty] | 0
_1025992339192.3576388889 | 10259923 |  | Parent | FALSE | HOTS-RCTS 220KV | 39192.3576 | 39192.7264 | REPDAILY | 00328509 | SPIMAINT | Replace Faulty insuators on HOTS - RCTS Line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025996339193.1111111111 | 10259963 |  | Parent | FALSE | NO.8 GEN 220/16.5KV TRANS AT HWPS | 39193.1111 | 39195.5674 | CONT | 00009649 | GENCO | Power Station Requirements | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_Z53158U039193.2708333333 | Z53158U0 |  | Parent | TRUE | EX - NO.4 220KV BUS AT ERTS | 39193.2708 | 39194.6646 | CONT | 00004380 | VEN_AUG | No 4 220kv BUS,No4 TRANS,CBTS No1,ROTS No2 LINE | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158U139193.2708333333 | Z53158U1 | Z53158U0 | Child | FALSE | B4 220/66KV TRANS AT ERTS | 39193.2708 | 39194.6646 | CONT | 00004372 | VEN_AUG | No4 TRANS AT ERTS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158U239193.2708333333 | Z53158U2 | Z53158U0 | Child | FALSE | ROTS NO.2 220KV LINE AT ERTS | 39193.2708 | 39194.6646 | CONT | 00012288 | VEN_AUG | ROTS No2 LINE | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158U339193.2708333333 | Z53158U3 | Z53158U0 | Child | FALSE | CBTS NO.1 220KV LINE AT ERTS | 39193.2708 | 39194.6646 | CONT | 00012286 | VEN_AUG | CBTS No1 LINE | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z56958C039193.3125 | Z56958C0 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 39193.3125 | 39193.6167 | DAILY | 00015976 | 3RDPARTY | dismantle old tower 29 | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61858A039194.2701388889 | Z61858A0 |  | Parent | FALSE | NO.1 22KV BUS AT RWTS | 39194.2701 | 39194.6451 | DAILY | 00007482 | DB_AUG | INSTALLATION AND CONSTRUCTION | SPIPOWER | Z618 | Z618 - (RWTS) NEW 22KV FDR RWT13 FOR EASTLINK TNL | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_Z56958B939194.3125 | Z56958B9 |  | Parent | FALSE | KTS -GTS 3 220KV WY | 39194.3125 | 39194.5396 | DAILY | 00022709 | 3RDPARTY | dismantle remaining old tower 29 - 1 & 3 lines | SPIPOWER | Z569 | Z569 - (GTS-KTS) DEER PARK PROJECT INCREASE LINE CLEARANCE | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025996839194.5520833333 | 10259968 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39194.5521 | 39196.4243 | CONT | 00019243 | FAULT | Forced outage after Cap fault | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025824039195.2569444444 | 10258240 | X49858C1 | Child | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39195.2569 | 39199.741 | CONT | 00011755 | SPICAPX | Out W/O DPS & MKPS lines. Remove diversion bridges | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858C139195.2569444444 | X49858C1 |  | Parent | TRUE | DPS 220KV LINE AT MBTS | 39195.2569 | 39199.741 | CONT | 00011754 | SPICAPX | Out W/O DPS & MKPS lines. Remove diversion bridges | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024953439195.2791666667 | 10249534 |  | Parent | FALSE | B2 220/66KV TRANS AT KTS | 39195.2792 | 39195.6597 | REPDAILY | 00001148 | SPIMAINT | O/HAUL Transformer Div Mechanism (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158R939195.2797685185 | Z53158R9 |  | Parent | FALSE | YPS NO.5 220KV LINE AT ROTS | 39195.2798 | 39196.5569 | CONT | 00024008 | VEN_AUG | Rebate to remove line traps | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X47758B339195.3097222222 | X47758B3 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39195.3097 | 39196.6708 | CONT | 00012436 | SPICAPX | prep work for rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024841439195.3145833333 | 10248414 |  | Parent | FALSE | HWTS NO.4 220KV LINE NO.3 BUS CB AT HWPS | 39195.3146 | 39199.4681 | CONT | [12 empty] | 0
_1025903639195.3173611111 | 10259036 | X46158N0 | Child | FALSE | TGTS 220KV LINE AT BATS | 39195.3174 | 39195.7174 | DAILY | 00012435 | SPICAPX | Rebate W/O TGTS Line during No1 220kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025903739195.3173611111 | 10259037 | X46158N0 | Child | FALSE | B2 220/66KV TRANS AT BATS | 39195.3174 | 39195.7174 | DAILY | 00006555 | SPICAPX | Perf calc W/O #2 Trans during No1 220kV Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158N039195.3173611111 | X46158N0 |  | Parent | TRUE | NO.1 220KV BUS AT BATS | 39195.3174 | 39195.7174 | DAILY | 00006558 | SPICAPX | Out W/O No1 220kV bus for prot upgrade | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49858B839195.4479166667 | X49858B8 |  | Parent | FALSE | B2 220/66KV TRANS AT MBTS | 39195.4479 | 39206.3125 | CONT | 00362372 | SPICAPX | Out W/O Commiss B1 TR 21/03-B2 TR out until -04/05 | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024953439196.2694444444 | 10249534 |  | Parent | FALSE | B2 220/66KV TRANS AT KTS | 39196.2694 | 39196.6417 | REPDAILY | 00001148 | SPIMAINT | O/HAUL Transformer Div Mechanism (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V62258A539196.2944444444 | V62258A5 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.2 BUS CB AT SMTS | 39196.2944 | 39199.6306 | CONT | [12 empty] | 0
_1026004639196.6215277778 | 10260046 |  | Parent | FALSE | NO.8 GEN 220/16.5KV TRANS AT HWPS | 39196.6215 | 39200.0326 | CONT | 00009649 | GENCO | SCAP: Isol'd for Power Station | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_Z53458B939198.2798611111 | Z53458B9 |  | Parent | FALSE | NO.2 500KV BUS AT ROTS | 39198.2799 | 39199.7042 | CONT | 00362955 | VEN_AUG | Extend Bus to Bay 4 First Energisation end of Pirm | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_X2A858T839198.2847222222 | X2A858T8 |  | Parent | FALSE | L2 220/22KV TRANS AT BTS | 39198.2847 | 39198.4611 | DAILY | 00360870 | SPICAPX | access to roof of trans enclosure for measurements | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024957439198.2923611111 | 10249574 |  | Parent | FALSE | EX - A2 TRANS NO.2 BUS 220KV CB AT KTS | 39198.2924 | 39199.6132 | CONT | [12 empty] | 0
_X43258O939198.2923611111 | X43258O9 |  | Parent | FALSE | BSS 220KV LINE AT RCTS | 39198.2924 | 39199.7549 | CONT | 00016966 | SPICAPX | change over BSS line CVT and connections | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026000539198.3916666667 | 10260005 |  | Parent | FALSE | HPS 66KV LINE AT WOTS | 39198.3917 | 39198.6368 | CONT | 00012055 | DBPROX | VSCAP to Distribution | DISTCO |  |  | Circuits | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X54758A039198.4881944444 | X54758A0 |  | Parent | FALSE | ROTS NO.4 500KV LINE NO.1 BUS CB AT CBTS | 39198.4882 | 39198.6035 | DAILY | [12 empty] | 0
_X47758B339198.5618055556 | X47758B3 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39198.5618 | 39200.6701 | CONT | 00012436 | SPICAPX | prep work for rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024872839199.2666666667 | 10248728 |  | Parent | FALSE | NO.1 CSC AT ROTS | 39199.2667 | 39199.4875 | DAILY | 00004718 | SPIMAINT | Yearly O/Haul - No.1 CSC at ROTS | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026011339199.7291666667 | 10260113 |  | Parent | FALSE | HWTS NO.3 500KV LINE NO.2 BUS CB AT ROTS (RTF) | 39199.7292 | 39202.5437 | CONT | [12 empty] | 0
_X49858C239199.7409722222 | X49858C2 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39199.741 | 39206.3125 | CONT | 00011755 | SPICAPX | Out W/O MKPS Line cutover to new 1Bus CB | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026011439200.0243055556 | 10260114 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39200.0243 | 39269.2535 | CONT | 00356082 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X47758B439200.2534722222 | X47758B4 |  | Parent | FALSE | SYTS NO.1 500KV LINE AT SMTS | 39200.2535 | 39200.684 | DAILY | 00012439 | SPICAPX | install rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058G239202.2715277778 | X32058G2 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39202.2715 | 39202.4847 | DAILY | 00004569 | SPICAPX | Remove 1-3 66kv Bus Tie CB from service | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058G339202.2715277778 | X32058G3 | X32058G2 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39202.2715 | 39202.4847 | DAILY | 00026900 | SPICAPX | Avail of plant for No 3 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258N839202.2833333333 | X43258N8 |  | Parent | FALSE | NO.2 66KV REACTOR AT RCTS | 39202.2833 | 39212.4694 | CONT | 00016897 | SPICAPX | Out W/O No2 66kV React to replace its CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025985339202.3041666667 | 10259853 | X41258D9 | Child | FALSE | GNTS-SHTS 3 220KV NW | 39202.3042 | 39202.6132 | DAILY | 00055389 | SPICAPX | Rebate W/O GNTS 3 L during No2 220kVBus Outage | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025985439202.3041666667 | 10259854 | X41258D9 | Child | FALSE | B3 220/66KV TRANS AT SHTS | 39202.3042 | 39202.6132 | DAILY | 00000842 | SPICAPX | Perf Calc W/O No3 TR during No2 220kv Bus outage | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025985539202.3041666667 | 10259855 | X41258D9 | Child | FALSE | DDTS-SHTS 220KV NW | 39202.3042 | 39202.6132 | DAILY | 00352425 | SPICAPX | Rebate W/O DDTS L during No2 220kv Bus outage | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X41258D939202.3041666667 | X41258D9 |  | Parent | TRUE | EX - NO.2 220KV BUS AT SHTS | 39202.3042 | 39202.6132 | DAILY | 00000846 | SPICAPX | Out W/O No2 220 Bus to adjust DDTS L 2B CB BS E/SW | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026012739202.4847222222 | 10260127 |  | Parent | FALSE | EX - 1-3 66KV BUS TIE CB AT MTS | 39202.4847 | 39288.4308 | CONT | [12 empty] | 0
_X32058G439202.4958333333 | X32058G4 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MTS | 39202.4958 | 39202.7292 | DAILY | 00004564 | SPICAPX | ReConnect B3 Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058G739202.4958333333 | X32058G7 | X32058G4 | Child | FALSE | EX - NO.1 220/66KV TRANS BANK AT MTS | 39202.4958 | 39202.7292 | DAILY | 00026898 | SPICAPX | trans avaiblity | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158S039203.2680555556 | Z53158S0 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39203.2681 | 39204.6979 | CONT | 00004776 | VEN_AUG | Bus in Bay R & Install RTS No1 Line Bus CB B/S ROI | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158S139203.2680555556 | Z53158S1 | Z53158S0 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39203.2681 | 39204.6979 | CONT | 00354024 | VEN_AUG | Rebate Construction work on bus | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024876539203.2930555556 | 10248765 |  | Parent | FALSE | B1 220/66KV TRANS AT HTS | 39203.2931 | 39203.6285 | DAILY | 00004445 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158M239203.2930555556 | X46158M2 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 39203.2931 | 39204.6201 | CONT | 00331109 | SPICAPX | Out W/O No1 Cap bank - Rewire Cap bk & CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X32058H639203.3347222222 | X32058H6 |  | Parent | FALSE | CFD 66KV FDR CB AT MTS | 39203.3347 | 39203.7514 | DAILY | [12 empty] | 0
_1024921639203.3423611111 | 10249216 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT MLTS | 39203.3424 | 39203.6368 | DAILY | 00003006 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458P639203.3659722222 | X38458P6 |  | Parent | FALSE | B1 220/66KV TRANS AT TGTS | 39203.366 | 39203.8514 | DAILY | 00363297 | SPICAPX | commission fut N01 s/s trans and connections | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026400439203.3708333333 | 10264004 |  | Parent | FALSE | BW 22KV FDR 68 CB AT MTS | 39203.3708 | 39420.5215 | CONT | [12 empty] | 0
_1026400139203.3708333333 | 10264001 |  | Parent | FALSE | VR CAULFIELD 22KV FDR 38 CB (ALINTA EQPT) AT MTS | 39203.3708 | 39420.5222 | CONT | [12 empty] | 0
_1026400239203.3708333333 | 10264002 |  | Parent | FALSE | SH 22KV FDR 36 CB AT MTS | 39203.3708 | 39422.5646 | CONT | [12 empty] | 0
_1026400339203.3708333333 | 10264003 |  | Parent | FALSE | T 22KV FDR 39 CB AT MTS | 39203.3708 | 39422.5867 | CONT | [12 empty] | 0
_X32058H739203.375 | X32058H7 |  | Parent | FALSE | NO.1 22KV BUS AT MTS | 39203.375 | 39203.6599 | DAILY | 00363340 | SPICAPX | Energise New No1, No2, & No3 22kv Bus in service | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058H839203.6597222222 | X32058H8 |  | Parent | FALSE | NO.1 11KV/415V S/S TRANS AT MTS | 39203.6597 | 39224.9306 | CONT | 00364879 | SPICAPX | No 2 S/S trans hold out permit | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Other Transformers | Eastern | 11 | NON AER ELEMENT | EXCLUDED |  | 0
_X47758B539204.2722222222 | X47758B5 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39204.2722 | 39204.6396 | DAILY | 00012436 | SPICAPX | prep work for rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024636139204.2736111111 | 10246361 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT KTS | 39204.2736 | 39204.6417 | REPDAILY | 00026096 | SPIMAINT | one phase per day / no access to tr connections | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X49758D339204.30625 | X49758D3 |  | Parent | FALSE | KGTS 220KV LINE AT BETS | 39204.3063 | 39204.691 | REPDAILY | 00016433 | SPICAPX | Out W/O KGTS Line to erect Fut 2B CB LS ROI | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024839039204.3131944445 | 10248390 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB AT HWTS | 39204.3132 | 39204.6118 | DAILY | [12 empty] | 0
_X32058H339204.3409722222 | X32058H3 |  | Parent | TRUE | EX - NO.1 66KV BUS AT MTS | 39204.341 | 39204.7354 | DAILY | 00004566 | SPICAPX | relocate OAK fdr & No1 66kv bus | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058H439204.3409722222 | X32058H4 | X32058H3 | Child | FALSE | EX - NO.1 220/66KV TRANS BANK AT MTS | 39204.341 | 39204.7354 | DAILY | 00026898 | SPICAPX | Avail of plant for No 1 66 bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058H539204.3409722222 | X32058H5 | X32058H3 | Child | FALSE | OAK 66KV FDR CB AT MTS | 39204.341 | 39204.7354 | DAILY | [12 empty] | 0
_X49058G139204.3416666667 | X49058G1 |  | Parent | FALSE | MSS NO.2 330KV LINE NO.2 BUS CB AT DDTS | 39204.3417 | 39204.6458 | CONT | [12 empty] | 0
_Z53458C439205.2673611111 | Z53458C4 | Z53458C3 | Child | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39205.2674 | 39212.6764 | CONT | 00354002 | VEN_AUG | trans outage times | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_Z53458C339205.2673611111 | Z53458C3 |  | Parent | TRUE | NO.1 500KV BUS AT ROTS | 39205.2674 | 39212.6765 | CONT | 00362956 | VEN_AUG | Move A1 trans 550kv conn & extend No1 500 bus | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058G539205.2708333333 | X32058G5 |  | Parent | TRUE | EX - NO.1 66KV BUS AT MTS | 39205.2708 | 39205.3674 | DAILY | 00004566 | SPICAPX | Remove part of No1 66kV Bus | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058G639205.2708333333 | X32058G6 | X32058G5 | Child | FALSE | EX - NO.1 220/66KV TRANS BANK AT MTS | 39205.2708 | 39205.3674 | DAILY | 00026898 | SPICAPX | Rebate Tran outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024636139205.2708333333 | 10246361 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT KTS | 39205.2708 | 39205.6333 | REPDAILY | 00026096 | SPIMAINT | one phase per day / no access to tr connections | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024877339205.2916666667 | 10248773 |  | Parent | TRUE | NO.3 220KV BUS AT HTS | 39205.2917 | 39205.6028 | DAILY | 00004453 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026015339205.2916666667 | 10260153 | 10248773 | Child | FALSE | B3 220/66KV TRANS AT HTS | 39205.2917 | 39205.6028 | DAILY | 00004447 | SPIMAINT | TRANS OUTAGE TIME | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49758D339205.3041666667 | X49758D3 |  | Parent | FALSE | KGTS 220KV LINE AT BETS | 39205.3042 | 39205.675 | REPDAILY | 00016433 | SPICAPX | Out W/O KGTS Line to erect Fut 2B CB LS ROI | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009267039205.3131944445 | 10092670 |  | Parent | FALSE | ROTS NO.7 220KV LINE AT YPS | 39205.3132 | 39206.6306 | CONT | 00016415 | SPIMAINT | O/Haul - ROTS No.7 220kV Line at YPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X47758B639205.3208333333 | X47758B6 |  | Parent | FALSE | SYTS NO.1 500KV LINE AT SMTS | 39205.3208 | 39205.6507 | DAILY | 00012439 | SPICAPX | prep work for rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49058G039205.35 | X49058G0 |  | Parent | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB AT DDTS | 39205.35 | 39205.5062 | DAILY | [12 empty] | 0
_X32058G839205.3791666667 | X32058G8 |  | Parent | TRUE | EX - NO.3 66KV BUS AT MTS | 39205.3792 | 39205.6111 | DAILY | 00004569 | SPICAPX | Remove Section of No3 66kV Bus | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058G939205.3791666667 | X32058G9 | X32058G8 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39205.3792 | 39205.6111 | DAILY | 00026900 | SPICAPX | Rebate Tran outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026023739205.60625 | 10260237 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 39205.6062 | 39205.6965 | DAILY | 00007456 | FORCED | Trans OLTC stuck on tap | SPIPOWER |  |  | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025825639206.25 | 10258256 | X49858C3 | Child | FALSE | EX - DDTS NO.2 220KV LINE AT MBTS | 39206.25 | 39206.5625 | DAILY | 00011750 | SPICAPX | Rebate W/O DDTS 2 Line during No1 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025825739206.25 | 10258257 | X49858C3 | Child | FALSE | EX - EPS NO.2 220KV LINE AT MBTS | 39206.25 | 39206.5625 | DAILY | 00011752 | SPICAPX | Rebate W/O EPS 2 Line during No1 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025825839206.25 | 10258258 | X49858C3 | Child | FALSE | WKPS 220KV LINE AT MBTS | 39206.25 | 39206.5625 | DAILY | 00011756 | SPICAPX | Rebate W/O WKPS Line during No1 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025826039206.25 | 10258260 | X49858C3 | Child | FALSE | DPS 220KV LINE AT MBTS | 39206.25 | 39206.5625 | DAILY | 00011754 | SPICAPX | Rebate W/O DPS Line during No1 220 bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858C339206.25 | X49858C3 |  | Parent | TRUE | EX - NO.1 220KV BUS AT MBTS | 39206.25 | 39206.5625 | DAILY | 00004001 | SPICAPX | Out W/O No1 220 bus to cutover new MKPS & B2 CB | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024636139206.2652777778 | 10246361 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT KTS | 39206.2653 | 39206.6653 | REPDAILY | 00026096 | SPIMAINT | one phase per day / no access to tr connections | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X47758B739206.2708333333 | X47758B7 |  | Parent | FALSE | HWTS NO.2 500KV LINE AT SMTS | 39206.2708 | 39207.6958 | CONT | 00012437 | SPICAPX | prep work for rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158M139206.2951388889 | X46158M1 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39206.2951 | 39206.6694 | CONT | 00331118 | SPICAPX | Out W/O No2 Cap bank - Rewire Cap bk & CB | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z50658A839206.3173611111 | Z50658A8 |  | Parent | FALSE | NO.6 66KV BUS AT HTS | 39206.3174 | 39206.6417 | DAILY | 00004460 | DB_AUG | Sub CRM/CBTS fdr & No 6 Bus | SPIPOWER | Z506 | Z506 - (HTS) OPTIMISING 66KV CBS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z61858A339208.2666666667 | Z61858A3 |  | Parent | TRUE | NO.1 22KV BUS AT RWTS | 39208.2667 | 39208.6618 | DAILY | 00007482 | DB_AUG | Install Reactor | SPIPOWER | Z618 | Z618 - (RWTS) NEW 22KV FDR RWT13 FOR EASTLINK TNL | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_Z61858A439208.2666666667 | Z61858A4 | Z61858A3 | Child | FALSE | L2 220/22KV TRANS BANK AT RWTS | 39208.2667 | 39208.6618 | DAILY | 00007447 | DB_AUG | TRANS OUTAGE No2 220/22 | SPIPOWER | Z618 | Z618 - (RWTS) NEW 22KV FDR RWT13 FOR EASTLINK TNL | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z61858A539208.2666666667 | Z61858A5 | Z61858A3 | Child | FALSE | U1 66/22KV TRANS AT RWTS | 39208.2667 | 39208.6618 | DAILY | 00007456 | DB_AUG | TRANS OUTAGE No1 66/22 | SPIPOWER | Z618 | Z618 - (RWTS) NEW 22KV FDR RWT13 FOR EASTLINK TNL | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_X23358C839208.2909722222 | X23358C8 |  | Parent | FALSE | L1 220/22KV TRANS AT WMTS | 39208.291 | 39208.5257 | DAILY | 00003234 | SPICAPX | commission new wti, insert new probe & remove old | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024636439209.2770833333 | 10246364 |  | Parent | FALSE | A3 500/220KV TRANS BANK AT KTS | 39209.2771 | 39209.616 | REPDAILY | 00026097 | SPIMAINT | o/h one phase per day - no access to connections | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X43258P339209.2777777778 | X43258P3 |  | Parent | FALSE | KGTS 220KV LINE AT RCTS | 39209.2778 | 39210.7486 | CONT | 00016959 | SPICAPX | replace cvt's and primary connections | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X47758B939209.2875 | X47758B9 |  | Parent | FALSE | HWTS NO.2 500KV LINE AT SMTS | 39209.2875 | 39213.6549 | CONT | 00012437 | SPICAPX | prep work for rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024584439209.3041666667 | 10245844 | 10248781 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HTS | 39209.3042 | 39210.6347 | CONT | 00331019 | SPIMAINT | O/Haul - Cap Bank & E/Sw (EM) | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024878139209.3041666667 | 10248781 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT HTS | 39209.3042 | 39210.6347 | CONT | 00004426 | SPIMAINT | O/Haul - Cap Bank & E/Sw (EM) | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025167439209.3083333333 | 10251674 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 39209.3083 | 39210.7764 | CONT | 00006554 | SPIMAINT | Condition Monitoring Country Trans 2day North Area | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49858C939210.2486111111 | X49858C9 |  | Parent | FALSE | EX - NO.2 220KV BUS AT MBTS | 39210.2486 | 39210.4812 | DAILY | 00004002 | SPICAPX | Out W/O Decommission No2 220kV bus | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z50658A739210.2666666667 | Z50658A7 |  | Parent | FALSE | NO.6 66KV BUS AT HTS | 39210.2667 | 39210.6472 | DAILY | 00004460 | DB_AUG | Sub HT fdr,Sub NB fdr,Sub CRM/CBTS fdr & No 6 Bus | SPIPOWER | Z506 | Z506 - (HTS) OPTIMISING 66KV CBS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024636439210.2743055556 | 10246364 |  | Parent | FALSE | A3 500/220KV TRANS BANK AT KTS | 39210.2743 | 39210.6438 | REPDAILY | 00026097 | SPIMAINT | o/h one phase per day - no access to connections | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009270739210.3125 | 10092707 |  | Parent | FALSE | A1 515/230KV TRANS AT HWTS | 39210.3125 | 39213.6062 | CONT | 00009772 | SPIMAINT | O/HAUL Transformer without Div Sw | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024970439210.3256944444 | 10249704 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT GNTS | 39210.3257 | 39210.625 | DAILY | [12 empty] | 0
_Z50658B039210.6472222222 | Z50658B0 |  | Parent | FALSE | EX - M/MC 66KV FDR CB AT HTS | 39210.6472 | 39283.4625 | CONT | [12 empty] | 0
_1024636439211.2756944444 | 10246364 |  | Parent | FALSE | A3 500/220KV TRANS BANK AT KTS | 39211.2757 | 39211.6194 | REPDAILY | 00026097 | SPIMAINT | o/h one phase per day - no access to connections | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024877039211.2895833333 | 10248770 |  | Parent | FALSE | B3 220/66KV TRANS AT HTS | 39211.2896 | 39211.6076 | DAILY | 00004447 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024875839211.2895833333 | 10248758 |  | Parent | FALSE | 1-6 66KV BUS TIE CB AT HTS | 39211.2896 | 39211.6174 | DAILY | [12 empty] | 0
_1025163639211.29375 | 10251636 |  | Parent | FALSE | B2 220/66KV TRANS AT BATS | 39211.2937 | 39212.7562 | CONT | 00006555 | SPIMAINT | Condition Monitoring Country Trans 2day North Area | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024977739211.3145833333 | 10249777 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT GNTS | 39211.3146 | 39211.7063 | DAILY | 00329962 | SPIMAINT | O/Haul - Cap Bank & E/Sw (N) | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026048639211.3229166667 | 10260486 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 39211.3229 | 39211.7468 | CONT | 00016423 | GENCO | YWPS No1 GTG 220kV line Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026022239211.3590277778 | 10260222 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39211.359 | 39211.5326 | DAILY | 00319998 | APDALCOA | Scap to APD for work at APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_V62258A839211.4826388889 | V62258A8 |  | Parent | FALSE | FUTURE F1 TRANS 500KV CB AT SMTS | 39211.4826 | 39211.6104 | DAILY | [12 empty] | 0
_1026004739212.2729166667 | 10260047 |  | Parent | FALSE | B2 220/66KV TRANS AT KTS | 39212.2729 | 39212.6389 | DAILY | 00001148 | SPIMAINT | replace faulty fan, check o.o.s. pump & oil topup | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024875639212.2972222222 | 10248756 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT HTS | 39212.2972 | 39212.6104 | DAILY | [12 empty] | 0
_X38458R139212.2986111111 | X38458R1 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39212.2986 | 39224.2972 | CONT | 00003104 | SPICAPX | Replace No1 66kv Cap BK CB with new CB & CT's | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025994239212.3111111111 | 10259942 |  | Parent | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39212.3111 | 39212.5111 | DAILY | 00007399 | SPIMAINT | Re-Balance Cap Bank at RWTS | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258Q439212.3125 | X43258Q4 |  | Parent | FALSE | BSS 220KV LINE AT RCTS | 39212.3125 | 39212.6667 | CONT | 00016966 | SPICAPX | change over BSS line CVT and connections | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V62258A939212.34375 | V62258A9 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.2 BUS CB AT SMTS | 39212.3438 | 39212.5618 | DAILY | [12 empty] | 0
_1025827939212.4694444445 | 10258279 | X43258N9 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 39212.4694 | 39212.509 | DAILY | 00359892 | SPICAPX | Rebate W/O No2 66 Cap bk during No 2 66 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025828039212.4694444445 | 10258280 | X43258N9 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 39212.4694 | 39212.509 | DAILY | 00016897 | SPICAPX | Rebate W/O No2 66 React during No2 66 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025828139212.4694444445 | 10258281 | X43258N9 | Child | FALSE | NO.2B TRANS AT RCTS | 39212.4694 | 39212.509 | DAILY | 00016760 | SPICAPX | Perf calc W/O 2B TR during No 2 66kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025828239212.4694444445 | 10258282 | X43258N9 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 39212.4694 | 39212.509 | DAILY | 00357254 | SPICAPX | Rebate W/O No3 66 React during No 2 66 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025828339212.4694444445 | 10258283 | X43258N9 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 39212.4694 | 39212.509 | DAILY | 00361128 | SPICAPX | Perf calc W/O No3 TR 66 during No 2 66 bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X43258N939212.4694444445 | X43258N9 |  | Parent | TRUE | NO.2 66KV BUS AT RCTS | 39212.4694 | 39212.509 | DAILY | 00016977 | SPICAPX | Out W/O No2 66kV bus de-energ -Commiss #2 React CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026062539212.6777777778 | 10260625 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39212.6778 | 39213.7826 | CONT | 00354002 | VEN_AUG | A1 trans Isolated for Commisioning changes | SPIPOWER |  | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1025994139213.2916666667 | 10259941 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT RTS | 39213.2917 | 39213.6042 | DAILY | 00007279 | SPIMAINT | Re-Balance Cap Bank at RTS | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024933739213.3180555556 | 10249337 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT GTS | 39213.3181 | 39213.566 | DAILY | 00002832 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_V5B858A139213.3263888889 | V5B858A1 |  | Parent | FALSE | BTS -RTS 220KV E (RTS to Joint Bay 7) (CABLE) | 39213.3264 | 39213.5604 | DAILY | 00119369 | SPIMAINT | Restore BTS-RTS Cable to service | SPIPOWER | V5B8 | V5B8 - (BTS-RTS) REPLACE CABLE JOINTS AT JOINT BAY 9 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026064539213.4729166667 | 10260645 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39213.4729 | 39213.4861 | DAILY | [12 empty] | 0
_1026063339213.5673611111 | 10260633 |  | Parent | TRUE | EX - NO.4 66KV CAPACITOR BANK CB AT GTS | 39213.5674 | 39220.5347 | CONT | [12 empty] | 0
_1026063539213.5673611111 | 10260635 | 10260633 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39213.5674 | 39220.5347 | DAILY | 00329879 | SPIMAINT | Rebate W/O No4 Cap Bk during cb outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026066739213.8125 | 10260667 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 39213.8125 | 39214.8656 | CONT | 00016423 | GENCO | YWPS No1 GTG 220kV Line Isolation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026066839214.0013888889 | 10260668 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 39214.0014 | 39218.0646 | CONT | 00356083 | GENCO | HWPS No5 Gen Trans SCAP Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024839539214.25 | 10248395 |  | Parent | TRUE | NO.2 220KV BUS AT HWPS | 39214.25 | 39215.634 | CONT | 00009659 | SPIMAINT | O/HAUL - 220kv Bus (Generic) & JLTS No2 LINE | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026047539214.25 | 10260475 | 10248395 | Child | FALSE | HWTS NO.1 220KV LINE AT HWPS | 39214.25 | 39215.634 | CONT | 00015794 | SPIMAINT | Rebate Bus Outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026047639214.25 | 10260476 | 10248395 | Child | FALSE | JLTS NO.2 220KV LINE AT HWPS | 39214.25 | 39215.634 | CONT | 00015765 | SPIMAINT | Rebate Bus Outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024850539214.2784722222 | 10248505 |  | Parent | TRUE | NO.1 220KV BUS AT RWTS | 39214.2785 | 39214.6507 | DAILY | 00007477 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026046339214.2784722222 | 10260463 | 10248505 | Child | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39214.2785 | 39214.6507 | DAILY | 00007452 | SPIMAINT | Trans Avail | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026046539214.2784722222 | 10260465 | 10248505 | Child | FALSE | B4 220/66KV TRANS AT RWTS | 39214.2785 | 39214.6507 | DAILY | 00007451 | SPIMAINT | Trans Avail | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49658F839214.2902777778 | X49658F8 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39214.2903 | 39214.6479 | DAILY | 00019243 | SPICAPX | Proximity outage of SVC and 220kv connections | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026051539214.2930555556 | 10260515 |  | Parent | FALSE | DDTS NO.1 330KV LINE SERIES CAPACITOR BANK AT SMTS | 39214.2931 | 39214.4951 | DAILY | 00327836 | FAULT | replace defective ventilator fans on white phase | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1026013239214.3013888889 | 10260132 | X38458Q6 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39214.3014 | 39214.7681 | CONT | 00003127 | SPICAPX | Perf Calc No2 Transformer | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458Q639214.3013888889 | X38458Q6 |  | Parent | TRUE | EX - NO.1 220KV BUS AT TGTS | 39214.3014 | 39214.7681 | CONT | 00003130 | SPICAPX | De comm exist No2 Trans CB's, Recomm as B2 Trans | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458Q739214.3013888889 | X38458Q7 | X38458Q6 | Child | FALSE | EX - NO.2 66KV BUS AT TGTS | 39214.3014 | 39214.7681 | CONT | 00003133 | SPICAPX | Decomm No2 Tran 220 &66 CB's recomm as B2 Tran | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458S039214.7694444444 | X38458S0 |  | Parent | FALSE | B2 220/66KV TRANS AT TGTS | 39214.7694 | 39217.5972 | CONT | 00003127 | SPICAPX | Reterminate 220 & 66kv CB Conn's to Fut B2 Trans | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025906039215.7923611111 | 10259060 |  | Parent | FALSE | A3 GEN TRANS NO.1 BUS 500KV CB AT LYPS | 39215.7924 | 39224.4771 | CONT | [12 empty] | 0
_Z62358A339216.2416666667 | Z62358A3 |  | Parent | FALSE | EPS-TTS 220KV LINE AT SMTS | 39216.2417 | 39216.8063 | REPDAILY | 00015363 | 3RDPARTY | build new tower to replace tower 225 | SPIPOWER | Z623 | Z623 - THE LAKES BOULEVARDE ROAD WORK | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026182639216.2430555556 | 10261826 |  | Parent | TRUE | MBTS-EPS 2 220KV N | 39216.2431 | 39216.8083 | REPDAILY | 00055381 | SW_NEM | Rebate-Nemco Sw High Volts on Bus Due EPS-TTS OOS | NEMMCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1026182739216.2430555556 | 10261827 | 10261826 | Child | FALSE | MBTS-EPS 1 220KV N | 39216.2431 | 39216.8083 | REPDAILY | 00055380 | SW_NEM | Rebate-Nemco Sw High Volts on Bus Due EPS-TTS OOS | NEMMCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_Z53458C539216.2680555556 | Z53458C5 |  | Parent | FALSE | HWTS NO.3 500KV LINE AT ROTS (RTF) | 39216.2681 | 39216.8542 | DAILY | 00359383 | VEN_AUG | Repair faulty ROI Tubes & trip test | SPIPOWER | Z534 | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258P239216.2979166667 | X43258P2 |  | Parent | FALSE | EX - NO.1 REACT 66KV CB AT RCTS | 39216.2979 | 39227.4681 | DAILY | [12 empty] | 0
_1025942239216.4381944445 | 10259422 | 10259426 | Child | FALSE | EX - MLTS NO.2 500KV LINE NO.2 BUS CB CT R/PH AT HYTS | 39216.4382 | 39216.5549 | CONT | [12 empty] | 0
_1025942639216.4381944445 | 10259426 |  | Parent | TRUE | SESS NO.2 275KV LINE/M2 TRANS CB CT R/PH AT HYTS | 39216.4382 | 39216.5549 | DAILY | [12 empty] | 0
_1026045639216.4381944445 | 10260456 | 10259426 | Child | FALSE | MLTS NO.2 500KV LINE CB AT HYTS | 39216.4382 | 39216.5549 | CONT | [12 empty] | 0
_1026048339216.4381944445 | 10260483 | 10259426 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 39216.4382 | 39216.5549 | CONT | 00002862 | SPIMAINT | Perf calc W/O M2 Trans Outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1026048439216.4381944445 | 10260484 | 10259426 | Child | FALSE | SESS NO.2 275KV LINE AT HYTS | 39216.4382 | 39216.5549 | CONT | 00026936 | SPIMAINT | Rebate W/O SESS No2 275kv Line outage | SPIPOWER |  |  | Circuits | Alstom | 275 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026068339216.5020833333 | 10260683 |  | Parent | FALSE | B2 220/66KV TRANS AT MBTS | 39216.5021 | 39217.6611 | CONT | 00362372 | FAULT | MBTS: B2 Trans | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026045539216.5590277778 | 10260455 |  | Parent | TRUE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39216.559 | 39216.6083 | DAILY | [12 empty] | 0
_1026047739216.5590277778 | 10260477 | 10260455 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39216.559 | 39216.6083 | CONT | 00002863 | SPIMAINT | Perf Calc W/O for M1 Trans outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1026047939216.5590277778 | 10260479 | 10260455 | Child | FALSE | SESS NO.1 275KV LINE AT HYTS | 39216.559 | 39216.6083 | CONT | 00021367 | SPIMAINT | Rebate W/O SESS No1 275kv Line | SPIPOWER |  |  | Circuits | Alstom | 275 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026023839216.7416666667 | 10260238 |  | Parent | FALSE | NO.1 66KV REACTOR AT RCTS | 39216.7417 | 39217.3056 | REPDAILY | 00016895 | SPICAPX | HVS to cover outage O/N of No1 Reactor | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z62358A339217.2534722222 | Z62358A3 |  | Parent | FALSE | EPS-TTS 220KV LINE AT SMTS | 39217.2535 | 39217.6715 | REPDAILY | 00015363 | 3RDPARTY | build new tower to replace tower 225 | SPIPOWER | Z623 | Z623 - THE LAKES BOULEVARDE ROAD WORK | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026182639217.2569444444 | 10261826 |  | Parent | TRUE | MBTS-EPS 2 220KV N | 39217.2569 | 39217.6708 | REPDAILY | 00055381 | SW_NEM | Rebate-Nemco Sw High Volts on Bus Due EPS-TTS OOS | NEMMCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1026182739217.2569444444 | 10261827 | 10261826 | Child | FALSE | MBTS-EPS 1 220KV N | 39217.2569 | 39217.6708 | REPDAILY | 00055380 | SW_NEM | Rebate-Nemco Sw High Volts on Bus Due EPS-TTS OOS | NEMMCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1024961739217.2666666667 | 10249617 |  | Parent | FALSE | EX - A4 TRANS 220KV E/SW AT KTS | 39217.2667 | 39217.6674 | DAILY | [12 empty] | 0
_1024872439217.2763888889 | 10248724 |  | Parent | FALSE | NO.2 CSC AT ROTS | 39217.2764 | 39217.6438 | DAILY | 00004716 | SPIMAINT | Yearly O/Haul - No.2 CSC at ROTS | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X49058F639217.2986111111 | X49058F6 |  | Parent | FALSE | MSS NO.1 330KV LINE AT DDTS | 39217.2986 | 39217.6535 | DAILY | 00012357 | SPICAPX | Install Spark Gaps on MSS No1 330kv Line s/d's | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024933139217.3173611111 | 10249331 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT GTS | 39217.3174 | 39217.7229 | DAILY | [12 empty] | 0
_1026022339217.3347222222 | 10260223 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39217.3347 | 39217.6681 | DAILY | 00319999 | APDALCOA | APD request for SCAP | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1026069339217.3381944444 | 10260693 |  | Parent | TRUE | JLA NO.1 220KV LINE CB AT TBTS | 39217.3382 | 39217.3833 | CONT | [12 empty] | 0
_1026170239217.3381944444 | 10261702 | 10260693 | Child | FALSE | JLA NO.1 220KV LINE AT TBTS | 39217.3382 | 39217.3833 | CONT | 00018301 | SPIMAINT | TBTS: JLA No 1 Line CB | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026069439217.4444444444 | 10260694 |  | Parent | FALSE | EX - NO.1 220KV BUS AT JLTS | 39217.4444 | 39217.4465 | DAILY | 00009889 | SPIMAINT | JLTS: No 1 220kV Bus | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026073939217.6284722222 | 10260739 |  | Parent | FALSE | EX - A4 TRANS NO.1 BUS 500KV CB AT KTS | 39217.6285 | 39218.6799 | CONT | [12 empty] | 0
_1026116139217.9715277778 | 10261161 |  | Parent | FALSE | R1 220/66/22KV TRANS AT KGTS | 39217.9715 | 39218.0035 | DAILY | 00357301 | FAULT | Spurious opening of No1 Transformer 220kV CB | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026077939218.1381944444 | 10260779 |  | Parent | FALSE | NO.1 GEN 220/16.5KV TRANS AT HWPS | 39218.1382 | 39225.1382 | CONT | 00009642 | GENCO | HWPS No 1 Gen Trans Isol'd for Gen | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_X46158M439218.2638888889 | X46158M4 |  | Parent | FALSE | NO.1 66KV BUS AT BATS | 39218.2639 | 39218.6736 | DAILY | 00006560 | SPICAPX | Out W/O No1 66kV Bus for prot upgrade & civil work | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024965339218.2680555556 | 10249653 |  | Parent | FALSE | EX - A4 TRANS NO.3 BUS 220KV CB TRANS SIDE ISOL AT KTS | 39218.2681 | 39218.6799 | REPDAILY | [12 empty] | 0
_Z53158V139218.2743055556 | Z53158V1 |  | Parent | FALSE | RTS NO.1 220KV LINE AT ROTS | 39218.2743 | 39219.7125 | CONT | 00023111 | VEN_AUG | Replace Line Between Racks at ROTS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z62358A139218.2819444445 | Z62358A1 |  | Parent | FALSE | DDTS NO.1 330KV LINE AT SMTS | 39218.2819 | 39218.7826 | DAILY | 00012749 | 3RDPARTY | build new tower to replace tower 545 | SPIPOWER | Z623 | Z623 - THE LAKES BOULEVARDE ROAD WORK | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458R239218.3083333333 | X38458R2 |  | Parent | FALSE | EX - 1-2 66KV BUS TIE CB AT TGTS | 39218.3083 | 39224.2972 | CONT | [12 empty] | 0
_X38458R939218.4055555556 | X38458R9 |  | Parent | FALSE | MLTS 220KV LINE NO.2 BUS CB AT TGTS | 39218.4056 | 39218.434 | DAILY | [12 empty] | 0
_Z62358A239219.2291666667 | Z62358A2 |  | Parent | FALSE | DDTS NO.2 330KV LINE AT SMTS | 39219.2292 | 39219.6701 | DAILY | 00012750 | 3RDPARTY | build new tower to replace tower 545 | SPIPOWER | Z623 | Z623 - THE LAKES BOULEVARDE ROAD WORK | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024965339219.2743055556 | 10249653 |  | Parent | FALSE | EX - A4 TRANS NO.3 BUS 220KV CB TRANS SIDE ISOL AT KTS | 39219.2743 | 39219.6562 | REPDAILY | [12 empty] | 0
_1024876339219.2979166667 | 10248763 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT HTS | 39219.2979 | 39219.6125 | DAILY | [12 empty] | 0
_1024830939219.3097222222 | 10248309 |  | Parent | FALSE | A2 GEN TRANS NO.1 BUS 500KV CB AT LYPS | 39219.3097 | 39219.5833 | DAILY | [12 empty] | 0
_1026105239219.3659722222 | 10261052 |  | Parent | FALSE | R1 220/66/22KV TRANS AT KGTS | 39219.366 | 39219.3958 | DAILY | 00357301 | FAULT | No1 Trans CB opened SIR 10260794 | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058I639219.4618055556 | X32058I6 |  | Parent | FALSE | EX - NO.1 220/22KV TRANS BANK AT MTS | 39219.4618 | 39225.3625 | CONT | 00026901 | SPICAPX | Re-Route L1 Trans 22KV cables to L2 22kv CB | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024964739220.2708333333 | 10249647 |  | Parent | FALSE | SYTS LINE/A4 TRANS 500KV CB TRANS SIDE ROI AT KTS | 39220.2708 | 39220.6667 | REPDAILY | [12 empty] | 0
_X47758C439220.2875 | X47758C4 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39220.2875 | 39220.6236 | DAILY | 00012436 | SPICAPX | rack to rack bypass project | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158M739220.3076388889 | X46158M7 |  | Parent | FALSE | NO.2 66KV BUS AT BATS | 39220.3076 | 39220.6674 | DAILY | 00006561 | SPICAPX | Out W/O No2 66kV Bus for prot upgrade | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024933339220.3097222222 | 10249333 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT GTS | 39220.3097 | 39220.4014 | DAILY | [12 empty] | 0
_1009267239220.325 | 10092672 |  | Parent | FALSE | LY NO.2 66KV FDR AT MWTS | 39220.325 | 39220.5951 | DAILY | 00016141 | SPIMAINT | O/Haul - LY No.2 66kV Line at MWTS | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024857439220.3631944444 | 10248574 |  | Parent | FALSE | B1 220/66KV TRANS AT RTS | 39220.3632 | 39220.6361 | DAILY | 00007329 | SPIMAINT | O/HAUL Transformer Div Mechanism (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026090139220.64375 | 10260901 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 39220.6438 | 39226.3917 | CONT | 00356080 | GENCO | Power Station Requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X47758C139221.25 | X47758C1 |  | Parent | FALSE | ROTS NO.3 500KV LINE AT SMTS | 39221.25 | 39221.7021 | DAILY | 00012438 | SPICAPX | install rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1022670539221.2729166667 | 10226705 | 10249220 | Child | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB BUS SIDE ROI AT MLTS | 39221.2729 | 39221.7472 | DAILY | [12 empty] | 0
_1024922039221.2729166667 | 10249220 |  | Parent | TRUE | NO.2 220KV BUS AT MLTS | 39221.2729 | 39221.7472 | REPDAILY | 00003015 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024924839221.2729166667 | 10249248 | 10249220 | Child | FALSE | NO.2 220KV BUS E/SW AT MLTS | 39221.2729 | 39221.7472 | REPDAILY | [12 empty] | 0
_1024019239221.2736111111 | 10240192 |  | Parent | FALSE | B1 220/66KV TRANS AT RTS | 39221.2736 | 39222.7208 | CONT | 00007329 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1022670539222.2708333333 | 10226705 | 10249220 | Child | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB BUS SIDE ROI AT MLTS | 39222.2708 | 39222.7118 | DAILY | [12 empty] | 0
_1024922039222.2708333333 | 10249220 |  | Parent | TRUE | NO.2 220KV BUS AT MLTS | 39222.2708 | 39222.7118 | REPDAILY | 00003015 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024924839222.2708333333 | 10249248 | 10249220 | Child | FALSE | NO.2 220KV BUS E/SW AT MLTS | 39222.2708 | 39222.7118 | REPDAILY | [12 empty] | 0
_V74458A039222.2868055556 | V74458A0 |  | Parent | FALSE | U1 TRANS-PAR 22KV CB AT BLTS | 39222.2868 | 39222.5986 | DAILY | [12 empty] | 0
_X23358C939222.2965277778 | X23358C9 |  | Parent | FALSE | L3 220/22KV TRANS AT WMTS | 39222.2965 | 39222.5444 | DAILY | 00003237 | SPICAPX | commission new wti, insert new probe & remove old | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X47758C239223.2611111111 | X47758C2 |  | Parent | FALSE | ROTS NO.3 500KV LINE AT SMTS | 39223.2611 | 39225.7562 | DAILY | 00012438 | SPICAPX | install rack to rack bypass conductors | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z50658B139223.26875 | Z50658B1 |  | Parent | FALSE | NO.6 66KV BUS AT HTS | 39223.2688 | 39223.6194 | DAILY | 00004460 | DB_AUG | Sub HT fdr,Sub NB fdr,Sub CRM/CBTS fdr & No 6 Bus | SPIPOWER | Z506 | Z506 - (HTS) OPTIMISING 66KV CBS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024959739223.2736111111 | 10249597 |  | Parent | FALSE | SYTS LINE/A4 TRANS 500KV CB TRANS SIDE E/SW AT KTS | 39223.2736 | 39223.6347 | REPDAILY | [12 empty] | 0
_X32058D539223.2854166667 | X32058D5 |  | Parent | TRUE | EX - OR 66KV FDR AT MTS | 39223.2854 | 39223.7889 | DAILY | 00018773 | SPICAPX | Re-route OR fdr, remove No3 66kv bus & oos old B3 | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058I739223.2854166667 | X32058I7 | X32058D5 | Child | FALSE | EX - NO.3 66KV BUS AT MTS | 39223.2854 | 39223.7889 | DAILY | 00004569 | SPICAPX | rebate bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058I839223.2854166667 | X32058I8 | X32058D5 | Child | FALSE | EX - NO.3 220/66KV TRANS BANK AT MTS | 39223.2854 | 39223.7889 | DAILY | 00026900 | SPICAPX | avail bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024857939223.2951388889 | 10248579 |  | Parent | FALSE | B2 220/66KV TRANS AT RTS | 39223.2951 | 39223.6056 | DAILY | 00007331 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V62258A739223.3104166667 | V62258A7 |  | Parent | FALSE | ROTS NO.3 LINE/KTS LINE 500KV CB AT SMTS | 39223.3104 | 39226.6361 | CONT | [12 empty] | 0
_1024831439223.3118055556 | 10248314 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.1 BUS CB AT LYPS | 39223.3118 | 39223.5625 | DAILY | [12 empty] | 0
_1025166439223.4680555556 | 10251664 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39223.4681 | 39226.8264 | CONT | 00002863 | SPIMAINT | Condition Monitoring Country Trans 3day North Area | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z50658B239223.6194444444 | Z50658B2 |  | Parent | FALSE | NO.6 66KV BUS AT HTS | 39223.6194 | 39227.6632 | CONT | 00004460 | DB_AUG | No 6 66kv Bus | SPIPOWER | Z506 | Z506 - (HTS) OPTIMISING 66KV CBS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258R639223.6666666667 | X43258R6 |  | Parent | FALSE | NO.1 66KV BUS AT RCTS | 39223.6667 | 39227.4722 | DAILY | 00016976 | SPICAPX | Commission No1 Reactor CB, CT's and Prot | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024959739224.2708333333 | 10249597 |  | Parent | FALSE | SYTS LINE/A4 TRANS 500KV CB TRANS SIDE E/SW AT KTS | 39224.2708 | 39224.6458 | REPDAILY | [12 empty] | 0
_1025140039224.2881944444 | 10251400 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK E/SW AT ROTS | 39224.2882 | 39224.6653 | DAILY | [12 empty] | 0
_X43258R839224.2888888889 | X43258R8 |  | Parent | TRUE | R1 220/66/22KV TRANS GROUP AT RCTS | 39224.2889 | 39224.7611 | DAILY | 00337581 | SPICAPX | Replace 1A & 1B Transformers surge Diverters | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258R939224.2888888889 | X43258R9 | X43258R8 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39224.2889 | 39224.7611 | DAILY | 00337581 | SPICAPX | perf calc, No1Trans Grp outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024857039224.29375 | 10248570 |  | Parent | FALSE | L1 TRANS 'A' NTH BUS 22KV CB AT RTS | 39224.2937 | 39224.5535 | DAILY | [12 empty] | 0
_X38458R039224.2972222222 | X38458R0 |  | Parent | TRUE | EX - NO.1 66KV BUS AT TGTS | 39224.2972 | 39224.7542 | DAILY | 00003132 | SPICAPX | Replace Isolators and droppers on No1 66kv Bus | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458R739224.2972222222 | X38458R7 | X38458R0 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39224.2972 | 39224.7542 | DAILY | 00363297 | SPICAPX | Out W/O Perf calc for 66kV bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458R839224.2972222222 | X38458R8 | X38458R0 | Child | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39224.2972 | 39224.7542 | DAILY | 00003104 | SPICAPX | Rebate W/O for 66kV bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010277939224.3131944445 | 10102779 |  | Parent | TRUE | YPS NO.2 220KV LINE NO.6 BUS CB AT HWPS | 39224.3132 | 39228.5104 | CONT | [12 empty] | 0
_1010288839224.3131944445 | 10102888 | 10102779 | Child | FALSE | YPS NO.2 220KV LINE NO.6 BUS CB REACTORS AT HWPS | 39224.3132 | 39228.5104 | CONT | 00337565 | SPIMAINT | O/Haul - 220kV REACTORS | SPIPOWER |  |  | Reactors | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158N139224.3201388889 | X46158N1 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 39224.3201 | 39224.7514 | REPDAILY | 00006559 | SPICAPX | Out W/O No2 220kV Bus for bus prot upgrade | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158N239224.3201388889 | X46158N2 | X46158N1 | Child | FALSE | WBTS 220KV LINE AT BATS | 39224.3201 | 39224.7514 | DAILY | 00012410 | SPICAPX | Rebate W/O HOTS Line during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158N339224.3201388889 | X46158N3 | X46158N1 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39224.3201 | 39224.7514 | DAILY | 00006554 | SPICAPX | Perf calc W/O #1 TR during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158Z139224.3201388889 | X46158Z1 | X46158N1 | Child | FALSE | MLTS NO.1 220KV LINE AT BATS | 39224.3201 | 39224.7514 | DAILY | 00012429 | SPICAPX | Rebate W/O HOTS Line during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458R339224.7541666667 | X38458R3 |  | Parent | FALSE | EX - 1-2 66KV BUS TIE CB AT TGTS | 39224.7542 | 39232.25 | CONT | [12 empty] | 0
_X38458Q939224.7541666667 | X38458Q9 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39224.7542 | 39288.6653 | CONT | 00003104 | SPICAPX | Replace No1 66kv Cap BK CB with new CB & CT's | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258R139225.2861111111 | X43258R1 |  | Parent | TRUE | NO.2 66KV BUS AT RCTS | 39225.2861 | 39225.7333 | DAILY | 00016977 | SPICAPX | Replace Bus VT Isols, droppers, disc & structures | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258R239225.2861111111 | X43258R2 | X43258R1 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39225.2861 | 39225.7333 | DAILY | 00337581 | SPICAPX | perf calc, No1Trans Grp for No2 66kv Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258R339225.2861111111 | X43258R3 | X43258R1 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 39225.2861 | 39225.7333 | DAILY | 00357254 | SPICAPX | Rebate W/O for No2 66kv Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258R439225.2861111111 | X43258R4 | X43258R1 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 39225.2861 | 39225.7333 | DAILY | 00016897 | SPICAPX | Rebate W/O for No2 66kv Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258R539225.2861111111 | X43258R5 | X43258R1 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 39225.2861 | 39225.7333 | DAILY | 00359892 | SPICAPX | Rebate W/O for No2 66kv Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024857239225.2930555556 | 10248572 |  | Parent | FALSE | L1 TRANS 'A' STH BUS 22KV CB AT RTS | 39225.2931 | 39225.4903 | DAILY | [12 empty] | 0
_X49058G839225.2930555556 | X49058G8 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT DDTS | 39225.2931 | 39225.7319 | DAILY | 00337558 | SPICAPX | Out W/O No1 Transformer- install lighting | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024800339225.3069444444 | 10248003 | 10248807 | Child | FALSE | O.O.S B 66KV FDR AT ERTS | 39225.3069 | 39225.7014 | DAILY | 00012513 | SPIMAINT | O/Haul - PHM No.1 Fdr Isol & S/D at ERTS | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024880739225.3069444444 | 10248807 |  | Parent | TRUE | O.O.S B 66KV FDR CB AT ERTS | 39225.3069 | 39225.7014 | DAILY | [12 empty] | 0
_X46158N139225.3111111111 | X46158N1 |  | Parent | TRUE | NO.2 220KV BUS AT BATS | 39225.3111 | 39225.6861 | REPDAILY | 00006559 | SPICAPX | Out W/O No2 220kV Bus for bus prot upgrade | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158N239225.3111111111 | X46158N2 | X46158N1 | Child | FALSE | WBTS 220KV LINE AT BATS | 39225.3111 | 39225.6861 | DAILY | 00012410 | SPICAPX | Rebate W/O HOTS Line during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158N339225.3111111111 | X46158N3 | X46158N1 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39225.3111 | 39225.6861 | DAILY | 00006554 | SPICAPX | Perf calc W/O #1 TR during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158Z139225.3111111111 | X46158Z1 | X46158N1 | Child | FALSE | MLTS NO.1 220KV LINE AT BATS | 39225.3111 | 39225.6861 | DAILY | 00012429 | SPICAPX | Rebate W/O HOTS Line during No2 220 Bus outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058I939225.3666666667 | X32058I9 |  | Parent | FALSE | EX - NO.1 220/22KV TRANS BANK AT MTS | 39225.3667 | 39227.7056 | DAILY | 00026901 | SPICAPX | Hipot new cable joint 22kv cable | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026098139225.5326388889 | 10260981 |  | Parent | FALSE | ROTS-RWTS 220KV E | 39225.5326 | 39225.5778 | DAILY | 00022759 | VICROADS | Z463 - LINE DEVIATION FOR MITCHAM-FRANKSTON RD | 3RDPARTY |  | Z463 - TRANSMISSION LINE DEVIATION FOR MITCHAM-FRANKSTON RD | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0 | Project outage initiated by SP AusNet
_1026006339225.5833333333 | 10260063 |  | Parent | FALSE | B4 TRANS NO.1 BUS 220KV CB AT SHTS | 39225.5833 | 39225.6826 | DAILY | [12 empty] | 0
_Z53158D339226.2513888889 | Z53158D3 | Z53158G4 | Child | FALSE | MTS NO.3 220KV LINE AT ROTS | 39226.2514 | 39227.534 | CONT | 00023099 | VEN_AUG | Line outage for No 3 Bus | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158G439226.2513888889 | Z53158G4 |  | Parent | TRUE | NO.3 220KV BUS AT ROTS | 39226.2514 | 39227.534 | CONT | 00329013 | VEN_AUG | Bus Outage for | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158N939226.2513888889 | Z53158N9 | Z53158G4 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39226.2514 | 39227.534 | DAILY | 00112417 | VEN_AUG | Cap Outage Rebate | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025052239226.2930555556 | 10250522 |  | Parent | FALSE | NO.1B 66KV CAPACITOR BANK AT ERTS | 39226.2931 | 39226.6813 | DAILY | 00337043 | SPIMAINT | O/Haul - Cap Bank & E/Sw (EM) | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49058G939226.2979166667 | X49058G9 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 39226.2979 | 39226.7389 | DAILY | 00352121 | SPICAPX | Out W/O No2 Transformer- install lighting | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1026105339226.4513888889 | 10261053 |  | Parent | FALSE | A2 515/220KV TRANS BANK AT ROTS | 39226.4514 | 39231.4889 | CONT | 00362994 | VEN_AUG | X & Y Prot Work | SPIPOWER |  | Z534 - (ROTS) RTF INTERFACE SPEC FOR 500/220KV TRANSFORMER | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1026023839226.7291666667 | 10260238 |  | Parent | FALSE | NO.1 66KV REACTOR AT RCTS | 39226.7292 | 39227.4681 | REPDAILY | 00016895 | SPICAPX | HVS to cover outage O/N of No1 Reactor | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026108339226.7388888889 | 10261083 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 39226.7389 | 39227.5729 | DAILY | 00352121 | FORCED | Out W/O-Investigate No2 TR 220kV CB fail to close | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X47758C539227.2833333333 | X47758C5 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39227.2833 | 39227.6472 | CONT | 00012436 | SPICAPX | rack to rack bypass project | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158V539227.5277777778 | Z53158V5 |  | Parent | FALSE | MTS NO.3 220KV LINE CB AT ROTS | 39227.5278 | 39315.3222 | CONT | [12 empty] | 0
_X32058J339227.7743055556 | X32058J3 |  | Parent | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39227.7743 | 39227.7875 | DAILY | 00351697 | SPICAPX | Decommission No3 220/22 TRANS | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026112039227.9347222222 | 10261120 |  | Parent | FALSE | NO.3 GEN TRANS NO.1 BUS 220KV CB AT HWPS | 39227.9347 | 39230.9368 | CONT | [12 empty] | 0
_X49658F739228.2673611111 | X49658F7 |  | Parent | TRUE | NO.2 220KV BUS AT HOTS | 39228.2674 | 39228.7611 | DAILY | 00006939 | SPICAPX | Modify No2 220kv Bus and bipods | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49658G039228.2673611111 | X49658G0 | X49658F7 | Child | FALSE | B3 220/66KV TRANS AT HOTS | 39228.2674 | 39228.7611 | DAILY | 00363102 | SPICAPX | perf calc for B3 trans | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024850739228.2736111111 | 10248507 |  | Parent | TRUE | NO.2 220KV BUS AT RWTS | 39228.2736 | 39228.6417 | DAILY | 00007478 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026097839228.2736111111 | 10260978 | 10248507 | Child | FALSE | L2 220/22KV TRANS BANK AT RWTS | 39228.2736 | 39228.6417 | DAILY | 00007447 | SPIMAINT | tran rebate for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026097939228.2736111111 | 10260979 | 10248507 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RWTS | 39228.2736 | 39228.6417 | DAILY | 00350529 | SPIMAINT | Cap Bank Rebate for Bus Outage | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026098039228.2736111111 | 10260980 | 10248507 | Child | FALSE | B3 220/66KV TRANS AT RWTS | 39228.2736 | 39228.6417 | DAILY | 00007455 | SPIMAINT | rebate for Bus Outage Trans | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49658F939229.2763888889 | X49658F9 |  | Parent | TRUE | RCTS 220KV LINE AT HOTS | 39229.2764 | 39229.8472 | DAILY | 00018715 | SPICAPX | Modify RCTS Li ne entry and assoc equipment | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49658G139229.2763888889 | X49658G1 | X49658F9 | Child | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39229.2764 | 39229.8472 | DAILY | 00019243 | SPICAPX | Proximity outage of SVC and 220kv connections | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z53158S539230.2756944444 | Z53158S5 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39230.2757 | 39234.8625 | CONT | 00004776 | VEN_AUG | Bus Outage & HWPS No2 LINE at ROTS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158S739230.2756944444 | Z53158S7 | Z53158S5 | Child | FALSE | HWPS NO.2 220KV LINE AT ROTS | 39230.2757 | 39234.8625 | CONT | 00024004 | VEN_AUG | Rebate Line outage for Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158S839230.2756944444 | Z53158S8 | Z53158S5 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39230.2757 | 39234.8625 | CONT | 00354024 | VEN_AUG | Rebate for Bus Outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X43258Q639230.2881944444 | X43258Q6 |  | Parent | TRUE | NO.2 66KV BUS AT RCTS | 39230.2882 | 39230.7181 | REPDAILY | 00016977 | SPICAPX | Replace Bus Side Droppers between CB's & isols | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258Q739230.2881944444 | X43258Q7 | X43258Q6 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39230.2882 | 39230.7181 | REPDAILY | 00337581 | SPICAPX | perf calc, No1Trans Grp for No2 66kv Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258Q839230.2881944444 | X43258Q8 | X43258Q6 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 39230.2882 | 39230.7181 | REPDAILY | 00357254 | SPICAPX | Rebate W/O for No2 66kv Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258Q939230.2881944444 | X43258Q9 | X43258Q6 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 39230.2882 | 39230.7181 | REPDAILY | 00359892 | SPICAPX | Rebate W/O for No2 66kv Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258R039230.2881944444 | X43258R0 | X43258Q6 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 39230.2882 | 39230.7181 | REPDAILY | 00016897 | SPICAPX | Rebate W/O for No2 66kv Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X32058K239230.2965277778 | X32058K2 |  | Parent | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39230.2965 | 39230.6639 | DAILY | 00351697 | SPICAPX | Decommission No3 220/22 TRANS | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024755539231.2861111111 | 10247555 |  | Parent | FALSE | EX - TTS NO.2 220KV LINE AT KTS | 39231.2861 | 39231.6319 | REPDAILY | 00015987 | SPIMAINT | O/Haul - 220kV Line (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024841039231.3125 | 10248410 |  | Parent | FALSE | HWTS NO.3 220KV LINE NO.2 BUS CB AT HWPS | 39231.3125 | 39233.6215 | CONT | [12 empty] | 0
_X23358D139231.3354166667 | X23358D1 |  | Parent | FALSE | B1 220/66KV TRANS AT HTS | 39231.3354 | 39231.6424 | DAILY | 00004445 | SPICAPX | Commission New WTI on B1 TRans | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026111739231.3451388889 | 10261117 |  | Parent | FALSE | EX - C 22KV FDR 191 AT BTS | 39231.3451 | 39241.4278 | CONT | 00015735 | SPIMAINT | Sub c 191 | SPIPOWER |  |  | Circuits | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53458G839231.5659722222 | Z53458G8 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39231.566 | 39231.634 | REPDAILY | [12 empty] | 0
_1026112839231.5993055556 | 10261128 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 39231.5993 | 39231.7056 | REPDAILY | [12 empty] | 0
_1026118239232.2131944444 | 10261182 |  | Parent | FALSE | AUX TRANS 'C' 220KV LINE AT YWPS | 39232.2132 | 39234.6951 | DAILY | 00016397 | GENCO | SCAP for genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158V339232.2722222222 | Z53158V3 |  | Parent | TRUE | EX - NO.3 220KV BUS AT ERTS | 39232.2722 | 39236.7069 | CONT | 00004379 | VEN_AUG | Replace Bus Work | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158V439232.2722222222 | Z53158V4 | Z53158V3 | Child | FALSE | B3 220/66KV TRANS AT ERTS | 39232.2722 | 39236.7069 | CONT | 00004371 | VEN_AUG | Rebate Trans outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53458G839232.2805555556 | Z53458G8 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39232.2806 | 39232.675 | REPDAILY | [12 empty] | 0
_1024755539232.2861111111 | 10247555 |  | Parent | FALSE | EX - TTS NO.2 220KV LINE AT KTS | 39232.2861 | 39232.691 | REPDAILY | 00015987 | SPIMAINT | O/Haul - 220kV Line (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X23358D239232.2930555556 | X23358D2 |  | Parent | FALSE | B2 220/66KV TRANS AT HTS | 39232.2931 | 39232.65 | DAILY | 00004446 | SPICAPX | Commission new WTI on B2 Trans | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258Q639232.2965277778 | X43258Q6 |  | Parent | TRUE | NO.2 66KV BUS AT RCTS | 39232.2965 | 39232.775 | REPDAILY | 00016977 | SPICAPX | Replace Bus Side Droppers between CB's & isols | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258Q739232.2965277778 | X43258Q7 | X43258Q6 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39232.2965 | 39232.775 | REPDAILY | 00337581 | SPICAPX | perf calc, No1Trans Grp for No2 66kv Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258Q839232.2965277778 | X43258Q8 | X43258Q6 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 39232.2965 | 39232.775 | REPDAILY | 00357254 | SPICAPX | Rebate W/O for No2 66kv Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258Q939232.2965277778 | X43258Q9 | X43258Q6 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 39232.2965 | 39232.775 | REPDAILY | 00359892 | SPICAPX | Rebate W/O for No2 66kv Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258R039232.2965277778 | X43258R0 | X43258Q6 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 39232.2965 | 39232.775 | REPDAILY | 00016897 | SPICAPX | Rebate W/O for No2 66kv Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024653239232.2986111111 | 10246532 |  | Parent | TRUE | GTS NO.2 220KV LINE AT MLTS | 39232.2986 | 39232.7319 | REPDAILY | 00022499 | SPIMAINT | O/Haul - GTS No.2 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024926039232.2986111111 | 10249260 | 10246532 | Child | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB LINE SIDE E/SW AT MLTS | 39232.2986 | 39232.7319 | REPDAILY | [12 empty] | 0
_1024926239232.2986111111 | 10249262 | 10246532 | Child | FALSE | GTS NO.2 220KV LINE E/SW AT MLTS | 39232.2986 | 39232.7319 | REPDAILY | [12 empty] | 0
_1024926439232.2986111111 | 10249264 | 10246532 | Child | FALSE | GTS NO.2 LINE/A1 TRANS 220KV CB LINE SIDE E/SW AT MLTS | 39232.2986 | 39232.7319 | REPDAILY | [12 empty] | 0
_1024928439232.2986111111 | 10249284 | 10246532 | Child | FALSE | GTS NO.2 LINE/A1 TRANS 220KV CB LINE SIDE ISOL AT MLTS | 39232.2986 | 39232.7319 | REPDAILY | [12 empty] | 0
_1024928639232.2986111111 | 10249286 | 10246532 | Child | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB LINE SIDE ISOL AT MLTS | 39232.2986 | 39232.7319 | REPDAILY | [12 empty] | 0
_1024736739232.3263888889 | 10247367 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39232.3264 | 39232.6146 | DAILY | 00017270 | SPIMAINT | 1 Yearly O/Haul - SVC at KGTS | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X49058G339232.3375 | X49058G3 |  | Parent | TRUE | NO.1 330KV BUS AT DDTS | 39232.3375 | 39232.8708 | DAILY | 00003978 | SPICAPX | Out W/O No1 330kv Bus- Connect new CVT's | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X49058G439232.3375 | X49058G4 | X49058G3 | Child | FALSE | NO.1 330KV CAPACITOR BANK AT DDTS | 39232.3375 | 39232.8708 | DAILY | 00352085 | SPICAPX | rebate w/o for No1 330 cap bank during bus outage | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_1026119539232.5895833333 | 10261195 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 39232.5896 | 39232.6278 | DAILY | [12 empty] | 0
_1026112839232.6125 | 10261128 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 39232.6125 | 39232.7083 | REPDAILY | [12 empty] | 0
_Z53158T239233.2784722222 | Z53158T2 |  | Parent | FALSE | RTS NO.1 220KV LINE AT ROTS | 39233.2785 | 39233.3465 | DAILY | 00023111 | VEN_AUG | Rebate Line outage for Bus Job RTS No1 Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458S139233.2791666667 | X38458S1 |  | Parent | TRUE | EX - NO.2 66KV BUS AT TGTS | 39233.2792 | 39233.8271 | DAILY | 00003133 | SPICAPX | Install conn's to Fut 1-2 66 B /T CB & commission | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458S239233.2791666667 | X38458S2 | X38458S1 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39233.2792 | 39233.8271 | DAILY | 00003127 | SPICAPX | Out W/O Perf calc for 66kV bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X46158N639233.2888888889 | X46158N6 |  | Parent | FALSE | WBTS 220KV LINE AT BATS | 39233.2889 | 39233.7604 | DAILY | 00012410 | SPICAPX | Out W/O HOTS Line to commiss No1 Tie | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024653239233.2909722222 | 10246532 |  | Parent | TRUE | GTS NO.2 220KV LINE AT MLTS | 39233.291 | 39233.7201 | REPDAILY | 00022499 | SPIMAINT | O/Haul - GTS No.2 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024926039233.2909722222 | 10249260 | 10246532 | Child | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB LINE SIDE E/SW AT MLTS | 39233.291 | 39233.7201 | REPDAILY | [12 empty] | 0
_1024926239233.2909722222 | 10249262 | 10246532 | Child | FALSE | GTS NO.2 220KV LINE E/SW AT MLTS | 39233.291 | 39233.7201 | REPDAILY | [12 empty] | 0
_1024926439233.2909722222 | 10249264 | 10246532 | Child | FALSE | GTS NO.2 LINE/A1 TRANS 220KV CB LINE SIDE E/SW AT MLTS | 39233.291 | 39233.7201 | REPDAILY | [12 empty] | 0
_1024928439233.2909722222 | 10249284 | 10246532 | Child | FALSE | GTS NO.2 LINE/A1 TRANS 220KV CB LINE SIDE ISOL AT MLTS | 39233.291 | 39233.7201 | REPDAILY | [12 empty] | 0
_1024928639233.2909722222 | 10249286 | 10246532 | Child | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB LINE SIDE ISOL AT MLTS | 39233.291 | 39233.7201 | REPDAILY | [12 empty] | 0
_1024736939233.2972222222 | 10247369 |  | Parent | TRUE | R2 220/66/22KV TRANS AT KGTS | 39233.2972 | 39233.6931 | DAILY | 00017344 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025396139233.2972222222 | 10253961 | 10247369 | Child | FALSE | R2 220/66/22KV TRANS AT KGTS | 39233.2972 | 39233.6931 | DAILY | 00017344 | SPIMAINT | Oil Level in Bushing | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026083039233.2972222222 | 10260830 | 10247369 | Child | TRUE | R2 220/66/22KV TRANS AT KGTS | 39233.2972 | 39233.6931 | DAILY | 00017344 | SPIMAINT | Perf calc No2 transformer outage at KGTS | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026083339233.2972222222 | 10260833 | 10260830 | Child | FALSE | R2 220/66/22KV TRANS AT KGTS | 39233.2972 | 39233.6931 | DAILY | 00017344 | SPIMAINT | Oil Level in Bushing | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X23358D339233.3006944444 | X23358D3 |  | Parent | FALSE | B3 220/66KV TRANS AT HTS | 39233.3007 | 39233.6521 | DAILY | 00004447 | SPICAPX | Commission new WTI on B3 Trans | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49058G539233.3048611111 | X49058G5 |  | Parent | TRUE | NO.2 330KV BUS AT DDTS | 39233.3049 | 39233.6486 | DAILY | 00003979 | SPICAPX | Out W/O No2 330kv Bus- Connect new bus CVT's | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X49058G639233.3048611111 | X49058G6 | X49058G5 | Child | FALSE | NO.2 330KV CAPACITOR BANK AT DDTS | 39233.3049 | 39233.6486 | DAILY | 00352093 | SPICAPX | Rebate w/o No2 330kv cap bank during bus outage | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_X49058G739233.3048611111 | X49058G7 | X49058G5 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 39233.3049 | 39233.6486 | DAILY | 00352121 | SPICAPX | Rebate w/o fNo2 Transformer during bus outage | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z53458G839233.3208333333 | Z53458G8 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39233.3208 | 39233.6799 | REPDAILY | [12 empty] | 0
_1026126539233.6506944444 | 10261265 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 39233.6507 | 39233.8688 | DAILY | 00352121 | FAULT | DDTS: H2 Trans unable to close 220kV CB | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1026127439233.8638888889 | 10261274 |  | Parent | FALSE | NO.1 TRANS 220KV CB AT KGTS | 39233.8639 | 39234.6354 | CONT | [12 empty] | 0
_1026128239233.8638888889 | 10261282 |  | Parent | FALSE | R1 220/66/22KV TRANS AT KGTS | 39233.8639 | 39234.6354 | CONT | 00357301 | FAULT | KGTS: No 1 Trans 220kV CB spurious opening | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026124839234.0409722222 | 10261248 |  | Parent | FALSE | LYBP-LYPS 1 500KV G | 39234.041 | 39235.9097 | CONT | 00023061 | GENCO | Isol & earth for Genco/Hazel AP | GENCO |  |  | Circuits | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158T239234.2791666667 | Z53158T2 |  | Parent | FALSE | RTS NO.1 220KV LINE AT ROTS | 39234.2792 | 39234.8625 | DAILY | 00023111 | VEN_AUG | Rebate Line outage for Bus Job RTS No1 Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024653239234.2902777778 | 10246532 |  | Parent | TRUE | GTS NO.2 220KV LINE AT MLTS | 39234.2903 | 39234.6806 | REPDAILY | 00022499 | SPIMAINT | O/Haul - GTS No.2 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024926039234.2902777778 | 10249260 | 10246532 | Child | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB LINE SIDE E/SW AT MLTS | 39234.2903 | 39234.6806 | REPDAILY | [12 empty] | 0
_1024926239234.2902777778 | 10249262 | 10246532 | Child | FALSE | GTS NO.2 220KV LINE E/SW AT MLTS | 39234.2903 | 39234.6806 | REPDAILY | [12 empty] | 0
_1024926439234.2902777778 | 10249264 | 10246532 | Child | FALSE | GTS NO.2 LINE/A1 TRANS 220KV CB LINE SIDE E/SW AT MLTS | 39234.2903 | 39234.6806 | REPDAILY | [12 empty] | 0
_1024928439234.2902777778 | 10249284 | 10246532 | Child | FALSE | GTS NO.2 LINE/A1 TRANS 220KV CB LINE SIDE ISOL AT MLTS | 39234.2903 | 39234.6806 | REPDAILY | [12 empty] | 0
_1024928639234.2902777778 | 10249286 | 10246532 | Child | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB LINE SIDE ISOL AT MLTS | 39234.2903 | 39234.6806 | REPDAILY | [12 empty] | 0
_1026127239234.3409722222 | 10261272 |  | Parent | FALSE | NO.1 TRANS 220KV CB AT KGTS | 39234.341 | 39234.6361 | DAILY | [12 empty] | 0
_1026131339234.5701388889 | 10261313 |  | Parent | FALSE | WMTS NO.2 220KV LINE CB AT FBTS | 39234.5701 | 39234.575 | CONT | [12 empty] | 0
_1026138039234.5701388889 | 10261380 |  | Parent | FALSE | WMTS NO.2 220KV LINE AT FBTS | 39234.5701 | 39234.575 | DAILY | 00017157 | FORCED | WMTS NO.2 220KV LINE CB AT FBTS Low SF6 Alarm | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1026133539234.9979166667 | 10261335 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 39234.9979 | 39237.4028 | CONT | [12 empty] | 0
_Z53158V639235.2652777778 | Z53158V6 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 39235.2653 | 39235.6431 | CONT | 00004778 | VEN_AUG | MTS No1 & A1Trans 220KV LINES & No 4 BUS outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158V739235.2652777778 | Z53158V7 | Z53158V6 | Child | FALSE | NO.4 220KV BUS AT ROTS | 39235.2653 | 39235.6431 | CONT | 00329012 | VEN_AUG | Remove bipods on No 2 bus CB & No 4 BUS outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158V839235.2652777778 | Z53158V8 | Z53158V6 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39235.2653 | 39235.6431 | CONT | 00112418 | VEN_AUG | Cap Bank Rebate For Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z53158V939235.2652777778 | Z53158V9 | Z53158V6 | Child | FALSE | MTS NO.1 220KV LINE AT ROTS | 39235.2653 | 39235.6431 | CONT | 00350667 | VEN_AUG | Line outge Rebate For Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158W039235.2652777778 | Z53158W0 | Z53158V6 | Child | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39235.2653 | 39235.6431 | CONT | 00354002 | VEN_AUG | Line outge Rebate For Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1024019639235.2965277778 | 10240196 |  | Parent | TRUE | B2 220/66KV TRANS AT RTS | 39235.2965 | 39236.6833 | CONT | 00007331 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026096839235.2965277778 | 10260968 | 10240196 | Child | FALSE | B2 220/66KV TRANS AT RTS | 39235.2965 | 39236.6833 | CONT | 00007331 | SPIMAINT | Condition Sup Monitoring Metro Trans 2day East Are | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024832539235.3243055556 | 10248325 |  | Parent | TRUE | NO.4 500KV BUS E/SW AT LYPS | 39235.3243 | 39235.5215 | CONT | [12 empty] | 0
_1026126239235.3243055556 | 10261262 | 10248325 | Child | FALSE | HWTS NO.3 500KV LINE AT LYPS | 39235.3243 | 39235.5215 | CONT | 00016088 | SPIMAINT | Bus outage rebate | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026119139235.75 | 10261191 |  | Parent | FALSE | EX - BK 22KV FDR 187 CB AT BTS | 39235.75 | 39237.7131 | DAILY | [12 empty] | 0
_1025760839236.2986111111 | 10257608 |  | Parent | FALSE | KTS -ATS 220KV WY | 39236.2986 | 39236.6097 | DAILY | 00074402 | SPIMAINT | Change faulty insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026116639236.2986111111 | 10261166 |  | Parent | FALSE | EX - ATS LINE/A2 TRANS 220KV CB AT KTS | 39236.2986 | 39236.6097 | DAILY | [12 empty] | 0
_X32058K439236.3333333333 | X32058K4 |  | Parent | FALSE | COMMUNICATIONS ROOM AT MTS | 39236.3333 | 39239.5764 | DAILY | [12 empty] | 0
_1026148839236.7236111111 | 10261488 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT KTS | 39236.7236 | 39238.6257 | CONT | 00327947 | FAULT | KTS: Trip of No 1 66kV Cap Bank (Out of Balance) | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026264039236.7236111111 | 10262640 | 10261488 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT KTS | 39236.7236 | 39238.6257 | CONT | 00337022 | FAULT | KTS: Trip of No 1 66kV Cap Bank (Out of Balance) | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258S539237.2784722222 | X43258S5 |  | Parent | TRUE | R1 220/66/22KV TRANS GROUP AT RCTS | 39237.2785 | 39237.5674 | DAILY | 00337581 | SPICAPX | upgrade No1 TR GRP 220 connections to strung bus | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258T039237.2784722222 | X43258T0 | X43258S5 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39237.2785 | 39237.5674 | DAILY | 00337581 | SPICAPX | perf calc, No1Trans Grp outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024895039237.2986111111 | 10248950 |  | Parent | TRUE | NO.1 330KV BUS AT WOTS | 39237.2986 | 39237.7333 | REPDAILY | 00004041 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 330 | NON AER ELEMENT | EXCLUDED |  | 0
_1026080839237.2986111111 | 10260808 | 10248950 | Child | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 39237.2986 | 39237.7333 | REPDAILY | 00004036 | SPIMAINT | Rebate W/O No1 Trans during 330kV bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56558A539237.2986111111 | X56558A5 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 39237.2986 | 39240.6854 | CONT | [12 empty] | 0
_1024646039237.3125 | 10246460 |  | Parent | FALSE | BATS NO.1 220KV LINE AT MLTS | 39237.3125 | 39237.7035 | REPDAILY | 00022946 | SPIMAINT | O/Haul - BATS No.1 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024825039237.3326388889 | 10248250 |  | Parent | FALSE | ROTS NO.5 220KV LINE NO.2 BUS CB AT YPS | 39237.3326 | 39428.4458 | CONT | [12 empty] | 0
_X49858D039237.35625 | X49858D0 |  | Parent | TRUE | EX - NO.1 220KV BUS AT MBTS | 39237.3562 | 39237.5069 | DAILY | 00004001 | SPICAPX | Remove loop from between EPS1 and DDTS1 220 lines | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49858D739237.35625 | X49858D7 | X49858D0 | Child | FALSE | EX - EPS NO.1 220KV LINE AT MBTS | 39237.3562 | 39237.5069 | CONT | 00011751 | SPICAPX | Rebate W/O EPS #1 Line, No1 220kv Bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49858D839237.35625 | X49858D8 | X49858D0 | Child | FALSE | EX - DDTS NO.1 220KV LINE AT MBTS | 39237.3562 | 39237.5069 | REPDAILY | 00011748 | SPICAPX | Rebate W/O DDTS1 Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858D939237.35625 | X49858D9 | X49858D0 | Child | FALSE | DPS 220KV LINE AT MBTS | 39237.3562 | 39237.5069 | CONT | 00011754 | SPICAPX | Rebate W/O DPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858E639237.35625 | X49858E6 | X49858D0 | Child | FALSE | WKPS 220KV LINE AT MBTS | 39237.3562 | 39237.5069 | CONT | 00011756 | SPICAPX | Rebate W/O WKPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858E739237.35625 | X49858E7 | X49858D0 | Child | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39237.3562 | 39237.5069 | CONT | 00011755 | SPICAPX | Rebate W/O MKPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858E839237.35625 | X49858E8 | X49858D0 | Child | FALSE | EX - EPS NO.2 220KV LINE AT MBTS | 39237.3562 | 39237.5069 | CONT | 00011752 | SPICAPX | Rebate W/O EPS No2Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49858E939237.35625 | X49858E9 | X49858D0 | Child | FALSE | B2 220/66KV TRANS AT MBTS | 39237.3562 | 39237.5069 | CONT | 00362372 | SPICAPX | Perf calc, B2 Trans during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49858F039237.35625 | X49858F0 | X49858D0 | Child | FALSE | EX - DDTS NO.2 220KV LINE AT MBTS | 39237.3562 | 39237.5069 | CONT | 00011750 | SPICAPX | Rebate W/O DDTS2 Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858F139237.35625 | X49858F1 | X49858D0 | Child | FALSE | B1 220/66KV TRANS (HOT SPARE) AT MBTS | 39237.3562 | 39237.5069 | CONT | 00360627 | SPICAPX | Perf calc, B1 Trans during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER | NORMALLY OPEN | 0
_1026143939237.5770833333 | 10261439 |  | Parent | FALSE | WBTS 220KV LINE NO.1 TIE BUS AT BATS | 39237.5771 | 39249.2507 | CONT | 00362536 | SPIMAINT | HVS-BATS: HOTS Line Tie Bus | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026140539237.65625 | 10261405 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT SHTS | 39237.6562 | 39237.7222 | DAILY | [12 empty] | 0
_1026140839237.65625 | 10261408 |  | Parent | FALSE | NO.2A 66KV CAPACITOR BANK AT SHTS | 39237.6562 | 39237.7222 | DAILY | 00350862 | SPIMAINT | Rebate W/O 2A Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026140939237.65625 | 10261409 | 10261405 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT SHTS | 39237.6562 | 39237.7222 | DAILY | 00330829 | SPIMAINT | Rebate W/O 2B Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026141039237.65625 | 10261410 | 10261405 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT SHTS | 39237.6562 | 39237.7222 | DAILY | 00350862 | SPIMAINT | Rebate W/O 2A Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49858F239238.2423611111 | X49858F2 |  | Parent | TRUE | EX - DDTS NO.1 220KV LINE AT MBTS | 39238.2424 | 39240.6146 | CONT | 00011748 | SPICAPX | Install Conn's between DDTS No1 Line & LS ROI | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858F339238.2423611111 | X49858F3 | X49858F2 | Child | FALSE | 1-2 220KV BUS TIE CB AT MBTS | 39238.2424 | 39240.6146 | DAILY | [12 empty] | 0
_X43258T239238.2708333333 | X43258T2 |  | Parent | TRUE | NO.1B 220/66/22KV TRANS AT RCTS | 39238.2708 | 39238.7528 | DAILY | 00016758 | SPICAPX | Upgrade 1B Trans 66kv connections to CB | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258T339238.2708333333 | X43258T3 | X43258T2 | Child | FALSE | NO.1B 220/66/22KV TRANS AT RCTS | 39238.2708 | 39238.7528 | DAILY | 00016758 | SPICAPX | perf calc, No1B Trans outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158W239238.2888888889 | Z53158W2 |  | Parent | FALSE | HWPS NO.2 220KV LINE AT ROTS | 39238.2889 | 39238.7056 | DAILY | 00024004 | VEN_AUG | Install flexible connections to ERTS/HWPS No2 Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458S639238.2902777778 | X38458S6 |  | Parent | TRUE | EX - NO.1 220KV BUS AT TGTS | 39238.2903 | 39238.8118 | REPDAILY | 00003130 | SPICAPX | Change No 1 220kV bus to Alumin & install bi-pods | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458S739238.2902777778 | X38458S7 | X38458S6 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39238.2903 | 39238.8118 | REPDAILY | 00363297 | SPICAPX | Out W/O Perf calc B1 Trans while bus is out | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V62258B039238.2930555556 | V62258B0 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT SMTS | 39238.2931 | 39241.6757 | CONT | [12 empty] | 0
_X23358D539238.2986111111 | X23358D5 |  | Parent | FALSE | B1 220/66KV TRANS AT SVTS | 39238.2986 | 39238.6632 | DAILY | 00004849 | SPICAPX | B1 New WTI Install | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024646039238.3034722222 | 10246460 |  | Parent | FALSE | BATS NO.1 220KV LINE AT MLTS | 39238.3035 | 39238.6979 | REPDAILY | 00022946 | SPIMAINT | O/Haul - BATS No.1 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024895039238.3194444444 | 10248950 |  | Parent | TRUE | NO.1 330KV BUS AT WOTS | 39238.3194 | 39238.7403 | REPDAILY | 00004041 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 330 | NON AER ELEMENT | EXCLUDED |  | 0
_1026080839238.3194444444 | 10260808 | 10248950 | Child | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 39238.3194 | 39238.7403 | REPDAILY | 00004036 | SPIMAINT | Rebate W/O No1 Trans during 330kV bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026091239238.3291666667 | 10260912 |  | Parent | FALSE | LY NO.4 66KV FDR NO.3 BUS CB AT MWTS | 39238.3292 | 39238.5917 | DAILY | [12 empty] | 0
_X46158N939238.33125 | X46158N9 |  | Parent | FALSE | EX - TGTS 220KV LINE NO.2 TIE CT R/PH AT BATS | 39238.3313 | 39238.5354 | DAILY | [12 empty] | 0
_X49858F939238.3736111111 | X49858F9 |  | Parent | FALSE | EX - EPS NO.1 220KV LINE AT MBTS | 39238.3736 | 39247.5875 | CONT | 00011751 | SPICAPX | Install conn's betw EPS 1 LN & EPS 1 Ln CB L/S ROI | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49058H139238.4305555556 | X49058H1 |  | Parent | FALSE | MSS NO.1 LINE/SMTS NO.1 LINE 330KV CB AT DDTS | 39238.4306 | 39238.5743 | DAILY | [12 empty] | 0
_Z53158W339239.2534722222 | Z53158W3 |  | Parent | FALSE | ERTS NO.1 220KV LINE AT ROTS | 39239.2535 | 39240.7125 | CONT | 00350666 | VEN_AUG | Install connections to ERTS No1 line/HWPS No2 Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458S639239.2916666667 | X38458S6 |  | Parent | TRUE | EX - NO.1 220KV BUS AT TGTS | 39239.2917 | 39239.7535 | REPDAILY | 00003130 | SPICAPX | Change No 1 220kV bus to Alumin & install bi-pods | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458S739239.2916666667 | X38458S7 | X38458S6 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39239.2917 | 39239.7535 | REPDAILY | 00363297 | SPICAPX | Out W/O Perf calc B1 Trans while bus is out | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X23358D639239.2993055556 | X23358D6 |  | Parent | FALSE | B2 220/66KV TRANS AT SVTS | 39239.2993 | 39239.6667 | DAILY | 00004850 | SPICAPX | B2 New WTI Install | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024646039239.3055555556 | 10246460 |  | Parent | FALSE | BATS NO.1 220KV LINE AT MLTS | 39239.3056 | 39239.6896 | REPDAILY | 00022946 | SPIMAINT | O/Haul - BATS No.1 LINE at MLTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258Q339239.3111111111 | X43258Q3 |  | Parent | FALSE | NO.2 22KV BUS AT RCTS | 39239.3111 | 39239.7417 | DAILY | 00016998 | SPICAPX | C'mission new No2 22kv B/P & 1-2 22kv Bus Tie prot | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1024895039239.3111111111 | 10248950 |  | Parent | TRUE | NO.1 330KV BUS AT WOTS | 39239.3111 | 39239.7681 | REPDAILY | 00004041 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 330 | NON AER ELEMENT | EXCLUDED |  | 0
_1026080839239.3111111111 | 10260808 | 10248950 | Child | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 39239.3111 | 39239.7681 | REPDAILY | 00004036 | SPIMAINT | Rebate W/O No1 Trans during 330kV bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49058H239239.3416666667 | X49058H2 |  | Parent | FALSE | MSS NO.2 LINE/SMTS NO.2 LINE 330KV CB AT DDTS | 39239.3417 | 39239.4903 | DAILY | [12 empty] | 0
_Z53458G839240.2916666667 | Z53458G8 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39240.2917 | 39240.625 | REPDAILY | [12 empty] | 0
_X23358D739240.2930555556 | X23358D7 |  | Parent | FALSE | B3 220/66KV TRANS AT SVTS | 39240.2931 | 39240.6694 | DAILY | 00004851 | SPICAPX | B3 New WTI Install | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024801439240.2972222222 | 10248014 |  | Parent | FALSE | DDTS 330KV LINE AT WOTS | 39240.2972 | 39240.6889 | REPDAILY | 00012054 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458S639240.3048611111 | X38458S6 |  | Parent | TRUE | EX - NO.1 220KV BUS AT TGTS | 39240.3049 | 39240.7208 | REPDAILY | 00003130 | SPICAPX | Change No 1 220kV bus to Alumin & install bi-pods | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458S739240.3048611111 | X38458S7 | X38458S6 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39240.3049 | 39240.7208 | REPDAILY | 00363297 | SPICAPX | Out W/O Perf calc B1 Trans while bus is out | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026095039240.3236111111 | 10260950 |  | Parent | TRUE | EX - NO.1 MAIN TRANS 500KV CB AT HWTS | 39240.3236 | 39240.6458 | DAILY | [12 empty] | 0
_1026266839240.3236111111 | 10262668 | 10260950 | Child | FALSE | A1 515/230KV TRANS AT HWTS | 39240.3236 | 39240.6458 | DAILY | 00009772 | SPIMAINT | Rebate - REPAIR CB AIR LEAKS. | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X43258S139240.3326388889 | X43258S1 |  | Parent | TRUE | NO.1 22KV BUS AT RCTS | 39240.3326 | 39240.616 | DAILY | 00016979 | SPICAPX | Commiss new prot and do trip checks No1 22kv Bus | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258S239240.3326388889 | X43258S2 | X43258S1 | Child | FALSE | NO.1 22KV CAPACITOR BANK AT RCTS | 39240.3326 | 39240.616 | DAILY | 00016710 | SPICAPX | Rebate W/O No 1 22kV Cap bk during 22kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258S339240.3326388889 | X43258S3 | X43258S1 | Child | FALSE | NO.1A TRANS AT RCTS | 39240.3326 | 39240.616 | DAILY | 00016722 | SPICAPX | Perf calc W/O 1A Trans during 22kV bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026142739240.3534722222 | 10261427 |  | Parent | FALSE | NO.6 GEN TRANS NO.3 BUS 220KV CB AT HWPS | 39240.3535 | 39247.3678 | DAILY | [12 empty] | 0
_1026159639240.9638888889 | 10261596 |  | Parent | FALSE | YWPS NO.3 220KV LINE AT YPS | 39240.9639 | 39245.7247 | CONT | 00016426 | GENCO | Isol & Earth for Genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158W439241.2708333333 | Z53158W4 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 39241.2708 | 39241.6771 | CONT | 00004778 | VEN_AUG | Removal BiPods to ERTS No1 line CB Bus Side isols | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158W539241.2708333333 | Z53158W5 | Z53158W4 | Child | FALSE | NO.2 220KV BUS AT ROTS | 39241.2708 | 39241.6771 | CONT | 00004778 | VEN_AUG | rEBATE FOR bUS oUTAGE | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058K039241.2722222222 | X32058K0 |  | Parent | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39241.2722 | 39241.6701 | DAILY | 00351697 | SPICAPX | Proximty Reasons | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026117439241.2763888889 | 10261174 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 39241.2764 | 39241.6278 | DAILY | 00001147 | SPIMAINT | low oil in tr bushing & air leak in cb cabinet | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024801439241.2958333333 | 10248014 |  | Parent | FALSE | DDTS 330KV LINE AT WOTS | 39241.2958 | 39241.6424 | REPDAILY | 00012054 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026041239241.3215277778 | 10260412 | 10251278 | Child | FALSE | JA NO.3 66KV FDR NO.2 BUS CB AT WMTS | 39241.3215 | 39241.5938 | DAILY | [12 empty] | 0
_1026176339243.3520833333 | 10261763 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT RTS | 39243.3521 | 39243.6408 | CONT | 00007279 | FAULT | RTS No1 Cap Bank X Prot Failure | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258T839244.2736111111 | X43258T8 |  | Parent | TRUE | R1 220/66/22KV TRANS GROUP AT RCTS | 39244.2736 | 39246.7035 | CONT | 00337581 | SPICAPX | C'over old No1 Trans Grp prot to new Prot circuits | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258T939244.2736111111 | X43258T9 | X43258T8 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39244.2736 | 39246.7035 | CONT | 00337581 | SPICAPX | Perf Calc No 1Trans Grp for prot changeover outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058K139245.2722222222 | X32058K1 |  | Parent | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39245.2722 | 39245.6826 | REPDAILY | 00351697 | SPICAPX | Proximty Reasons for removing OOS Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058K139246.2555555556 | X32058K1 |  | Parent | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39246.2556 | 39246.6965 | REPDAILY | 00351697 | SPICAPX | Proximty Reasons for removing OOS Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026121739246.2729166667 | 10261217 |  | Parent | FALSE | ROTS-RTS 1 220KV E | 39246.2729 | 39246.6722 | REPDAILY | 00022749 | SPIMAINT | Replace Insulators on RTS - ROTS 1 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024866239246.29375 | 10248662 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT TBTS | 39246.2937 | 39246.5014 | DAILY | [12 empty] | 0
_X23358D939246.3006944444 | X23358D9 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 39246.3007 | 39246.6639 | DAILY | 00002830 | SPICAPX | Out W/O No4 Trans - New WTI installation | SPIPOWER | X233 | X233 - REPLACE TRANSFMR WINDING TEMP INDICATORS-ST1 | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56558A939246.3090277778 | X56558A9 |  | Parent | FALSE | TGTS 220KV LINE NO.2 BUS CB AT MLTS | 39246.309 | 39248.6208 | CONT | [12 empty] | 0
_1025951439246.3152777778 | 10259514 |  | Parent | FALSE | AUX TRANS 'C' NO.2 BUS 220KV CB CT R/PH AT YPS | 39246.3153 | 39246.4382 | DAILY | [12 empty] | 0
_X41258E039246.3298611111 | X41258E0 |  | Parent | FALSE | B2 220/66KV TRANS AT SHTS | 39246.3299 | 39246.7136 | DAILY | 00000841 | SPICAPX | Out W/O B2 Trans to modify 220kV Hstring droppers | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025949439246.3854166667 | 10259494 |  | Parent | FALSE | RWTS 220KV LINE NO.4 BUS CB CT R/PH AT ROTS | 39246.3854 | 39246.4271 | DAILY | [12 empty] | 0
_1025149039246.40625 | 10251490 |  | Parent | FALSE | 66KV SHUNT REACTOR AT KGTS | 39246.4062 | 39246.6827 | REPDAILY | 00354076 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025951839246.4388888889 | 10259518 |  | Parent | FALSE | AUX TRANS 'C' NO.1 BUS 220KV CB CT R/PH AT YPS | 39246.4389 | 39246.5007 | DAILY | [12 empty] | 0
_1026262739247.23125 | 10262627 |  | Parent | FALSE | SYN/COND AT BLTS | 39247.2312 | 39247.3632 | DAILY | 00002547 | FAULT | Syncon tripped when 220 KV Cap bank placed inserv | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026121739247.2701388889 | 10261217 |  | Parent | FALSE | ROTS-RTS 1 220KV E | 39247.2701 | 39247.6625 | REPDAILY | 00022749 | SPIMAINT | Replace Insulators on RTS - ROTS 1 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158N739247.2770833333 | X46158N7 |  | Parent | FALSE | TGTS 220KV LINE AT BATS | 39247.2771 | 39247.7792 | DAILY | 00012435 | SPICAPX | Out W/O TGTS Line to commiss No1 Tie | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026182939247.2958333333 | 10261829 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT MLTS | 39247.2958 | 39258.3792 | CONT | 00350825 | FORCED | HVS: MLTS-No 2 220kV Cap Bank | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1025954039247.3180555556 | 10259540 |  | Parent | FALSE | W3 GEN TRANS NO.2 BUS 220KV CB CT R/PH AT YPS | 39247.3181 | 39247.4549 | DAILY | [12 empty] | 0
_1026127239247.3409722222 | 10261272 |  | Parent | FALSE | NO.1 TRANS 220KV CB AT KGTS | 39247.341 | 39247.6326 | DAILY | [12 empty] | 0
_Z53458G939247.39375 | Z53458G9 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39247.3938 | 39247.7361 | REPDAILY | 00354002 | VEN_AUG | Point of Wave Test on A1 & A2 Trans CB's | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1025950639247.4333333333 | 10259506 |  | Parent | FALSE | EX - B1 TRANS 220KV CB CT R/PH AT TBTS | 39247.4333 | 39247.4479 | DAILY | [12 empty] | 0
_1025950839247.4493055556 | 10259508 |  | Parent | FALSE | EX - B2 TRANS 220KV CB CT R/PH AT TBTS | 39247.4493 | 39247.4701 | DAILY | [12 empty] | 0
_X43858S939247.5416666667 | X43858S9 |  | Parent | FALSE | EX - NO.2 66KV BUS VT AT TGTS | 39247.5417 | 39254.25 | CONT | [12 empty] | 0
_X49858D339247.5875 | X49858D3 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MBTS | 39247.5875 | 39247.6806 | DAILY | 00004002 | SPICAPX | Install bipods to Fut EPS No1 Ln CB Bus side ROI | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49858E439247.5875 | X49858E4 | X49858D3 | Child | FALSE | EX - DDTS NO.1 220KV LINE AT MBTS | 39247.5875 | 39247.6806 | CONT | 00011748 | SPICAPX | Rebate W/O DDTS1 Line during No2 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858E539247.5875 | X49858E5 | X49858D3 | Child | FALSE | EX - EPS NO.1 220KV LINE AT MBTS | 39247.5875 | 39247.6806 | CONT | 00011751 | SPICAPX | Rebate W/O EPS #1 Line, No2 220kv Bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X38458S939247.6145833333 | X38458S9 |  | Parent | FALSE | EX - NO.2 66KV BUS AT TGTS | 39247.6146 | 39254.3069 | REPDAILY | 00003133 | SPICAPX | Change No 2 66kV bus VT | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026181939247.6215277778 | 10261819 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39247.6215 | 39247.6306 | DAILY | [12 empty] | 0
_1026183139247.6361111111 | 10261831 |  | Parent | FALSE | NO.1A TRANS AT RCTS | 39247.6361 | 39247.6542 | DAILY | 00016722 | SPIMAINT | HVS: RCTS: No 1A-1B Trans Group | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49658H039248.2784722222 | X49658H0 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 39248.2785 | 39255.2722 | CONT | 00359897 | SPICAPX | Replace No2 Cap BK CB,CT's & Connections | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026138639248.2923611111 | 10261386 |  | Parent | FALSE | 2-3 220KV BUS TIE CB AT TTS | 39248.2924 | 39248.6549 | DAILY | [12 empty] | 0
_1026118739248.325 | 10261187 |  | Parent | FALSE | EX - BK 22KV FDR 194 CB AT BTS | 39248.325 | 39248.7063 | DAILY | [12 empty] | 0
_1025951239248.3361111111 | 10259512 |  | Parent | FALSE | 5 GRP TRANS 220KV CB CT R/PH AT YPS | 39248.3361 | 39248.5972 | DAILY | [12 empty] | 0
_Z53458G939248.4208333333 | Z53458G9 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39248.4208 | 39248.5389 | REPDAILY | 00354002 | VEN_AUG | Point of Wave Test on A1 & A2 Trans CB's | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1026194039249.2506944445 | 10261940 | X49758D4 | Child | FALSE | WBTS 220KV LINE AT BATS | 39249.2507 | 39249.2708 | DAILY | 00012410 | SPIMAINT | BATS-HOTS LIne to commission HOTS No 1 Tie Bus | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024921839249.2645833333 | 10249218 |  | Parent | TRUE | NO.1 220KV BUS AT MLTS | 39249.2646 | 39249.7083 | REPDAILY | 00003014 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024923639249.2645833333 | 10249236 | 10249218 | Child | FALSE | 220KV SHUNT REACTOR CB BUS SIDE E/SW AT MLTS | 39249.2646 | 39249.7083 | REPDAILY | [12 empty] | 0
_1024924439249.2645833333 | 10249244 | 10249218 | Child | FALSE | NO.1 220KV BUS E/SW AT MLTS | 39249.2646 | 39249.7083 | REPDAILY | [12 empty] | 0
_1024926639249.2645833333 | 10249266 | 10249218 | Child | FALSE | A2 TRANS NO.1 BUS 220KV CB BUS SIDE E/SW AT MLTS | 39249.2646 | 39249.7083 | REPDAILY | [12 empty] | 0
_1024927039249.2645833333 | 10249270 | 10249218 | Child | FALSE | BATS NO.1 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT MLTS | 39249.2646 | 39249.7083 | REPDAILY | [12 empty] | 0
_1024928039249.2645833333 | 10249280 | 10249218 | Child | FALSE | A2 TRANS NO.1 BUS 220KV CB BUS SIDE ROI AT MLTS | 39249.2646 | 39249.7083 | REPDAILY | [12 empty] | 0
_1024928839249.2645833333 | 10249288 | 10249218 | Child | FALSE | 220KV SHUNT REACTOR CB BUS SIDE ROI AT MLTS | 39249.2646 | 39249.7083 | REPDAILY | [12 empty] | 0
_1024930139249.2645833333 | 10249301 | 10249218 | Child | FALSE | A1 TRANS NO.1 BUS 220KV CB BUS SIDE ROI AT MLTS | 39249.2646 | 39249.7083 | REPDAILY | [12 empty] | 0
_1024930339249.2645833333 | 10249303 | 10249218 | Child | FALSE | BATS NO.1 220KV LINE NO.1 BUS CB BUS SIDE ROI AT MLTS | 39249.2646 | 39249.7083 | REPDAILY | [12 empty] | 0
_1026074739249.2645833333 | 10260747 | 10249218 | Child | FALSE | A1 TRANS NO.1 BUS 220KV CB BUS SIDE E/SW AT MLTS | 39249.2646 | 39249.7083 | REPDAILY | [12 empty] | 0
_1026084239249.2645833333 | 10260842 | 10249218 | Child | FALSE | 220KV SHUNT REACTOR AT MLTS | 39249.2646 | 39249.7083 | REPDAILY | 00003011 | SPIMAINT | Perf calc 220kv shunt reactor, Bus outage at MLTS | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026084439249.2645833333 | 10260844 | 10249218 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT MLTS | 39249.2646 | 39249.7083 | REPDAILY | 00360001 | SPIMAINT | Rebate w/o No1 Cap Bk, Bus outage at MLTS | SPIPOWER |  |  | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026092739249.2888888889 | 10260927 |  | Parent | FALSE | NO.2 11/220KV TRANS W/PH AT MPS | 39249.2889 | 39249.3785 | DAILY | 00350229 | SPIMAINT | ADJUST WHITE PHASE 220KV BUSHING OIL LEVEL. | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026147839249.2930555556 | 10261478 |  | Parent | FALSE | EX - GTS NO.1 220KV LINE NO.3 BUS CB AT KTS | 39249.2931 | 39249.6076 | DAILY | [12 empty] | 0
_X49758D439249.2986111111 | X49758D4 |  | Parent | TRUE | BATS-BETS 220KV | 39249.2986 | 39249.7715 | DAILY | 00328505 | SPICAPX | Out W/O BATS -BETS Line for work at BETS | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49758D539249.2986111111 | X49758D5 | X49758D4 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39249.2986 | 39249.7715 | DAILY | 00016040 | SPICAPX | Perf calc W/O No2 Trans Grp outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026262839249.31875 | 10262628 |  | Parent | FALSE | SYN/COND AT BLTS | 39249.3187 | 39249.3972 | DAILY | 00002547 | FAULT | Syncon tripped when 220 KV Cap bank placed inserv | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758E339249.7715277778 | X49758E3 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39249.7715 | 39252.7063 | CONT | 00016040 | SPICAPX | Out W/O Comm'n Fut No2 Trans Grp 220kv CB & Prot | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51058A939250.2513888889 | Z51058A9 |  | Parent | FALSE | NO.2 66KV BUS AT ATS | 39250.2514 | 39250.6556 | DAILY | 00060169 | SPICAPX | connect busbar in place to form 1-2 66kv bus tie | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024921839250.2715277778 | 10249218 |  | Parent | TRUE | NO.1 220KV BUS AT MLTS | 39250.2715 | 39250.7083 | REPDAILY | 00003014 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024923639250.2715277778 | 10249236 | 10249218 | Child | FALSE | 220KV SHUNT REACTOR CB BUS SIDE E/SW AT MLTS | 39250.2715 | 39250.7083 | REPDAILY | [12 empty] | 0
_1024924439250.2715277778 | 10249244 | 10249218 | Child | FALSE | NO.1 220KV BUS E/SW AT MLTS | 39250.2715 | 39250.7083 | REPDAILY | [12 empty] | 0
_1024926639250.2715277778 | 10249266 | 10249218 | Child | FALSE | A2 TRANS NO.1 BUS 220KV CB BUS SIDE E/SW AT MLTS | 39250.2715 | 39250.7083 | REPDAILY | [12 empty] | 0
_1024927039250.2715277778 | 10249270 | 10249218 | Child | FALSE | BATS NO.1 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT MLTS | 39250.2715 | 39250.7083 | REPDAILY | [12 empty] | 0
_1024928039250.2715277778 | 10249280 | 10249218 | Child | FALSE | A2 TRANS NO.1 BUS 220KV CB BUS SIDE ROI AT MLTS | 39250.2715 | 39250.7083 | REPDAILY | [12 empty] | 0
_1024928839250.2715277778 | 10249288 | 10249218 | Child | FALSE | 220KV SHUNT REACTOR CB BUS SIDE ROI AT MLTS | 39250.2715 | 39250.7083 | REPDAILY | [12 empty] | 0
_1024930139250.2715277778 | 10249301 | 10249218 | Child | FALSE | A1 TRANS NO.1 BUS 220KV CB BUS SIDE ROI AT MLTS | 39250.2715 | 39250.7083 | REPDAILY | [12 empty] | 0
_1024930339250.2715277778 | 10249303 | 10249218 | Child | FALSE | BATS NO.1 220KV LINE NO.1 BUS CB BUS SIDE ROI AT MLTS | 39250.2715 | 39250.7083 | REPDAILY | [12 empty] | 0
_1026074739250.2715277778 | 10260747 | 10249218 | Child | FALSE | A1 TRANS NO.1 BUS 220KV CB BUS SIDE E/SW AT MLTS | 39250.2715 | 39250.7083 | REPDAILY | [12 empty] | 0
_1026084239250.2715277778 | 10260842 | 10249218 | Child | FALSE | 220KV SHUNT REACTOR AT MLTS | 39250.2715 | 39250.7083 | REPDAILY | 00003011 | SPIMAINT | Perf calc 220kv shunt reactor, Bus outage at MLTS | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026084439250.2715277778 | 10260844 | 10249218 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT MLTS | 39250.2715 | 39250.7083 | REPDAILY | 00360001 | SPIMAINT | Rebate w/o No1 Cap Bk, Bus outage at MLTS | SPIPOWER |  |  | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026121639250.2729166667 | 10261216 |  | Parent | FALSE | ROTS-RTS 4 220KV E | 39250.2729 | 39250.6403 | DAILY | 00022750 | SPIMAINT | Replace Insulators on RTS - ROTS 4 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258S839251.2763888889 | X43258S8 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39251.2764 | 39251.7312 | DAILY | 00337581 | SPICAPX | Replace No1 Trans Grp 220 kv S/D's | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49758E139251.2805555556 | X49758E1 |  | Parent | FALSE | BETS-KGTS 220KV NB | 39251.2806 | 39251.6444 | DAILY | 00026196 | SPICAPX | Out W/O BETS-KGTS Line for work on Line at BETS | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558A739251.2923611111 | X56558A7 |  | Parent | FALSE | NO.2 CSC NO.3 BUS CB AT ROTS | 39251.2924 | 39255.8979 | CONT | [12 empty] | 0
_X2A858U239252.25 | X2A858U2 |  | Parent | FALSE | NO.2 22KV BUS LINK CABLE CB AT BTS | 39252.25 | 39252.4014 | DAILY | [12 empty] | 0
_1024932039252.2944444444 | 10249320 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB BUS SIDE ROI AT MLTS | 39252.2944 | 39252.7236 | REPDAILY | [12 empty] | 0
_1024937339252.2965277778 | 10249373 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT FBTS | 39252.2965 | 39252.65 | DAILY | [12 empty] | 0
_Z50658B439252.3479166667 | Z50658B4 |  | Parent | FALSE | NO.6 66KV BUS AT HTS | 39252.3479 | 39252.6611 | DAILY | 00004460 | DB_AUG | Sub HT fdr,Future Sub M/MC-CRM-FTN fdr & No 6 Bus | SPIPOWER | Z506 | Z506 - (HTS) OPTIMISING 66KV CBS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758D939253.25 | X49758D9 |  | Parent | TRUE | BATS-BETS 220KV | 39253.25 | 39254.7243 | CONT | 00328505 | SPICAPX | Out W/O BATS -BETS Line for work on Line at BETS | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49758E039253.25 | X49758E0 | X49758D9 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39253.25 | 39254.7243 | CONT | 00016040 | SPICAPX | Perf calc No2 Trans Group | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026108539253.2916666667 | 10261085 |  | Parent | FALSE | H2 TRANS 220KV CB AT DDTS | 39253.2917 | 39253.6597 | REPDAILY | [12 empty] | 0
_1024936139253.2916666667 | 10249361 |  | Parent | FALSE | B1 220/66KV TRANS AT FBTS | 39253.2917 | 39254.6375 | DAILY | 00002726 | SPIMAINT | class 2 o/h of cb & o/h trans mech | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024932039253.2965277778 | 10249320 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB BUS SIDE ROI AT MLTS | 39253.2965 | 39253.6937 | REPDAILY | [12 empty] | 0
_1026124639253.3229166667 | 10261246 |  | Parent | FALSE | HPS 66KV LINE AT WOTS | 39253.3229 | 39253.6028 | DAILY | 00012055 | TRANSGRD | HPS Line CB | TRANSGRD |  |  | Circuits | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 3
_1026213239253.3770833333 | 10262132 |  | Parent | FALSE | SMTS NO.2 220KV LINE CB AT TTS | 39253.3771 | 39253.4014 | DAILY | [12 empty] | 0
_1026216639253.58125 | 10262166 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39253.5813 | 39253.6167 | DAILY | [12 empty] | 0
_1026142339253.6173611111 | 10261423 |  | Parent | FALSE | BETS LINE NO.2 BUS CB AT KGTS | 39253.6174 | 39253.6569 | DAILY | [12 empty] | 0
_Z53158W939254.2715277778 | Z53158W9 |  | Parent | FALSE | YPS NO.5 220KV LINE AT ROTS | 39254.2715 | 39254.6097 | DAILY | 00024008 | VEN_AUG | YPS No 5 220kv Line @ ROTS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024932039254.2895833333 | 10249320 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB BUS SIDE ROI AT MLTS | 39254.2896 | 39254.6521 | REPDAILY | [12 empty] | 0
_1024819639254.3111111111 | 10248196 |  | Parent | FALSE | ROTS NO.6 220KV LINE NO.2 BUS CB AT YPS | 39254.3111 | 39254.5847 | DAILY | [12 empty] | 0
_1026139139254.3527777778 | 10261391 | X38458S8 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39254.3528 | 39254.6438 | DAILY | 00003127 | SPICAPX | Perf calc B2 Trans during No2 66kv Bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458S839254.3527777778 | X38458S8 |  | Parent | TRUE | EX - NO.2 66KV BUS AT TGTS | 39254.3528 | 39254.6438 | DAILY | 00003133 | SPICAPX | Install new droppers to No2 66kv Bus VT Disc Sw | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025950239254.3777777778 | 10259502 |  | Parent | FALSE | JLA NO.1 220KV LINE CB CT R/PH AT TBTS | 39254.3778 | 39254.4056 | DAILY | [12 empty] | 0
_1025950439254.4194444444 | 10259504 |  | Parent | FALSE | JLA NO.2 220KV LINE CB CT R/PH AT TBTS | 39254.4194 | 39254.4458 | DAILY | [12 empty] | 0
_1026144639254.4666666667 | 10261446 |  | Parent | FALSE | EX - F 22KV FDR 189 CB AT BTS | 39254.4667 | 39266.6681 | DAILY | [12 empty] | 0
_1026262039254.5263888889 | 10262620 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT SMTS | 39254.5264 | 39254.6 | DAILY | 00026101 | FAULT | Unexplained Opening of H1 Transf 330kV CB | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X49758D739255.25625 | X49758D7 | X49758D6 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT BETS | 39255.2562 | 39255.2764 | DAILY | 00350819 | SPICAPX | Rebate W/O 2A cap bank. Prox for KGTS line work | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49758E939255.25625 | X49758E9 | X49758D6 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 39255.2562 | 39255.2764 | DAILY | 00016274 | SPICAPX | Rebate W/O 2B cap bank. Prox for KGTS line work | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026261939255.2618055556 | 10262619 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39255.2618 | 39255.2764 | DAILY | 00016040 | FAULT | Trans grp tripped on protection when 22 CB opened | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49658G639255.2722222222 | X49658G6 |  | Parent | TRUE | NO.2 66KV BUS AT HOTS | 39255.2722 | 39255.6236 | DAILY | 00006941 | SPICAPX | Upgrade droppers No2 Cap Bk CB to No2 66kv Bus | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X49658G739255.2722222222 | X49658G7 | X49658G6 | Child | FALSE | NO.2 66KV REACTOR AT HOTS | 39255.2722 | 39255.6236 | DAILY | 00357255 | SPICAPX | Rebate W/O No2 Reactor during No2 66 bus Outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49658G839255.2722222222 | X49658G8 | X49658G6 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 39255.2722 | 39255.6236 | DAILY | 00359897 | SPICAPX | Rebate W/O No2 Cap Bk during No2 66 bus Outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49658G939255.2722222222 | X49658G9 | X49658G6 | Child | FALSE | B3 220/66KV TRANS AT HOTS | 39255.2722 | 39255.6236 | DAILY | 00363102 | SPICAPX | perf calc B3 Trans during No2 66 bus Outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026144439255.29375 | 10261444 |  | Parent | FALSE | EX - F 22KV FDR 179 CB AT BTS | 39255.2937 | 39255.6389 | DAILY | [12 empty] | 0
_1026214439255.2979166667 | 10262144 |  | Parent | FALSE | NO.1 66KV BUS AT ATS | 39255.2979 | 39257.75 | DAILY | 00363714 | FAULT | repair earth recepticle on lvn fdr cb b/s isol | SPIPOWER |  |  | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158X039255.3152777778 | Z53158X0 |  | Parent | FALSE | NO.1 CSC NO.1 BUS CB AT ROTS | 39255.3153 | 39255.6028 | DAILY | [12 empty] | 0
_1024821139255.31875 | 10248211 |  | Parent | FALSE | W3 GEN TRANS NO.1 BUS 220KV CB AT YPS | 39255.3187 | 39255.5826 | DAILY | [12 empty] | 0
_1026406739255.3333333333 | 10264067 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT HOTS | 39255.3333 | 39309.4035 | CONT | [12 empty] | 0
_1024936439255.4409722222 | 10249364 |  | Parent | FALSE | B3 220/66KV TRANS AT FBTS | 39255.441 | 39255.5576 | DAILY | 00002727 | SPIMAINT | O/HAUL Transformer Div Mechanism (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026456739255.6243055556 | 10264567 | 10264067 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 39255.6243 | 39309.4035 | CONT | 00359897 | SPICAPX | HVS for No 2 Cap Bank Isolation pending Commission | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026239939255.6340277778 | 10262399 |  | Parent | FALSE | A2 515/220KV TRANS BANK AT ROTS | 39255.634 | 39263.6328 | CONT | 00362994 | FORCED | ROTS-A2 Trans de-energised(forced outage) | SPIPOWER |  |  | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 4 | Non prescribed asset
_1024943139256.2930555556 | 10249431 |  | Parent | FALSE | U1 TRANS-PAR 66KV CB AT BLTS | 39256.2931 | 39256.659 | DAILY | [12 empty] | 0
_1024879739256.2951388889 | 10248797 |  | Parent | FALSE | B1 220/66KV TRANS AT ERTS | 39256.2951 | 39256.584 | DAILY | 00004370 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026121939257.2833333333 | 10261219 |  | Parent | FALSE | ROTS-SVTS 1 220KV E | 39257.2833 | 39257.6813 | DAILY | 00022752 | SPIMAINT | Replace Insulators on ROTS - SVTS 1 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026240739257.3125 | 10262407 | Z62358A6 | Child | FALSE | MBTS-EPS 2 220KV N | 39257.3125 | 39257.5576 | DAILY | 00055381 | SW_NEM | EPS-MBTS No 2 Line out with TTS-EPS | NEMMCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1026240839257.3125 | 10262408 | Z62358A6 | Child | FALSE | MBTS-EPS 1 220KV N | 39257.3125 | 39257.5576 | DAILY | 00055380 | SW_NEM | EPS-MBTS No 1 Line out with TTS-EPS | NEMMCO | Z623 | Z623 - THE LAKES BOULEVARDE ROAD WORK | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_Z62358A639257.3125 | Z62358A6 |  | Parent | TRUE | EPS -TTS 2 220KV N | 39257.3125 | 39257.5576 | DAILY | 00328508 | 3RDPARTY | Out W/O EPS-TTS Line- Replace GW attachment T225 | SPIPOWER | Z623 | Z623 - THE LAKES BOULEVARDE ROAD WORK | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026240539257.3576388889 | 10262405 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39257.3576 | 39257.6368 | CONT | 00016040 | FAULT | BETS: No 2 Trans Group | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026164539258.2951388889 | 10261645 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39258.2951 | 39258.7528 | REPDAILY | 00022691 | DBPROX | GTS-PTH No 2 Line | HVCUST |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026239639258.3625 | 10262396 |  | Parent | FALSE | NO.4 UNIT 230/10.5KV TRANS AT JLGA | 39258.3625 | 39258.6507 | DAILY | 00009819 | SPIMAINT | SCAP: JLGS A4 Isol'd and Earthed. | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1026181239258.3930555556 | 10261812 | 10262006 | Child | FALSE | BATS NO.2 220KV LINE AT MLTS | 39258.3931 | 39258.6243 | DAILY | 00022969 | SPIMAINT | Rebate W/O BATS 2 Line during bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026200639258.3930555556 | 10262006 |  | Parent | TRUE | NO.2 220KV BUS AT MLTS | 39258.3931 | 39258.6243 | DAILY | 00003015 | SPIMAINT | Out W/O No2 220kV BUS to disconnect bay H from J | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026180639258.6277777778 | 10261806 |  | Parent | TRUE | EX - NO.2 220KV CAPACITOR BANK CB BUS SIDE ROI AT MLTS | 39258.6278 | 39270.3021 | CONT | [12 empty] | 0
_1026181039258.6277777778 | 10261810 | 10261806 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT MLTS | 39258.6278 | 39270.3021 | DAILY | 00350825 | FORCED | Rebate W/O No2 220kV Cap bank during bus outage | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_Z53158V639259.2638888889 | Z53158V6 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 39259.2639 | 39260.6465 | CONT | 00004778 | VEN_AUG | MTS No1 & A1Trans 220KV LINES & No 4 BUS outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158V739259.2638888889 | Z53158V7 | Z53158V6 | Child | FALSE | NO.4 220KV BUS AT ROTS | 39259.2639 | 39260.6465 | CONT | 00329012 | VEN_AUG | Remove bipods on No 2 bus CB & No 4 BUS outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158V839259.2638888889 | Z53158V8 | Z53158V6 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39259.2639 | 39260.6465 | CONT | 00112418 | VEN_AUG | Cap Bank Rebate For Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z53158V939259.2638888889 | Z53158V9 | Z53158V6 | Child | FALSE | MTS NO.1 220KV LINE AT ROTS | 39259.2639 | 39260.6465 | CONT | 00350667 | VEN_AUG | Line outge Rebate For Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158W039259.2638888889 | Z53158W0 | Z53158V6 | Child | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39259.2639 | 39260.6465 | CONT | 00354002 | VEN_AUG | Line outge Rebate For Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1026123139259.2791666667 | 10261231 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT SMTS | 39259.2792 | 39262.4542 | CONT | [12 empty] | 0
_1025016139259.29375 | 10250161 |  | Parent | FALSE | DDTS NO.1 330KV LINE NO.1 BUS CB AT SMTS | 39259.2937 | 39259.5854 | CONT | [12 empty] | 0
_1026164539259.3006944444 | 10261645 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39259.3007 | 39259.4535 | REPDAILY | 00022691 | DBPROX | GTS-PTH No 2 Line | HVCUST |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026236739259.3368055556 | 10262367 |  | Parent | FALSE | APD NO.2/MLTS NO.2 LINE 500KV CB AT HYTS | 39259.3368 | 39259.5514 | DAILY | [12 empty] | 0
_X56558B639259.3680555556 | X56558B6 |  | Parent | FALSE | B1 TRANS 220KV CB AT GTS | 39259.3681 | 39267.4181 | CONT | [12 empty] | 0
_1025057739259.375 | 10250577 |  | Parent | FALSE | STANDBY DIESEL GENERATOR AT DDTS | 39259.375 | 39259.4792 | DAILY | [12 empty] | 0
_1026255439259.3944444444 | 10262554 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 39259.3944 | 39263.3333 | CONT | 00016424 | GENCO | Isolation for Genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025057339259.4941203704 | 10250573 |  | Parent | FALSE | STANDBY DIESEL GENERATOR AT MBTS | 39259.4941 | 39259.5798 | DAILY | [12 empty] | 0
_1026261539260.0763888889 | 10262615 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39260.0764 | 39260.1424 | DAILY | 00017270 | FAULT | Prot Trip of SVC at KGTS | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024820839260.3111111111 | 10248208 | 10248233 | Child | FALSE | W2 GEN TRANS NO.2 BUS 220KV CB AT YPS | 39260.3111 | 39262.6257 | CONT | [12 empty] | 0
_1024823139260.3111111111 | 10248231 | 10248233 | Child | FALSE | W2 GEN TRANS 220KV CB LINE SIDE E/SW AT YPS | 39260.3111 | 39262.6257 | CONT | [12 empty] | 0
_1024823339260.3111111111 | 10248233 |  | Parent | TRUE | W2 GEN TRANS 220KV LINE E/SW AT YPS | 39260.3111 | 39262.6257 | CONT | [12 empty] | 0
_1024827539260.3111111111 | 10248275 | 10248233 | Child | FALSE | W2 GEN TRANS NO.2 BUS 220KV CB LINE SIDE ISOL AT YPS | 39260.3111 | 39262.6257 | CONT | [12 empty] | 0
_1026141839260.3680555556 | 10261418 |  | Parent | FALSE | EX - F 22KV FDR 182 CB AT BTS | 39260.3681 | 39263.6139 | DAILY | [12 empty] | 0
_1026131439260.3888888889 | 10261314 |  | Parent | FALSE | KTS -BLTS 220KV WY | 39260.3889 | 39260.6229 | DAILY | 00022716 | SPIMAINT | Change insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026164739261.2993055556 | 10261647 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 39261.2993 | 39261.6306 | REPDAILY | 00022690 | DBPROX | GTS-PTH No 1 220kv Line | HVCUST |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026130939261.3131944445 | 10261309 |  | Parent | FALSE | TTS -BTS 3 220KV WT | 39261.3132 | 39261.5819 | DAILY | 00023086 | SPIMAINT | Change insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558B739261.3270833333 | X56558B7 |  | Parent | FALSE | W3 GEN TRANS NO.2 BUS 220KV CB AT YPS | 39261.3271 | 39261.5014 | DAILY | [12 empty] | 0
_1026236939261.3381944444 | 10262369 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39261.3382 | 39261.3826 | DAILY | 00319998 | APDALCOA | APD Work-APD-HYTS No 1 Line de-energised | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z51058B839261.3541666667 | Z51058B8 |  | Parent | FALSE | BLTS 66KV LINE CB AT ATS | 39261.3542 | 39311.4131 | CONT | [12 empty] | 0
_1026270739262.2979166667 | 10262707 |  | Parent | FALSE | SYN/COND AT TSTS | 39262.2979 | 39262.5806 | DAILY | 00007626 | FAULT | TSTS Syn Cond tripped | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026164739262.2979166667 | 10261647 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 39262.2979 | 39262.6604 | REPDAILY | 00022690 | DBPROX | GTS-PTH No 1 220kv Line | HVCUST |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458T239262.3805555556 | X38458T2 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 39262.3806 | 39262.5493 | REPDAILY | 00003131 | SPICAPX | Change No 2 220kV bus to Alumin & remove bi-pods | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458T339262.3805555556 | X38458T3 | X38458T2 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39262.3806 | 39262.5493 | REPDAILY | 00363297 | SPICAPX | Perf calc B1 Trans while No2 220kv Bus is out | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026254939262.4506944444 | 10262549 |  | Parent | FALSE | VR VICTORIA PARK 22KV FDR 180 CB (CITIPOWER EQPT) AT BTS | 39262.4507 | 39267.75 | DAILY | [12 empty] | 0
_1026271939262.5694444444 | 10262719 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 39262.5694 | 39262.6451 | CONT | 00060938 | APDALCOA | HYTS-APD No2 Line De-energised for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025165239263.2916666667 | 10251652 |  | Parent | FALSE | B3 220/66KV TRANS AT ERTS | 39263.2917 | 39264.6667 | CONT | 00004371 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026131539263.29375 | 10261315 |  | Parent | FALSE | NO.2B 220KV BUS AT BLTS | 39263.2937 | 39263.6597 | DAILY | 00002643 | SPIMAINT | Change insulators | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026275139263.4340277778 | 10262751 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 39263.434 | 39264.7117 | CONT | 00016424 | GENCO | YWPS No2 Gen Trans 220KV Line Isolated for YWPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026272839263.6284722222 | 10262728 |  | Parent | FALSE | EX - VR RUSHALL 22KV FDR 177 CB AT BTS | 39263.6285 | 39297.6069 | DAILY | [12 empty] | 0
_1026275239263.7611111111 | 10262752 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39263.7611 | 39264.9444 | CONT | 00356084 | GENCO | Gen 6 SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026122139264.2736111111 | 10261221 |  | Parent | FALSE | ROTS-SVTS 2 220KV E | 39264.2736 | 39264.6875 | DAILY | 00022756 | SPIMAINT | Replace Insulators on ROTS - SVTS 2 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024857639264.2916666667 | 10248576 |  | Parent | FALSE | L1 220/22KV TRANS AT RTS | 39264.2917 | 39264.6271 | DAILY | 00007330 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026131039264.3020833333 | 10261310 |  | Parent | FALSE | KTS -ATS 220KV WY | 39264.3021 | 39264.6743 | DAILY | 00074402 | SPIMAINT | Change insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858H239265.2465277778 | X49858H2 |  | Parent | FALSE | DPS 220KV LINE AT MBTS | 39265.2465 | 39274.2083 | CONT | 00011754 | SPICAPX | Rebate W/O DPS Line outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458T239265.25625 | X38458T2 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 39265.2562 | 39265.7063 | REPDAILY | 00003131 | SPICAPX | Change No 2 220kV bus to Alumin & remove bi-pods | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458T339265.25625 | X38458T3 | X38458T2 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39265.2562 | 39265.7063 | REPDAILY | 00363297 | SPICAPX | Perf calc B1 Trans while No2 220kv Bus is out | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158Y139265.2715277778 | Z53158Y1 |  | Parent | FALSE | ERTS NO.1 220KV LINE AT ROTS | 39265.2715 | 39265.7222 | DAILY | 00350666 | VEN_AUG | Line Outage for proximety Reasons at ROTS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026204139265.2923611111 | 10262041 |  | Parent | TRUE | SVC TRANS AT HOTS | 39265.2924 | 39266.7757 | CONT | 00006926 | SPIMAINT | Condition Sup Monitoring Country Trans 2day North | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1026227739265.2923611111 | 10262277 | 10262041 | Child | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39265.2924 | 39266.7757 | CONT | 00019243 | SPIMAINT | Rebate W/O for SVC during SVC Trans Outage | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025019339265.29375 | 10250193 |  | Parent | FALSE | DDTS NO.2 330KV LINE NO.2 BUS CB AT SMTS | 39265.2937 | 39265.5806 | CONT | [12 empty] | 0
_1026267839265.2965277778 | 10262678 |  | Parent | FALSE | B1 TRANS 66KV CB AT WMTS | 39265.2965 | 39265.6583 | DAILY | [12 empty] | 0
_X43258T639265.3055555556 | X43258T6 |  | Parent | TRUE | R2 220/66/22KV TRANS GROUP AT RCTS | 39265.3056 | 39267.5854 | CONT | 00337584 | SPICAPX | C'over old No2 Trans Grp prot to new Prot circuits | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258T739265.3055555556 | X43258T7 | X43258T6 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39265.3056 | 39267.5854 | CONT | 00337584 | SPICAPX | Perf Calc No2 Trans Grp for prot changeover outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026130739265.3104166667 | 10261307 |  | Parent | FALSE | KTS -WMTS 2 220KV WT | 39265.3104 | 39265.6632 | REPDAILY | 00022719 | SPIMAINT | Change insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026091439265.3131944445 | 10260914 |  | Parent | FALSE | C 66/11KV S/S TRANS 66KV FDR NO.2 BUS CB AT LY | 39265.3132 | 39265.4069 | DAILY | [12 empty] | 0
_1024849439265.4145833333 | 10248494 |  | Parent | FALSE | SYN/COND AT TSTS | 39265.4146 | 39269.5042 | CONT | 00007626 | SPIMAINT | Annual O/HAUL - TSTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026277739265.5 | 10262777 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39265.5 | 39267.7063 | CONT | 00356084 | GENCO | SCAP:HWPS No6 Gen Tran Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458T239266.2597222222 | X38458T2 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 39266.2597 | 39266.6528 | REPDAILY | 00003131 | SPICAPX | Change No 2 220kV bus to Alumin & remove bi-pods | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458T339266.2597222222 | X38458T3 | X38458T2 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39266.2597 | 39266.6528 | REPDAILY | 00363297 | SPICAPX | Perf calc B1 Trans while No2 220kv Bus is out | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158Y239266.26875 | Z53158Y2 |  | Parent | FALSE | NO.2 220KV BUS AT ROTS | 39266.2688 | 39266.7917 | DAILY | 00004778 | VEN_AUG | Install Future ERTS Line 1 No2 Bus CB ROI | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758E639266.2923611111 | X49758E6 |  | Parent | FALSE | BETS-FVTS-SHTS 220KV NB | 39266.2924 | 39266.4931 | DAILY | 00026225 | SPICAPX | Out W/O BETS-FVTS-SHTS Line remove bridges | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026268039266.29375 | 10262680 |  | Parent | FALSE | B2 TRANS 66KV CB AT WMTS | 39266.2937 | 39266.6729 | DAILY | [12 empty] | 0
_1026130739266.3152777778 | 10261307 |  | Parent | FALSE | KTS -WMTS 2 220KV WT | 39266.3153 | 39266.6667 | REPDAILY | 00022719 | SPIMAINT | Change insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49758E739266.4930555556 | X49758E7 |  | Parent | FALSE | BETS-FVTS-SHTS 220KV NB | 39266.4931 | 39269.2944 | CONT | 00026225 | SPICAPX | Out W/O BETS-FVTS section-work on line and at BETS | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026384239266.625 | 10263842 |  | Parent | FALSE | LNGS NO.2 GEN TRANS 220KV CB AT ATS | 39266.625 | 39296.6667 | CONT | [12 empty] | 0
_X38458T239267.2590277778 | X38458T2 |  | Parent | TRUE | EX - NO.2 220KV BUS AT TGTS | 39267.259 | 39267.6528 | REPDAILY | 00003131 | SPICAPX | Change No 2 220kV bus to Alumin & remove bi-pods | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X38458T339267.2590277778 | X38458T3 | X38458T2 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39267.259 | 39267.6528 | REPDAILY | 00363297 | SPICAPX | Perf calc B1 Trans while No2 220kv Bus is out | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158Y439267.2722222222 | Z53158Y4 | Z53158Y5 | Child | FALSE | YPS NO.5 220KV LINE AT ROTS | 39267.2722 | 39268.7417 | DAILY | 00024008 | VEN_AUG | Rebate Line outage YPS 5 | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158Y539267.2722222222 | Z53158Y5 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39267.2722 | 39268.7417 | CONT | 00004776 | VEN_AUG | YPS 5 line & No1 220kv Bus | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158Y639267.2722222222 | Z53158Y6 | Z53158Y5 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39267.2722 | 39268.7417 | DAILY | 00354024 | VEN_AUG | Rebate Cap Bank for Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_Z53158Y839267.2722222222 | Z53158Y8 | Z53158Y5 | Child | FALSE | RTS NO.1 220KV LINE AT ROTS | 39267.2722 | 39268.7417 | CONT | 00023111 | VEN_AUG | Line Rebate | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026130739267.2930555556 | 10261307 |  | Parent | FALSE | KTS -WMTS 2 220KV WT | 39267.2931 | 39267.666 | REPDAILY | 00022719 | SPIMAINT | Change insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51058B539267.2972222222 | Z51058B5 |  | Parent | FALSE | B3 TRANS 220KV BUS AT ATS | 39267.2972 | 39267.6188 | DAILY | 00360125 | SPICAPX | excavate foundations under bus for fut b4 trans | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X56558B239267.4180555556 | X56558B2 |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 39267.4181 | 39268.3785 | DAILY | 00002828 | SPICAPX | Out W/O No1 Trans to complete 1B 220 CB CT replace | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49658E239267.5520833333 | X49658E2 |  | Parent | FALSE | NO.1 66KV BUS AT HOTS | 39267.5521 | 39267.6104 | DAILY | 00006940 | SPICAPX | Out W/O No1 66kV Bus de-energ for B2 TR ph out | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025020139268.29375 | 10250201 |  | Parent | FALSE | DDTS NO.1 330KV LINE NO.2 BUS CB AT SMTS | 39268.2937 | 39269.5979 | CONT | [12 empty] | 0
_1026268239268.3027777778 | 10262682 |  | Parent | FALSE | B3 TRANS 66KV CB AT WMTS | 39268.3028 | 39268.6306 | DAILY | [12 empty] | 0
_1026205439268.3326388889 | 10262054 |  | Parent | FALSE | GTS NO.1 220KV LINE NO.2 BUS CB BUS SIDE ROI AT MLTS | 39268.3326 | 39268.4792 | DAILY | [12 empty] | 0
_1026288539268.3479166667 | 10262885 |  | Parent | FALSE | B3 220/66KV TRANS AT SVTS | 39268.3479 | 39268.5813 | DAILY | 00004851 | SPIMAINT | Repair Motor on Trans De Energise Trans | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026205339268.4819444444 | 10262053 |  | Parent | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB BUS SIDE ROI AT MLTS | 39268.4819 | 39268.5069 | DAILY | [12 empty] | 0
_X49658E339268.5715277778 | X49658E3 |  | Parent | FALSE | B2 220/66KV TRANS AT HOTS | 39268.5715 | 39268.5847 | DAILY | 00363103 | SPICAPX | Out W/O Fut B2 commiss in to service | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49758E839269.2944444444 | X49758E8 |  | Parent | FALSE | BETS-FVTS-SHTS 220KV NB | 39269.2944 | 39269.5181 | DAILY | 00026225 | SPICAPX | Out W/O BETS-FVTS-SHTS Line restore bridges | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49658H139269.3125 | X49658H1 |  | Parent | TRUE | EX - NO.1 S/S TRANS AT HOTS | 39269.3125 | 39269.6222 | DAILY | 00006933 | SPICAPX | Install new Station Service Transformer | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_X49658H239269.3125 | X49658H2 | X49658H1 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39269.3125 | 39269.6222 | DAILY | 00337581 | SPICAPX | Perf calc No1 Trans Outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026401339269.4333333333 | 10264013 |  | Parent | FALSE | EX - FVTS/SHTS 220KV LINE NO.2 BUS CB AT BETS | 39269.4333 | 39310.7063 | CONT | [12 empty] | 0
_1026389139269.5215277778 | 10263891 |  | Parent | FALSE | TGTS 220KV LINE AT BATS | 39269.5215 | 39269.5278 | DAILY | 00012435 | FAULT | Rebate for TGTS - BATS trip reclose one end only | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026317239269.8416666667 | 10263172 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39269.8417 | 39270.5153 | CONT | 00356082 | GENCO | HWPS No4 Gen Trans Isolations & Earths for SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026389439270.2208333333 | 10263894 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39270.2208 | 39270.7326 | DAILY | 00011755 | FORCED | Rebate for OPGW drop | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158W639270.2763888889 | Z53158W6 |  | Parent | TRUE | EX - NO.4 220KV BUS AT ERTS | 39270.2764 | 39271.6049 | CONT | 00004380 | VEN_AUG | Bus outge No4 Bus & ROTS No 2 Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158W739270.2763888889 | Z53158W7 | Z53158W6 | Child | FALSE | B4 220/66KV TRANS AT ERTS | 39270.2764 | 39271.6049 | CONT | 00004372 | VEN_AUG | rebate bus outage trans | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158W839270.2763888889 | Z53158W8 | Z53158W6 | Child | FALSE | ROTS NO.2 220KV LINE AT ERTS | 39270.2764 | 39271.6049 | CONT | 00012288 | VEN_AUG | rebate bus outage Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49658H339270.2916666667 | X49658H3 |  | Parent | TRUE | B3 220/66KV TRANS AT HOTS | 39270.2917 | 39273.6868 | CONT | 00363102 | SPICAPX | Install new No2 Station Service Transformer | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49658H439270.2916666667 | X49658H4 | X49658H3 | Child | FALSE | B3 220/66KV TRANS AT HOTS | 39270.2917 | 39273.6868 | CONT | 00363102 | SPICAPX | perf calc B3 Trans during Outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026200939270.3020833333 | 10262009 |  | Parent | FALSE | NO.2 220KV BUS AT MLTS | 39270.3021 | 39270.6424 | DAILY | 00003015 | SPIMAINT | Out W/O No2 220kV BUS to reconnect bay H to J | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026259639271.2694444444 | 10262596 |  | Parent | FALSE | ROTS-SVTS 1 220KV E | 39271.2694 | 39271.5931 | DAILY | 00022752 | SPIMAINT | Replace Insulators on ROTS - SVTS 1 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258U039272.275 | X43258U0 |  | Parent | FALSE | BSS 220KV LINE AT RCTS | 39272.275 | 39272.6215 | DAILY | 00016966 | SPICAPX | Replace the BSS line CVT W Ph connections | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026318139272.2847222222 | 10263181 |  | Parent | FALSE | NO.3 GEN TRANS NO.2 BUS 220KV CB AT HWPS | 39272.2847 | 39273.75 | CONT | [12 empty] | 0
_X51958A139272.3583333333 | X51958A1 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 39272.3583 | 39272.6493 | DAILY | [12 empty] | 0
_1026208939273.2972222222 | 10262089 |  | Parent | FALSE | NO.1 66KV BUS VT AT TSTS | 39273.2972 | 39273.5903 | DAILY | [12 empty] | 0
_1024957939273.2972222222 | 10249579 |  | Parent | FALSE | EX - BLTS 220KV LINE NO.1 BUS CB AT KTS | 39273.2972 | 39274.6153 | CONT | [12 empty] | 0
_X51958A239273.2986111111 | X51958A2 |  | Parent | FALSE | JINDERA 330KV LINE NO.1 BUS CB AT WOTS | 39273.2986 | 39273.4306 | DAILY | [12 empty] | 0
_1026130039273.3055555556 | 10261300 |  | Parent | FALSE | KTS -WMTS 1 220KV WT | 39273.3056 | 39273.6549 | REPDAILY | 00022718 | SPIMAINT | Insulator replacement | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V62258B239273.3104166667 | V62258B2 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.2 BUS CB AT SMTS | 39273.3104 | 39276.6375 | CONT | [12 empty] | 0
_1026151039273.3465277778 | 10261510 |  | Parent | FALSE | HOTS-RCTS 220KV | 39273.3465 | 39273.709 | REPDAILY | 00328509 | SPIMAINT | Replace Insulators at Tower 54 B ph | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458U639273.4013888889 | X38458U6 |  | Parent | FALSE | NO.1 66KV BUS VT R/PH AT TGTS | 39273.4014 | 39273.6465 | DAILY | [12 empty] | 0
_X51958A539273.4965277778 | X51958A5 |  | Parent | FALSE | NO.2 330KV CAPACITOR BANK AT WOTS | 39273.4965 | 39273.6076 | DAILY | 00354001 | SPICAPX | Out W/O No2 330kV Cap BK SCIMS cutover | SPIPOWER | X519 | X519 - RTU/SCIMS WORK 2005-2008 | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_X49858G739274.2083333333 | X49858G7 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MBTS | 39274.2083 | 39274.7458 | DAILY | 00004002 | SPICAPX | Install bipods to Fut DPS Line CB Bus Side ROI | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49858G839274.2083333333 | X49858G8 | X49858G7 | Child | FALSE | DPS 220KV LINE AT MBTS | 39274.2083 | 39274.7458 | DAILY | 00011754 | SPICAPX | Rebate W/O DPS Line during No2 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858G939274.2083333333 | X49858G9 | X49858G7 | Child | FALSE | EX - DDTS NO.1 220KV LINE AT MBTS | 39274.2083 | 39274.7458 | CONT | 00011748 | SPICAPX | Rebate W/O DDTS1 Line during No2 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858H039274.2083333333 | X49858H0 | X49858G7 | Child | FALSE | EX - EPS NO.1 220KV LINE AT MBTS | 39274.2083 | 39274.7458 | DAILY | 00011751 | SPICAPX | Rebate W/O EPS #1 Line, No2 220kv Bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X43258U339274.2861111111 | X43258U3 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39274.2861 | 39275.6639 | CONT | 00359891 | SPICAPX | C'over & commission No1 Cap Bk Prot on P9,P50,P83 | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026208139274.2951388889 | 10262081 |  | Parent | FALSE | NO.1 66KV BUS VT AT RWTS | 39274.2951 | 39274.6792 | DAILY | [12 empty] | 0
_Z51058B039274.3013888889 | Z51058B0 |  | Parent | FALSE | NO.3 66KV BUS AT ATS | 39274.3014 | 39274.8785 | DAILY | 00352210 | SPICAPX | commission work associated with no.3 66kv bus | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026130039274.3048611111 | 10261300 |  | Parent | FALSE | KTS -WMTS 1 220KV WT | 39274.3049 | 39274.6597 | REPDAILY | 00022718 | SPIMAINT | Insulator replacement | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026151039274.3138888889 | 10261510 |  | Parent | FALSE | HOTS-RCTS 220KV | 39274.3139 | 39274.6882 | REPDAILY | 00328509 | SPIMAINT | Replace Insulators at Tower 54 B ph | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X51958A339274.3270833333 | X51958A3 |  | Parent | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 39274.3271 | 39274.6153 | DAILY | 00004036 | SPICAPX | Out W/O No1 Trans, itsROI & CB's SCIMS cutover | SPIPOWER | X519 | X519 - RTU/SCIMS WORK 2005-2008 | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458U139274.3777777778 | X38458U1 |  | Parent | TRUE | B2 220/66KV TRANS AT TGTS | 39274.3778 | 39274.6854 | DAILY | 00003127 | SPICAPX | Nemmco Compliance tests on B2 Transf,CB's & CT's | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458U239274.3777777778 | X38458U2 | X38458U1 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39274.3778 | 39274.6854 | DAILY | 00003127 | SPICAPX | Perf Calc on B2 Transformer | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026286539274.3854166667 | 10262865 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 39274.3854 | 39276.5771 | CONT | [12 empty] | 0
_1026328039275.2083333333 | 10263280 |  | Parent | FALSE | NO.7 GEN TRANS 220KV CB AT HWPS | 39275.2083 | 39277.9722 | CONT | [12 empty] | 0
_1024860939275.3013888889 | 10248609 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT HOTS | 39275.3014 | 39275.7208 | DAILY | [12 empty] | 0
_1026130039275.30625 | 10261300 |  | Parent | FALSE | KTS -WMTS 1 220KV WT | 39275.3063 | 39275.6479 | REPDAILY | 00022718 | SPIMAINT | Insulator replacement | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026151039275.3152777778 | 10261510 |  | Parent | FALSE | HOTS-RCTS 220KV | 39275.3153 | 39275.6403 | REPDAILY | 00328509 | SPIMAINT | Replace Insulators at Tower 54 B ph | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026268439275.3180555556 | 10262684 |  | Parent | FALSE | L1 220/22KV TRANS NO.1 BUS 22KV VT AT WMTS | 39275.3181 | 39275.5236 | DAILY | [12 empty] | 0
_X51958A439275.3208333333 | X51958A4 |  | Parent | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 39275.3208 | 39275.4944 | DAILY | 00004037 | SPICAPX | Out W/O No2 Trans, its & ROI & CB's SCIMS cutover | SPIPOWER | X519 | X519 - RTU/SCIMS WORK 2005-2008 | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026206439275.3215277778 | 10262064 |  | Parent | TRUE | DMA NO.1 66KV FDR CB BUS SIDE ISOL AT TBTS | 39275.3215 | 39275.5826 | DAILY | [12 empty] | 0
_1026261639275.3215277778 | 10262616 | 10262064 | Child | FALSE | B1 220/66KV TRANS AT TBTS | 39275.3215 | 39275.5826 | DAILY | 00004901 | SPIMAINT | Trans Rebate for bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026261739275.3215277778 | 10262617 | 10262064 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT TBTS | 39275.3215 | 39275.5826 | DAILY | 00351938 | SPIMAINT | Cap Bank Rebate for bus outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_Z51058C039275.4055555556 | Z51058C0 |  | Parent | FALSE | WBE 66KV FDR CB AT ATS | 39275.4056 | 39421.375 | CONT | [12 empty] | 0
_Z51058B939275.4354166667 | Z51058B9 |  | Parent | FALSE | B4 220/66KV TRANS AT ATS | 39275.4354 | 39348.5521 | CONT | 00363708 | SPICAPX | complete work before trans commissioning | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_Z51058B639275.4763888889 | Z51058B6 |  | Parent | FALSE | LV NO.1 66KV FDR AT ATS | 39275.4764 | 39288.7875 | CONT | 00363729 | SPICAPX | primary connections between fdr pole and isols | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Circuits | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026268539275.5236111111 | 10262685 |  | Parent | FALSE | L1 220/22KV TRANS NO.2 BUS 22KV VT AT WMTS | 39275.5236 | 39275.6549 | DAILY | [12 empty] | 0
_1026329739275.5638888889 | 10263297 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39275.5639 | 39275.5722 | DAILY | 00017270 | FAULT | Loss of KGTS SVC during fault investigation | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258U739276.2666666667 | X43258U7 |  | Parent | TRUE | NO.1 66KV REACTOR AT RCTS | 39276.2667 | 39276.6139 | DAILY | 00016895 | SPICAPX | Modify No1 66kv Reactor conn's and 1B Trans conn's | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258U839276.2666666667 | X43258U8 | X43258U7 | Child | FALSE | NO.1B 220/66/22KV TRANS AT RCTS | 39276.2667 | 39276.6139 | DAILY | 00016758 | SPICAPX | Perf Calc for 1B Transformer outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026286039276.3333333333 | 10262860 |  | Parent | FALSE | JLTS NO.4 220KV LINE NO.4 BUS CB AT HWPS | 39276.3333 | 39276.5736 | DAILY | [12 empty] | 0
_1026331339277.2402777778 | 10263313 |  | Parent | FALSE | TSTS LINE/YPS NO.6 LINE 220KV CB AT ROTS | 39277.2403 | 39277.334 | DAILY | [12 empty] | 0
_Z53158X239277.2854166667 | Z53158X2 |  | Parent | TRUE | EX - NO.1 220KV BUS AT ERTS | 39277.2854 | 39279.6222 | CONT | 00004378 | VEN_AUG | No1 Trans, ERTS-ROTS 1 Line & No 1 220kv BUS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158X339277.2854166667 | Z53158X3 | Z53158X2 | Child | FALSE | B1 220/66KV TRANS AT ERTS | 39277.2854 | 39279.6222 | CONT | 00004370 | VEN_AUG | Trans Outage rebate | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158X439277.2854166667 | Z53158X4 | Z53158X2 | Child | FALSE | ROTS NO.1 220KV LINE AT ERTS | 39277.2854 | 39279.6222 | CONT | 00012289 | VEN_AUG | Line Outage rebate | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024755239277.29375 | 10247552 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE AT KTS | 39277.2937 | 39277.6576 | REPDAILY | 00015986 | SPIMAINT | O/Haul - 220kV Line (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026334139277.6173611111 | 10263341 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 39277.6174 | 39278.9931 | CONT | 00356081 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X46158P639278.2708333333 | X46158P6 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 39278.2708 | 39308.4688 | CONT | 00331109 | SPICAPX | Out W/O No1 66kV Cap Bk prot & control mods | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024755239278.2743055556 | 10247552 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE AT KTS | 39278.2743 | 39278.7528 | REPDAILY | 00015986 | SPIMAINT | O/Haul - 220kV Line (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026334639278.5729166667 | 10263346 |  | Parent | FALSE | TSTS LINE/YPS NO.6 LINE 220KV CB AT ROTS | 39278.5729 | 39279.4194 | CONT | [12 empty] | 0
_1024944839279.2680555556 | 10249448 |  | Parent | FALSE | SYN/COND AT BLTS | 39279.2681 | 39283.6507 | CONT | 00002547 | SPIMAINT | Annual O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026203439279.3006944444 | 10262034 |  | Parent | TRUE | SVC TRANS AT KGTS | 39279.3007 | 39280.7083 | CONT | 00017158 | SPIMAINT | Condition Sup Monitoring Country Trans 2day North | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1026227939279.3006944444 | 10262279 | 10262034 | Child | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39279.3007 | 39280.7083 | CONT | 00017270 | SPIMAINT | Rebate W/O for SCV during SVC Trans Outage | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X38458T139279.3111111111 | X38458T1 |  | Parent | FALSE | MLTS 220KV LINE AT TGTS | 39279.3111 | 39279.7493 | DAILY | 00023131 | SPICAPX | Replace CVT sec cables & palms on L/T droppers | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024838539279.3138888889 | 10248385 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.2 BUS CB AT HWTS | 39279.3139 | 39279.5993 | DAILY | [12 empty] | 0
_X2A858U839279.4111111111 | X2A858U8 |  | Parent | FALSE | NO.2 22KV BUS LINK CABLE CB AT BTS | 39279.4111 | 39279.7201 | DAILY | [12 empty] | 0
_1026335039279.4194444444 | 10263350 |  | Parent | FALSE | TSTS LINE/YPS NO.6 LINE 220KV CB AT ROTS | 39279.4194 | 39283.6819 | CONT | [12 empty] | 0
_X38458U339279.6326388889 | X38458U3 |  | Parent | FALSE | EX - 1-2 66KV BUS TIE CB AT TGTS | 39279.6326 | 39279.7611 | DAILY | [12 empty] | 0
_1026327539279.6951388889 | 10263275 |  | Parent | FALSE | EX - C 22KV FDR 186 CB AT BTS | 39279.6951 | 39281.6806 | DAILY | [12 empty] | 0
_1026327639279.6951388889 | 10263276 |  | Parent | FALSE | EX - C 22KV FDR 196 CB AT BTS | 39279.6951 | 39283.5694 | DAILY | [12 empty] | 0
_X49858I139280.2423611111 | X49858I1 | X49858I0 | Child | FALSE | EX - EPS NO.1 220KV LINE AT MBTS | 39280.2424 | 39280.3104 | REPDAILY | 00011751 | SPICAPX | Rebate W/O EPS #1 Line, No1 220kv Bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49858I239280.2423611111 | X49858I2 | X49858I0 | Child | FALSE | EX - DDTS NO.1 220KV LINE AT MBTS | 39280.2424 | 39280.3104 | REPDAILY | 00011748 | SPICAPX | Rebate W/O DDTS1 Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858I439280.2423611111 | X49858I4 | X49858I0 | Child | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39280.2424 | 39280.3104 | REPDAILY | 00011755 | SPICAPX | Rebate W/O MKPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858I539280.2423611111 | X49858I5 | X49858I0 | Child | FALSE | B2 220/66KV TRANS AT MBTS | 39280.2424 | 39280.3104 | REPDAILY | 00362372 | SPICAPX | Perf calc, B2 Trans during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49858I639280.2423611111 | X49858I6 | X49858I0 | Child | FALSE | MBTS-EPS 2 220KV N | 39280.2424 | 39280.3104 | REPDAILY | 00055381 | SPICAPX | Rebate W/O EPS #2 Line, No1 220kv Bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49858I739280.2423611111 | X49858I7 | X49858I0 | Child | FALSE | WKPS 220KV LINE AT MBTS | 39280.2424 | 39280.3104 | REPDAILY | 00011756 | SPICAPX | Rebate W/O WKPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858I839280.2423611111 | X49858I8 | X49858I0 | Child | FALSE | EX - DDTS NO.2 220KV LINE AT MBTS | 39280.2424 | 39280.3104 | REPDAILY | 00011750 | SPICAPX | Rebate W/O DDTS2 Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858I039280.2423611111 | X49858I0 |  | Parent | TRUE | EX - NO.1 220KV BUS AT MBTS | 39280.2424 | 39280.3108 | REPDAILY | 00004001 | SPICAPX | Remove Temp O/head Loop EPS No1& DDTS No1 Lines | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258U539280.2881944444 | X43258U5 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 39280.2882 | 39281.6806 | CONT | 00359892 | SPICAPX | C'over & commission No2 Cap Bk Prot on P9,P51,P52 | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026206039280.3159722222 | 10262060 |  | Parent | FALSE | W1 GEN TRANS NO.2 BUS 220KV CB AT YPS | 39280.316 | 39280.4451 | DAILY | [12 empty] | 0
_X38458U739280.3333333333 | X38458U7 |  | Parent | FALSE | BATS 220KV LINE AT TGTS | 39280.3333 | 39280.6472 | DAILY | 00023130 | SPICAPX | Install Drain Coil & E/sw on LMU's, modify CVT box | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X51958A739280.36875 | X51958A7 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT WOTS | 39280.3688 | 39280.5285 | DAILY | [12 empty] | 0
_1026344139280.8229166667 | 10263441 |  | Parent | FALSE | WBTS 220KV LINE AT BATS | 39280.8229 | 39280.8931 | DAILY | 00012410 | FAULT | BATS - HOTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026324339281.2368055556 | 10263243 |  | Parent | FALSE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39281.2368 | 39281.2708 | DAILY | [12 empty] | 0
_Z53158Y939281.2756944444 | Z53158Y9 |  | Parent | FALSE | RTS NO.1 220KV LINE AT ROTS | 39281.2757 | 39282.6875 | CONT | 00023111 | VEN_AUG | Installation of Harp Strings | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026195939281.3208333333 | 10261959 |  | Parent | TRUE | EX - NO.3 66KV CAPACITOR BANK CB AT BETS | 39281.3208 | 39281.7243 | DAILY | [12 empty] | 0
_1026289039281.3208333333 | 10262890 | 10261959 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 39281.3208 | 39281.7243 | DAILY | 00016304 | SPIMAINT | Rebate W/O No3B Cap bank during CB O/H | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X38458T939281.3638888889 | X38458T9 |  | Parent | TRUE | B1 220/66KV TRANS AT TGTS | 39281.3639 | 39281.6368 | DAILY | 00363297 | SPICAPX | Nemmco Compliance tests on B1 Transf,CB's & CT's | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458U039281.3638888889 | X38458U0 | X38458T9 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39281.3639 | 39281.6368 | DAILY | 00363297 | SPICAPX | Perf Calc on B1 Transformer | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026344839281.55625 | 10263448 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39281.5563 | 39281.5674 | DAILY | [12 empty] | 0
_1025166839282.2909722222 | 10251668 |  | Parent | FALSE | B3 220/66KV TRANS AT KTS | 39282.291 | 39283.6396 | CONT | 00350448 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z33458H739282.2958333333 | Z33458H7 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 39282.2958 | 39282.7674 | DAILY | 00352791 | VEN_AUG | Remove & Replace oil pump | SPIPOWER | Z334 | Z334 - (SVTS) 4TH TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X3D258E839282.3222222222 | X3D258E8 |  | Parent | FALSE | EX - LY NO.1 66KV FDR X PROT AT MWTS | 39282.3222 | 39283.6556 | CONT | [12 empty] | 0
_X43258W339282.3340277778 | X43258W3 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39282.334 | 39282.5625 | DAILY | 00359891 | SPICAPX | Out W/O No1 66kV Cap Bk & CB earthing & prot mods | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026338639282.3534722222 | 10263386 |  | Parent | FALSE | A1 TRANS 220KV LINE AT ROTS (RTF) | 39282.3535 | 39282.5153 | DAILY | 00023965 | SPIMAINT | proximty reasons for Bushing replacement | SPIPOWER |  |  | Circuits | Eastern | 220 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1026353439282.6875 | 10263534 |  | Parent | FALSE | RTS NO.1 220KV LINE NO.2 BUS CB AT ROTS | 39282.6875 | 39287.6826 | CONT | [12 empty] | 0
_X43258W139283.2881944444 | X43258W1 |  | Parent | FALSE | BSS 220KV LINE NO.1 BUS CB AT RCTS | 39283.2882 | 39283.4896 | DAILY | [12 empty] | 0
_Z50658B539283.4625 | Z50658B5 |  | Parent | TRUE | NO.3 66KV BUS AT HTS | 39283.4625 | 39283.4931 | DAILY | 00004458 | DB_AUG | Commission M/MC Feeder | SPIPOWER | Z506 | Z506 - (HTS) OPTIMISING 66KV CBS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z50658B639283.4625 | Z50658B6 | Z50658B5 | Child | FALSE | B3 220/66KV TRANS AT HTS | 39283.4625 | 39283.4931 | DAILY | 00004447 | DB_AUG | Trans Rebate for Bus outage | SPIPOWER | Z506 | Z506 - (HTS) OPTIMISING 66KV CBS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026357639283.4833333333 | 10263576 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 39283.4833 | 39283.5104 | DAILY | 00352791 | SPICAPX | B4 Trans | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026359239283.49375 | 10263592 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT HTS | 39283.4938 | 39301.5208 | CONT | [12 empty] | 0
_1026356939283.5763888889 | 10263569 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39283.5764 | 39283.6368 | DAILY | [12 empty] | 0
_1026356839283.5923611111 | 10263568 |  | Parent | FALSE | HWTS NO.3 500KV LINE CB AT LYPS | 39283.5924 | 39283.6514 | DAILY | [12 empty] | 0
_Z53158X539284.2694444444 | Z53158X5 |  | Parent | TRUE | EX - NO.1 220KV BUS AT ERTS | 39284.2694 | 39285.5993 | CONT | 00004378 | VEN_AUG | No1 Trans, ERTS-ROTS 1 Line & No 1 220kv BUS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158X639284.2694444444 | Z53158X6 | Z53158X5 | Child | FALSE | B1 220/66KV TRANS AT ERTS | 39284.2694 | 39285.5993 | CONT | 00004370 | VEN_AUG | Trans Outage rebate | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158X739284.2694444444 | Z53158X7 | Z53158X5 | Child | FALSE | ROTS NO.1 220KV LINE AT ERTS | 39284.2694 | 39285.5993 | CONT | 00012289 | VEN_AUG | Line Outage rebate | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558B839284.2777777778 | X56558B8 |  | Parent | FALSE | HWPS NO.2 220KV LINE NO.2 BUS CB AT YPS | 39284.2778 | 39285.5104 | CONT | [12 empty] | 0
_1026427439284.3798611111 | 10264274 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39284.3799 | 39284.6757 | DAILY | 00112417 | FAULT | Rebate outage | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z51358A439285.2722222222 | Z51358A4 |  | Parent | TRUE | U1 66/22KV TRANS AT RWTS | 39285.2722 | 39285.784 | DAILY | 00007456 | SPICAPX | Erect Future B1 Trans Gantry & No2 220/66kv Trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358A539285.2722222222 | Z51358A5 | Z51358A4 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 39285.2722 | 39285.784 | DAILY | 00007450 | SPICAPX | Trans outage Rebate | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56558C139285.2770833333 | X56558C1 |  | Parent | FALSE | HWPS NO.2 220KV LINE AT YPS | 39285.2771 | 39285.5104 | DAILY | 00016412 | SPICAPX | excavate & install foundations | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158Z039286.2659722222 | Z53158Z0 |  | Parent | TRUE | RTS NO.1 220KV LINE AT ROTS | 39286.266 | 39287.6826 | CONT | 00023111 | VEN_AUG | No 2 & No 4 220kv Bus & MTS No1 | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158Z139286.2659722222 | Z53158Z1 | Z53158Z0 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39286.266 | 39287.6826 | CONT | 00112418 | VEN_AUG | Capbank Rebate for Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z53158Z339286.2659722222 | Z53158Z3 | Z53158Z0 | Child | FALSE | MTS NO.1 220KV LINE AT ROTS | 39286.266 | 39287.6826 | CONT | 00350667 | VEN_AUG | Lines Rebate for Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49758D639287.2493055556 | X49758D6 |  | Parent | TRUE | BETS-KGTS 220KV NB | 39287.2493 | 39287.7472 | DAILY | 00026196 | SPICAPX | Out W/O BETS-KGTS Line for work on Line at BETS | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49758D739287.2493055556 | X49758D7 | X49758D6 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT BETS | 39287.2493 | 39287.7472 | DAILY | 00350819 | SPICAPX | Rebate W/O 2A cap bank. Prox for KGTS line work | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49758E939287.2493055556 | X49758E9 | X49758D6 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 39287.2493 | 39287.7472 | DAILY | 00016274 | SPICAPX | Rebate W/O 2B cap bank. Prox for KGTS line work | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758F039287.2493055556 | X49758F0 | X49758D6 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39287.2493 | 39287.7472 | DAILY | 00016040 | SPICAPX | Perf calc W/O No2 Trans. Prox for KGTS line work | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024937839287.2708333333 | 10249378 |  | Parent | FALSE | SYN/COND AT FBTS | 39287.2708 | 39290.6931 | CONT | 00002697 | SPIMAINT | 5 Yearly O/HAUL - FBTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026319539287.2916666667 | 10263195 |  | Parent | TRUE | NO.3 220KV CAPACITOR BANK CB AT ROTS | 39287.2917 | 39287.6681 | DAILY | [12 empty] | 0
_1026382339287.2916666667 | 10263823 | 10263195 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39287.2917 | 39287.6681 | DAILY | 00112417 | SPIMAINT | rebate INVESTIGATE MAL-OPERATION OF CB | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026070339287.3041666667 | 10260703 |  | Parent | FALSE | L1 TRANS 'A' NTH BUS 22KV CB AT RTS | 39287.3042 | 39287.6646 | DAILY | [12 empty] | 0
_X56558B939287.3145833333 | X56558B9 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 39287.3146 | 39287.45 | DAILY | [12 empty] | 0
_Z50658B739287.3631944444 | Z50658B7 |  | Parent | FALSE | NO.3 66KV BUS AT HTS | 39287.3632 | 39301.5208 | DAILY | 00004458 | DB_AUG | Commission M/MC Feeder | SPIPOWER | Z506 | Z506 - (HTS) OPTIMISING 66KV CBS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024724139287.4064930556 | 10247241 |  | Parent | FALSE | STANDBY DIESEL GENERATOR AT HWTS | 39287.4065 | 39287.6079 | DAILY | [12 empty] | 0
_X56558C039287.4513888889 | X56558C0 |  | Parent | FALSE | JINDERA 330KV LINE NO.1 BUS CB AT WOTS | 39287.4514 | 39287.5563 | DAILY | [12 empty] | 0
_X56558A839288.2888888889 | X56558A8 |  | Parent | FALSE | A1 TRANS/NO.2 CSC CB AT ROTS | 39288.2889 | 39293.5785 | CONT | [12 empty] | 0
_1026070439288.2972222222 | 10260704 |  | Parent | FALSE | L1 TRANS 'A' STH BUS 22KV CB AT RTS | 39288.2972 | 39288.5819 | DAILY | [12 empty] | 0
_V62258B339288.3076388889 | V62258B3 |  | Parent | FALSE | HWTS NO.2 LINE/SYTS NO.2 LINE 500KV CB AT SMTS | 39288.3076 | 39289.6542 | CONT | [12 empty] | 0
_X3D258E939288.3319444444 | X3D258E9 |  | Parent | FALSE | LY NO.2 66KV FDR AT MWTS | 39288.3319 | 39289.7463 | CONT | 00016141 | SPIMAINT | install new MWTS-LY 2 Prot & Control Trip Checks | SPIPOWER | X3D2 | X3D2 - (MWTS) INSTALL SCIMS & 66KV BAY PROT/CONT SCHEMES | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51058D239288.3444444445 | Z51058D2 |  | Parent | FALSE | NO.3 66KV BUS AT ATS | 39288.3444 | 39288.4174 | DAILY | 00352210 | SPICAPX | investigate/repair electrical discharge | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026342239288.3555555556 | 10263422 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK X & X BACKUP PROT AT RWTS | 39288.3556 | 39288.516 | DAILY | [12 empty] | 0
_1026356239288.3590277778 | 10263562 |  | Parent | FALSE | LV NO.1 66KV FDR CB AT ATS | 39288.359 | 39288.6931 | DAILY | [12 empty] | 0
_X38458T839288.4236111111 | X38458T8 | X38458T7 | Child | FALSE | EX - NO.1 66KV BUS AT TGTS | 39288.4236 | 39288.5333 | DAILY | 00003132 | SPICAPX | perf calc B1 Trans during No1 66 kv bus outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026374939288.4722337963 | 10263749 |  | Parent | FALSE | EX - DC SUPPLY SYSTEMS AT HOTS | 39288.4722 | 39300.4681 | DAILY | [12 empty] | 0
_1026361939289.04375 | 10263619 |  | Parent | FALSE | W4 GEN TRANS 220KV CB LINE SIDE ISOL AT YPS | 39289.0437 | 39296.3972 | CONT | [12 empty] | 0
_1026070539289.2951388889 | 10260705 |  | Parent | FALSE | L4 TRANS 'C' NTH BUS 22KV CB AT RTS | 39289.2951 | 39289.675 | DAILY | [12 empty] | 0
_1024977939289.3159722222 | 10249779 |  | Parent | FALSE | DDTS NO.1 LINE/SHTS NO.1 LINE 220KV CB AT GNTS | 39289.316 | 39290.6868 | DAILY | [12 empty] | 0
_1024756539289.3215277778 | 10247565 |  | Parent | FALSE | 2-4 22KV BUS TIE CB AT BETS | 39289.3215 | 39289.7063 | DAILY | [12 empty] | 0
_1026274839289.3493055556 | 10262748 |  | Parent | FALSE | R3 220/66/22KV TRANS AT KGTS | 39289.3493 | 39289.7583 | REPDAILY | 00017375 | SPIMAINT | KGTS Trans OLTC's Out Of Step | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026385339290.06875 | 10263853 |  | Parent | TRUE | EX - EPS NO.1 220KV LINE AT MBTS | 39290.0687 | 39290.0722 | DAILY | 00011751 | FAULT | Rebate work orders for MBTS-EPS 1&2 line trips | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1026385439290.06875 | 10263854 | 10263853 | Child | FALSE | EX - EPS NO.2 220KV LINE AT MBTS | 39290.0687 | 39290.0722 | DAILY | 00011752 | FAULT | Rebate work orders for MBTS-EPS 1&2 line trips | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1026070639290.2958333333 | 10260706 |  | Parent | FALSE | L4 TRANS 'C' STH BUS 22KV CB AT RTS | 39290.2958 | 39290.6181 | DAILY | [12 empty] | 0
_1026378239290.3333333333 | 10263782 |  | Parent | FALSE | 50V CONTROL BATTERY AT TTS | 39290.3333 | 39290.5927 | DAILY | [12 empty] | 0
_1026368039290.4145833333 | 10263680 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK X & Y PROT & CONTROLS AT DDTS | 39290.4146 | 39290.6625 | DAILY | [12 empty] | 0
_1024914339291.25 | 10249143 |  | Parent | TRUE | NO.1 220KV BUS E/SW AT WMTS | 39291.25 | 39291.6243 | REPDAILY | [12 empty] | 0
_1026381939291.25 | 10263819 | 10249143 | Child | FALSE | KTS NO.1 220KV LINE AT WMTS | 39291.25 | 39291.6243 | REPDAILY | 00025734 | SPIMAINT | Out wo Rebate for Bus outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026382039291.25 | 10263820 | 10249143 | Child | FALSE | FBTS NO.1 220KV LINE AT WMTS | 39291.25 | 39291.6243 | REPDAILY | 00025735 | SPIMAINT | Out wo Rebate for Bus outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1026382139291.25 | 10263821 | 10249143 | Child | FALSE | B1 220/66KV TRANS AT WMTS | 39291.25 | 39291.6243 | REPDAILY | 00003233 | SPIMAINT | Out wo Rebate for Bus outage | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158Z939291.2611111111 | Z53158Z9 |  | Parent | FALSE | SVTS NO.1 220KV LINE AT ROTS | 39291.2611 | 39292.6882 | CONT | 00350027 | VEN_AUG | SVTS Line outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025165039291.3041666667 | 10251650 | Z53158X8 | Child | TRUE | B1 220/66KV TRANS AT ERTS | 39291.3042 | 39292.6576 | CONT | 00004370 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026201939291.3041666667 | 10262019 | 10251650 | Child | FALSE | B1 220/66KV TRANS AT ERTS | 39291.3042 | 39292.6576 | CONT | 00004370 | SPIMAINT | Condition Sup Monitoring MetroTrans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158X839291.3041666667 | Z53158X8 |  | Parent | TRUE | EX - NO.1 220KV BUS AT ERTS | 39291.3042 | 39292.6576 | CONT | 00004378 | VEN_AUG | No1 Trans, ERTS-ROTS 1 Line & No 1 220kv BUS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158X939291.3041666667 | Z53158X9 | Z53158X8 | Child | FALSE | B1 220/66KV TRANS AT ERTS | 39291.3042 | 39292.6576 | CONT | 00004370 | VEN_AUG | Trans Outage rebate | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158Y039291.3041666667 | Z53158Y0 | Z53158X8 | Child | FALSE | ROTS NO.1 220KV LINE AT ERTS | 39291.3042 | 39292.6576 | CONT | 00012289 | VEN_AUG | Line Outage rebate | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358B839292.2590277778 | Z51358B8 |  | Parent | TRUE | NO.1 220KV BUS AT RWTS | 39292.259 | 39292.6542 | DAILY | 00007477 | SPICAPX | No1 220 kv Bus & No 4 220/66Kv Trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358B939292.2590277778 | Z51358B9 | Z51358B8 | Child | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39292.259 | 39292.6542 | DAILY | 00007452 | SPICAPX | Rebate Tran for bus outage No 3 220/22Kv Trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358C039292.2590277778 | Z51358C0 | Z51358B8 | Child | FALSE | B4 220/66KV TRANS AT RWTS | 39292.259 | 39292.6542 | DAILY | 00007451 | SPICAPX | Rebate Tran for bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024914339292.2833333333 | 10249143 |  | Parent | TRUE | NO.1 220KV BUS E/SW AT WMTS | 39292.2833 | 39292.6569 | REPDAILY | [12 empty] | 0
_1026381939292.2833333333 | 10263819 | 10249143 | Child | FALSE | KTS NO.1 220KV LINE AT WMTS | 39292.2833 | 39292.6569 | REPDAILY | 00025734 | SPIMAINT | Out wo Rebate for Bus outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026382039292.2833333333 | 10263820 | 10249143 | Child | FALSE | FBTS NO.1 220KV LINE AT WMTS | 39292.2833 | 39292.6569 | REPDAILY | 00025735 | SPIMAINT | Out wo Rebate for Bus outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1026382139292.2833333333 | 10263821 | 10249143 | Child | FALSE | B1 220/66KV TRANS AT WMTS | 39292.2833 | 39292.6569 | REPDAILY | 00003233 | SPIMAINT | Out wo Rebate for Bus outage | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026375039292.3340277778 | 10263750 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE AT HWTS | 39292.334 | 39292.5826 | DAILY | 00016237 | SPIMAINT | Repair Defects | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024971339293.2958333333 | 10249713 |  | Parent | FALSE | NO.2 220KV BUS AT GNTS | 39293.2958 | 39293.6903 | REPDAILY | 00000747 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X56558C239293.30625 | X56558C2 |  | Parent | FALSE | KTS NO.2 220KV LINE AT WMTS | 39293.3063 | 39293.65 | REPDAILY | 00025731 | SPICAPX | excavate & install foundations for ct changes | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024923039293.3069444444 | 10249230 |  | Parent | FALSE | A1 TRANS NO.2 BUS 500KV CB AT MLTS | 39293.3069 | 39293.6868 | REPDAILY | [12 empty] | 0
_X49058H339293.3208333333 | X49058H3 |  | Parent | FALSE | MBTS NO.1 220KV LINE CB AT DDTS | 39293.3208 | 39297.9285 | CONT | [12 empty] | 0
_1024837939293.3402777778 | 10248379 |  | Parent | FALSE | LYPS NO.3 LINE/CBTS NO.4 LINE 500KV CB AT HWTS | 39293.3403 | 39293.3583 | DAILY | [12 empty] | 0
_1026381639293.5590277778 | 10263816 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39293.559 | 39293.5951 | DAILY | [12 empty] | 0
_X49658I039294.2534722222 | X49658I0 |  | Parent | TRUE | NO.1 220KV BUS AT HOTS | 39294.2535 | 39294.7361 | DAILY | 00006938 | SPICAPX | Decommission No1 Transformer and its 220&66kv CB's | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49658I139294.2534722222 | X49658I1 | X49658I0 | Child | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39294.2535 | 39294.7361 | DAILY | 00019243 | SPICAPX | Rebate W/O SVC during No1 220 Bus outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X49658I239294.2534722222 | X49658I2 | X49658I0 | Child | FALSE | B2 220/66KV TRANS AT HOTS | 39294.2535 | 39294.7361 | DAILY | 00363103 | SPICAPX | Perf Calc B2 Trans during No1 220kv Bus Outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49658I339294.2534722222 | X49658I3 | X49658I0 | Child | FALSE | EX - NO.1 SHUNT REACTOR X PROT AT HOTS | 39294.2535 | 39294.7361 | DAILY | [12 empty] | 0
_X49658I439294.2534722222 | X49658I4 | X49658I0 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT HOTS | 39294.2535 | 39294.7361 | DAILY | 00359898 | SPICAPX | Rebate W/O No1A Cap Bk during No1 66 bus Outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49658I539294.2534722222 | X49658I5 | X49658I0 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HOTS | 39294.2535 | 39294.7361 | DAILY | 00359901 | SPICAPX | Rebate W/O No1B Cap Bk during No1 66 bus Outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024867339294.2847222222 | 10248673 |  | Parent | FALSE | B3 220/66KV TRANS AT SVTS | 39294.2847 | 39294.6215 | DAILY | 00004851 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024971339294.2965277778 | 10249713 |  | Parent | FALSE | NO.2 220KV BUS AT GNTS | 39294.2965 | 39294.6972 | REPDAILY | 00000747 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024923039294.3166666667 | 10249230 |  | Parent | FALSE | A1 TRANS NO.2 BUS 500KV CB AT MLTS | 39294.3167 | 39294.6389 | REPDAILY | [12 empty] | 0
_X43258W639294.3208333333 | X43258W6 |  | Parent | TRUE | R3 TRANS 66KV CB AT RCTS | 39294.3208 | 39294.5111 | DAILY | [12 empty] | 0
_X43258W739294.3208333333 | X43258W7 | X43258W6 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 39294.3208 | 39294.5111 | DAILY | 00361128 | SPICAPX | Perf Calc, R3 Trans during R3 Trans 66 CB outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X56558C239294.3361111111 | X56558C2 |  | Parent | FALSE | KTS NO.2 220KV LINE AT WMTS | 39294.3361 | 39294.4611 | REPDAILY | 00025731 | SPICAPX | excavate & install foundations for ct changes | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024778739294.34375 | 10247787 |  | Parent | FALSE | YWPS AUX TRANS 'A' 220KV LINE X PROT AT YPS | 39294.3438 | 39295.4757 | CONT | [12 empty] | 0
_Z53158Z439295.2743055556 | Z53158Z4 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 39295.2743 | 39296.75 | CONT | 00004778 | VEN_AUG | No 2 220Kv Bus | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158Z539295.2743055556 | Z53158Z5 | Z53158Z4 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39295.2743 | 39296.75 | CONT | 00112418 | VEN_AUG | Rebate Capbank for Bus Outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024922739295.3034722222 | 10249227 |  | Parent | FALSE | HYTS NO.2/SYTS NO.2 LINE 500KV CB AT MLTS | 39295.3035 | 39295.7049 | REPDAILY | [12 empty] | 0
_1024978439295.3083333333 | 10249784 |  | Parent | FALSE | DDTS NO.1 220KV LINE NO.1 BUS CB AT GNTS | 39295.3083 | 39296.6736 | CONT | [12 empty] | 0
_Z53158AD39296.2847222222 | Z53158AD |  | Parent | FALSE | CBTS NO.2 220KV LINE AT ERTS | 39296.2847 | 39296.6937 | DAILY | 00012284 | VEN_AUG | Remove CBTS No 2 Line Chokes | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024867039296.2916666667 | 10248670 |  | Parent | FALSE | B2 220/66KV TRANS AT SVTS | 39296.2917 | 39296.6389 | DAILY | 00004850 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49858J439296.2944444444 | X49858J4 |  | Parent | FALSE | B1 220/66KV TRANS (HOT SPARE) AT MBTS | 39296.2944 | 39296.55 | DAILY | 00360627 | SPICAPX | Replace OLTC Pressure Switch on B1 Trans | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER | NORMALLY OPEN | 0
_1024922739296.3034722222 | 10249227 |  | Parent | FALSE | HYTS NO.2/SYTS NO.2 LINE 500KV CB AT MLTS | 39296.3035 | 39296.5778 | REPDAILY | [12 empty] | 0
_1024779539296.3381944444 | 10247795 |  | Parent | FALSE | YWPS AUX TRANS 'C' 220KV LINE X PROT AT YPS | 39296.3382 | 39297.4403 | CONT | [12 empty] | 0
_1026357439296.3604166667 | 10263574 |  | Parent | FALSE | EX - FF 22KV FDR 181 CB AT BTS | 39296.3604 | 39297.5993 | CONT | [12 empty] | 0
_Z53158Z639297.2729166667 | Z53158Z6 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 39297.2729 | 39297.8097 | DAILY | 00004778 | VEN_AUG | No 2 220Kv Bus & ERTS No 1 Line @ ROTS | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158Z739297.2729166667 | Z53158Z7 | Z53158Z6 | Child | FALSE | ERTS NO.1 220KV LINE AT ROTS | 39297.2729 | 39297.8097 | CONT | 00350666 | VEN_AUG | Line Rebate | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158Z839297.2729166667 | Z53158Z8 | Z53158Z6 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39297.2729 | 39297.8097 | DAILY | 00112418 | VEN_AUG | Cap Bank Rebate for Bus Outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024866739297.2909722222 | 10248667 |  | Parent | TRUE | B1 220/66KV TRANS AT SVTS | 39297.291 | 39297.5681 | DAILY | 00004849 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026208639297.2909722222 | 10262086 | 10248667 | Child | FALSE | B1 220/66KV TRANS AT SVTS | 39297.291 | 39297.5681 | DAILY | 00004849 | SPIMAINT | Repair Pump | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158AE39297.2993055556 | Z53158AE |  | Parent | FALSE | CBTS NO.1 220KV LINE AT ERTS | 39297.2993 | 39297.6868 | DAILY | 00012286 | VEN_AUG | Remove CBTS No 1 Line Chokes | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026400039297.3180555556 | 10264000 |  | Parent | FALSE | LNGS NO.2 GEN TRANS 220KV CB AT ATS | 39297.3181 | 39301.6299 | CONT | [12 empty] | 0
_1026397039298.1097222222 | 10263970 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 39298.1097 | 39299.6512 | CONT | 00016424 | GENCO | Gen 4 Isolations | GENCO |  |  | Circuits | 3rd Party | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026397139298.1097222222 | 10263971 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 39298.1097 | 39300.3783 | CONT | 00356086 | GENCO | Unit 8 Isolations | GENCO |  |  | Circuits | 3rd Party | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X41758A539298.2597222222 | X41758A5 |  | Parent | FALSE | B2 220/66KV TRANS AT RWTS | 39298.2597 | 39298.6479 | CONT | 00007450 | SPICAPX | Replace 220kV Bushings in No2 Trans | SPIPOWER | X417 | X417 - 220KV BUSHING REPLACEMENT 2004/05 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358A739299.2826388889 | Z51358A7 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39299.2826 | 39299.6403 | DAILY | 00007480 | SPICAPX | Bore piers for new No3 Bus VT | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358A839299.2826388889 | Z51358A8 | Z51358A7 | Child | FALSE | U1 66/22KV TRANS AT RWTS | 39299.2826 | 39299.6403 | DAILY | 00007456 | SPICAPX | No1 Trans outage rebate for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358A939299.2826388889 | Z51358A9 | Z51358A7 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 39299.2826 | 39299.6403 | DAILY | 00007450 | SPICAPX | No2 Trans outage rebate for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026276539299.2965277778 | 10262765 |  | Parent | FALSE | L1 TRANS NO.1 BUS 22KV CB AT WMTS | 39299.2965 | 39299.6549 | DAILY | [12 empty] | 0
_Z53158AF39300.4444444444 | Z53158AF |  | Parent | FALSE | ERTS NO.1 LINE/HWPS NO.2 LINE 220KV CB AT ROTS | 39300.4444 | 39300.6118 | DAILY | [12 empty] | 0
_V62258B539301.2930555556 | V62258B5 |  | Parent | FALSE | HWTS NO.2 LINE/SYTS NO.2 LINE 500KV CB AT SMTS | 39301.2931 | 39302.6417 | CONT | [12 empty] | 0
_1010620239301.3 | 10106202 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39301.3 | 39302.7097 | DAILY | [12 empty] | 0
_X56558C339301.3083333333 | X56558C3 |  | Parent | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39301.3083 | 39301.7299 | DAILY | 00017906 | SPICAPX | Out W/O PTH No2 Line & CB for CT replacement | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158AG39301.3125 | Z53158AG |  | Parent | FALSE | HWPS NO.1 220KV LINE AT ROTS | 39301.3125 | 39301.5722 | DAILY | 00023990 | VEN_AUG | Modify Trip wiring & perform Trip test | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024894039301.3333333333 | 10248940 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT WOTS | 39301.3333 | 39301.6542 | DAILY | [12 empty] | 0
_1026359039301.3479166667 | 10263590 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT HTS | 39301.3479 | 39301.5208 | DAILY | [12 empty] | 0
_1026399539301.3715277778 | 10263995 |  | Parent | FALSE | YWPS NO.3 220KV LINE AT YPS | 39301.3715 | 39303.6507 | CONT | 00016426 | GENCO | YWPS W3 Gen Trans Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258W239301.3722222222 | X43258W2 |  | Parent | FALSE | MLRC 220KV LINE AT RCTS | 39301.3722 | 39303.8764 | CONT | 00352130 | SPICAPX | Replace MLRC Ln CB's Control & Prot on P63 & P64 | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 4
_1026397239301.4770833333 | 10263972 |  | Parent | FALSE | A 66/11KV S/S TRANS 66KV FDR CB AT LY | 39301.4771 | 39304.8958 | DAILY | [12 empty] | 0
_X38458V539301.5680555556 | X38458V5 |  | Parent | FALSE | EX - 1-2 66KV BUS TIE CB AT TGTS | 39301.5681 | 39301.5861 | DAILY | [12 empty] | 0
_X38458V639301.5861111111 | X38458V6 |  | Parent | TRUE | B1 TRANS 66KV CB AT TGTS | 39301.5861 | 39301.6058 | DAILY | [12 empty] | 0
_X38458V739301.5868055556 | X38458V7 | X38458V6 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39301.5868 | 39301.6056 | DAILY | 00363297 | SPICAPX | Perf Calc B1 Trans during work on B1 trans 66kv CB | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51058D539302.2965277778 | Z51058D5 |  | Parent | FALSE | B3 TRANS 220KV BUS AT ATS | 39302.2965 | 39302.566 | DAILY | 00360125 | SPICAPX | position cable support structure stands | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X56558C439302.3 | X56558C4 |  | Parent | TRUE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39302.3 | 39302.7799 | REPDAILY | 00017906 | SPICAPX | Out W/O PTH 2 L CB CT replace- Inc MLTS 2Line prox | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558C539302.3 | X56558C5 | X56558C4 | Child | FALSE | EX - MLTS NO.2 220KV LINE AT GTS | 39302.3 | 39302.7799 | REPDAILY | 00017904 | SPICAPX | Rebate W/O MLTS 2Line prox during PTH 2 CT replac | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025954839302.3104166667 | 10259548 |  | Parent | FALSE | EX - NO.4 MAIN TRANS NO.1 BUS 500KV CB CT R/PH AT HWTS | 39302.3104 | 39302.466 | DAILY | [12 empty] | 0
_1026392439302.3277777778 | 10263924 |  | Parent | FALSE | SYN/COND AT TSTS | 39302.3278 | 39302.4861 | DAILY | 00007626 | SPIMAINT | Repaire Oil Pump, Clean Oil Coolers | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024893139302.3277777778 | 10248931 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 39302.3278 | 39303.675 | CONT | [12 empty] | 0
_1024744339302.3298611111 | 10247443 |  | Parent | TRUE | NO.1 22KV CAPACITOR BANK CB AT RCTS | 39302.3299 | 39302.6056 | DAILY | [12 empty] | 0
_1026374739302.3298611111 | 10263747 | 10247443 | Child | FALSE | NO.1 22KV CAPACITOR BANK AT RCTS | 39302.3299 | 39302.6056 | DAILY | 00016710 | SPIMAINT | Rebate W/O No1 22kV Cap bk during its CB O-H | SPIPOWER |  |  | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X56558C739302.3319444444 | X56558C7 |  | Parent | FALSE | KTS NO.2 220KV LINE AT WMTS | 39302.3319 | 39302.7333 | REPDAILY | 00025731 | SPICAPX | unload ct's & excavate for control cables | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458V839302.3486111111 | X38458V8 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT TGTS | 39302.3486 | 39302.6743 | DAILY | 00003129 | SPICAPX | Replace cables between No2 S/S Tran & its 415V cub | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1025954639302.4666666667 | 10259546 |  | Parent | FALSE | EX - NO.3 MAIN TRANS NO.1 BUS 500KV CB CT R/PH AT HWTS | 39302.4667 | 39302.4785 | DAILY | [12 empty] | 0
_1010620339303.2881944444 | 10106203 |  | Parent | FALSE | SMTS NO.3 500KV LINE NO.1 BUS CB AT ROTS (RTF) | 39303.2882 | 39304.6139 | DAILY | [12 empty] | 0
_X56558C439303.2958333333 | X56558C4 |  | Parent | TRUE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39303.2958 | 39303.6813 | REPDAILY | 00017906 | SPICAPX | Out W/O PTH 2 L CB CT replace- Inc MLTS 2Line prox | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558C539303.2958333333 | X56558C5 | X56558C4 | Child | FALSE | EX - MLTS NO.2 220KV LINE AT GTS | 39303.2958 | 39303.6813 | REPDAILY | 00017904 | SPICAPX | Rebate W/O MLTS 2Line prox during PTH 2 CT replac | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026413439303.3098263889 | 10264134 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 39303.3098 | 39303.5549 | CONT | 00356083 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024744539303.3305555556 | 10247445 |  | Parent | TRUE | NO.2 22KV CAPACITOR BANK CB AT RCTS | 39303.3306 | 39303.6 | DAILY | [12 empty] | 0
_1026374839303.3305555556 | 10263748 | 10247445 | Child | FALSE | NO.2 22KV CAPACITOR BANK AT RCTS | 39303.3306 | 39303.6 | DAILY | 00016713 | SPIMAINT | Rebate W/O No2 22kV Cap bank during its CB O-H | SPIPOWER |  |  | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026419839303.8694444444 | 10264198 |  | Parent | FALSE | JINDERA 330KV LINE AT WOTS | 39303.8694 | 39303.9187 | DAILY | 00012053 | FORCED | WOTS: JINDERA Line de-energised for RF checks | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026421739303.9715277778 | 10264217 |  | Parent | FALSE | ROTS-MTS 1 220KV E | 39303.9715 | 39304.0306 | CONT | 00022746 | FAULT | ROTS-MTS 1 Line Trip for Transformer fault at MTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026420039303.9715277778 | 10264200 |  | Parent | FALSE | EX - NO.1 220/22KV TRANS BANK AT MTS | 39303.9715 | 39304.3236 | CONT | 00026901 | FAULT | MTS No1 220/22 Transf Fault on 22kV due to possum | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026411339304.2972222222 | 10264113 |  | Parent | FALSE | LNGS NO.1 GEN TRANS 220KV CB TRANS SIDE ROI AT ATS | 39304.2972 | 39304.6451 | DAILY | [12 empty] | 0
_X56558C739304.4222222222 | X56558C7 |  | Parent | FALSE | KTS NO.2 220KV LINE AT WMTS | 39304.4222 | 39304.5104 | REPDAILY | 00025731 | SPICAPX | unload ct's & excavate for control cables | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026421139304.46875 | 10264211 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 39304.4688 | 39304.4736 | DAILY | [12 empty] | 0
_1026423539304.46875 | 10264235 |  | Parent | FALSE | DDTS 330KV LINE AT WOTS | 39304.4688 | 39304.4736 | DAILY | 00012054 | FORCED | WOTS: DDTS Line de-energised for RF Checks | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026425039304.9854166667 | 10264250 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 39304.9854 | 39306.875 | CONT | 00356079 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758F139305.25 | X49758F1 |  | Parent | FALSE | R4 220/66/22KV TRANS AT BETS | 39305.25 | 39310.5451 | CONT | 00016220 | SPICAPX | Out W/O No4 Trans cutover & commiss No2 220 Bus | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X41758A639305.275 | X41758A6 |  | Parent | FALSE | B2 220/66KV TRANS AT RWTS | 39305.275 | 39305.6132 | CONT | 00007450 | SPICAPX | Proximity outage No2 Trans for gantry repair | SPIPOWER | X417 | X417 - 220KV BUSHING REPLACEMENT 2004/05 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358C739305.275 | Z51358C7 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 39305.275 | 39305.6153 | DAILY | 00007456 | SPICAPX | Trans outage rebate for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024019039305.3020833333 | 10240190 |  | Parent | TRUE | L4 220/22KV TRANS AT RTS | 39305.3021 | 39306.6639 | CONT | 00007333 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area(W) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026211039305.3020833333 | 10262110 | 10240190 | Child | FALSE | L4 220/22KV TRANS AT RTS | 39305.3021 | 39306.6639 | CONT | 00007333 | SPIMAINT | Condition Sup Monitoring Metro Trans 2day East | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026284339305.3166666667 | 10262843 |  | Parent | TRUE | NO.1 66KV BUS VT AT WMTS | 39305.3167 | 39305.4132 | DAILY | [12 empty] | 0
_1026444839305.3166666667 | 10264448 | 10262843 | Child | FALSE | B1 220/66KV TRANS AT WMTS | 39305.3167 | 39305.4132 | DAILY | 00003233 | SPIMAINT | ROUTINE SUP TESTING OF ENERGY METERING AT WMTS | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026284439305.4131944444 | 10262844 |  | Parent | TRUE | NO.2 66KV BUS VT AT WMTS | 39305.4132 | 39305.484 | DAILY | [12 empty] | 0
_1026445539305.4131944444 | 10264455 | 10262844 | Child | FALSE | B2 220/66KV TRANS AT WMTS | 39305.4132 | 39305.484 | DAILY | 00003235 | SPIMAINT | ROUTINE SUP TESTING OF ENERGY METERING AT WMTS | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026445639305.4131944444 | 10264456 | 10262844 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT WMTS | 39305.4132 | 39305.484 | DAILY | 00074391 | SPIMAINT | ROUTINE SUP TESTING OF ENERGY METERING AT WMTS | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026445839305.4923611111 | 10264458 | 10262845 | Child | FALSE | B3 220/66KV TRANS AT WMTS | 39305.4924 | 39305.5965 | DAILY | 00003236 | SPIMAINT | Avail of plant SUP TESTING OF ENERGY METERING | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026445939305.4923611111 | 10264459 | 10262845 | Child | FALSE | NO.3 66KV CAPACITOR BANK AT WMTS | 39305.4924 | 39305.5965 | DAILY | 00003191 | SPIMAINT | rebate bus out SUP TESTING OF ENERGY METERING | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026284539305.4923611111 | 10262845 |  | Parent | TRUE | NO.3 66KV BUS VT R/PH AT WMTS | 39305.4924 | 39305.5972 | DAILY | [12 empty] | 0
_1026182339306.3020833333 | 10261823 |  | Parent | TRUE | S001 KTS -BLTS 1 220KV | 39306.3021 | 39306.466 | DAILY | [12 empty] | 0
_1026446339306.3020833333 | 10264463 | 10261823 | Child | FALSE | KTS -BLTS 220KV WY | 39306.3021 | 39306.466 | DAILY | 00022716 | SPIMAINT | Rebate Change insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358B039306.3145833333 | Z51358B0 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39306.3146 | 39306.6035 | DAILY | 00007480 | SPICAPX | Install new No3 66kv Bus VT Isolator | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358B139306.3145833333 | Z51358B1 | Z51358B0 | Child | FALSE | U1 66/22KV TRANS AT RWTS | 39306.3146 | 39306.6035 | DAILY | 00007456 | SPICAPX | Trans outage rebate for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358B239306.3145833333 | Z51358B2 | Z51358B0 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 39306.3146 | 39306.6035 | DAILY | 00007450 | SPICAPX | 2 ND Trans outage rebate for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026182439306.4666666667 | 10261824 |  | Parent | TRUE | S001 KTS -ATS 220KV | 39306.4667 | 39306.5965 | DAILY | [12 empty] | 0
_1026446439306.4666666667 | 10264464 | 10261824 | Child | FALSE | KTS -ATS 220KV WY | 39306.4667 | 39306.5965 | DAILY | 00074402 | SPIMAINT | rebate - Change insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026427339306.9145833333 | 10264273 |  | Parent | FALSE | DDTS-GNTS 1 220KV NW | 39306.9146 | 39306.9167 | DAILY | 00060184 | FAULT | Out work order for line trip | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026425739306.9583333333 | 10264257 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 39306.9583 | 39313.6465 | CONT | [12 empty] | 0
_1026411539307.2784722222 | 10264115 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 39307.2785 | 39308.6674 | DAILY | [12 empty] | 0
_1010620439307.2888888889 | 10106204 |  | Parent | FALSE | CBTS NO.4 LINE/SMTS NO.3 LINE 500KV CB AT ROTS (RTF) | 39307.2889 | 39308.5736 | DAILY | [12 empty] | 0
_X56558C839307.3 | X56558C8 |  | Parent | FALSE | KTS NO.2 220KV LINE AT WMTS | 39307.3 | 39311.5924 | CONT | 00025731 | SPICAPX | replace kts 2l cb ct's & install kts 2l cvt | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026423839307.41875 | 10264238 |  | Parent | FALSE | B 66/11KV S/S TRANS CABLE AT LY | 39307.4187 | 39311.8083 | CONT | 00027177 | GENCO | LYPS 66/11kV S/S Trans B & C SCAP | GENCO |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026413739308.2923611111 | 10264137 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39308.2924 | 39308.3958 | DAILY | 00112417 | SPIMAINT | Hot Joint | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X3D258F439308.3166666667 | X3D258F4 |  | Parent | TRUE | EX - LY NO.3 66KV FDR X PROT AT MWTS | 39308.3167 | 39309.5007 | CONT | [12 empty] | 0
_X3D258Z039308.3166666667 | X3D258Z0 | X3D258F4 | Child | FALSE | MWTS NO.3 66KV FDR AT LY | 39308.3167 | 39309.5007 | CONT | 00015996 | SPIMAINT | rebate - install new MWTS-LY 3 Prot & Control | SPIPOWER | X3D2 | X3D2 - (MWTS) INSTALL SCIMS & 66KV BAY PROT/CONT SCHEMES | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49058H539308.3319444444 | X49058H5 |  | Parent | TRUE | MBTS NO.2 220KV LINE CB AT DDTS | 39308.3319 | 39310.7007 | CONT | [12 empty] | 0
_X49058H639308.3319444444 | X49058H6 | X49058H5 | Child | FALSE | MBTS NO.2 220KV LINE AT DDTS | 39308.3319 | 39310.7007 | CONT | 00012363 | SPICAPX | Rebate W/O MBTS 2 Line during CB management works | SPIPOWER | X490 | X490 - (DDTS) 220KV REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46158P739308.46875 | X46158P7 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39308.4688 | 39333.4736 | CONT | 00331118 | SPICAPX | Out W/O No2 66kV Cap Bk prot & control mods | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026443139308.9638888889 | 10264431 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 39308.9639 | 39312.3757 | CONT | 00016423 | GENCO | Gen Co request | GENCO |  |  | Circuits | 3rd Party | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025138039309.2923611111 | 10251380 |  | Parent | FALSE | A1 TRANS NO.4 BUS 220KV CB AT ROTS | 39309.2924 | 39309.6382 | DAILY | [12 empty] | 0
_1026411739309.2958333333 | 10264117 |  | Parent | FALSE | EX - SMTS LINE/A2 TRANS 500KV CB AT KTS | 39309.2958 | 39309.6701 | DAILY | [12 empty] | 0
_1026284939309.2979166667 | 10262849 |  | Parent | FALSE | NO.1 330/66/22KV TRANS 22KV VT AT WOTS | 39309.2979 | 39309.4674 | DAILY | [12 empty] | 0
_1024923339309.3125 | 10249233 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT MLTS | 39309.3125 | 39309.6894 | REPDAILY | [12 empty] | 0
_X43258X039309.3555555556 | X43258X0 |  | Parent | FALSE | BSS 220KV LINE NO.1 BUS CB AT RCTS | 39309.3556 | 39309.4028 | DAILY | [12 empty] | 0
_X56558C939309.3659722222 | X56558C9 |  | Parent | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB AT MLTS | 39309.366 | 39311.4167 | CONT | [12 empty] | 0
_X49658J139309.4041666667 | X49658J1 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 39309.4042 | 39311.6458 | CONT | 00359897 | SPICAPX | Disconnect & Rotate No2 Cap Bank CB 180 Degrees | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258W939309.4486111111 | X43258W9 |  | Parent | FALSE | KGTS 220KV LINE CB AT RCTS | 39309.4486 | 39309.4819 | DAILY | [12 empty] | 0
_1024893439309.4784722222 | 10248934 |  | Parent | FALSE | JINDERA 330KV LINE NO.2 BUS CB AT WOTS | 39309.4785 | 39309.6396 | CONT | [12 empty] | 0
_1026285039309.48125 | 10262850 |  | Parent | FALSE | NO.2 330/66/22KV TRANS 22KV VT AT WOTS | 39309.4812 | 39309.6424 | DAILY | [12 empty] | 0
_X43258W839309.5041666667 | X43258W8 |  | Parent | FALSE | HOTS 220KV LINE CB AT RCTS | 39309.5042 | 39309.525 | DAILY | [12 empty] | 0
_X32058B139309.6298611111 | X32058B1 |  | Parent | FALSE | U2 TRANS 22KV CB AT MTS | 39309.6299 | 39393.5875 | CONT | [12 empty] | 0
_1026414539310.2888888889 | 10264145 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT ERTS | 39310.2889 | 39310.5694 | DAILY | 00004344 | SPIMAINT | Rebalance Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026206339310.29375 | 10262063 |  | Parent | FALSE | B2 TRANS 66KV CB AT TBTS | 39310.2937 | 39310.5799 | DAILY | [12 empty] | 0
_1024722939310.2986111111 | 10247229 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39310.2986 | 39310.7028 | REPDAILY | 00019243 | SPIMAINT | 4 Yearly O/Haul - SVC at HOTS | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026412039310.3020833333 | 10264120 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 39310.3021 | 39310.6597 | DAILY | [12 empty] | 0
_1024923339310.3090277778 | 10249233 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT MLTS | 39310.309 | 39310.6083 | REPDAILY | [12 empty] | 0
_1026284739310.3118055556 | 10262847 |  | Parent | FALSE | NO.1 66KV BUS VT R/PH AT WOTS | 39310.3118 | 39310.5806 | DAILY | [12 empty] | 0
_1026357739310.3333333333 | 10263577 |  | Parent | FALSE | EX - FF 22KV FDR 188 CB AT BTS | 39310.3333 | 39311.5687 | CONT | [12 empty] | 0
_X38458V939310.3451388889 | X38458V9 |  | Parent | TRUE | NO.1 22KV/415V S/S TRANS AT TGTS | 39310.3451 | 39310.5833 | DAILY | 00003128 | SPICAPX | Replace cables between No1 S/S Tran & its 415V cub | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_X38458W039310.3451388889 | X38458W0 | X38458V9 | Child | FALSE | NO.1 22KV/415V S/S TRANS AT TGTS | 39310.3451 | 39310.5833 | DAILY | 00003128 | SPICAPX | Perf Calc for B1 Trans during No1 S/S Trans Outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1026450439310.39375 | 10264504 |  | Parent | FALSE | HWPS NO.3 LINE/MWTS NO.2 LINE 220KV CB AT JLTS | 39310.3938 | 39310.5854 | DAILY | [12 empty] | 0
_X43258X339310.4722222222 | X43258X3 |  | Parent | TRUE | NO.2 66KV BUS AT RCTS | 39310.4722 | 39310.6493 | DAILY | 00016977 | SPICAPX | Modify No2 66kv Bus VT, Bus Side Isol connections | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258X439310.4722222222 | X43258X4 | X43258X3 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39310.4722 | 39310.6493 | DAILY | 00337581 | SPICAPX | perf calc, No1Trans Grp for No2 66kv Bus outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258X539310.4722222222 | X43258X5 | X43258X3 | Child | FALSE | NO.3 66KV REACTOR AT RCTS | 39310.4722 | 39310.6493 | DAILY | 00357254 | SPICAPX | Rebate W/O for No2 66kv Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258X639310.4722222222 | X43258X6 | X43258X3 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 39310.4722 | 39310.6493 | DAILY | 00359892 | SPICAPX | Rebate W/O for No2 66kv Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258X739310.4722222222 | X43258X7 | X43258X3 | Child | FALSE | NO.2 66KV REACTOR AT RCTS | 39310.4722 | 39310.6493 | DAILY | 00016897 | SPICAPX | Rebate W/O for No2 66kv Bus Outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026446839310.5027777778 | 10264468 |  | Parent | FALSE | DC SUPPLY SYSTEMS - SPI AT FVTS | 39310.5028 | 39310.7097 | DAILY | [12 empty] | 0
_1026493739310.5451388889 | 10264937 |  | Parent | FALSE | R4 220/66/22KV TRANS AT BETS | 39310.5451 | 39310.6646 | DAILY | 00016220 | FAULT | BETS: No4 Trans tripped during commissioning | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026284839310.5833333333 | 10262848 |  | Parent | FALSE | NO.2 66KV BUS VT R/PH AT WOTS | 39310.5833 | 39310.6722 | DAILY | [12 empty] | 0
_X49758F239310.70625 | X49758F2 |  | Parent | FALSE | EX - FVTS/SHTS 220KV LINE NO.2 BUS CB AT BETS | 39310.7063 | 39312.0028 | DAILY | [12 empty] | 0
_X43258X839311.2597222222 | X43258X8 |  | Parent | FALSE | NO.1 66KV REACTOR AT RCTS | 39311.2597 | 39311.4757 | DAILY | 00016895 | SPICAPX | Modify the No1 66kv Reactor Neutral Isol Sw | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z53158AK39311.2645833333 | Z53158AK |  | Parent | TRUE | NO.4 220KV BUS AT ROTS | 39311.2646 | 39311.7569 | DAILY | 00329012 | VEN_AUG | No4 Bus outage to Install SVTS No1 Line Bus ROI | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158AL39311.2645833333 | Z53158AL | Z53158AK | Child | FALSE | MTS NO.1 220KV LINE AT ROTS | 39311.2646 | 39311.7569 | DAILY | 00350667 | VEN_AUG | Rebate Line for Bus Outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026275739311.2902777778 | 10262757 | 10263579 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39311.2903 | 39311.5125 | DAILY | 00331179 | SPIMAINT | RWTS: No 2 66kV Cap Bank -Cap Fault Alarm | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026357939311.2902777778 | 10263579 |  | Parent | TRUE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39311.2903 | 39311.5125 | DAILY | 00007399 | SPIMAINT | Re-Balance Cap Bank at RWTS | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1023562639311.2965277778 | 10235626 |  | Parent | FALSE | B3 220/66KV TRANS AT TSTS | 39311.2965 | 39311.5896 | DAILY | 00007659 | SPIMAINT | Cooling fan failure Incorrect operation | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024923339311.3 | 10249233 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT MLTS | 39311.3 | 39311.7028 | REPDAILY | [12 empty] | 0
_1024722939311.3013888889 | 10247229 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39311.3014 | 39311.7069 | REPDAILY | 00019243 | SPIMAINT | 4 Yearly O/Haul - SVC at HOTS | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1010280839311.3111111111 | 10102808 |  | Parent | FALSE | NO.3 GEN TRANS 220KV E/SW AT HWPS | 39311.3111 | 39311.6007 | DAILY | [12 empty] | 0
_1025947439311.33125 | 10259474 |  | Parent | FALSE | EX - B2 TRANS NO.1 BUS TIE CT R/PH AT GNTS | 39311.3313 | 39311.4201 | DAILY | [12 empty] | 0
_1026426339311.4027777778 | 10264263 |  | Parent | FALSE | BLTS 66KV LINE CB AT ATS | 39311.4028 | 39313.7472 | DAILY | [12 empty] | 0
_1026494239311.40625 | 10264942 |  | Parent | FALSE | MLTS-GTS 2 220KV WY | 39311.4062 | 39311.4167 | DAILY | 00022687 | FAULT | Out w/order for trip assoc commi with SIR 10264559 | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025947639311.4166666667 | 10259476 |  | Parent | FALSE | SHTS NO.1 220KV LINE NO.2 BUS CB CT R/PH AT GNTS | 39311.4167 | 39311.5035 | DAILY | [12 empty] | 0
_1025947839311.5041666667 | 10259478 |  | Parent | FALSE | SHTS NO.3 220KV LINE NO.2 BUS CB CT R/PH AT GNTS | 39311.5042 | 39311.5583 | DAILY | [12 empty] | 0
_X43258X939311.5069444444 | X43258X9 |  | Parent | FALSE | NO.2 66KV REACTOR AT RCTS | 39311.5069 | 39311.5854 | DAILY | 00016897 | SPICAPX | Modify the No2 66kv Reactor Neutral Isol Sw | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X43258Y039311.6034722222 | X43258Y0 |  | Parent | FALSE | NO.3 66KV REACTOR AT RCTS | 39311.6035 | 39311.6958 | DAILY | 00357254 | SPICAPX | Modify the No3 66kv Reactor Neutral Isol Sw | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026495539311.6055555556 | 10264955 | X49658I8 | Child | FALSE | NO.2 66KV REACTOR AT HOTS | 39311.6056 | 39311.6451 | DAILY | 00357255 | SPICAPX | Rebate W/O No2 Cap bank during No2 66 Bus outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49658I839311.6055555556 | X49658I8 |  | Parent | TRUE | NO.2 66KV BUS AT HOTS | 39311.6056 | 39311.6451 | DAILY | 00006941 | SPICAPX | Out W/O No2 66 Bus for No2 Cap bank CB commiss | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X49658I939311.6055555556 | X49658I9 | X49658I8 | Child | FALSE | B3 220/66KV TRANS AT HOTS | 39311.6056 | 39311.6451 | DAILY | 00363102 | SPICAPX | Perf calc W/O B3 Trans during No2 66 Bus outage | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X47758D239312.2875 | X47758D2 |  | Parent | FALSE | ROTS NO.3 500KV LINE AT SMTS | 39312.2875 | 39312.6514 | DAILY | 00012438 | SPICAPX | manufacture & fit droppers between rack to rack | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024856639313.2743055556 | 10248566 |  | Parent | TRUE | NO.1 220KV BUS AT RTS | 39313.2743 | 39313.6667 | DAILY | 00007347 | SPIMAINT | O/HAUL 220kv Bus, B1, L1 ROTS No1 LINE at RTS | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026178339313.2743055556 | 10261783 | 10248566 | Child | FALSE | B1 220/66KV TRANS AT RTS | 39313.2743 | 39313.6667 | DAILY | 00007329 | SPIMAINT | B1 Trans Rebate | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026178439313.2743055556 | 10261784 | 10248566 | Child | FALSE | L1 220/22KV TRANS AT RTS | 39313.2743 | 39313.6667 | DAILY | 00007330 | SPIMAINT | L1 Trans outage rebate | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026199339313.2743055556 | 10261993 | 10248566 | Child | FALSE | B1 TRANS 220KV ISOL AT RTS | 39313.2743 | 39313.6667 | DAILY | [12 empty] | 0
_1026199939313.2743055556 | 10261999 | 10248566 | Child | FALSE | B1 220/66KV TRANS 66KV CB TRANS SIDE ISOL AT RTS | 39313.2743 | 39313.6667 | DAILY | [12 empty] | 0
_1026200839313.2743055556 | 10262008 | 10248566 | Child | FALSE | ROTS NO.1 220KV LINE CB BUS SIDE ISOL AT RTS | 39313.2743 | 39313.6667 | DAILY | [12 empty] | 0
_1026495639313.2743055556 | 10264956 | 10248566 | Child | FALSE | ROTS NO.1 220KV LINE AT RTS | 39313.2743 | 39313.6667 | DAILY | 00021385 | SPIMAINT | Rebate for Bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X47758D339313.2819444445 | X47758D3 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39313.2819 | 39313.6181 | DAILY | 00012436 | SPICAPX | comms circuits & equip to be changed | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358B339313.2979166667 | Z51358B3 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39313.2979 | 39313.7569 | DAILY | 00007480 | SPICAPX | Commission new No3 66kv Bus VT | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358B439313.2979166667 | Z51358B4 | Z51358B3 | Child | FALSE | U1 66/22KV TRANS AT RWTS | 39313.2979 | 39313.7569 | DAILY | 00007456 | SPICAPX | Trans outage rebate for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358B539313.2979166667 | Z51358B5 | Z51358B3 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 39313.2979 | 39313.7569 | DAILY | 00007450 | SPICAPX | 2 ND Trans outage rebate for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49758F639314.2895833333 | X49758F6 |  | Parent | TRUE | NO.3 66KV BUS AT BETS | 39314.2896 | 39314.7194 | DAILY | 00016366 | SPICAPX | Out W/O No3 66kV bus to disconnect VT & 3A/B Cap | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758F739314.2895833333 | X49758F7 | X49758F6 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT BETS | 39314.2896 | 39314.7194 | DAILY | 00350820 | SPICAPX | Rebate W/O No3A Cap bk during No3 66kV bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49758F839314.2895833333 | X49758F8 | X49758F6 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 39314.2896 | 39314.7194 | DAILY | 00016304 | SPICAPX | Rebate W/O No3B Cap bk during No3 66kV bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758F939314.2895833333 | X49758F9 | X49758F6 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39314.2896 | 39314.7194 | DAILY | 00016040 | SPICAPX | Perf calc W/O No2 Trans during No3 66kV bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026462539314.5493055556 | 10264625 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 39314.5493 | 39318.7999 | CONT | 00356080 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026446639314.7194444445 | 10264466 |  | Parent | TRUE | EX - NO.3 66KV CAPACITOR BANK CB AT BETS | 39314.7194 | 39339.3264 | CONT | [12 empty] | 0
_X49758Z039314.7194444445 | X49758Z0 | 10264466 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 39314.7194 | 39339.3264 | CONT | 00016304 | SPICAPX | Rebate for CB Replacement | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758Z139314.7194444445 | X49758Z1 | 10264466 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT BETS | 39314.7194 | 39339.3264 | CONT | 00350820 | SPICAPX | Rebate for CB Replacement | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024849039315.2895833333 | 10248490 |  | Parent | FALSE | NO.1 S/S TRANS 6.6KV CB AT TSTS | 39315.2896 | 39315.6158 | DAILY | [12 empty] | 0
_1026464139315.2923611111 | 10264641 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 39315.2924 | 39315.3708 | CONT | 00119824 | FAULT | Cap Bank CB trip on Phase descrepancy when closed | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025011239315.3055555556 | 10250112 |  | Parent | FALSE | H1 TRANS NO.1 BUS 330KV CB AT DDTS | 39315.3056 | 39316.7256 | CONT | [12 empty] | 0
_V62258B439315.30625 | V62258B4 |  | Parent | FALSE | HWTS NO.2 LINE/SYTS NO.2 LINE 500KV CB AT SMTS | 39315.3063 | 39315.6278 | CONT | [12 empty] | 0
_Z60258A039315.3229166667 | Z60258A0 |  | Parent | FALSE | NO.8 22KV/415V S/S TRANS AT SMTS | 39315.3229 | 39315.4958 | DAILY | 00001327 | SPICAPX | connect 415v cable to existing s/s dist cubicle | SPIPOWER | Z602 | Z602 - NOW Z730 (SMTS) ESTABLISH A 220KV SWITCHYARD | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1027441839315.6277777778 | 10274418 |  | Parent | FALSE | HWTS NO.2 LINE/SYTS NO.2 LINE 500KV CB AT SMTS | 39315.6278 | 39334.4819 | CONT | [12 empty] | 0
_1024849239316.2875 | 10248492 |  | Parent | FALSE | NO.2 S/S TRANS 6.6KV CB AT TSTS | 39316.2875 | 39316.5903 | DAILY | [12 empty] | 0
_1010166339316.3 | 10101663 |  | Parent | TRUE | B4 TRANS 66KV CB AT GTS | 39316.3 | 39316.6674 | DAILY | [12 empty] | 0
_1024145439316.3 | 10241454 | 10101663 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39316.3 | 39316.6674 | DAILY | 00002830 | SPIMAINT | Perf calc W/O No4 Trans for 66kV CB O/H | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X3D258F639316.31875 | X3D258F6 |  | Parent | TRUE | EX - LY NO.4 66KV FDR Y PROT AT MWTS | 39316.3187 | 39318.4688 | CONT | [12 empty] | 0
_X3D258Z139316.31875 | X3D258Z1 | X3D258F6 | Child | FALSE | MWTS NO.4 66KV FDR AT LY | 39316.3187 | 39318.4688 | CONT | 00015997 | SPIMAINT | rebate- install new MWTS-LY 4 Prot & Control | SPIPOWER | X3D2 | X3D2 - (MWTS) INSTALL SCIMS & 66KV BAY PROT/CONT SCHEMES | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49758F339316.46875 | X49758F3 |  | Parent | TRUE | NO.1 220KV BUS AT BETS | 39316.4688 | 39316.7174 | DAILY | 00016305 | SPICAPX | Out W/O Decommiss No1 220kV Bus in bay F | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758F439316.46875 | X49758F4 | X49758F3 | Child | FALSE | BATS 220KV LINE AT BETS | 39316.4688 | 39316.7174 | DAILY | 00016470 | SPICAPX | Rebate W/O BATS L during No1 220kV Bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49758F539316.46875 | X49758F5 | X49758F3 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39316.4688 | 39316.7174 | DAILY | 00016040 | SPICAPX | Perf calc W/O #2 Trans during No1 220 Bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024878339317.2923611111 | 10248783 |  | Parent | FALSE | 1-3 220KV BUS TIE CB AT HTS | 39317.2924 | 39317.6326 | DAILY | [12 empty] | 0
_1026196739317.2944444444 | 10261967 |  | Parent | TRUE | EX - NO.4 66KV CAPACITOR BANK CB AT GTS | 39317.2944 | 39317.684 | DAILY | [12 empty] | 0
_1026406139317.2944444444 | 10264061 | 10261967 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39317.2944 | 39317.684 | DAILY | 00329879 | SPIMAINT | Rebate W/O No4 Cap bank during CB O/H | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X56558D039317.2979166667 | X56558D0 |  | Parent | FALSE | GTS NO.1 220KV LINE NO.2 BUS CB AT MLTS | 39317.2979 | 39319.3632 | CONT | [12 empty] | 0
_1025011539317.3138888889 | 10250115 |  | Parent | FALSE | SMTS NO.2 330KV LINE NO.1 BUS CB AT DDTS | 39317.3139 | 39317.6889 | REPDAILY | [12 empty] | 0
_1026347239317.3375 | 10263472 |  | Parent | FALSE | NO.1 66KV BUS VT AT RTS | 39317.3375 | 39317.4167 | DAILY | [12 empty] | 0
_1026494039317.3777777778 | 10264940 |  | Parent | FALSE | R3 220/66/22KV TRANS AT RCTS | 39317.3778 | 39317.4097 | DAILY | 00361128 | FAULT | Out record for Trans trip due to SIR 10264762 | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 4
_1026494139317.3777777778 | 10264941 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39317.3778 | 39317.4097 | DAILY | 00337584 | FAULT | Out record for Trans trip due to SIR 10264762 | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026347439317.4173611111 | 10263474 |  | Parent | FALSE | NO.2 66KV BUS VT AT RTS | 39317.4174 | 39317.4868 | DAILY | [12 empty] | 0
_1026483939317.7118055556 | 10264839 |  | Parent | FALSE | HWTS-SMTS 2 500KV WT | 39317.7118 | 39317.7194 | DAILY | 00119315 | FORCED | HWTS No2 500kV Line deenergised inspect faulty ROI | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026484139317.9173611111 | 10264841 |  | Parent | FALSE | HWTS-SMTS 2 500KV WT | 39317.9174 | 39317.9319 | DAILY | 00119315 | FORCED | HWTS No2 Line de-energised for temp repairs to ROI | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026484439317.9319444444 | 10264844 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB AT HWTS | 39317.9319 | 39317.9819 | DAILY | [12 empty] | 0
_1025011539318.3138888889 | 10250115 |  | Parent | FALSE | SMTS NO.2 330KV LINE NO.1 BUS CB AT DDTS | 39318.3139 | 39318.6715 | REPDAILY | [12 empty] | 0
_1024933339318.3145833333 | 10249333 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT GTS | 39318.3146 | 39318.6139 | DAILY | [12 empty] | 0
_1024878639318.3145833333 | 10248786 |  | Parent | FALSE | 2-4 220KV BUS TIE CB AT HTS | 39318.3146 | 39318.6472 | DAILY | [12 empty] | 0
_V75658A039319.2534722222 | V75658A0 |  | Parent | FALSE | A2 500/220KV TRANS B/PH AT KTS | 39319.2535 | 39320.7243 | CONT | 00001138 | SPICAPX | contractors "Aisteng" to weld blue phase trans lid | SPIPOWER | V756 | V756 - (KTS) OIL LEAK REPAIR WELD LID | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024918139319.2673611111 | 10249181 |  | Parent | TRUE | KTS NO.1 220KV LINE CB NO.1 BUS SIDE ROI AT WMTS | 39319.2674 | 39319.6569 | REPDAILY | [12 empty] | 0
_1026500339319.2673611111 | 10265003 | 10249181 | Child | FALSE | KTS NO.1 220KV LINE AT WMTS | 39319.2674 | 39319.6569 | REPDAILY | 00025734 | SPIMAINT | outage workorder for kts 1l rebates | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026502239319.2673611111 | 10265022 | 10249181 | Child | FALSE | FBTS NO.1 220KV LINE AT WMTS | 39319.2674 | 39319.6569 | REPDAILY | 00025735 | SPIMAINT | outage workorder for fbts 1l rebates | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_Z53158AM39319.2743055556 | Z53158AM |  | Parent | TRUE | EX - NO.4 220KV BUS AT ERTS | 39319.2743 | 39319.4153 | DAILY | 00004380 | VEN_AUG | No 4 Bus & ROTS No2 Line | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158AN39319.2743055556 | Z53158AN | Z53158AM | Child | FALSE | ROTS NO.2 220KV LINE AT ERTS | 39319.2743 | 39319.4153 | DAILY | 00012288 | VEN_AUG | Rebate Line outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026202139319.2743055556 | 10262021 |  | Parent | FALSE | B4 220/66KV TRANS AT ERTS | 39319.2743 | 39320.6104 | CONT | 00004372 | SPIMAINT | Condition Sup Monitoring Metro Trans 2dayEast Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058F939320.1659722222 | X32058F9 | X32058J9 | Child | FALSE | B3 220/66KV TRANS AT MTS | 39320.166 | 39320.334 | DAILY | 00363305 | SPICAPX | Trans Rebate for Bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058J939320.1659722222 | X32058J9 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MTS | 39320.166 | 39320.334 | DAILY | 00004564 | SPICAPX | No 2 220kv Bus, B3 Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024918139320.26875 | 10249181 |  | Parent | TRUE | KTS NO.1 220KV LINE CB NO.1 BUS SIDE ROI AT WMTS | 39320.2688 | 39320.5917 | REPDAILY | [12 empty] | 0
_1026500339320.26875 | 10265003 | 10249181 | Child | FALSE | KTS NO.1 220KV LINE AT WMTS | 39320.2688 | 39320.5917 | REPDAILY | 00025734 | SPIMAINT | outage workorder for kts 1l rebates | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026502239320.26875 | 10265022 | 10249181 | Child | FALSE | FBTS NO.1 220KV LINE AT WMTS | 39320.2688 | 39320.5917 | REPDAILY | 00025735 | SPIMAINT | outage workorder for fbts 1l rebates | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1026492139320.2791666667 | 10264921 |  | Parent | FALSE | W1 GEN TRANS NO.1 BUS 220KV CB AT YPS | 39320.2792 | 39321.3889 | CONT | [12 empty] | 0
_1026464639320.2881944444 | 10264646 |  | Parent | FALSE | SVTS-HTS 1 220KV E | 39320.2882 | 39320.4715 | DAILY | 00022771 | SPIMAINT | REPAIR HOT JOINT SVTS-HTS 1 LINE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024672839320.3138888889 | 10246728 |  | Parent | FALSE | A NORTH 22KV BUS PROT AT RTS | 39320.3139 | 39320.6 | DAILY | [12 empty] | 0
_1026471939320.4333333333 | 10264719 |  | Parent | FALSE | NO.8 22KV/415V S/S TRANS AT SMTS | 39320.4333 | 39321.5333 | DAILY | 00001327 | DBPROX | VSCAP to Dist Operation Centre for DISCO work | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1026464739320.475 | 10264647 |  | Parent | FALSE | SVTS-HTS 2 220KV E | 39320.475 | 39320.6299 | DAILY | 00022773 | SPIMAINT | REPAIR HOT JOINT | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858J539321.2506944445 | X49858J5 |  | Parent | FALSE | B1 220/66KV TRANS (HOT SPARE) AT MBTS | 39321.2507 | 39321.4035 | CONT | 00360627 | SPICAPX | Reconnect 220kv Droppers to Rack Structure & CT's | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER | NORMALLY OPEN | 0
_1024953639321.2930555556 | 10249536 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE NO.3 BUS CB AT KTS | 39321.2931 | 39322.5806 | CONT | [12 empty] | 0
_1025012439321.3125 | 10250124 |  | Parent | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB AT DDTS | 39321.3125 | 39322.6396 | DAILY | [12 empty] | 0
_Z53158AP39321.3430555556 | Z53158AP |  | Parent | FALSE | NO.1 CSC AT ROTS | 39321.3431 | 39321.691 | REPDAILY | 00004718 | VEN_AUG | De Energised Only Due to Exclusion zones | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026481139321.4034722222 | 10264811 |  | Parent | FALSE | B1 220/66KV TRANS (HOT SPARE) AT MBTS | 39321.4035 | 39322.291 | CONT | 00360627 | SPICAPX | Isolated Pending Commissioning | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER | NORMALLY OPEN | 0
_1026451539321.5493055556 | 10264515 |  | Parent | FALSE | WBTS 220KV LINE NO.1 BUS CB AT HOTS | 39321.5493 | 39321.7431 | DAILY | [12 empty] | 0
_Z53158AQ39322.2666666667 | Z53158AQ |  | Parent | FALSE | MTS NO.3 220KV LINE AT ROTS | 39322.2667 | 39323.659 | CONT | 00023099 | VEN_AUG | Transfer Conductors to adjacent Bay | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026204539322.2909722222 | 10262045 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 39322.291 | 39323.6694 | CONT | 00002830 | SPIMAINT | Condition Monitoring Metro Trans 2day North Area | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158AP39322.3076388889 | Z53158AP |  | Parent | FALSE | NO.1 CSC AT ROTS | 39322.3076 | 39322.7403 | REPDAILY | 00004718 | VEN_AUG | De Energised Only Due to Exclusion zones | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025149239322.3166666667 | 10251492 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CABLE AT RCTS | 39322.3167 | 39322.4896 | DAILY | 00356645 | SPIMAINT | OVERHAUL POWER CABLE (220KV & 66KV) (N) | SPIPOWER |  |  | Circuits | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026504139322.3166666667 | 10265041 | 10251492 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39322.3167 | 39322.4896 | DAILY | 00359891 | SPIMAINT | Rebate -OVERHAUL POWER CABLE (220KV & 66KV) (N) | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49858J639322.3180555556 | X49858J6 |  | Parent | FALSE | B1 220/66KV TRANS (HOT SPARE) AT MBTS | 39322.3181 | 39322.4979 | DAILY | 00360627 | SPICAPX | Commission B1 Transformer | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER | NORMALLY OPEN | 0
_X43258Y339322.3770833333 | X43258Y3 |  | Parent | FALSE | BSS 220KV LINE NO.1 BUS CB AT RCTS | 39322.3771 | 39322.5319 | DAILY | [12 empty] | 0
_1026451639322.3861111111 | 10264516 |  | Parent | FALSE | RCTS 220KV LINE NO.2 BUS CB AT HOTS | 39322.3861 | 39322.5361 | DAILY | [12 empty] | 0
_1027836739322.4569444445 | 10278367 |  | Parent | FALSE | B2 220/66KV TRANS AT MBTS | 39322.4569 | 39518.6528 | CONT | 00362372 | SPICAPX | B2 Trans Isolated / De-energised pending C/O | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026493939322.4986111111 | 10264939 |  | Parent | FALSE | B2 220/66KV TRANS AT MBTS | 39322.4986 | 39323.25 | CONT | 00362372 | SPICAPX | B2 Trans Isolated / De-energised pending C/O | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027836739322.4986111111 | 10278367 |  | Parent | FALSE | B2 220/66KV TRANS AT MBTS | 39322.4986 | 39518.6528 | CONT | 00362372 | SPICAPX | B2 Trans Isolated / De-energised pending C/O | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026451939322.5541666667 | 10264519 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT HOTS | 39322.5542 | 39322.6646 | DAILY | [12 empty] | 0
_1024779139322.5819444444 | 10247791 |  | Parent | FALSE | YWPS AUX TRANS 'B' 220KV LINE X PROT AT YPS | 39322.5819 | 39323.6312 | CONT | [12 empty] | 0
_X49858J839323.25 | X49858J8 |  | Parent | TRUE | EX - NO.1 220KV BUS AT MBTS | 39323.25 | 39323.7229 | REPDAILY | 00004001 | SPICAPX | Remove Bipods between OOS DPS Ln BSI and No1 Bus | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49858J939323.25 | X49858J9 | X49858J8 | Child | FALSE | EX - DDTS NO.2 220KV LINE AT MBTS | 39323.25 | 39323.7229 | REPDAILY | 00011750 | SPICAPX | Rebate W/O DDTS2 Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858K039323.25 | X49858K0 | X49858J8 | Child | FALSE | B2 220/66KV TRANS AT MBTS | 39323.25 | 39323.7229 | REPDAILY | 00362372 | SPICAPX | Perf calc, B2 Trans during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49858K139323.25 | X49858K1 | X49858J8 | Child | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39323.25 | 39323.7229 | REPDAILY | 00011755 | SPICAPX | Rebate W/O MKPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858K239323.25 | X49858K2 | X49858J8 | Child | FALSE | MBTS-EPS 2 220KV N | 39323.25 | 39323.7229 | REPDAILY | 00055381 | SPICAPX | Rebate W/O EPS #2 Line, No1 220kv Bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49858K339323.25 | X49858K3 | X49858J8 | Child | FALSE | WKPS 220KV LINE AT MBTS | 39323.25 | 39323.7229 | REPDAILY | 00011756 | SPICAPX | Rebate W/O WKPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49758G039323.2819444445 | X49758G0 |  | Parent | FALSE | BATS 220KV LINE AT BETS | 39323.2819 | 39325.9396 | CONT | 00016470 | SPICAPX | Out W/O BATS Line for cutover to its new 2B CB | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024954139323.2902777778 | 10249541 |  | Parent | FALSE | EX - B4 TRANS/GTS NO.3 220KV LINE CB AT KTS | 39323.2903 | 39324.6104 | CONT | [12 empty] | 0
_Z53158AP39323.3 | Z53158AP |  | Parent | FALSE | NO.1 CSC AT ROTS | 39323.3 | 39323.7222 | REPDAILY | 00004718 | VEN_AUG | De Energised Only Due to Exclusion zones | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025012139323.3131944445 | 10250121 |  | Parent | FALSE | MSS NO.2 LINE/SMTS NO.2 LINE 330KV CB AT DDTS | 39323.3132 | 39324.6819 | DAILY | [12 empty] | 0
_X49858K539323.3152777778 | X49858K5 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT MBTS | 39323.3153 | 39323.6181 | DAILY | [12 empty] | 0
_1025149439323.3215277778 | 10251494 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK CABLE AT RCTS | 39323.3215 | 39323.5083 | DAILY | 00356646 | SPIMAINT | OVERHAUL POWER CABLE (220KV & 66KV) (N) | SPIPOWER |  |  | Circuits | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258Y739323.3493055556 | X43258Y7 |  | Parent | FALSE | NO.1 TRANS GROUP 220KV CB AT RCTS | 39323.3493 | 39323.5 | DAILY | [12 empty] | 0
_1026452139323.3833333333 | 10264521 |  | Parent | FALSE | RCTS 220KV LINE NO.2 BUS CB AT HOTS | 39323.3833 | 39323.4931 | DAILY | [12 empty] | 0
_1026452039323.5486111111 | 10264520 |  | Parent | FALSE | WBTS 220KV LINE NO.1 BUS CB AT HOTS | 39323.5486 | 39323.6847 | DAILY | [12 empty] | 0
_X43258Y839323.5555555556 | X43258Y8 |  | Parent | FALSE | NO.2 TRANS GROUP 220KV CB AT RCTS | 39323.5556 | 39323.634 | DAILY | [12 empty] | 0
_1027018339323.9548611111 | 10270183 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 39323.9549 | 39327.8278 | CONT | [12 empty] | 0
_X49858J839324.25 | X49858J8 |  | Parent | TRUE | EX - NO.1 220KV BUS AT MBTS | 39324.25 | 39324.5597 | REPDAILY | 00004001 | SPICAPX | Remove Bipods between OOS DPS Ln BSI and No1 Bus | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49858J939324.25 | X49858J9 | X49858J8 | Child | FALSE | EX - DDTS NO.2 220KV LINE AT MBTS | 39324.25 | 39324.5597 | REPDAILY | 00011750 | SPICAPX | Rebate W/O DDTS2 Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858K039324.25 | X49858K0 | X49858J8 | Child | FALSE | B2 220/66KV TRANS AT MBTS | 39324.25 | 39324.5597 | REPDAILY | 00362372 | SPICAPX | Perf calc, B2 Trans during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49858K139324.25 | X49858K1 | X49858J8 | Child | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39324.25 | 39324.5597 | REPDAILY | 00011755 | SPICAPX | Rebate W/O MKPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858K239324.25 | X49858K2 | X49858J8 | Child | FALSE | MBTS-EPS 2 220KV N | 39324.25 | 39324.5597 | REPDAILY | 00055381 | SPICAPX | Rebate W/O EPS #2 Line, No1 220kv Bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49858K339324.25 | X49858K3 | X49858J8 | Child | FALSE | WKPS 220KV LINE AT MBTS | 39324.25 | 39324.5597 | REPDAILY | 00011756 | SPICAPX | Rebate W/O WKPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158AP39324.2944444444 | Z53158AP |  | Parent | FALSE | NO.1 CSC AT ROTS | 39324.2944 | 39324.7229 | REPDAILY | 00004718 | VEN_AUG | De Energised Only Due to Exclusion zones | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026357539324.3291666667 | 10263575 |  | Parent | FALSE | EX - FF 22KV FDR 184 CB AT BTS | 39324.3292 | 39309.6667 | CONT | [12 empty] | 0
_X43258Y939324.3638888889 | X43258Y9 |  | Parent | FALSE | R3 TRANS NO.1 BUS 220KV CB AT RCTS | 39324.3639 | 39324.5333 | DAILY | [12 empty] | 0
_1027473339324.3881944444 | 10274733 |  | Parent | FALSE | CBTS NO.4 500KV LINE AT HWTS | 39324.3882 | 39324.3965 | DAILY | 00016240 | FAULT | Rebate for line trip one end only SIR 10270387 | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026452239324.4597222222 | 10264522 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT HOTS | 39324.4597 | 39324.5153 | DAILY | [12 empty] | 0
_1027277739324.7777777778 | 10272777 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 39324.7778 | 39327.5137 | CONT | 00356080 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X2A858U039325.2645833333 | X2A858U0 |  | Parent | TRUE | NO.1 22KV CAP BANK S/S NO.1 BUS LINK CABLE CB AT BTS | 39325.2646 | 39325.4181 | DAILY | [12 empty] | 0
_X2A858Z139325.2645833333 | X2A858Z1 | X2A858U0 | Child | FALSE | NO.1 22KV CAPACITOR BANK AT BTS | 39325.2646 | 39325.4181 | DAILY | 00337002 | SPICAPX | rebate cb & esw changed over to new ones | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z53158AP39325.2916666667 | Z53158AP |  | Parent | FALSE | NO.1 CSC AT ROTS | 39325.2917 | 39325.7083 | REPDAILY | 00004718 | VEN_AUG | De Energised Only Due to Exclusion zones | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258Z139325.3333333333 | X43258Z1 |  | Parent | FALSE | R3 TRANS NO.2 BUS 220KV CB AT RCTS | 39325.3333 | 39325.4201 | DAILY | [12 empty] | 0
_1024953239325.3625 | 10249532 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 39325.3625 | 39325.6944 | DAILY | 00001147 | SPIMAINT | O/HAUL Transformer Div Mechanism (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025053139325.3993055556 | 10250531 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT WOTS | 39325.3993 | 39325.5903 | DAILY | 00004040 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_X2A858U139325.4277777778 | X2A858U1 |  | Parent | TRUE | NO.3 22KV CAP BANK S/S NO.3 BUS LINK CABLE CB AT BTS | 39325.4278 | 39325.634 | DAILY | [12 empty] | 0
_X2A858Z039325.4277777778 | X2A858Z0 | X2A858U1 | Child | FALSE | NO.3 22KV CAPACITOR BANK AT BTS | 39325.4278 | 39325.634 | DAILY | 00337011 | SPICAPX | Rebate cb & esw changed over to new ones | SPIPOWER | X2A8 | X2A8 - (BTS) STATION REBUILD | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V60458A039326.25625 | V60458A0 |  | Parent | FALSE | O.O.S BAY F LINE/F2 TRANS BYPASS AT SMTS | 39326.2562 | 39326.5701 | DAILY | 00363791 | SPICAPX | ERECT HYPOTRONICS | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_V75658A139326.2604166667 | V75658A1 |  | Parent | FALSE | A2 500/220KV TRANS B/PH AT KTS | 39326.2604 | 39327.6444 | CONT | 00001138 | SPICAPX | contractors "Aisteng" to weld blue phase trans lid | SPIPOWER | V756 | V756 - (KTS) OIL LEAK REPAIR WELD LID | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z51358D339326.2736111111 | Z51358D3 |  | Parent | FALSE | NO.2 220KV BUS AT RWTS | 39326.2736 | 39326.5139 | DAILY | 00007478 | DB_AUG | No 2 220kv Bus & No 3 220/66kv Trans 220kv CB | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027492639327.0027777778 | 10274926 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 39327.0028 | 39327.0049 | DAILY | 00060187 | FAULT | DDTS-MBTS No1 Line Auto Reclose at MBTS only | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027492739327.2159722222 | 10274927 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 39327.216 | 39327.2188 | DAILY | 00060194 | FAULT | DDTS-MBTS No2 Line Auto Reclose MBTS only | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027448639327.9263888889 | 10274486 |  | Parent | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39327.9264 | 39327.9701 | CONT | 00017905 | FAULT | GTS-PTH No1 Line Tripping | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058L339328.2298611111 | X32058L3 |  | Parent | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39328.2299 | 39328.6833 | REPDAILY | 00351697 | SPICAPX | Proxity Reasons | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158AR39328.2875 | Z53158AR |  | Parent | FALSE | RTS NO.1 220KV LINE AT ROTS | 39328.2875 | 39328.4778 | DAILY | 00023111 | VEN_AUG | Replacement of CVT | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158AP39328.3034722222 | Z53158AP |  | Parent | FALSE | NO.1 CSC AT ROTS | 39328.3035 | 39328.6 | REPDAILY | 00004718 | VEN_AUG | De Energised Only Due to Exclusion zones | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X49758G139328.3125 | X49758G1 |  | Parent | TRUE | NO.1 220KV BUS AT BETS | 39328.3125 | 39328.6458 | DAILY | 00016305 | SPICAPX | Out W/O No1 220kV Bus to remove OOS bay E ROI | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758G239328.3125 | X49758G2 | X49758G1 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39328.3125 | 39328.6458 | DAILY | 00016040 | SPICAPX | Perf calc W/O No2 Trans during No1 220 Bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027449139328.3506944444 | 10274491 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 39328.3507 | 39330.6993 | CONT | 00016424 | GENCO | W2 Gen Isolations | GENCO |  |  | Circuits | 3rd Party | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258Y539328.4402777778 | X43258Y5 |  | Parent | TRUE | KGTS 220KV LINE CB AT RCTS | 39328.4403 | 39328.5625 | DAILY | [12 empty] | 0
_X43258Z839328.4402777778 | X43258Z8 | X43258Y5 | Child | FALSE | KGTS 220KV LINE AT RCTS | 39328.4403 | 39328.5625 | DAILY | 00016959 | SPICAPX | rebate W/O for KGTS Line outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258Y639328.5833333333 | X43258Y6 |  | Parent | TRUE | HOTS 220KV LINE CB AT RCTS | 39328.5833 | 39328.659 | DAILY | [12 empty] | 0
_X43258Z939328.5833333333 | X43258Z9 | X43258Y6 | Child | FALSE | HOTS 220KV LINE AT RCTS | 39328.5833 | 39328.659 | DAILY | 00016954 | SPICAPX | Rebate W/O for HOTS line outage | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026496539329.2631944444 | 10264965 |  | Parent | TRUE | HWTS NO.2 LINE/SYTS NO.2 LINE CB HWTS LINE SIDE ISOL AT SMTS | 39329.2632 | 39333.309 | CONT | [12 empty] | 0
_1027491639329.2631944444 | 10274916 | 10264965 | Child | FALSE | HWTS NO.2 500KV LINE AT SMTS | 39329.2632 | 39333.691 | CONT | 00012437 | SPIMAINT | Rebate -SMTS 500kV GIS Sw/gear Repair Faulty Isol | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158AP39329.2916666667 | Z53158AP |  | Parent | FALSE | NO.1 CSC AT ROTS | 39329.2917 | 39329.7083 | REPDAILY | 00004718 | VEN_AUG | De Energised Only Due to Exclusion zones | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026487439329.2951388889 | 10264874 |  | Parent | FALSE | B3 220/66KV TRANS AT HTS | 39329.2951 | 39329.6764 | DAILY | 00004447 | SPIMAINT | Low CT IRs 3 66 X Bus Prot at HTS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058L339329.3131944445 | X32058L3 |  | Parent | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39329.3132 | 39329.6354 | REPDAILY | 00351697 | SPICAPX | Proxity Reasons | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158AX39329.3444444445 | Z53158AX |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39329.3444 | 39329.7007 | DAILY | 00112418 | VEN_AUG | No 2 220kv Cap Bank CB & TTS Line No2 Bus CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258Y439329.3722222222 | X43258Y4 |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT RCTS | 39329.3722 | 39329.4361 | DAILY | [12 empty] | 0
_1025011839329.4194444444 | 10250118 |  | Parent | FALSE | MSS NO.2 330KV LINE NO.2 BUS CB AT DDTS | 39329.4194 | 39330.641 | CONT | [12 empty] | 0
_1026488939329.8298611111 | 10264889 |  | Parent | FALSE | EX - NO.1 220/22KV TRANS BANK AT MTS | 39329.8299 | 39330.1722 | DAILY | 00026901 | SPIMAINT | Repaire Cable to transformer | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027455839329.9666666667 | 10274558 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39329.9667 | 39332.8104 | CONT | 00356084 | GENCO | Gen 6 at HWPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158AS39330.2694444444 | Z53158AS |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 39330.2694 | 39330.6583 | DAILY | 00004776 | VEN_AUG | Replaced bipod sliding supports & O/Haul Cap Bank | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158AT39330.2694444444 | Z53158AT | Z53158AS | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39330.2694 | 39330.6583 | DAILY | 00354024 | VEN_AUG | Rebate Cap Bank | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1026476339330.2916666667 | 10264763 |  | Parent | FALSE | M2 500/275KV TRANS OIL PUMP B AT HYTS | 39330.2917 | 39330.7201 | CONT | [12 empty] | 0
_1010525739330.2965277778 | 10105257 |  | Parent | FALSE | R3 220/66/22KV TRANS AT KGTS | 39330.2965 | 39330.7236 | REPDAILY | 00017375 | SPIMAINT | Repair Oil Leaks | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158AP39330.3097222222 | Z53158AP |  | Parent | FALSE | NO.1 CSC AT ROTS | 39330.3097 | 39330.6653 | REPDAILY | 00004718 | VEN_AUG | De Energised Only Due to Exclusion zones | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027459039330.5173611111 | 10274590 |  | Parent | TRUE | NO.1 TRANS 66KV CB AT BATS | 39330.5174 | 39330.625 | DAILY | [12 empty] | 0
_1027471939330.5173611111 | 10274719 | 10274590 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39330.5174 | 39330.625 | DAILY | 00006554 | FAULT | Perf calc W/O No1 Trans during 66kV CB CT replace | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027462139330.83125 | 10274621 |  | Parent | FALSE | ROTS NO.4 500KV LINE AT CBTS | 39330.8313 | 39330.9306 | DAILY | 00359492 | FORCED | Remove B Phase CVT | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158AU39331.2708333333 | Z53158AU |  | Parent | TRUE | NO.4 220KV BUS AT ROTS | 39331.2708 | 39331.7486 | CONT | 00329012 | VEN_AUG | No4 Bus outage to Install SVTS No1 Line Bus ROI | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158AV39331.2708333333 | Z53158AV | Z53158AU | Child | FALSE | MTS NO.1 220KV LINE AT ROTS | 39331.2708 | 39331.7486 | DAILY | 00350667 | VEN_AUG | Rebate Line for Bus Outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z54558A139331.2708333333 | Z54558A1 |  | Parent | FALSE | A2 515/220KV TRANS BANK AT ROTS | 39331.2708 | 39332.6903 | CONT | 00362994 | SPIMAINT | A2 Tran , SS Trans & Trans 500kv CB's | SPIPOWER | Z545 | Z545 - (ROTS) A2 500/220KV TRANSFORMER CONTESTABLE | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1024850339331.2902777778 | 10248503 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 39331.2903 | 39331.6139 | DAILY | 00007456 | SPIMAINT | O/HAUL Transformer Div Mechanism (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025166639331.3090277778 | 10251666 |  | Parent | FALSE | B5 220/66KV TRANS GROUP AT BLTS | 39331.309 | 39332.7028 | CONT | 00018452 | SPIMAINT | Condition Monitoring Metro Trans 5day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010525739331.3118055556 | 10105257 |  | Parent | FALSE | R3 220/66/22KV TRANS AT KGTS | 39331.3118 | 39331.7208 | REPDAILY | 00017375 | SPIMAINT | Repair Oil Leaks | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027465339331.5777777778 | 10274653 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39331.5778 | 39331.9854 | DAILY | 00002862 | SPIMAINT | Repair 22kV Cable at S/S trans | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027459339331.5861111111 | 10274593 |  | Parent | TRUE | JLA NO.1 220KV LINE CB AT TBTS | 39331.5861 | 39331.6056 | DAILY | [12 empty] | 0
_1027460239331.5861111111 | 10274602 | 10274593 | Child | FALSE | JLA NO.1 220KV LINE AT TBTS | 39331.5861 | 39331.6056 | DAILY | 00018301 | SPIMAINT | Rebat Line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058L639331.5951388889 | X32058L6 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT MTS | 39331.5951 | 39367.4542 | CONT | [12 empty] | 0
_Z53158BA39331.75 | Z53158BA |  | Parent | FALSE | EX - SVTS NO.1 220KV LINE NO.4 BUS CB AT ROTS | 39331.75 | 39339.3278 | CONT | [12 empty] | 0
_1027470639331.9201388889 | 10274706 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 39331.9201 | 39334.0736 | CONT | [12 empty] | 0
_1027470739331.9763888889 | 10274707 |  | Parent | FALSE | NO.4 GEN TRANS NO.1 BUS 220KV CB AT HWPS | 39331.9764 | 39334.7188 | CONT | [12 empty] | 0
_1024850939332.2909722222 | 10248509 |  | Parent | FALSE | 2-4 66KV BUS TIE CB AT RWTS | 39332.291 | 39332.5958 | DAILY | [12 empty] | 0
_Z53158AP39332.2916666667 | Z53158AP |  | Parent | FALSE | NO.1 CSC AT ROTS | 39332.2917 | 39332.6667 | REPDAILY | 00004718 | VEN_AUG | De Energised Only Due to Exclusion zones | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024736939332.3055555556 | 10247369 |  | Parent | TRUE | R2 220/66/22KV TRANS AT KGTS | 39332.3056 | 39332.7069 | DAILY | 00017344 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025396139332.3055555556 | 10253961 | 10247369 | Child | FALSE | R2 220/66/22KV TRANS AT KGTS | 39332.3056 | 39332.7069 | DAILY | 00017344 | SPIMAINT | Oil Level in Bushing | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026083039332.3055555556 | 10260830 | 10247369 | Child | TRUE | R2 220/66/22KV TRANS AT KGTS | 39332.3056 | 39332.7069 | DAILY | 00017344 | SPIMAINT | Perf calc No2 transformer outage at KGTS | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026083339332.3055555556 | 10260833 | 10260830 | Child | FALSE | R2 220/66/22KV TRANS AT KGTS | 39332.3056 | 39332.7069 | DAILY | 00017344 | SPIMAINT | Oil Level in Bushing | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027465539332.375 | 10274655 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39332.375 | 39332.6451 | DAILY | 00002863 | SPIMAINT | Investigate 22kV Cable integrity at S/S trans | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_V75658A239333.2541666667 | V75658A2 |  | Parent | FALSE | A2 500/220KV TRANS B/PH AT KTS | 39333.2542 | 39333.5306 | CONT | 00001138 | SPICAPX | contractors "Aisteng" to weld blue phase trans lid | SPIPOWER | V756 | V756 - (KTS) OIL LEAK REPAIR WELD LID | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z51358E039333.2826388889 | Z51358E0 |  | Parent | FALSE | NO.3 66KV BUS AT RWTS | 39333.2826 | 39333.7667 | REPDAILY | 00007480 | SPICAPX | Remove redundant O.O.S No 3 66Kv Bus VT | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026203239333.2881944444 | 10262032 |  | Parent | FALSE | B1 220/66KV TRANS AT HTS | 39333.2882 | 39334.6285 | CONT | 00004445 | SPIMAINT | Condition Sup Monitoring Metro Trans 2day East | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024858839333.2902777778 | 10248588 |  | Parent | FALSE | 1-2A 220KV BUS TIE CB AT RTS | 39333.2903 | 39334.5757 | CONT | [12 empty] | 0
_1027040739333.30625 | 10270407 |  | Parent | FALSE | HWTS NO.2 LINE/SYTS NO.2 LINE CB HWTS LINE SIDE ISOL AT SMTS | 39333.3063 | 39333.6882 | DAILY | [12 empty] | 0
_1027459039333.3243055556 | 10274590 |  | Parent | TRUE | NO.1 TRANS 66KV CB AT BATS | 39333.3243 | 39333.6819 | DAILY | [12 empty] | 0
_1027491939333.3243055556 | 10274919 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 39333.3243 | 39333.6819 | DAILY | 00006554 | SPIMAINT | Perf calc W/O No1 Trans during 66kV CB CT replace | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026496739333.6909722222 | 10264967 |  | Parent | FALSE | HWTS-SMTS 2 500KV G | 39333.691 | 39334.4819 | DAILY | 00020242 | SPIMAINT | restore flexible connect to hwts 2l entrance bush | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358E039334.2722222222 | Z51358E0 |  | Parent | FALSE | NO.3 66KV BUS AT RWTS | 39334.2722 | 39334.8264 | REPDAILY | 00007480 | SPICAPX | Remove redundant O.O.S No 3 66Kv Bus VT | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025076339334.2888888889 | 10250763 |  | Parent | FALSE | JLGA 220KV BUS AT JLGA | 39334.2889 | 39334.6667 | DAILY | 00325257 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024673239334.2993055556 | 10246732 |  | Parent | FALSE | C NORTH 22KV BUS PROT AT RTS | 39334.2993 | 39334.5764 | DAILY | [12 empty] | 0
_1002306639334.3034722222 | 10023066 |  | Parent | TRUE | T028 KTS -BLTS 1 220KV | 39334.3035 | 39334.5535 | DAILY | [12 empty] | 0
_1027552739334.3034722222 | 10275527 | 10023066 | Child | FALSE | KTS 220KV LINE AT BLTS | 39334.3035 | 39334.5535 | DAILY | 00024011 | SPIMAINT | Rebate-Flashed ins, B Ph, both strings (4) STRAIN | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027474039334.3402777778 | 10274740 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 39334.3403 | 39334.3597 | DAILY | 00356081 | GENCO | GenCo work | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027453439334.39375 | 10274534 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT SMTS | 39334.3938 | 39335.3333 | DAILY | 00001323 | DBPROX | VSCAP to DOC | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1027463039334.5 | 10274630 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39334.5 | 39334.5083 | DAILY | 00012436 | FAULT | inspect GIS ROI moving arcing contact | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027462639334.5138888889 | 10274626 |  | Parent | FALSE | ROTS NO.3 500KV LINE AT SMTS | 39334.5139 | 39334.5222 | DAILY | 00012438 | FAULT | inspect GIS ROI moving arcing contact | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027462239334.5590277778 | 10274622 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT SMTS | 39334.559 | 39334.5694 | DAILY | 00012440 | FAULT | inspect GIS ROI moving arcing contact | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027462839334.5694444444 | 10274628 |  | Parent | FALSE | SYTS NO.1 500KV LINE AT SMTS | 39334.5694 | 39334.5792 | DAILY | 00012439 | FAULT | inspect GIS ROI moving arcing contact | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027462439334.5819444444 | 10274624 |  | Parent | FALSE | KTS 500KV LINE AT SMTS | 39334.5819 | 39334.5917 | DAILY | 00012441 | FAULT | inspect GIS ROI moving arcing contact | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025012739335.3159722222 | 10250127 |  | Parent | FALSE | SMTS NO.1 330KV LINE NO.1 BUS CB AT DDTS | 39335.316 | 39336.6958 | CONT | [12 empty] | 0
_1024840339335.3340277778 | 10248403 |  | Parent | FALSE | NO.3 GEN TRANS NO.2 BUS 220KV CB AT HWPS | 39335.334 | 39339.6021 | CONT | [12 empty] | 0
_1027471439335.3548611111 | 10274714 |  | Parent | FALSE | JLGB NO.1 UNIT TRANS DISC CB AT JLGB | 39335.3549 | 39378.6375 | CONT | [12 empty] | 0
_1026285139335.4909722222 | 10262851 |  | Parent | FALSE | JINDERA 330KV LINE NO.1 BUS CB CT R/PH AT WOTS | 39335.491 | 39335.7319 | DAILY | [12 empty] | 0
_1027477439335.5604166667 | 10274774 |  | Parent | FALSE | YWPS NO.3 220KV LINE AT YPS | 39335.5604 | 39338.6056 | CONT | 00016426 | GENCO | W3 GTG 220kV Line Isols & Earths for SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027477039335.5611111111 | 10274770 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS AT JLGA | 39335.5611 | 39337.5993 | CONT | 00009820 | GENCO | JLGS Genco WSCAP | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1025164239336.29375 | 10251642 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT MLTS | 39336.2937 | 39338.7993 | CONT | 00337580 | SPIMAINT | Condition Monitoring Metro Trans 3day North Area | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025052439336.3381944444 | 10250524 | 10250527 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT TTS | 39336.3382 | 39336.6667 | DAILY | 00337509 | SPIMAINT | O/Haul - Cap Bank & E/Sw (W) | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025052739336.3381944444 | 10250527 |  | Parent | TRUE | NO.4B 66KV CAPACITOR BANK CB AT TTS | 39336.3382 | 39336.6667 | DAILY | [12 empty] | 0
_1027452039336.3548611111 | 10274520 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39336.3549 | 39336.6771 | DAILY | 00319998 | APDALCOA | SCAP for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1026285239336.3854166667 | 10262852 |  | Parent | FALSE | EX - JINDERA LINE NO.2 BUS CB CT R/PH AT WOTS | 39336.3854 | 39336.6194 | DAILY | [12 empty] | 0
_1024871639336.4361111111 | 10248716 |  | Parent | FALSE | YPS NO.6 220KV LINE NO.3 BUS CB AT ROTS | 39336.4361 | 39338.4653 | CONT | [12 empty] | 0
_1027453939337.2861111111 | 10274539 |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39337.2861 | 39337.4187 | DAILY | 00007452 | SPIMAINT | Repair Hot Joint | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026270239337.2881944444 | 10262702 |  | Parent | FALSE | YPS -ROTS 5 220KV G | 39337.2882 | 39337.6868 | DAILY | 00020472 | SPIMAINT | Repair hot joint | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026285439337.3069444444 | 10262854 |  | Parent | TRUE | DDTS 330KV LINE CVT R/PH AT WOTS | 39337.3069 | 39337.7014 | DAILY | [12 empty] | 0
_1027493539337.3069444444 | 10274935 | 10262854 | Child | FALSE | DDTS 330KV LINE AT WOTS | 39337.3069 | 39337.7014 | DAILY | 00012054 | SPIMAINT | Rebate W/O for DDTS Line Outage | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024823539337.3333333333 | 10248235 |  | Parent | FALSE | W3 GEN TRANS 220KV LINE E/SW AT YPS | 39337.3333 | 39337.5625 | DAILY | [12 empty] | 0
_1027484839337.6027777778 | 10274848 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39337.6028 | 39338.4514 | CONT | 00003104 | FORCED | Replace Cap bank broken isulators | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027467139338.3298611111 | 10274671 |  | Parent | FALSE | HWPS-YPS 1 220KV G | 39338.3299 | 39338.6451 | DAILY | 00020461 | SPIMAINT | Hot Joint | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027482539338.3708333333 | 10274825 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 39338.3708 | 39338.3965 | DAILY | 00001328 | FAULT | inspect GIS ROI moving contacts | SPIPOWER |  |  | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1027489839338.3729861111 | 10274898 |  | Parent | FALSE | A1 TRANS NO.1 BUS 220KV CB AT MLTS | 39338.373 | 39339.3701 | CONT | [12 empty] | 0
_X43258Z639338.4208333333 | X43258Z6 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39338.4208 | 39338.5826 | DAILY | 00337581 | SPICAPX | Out W/O No1 Tr de-energ to repair DC E-fault | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49758H539339.2680555556 | X49758H5 |  | Parent | FALSE | BATS 220KV LINE AT BETS | 39339.2681 | 39339.6944 | DAILY | 00016470 | SPICAPX | Out W/O BATS Line to decommiss it CVT's | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027482339339.2895833333 | 10274823 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 39339.2896 | 39339.3028 | DAILY | 00026099 | FORCED | Urgent Inspection GIS ROI moving contact fail | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024590939339.2923611111 | 10245909 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT TSTS | 39339.2924 | 39339.6035 | DAILY | 00329164 | SPIMAINT | O/Haul - 220kV CAP BANK (EM) | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1024911239339.2951388889 | 10249112 |  | Parent | FALSE | B2 TRANS 66KV CB AT WMTS | 39339.2951 | 39339.6396 | DAILY | [12 empty] | 0
_1026357939339.2986111111 | 10263579 |  | Parent | TRUE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39339.2986 | 39339.625 | DAILY | 00007399 | SPIMAINT | Re-Balance Cap Bank at RWTS | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027468439339.3138888889 | 10274684 |  | Parent | FALSE | HWPS-YPS 2 220KV G | 39339.3139 | 39339.5813 | DAILY | 00020462 | SPIMAINT | Repaire Hot Joint | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024895239339.3243055556 | 10248952 |  | Parent | FALSE | O.O.S SPARE TRANS BANK AT DDTS | 39339.3243 | 39339.6354 | DAILY | 00337559 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Main Transformers | Alstom | 330 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758G839339.3263888889 | X49758G8 |  | Parent | TRUE | NO.3 66KV BUS AT BETS | 39339.3264 | 39339.7812 | DAILY | 00016366 | SPICAPX | Out W/O No3 66kV bus to reconnect VT & 3A/B Cap | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758G939339.3263888889 | X49758G9 | X49758G8 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT BETS | 39339.3264 | 39339.7812 | DAILY | 00350820 | SPICAPX | Rebate W/O No3A Cap bk during No3 66kV bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49758H039339.3263888889 | X49758H0 | X49758G8 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 39339.3264 | 39339.7812 | DAILY | 00016304 | SPICAPX | Rebate W/O No3B Cap bk during No3 66kV bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758H139339.3263888889 | X49758H1 | X49758G8 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39339.3264 | 39339.7812 | DAILY | 00016040 | SPICAPX | Perf calc W/O No2 Trans during No3 66kV bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158BM39339.3333333333 | Z53158BM |  | Parent | TRUE | NO.4 220KV BUS AT ROTS | 39339.3333 | 39339.5354 | DAILY | 00329012 | VEN_AUG | Functional test on Future SVTS 1 Line 4 Bus CB ROI | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158BN39339.3333333333 | Z53158BN | Z53158BM | Child | FALSE | MTS NO.1 220KV LINE AT ROTS | 39339.3333 | 39339.5354 | DAILY | 00350667 | VEN_AUG | rebate for Bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158BO39339.5361111111 | Z53158BO |  | Parent | FALSE | SVTS NO.1 220KV LINE NO.4 BUS CB AT ROTS | 39339.5361 | 39340.3076 | DAILY | [12 empty] | 0
_X49758H239339.78125 | X49758H2 |  | Parent | TRUE | EX - NO.3 66KV CAPACITOR BANK CB AT BETS | 39339.7812 | 39343.6896 | CONT | [12 empty] | 0
_X49758H339339.78125 | X49758H3 | X49758H2 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT BETS | 39339.7812 | 39343.6896 | CONT | 00350820 | SPICAPX | Rebate W/O 3A Cap bank during CB commission | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49758H439339.78125 | X49758H4 | X49758H2 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 39339.7812 | 39343.6896 | CONT | 00016304 | SPICAPX | Rebate W/O 3B Cap bank during CB commission | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z53158AW39340.2777777778 | Z53158AW |  | Parent | FALSE | SVTS NO.1 220KV LINE AT ROTS | 39340.2778 | 39341.6528 | CONT | 00350027 | VEN_AUG | Commission SVTS No 1 line No4 Bus CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158BB39340.2951388889 | Z53158BB |  | Parent | TRUE | EX - NO.1 220KV BUS AT ERTS | 39340.2951 | 39340.5028 | DAILY | 00004378 | VEN_AUG | Proving interlocks on No 1 Bus ROI & Trans ROI | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158BC39340.2951388889 | Z53158BC | Z53158BB | Child | FALSE | B1 220/66KV TRANS AT ERTS | 39340.2951 | 39340.5028 | DAILY | 00004370 | VEN_AUG | Trans Rebate for bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158BD39340.2951388889 | Z53158BD | Z53158BB | Child | FALSE | CBTS NO.2 220KV LINE AT ERTS | 39340.2951 | 39340.5028 | DAILY | 00012284 | VEN_AUG | Line Rebate for bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158BE39340.2951388889 | Z53158BE | Z53158BB | Child | FALSE | ROTS NO.1 220KV LINE AT ERTS | 39340.2951 | 39340.5028 | DAILY | 00012289 | VEN_AUG | Line Rebate for bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027493139340.4722222222 | 10274931 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39340.4722 | 39340.4917 | DAILY | [12 empty] | 0
_Z53158BF39340.5048611111 | Z53158BF |  | Parent | TRUE | EX - NO.4 220KV BUS AT ERTS | 39340.5049 | 39340.6021 | DAILY | 00004380 | VEN_AUG | Proving interlocks on No 4 Bus ROI & Trans ROI | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158BG39340.5048611111 | Z53158BG | Z53158BF | Child | FALSE | B4 220/66KV TRANS AT ERTS | 39340.5049 | 39340.6021 | DAILY | 00004372 | VEN_AUG | Trans Rebate for bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158BH39340.5048611111 | Z53158BH | Z53158BF | Child | FALSE | CBTS NO.1 220KV LINE AT ERTS | 39340.5049 | 39340.6021 | DAILY | 00012286 | VEN_AUG | Line Rebate for bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158BI39340.5048611111 | Z53158BI | Z53158BF | Child | FALSE | ROTS NO.2 220KV LINE AT ERTS | 39340.5049 | 39340.6021 | DAILY | 00012288 | VEN_AUG | Line Rebate for bus outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158BJ39340.6041666667 | Z53158BJ |  | Parent | FALSE | EX - NO.3 220KV BUS AT ERTS | 39340.6042 | 39340.7 | DAILY | 00004379 | VEN_AUG | Check ROI on No3 Bus & Trans ROI | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027493239340.9625 | 10274932 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 39340.9625 | 39350.9042 | CONT | 00356080 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358B639341.2805555556 | Z51358B6 |  | Parent | TRUE | NO.4 66KV BUS AT RWTS | 39341.2806 | 39341.6826 | DAILY | 00007481 | SPICAPX | Bus outage & BH 66kv FDR | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358B739341.2805555556 | Z51358B7 | Z51358B6 | Child | FALSE | B4 220/66KV TRANS AT RWTS | 39341.2806 | 39341.6826 | DAILY | 00007451 | SPICAPX | Rebate Tran for bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z60258A139342.2638888889 | Z60258A1 |  | Parent | FALSE | EX - TTS NO.2 220KV LINE AT SMTS | 39342.2639 | 39342.9042 | DAILY | 00013358 | VEN_AUG | remove tts 2l isol, esw & line vt & h2 tr esw | SPIPOWER | Z602 | Z602 - NOW Z730 (SMTS) ESTABLISH A 220KV SWITCHYARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z54358A039342.2763888889 | Z54358A0 |  | Parent | FALSE | GTS NO.1 220KV LINE AT MLTS | 39342.2764 | 39344.6597 | CONT | 00022489 | VEN_AUG | Remove Line Traps and Connections | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027493839342.3805555556 | 10274938 |  | Parent | FALSE | YWPS NO.3 220KV LINE AT YPS | 39342.3806 | 39344.5062 | CONT | 00016426 | GENCO | Gen 3 at YPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026414239342.575 | 10264142 |  | Parent | TRUE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39342.575 | 39342.675 | REPDAILY | 00016040 | SPIMAINT | OPTEC Operator training | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026414339342.575 | 10264143 | 10264142 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39342.575 | 39342.675 | REPDAILY | 00016040 | SPIMAINT | perf Calc for 2A/2BTrans Grp during Outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026204739343.2708333333 | 10262047 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT SMTS | 39343.2708 | 39345.7 | CONT | 00026101 | SPIMAINT | Condition Sup Monitoring Metro Trans 3day West | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027475139343.2993055556 | 10274751 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39343.2993 | 39343.7 | REPDAILY | 00022691 | APDALCOA | SCAP to PTH work by ALCOA PT HENRY | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1024874239343.3013888889 | 10248742 |  | Parent | FALSE | RWTS 220KV LINE NO.4 BUS CB AT ROTS | 39343.3014 | 39345.4701 | CONT | [12 empty] | 0
_1027475039343.3138888889 | 10274750 |  | Parent | FALSE | A1 TRANS NO.3 BUS 500KV CB TRANS SIDE ROI AT LYPS | 39343.3139 | 39343.6715 | DAILY | [12 empty] | 0
_1010278839343.3180555556 | 10102788 |  | Parent | FALSE | HWTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 39343.3181 | 39343.3243 | CONT | [12 empty] | 0
_1025807639343.3361111111 | 10258076 |  | Parent | FALSE | WOTS 330KV LINE/H3 TRANS CB CT R/PH AT DDTS | 39343.3361 | 39343.4764 | DAILY | [12 empty] | 0
_V62258B739343.3395833333 | V62258B7 |  | Parent | FALSE | HWTS NO.2 LINE/SYTS NO.2 LINE 500KV CB AT SMTS | 39343.3396 | 39344.6188 | CONT | [12 empty] | 0
_1026095639343.3479166667 | 10260956 |  | Parent | FALSE | LYGS A1 TRANS 500KV CB AT LYPS | 39343.3479 | 39343.4424 | DAILY | [12 empty] | 0
_1025836739343.4770833333 | 10258367 |  | Parent | FALSE | H1 TRANS NO.2 BUS 330KV CB CT R/PH AT DDTS | 39343.4771 | 39343.575 | DAILY | [12 empty] | 0
_1026414239343.5722222222 | 10264142 |  | Parent | TRUE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39343.5722 | 39343.6354 | REPDAILY | 00016040 | SPIMAINT | OPTEC Operator training | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026414339343.5722222222 | 10264143 | 10264142 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39343.5722 | 39343.6354 | REPDAILY | 00016040 | SPIMAINT | perf Calc for 2A/2BTrans Grp during Outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027475139344.2993055556 | 10274751 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39344.2993 | 39344.7055 | REPDAILY | 00022691 | APDALCOA | SCAP to PTH work by ALCOA PT HENRY | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z53158BR39344.3083333333 | Z53158BR |  | Parent | FALSE | CBTS NO.1 220KV LINE AT ERTS | 39344.3083 | 39344.6736 | DAILY | 00012286 | VEN_AUG | Install Screens on rack leg | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024977939344.3180555556 | 10249779 |  | Parent | FALSE | DDTS NO.1 LINE/SHTS NO.1 LINE 220KV CB AT GNTS | 39344.3181 | 39344.6639 | DAILY | [12 empty] | 0
_1027502839344.4208333333 | 10275028 |  | Parent | FALSE | SMTS NO.1 500KV LINE AT SYTS | 39344.4208 | 39344.4299 | CONT | 00016971 | FAULT | SYTS - SMTS NO.1 500KV LINE Tripped | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026414239344.55625 | 10264142 |  | Parent | TRUE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39344.5563 | 39344.6312 | REPDAILY | 00016040 | SPIMAINT | OPTEC Operator training | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026414339344.55625 | 10264143 | 10264142 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39344.5563 | 39344.6312 | REPDAILY | 00016040 | SPIMAINT | perf Calc for 2A/2BTrans Grp during Outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z54358A139344.6173611111 | Z54358A1 |  | Parent | FALSE | A2 TRANS NO.1 BUS 220KV CB AT MLTS | 39344.6174 | 39514.6595 | CONT | [12 empty] | 0
_Z54358A139344.6590277778 | Z54358A1 |  | Parent | FALSE | A2 TRANS NO.1 BUS 220KV CB AT MLTS | 39344.659 | 39514.6595 | CONT | [12 empty] | 0
_1027502739345.01875 | 10275027 |  | Parent | FALSE | W2 GEN TRANS NO.2 BUS 220KV CB AT YPS | 39345.0188 | 39348.7111 | CONT | [12 empty] | 0
_1024768439345.2729166667 | 10247684 |  | Parent | FALSE | TSTS 220KV LINE AT TTS | 39345.2729 | 39345.6722 | REPDAILY | 00015736 | SPIMAINT | O/Haul - 220kV Line (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009266039345.2916666667 | 10092660 |  | Parent | FALSE | DDTS NO.1 220KV LINE AT GNTS | 39345.2917 | 39345.7028 | REPDAILY | 00021791 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027475139345.2979166667 | 10274751 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39345.2979 | 39345.7188 | REPDAILY | 00022691 | APDALCOA | SCAP to PTH work by ALCOA PT HENRY | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1026414039345.4472222222 | 10264140 |  | Parent | FALSE | EX - 3-4 66KV BUS TIE CB AT BETS | 39345.4472 | 39345.6583 | DAILY | [12 empty] | 0
_1027523739345.9263888889 | 10275237 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 39345.9264 | 39345.9306 | DAILY | 00060194 | FAULT | DDTS-MBTS No2 Line Auto Reclose MBTS only | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024768439346.2770833333 | 10247684 |  | Parent | FALSE | TSTS 220KV LINE AT TTS | 39346.2771 | 39346.5736 | REPDAILY | 00015736 | SPIMAINT | O/Haul - 220kV Line (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009266039346.2923611111 | 10092660 |  | Parent | FALSE | DDTS NO.1 220KV LINE AT GNTS | 39346.2924 | 39346.6451 | REPDAILY | 00021791 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024851639346.2979166667 | 10248516 |  | Parent | FALSE | L2 TRANS 22KV CB AT RWTS | 39346.2979 | 39346.6056 | DAILY | [12 empty] | 0
_1026326739346.4090277778 | 10263267 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39346.409 | 39346.4549 | DAILY | [12 empty] | 0
_1027514639346.4868055556 | 10275146 |  | Parent | FALSE | SYN/COND AT FBTS | 39346.4868 | 39346.6701 | CONT | 00002697 | FAULT | FBTS Sync Cond Repairs | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027460339346.5 | 10274603 |  | Parent | FALSE | B1 TRANS 220KV CB AT TBTS | 39346.5 | 39346.5208 | DAILY | [12 empty] | 0
_Z51358E939347.2583333333 | Z51358E9 |  | Parent | FALSE | NO.3 66KV BUS AT RWTS | 39347.2583 | 39347.7667 | REPDAILY | 00007480 | SPICAPX | No3 66KV BUS & No1 66/22KV Trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X41758A439347.2597222222 | X41758A4 |  | Parent | FALSE | B2 220/66KV TRANS AT RWTS | 39347.2597 | 39348.7292 | CONT | 00007450 | SPICAPX | Replace 220kv Bushings in No2 Trans | SPIPOWER | X417 | X417 - 220KV BUSHING REPLACEMENT 2004/05 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V60458A239347.2708333333 | V60458A2 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39347.2708 | 39347.6444 | REPDAILY | 00012436 | SPICAPX | erect hv test bus in bay a | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026211239347.2944444444 | 10262112 |  | Parent | FALSE | B4 220/66KV TRANS AT RTS | 39347.2944 | 39348.5625 | CONT | 00007332 | SPIMAINT | Condition Sup Monitoring Metro Trans 2day East | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51058E239347.2958333333 | Z51058E2 |  | Parent | FALSE | B3 TRANS NO.3 BUS 220KV CB AT ATS | 39347.2958 | 39348.5986 | CONT | [12 empty] | 0
_X66558A039347.3020833333 | X66558A0 |  | Parent | FALSE | SVTS-HTS 1 220KV E | 39347.3021 | 39347.6896 | DAILY | 00022771 | SPIMAINT | Replace INSULATOR REPLACEMENT SVTS-HTS 1 Line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027525239347.5715277778 | 10275252 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 39347.5715 | 39347.5743 | DAILY | 00060194 | FAULT | DDTS-MBTS No2 Line Auto Reclose MBTS only | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027515639347.6444444444 | 10275156 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 39347.6444 | 39349.6111 | CONT | [12 empty] | 0
_V60458A239348.2847222222 | V60458A2 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39348.2847 | 39348.6771 | REPDAILY | 00012436 | SPICAPX | erect hv test bus in bay a | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027516339348.5486111111 | 10275163 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 39348.5486 | 39349.4667 | CONT | [12 empty] | 0
_Z51058E739348.5729166667 | Z51058E7 |  | Parent | FALSE | B4 TRANS NO.3 BUS 220KV CB AT ATS | 39348.5729 | 39437.4333 | CONT | [12 empty] | 0
_X32058L439349.2284722222 | X32058L4 |  | Parent | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39349.2285 | 39349.7583 | REPDAILY | 00351697 | SPICAPX | Proxity Reasons for A northern Rack Structure | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026204939349.2777777778 | 10262049 |  | Parent | FALSE | H2 330/220KV TRANS BANK AT SMTS | 39349.2778 | 39351.6215 | CONT | 00026102 | SPIMAINT | Condition Sup Monitoring Metro Trans 3day West | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X56558D339349.3090277778 | X56558D3 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 39349.309 | 39349.6354 | DAILY | 00002829 | SPICAPX | Out W/O No3 Tr 220CB prox to remove old O.O.C CT's | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027516539349.34375 | 10275165 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 39349.3438 | 39349.6111 | DAILY | [12 empty] | 0
_1025939439349.3881944444 | 10259394 |  | Parent | FALSE | H3 TRANS NO.1 BUS 330KV CB CT R/PH AT DDTS | 39349.3882 | 39349.4868 | DAILY | [12 empty] | 0
_1027520439349.4680555556 | 10275204 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 39349.4681 | 39381.9701 | CONT | [12 empty] | 0
_1025939839349.4868055556 | 10259398 |  | Parent | FALSE | EX - MBTS NO.1 220KV LINE CB CT R/PH AT DDTS | 39349.4868 | 39349.5993 | DAILY | [12 empty] | 0
_1027493639349.4868055556 | 10274936 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT DDTS | 39349.4868 | 39349.5993 | DAILY | 00012361 | SPIMAINT | Rebate W/O MBTS No1 Line during CB outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027518839349.5361111111 | 10275188 |  | Parent | TRUE | WMTS NO.2 220KV LINE CB AT FBTS | 39349.5361 | 39349.5437 | DAILY | [12 empty] | 0
_1027519039349.5361111111 | 10275190 | 10275188 | Child | FALSE | WMTS NO.2 220KV LINE AT FBTS | 39349.5361 | 39349.5437 | DAILY | 00017157 | SPIMAINT | top up sf6 gas | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X56558D439350.26875 | X56558D4 |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 39350.2688 | 39350.7882 | DAILY | 00002828 | SPICAPX | Out W/O No1 Trans to install 220kV CVT | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058L439350.2715277778 | X32058L4 |  | Parent | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39350.2715 | 39350.6674 | REPDAILY | 00351697 | SPICAPX | Proxity Reasons for A northern Rack Structure | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024851839350.29375 | 10248518 |  | Parent | FALSE | L3 TRANS 22KV CB AT RWTS | 39350.2937 | 39350.5625 | DAILY | [12 empty] | 0
_1024895839350.2965277778 | 10248958 |  | Parent | TRUE | H2 TRANS 220KV CB AT DDTS | 39350.2965 | 39351.8125 | CONT | [12 empty] | 0
_1027484239350.2965277778 | 10274842 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 39350.2965 | 39351.8125 | CONT | 00352121 | SPIMAINT | Rebate W/O No2 Trans during 220kV CB O-Haul | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027445339350.3131944445 | 10274453 |  | Parent | TRUE | HWTS NO.3 500KV LINE CB AT LYPS | 39350.3132 | 39351.4778 | CONT | [12 empty] | 0
_1027573439350.3131944445 | 10275734 | 10274453 | Child | FALSE | HWTS NO.3 500KV LINE AT LYPS | 39350.3132 | 39351.4778 | CONT | 00016088 | SPIMAINT | Repaire SF6 gas leaks | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X38458W339350.3166666667 | X38458W3 |  | Parent | TRUE | B1 220/66KV TRANS AT TGTS | 39350.3167 | 39350.35 | REPDAILY | 00363297 | SPICAPX | Erect Hebel Block Wall adjacent to B1 Trans | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458W439350.3166666667 | X38458W4 | X38458W3 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39350.3167 | 39350.35 | REPDAILY | 00363297 | SPICAPX | Perf Calc for B1 Trans during Outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024722739350.3451388889 | 10247227 |  | Parent | FALSE | RCTS 220KV LINE AT HOTS | 39350.3451 | 39350.7715 | DAILY | 00018715 | SPIMAINT | O/Haul - CVT & Line Choke at HOTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026396639350.5555555556 | 10263966 |  | Parent | TRUE | NO.2A 66KV CAPACITOR BANK AT BETS | 39350.5556 | 39350.625 | REPDAILY | 00350819 | SPIMAINT | OPTEC Operator Training | SPIPOWER |  |  | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1027555939350.5555555556 | 10275559 | 10263966 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 39350.5556 | 39350.625 | REPDAILY | 00016274 | SPIMAINT | rebate for OPTEC Operator Training | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X38458W339351.2736111111 | X38458W3 |  | Parent | TRUE | B1 220/66KV TRANS AT TGTS | 39351.2736 | 39351.7035 | REPDAILY | 00363297 | SPICAPX | Erect Hebel Block Wall adjacent to B1 Trans | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458W439351.2736111111 | X38458W4 | X38458W3 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39351.2736 | 39351.7035 | REPDAILY | 00363297 | SPICAPX | Perf Calc for B1 Trans during Outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z73058A139351.275 | Z73058A1 |  | Parent | FALSE | EPS-TTS 220KV LINE AT SMTS | 39351.275 | 39351.5167 | DAILY | 00015363 | DB_AUG | bore holes in bay j & l | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026396639351.2847222222 | 10263966 |  | Parent | TRUE | NO.2A 66KV CAPACITOR BANK AT BETS | 39351.2847 | 39351.491 | REPDAILY | 00350819 | SPIMAINT | OPTEC Operator Training | SPIPOWER |  |  | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1027555939351.2847222222 | 10275559 | 10263966 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 39351.2847 | 39351.491 | REPDAILY | 00016274 | SPIMAINT | rebate for OPTEC Operator Training | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024861739351.3256944444 | 10248617 |  | Parent | FALSE | RCTS 220KV LINE NO.1 BUS CB AT HOTS | 39351.3257 | 39352.6583 | CONT | [12 empty] | 0
_X38458W339352.2958333333 | X38458W3 |  | Parent | TRUE | B1 220/66KV TRANS AT TGTS | 39352.2958 | 39352.6993 | REPDAILY | 00363297 | SPICAPX | Erect Hebel Block Wall adjacent to B1 Trans | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458W439352.2958333333 | X38458W4 | X38458W3 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39352.2958 | 39352.6993 | REPDAILY | 00363297 | SPICAPX | Perf Calc for B1 Trans during Outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1023681939352.3041666667 | 10236819 |  | Parent | FALSE | B4 220/66KV TRANS Y PROT AT SVTS | 39352.3042 | 39352.4917 | DAILY | [12 empty] | 0
_X56558B139352.3104166667 | X56558B1 |  | Parent | TRUE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39352.3104 | 39352.8028 | REPDAILY | 00017905 | SPICAPX | Out W/O PTH No1 Line & CB for CT replacement | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558D239352.3104166667 | X56558D2 | X56558B1 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39352.3104 | 39352.8028 | REPDAILY | 00002830 | SPICAPX | Perf calc W/O No4Trans for its 220CB proximity | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X3D258G039352.3208333333 | X3D258G0 |  | Parent | FALSE | B2 220/66KV TRANS AT MWTS | 39352.3208 | 39354.3979 | CONT | 00010266 | SPIMAINT | Remove old wiring and Equipment | SPIPOWER | X3D2 | X3D2 - (MWTS) INSTALL SCIMS & 66KV BAY PROT/CONT SCHEMES | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027532539352.3298611111 | 10275325 |  | Parent | FALSE | EX - SSS X CB PROT O/C & CB FAIL PROT & CONT RELAY P143 AT TTS | 39352.3299 | 39352.6542 | REPDAILY | [12 empty] | 0
_1024910039352.3333333333 | 10249100 |  | Parent | FALSE | L3 TRANS NO.3 BUS 22KV CB AT WMTS | 39352.3333 | 39352.6319 | DAILY | [12 empty] | 0
_X38458W339353.2770833333 | X38458W3 |  | Parent | TRUE | B1 220/66KV TRANS AT TGTS | 39353.2771 | 39353.3486 | REPDAILY | 00363297 | SPICAPX | Erect Hebel Block Wall adjacent to B1 Trans | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458W439353.2770833333 | X38458W4 | X38458W3 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39353.2771 | 39353.3486 | REPDAILY | 00363297 | SPICAPX | Perf Calc for B1 Trans during Outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56558B139353.28125 | X56558B1 |  | Parent | TRUE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39353.2812 | 39353.7604 | REPDAILY | 00017905 | SPICAPX | Out W/O PTH No1 Line & CB for CT replacement | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558D239353.28125 | X56558D2 | X56558B1 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39353.2812 | 39353.7604 | REPDAILY | 00002830 | SPICAPX | Perf calc W/O No4Trans for its 220CB proximity | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024911439353.2916666667 | 10249114 |  | Parent | FALSE | NO.3 66KV CAPACITOR BANK CB AT WMTS | 39353.2917 | 39353.6215 | DAILY | [12 empty] | 0
_X49058H939353.3555555556 | X49058H9 |  | Parent | FALSE | MBTS NO.1 220KV LINE X PROT AT DDTS | 39353.3556 | 39353.4354 | DAILY | [12 empty] | 0
_1027535739353.9791666667 | 10275357 |  | Parent | FALSE | W1 GEN TRANS NO.1 BUS 220KV CB AT YPS | 39353.9792 | 39357.8639 | CONT | [12 empty] | 0
_Z73058A239354.2604166667 | Z73058A2 |  | Parent | FALSE | EPS-TTS 220KV LINE AT SMTS | 39354.2604 | 39354.7431 | DAILY | 00015363 | DB_AUG | relocate eps-tts line poles from bay h to j | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X66558A139355.2923611111 | X66558A1 |  | Parent | FALSE | SVTS-HTS 2 220KV E | 39355.2924 | 39355.6486 | DAILY | 00022773 | SPIMAINT | Replace INSULATOR REPLACEMENT SVTS-HTS 2 Line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024673439355.35 | 10246734 |  | Parent | FALSE | A SOUTH 22KV BUS PROT AT RTS | 39355.35 | 39355.5896 | DAILY | [12 empty] | 0
_1027519939357.2916666667 | 10275199 |  | Parent | FALSE | NO.1 500KV BUS AT HWTS | 39357.2917 | 39357.6687 | DAILY | 00009798 | SPIMAINT | Repaire ROI | SPIPOWER |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1024936639357.2965277778 | 10249366 |  | Parent | FALSE | B4 220/66KV TRANS AT FBTS | 39357.2965 | 39358.6319 | CONT | 00002728 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024800739357.3118055556 | 10248007 |  | Parent | FALSE | MSS NO.2 330KV LINE AT DDTS | 39357.3118 | 39357.7007 | REPDAILY | 00012358 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027520639357.3291666667 | 10275206 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT RWTS | 39357.3292 | 39357.6826 | DAILY | [12 empty] | 0
_1027532539357.3958333333 | 10275325 |  | Parent | FALSE | EX - SSS X CB PROT O/C & CB FAIL PROT & CONT RELAY P143 AT TTS | 39357.3958 | 39357.684 | REPDAILY | [12 empty] | 0
_1027541539357.6680555556 | 10275415 |  | Parent | FALSE | A1 515/230KV TRANS AT HWTS | 39357.6681 | 39358.5479 | CONT | 00009772 | SPIMAINT | No 1 Main Trans 500kV CB | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1026346539358.2944444444 | 10263465 |  | Parent | FALSE | A NTH 22KV BUS VT AT RTS | 39358.2944 | 39358.3306 | DAILY | [12 empty] | 0
_X38458W539358.2972222222 | X38458W5 |  | Parent | TRUE | B1 220/66KV TRANS AT TGTS | 39358.2972 | 39358.6632 | REPDAILY | 00363297 | SPICAPX | Erect Hebel Block Wall adjacent to B1 Trans | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458W639358.2972222222 | X38458W6 | X38458W5 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39358.2972 | 39358.6632 | REPDAILY | 00363297 | SPICAPX | Perf calc for B1 Transformer during outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024800739358.2972222222 | 10248007 |  | Parent | FALSE | MSS NO.2 330KV LINE AT DDTS | 39358.2972 | 39358.6715 | REPDAILY | 00012358 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49658K139358.3263888889 | X49658K1 |  | Parent | FALSE | RCTS 220KV LINE NO.1 BUS CB AT HOTS | 39358.3264 | 39359.741 | CONT | [12 empty] | 0
_1025942039358.4833333333 | 10259420 |  | Parent | TRUE | EX - APD-MLTS NO.1 500KV LINE CT R/PH AT HYTS | 39358.4833 | 39358.5389 | DAILY | [12 empty] | 0
_1027502939358.4833333333 | 10275029 | 10259420 | Child | FALSE | MLTS NO.1 500KV LINE AT HYTS | 39358.4833 | 39358.5389 | DAILY | 00021195 | SPIMAINT | Rebate W/O MLTS-HYTS 1 Line during CT SAMPLING | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027558639358.4833333333 | 10275586 | 10259420 | Child | FALSE | APD NO.1 500KV LINE AT HYTS | 39358.4833 | 39358.5389 | DAILY | 00027386 | SPIMAINT | Rebate W/O HYTS-APD 1 Line during CT SAMPLING | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027558839358.4833333333 | 10275588 | 10259420 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39358.4833 | 39358.5389 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during CT SAMPLING | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027559039358.4833333333 | 10275590 | 10259420 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 39358.4833 | 39358.5389 | DAILY | 00003007 | SPIMAINT | Rebate W/O HYTS 1 LIne Reactor during CT SAMPLING | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026346639358.5416666667 | 10263466 |  | Parent | FALSE | A STH 22KV BUS VT AT RTS | 39358.5417 | 39358.6007 | DAILY | [12 empty] | 0
_1025941639358.5493055556 | 10259416 |  | Parent | TRUE | EX - APD-MLTS NO.2 500KV LINE CT R/PH AT HYTS | 39358.5493 | 39358.5951 | DAILY | [12 empty] | 0
_1027503139358.5493055556 | 10275031 | 10259416 | Child | FALSE | MLTS NO.2 500KV LINE AT HYTS | 39358.5493 | 39358.5951 | DAILY | 00021330 | SPIMAINT | Rebate W/O MLTS-HYTS 2 Line during CT SAMPLING | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027559639358.5493055556 | 10275596 | 10259416 | Child | FALSE | APD NO.2 500KV LINE AT HYTS | 39358.5493 | 39358.5951 | DAILY | 00060938 | SPIMAINT | Rebate W/O HYTS-APD 2 Line during CT SAMPLING | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027559839358.5493055556 | 10275598 | 10259416 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 39358.5493 | 39358.5951 | DAILY | 00002862 | SPIMAINT | Rebate W/O M2 Trans during CT SAMPLING | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027560039358.5493055556 | 10275600 | 10259416 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 39358.5493 | 39358.5951 | DAILY | 00003008 | SPIMAINT | Rebate W/O HYTS 2 Line Reactor during CT SAMPLING | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026346739359.3118055556 | 10263467 |  | Parent | FALSE | B NTH 22KV BUS VT AT RTS | 39359.3118 | 39359.5076 | DAILY | [12 empty] | 0
_1026346839359.5076388889 | 10263468 |  | Parent | FALSE | B STH 22KV BUS VT AT RTS | 39359.5076 | 39359.6743 | DAILY | [12 empty] | 0
_1027547339359.5354166667 | 10275473 |  | Parent | TRUE | 66KV CAPACITOR BANK CB AT TGTS | 39359.5354 | 39359.5507 | DAILY | [12 empty] | 0
_1027573339359.5354166667 | 10275733 | 10275473 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT WMTS | 39359.5354 | 39359.5507 | DAILY | 00074391 | SPIMAINT | No2 Cap Bk Low SF6 Alarm | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X41758A239360.2680555556 | X41758A2 |  | Parent | FALSE | B2 220/66KV TRANS AT BATS | 39360.2681 | 39361.6375 | CONT | 00006555 | SPICAPX | Replace 220kv Bushings in No2 Transformer | SPIPOWER | X417 | X417 - 220KV BUSHING REPLACEMENT 2004/05 | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V78658A039360.2895833333 | V78658A0 |  | Parent | FALSE | ROTS NO.4 500KV LINE AT CBTS | 39360.2896 | 39360.5938 | DAILY | 00359492 | SPIMAINT | Replace CVT | SPIPOWER | V786 | V786 - (CBTS) URGENT REPLACEMENT OF ROTS 4L 500KV CVT | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026346939360.3076388889 | 10263469 |  | Parent | FALSE | C NTH 22KV BUS VT AT RTS | 39360.3076 | 39360.55 | DAILY | [12 empty] | 0
_1027537839360.3298611111 | 10275378 |  | Parent | FALSE | 380V/415V S/S TRANS AT JLTS | 39360.3299 | 39360.6132 | DAILY | 00009888 | DBPROX | VSCAP to Distribution Operations Centre | DISTCO |  |  | Other Transformers | Eastern | 6.6 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1027531939360.33125 | 10275319 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB AT HWTS | 39360.3313 | 39360.4139 | DAILY | [12 empty] | 0
_1026347039360.55 | 10263470 |  | Parent | FALSE | C STH 22KV BUS VT AT RTS | 39360.55 | 39360.6042 | DAILY | [12 empty] | 0
_1027535139360.6041666667 | 10275351 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39360.6042 | 39360.6104 | DAILY | [12 empty] | 0
_1027541339360.6041666667 | 10275413 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39360.6042 | 39360.6104 | DAILY | [12 empty] | 0
_1027550839360.9201388889 | 10275508 |  | Parent | FALSE | NO.7 GEN TRANS LINE AT HWPS | 39360.9201 | 39366.9451 | CONT | 00356085 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358F539361.2194444445 | Z51358F5 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39361.2194 | 39361.7812 | DAILY | 00007480 | SPICAPX | No3 66KV BUS | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358F639361.2194444445 | Z51358F6 | Z51358F5 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 39361.2194 | 39361.7812 | CONT | 00007450 | SPICAPX | 2 ND Trans outage rebate for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358F339361.2395833333 | Z51358F3 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 39361.2396 | 39362.7847 | CONT | 00007456 | SPICAPX | Moving 66Kv Trans Connections | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358F239362.2375 | Z51358F2 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39362.2375 | 39362.7847 | DAILY | 00007480 | SPICAPX | No3 66KV BUS | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358F439362.2375 | Z51358F4 | Z51358F2 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 39362.2375 | 39362.7847 | CONT | 00007450 | SPICAPX | 2 ND Trans outage rebate for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027546539362.4604166667 | 10275465 |  | Parent | FALSE | GEN TRANS 220KV BUS AT NPSD | 39362.4604 | 39378.8883 | CONT | 00003077 | GENCO | SCAP to Ecogen | GENCO |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027551139362.6480787037 | 10275511 |  | Parent | FALSE | ISOLATION TRANS #3 | 39362.6481 | 39385.6066 | CONT | [12 empty] | 0
_1024970939363.2805555556 | 10249709 |  | Parent | FALSE | NO.2 TRANS 66KV CB AT GNTS | 39363.2806 | 39365.7069 | CONT | [12 empty] | 0
_1024971139363.2805555556 | 10249711 |  | Parent | FALSE | B2 220/66KV TRANS AT GNTS | 39363.2806 | 39365.7069 | CONT | 00000743 | SPIMAINT | O/HAUL Transformer Div Mechanism (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024978939363.2805555556 | 10249789 |  | Parent | FALSE | B2 TRANS 220KV CB AT GNTS | 39363.2806 | 39365.7069 | CONT | [12 empty] | 0
_1027517739363.2805555556 | 10275177 |  | Parent | FALSE | B2 220/66KV TRANS AT GNTS | 39363.2806 | 39365.7069 | CONT | 00000743 | SPIMAINT | Perf Calc for No2 Transformer | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027517939363.2805555556 | 10275179 |  | Parent | FALSE | NO.2 TRANS 66KV CB AT GNTS | 39363.2806 | 39365.7069 | CONT | [12 empty] | 0
_1027518139363.2805555556 | 10275181 |  | Parent | FALSE | B2 TRANS 220KV CB AT GNTS | 39363.2806 | 39365.7069 | CONT | [12 empty] | 0
_1027445339363.2958333333 | 10274453 |  | Parent | TRUE | HWTS NO.3 500KV LINE CB AT LYPS | 39363.2958 | 39366.5743 | CONT | [12 empty] | 0
_1027573439363.2958333333 | 10275734 | 10274453 | Child | FALSE | HWTS NO.3 500KV LINE AT LYPS | 39363.2958 | 39366.5743 | CONT | 00016088 | SPIMAINT | Repaire SF6 gas leaks | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010212139363.2979166667 | 10102121 |  | Parent | FALSE | SYTS 500KV LINE AT KTS | 39363.2979 | 39363.6687 | REPDAILY | 00015990 | SPIMAINT | O/Haul - 500kV Line (W) | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027527639364.2944444444 | 10275276 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT ERTS | 39364.2944 | 39364.425 | DAILY | 00004344 | SPIMAINT | CT oil Samples | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1010212139364.2958333333 | 10102121 |  | Parent | FALSE | SYTS 500KV LINE AT KTS | 39364.2958 | 39365.6854 | REPDAILY | 00015990 | SPIMAINT | O/Haul - 500kV Line (W) | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025146039364.3034722222 | 10251460 |  | Parent | TRUE | FBTS NO.1 220KV LINE CABLE AT WMTS | 39364.3035 | 39364.4278 | DAILY | 00026298 | SPIMAINT | OVERHAUL POWER CABLE (220KV & 66KV) (W) | SPIPOWER |  |  | Circuits | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027573639364.3034722222 | 10275736 | 10251460 | Child | FALSE | FBTS NO.1 220KV LINE AT WMTS | 39364.3035 | 39364.4278 | DAILY | 00025735 | SPIMAINT | OVERHAUL POWER CABLE (220KV & 66KV) (W) | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1025137639364.3166666667 | 10251376 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT BATS | 39364.3167 | 39364.6479 | DAILY | [12 empty] | 0
_1027526439364.3166666667 | 10275264 | 10251376 | Child | FALSE | NO.1 66KV CAPACITOR BANK CB AT BATS | 39364.3167 | 39364.6479 | DAILY | [12 empty] | 0
_Z51358D939364.3409722222 | Z51358D9 |  | Parent | FALSE | B2 220/66KV TRANS AT RWTS | 39364.341 | 39364.5694 | DAILY | 00007450 | SPICAPX | Trans outage Rebate | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49758H639365.2777777778 | X49758H6 |  | Parent | FALSE | BATS 220KV LINE AT BETS | 39365.2778 | 39365.7021 | DAILY | 00016470 | SPICAPX | Out W/O BATS Line to recommiss it CVT's | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024865839365.3166666667 | 10248658 |  | Parent | FALSE | WBTS 220KV LINE NO.1 TIE BUS BUS SIDE ROI AT BATS | 39365.3167 | 39365.6757 | DAILY | [12 empty] | 0
_1027527839365.3277777778 | 10275278 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39365.3278 | 39365.3931 | DAILY | 00112418 | SPIMAINT | CT oil Samples | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1025711839365.3277777778 | 10257118 |  | Parent | TRUE | TY48PROTS-TTS 220KV | 39365.3278 | 39365.6542 | DAILY | [12 empty] | 0
_1027573839365.3277777778 | 10275738 |  | Parent | FALSE | TY48PROTS-TTS 220KV | 39365.3278 | 39365.6542 | DAILY | [12 empty] | 0
_1027573939365.3277777778 | 10275739 | 10257118 | Child | FALSE | ROTS 220KV LINE AT TTS | 39365.3278 | 39365.6542 | DAILY | 00015733 | SPIMAINT | rebate for Split crossarms repair | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49758H739365.3541666667 | X49758H7 |  | Parent | FALSE | KGTS 220KV LINE NO.2 BUS CB AT BETS | 39365.3542 | 39365.7181 | REPDAILY | [12 empty] | 0
_1027560839365.6854166667 | 10275608 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 39365.6854 | 39366.2931 | CONT | [12 empty] | 0
_X49758H739366.2784722222 | X49758H7 |  | Parent | FALSE | KGTS 220KV LINE NO.2 BUS CB AT BETS | 39366.2785 | 39366.7451 | REPDAILY | [12 empty] | 0
_1010212139366.29375 | 10102121 |  | Parent | FALSE | SYTS 500KV LINE AT KTS | 39366.2937 | 39366.6264 | REPDAILY | 00015990 | SPIMAINT | O/Haul - 500kV Line (W) | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009831939366.2972222222 | 10098319 |  | Parent | TRUE | TGTS 220KV LINE NO.2 TIE BUS LINE SIDE ISOL AT BATS | 39366.2972 | 39366.6667 | DAILY | [12 empty] | 0
_1027555439366.2972222222 | 10275554 | 10098319 | Child | FALSE | TGTS 220KV LINE AT BATS | 39366.2972 | 39366.6667 | DAILY | 00012435 | SPIMAINT | Rebate W/O TGTS Line Outage at BATS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027527939366.3708333333 | 10275279 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT TBTS | 39366.3708 | 39366.4 | DAILY | [12 empty] | 0
_1027560439366.3847222222 | 10275604 |  | Parent | TRUE | EX - MBTS NO.1 220KV LINE CB CT R/PH AT DDTS | 39366.3847 | 39366.441 | DAILY | [12 empty] | 0
_1027560539366.3847222222 | 10275605 | 10275604 | Child | FALSE | MBTS NO.1 220KV LINE AT DDTS | 39366.3847 | 39366.441 | DAILY | 00012361 | SPIMAINT | Rebate W/O MBTS No1 Line during CB outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027528039366.4291666667 | 10275280 |  | Parent | FALSE | B1 220/66KV TRANS AT TBTS | 39366.4292 | 39366.4528 | DAILY | 00004901 | SPIMAINT | CT oil Samples | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024959939367.275 | 10249599 |  | Parent | TRUE | EX - TTS NO.2 LINE/WMTS NO.2 LINE CB TTS LINE SIDE E/SW AT KTS | 39367.275 | 39367.65 | DAILY | [12 empty] | 0
_1027593639367.275 | 10275936 | 10249599 | Child | FALSE | EX - TTS NO.2 220KV LINE AT KTS | 39367.275 | 39367.65 | DAILY | 00015987 | SPIMAINT | rebate workorder for 220kV switchgear Esw o/h | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024952539367.2902777778 | 10249525 |  | Parent | FALSE | EX - NO.1 BUS - NO.4 BUS EXT CB AT KTS | 39367.2903 | 39367.6604 | DAILY | [12 empty] | 0
_1024755739367.3131944445 | 10247557 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT LYPS | 39367.3132 | 39367.5681 | DAILY | 00016086 | SPIMAINT | O/Haul - HWTS No.1 Line at LYPS | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027528139367.38125 | 10275281 |  | Parent | FALSE | B2 220/66KV TRANS AT TBTS | 39367.3812 | 39367.409 | DAILY | 00004902 | SPIMAINT | CT oil Samples | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058A039367.4541666667 | X32058A0 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT MTS | 39367.4542 | 39393.5722 | CONT | [12 empty] | 0
_1027567639367.5305555556 | 10275676 |  | Parent | FALSE | A3 GEN TRANS NO.1 BUS 500KV CB AT LYPS | 39367.5306 | 39368.7 | CONT | [12 empty] | 0
_1027568839367.5444444444 | 10275688 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT DDTS | 39367.5444 | 39370.291 | CONT | 00012361 | SPIMAINT | Replace noisy Tyree CT at DDTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358E639368.2270833333 | Z51358E6 |  | Parent | TRUE | NO.1 220KV BUS AT RWTS | 39368.2271 | 39368.6722 | DAILY | 00007477 | SPICAPX | Assemble new 220kv ROI Structure in bay M | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358E739368.2270833333 | Z51358E7 | Z51358E6 | Child | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39368.2271 | 39368.6722 | DAILY | 00007452 | SPICAPX | Rebate Tran for bus outage No 3 220/22Kv Trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358E839368.2270833333 | Z51358E8 | Z51358E6 | Child | FALSE | B4 220/66KV TRANS AT RWTS | 39368.2271 | 39368.6722 | DAILY | 00007451 | SPICAPX | Rebate Tran for bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X47758D939368.25 | X47758D9 |  | Parent | TRUE | HWTS NO.1 500KV LINE AT SMTS | 39368.25 | 39368.7292 | DAILY | 00012436 | SPICAPX | invoke smts 500kv bypass bay a -hwts 1l & syts 1l | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X47758Z039368.25 | X47758Z0 | X47758D9 | Child | FALSE | SYTS NO.1 500KV LINE AT SMTS | 39368.25 | 39368.7292 | DAILY | 00012439 | SPICAPX | invoke smts 500kv bypass bay a -hwts 1l & syts 1l | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658A539368.2631944444 | X55658A5 |  | Parent | FALSE | EX - RWN NO.1 66KV FDR AT RWTS | 39368.2632 | 39368.7347 | DAILY | 00020115 | SPICAPX | All of the No 2 & No4 66kv Buses Fdr Outages | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026276739368.3 | 10262767 |  | Parent | FALSE | L3 TRANS NO.2 BUS 22KV CB AT WMTS | 39368.3 | 39368.6687 | DAILY | [12 empty] | 0
_V4S258F039368.6555555556 | V4S258F0 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.2 BUS CB AT SMTS | 39368.6556 | 39420.5056 | CONT | 00001293 | SPIMAINT | silicon injection - red phase | SPIPOWER | V4S2 |  | CB | Western | 500 | CB |  |  | 0 | V4S258F0 |  | silicon injection - red phase | 00001293 | CB | V4S2 | SMTS | CB | SPIMAINT | CONT
_1027570439368.9548611111 | 10275704 |  | Parent | FALSE | EPS 220KV LINE AT TTS | 39368.9549 | 39369.5236 | CONT | 00015730 | FAULT | TTS - EPS 220kV Line Tripped with no reclose | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024866539369.2833333333 | 10248665 |  | Parent | TRUE | NO.4 220KV BUS AT SVTS | 39369.2833 | 39369.484 | DAILY | 00004859 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026178139369.2833333333 | 10261781 | 10248665 | Child | FALSE | B4 220/66KV TRANS AT SVTS | 39369.2833 | 39369.484 | DAILY | 00352791 | SPIMAINT | Rebate Tran Outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025148439369.5361111111 | 10251484 |  | Parent | FALSE | A 66/11KV S/S TRANS CABLE AT LY | 39369.5361 | 39370.5903 | CONT | 00027176 | SPIMAINT | OVERHAUL POWER CABLE (220KV & 66KV) (EH) | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027560439370.2736111111 | 10275604 |  | Parent | TRUE | EX - MBTS NO.1 220KV LINE CB CT R/PH AT DDTS | 39370.2736 | 39370.7514 | DAILY | [12 empty] | 0
_1027560539370.2909722222 | 10275605 | 10275604 | Child | FALSE | MBTS NO.1 220KV LINE AT DDTS | 39370.291 | 39370.7514 | DAILY | 00012361 | SPIMAINT | Rebate W/O MBTS No1 Line during CB outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158R239370.2916666667 | Z53158R2 |  | Parent | FALSE | TTS 220KV LINE AT ROTS | 39370.2917 | 39370.4417 | DAILY | 00023972 | VEN_AUG | repaire line droppers from rubbing | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1027542039370.4048611111 | 10275420 |  | Parent | FALSE | MLRC 220KV LINE AT RCTS | 39370.4049 | 39372.7319 | CONT | 00352130 | DBPROX | SCAP to Murraylink | HVCUST |  |  | Circuits | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 3
_Z53158R339370.4479166667 | Z53158R3 |  | Parent | FALSE | A2 515/220KV TRANS BANK AT ROTS | 39370.4479 | 39370.5903 | DAILY | 00362994 | VEN_AUG | Repair Line Droppers | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1027545239371.3125 | 10275452 |  | Parent | FALSE | LYPS NO.1 500KV LINE AT HWTS | 39371.3125 | 39371.5993 | DAILY | 00016234 | SPIMAINT | O/Haul line Gear | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858J739371.4555555556 | X49858J7 |  | Parent | FALSE | MBTS-EPS 2 220KV N | 39371.4556 | 39371.4778 | DAILY | 00055381 | SPICAPX | Replace damaged Brace on EPS 2 Ln CB Ln Side ROI | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1027545339372.2965277778 | 10275453 |  | Parent | FALSE | EX - DDTS 220KV LINE AT SHTS | 39372.2965 | 39372.7688 | DAILY | 00000811 | SPICAPX | Manufacturers adjustments to Earth Switches | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458A339372.2993055556 | V60458A3 |  | Parent | FALSE | BAY F 500KV LINE AT SMTS (O.O.S) | 39372.2993 | 39373.5056 | CONT | 00012398 | SPIMAINT | Dismantle hypotronics | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1024916939372.3173611111 | 10249169 |  | Parent | TRUE | B2 220/66KV TRANS AT TGTS | 39372.3174 | 39372.6937 | REPDAILY | 00003127 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027539539372.3173611111 | 10275395 | 10249169 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39372.3174 | 39372.6937 | REPDAILY | 00003127 | SPIMAINT | Replace DIA Insulators on B2 Trans conn's at Rack | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027539839372.3173611111 | 10275398 | 10249169 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39372.3174 | 39372.6937 | REPDAILY | 00003127 | SPIMAINT | Perf Calc B2 Transformer outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025148639372.5694444444 | 10251486 |  | Parent | FALSE | B 66/11KV S/S TRANS CABLE AT LY | 39372.5694 | 39373.5868 | CONT | 00027177 | SPIMAINT | OVERHAUL POWER CABLE (220KV & 66KV) (EH) | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027582939372.5868055556 | 10275829 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39372.5868 | 39372.5944 | DAILY | [12 empty] | 0
_1027546039373.2708333333 | 10275460 |  | Parent | FALSE | LYPS NO.3 500KV LINE AT HWTS | 39373.2708 | 39373.4347 | DAILY | 00016236 | SPIMAINT | REBATE LINE OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027545539373.2708333333 | 10275455 |  | Parent | TRUE | LYPS NO.3 LINE/CBTS NO.4 LINE CB CBTS NO.4 LINE SIDE 500KV ROI AT HWTS | 39373.2708 | 39374.6181 | CONT | [12 empty] | 0
_1027545739373.2708333333 | 10275457 | 10275455 | Child | FALSE | CBTS NO.4 500KV LINE AT HWTS | 39373.2708 | 39374.6181 | DAILY | 00016240 | SPIMAINT | Rebate for Line outage Repair Line Side ROI | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024916939373.2930555556 | 10249169 |  | Parent | TRUE | B2 220/66KV TRANS AT TGTS | 39373.2931 | 39373.7264 | REPDAILY | 00003127 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027539539373.2930555556 | 10275395 | 10249169 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39373.2931 | 39373.7264 | REPDAILY | 00003127 | SPIMAINT | Replace DIA Insulators on B2 Trans conn's at Rack | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027539839373.2930555556 | 10275398 | 10249169 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39373.2931 | 39373.7264 | REPDAILY | 00003127 | SPIMAINT | Perf Calc B2 Transformer outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027547239373.30625 | 10275472 |  | Parent | TRUE | EX - GNTS NO.1 220KV LINE AT SHTS | 39373.3063 | 39373.7444 | DAILY | 00000812 | SPIMAINT | Manufacturers adjustments to Earth Switches | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X41258F139373.30625 | X41258F1 | 10275472 | Child | FALSE | EX - GNTS NO.1 220KV LINE NO.1 BUS CB AT SHTS | 39373.3063 | 39373.7444 | DAILY | [12 empty] | 0
_1027552939373.3097222222 | 10275529 |  | Parent | TRUE | NO.1 330KV BUS AT WOTS | 39373.3097 | 39373.5819 | DAILY | 00004041 | SPIMAINT | Out W/O No1 330kV Bus- Bonding of expansion joints | SPIPOWER |  |  | Bus | Alstom | 330 | NON AER ELEMENT | EXCLUDED |  | 0
_1027553139373.3097222222 | 10275531 | 10275529 | Child | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 39373.3097 | 39373.5819 | DAILY | 00004036 | SPIMAINT | Perf calc W/O No1 Trans during 330 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027529239373.4791666667 | 10275292 |  | Parent | FALSE | 1-4 66KV BUS TIE CB AT TSTS | 39373.4792 | 39373.5415 | DAILY | [12 empty] | 0
_1025148839373.5902777778 | 10251488 |  | Parent | FALSE | C 66/11KV S/S TRANS CABLE AT LY | 39373.5903 | 39374.6042 | CONT | 00027178 | SPIMAINT | OVERHAUL POWER CABLE (220KV & 66KV) (EH) | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X41758A339374.2805555556 | X41758A3 |  | Parent | FALSE | B2 220/66KV TRANS AT BATS | 39374.2806 | 39378.5437 | CONT | 00006555 | SPICAPX | Replace 220kv Bushings in No2 Trans continued | SPIPOWER | X417 | X417 - 220KV BUSHING REPLACEMENT 2004/05 | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027527639374.2993055556 | 10275276 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT ERTS | 39374.2993 | 39374.4319 | DAILY | 00004344 | SPIMAINT | CT oil Samples | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027601739374.3048611111 | 10276017 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT RWTS | 39374.3049 | 39374.4181 | DAILY | [12 empty] | 0
_1027613739374.3048611111 | 10276137 | 10276017 | Child | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39374.3049 | 39374.4181 | DAILY | 00007399 | FORCED | Cap SF6 Low | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027613839374.3048611111 | 10276138 | 10276017 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39374.3049 | 39374.4181 | DAILY | 00331179 | FORCED | Rebate for Cap CB SF6 Low | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027555639374.3104166667 | 10275556 |  | Parent | TRUE | S067 MBTS-DDTS 2 220KV | 39374.3104 | 39374.6042 | DAILY | [12 empty] | 0
_1027555739374.3104166667 | 10275557 | 10275556 | Child | FALSE | S067 MBTS-DDTS 2 220KV | 39374.3104 | 39374.6042 | DAILY | [12 empty] | 0
_1027614039374.3104166667 | 10276140 | 10276139 | Child | FALSE | S067 MBTS-DDTS 2 220KV | 39374.3104 | 39374.6042 | DAILY | [12 empty] | 0
_1027614139374.3104166667 | 10276141 | 10275556 | Child | FALSE | MBTS NO.2 220KV LINE AT DDTS | 39374.3104 | 39374.6042 | DAILY | 00012363 | SPIMAINT | RebatReplace Insulators at S067 MBTS-DDTS N02 Line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027614239374.3104166667 | 10276142 |  | Parent | FALSE | S067 MBTS-DDTS 2 220KV | 39374.3104 | 39374.6042 | DAILY | [12 empty] | 0
_1026347839374.3125 | 10263478 |  | Parent | FALSE | FR NO.2 66KV FDR NO.4 BUS CB AT RTS | 39374.3125 | 39374.5847 | DAILY | [12 empty] | 0
_1026348139374.3125 | 10263481 |  | Parent | FALSE | EX - FR NO.2 66KV FDR NO.3 BUS CB AT RTS | 39374.3125 | 39374.5847 | DAILY | [12 empty] | 0
_1027553339374.3131944445 | 10275533 | 10275532 | Child | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 39374.3132 | 39374.6076 | DAILY | 00004037 | SPIMAINT | Perf calc W/O No2 Trans during 330 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027555139374.3131944445 | 10275551 | 10275532 | Child | FALSE | NO.2 330KV CAPACITOR BANK AT WOTS | 39374.3132 | 39374.6076 | DAILY | 00354001 | SPIMAINT | Rebate W/O No2 330 Cap bk during 330 bus outage | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_1027553239374.3138888889 | 10275532 |  | Parent | TRUE | NO.2 330KV BUS AT WOTS | 39374.3139 | 39374.6076 | DAILY | 00004042 | SPIMAINT | Out W/O No2 330kV Bus- Bonding of expansion joints | SPIPOWER |  |  | Bus | Alstom | 330 | NON AER ELEMENT | EXCLUDED |  | 0
_1027582639374.3229166667 | 10275826 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 39374.3229 | 39374.6403 | DAILY | [12 empty] | 0
_1027543639374.33125 | 10275436 |  | Parent | TRUE | EX - 66KV CAPACITOR BANK AT TGTS | 39374.3313 | 39374.5014 | DAILY | 00003104 | SPIMAINT | No1 Cap Bank Insulator replacement | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027546839374.33125 | 10275468 | 10275436 | Child | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39374.3313 | 39374.5014 | DAILY | 00003104 | SPIMAINT | Rebate W/O for Cap Bank Outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027527739374.4319444444 | 10275277 |  | Parent | FALSE | NO.1A 66KV CAPACITOR BANK AT ERTS | 39374.4319 | 39374.4944 | DAILY | 00004345 | SPIMAINT | CT oil Samples | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027589139375.0798611111 | 10275891 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39375.0799 | 39375.4326 | CONT | 00003104 | FORCED | Cap Bank AVC Blocked alarms when Cap Bank CB was o | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z51358G339375.2395833333 | Z51358G3 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39375.2396 | 39375.8229 | DAILY | 00007480 | SPICAPX | No3 66KV BUS Sub RWN 2 Fdr CB | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358G539375.2395833333 | Z51358G5 | Z51358G3 | Child | FALSE | U1 66/22KV TRANS AT RWTS | 39375.2396 | 39375.8229 | DAILY | 00007456 | SPICAPX | Trans outage rebate for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z73058A439375.2826388889 | Z73058A4 |  | Parent | FALSE | ROTS 220KV LINE AT TTS | 39375.2826 | 39375.7236 | REPDAILY | 00015733 | DB_AUG | line deviation for SMTS 220kv augmentation | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X66858A039375.2930555556 | X66858A0 |  | Parent | FALSE | SVTS-HTS 1 220KV E | 39375.2931 | 39375.6687 | DAILY | 00022771 | SPIMAINT | Replace insulators | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027581939375.3479166667 | 10275819 |  | Parent | FALSE | NO.2 GEN TRANS 500KV LINE E/SW AT LYPS | 39375.3479 | 39381.6528 | CONT | [12 empty] | 0
_1027583939375.8229166667 | 10275839 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 39375.8229 | 39376.2299 | CONT | 00007456 | SPICAPX | Trans outage rebate for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027587339375.9791666667 | 10275873 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 39375.9792 | 39381.3569 | CONT | 00356086 | GENCO | HWPS No8 Gen Trans Isolated & Earthed for SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358G639376.2298611111 | Z51358G6 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39376.2299 | 39376.8465 | DAILY | 00007480 | SPICAPX | No3 66KV BUS | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358G839376.2298611111 | Z51358G8 | Z51358G6 | Child | FALSE | U1 66/22KV TRANS AT RWTS | 39376.2299 | 39376.8465 | DAILY | 00007456 | SPICAPX | Trans outage rebate for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z73058A439376.2604166667 | Z73058A4 |  | Parent | FALSE | ROTS 220KV LINE AT TTS | 39376.2604 | 39376.6361 | REPDAILY | 00015733 | DB_AUG | line deviation for SMTS 220kv augmentation | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X66858A139376.2916666667 | X66858A1 |  | Parent | FALSE | SVTS-HTS 2 220KV E | 39376.2917 | 39376.675 | DAILY | 00022773 | SPIMAINT | Replace insulators SVTS-HTS No 2 Line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024867639376.3041666667 | 10248676 |  | Parent | TRUE | NO.3 220KV BUS AT SVTS | 39376.3042 | 39376.5528 | DAILY | 00004858 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026434139376.3041666667 | 10264341 | 10248676 | Child | FALSE | B3 220/66KV TRANS AT SVTS | 39376.3042 | 39376.5528 | DAILY | 00004851 | SPIMAINT | Trans Rebate For Bus Outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025938839377.2923611111 | 10259388 |  | Parent | FALSE | EX - A4 TRANS NO.1 BUS 500KV CB CT R/PH AT KTS | 39377.2924 | 39377.4472 | DAILY | [12 empty] | 0
_V76958A039377.29375 | V76958A0 |  | Parent | FALSE | NO.2 66KV BUS AT CBTS | 39377.2937 | 39377.666 | DAILY | 00359471 | SPICAPX | Modify 1-2 66kv B/T CB No2 Bus Side isol SW | SPIPOWER | V769 | V769 - (CBTS) PRIMARY EQUIPMENT DEFECTS REPAIR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027575739377.3006944444 | 10275757 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT WMTS | 39377.3007 | 39377.5319 | DAILY | 00003239 | DBPROX | VSCAP to Citipower | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1010201039377.325 | 10102010 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT BETS | 39377.325 | 39377.5299 | DAILY | 00016035 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1025148039377.3256944444 | 10251480 |  | Parent | FALSE | NPSD-BLTS 220KV CABLE A AT NPSD | 39377.3257 | 39377.4688 | DAILY | 00026300 | SPIMAINT | o/h power cables both cable a & b | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027589339377.3923611111 | 10275893 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS (CONNECTED TO BAN 8) AT BATS | 39377.3924 | 39377.5729 | DAILY | 00006556 | SPIMAINT | Loss of 415V due to loss of No 1 S/S Trans at BATS | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1025146639377.4736111111 | 10251466 |  | Parent | FALSE | NPSD-FBTS 220KV CABLE A AT NPSD | 39377.4736 | 39377.6132 | DAILY | 00026841 | SPIMAINT | o/h power cable - both cables a & b | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027592639377.6090277778 | 10275926 |  | Parent | FALSE | HYTS NO.1 500KV LINE AT APD | 39377.609 | 39377.6681 | DAILY | 00005921 | APDALCOA | Line De-en for APD | APDALCOA |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1009937739378.2604166667 | 10099377 |  | Parent | TRUE | B4 TRANS NO.1 BUS 220KV CB BUS SIDE ROI AT SHTS | 39378.2604 | 39378.4972 | DAILY | [12 empty] | 0
_1027571039378.2604166667 | 10275710 | 10099377 | Child | FALSE | B2 220/66KV TRANS AT SHTS | 39378.2604 | 39378.4972 | DAILY | 00000841 | SPIMAINT | Perf calc for No2 Trans during No1 Bus Outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027579339378.2868055556 | 10275793 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39378.2868 | 39378.5938 | DAILY | [12 empty] | 0
_V76958A139378.2902777778 | V76958A1 |  | Parent | FALSE | NO.2 66KV BUS AT CBTS | 39378.2903 | 39378.6458 | DAILY | 00359471 | SPICAPX | Modify 2-3 66kv B/T CB No2 Bus Side isol SW | SPIPOWER | V769 | V769 - (CBTS) PRIMARY EQUIPMENT DEFECTS REPAIR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1025938439378.2944444444 | 10259384 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB CT R/PH AT KTS | 39378.2944 | 39378.6097 | DAILY | [12 empty] | 0
_1027575639378.3055555556 | 10275756 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT WMTS | 39378.3056 | 39378.4771 | DAILY | 00003239 | DBPROX | VSCAP to Citipower | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1027581439378.3118055556 | 10275814 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.1 BUS CB AT LYPS | 39378.3118 | 39378.5965 | DAILY | [12 empty] | 0
_1027580639378.3125 | 10275806 |  | Parent | TRUE | S001 HWPS-HWTS 3 220KV | 39378.3125 | 39378.4354 | DAILY | [12 empty] | 0
_1027614439378.3125 | 10276144 | 10275806 | Child | FALSE | HWPS NO.3 220KV LINE AT HWTS | 39378.3125 | 39378.4354 | DAILY | 00016244 | SPIMAINT | Rebate Hot joint to repair | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027597439378.4270833333 | 10275974 |  | Parent | FALSE | BATS 220KV LINE AT TGTS | 39378.4271 | 39378.4333 | DAILY | 00023130 | SPIMAINT | Line de energised only | ALSTOM |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027570739378.4527777778 | 10275707 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 39378.4528 | 39378.6431 | DAILY | [12 empty] | 0
_1027562439378.5097222222 | 10275624 |  | Parent | FALSE | EX - FVTS/BETS 220KV LINE E/SW AT SHTS | 39378.5097 | 39378.7201 | DAILY | [12 empty] | 0
_1027570939378.5097222222 | 10275709 |  | Parent | FALSE | EX - FVTS/BETS 220KV LINE AT SHTS | 39378.5097 | 39378.7201 | DAILY | 00000810 | SPICAPX | Rebate W/O FVTS Line Outage for E/SW adjustment | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027580739378.5111111111 | 10275807 |  | Parent | TRUE | S001 HWPS-JLTS 1 220KV | 39378.5111 | 39378.6472 | DAILY | [12 empty] | 0
_1027614639378.5111111111 | 10276146 | 10275807 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 39378.5111 | 39378.6472 | DAILY | 00015936 | SPIMAINT | Repair Hot joint Tower 1 | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027574239378.5340277778 | 10275742 |  | Parent | FALSE | BETS/SHTS 220KV LINE AT FVTS | 39378.534 | 39378.6319 | DAILY | 00358158 | 3RDPARTY | SCAP on PSV Fdr | 3RDPARTY |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027599839378.5715277778 | 10275998 |  | Parent | FALSE | NO.2 66KV BUS AT SHTS | 39378.5715 | 39378.5912 | DAILY | 00000847 | FAULT | De-Energised to repair loose prot cable connection | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758I439379.2652777778 | X49758I4 |  | Parent | TRUE | NO.1 220KV BUS AT BETS | 39379.2653 | 39379.7104 | REPDAILY | 00016305 | SPICAPX | Out W/O No1 220kV Bus- replace section in bays E&F | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758I539379.2652777778 | X49758I5 | X49758I4 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39379.2653 | 39379.7104 | REPDAILY | 00016040 | SPICAPX | Perf calc W/O No2 Trans during No1 220 Bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027571739379.2666666667 | 10275717 |  | Parent | TRUE | EX - NO.1 220KV BUS AT SHTS | 39379.2667 | 39379.7028 | DAILY | 00000845 | SPICAPX | Manufacturers adjustments to Earth Switches | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027571839379.2666666667 | 10275718 | 10275717 | Child | FALSE | B2 220/66KV TRANS AT SHTS | 39379.2667 | 39379.7028 | DAILY | 00000841 | SPICAPX | Perf calc No2 Trans during No1 220kv Bus Outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027544639379.29375 | 10275446 | X38458X0 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39379.2937 | 39379.6917 | REPDAILY | 00363297 | SPICAPX | Perf calc for B1 Transformer during outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458W939379.29375 | X38458W9 |  | Parent | TRUE | B1 220/66KV TRANS AT TGTS | 39379.2937 | 39379.6917 | REPDAILY | 00363297 | SPICAPX | Erect Hebel Block Wall adjacent to B1 Trans | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458X039379.29375 | X38458X0 | X38458W9 | Child | TRUE | B1 220/66KV TRANS AT TGTS | 39379.2937 | 39379.6917 | REPDAILY | 00363297 | SPICAPX | perf calc for B1 transformer Outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009442139379.2944444444 | 10094421 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 39379.2944 | 39379.4715 | DAILY | 00352791 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025935439379.2958333333 | 10259354 |  | Parent | TRUE | FBTS NO.1 220KV LINE CB CT R/PH AT WMTS | 39379.2958 | 39379.4625 | DAILY | [12 empty] | 0
_1025938039379.2958333333 | 10259380 | 10259354 | Child | FALSE | EX - WMTS NO.1 220KV LINE CB CT R/PH AT FBTS | 39379.2958 | 39379.4625 | DAILY | [12 empty] | 0
_1027578139379.30625 | 10275781 |  | Parent | FALSE | S008 HWPS-YPS 2 220KV | 39379.3063 | 39379.6597 | DAILY | [12 empty] | 0
_1025935639379.46875 | 10259356 |  | Parent | TRUE | FBTS NO.2 220KV LINE CB CT R/PH AT WMTS | 39379.4688 | 39379.5819 | DAILY | [12 empty] | 0
_1025938239379.46875 | 10259382 | 10259356 | Child | FALSE | EX - WMTS NO.2 220KV LINE CB CT R/PH AT FBTS | 39379.4688 | 39379.5819 | DAILY | [12 empty] | 0
_1027614739379.46875 | 10276147 | 10259356 | Child | FALSE | FBTS NO.2 220KV LINE AT WMTS | 39379.4688 | 39379.5819 | DAILY | 00025736 | SPIMAINT | CT OIL SAMPLING | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X56558D539379.4798611111 | X56558D5 |  | Parent | FALSE | NO.1 CSC AT ROTS | 39379.4799 | 39379.5938 | DAILY | 00004718 | SPICAPX | proximity of faulty ct's de-energised only | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X49758I439380.2625 | X49758I4 |  | Parent | TRUE | NO.1 220KV BUS AT BETS | 39380.2625 | 39380.6826 | REPDAILY | 00016305 | SPICAPX | Out W/O No1 220kV Bus- replace section in bays E&F | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758I539380.2625 | X49758I5 | X49758I4 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39380.2625 | 39380.6826 | REPDAILY | 00016040 | SPICAPX | Perf calc W/O No2 Trans during No1 220 Bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V76958A239380.2847222222 | V76958A2 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT CBTS | 39380.2847 | 39380.6312 | DAILY | 00359493 | SPICAPX | Repaire Oil leak | SPIPOWER | V769 | V769 - (CBTS) PRIMARY EQUIPMENT DEFECTS REPAIR | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1027578939380.2916666667 | 10275789 |  | Parent | FALSE | HWTS-ROTS 3 500KV E | 39380.2917 | 39380.6403 | DAILY | 00360709 | SPIMAINT | Hot joint to repair | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027572439380.2958333333 | 10275724 |  | Parent | TRUE | EX - NO.2 220KV BUS AT SHTS | 39380.2958 | 39380.6917 | REPDAILY | 00000846 | SPICAPX | Manufacturers adjustments to Earth Switches | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027572639380.2958333333 | 10275726 | 10275724 | Child | FALSE | GNTS NO.3 220KV LINE AT SHTS | 39380.2958 | 39380.6917 | REPDAILY | 00352426 | SPICAPX | Rebate for line outage during No2 220kv Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027544639380.3069444444 | 10275446 | X38458X0 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39380.3069 | 39380.6639 | REPDAILY | 00363297 | SPICAPX | Perf calc for B1 Transformer during outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458W939380.3069444444 | X38458W9 |  | Parent | TRUE | B1 220/66KV TRANS AT TGTS | 39380.3069 | 39380.6639 | REPDAILY | 00363297 | SPICAPX | Erect Hebel Block Wall adjacent to B1 Trans | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X38458X039380.3069444444 | X38458X0 | X38458W9 | Child | TRUE | B1 220/66KV TRANS AT TGTS | 39380.3069 | 39380.6639 | REPDAILY | 00363297 | SPICAPX | perf calc for B1 transformer Outage | SPIPOWER | X384 | X384 - (TGTS) STATION REFURBISHMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025937039380.3784722222 | 10259370 | 10259376 | Child | FALSE | FBTS 220KV LINE CB CT R/PH AT BLTS | 39380.3785 | 39380.6188 | DAILY | [12 empty] | 0
_1025937639380.3784722222 | 10259376 |  | Parent | TRUE | EX - BLTS 220KV LINE CB CT R/PH AT FBTS | 39380.3785 | 39380.6188 | DAILY | [12 empty] | 0
_X66858A439380.3944444444 | X66858A4 |  | Parent | FALSE | MLTS-TGTS 220KV W | 39380.3944 | 39380.6972 | REPDAILY | 00022740 | SPIMAINT | Replace insulators MLTS-TGTS 220kv Line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027570839380.45 | 10275708 |  | Parent | FALSE | DDTS NO.3 220KV LINE NO.1 BUS CB AT GNTS | 39380.45 | 39380.5903 | REPDAILY | [12 empty] | 0
_1027606739380.875 | 10276067 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 39380.875 | 39384.3243 | CONT | [12 empty] | 0
_1027606839381.2840277778 | 10276068 |  | Parent | FALSE | YPS -YWPS 3 220KV G | 39381.284 | 39381.9243 | CONT | 00020520 | GENCO | Isolation for GenCO | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025933439381.2916666667 | 10259334 |  | Parent | FALSE | EX - NO.4 220KV CAPACITOR BANK CB CT R/PH AT BLTS | 39381.2917 | 39381.4597 | DAILY | [12 empty] | 0
_1027579839381.2944444444 | 10275798 |  | Parent | FALSE | HWTS-CBTS 4 500KV G | 39381.2944 | 39381.6438 | DAILY | 00362364 | SPIMAINT | Hot joint to repair | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027572439381.2972222222 | 10275724 |  | Parent | TRUE | EX - NO.2 220KV BUS AT SHTS | 39381.2972 | 39381.6875 | REPDAILY | 00000846 | SPICAPX | Manufacturers adjustments to Earth Switches | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027572639381.2972222222 | 10275726 | 10275724 | Child | FALSE | GNTS NO.3 220KV LINE AT SHTS | 39381.2972 | 39381.6875 | REPDAILY | 00352426 | SPICAPX | Rebate for line outage during No2 220kv Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X66858A439381.3173611111 | X66858A4 |  | Parent | FALSE | MLTS-TGTS 220KV W | 39381.3174 | 39381.6507 | REPDAILY | 00022740 | SPIMAINT | Replace insulators MLTS-TGTS 220kv Line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025933639381.4625 | 10259336 |  | Parent | FALSE | 1A-2A 220KV BUS TIE CB CT R/PH AT BLTS | 39381.4625 | 39381.5778 | DAILY | [12 empty] | 0
_1027611839381.9708333333 | 10276118 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 39381.9708 | 39388.5811 | CONT | 00356081 | GENCO | Isolations and Earthing | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358G039382.2791666667 | Z51358G0 |  | Parent | TRUE | NO.2 220KV BUS AT RWTS | 39382.2792 | 39382.6201 | REPDAILY | 00007478 | DB_AUG | Assemble new 220kv ROI Structure in bay M | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358I039382.2791666667 | Z51358I0 | Z51358G0 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RWTS | 39382.2792 | 39382.6201 | REPDAILY | 00350529 | DB_AUG | Rebate Cap Bank for bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X66858A339382.2930555556 | X66858A3 |  | Parent | FALSE | SVTS-HTS 1 220KV E | 39382.2931 | 39382.4431 | DAILY | 00022771 | SPIMAINT | Replace insulators | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X66858A539382.2958333333 | X66858A5 |  | Parent | FALSE | KTS NO.2 220KV LINE AT TTS | 39382.2958 | 39382.6132 | DAILY | 00015727 | SPIMAINT | Replace insulators TTS - KTS 2 220kv Line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X41758A839382.3034722222 | X41758A8 |  | Parent | FALSE | L1 220/22KV TRANS AT WMTS | 39382.3035 | 39382.6826 | CONT | 00003234 | SPICAPX | clean down the transformer | SPIPOWER | X417 | X417 - 220KV BUSHING REPLACEMENT 2004/05 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024868639382.3041666667 | 10248686 |  | Parent | FALSE | 1-3 220KV BUS TIE CB AT SVTS | 39382.3042 | 39382.5785 | DAILY | [12 empty] | 0
_X66858A239382.4458333333 | X66858A2 |  | Parent | FALSE | SVTS-HTS 2 220KV E | 39382.4458 | 39382.5979 | DAILY | 00022773 | SPIMAINT | Replace insulators SVTS-HTS No 2 Line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024868939383.2541666667 | 10248689 |  | Parent | TRUE | 2-4 220KV BUS TIE CB AT SVTS | 39383.2542 | 39383.5535 | DAILY | [12 empty] | 0
_1025950039383.2541666667 | 10259500 | 10248689 | Child | FALSE | 2-4 220KV BUS TIE CB NO.2 BUS CT R/PH AT SVTS | 39383.2542 | 39383.5535 | DAILY | [12 empty] | 0
_1024673839383.2597222222 | 10246738 |  | Parent | FALSE | C SOUTH 22KV BUS PROT AT RTS | 39383.2597 | 39383.5375 | DAILY | [12 empty] | 0
_X62258A339384.2458333333 | X62258A3 |  | Parent | TRUE | A3 TRANS 500KV CB AT KTS | 39384.2458 | 39389.5674 | CONT | [12 empty] | 0
_X62258Z039384.2458333333 | X62258Z0 | X62258A3 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 39384.2458 | 39389.5674 | CONT | 00026097 | SPICAPX | replace 500kv ct's | SPIPOWER | X622 | X622 - 500KV CTS FOR REPLACEMENT/SPARES | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027612839384.5291666667 | 10276128 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39384.5292 | 39384.6166 | DAILY | 00319999 | APDALCOA | APD No2 500kV line de-energised for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X41258F339385.2083333333 | X41258F3 |  | Parent | TRUE | B3 220/66KV TRANS AT SHTS | 39385.2083 | 39385.2826 | DAILY | 00000842 | SPICAPX | Wiring Mods for 220 and 66kv CB and VT Prot | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X41258F439385.2083333333 | X41258F4 | X41258F3 | Child | FALSE | B3 220/66KV TRANS AT SHTS | 39385.2083 | 39385.2826 | DAILY | 00000842 | SPICAPX | Perf calc for No3 Transformer outage | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024944639385.2298611111 | 10249446 |  | Parent | FALSE | SYN/COND AT BLTS | 39385.2299 | 39388.4741 | CONT | 00002547 | SPIMAINT | 3 Monthly O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758H939385.2555555556 | X49758H9 |  | Parent | FALSE | EX - 3-4 66KV BUS TIE CB AT BETS | 39385.2556 | 39387.2771 | CONT | [12 empty] | 0
_1027578439385.2701388889 | 10275784 |  | Parent | TRUE | S011 HWPS-YPS 1 220KV | 39385.2701 | 39385.5951 | DAILY | [12 empty] | 0
_1027655239385.2701388889 | 10276552 | 10275784 | Child | FALSE | HWPS NO.1 220KV LINE AT YPS | 39385.2701 | 39385.5951 | DAILY | 00016409 | SPIMAINT | Rebate for Hot joint to repair | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025952039385.44375 | 10259520 |  | Parent | FALSE | EX - HWPS NO.1 220KV LINE CB CT R/PH AT YPS | 39385.4437 | 39385.5951 | DAILY | [12 empty] | 0
_1027618839385.4659722222 | 10276188 |  | Parent | FALSE | B1 220/66KV TRANS AT TSTS | 39385.466 | 39385.4708 | DAILY | 00007657 | FORCED | No1Trans switched to remove foreign object | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358H039385.59375 | Z51358H0 |  | Parent | FALSE | 1-2 EXT 66KV BUS TIE CB AT RWTS | 39385.5938 | 39389.2778 | CONT | [12 empty] | 0
_Z51358H239385.6055555556 | Z51358H2 |  | Parent | FALSE | NW 66KV FDR CB AT RWTS | 39385.6056 | 39484.3208 | CONT | [12 empty] | 0
_Z51358H139385.6166666667 | Z51358H1 |  | Parent | FALSE | RWN NO.2 66KV FDR CB AT RWTS | 39385.6167 | 39484.3197 | CONT | [12 empty] | 0
_Z51358G939385.6340277778 | Z51358G9 |  | Parent | FALSE | B1 TRANS 66KV CB AT RWTS | 39385.634 | 39402.5195 | CONT | [12 empty] | 0
_X41258F339386.2097222222 | X41258F3 |  | Parent | TRUE | B3 220/66KV TRANS AT SHTS | 39386.2097 | 39387.7264 | DAILY | 00000842 | SPICAPX | Wiring Mods for 220 and 66kv CB and VT Prot | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X41258F439386.2097222222 | X41258F4 | X41258F3 | Child | FALSE | B3 220/66KV TRANS AT SHTS | 39386.2097 | 39387.7264 | DAILY | 00000842 | SPICAPX | Perf calc for No3 Transformer outage | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025147639386.2534722222 | 10251476 |  | Parent | TRUE | EPS-TTS 220KV CABLE A | 39386.2535 | 39386.5833 | DAILY | 00026839 | SPIMAINT | OVERHAUL POWER CABLE A & B | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027620639386.2534722222 | 10276206 | 10251476 | Child | FALSE | EPS-TTS 220KV LINE AT SMTS | 39386.2535 | 39386.5833 | DAILY | 00015363 | SPIMAINT | REBATE W/O FOR OVERHAUL POWER CABLE A & B | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027584939386.2534722222 | 10275849 |  | Parent | FALSE | CBTS NO.4 500KV LINE AT ROTS (RTF) | 39386.2535 | 39386.5908 | DAILY | 00356730 | SPIMAINT | Repaire Earth Switch | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027562639386.2722222222 | 10275626 |  | Parent | TRUE | EX - KTS NO.2 220KV LINE CB AT GTS | 39386.2722 | 39386.4799 | DAILY | [12 empty] | 0
_1027575839386.2722222222 | 10275758 | 10275626 | Child | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39386.2722 | 39386.4799 | DAILY | 00017901 | SPIMAINT | Rebate W/O for KTS No2 220kv Line Outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025954439386.2881944444 | 10259544 | 10260909 | Child | FALSE | EX - NO.2 MAIN TRANS 500KV CB CT R/PH AT HWTS | 39386.2882 | 39386.6285 | DAILY | [12 empty] | 0
_1026090939386.2881944444 | 10260909 |  | Parent | TRUE | A2 515/230KV TRANS B/PH AT HWTS | 39386.2882 | 39386.6285 | DAILY | 00009775 | SPIMAINT | REPAIR CONSERVATOR OIL LEVEL GAUGE | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027619339386.4069444445 | 10276193 |  | Parent | FALSE | JLGB NO.1 UNIT TRANS DISC CB AT JLGB | 39386.4069 | 39394.4451 | CONT | [12 empty] | 0
_1027580339386.8083333333 | 10275803 |  | Parent | FALSE | S005 YPS -YWPS 3 220KV | 39386.8083 | 39389.3583 | CONT | [12 empty] | 0
_1027622139386.8125 | 10276221 |  | Parent | FALSE | YWPS NO.3 220KV LINE AT YPS | 39386.8125 | 39389.3569 | CONT | 00016426 | GENCO | Isolation and earthing for YWPS Unit 3 | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758I139387.2395833333 | X49758I1 | X49758I0 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT BETS | 39387.2396 | 39387.8924 | DAILY | 00350819 | SPICAPX | Rebate W/O 2A Cap bk during No4 66kV Bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49758I239387.2395833333 | X49758I2 | X49758I0 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 39387.2396 | 39387.8924 | DAILY | 00016274 | SPICAPX | Rebate W/O 2B Cap bk during No4 66kV Bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758I339387.2395833333 | X49758I3 | X49758I0 | Child | FALSE | R4 220/66/22KV TRANS AT BETS | 39387.2396 | 39387.8924 | DAILY | 00016220 | SPICAPX | Perc calc W/O No4 Trans during No4 66kV Bus outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49758I039387.2395833333 | X49758I0 |  | Parent | TRUE | NO.4 66KV BUS AT BETS | 39387.2396 | 39387.8926 | DAILY | 00016367 | SPICAPX | Out W/O No4 66kV Bus-commiss new 3-4 Bus Tie CB | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024609939387.2604166667 | 10246099 |  | Parent | FALSE | 3-4 220KV BUS TIE CB AT RTS | 39387.2604 | 39387.5514 | DAILY | [12 empty] | 0
_1027578939387.2611111111 | 10275789 |  | Parent | FALSE | HWTS-ROTS 3 500KV E | 39387.2611 | 39387.6076 | DAILY | 00360709 | SPIMAINT | Hot joint to repair | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026284239387.2715277778 | 10262842 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39387.2715 | 39387.4785 | DAILY | [12 empty] | 0
_1024894339387.2763888889 | 10248943 |  | Parent | FALSE | NO.2 TRANS 66KV CB AT WOTS | 39387.2764 | 39387.6993 | DAILY | [12 empty] | 0
_1024934139387.2777777778 | 10249341 |  | Parent | FALSE | EX - KTS NO.3 220KV LINE NO.2 BUS CB AT GTS | 39387.2778 | 39388.5729 | CONT | [12 empty] | 0
_1027578439388.2708333333 | 10275784 |  | Parent | TRUE | S011 HWPS-YPS 1 220KV | 39388.2708 | 39388.5847 | DAILY | [12 empty] | 0
_1027655239388.2708333333 | 10276552 | 10275784 | Child | FALSE | HWPS NO.1 220KV LINE AT YPS | 39388.2708 | 39388.5847 | DAILY | 00016409 | SPIMAINT | Rebate for Hot joint to repair | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027624939388.3194444444 | 10276249 |  | Parent | TRUE | EPS 220KV LINE CB AT TTS | 39388.3194 | 39388.6111 | DAILY | [12 empty] | 0
_1027655439388.3194444444 | 10276554 | 10276249 | Child | FALSE | EPS 220KV LINE AT TTS | 39388.3194 | 39388.6111 | DAILY | 00015730 | SPIMAINT | Rebate tests on auto recl rel&replace close cutout | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026286939388.4875 | 10262869 |  | Parent | FALSE | NO.1 11/220KV TRANS BANK AT MPS | 39388.4875 | 39389.8972 | CONT | 00001082 | SPIMAINT | ADJUST 220KV BUSHING OIL LEVELS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X41758A939389.2409722222 | X41758A9 |  | Parent | FALSE | L1 220/22KV TRANS AT WMTS | 39389.241 | 39389.3007 | CONT | 00003234 | SPICAPX | replace transformer 220KV bushings | SPIPOWER | X417 | X417 - 220KV BUSHING REPLACEMENT 2004/05 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027630639389.5534722222 | 10276306 |  | Parent | FALSE | EX - TTS NO.1 220KV LINE NO.2 BUS CB AT KTS | 39389.5535 | 39391.5278 | CONT | [12 empty] | 0
_1027631139389.8208333333 | 10276311 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39389.8208 | 39390.191 | CONT | 00026089 | FAULT | Fault operation | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027631239390.2284722222 | 10276312 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 39390.2285 | 39391.0792 | CONT | 00356083 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025076539390.2569444444 | 10250765 |  | Parent | FALSE | JLGB 220KV BUS AT JLGB | 39390.2569 | 39390.5889 | DAILY | 00325273 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026138439391.3083333333 | 10261384 |  | Parent | TRUE | KTS NO.2 220KV LINE CB AT TTS | 39391.3083 | 39391.6056 | DAILY | [12 empty] | 0
_1027655839391.3083333333 | 10276558 | 10261384 | Child | FALSE | KTS NO.2 220KV LINE AT TTS | 39391.3083 | 39391.6056 | DAILY | 00015727 | SPIMAINT | Rebate for repair air leak in cb cubicle | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027630239391.3090277778 | 10276302 |  | Parent | FALSE | BATS NO.1 220KV LINE NO.1 BUS CB AT MLTS | 39391.309 | 39391.5243 | DAILY | [12 empty] | 0
_1027641139391.5506944445 | 10276411 |  | Parent | FALSE | EX - NO.4 MAIN TRANS NO.1 BUS 500KV CB AT HWTS | 39391.5507 | 39391.5639 | CONT | [12 empty] | 0
_1024937639393.2229166667 | 10249376 |  | Parent | FALSE | SYN/COND AT FBTS | 39393.2229 | 39395.5854 | CONT | 00002697 | SPIMAINT | 3 Monthly O/HAUL - FBTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027585039393.2291666667 | 10275850 |  | Parent | FALSE | SMTS NO.3 500KV LINE AT ROTS (RTF) | 39393.2292 | 39393.6382 | DAILY | 00356731 | SPIMAINT | Repaire Earth Switch on SMTS Line | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027602539393.3125 | 10276025 |  | Parent | TRUE | MLTS NO.1 220KV LINE CB AT BATS | 39393.3125 | 39393.5417 | DAILY | [12 empty] | 0
_1027602639393.3125 | 10276026 | 10276025 | Child | FALSE | MLTS NO.1 220KV LINE AT BATS | 39393.3125 | 39393.5417 | DAILY | 00012429 | SPICAPX | Rebate W/O for MLTS No1 220kv Line outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027642739393.3291666667 | 10276427 |  | Parent | FALSE | 2-4 22KV BUS TIE CB AT BETS | 39393.3292 | 39393.6049 | DAILY | [12 empty] | 0
_1027646139393.5861111111 | 10276461 |  | Parent | FALSE | B1 TRANS 66KV CB AT MTS | 39393.5861 | 39413.4703 | CONT | [12 empty] | 0
_X32058M339393.5909722222 | X32058M3 |  | Parent | FALSE | U2 66/22KV TRANS AT MTS | 39393.591 | 39394.4479 | CONT | 00363319 | SPICAPX | Hold out permit on New U2 Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058M139393.6409722222 | X32058M1 |  | Parent | FALSE | OR 66KV FDR CB AT MTS | 39393.641 | 39415.5333 | CONT | [12 empty] | 0
_X32058M239393.6409722222 | X32058M2 |  | Parent | FALSE | EM 66KV FDR CB AT MTS | 39393.641 | 39415.534 | CONT | [12 empty] | 0
_1027646839394.0895833333 | 10276468 |  | Parent | TRUE | MWTS-MPS LINE 220KV CB AT HWPS | 39394.0896 | 39394.1528 | CONT | [12 empty] | 0
_1027656039394.0895833333 | 10276560 | 10276468 | Child | FALSE | MPS-MWTS 220KV LINE AT HWPS | 39394.0896 | 39394.1528 | CONT | 00015789 | GENCO | Rebate CB Opened Auto by R/T from MPS Gen Prot | GENCO |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024753039394.2555555556 | 10247530 |  | Parent | FALSE | R4 220/66/22KV TRANS AT BETS | 39394.2556 | 39394.6847 | REPDAILY | 00016220 | SPIMAINT | O/HAUL Transformer and Trafo Union Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027583239394.2555555556 | 10275832 |  | Parent | FALSE | R4 220/66/22KV TRANS AT BETS | 39394.2556 | 39394.6847 | REPDAILY | 00016220 | SPIMAINT | Perf Calc for No4 Transformer Outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027604239394.2784722222 | 10276042 |  | Parent | TRUE | NO.1 330KV CAPACITOR BANK AT DDTS | 39394.2785 | 39394.3514 | DAILY | 00352085 | TRANSGRD | Spray weeds and grass in Cap Bank enclosure | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_1027604439394.2784722222 | 10276044 | 10276042 | Child | FALSE | NO.1 330KV CAPACITOR BANK AT DDTS | 39394.2785 | 39394.3514 | DAILY | 00352085 | TRANSGRD | Rebate W/O for Cap Bk Outage | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_X49758I839394.2805555556 | X49758I8 |  | Parent | FALSE | BATS 220KV LINE NO.1 BUS CB AT BETS | 39394.2806 | 39401.4549 | DAILY | [12 empty] | 0
_1027642939394.3048611111 | 10276429 |  | Parent | FALSE | HPS 66KV LINE CB AT WOTS | 39394.3049 | 39394.625 | DAILY | [12 empty] | 0
_1027602439394.3208333333 | 10276024 |  | Parent | FALSE | MLTS NO.2 220KV LINE NO.2 BUS CB AT BATS | 39394.3208 | 39394.4861 | DAILY | [12 empty] | 0
_1025943439394.3340277778 | 10259434 |  | Parent | FALSE | EX - BATS NO.2 220KV LINE CB CT R/PH AT MLTS | 39394.334 | 39394.4861 | DAILY | [12 empty] | 0
_1027604539394.3777777778 | 10276045 |  | Parent | TRUE | NO.2 330KV CAPACITOR BANK AT DDTS | 39394.3778 | 39394.4465 | DAILY | 00352093 | TRANSGRD | Spray Weeds and grass in Cap Bank enclosure | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_1027604639394.3777777778 | 10276046 | 10276045 | Child | FALSE | NO.2 330KV CAPACITOR BANK AT DDTS | 39394.3778 | 39394.4465 | DAILY | 00352093 | TRANSGRD | Rebate W/O for Cap Bk Outage | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_1027646539394.4458333333 | 10276465 |  | Parent | FALSE | JLGB NO.3 UNIT TRANS DISC CB AT JLGB | 39394.4458 | 39409.5701 | CONT | [12 empty] | 0
_1027646439394.9916666667 | 10276464 |  | Parent | FALSE | YWPS NO.4 220KV LINE AT YPS | 39394.9917 | 39420.8194 | CONT | 00016428 | GENCO | W4 GTG Isolation and Earth requested by P Station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758I939395.25 | X49758I9 |  | Parent | TRUE | EX - NO.3 66KV CAPACITOR BANK CB AT BETS | 39395.25 | 39395.4618 | DAILY | [12 empty] | 0
_X49758J039395.25 | X49758J0 | X49758I9 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT BETS | 39395.25 | 39395.4618 | DAILY | 00350820 | SPICAPX | Rebate W/O 3A Cap bank during 3A/B CB outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49758J139395.25 | X49758J1 | X49758I9 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 39395.25 | 39395.4618 | DAILY | 00016304 | SPICAPX | Rebate W/O 3B Cap bank during 3A/B CB outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024753039395.2631944444 | 10247530 |  | Parent | FALSE | R4 220/66/22KV TRANS AT BETS | 39395.2632 | 39395.6083 | REPDAILY | 00016220 | SPIMAINT | O/HAUL Transformer and Trafo Union Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027583239395.2631944444 | 10275832 |  | Parent | FALSE | R4 220/66/22KV TRANS AT BETS | 39395.2632 | 39395.6083 | REPDAILY | 00016220 | SPIMAINT | Perf Calc for No4 Transformer Outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027604139395.2715277778 | 10276041 |  | Parent | TRUE | NO.2 330KV CAPACITOR BANK AT WOTS | 39395.2715 | 39395.3479 | DAILY | 00354001 | TRANSGRD | Spray weeds and grass in Cap Bank Enclosure | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_1027604339395.2715277778 | 10276043 | 10276041 | Child | FALSE | NO.2 330KV CAPACITOR BANK AT WOTS | 39395.2715 | 39395.3479 | DAILY | 00354001 | TRANSGRD | Rebate W/O for N02 Cap Bk Outage | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_1025945639395.2743055556 | 10259456 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE/A1 TRANS CB CT R/PH AT MLTS | 39395.2743 | 39395.3208 | DAILY | [12 empty] | 0
_1027532139395.2798611111 | 10275321 |  | Parent | FALSE | C 66/11KV S/S TRANS 66KV FDR NO.2 BUS CB AT LY | 39395.2799 | 39395.5326 | DAILY | [12 empty] | 0
_1027602339395.3041666667 | 10276023 |  | Parent | FALSE | MLTS NO.2 220KV LINE NO.1 BUS CB AT BATS | 39395.3042 | 39395.4 | DAILY | [12 empty] | 0
_1027653639395.9493055556 | 10276536 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 39395.9493 | 39397.8607 | CONT | 00356080 | GENCO | HWPS U2 SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027653739396.0069444444 | 10276537 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39396.0069 | 39398.5076 | CONT | 00356082 | GENCO | HWPS U4 Isolation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51058F039396.2305555556 | Z51058F0 |  | Parent | FALSE | B2 220/66KV TRANS AT ATS | 39396.2306 | 39397.5687 | CONT | 00060871 | SPICAPX | rem trans bus in bay 5&6 install connect in bay 6 | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027610339396.2576388889 | 10276103 |  | Parent | TRUE | S182 MSS -DDTS 2 330KV VIC | 39396.2576 | 39396.5243 | DAILY | [12 empty] | 0
_1027656139396.2576388889 | 10276561 | 10276103 | Child | FALSE | MSS -DDTS 2 330KV NW | 39396.2576 | 39396.5243 | DAILY | 00060191 | SPIMAINT | Rebate-Replace Flashed Insulators at S182 W ph | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027652839396.2951388889 | 10276528 |  | Parent | FALSE | RCTS LINE NO.1 BUS CB AT KGTS | 39396.2951 | 39396.3632 | DAILY | [12 empty] | 0
_1027620539396.3923611111 | 10276205 |  | Parent | FALSE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39396.3924 | 39396.4153 | DAILY | [12 empty] | 0
_1027652639396.3923611111 | 10276526 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39396.3924 | 39396.4153 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during 275kV CB outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027653839396.4604166667 | 10276538 |  | Parent | FALSE | SYN/COND AT FBTS | 39396.4604 | 39396.5236 | CONT | 00002697 | FAULT | FBTS Synch Cond Tripped | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024880039397.2493055556 | 10248800 |  | Parent | FALSE | B3 220/66KV TRANS AT ERTS | 39397.2493 | 39397.5813 | DAILY | 00004371 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027647139397.2777777778 | 10276471 |  | Parent | FALSE | EX - NO.1 22KV/415V S/S TRANS AT WMTS | 39397.2778 | 39397.5833 | DAILY | 00003238 | DBPROX | VSCAP to Citipower | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1027654439397.2847222222 | 10276544 |  | Parent | FALSE | SYN/COND AT FBTS | 39397.2847 | 39399.2944 | CONT | 00002697 | FAULT | Syn Con trip | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027623339397.4479166667 | 10276233 | V60458A5 | Child | FALSE | HWTS-SMTS 1 500KV WT | 39397.4479 | 39397.4611 | DAILY | 00119314 | SPIMAINT | Rebat W/O for HWTS-SMTS 1 | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027623439397.4479166667 | 10276234 | V60458A5 | Child | FALSE | SMTS-SYTS 1 500KV WT | 39397.4479 | 39397.4611 | DAILY | 00022640 | SPIMAINT | Rebate W/O for SMTS-SYTS 1 | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458A539397.4479166667 | V60458A5 |  | Parent | TRUE | SYTS NO.1 500KV LINE NO.1 BUS CB AT SMTS | 39397.4479 | 39397.4611 | DAILY | [12 empty] | 0
_Z51058F339397.59375 | Z51058F3 |  | Parent | FALSE | B2 220/66KV TRANS AT ATS | 39397.5938 | 39434.316 | CONT | 00060871 | SPICAPX | FUTURE B4 TRANS #2 BUS 220KV CB AT ATS | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z73058A539398.2284722222 | Z73058A5 |  | Parent | FALSE | ROTS 220KV LINE AT TTS | 39398.2285 | 39403.7028 | CONT | 00015733 | DB_AUG | line deviation for SMTS 220kv augmentation | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1009266939398.2597222222 | 10092669 |  | Parent | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39398.2597 | 39398.6639 | REPDAILY | 00017906 | SPIMAINT | O/Haul - PT.HENRY 220kV No.2 LINE at GTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027601039398.2597222222 | 10276010 |  | Parent | FALSE | EX - MLTS NO.2 220KV LINE AT GTS | 39398.2597 | 39398.6639 | REPDAILY | 00017904 | SPIMAINT | Rebate W/O MLTS No2 Line- CT's de-energ for prox. | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027646039398.29375 | 10276460 |  | Parent | FALSE | AUX TRANS 'C' 220KV LINE AT YPS | 39398.2937 | 39403.0312 | CONT | 00016421 | GENCO | SCAP requested by Genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024824339399.25 | 10248243 |  | Parent | FALSE | W4 GEN TRANS 220KV LINE E/SW AT YPS | 39399.25 | 39399.6042 | DAILY | [12 empty] | 0
_1025010939399.25 | 10250109 |  | Parent | TRUE | H2 TRANS 330KV CB AT DDTS | 39399.25 | 39399.6153 | REPDAILY | [12 empty] | 0
_1027612539399.25 | 10276125 | 10250109 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 39399.25 | 39399.6153 | REPDAILY | 00352121 | SPIMAINT | Rebate W/O No2 Trans during 330kV CB O/H | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009266939399.2583333333 | 10092669 |  | Parent | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39399.2583 | 39399.6694 | REPDAILY | 00017906 | SPIMAINT | O/Haul - PT.HENRY 220kV No.2 LINE at GTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027601039399.2583333333 | 10276010 |  | Parent | FALSE | EX - MLTS NO.2 220KV LINE AT GTS | 39399.2583 | 39399.6694 | REPDAILY | 00017904 | SPIMAINT | Rebate W/O MLTS No2 Line- CT's de-energ for prox. | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027656539399.2944444444 | 10276565 |  | Parent | FALSE | SYN/COND AT FBTS | 39399.2944 | 39399.575 | DAILY | 00002697 | FAULT | investigate bearing temperature trip | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027656439399.3166666667 | 10276564 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 39399.3167 | 39399.6424 | DAILY | 00027386 | APDALCOA | For Alcoa | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027645439399.3361111111 | 10276454 |  | Parent | FALSE | 2-3 220KV BUS TIE CB AT TTS | 39399.3361 | 39399.5417 | DAILY | [12 empty] | 0
_1027663639399.6270833333 | 10276636 |  | Parent | FALSE | BETS-FVTS-SHTS 220KV NB | 39399.6271 | 39399.6465 | DAILY | 00026225 | FAULT | BETS : SHTS-FVTS Line Trip OUT outage capture | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025010939400.2479166667 | 10250109 |  | Parent | TRUE | H2 TRANS 330KV CB AT DDTS | 39400.2479 | 39400.6139 | REPDAILY | [12 empty] | 0
_1027612539400.2479166667 | 10276125 | 10250109 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 39400.2479 | 39400.6139 | REPDAILY | 00352121 | SPIMAINT | Rebate W/O No2 Trans during 330kV CB O/H | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027657239400.2513888889 | 10276572 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39400.2514 | 39400.6549 | DAILY | 00319999 | APDALCOA | SCAP to APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1024849639400.2743055556 | 10248496 |  | Parent | FALSE | SYN/COND AT TSTS | 39400.2743 | 39402.566 | CONT | 00007626 | SPIMAINT | 4 Monthly O/HAUL - TSTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1009267139400.2777777778 | 10092671 |  | Parent | TRUE | ROTS NO.8 220KV LINE AT YPS | 39400.2778 | 39400.6285 | DAILY | 00016416 | SPIMAINT | O/Haul - ROTS No.8 220kV Line at YPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009268739400.2777777778 | 10092687 | 10092671 | Child | FALSE | ROTS NO.8 220KV LINE NO.2 BUS CB AT YPS | 39400.2778 | 39400.6285 | DAILY | [12 empty] | 0
_1009269039400.2777777778 | 10092690 | 10092671 | Child | FALSE | ROTS NO.8 220KV LINE NO.2 BUS CB LINE SIDE E/SW AT YPS | 39400.2778 | 39400.6285 | DAILY | [12 empty] | 0
_1009269239400.2777777778 | 10092692 | 10092671 | Child | FALSE | ROTS NO.8 220KV LINE E/SW AT YPS | 39400.2778 | 39400.6285 | DAILY | [12 empty] | 0
_1009269439400.2777777778 | 10092694 | 10092671 | Child | FALSE | ROTS NO.8 220KV LINE NO.2 BUS CB LINE SIDE ISOL AT YPS | 39400.2778 | 39400.6285 | DAILY | [12 empty] | 0
_1025953039400.2777777778 | 10259530 | 10092671 | Child | FALSE | ROTS NO.8 220KV LINE NO.2 BUS CB CT R/PH AT YPS | 39400.2778 | 39400.6285 | DAILY | [12 empty] | 0
_X41258F739400.33125 | X41258F7 |  | Parent | FALSE | B3 220/66KV TRANS AT SHTS | 39400.3313 | 39400.541 | DAILY | 00000842 | SPICAPX | Out W/O B3 Transformer for Prot wiring mods | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158BT39400.4694444445 | Z53158BT |  | Parent | FALSE | ERTS NO.1 220KV LINE AT ROTS | 39400.4694 | 39400.6979 | DAILY | 00350666 | SPICAPX | Spacer and spake gap rods | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027660339400.5715277778 | 10276603 |  | Parent | FALSE | WMTS NO.2 220KV LINE CB AT FBTS | 39400.5715 | 39400.5833 | CONT | [12 empty] | 0
_1027660439400.6236111111 | 10276604 |  | Parent | FALSE | ROTS NO.4 500KV LINE AT CBTS | 39400.6236 | 39400.7868 | DAILY | 00359492 | SPIMAINT | Repaire CVT | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027648639401.2666666667 | 10276486 |  | Parent | FALSE | HWPS NO.1 220KV LINE AT YPS | 39401.2667 | 39401.4396 | DAILY | 00016409 | SPIMAINT | CT Oil Samples | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027544739401.2722222222 | 10275447 |  | Parent | TRUE | M1 500/275KV TRANS 22KV VT B/PH AT HYTS | 39401.2722 | 39401.6229 | DAILY | [12 empty] | 0
_1027612439401.2722222222 | 10276124 | 10275447 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39401.2722 | 39401.6229 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during 22kV VT replacement | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025013339401.2770833333 | 10250133 |  | Parent | TRUE | GNTS NO.1 220KV LINE CB AT DDTS | 39401.2771 | 39401.5931 | DAILY | [12 empty] | 0
_1027614939401.2770833333 | 10276149 | 10250133 | Child | FALSE | GNTS NO.1 220KV LINE AT DDTS | 39401.2771 | 39401.5931 | DAILY | 00352475 | SPIMAINT | Rebate W/O GNTS No1 Line during CB O/H | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027662039401.2770833333 | 10276620 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 39401.2771 | 39404.7937 | CONT | 00356080 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027661939401.2819444445 | 10276619 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 39401.2819 | 39405.2097 | CONT | 00356079 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027623939401.2888888889 | 10276239 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT ATS | 39401.2889 | 39401.3528 | DAILY | [12 empty] | 0
_1025935839401.3444444445 | 10259358 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE CB CT R/PH AT WMTS | 39401.3444 | 39401.5965 | DAILY | [12 empty] | 0
_1027662739401.3826388889 | 10276627 |  | Parent | FALSE | SRR 66KV FDR CB AT RWTS | 39401.3826 | 39410.6035 | CONT | [12 empty] | 0
_1027662439401.3958333333 | 10276624 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS AT JLGB | 39401.3958 | 39401.4792 | CONT | 00009830 | GENCO | Power Station req'ment | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1027651639401.5694444444 | 10276516 |  | Parent | FALSE | WBTS 220KV LINE AT BATS | 39401.5694 | 39401.6458 | DAILY | 00330862 | SPIMAINT | Rectify HOTS Line ARC issues | SPIPOWER |  |  | CONTL | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0 | 10276516 |  | Rectify HOTS Line ARC issues | 00330862 | CONTL |  | BATS | CONEQUIP | SPIMAINT | IN-SERV
_1027663939401.6770833333 | 10276639 |  | Parent | FALSE | W3 GEN TRANS NO.1 BUS 220KV CB AT YPS | 39401.6771 | 39418.5493 | DAILY | [12 empty] | 0
_1024839339402.2555555556 | 10248393 |  | Parent | TRUE | NO.1 220KV BUS AT HWPS | 39402.2556 | 39402.641 | DAILY | 00009658 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024842239402.2555555556 | 10248422 | 10248393 | Child | FALSE | EX - NO.3 GEN TRANS NO.1 BUS 220KV CB BUS SIDE E/SW AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024842639402.2555555556 | 10248426 | 10248393 | Child | FALSE | EX - NO.4 GEN TRANS NO.1 BUS 220KV CB BUS SIDE E/SW AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024843039402.2555555556 | 10248430 | 10248393 | Child | FALSE | NO.1 BUS 220KV E/SW AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024843239402.2555555556 | 10248432 | 10248393 | Child | FALSE | EX - NO.1 GEN TRANS 220KV CB BUS SIDE E/SW AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024843639402.2555555556 | 10248436 | 10248393 | Child | FALSE | EX - NO.2 GEN TRANS 220KV CB BUS SIDE E/SW AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024844239402.2555555556 | 10248442 | 10248393 | Child | FALSE | EX - JLTS NO.1 LINE/AUX TRANS 'B' 220KV CB BUS SIDE E/SW AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024844639402.2555555556 | 10248446 | 10248393 | Child | FALSE | EX - ROTS NO.2 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024845239402.2555555556 | 10248452 | 10248393 | Child | FALSE | EX - HWTS NO.2 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024845639402.2555555556 | 10248456 | 10248393 | Child | FALSE | EX - NO.4 GEN TRANS NO.1 BUS 220KV CB BUS SIDE ISOL AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024846239402.2555555556 | 10248462 | 10248393 | Child | FALSE | EX - ROTS NO.2 220KV LINE NO.1 BUS CB BUS SIDE ISOL AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024846439402.2555555556 | 10248464 | 10248393 | Child | FALSE | EX - NO.1 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024846639402.2555555556 | 10248466 | 10248393 | Child | FALSE | EX - NO.2 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024847239402.2555555556 | 10248472 | 10248393 | Child | FALSE | EX - NO.3 GEN TRANS NO.1 BUS 220KV CB BUS SIDE ISOL AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024847839402.2555555556 | 10248478 | 10248393 | Child | FALSE | EX - HWTS NO.2 220KV LINE NO.1 BUS CB BUS SIDE ISOL AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1024848039402.2555555556 | 10248480 | 10248393 | Child | FALSE | EX - JLTS NO.1 LINE-AUX TRANS 'B' 220KV CB BUS SIDE ISOL AT HWPS | 39402.2556 | 39402.641 | DAILY | [12 empty] | 0
_1027654639402.2597222222 | 10276546 |  | Parent | TRUE | SESS NO.2 275KV LINE/M2 TRANS CB AT HYTS | 39402.2597 | 39402.3167 | DAILY | [12 empty] | 0
_1027654739402.2597222222 | 10276547 | 10276546 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 39402.2597 | 39402.3167 | DAILY | 00002862 | SPIMAINT | Rebate W/O M2 Trans during 275kV CB outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024753839402.2729166667 | 10247538 |  | Parent | FALSE | NO.4 TRANS 66KV CB AT BETS | 39402.2729 | 39402.6875 | DAILY | [12 empty] | 0
_1025934639402.3069444445 | 10259346 |  | Parent | TRUE | NO.4 220KV CAPACITOR BANK CB CT R/PH AT FBTS | 39402.3069 | 39402.5951 | DAILY | [12 empty] | 0
_1027674239402.3069444445 | 10276742 | 10259346 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 39402.3069 | 39402.5951 | DAILY | 00327661 | SPIMAINT | CT OIL SAMPLING | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z51358I739402.5201967593 | Z51358I7 |  | Parent | FALSE | B1 220/66KV TRANS AT RWTS | 39402.5202 | 39417.1875 | CONT | 00364702 | DB_AUG | Pre Commissioning access Fut B1 Connection Transf | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1024821439403.2069444445 | 10248214 |  | Parent | TRUE | NO.2 220KV BUS AT YPS | 39403.2069 | 39403.5778 | DAILY | 00010589 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024822939403.2069444445 | 10248229 | 10248214 | Child | FALSE | W2 GEN TRANS 220KV CB BUS SIDE E/SW AT YPS | 39403.2069 | 39403.5778 | DAILY | [12 empty] | 0
_1024823939403.2069444445 | 10248239 | 10248214 | Child | FALSE | W3 GEN TRANS NO.2 BUS 220KV CB BUS SIDE E/SW AT YPS | 39403.2069 | 39403.5778 | DAILY | [12 empty] | 0
_1024825339403.2069444445 | 10248253 | 10248214 | Child | FALSE | ROTS NO.8 220KV LINE NO.2 BUS CB BUS SIDE E/SW AT YPS | 39403.2069 | 39403.5778 | DAILY | [12 empty] | 0
_1024825539403.2069444445 | 10248255 | 10248214 | Child | FALSE | ROTS NO.5 220KV LINE NO.2 BUS CB BUS SIDE E/SW AT YPS | 39403.2069 | 39403.5778 | DAILY | [12 empty] | 0
_1024825739403.2069444445 | 10248257 | 10248214 | Child | FALSE | W1 GEN TRANS NO.2 BUS 220KV CB BUS SIDE E/SW AT YPS | 39403.2069 | 39403.5778 | DAILY | [12 empty] | 0
_1024826539403.2069444445 | 10248265 | 10248214 | Child | FALSE | AUX TRANS 'A' 220KV CB BUS SIDE E/SW AT YPS | 39403.2069 | 39403.5778 | DAILY | [12 empty] | 0
_1024826739403.2069444445 | 10248267 | 10248214 | Child | FALSE | HWPS NO.2 220KV LINE CB BUS SIDE E/SW AT YPS | 39403.2069 | 39403.5778 | CONT | [12 empty] | 0
_1024827139403.2069444445 | 10248271 | 10248214 | Child | FALSE | W1 GEN TRANS NO.2 BUS 220KV CB BUS SIDE ISOL AT YPS | 39403.2069 | 39403.5778 | CONT | [12 empty] | 0
_1024827939403.2069444445 | 10248279 | 10248214 | Child | FALSE | W2 GEN TRANS 220KV CB BUS SIDE ISOL AT YPS | 39403.2069 | 39403.5778 | CONT | [12 empty] | 0
_1024828139403.2069444445 | 10248281 | 10248214 | Child | FALSE | W3 GEN TRANS NO.2 BUS 220KV CB BUS SIDE ISOL AT YPS | 39403.2069 | 39403.5778 | CONT | [12 empty] | 0
_1024828739403.2069444445 | 10248287 | 10248214 | Child | FALSE | NO.2 220KV BUS E/SW AT YPS | 39403.2069 | 39403.5778 | DAILY | [12 empty] | 0
_1024828939403.2069444445 | 10248289 | 10248214 | Child | FALSE | AUX TRANS 'C' NO.2 BUS 220KV CB BUS SIDE E/SW AT YPS | 39403.2069 | 39403.5778 | DAILY | [12 empty] | 0
_1024829139403.2069444445 | 10248291 | 10248214 | Child | FALSE | HWPS NO.2 220KV LINE NO.2 BUS CB BUS SIDE ISOL AT YPS | 39403.2069 | 39403.5778 | DAILY | [12 empty] | 0
_1024829339403.2069444445 | 10248293 | 10248214 | Child | FALSE | ROTS NO.5 220KV LINE NO.2 BUS CB BUS SIDE ROI AT YPS | 39403.2069 | 39403.5778 | CONT | [12 empty] | 0
_1024829539403.2069444445 | 10248295 | 10248214 | Child | FALSE | ROTS NO.6 220KV LINE NO.2 BUS CB BUS SIDE ISOL AT YPS | 39403.2069 | 39403.5778 | CONT | [12 empty] | 0
_1024829739403.2069444445 | 10248297 | 10248214 | Child | FALSE | ROTS NO.8 220KV LINE NO.2 BUS CB BUS SIDE ISOL AT YPS | 39403.2069 | 39403.5778 | CONT | [12 empty] | 0
_1024830239403.2069444445 | 10248302 | 10248214 | Child | FALSE | AUX TRANS 'C' NO.2 BUS 220KV CB BUS SIDE ISOL AT YPS | 39403.2069 | 39403.5778 | CONT | [12 empty] | 0
_1024830439403.2069444445 | 10248304 | 10248214 | Child | FALSE | AUX TRANS 'A' 220KV CB BUS SIDE ROI AT YPS | 39403.2069 | 39403.5778 | CONT | [12 empty] | 0
_1024995739403.2069444445 | 10249957 | 10248214 | Child | FALSE | ROTS NO.6 220KV LINE NO.2 BUS CB BUS SIDE E/SW AT YPS | 39403.2069 | 39403.5778 | DAILY | [12 empty] | 0
_1027664439403.2069444445 | 10276644 | 10248214 | Child | FALSE | ROTS NO.8 220KV LINE AT YPS | 39403.2069 | 39403.5778 | DAILY | 00016416 | SPIMAINT | Rebate for Bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027688439403.2069444445 | 10276884 | 10248214 | Child | FALSE | HWPS NO.2 220KV LINE AT YPS | 39403.2069 | 39403.5778 | DAILY | 00016412 | SPIMAINT | Rebate for Bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858K639403.2138888889 | X49858K6 |  | Parent | TRUE | NO.1 220KV BUS AT MBTS | 39403.2139 | 39403.4021 | DAILY | 00364502 | SPICAPX | Out W/O #1 220 bus-Remove DDTS 1L-EPS 1L temp loop | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49858K739403.2138888889 | X49858K7 | X49858K6 | Child | FALSE | MBTS NO.2 220KV LINE AT DDTS | 39403.2139 | 39403.4021 | DAILY | 00012363 | SPICAPX | Rebate W/O DDTS2 Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858K839403.2138888889 | X49858K8 | X49858K6 | Child | FALSE | B2 220/66KV TRANS AT MBTS | 39403.2139 | 39403.4021 | DAILY | 00362372 | SPICAPX | Perf calc W/O B2 Trans during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49858K939403.2138888889 | X49858K9 | X49858K6 | Child | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39403.2139 | 39403.4021 | DAILY | 00011755 | SPICAPX | Rebate W/O MKPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858L039403.2138888889 | X49858L0 | X49858K6 | Child | FALSE | MBTS-EPS 2 220KV N | 39403.2139 | 39403.4021 | DAILY | 00055381 | SPICAPX | Rebate W/O EPS #2 Line during No1 220kv Bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49858L139403.2138888889 | X49858L1 | X49858K6 | Child | FALSE | WKPS 220KV LINE AT MBTS | 39403.2139 | 39403.4021 | DAILY | 00011756 | SPICAPX | Rebate W/O WKPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858L239403.2138888889 | X49858L2 | X49858K6 | Child | FALSE | MBTS NO.1 220KV LINE AT DDTS | 39403.2139 | 39403.4021 | DAILY | 00012361 | SPICAPX | Rebate W/O DDTS 1 Line outage for proximity | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858L339403.4083333333 | X49858L3 |  | Parent | TRUE | NO.1 220KV BUS AT MBTS | 39403.4083 | 39403.5972 | DAILY | 00364502 | SPICAPX | Out W/O #1 220 bus-Remove DDTS 1L-EPS 1L temp loop | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X49858L439403.4083333333 | X49858L4 | X49858L3 | Child | FALSE | MBTS NO.2 220KV LINE AT DDTS | 39403.4083 | 39403.5972 | DAILY | 00012363 | SPICAPX | Rebate W/O DDTS2 Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858L539403.4083333333 | X49858L5 | X49858L3 | Child | FALSE | B2 220/66KV TRANS AT MBTS | 39403.4083 | 39403.5972 | DAILY | 00362372 | SPICAPX | Perf calc W/O B2 Trans during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49858L639403.4083333333 | X49858L6 | X49858L3 | Child | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39403.4083 | 39403.5972 | DAILY | 00011755 | SPICAPX | Rebate W/O MKPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858L739403.4083333333 | X49858L7 | X49858L3 | Child | FALSE | MBTS-EPS 2 220KV N | 39403.4083 | 39403.5972 | DAILY | 00055381 | SPICAPX | Rebate W/O EPS #2 Line during No1 220kv Bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X49858L839403.4083333333 | X49858L8 | X49858L3 | Child | FALSE | WKPS 220KV LINE AT MBTS | 39403.4083 | 39403.5972 | DAILY | 00011756 | SPICAPX | Rebate W/O WKPS Line during No1 220kv bus outage | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49858L939403.4083333333 | X49858L9 | X49858L3 | Child | FALSE | MBTS NO.1 220KV LINE AT EPSY | 39403.4083 | 39403.5972 | DAILY | 00087035 | SPICAPX | Rebate W/O EPS 1 Line outage for proximity | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1027666539405.2555555556 | 10276665 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT TTS | 39405.2556 | 39405.3993 | DAILY | 00001485 | FAULT | cap bank tripped on out of balance | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1025013039405.2611111111 | 10250130 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.1 BUS CB AT DDTS | 39405.2611 | 39405.6083 | DAILY | [12 empty] | 0
_X55658B339405.6994560185 | X55658B3 |  | Parent | FALSE | SRR 66KV FDR CB AT RWTS | 39405.6995 | 39405.6996 | CONT | [12 empty] | 0
_Z53158BS39406.2263888889 | Z53158BS |  | Parent | FALSE | A2 515/220KV TRANS BANK AT ROTS | 39406.2264 | 39406.3882 | DAILY | 00362994 | SPICAPX | A2 220kv Connections & No 4 220kv Bus CB | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1024943439406.25625 | 10249434 |  | Parent | FALSE | NO.3A TRANS 66KV CB AT BLTS | 39406.2562 | 39406.5979 | DAILY | [12 empty] | 0
_1025013639406.2590277778 | 10250136 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.2 BUS CB AT DDTS | 39406.259 | 39406.6035 | DAILY | [12 empty] | 0
_1027666339407.2090277778 | 10276663 |  | Parent | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39407.209 | 39407.3958 | DAILY | 00007399 | SPIMAINT | RE_BALANCE CAP BANK | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z53158BU39407.2208333333 | Z53158BU |  | Parent | FALSE | RTS NO.1 220KV LINE AT ROTS | 39407.2208 | 39407.4174 | DAILY | 00023111 | SPICAPX | replace line spacers and spak gaps | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024303039407.2472222222 | 10243030 |  | Parent | FALSE | AUX TRANS 'C' NO.1 BUS 220KV CB AT YPS | 39407.2472 | 39407.4062 | DAILY | [12 empty] | 0
_X66858A939407.2506944445 | X66858A9 |  | Parent | FALSE | ROTS NO.8 220KV LINE AT YPS | 39407.2507 | 39407.5986 | REPDAILY | 00016416 | SPIMAINT | Replace insulators rots-yps no 8 220kv Ln | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V71158A039407.2840277778 | V71158A0 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39407.284 | 39433.566 | CONT | [12 empty] | 0
_1027674039407.3027777778 | 10276740 |  | Parent | FALSE | ATS 66KV LINE AT BLTS | 39407.3028 | 39407.5938 | CONT | 00017843 | SPIMAINT | HVS: ATS-BLTS 66kV Fdr | SPIPOWER |  |  | Circuits | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027667739407.3125 | 10276677 |  | Parent | FALSE | AUX TRANS 'B' 220KV CB AT YPS | 39407.3125 | 39416.5847 | CONT | [12 empty] | 0
_1024862239407.3861111111 | 10248622 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 39407.3861 | 39407.6368 | CONT | 00006554 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024302739407.4048611111 | 10243027 |  | Parent | FALSE | AUX TRANS 'B' 220KV CB AT YPS | 39407.4049 | 39407.5257 | DAILY | [12 empty] | 0
_1024303139407.5277777778 | 10243031 |  | Parent | FALSE | AUX TRANS 'C' NO.2 BUS 220KV CB AT YPS | 39407.5278 | 39407.6271 | DAILY | [12 empty] | 0
_X66858A939408.2479166667 | X66858A9 |  | Parent | FALSE | ROTS NO.8 220KV LINE AT YPS | 39408.2479 | 39408.6014 | REPDAILY | 00016416 | SPIMAINT | Replace insulators rots-yps no 8 220kv Ln | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024862539408.25 | 10248625 |  | Parent | FALSE | B2 220/66KV TRANS AT BATS | 39408.25 | 39408.625 | REPDAILY | 00006555 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026071239408.2840277778 | 10260712 |  | Parent | FALSE | 5 GRP 220/11KV TRANS AT YPS | 39408.284 | 39408.6312 | DAILY | 00010550 | SPIMAINT | YPS No 5 Grp Trans 11kv VT & CT | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027665239408.4819444444 | 10276652 |  | Parent | FALSE | W3 GEN TRANS NO.1 BUS 220KV CB AT YPS | 39408.4819 | 39408.6528 | DAILY | [12 empty] | 0
_1027665339408.6006944444 | 10276653 |  | Parent | FALSE | W3 GEN TRANS NO.2 BUS 220KV CB AT YPS | 39408.6007 | 39408.7264 | DAILY | [12 empty] | 0
_X32058M539409.20625 | X32058M5 |  | Parent | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39409.2063 | 39411.5924 | CONT | 00351697 | SPICAPX | Transfer Conductors | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X66858B039409.25 | X66858B0 |  | Parent | FALSE | ROTS NO.7 220KV LINE AT YPS | 39409.25 | 39409.5896 | REPDAILY | 00016415 | SPIMAINT | Replace insulators rots-yps no 7 220kv Ln | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024862539409.2548611111 | 10248625 |  | Parent | FALSE | B2 220/66KV TRANS AT BATS | 39409.2549 | 39409.6403 | REPDAILY | 00006555 | SPIMAINT | O/HAUL Transformer / Ferranti Div Sw | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027666139409.2625 | 10276661 |  | Parent | FALSE | S201 MSS -DDTS 1 330KV VIC | 39409.2625 | 39409.4222 | DAILY | [12 empty] | 0
_1010200939409.3006944445 | 10102009 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT BETS | 39409.3007 | 39409.6111 | DAILY | 00016431 | SPIMAINT | O/HAUL Transformer without Div Sw (N) | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1025936639409.3833333333 | 10259366 |  | Parent | FALSE | 2B-4 220KV BUS TIE CB CT R/PH AT BLTS | 39409.3833 | 39409.4361 | DAILY | [12 empty] | 0
_1025934239409.5208333333 | 10259342 |  | Parent | FALSE | 4-5 220KV BUS TIE CB CT R/PH AT BLTS | 39409.5208 | 39409.5521 | DAILY | [12 empty] | 0
_Z51358I839410.2291666667 | Z51358I8 |  | Parent | FALSE | SRR 66KV FDR CB AT RWTS | 39410.2292 | 39410.625 | DAILY | [12 empty] | 0
_X41758B039410.2368055556 | X41758B0 |  | Parent | FALSE | L1 220/22KV TRANS AT WMTS | 39410.2368 | 39412.5944 | CONT | 00003234 | SPICAPX | replace transformer 220KV bushings | SPIPOWER | X417 | X417 - 220KV BUSHING REPLACEMENT 2004/05 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027674139410.2722222222 | 10276741 |  | Parent | FALSE | SRR 66KV FDR CB AT RWTS | 39410.2722 | 39410.4625 | CONT | [12 empty] | 0
_Z53158CA39410.2743055556 | Z53158CA |  | Parent | TRUE | NO.3 220KV BUS AT ROTS | 39410.2743 | 39410.5882 | DAILY | 00329013 | SPICAPX | Bus Outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53158CB39410.2743055556 | Z53158CB | Z53158CA | Child | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39410.2743 | 39410.5882 | DAILY | 00112417 | SPICAPX | Rebate Cap Bank for Bus Outage | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027667039410.2993055556 | 10276670 |  | Parent | FALSE | 66KV CAPACITOR BANK CB AT TGTS | 39410.2993 | 39410.5889 | DAILY | [12 empty] | 0
_Z61858A639411.21875 | Z61858A6 |  | Parent | TRUE | NO.1 22KV BUS AT RWTS | 39411.2188 | 39411.5493 | DAILY | 00007482 | DB_AUG | No1 22kv Bus & EMESR Fdr RWT 14 CB, Fdr RWT 13CB | SPIPOWER | Z618 | Z618 - (RWTS) NEW 22KV FDR RWT13 FOR EASTLINK TNL | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_Z61858A739411.21875 | Z61858A7 | Z61858A6 | Child | FALSE | NO.1 22KV CAPACITOR BANK AT RWTS | 39411.2188 | 39411.5493 | DAILY | 00356999 | DB_AUG | Rebate Capbank during Bus outage for DB AUG | SPIPOWER | Z618 | Z618 - (RWTS) NEW 22KV FDR RWT13 FOR EASTLINK TNL | Capacitors | Eastern | 22 | CONNECTION ASSET | EXCLUDED |  | 0
_1027667139411.2798611111 | 10276671 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK CB AT ROTS | 39411.2799 | 39411.4111 | CONT | [12 empty] | 0
_V4S258F239411.3569444444 | V4S258F2 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39411.3569 | 39411.5132 | CONT | 00012436 | SPIMAINT | silicon injection blue phase | SPIPOWER | V4S2 | V4S2 - (SMTS) SILICONE NO.1 & NO.2 500KV BUSES | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058N639411.7222222222 | X32058N6 |  | Parent | FALSE | ROTS NO.3 LINE/B3 TRANS 220KV CB AT MTS | 39411.7222 | 39500.5493 | CONT | [12 empty] | 0
_X32058P339412.2118055556 | X32058P3 |  | Parent | TRUE | EX - ROTS NO.3 220KV LINE AT MTS | 39412.2118 | 39412.5285 | DAILY | 00351697 | SPICAPX | Rots 3 line No 2 66kv Bus & U2 Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058P439412.2118055556 | X32058P4 | X32058P3 | Child | FALSE | U2 66/22KV TRANS AT MTS | 39412.2118 | 39412.5285 | DAILY | 00363319 | SPICAPX | Rebate trans for Line | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058P539412.2118055556 | X32058P5 | X32058P3 | Child | FALSE | NO.2 66KV BUS AT MTS | 39412.2118 | 39412.5285 | DAILY | 00364552 | SPICAPX | Rebate trans for Line | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027678539412.2868055556 | 10276785 |  | Parent | FALSE | 22KV/415V S/S TRANS AT FTS | 39412.2868 | 39412.4299 | DAILY | 00004393 | DBPROX | 415 Volt Supplies | DISTCO |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X66858B239413.2479166667 | X66858B2 |  | Parent | FALSE | ROTS NO.7 220KV LINE AT YPS | 39413.2479 | 39413.5757 | DAILY | 00016415 | SPIMAINT | Replace insulators rots-yps no 7 220kv Ln | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024019839413.275 | 10240198 |  | Parent | FALSE | B1 220/66KV TRANS AT WMTS | 39413.275 | 39414.6826 | CONT | 00003233 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027547739413.2791666667 | 10275477 |  | Parent | TRUE | NO.1 22KV/415V S/S TRANS AT WOTS | 39413.2792 | 39413.4521 | DAILY | 00004038 | SPIMAINT | No1 S/S Trans replace insulator covers | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1027655639413.2791666667 | 10276556 | 10275477 | Child | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 39413.2792 | 39413.4521 | DAILY | 00004036 | SPIMAINT | Perf calc W/O No1 Trans during S/S Trans works | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027547839413.4659722222 | 10275478 |  | Parent | TRUE | NO.2 22KV/415V S/S TRANS AT WOTS | 39413.466 | 39413.5826 | DAILY | 00004039 | SPIMAINT | No2S/S Trans replace insulator covers | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1027655739413.4659722222 | 10276557 | 10275478 | Child | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 39413.466 | 39413.5826 | DAILY | 00004037 | SPIMAINT | Perf calc W/O No2 Trans during S/S Trans works | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058N339414.1729166667 | X32058N3 |  | Parent | TRUE | EX - NO.2 220KV BUS AT MTS | 39414.1729 | 39414.6972 | CONT | 00004564 | SPICAPX | DeCommission No 2 220kv Bus at MTS | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058N439414.1729166667 | X32058N4 | X32058N3 | Child | FALSE | B3 220/66KV TRANS AT MTS | 39414.1729 | 39414.6972 | CONT | 00363305 | SPICAPX | Trans Rebate for Bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X66858B339414.2493055556 | X66858B3 |  | Parent | FALSE | ROTS NO.8 220KV LINE AT YPS | 39414.2493 | 39414.6146 | REPDAILY | 00016416 | SPIMAINT | Replace insulators rots-yps no 8 220kv Ln | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027660239414.2875 | 10276602 |  | Parent | FALSE | B3 220/66KV TRANS AT TSTS | 39414.2875 | 39414.5007 | DAILY | 00007659 | SPIMAINT | Repair Cooling Fan No3 Transf TSTS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X66858B339415.2493055556 | X66858B3 |  | Parent | FALSE | ROTS NO.8 220KV LINE AT YPS | 39415.2493 | 39415.6132 | REPDAILY | 00016416 | SPIMAINT | Replace insulators rots-yps no 8 220kv Ln | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058P939415.25625 | X32058P9 |  | Parent | FALSE | EX - NO.2 220/66KV TRANS BANK NO.3 BUS 66KV CB AT MTS | 39415.2562 | 39415.4201 | DAILY | [12 empty] | 0
_1027668239415.2631944444 | 10276682 |  | Parent | FALSE | B2 220/66KV TRANS AT WMTS | 39415.2632 | 39416.6271 | CONT | 00003235 | SPIMAINT | clean trans, replace faulty oil pump & o/h div sw | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058P739415.5340277778 | X32058P7 |  | Parent | FALSE | OR 66KV FDR CB AT MTS | 39415.534 | 39419.2819 | CONT | [12 empty] | 0
_X32058P839415.5347222222 | X32058P8 |  | Parent | FALSE | EM 66KV FDR CB AT MTS | 39415.5347 | 39421.2188 | CONT | [12 empty] | 0
_1025647539416.2472222222 | 10256475 |  | Parent | FALSE | S431 RWTS-TTS L 220KV | 39416.2472 | 39416.4486 | DAILY | [12 empty] | 0
_X66858B339416.25 | X66858B3 |  | Parent | FALSE | ROTS NO.8 220KV LINE AT YPS | 39416.25 | 39416.5722 | REPDAILY | 00016416 | SPIMAINT | Replace insulators rots-yps no 8 220kv Ln | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027697839416.6423611111 | 10276978 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS AT JLGB | 39416.6424 | 39421.5542 | CONT | 00009830 | GENCO | SCAP: B1 Gen Trans | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1027697939416.9590277778 | 10276979 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 39416.959 | 39438.6737 | CONT | [12 empty] | 0
_X47758E039417.2159722222 | X47758E0 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39417.216 | 39417.5847 | DAILY | 00012436 | SPICAPX | X477 - (SMTS) INSTL RACK TO RACK BYPASS CONDUCTRS | SPIPOWER | X477 | X477 - (SMTS) INSTALL RACK TO RACK BYPASS CONDUCTORS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358J039417.2402777778 | Z51358J0 |  | Parent | FALSE | NO.1 66KV BUS AT RWTS | 39417.2403 | 39417.3403 | DAILY | 00364660 | SPICAPX | no load soak test on B1 Trans & No1 66 Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z60258A539417.275 | Z60258A5 |  | Parent | FALSE | ROTS-TTS 220KV E | 39417.275 | 39417.4882 | DAILY | 00022762 | SPICAPX | removal of service span from tower 1 to 220kv rack | SPIPOWER | Z602 | Z602 - NOW Z730 (SMTS) ESTABLISH A 220KV SWITCHYARD | Circuits | Western | 500 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1027687639417.3048611111 | 10276876 |  | Parent | FALSE | NO.8 22KV/415V S/S TRANS AT SMTS | 39417.3049 | 39417.4674 | DAILY | 00001327 | DBPROX | VSCAP to Distribution Opns Centre (DOC) | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358H339417.3416666667 | Z51358H3 |  | Parent | TRUE | NO.2 220KV BUS AT RWTS | 39417.3417 | 39417.6986 | DAILY | 00007478 | SPICAPX | Install new Bus BiPods | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358H439417.3416666667 | Z51358H4 | Z51358H3 | Child | FALSE | L2 220/22KV TRANS BANK AT RWTS | 39417.3417 | 39417.6986 | DAILY | 00007447 | SPICAPX | Rebate Tran for bus outage No 2 220/22Kv Trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358H539417.3416666667 | Z51358H5 | Z51358H3 | Child | FALSE | B3 220/66KV TRANS AT RWTS | 39417.3417 | 39417.6986 | DAILY | 00007455 | SPICAPX | Rebate Tran for bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358H639417.3416666667 | Z51358H6 | Z51358H3 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RWTS | 39417.3417 | 39417.6986 | DAILY | 00350529 | SPICAPX | Rebate Cap Bank for bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z51358H739418.2 | Z51358H7 |  | Parent | TRUE | NO.1 220KV BUS AT RWTS | 39418.2 | 39418.6264 | DAILY | 00007477 | SPICAPX | Install New Bus Bipods on No1 220kv Bus | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358H839418.2 | Z51358H8 | Z51358H7 | Child | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39418.2 | 39418.6264 | DAILY | 00007452 | SPICAPX | Rebate L3 Transformer during No1 220kV Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358H939418.2 | Z51358H9 | Z51358H7 | Child | FALSE | B4 220/66KV TRANS AT RWTS | 39418.2 | 39418.6264 | DAILY | 00007451 | SPICAPX | Rebate B4 Transformer during No1 220kV Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z50658B939418.2215277778 | Z50658B9 |  | Parent | FALSE | NO.1 66KV BUS AT HTS | 39418.2215 | 39418.5292 | DAILY | 00004456 | DB_AUG | Remove old CRM No2 fdr cb Bus Side Isol | SPIPOWER | Z506 | Z506 - (HTS) OPTIMISING 66KV CBS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1024909439418.2451388889 | 10249094 |  | Parent | FALSE | NO.2 220KV BUS AT WMTS | 39418.2451 | 39418.6035 | DAILY | 00003254 | SPIMAINT | O/HAUL No2 220kV Bus at WMTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358J139418.625 | Z51358J1 |  | Parent | FALSE | B1 220/66KV TRANS AT RWTS | 39418.625 | 39422.2917 | CONT | 00364702 | DB_AUG | Pre Commissioning access Fut B1 Connection Transf | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_Z51358J239418.6645833333 | Z51358J2 |  | Parent | FALSE | B2 TRANS NO.1 BUS 220KV CB AT RWTS | 39418.6646 | 39431.2278 | CONT | [12 empty] | 0
_V79958A139419.2451388889 | V79958A1 |  | Parent | FALSE | A4 500/220KV TRANS BANK AT KTS | 39419.2451 | 39419.4201 | DAILY | 00026098 | SPIMAINT | Disconnect Unit Trans on A4 Transformer at KTS | SPIPOWER | V799 | V799 - (KTS) REPLACE PCB CONTAMINATED INSULATING OIL | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X32058Q039419.2520833333 | X32058Q0 |  | Parent | FALSE | EX - OR 66KV FDR AT MTS | 39419.2521 | 39419.7111 | DAILY | 00018773 | SPICAPX | Diconnect the OR FDR from Fdr Side Isol | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358I539419.2881944444 | Z51358I5 |  | Parent | FALSE | B2 TRANS NO.1 BUS 220KV CB AT RWTS | 39419.2882 | 39422.2917 | CONT | [12 empty] | 0
_1027704039419.5451388889 | 10277040 |  | Parent | FALSE | MKPS-BOPS-MBTS 220KV NW | 39419.5451 | 39419.6667 | DAILY | 00060197 | FAULT | MBTS: MKPS 220kV Line Tripped Auto | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027701439419.8131944445 | 10277014 |  | Parent | FALSE | NO.2 GEN 220/16.5KV TRANS AT HWPS | 39419.8132 | 39423.8361 | CONT | 00009641 | GENCO | HVS: No 2 Gen Isolation requested by Power Station | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1027690239420.2076388889 | 10276902 |  | Parent | TRUE | GNTS NO.3 220KV LINE NO.1 BUS CB AT DDTS | 39420.2076 | 39420.3972 | DAILY | [12 empty] | 0
_1027692439420.2076388889 | 10276924 | 10276902 | Child | FALSE | GNTS NO.3 220KV LINE AT DDTS | 39420.2076 | 39420.3972 | DAILY | 00012373 | SPIMAINT | Rebate W/O GNTS 3 Line 1 Bus CB CT oil re-sample | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027690339420.2104166667 | 10276903 |  | Parent | FALSE | NO.1 CSC AT ROTS | 39420.2104 | 39420.4139 | DAILY | 00004718 | SPIMAINT | Clean wall bushings | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027701539420.2583333333 | 10277015 |  | Parent | FALSE | AUX TRANS 'A' 220KV CB AT YPS | 39420.2583 | 39423.3986 | CONT | [12 empty] | 0
_V62258B839420.2777777778 | V62258B8 |  | Parent | FALSE | KTS 500KV LINE NO.1 BUS CB AT SMTS | 39420.2778 | 39422.5035 | CONT | [12 empty] | 0
_1027690139421.20625 | 10276901 |  | Parent | FALSE | NO.2 CSC AT ROTS | 39421.2063 | 39421.3833 | DAILY | 00004716 | SPIMAINT | Clean wall bushings | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X32058N739421.21875 | X32058N7 |  | Parent | FALSE | EX - NO.1 220/66KV TRANS BANK AT MTS | 39421.2188 | 39423.5332 | CONT | 00026898 | SPICAPX | De Commission No1 220/66 trans EM & OR Fdr | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058Q139421.2263888889 | X32058Q1 |  | Parent | FALSE | EX - EM 66KV FDR AT MTS | 39421.2264 | 39421.6201 | DAILY | 00018861 | SPICAPX | Disconnect the EM 66kV FDR from Fdr Side Isol | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X41258G139421.2291666667 | X41258G1 |  | Parent | TRUE | B2 220/66KV TRANS AT SHTS | 39421.2292 | 39422.7201 | CONT | 00000841 | SPICAPX | Out W/O B2 Transformer for Prot wiring mods | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X41258G239421.2291666667 | X41258G2 | X41258G1 | Child | FALSE | B2 220/66KV TRANS AT SHTS | 39421.2292 | 39422.7201 | DAILY | 00000841 | SPICAPX | Perf calc for W/O B2 Transformer outage | SPIPOWER | X412 | X412 - (SHTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51058G239421.2861111111 | Z51058G2 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT ATS | 39421.2861 | 39421.4111 | DAILY | [12 empty] | 0
_V79958A339421.3402777778 | V79958A3 |  | Parent | FALSE | A4 500/220KV TRANS BANK AT KTS | 39421.3403 | 39421.4181 | DAILY | 00026098 | SPIMAINT | Reconnect Unit Trans to A4 500kV Transformer KTS | SPIPOWER | V799 | V799 - (KTS) REPLACE PCB CONTAMINATED INSULATING OIL | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028485139421.3645833333 | 10284851 |  | Parent | FALSE | WBE 66KV FDR CB AT ATS | 39421.3646 | 39722.2535 | CONT | [12 empty] | 0
_1028485139421.3645833333 | 10284851 |  | Parent | FALSE | WBE 66KV FDR CB AT ATS | 39421.3646 | 39722.2951 | CONT | [12 empty] | 0
_1027693439421.5229166667 | 10276934 |  | Parent | FALSE | EX - B1 TRANS NO.2 BUS 220KV CB AT GTS | 39421.5229 | 39421.5826 | DAILY | [12 empty] | 0
_1027693339421.5847222222 | 10276933 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT GTS | 39421.5847 | 39421.6222 | DAILY | [12 empty] | 0
_Z51358J339422.2916666667 | Z51358J3 |  | Parent | TRUE | B1 TRANS NO.1 BUS 220KV CB AT RWTS | 39422.2917 | 39422.6854 | DAILY | [12 empty] | 0
_Z51358J439422.2916666667 | Z51358J4 | Z51358J3 | Child | FALSE | B1 220/66KV TRANS AT RWTS | 39422.2917 | 39422.6854 | DAILY | 00364702 | DB_AUG | Pre Commissioning access Fut B1 Connection Transf | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1027650739422.3263888889 | 10276507 |  | Parent | FALSE | NO.3 66KV CAPACITOR BANK AT WMTS | 39422.3264 | 39422.3792 | DAILY | 00003191 | FORCED | Repair Hot Spot found by Thermoview | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027672739422.4034722222 | 10276727 |  | Parent | FALSE | TTS 220KV LINE NO.2 BUS CB AT EPSY | 39422.4035 | 39422.4431 | DAILY | [12 empty] | 0
_1027672839422.4034722222 | 10276728 |  | Parent | FALSE | EPS -TTS 2 220KV N | 39422.4035 | 39422.4431 | DAILY | 00328508 | SPIMAINT | Rebate W/O TTS Line during its No2 Bus CB outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358J639422.6930555556 | Z51358J6 |  | Parent | FALSE | B1 220/66KV TRANS AT RWTS | 39422.6931 | 39424.2493 | CONT | 00364702 | SPICAPX | Pre Commissioning access Fut B1 Connection Transf | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X32058N839423.2173611111 | X32058N8 |  | Parent | TRUE | EX - NO.1 220KV BUS AT MTS | 39423.2174 | 39423.4736 | DAILY | 00004563 | SPICAPX | De Commission No1 220/66 trans 220KV iSOL SW | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058N939423.2173611111 | X32058N9 | X32058N8 | Child | FALSE | EX - NO.1 220/22KV TRANS BANK AT MTS | 39423.2174 | 39423.4736 | DAILY | 00026901 | SPICAPX | Rebate Tran for Bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027699339423.2826388889 | 10276993 |  | Parent | TRUE | BATS NO.1 220KV LINE NO.1 BUS CB AT MLTS | 39423.2826 | 39423.5972 | DAILY | [12 empty] | 0
_1027699439423.2826388889 | 10276994 | 10276993 | Child | FALSE | 220KV SHUNT REACTOR AT MLTS | 39423.2826 | 39423.5972 | DAILY | 00003011 | SPIMAINT | Rebate W/O 220kV Reactor outage for CT proximity | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027713739423.3277777778 | 10277137 |  | Parent | FALSE | HPS 66KV LINE AT WOTS | 39423.3278 | 39423.3674 | DAILY | 00012055 | FAULT | Line Trip Auto Lightning | SPIPOWER |  |  | Circuits | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027714639423.3416666667 | 10277146 |  | Parent | FALSE | DPS 220KV LINE AT MBTS | 39423.3417 | 39423.3854 | DAILY | 00011754 | FAULT | DPS 220kV line tripped from protection | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027715239423.3875 | 10277152 |  | Parent | FALSE | DPS 220KV LINE AT MBTS | 39423.3875 | 39423.7049 | DAILY | 00011754 | STHHYDRO | DPS line de-energised for AGL/SHCC | STHHYDRO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027713839423.4354166667 | 10277138 |  | Parent | FALSE | B2 220/66KV TRANS AT SHTS | 39423.4354 | 39423.4375 | DAILY | 00000841 | FORCED | No2 Trans de-energised to test faulty ROI controls | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358I339424.2041666667 | Z51358I3 |  | Parent | FALSE | B2 220/66KV TRANS AT RWTS | 39424.2042 | 39431.716 | CONT | 00007450 | DB_AUG | B2 Trans Outage Rebate | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027715439424.2229166667 | 10277154 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39424.2229 | 39424.475 | DAILY | 00011755 | SPIMAINT | MKPS 220kV Line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027708539424.25 | 10277085 |  | Parent | FALSE | 66KV CAPACITOR BANK CB AT TGTS | 39424.25 | 39424.6174 | DAILY | [12 empty] | 0
_1026458739424.2513888889 | 10264587 |  | Parent | TRUE | S193 HWPS-ROTS 2 220KV | 39424.2514 | 39424.5917 | REPDAILY | [12 empty] | 0
_1027692339424.2513888889 | 10276923 |  | Parent | FALSE | ROTS NO.2 220KV LINE AT HWPS | 39424.2514 | 39424.5917 | DAILY | 00369011 | SPIMAINT | Rebate for Line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027716139424.2513888889 | 10277161 | 10264587 | Child | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 39424.2514 | 39424.5917 | REPDAILY | 00015793 | SPIMAINT | 220kV Line outage during Yall Open Cut collapse | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027667139424.2694444445 | 10276671 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK CB AT ROTS | 39424.2694 | 39425.9417 | CONT | [12 empty] | 0
_X46158O039424.4375 | X46158O0 |  | Parent | FALSE | MLRC VERY FAST RUNBACK SATELLITE SYSTEM AT BATS | 39424.4375 | 39424.559 | DAILY | [12 empty] | 0
_1026458739425.2479166667 | 10264587 |  | Parent | TRUE | S193 HWPS-ROTS 2 220KV | 39425.2479 | 39425.6312 | REPDAILY | [12 empty] | 0
_1027692339425.2479166667 | 10276923 |  | Parent | FALSE | ROTS NO.2 220KV LINE AT HWPS | 39425.2479 | 39425.6312 | DAILY | 00369011 | SPIMAINT | Rebate for Line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027716139425.2479166667 | 10277161 | 10264587 | Child | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 39425.2479 | 39425.6312 | REPDAILY | 00015793 | SPIMAINT | 220kV Line outage during Yall Open Cut collapse | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027698039425.2513888889 | 10276980 |  | Parent | FALSE | B1 220/66KV TRANS AT ERTS | 39425.2514 | 39425.4174 | DAILY | 00004370 | SPIMAINT | INSTALL COOLING FAN | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51058G439425.2666666667 | Z51058G4 |  | Parent | FALSE | NO.3 220KV BUS AT ATS | 39425.2667 | 39425.3924 | DAILY | 00356843 | SPICAPX | Operational checks on Fut B4 Tr 3B CB & isol / Esw | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027710639426.4201388889 | 10277106 |  | Parent | FALSE | BETS 220KV LINE NO.1 BUS CB AT BATS | 39426.4201 | 39426.4819 | DAILY | [12 empty] | 0
_1027710739426.4201388889 | 10277107 |  | Parent | FALSE | BETS 220KV LINE NO.2 BUS CB AT BATS | 39426.4201 | 39426.4819 | DAILY | [12 empty] | 0
_1025164639427.2506944445 | 10251646 |  | Parent | FALSE | B2 220/66KV TRANS AT WMTS | 39427.2507 | 39428.6167 | CONT | 00003235 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51058G539427.2631944444 | Z51058G5 |  | Parent | FALSE | B4 TRANS NO.3 BUS 220KV CB AT ATS | 39427.2632 | 39437.4333 | CONT | [12 empty] | 0
_X41258H039427.2638888889 | X41258H0 |  | Parent | FALSE | GNTS NO.1 220KV LINE NO.2 BUS CB AT SHTS | 39427.2639 | 39427.6493 | DAILY | [12 empty] | 0
_1027717839427.3111111111 | 10277178 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39427.3111 | 39427.3271 | DAILY | [12 empty] | 0
_1027700839427.3340277778 | 10277008 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39427.334 | 39427.391 | DAILY | 00319998 | APDALCOA | Line de-energised for Ins washing by APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027695739427.3631944445 | 10276957 |  | Parent | FALSE | RCTS 220KV LINE NO.2 BUS CB AT HOTS | 39427.3632 | 39427.4069 | DAILY | [12 empty] | 0
_1027695639427.4236111111 | 10276956 |  | Parent | FALSE | WBTS 220KV LINE NO.1 BUS CB AT HOTS | 39427.4236 | 39427.5604 | DAILY | [12 empty] | 0
_1027701239427.4583333333 | 10277012 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39427.4583 | 39427.4771 | DAILY | 00319999 | APDALCOA | Line de-en for Ins washing by APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027695539427.5625 | 10276955 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT HOTS | 39427.5625 | 39427.6021 | DAILY | [12 empty] | 0
_1027717739427.7340277778 | 10277177 |  | Parent | FALSE | EX - O.O.S 220/66KV TRANS BANK (9 SINGLE PHASE UNITS) AT TTS | 39427.734 | 39427.8167 | REPDAILY | 00026062 | SPICAPX | De-energised for proximity work | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER | Out of Service | 0
_X41258H139428.2631944444 | X41258H1 |  | Parent | FALSE | DDTS 220KV LINE NO.2 BUS CB AT SHTS | 39428.2632 | 39428.6632 | DAILY | [12 empty] | 0
_Z53158CC39428.3076388889 | Z53158CC |  | Parent | FALSE | SVTS NO.1 220KV LINE NO.4 BUS CB AT ROTS | 39428.3076 | 39428.3396 | DAILY | [12 empty] | 0
_1027694939428.3236111111 | 10276949 |  | Parent | FALSE | 2-3 220KV BUS TIE CB AT TTS | 39428.3236 | 39428.4931 | DAILY | [12 empty] | 0
_1027547639428.3375 | 10275476 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT WOTS | 39428.3375 | 39428.3958 | DAILY | 00004040 | SPIMAINT | No3 S/STrans replace insulated bird covers | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_Z53158CD39428.3423611111 | Z53158CD |  | Parent | FALSE | TTS 220KV LINE NO.1 BUS CB AT ROTS | 39428.3424 | 39428.4222 | DAILY | [12 empty] | 0
_1027715739428.3548611111 | 10277157 |  | Parent | FALSE | B2 TRANS 220KV CB AT HOTS | 39428.3549 | 39428.3694 | DAILY | [12 empty] | 0
_1027726039428.3548611111 | 10277260 |  | Parent | FALSE | B1 220/66KV TRANS (HOT SPARE) AT MBTS | 39428.3549 | 39428.4174 | DAILY | 00360627 | FAULT | MBTS: B1 Trans Off loaded | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER | NORMALLY OPEN | 0
_1027706139428.3861111111 | 10277061 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT RCTS | 39428.3861 | 39428.6285 | DAILY | [12 empty] | 0
_Z53158CE39428.4263888889 | Z53158CE |  | Parent | FALSE | TTS 220KV LINE NO.2 BUS CB AT ROTS | 39428.4264 | 39428.4556 | DAILY | [12 empty] | 0
_Z53158CF39428.4986111111 | Z53158CF |  | Parent | FALSE | RTS NO.1 220KV LINE NO.1 BUS CB AT ROTS | 39428.4986 | 39428.5319 | DAILY | [12 empty] | 0
_Z53158CG39428.5340277778 | Z53158CG |  | Parent | FALSE | RTS NO.1 220KV LINE NO.2 BUS CB AT ROTS | 39428.534 | 39428.5521 | DAILY | [12 empty] | 0
_1027715639428.5625 | 10277156 |  | Parent | FALSE | B3 TRANS 220KV CB AT HOTS | 39428.5625 | 39428.5639 | DAILY | [12 empty] | 0
_1027717739428.7569444444 | 10277177 |  | Parent | FALSE | EX - O.O.S 220/66KV TRANS BANK (9 SINGLE PHASE UNITS) AT TTS | 39428.7569 | 39428.7937 | REPDAILY | 00026062 | SPICAPX | De-energised for proximity work | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER | Out of Service | 0
_1025164839429.2534722222 | 10251648 |  | Parent | FALSE | B4 220/66KV TRANS AT WMTS | 39429.2535 | 39430.5889 | CONT | 00350829 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027715839429.2569444444 | 10277158 |  | Parent | FALSE | RCTS 220KV LINE NO.2 BUS CB AT HOTS | 39429.2569 | 39429.3403 | DAILY | [12 empty] | 0
_X41258H239429.2625 | X41258H2 |  | Parent | FALSE | FVTS/BETS 220KV LINE NO.2 BUS CB AT SHTS | 39429.2625 | 39429.6438 | DAILY | [12 empty] | 0
_1027715939429.2722222222 | 10277159 |  | Parent | FALSE | DPS -MBTS 220KV NW | 39429.2722 | 39429.5757 | DAILY | 00060195 | SPIMAINT | DPS-MBTS Line: Replace flashed insulators | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X3D258G339429.28125 | X3D258G3 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT MWTS | 39429.2812 | 39430.5792 | CONT | 00010265 | SPIMAINT | Remove old wiring and Equipment | SPIPOWER | X3D2 | X3D2 - (MWTS) INSTALL SCIMS & 66KV BAY PROT/CONT SCHEMES | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158CH39429.29375 | Z53158CH |  | Parent | FALSE | A2 TRANS NO.1 BUS 220KV CB AT ROTS | 39429.2937 | 39429.3806 | DAILY | [12 empty] | 0
_1027706239429.2951388889 | 10277062 |  | Parent | FALSE | R3 TRANS NO.1 BUS 220KV CB AT RCTS | 39429.2951 | 39429.4771 | DAILY | [12 empty] | 0
_Z53158CI39429.3826388889 | Z53158CI |  | Parent | FALSE | A2 TRANS NO.2 BUS 220KV CB AT ROTS | 39429.3826 | 39429.4451 | DAILY | [12 empty] | 0
_1027726239429.4076388889 | 10277262 |  | Parent | FALSE | C 66/11KV S/S TRANS AT LYPS | 39429.4076 | 39437.6667 | CONT | 00325332 | GENCO | Water leak on GENCO cable at S/S Transf C LYPS | GENCO |  |  | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53158CJ39429.4472222222 | Z53158CJ |  | Parent | FALSE | HWPS NO.2 220KV LINE NO.1 BUS CB AT ROTS | 39429.4472 | 39429.4826 | DAILY | [12 empty] | 0
_Z53158CO39429.5 | Z53158CO |  | Parent | FALSE | ERTS NO.1 LINE/HWPS NO.2 LINE 220KV CB AT ROTS | 39429.5 | 39429.6097 | DAILY | [12 empty] | 0
_1027706339429.5763888889 | 10277063 |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT RCTS | 39429.5764 | 39429.5944 | DAILY | [12 empty] | 0
_Z53158CK39429.6104166667 | Z53158CK |  | Parent | FALSE | ERTS NO.1 220KV LINE NO.2 BUS CB AT ROTS | 39429.6104 | 39429.6354 | DAILY | [12 empty] | 0
_Z53158CL39430.2590277778 | Z53158CL |  | Parent | FALSE | A2 TRANS NO.4 BUS 220KV CB AT ROTS | 39430.259 | 39430.3493 | DAILY | [12 empty] | 0
_1027717339430.2909722222 | 10277173 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT MLTS | 39430.291 | 39430.5097 | DAILY | 00003006 | DBPROX | VSCAP to Powercor | DISTCO |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058Q239430.3041666667 | X32058Q2 |  | Parent | FALSE | EX - NO.1 S/S TRANS AT MTS | 39430.3042 | 39430.3354 | DAILY | 00004558 | SPICAPX | Change tap setting on No1 & 3 S/S trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Other Transformers | Eastern | 6.6 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_Z53158CM39430.3513888889 | Z53158CM |  | Parent | FALSE | YPS NO.5 220KV LINE NO.1 BUS CB AT ROTS | 39430.3514 | 39430.3722 | DAILY | [12 empty] | 0
_Z53158CN39430.3743055556 | Z53158CN |  | Parent | FALSE | HWPS NO.1 220KV LINE NO.1 BUS CB AT ROTS | 39430.3743 | 39430.4542 | DAILY | [12 empty] | 0
_Z53158CP39430.4548611111 | Z53158CP |  | Parent | FALSE | ERTS NO.2 220KV LINE NO.2 BUS CB AT ROTS | 39430.4549 | 39430.4868 | DAILY | [12 empty] | 0
_Z51358J839431.2277777778 | Z51358J8 |  | Parent | TRUE | NO.2 220KV BUS AT RWTS | 39431.2278 | 39431.716 | DAILY | 00007478 | DB_AUG | Install 220kv droppers for B2 Trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358K539431.2277777778 | Z51358K5 | Z51358J8 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RWTS | 39431.2278 | 39431.716 | DAILY | 00350529 | DB_AUG | Cap Bank off during 220kV Bus outage at RWTS | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z51358K639431.2277777778 | Z51358K6 | Z51358J8 | Child | FALSE | B3 220/66KV TRANS AT RWTS | 39431.2278 | 39431.716 | DAILY | 00007455 | DB_AUG | Rebate Tran for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z51358K739431.2277777778 | Z51358K7 | Z51358J8 | Child | FALSE | L2 220/22KV TRANS BANK AT RWTS | 39431.2278 | 39431.716 | DAILY | 00007447 | DB_AUG | Rebate Tran for Bus outage | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009934639431.2416666667 | 10099346 |  | Parent | FALSE | NO.3 220KV BUS AT WMTS | 39431.2417 | 39431.4339 | REPDAILY | 00351770 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53358A239431.2618055556 | Z53358A2 |  | Parent | FALSE | HWPS-ROTS 1 220KV G | 39431.2618 | 39431.6462 | REPDAILY | 00020454 | GEN_AUG | Excavate under Lines for open cut tower diversion | SPIPOWER | Z533 | Z533 - (HWPS-ROTS) LINE 3 HW MINE EXTENSION - ST2 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358K839431.7159722222 | Z51358K8 |  | Parent | FALSE | B2 220/66KV TRANS AT RWTS | 39431.716 | 39466.6549 | CONT | 00007450 | DB_AUG | B2 Transf replaced by new B1 till 16 January | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X72758A039432.2256944444 | X72758A0 |  | Parent | FALSE | B2 220/66KV TRANS AT TTS | 39432.2257 | 39432.7389 | DAILY | 00362454 | SPICAPX | install bushing & conservator into metro sp trans | SPIPOWER | X727 | X727 - (TTS) B2 TRANSFORMER REPLACEMENT | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009934639432.2395833333 | 10099346 |  | Parent | FALSE | NO.3 220KV BUS AT WMTS | 39432.2396 | 39432.5806 | REPDAILY | 00351770 | SPIMAINT | O/HAUL - 330 & 220kv Bus (Generic) | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z53358A239432.2541666667 | Z53358A2 |  | Parent | FALSE | HWPS-ROTS 1 220KV G | 39432.2542 | 39432.6187 | REPDAILY | 00020454 | GEN_AUG | Excavate under Lines for open cut tower diversion | SPIPOWER | Z533 | Z533 - (HWPS-ROTS) LINE 3 HW MINE EXTENSION - ST2 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358I639432.3013888889 | Z51358I6 |  | Parent | FALSE | B1 220/66KV TRANS AT RWTS | 39432.3014 | 39432.6521 | DAILY | 00364702 | DB_AUG | Commissioning of B1 Trans No2 Bus 220kv CB | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1027723839433.3138888889 | 10277238 |  | Parent | FALSE | AUX TRANS 'C' 220KV LINE AT YPS | 39433.3139 | 39434.5257 | CONT | 00016421 | GENCO | SCAP to YWPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X41258H339434.2659722222 | X41258H3 |  | Parent | FALSE | FVTS/BETS 220KV LINE NO.1 BUS CB AT SHTS | 39434.266 | 39434.6229 | DAILY | [12 empty] | 0
_Z51058G839434.2875 | Z51058G8 |  | Parent | FALSE | NO.2 220KV BUS AT ATS | 39434.2875 | 39434.4347 | DAILY | 00055544 | SPICAPX | carry out op checks on b/s sios & esw | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027709939434.3386805556 | 10277099 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT HYTS | 39434.3387 | 39434.3826 | DAILY | 00331066 | DBPROX | VSCAP to Powercor | DISTCO |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1027747139434.4375 | 10277471 |  | Parent | FALSE | B4 TRANS NO.2 BUS 220KV CB AT ATS | 39434.4375 | 39437.3125 | CONT | [12 empty] | 0
_1027725039435.2576388889 | 10277250 |  | Parent | FALSE | B3 220/66KV TRANS AT TSTS | 39435.2576 | 39435.4861 | DAILY | 00007659 | SPIMAINT | repair defective cooling fan | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X41258H539435.2597222222 | X41258H5 |  | Parent | FALSE | GNTS NO.1 220KV LINE NO.1 BUS CB AT SHTS | 39435.2597 | 39435.6014 | DAILY | [12 empty] | 0
_1027721639435.34375 | 10277216 |  | Parent | TRUE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39435.3438 | 39435.3778 | DAILY | [12 empty] | 0
_1027721739435.34375 | 10277217 | 10277216 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39435.3438 | 39435.3778 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during 275kV CB outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024946239436.25 | 10249462 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT TTS | 39436.25 | 39436.5618 | DAILY | [12 empty] | 0
_1026209139436.2527777778 | 10262091 |  | Parent | FALSE | B2 220/66KV TRANS AT TSTS | 39436.2528 | 39436.5958 | DAILY | 00007658 | SPIMAINT | Repair defective cooling Fan | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027721139436.3208333333 | 10277211 |  | Parent | FALSE | VNSC SUPPLY TRANS CB AT RTS | 39436.3208 | 39436.3708 | DAILY | [12 empty] | 0
_Z51058H139437.4333333333 | Z51058H1 |  | Parent | FALSE | B4 220/66KV TRANS AT ATS | 39437.4333 | 39498.4785 | CONT | 00363708 | SPICAPX | installation works - all future equipment | SPIPOWER | Z510 | Z510 - (ATS) 3RD TRANSFORMER | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X72758A239438.2034722222 | X72758A2 |  | Parent | FALSE | EX - O.O.S 220/66KV TRANS BANK (9 SINGLE PHASE UNITS) AT TTS | 39438.2035 | 39440.525 | CONT | 00026062 | SPICAPX | restring o/head tr connections | SPIPOWER | X727 | X727 - (TTS) B2 TRANSFORMER REPLACEMENT | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER | Out of Service | 0
_1027754139443.1493055556 | 10277541 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 39443.1493 | 39450.5965 | CONT | 00356081 | GENCO | HWPS No3 Gen Trans Isols, Eths & SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027747039443.2881944444 | 10277470 |  | Parent | TRUE | S114 SYTS-MLTS 2 500KV | 39443.2882 | 39443.4646 | DAILY | [12 empty] | 0
_1027767339443.2881944444 | 10277673 | 10277470 | Child | FALSE | SYTS-MLTS 2 500KV WY | 39443.2882 | 39443.4646 | DAILY | 00022638 | SPIMAINT | Rebate - Loose spacer - conductor damage C Ph #6 | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027754239443.3769444445 | 10277542 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39443.3769 | 39448.3301 | CONT | 00356082 | GENCO | HWPS No4 Gen Trans Isolated | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027754339443.3909722222 | 10277543 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.4 MAIN TRANS CB AT HWTS | 39443.391 | 39443.5535 | CONT | [12 empty] | 0
_1027756539445.3840277778 | 10277565 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39445.384 | 39447.4472 | CONT | 00017270 | FAULT | KGTS: SVC Trip | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027757439445.8152777778 | 10277574 |  | Parent | FALSE | NO.2 22KV BUS AT BETS | 39445.8153 | 39445.8417 | CONT | 00016376 | FAULT | BETS: TRIP No2 22kV BUS for DISCO Fault | DISTCO |  |  | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1027757839446.0944444445 | 10277578 |  | Parent | FALSE | 2-4 500KV BUS TIE CB AT LYPS | 39446.0944 | 39446.1618 | CONT | [12 empty] | 0
_1027767039447.5263888889 | 10277670 |  | Parent | TRUE | GTS NO.1 220KV LINE AT MLTS | 39447.5264 | 39447.5403 | DAILY | 00022489 | FAULT | Rebate GTS 1 Line off loaded at MLTS by Bus2 Trip | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027767139447.5263888889 | 10277671 | 10277670 | Child | FALSE | BATS NO.2 220KV LINE AT MLTS | 39447.5264 | 39447.5403 | DAILY | 00022969 | FAULT | Rebate BATS 2 Line off loaded at MLTS by Bus2 Trip | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027763439447.5263888889 | 10277634 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT MLTS | 39447.5264 | 39450.3632 | CONT | 00350825 | FAULT | MLTS No2 Cap Bank & CB Fault | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1027763939447.9409722222 | 10277639 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 39447.941 | 39448.275 | CONT | [12 empty] | 0
_1027764039448.275 | 10277640 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 39448.275 | 39448.3076 | DAILY | [12 empty] | 0
_1027767439449.8611111111 | 10277674 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 39449.8611 | 39454.8049 | CONT | [12 empty] | 0
_1027767539449.8868055556 | 10277675 |  | Parent | FALSE | NO.4 GEN TRANS NO.1 BUS 220KV CB AT HWPS | 39449.8868 | 39451.316 | CONT | [12 empty] | 0
_1027766139450.2652777778 | 10277661 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39450.2653 | 39450.5146 | DAILY | 00022691 | 3RDPARTY | Line outage for PTH | HVCUST |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027882039450.3631944445 | 10278820 | 10278819 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT MLTS | 39450.3632 | 39450.6458 | DAILY | 00350825 | SPIMAINT | Rebate W/O No2 220kV Cap bank during CB repair | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1027765539450.3631944445 | 10277655 |  | Parent | TRUE | NO.2 220KV CAPACITOR BANK X & X BACKUP PROT AT MLTS | 39450.3632 | 39455.5938 | CONT | [12 empty] | 0
_1027778239450.3631944445 | 10277782 | 10277655 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT MLTS | 39450.3632 | 39486.5938 | DAILY | 00350825 | SPIMAINT | Rebate W/O No2 220kV Cap bank during CB repair | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_Z64358A239451.275 | Z64358A2 |  | Parent | FALSE | NO.5 66KV BUS AT SVTS | 39451.275 | 39451.6104 | DAILY | 00004863 | SPIMAINT | No 5 & 6 66kV Buses | SPIPOWER | Z643 | Z643 - (SVTS) EB 66KV LINE PROTECTION UPGRADE | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027775439451.5701388889 | 10277754 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39451.5701 | 39453.4403 | CONT | 00017270 | FAULT | KGTS:SVC cap unbalance | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027779439455.2868055556 | 10277794 |  | Parent | FALSE | EX - A4 TRANS NO.3 BUS 220KV CB AT KTS | 39455.2868 | 39455.3819 | DAILY | [12 empty] | 0
_1027752239455.3638888889 | 10277522 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT HYTS | 39455.3639 | 39455.4326 | DAILY | 00331066 | 3RDPARTY | VSCAP to Powercor | DISTCO |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 3
_1027784339456.0194444445 | 10277843 |  | Parent | FALSE | NO.4 GEN TRANS NO.2 BUS 220KV CB AT HWPS | 39456.0194 | 39458.2785 | CONT | [12 empty] | 0
_1027785439456.5055555556 | 10277854 |  | Parent | FALSE | EX - ROTS NO.1 220KV LINE AT MTS | 39456.5056 | 39456.5681 | DAILY | 00351696 | SPICAPX | Line required OOS due to transformer movement | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027779839457.2104166667 | 10277798 |  | Parent | TRUE | EX - NO.1 66KV CAPACITOR BANK CB AT TSTS | 39457.2104 | 39457.3986 | DAILY | [12 empty] | 0
_1027881539457.2104166667 | 10278815 | 10277798 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT TSTS | 39457.2104 | 39457.3986 | DAILY | 00351937 | SPIMAINT | Rebate - REPAIR CB GAS ALARM | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1027784739457.2604166667 | 10277847 |  | Parent | TRUE | WMTS NO.2 220KV LINE CB AT FBTS | 39457.2604 | 39457.2694 | DAILY | [12 empty] | 0
_1027784939457.2604166667 | 10277849 | 10277847 | Child | FALSE | WMTS NO.2 220KV LINE AT FBTS | 39457.2604 | 39457.2694 | DAILY | 00017157 | SPIMAINT | top up sf6 gas | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1027786039457.2618055556 | 10277860 |  | Parent | FALSE | MLTS-HYTS 1 500KV W | 39457.2618 | 39457.2694 | DAILY | 00022630 | SW_NEM | MLTS reactor Switching | VENCORP |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027786139457.2694444445 | 10277861 |  | Parent | FALSE | MLTS-HYTS 2 500KV W | 39457.2694 | 39457.275 | DAILY | 00022633 | SW_NEM | MLTS reactor Switching | VENCORP |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027783139457.2965277778 | 10277831 |  | Parent | FALSE | EX - A4 TRANS NO.3 BUS 220KV CB AT KTS | 39457.2965 | 39457.3299 | DAILY | [12 empty] | 0
_1027789339457.4993055556 | 10277893 |  | Parent | FALSE | A3 500/220KV TRANS R/PH AT KTS | 39457.4993 | 39457.5285 | CONT | 00001142 | FAULT | KTS: A3 Trans Trip | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027790839457.7909722222 | 10277908 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 39457.791 | 39458.6208 | CONT | [12 empty] | 0
_1027785539459.2013888889 | 10277855 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 39459.2014 | 39462.6744 | CONT | 00016423 | GENCO | SCAP to PS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027796239459.5888888889 | 10277962 |  | Parent | FALSE | KTS 220KV LINE AT BLTS | 39459.5889 | 39459.6049 | CONT | 00024011 | FORCED | KTS-BLTS 220kV Line De-Energised | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027796839459.7090277778 | 10277968 |  | Parent | FALSE | DDTS NO.2 330KV LINE SERIES CAPACITOR BANK AT SMTS | 39459.709 | 39459.7771 | DAILY | 00327837 | FAULT | Prot Trip of DDTS-SMTS No 2 330kV Line | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1027796439459.7701388889 | 10277964 |  | Parent | FALSE | NO.8 UNIT TRANS 16.5/6.6KV AT HWPS | 39459.7701 | 39462.9694 | CONT | 00009657 | 3RDPARTY | HVS: HWPS 8 Gen Isol'd for Gen | GENCO |  |  | Other Transformers | Eastern | 22 | NON SP ASSET | NON SP ASSET |  | 3
_1027796939459.8201388889 | 10277969 |  | Parent | FALSE | DDTS NO.2 330KV LINE SERIES CAPACITOR BANK AT SMTS | 39459.8201 | 39461.2708 | CONT | 00327837 | FAULT | Prot Trip DDTS No 2 330kV Line Series Cap at SMTS | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024673039460.2833333333 | 10246730 |  | Parent | FALSE | B NORTH 22KV BUS PROT AT RTS | 39460.2833 | 39460.5347 | DAILY | [12 empty] | 0
_1027751639461.21875 | 10277516 | X62258A6 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 39461.2188 | 39461.3729 | DAILY | 00026097 | SPICAPX | replace 500kv ct's | SPIPOWER | X622 | X622 - 500KV CTS FOR REPLACEMENT/SPARES | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X62258A639461.21875 | X62258A6 |  | Parent | TRUE | A3 TRANS 500KV CB AT KTS | 39461.2188 | 39461.3729 | DAILY | [12 empty] | 0
_1027797639461.2708333333 | 10277976 |  | Parent | FALSE | DDTS NO.2 330KV LINE SERIES CAPACITOR BANK AT SMTS | 39461.2708 | 39461.5965 | DAILY | 00327837 | FAULT | investigate/repair unbalance alarm on white phase | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024838239461.2805555556 | 10248382 |  | Parent | FALSE | LYPS NO.3 500KV LINE NO.4 BUS CB AT HWTS | 39461.2806 | 39461.5292 | DAILY | [12 empty] | 0
_1027801039462.23125 | 10278010 |  | Parent | TRUE | S093 SYTS-MLTS 1 500KV | 39462.2312 | 39462.4 | DAILY | [12 empty] | 0
_1027881639462.23125 | 10278816 | 10278010 | Child | FALSE | SYTS-MLTS 1 500KV WY | 39462.2312 | 39462.4 | DAILY | 00022637 | SPIMAINT | Rebate for repair of Loose spacer | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027782439462.2527777778 | 10277824 |  | Parent | TRUE | MBTS NO.2 220KV LINE CB AT DDTS | 39462.2528 | 39462.4014 | DAILY | [12 empty] | 0
_1027782539462.2527777778 | 10277825 | 10277824 | Child | FALSE | MBTS NO.2 220KV LINE AT DDTS | 39462.2528 | 39462.4014 | DAILY | 00012363 | SPIMAINT | Rebate W/O MBTS No2 Line during CB outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026152439462.2833333333 | 10261524 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT SHTS | 39462.2833 | 39462.4396 | DAILY | [12 empty] | 0
_1027803639462.2833333333 | 10278036 | 10261524 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT SHTS | 39462.2833 | 39462.4396 | DAILY | 00350862 | SPIMAINT | Rebate W/O No2A Cap bk during 2A/B Cap CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027803739462.2833333333 | 10278037 | 10261524 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT SHTS | 39462.2833 | 39462.4396 | DAILY | 00330829 | SPIMAINT | Rebate W/O No2B Cap bk during 2A/B Cap CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027782639462.4145833333 | 10277826 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.1 BUS CB AT DDTS | 39462.4146 | 39462.5215 | DAILY | [12 empty] | 0
_1027811239463.0798611111 | 10278112 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT CBTS | 39463.0799 | 39463.4208 | CONT | 00359493 | FAULT | A1 Transformer Tripped on low oil | SPIPOWER |  |  | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 4
_X32058D039463.1909722222 | X32058D0 |  | Parent | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39463.191 | 39463.4472 | DAILY | 00351697 | SPICAPX | Poximty work | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027782839463.2673611111 | 10277828 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB AT DDTS | 39463.2674 | 39463.375 | DAILY | [12 empty] | 0
_1027782939463.2673611111 | 10277829 | 10277828 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 39463.2674 | 39463.375 | DAILY | 00351939 | SPIMAINT | Rebate W/O No1 220kV Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1024954639463.2701388889 | 10249546 |  | Parent | FALSE | EX - TTS NO.2 LINE/WMTS NO.2 LINE 220KV CB AT KTS | 39463.2701 | 39464.5958 | CONT | [12 empty] | 0
_1025952839463.275 | 10259528 |  | Parent | TRUE | EX - ROTS NO.7 220KV LINE NO.1 BUS CB CT R/PH AT YPS | 39463.275 | 39463.3368 | DAILY | [12 empty] | 0
_1027881739463.275 | 10278817 | 10259528 | Child | FALSE | ROTS NO.7 220KV LINE AT YPS | 39463.275 | 39463.3368 | DAILY | 00016415 | SPIMAINT | Rebate - CT OIL SAMPLING | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025939639463.3819444444 | 10259396 |  | Parent | FALSE | H3 TRANS NO.1 BUS 330KV CB CT R/PH AT DDTS | 39463.3819 | 39463.5014 | DAILY | [12 empty] | 0
_1027815139463.9027777778 | 10278151 |  | Parent | FALSE | HWTS NO.1 220KV LINE CB LINE SIDE ISOL AT HWPS | 39463.9028 | 39466.2125 | CONT | [12 empty] | 0
_1027779939464.3027777778 | 10277799 |  | Parent | TRUE | SVC 220KV CB AT KGTS | 39464.3028 | 39464.3583 | DAILY | [12 empty] | 0
_1027780039464.3027777778 | 10277800 | 10277799 | Child | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39464.3028 | 39464.3583 | DAILY | 00017270 | SPIMAINT | Rebate W/O for SVC during 220kV CB outage | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027780139464.3993055556 | 10277801 |  | Parent | FALSE | BETS LINE NO.1 BUS CB AT KGTS | 39464.3993 | 39464.4389 | DAILY | [12 empty] | 0
_1027780239464.4402777778 | 10277802 |  | Parent | FALSE | BETS LINE NO.2 BUS CB AT KGTS | 39464.4403 | 39464.5424 | DAILY | [12 empty] | 0
_1027823039464.5597222222 | 10278230 |  | Parent | FALSE | EX - B3 TR 220KV (WAS 1-2 220KV BUS TIE) CB AT MTS | 39464.5597 | 39464.6139 | CONT | [12 empty] | 0
_1027795539465.2743055556 | 10277955 |  | Parent | FALSE | TTS -KTS 1S220KV WT | 39465.2743 | 39465.5604 | DAILY | 00022720 | 3RDPARTY | SCAP to Alinta AE | DISTCO |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025953839465.2854166667 | 10259538 |  | Parent | FALSE | EX - W3 GEN TRANS NO.1 BUS 220KV CB CT R/PH AT YPS | 39465.2854 | 39465.3313 | DAILY | [12 empty] | 0
_1025946639465.2958333333 | 10259466 |  | Parent | FALSE | EX - DDTS LINE NO.1 BUS CB CT R/PH AT WOTS | 39465.2958 | 39465.334 | DAILY | [12 empty] | 0
_1024952339465.3055555556 | 10249523 |  | Parent | FALSE | EX - 1-2 66KV BUS TIE CB AT KTS | 39465.3056 | 39465.5687 | DAILY | [12 empty] | 0
_1024584039465.3097222222 | 10245840 |  | Parent | FALSE | EX - B2 TRANS NO.1 BUS TIE CT R/PH AT GNTS | 39465.3097 | 39465.541 | DAILY | [12 empty] | 0
_1027837239466.7173611111 | 10278372 |  | Parent | FALSE | ROTS-TTS 220KV E | 39466.7174 | 39466.7201 | DAILY | 00022762 | FAULT | Out for SEAR operation | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X66258A039467.2611111111 | X66258A0 |  | Parent | FALSE | KTS -GTS 2 220KV WY | 39467.2611 | 39467.6069 | DAILY | 00022705 | SPICAPX | replace defective insulators | SPIPOWER | X658 | X658 - (KTS-GTS2 & YPS-ROTS8) INSULATOR REPLACEMENT | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027805439467.3013888889 | 10278054 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK X & X BACKUP PROT AT RWTS | 39467.3014 | 39467.6444 | REPDAILY | [12 empty] | 0
_1027831939467.90625 | 10278319 |  | Parent | FALSE | NO.4 GEN TRANS NO.1 BUS 220KV CB AT HWPS | 39467.9062 | 39469.4396 | CONT | [12 empty] | 0
_1027832439468.4236111111 | 10278324 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 39468.4236 | 39468.4764 | DAILY | 00060938 | APDALCOA | SF6 Top up at APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027832839468.8263888889 | 10278328 |  | Parent | FALSE | NO.6 GEN TRANS NO.4 BUS 220KV CB AT HWPS | 39468.8264 | 39472.2576 | CONT | [12 empty] | 0
_1027780339469.4916666667 | 10277803 |  | Parent | FALSE | RCTS LINE NO.1 BUS CB AT KGTS | 39469.4917 | 39469.5354 | DAILY | [12 empty] | 0
_1027780839470.2944444444 | 10277808 |  | Parent | TRUE | NO.3 TRANS 220KV CB AT KGTS | 39470.2944 | 39470.3354 | DAILY | [12 empty] | 0
_1027780939470.2944444444 | 10277809 | 10277808 | Child | FALSE | R3 220/66/22KV TRANS AT KGTS | 39470.2944 | 39470.3354 | DAILY | 00017375 | SPIMAINT | Perf calc W/O No3 Trans during 220kV CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027788939470.3125 | 10277889 |  | Parent | TRUE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39470.3125 | 39470.35 | DAILY | [12 empty] | 0
_1027789039470.3125 | 10277890 | 10277889 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39470.3125 | 39470.35 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during 275kV CB outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027781039470.4770833333 | 10277810 |  | Parent | FALSE | NO.2 TRANS NO.1 BUS 220KV CB AT KGTS | 39470.4771 | 39470.4986 | DAILY | [12 empty] | 0
_1027781339470.4993055556 | 10277813 |  | Parent | FALSE | NO.2 TRANS NO.2 BUS 220KV CB AT KGTS | 39470.4993 | 39470.5285 | DAILY | [12 empty] | 0
_1027781139471.2979166667 | 10277811 |  | Parent | TRUE | NO.1 TRANS 220KV CB AT KGTS | 39471.2979 | 39471.3472 | DAILY | [12 empty] | 0
_1027781239471.2979166667 | 10277812 | 10277811 | Child | FALSE | R1 220/66/22KV TRANS AT KGTS | 39471.2979 | 39471.3472 | DAILY | 00357301 | SPIMAINT | Perf calc W/O No1 Trans during 220kV CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058Q639472.2118055556 | X32058Q6 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39472.2118 | 39472.316 | DAILY | 00363305 | SPICAPX | REWIRE CTS | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027834139472.2972222222 | 10278341 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT RWTS | 39472.2972 | 39472.3819 | DAILY | 00007458 | SPIMAINT | REPAIR HOT JOINT | SPIPOWER |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_1027850239472.8194444444 | 10278502 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39472.8194 | 39475.3313 | CONT | 00356082 | GENCO | Genco isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X66858B639473.2604166667 | X66858B6 |  | Parent | FALSE | KTS -GTS 2 220KV WY | 39473.2604 | 39473.5625 | REPDAILY | 00022705 | SPICAPX | Replace faulty insulators | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z53158K839473.2916666667 | Z53158K8 |  | Parent | FALSE | A2 515/220KV TRANS BANK AT ROTS | 39473.2917 | 39473.4181 | DAILY | 00362994 | SPICAPX | A2 TRANS TAP CHARGER | SPIPOWER | Z531 | Z531 - (ROTS) INTERFACE SPEC FOR 500/220KV TRANS | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1027850739473.5756944444 | 10278507 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39473.5757 | 39476.2826 | CONT | 00017270 | FAULT | Isolated pending repairs | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X66858B639474.2604166667 | X66858B6 |  | Parent | FALSE | KTS -GTS 2 220KV WY | 39474.2604 | 39474.6174 | REPDAILY | 00022705 | SPICAPX | Replace faulty insulators | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X72758A639474.2631944444 | X72758A6 |  | Parent | FALSE | B2 220/66KV TRANS AT TTS | 39474.2632 | 39474.3313 | DAILY | 00362454 | SPICAPX | replace faulty oil pump | SPIPOWER | X727 | X727 - (TTS) B2 TRANSFORMER REPLACEMENT | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027805439474.30625 | 10278054 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK X & X BACKUP PROT AT RWTS | 39474.3063 | 39474.7312 | REPDAILY | [12 empty] | 0
_1027850439476.2826388889 | 10278504 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39476.2826 | 39507.3903 | CONT | 00017270 | FAULT | Investigate KGTS SVC trip | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z51358L839476.3041666667 | Z51358L8 |  | Parent | FALSE | B4 220/66KV TRANS AT RWTS | 39476.3042 | 39483.2528 | CONT | 00007451 | DB_AUG | COMMISSION NEW OLTC | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027763039476.3083333333 | 10277630 |  | Parent | FALSE | ATS 66KV LINE CB AT BLTS | 39476.3083 | 39476.6191 | DAILY | [12 empty] | 0
_1027855039476.6902777778 | 10278550 |  | Parent | FALSE | EX - KTS NO.3 220KV LINE AT GTS | 39476.6903 | 39477.7049 | CONT | 00017902 | FORCED | Replace faulty Line CVT at GTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027854939476.8576388889 | 10278549 |  | Parent | FALSE | NO.4 GEN TRANS NO.1 BUS 220KV CB AT HWPS | 39476.8576 | 39479.6917 | CONT | [12 empty] | 0
_1027848839477.2534722222 | 10278488 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 39477.2535 | 39477.6674 | DAILY | 00352791 | SPIMAINT | INVESTIGATE TRANS FAULT SVTS B4 | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027801939477.26875 | 10278019 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 39477.2688 | 39477.5687 | DAILY | 00022690 | APDALCOA | Alcoa request for outage | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027813539477.2701388889 | 10278135 |  | Parent | FALSE | AUTO RECLOSE CONTROL EQUIPMENT AT ROTS | 39477.2701 | 39477.4431 | DAILY | [12 empty] | 0
_X72758A739477.9548611111 | X72758A7 |  | Parent | FALSE | B2 220/66KV TRANS AT TTS | 39477.9549 | 39478.1708 | CONT | 00362454 | SPICAPX | replace faulty oil pump | SPIPOWER | X727 | X727 - (TTS) B2 TRANSFORMER REPLACEMENT | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027851739478.2861111111 | 10278517 |  | Parent | FALSE | ROTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 39478.2861 | 39478.3972 | DAILY | [12 empty] | 0
_1027862039478.4027777778 | 10278620 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.2 BUS CB AT SMTS | 39478.4028 | 39478.4951 | CONT | [12 empty] | 0
_1027864139478.4465277778 | 10278641 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 39478.4465 | 39482.2292 | CONT | 00001328 | FAULT | Repairs on SYTS No1 line No1 Bus CB B/S ROI | SPIPOWER |  |  | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_Z64358A339479.2833333333 | Z64358A3 |  | Parent | FALSE | NO.5 66KV BUS AT SVTS | 39479.2833 | 39479.6701 | DAILY | 00004863 | SPIMAINT | No 5 & 6 66kV Buses | SPIPOWER | Z643 | Z643 - (SVTS) EB 66KV LINE PROTECTION UPGRADE | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027851839479.2868055556 | 10278518 |  | Parent | FALSE | JLTS NO.4 220KV LINE NO.3 BUS CB AT HWPS | 39479.2868 | 39479.3306 | DAILY | [12 empty] | 0
_1024942839480.2645833333 | 10249428 |  | Parent | FALSE | PHASE ANGLE REGULATOR AT BLTS | 39480.2646 | 39480.5701 | DAILY | 00002624 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X66858B739480.3243055556 | X66858B7 |  | Parent | FALSE | KTS -GTS 2 220KV WY | 39480.3243 | 39480.6535 | REPDAILY | 00022705 | SPICAPX | Replace faulty insulators | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027873539480.7319444444 | 10278735 |  | Parent | FALSE | A4 500/220KV TRANS BANK AT KTS | 39480.7319 | 39481.7049 | CONT | 00026098 | FAULT | A4 Trans W phase 500kV Bushing flashed over | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_V77558A039481.2673611111 | V77558A0 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK X & Y PROT & CONTROLS AT DDTS | 39481.2674 | 39481.7347 | DAILY | [12 empty] | 0
_V77558A139481.2673611111 | V77558A1 | V77558A0 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 39481.2674 | 39481.7347 | DAILY | 00351939 | SPIMAINT | Rebate W/O No1 220 Cap bank during setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X66858B739481.26875 | X66858B7 |  | Parent | FALSE | KTS -GTS 2 220KV WY | 39481.2688 | 39481.6076 | REPDAILY | 00022705 | SPICAPX | Replace faulty insulators | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027872339482.2291666667 | 10278723 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 39482.2292 | 39494.7053 | CONT | 00001328 | FAULT | remove contaminated gas from b/s roi compartments | SPIPOWER |  |  | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1024850039483.2527777778 | 10248500 |  | Parent | TRUE | B4 220/66KV TRANS AT RWTS | 39483.2528 | 39486.6521 | CONT | 00007451 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024851239483.2527777778 | 10248512 | 10248500 | Child | FALSE | B4 TRANS 66KV CB AT RWTS | 39483.2528 | 39486.6521 | CONT | [12 empty] | 0
_1024853839483.2527777778 | 10248538 | 10248500 | Child | FALSE | B4 TRANS 220KV CB AT RWTS | 39483.2528 | 39486.6521 | CONT | [12 empty] | 0
_1027878039483.2631944444 | 10278780 |  | Parent | FALSE | NO.6 GEN TRANS NO.3 BUS 220KV CB AT HWPS | 39483.2632 | 39493.3347 | CONT | [12 empty] | 0
_1027809739483.2694444445 | 10278097 |  | Parent | FALSE | EX - B1 TRANS NO.2 BUS 220KV CB AT GTS | 39483.2694 | 39483.6104 | DAILY | [12 empty] | 0
_1027853539483.2854166667 | 10278535 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 39483.2854 | 39483.5243 | DAILY | [12 empty] | 0
_X49658L139483.4534722222 | X49658L1 |  | Parent | FALSE | NO.2 220KV BUS E/SW AT HOTS | 39483.4535 | 39483.4903 | DAILY | [12 empty] | 0
_X55658A939484.2375 | X55658A9 |  | Parent | FALSE | RWN NO.2 66KV FDR CB AT RWTS | 39484.2375 | 39484.9368 | DAILY | [12 empty] | 0
_1027786239484.2701388889 | 10277862 |  | Parent | FALSE | LYPS NO.2 LINE/ROTS NO.3 LINE 500KV CB AT HWTS | 39484.2701 | 39484.5153 | DAILY | [12 empty] | 0
_1027795139484.30625 | 10277951 |  | Parent | FALSE | B2 TRANS 66KV CB AT TBTS | 39484.3063 | 39484.4382 | DAILY | [12 empty] | 0
_1027795039484.4449537037 | 10277950 |  | Parent | FALSE | B1 TRANS 66KV CB AT TBTS | 39484.445 | 39484.566 | DAILY | [12 empty] | 0
_X55658B039484.9166666667 | X55658B0 |  | Parent | FALSE | LDL NO.1 66KV FDR CB AT RWTS | 39484.9167 | 39582.5667 | CONT | [12 empty] | 0
_X49658K739485.2388888889 | X49658K7 |  | Parent | FALSE | RCTS 220KV LINE AT HOTS | 39485.2389 | 39485.3569 | DAILY | 00018715 | SPICAPX | Test new Aux Switch on RCTS Line E/Switch | SPIPOWER | X496 | X496 - (HOTS) STATION REDEVELOPMENT - STAGE ONE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49758K139485.2638888889 | X49758K1 |  | Parent | TRUE | EX - NO.3 66KV CAPACITOR BANK CB AT BETS | 39485.2639 | 39485.3854 | DAILY | [12 empty] | 0
_X49758K239485.2638888889 | X49758K2 | X49758K1 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT BETS | 39485.2639 | 39485.3854 | DAILY | 00350820 | SPICAPX | Rebate W/O 3A Cap bank during 3A/B CB outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X49758K339485.2638888889 | X49758K3 | X49758K1 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 39485.2639 | 39485.3854 | DAILY | 00016304 | SPICAPX | Rebate W/O 3B Cap bank during 3A/B CB outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027861439487.2625 | 10278614 |  | Parent | FALSE | NO.1 11/220KV TRANS BANK AT MPS | 39487.2625 | 39487.384 | DAILY | 00001082 | SPIMAINT | ADJUST TRANS 220KV BUSHING OIL LEVELS. | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027874839487.2652777778 | 10278748 |  | Parent | FALSE | EX - KTS NO.3 220KV LINE AT GTS | 39487.2653 | 39487.6285 | DAILY | 00017902 | SPIMAINT | Out W/O KTS No3 Line to replace VT | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025164439487.5027777778 | 10251644 |  | Parent | TRUE | NO.1 CSC 220/10.5KV TRANS AT ROTS | 39487.5028 | 39487.7229 | CONT | 00004758 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1028643939487.5027777778 | 10286439 | 10251644 | Child | FALSE | NO.1 CSC AT ROTS | 39487.5028 | 39487.7229 | CONT | 00004718 | SPIMAINT | rebate for SVC tran outage | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X66858B839488.2673611111 | X66858B8 |  | Parent | FALSE | KTS NO.2 220KV LINE AT TTS | 39488.2674 | 39488.6882 | DAILY | 00015727 | SPICAPX | Replace faulty insulators | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024547639489.2555555556 | 10245476 |  | Parent | FALSE | MLTS NO.1 LINE/SMTS NO.1 LINE 500KV CB AT SYTS | 39489.2556 | 39490.5806 | CONT | [12 empty] | 0
_1027805239489.2763888889 | 10278052 | 10247518 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 39489.2764 | 39489.4375 | DAILY | 00016304 | SPIMAINT | Rebate Work Order for 3B Cap Bk Outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027861739489.2833333333 | 10278617 |  | Parent | FALSE | EX - NO.3 MAIN TRANS NO.1 BUS 500KV CB AT HWTS | 39489.2833 | 39489.4215 | DAILY | [12 empty] | 0
_1027805039489.5097222222 | 10278050 |  | Parent | TRUE | 2A/2B TRANS 66KV CB AT BETS | 39489.5097 | 39489.5792 | DAILY | [12 empty] | 0
_1027805539489.5097222222 | 10278055 | 10278050 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39489.5097 | 39489.5792 | DAILY | 00016040 | SPIMAINT | Perf Calc, 2A/2B Trans for 66kv CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027899339489.8645833333 | 10278993 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 39489.8646 | 39490.0687 | CONT | 00356086 | GENCO | HWPS No8 Gen Trans Isolations for Powerstation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027843239490.2534722222 | 10278432 |  | Parent | FALSE | B2 220/66KV TRANS AT RTS | 39490.2535 | 39490.5694 | DAILY | 00007331 | SPIMAINT | REPAIR OIL LEAKS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027885439490.2736111111 | 10278854 |  | Parent | FALSE | KGTS-RCTS 220KV NB | 39490.2736 | 39490.6243 | REPDAILY | 00026223 | SPIMAINT | OUT W/O KGTS-RCTS L de-energ to clear easement veg | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027861839490.2777777778 | 10278618 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 39490.2778 | 39490.4118 | DAILY | [12 empty] | 0
_1027835939490.3618055556 | 10278359 |  | Parent | FALSE | AUTO RECLOSE CONTROL EQUIPMENT AT ROTS | 39490.3618 | 39490.4028 | DAILY | [12 empty] | 0
_1027902539491.0034722222 | 10279025 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39491.0035 | 39497.2036 | CONT | 00356082 | GENCO | HWPS No4 Gen Trans Isolations for Powerstation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024914939491.2555555556 | 10249149 |  | Parent | FALSE | NO.2 220KV BUS E/SW AT WMTS | 39491.2556 | 39491.616 | DAILY | [12 empty] | 0
_1027843339491.2569444444 | 10278433 |  | Parent | FALSE | B3 220/66KV TRANS AT RTS | 39491.2569 | 39492.4708 | DAILY | 00329288 | SPIMAINT | REPAIR OIL LEAKS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027861939491.2972222222 | 10278619 |  | Parent | FALSE | EX - NO.4 MAIN TRANS NO.1 BUS 500KV CB AT HWTS | 39491.2972 | 39491.391 | DAILY | [12 empty] | 0
_1027795239491.3020833333 | 10277952 |  | Parent | TRUE | NO.1 66KV BUS VT R/PH AT TBTS | 39491.3021 | 39491.4437 | DAILY | [12 empty] | 0
_1027811339491.3020833333 | 10278113 | 10277952 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT TBTS | 39491.3021 | 39491.4437 | DAILY | 00351938 | SPIMAINT | CAP BANK REBATE FOR BUS OUTAGE | SPIPOWER |  | bvt1 | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1027795339491.4583333333 | 10277953 |  | Parent | FALSE | NO.2 66KV BUS VT R/PH AT TBTS | 39491.4583 | 39491.5451 | DAILY | [12 empty] | 0
_1027910639491.8166666667 | 10279106 |  | Parent | FALSE | NO.7 GEN 220/16.5KV TRANS AT HWPS | 39491.8167 | 39492 | CONT | 00009648 | GENCO | Power Station Requirements | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1027832339492.3027777778 | 10278323 |  | Parent | FALSE | BATS 220KV LINE NO.1 BUS CB AT BETS | 39492.3028 | 39492.4632 | DAILY | [12 empty] | 0
_1027911339492.375 | 10279113 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39492.375 | 39493.4958 | DAILY | 00329879 | FORCED | Replace broken connection on No4 Cap bank | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027910139492.3763888889 | 10279101 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS AT JLGA | 39492.3764 | 39492.4681 | CONT | 00009820 | GENCO | Power station requirement | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1027832239492.4944444445 | 10278322 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT BETS | 39492.4944 | 39492.5549 | DAILY | [12 empty] | 0
_1024950139493.2826388889 | 10249501 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT SYTS | 39493.2826 | 39493.4465 | DAILY | 00001387 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1025943039493.2840277778 | 10259430 |  | Parent | FALSE | EX - A1 TRANS NO.1 BUS 220KV CB CT R/PH AT MLTS | 39493.284 | 39493.3443 | DAILY | [12 empty] | 0
_1024950339493.4826388889 | 10249503 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT SYTS | 39493.4826 | 39493.5958 | DAILY | 00001388 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1027920339493.7423611111 | 10279203 |  | Parent | FALSE | NO.6 GEN TRANS NO.3 BUS 220KV CB AT HWPS | 39493.7424 | 39494.4757 | CONT | [12 empty] | 0
_1027920439493.84375 | 10279204 |  | Parent | FALSE | JLGA NO.4 UNIT TRANS DISC CB AT JLGA | 39493.8438 | 39503.5903 | CONT | [12 empty] | 0
_1027938139494.225 | 10279381 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 39494.225 | 39494.2424 | DAILY | 00022630 | FAULT | Rebate outage for SIR | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027938539494.225 | 10279385 | 10279381 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39494.225 | 39494.2424 | DAILY | 00002863 | FAULT | M1 Transf Stranded by Line Fault | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027938639494.225 | 10279386 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39494.225 | 39494.2556 | DAILY | 00319998 | FAULT | Rebate outage for SIR | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027866339494.2548611111 | 10278663 |  | Parent | TRUE | 66KV CAPACITOR BANK CB AT TGTS | 39494.2549 | 39495.7847 | CONT | [12 empty] | 0
_1027924839494.2548611111 | 10279248 | 10278663 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT WMTS | 39494.2549 | 39495.7847 | CONT | 00074391 | SPIMAINT | Rebate - replace faulty cb | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758K439494.2680555556 | X49758K4 |  | Parent | TRUE | NO.2 22KV BUS AT BETS | 39494.2681 | 39494.9896 | DAILY | 00016376 | SPICAPX | Out W/O No2 22kV BUS - Cutover new bus prot | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758K539494.2680555556 | X49758K5 | X49758K4 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39494.2681 | 39494.9896 | DAILY | 00016040 | SPICAPX | Perf calc W/O No2 Tr grp during No2 22 BUS outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V79058A039494.2868055556 | V79058A0 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39494.2868 | 39494.6132 | DAILY | 00012436 | SPICAPX | invoke SMTS 500kv bypass in bay a | SPIPOWER | V790 | V790 - URGENT MAINTENANCE WORKS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027742839495.2798611111 | 10277428 |  | Parent | TRUE | NO.4 66KV BUS AT RTS | 39495.2799 | 39495.4403 | DAILY | 00022330 | SPIMAINT | Accuracy Test on No4 66Kv Bus CVT | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027743039495.2798611111 | 10277430 | 10277428 | Child | FALSE | B2 220/66KV TRANS AT RTS | 39495.2799 | 39495.4403 | DAILY | 00007331 | SPIMAINT | Trans rebate for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027743139495.2798611111 | 10277431 | 10277428 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT RTS | 39495.2799 | 39495.4403 | DAILY | 00055373 | SPIMAINT | Cap Bank rebate for Bus outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V77558A339495.3 | V77558A3 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39495.3 | 39495.7861 | DAILY | 00354024 | SPIMAINT | No1 220 Cap bank during setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1027741439495.5173611111 | 10277414 |  | Parent | TRUE | NO.3 66KV BUS AT RTS | 39495.5174 | 39495.6188 | DAILY | 00022329 | SPIMAINT | Test No3 66KV Bus CVT | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027742639495.5173611111 | 10277426 | 10277414 | Child | FALSE | B3 220/66KV TRANS AT RTS | 39495.5174 | 39495.6188 | DAILY | 00329288 | SPIMAINT | Tran rebate for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058Q439496.2048611111 | X32058Q4 |  | Parent | TRUE | B1 220/66KV TRANS AT MTS | 39496.2049 | 39496.7688 | DAILY | 00364562 | SPICAPX | B1 & ROTS No 3 Line | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058Q739496.2048611111 | X32058Q7 | X32058Q4 | Child | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39496.2049 | 39496.7688 | DAILY | 00351697 | SPICAPX | Rebate for Line outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058Q939496.7729166667 | X32058Q9 |  | Parent | FALSE | ROTS NO.1 LINE/B1 TRANS 220KV CB AT MTS | 39496.7729 | 39500.5493 | CONT | [12 empty] | 0
_1027896639497.2090277778 | 10278966 |  | Parent | FALSE | SYN/COND AT FBTS | 39497.209 | 39497.4153 | DAILY | 00002697 | SPIMAINT | investigate overheating problem | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027861339497.2527777778 | 10278613 |  | Parent | TRUE | YPS NO.1 220KV LINE NO.6 BUS CB AT HWPS | 39497.2528 | 39497.3403 | DAILY | [12 empty] | 0
_1027886439497.2527777778 | 10278864 | 10278613 | Child | FALSE | YPS NO.1 220KV LINE AT HWPS | 39497.2528 | 39497.3403 | DAILY | 00015795 | SPIMAINT | Rebate Line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027923239497.4326388889 | 10279232 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39497.4326 | 39497.4486 | DAILY | [12 empty] | 0
_X32058R139498.2013888889 | X32058R1 |  | Parent | FALSE | U1 66/22KV TRANS AT MTS | 39498.2014 | 39498.5931 | REPDAILY | 00363343 | SPICAPX | Install sound dampners & No3 S/S Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058R139499.1951388889 | X32058R1 |  | Parent | FALSE | U1 66/22KV TRANS AT MTS | 39499.1951 | 39499.6479 | REPDAILY | 00363343 | SPICAPX | Install sound dampners & No3 S/S Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027923939499.2083333333 | 10279239 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT RTS | 39499.2083 | 39499.3639 | DAILY | 00007279 | SPIMAINT | RE-BALANCE CAP BANK | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027898939499.2625 | 10278989 |  | Parent | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 39499.2625 | 39499.3736 | DAILY | 00015793 | SPIMAINT | HWPS-ROTS 2 Line X&Y Prot preps | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027937439500.0513888889 | 10279374 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39500.0514 | 39500.4986 | CONT | [12 empty] | 0
_X32058R139500.1916666667 | X32058R1 |  | Parent | FALSE | U1 66/22KV TRANS AT MTS | 39500.1917 | 39500.55 | REPDAILY | 00363343 | SPICAPX | Install sound dampners & No3 S/S Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027660439500.2083333333 | 10276604 |  | Parent | FALSE | ROTS NO.4 500KV LINE AT CBTS | 39500.2083 | 39500.4083 | DAILY | 00359492 | SPIMAINT | Repaire CVT | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058R439500.5923611111 | X32058R4 |  | Parent | FALSE | ROTS NO.1 LINE/B1 TRANS 220KV CB AT MTS | 39500.5924 | 39508.2576 | CONT | [12 empty] | 0
_X70858A039501.2340277778 | X70858A0 |  | Parent | FALSE | EX - B3 220/66KV TRANS AT TTS | 39501.234 | 39501.641 | CONT | 00001544 | SPICAPX | replace surge arrestors | SPIPOWER | X708 | X708 - REPLACEMENT OF AGEING 22KV TO 500KV SURGE ARRESTERS | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027925239501.28125 | 10279252 |  | Parent | FALSE | TTS -KTS 1S220KV WT | 39501.2812 | 39501.6424 | REPDAILY | 00022720 | SPIMAINT | Replace insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V79058A139501.3020833333 | V79058A1 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT SMTS | 39501.3021 | 39515.3063 | DAILY | 00001328 | SPICAPX | fault repairs to syts 1l 1b cb b/s roi | SPIPOWER | V790 | [7 empty] | 0 | V79058A1 |  | fault repairs to syts 1l 1b cb b/s roi | 00001328 | BUS | V790 | SMTS | BUS | SPICAPX | IN-SERV
_X49058J139501.3111111111 | X49058J1 |  | Parent | FALSE | DDTS NO.1 330KV LINE AT SMTS | 39501.3111 | 39501.6361 | DAILY | 00012749 | SPICAPX | decommission & recommission of auto reclose scheme | SPIPOWER | X490 | [7 empty] | 0 | X49058J1 |  | decommission & recommission of auto reclose scheme | 00012749 | CIRCUIT | X490 | SMTS | CIRCEND | SPICAPX | IN-SERV
_1027936139501.3444444445 | 10279361 |  | Parent | TRUE | HWTS-SMTS 1 500KV WT | 39501.3444 | 39501.4764 | DAILY | 00119314 | SPIMAINT | Line de-en for tests at SMTS | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027936239501.3444444445 | 10279362 | 10279361 | Child | FALSE | SMTS-SYTS 1 500KV WT | 39501.3444 | 39501.4764 | DAILY | 00022640 | SPIMAINT | Rebate child | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027941239501.9604166667 | 10279412 |  | Parent | FALSE | NO.4 GEN 220/16.5KV TRANS AT HWPS | 39501.9604 | 39507.2792 | CONT | 00009645 | GENCO | Power Station Requirements | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1023953039502.2708333333 | 10239530 |  | Parent | TRUE | NO.2 22KV BUS AT RWTS | 39502.2708 | 39502.4042 | DAILY | 00007483 | SPIMAINT | Hot Joiont on RWT28 Bus side Isol | SPIPOWER |  |  | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1027883139502.2708333333 | 10278831 | 10239530 | Child | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39502.2708 | 39502.4042 | DAILY | 00007452 | SPIMAINT | rebate Tran for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027925239502.2722222222 | 10279252 |  | Parent | FALSE | TTS -KTS 1S220KV WT | 39502.2722 | 39502.6229 | REPDAILY | 00022720 | SPIMAINT | Replace insulators | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V77558A439502.2993055556 | V77558A4 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39502.2993 | 39502.725 | DAILY | 00354024 | SPIMAINT | No1 220 Cap bank during setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1025135239503.2513888889 | 10251352 |  | Parent | FALSE | B4 TRANS 220KV CB AT WMTS | 39503.2514 | 39504.5806 | CONT | [12 empty] | 0
_1027900139503.26875 | 10279001 |  | Parent | FALSE | AUX D 220/22KV TRANS AT YPS | 39503.2688 | 39507.4333 | CONT | 00356098 | SPIMAINT | PILOTWIRE PROTECTION (EH) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Owned by SPAusNet | 0
_V71158A139503.2784722222 | V71158A1 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39503.2785 | 39527.4132 | CONT | [12 empty] | 0
_X55658C139504.2361111111 | X55658C1 |  | Parent | FALSE | EX - LDL NO.1 66KV FDR CB AT RWTS | 39504.2361 | 39504.7715 | DAILY | [12 empty] | 0
_X55658B139504.2361111111 | X55658B1 |  | Parent | FALSE | NW 66KV FDR CB AT RWTS | 39504.2361 | 39504.8542 | DAILY | [12 empty] | 0
_1027921939504.2715277778 | 10279219 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT HOTS | 39504.2715 | 39504.3785 | DAILY | [12 empty] | 0
_1027922039504.2715277778 | 10279220 | 10279219 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT HOTS | 39504.2715 | 39504.3785 | DAILY | 00359898 | SPIMAINT | Rebate W/O 1A Cap Bank during 1A/B CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027922139504.2715277778 | 10279221 | 10279219 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HOTS | 39504.2715 | 39504.3785 | DAILY | 00359901 | SPIMAINT | Rebate W/O 1B Cap Bank during 1A/B CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027943439504.275 | 10279434 |  | Parent | TRUE | APD NO.2/MLTS NO.2 LINE 500KV CB AT HYTS | 39504.275 | 39504.391 | DAILY | [12 empty] | 0
_1027943539504.275 | 10279435 | 10279434 | Child | FALSE | HYTS-APD 2 500KV W | 39504.275 | 39504.391 | DAILY | 00319999 | SPIMAINT | Rebate W/O APD No2 Line during CB outage | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028164839504.2888888889 | 10281648 |  | Parent | FALSE | KGTS-RCTS 220KV NB | 39504.2889 | 39504.2937 | DAILY | 00026223 | FAULT | rebate fir SIR | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027943039504.7631944444 | 10279430 |  | Parent | FALSE | 1-2 EXT 66KV BUS TIE CB AT RWTS | 39504.7632 | 39518.2542 | CONT | [12 empty] | 0
_1027891039505.2694444445 | 10278910 |  | Parent | FALSE | EX - KTS NO.3 220KV LINE NO.2 BUS CB AT GTS | 39505.2694 | 39505.6431 | DAILY | [12 empty] | 0
_1027924139505.3756944445 | 10279241 |  | Parent | FALSE | R3 220/66/22KV TRANS AT KGTS | 39505.3757 | 39505.625 | DAILY | 00017375 | SPIMAINT | KGTS OOS 415V MCB'S TRIPPED N0 3 OFF TAP | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X55658C539506.2451388889 | X55658C5 |  | Parent | FALSE | 1-2 66KV TIE BUS AT RWTS | 39506.2451 | 39514.609 | CONT | 00364661 | SPICAPX | 1-2 EXT 66kv BUS TIE | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027909239507.2986111111 | 10279092 |  | Parent | FALSE | RWTS 220KV LINE NO.2 BUS CB AT TTS | 39507.2986 | 39507.5729 | DAILY | [12 empty] | 0
_1027954839507.325 | 10279548 |  | Parent | FALSE | NO.4 GEN TRANS NO.1 BUS 220KV CB AT HWPS | 39507.325 | 39511.2514 | CONT | [12 empty] | 0
_1027850439507.3909722222 | 10278504 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39507.391 | 39549.6556 | CONT | 00017270 | FAULT | Investigate KGTS SVC trip | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027968239507.7881944444 | 10279682 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39507.7882 | 39508.2979 | CONT | [12 empty] | 0
_1027967639507.8118055556 | 10279676 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39507.8118 | 39508.2562 | DAILY | [12 empty] | 0
_1027967739507.8425810185 | 10279677 |  | Parent | FALSE | EX - NO.1 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 39507.8426 | 39513.4181 | CONT | [12 empty] | 0
_1027852739508.2270833333 | 10278527 | X49758K6 | Child | FALSE | R4 220/66/22KV TRANS AT BETS | 39508.2271 | 39508.7979 | DAILY | 00016220 | SPICAPX | Perf calc W/O No4 Trans during No2 22 BUS outage | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X49758K639508.2270833333 | X49758K6 |  | Parent | TRUE | NO.4 22KV BUS AT BETS | 39508.2271 | 39508.7979 | DAILY | 00016373 | SPICAPX | Out W/O No4 22kV BUS - Cutover new bus prot | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058R539508.2291666667 | X32058R5 |  | Parent | TRUE | B1 220/66KV TRANS AT MTS | 39508.2292 | 39508.4632 | DAILY | 00364562 | SPICAPX | B1 & ROTS No 3 Line | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058R639508.2291666667 | X32058R6 | X32058R5 | Child | FALSE | EX - ROTS NO.3 220KV LINE AT MTS | 39508.2292 | 39508.4632 | DAILY | 00351697 | SPICAPX | Rebate for Line outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025945039508.2513888889 | 10259450 |  | Parent | FALSE | 3-4 220KV BUS TIE CB NO.4 BUS CT R/PH AT WMTS | 39508.2514 | 39508.4389 | DAILY | [12 empty] | 0
_X66858C539508.2645833333 | X66858C5 |  | Parent | FALSE | KTS NO.2 220KV LINE AT TTS | 39508.2646 | 39508.6472 | DAILY | 00015727 | SPICAPX | Replace 16mm glass insulators | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009272539508.3381944445 | 10092725 |  | Parent | FALSE | ATS 220KV LINE NO.4 BUS CB AT BLTS | 39508.3382 | 39508.7569 | DAILY | [12 empty] | 0
_X32058R739508.5152777778 | X32058R7 |  | Parent | FALSE | ROTS NO.1 LINE/B1 TRANS 220KV CB AT MTS | 39508.5153 | 39520.4958 | CONT | [12 empty] | 0
_1025934839509.25625 | 10259348 |  | Parent | FALSE | 1-2 220KV BUS TIE CB NO.1 BUS CT R/PH AT WMTS | 39509.2562 | 39509.4549 | DAILY | [12 empty] | 0
_X66858C639509.2576388889 | X66858C6 |  | Parent | FALSE | TSTS 220KV LINE AT TTS | 39509.2576 | 39509.6299 | DAILY | 00015736 | SPICAPX | Replace 16mm glass insulators | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010190639509.2604166667 | 10101906 |  | Parent | FALSE | NO.2A 220KV BUS AT BLTS | 39509.2604 | 39509.7764 | DAILY | 00002644 | SPIMAINT | o/h bus & isol/esw, no. 2 220/66&22 trs isol/esw, | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027925039509.2611111111 | 10279250 |  | Parent | FALSE | A NTH 22KV BUS AT RTS | 39509.2611 | 39509.4257 | DAILY | 00007354 | SPIMAINT | REPAIR DEFECTIVE ISOL | SPIPOWER |  |  | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_V77558A539509.3208333333 | V77558A5 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT RWTS | 39509.3208 | 39509.6771 | DAILY | 00350529 | SPIMAINT | No1 220 Cap bank during setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027968839510.1819444445 | 10279688 |  | Parent | FALSE | YPS NO.2 220KV LINE NO.6 BUS CB AT HWPS | 39510.1819 | 39510.2319 | CONT | [12 empty] | 0
_X32058R839511.2118055556 | X32058R8 |  | Parent | FALSE | U2 66/22KV TRANS AT MTS | 39511.2118 | 39511.5701 | DAILY | 00363319 | SPICAPX | Investigate conservator | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027949139511.2583333333 | 10279491 |  | Parent | FALSE | B3 220/66KV TRANS AT WMTS | 39511.2583 | 39511.6062 | DAILY | 00003236 | SPIMAINT | clean out raditors, clean down trans & oil topup | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027950239511.2854166667 | 10279502 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39511.2854 | 39511.3347 | DAILY | 00319998 | APDALCOA | Alcoa work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1025946639511.2986111111 | 10259466 |  | Parent | FALSE | EX - DDTS LINE NO.1 BUS CB CT R/PH AT WOTS | 39511.2986 | 39511.4521 | DAILY | [12 empty] | 0
_1027952139512.2284722222 | 10279521 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT RWTS | 39512.2285 | 39512.3806 | DAILY | [12 empty] | 0
_1027994239512.2284722222 | 10279942 | 10279521 | Child | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39512.2285 | 39512.3806 | DAILY | 00007399 | SPIMAINT | Rebate - REPAIR CT OIL LEAK | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027994339512.2284722222 | 10279943 | 10279521 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39512.2285 | 39512.3806 | DAILY | 00331179 | SPIMAINT | Rebate - REPAIR CT OIL LEAK | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027530439512.2611111111 | 10275304 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 39512.2611 | 39512.6424 | REPDAILY | 00006554 | SPIMAINT | No1 Trans oil leaks Audit 07 | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027952239512.2659722222 | 10279522 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 39512.266 | 39512.6229 | DAILY | 00001147 | SPIMAINT | clean out radiators & top up conservator | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027950339512.2902777778 | 10279503 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39512.2903 | 39512.3632 | DAILY | 00319999 | APDALCOA | Alcoa work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027985039512.4993055556 | 10279850 |  | Parent | FALSE | H1 TRANS NO.1 BUS 330KV CB AT DDTS | 39512.4993 | 39512.5347 | DAILY | [12 empty] | 0
_1027952439513.2645833333 | 10279524 |  | Parent | FALSE | B2 220/66KV TRANS AT KTS | 39513.2646 | 39514.6222 | CONT | 00001148 | SPIMAINT | clean out radiators & investigate faulty pump &fan | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027530439513.3041666667 | 10275304 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 39513.3042 | 39513.6681 | REPDAILY | 00006554 | SPIMAINT | No1 Trans oil leaks Audit 07 | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027986139513.4180555556 | 10279861 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 39513.4181 | 39560.8236 | CONT | 00356079 | GENCO | GenCo requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027967639514.3055555556 | 10279676 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39514.3056 | 39514.3639 | DAILY | [12 empty] | 0
_1027943839514.3430555556 | 10279438 |  | Parent | FALSE | YPS NO.7 220KV LINE NO.3 BUS CB AT ROTS | 39514.3431 | 39514.4743 | DAILY | [12 empty] | 0
_1027981339514.5826388889 | 10279813 |  | Parent | FALSE | A2 TRANS NO.1 BUS 220KV CB AT MLTS | 39514.5826 | 39522.2826 | CONT | [12 empty] | 0
_1024943639515.2513888889 | 10249436 |  | Parent | FALSE | 1B-3 220KV BUS TIE CB AT BLTS | 39515.2514 | 39515.7944 | DAILY | [12 empty] | 0
_V79058A339515.2645833333 | V79058A3 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB BUS SIDE ISOL AT SMTS | 39515.2646 | 39522.3125 | CONT | [12 empty] | 0
_1027985239515.2854166667 | 10279852 |  | Parent | FALSE | 1-2 66KV TIE BUS AT RWTS | 39515.2854 | 39515.6528 | DAILY | 00364661 | SPICAPX | VSCAP to DOC | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_V79058A439515.3381944445 | V79058A4 |  | Parent | TRUE | HWTS NO.1 500KV LINE AT SMTS | 39515.3382 | 39515.4292 | DAILY | 00012436 | SPICAPX | hv testings of gis equip in bay a (hwts - syts 1L) | SPIPOWER | V790 | V790 - URGENT MAINTENANCE WORKS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V79058R039515.3381944445 | V79058R0 | V79058A4 | Child | FALSE | SYTS NO.1 500KV LINE AT SMTS | 39515.3382 | 39515.4292 | DAILY | 00012439 | SPICAPX | hv testings of gis equip in bay a (hwts - syts 1L) | SPIPOWER | V790 | V790 - URGENT MAINTENANCE WORKS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027966339516.2493055556 | 10279663 |  | Parent | TRUE | NO.2 66KV BUS AT HTS | 39516.2493 | 39516.3826 | DAILY | 00004457 | SPIMAINT | REPLACE DEFECTIVE DROPPER | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027966839516.2493055556 | 10279668 | 10279663 | Child | FALSE | B2 220/66KV TRANS AT HTS | 39516.2493 | 39516.3826 | DAILY | 00004446 | SPIMAINT | REBATE TRAN OUTAGE | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025937239516.2520833333 | 10259372 |  | Parent | FALSE | EX - 1-3 220KV BUS TIE CB CT R/PH AT FBTS | 39516.2521 | 39516.3917 | DAILY | [12 empty] | 0
_1025489539516.2569444444 | 10254895 |  | Parent | FALSE | NO.2B 220KV BUS AT BLTS | 39516.2569 | 39516.6903 | DAILY | 00002643 | SPIMAINT | O/Haul NO.2B 220KV BUS AT BLTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1025937439516.3916666667 | 10259374 |  | Parent | FALSE | EX - 3-4 220KV BUS TIE CB CT R/PH AT FBTS | 39516.3917 | 39516.5938 | DAILY | [12 empty] | 0
_1027969439518.2409722222 | 10279694 | Z54358A7 | Child | FALSE | NO.1 220KV BUS AT MLTS | 39518.241 | 39518.7035 | REPDAILY | 00003014 | VEN_AUG | Rebate W/O, No1 220kv Cap Bank, No1 220 Bus outage | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z54358A339518.2409722222 | Z54358A3 |  | Parent | TRUE | NO.1 220KV BUS AT MLTS | 39518.241 | 39518.7035 | REPDAILY | 00003014 | VEN_AUG | Uprate Bus Connections in Bay H of No1 22okv Bus | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z54358A639518.2409722222 | Z54358A6 | Z54358A3 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT MLTS | 39518.241 | 39518.7035 | REPDAILY | 00360001 | VEN_AUG | Rebate W/O, No1 220kv Cap Bank, No1 220 Bus outage | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z54358A739518.2409722222 | Z54358A7 | Z54358A3 | Child | TRUE | 220KV SHUNT REACTOR AT MLTS | 39518.241 | 39518.7035 | REPDAILY | 00003011 | VEN_AUG | Rebate W/O for 220kv Shunt Reactor | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X55658D139518.25625 | X55658D1 |  | Parent | FALSE | LDL NO.2 66KV FDR AT RWTS | 39518.2562 | 39518.6936 | DAILY | 00020118 | SPICAPX | Diconnect FDR cb in Bay K to FDR | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027967039518.275 | 10279670 |  | Parent | FALSE | EX - A4 TRANS/B2 TRANS 220KV CB AT KTS | 39518.275 | 39518.5736 | DAILY | [12 empty] | 0
_1027989739518.3375 | 10279897 |  | Parent | FALSE | JLGA NO.4 UNIT TRANS DISC CB AT JLGA | 39518.3375 | 39518.5778 | DAILY | [12 empty] | 0
_X55658C239518.6833333333 | X55658C2 |  | Parent | FALSE | EX - LDL NO.2 66KV FDR CB AT RWTS | 39518.6833 | 39527.2354 | CONT | [12 empty] | 0
_1027969439519.2534722222 | 10279694 | Z54358A7 | Child | FALSE | NO.1 220KV BUS AT MLTS | 39519.2535 | 39519.7549 | REPDAILY | 00003014 | VEN_AUG | Rebate W/O, No1 220kv Cap Bank, No1 220 Bus outage | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z54358A339519.2534722222 | Z54358A3 |  | Parent | TRUE | NO.1 220KV BUS AT MLTS | 39519.2535 | 39519.7549 | REPDAILY | 00003014 | VEN_AUG | Uprate Bus Connections in Bay H of No1 22okv Bus | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z54358A639519.2534722222 | Z54358A6 | Z54358A3 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT MLTS | 39519.2535 | 39519.7549 | REPDAILY | 00360001 | VEN_AUG | Rebate W/O, No1 220kv Cap Bank, No1 220 Bus outage | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z54358A739519.2534722222 | Z54358A7 | Z54358A3 | Child | TRUE | 220KV SHUNT REACTOR AT MLTS | 39519.2535 | 39519.7549 | REPDAILY | 00003011 | VEN_AUG | Rebate W/O for 220kv Shunt Reactor | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027970639519.3506944444 | 10279706 |  | Parent | FALSE | B1 220/66KV TRANS AT TGTS | 39519.3507 | 39519.4819 | DAILY | 00363297 | SPIMAINT | Out W/O B1 Transformer to test its gas prot | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027953239520.2618055556 | 10279532 |  | Parent | FALSE | B1 220/66KV TRANS BANK AT BLTS | 39520.2618 | 39520.4729 | DAILY | 00018514 | SPIMAINT | top up the white phase 220kv bushing | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027969439520.2923611111 | 10279694 | Z54358A7 | Child | FALSE | NO.1 220KV BUS AT MLTS | 39520.2924 | 39520.7188 | REPDAILY | 00003014 | VEN_AUG | Rebate W/O, No1 220kv Cap Bank, No1 220 Bus outage | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z54358A339520.2923611111 | Z54358A3 |  | Parent | TRUE | NO.1 220KV BUS AT MLTS | 39520.2924 | 39520.7188 | REPDAILY | 00003014 | VEN_AUG | Uprate Bus Connections in Bay H of No1 22okv Bus | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z54358A639520.2923611111 | Z54358A6 | Z54358A3 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT MLTS | 39520.2924 | 39520.7188 | REPDAILY | 00360001 | VEN_AUG | Rebate W/O, No1 220kv Cap Bank, No1 220 Bus outage | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z54358A739520.2923611111 | Z54358A7 | Z54358A3 | Child | TRUE | 220KV SHUNT REACTOR AT MLTS | 39520.2924 | 39520.7188 | REPDAILY | 00003011 | VEN_AUG | Rebate W/O for 220kv Shunt Reactor | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027940539520.3138888889 | 10279405 |  | Parent | TRUE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39520.3139 | 39520.3465 | DAILY | [12 empty] | 0
_1027979839520.3138888889 | 10279798 | 10279405 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39520.3139 | 39520.3465 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during 275kV CB outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028121739520.3645833333 | 10281217 |  | Parent | FALSE | CBTS NO.4 500KV LINE AT ROTS (RTF) | 39520.3646 | 39520.3667 | DAILY | 00356730 | 3RDPARTY | ROTS (RTF) - Trip CBTS No 4 500 kV Line CB's | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1028008839520.6340277778 | 10280088 |  | Parent | TRUE | ROTS NO.1 220KV LINE AT RTS | 39520.634 | 39520.6736 | CONT | 00021385 | FAULT | No1 220kV Bus Tripped due to L1 Trans fault | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028009239520.6340277778 | 10280092 | 10280088 | Child | FALSE | NO.1 220KV BUS AT RTS | 39520.634 | 39520.6736 | CONT | 00007347 | FAULT | No1 220kV Bus Tripped due to L1 Trans fault | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028009339520.6340277778 | 10280093 | 10280088 | Child | FALSE | B1 220/66KV TRANS AT RTS | 39520.634 | 39520.6736 | CONT | 00007329 | FAULT | B1 trip for Cable fault on L1 Trans 22 kV Cable | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028004539520.6340277778 | 10280045 |  | Parent | FALSE | L1 220/22KV TRANS AT RTS | 39520.634 | 39521.8528 | CONT | 00007330 | FAULT | L1,B1, RTS-ROTS No 1 Line | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027921839521.2673611111 | 10279218 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39521.2674 | 39521.4819 | DAILY | [12 empty] | 0
_1027787639521.2916666667 | 10277876 |  | Parent | FALSE | WBTS 220KV LINE NO.1 BUS CB CT R/PH AT HOTS | 39521.2917 | 39521.4167 | DAILY | [12 empty] | 0
_1027969439521.2916666667 | 10279694 | Z54358A7 | Child | FALSE | NO.1 220KV BUS AT MLTS | 39521.2917 | 39521.6118 | REPDAILY | 00003014 | VEN_AUG | Rebate W/O, No1 220kv Cap Bank, No1 220 Bus outage | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z54358A339521.2916666667 | Z54358A3 |  | Parent | TRUE | NO.1 220KV BUS AT MLTS | 39521.2917 | 39521.6118 | REPDAILY | 00003014 | VEN_AUG | Uprate Bus Connections in Bay H of No1 22okv Bus | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z54358A639521.2916666667 | Z54358A6 | Z54358A3 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT MLTS | 39521.2917 | 39521.6118 | REPDAILY | 00360001 | VEN_AUG | Rebate W/O, No1 220kv Cap Bank, No1 220 Bus outage | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z54358A739521.2916666667 | Z54358A7 | Z54358A3 | Child | TRUE | 220KV SHUNT REACTOR AT MLTS | 39521.2917 | 39521.6118 | REPDAILY | 00003011 | VEN_AUG | Rebate W/O for 220kv Shunt Reactor | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028010039521.3438194444 | 10280100 |  | Parent | FALSE | L1 TRANS 'A' STH BUS 22KV CB AT RTS | 39521.3438 | 39544.7632 | CONT | [12 empty] | 0
_1027980939521.3680555556 | 10279809 |  | Parent | TRUE | GNTS NO.1 220KV LINE CB BUS SIDE ROI AT DDTS | 39521.3681 | 39521.3979 | DAILY | [12 empty] | 0
_1027981239521.3680555556 | 10279812 | 10279809 | Child | FALSE | GNTS NO.1 220KV LINE AT DDTS | 39521.3681 | 39521.3979 | DAILY | 00352475 | SPIMAINT | Rebate W/O GNTS No1 Line during CB/ROI outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027790539521.4229166667 | 10277905 |  | Parent | FALSE | SMTS NO.1 330KV LINE NO.1 BUS CB LINE SIDE ISOL AT DDTS | 39521.4229 | 39521.4514 | DAILY | [12 empty] | 0
_1028010139521.5493055556 | 10280101 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39521.5493 | 39524.3917 | CONT | 00003104 | FAULT | Cap Bank trip from protection | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028010239521.8034722222 | 10280102 |  | Parent | FALSE | BATS-BETS 220KV | 39521.8035 | 39521.9528 | CONT | 00328505 | DBPROX | Powercor Request for fault work beneath line | DISTCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1028010639522.0138888889 | 10280106 |  | Parent | FALSE | KTS 500KV LINE AT SMTS | 39522.0139 | 39522.0361 | CONT | 00012441 | FORCED | Bleed ROTS No 3 Line / KTS Line 500 kV CB | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027988839522.2645833333 | 10279888 |  | Parent | TRUE | NO.4 66KV BUS AT GTS | 39522.2646 | 39522.6076 | DAILY | 00002838 | SPIMAINT | SCAN - Gle No2 Fdr No4 Bus side isol R ph hot spot | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1027989939522.2645833333 | 10279899 | 10279888 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39522.2646 | 39522.6076 | DAILY | 00329879 | SPIMAINT | Rebate W/O No4 66kV Cap bank during bus outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027990039522.2645833333 | 10279900 | 10279888 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39522.2646 | 39522.6076 | DAILY | 00002830 | SPIMAINT | Perf calc W/O No4 Trans during #4 66kV bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027969439522.2798611111 | 10279694 | Z54358A7 | Child | FALSE | NO.1 220KV BUS AT MLTS | 39522.2799 | 39522.6507 | REPDAILY | 00003014 | VEN_AUG | Rebate W/O, No1 220kv Cap Bank, No1 220 Bus outage | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z54358A339522.2798611111 | Z54358A3 |  | Parent | TRUE | NO.1 220KV BUS AT MLTS | 39522.2799 | 39522.6507 | REPDAILY | 00003014 | VEN_AUG | Uprate Bus Connections in Bay H of No1 22okv Bus | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z54358A639522.2798611111 | Z54358A6 | Z54358A3 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT MLTS | 39522.2799 | 39522.6507 | REPDAILY | 00360001 | VEN_AUG | Rebate W/O, No1 220kv Cap Bank, No1 220 Bus outage | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z54358A739522.2798611111 | Z54358A7 | Z54358A3 | Child | TRUE | 220KV SHUNT REACTOR AT MLTS | 39522.2799 | 39522.6507 | REPDAILY | 00003011 | VEN_AUG | Rebate W/O for 220kv Shunt Reactor | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V79058A539522.3277777778 | V79058A5 |  | Parent | TRUE | HWTS NO.1 500KV LINE AT SMTS | 39522.3278 | 39522.4639 | DAILY | 00012436 | SPICAPX | hv testings of gis equip in bay a (hwts - syts 1L) | SPIPOWER | V790 | V790 - URGENT MAINTENANCE WORKS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V79058R239522.3277777778 | V79058R2 | V79058A5 | Child | FALSE | SYTS NO.1 500KV LINE AT SMTS | 39522.3278 | 39522.4639 | DAILY | 00012439 | SPICAPX | hv testings of gis equip in bay a (hwts - syts 1L) | SPIPOWER | V790 | V790 - URGENT MAINTENANCE WORKS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028485339522.5361111111 | 10284853 |  | Parent | FALSE | FUTURE F1 TRANS 500KV CB AT SMTS | 39522.5361 | 40532.2083 | CONT | [12 empty] | 0
_V79058A639522.6194444445 | V79058A6 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 39522.6194 | 39523.4965 | DAILY | 00001328 | SPICAPX | hv test the blue phase | SPIPOWER | V790 | V790 - URGENT MAINTENANCE WORKS | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_Z54358A439522.6576388889 | Z54358A4 |  | Parent | TRUE | A2 TRANS NO.1 BUS 220KV CB AT MLTS | 39522.6576 | 39573.3021 | CONT | [12 empty] | 0
_Z54358A539522.6576388889 | Z54358A5 | Z54358A4 | Child | FALSE | A2 TRANS NO.1 BUS 220KV CB AT MLTS | 39522.6576 | 39573.3021 | CONT | [12 empty] | 0
_1028025839523.2638888889 | 10280258 | V79058A7 | Child | FALSE | SYTS NO.1 500KV LINE AT SMTS | 39523.2639 | 39523.5458 | DAILY | 00012439 | SPICAPX | restore smts 500kv by-pass in bay a | SPIPOWER | V790 | V790 - URGENT MAINTENANCE WORKS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V79058A739523.2638888889 | V79058A7 |  | Parent | TRUE | HWTS NO.1 500KV LINE AT SMTS | 39523.2639 | 39523.5458 | DAILY | 00012436 | SPICAPX | restore smts 500kv by-pass in bay a | SPIPOWER | V790 | V790 - URGENT MAINTENANCE WORKS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V77558A639523.3020833333 | V77558A6 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39523.3021 | 39523.7583 | DAILY | 00354024 | SPIMAINT | No1 220 Cap bank during setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1028011239523.3180555556 | 10280112 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 39523.3181 | 39523.5819 | CONT | 00356086 | GENCO | Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028025939523.4770833333 | 10280259 |  | Parent | FALSE | JLA NO.1 220KV LINE AT TBTS | 39523.4771 | 39523.5194 | DAILY | 00018301 | FORCED | Low SF 6 | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028011639523.7625 | 10280116 |  | Parent | FALSE | AUX TRANS 'C' 220KV LINE AT YWPS | 39523.7625 | 39528.65 | CONT | 00016397 | GENCO | Auxilliary Trans C | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1024478939524.2791666667 | 10244789 |  | Parent | FALSE | B1 220/66KV TRANS AT SVTS | 39524.2792 | 39524.4049 | DAILY | 00004849 | SPIMAINT | More Operator Training at SVTS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028014839524.36875 | 10280148 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39524.3688 | 39525.6544 | CONT | [12 empty] | 0
_1028009939524.3916666667 | 10280099 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39524.3917 | 39524.4514 | DAILY | 00003104 | FAULT | Investigate Cap Bank trip from protection | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027953139525.2583333333 | 10279531 |  | Parent | FALSE | NO.4B 66KV CAPACITOR BANK CB AT SVTS | 39525.2583 | 39525.3431 | DAILY | [12 empty] | 0
_1024849839525.2722222222 | 10248498 |  | Parent | FALSE | SYN/COND AT TSTS | 39525.2722 | 39527.5701 | CONT | 00007626 | SPIMAINT | 4 Monthly O/HAUL - TSTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027986439525.2972222222 | 10279864 |  | Parent | FALSE | EX - KTS NO.3 220KV LINE NO.2 BUS CB AT GTS | 39525.2972 | 39525.6243 | DAILY | [12 empty] | 0
_1027999739525.3652777778 | 10279997 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT TTS | 39525.3653 | 39526.5542 | CONT | 00001485 | FAULT | white & blue phase out of balance | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028002739525.6548611111 | 10280027 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39525.6549 | 39525.684 | DAILY | [12 empty] | 0
_Z73058A939526.2305555556 | Z73058A9 |  | Parent | FALSE | EPS-TTS 220KV LINE AT SMTS | 39526.2306 | 39526.6819 | DAILY | 00015363 | DB_AUG | install gantry - proximity outage only | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028022439526.2354166667 | 10280224 |  | Parent | FALSE | MBTS NO.2 220KV LINE AT EPSY | 39526.2354 | 39526.3271 | CONT | 00087036 | SW_NEM | Line de-energised for voltage control by NEMMCo | NEMMCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 3
_X66858C739526.2527777778 | X66858C7 |  | Parent | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 39526.2528 | 39526.6069 | DAILY | 00015793 | SPICAPX | Replace insulators HWPS-ROTS No 2 LINE | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027999539526.3208333333 | 10279995 |  | Parent | FALSE | ERTS NO.2 220KV LINE NO.2 BUS CB AT ROTS | 39526.3208 | 39526.341 | DAILY | [12 empty] | 0
_1028022639526.3277777778 | 10280226 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT EPSY | 39526.3278 | 39526.7056 | CONT | 00087035 | SW_NEM | Line de-energised for voltage control by NEMMCo' | NEMMCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 3
_X55658B539527.2423611111 | X55658B5 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39527.2424 | 39527.6062 | DAILY | 00007480 | SPICAPX | Install new Bus Connection to CB | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X55658B939527.2423611111 | X55658B9 | X55658B5 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 39527.2424 | 39527.6062 | DAILY | 00007450 | SPICAPX | Tran outage Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028024739527.2506944445 | 10280247 |  | Parent | FALSE | DDTS NO.1 330KV LINE SERIES CAPACITOR BANK AT SMTS | 39527.2507 | 39527.5597 | DAILY | 00327836 | FAULT | investigate/repair unbalance alarm on white phase | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1028017439527.2930555556 | 10280174 |  | Parent | FALSE | MLTS-HYTS 1 500KV W | 39527.2931 | 39527.3833 | DAILY | 00022630 | SW_NEM | MLTS Reactor Switching | VENCORP |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027950939527.2930555556 | 10279509 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT GNTS | 39527.2931 | 39527.6076 | DAILY | [12 empty] | 0
_1028005639527.2930555556 | 10280056 | 10279509 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT GNTS | 39527.2931 | 39527.6076 | DAILY | 00329962 | SPIMAINT | Rebate W/O No1 66kV Cap bank during CT sampling | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028017739527.3868055556 | 10280177 |  | Parent | FALSE | MLTS-HYTS 2 500KV W | 39527.3868 | 39527.3931 | DAILY | 00022633 | SW_NEM | MLTS Reactor Switching | VENCORP |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1028026739527.4055555556 | 10280267 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39527.4056 | 39534.3049 | DAILY | [12 empty] | 0
_1028013339528.0840277778 | 10280133 |  | Parent | FALSE | LYBP-LYPS 2 500KV G | 39528.084 | 39532.1042 | CONT | 00023068 | GENCO | SCAP to LYPB | GENCO |  |  | Circuits | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1028121839531.8861111111 | 10281218 |  | Parent | FALSE | KTS -GTS 3 220KV WY | 39531.8861 | 39531.8882 | DAILY | 00022709 | FAULT | GTS - KTS No3 Line auto | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z73058B039532.2118055556 | Z73058B0 |  | Parent | FALSE | EPS-TTS 220KV LINE AT SMTS | 39532.2118 | 39532.6965 | DAILY | 00015363 | DB_AUG | install gantry - proximity outage only | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024945039532.2305555556 | 10249450 |  | Parent | FALSE | SYN/COND AT BLTS | 39532.2306 | 39534.6687 | CONT | 00002547 | SPIMAINT | 3 Monthly O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X66858D039532.2479166667 | X66858D0 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT HWPS | 39532.2479 | 39532.6069 | DAILY | 00015790 | SPICAPX | Replace insulators hwps-rots No1 line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027980039532.2638888889 | 10279800 | 10248958 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 39532.2639 | 39540.5417 | CONT | 00352121 | SPIMAINT | Rebate W/O No2 Trans during 220kV CB O-Haul | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024895839532.2638888889 | 10248958 |  | Parent | TRUE | H2 TRANS 220KV CB AT DDTS | 39532.2639 | 39542.6243 | CONT | [12 empty] | 0
_1028108439532.7395833333 | 10281084 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 39532.7396 | 39550.2757 | CONT | 00356080 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z73058B139533.2236111111 | Z73058B1 |  | Parent | FALSE | EPS-TTS 220KV LINE AT SMTS | 39533.2236 | 39533.7028 | DAILY | 00015363 | DB_AUG | install ground wire - rots-tts & eps-tts lines | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027991639533.2409722222 | 10279916 |  | Parent | FALSE | ROTS-TTS 220KV WT | 39533.241 | 39533.6965 | DAILY | 00119309 | DB_AUG | Proximity at SMTS (rebate record for Z73058B1) | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 500 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X66858C839533.2520833333 | X66858C8 |  | Parent | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 39533.2521 | 39533.5938 | DAILY | 00015793 | SPICAPX | Replace insulators HWPS-ROTS No 2 LINE | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028004039533.3715277778 | 10280040 |  | Parent | FALSE | ROTSVT 911 ROTS - SVTS FIBRE OPTIC CABLE | 39533.3715 | 39533.5603 | DAILY | 00112371 | SPIMAINT | Underground Section of 911 Cable at Wellington Rd | SPIPOWER |  |  | Other | Eastern |  | NON AER ELEMENT | EXCLUDED |  | 0
_X66858C939534.2472222222 | X66858C9 |  | Parent | FALSE | ROTS NO.8 220KV LINE AT YPS | 39534.2472 | 39534.4792 | DAILY | 00016416 | SPICAPX | Replace insulators YPS-ROTS No8 Line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028015939534.2541666667 | 10280159 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT SMTS | 39534.2542 | 39534.6903 | DAILY | 00026101 | SPIMAINT | top up white ph diverter switch & all conservators | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027970039534.2611111111 | 10279700 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39534.2611 | 39534.6507 | DAILY | 00016040 | SPIMAINT | 2B Trans bank oil leak Red phase | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028014239534.2895833333 | 10280142 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39534.2896 | 39535.5708 | DAILY | [12 empty] | 0
_1028025039534.3645833333 | 10280250 |  | Parent | FALSE | MSS -DDTS 1 330KV NW | 39534.3646 | 39534.4806 | DAILY | 00060190 | TRANSGRD | Transgrid Outage | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1028114639534.4166666667 | 10281146 |  | Parent | FALSE | EX - APD-MLTS NO.2 500KV LINE CT R/PH AT HYTS | 39534.4167 | 39534.616 | CONT | [12 empty] | 0
_1028025139534.4979166667 | 10280251 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39534.4979 | 39534.6299 | DAILY | 00060191 | TRANSGRD | Transgrid Outage | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X32058S639535.2 | X32058S6 |  | Parent | TRUE | EX - ROTS NO.1 220KV LINE AT MTS | 39535.2 | 39537.6194 | CONT | 00351696 | SPICAPX | MTS-ROTS 1 Line B3 Trans No3 S/S Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058S739535.2 | X32058S7 | X32058S6 | Child | FALSE | NO.3 11KV/415V S/S TRANS AT MTS | 39535.2 | 39537.6194 | CONT | 00364880 | SPICAPX | Rebate Trans for Line outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Other Transformers | Eastern | 11 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1028032039535.2152777778 | 10280320 |  | Parent | FALSE | W2 20/6.6KV UNIT TRANS AT YWPS | 39535.2153 | 39647.7708 | CONT | 00010638 | GENCO | W2 GenTrans 220kV Isolation and earthing scap | GENCO |  |  | Other Transformers | Eastern | 20 | NON SP ASSET | EXCLUDED |  | 0
_1028039939535.24375 | 10280399 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39535.2438 | 39535.4181 | DAILY | 00354002 | SPIMAINT | TOP UP TRANS D/SW OIL LEVEL | SPIPOWER |  |  | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_X66858D139535.2451388889 | X66858D1 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT HWPS | 39535.2451 | 39535.55 | DAILY | 00015790 | SPICAPX | Replace insulators hwps-rots No1 line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009273239535.2527777778 | 10092732 |  | Parent | FALSE | KTS NO.1 220KV LINE NO.1 BUS CB LINE SIDE ISOL AT TTS | 39535.2528 | 39535.6264 | DAILY | [12 empty] | 0
_1025195539536.1666666667 | 10251955 |  | Parent | TRUE | AUX B 220KV TRANS LINE AT HWPS | 39536.1667 | 39536.5382 | DAILY | 00356087 | SPIMAINT | O/Haul - 220kV LINE CTS (EH) | SPIPOWER |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028026439536.1666666667 | 10280264 | 10251955 | Child | FALSE | JLTS NO.1 220KV LINE AT HWPS | 39536.1667 | 39536.5382 | DAILY | 00015784 | SPIMAINT | rebate Line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028007739536.1763888889 | 10280077 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39536.1764 | 39536.5618 | DAILY | 00002833 | SPIMAINT | Out W/O No1 220 Bus install bonding to exp joints | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028007839536.1763888889 | 10280078 | 10280077 | Child | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39536.1764 | 39536.5618 | DAILY | 00017906 | SPIMAINT | Rebate W/O PTH No2 Line during No1 220 Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028007939536.1763888889 | 10280079 | 10280077 | Child | FALSE | EX - MLTS NO.2 220KV LINE AT GTS | 39536.1764 | 39536.5618 | DAILY | 00017904 | SPIMAINT | Rebate W/O MLTS No2 Line during No1 220 Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028008139536.1763888889 | 10280081 | 10280077 | Child | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39536.1764 | 39536.5618 | DAILY | 00017901 | SPIMAINT | Rebate W/O KTS No2 Line during No1 220 Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028008239536.1763888889 | 10280082 | 10280077 | Child | FALSE | B3 220/66KV TRANS AT GTS | 39536.1764 | 39536.5618 | DAILY | 00002829 | SPIMAINT | Perf calc W/O No3 Trans during No1 220 Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70858A739536.2215277778 | X70858A7 |  | Parent | FALSE | DDTS NO.1 330KV LINE AT SMTS | 39536.2215 | 39536.7292 | DAILY | 00012749 | SPICAPX | replace line surge arrestors | SPIPOWER | X708 | X708 - REPLACEMENT OF AGEING 22KV TO 500KV SURGE ARRESTERS | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024946739536.2527777778 | 10249467 |  | Parent | FALSE | EX - B3 220/66KV TRANS AT TTS | 39536.2528 | 39536.6868 | REPDAILY | 00001544 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X55658E139536.2888888889 | X55658E1 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39536.2889 | 39536.3806 | DAILY | 00007480 | SPICAPX | Pressure Test Future CB | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X55658E239536.2888888889 | X55658E2 | X55658E1 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 39536.2889 | 39536.3806 | DAILY | 00007450 | SPICAPX | Trans Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028122039536.3805555556 | 10281220 |  | Parent | FALSE | LDL NO.2 66KV FDR CB AT RWTS | 39536.3806 | 39539.625 | CONT | [12 empty] | 0
_1028121939536.3805555556 | 10281219 |  | Parent | FALSE | BH 66KV FDR CB AT RWTS | 39536.3806 | 39554.625 | CONT | [12 empty] | 0
_1028016439536.4083333333 | 10280164 |  | Parent | FALSE | L3 TRANS NO.2 BUS 22KV CB AT WMTS | 39536.4083 | 39536.4868 | DAILY | [12 empty] | 0
_1024946739537.2125 | 10249467 |  | Parent | FALSE | EX - B3 220/66KV TRANS AT TTS | 39537.2125 | 39537.6687 | REPDAILY | 00001544 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028008339537.2326388889 | 10280083 |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 39537.2326 | 39537.5264 | DAILY | 00002834 | SPIMAINT | Out W/O No2 220 Bus install bonding to exp joints | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028008439537.2326388889 | 10280084 | 10280083 | Child | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39537.2326 | 39537.5264 | DAILY | 00017905 | SPIMAINT | Rebate W/O PTH No1 Line during No2 220 Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028008539537.2326388889 | 10280085 | 10280083 | Child | FALSE | EX - MLTS NO.1 220KV LINE AT GTS | 39537.2326 | 39537.5264 | DAILY | 00017903 | SPIMAINT | Rebate W/O MLTS No1 Line during No2 220 Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028008639537.2326388889 | 10280086 | 10280083 | Child | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39537.2326 | 39537.5264 | DAILY | 00017900 | SPIMAINT | Rebate W/O KTS No1 Line during No2 220 Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028008739537.2326388889 | 10280087 | 10280083 | Child | FALSE | B1 220/66KV TRANS AT GTS | 39537.2326 | 39537.5264 | DAILY | 00002828 | SPIMAINT | Perf calc W/O No1 Trans during No2 220 Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058S239538.1972222222 | X32058S2 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39538.1972 | 39538.7042 | REPDAILY | 00363305 | SPICAPX | Complete more hand rail on Trans Rack | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70858A839538.2298611111 | X70858A8 |  | Parent | FALSE | DDTS NO.2 330KV LINE AT SMTS | 39538.2299 | 39538.675 | DAILY | 00012750 | SPICAPX | replace line surge arrestors | SPIPOWER | X708 | X708 - REPLACEMENT OF AGEING 22KV TO 500KV SURGE ARRESTERS | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X43258AM39538.2465277778 | X43258AM |  | Parent | FALSE | R3 220/66/22KV TRANS AT RCTS | 39538.2465 | 39549.7342 | CONT | 00361128 | SPICAPX | Out W/O No3 Trans warranty works | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X32058S239539.1930555556 | X32058S2 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39539.1931 | 39539.7465 | REPDAILY | 00363305 | SPICAPX | Complete more hand rail on Trans Rack | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024938039539.2277777778 | 10249380 |  | Parent | FALSE | SYN/COND AT FBTS | 39539.2278 | 39541.3944 | CONT | 00002697 | SPIMAINT | 3 Monthly O/HAUL - FBTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X55658C039539.2368055556 | X55658C0 |  | Parent | FALSE | LDL NO.2 66KV FDR AT RWTS | 39539.2368 | 39539.4778 | DAILY | 00020118 | SPICAPX | Commission New Sub LDL No2 Fdr CB & Transfer Bus | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1028116539539.2513888889 | 10281165 |  | Parent | FALSE | RTS 220KV LINE AT BTS | 39539.2514 | 39575.6035 | CONT | 00015960 | SPIMAINT | BTS-RTS 220kV Line CBs at and RTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028010739539.2868055556 | 10280107 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.1 BUS CB AT DDTS | 39539.2868 | 39539.459 | DAILY | [12 empty] | 0
_1028112139539.2923611111 | 10281121 |  | Parent | FALSE | HYTS NO.1 500KV LINE AT APD | 39539.2924 | 39539.5417 | CONT | 00005921 | APDALCOA | Work by APD on APD-HYTS NO1 500KV Line at APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_V60458A939539.3194444444 | V60458A9 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT SMTS | 39539.3194 | 39539.6396 | REPDAILY | 00012440 | SPIMAINT | drill flanges & prepare for silicon injection | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028010839539.4930555556 | 10280108 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.2 BUS CB AT DDTS | 39539.4931 | 39539.6007 | DAILY | [12 empty] | 0
_X32058S239540.1951388889 | X32058S2 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39540.1951 | 39540.6847 | REPDAILY | 00363305 | SPICAPX | Complete more hand rail on Trans Rack | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028003839540.2534722222 | 10280038 |  | Parent | FALSE | NO.2 CSC NO.3 BUS CB AT ROTS | 39540.2535 | 39540.4694 | DAILY | [12 empty] | 0
_1027165339540.2597222222 | 10271653 |  | Parent | FALSE | ROTS 220KV LINE NO.1 BUS CB AT TSTS | 39540.2597 | 39540.6 | DAILY | [12 empty] | 0
_1027015839540.2743055556 | 10270158 |  | Parent | FALSE | B1 TRANS 220KV CB AT GTS | 39540.2743 | 39541.5604 | CONT | [12 empty] | 0
_1027153539540.2819444445 | 10271535 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK AT BTS | 39540.2819 | 39540.6243 | DAILY | 00337002 | SPIMAINT | O/Haul NO.1 22KV CAPACITOR BANK AT BTS | SPIPOWER |  |  | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028010939540.2833333333 | 10280109 |  | Parent | TRUE | MBTS NO.2 220KV LINE CB AT DDTS | 39540.2833 | 39540.4757 | DAILY | [12 empty] | 0
_1028022939540.2833333333 | 10280229 | 10280109 | Child | FALSE | MBTS NO.2 220KV LINE AT DDTS | 39540.2833 | 39540.4757 | DAILY | 00012363 | SPIMAINT | Rebate W/O MBTS No2 Line during CB outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458A939540.3125 | V60458A9 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT SMTS | 39540.3125 | 39540.6583 | REPDAILY | 00012440 | SPIMAINT | drill flanges & prepare for silicon injection | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028122439540.5423611111 | 10281224 |  | Parent | FALSE | H2 TRANS 220KV CB AT DDTS | 39540.5424 | 39543.625 | CONT | [12 empty] | 0
_1028142839540.9576388889 | 10281428 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39540.9576 | 39541.4014 | CONT | [12 empty] | 0
_X32058S239541.2166666667 | X32058S2 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39541.2167 | 39541.6444 | REPDAILY | 00363305 | SPICAPX | Complete more hand rail on Trans Rack | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027165539541.2569444444 | 10271655 |  | Parent | FALSE | ROTS 220KV LINE NO.2 BUS CB AT TSTS | 39541.2569 | 39541.5625 | DAILY | [12 empty] | 0
_1027153739541.2694444445 | 10271537 |  | Parent | FALSE | NO.3 22KV CAPACITOR BANK AT BTS | 39541.2694 | 39541.5729 | DAILY | 00337011 | SPIMAINT | O/Haul NO.3 22KV CAPACITOR BANK AT BTS | SPIPOWER |  |  | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028147039541.2736111111 | 10281470 |  | Parent | FALSE | LY NO.4 66KV FDR NO.4 BUS CB AT MWTS | 39541.2736 | 39588.6507 | DAILY | [12 empty] | 0
_1027338539541.2916666667 | 10273385 |  | Parent | FALSE | EX - DDTS LINE NO.2 BUS CB CT R/PH AT WOTS | 39541.2917 | 39541.4062 | DAILY | [12 empty] | 0
_V60458A939541.3034722222 | V60458A9 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT SMTS | 39541.3035 | 39541.7306 | REPDAILY | 00012440 | SPIMAINT | drill flanges & prepare for silicon injection | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028146939541.4895833333 | 10281469 |  | Parent | FALSE | LY NO.4 66KV FDR NO.4 BUS CB AT MWTS | 39541.4896 | 39588.3146 | CONT | [12 empty] | 0
_1028146139541.5416666667 | 10281461 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT GNTS | 39541.5417 | 39541.6743 | DAILY | 00000745 | SPIMAINT | Blown L/A No2 s/sTrans w phase | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1028150439541.6993055556 | 10281504 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT SMTS | 39541.6993 | 39543.2097 | CONT | [12 empty] | 0
_X32058S239542.2125 | X32058S2 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39542.2125 | 39542.5569 | REPDAILY | 00363305 | SPICAPX | Complete more hand rail on Trans Rack | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027165739542.2472222222 | 10271657 |  | Parent | FALSE | TTS LINE/B1 TRANS 220KV CB AT TSTS | 39542.2472 | 39542.575 | DAILY | [12 empty] | 0
_1027176539542.2673611111 | 10271765 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK AT GTS | 39542.2674 | 39542.5826 | DAILY | 00350421 | SPIMAINT | O/Haul NO.1 66KV CAPACITOR BANK AT GTS | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027176739542.2673611111 | 10271767 | 10271765 | Child | FALSE | NO.1 66KV CAPACITOR BANK CB AT GTS | 39542.2674 | 39542.5826 | DAILY | [12 empty] | 0
_1027018439542.2743055556 | 10270184 |  | Parent | FALSE | 1-2 6.6KV BUS TIE CB AT FBTS | 39542.2743 | 39542.525 | DAILY | [12 empty] | 0
_1027068039542.2847222222 | 10270680 |  | Parent | FALSE | EX - 3-4 66KV BUS TIE CB AT KTS | 39542.2847 | 39542.5931 | DAILY | [12 empty] | 0
_V60458A939542.3034722222 | V60458A9 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT SMTS | 39542.3035 | 39542.6611 | REPDAILY | 00012440 | SPIMAINT | drill flanges & prepare for silicon injection | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027338739542.3090277778 | 10273387 |  | Parent | FALSE | JINDERA 330KV LINE NO.1 BUS CB CT R/PH AT WOTS | 39542.309 | 39542.4292 | DAILY | [12 empty] | 0
_1028147439542.3479166667 | 10281474 |  | Parent | FALSE | MBTS-EPS 1 220KV N | 39542.3479 | 39542.3514 | CONT | 00055380 | FORCED | Removal of foreign object | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1028147539542.3527777778 | 10281475 |  | Parent | FALSE | MBTS-EPS 2 220KV N | 39542.3528 | 39542.3549 | CONT | 00055381 | FORCED | Removal of foreign object | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1027338939542.4305555556 | 10273389 |  | Parent | FALSE | EX - JINDERA LINE NO.2 BUS CB CT R/PH AT WOTS | 39542.4306 | 39542.5451 | DAILY | [12 empty] | 0
_X55658E739542.6333333333 | X55658E7 |  | Parent | FALSE | CYN NO.1 66KV FDR CB AT RWTS | 39542.6333 | 39558.2535 | CONT | [12 empty] | 0
_1028013239543.2097222222 | 10280132 | V60458B0 | Child | FALSE | HWTS NO.2 500KV LINE AT SMTS | 39543.2097 | 39543.7368 | DAILY | 00012437 | SPIMAINT | Rebate W/O for SMTS-HWTS 2 Line | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458B039543.2097222222 | V60458B0 |  | Parent | TRUE | SYTS NO.2 500KV LINE AT SMTS | 39543.2097 | 39543.7368 | DAILY | 00012440 | SPIMAINT | invoke by-pass in bay "b" | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458B139543.6590277778 | V60458B1 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT SMTS | 39543.659 | 39570.3229 | CONT | [12 empty] | 0
_1024912539544.29375 | 10249125 |  | Parent | FALSE | NO.4 220KV BUS E/SW AT WMTS | 39544.2937 | 39544.7549 | DAILY | [12 empty] | 0
_Z53358A339544.2951388889 | Z53358A3 |  | Parent | FALSE | HWPS-ROTS 1 220KV G | 39544.2951 | 39544.5694 | REPDAILY | 00020454 | GEN_AUG | Errect a New Tower | SPIPOWER | Z533 | Z533 - (HWPS-ROTS) LINE 3 HW MINE EXTENSION - ST2 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028029939544.3027777778 | 10280299 |  | Parent | FALSE | L1 220/22KV TRANS AT RTS | 39544.3028 | 39544.7639 | DAILY | 00007330 | SPIMAINT | replace Damage Cable | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028163339544.4652777778 | 10281633 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39544.4653 | 39545.5278 | CONT | 00002863 | FORCED | M1 Tertiary Alarm | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028163939544.7166666667 | 10281639 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39544.7167 | 39544.7764 | CONT | [12 empty] | 0
_1027003939545.2791666667 | 10270039 |  | Parent | TRUE | NO.1 220KV BUS AT NPSD | 39545.2792 | 39549.6694 | CONT | 00003078 | SPIMAINT | CL.1 O/HAUL - S&S SF6 GIS Bus & other Compartments | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_1028267939545.2791666667 | 10282679 | 10270039 | Child | FALSE | BLTS 220KV LINE AT NPSD | 39545.2792 | 39549.6694 | CONT | 00024005 | SPIMAINT | CL.1 O/HAUL - S&S SF6 GIS Isolator | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027263539545.28125 | 10272635 |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT KGTS | 39545.2812 | 39545.6486 | DAILY | [12 empty] | 0
_1027176339545.2930555556 | 10271763 |  | Parent | FALSE | TTS 220KV LINE NO.2 BUS CB AT TSTS | 39545.2931 | 39545.6347 | DAILY | [12 empty] | 0
_Z53358A339545.2972222222 | Z53358A3 |  | Parent | FALSE | HWPS-ROTS 1 220KV G | 39545.2972 | 39545.6424 | REPDAILY | 00020454 | GEN_AUG | Errect a New Tower | SPIPOWER | Z533 | Z533 - (HWPS-ROTS) LINE 3 HW MINE EXTENSION - ST2 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027068239545.3138888889 | 10270682 |  | Parent | FALSE | EX - B2 TRANS NO.1 BUS 220KV CB AT KTS | 39545.3139 | 39546.6549 | CONT | [12 empty] | 0
_1027986439545.3645833333 | 10279864 |  | Parent | FALSE | EX - KTS NO.3 220KV LINE NO.2 BUS CB AT GTS | 39545.3646 | 39545.6042 | DAILY | [12 empty] | 0
_1028165339545.4833333333 | 10281653 |  | Parent | TRUE | SMTS-SYTS 2 500KV WT | 39545.4833 | 39545.5535 | CONT | 00022643 | FAULT | SMTS No2 500kV Line Tripped at SYTS | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028165439545.4833333333 | 10281654 | 10281653 | Child | FALSE | HWTS-SMTS 2 500KV WT | 39545.4833 | 39545.5535 | CONT | 00119315 | FAULT | SMTS No2 500kV Line Tripped at SYTS | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028151239545.6430555556 | 10281512 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39545.6431 | 39545.6764 | DAILY | [12 empty] | 0
_1028166839546.0868055556 | 10281668 |  | Parent | FALSE | CBTS NO.1 66KV FDR AT FTS | 39546.0868 | 39546.0993 | CONT | 00012275 | FORCED | Foreign Object on Conductors | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026800639546.2930555556 | 10268006 |  | Parent | FALSE | NO.3 TRANS 22KV CB AT KGTS | 39546.2931 | 39546.6993 | DAILY | [12 empty] | 0
_1026924439546.2972222222 | 10269244 | 10269251 | Child | FALSE | B2 TRANS 66KV CB AT TSTS | 39546.2972 | 39546.6625 | DAILY | [12 empty] | 0
_1026925139546.2972222222 | 10269251 |  | Parent | TRUE | B2 220/66KV TRANS AT TSTS | 39546.2972 | 39546.6625 | DAILY | 00007658 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027012239546.3236111111 | 10270122 |  | Parent | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB AT MLTS | 39546.3236 | 39548.4778 | CONT | [12 empty] | 0
_1028148739546.3263888889 | 10281487 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK CB AT SVTS | 39546.3264 | 39546.4319 | DAILY | [12 empty] | 0
_X46158Q439546.4708333333 | X46158Q4 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 39546.4708 | 39560.5703 | CONT | 00006554 | SPICAPX | Out W/O No1 Trans to cutover new OLTC control | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058R939547.23125 | X32058R9 |  | Parent | FALSE | B1 220/66KV TRANS AT MTS | 39547.2312 | 39547.7139 | DAILY | 00364562 | SPICAPX | Installhebal wall columns | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027306739547.2951388889 | 10273067 |  | Parent | FALSE | B2 220/66KV TRANS AT GNTS | 39547.2951 | 39549.6601 | CONT | 00000743 | SPIMAINT | Condition Monitoring Country Trans 2day North Area | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026921639547.2958333333 | 10269216 |  | Parent | TRUE | B3 220/66KV TRANS AT TSTS | 39547.2958 | 39547.659 | DAILY | 00007659 | SPIMAINT | O/H No.3 Trans Div. Switch @ TSTS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026924639547.2958333333 | 10269246 | 10269216 | Child | FALSE | B3 TRANS 66KV CB AT TSTS | 39547.2958 | 39547.659 | DAILY | [12 empty] | 0
_1027068739547.3173611111 | 10270687 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE NO.3 BUS CB AT KTS | 39547.3174 | 39548.6451 | CONT | [12 empty] | 0
_1027263339547.3347222222 | 10272633 |  | Parent | FALSE | NO.2 TRANS 22KV CB AT KGTS | 39547.3347 | 39547.6954 | DAILY | [12 empty] | 0
_V77558A739547.4326388889 | V77558A7 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT TBTS | 39547.4326 | 39547.7479 | DAILY | 00351938 | SPIMAINT | No1 66 Cap bank during setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1028157139547.5034722222 | 10281571 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39547.5035 | 39547.5389 | DAILY | [12 empty] | 0
_1028183739548.0244097222 | 10281837 |  | Parent | FALSE | EX - NO.7 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 39548.0244 | 39552.0042 | CONT | [12 empty] | 0
_1028184039548.1125 | 10281840 |  | Parent | TRUE | EX - 66KV CAPACITOR BANK CB AT TGTS | 39548.1125 | 39561.4847 | CONT | [12 empty] | 0
_1028261539548.1125 | 10282615 | 10281840 | Child | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39548.1125 | 39561.4847 | CONT | 00003104 | FAULT | Cap Bank 66kV CB failure | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026924039548.2916666667 | 10269240 | 10269248 | Child | FALSE | B1 TRANS 66KV CB AT TSTS | 39548.2917 | 39548.6507 | DAILY | [12 empty] | 0
_1026924839548.2916666667 | 10269248 |  | Parent | TRUE | B1 220/66KV TRANS AT TSTS | 39548.2917 | 39548.6507 | DAILY | 00007657 | SPIMAINT | O/HAUL Transformer and Trafo Union Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027345539548.2958333333 | 10273455 |  | Parent | FALSE | EX - NO.1 MAIN TRANS 500KV CB CT R/PH AT HWTS | 39548.2958 | 39548.5708 | DAILY | [12 empty] | 0
_X32058S139548.3222222222 | X32058S1 |  | Parent | FALSE | MTS NO.3 220KV LINE AT ROTS | 39548.3222 | 39548.5521 | DAILY | 00023099 | SPICAPX | modifications to MTS No3 Line X & Y Prot | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058S039549.2347222222 | X32058S0 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39549.2347 | 39549.5132 | DAILY | 00363305 | SPICAPX | Install ground wire Proximty only | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027165139549.2916666667 | 10271651 |  | Parent | FALSE | B1 TRANS NO.1 BUS 220KV CB AT TSTS | 39549.2917 | 39549.5951 | DAILY | [12 empty] | 0
_1027025239549.3131944445 | 10270252 |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT BLTS | 39549.3132 | 39549.3667 | DAILY | [12 empty] | 0
_1027030939549.3277777778 | 10270309 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT TTS | 39549.3278 | 39549.6118 | DAILY | [12 empty] | 0
_1028237939549.3277777778 | 10282379 | 10270309 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT TTS | 39549.3278 | 39549.6118 | DAILY | 00001485 | SPIMAINT | Rebate - CL.1 O/HAUL - S&S HGF 309 CB | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027339139549.3541666667 | 10273391 |  | Parent | FALSE | EX - B2 TRANS NO.1 BUS TIE CT R/PH AT GNTS | 39549.3542 | 39549.4688 | DAILY | [12 empty] | 0
_1028185439549.3541666667 | 10281854 |  | Parent | FALSE | NO.7 GEN TRANS 220KV CB AT HWPS | 39549.3542 | 39549.5347 | DAILY | [12 empty] | 0
_1027342339549.3583333333 | 10273423 |  | Parent | TRUE | EX - NO.1 220KV CAPACITOR BANK CB CT R/PH AT TSTS | 39549.3583 | 39549.5771 | DAILY | [12 empty] | 0
_1028238239549.3583333333 | 10282382 | 10273423 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT TSTS | 39549.3583 | 39549.5771 | DAILY | 00329164 | SPIMAINT | CT OIL SAMPLING | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_V77558A839549.55625 | V77558A8 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT TBTS | 39549.5563 | 39549.7521 | DAILY | 00351938 | SPIMAINT | No1 66 Cap bank during setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1028192739549.6555555556 | 10281927 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39549.6556 | 39554.3368 | CONT | 00017270 | FAULT | WO for SOR to hold out KGTS SVC | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028151339549.7319444444 | 10281513 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39549.7319 | 39549.7535 | DAILY | [12 empty] | 0
_X70858A939550.2493055556 | X70858A9 |  | Parent | FALSE | L4 220/22KV TRANS AT RTS | 39550.2493 | 39551.7361 | CONT | 00007333 | SPICAPX | replace Transformer Surge Arrestors | SPIPOWER | X708 | X708 - REPLACEMENT OF AGEING 22KV TO 500KV SURGE ARRESTERS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028005839550.2694444444 | 10280058 |  | Parent | FALSE | EX - BLTS 220KV LINE AT KTS | 39550.2694 | 39550.8375 | DAILY | 00015980 | SPIMAINT | replace G/W's between T38 & T40 | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56958B039550.2916666667 | X56958B0 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39550.2917 | 39550.6771 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 1 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028193039551.2652777778 | 10281930 |  | Parent | FALSE | W1 GEN TRANS NO.1 BUS 220KV CB AT YPS | 39551.2653 | 39559.9382 | CONT | [12 empty] | 0
_1028006039551.2902777778 | 10280060 |  | Parent | FALSE | BLTS 220KV LINE AT ATS | 39551.2903 | 39551.7583 | DAILY | 00055536 | SPIMAINT | replace G/W's between T38 & T40 | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56958B039551.2965277778 | X56958B0 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39551.2965 | 39551.7063 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 1 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70858B339551.3013888889 | X70858B3 |  | Parent | FALSE | B4 220/66KV TRANS AT TTS | 39551.3014 | 39551.6715 | DAILY | 00001543 | SPICAPX | replace 66kv Surge Arrestors | SPIPOWER | X708 | X708 - REPLACEMENT OF AGEING 22KV TO 500KV SURGE ARRESTERS | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028263639552.2909722222 | 10282636 | X70858B0 | Child | FALSE | KTS NO.1 220KV LINE AT WMTS | 39552.291 | 39556.6674 | CONT | 00025734 | SPICAPX | replace Surge Arrestors | SPIPOWER | X708 | X708 - REPLACEMENT OF AGEING 22KV TO 500KV SURGE ARRESTERS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70858B039552.2909722222 | X70858B0 |  | Parent | TRUE | KTS NO.1 220KV LINE CB AT WMTS | 39552.291 | 39556.6674 | CONT | [12 empty] | 0
_X49758L339552.3763888889 | X49758L3 |  | Parent | FALSE | BATS 220KV LINE NO.1 BUS CB AT BETS | 39552.3764 | 39553.6139 | CONT | [12 empty] | 0
_1026717939553.2881944444 | 10267179 |  | Parent | FALSE | SHTS NO.1 220KV LINE AT GNTS | 39553.2882 | 39553.7403 | DAILY | 00021792 | SPIMAINT | O/Haul SHTS NO.1 220KV LINE AT GNTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026816639553.2944444444 | 10268166 |  | Parent | TRUE | ROTS NO.5 220KV LINE AT YPS | 39553.2944 | 39553.6542 | DAILY | 00016413 | SPIMAINT | Overhaul ROTS No 5 220 Kv Line at YPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028652139553.2944444444 | 10286521 | 10268166 | Child | FALSE | ROTS NO.5 220KV LINE NO.2 BUS CB LINE SIDE ROI AT YPS | 39553.2944 | 39553.6542 | DAILY | [12 empty] | 0
_1027002639553.2965277778 | 10270026 |  | Parent | FALSE | 220KV TIE BUS AT NPSD | 39553.2965 | 39554.6882 | CONT | 00003080 | SPIMAINT | CL.1 O/HAUL - S&S SF6 GIS Bus & other Compartments | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_1027071039553.2986111111 | 10270710 |  | Parent | FALSE | EX - A4 TRANS/B2 TRANS 220KV CB AT KTS | 39553.2986 | 39554.5715 | CONT | [12 empty] | 0
_1027336339553.3208333333 | 10273363 |  | Parent | FALSE | EX - BATS NO.1 220KV LINE/TGTS 220KV LINE CB CT R/PH AT MLTS | 39553.3208 | 39553.3792 | DAILY | [12 empty] | 0
_1028184339553.3333333333 | 10281843 |  | Parent | TRUE | EX - A3 TRANS 220KV CB AT KTS | 39553.3333 | 39553.6243 | DAILY | [12 empty] | 0
_1028263839553.3333333333 | 10282638 | 10281843 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 39553.3333 | 39553.6243 | DAILY | 00026097 | SPIMAINT | air leak in cb mechanism | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027335139553.3826388889 | 10273351 |  | Parent | FALSE | EX - A1 TRANS NO.1 BUS 220KV CB CT R/PH AT MLTS | 39553.3826 | 39553.4417 | DAILY | [12 empty] | 0
_1010670239553.5423611111 | 10106702 | 10281878 | Child | FALSE | S003 YPS -YWPS 2 220KV | 39553.5424 | 39555.6458 | DAILY | [12 empty] | 0
_1028187839553.5423611111 | 10281878 |  | Parent | TRUE | YWPS NO.2 220KV LINE AT YPS | 39553.5424 | 39555.6458 | DAILY | 00016424 | SPIMAINT | W2 - YPS No 2 220kv Line | SPIPOWER |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028151439553.5472222222 | 10281514 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39553.5472 | 39553.5722 | DAILY | [12 empty] | 0
_X55658F139554.2854166667 | X55658F1 |  | Parent | FALSE | BH 66KV FDR CB AT RWTS | 39554.2854 | 39554.7625 | DAILY | [12 empty] | 0
_1027083439554.30625 | 10270834 |  | Parent | FALSE | B1 TRANS GROUP 220KV CB AT GNTS | 39554.3063 | 39554.6889 | REPDAILY | [12 empty] | 0
_1027994639554.3104166667 | 10279946 |  | Parent | FALSE | A2 GEN TRANS NO.1 BUS 500KV CB AT LYPS | 39554.3104 | 39554.5847 | DAILY | [12 empty] | 0
_1028184539554.3138888889 | 10281845 |  | Parent | FALSE | EX - SMTS LINE/A2 TRANS 500KV CB AT KTS | 39554.3139 | 39554.6604 | DAILY | [12 empty] | 0
_1027337939554.3291666667 | 10273379 |  | Parent | TRUE | EX - 220KV SHUNT REACTOR CB CT R/PH AT MLTS | 39554.3292 | 39554.3972 | DAILY | [12 empty] | 0
_1028265339554.3291666667 | 10282653 | 10273379 | Child | FALSE | 220KV SHUNT REACTOR AT MLTS | 39554.3292 | 39554.3972 | DAILY | 00003011 | SPIMAINT | CT OIL SAMPLING | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028189339554.3368055556 | 10281893 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39554.3368 | 39560.7097 | CONT | 00017270 | SPIMAINT | Disconn Leads between Wall Bushings & Thyristors | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027335739554.4479166667 | 10273357 |  | Parent | TRUE | EX - BATS NO.2 220KV LINE CB CT R/PH AT MLTS | 39554.4479 | 39554.5 | DAILY | [12 empty] | 0
_1028265139554.4479166667 | 10282651 | 10273357 | Child | FALSE | BATS NO.2 220KV LINE AT MLTS | 39554.4479 | 39554.5 | DAILY | 00022969 | SPIMAINT | Rebate CT OIL SAMPLING | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027995039554.5395833333 | 10279950 |  | Parent | FALSE | A3 GEN TRANS NO.1 BUS 500KV CB AT LYPS | 39554.5396 | 39554.7208 | DAILY | [12 empty] | 0
_1028200039554.6680555556 | 10282000 |  | Parent | FALSE | AUX B 220KV TRANS LINE AT HWPS | 39554.6681 | 39555.5815 | CONT | 00356087 | FORCED | Aux Trans B | SPIPOWER |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X67058A039554.6680555556 | X67058A0 |  | Parent | TRUE | JLTS NO.1 LINE/AUX TRANS 'B' 220KV CB AT HWPS | 39554.6681 | 39556.0132 | CONT | [12 empty] | 0
_X67058A139554.6680555556 | X67058A1 | X67058A0 | Child | FALSE | JLTS NO.1 220KV LINE AT HWPS | 39554.6681 | 39556.0132 | CONT | 00015784 | FORCED | Line outage rebate for Aux Trans B CTs faulty | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658E939554.6736111111 | X55658E9 |  | Parent | FALSE | BRA 66KV FDR CB AT RWTS | 39554.6736 | 39562.3083 | CONT | [12 empty] | 0
_1028200539554.98125 | 10282005 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 39554.9812 | 39559.0764 | CONT | 00356083 | GENCO | Isolation & Earthing | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028200739555.0013888889 | 10282007 |  | Parent | FALSE | JLA NO.2 220KV LINE AT TBTS | 39555.0014 | 39555.0931 | CONT | 00026919 | FAULT | TRIPPING OF TBTS-JLA No2 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027578339555.2868055556 | 10275783 |  | Parent | TRUE | S011 HWPS-YPS 1 220KV | 39555.2868 | 39555.2944 | DAILY | [12 empty] | 0
_1028187639555.2868055556 | 10281876 | 10275783 | Child | FALSE | YPS NO.1 220KV LINE AT HWPS | 39555.2868 | 39555.2944 | DAILY | 00015795 | SPIMAINT | Rebate for Line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027071539555.2930555556 | 10270715 |  | Parent | FALSE | EX - A4 TRANS NO.3 BUS 220KV CB AT KTS | 39555.2931 | 39556.6722 | CONT | [12 empty] | 0
_1026924239555.3013888889 | 10269242 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT TSTS | 39555.3014 | 39555.6014 | DAILY | [12 empty] | 0
_1027083439555.3076388889 | 10270834 |  | Parent | FALSE | B1 TRANS GROUP 220KV CB AT GNTS | 39555.3076 | 39555.7521 | REPDAILY | [12 empty] | 0
_1027178339555.3138888889 | 10271783 |  | Parent | FALSE | B3 TRANS 66KV CB AT KTS | 39555.3139 | 39555.625 | DAILY | [12 empty] | 0
_1026756339555.3263888889 | 10267563 |  | Parent | FALSE | NO.1 AUX TRANS 220KV BUS AT NPSD | 39555.3264 | 39555.6806 | DAILY | 00020456 | SPIMAINT | CL.1 O/HAUL - S&S SF6 GIS Bus & other Compartments | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_1027995139555.3298611111 | 10279951 |  | Parent | FALSE | A2 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39555.3299 | 39555.5181 | DAILY | [12 empty] | 0
_1027337539555.3423611111 | 10273375 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE/A1 TRANS CB CT R/PH AT MLTS | 39555.3424 | 39555.4021 | DAILY | [12 empty] | 0
_1027995239555.51875 | 10279952 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39555.5188 | 39555.6597 | DAILY | [12 empty] | 0
_1027332939555.5666666667 | 10273329 |  | Parent | FALSE | EX - B4 TRANS 220KV CB CT R/PH AT GTS | 39555.5667 | 39555.6319 | DAILY | [12 empty] | 0
_1026923739556.2965277778 | 10269237 |  | Parent | FALSE | 1-4 66KV BUS TIE CB AT TSTS | 39556.2965 | 39556.6438 | DAILY | [12 empty] | 0
_1028012339556.3 | 10280123 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39556.3 | 39556.7562 | DAILY | 00337584 | SPIMAINT | SCAN - 2a Trans 220kv B ph LA High RF | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027077639556.30625 | 10270776 |  | Parent | FALSE | NO.1 TRANS GROUP 66KV CB AT GNTS | 39556.3063 | 39556.6507 | DAILY | [12 empty] | 0
_1027330539556.3215277778 | 10273305 |  | Parent | TRUE | EX - NPSD 220KV LINE CB CT R/PH AT FBTS | 39556.3215 | 39556.4111 | DAILY | [12 empty] | 0
_1028265639556.3215277778 | 10282656 | 10273305 | Child | FALSE | NPSD 220KV LINE AT FBTS | 39556.3215 | 39556.4111 | DAILY | 00002662 | SPIMAINT | Rebate - CT OIL SAMPLING | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56958A339556.3243055556 | X56958A3 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39556.3243 | 39556.8146 | REPDAILY | 00060188 | SPICAPX | Out W/O JDSS-WOTS Line OPGW - Run 1 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027339539556.4347222222 | 10273395 |  | Parent | FALSE | SHTS NO.3 220KV LINE NO.2 BUS CB CT R/PH AT GNTS | 39556.4347 | 39556.4931 | DAILY | [12 empty] | 0
_1028151539556.5465277778 | 10281515 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39556.5465 | 39556.5674 | DAILY | [12 empty] | 0
_1028210139557.0180555556 | 10282101 |  | Parent | FALSE | NO.3 GEN 220/16.5KV TRANS AT HWPS | 39557.0181 | 39617.6618 | CONT | 00009644 | GENCO | HWPS Unit3 SCAP | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_X50858A739557.2333333333 | X50858A7 |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 39557.2333 | 39557.641 | CONT | 00002834 | SPICAPX | Remove 220kv Connections, Bi pods and structures | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858A839557.2333333333 | X50858A8 | X50858A7 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39557.2333 | 39557.641 | CONT | 00002830 | SPICAPX | Perf Calc No4 Trans, during No2 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858A939557.2333333333 | X50858A9 | X50858A7 | Child | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39557.2333 | 39557.641 | CONT | 00017905 | SPICAPX | Rebate W/O, PTH No1 Ln during No2 220 bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858B039557.2333333333 | X50858B0 | X50858A7 | Child | FALSE | EX - MLTS NO.1 220KV LINE AT GTS | 39557.2333 | 39557.641 | CONT | 00017903 | SPICAPX | Rebate W/O, MLTS No1 Ln during No2 220 bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858B239557.2333333333 | X50858B2 | X50858A7 | Child | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39557.2333 | 39557.641 | CONT | 00017900 | SPICAPX | Rebate W/O, KTS No1 Ln during No2 220 bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z54558A539557.2916666667 | Z54558A5 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39557.2917 | 39557.5382 | DAILY | [12 empty] | 0
_1028186439557.2930555556 | 10281864 |  | Parent | FALSE | EX - NO.1 22KV/415V S/S TRANS AT WMTS | 39557.2931 | 39557.7103 | DAILY | 00003238 | SPIMAINT | VSCAP to Citipower | SPIPOWER |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1028266039558.2534722222 | 10282660 | X55658D5 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39558.2535 | 39558.4979 | DAILY | 00331179 | SPICAPX | Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X55658D539558.2534722222 | X55658D5 |  | Parent | TRUE | NO.2 66KV BUS AT RWTS | 39558.2535 | 39558.4979 | DAILY | 00007479 | SPICAPX | Bus outage & Future Sub CYN No 1 CB | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 |  |  |  | 0
_X55658D639558.2534722222 | X55658D6 | X55658D5 | Child | FALSE | B3 220/66KV TRANS AT RWTS | 39558.2535 | 39558.4979 | DAILY | 00007455 | SPICAPX | Trans Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X55658L039558.2534722222 | X55658L0 | X55658D5 | Child | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39558.2535 | 39558.4979 | DAILY | 00007399 | SPICAPX | Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028022139558.2881944444 | 10280221 |  | Parent | TRUE | NO.1 66KV BUS AT TSTS | 39558.2882 | 39558.6 | DAILY | 00007672 | SPIMAINT | Replace Sub BU Fdr CB Bus Droppers o/haul SLF fdr | SPIPOWER |  |  | Bus | Eastern | 66 |  |  |  | 0
_1028022739558.2881944444 | 10280227 | 10280221 | Child | FALSE | B1 220/66KV TRANS AT TSTS | 39558.2882 | 39558.6 | DAILY | 00007657 | SPIMAINT | rebate trans for bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028265839558.2881944444 | 10282658 | 10280221 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT TSTS | 39558.2882 | 39558.6 | DAILY | 00351937 | SPIMAINT | rebate for bus outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_Z53358A439558.2944444444 | Z53358A4 |  | Parent | FALSE | HWPS-ROTS 1 220KV G | 39558.2944 | 39558.7799 | REPDAILY | 00020454 | GEN_AUG | Errect a New Tower | SPIPOWER | Z533 | Z533 - (HWPS-ROTS) LINE 3 HW MINE EXTENSION - ST2 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028210739558.3333333333 | 10282107 |  | Parent | TRUE | MLTS NO.2 500KV LINE CB AT HYTS | 39558.3333 | 39558.3833 | CONT | [12 empty] | 0
_1028210839558.3333333333 | 10282108 | 10282107 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 39558.3333 | 39558.3833 | CONT | 00002862 | FORCED | MLTS NO.2 500KV LINE NO.2 BUS CB to Top Up SF6 | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X55658A339558.4590277778 | X55658A3 |  | Parent | FALSE | CYN NO.1 66KV FDR CB AT RWTS | 39558.459 | 39578.3674 | CONT | [12 empty] | 0
_1028204039558.6680555556 | 10282040 |  | Parent | FALSE | EX - LDL NO.1 66KV FDR CB AT RWTS | 39558.6681 | 39562.4881 | CONT | [12 empty] | 0
_1027304939559.2965277778 | 10273049 |  | Parent | FALSE | B4 220/66KV TRANS AT SHTS | 39559.2965 | 39561.5813 | CONT | 00350590 | SPIMAINT | Condition Monitoring Country Trans 2day North Area | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53358A439559.3090277778 | Z53358A4 |  | Parent | FALSE | HWPS-ROTS 1 220KV G | 39559.309 | 39559.666 | REPDAILY | 00020454 | GEN_AUG | Errect a New Tower | SPIPOWER | Z533 | Z533 - (HWPS-ROTS) LINE 3 HW MINE EXTENSION - ST2 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027327739559.3131944445 | 10273277 |  | Parent | TRUE | NO.4 220KV CAPACITOR BANK CB CT R/PH AT FBTS | 39559.3132 | 39559.5069 | DAILY | [12 empty] | 0
_1028267339559.3131944445 | 10282673 | 10273277 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 39559.3132 | 39559.5069 | DAILY | 00327661 | SPIMAINT | Rebate - CT OIL SAMPLING | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027995439559.3138888889 | 10279954 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.1 BUS CB AT LYPS | 39559.3139 | 39560.4056 | CONT | [12 empty] | 0
_1027072539559.3208333333 | 10270725 |  | Parent | FALSE | EX - ATS LINE/A2 TRANS 220KV CB AT KTS | 39559.3208 | 39560.6681 | CONT | [12 empty] | 0
_1027003539559.3284722222 | 10270035 |  | Parent | FALSE | 220KV TIE BUS NO.1 BUS CB AT NPSD | 39559.3285 | 39559.6444 | DAILY | [12 empty] | 0
_1028151639559.3298611111 | 10281516 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39559.3299 | 39559.3757 | DAILY | [12 empty] | 0
_1027262539559.3618055556 | 10272625 |  | Parent | FALSE | NO.1 TRANS 66KV CB AT KGTS | 39559.3618 | 39559.6917 | DAILY | [12 empty] | 0
_1028214939559.5444444444 | 10282149 |  | Parent | FALSE | SYN/COND AT BLTS | 39559.5444 | 39559.616 | DAILY | 00002547 | FAULT | BLTS: SynCon Prot Trip | SPIPOWER |  |  | Sync Condensers | 3rd Party | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027329939559.5520833333 | 10273299 |  | Parent | FALSE | EX - 1-3 220KV BUS TIE CB CT R/PH AT FBTS | 39559.5521 | 39559.6201 | DAILY | [12 empty] | 0
_1028146739560.2916666667 | 10281467 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39560.2917 | 39560.4931 | DAILY | 00002863 | SPIMAINT | Inspect/clean inside S/S cubicles of moisture | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027326539560.3131944445 | 10273265 |  | Parent | TRUE | EX - NO.4 220KV CAPACITOR BANK CB CT R/PH AT BLTS | 39560.3132 | 39560.4993 | DAILY | [12 empty] | 0
_1028267539560.3131944445 | 10282675 | 10273265 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT BLTS | 39560.3132 | 39560.4993 | DAILY | 00327921 | SPIMAINT | Rebate - CT OIL SAMPLING | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027003739560.3201388889 | 10270037 |  | Parent | FALSE | 220KV TIE BUS NO.2 BUS CB AT NPSD | 39560.3201 | 39560.6576 | DAILY | [12 empty] | 0
_1027262739560.3534722222 | 10272627 |  | Parent | FALSE | NO.2 TRANS NO.1 BUS 66KV CB AT KGTS | 39560.3535 | 39560.6118 | DAILY | [12 empty] | 0
_1027995639560.40625 | 10279956 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.2 BUS CB AT LYPS | 39560.4062 | 39560.6201 | DAILY | [12 empty] | 0
_1028146839560.4965277778 | 10281468 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39560.4965 | 39560.6479 | DAILY | 00002862 | SPIMAINT | Inspect/clean S/S cubicles of moisture inside | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027326739560.5444444444 | 10273267 |  | Parent | FALSE | 1A-2A 220KV BUS TIE CB CT R/PH AT BLTS | 39560.5444 | 39560.6242 | DAILY | [12 empty] | 0
_1028208639560.7097222222 | 10282086 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39560.7097 | 39562.6778 | DAILY | 00017270 | SPIMAINT | Pre Commissioning Testing and Reconnections, SVC | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027578339561.2861111111 | 10275783 |  | Parent | TRUE | S011 HWPS-YPS 1 220KV | 39561.2861 | 39561.584 | DAILY | [12 empty] | 0
_1028187639561.2861111111 | 10281876 | 10275783 | Child | FALSE | YPS NO.1 220KV LINE AT HWPS | 39561.2861 | 39561.584 | DAILY | 00015795 | SPIMAINT | Rebate for Line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058Z139561.2944444444 | X32058Z1 |  | Parent | FALSE | U2 66/22KV TRANS AT MTS | 39561.2944 | 39561.6458 | REPDAILY | 00363319 | SPIMAINT | U 2 Trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027178139561.3145833333 | 10271781 |  | Parent | FALSE | B4 TRANS NO.1 BUS 220KV CB AT KTS | 39561.3146 | 39562.659 | CONT | [12 empty] | 0
_1027006739561.3159722222 | 10270067 |  | Parent | FALSE | GEN TRANS NO.1 BUS CB AT NPSD | 39561.316 | 39561.6174 | DAILY | [12 empty] | 0
_X46158Q739561.3166666667 | X46158Q7 |  | Parent | FALSE | TGTS 220KV LINE NO.1 BUS CB AT BATS | 39561.3167 | 39561.659 | DAILY | [12 empty] | 0
_X46158Q839561.3166666667 | X46158Q8 |  | Parent | FALSE | TGTS 220KV LINE AT BATS | 39561.3167 | 39561.659 | DAILY | 00012435 | SPICAPX | Out W/O TGTS Line during CB & Tie outage | SPIPOWER | X461 | X461 - (BATS) TERMINAL STATION REBUILD | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027995839561.3236111111 | 10279958 |  | Parent | FALSE | 2-4 500KV BUS TIE CB AT LYPS | 39561.3236 | 39561.5111 | DAILY | [12 empty] | 0
_1027262939561.3402777778 | 10272629 |  | Parent | FALSE | NO.2 TRANS NO.2 BUS 66KV CB AT KGTS | 39561.3403 | 39561.4924 | DAILY | [12 empty] | 0
_1028216839561.3527777778 | 10282168 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 39561.3528 | 39561.3792 | DAILY | [12 empty] | 0
_1027327139561.4104166667 | 10273271 |  | Parent | FALSE | 3-5 220KV BUS TIE CB CT R/PH AT BLTS | 39561.4104 | 39561.4583 | DAILY | [12 empty] | 0
_1028198939561.44375 | 10281989 |  | Parent | TRUE | NO.1 66KV BUS AT TGTS | 39561.4437 | 39561.4847 | DAILY | 00364790 | SPIMAINT | Out W/O No1 66 BUS de-energ to commiss new Cap CB | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1028199039561.44375 | 10281990 | 10281989 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39561.4437 | 39561.4847 | DAILY | 00363297 | SPIMAINT | Perf calc W/O B1 Trans during bus de-energ | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027996039561.5111111111 | 10279960 |  | Parent | TRUE | HWTS NO.2 500KV LINE CB AT LYPS | 39561.5111 | 39561.6778 | DAILY | [12 empty] | 0
_1027996139561.5111111111 | 10279961 | 10279960 | Child | FALSE | HWTS NO.2 500KV LINE AT LYPS | 39561.5111 | 39561.6778 | DAILY | 00016087 | SPIMAINT | REBATE LINE FOR CB OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028214139561.8819444444 | 10282141 | X67058A4 | Child | FALSE | JLTS NO.1 220KV LINE AT HWPS | 39561.8819 | 39562.6965 | CONT | 00015784 | SPIMAINT | Line outage rebate for Aux Trans B CTs faulty | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X67058A339561.8819444444 | X67058A3 |  | Parent | TRUE | EX - AUX C 220KV TRANS LINE CT R/PH AT HWPS | 39561.8819 | 39562.6965 | DAILY | [12 empty] | 0
_X67058A439561.8819444444 | X67058A4 | X67058A3 | Child | TRUE | JLTS NO.3 220KV LINE AT HWPS | 39561.8819 | 39562.6965 | DAILY | 00015787 | SPICAPX | REBATE FOR HWPS-JLTS No3 LINE (CT CHANGE) | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z54358A839562.2513888889 | Z54358A8 |  | Parent | TRUE | NO.2 220KV BUS AT MLTS | 39562.2514 | 39562.6514 | REPDAILY | 00003015 | VEN_AUG | Uprate connections in Bay H for Fut A2 Trans | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z54358A939562.2513888889 | Z54358A9 | Z54358A8 | Child | FALSE | NO.2 220KV CAPACITOR BANK CB AT MLTS | 39562.2514 | 39562.6514 | REPDAILY | [12 empty] | 0
_Z54358B039562.2513888889 | Z54358B0 | Z54358A8 | Child | FALSE | BATS NO.2 220KV LINE AT MLTS | 39562.2514 | 39562.6514 | REPDAILY | 00022969 | VEN_AUG | Rebate W/O, BATS 2 LN during No2 220 Bus outage | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658F239562.2708333333 | X55658F2 |  | Parent | FALSE | CYN NO.2 66KV FDR CB AT RWTS | 39562.2708 | 39562.5312 | DAILY | [12 empty] | 0
_1027327339562.3145833333 | 10273273 |  | Parent | FALSE | 4-5 220KV BUS TIE CB CT R/PH AT BLTS | 39562.3146 | 39562.3847 | DAILY | [12 empty] | 0
_1027263139562.3416666667 | 10272631 |  | Parent | FALSE | NO.3 TRANS 66KV CB AT KGTS | 39562.3417 | 39562.5 | DAILY | [12 empty] | 0
_X55658F639562.4736111111 | X55658F6 |  | Parent | FALSE | EX - LDL NO.1 66KV FDR CB AT RWTS | 39562.4736 | 39582.7917 | CONT | [12 empty] | 0
_X55658F339562.5506944444 | X55658F3 |  | Parent | FALSE | BRA 66KV FDR CB AT RWTS | 39562.5507 | 39562.5625 | CONT | [12 empty] | 0
_1028151739562.5527777778 | 10281517 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39562.5528 | 39562.5674 | DAILY | [12 empty] | 0
_V77558A939562.5527777778 | V77558A9 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT TBTS | 39562.5528 | 39562.7667 | DAILY | 00351938 | SPIMAINT | No1 66 Cap bank during setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X56958B139564.2958333333 | X56958B1 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39564.2958 | 39564.7333 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 2 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028228939564.9833333333 | 10282289 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT RTS | 39564.9833 | 39566.3486 | CONT | 00007335 | FAULT | RTS: Tripping of No1 S/S Trans | SPIPOWER |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_1028229839565.1527777778 | 10282298 |  | Parent | FALSE | SYN/COND AT BLTS | 39565.1528 | 39565.4333 | CONT | 00002547 | FAULT | Tripped Syn / Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X56958B139565.2916666667 | X56958B1 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39565.2917 | 39565.5833 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 2 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028485239566.3048611111 | 10284852 |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 39566.3049 | 39644.2917 | CONT | [12 empty] | 0
_1028199239566.3145833333 | 10281992 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39566.3146 | 39566.3576 | DAILY | [12 empty] | 0
_1026753739567.2861111111 | 10267537 | 10270024 | Child | FALSE | NO.2 AUX TRANS 220KV BUS AT NPSD | 39567.2861 | 39567.7 | DAILY | 00020470 | SPIMAINT | O/H BUS | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_1027002439567.2861111111 | 10270024 |  | Parent | TRUE | NO.2 220KV BUS AT NPSD | 39567.2861 | 39567.7 | REPDAILY | 00003079 | SPIMAINT | CL.1 O/HAUL - S&S SF6 GIS Bus & other Compartments | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_1028267739567.2861111111 | 10282677 | 10270024 | Child | FALSE | FBTS 220KV LINE AT NPSD | 39567.2861 | 39567.7 | REPDAILY | 00024003 | SPIMAINT | Rebate for Bus outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027577739567.2868055556 | 10275777 |  | Parent | TRUE | S021 HWPS-YPS 2 220KV | 39567.2868 | 39567.6813 | DAILY | [12 empty] | 0
_1028194539567.2868055556 | 10281945 | 10275777 | Child | FALSE | YPS NO.2 220KV LINE AT HWPS | 39567.2868 | 39567.6813 | DAILY | 00015796 | SPIMAINT | line rebate | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026625939567.2965277778 | 10266259 |  | Parent | FALSE | B2 TRANS 220KV ISOL AT ATS | 39567.2965 | 39567.6583 | REPDAILY | [12 empty] | 0
_1028219239568.275 | 10282192 |  | Parent | FALSE | W3 GEN TRANS NO.1 BUS 220KV CB AT YPS | 39568.275 | 39569.0014 | CONT | [12 empty] | 0
_1026753739568.2819444445 | 10267537 | 10270024 | Child | FALSE | NO.2 AUX TRANS 220KV BUS AT NPSD | 39568.2819 | 39568.6715 | DAILY | 00020470 | SPIMAINT | O/H BUS | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_1027002439568.2819444445 | 10270024 |  | Parent | TRUE | NO.2 220KV BUS AT NPSD | 39568.2819 | 39568.6715 | REPDAILY | 00003079 | SPIMAINT | CL.1 O/HAUL - S&S SF6 GIS Bus & other Compartments | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_1028267739568.2819444445 | 10282677 | 10270024 | Child | FALSE | FBTS 220KV LINE AT NPSD | 39568.2819 | 39568.6715 | REPDAILY | 00024003 | SPIMAINT | Rebate for Bus outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026625939568.2944444444 | 10266259 |  | Parent | FALSE | B2 TRANS 220KV ISOL AT ATS | 39568.2944 | 39568.5889 | REPDAILY | [12 empty] | 0
_1027266939568.2958333333 | 10272669 |  | Parent | TRUE | MBTS NO.2 220KV LINE CB AT EPSY | 39568.2958 | 39568.7576 | DAILY | [12 empty] | 0
_1028194039568.2958333333 | 10281940 | 10272669 | Child | FALSE | MBTS NO.2 220KV LINE AT EPSY | 39568.2958 | 39568.7576 | DAILY | 00087036 | SPIMAINT | Rebate W/O MBTS No2 Line during CB, Isol & Esw OH | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1026927939568.3 | 10269279 |  | Parent | TRUE | U1 TRANS 22KV CB AT RWTS | 39568.3 | 39568.5965 | DAILY | [12 empty] | 0
_1028211039568.3 | 10282110 | 10269279 | Child | FALSE | U1 66/22KV TRANS AT RWTS | 39568.3 | 39568.5965 | DAILY | 00007456 | SPIMAINT | rebate tran outage | SPIPOWER |  |  | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56958A639568.3034722222 | X56958A6 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39568.3035 | 39568.784 | DAILY | 00060188 | SPICAPX | Out W/O JDSS-WOTS Line OPGW - Run 4 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027996239568.3041666667 | 10279962 |  | Parent | FALSE | ROTS NO.5 220KV LINE AT YPS | 39568.3042 | 39568.65 | DAILY | 00016413 | SPIMAINT | ROTS NO.5 220KV LINE CT's | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026902039568.325 | 10269020 |  | Parent | FALSE | NO.3 GEN TRANS 500KV LINE E/SW AT LYPS | 39568.325 | 39570.5549 | CONT | [12 empty] | 0
_1028241139568.7347222222 | 10282411 |  | Parent | FALSE | MBTS NO.2 220KV LINE CB BUS SIDE ROI AT EPSY | 39568.7347 | 39568.7556 | DAILY | [12 empty] | 0
_1028245539568.9645833333 | 10282455 |  | Parent | FALSE | NO.6 GEN TRANS NO.4 BUS 220KV CB BUS SIDE ISOL AT HWPS | 39568.9646 | 39573.0521 | CONT | [12 empty] | 0
_1026753739569.2805555556 | 10267537 | 10270024 | Child | FALSE | NO.2 AUX TRANS 220KV BUS AT NPSD | 39569.2806 | 39569.9993 | DAILY | 00020470 | SPIMAINT | O/H BUS | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_1027002439569.2805555556 | 10270024 |  | Parent | TRUE | NO.2 220KV BUS AT NPSD | 39569.2806 | 39569.9993 | REPDAILY | 00003079 | SPIMAINT | CL.1 O/HAUL - S&S SF6 GIS Bus & other Compartments | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_1028267739569.2805555556 | 10282677 | 10270024 | Child | FALSE | FBTS 220KV LINE AT NPSD | 39569.2806 | 39569.9993 | REPDAILY | 00024003 | SPIMAINT | Rebate for Bus outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027288139569.2847222222 | 10272881 |  | Parent | TRUE | MBTS NO.1 220KV LINE CB AT EPSY | 39569.2847 | 39569.6896 | REPDAILY | [12 empty] | 0
_1028193939569.2847222222 | 10281939 | 10272881 | Child | FALSE | MBTS NO.1 220KV LINE AT EPSY | 39569.2847 | 39569.6896 | DAILY | 00087035 | SPIMAINT | Rebate W/O MBTS No1 Line during CB, Isol & Esw OH | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1027996639569.2909722222 | 10279966 |  | Parent | FALSE | ROTS NO.6 220KV LINE AT YPS | 39569.291 | 39569.5514 | DAILY | 00016414 | SPIMAINT | ROTS NO.6 220KV LINE CT's | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027177739569.2916666667 | 10271777 |  | Parent | FALSE | B4 TRANS NO.1 BUS 220KV CB TRANS SIDE ROI AT KTS | 39569.2917 | 39570.4528 | CONT | [12 empty] | 0
_1028216439569.2986111111 | 10282164 |  | Parent | TRUE | NO.2 TRANS 220KV E/SW AT TSTS | 39569.2986 | 39569.6215 | DAILY | [12 empty] | 0
_1028218139569.2986111111 | 10282181 | 10282164 | Child | FALSE | B2 220/66KV TRANS AT TSTS | 39569.2986 | 39569.6215 | DAILY | 00007658 | SPIMAINT | Rebate for No1 220kv Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028219539569.2986111111 | 10282195 | 10282164 | Child | TRUE | NO.1 220KV CAPACITOR BANK AT TSTS | 39569.2986 | 39569.6215 | DAILY | 00329164 | SPIMAINT | Rebate Cap Bank for No1 220kv Bus outage | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028219639569.2986111111 | 10282196 | 10282195 | Child | FALSE | NO.2 TRANS 220KV E/SW AT TSTS | 39569.2986 | 39569.6215 | DAILY | [12 empty] | 0
_X56958A739569.3145833333 | X56958A7 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39569.3146 | 39569.6319 | REPDAILY | 00060188 | SPICAPX | Out W/O JDSS-WOTS Line OPGW - Run 5 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028243339569.3152777778 | 10282433 | 10273397 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39569.3153 | 39569.4271 | DAILY | 00112417 | SPIMAINT | REBATE FOR CAP BANK OUTAGE | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027339739569.3152777778 | 10273397 |  | Parent | TRUE | EX - NO.3 220KV CAPACITOR BANK CB CT R/PH AT ROTS | 39569.3153 | 39569.4277 | DAILY | [12 empty] | 0
_1028232939569.3326388889 | 10282329 |  | Parent | TRUE | EX - NO.2 66KV CAPACITOR BANK CB AT WMTS | 39569.3326 | 39570.634 | CONT | [12 empty] | 0
_1028312839569.3326388889 | 10283128 | 10282329 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT WMTS | 39569.3326 | 39570.634 | CONT | 00074391 | SPIMAINT | out w/o for cap bank assoc with cb timing with abb | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028247839569.3715277778 | 10282478 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39569.3715 | 39569.4306 | DAILY | 00016040 | FAULT | No 2 Trans Trip | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028250239569.4701388889 | 10282502 |  | Parent | FALSE | YWPS NO.3 220KV LINE AT YPS | 39569.4701 | 39570.8611 | CONT | 00016426 | GENCO | W3 isolation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026753739570 | 10267537 | 10270024 | Child | FALSE | NO.2 AUX TRANS 220KV BUS AT NPSD | 39570 | 39570.6583 | DAILY | 00020470 | SPIMAINT | O/H BUS | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_1027002439570 | 10270024 |  | Parent | TRUE | NO.2 220KV BUS AT NPSD | 39570 | 39570.6583 | REPDAILY | 00003079 | SPIMAINT | CL.1 O/HAUL - S&S SF6 GIS Bus & other Compartments | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_1028267739570 | 10282677 | 10270024 | Child | FALSE | FBTS 220KV LINE AT NPSD | 39570 | 39570.6583 | REPDAILY | 00024003 | SPIMAINT | Rebate for Bus outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027996739570.2902777778 | 10279967 |  | Parent | FALSE | ROTS NO.7 220KV LINE AT YPS | 39570.2903 | 39570.5507 | DAILY | 00016415 | SPIMAINT | ROTS NO.7 220KV LINE CT's | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027288139570.2930555556 | 10272881 |  | Parent | TRUE | MBTS NO.1 220KV LINE CB AT EPSY | 39570.2931 | 39570.5708 | REPDAILY | [12 empty] | 0
_1028193939570.2930555556 | 10281939 | 10272881 | Child | FALSE | MBTS NO.1 220KV LINE AT EPSY | 39570.2931 | 39570.5708 | DAILY | 00087035 | SPIMAINT | Rebate W/O MBTS No1 Line during CB, Isol & Esw OH | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X56958A739570.3055555556 | X56958A7 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39570.3056 | 39570.7785 | REPDAILY | 00060188 | SPICAPX | Out W/O JDSS-WOTS Line OPGW - Run 5 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458B339570.3270833333 | V60458B3 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT SMTS | 39570.3271 | 39584.5 | CONT | [12 empty] | 0
_1028199439570.3416666667 | 10281994 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39570.3417 | 39570.3792 | DAILY | [12 empty] | 0
_1028209039570.3604166667 | 10282090 | V60458C2 | Child | FALSE | SYTS NO.2 500KV LINE AT SMTS | 39570.3604 | 39570.5153 | DAILY | 00012440 | SPICAPX | child workorder for other end of line | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458C239570.3604166667 | V60458C2 |  | Parent | TRUE | HWTS NO.2 500KV LINE AT SMTS | 39570.3604 | 39570.5153 | DAILY | 00012437 | SPICAPX | DEENERGISE LINE FOR HV TESTING | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028254239570.5625 | 10282542 |  | Parent | FALSE | 1A-2A 220KV BUS TIE CB CT R/PH AT BLTS | 39570.5625 | 39570.5875 | DAILY | [12 empty] | 0
_1024913539571.29375 | 10249135 |  | Parent | FALSE | KTS NO.2 220KV LINE CB NO.4 BUS SIDE E/SW AT WMTS | 39571.2937 | 39571.6167 | DAILY | [12 empty] | 0
_X56958B539571.29375 | X56958B5 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39571.2937 | 39571.7014 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 3 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028183939571.3493055556 | 10281839 |  | Parent | TRUE | EX - 66KV CAPACITOR BANK CB AT TGTS | 39571.3493 | 39571.575 | DAILY | [12 empty] | 0
_1028184239571.3493055556 | 10281842 | 10281839 | Child | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39571.3493 | 39571.575 | DAILY | 00003104 | SPIMAINT | Rebate W/O 66kV Cap Bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X50858A239572.25625 | X50858A2 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39572.2562 | 39572.7167 | DAILY | 00002833 | SPICAPX | Remove 220kv Connections, Bi pods and structures | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858A339572.25625 | X50858A3 | X50858A2 | Child | FALSE | B3 220/66KV TRANS AT GTS | 39572.2562 | 39572.7167 | CONT | 00002829 | SPICAPX | Perf Calc No3 Trans during No1 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858A439572.25625 | X50858A4 | X50858A2 | Child | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39572.2562 | 39572.7167 | CONT | 00017906 | SPICAPX | Rebate W/O PTH No2 Ln during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858A539572.25625 | X50858A5 | X50858A2 | Child | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39572.2562 | 39572.7167 | CONT | 00017901 | SPICAPX | Rebate W/O KTS No2 Ln during No1 220 Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858A639572.25625 | X50858A6 | X50858A2 | Child | FALSE | EX - MLTS NO.2 220KV LINE AT GTS | 39572.2562 | 39572.7167 | CONT | 00017904 | SPICAPX | Rebate W/O MLTS No2 Ln during No1 220 Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009265239572.2868055556 | 10092652 |  | Parent | TRUE | ROTS NO.2 220KV LINE AT ERTS | 39572.2868 | 39572.6389 | DAILY | 00012288 | SPIMAINT | O/H No4 220kv Bus, ROTS No2 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026943339572.2868055556 | 10269433 | 10092652 | Child | FALSE | NO.4 220KV BUS E/SW AT ERTS | 39572.2868 | 39572.6389 | DAILY | [12 empty] | 0
_X55658F739572.2923611111 | X55658F7 |  | Parent | TRUE | NO.4 66KV BUS AT RWTS | 39572.2924 | 39572.5924 | DAILY | 00007481 | SPICAPX | No 4 66kv Bus & Sub BWR CB | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X55658F839572.2923611111 | X55658F8 | X55658F7 | Child | FALSE | B4 220/66KV TRANS AT RWTS | 39572.2924 | 39572.5924 | DAILY | 00007451 | SPICAPX | Tran rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56958B539572.2930555556 | X56958B5 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39572.2931 | 39572.6458 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 3 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026998039572.2979166667 | 10269980 |  | Parent | FALSE | L3 220/22KV TRANS AT WMTS | 39572.2979 | 39572.6278 | DAILY | 00003237 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028227939572.3354166667 | 10282279 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT ATS | 39572.3354 | 39572.8424 | DAILY | 00060869 | DBPROX | VSCAP to Powercor | DISTCO |  |  | Other Transformers | Western | 22 |  |  |  | 0
_Z56258A039572.5104166667 | Z56258A0 |  | Parent | FALSE | MKPS-BOPS-MBTS 220KV NW | 39572.5104 | 39590.6819 | CONT | 00060197 | GEN_AUG | re sag MKPS Line | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658F939572.5888888889 | X55658F9 |  | Parent | FALSE | BRA 66KV FDR CB AT RWTS | 39572.5889 | 39593.3333 | CONT | [12 empty] | 0
_1026934439573.2673611111 | 10269344 |  | Parent | FALSE | NO.1 CSC 220/10.5KV TRANS AT ROTS | 39573.2674 | 39577.934 | CONT | 00004758 | SPIMAINT | CL.2 O/HAUL - ASEA HLR 245/250 CB | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1026935739573.2673611111 | 10269357 |  | Parent | FALSE | NO.1 CSC AT ROTS | 39573.2674 | 39577.934 | DAILY | 00004718 | SPIMAINT | Replace Defective insulators | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z63358A239573.2909722222 | Z63358A2 |  | Parent | FALSE | MWTS NO.2 220KV LINE AT JLTS | 39573.291 | 39574.6333 | CONT | 00015948 | VEN_AUG | MWTS 2 Line | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028216639573.2972222222 | 10282166 |  | Parent | FALSE | NO.2 11/6.6KV AUX TRANS AT TSTS | 39573.2972 | 39573.6243 | DAILY | 00007661 | SPIMAINT | REPAIR OIL LEAK | SPIPOWER |  |  | Other Transformers | Eastern | 11 |  |  |  | 0
_1028231239573.3020833333 | 10282312 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT KTS | 39573.3021 | 39573.6076 | DAILY | 00026096 | SPIMAINT | Inspect and top up white phase 220kV bushing | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009442739573.3027777778 | 10094427 | 10269622 | Child | FALSE | H1 TRANS NO.2 BUS 330KV CB BUS SIDE E/SW AT DDTS | 39573.3028 | 39573.709 | REPDAILY | [12 empty] | 0
_1009443739573.3027777778 | 10094437 | 10269622 | Child | FALSE | H1 TRANS NO.2 BUS 330KV CB BUS SIDE ROI AT DDTS | 39573.3028 | 39573.709 | REPDAILY | [12 empty] | 0
_1026873539573.3027777778 | 10268735 | 10269622 | Child | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB BUS SIDE ROI AT DDTS | 39573.3028 | 39573.709 | REPDAILY | [12 empty] | 0
_1026873739573.3027777778 | 10268737 | 10269622 | Child | FALSE | MSS NO.2 330KV LINE NO.2 BUS CB BUS SIDE ROI AT DDTS | 39573.3028 | 39573.709 | REPDAILY | [12 empty] | 0
_1026873939573.3027777778 | 10268739 | 10269622 | Child | FALSE | WOTS 330KV LINE NO.2 BUS CB BUS SIDE ROI AT DDTS | 39573.3028 | 39573.709 | REPDAILY | [12 empty] | 0
_1026874139573.3027777778 | 10268741 | 10269622 | Child | FALSE | H2 TRANS 330KV CB BUS SIDE ROI AT DDTS | 39573.3028 | 39573.709 | REPDAILY | [12 empty] | 0
_1026874339573.3027777778 | 10268743 | 10269622 | Child | FALSE | MSS NO.2 330KV LINE NO.2 BUS CB BUS SIDE E/SW AT DDTS | 39573.3028 | 39573.709 | REPDAILY | [12 empty] | 0
_1026877239573.3027777778 | 10268772 | 10269622 | Child | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB BUS SIDE E/SW AT DDTS | 39573.3028 | 39573.709 | REPDAILY | [12 empty] | 0
_1026877439573.3027777778 | 10268774 | 10269622 | Child | FALSE | WOTS 330KV LINE NO.2 BUS CB BUS SIDE E/SW AT DDTS | 39573.3028 | 39573.709 | REPDAILY | [12 empty] | 0
_1026878439573.3027777778 | 10268784 | 10269622 | Child | FALSE | NO.2 330KV BUS E/SW AT DDTS | 39573.3028 | 39573.709 | REPDAILY | [12 empty] | 0
_1026962239573.3027777778 | 10269622 |  | Parent | TRUE | NO.2 330KV BUS AT DDTS | 39573.3028 | 39573.709 | REPDAILY | 00003979 | SPIMAINT | O/Haul NO.2 330KV BUS AT DDTS | SPIPOWER |  |  | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028208339573.3027777778 | 10282083 | 10269622 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 39573.3028 | 39573.709 | REPDAILY | 00352121 | SPIMAINT | Perf Calc for H2 Trans during No2 220kv Bus Outage | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028208439573.3027777778 | 10282084 | 10269622 | Child | FALSE | NO.2 330KV CAPACITOR BANK AT DDTS | 39573.3028 | 39573.709 | REPDAILY | 00352093 | SPIMAINT | Rebate W/O for No2 Cap BK during No2 Bus Outage | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_Z54358B139573.3104166667 | Z54358B1 |  | Parent | FALSE | GTS NO.1 LINE/A2 TRANS 220KV CB AT MLTS | 39573.3104 | 39576.2514 | CONT | [12 empty] | 0
_1027306339573.3131944445 | 10273063 |  | Parent | FALSE | B4 220/66KV TRANS AT BLTS | 39573.3132 | 39574.6667 | CONT | 00002615 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area(W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028256039573.3326388889 | 10282560 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39573.3326 | 39573.7222 | DAILY | 00060188 | SPIMAINT | Extra outage for OPGW installation | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028208839573.3763888889 | 10282088 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39573.3764 | 39573.4181 | DAILY | [12 empty] | 0
_1028259739573.4631944444 | 10282597 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39573.4632 | 39574.4535 | CONT | 00356084 | GENCO | Isolation for GenCo | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028264239573.7395833333 | 10282642 |  | Parent | FALSE | SYN/COND AT BLTS | 39573.7396 | 39573.7792 | DAILY | 00002547 | FAULT | Protection Trip of Syn Cond at BLTS | SPIPOWER |  |  | Sync Condensers | 3rd Party | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X32058S339574.2527777778 | X32058S3 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39574.2528 | 39574.7076 | REPDAILY | 00363305 | SPICAPX | Install hebel wall on B3 trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028231139574.2923611111 | 10282311 |  | Parent | FALSE | A3 500/220KV TRANS BANK AT KTS | 39574.2924 | 39574.6132 | DAILY | 00026097 | SPIMAINT | top up blue ph 220kV bushing & replace faulty fan | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009442739574.2923611111 | 10094427 | 10269622 | Child | FALSE | H1 TRANS NO.2 BUS 330KV CB BUS SIDE E/SW AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | [12 empty] | 0
_1009443739574.2923611111 | 10094437 | 10269622 | Child | FALSE | H1 TRANS NO.2 BUS 330KV CB BUS SIDE ROI AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | [12 empty] | 0
_1026873539574.2923611111 | 10268735 | 10269622 | Child | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB BUS SIDE ROI AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | [12 empty] | 0
_1026873739574.2923611111 | 10268737 | 10269622 | Child | FALSE | MSS NO.2 330KV LINE NO.2 BUS CB BUS SIDE ROI AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | [12 empty] | 0
_1026873939574.2923611111 | 10268739 | 10269622 | Child | FALSE | WOTS 330KV LINE NO.2 BUS CB BUS SIDE ROI AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | [12 empty] | 0
_1026874139574.2923611111 | 10268741 | 10269622 | Child | FALSE | H2 TRANS 330KV CB BUS SIDE ROI AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | [12 empty] | 0
_1026874339574.2923611111 | 10268743 | 10269622 | Child | FALSE | MSS NO.2 330KV LINE NO.2 BUS CB BUS SIDE E/SW AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | [12 empty] | 0
_1026877239574.2923611111 | 10268772 | 10269622 | Child | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB BUS SIDE E/SW AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | [12 empty] | 0
_1026877439574.2923611111 | 10268774 | 10269622 | Child | FALSE | WOTS 330KV LINE NO.2 BUS CB BUS SIDE E/SW AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | [12 empty] | 0
_1026878439574.2923611111 | 10268784 | 10269622 | Child | FALSE | NO.2 330KV BUS E/SW AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | [12 empty] | 0
_1026962239574.2923611111 | 10269622 |  | Parent | TRUE | NO.2 330KV BUS AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | 00003979 | SPIMAINT | O/Haul NO.2 330KV BUS AT DDTS | SPIPOWER |  |  | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028208339574.2923611111 | 10282083 | 10269622 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | 00352121 | SPIMAINT | Perf Calc for H2 Trans during No2 220kv Bus Outage | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028208439574.2923611111 | 10282084 | 10269622 | Child | FALSE | NO.2 330KV CAPACITOR BANK AT DDTS | 39574.2924 | 39574.7014 | REPDAILY | 00352093 | SPIMAINT | Rebate W/O for No2 Cap BK during No2 Bus Outage | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_1028216739574.2993055556 | 10282167 |  | Parent | FALSE | NO.3 11/6.6KV AUX TRANS AT TSTS | 39574.2993 | 39574.6042 | DAILY | 00007662 | SPIMAINT | REPAIR OIL LEAK | SPIPOWER |  |  | Other Transformers | Eastern | 11 |  |  |  | 0
_Z63358C539574.5916666667 | Z63358C5 |  | Parent | FALSE | MWTS NO.2 220KV LINE NO.1 BUS CB AT JLTS | 39574.5917 | 39582.3125 | CONT | [12 empty] | 0
_1028270039575.0625 | 10282700 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 39575.0625 | 39576.587 | CONT | 00356080 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058S339575.2548611111 | X32058S3 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39575.2549 | 39575.6951 | REPDAILY | 00363305 | SPICAPX | Install hebel wall on B3 trans | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028231039575.2916666667 | 10282310 |  | Parent | FALSE | A4 500/220KV TRANS BANK AT KTS | 39575.2917 | 39575.6347 | DAILY | 00026098 | SPIMAINT | Top up Rph 220 kV bushing & replace faulty fans | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009442739575.29375 | 10094427 | 10269622 | Child | FALSE | H1 TRANS NO.2 BUS 330KV CB BUS SIDE E/SW AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | [12 empty] | 0
_1009443739575.29375 | 10094437 | 10269622 | Child | FALSE | H1 TRANS NO.2 BUS 330KV CB BUS SIDE ROI AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | [12 empty] | 0
_1026873539575.29375 | 10268735 | 10269622 | Child | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB BUS SIDE ROI AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | [12 empty] | 0
_1026873739575.29375 | 10268737 | 10269622 | Child | FALSE | MSS NO.2 330KV LINE NO.2 BUS CB BUS SIDE ROI AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | [12 empty] | 0
_1026873939575.29375 | 10268739 | 10269622 | Child | FALSE | WOTS 330KV LINE NO.2 BUS CB BUS SIDE ROI AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | [12 empty] | 0
_1026874139575.29375 | 10268741 | 10269622 | Child | FALSE | H2 TRANS 330KV CB BUS SIDE ROI AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | [12 empty] | 0
_1026874339575.29375 | 10268743 | 10269622 | Child | FALSE | MSS NO.2 330KV LINE NO.2 BUS CB BUS SIDE E/SW AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | [12 empty] | 0
_1026877239575.29375 | 10268772 | 10269622 | Child | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB BUS SIDE E/SW AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | [12 empty] | 0
_1026877439575.29375 | 10268774 | 10269622 | Child | FALSE | WOTS 330KV LINE NO.2 BUS CB BUS SIDE E/SW AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | [12 empty] | 0
_1026878439575.29375 | 10268784 | 10269622 | Child | FALSE | NO.2 330KV BUS E/SW AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | [12 empty] | 0
_1026962239575.29375 | 10269622 |  | Parent | TRUE | NO.2 330KV BUS AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | 00003979 | SPIMAINT | O/Haul NO.2 330KV BUS AT DDTS | SPIPOWER |  |  | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028208339575.29375 | 10282083 | 10269622 | Child | FALSE | H2 330/220KV TRANS AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | 00352121 | SPIMAINT | Perf Calc for H2 Trans during No2 220kv Bus Outage | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028208439575.29375 | 10282084 | 10269622 | Child | FALSE | NO.2 330KV CAPACITOR BANK AT DDTS | 39575.2937 | 39575.7424 | REPDAILY | 00352093 | SPIMAINT | Rebate W/O for No2 Cap BK during No2 Bus Outage | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_Z54358B339576.2527777778 | Z54358B3 |  | Parent | TRUE | GTS NO.1 220KV LINE NO.2 BUS CB AT MLTS | 39576.2528 | 39576.7694 | CONT | [12 empty] | 0
_Z54358B439576.2527777778 | Z54358B4 | Z54358B3 | Child | FALSE | GTS NO.1 220KV LINE AT MLTS | 39576.2528 | 39576.7694 | CONT | 00022489 | VEN_AUG | Rebate W/O GTS No1 Line | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028198839576.2895833333 | 10281988 |  | Parent | FALSE | B4 220/66KV TRANS AT RTS | 39576.2896 | 39576.65 | DAILY | 00007332 | SPIMAINT | Conditional Monitoring Trans 1Day RTS B4 | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028213539576.2923611111 | 10282135 |  | Parent | FALSE | H3 330/220KV TRANS AT DDTS | 39576.2924 | 39576.6569 | REPDAILY | 00003971 | SPIMAINT | Rebat W/O No3 Trans - O'Haul of its 330 ROIs & ESW | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028222139576.2972222222 | 10282221 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39576.2972 | 39576.7701 | DAILY | 00337581 | SPIMAINT | No1 Trans Group oil leaks | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027331139576.3013888889 | 10273311 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB CT R/PH AT KTS | 39576.3014 | 39576.6139 | DAILY | [12 empty] | 0
_1028279839576.9506944444 | 10282798 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 39576.9507 | 39577.875 | CONT | 00356083 | GENCO | GenCo work | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028280839577.2452893519 | 10282808 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 39577.2453 | 39579.075 | CONT | [12 empty] | 0
_1028213539577.2944444444 | 10282135 |  | Parent | FALSE | H3 330/220KV TRANS AT DDTS | 39577.2944 | 39577.6312 | REPDAILY | 00003971 | SPIMAINT | Rebat W/O No3 Trans - O'Haul of its 330 ROIs & ESW | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027331539577.3020833333 | 10273315 |  | Parent | FALSE | EX - A4 TRANS NO.1 BUS 500KV CB CT R/PH AT KTS | 39577.3021 | 39577.584 | DAILY | [12 empty] | 0
_1028276939577.3215277778 | 10282769 |  | Parent | FALSE | GTS NO.1 LINE/A2 TRANS 220KV CB AT MLTS | 39577.3215 | 39583.7396 | CONT | [12 empty] | 0
_1028208939577.3604166667 | 10282089 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39577.3604 | 39577.4097 | DAILY | [12 empty] | 0
_X55658L139578.34375 | X55658L1 |  | Parent | TRUE | NO.2 66KV BUS AT RWTS | 39578.3438 | 39578.4062 | DAILY | 00007479 | SPICAPX | Bus outage for pressure test | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 |  |  |  | 0
_X55658L239578.34375 | X55658L2 | X55658L1 | Child | FALSE | B3 220/66KV TRANS AT RWTS | 39578.3438 | 39578.4062 | DAILY | 00007455 | SPICAPX | Trans Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X55658L339578.34375 | X55658L3 | X55658L1 | Child | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39578.3438 | 39578.4062 | DAILY | 00007399 | SPICAPX | Cap Bank Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X55658L439578.34375 | X55658L4 | X55658L1 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39578.3438 | 39578.4062 | DAILY | 00331179 | SPICAPX | Cap Bank Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028281239578.40625 | 10282812 |  | Parent | FALSE | CYN NO.1 66KV FDR CB AT RWTS | 39578.4062 | 39592.5763 | CONT | [12 empty] | 0
_1028281139578.4173611111 | 10282811 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39578.4174 | 39578.4542 | DAILY | 00354002 | SPIMAINT | See W/O No. 10269344 | SPIPOWER |  |  | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1028265039579.3388888889 | 10282650 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 39579.3389 | 39579.4042 | DAILY | 00351939 | SPIMAINT | Out W/O No1 220kV Cap bank prot setting changes | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_Z54358B639580.2340277778 | Z54358B6 | Z54658A3 | Child | FALSE | A1 500/220KV TRANS BANK AT MLTS | 39580.234 | 39580.709 | DAILY | 00337580 | VEN_AUG | Perf calc A1Trans During No1 500kv Bus Outage | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z54658A339580.2340277778 | Z54658A3 |  | Parent | TRUE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39580.234 | 39580.709 | DAILY | [12 empty] | 0
_Z54358B539580.2340277778 | Z54358B5 |  | Parent | FALSE | NO.1 500KV BUS AT MLTS | 39580.234 | 39582.7417 | CONT | 00003012 | VEN_AUG | Connect new Bus Extn to No1 500kv Bus in Bay H | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Bus | Alstom | 500 |  |  |  | 0
_X49858M339580.3215277778 | X49858M3 |  | Parent | FALSE | B1 220/66KV TRANS (HOT SPARE) AT MBTS | 39580.3215 | 39589.5007 | CONT | 00360627 | SPICAPX | Out W/O B1 Trans to connect to fut No2 S-S trans | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER | NORMALLY OPEN | 0
_1028244739580.4111111111 | 10282447 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39580.4111 | 39580.534 | DAILY | [12 empty] | 0
_1026935139581.2819444445 | 10269351 |  | Parent | FALSE | NO.2 CSC AT ROTS | 39581.2819 | 39584.5118 | CONT | 00004716 | SPIMAINT | 4 Yearly O/Haul - No.2 CSC at ROTS | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027305739581.2847222222 | 10273057 |  | Parent | FALSE | H3 330/220KV TRANS AT DDTS | 39581.2847 | 39583.6319 | CONT | 00003971 | SPIMAINT | Condition Monitoring Country Trans 2day North Area | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1026840239581.2895833333 | 10268402 |  | Parent | FALSE | RWTS 220KV LINE AT TTS | 39581.2896 | 39582.6167 | CONT | 00015734 | SPIMAINT | RWTS 220kv Line VT | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027328939581.29375 | 10273289 | 10274427 | Child | FALSE | EX - KTS NO.1 220KV LINE CB CT R/PH AT WMTS | 39581.2937 | 39582.6403 | DAILY | [12 empty] | 0
_1027442739581.29375 | 10274427 |  | Parent | TRUE | KTS NO.1 220KV LINE AT WMTS | 39581.2937 | 39582.6403 | CONT | 00025734 | SPIMAINT | OVERHAUL OF A 220KV LINE | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026935939581.2979166667 | 10269359 |  | Parent | FALSE | SVTS NO.2 220KV LINE/NO.1 CSC CB AT ROTS | 39581.2979 | 39584.5826 | CONT | [12 empty] | 0
_1028283539581.4430555556 | 10282835 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39581.4431 | 39581.4569 | DAILY | [12 empty] | 0
_1028284239581.6024768519 | 10282842 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 39581.6025 | 39581.6569 | DAILY | 00027386 | APDALCOA | SF6 Top Up at APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X55658L839582.2916666667 | X55658L8 |  | Parent | FALSE | EX - LDL NO.1 66KV FDR CB AT RWTS | 39582.2917 | 39582.7917 | DAILY | [12 empty] | 0
_1028246539582.3159722222 | 10282465 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39582.316 | 39582.3535 | DAILY | [12 empty] | 0
_1028288139582.7916666667 | 10282881 |  | Parent | FALSE | 1-2 EXT 66KV BUS TIE CB AT RWTS | 39582.7917 | 39648.5139 | CONT | [12 empty] | 0
_X50858B339583.25 | X50858B3 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39583.25 | 39583.7285 | REPDAILY | 00017901 | SPICAPX | KTS No2 Line - Construct new footings in Bay J | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028282339583.2916666667 | 10282823 |  | Parent | FALSE | RCTS 220KV LINE AT KGTS | 39583.2917 | 39583.7042 | REPDAILY | 00017416 | SPIMAINT | Out W/O KGTS-RCTS Line for CB & Line & equip O-H | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027173539583.2986111111 | 10271735 |  | Parent | FALSE | FBTS NO.1 220KV LINE AT WMTS | 39583.2986 | 39584.6257 | CONT | 00025735 | SPIMAINT | INSPECTION OF LINE (FBTS NO.1 220KV) AT WMTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1027012739583.3027777778 | 10270127 |  | Parent | FALSE | HYTS NO.1 500KV LINE NO.2 BUS CB AT MLTS | 39583.3028 | 39584.5938 | CONT | [12 empty] | 0
_Z63358C739583.6527777778 | Z63358C7 |  | Parent | FALSE | HWPS NO.3 LINE/MWTS NO.2 LINE 220KV CB AT JLTS | 39583.6528 | 39595.3882 | CONT | [12 empty] | 0
_Z54358C039583.83125 | Z54358C0 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT MLTS | 39583.8313 | 39588.491 | CONT | 00364782 | VEN_AUG | Out W/O A2 TRANS isolated pending test energ | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Main Transformers | Alstom | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1028274039584.0291666667 | 10282740 |  | Parent | FALSE | LYBPS NO.1 500KV LINE AT LYPS | 39584.0292 | 39587.8736 | CONT | 00023074 | GENCO | SCAP to LYPS B | GENCO |  |  | Circuits | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858B339584.25 | X50858B3 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39584.25 | 39584.5632 | REPDAILY | 00017901 | SPICAPX | KTS No2 Line - Construct new footings in Bay J | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028282339584.2951388889 | 10282823 |  | Parent | FALSE | RCTS 220KV LINE AT KGTS | 39584.2951 | 39584.6847 | REPDAILY | 00017416 | SPIMAINT | Out W/O KGTS-RCTS Line for CB & Line & equip O-H | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026625139584.3496875 | 10266251 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK X PROT AT GNTS | 39584.3497 | 39584.484 | DAILY | [12 empty] | 0
_1028292839584.4305555556 | 10282928 |  | Parent | FALSE | B1 GEN TRANS 500KV CB AT LYPS | 39584.4306 | 39584.4451 | DAILY | [12 empty] | 0
_V60458C939584.5 | V60458C9 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT SMTS | 39584.5 | 39592.25 | DAILY | [12 empty] | 0
_1028209139584.5729166667 | 10282091 | V60458C3 | Child | FALSE | SYTS NO.2 500KV LINE AT SMTS | 39584.5729 | 39584.6236 | DAILY | 00012440 | SPICAPX | child workorder for other end of line | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458C339584.5729166667 | V60458C3 |  | Parent | TRUE | HWTS NO.2 500KV LINE AT SMTS | 39584.5729 | 39584.6236 | DAILY | 00012437 | SPICAPX | DEENERGISE LINE FOR HV TESTING | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028244839584.5958333333 | 10282448 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39584.5958 | 39584.6125 | DAILY | [12 empty] | 0
_1028298739584.9576388889 | 10282987 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39584.9576 | 39587.4146 | CONT | 00356082 | GENCO | Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858B339585.25 | X50858B3 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39585.25 | 39585.5701 | REPDAILY | 00017901 | SPICAPX | KTS No2 Line - Construct new footings in Bay J | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56958B639585.2965277778 | X56958B6 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39585.2965 | 39585.6222 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 4 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028296039585.3770833333 | 10282960 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39585.3771 | 39585.5403 | DAILY | 00319999 | APDALCOA | APD work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1028299039585.3777777778 | 10282990 |  | Parent | FALSE | W4 GEN TRANS 220KV LINE E/SW AT YPS | 39585.3778 | 39586.3167 | CONT | [12 empty] | 0
_1026940839586.28125 | 10269408 |  | Parent | TRUE | NO.4 66KV BUS AT ERTS | 39586.2812 | 39586.6681 | DAILY | 00004384 | SPIMAINT | O/Haul NO.4 66KV BUS AT ERTS | SPIPOWER |  |  | Bus | Eastern | 66 |  |  |  | 0
_1027164939586.28125 | 10271649 | 10269408 | Child | FALSE | NO.4 TRANS 66KV CB AT ERTS | 39586.2812 | 39586.6681 | DAILY | [12 empty] | 0
_1028261639586.28125 | 10282616 | 10269408 | Child | FALSE | B4 220/66KV TRANS AT ERTS | 39586.2812 | 39586.6681 | DAILY | 00004372 | SPIMAINT | Rebate for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028315339586.28125 | 10283153 | 10269408 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT ERTS | 39586.2812 | 39586.6681 | DAILY | 00004344 | SPIMAINT | CAP BANK FOR BUS OUTAGE | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X56958B639586.2965277778 | X56958B6 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39586.2965 | 39586.7299 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 4 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027173139586.3076388889 | 10271731 |  | Parent | FALSE | EX - ATS 220KV LINE AT KTS | 39586.3076 | 39586.6424 | DAILY | 00015978 | SPIMAINT | INSPECTION OF LINE (ATS 220KV) AT KTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028279539586.3263888889 | 10282795 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT ATS | 39586.3264 | 39586.7347 | DAILY | 00060869 | DBPROX | VSCAP to Powercor | DISTCO |  |  | Other Transformers | Western | 22 |  |  |  | 0
_X50858B339587.2569444444 | X50858B3 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39587.2569 | 39587.6965 | REPDAILY | 00017901 | SPICAPX | KTS No2 Line - Construct new footings in Bay J | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658L939587.2875 | X55658L9 |  | Parent | FALSE | CYN NO.1 66KV FDR CB AT RWTS | 39587.2875 | 39587.8611 | DAILY | [12 empty] | 0
_1026999139587.2951388889 | 10269991 |  | Parent | FALSE | 3-4 220KV BUS TIE CB AT WMTS | 39587.2951 | 39591.6194 | CONT | [12 empty] | 0
_1026880939587.2979166667 | 10268809 |  | Parent | FALSE | CBTS NO.2 220KV LINE AT ERTS | 39587.2979 | 39587.6479 | DAILY | 00012284 | SPIMAINT | O/H 220KV LINE & EQUIP AS PER E.A.P APPL. | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028217139587.2986111111 | 10282171 |  | Parent | FALSE | WOTS 330KV LINE AT DDTS | 39587.2986 | 39587.7035 | REPDAILY | 00012359 | SPIMAINT | O/Haul WOTS 330KV LINE AT DDTS | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026514939587.3076388889 | 10265149 | 10272755 | Child | FALSE | NO.2 TRANS NO.2 BUS 220KV CB BUS SIDE ROI AT KGTS | 39587.3076 | 39587.7264 | REPDAILY | [12 empty] | 0
_1026517339587.3076388889 | 10265173 | 10272755 | Child | FALSE | BETS 220KV LINE NO.2 BUS CB BUS SIDE E/SW AT KGTS | 39587.3076 | 39587.7264 | REPDAILY | [12 empty] | 0
_1026518539587.3076388889 | 10265185 | 10272755 | Child | FALSE | NO.2 220KV BUS E/SW AT KGTS | 39587.3076 | 39587.7264 | REPDAILY | [12 empty] | 0
_1026518739587.3076388889 | 10265187 | 10272755 | Child | FALSE | RCTS 220KV LINE NO.2 TIE BUS BUS SIDE E/SW AT KGTS | 39587.3076 | 39587.7264 | REPDAILY | [12 empty] | 0
_1026518939587.3076388889 | 10265189 | 10272755 | Child | FALSE | NO.3 TRANS 220KV CB BUS SIDE E/SW AT KGTS | 39587.3076 | 39587.7264 | REPDAILY | [12 empty] | 0
_1026519939587.3076388889 | 10265199 | 10272755 | Child | FALSE | NO.2 TRANS NO.2 BUS 220KV CB BUS SIDE E/SW AT KGTS | 39587.3076 | 39587.7264 | REPDAILY | [12 empty] | 0
_1027264739587.3076388889 | 10272647 | 10272755 | Child | FALSE | BETS 220KV LINE NO.2 BUS CB BUS SIDE ROI AT KGTS | 39587.3076 | 39587.7264 | REPDAILY | [12 empty] | 0
_1027265539587.3076388889 | 10272655 | 10272755 | Child | FALSE | RCTS 220KV LINE NO.2 TIE BUS BUS SIDE ROI AT KGTS | 39587.3076 | 39587.7264 | REPDAILY | [12 empty] | 0
_1027265739587.3076388889 | 10272657 | 10272755 | Child | FALSE | NO.3 TRANS 220KV CB BUS SIDE ROI AT KGTS | 39587.3076 | 39587.7264 | REPDAILY | [12 empty] | 0
_1027275539587.3076388889 | 10272755 |  | Parent | TRUE | NO.2 220KV BUS AT KGTS | 39587.3076 | 39587.7264 | REPDAILY | 00357752 | SPIMAINT | O/Haul NO.2 220KV BUS AT KGTS | SPIPOWER |  |  | Bus | Alstom | 220 |  |  |  | 0
_1028268339587.3076388889 | 10282683 | 10272755 | Child | FALSE | R3 220/66/22KV TRANS AT KGTS | 39587.3076 | 39587.7264 | REPDAILY | 00017375 | SPIMAINT | Perf calc W/O No3 Trans during No2 220 Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028282739587.3236111111 | 10282827 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39587.3236 | 39587.3569 | DAILY | [12 empty] | 0
_1028305839587.7490046296 | 10283058 |  | Parent | FALSE | 1-2 66KV BUS TIE CB 1-2 TIE BUS SIDE ISOL AT RWTS | 39587.749 | 39587.7563 | CONT | [12 empty] | 0
_X50858B339588.2576388889 | X50858B3 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39588.2576 | 39588.6896 | REPDAILY | 00017901 | SPICAPX | KTS No2 Line - Construct new footings in Bay J | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026514939588.2902777778 | 10265149 | 10272755 | Child | FALSE | NO.2 TRANS NO.2 BUS 220KV CB BUS SIDE ROI AT KGTS | 39588.2903 | 39588.675 | REPDAILY | [12 empty] | 0
_1026517339588.2902777778 | 10265173 | 10272755 | Child | FALSE | BETS 220KV LINE NO.2 BUS CB BUS SIDE E/SW AT KGTS | 39588.2903 | 39588.675 | REPDAILY | [12 empty] | 0
_1026518539588.2902777778 | 10265185 | 10272755 | Child | FALSE | NO.2 220KV BUS E/SW AT KGTS | 39588.2903 | 39588.675 | REPDAILY | [12 empty] | 0
_1026518739588.2902777778 | 10265187 | 10272755 | Child | FALSE | RCTS 220KV LINE NO.2 TIE BUS BUS SIDE E/SW AT KGTS | 39588.2903 | 39588.675 | REPDAILY | [12 empty] | 0
_1026518939588.2902777778 | 10265189 | 10272755 | Child | FALSE | NO.3 TRANS 220KV CB BUS SIDE E/SW AT KGTS | 39588.2903 | 39588.675 | REPDAILY | [12 empty] | 0
_1026519939588.2902777778 | 10265199 | 10272755 | Child | FALSE | NO.2 TRANS NO.2 BUS 220KV CB BUS SIDE E/SW AT KGTS | 39588.2903 | 39588.675 | REPDAILY | [12 empty] | 0
_1027264739588.2902777778 | 10272647 | 10272755 | Child | FALSE | BETS 220KV LINE NO.2 BUS CB BUS SIDE ROI AT KGTS | 39588.2903 | 39588.675 | REPDAILY | [12 empty] | 0
_1027265539588.2902777778 | 10272655 | 10272755 | Child | FALSE | RCTS 220KV LINE NO.2 TIE BUS BUS SIDE ROI AT KGTS | 39588.2903 | 39588.675 | REPDAILY | [12 empty] | 0
_1027265739588.2902777778 | 10272657 | 10272755 | Child | FALSE | NO.3 TRANS 220KV CB BUS SIDE ROI AT KGTS | 39588.2903 | 39588.675 | REPDAILY | [12 empty] | 0
_1027275539588.2902777778 | 10272755 |  | Parent | TRUE | NO.2 220KV BUS AT KGTS | 39588.2903 | 39588.675 | REPDAILY | 00357752 | SPIMAINT | O/Haul NO.2 220KV BUS AT KGTS | SPIPOWER |  |  | Bus | Alstom | 220 |  |  |  | 0
_1028268339588.2902777778 | 10282683 | 10272755 | Child | FALSE | R3 220/66/22KV TRANS AT KGTS | 39588.2903 | 39588.675 | REPDAILY | 00017375 | SPIMAINT | Perf calc W/O No3 Trans during No2 220 Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028217139588.2916666667 | 10282171 |  | Parent | FALSE | WOTS 330KV LINE AT DDTS | 39588.2917 | 39588.6632 | REPDAILY | 00012359 | SPIMAINT | O/Haul WOTS 330KV LINE AT DDTS | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026881139588.2986111111 | 10268811 |  | Parent | FALSE | CBTS NO.1 220KV LINE AT ERTS | 39588.2986 | 39588.6375 | DAILY | 00012286 | SPIMAINT | O/Haul CBTS 1 L CVTs at ERTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028193839588.3125 | 10281938 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39588.3125 | 39588.7639 | DAILY | [12 empty] | 0
_1028181839588.3173611111 | 10281818 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39588.3174 | 39588.6472 | DAILY | 00022691 | APDALCOA | SCAP to PTH | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X55658M839588.5201388889 | X55658M8 |  | Parent | FALSE | BWR 66KV FDR CB AT RWTS | 39588.5201 | 39597.2951 | CONT | [12 empty] | 0
_Z54358C139588.5381944444 | Z54358C1 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT MLTS | 39588.5382 | 39588.7007 | CONT | 00364782 | VEN_AUG | Out W/O A2 Trans test energ & commiss | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Main Transformers | Alstom | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1028308939588.8680555556 | 10283089 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 39588.8681 | 39590.7701 | CONT | 00016424 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858B439589.2513888889 | X50858B4 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39589.2514 | 39589.6792 | REPDAILY | 00017900 | SPICAPX | Out W/O KTS 1 Line-construct new footings bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z54358C239589.29375 | Z54358C2 |  | Parent | FALSE | GTS NO.1 220KV LINE AT MLTS | 39589.2937 | 39589.8792 | DAILY | 00022489 | VEN_AUG | Out W/O GTS 1 Line to connect bay H Tie CB LS ROI | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X67058A639589.2958333333 | X67058A6 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39589.2958 | 39591.6 | CONT | 00112417 | SPICAPX | Replace CT on No 3 220kv Cap Bank CB | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026515139589.3027777778 | 10265151 | 10272757 | Child | FALSE | NO.1 TRANS 220KV CB BUS SIDE ROI AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | [12 empty] | 0
_1026515339589.3027777778 | 10265153 | 10272757 | Child | FALSE | SVC 220KV CB BUS SIDE E/SW AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | [12 empty] | 0
_1026515739589.3027777778 | 10265157 | 10272757 | Child | FALSE | BETS 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | [12 empty] | 0
_1026517539589.3027777778 | 10265175 | 10272757 | Child | FALSE | RCTS 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | [12 empty] | 0
_1026517739589.3027777778 | 10265177 | 10272757 | Child | FALSE | NO.1 220KV BUS E/SW AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | [12 empty] | 0
_1026519139589.3027777778 | 10265191 | 10272757 | Child | FALSE | NO.2 TRANS NO.1 BUS 220KV CB BUS SIDE E/SW AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | [12 empty] | 0
_1026520139589.3027777778 | 10265201 | 10272757 | Child | FALSE | NO.1 TRANS 220KV CB BUS SIDE E/SW AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | [12 empty] | 0
_1027263739589.3027777778 | 10272637 | 10272757 | Child | FALSE | SVC 220KV CB BUS SIDE ROI AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | [12 empty] | 0
_1027264139589.3027777778 | 10272641 | 10272757 | Child | FALSE | BETS 220KV LINE NO.1 BUS CB BUS SIDE ROI AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | [12 empty] | 0
_1027264939589.3027777778 | 10272649 | 10272757 | Child | FALSE | RCTS 220KV LINE NO.1 BUS CB BUS SIDE ROI AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | [12 empty] | 0
_1027265939589.3027777778 | 10272659 | 10272757 | Child | FALSE | NO.2 TRANS NO.1 BUS 220KV CB BUS SIDE ROI AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | [12 empty] | 0
_1027275739589.3027777778 | 10272757 |  | Parent | TRUE | NO.1 220KV BUS AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | 00357751 | SPIMAINT | O/Haul NO.1 220KV BUS AT KGTS | SPIPOWER |  |  | Bus | Alstom | 220 |  |  |  | 0
_1028268739589.3027777778 | 10282687 | 10272757 | Child | FALSE | R1 220/66/22KV TRANS AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | 00357301 | SPIMAINT | Perf calc W/O No1 Trans during No1 220 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028269339589.3027777778 | 10282693 | 10272757 | Child | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39589.3028 | 39589.7167 | REPDAILY | 00017270 | SPIMAINT | Rebate W/O SVC during No1 220 bus outage | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028237839589.3097222222 | 10282378 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT RTS | 39589.3097 | 39590.4819 | DAILY | 00007335 | SPIMAINT | REPAIR LEAKING TRANS | SPIPOWER |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_1028222239589.3881944444 | 10282222 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT WOTS | 39589.3882 | 39589.4618 | DAILY | [12 empty] | 0
_1028222539589.4625 | 10282225 |  | Parent | FALSE | NO.2 TRANS 66KV CB AT WOTS | 39589.4625 | 39589.5021 | DAILY | [12 empty] | 0
_X49858M539589.5166666667 | X49858M5 |  | Parent | FALSE | B2 220/66KV TRANS AT MBTS | 39589.5167 | 39589.5597 | DAILY | 00362372 | SPICAPX | Out W/O De-energ B2 Tr- Commiss B1 Tr hot spare | SPIPOWER | X498 | X498 - (MBTS) REDEVELOPMENT 220KV SWITCHYARD | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028313639589.5291666667 | 10283136 |  | Parent | TRUE | WMTS NO.2 220KV LINE CB AT FBTS | 39589.5292 | 39589.5347 | DAILY | [12 empty] | 0
_1028344739589.5291666667 | 10283447 | 10283136 | Child | FALSE | WMTS NO.2 220KV LINE AT FBTS | 39589.5292 | 39589.5347 | DAILY | 00017157 | SPIMAINT | out workorder for line assoc with cb gas top up | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X50858B439590.2506944445 | X50858B4 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39590.2507 | 39590.7083 | REPDAILY | 00017900 | SPICAPX | Out W/O KTS 1 Line-construct new footings bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028316539590.2791666667 | 10283165 |  | Parent | FALSE | EX - B3 TRANS 220KV CB AT GTS | 39590.2792 | 39590.4889 | DAILY | [12 empty] | 0
_1028385139590.2791666667 | 10283851 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 39590.2792 | 39590.4889 | DAILY | 00002829 | FORCED | No 3 Trans at GTS | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026515139590.3013888889 | 10265151 | 10272757 | Child | FALSE | NO.1 TRANS 220KV CB BUS SIDE ROI AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | [12 empty] | 0
_1026515339590.3013888889 | 10265153 | 10272757 | Child | FALSE | SVC 220KV CB BUS SIDE E/SW AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | [12 empty] | 0
_1026515739590.3013888889 | 10265157 | 10272757 | Child | FALSE | BETS 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | [12 empty] | 0
_1026517539590.3013888889 | 10265175 | 10272757 | Child | FALSE | RCTS 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | [12 empty] | 0
_1026517739590.3013888889 | 10265177 | 10272757 | Child | FALSE | NO.1 220KV BUS E/SW AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | [12 empty] | 0
_1026519139590.3013888889 | 10265191 | 10272757 | Child | FALSE | NO.2 TRANS NO.1 BUS 220KV CB BUS SIDE E/SW AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | [12 empty] | 0
_1026520139590.3013888889 | 10265201 | 10272757 | Child | FALSE | NO.1 TRANS 220KV CB BUS SIDE E/SW AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | [12 empty] | 0
_1027263739590.3013888889 | 10272637 | 10272757 | Child | FALSE | SVC 220KV CB BUS SIDE ROI AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | [12 empty] | 0
_1027264139590.3013888889 | 10272641 | 10272757 | Child | FALSE | BETS 220KV LINE NO.1 BUS CB BUS SIDE ROI AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | [12 empty] | 0
_1027264939590.3013888889 | 10272649 | 10272757 | Child | FALSE | RCTS 220KV LINE NO.1 BUS CB BUS SIDE ROI AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | [12 empty] | 0
_1027265939590.3013888889 | 10272659 | 10272757 | Child | FALSE | NO.2 TRANS NO.1 BUS 220KV CB BUS SIDE ROI AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | [12 empty] | 0
_1027275739590.3013888889 | 10272757 |  | Parent | TRUE | NO.1 220KV BUS AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | 00357751 | SPIMAINT | O/Haul NO.1 220KV BUS AT KGTS | SPIPOWER |  |  | Bus | Alstom | 220 |  |  |  | 0
_1028268739590.3013888889 | 10282687 | 10272757 | Child | FALSE | R1 220/66/22KV TRANS AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | 00357301 | SPIMAINT | Perf calc W/O No1 Trans during No1 220 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028269339590.3013888889 | 10282693 | 10272757 | Child | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39590.3014 | 39590.7229 | REPDAILY | 00017270 | SPIMAINT | Rebate W/O SVC during No1 220 bus outage | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028222639590.3347222222 | 10282226 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 39590.3347 | 39590.4674 | DAILY | 00351939 | SPIMAINT | CT - No1 220kv Cap Bank CB CT oil samples | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1028306039590.3972222222 | 10283060 |  | Parent | FALSE | GTS NO.1 220KV LINE AT MLTS | 39590.3972 | 39590.4257 | CONT | 00022489 | VEN_AUG | MLTS-GTS No1 Line Required to be De-Energised | SPIPOWER |  | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028222939590.4708333333 | 10282229 |  | Parent | FALSE | H1 TRANS NO.1 BUS 330KV CB AT DDTS | 39590.4708 | 39590.6146 | DAILY | [12 empty] | 0
_1028319339590.4930555556 | 10283193 |  | Parent | FALSE | EX - B3 TRANS 220KV CB AT GTS | 39590.4931 | 39590.6139 | DAILY | [12 empty] | 0
_1028385239590.4930555556 | 10283852 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 39590.4931 | 39590.6139 | DAILY | 00002829 | FORCED | No 3 Trans at GTS | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028322439591.0625 | 10283224 |  | Parent | FALSE | SMTS 500KV LINE AT KTS | 39591.0625 | 39591.5403 | DAILY | 00015991 | SW_NEM | Nemmco Directed switching of KTS-SMTS 500kV Line | SPIPOWER |  |  | Circuits | 3rd Party | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026515139591.2909722222 | 10265151 | 10272757 | Child | FALSE | NO.1 TRANS 220KV CB BUS SIDE ROI AT KGTS | 39591.291 | 39591.5813 | REPDAILY | [12 empty] | 0
_1026515339591.2909722222 | 10265153 | 10272757 | Child | FALSE | SVC 220KV CB BUS SIDE E/SW AT KGTS | 39591.291 | 39591.5813 | REPDAILY | [12 empty] | 0
_1026515739591.2909722222 | 10265157 | 10272757 | Child | FALSE | BETS 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT KGTS | 39591.291 | 39591.5813 | REPDAILY | [12 empty] | 0
_1026517539591.2909722222 | 10265175 | 10272757 | Child | FALSE | RCTS 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT KGTS | 39591.291 | 39591.5813 | REPDAILY | [12 empty] | 0
_1026517739591.2909722222 | 10265177 | 10272757 | Child | FALSE | NO.1 220KV BUS E/SW AT KGTS | 39591.291 | 39591.5813 | REPDAILY | [12 empty] | 0
_1026519139591.2909722222 | 10265191 | 10272757 | Child | FALSE | NO.2 TRANS NO.1 BUS 220KV CB BUS SIDE E/SW AT KGTS | 39591.291 | 39591.5813 | REPDAILY | [12 empty] | 0
_1026520139591.2909722222 | 10265201 | 10272757 | Child | FALSE | NO.1 TRANS 220KV CB BUS SIDE E/SW AT KGTS | 39591.291 | 39591.5813 | REPDAILY | [12 empty] | 0
_1027263739591.2909722222 | 10272637 | 10272757 | Child | FALSE | SVC 220KV CB BUS SIDE ROI AT KGTS | 39591.291 | 39591.5813 | REPDAILY | [12 empty] | 0
_1027264139591.2909722222 | 10272641 | 10272757 | Child | FALSE | BETS 220KV LINE NO.1 BUS CB BUS SIDE ROI AT KGTS | 39591.291 | 39591.5813 | REPDAILY | [12 empty] | 0
_1027264939591.2909722222 | 10272649 | 10272757 | Child | FALSE | RCTS 220KV LINE NO.1 BUS CB BUS SIDE ROI AT KGTS | 39591.291 | 39591.5813 | REPDAILY | [12 empty] | 0
_1027265939591.2909722222 | 10272659 | 10272757 | Child | FALSE | NO.2 TRANS NO.1 BUS 220KV CB BUS SIDE ROI AT KGTS | 39591.291 | 39591.5813 | REPDAILY | [12 empty] | 0
_1027275739591.2909722222 | 10272757 |  | Parent | TRUE | NO.1 220KV BUS AT KGTS | 39591.291 | 39591.5813 | REPDAILY | 00357751 | SPIMAINT | O/Haul NO.1 220KV BUS AT KGTS | SPIPOWER |  |  | Bus | Alstom | 220 |  |  |  | 0
_1028268739591.2909722222 | 10282687 | 10272757 | Child | FALSE | R1 220/66/22KV TRANS AT KGTS | 39591.291 | 39591.5813 | REPDAILY | 00357301 | SPIMAINT | Perf calc W/O No1 Trans during No1 220 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028269339591.2909722222 | 10282693 | 10272757 | Child | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39591.291 | 39591.5813 | REPDAILY | 00017270 | SPIMAINT | Rebate W/O SVC during No1 220 bus outage | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z54358C339591.2958333333 | Z54358C3 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT MLTS | 39591.2958 | 39591.5931 | DAILY | 00364782 | VEN_AUG | Out W/O A2 Trans for 22kV isol int'lock mods | SPIPOWER | Z543 | Z543 - (MLTS) INTERFACE WORK FOR NEXT 500/220KV TRANSFORMER | Main Transformers | Alstom | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_V77558B039591.3576388889 | V77558B0 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39591.3576 | 39591.7889 | DAILY | 00003104 | SPIMAINT | Out W/O No1 66kV Cap bank prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026931039591.3770833333 | 10269310 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS (CONNECTED TO BAN 8) AT BATS | 39591.3771 | 39591.5757 | DAILY | 00006556 | SPIMAINT | O/Haul No 1 S/S Trans at BATS | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1028324839591.5875 | 10283248 |  | Parent | FALSE | JLA NO.1 220KV LINE CB AT TBTS | 39591.5875 | 39591.6104 | CONT | [12 empty] | 0
_1028324939591.5875 | 10283249 |  | Parent | FALSE | TBTS-JLA 1 220KV E | 39591.5875 | 39591.6104 | DAILY | 00022774 | FORCED | Low SF6 Gas Alarm | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028283239591.6055555556 | 10282832 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 39591.6056 | 39591.6285 | DAILY | [12 empty] | 0
_1028324239591.9618055556 | 10283242 |  | Parent | FALSE | YWPS NO.3 220KV LINE AT YPS | 39591.9618 | 39596.384 | CONT | 00016426 | GENCO | SCAP to YWPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V60458B439592.25 | V60458B4 |  | Parent | TRUE | HWTS NO.2 500KV LINE AT SMTS | 39592.25 | 39592.6424 | DAILY | 00012437 | SPICAPX | restore by-pass in bay "b" | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458L239592.25 | V60458L2 | V60458B4 | Child | FALSE | SYTS NO.2 500KV LINE AT SMTS | 39592.25 | 39592.6424 | DAILY | 00012440 | SPICAPX | restore by-pass in bay "b" | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058Z639592.3159722222 | X32058Z6 |  | Parent | FALSE | ROTS-MTS 1 220KV E | 39592.316 | 39592.6083 | DAILY | 00022746 | SPICAPX | INSTALL BRIDGE STRING INSULATORS | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V77558B139592.4006944444 | V77558B1 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 39592.4007 | 39592.5764 | DAILY | 00331109 | SPIMAINT | Out W/O No1 66kV Cap bank prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028328539592.5111111111 | 10283285 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39592.5111 | 39593.7576 | CONT | 00356084 | GENCO | GEN Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028317039592.7665046296 | 10283170 |  | Parent | FALSE | HWTS NO.2 LINE/SYTS NO.2 LINE 500KV CB AT SMTS | 39592.7665 | 39596.6146 | CONT | [12 empty] | 0
_1028328839593.2506944445 | 10283288 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39593.2507 | 39597.6417 | CONT | 00356082 | GENCO | No 4 Gen Trans CBs | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X56958B739593.2958333333 | X56958B7 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39593.2958 | 39593.7167 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 5 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X66858D339593.3020833333 | X66858D3 |  | Parent | FALSE | TSTS 220KV LINE AT TTS | 39593.3021 | 39593.6764 | REPDAILY | 00015736 | SPICAPX | Replace insulators tsts - tts line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658M139593.3472222222 | X55658M1 |  | Parent | TRUE | NO.4 66KV BUS AT RWTS | 39593.3472 | 39593.3646 | DAILY | 00007481 | SPICAPX | Bus Outage to Pressure test CB | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X55658M239593.3472222222 | X55658M2 | X55658M1 | Child | FALSE | B4 220/66KV TRANS AT RWTS | 39593.3472 | 39593.3646 | DAILY | 00007451 | SPICAPX | Rebate Tran for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028311139593.3569444444 | 10283111 |  | Parent | FALSE | NO.8 22KV/415V S/S TRANS AT SMTS | 39593.3569 | 39593.6917 | DAILY | 00001327 | DBPROX | VSCAP to DOC | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1028300939593.3645833333 | 10283009 |  | Parent | FALSE | BRA 66KV FDR CB AT RWTS | 39593.3646 | 39597.5722 | CONT | [12 empty] | 0
_X55658M439593.3756944445 | X55658M4 |  | Parent | TRUE | NO.2 66KV BUS AT RWTS | 39593.3757 | 39593.4917 | DAILY | 00007479 | SPICAPX | Replace Bus Side Droppers of Sub Fut BWR Fdr CB | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 |  |  |  | 0
_X55658M539593.3756944445 | X55658M5 | X55658M4 | Child | FALSE | B3 220/66KV TRANS AT RWTS | 39593.3757 | 39593.4917 | DAILY | 00007455 | SPICAPX | Trans Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X55658M639593.3756944445 | X55658M6 | X55658M4 | Child | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39593.3757 | 39593.4917 | DAILY | 00007399 | SPICAPX | Cap Bank Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X55658M739593.3756944445 | X55658M7 | X55658M4 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39593.3757 | 39593.4917 | DAILY | 00331179 | SPICAPX | Cap Bank Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028329039594.1909722222 | 10283290 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT HWPS | 39594.191 | 39594.5868 | CONT | 00015790 | FAULT | Investigate / Repair line after auto | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858B539594.2541666667 | X50858B5 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39594.2542 | 39594.7146 | DAILY | 00017900 | SPICAPX | Out W/O KTS 1 Line-construct new footings bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56958B739594.2944444444 | X56958B7 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39594.2944 | 39594.6694 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 5 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028324339594.3895833333 | 10283243 |  | Parent | FALSE | JLGA NO.4 UNIT TRANS DISC CB AT JLGA | 39594.3896 | 39609.6403 | CONT | [12 empty] | 0
_V77558B139594.4402777778 | V77558B1 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 39594.4403 | 39594.7736 | DAILY | 00331109 | SPIMAINT | Out W/O No1 66kV Cap bank prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028337539594.6083333333 | 10283375 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 39594.6083 | 39594.6451 | DAILY | 00060938 | APDALCOA | APD No2 Line de-energised for Alcoa. | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X32058Z239595.2569444444 | X32058Z2 |  | Parent | TRUE | NO.1 66KV BUS AT MTS | 39595.2569 | 39595.6965 | REPDAILY | 00363432 | SPIMAINT | Install safety screens | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058Z339595.2569444444 | X32058Z3 | X32058Z2 | Child | FALSE | B3 220/66KV TRANS AT MTS | 39595.2569 | 39595.6965 | REPDAILY | 00363305 | SPIMAINT | Tran rebate for Bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058Z439595.2569444444 | X32058Z4 | X32058Z2 | Child | FALSE | U1 66/22KV TRANS AT MTS | 39595.2569 | 39595.6965 | REPDAILY | 00363343 | SPIMAINT | Tran rebate for Bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026935739595.2715277778 | 10269357 |  | Parent | FALSE | NO.1 CSC AT ROTS | 39595.2715 | 39595.6069 | DAILY | 00004718 | SPIMAINT | Replace Defective insulators | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028234439595.2986111111 | 10282344 |  | Parent | FALSE | B3 220/66KV TRANS AT RTS | 39595.2986 | 39595.6514 | DAILY | 00329288 | SPIMAINT | OVERHAUL TRANSFORMER | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X66858D439595.3069444444 | X66858D4 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE AT KTS | 39595.3069 | 39595.6618 | REPDAILY | 00015986 | SPICAPX | Replace insulators kts - gts no.3 line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56958A439595.3111111111 | X56958A4 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39595.3111 | 39595.7705 | REPDAILY | 00060188 | SPICAPX | Out W/O JDSS-WOTS Line OPGW - Run 2 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026998839595.3236111111 | 10269988 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT WMTS | 39595.3236 | 39598.4837 | CONT | [12 empty] | 0
_1027174939595.3583333333 | 10271749 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT SHTS | 39595.3583 | 39595.6285 | DAILY | [12 empty] | 0
_Z63358C839595.3881944444 | Z63358C8 |  | Parent | FALSE | MWTS NO.2 220KV LINE AT JLTS | 39595.3882 | 39595.7167 | DAILY | 00015948 | VEN_AUG | MWTS 2 Line | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028320939595.4729166667 | 10283209 |  | Parent | FALSE | 1-3 66KV BUS TIE CB AT RWTS | 39595.4729 | 39595.4938 | DAILY | [12 empty] | 0
_X32058Z239596.2569444444 | X32058Z2 |  | Parent | TRUE | NO.1 66KV BUS AT MTS | 39596.2569 | 39596.6444 | REPDAILY | 00363432 | SPIMAINT | Install safety screens | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058Z339596.2569444444 | X32058Z3 | X32058Z2 | Child | FALSE | B3 220/66KV TRANS AT MTS | 39596.2569 | 39596.6444 | REPDAILY | 00363305 | SPIMAINT | Tran rebate for Bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058Z439596.2569444444 | X32058Z4 | X32058Z2 | Child | FALSE | U1 66/22KV TRANS AT MTS | 39596.2569 | 39596.6444 | REPDAILY | 00363343 | SPIMAINT | Tran rebate for Bus outage | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026928939596.3055555556 | 10269289 |  | Parent | FALSE | B4 220/66KV TRANS AT RTS | 39596.3056 | 39596.6396 | DAILY | 00007332 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56958A439596.3194444444 | X56958A4 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39596.3194 | 39596.75 | REPDAILY | 00060188 | SPICAPX | Out W/O JDSS-WOTS Line OPGW - Run 2 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X66858D439596.3236111111 | X66858D4 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE AT KTS | 39596.3236 | 39596.6674 | REPDAILY | 00015986 | SPICAPX | Replace insulators kts - gts no.3 line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358A339596.3243055556 | Z63358A3 |  | Parent | FALSE | HWPS NO.3 220KV LINE AT JLTS | 39596.3243 | 39598.3316 | CONT | 00015939 | VEN_AUG | HWPS 3 Line | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X67058A539596.3263888889 | X67058A5 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39596.3264 | 39598.6896 | CONT | 00112418 | SPICAPX | Replace CT on No 2 220kv Cap Bank CB | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027174739596.3409722222 | 10271747 |  | Parent | FALSE | 2 EXT-4 66KV BUS TIE CB AT SHTS | 39596.341 | 39596.5924 | DAILY | [12 empty] | 0
_1028348639596.4375 | 10283486 |  | Parent | TRUE | EX - NO.4A 66KV CAPACITOR BANK AT TTS | 39596.4375 | 39597.4097 | CONT | 00001486 | FAULT | Rebate for No4A Cap Fault | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028384839596.4375 | 10283848 | 10283486 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT TTS | 39596.4375 | 39597.4097 | CONT | 00337509 | SPIMAINT | out workorder for Cap Fault | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X55658M939597.2277777778 | X55658M9 |  | Parent | FALSE | BWR 66KV FDR CB AT RWTS | 39597.2278 | 39597.9792 | DAILY | [12 empty] | 0
_X50858C139597.2506944445 | X50858C1 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39597.2507 | 39597.6729 | DAILY | 00017901 | SPICAPX | Out W/O KTS 2 Line- Relocate VT's to new Position | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028276439597.3027777778 | 10282764 |  | Parent | FALSE | B1 220/66KV TRANS AT RTS | 39597.3028 | 39597.6694 | DAILY | 00007329 | SPIMAINT | REPAIR TRANS COOLING | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56958A539597.3090277778 | X56958A5 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39597.309 | 39597.7653 | REPDAILY | 00060188 | SPICAPX | Out W/O JDSS-WOTS Line OPGW - Run 3 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V77558B339597.3243055556 | V77558B3 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT ATS | 39597.3243 | 39597.7333 | DAILY | 00350821 | SPIMAINT | Out W/O No2 66kV Cap bank prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Western | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1027286739597.3555555556 | 10272867 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT SHTS | 39597.3556 | 39597.6326 | DAILY | [12 empty] | 0
_1028301239597.3555555556 | 10283012 | 10272867 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT SHTS | 39597.3556 | 39597.6326 | DAILY | 00350862 | SPIMAINT | Rebate W/O 2A 66kV Cap Bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028301339597.3555555556 | 10283013 | 10272867 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT SHTS | 39597.3556 | 39597.6326 | DAILY | 00330829 | SPIMAINT | Rebate W/O 2B 66kV Cap Bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028351639597.4097222222 | 10283516 |  | Parent | TRUE | EX - NO.4A 66KV CAPACITOR BANK AT TTS | 39597.4097 | 39597.6458 | DAILY | 00001486 | SPIMAINT | cap bank unbalance | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028384939597.4097222222 | 10283849 | 10283516 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT TTS | 39597.4097 | 39597.6458 | CONT | 00337509 | SPIMAINT | out workorder for Cap Fault | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X55658N939597.5722222222 | X55658N9 |  | Parent | FALSE | BRA 66KV FDR AT RWTS | 39597.5722 | 39604.2917 | CONT | 00020124 | SPICAPX | future SUB BRA FDR | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Circuits | Eastern | 66 |  |  |  | 0
_X55658N139597.9625 | X55658N1 |  | Parent | FALSE | CYN NO.2 66KV FDR CB AT RWTS | 39597.9625 | 39615.3153 | CONT | [12 empty] | 0
_1028360739598.0125 | 10283607 |  | Parent | FALSE | NO.8 GEN TRANS 220KV CB TRANS SIDE ISOL AT HWPS | 39598.0125 | 39603.6965 | CONT | [12 empty] | 0
_X32058Z539598.2506944445 | X32058Z5 |  | Parent | FALSE | B1 220/66KV TRANS AT MTS | 39598.2507 | 39598.65 | DAILY | 00364562 | SPIMAINT | Install Column wall B1 Trans & No2 66kv Bus | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56958A539598.2979166667 | X56958A5 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39598.2979 | 39598.6333 | REPDAILY | 00060188 | SPICAPX | Out W/O JDSS-WOTS Line OPGW - Run 3 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X66858D239598.3013888889 | X66858D2 |  | Parent | FALSE | KTS NO.2 220KV LINE AT TTS | 39598.3014 | 39598.4743 | DAILY | 00015727 | SPICAPX | Replace insulators tts - kts No2 line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026928339598.3236111111 | 10269283 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT RTS | 39598.3236 | 39598.6056 | DAILY | 00007336 | SPIMAINT | Station Service Trans O/H | SPIPOWER |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_1026813839598.3416666667 | 10268138 | 10268580 | Child | FALSE | LYPA 66/11KV TRANS 'A' FDR Y PROT AT LY | 39598.3417 | 39598.4507 | DAILY | [12 empty] | 0
_Z63358C939598.34375 | Z63358C9 |  | Parent | FALSE | HWPS NO.3 LINE/MWTS NO.2 LINE 220KV CB AT JLTS | 39598.3438 | 39610.3125 | CONT | [12 empty] | 0
_1028360939598.3673611111 | 10283609 |  | Parent | FALSE | EX - NO.4A 66KV CAPACITOR BANK AT TTS | 39598.3674 | 39598.6174 | DAILY | 00001486 | SPIMAINT | cap bank unbalance | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V77558B239598.425 | V77558B2 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39598.425 | 39598.8542 | DAILY | 00331118 | SPIMAINT | Out W/O No2 66kV Cap bank prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X50858B639599.25 | X50858B6 |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 39599.25 | 39599.7431 | DAILY | 00002834 | SPICAPX | Erect Gantry, ROI's and Bus Ext'n in Bays A, B, &J | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858B739599.25 | X50858B7 | X50858B6 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39599.25 | 39599.7431 | DAILY | 00002830 | SPICAPX | Perf Calc B4 Trans during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858B839599.25 | X50858B8 | X50858B6 | Child | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39599.25 | 39599.7431 | DAILY | 00017905 | SPICAPX | Rebate W/O PTH No1 Line during No2 220 Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858B939599.25 | X50858B9 | X50858B6 | Child | FALSE | EX - MLTS NO.1 220KV LINE AT GTS | 39599.25 | 39599.7431 | DAILY | 00017903 | SPICAPX | Rebate W/O MLTS No1 Line during No2 220 Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858C039599.25 | X50858C0 | X50858B6 | Child | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39599.25 | 39599.7431 | DAILY | 00017900 | SPICAPX | Rebate W/O KTS No1 Line during No2 220 Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1007392939599.2881944444 | 10073929 | 10283480 | Child | FALSE | S095 HWPS-ROTS 1 220KV | 39599.2882 | 39599.684 | DAILY | [12 empty] | 0
_1028348039599.2881944444 | 10283480 |  | Parent | TRUE | HWPS NO.1 220KV LINE AT ROTS | 39599.2882 | 39599.6846 | DAILY | 00023990 | SPIMAINT | REBATE WORK ORDER LINE OUTAGE Book X668 | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56958B839599.2951388889 | X56958B8 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39599.2951 | 39599.7812 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 11 & 12 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024946439599.2993055556 | 10249464 |  | Parent | FALSE | B4 220/66KV TRANS AT TTS | 39599.2993 | 39599.6424 | DAILY | 00001543 | SPIMAINT | O/HAUL Transformer and Div Sw & 66kv cb | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027341139599.3006944444 | 10273411 |  | Parent | FALSE | EX - 1-3 220KV BUS TIE CB NO.3 BUS CT R/PH AT SVTS | 39599.3007 | 39599.416 | DAILY | [12 empty] | 0
_1028354939599.3131944445 | 10283549 |  | Parent | FALSE | NO.1 GEN 500/21KV TRANS AT LYPA | 39599.3132 | 39600.5743 | CONT | 00010006 | GENCO | LYA 1 Gen Trans isolation | GENCO |  |  | Main Transformers | Eastern | 500 |  |  |  | 0
_1027341339599.4166666667 | 10273413 |  | Parent | FALSE | 2-4 220KV BUS TIE CB NO.2 BUS CT R/PH AT SVTS | 39599.4167 | 39599.4979 | DAILY | [12 empty] | 0
_1026695439600.2791666667 | 10266954 |  | Parent | TRUE | NO.1 66KV BUS AT RTS | 39600.2792 | 39600.6083 | DAILY | 00022323 | SPIMAINT | O/Haul NO.1 66KV BUS AT RTS | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1028264639600.2791666667 | 10282646 | 10266954 | Child | FALSE | B1 220/66KV TRANS AT RTS | 39600.2792 | 39600.6083 | DAILY | 00007329 | SPIMAINT | rebate Tran for bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028264739600.2791666667 | 10282647 | 10266954 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RTS | 39600.2792 | 39600.6083 | DAILY | 00007279 | SPIMAINT | rebate Cap Bank for bus outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028343139600.2791666667 | 10283431 | 10266954 | Child | FALSE | TK 66KV FDR CB FDR SIDE CT R/PH AT RTS | 39600.2792 | 39600.6083 | DAILY | [12 empty] | 0
_1028343539600.2791666667 | 10283435 | 10266954 | Child | FALSE | CW 66KV FDR CB FDR SIDE CT R/PH AT RTS | 39600.2792 | 39600.6083 | DAILY | [12 empty] | 0
_1028352139600.2791666667 | 10283521 | 10266954 | Child | FALSE | NO.1 66KV CAPACITOR BANK CB NO.1 CAPACITOR BANK SIDE CT R/PH AT RTS | 39600.2792 | 39600.6083 | DAILY | [12 empty] | 0
_1028348139600.29375 | 10283481 |  | Parent | FALSE | HWPS NO.2 220KV LINE AT ROTS | 39600.2937 | 39600.5528 | DAILY | 00024004 | SPIMAINT | REPLACE GLASS INSULATORS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56958B839600.2951388889 | X56958B8 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39600.2951 | 39600.7764 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 11 & 12 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024949039600.2965277778 | 10249490 |  | Parent | FALSE | B4 TRANS NO.1 BUS 220KV CB TRANS SIDE ISOL AT TTS | 39600.2965 | 39600.6493 | DAILY | [12 empty] | 0
_1024830639600.3222222222 | 10248306 |  | Parent | TRUE | A1 GEN TRANS 500KV CB AT LYPS | 39600.3222 | 39604.5653 | DAILY | [12 empty] | 0
_1024831239600.3222222222 | 10248312 | 10248306 | Child | FALSE | NO.1 GEN TRANS 500KV LINE E/SW AT LYPS | 39600.3222 | 39604.5653 | DAILY | [12 empty] | 0
_1028366139600.4013888889 | 10283661 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39600.4014 | 39600.5201 | DAILY | 00356084 | GENCO | unit 6 isols | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858C839601.25 | X50858C8 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39601.25 | 39601.6729 | DAILY | 00017900 | SPICAPX | Out W/O KTS 1 Line-construct new footings bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027049839601.2923611111 | 10270498 |  | Parent | FALSE | MLTS NO.2 500KV LINE NO.2 BUS CB AT SYTS | 39601.2924 | 39602.6528 | CONT | [12 empty] | 0
_X67058A739601.2965277778 | X67058A7 |  | Parent | FALSE | B2 220/66KV TRANS AT TBTS | 39601.2965 | 39605.5368 | CONT | 00004902 | SPICAPX | Replace CT on B2 Trans 220kv CB | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028355039601.31875 | 10283550 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 39601.3187 | 39601.6375 | DAILY | [12 empty] | 0
_Z56258A139601.3395833333 | Z56258A1 |  | Parent | FALSE | MKPS-BOPS-MBTS 220KV NW | 39601.3396 | 39601.6208 | DAILY | 00060197 | GEN_AUG | Out W/O MKPS Line Clamp in line at T15 | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858C239602.2534722222 | X50858C2 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39602.2535 | 39602.6236 | DAILY | 00017900 | SPICAPX | Out W/O KTS 1 Line Relocate W ph VT to new Pos'n | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028300639602.2736111111 | 10283006 | 10283008 | Child | FALSE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39602.2736 | 39602.375 | DAILY | [12 empty] | 0
_1028300839602.2736111111 | 10283008 |  | Parent | TRUE | MLTS NO.1 500KV LINE CB AT HYTS | 39602.2736 | 39602.375 | DAILY | [12 empty] | 0
_1028347539602.2736111111 | 10283475 | 10283008 | Child | TRUE | M1 500/275KV TRANS AT HYTS | 39602.2736 | 39602.375 | DAILY | 00002863 | SPIMAINT | Perf Calc W/O for M1 Trans outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028347639602.2736111111 | 10283476 | 10283475 | Child | FALSE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39602.2736 | 39602.375 | DAILY | [12 empty] | 0
_1028355239602.3166666667 | 10283552 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 39602.3167 | 39602.6312 | DAILY | [12 empty] | 0
_1026514439602.3236111111 | 10265144 | 10272619 | Child | FALSE | NO.2 TRANS NO.1 BUS 220KV CB TRANS SIDE ROI AT KGTS | 39602.3236 | 39602.7208 | REPDAILY | [12 empty] | 0
_1026514639602.3236111111 | 10265146 | 10272619 | Child | FALSE | NO.2 TRANS NO.2 BUS 220KV CB TRANS SIDE ROI AT KGTS | 39602.3236 | 39602.7208 | REPDAILY | [12 empty] | 0
_1026519339602.3236111111 | 10265193 | 10272619 | Child | FALSE | NO.2 TRANS 220KV E/SW AT KGTS | 39602.3236 | 39602.7208 | REPDAILY | [12 empty] | 0
_1026519539602.3236111111 | 10265195 | 10272619 | Child | FALSE | NO.2 TRANS NO.1 BUS 220KV CB TRANS SIDE E/SW AT KGTS | 39602.3236 | 39602.7208 | REPDAILY | [12 empty] | 0
_1026519739602.3236111111 | 10265197 | 10272619 | Child | FALSE | NO.2 TRANS NO.2 BUS 220KV CB TRANS SIDE E/SW AT KGTS | 39602.3236 | 39602.7208 | REPDAILY | [12 empty] | 0
_1027261939602.3236111111 | 10272619 |  | Parent | TRUE | NO.2 TRANS NO.1 BUS 220KV CB AT KGTS | 39602.3236 | 39602.7208 | REPDAILY | [12 empty] | 0
_1028345839602.3236111111 | 10283458 | 10272619 | Child | FALSE | R2 220/66/22KV TRANS AT KGTS | 39602.3236 | 39602.7208 | REPDAILY | 00017344 | SPIMAINT | Out W/O Perf Calc No2 Transformer | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028337939602.3819444444 | 10283379 |  | Parent | FALSE | MLRC 220KV LINE NO.2 BUS CB AT RCTS | 39602.3819 | 39602.5 | DAILY | [12 empty] | 4
_1024776739602.4166666667 | 10247767 | 10246490 | Child | FALSE | A1 GEN TRANS 500KV X ZONE PROT AT LYPS <RHA> | 39602.4167 | 39602.5035 | CONT | [12 empty] | 0
_1024776939602.4166666667 | 10247769 | 10246490 | Child | FALSE | A1 GEN TRANS 500KV Y ZONE PROT AT LYPS <RHA> | 39602.4167 | 39602.5035 | CONT | [12 empty] | 0
_1028296539602.4423611111 | 10282965 |  | Parent | FALSE | L2 220/22KV TRANS BANK AT RWTS | 39602.4424 | 39602.5125 | DAILY | 00007447 | SPIMAINT | REMOVE BIRD NEST | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028338039602.5152777778 | 10283380 |  | Parent | FALSE | MLRC 220KV LINE NO.1 BUS CB AT RCTS | 39602.5153 | 39602.5833 | DAILY | [12 empty] | 4
_1026934039603.2923611111 | 10269340 |  | Parent | FALSE | TSTS LINE/YPS NO.6 LINE 220KV CB AT ROTS | 39603.2924 | 39604.6222 | CONT | [12 empty] | 0
_1026514439603.29375 | 10265144 | 10272619 | Child | FALSE | NO.2 TRANS NO.1 BUS 220KV CB TRANS SIDE ROI AT KGTS | 39603.2937 | 39603.7174 | REPDAILY | [12 empty] | 0
_1026514639603.29375 | 10265146 | 10272619 | Child | FALSE | NO.2 TRANS NO.2 BUS 220KV CB TRANS SIDE ROI AT KGTS | 39603.2937 | 39603.7174 | REPDAILY | [12 empty] | 0
_1026519339603.29375 | 10265193 | 10272619 | Child | FALSE | NO.2 TRANS 220KV E/SW AT KGTS | 39603.2937 | 39603.7174 | REPDAILY | [12 empty] | 0
_1026519539603.29375 | 10265195 | 10272619 | Child | FALSE | NO.2 TRANS NO.1 BUS 220KV CB TRANS SIDE E/SW AT KGTS | 39603.2937 | 39603.7174 | REPDAILY | [12 empty] | 0
_1026519739603.29375 | 10265197 | 10272619 | Child | FALSE | NO.2 TRANS NO.2 BUS 220KV CB TRANS SIDE E/SW AT KGTS | 39603.2937 | 39603.7174 | REPDAILY | [12 empty] | 0
_1027261939603.29375 | 10272619 |  | Parent | TRUE | NO.2 TRANS NO.1 BUS 220KV CB AT KGTS | 39603.2937 | 39603.7174 | REPDAILY | [12 empty] | 0
_1028345839603.29375 | 10283458 | 10272619 | Child | FALSE | R2 220/66/22KV TRANS AT KGTS | 39603.2937 | 39603.7174 | REPDAILY | 00017344 | SPIMAINT | Out W/O Perf Calc No2 Transformer | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028369239603.3104166667 | 10283692 |  | Parent | FALSE | EX - SMTS LINE/A2 TRANS 500KV CB AT KTS | 39603.3104 | 39603.6472 | DAILY | [12 empty] | 0
_1028338139603.3576388889 | 10283381 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB AT RCTS | 39603.3576 | 39603.4403 | DAILY | [12 empty] | 0
_1028347339603.3576388889 | 10283473 | 10283381 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT RCTS | 39603.3576 | 39603.4403 | DAILY | 00360382 | SPIMAINT | Rebate W/O No1 220kv Cap Bank | SPIPOWER |  |  | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028320539603.3605208333 | 10283205 |  | Parent | FALSE | A1 GEN TRANS 500KV CB CT R/PH AT LYPS | 39603.3605 | 39603.6417 | DAILY | [12 empty] | 0
_1028338239603.4409722222 | 10283382 |  | Parent | TRUE | NO.2 220KV CAPACITOR BANK CB AT RCTS | 39603.441 | 39603.5021 | DAILY | [12 empty] | 0
_1028347239603.4409722222 | 10283472 | 10283382 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RCTS | 39603.441 | 39603.5021 | DAILY | 00360383 | SPIMAINT | Rebate W/O No2 220kv cap bank | SPIPOWER |  |  | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X55658N239604.2854166667 | X55658N2 |  | Parent | FALSE | BRA 66KV FDR CB AT RWTS | 39604.2854 | 39604.884 | DAILY | [12 empty] | 0
_1027050139604.2916666667 | 10270501 |  | Parent | FALSE | MLTS NO.2 LINE/SMTS NO.2 LINE 500KV CB AT SYTS | 39604.2917 | 39605.6153 | CONT | [12 empty] | 0
_1026898639604.3131944445 | 10268986 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT MWTS | 39604.3132 | 39604.6257 | DAILY | [12 empty] | 0
_1027262139604.3201388889 | 10272621 |  | Parent | FALSE | NO.2 TRANS NO.2 BUS 220KV CB AT KGTS | 39604.3201 | 39604.5931 | DAILY | [12 empty] | 0
_1028369439604.3229166667 | 10283694 |  | Parent | FALSE | EX - A4 TRANS NO.1 BUS 500KV CB AT KTS | 39604.3229 | 39604.6569 | DAILY | [12 empty] | 0
_1028387739604.6666666667 | 10283877 |  | Parent | FALSE | EX - A4 TRANS NO.1 BUS 500KV CB AT KTS | 39604.6667 | 39605.3722 | CONT | [12 empty] | 0
_1028390339605.0214467593 | 10283903 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 39605.0214 | 39606.9118 | CONT | 00356083 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027261339605.3125 | 10272613 |  | Parent | FALSE | BETS LINE NO.2 BUS CB AT KGTS | 39605.3125 | 39605.6118 | DAILY | [12 empty] | 0
_1028390439605.3722222222 | 10283904 |  | Parent | TRUE | A4 TRANS NO.1 BUS 500KV CB TRANS SIDE ROI AT KTS | 39605.3722 | 39605.5118 | DAILY | [12 empty] | 0
_1028390839605.3722222222 | 10283908 | 10283904 | Child | FALSE | A4 500/220KV TRANS BANK AT KTS | 39605.3722 | 39605.5118 | DAILY | 00026098 | SPIMAINT | out workorder for faulty a4 tr 1 bus cb t/s roi | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028377639605.5833333333 | 10283776 |  | Parent | FALSE | LY NO.4 66KV FDR NO.3 BUS CB AT MWTS | 39605.5833 | 39605.609 | DAILY | [12 empty] | 0
_1028377939605.6423611111 | 10283779 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 39605.6424 | 39605.6951 | DAILY | [12 empty] | 0
_X56958B939606.2986111111 | X56958B9 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39606.2986 | 39606.6597 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 13, 14 & 15 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V77558B139606.4048611111 | V77558B1 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 39606.4049 | 39606.5736 | DAILY | 00331109 | SPIMAINT | Out W/O No1 66kV Cap bank prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V77558B239606.60625 | V77558B2 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39606.6062 | 39606.6986 | DAILY | 00331118 | SPIMAINT | Out W/O No2 66kV Cap bank prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028401739607.0215277778 | 10284017 |  | Parent | FALSE | BLLY 500KV LINE AT LYPS | 39607.0215 | 39607.1083 | DAILY | 00360516 | GENCO | Basslink Remote Trip for CB fault at BLLY | GENCO |  |  | Circuits | Eastern | 500 | CONNECTION ASSET | EXCLUDED |  | 0
_1028400439607.1541666667 | 10284004 |  | Parent | FALSE | SYN/COND AT TSTS | 39607.1542 | 39607.3319 | CONT | 00007626 | FORCED | Sync Cond shut down for investigation. | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X56958B939607.2986111111 | X56958B9 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39607.2986 | 39607.5222 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 13, 14 & 15 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56958B939608.2930555556 | X56958B9 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39608.2931 | 39608.5944 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 13, 14 & 15 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028400739608.7625 | 10284007 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 39608.7625 | 39615.8854 | CONT | 00356080 | GENCO | Isolation for Genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028393539609.6465277778 | 10283935 |  | Parent | FALSE | NO.2 UNIT 230/10.5KV TRANS AT JLGA | 39609.6465 | 39645.6194 | CONT | 00009821 | GENCO | SCAP to JLGS | GENCO |  |  | Connection Transformers | Eastern | 220 |  |  |  | 0
_Z63358A439610.3131944445 | Z63358A4 |  | Parent | FALSE | HWPS NO.3 220KV LINE AT JLTS | 39610.3132 | 39610.6715 | DAILY | 00015939 | VEN_AUG | HWPS No3 Line Single Day | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028378439610.3958333333 | 10283784 |  | Parent | FALSE | 22KV/415V S/S TRANS AT FTS | 39610.3958 | 39610.7208 | DAILY | 00004393 | DBPROX | VSCAP to Alinta | DISTCO |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1027303939611.3034722222 | 10273039 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT MWTS | 39611.3035 | 39612.5986 | CONT | 00010265 | SPIMAINT | Condition Monitoring Metro Trans 2day Valley Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z63358A139611.3131944445 | Z63358A1 |  | Parent | FALSE | MWTS NO.1 220KV LINE AT JLTS | 39611.3132 | 39612.6819 | CONT | 00015947 | VEN_AUG | MWTS 1 Line outage | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027073039611.4166666667 | 10270730 |  | Parent | FALSE | STANDBY DIESEL GENERATOR AT KTS | 39611.4167 | 39611.6771 | CONT | [12 empty] | 0
_1028411639612.0979166667 | 10284116 |  | Parent | TRUE | NO.4A 66KV CAPACITOR BANK AT SVTS | 39612.0979 | 39612.5743 | CONT | 00004825 | FAULT | Faulty protection relay SPAJ 104 | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028488239612.0979166667 | 10284882 | 10284116 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT SVTS | 39612.0979 | 39612.5743 | DAILY | 00329600 | FORCED | Stranded by fault on 4A 66kV Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028385339612.3152777778 | 10283853 |  | Parent | FALSE | EX - A4 TRANS/B2 TRANS 220KV CB AT KTS | 39612.3153 | 39612.5618 | DAILY | [12 empty] | 0
_Z63358D239612.6666666667 | Z63358D2 |  | Parent | FALSE | HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 39612.6667 | 39623.7083 | CONT | [12 empty] | 0
_X50858C939613.24375 | X50858C9 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 39613.2438 | 39613.6597 | DAILY | 00002830 | SPICAPX | Install Rack Structure Handrails and Lighting | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V60458B539613.2569444444 | V60458B5 |  | Parent | TRUE | ROTS NO.3 500KV LINE AT SMTS | 39613.2569 | 39613.7153 | DAILY | 00012438 | SPICAPX | invoke by-pass in bay "c" | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458C739613.2569444444 | V60458C7 | V60458B5 | Child | FALSE | KTS 500KV LINE AT SMTS | 39613.2569 | 39613.7153 | DAILY | 00012441 | SPICAPX | out workorder for invoking by-pass in bay "c" | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028355439613.2680555556 | 10283554 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39613.2681 | 39613.8132 | CONT | 00354002 | SPIMAINT | Repaire Oil leaks | SPIPOWER |  |  | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_Z63358D139613.3041666667 | Z63358D1 |  | Parent | FALSE | JLTS NO.1 220KV LINE AT MWTS | 39613.3042 | 39613.6694 | DAILY | 00016130 | VEN_AUG | MWTS-JLTS 1 Line outage | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V77558B439613.3395833333 | V77558B4 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 39613.3396 | 39613.6042 | DAILY | 00351939 | SPIMAINT | Out W/O No1 220kV Cap bank prot setting changes | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_V60458B639613.7201388889 | V60458B6 |  | Parent | FALSE | KTS 500KV LINE NO.1 BUS CB AT SMTS | 39613.7201 | 39641.6102 | CONT | [12 empty] | 0
_X56958C039614.2944444444 | X56958C0 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39614.2944 | 39614.7056 | DAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 16 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X66858D639614.3131944445 | X66858D6 |  | Parent | FALSE | TSTS 220KV LINE AT TTS | 39614.3132 | 39614.6674 | DAILY | 00015736 | SPICAPX | Replace insulators tsts - tts line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858D139615.2291666667 | X50858D1 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39615.2292 | 39615.7569 | DAILY | 00017901 | SPICAPX | KTS No2 Ln, Change Line Insulators and Harpstrings | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058AA39615.2645833333 | X32058AA |  | Parent | FALSE | NO.1 11KV/415V S/S TRANS AT MTS | 39615.2646 | 39615.684 | REPDAILY | 00364879 | SPIMAINT | Install the hebel wall | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Other Transformers | Eastern | 11 | NON AER ELEMENT | EXCLUDED |  | 0
_X55658N639615.2708333333 | X55658N6 |  | Parent | FALSE | CYN NO.2 66KV FDR CB AT RWTS | 39615.2708 | 39615.9542 | DAILY | [12 empty] | 0
_X67058A839615.2951388889 | X67058A8 |  | Parent | FALSE | B1 220/66KV TRANS AT TBTS | 39615.2951 | 39618.4903 | CONT | 00004901 | SPICAPX | Replace CT on B1 Trans 220kv CB | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026928539615.3222222222 | 10269285 |  | Parent | FALSE | NO.1 S/S TRANS CB AT RTS | 39615.3222 | 39615.491 | DAILY | [12 empty] | 0
_1027342539615.3395833333 | 10273425 |  | Parent | FALSE | 5 GRP TRANS 220KV CB CT R/PH AT YPS | 39615.3396 | 39615.491 | DAILY | [12 empty] | 0
_1026783639615.4270833333 | 10267836 |  | Parent | FALSE | B5 220/66KV TRANS GROUP AT BLTS | 39615.4271 | 39616.6583 | CONT | 00018452 | SPIMAINT | OVERHAUL OF A TRANSFORMER BANK/GROUP | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027343739615.5284722222 | 10273437 |  | Parent | FALSE | ROTS NO.6 220KV LINE NO.2 BUS CB CT R/PH AT YPS | 39615.5285 | 39615.5938 | DAILY | [12 empty] | 0
_1028438939615.8180555556 | 10284389 |  | Parent | FALSE | EX - LDL NO.1 66KV FDR CB AT RWTS | 39615.8181 | 39616.0167 | CONT | [12 empty] | 0
_X55658N339615.9826388889 | X55658N3 |  | Parent | FALSE | BRA 66KV FDR CB AT RWTS | 39615.9826 | 39621.3194 | CONT | [12 empty] | 0
_X50858D339616.2298611111 | X50858D3 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39616.2299 | 39616.7917 | DAILY | 00017900 | SPICAPX | KTS No1 Ln, Replace Insulators and harpstrings | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058AA39616.2729166667 | X32058AA |  | Parent | FALSE | NO.1 11KV/415V S/S TRANS AT MTS | 39616.2729 | 39616.6771 | REPDAILY | 00364879 | SPIMAINT | Install the hebel wall | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Other Transformers | Eastern | 11 | NON AER ELEMENT | EXCLUDED |  | 0
_1027271139616.2916666667 | 10272711 |  | Parent | TRUE | NO.2 220KV BUS E/SW AT EPSY | 39616.2917 | 39617.7292 | CONT | [12 empty] | 0
_1028364439616.2916666667 | 10283644 | 10272711 | Child | FALSE | MBTS NO.1 220KV LINE AT EPSY | 39616.2917 | 39617.7292 | CONT | 00087035 | SPIMAINT | Rebate W/O MBTS No1 Line during No2 220 Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1027344939616.325 | 10273449 |  | Parent | FALSE | EX - W3 GEN TRANS NO.1 BUS 220KV CB CT R/PH AT YPS | 39616.325 | 39616.4479 | DAILY | [12 empty] | 0
_1028433939616.4576388889 | 10284339 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39616.4576 | 39616.4681 | DAILY | [12 empty] | 0
_1027345339616.53125 | 10273453 |  | Parent | FALSE | W3 GEN TRANS NO.2 BUS 220KV CB CT R/PH AT YPS | 39616.5312 | 39616.5778 | DAILY | [12 empty] | 0
_X50858D539617.2291666667 | X50858D5 |  | Parent | FALSE | EX - KTS NO.3 220KV LINE AT GTS | 39617.2292 | 39617.6597 | DAILY | 00017902 | SPICAPX | KTS No3 Ln, Replace Insulators and harpstrings | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058AA39617.2729166667 | X32058AA |  | Parent | FALSE | NO.1 11KV/415V S/S TRANS AT MTS | 39617.2729 | 39617.6986 | REPDAILY | 00364879 | SPIMAINT | Install the hebel wall | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Other Transformers | Eastern | 11 | NON AER ELEMENT | EXCLUDED |  | 0
_1027024339617.3166666667 | 10270243 |  | Parent | FALSE | SYN/COND TRANS NO.2 BUS 66KV CB AT BLTS | 39617.3167 | 39617.6528 | DAILY | [12 empty] | 0
_1028365239617.3236111111 | 10283652 |  | Parent | TRUE | APD NO.1 500KV LINE CVT R/PH AT HYTS | 39617.3236 | 39617.959 | DAILY | [12 empty] | 0
_1028365339617.3236111111 | 10283653 | 10283652 | Child | FALSE | APD NO.1 500KV LINE AT HYTS | 39617.3236 | 39617.959 | DAILY | 00027386 | SPIMAINT | Line outage rebate for APD NO.1 500KV LINE | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028449139617.8666666667 | 10284491 |  | Parent | TRUE | MLTS-HYTS 2 500KV W | 39617.8667 | 39617.9507 | DAILY | 00022633 | FAULT | MLTS-HYTS-APD 2 Line Trip | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028449239617.8666666667 | 10284492 | 10284491 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 39617.8667 | 39617.9507 | DAILY | 00002862 | FAULT | MLTS-HYTS-APD 2 Line Trip | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028365439617.8666666667 | 10283654 |  | Parent | FALSE | APD NO.2 500KV LINE CVT R/PH AT HYTS | 39617.8667 | 39618.4236 | CONT | [12 empty] | 0
_1028449339617.8666666667 | 10284493 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39617.8667 | 39619.4236 | CONT | 00319999 | FAULT | MLTS-HYTS-APD 2 Line Trip | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858D239618.25 | X50858D2 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39618.25 | 39618.7285 | REPDAILY | 00017901 | SPICAPX | KTS No2 Ln, Demolish and Consruct footings, Bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058AA39618.2708333333 | X32058AA |  | Parent | FALSE | NO.1 11KV/415V S/S TRANS AT MTS | 39618.2708 | 39618.5972 | REPDAILY | 00364879 | SPIMAINT | Install the hebel wall | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Other Transformers | Eastern | 11 | NON AER ELEMENT | EXCLUDED |  | 0
_1028451339618.3013888889 | 10284513 |  | Parent | FALSE | LY NO.1 66KV FDR AT MWTS | 39618.3014 | 39618.3771 | CONT | 00016140 | FAULT | LY NO.1 66KV LINE FAULT | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027050439618.3111111111 | 10270504 |  | Parent | FALSE | SMTS NO.2 500KV LINE NO.1 BUS CB AT SYTS | 39618.3111 | 39619.6382 | CONT | [12 empty] | 0
_1027033739618.3166666667 | 10270337 |  | Parent | FALSE | EX - B4 TRANS NO.2 BUS 220KV CB AT TTS | 39618.3167 | 39619.6285 | CONT | [12 empty] | 0
_1028453739618.71875 | 10284537 |  | Parent | FALSE | NO.2 220KV BUS AT EPSY | 39618.7188 | 39618.7208 | DAILY | 00357774 | SPIMAINT | EPS: No 2 220kV Bus Outage | SPIPOWER |  |  | Bus | 3rd Party | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858D239619.25 | X50858D2 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39619.25 | 39619.6701 | REPDAILY | 00017901 | SPICAPX | KTS No2 Ln, Demolish and Consruct footings, Bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027345939619.31875 | 10273459 |  | Parent | FALSE | EX - NO.3 MAIN TRANS NO.1 BUS 500KV CB CT R/PH AT HWTS | 39619.3187 | 39619.4667 | DAILY | [12 empty] | 0
_1028356239619.3513888889 | 10283562 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT GNTS | 39619.3514 | 39619.4653 | DAILY | [12 empty] | 0
_1028356439619.3513888889 | 10283564 | 10283562 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT GNTS | 39619.3514 | 39619.4653 | DAILY | 00329962 | SPIMAINT | Rebate W/O No1 66kv Cap Bank | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028356639619.4659722222 | 10283566 |  | Parent | FALSE | SHTS NO.3 220KV LINE NO.2 BUS CB AT GNTS | 39619.466 | 39619.6285 | DAILY | [12 empty] | 0
_1028455539619.6145833333 | 10284555 |  | Parent | FALSE | R3 TRANS NO.2 BUS 220KV CB AT RCTS | 39619.6146 | 39619.7097 | DAILY | [12 empty] | 0
_1028449539619.6236111111 | 10284495 |  | Parent | FALSE | LYPS NO.3 500KV LINE NO.4 BUS CB AT HWTS | 39619.6236 | 39619.6278 | DAILY | [12 empty] | 0
_1028355539620.2611111111 | 10283555 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT CBTS | 39620.2611 | 39621.6438 | CONT | 00359493 | SPIMAINT | Repaire Oil leaks | SPIPOWER |  |  | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_X56958C239620.2923611111 | X56958C2 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39620.2924 | 39620.6979 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 17 & 18 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V78658A139620.2951388889 | V78658A1 |  | Parent | TRUE | NO.1 66KV BUS AT CBTS | 39620.2951 | 39620.6882 | DAILY | 00359470 | SPIMAINT | Install lower under slung isols on No 1 66kv bus | SPIPOWER | V786 | V786 - (CBTS) URGENT REPLACEMENT OF ROTS 4L 500KV CVT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_V78658A239620.2951388889 | V78658A2 | V78658A1 | Child | FALSE | B1 220/66KV TRANS AT CBTS | 39620.2951 | 39620.6882 | DAILY | 00353076 | SPIMAINT | Rebate Trans for Bus outage | SPIPOWER | V786 | V786 - (CBTS) URGENT REPLACEMENT OF ROTS 4L 500KV CVT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_V77558B639620.3388888889 | V77558B6 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT RCTS | 39620.3389 | 39620.7632 | REPDAILY | 00360382 | SPIMAINT | Out W/O No1 220kV Cap bank prot setting changes | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028403539620.4638888889 | 10284035 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT RTS | 39620.4639 | 39621.2944 | CONT | 00021385 | DBPROX | Request by City Power | DISTCO |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56958C239621.29375 | X56958C2 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39621.2937 | 39621.6944 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 17 & 18 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658O739621.3180555556 | X55658O7 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39621.3181 | 39621.5083 | DAILY | 00007480 | SPICAPX | Install Bus Side Connection Future Sub RWN No1 CB | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X55658O839621.3180555556 | X55658O8 | X55658O7 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 39621.3181 | 39621.5083 | DAILY | 00007450 | SPICAPX | Rebate Tran for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X55658O939621.5097222222 | X55658O9 |  | Parent | FALSE | RWN NO.1 66KV FDR CB AT RWTS | 39621.5097 | 39627.3194 | CONT | [12 empty] | 0
_V77558B639621.6388888889 | V77558B6 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT RCTS | 39621.6389 | 39621.8271 | REPDAILY | 00360382 | SPIMAINT | Out W/O No1 220kV Cap bank prot setting changes | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X50858D439622.2625 | X50858D4 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39622.2625 | 39622.6875 | REPDAILY | 00017901 | SPICAPX | KTS No2 Ln, Demolish &construct footings in Bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858D639622.3104166667 | X50858D6 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT GTS | 39622.3104 | 39622.3549 | CONT | [12 empty] | 0
_V77558B839622.3611111111 | V77558B8 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39622.3611 | 39622.7674 | DAILY | 00359891 | SPIMAINT | Out W/O No1 66kV Cap bank prot setting changes | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X50858D439623.2340277778 | X50858D4 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39623.234 | 39623.7438 | REPDAILY | 00017901 | SPICAPX | KTS No2 Ln, Demolish &construct footings in Bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858D939623.2708333333 | X50858D9 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT GTS | 39623.2708 | 39626.5625 | CONT | [12 empty] | 0
_Z63358E239623.2951388889 | Z63358E2 |  | Parent | FALSE | MWTS NO.1 220KV LINE AT JLTS | 39623.2951 | 39623.7118 | DAILY | 00015947 | VEN_AUG | RECONNECT HWPS4L/MWTS1L CB MWTS1L ISOL | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026206239623.2979166667 | 10262062 | 10269326 | Child | FALSE | NO.2 TRANS 66KV CB ISOL AT SVTS | 39623.2979 | 39623.6569 | DAILY | [12 empty] | 0
_1026932639623.2979166667 | 10269326 |  | Parent | TRUE | NO.2 66KV BUS AT SVTS | 39623.2979 | 39623.6569 | DAILY | 00004861 | SPIMAINT | O/Haul NO.2 66KV BUS AT SVTS | SPIPOWER |  |  | Bus | Eastern | 66 |  |  |  | 0
_1028264439623.2979166667 | 10282644 | 10269326 | Child | FALSE | B2 220/66KV TRANS AT SVTS | 39623.2979 | 39623.6569 | DAILY | 00004850 | SPIMAINT | tran rebate for bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027034139623.3097222222 | 10270341 |  | Parent | FALSE | EX - B4 TRANS NO.1 BUS 220KV CB AT TTS | 39623.3097 | 39625.6771 | CONT | [12 empty] | 0
_1026998539623.3145833333 | 10269985 |  | Parent | FALSE | 3-4 220KV BUS TIE CB AT FBTS | 39623.3146 | 39624.6243 | CONT | [12 empty] | 0
_1027346139623.3833333333 | 10273461 |  | Parent | FALSE | EX - NO.4 MAIN TRANS NO.1 BUS 500KV CB CT R/PH AT HWTS | 39623.3833 | 39623.475 | DAILY | [12 empty] | 0
_1028460839623.4520833333 | 10284608 |  | Parent | FALSE | DDTS NO.1 330KV LINE SERIES CAPACITOR BANK AT SMTS | 39623.4521 | 39623.4639 | CONT | 00327836 | FAULT | SMTS - DDTS No 1 Line Series Cap Bank Bypassed | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1028461639623.7083333333 | 10284616 |  | Parent | FALSE | HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 39623.7083 | 39624.3139 | CONT | [12 empty] | 0
_X50858D439624.2534722222 | X50858D4 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39624.2535 | 39624.6931 | REPDAILY | 00017901 | SPICAPX | KTS No2 Ln, Demolish &construct footings in Bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027270939624.2902777778 | 10272709 |  | Parent | TRUE | NO.1 220KV BUS E/SW AT EPSY | 39624.2903 | 39625.6569 | CONT | [12 empty] | 0
_1028361239624.2902777778 | 10283612 | 10272709 | Child | FALSE | MBTS NO.2 220KV LINE AT EPSY | 39624.2903 | 39625.6569 | CONT | 00087036 | SPIMAINT | Rebate W/O MBTS No2 Line during No1 220 Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1026907439624.3118055556 | 10269074 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB AT HWTS | 39624.3118 | 39624.6007 | DAILY | [12 empty] | 0
_Z63358A639624.3118055556 | Z63358A6 |  | Parent | FALSE | HWPS NO.4 220KV LINE AT JLTS | 39624.3118 | 39626.6229 | CONT | 00015940 | VEN_AUG | HWPS No4 Line Continous | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028459439624.3173611111 | 10284594 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 39624.3174 | 39624.7201 | DAILY | 00060938 | APDALCOA | Work at APD No2 Reactor Gas Relay | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X50858D439625.25 | X50858D4 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39625.25 | 39625.7007 | REPDAILY | 00017901 | SPICAPX | KTS No2 Ln, Demolish &construct footings in Bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028461939625.3111111111 | 10284619 |  | Parent | FALSE | B3 TRANS 66KV CB AT FBTS | 39625.3111 | 39625.4965 | DAILY | [12 empty] | 0
_1028466739625.6777777778 | 10284667 |  | Parent | TRUE | NO.1 275KV CAPACITOR BANK/SESS NO.2 LINE CB CT R/PH AT HYTS | 39625.6778 | 39626.5181 | CONT | [12 empty] | 0
_1028467139625.6777777778 | 10284671 | 10284667 | Child | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 39625.6778 | 39626.5181 | CONT | 00331027 | SPIMAINT | Rebate W/O No1 275kV Cap bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028469639625.7895833333 | 10284696 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 39625.7896 | 39628.8549 | CONT | 00356081 | GENCO | Switching for Gen-Co | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858D439626.2527777778 | X50858D4 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39626.2528 | 39626.7264 | REPDAILY | 00017901 | SPICAPX | KTS No2 Ln, Demolish &construct footings in Bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028469739626.3034722222 | 10284697 |  | Parent | FALSE | NO.1 220KV BUS AT EPSY | 39626.3035 | 39626.3056 | CONT | 00357773 | GENCO | De-energisation of No 1 220 kV Bus for AGL Hydro | STHHYDRO |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026900739626.3111111111 | 10269007 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT MWTS | 39626.3111 | 39626.6285 | DAILY | [12 empty] | 0
_1027019139626.3125 | 10270191 |  | Parent | FALSE | SYN/COND TRANS NO.3 BUS 66KV CB AT FBTS | 39626.3125 | 39626.5986 | DAILY | [12 empty] | 0
_Z63358D639626.6180555556 | Z63358D6 |  | Parent | FALSE | HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 39626.6181 | 39637.3271 | CONT | [12 empty] | 0
_1028471039626.9909722222 | 10284710 |  | Parent | FALSE | NO.1 GEN 220/16.5KV TRANS AT HWPS | 39626.991 | 39630.1125 | CONT | 00009642 | GENCO | Power Station requirements | GENCO |  | Updated from isolation to earthing SCAP 28/06 Bert | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_X50858D739627.2319444444 | X50858D7 |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 39627.2319 | 39627.7479 | DAILY | 00002828 | SPICAPX | B1 Trans OUT W/O - Replace Insulators at the Rack | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56958C339627.2944444444 | X56958C3 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39627.2944 | 39627.6556 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Runs 19 & 20 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024989739627.2951388889 | 10249897 |  | Parent | FALSE | B5 220/66KV TRANS AT TTS | 39627.2951 | 39627.7364 | REPDAILY | 00327874 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X66858D739627.3013888889 | X66858D7 |  | Parent | FALSE | TSTS 220KV LINE AT TTS | 39627.3014 | 39627.6681 | REPDAILY | 00015736 | SPICAPX | Replace insulators tsts - tts line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658O139627.4006944444 | X55658O1 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39627.4007 | 39627.4632 | DAILY | 00007480 | SPICAPX | Pressure Test Future Sub RWN1 Fdr CB | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X55658O239627.4006944444 | X55658O2 | X55658O1 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 39627.4007 | 39627.4632 | DAILY | 00007450 | SPICAPX | Trans Rebate for Bus Outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1024989739628.2902777778 | 10249897 |  | Parent | FALSE | B5 220/66KV TRANS AT TTS | 39628.2903 | 39628.6424 | REPDAILY | 00327874 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56958C339628.2951388889 | X56958C3 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39628.2951 | 39628.7167 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Runs 19 & 20 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V78658A339628.2979166667 | V78658A3 |  | Parent | TRUE | NO.3 66KV BUS AT CBTS | 39628.2979 | 39628.6118 | DAILY | 00359472 | SPIMAINT | Install lower under slung isols on No 3 66kv bus | SPIPOWER | V786 | V786 - (CBTS) URGENT REPLACEMENT OF ROTS 4L 500KV CVT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_V78658A439628.2979166667 | V78658A4 | V78658A3 | Child | FALSE | B2 220/66KV TRANS AT CBTS | 39628.2979 | 39628.6118 | DAILY | 00353077 | SPIMAINT | Rebate Trans for Bus outage | SPIPOWER | V786 | V786 - (CBTS) URGENT REPLACEMENT OF ROTS 4L 500KV CVT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X66858D739628.3013888889 | X66858D7 |  | Parent | FALSE | TSTS 220KV LINE AT TTS | 39628.3014 | 39628.625 | REPDAILY | 00015736 | SPICAPX | Replace insulators tsts - tts line | SPIPOWER | X668 | X668 - REPLACE WORN 16MM PIN INSULATORS ON ROAD CROSSINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028477939628.6277777778 | 10284779 |  | Parent | FALSE | 2-3 66KV BUS TIE CB NO.2 BUS SIDE ISOL AT CBTS | 39628.6278 | 39628.6923 | DAILY | [12 empty] | 0
_1028478039628.8618055556 | 10284780 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 39628.8618 | 39636.5743 | CONT | 00356086 | GENCO | GEN-C0 Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858E039629.2291666667 | X50858E0 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39629.2292 | 39629.8125 | DAILY | 00017900 | SPICAPX | KTS No1 Ln, Replace harpstrings and bridges | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027255139629.2916666667 | 10272551 |  | Parent | FALSE | B3 TRANS 220KV ROI AT ATS | 39629.2917 | 39631.5729 | CONT | [12 empty] | 0
_1027266739629.3361111111 | 10272667 | 10272883 | Child | FALSE | AUX 'D' 220/22KV TRANS 220KV CB AT YPS | 39629.3361 | 39630.5764 | CONT | [12 empty] | 0
_1027288339629.3361111111 | 10272883 |  | Parent | TRUE | AUX D 220/22KV TRANS AT YPS | 39629.3361 | 39630.5764 | CONT | 00356098 | SPIMAINT | Overhaul Transformer at YPS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Owned by SPAusNet | 0
_1027290939629.3361111111 | 10272909 | 10272883 | Child | FALSE | AUX 'D' 220/22KV TRANS 220KV CB TRANS SIDE ROI AT YPS | 39629.3361 | 39630.5764 | CONT | [12 empty] | 0
_1027291739629.3361111111 | 10272917 | 10272883 | Child | FALSE | AUX 'D' 220/22KV TRANS 220KV CB TRANS SIDE E/SW AT YPS | 39629.3361 | 39630.5764 | CONT | [12 empty] | 0
_1027291939629.3361111111 | 10272919 | 10272883 | Child | FALSE | AUX 'D' 220/22KV TRANS 220KV E/SW AT YPS | 39629.3361 | 39630.5764 | CONT | [12 empty] | 0
_X55658R139629.4861111111 | X55658R1 |  | Parent | FALSE | RWN NO.1 66KV FDR CB AT RWTS | 39629.4861 | 39638.2292 | CONT | [12 empty] | 0
_1028481839629.5069444444 | 10284818 |  | Parent | FALSE | B2 220/66KV TRANS AT RWTS | 39629.5069 | 39629.6868 | DAILY | 00007450 | FAULT | B2 Trans wiring modifications | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028467239629.5465277778 | 10284672 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39629.5465 | 39629.709 | REPDAILY | 00319999 | APDALCOA | APD work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027348539629.575 | 10273485 |  | Parent | FALSE | B2 220/66KV TRANS AT HOTS | 39629.575 | 39629.691 | DAILY | 00363103 | SPIMAINT | O/HAUL Transformer Div Mechanism (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028470939629.5958333333 | 10284709 |  | Parent | FALSE | JLGB 220KV BUS AT JLGB | 39629.5958 | 39629.7188 | CONT | 00325273 | GENCO | JLGS B Station Bus | GENCO |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026932839630.2916666667 | 10269328 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT ROTS | 39630.2917 | 39630.6431 | DAILY | 00004761 | SPIMAINT | O/H No 2 S/S Trans,Surge Div at ROTS | SPIPOWER |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1010068839630.3069444444 | 10100688 |  | Parent | FALSE | B NTH - C NTH 22KV BUS TIE CB AT RTS | 39630.3069 | 39630.5944 | DAILY | [12 empty] | 0
_1028411939630.3194444444 | 10284119 |  | Parent | FALSE | LY NO.4 66KV FDR NO.3 BUS CB AT MWTS | 39630.3194 | 39630.6625 | DAILY | [12 empty] | 0
_1027260339630.3340277778 | 10272603 |  | Parent | FALSE | NO.2 66KV REACTOR AT HOTS | 39630.334 | 39630.6375 | DAILY | 00357255 | SPIMAINT | O/Haul - 66kV reactor | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028485939630.4284722222 | 10284859 |  | Parent | FALSE | B1 TRANS NO.2 BUS 220KV CB AT RWTS | 39630.4285 | 39630.4854 | CONT | [12 empty] | 0
_1028412139631.2944444444 | 10284121 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB AT ROTS | 39631.2944 | 39631.725 | DAILY | [12 empty] | 0
_1028501539631.2944444444 | 10285015 | 10284121 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 39631.2944 | 39631.725 | DAILY | 00354024 | SPIMAINT | Rebate for Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1010069039631.3055555556 | 10100690 |  | Parent | FALSE | B NTH - B STH 22KV BUS TIE CB AT RTS | 39631.3056 | 39631.5667 | DAILY | [12 empty] | 0
_1027286939631.3298611111 | 10272869 | 10272885 | Child | FALSE | AUX 'E' 220/22KV TRANS 220KV CB AT YPS | 39631.3299 | 39632.575 | CONT | [12 empty] | 0
_1027288539631.3298611111 | 10272885 |  | Parent | TRUE | AUX E 220/22KV TRANS AT YPS | 39631.3299 | 39632.575 | CONT | 00358032 | SPIMAINT | Overhaul Transformer at YPS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Owned by SPAusNet | 0
_1027291539631.3298611111 | 10272915 | 10272885 | Child | FALSE | AUX 'E' 220/22KV TRANS 220KV CB TRANS SIDE ROI AT YPS | 39631.3299 | 39632.575 | CONT | [12 empty] | 0
_1027292339631.3298611111 | 10272923 | 10272885 | Child | FALSE | AUX 'E' 220/22KV TRANS 220KV CB TRANS SIDE E/SW AT YPS | 39631.3299 | 39632.575 | CONT | [12 empty] | 0
_1027292539631.3298611111 | 10272925 | 10272885 | Child | FALSE | AUX 'E' 220/22KV TRANS 220KV E/SW AT YPS | 39631.3299 | 39632.575 | CONT | [12 empty] | 0
_X67058B339631.3979166667 | X67058B3 |  | Parent | FALSE | A1 TRANS/NO.2 CSC CB AT ROTS | 39631.3979 | 39631.6292 | DAILY | [12 empty] | 0
_1028463139632.2986111111 | 10284631 |  | Parent | TRUE | NO.3 220KV CAPACITOR BANK CB AT TTS | 39632.2986 | 39632.6076 | DAILY | [12 empty] | 0
_1028501739632.2986111111 | 10285017 | 10284631 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT TTS | 39632.2986 | 39632.6076 | DAILY | 00327615 | SPIMAINT | out w/o for cap bank HPL - B1GS CB TESTING BY ABB | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1010068939632.3034722222 | 10100689 |  | Parent | FALSE | B STH - C STH 22KV BUS TIE CB AT RTS | 39632.3035 | 39632.5917 | DAILY | [12 empty] | 0
_1027790339632.3097222222 | 10277903 |  | Parent | TRUE | T159 MLTS-BATS 2 220KV | 39632.3097 | 39632.6861 | DAILY | [12 empty] | 0
_1028447539632.3097222222 | 10284475 | 10277903 | Child | FALSE | MLTS-BATS 2 220KV WY | 39632.3097 | 39632.6861 | DAILY | 00022731 | SPIMAINT | Rebate W/O MLTS-BATS 2 Line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027254539632.3111111111 | 10272545 |  | Parent | FALSE | B2 TRANS/B3 TRANS 220KV CB AT ATS | 39632.3111 | 39632.6132 | DAILY | [12 empty] | 0
_X55658R339633.28125 | X55658R3 |  | Parent | FALSE | 1-2 EXT 66KV BUS TIE CB AT RWTS | 39633.2812 | 39648.4167 | CONT | [12 empty] | 0
_1010344939633.3020833333 | 10103449 |  | Parent | FALSE | A STH - B STH 22KV BUS TIE CB AT RTS | 39633.3021 | 39633.5778 | DAILY | [12 empty] | 0
_1027348339633.3270833333 | 10273483 |  | Parent | FALSE | B3 220/66KV TRANS AT HOTS | 39633.3271 | 39633.5556 | DAILY | 00363102 | SPIMAINT | O/HAUL Transformer Div Mechanism (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026997839633.3645833333 | 10269978 |  | Parent | FALSE | B1 220/66KV TRANS AT WMTS | 39633.3646 | 39633.6319 | DAILY | 00003233 | SPIMAINT | O/HAUL Transformer Div Mechanism - bucs | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027783039633.3666666667 | 10277830 |  | Parent | TRUE | S368 BATS-WBTS 220KV | 39633.3667 | 39633.5764 | DAILY | [12 empty] | 0
_1028447639633.3666666667 | 10284476 | 10277830 | Child | FALSE | EX - BATS-HOTS 220KV W | 39633.3667 | 39633.5764 | DAILY | 00026089 | SPIMAINT | Rebate W/O BATS-HOTS Line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028498039633.8590277778 | 10284980 |  | Parent | FALSE | A1 GEN TRANS 500KV CB AT LYPS | 39633.859 | 39634.0382 | CONT | [12 empty] | 0
_X56958C439634.275 | X56958C4 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39634.275 | 39634.7562 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Runs 21 & 22 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027783539634.3097222222 | 10277835 |  | Parent | TRUE | S233 MLTS-TGTS 220KV | 39634.3097 | 39634.5236 | DAILY | [12 empty] | 0
_1028447739634.3097222222 | 10284477 | 10277835 | Child | FALSE | MLTS-TGTS 220KV W | 39634.3097 | 39634.5236 | DAILY | 00022740 | SPIMAINT | Rebate W/O MLTS-TGTS Line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V77558C239634.4361111111 | V77558C2 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 39634.4361 | 39634.8493 | DAILY | 00359897 | SPIMAINT | Out W/O No2 66kV Cap bank prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X56958C439635.2923611111 | X56958C4 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39635.2924 | 39635.7069 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Runs 21 & 22 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V76958B439635.3270833333 | V76958B4 |  | Parent | TRUE | NO.1 220KV BUS AT CBTS | 39635.3271 | 39635.6257 | DAILY | 00359378 | SPICAPX | No 1 220kv Bus & No1 66kv Bus | SPIPOWER | V769 | V769 - (CBTS) PRIMARY EQUIPMENT DEFECTS REPAIR | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V76958B539635.3270833333 | V76958B5 | V76958B4 | Child | FALSE | B1 220/66KV TRANS AT CBTS | 39635.3271 | 39635.6257 | DAILY | 00353076 | SPICAPX | Tran Rebate for Bus Outage | SPIPOWER | V769 | V769 - (CBTS) PRIMARY EQUIPMENT DEFECTS REPAIR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_V77558C039635.3361111111 | V77558C0 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT HOTS | 39635.3361 | 39635.7417 | REPDAILY | 00359898 | SPIMAINT | Out W/O No1A/B 66kV Cap banks prot setting changes | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V77558C139635.3361111111 | V77558C1 | V77558C0 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HOTS | 39635.3361 | 39635.7417 | DAILY | 00359901 | SPIMAINT | Rebate W/O 1B 66kV Cap during prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028498939636.3333333333 | 10284989 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39636.3333 | 39636.634 | DAILY | 00022691 | APDALCOA | PTH Work | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_V77558C039636.5736111111 | V77558C0 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT HOTS | 39636.5736 | 39636.7944 | REPDAILY | 00359898 | SPIMAINT | Out W/O No1A/B 66kV Cap banks prot setting changes | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V77558C139636.5736111111 | V77558C1 | V77558C0 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HOTS | 39636.5736 | 39636.7944 | DAILY | 00359901 | SPIMAINT | Rebate W/O 1B 66kV Cap during prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028362339637.2986111111 | 10283623 |  | Parent | FALSE | B3 220/66KV TRANS AT HTS | 39637.2986 | 39637.6097 | DAILY | 00004447 | SPIMAINT | SCAN Repaire hot joint | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X55658R239637.3013888889 | X55658R2 |  | Parent | FALSE | 1-3 66KV BUS TIE CB AT RWTS | 39637.3014 | 39637.3326 | DAILY | [12 empty] | 0
_1027022239637.3020833333 | 10270222 |  | Parent | FALSE | B4 220/66KV TRANS AT BLTS | 39637.3021 | 39638.6424 | CONT | 00002615 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027050739637.3125 | 10270507 |  | Parent | FALSE | NO.1 500KV BUS AT SYTS | 39637.3125 | 39638.6771 | CONT | 00001389 | SPIMAINT | O/Haul NO.1 500KV BUS AT SYTS | SPIPOWER |  |  | Bus | Western | 500 |  |  |  | 0
_1028471139637.3215277778 | 10284711 |  | Parent | FALSE | EX - B2 TRANS NO.1 BUS 220KV CB CT R/PH AT KTS | 39637.3215 | 39637.5861 | DAILY | [12 empty] | 0
_Z63358A539637.3243055556 | Z63358A5 |  | Parent | FALSE | HWPS NO.4 220KV LINE AT JLTS | 39637.3243 | 39637.6875 | DAILY | 00015940 | VEN_AUG | HWPS No4 Line Day | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V77558C439637.3777777778 | V77558C4 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 39637.3778 | 39637.6813 | DAILY | 00359897 | SPIMAINT | Out W/O No2 66kV Cap bank prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X55658O439638.0055555556 | X55658O4 |  | Parent | FALSE | RWN NO.1 66KV FDR CB AT RWTS | 39638.0056 | 39638.2417 | DAILY | [12 empty] | 0
_X55658O539638.2326388889 | X55658O5 |  | Parent | FALSE | RWN NO.1 66KV FDR CB AT RWTS | 39638.2326 | 39638.6807 | DAILY | [12 empty] | 0
_1028504739638.2486111111 | 10285047 |  | Parent | FALSE | NO.3 66KV CAPACITOR BANK AT WMTS | 39638.2486 | 39638.6042 | CONT | 00003191 | FAULT | No3 66kV Cap Bank Tripped for an X prot relay faul | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027302939638.2875 | 10273029 |  | Parent | FALSE | R4 220/66/22KV TRANS AT BETS | 39638.2875 | 39640.5389 | CONT | 00016220 | SPIMAINT | Condition Monitoring Country Trans 2day North | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028471339638.3125 | 10284713 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE NO.3 BUS CB CT R/PH AT KTS | 39638.3125 | 39638.6479 | DAILY | [12 empty] | 0
_Z63358D339638.3159722222 | Z63358D3 |  | Parent | FALSE | MWTS NO.1 220KV LINE AT JLTS | 39638.316 | 39638.325 | CONT | 00015947 | VEN_AUG | MWTS 1 Line outage | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658R439638.6597222222 | X55658R4 |  | Parent | FALSE | 1-2 66KV TIE BUS AT RWTS | 39638.6597 | 39641.625 | CONT | 00364661 | SPICAPX | No 2 EXT 66kv Bus | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1010066839639.2979166667 | 10100668 |  | Parent | FALSE | A NTH 22KV BUS AT RTS | 39639.2979 | 39639.6215 | DAILY | 00007354 | SPIMAINT | O/HAUL - 22kv Outdoor Bus & 22KV Fdr 134 | SPIPOWER |  |  | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1028471539639.3180555556 | 10284715 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE NO.3 BUS CB CT R/PH AT KTS | 39639.3181 | 39639.6292 | DAILY | [12 empty] | 0
_1027026139639.31875 | 10270261 |  | Parent | FALSE | SYN/COND TRANS NO.4 BUS 66KV CB AT BLTS | 39639.3187 | 39639.6076 | DAILY | [12 empty] | 0
_1028481539639.3652777778 | 10284815 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT GNTS | 39639.3653 | 39639.4403 | DAILY | [12 empty] | 0
_1028502139639.3763888889 | 10285021 |  | Parent | FALSE | B2 220/66KV TRANS AT HOTS | 39639.3764 | 39639.6222 | DAILY | 00363103 | SPIMAINT | Investigate incorrect B2 Tran Gas Relay operation | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028507539639.4611111111 | 10285075 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 39639.4611 | 39639.5146 | DAILY | [12 empty] | 0
_1028481639639.4784722222 | 10284816 |  | Parent | FALSE | DDTS NO.1 LINE/SHTS NO.1 LINE 220KV CB AT GNTS | 39639.4785 | 39639.5174 | DAILY | [12 empty] | 0
_1028455439639.5763888889 | 10284554 |  | Parent | FALSE | R3 TRANS NO.2 BUS 220KV CB AT RCTS | 39639.5764 | 39639.6639 | DAILY | [12 empty] | 0
_1028509839640.125 | 10285098 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39640.125 | 39640.2194 | DAILY | 00011755 | FAULT | MBTS-MKPS 220kV Line Outage | SPIPOWER |  |  | Circuits | 3rd Party | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358D339640.3104166667 | Z63358D3 |  | Parent | FALSE | MWTS NO.1 220KV LINE AT JLTS | 39640.3104 | 39640.5028 | CONT | 00015947 | VEN_AUG | MWTS 1 Line outage | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028471739640.3131944445 | 10284717 |  | Parent | FALSE | EX - GTS NO.1 220KV LINE NO.3 BUS CB CT R/PH AT KTS | 39640.3132 | 39640.6784 | DAILY | [12 empty] | 0
_1027018939640.3159722222 | 10270189 |  | Parent | FALSE | SYN/COND TRANS NO.2 BUS 66KV CB AT FBTS | 39640.316 | 39640.6236 | DAILY | [12 empty] | 0
_1028509139640.4618055556 | 10285091 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 39640.4618 | 39648.9569 | CONT | 00356083 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X55658P439641.2743055556 | X55658P4 |  | Parent | TRUE | NO.2 66KV BUS AT RWTS | 39641.2743 | 39641.5319 | DAILY | 00007479 | SPICAPX | Upgrade No2 Bus Side Droppers to 2-4 66kv B/T CB | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 |  |  |  | 0
_X55658P539641.2743055556 | X55658P5 | X55658P4 | Child | FALSE | B3 220/66KV TRANS AT RWTS | 39641.2743 | 39641.5319 | DAILY | 00007455 | SPICAPX | Trans Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X55658P639641.2743055556 | X55658P6 | X55658P4 | Child | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39641.2743 | 39641.5319 | DAILY | 00007399 | SPICAPX | Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X55658P739641.2743055556 | X55658P7 | X55658P4 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39641.2743 | 39641.5319 | DAILY | 00331179 | SPICAPX | Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028364039641.3104166667 | 10283640 |  | Parent | FALSE | NO.2 66KV BUS AT HTS | 39641.3104 | 39641.6062 | DAILY | 00004457 | SPIMAINT | SCAN repaire hot joint | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1028209339641.3951388889 | 10282093 | V60458C5 | Child | FALSE | KTS 500KV LINE AT SMTS | 39641.3951 | 39641.4986 | DAILY | 00012441 | SPICAPX | child workorder fo other end of line | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458C539641.3951388889 | V60458C5 |  | Parent | TRUE | ROTS NO.3 500KV LINE AT SMTS | 39641.3951 | 39641.4986 | DAILY | 00012438 | SPICAPX | DEENERGISE LINE FOR HV TESTING | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X49758L939641.3958333333 | X49758L9 |  | Parent | TRUE | NO.2 22KV BUS AT BETS | 39641.3958 | 39641.7639 | DAILY | 00016376 | SPICAPX | Out W/O No2 22kV Bus off loaded for BT auto close | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758M139641.3958333333 | X49758M1 | X49758L9 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39641.3958 | 39641.7639 | DAILY | 00016040 | SPICAPX | Perf calc W/O No2 Trans GRP 22kV only | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V60458B839641.5138888889 | V60458B8 |  | Parent | FALSE | KTS 500KV LINE NO.1 BUS CB AT SMTS | 39641.5139 | 39655.3229 | CONT | [12 empty] | 0
_X55658P839641.55 | X55658P8 |  | Parent | TRUE | NO.4 66KV BUS AT RWTS | 39641.55 | 39641.7729 | DAILY | 00007481 | SPICAPX | upgrade No4 BUS SIDE DROPPERS OF 2-4 66KV B/T CB | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X55658P939641.55 | X55658P9 | X55658P8 | Child | FALSE | B4 220/66KV TRANS AT RWTS | 39641.55 | 39641.7729 | DAILY | 00007451 | SPICAPX | Tran rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X55658S539641.6347222222 | X55658S5 |  | Parent | FALSE | 1-2 66KV TIE BUS AT RWTS | 39641.6347 | 39648.5139 | DAILY | 00364661 | SPICAPX | Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X55658R939642.2784722222 | X55658R9 |  | Parent | TRUE | NO.1 66KV BUS AT RWTS | 39642.2785 | 39642.5292 | DAILY | 00364660 | SPICAPX | Upgrade Bus Side Isols | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X55658S139642.2784722222 | X55658S1 | X55658R9 | Child | FALSE | U1 66/22KV TRANS AT RWTS | 39642.2785 | 39642.5292 | DAILY | 00007456 | SPICAPX | Rebate Tran for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_X55658S239642.2784722222 | X55658S2 | X55658R9 | Child | FALSE | B1 220/66KV TRANS AT RWTS | 39642.2785 | 39642.5292 | DAILY | 00364702 | SPICAPX | Rebate Tran for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X49758M039642.2944444444 | X49758M0 |  | Parent | TRUE | NO.4 22KV BUS AT BETS | 39642.2944 | 39642.5 | DAILY | 00016373 | SPICAPX | Out W/O No4 22kV Bus off loaded for BT auto close | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758M239642.2944444444 | X49758M2 | X49758M0 | Child | FALSE | R4 220/66/22KV TRANS AT BETS | 39642.2944 | 39642.5 | DAILY | 00016220 | SPICAPX | Perf calc W/O No4 Trans 22kV only | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027031439642.2965277778 | 10270314 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT TTS | 39642.2965 | 39642.6903 | DAILY | 00001533 | SPIMAINT | O/HAUL Transformer and Trafo Union Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1010066939642.3111111111 | 10100669 |  | Parent | FALSE | C NTH 22KV BUS AT RTS | 39642.3111 | 39642.5993 | DAILY | 00007358 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 22 |  |  |  | 0
_V76958B639642.3180555556 | V76958B6 |  | Parent | FALSE | NO.1 220KV BUS AT CBTS | 39642.3181 | 39642.6354 | DAILY | 00359378 | SPICAPX | No 1 220kv Bus & No1 66kv Bus | SPIPOWER | V769 | V769 - (CBTS) PRIMARY EQUIPMENT DEFECTS REPAIR | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X56958C539642.3333333333 | X56958C5 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39642.3333 | 39642.6792 | DAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 23 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658S339642.5409722222 | X55658S3 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39642.541 | 39642.7722 | DAILY | 00007480 | SPICAPX | Bus Outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X55658S439642.5409722222 | X55658S4 | X55658S3 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 39642.541 | 39642.7722 | DAILY | 00007450 | SPICAPX | Tran Rebate for Bus outage | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028450939642.6534722222 | 10284509 |  | Parent | FALSE | S028 KTS -GTS 2 220KV | 39642.6535 | 39643.3694 | CONT | [12 empty] | 0
_1026925639643.2902777778 | 10269256 |  | Parent | FALSE | SYN/COND AT TSTS | 39643.2903 | 39645.625 | CONT | 00007626 | SPIMAINT | 4 Monthly O/HAUL - TSTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1024910739643.2944444444 | 10249107 |  | Parent | FALSE | B3 220/66KV TRANS AT WMTS | 39643.2944 | 39643.6486 | DAILY | 00003236 | SPIMAINT | O/H Trans | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028507639643.3111111111 | 10285076 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 39643.3111 | 39643.6986 | DAILY | [12 empty] | 0
_1028506939643.3263888889 | 10285069 |  | Parent | FALSE | LNGS NO.2 GEN TRANS 220KV LINE AT ATS | 39643.3264 | 39646.6104 | CONT | 00360129 | GENCO | LNGS 2 SCAP | GENCO |  |  | Circuits | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358E639643.3548611111 | Z63358E6 |  | Parent | FALSE | JLTS NO.1 220KV LINE AT MWTS | 39643.3549 | 39643.6722 | REPDAILY | 00016130 | VEN_AUG | No1 220/66KV TX 220KV ISOLS @ MWTS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028513639643.3583333333 | 10285136 |  | Parent | FALSE | NO.8 GEN TRANS 220KV CB BUS SIDE ROI AT HWPS | 39643.3583 | 39654.7639 | CONT | [12 empty] | 0
_1028512639643.6729166667 | 10285126 |  | Parent | FALSE | MWTS NO.1 220KV LINE NO.1 BUS CB AT JLTS | 39643.6729 | 39645.3208 | CONT | [12 empty] | 0
_1027035039644.3055555556 | 10270350 |  | Parent | FALSE | RWTS 220KV LINE NO.2 BUS CB AT TTS | 39644.3056 | 39645.6215 | CONT | [12 empty] | 0
_1028433839644.3104166667 | 10284338 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 39644.3104 | 39645.6125 | CONT | [12 empty] | 0
_1028507839644.3118055556 | 10285078 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 39644.3118 | 39644.4993 | DAILY | [12 empty] | 0
_1027072039644.3159722222 | 10270720 |  | Parent | FALSE | EX - ATS 220KV LINE NO.1 BUS CB AT KTS | 39644.316 | 39645.6333 | CONT | [12 empty] | 0
_Z63358E639644.3291666667 | Z63358E6 |  | Parent | FALSE | JLTS NO.1 220KV LINE AT MWTS | 39644.3292 | 39644.6542 | REPDAILY | 00016130 | VEN_AUG | No1 220/66KV TX 220KV ISOLS @ MWTS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028517639644.3916666667 | 10285176 |  | Parent | TRUE | JLA NO.1 220KV LINE CB AT TBTS | 39644.3917 | 39644.4174 | DAILY | [12 empty] | 0
_1028532539644.3916666667 | 10285325 | 10285176 | Child | FALSE | JLA NO.1 220KV LINE AT TBTS | 39644.3917 | 39644.4174 | DAILY | 00018301 | FORCED | REBATE LINE OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028517739644.41875 | 10285177 |  | Parent | TRUE | JLA NO.2 220KV LINE CB AT TBTS | 39644.4187 | 39644.441 | DAILY | [12 empty] | 0
_1028532639644.41875 | 10285326 | 10285177 | Child | FALSE | JLA NO.2 220KV LINE AT TBTS | 39644.4187 | 39644.441 | DAILY | 00026919 | FORCED | Rebate for Line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028471939645.3152777778 | 10284719 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE NO.1 BUS CB CT R/PH AT KTS | 39645.3153 | 39645.634 | DAILY | [12 empty] | 0
_Z63358E639645.3208333333 | Z63358E6 |  | Parent | FALSE | JLTS NO.1 220KV LINE AT MWTS | 39645.3208 | 39645.675 | REPDAILY | 00016130 | VEN_AUG | No1 220/66KV TX 220KV ISOLS @ MWTS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028512139645.3243055556 | 10285121 |  | Parent | FALSE | B3 TRANS 66KV CB AT ATS | 39645.3243 | 39645.3993 | DAILY | [12 empty] | 0
_1028492239645.3930555556 | 10284922 |  | Parent | FALSE | ROTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 39645.3931 | 39645.6507 | DAILY | [12 empty] | 0
_1028486639645.5479166667 | 10284866 |  | Parent | FALSE | TGTS 220KV LINE NO.2 BUS CB AT MLTS | 39645.5479 | 39645.5958 | DAILY | [12 empty] | 0
_Z63358E739645.6486111111 | Z63358E7 |  | Parent | FALSE | EX - MWTS NO.1 220KV LINE NO.1 BUS CB LINE SIDE ROI AT JLTS | 39645.6486 | 39658.316 | CONT | [12 empty] | 0
_1028320139646.2506944445 | 10283201 |  | Parent | TRUE | JLTS NO.1 LINE/AUX TRANS 'B' 220KV CB AT HWPS | 39646.2507 | 39646.6611 | DAILY | [12 empty] | 0
_1028320239646.2506944445 | 10283202 | 10283201 | Child | FALSE | JLTS NO.1 220KV LINE AT HWPS | 39646.2507 | 39646.6611 | DAILY | 00015784 | SPIMAINT | Line outage rebate for Aux Trans B CTs | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058AB39646.2659722222 | X32058AB |  | Parent | FALSE | ROTS NO.1 LINE/B3 TRANS 220KV CB AT MTS | 39646.266 | 39646.6389 | DAILY | [12 empty] | 0
_X55658T439646.2965277778 | X55658T4 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 39646.2965 | 39646.6424 | DAILY | 00007456 | SPICAPX | SF6 Alarm to moved from RTU to SCIMS | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027031939646.3118055556 | 10270319 |  | Parent | FALSE | TSTS 220KV LINE NO.3 BUS CB AT TTS | 39646.3118 | 39647.591 | CONT | [12 empty] | 0
_1028472139646.3125 | 10284721 |  | Parent | FALSE | EX - TTS NO.2 220KV LINE NO.2 BUS CB CT R/PH AT KTS | 39646.3125 | 39646.6062 | DAILY | [12 empty] | 0
_V71158A339646.33125 | V71158A3 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.1 BUS CB AT LYPS | 39646.3313 | 39647.6 | CONT | [12 empty] | 0
_1028472339647.3145833333 | 10284723 |  | Parent | FALSE | EX - B3 TRANS 220KV CB TRANS SIDE CT R/PH AT KTS | 39647.3146 | 39647.6257 | DAILY | [12 empty] | 0
_1027605439647.3208333333 | 10276054 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT RTS | 39647.3208 | 39647.4944 | DAILY | 00055373 | SPIMAINT | Cap Bank Rebate for CT checks | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027534039647.3354166667 | 10275340 |  | Parent | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 39647.3354 | 39647.5889 | DAILY | 00004036 | SPIMAINT | Repair No 1 Trans oil leaks | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028484839647.3486111111 | 10284848 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT SHTS | 39647.3486 | 39647.3958 | DAILY | [12 empty] | 0
_1028531439647.3486111111 | 10285314 | 10284848 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT SHTS | 39647.3486 | 39647.3958 | DAILY | 00350862 | SPIMAINT | Rebate W/O for No2A 66kv Cap Bk outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028531639647.3486111111 | 10285316 | 10284848 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT SHTS | 39647.3486 | 39647.3958 | DAILY | 00330829 | SPIMAINT | Rebate W/O for No2B 66kv Cap Bk outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028528939647.4423611111 | 10285289 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT GTS | 39647.4424 | 39647.7361 | CONT | 00350421 | FAULT | No1 Cap Bank out W/O | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028495139647.5430555556 | 10284951 |  | Parent | FALSE | B4 TRANS 66KV CB AT SHTS | 39647.5431 | 39647.6326 | DAILY | [12 empty] | 0
_1028302139647.5465277778 | 10283021 |  | Parent | FALSE | EX - 3-4 66KV BUS TIE CB CT R/PH AT MWTS | 39647.5465 | 39647.5813 | DAILY | [12 empty] | 0
_1028529739647.9166666667 | 10285297 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 39647.9167 | 39652.0222 | CONT | 00356079 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X56958C639648.2923611111 | X56958C6 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39648.2924 | 39648.6007 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 24 & 25 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028503039648.3333333333 | 10285030 |  | Parent | TRUE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39648.3333 | 39648.3653 | DAILY | [12 empty] | 0
_1028512039648.3333333333 | 10285120 | 10285030 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39648.3333 | 39648.3653 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during 275kV CB de-energ | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z54658A739648.3347222222 | Z54658A7 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT MLTS | 39648.3347 | 39648.7132 | DAILY | 00364782 | VEN_AUG | Sealing of A2 Trans Enclosure Wall seams | SPIPOWER | Z546 | Z546 - (MLTS) 500/220KV TRANSFORMER CONTESTABLE | Main Transformers | Alstom | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_X56958C639649.2951388889 | X56958C6 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39649.2951 | 39649.575 | REPDAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 24 & 25 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V76958A939649.2986111111 | V76958A9 |  | Parent | TRUE | NO.2 220KV BUS AT CBTS | 39649.2986 | 39649.6139 | DAILY | 00359379 | SPICAPX | No 2 220kv Bus & No3 66kv Bus | SPIPOWER | V769 | V769 - (CBTS) PRIMARY EQUIPMENT DEFECTS REPAIR | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V76958B039649.2986111111 | V76958B0 | V76958A9 | Child | FALSE | B2 220/66KV TRANS AT CBTS | 39649.2986 | 39649.6139 | DAILY | 00353077 | SPICAPX | Tran Rebate for Bus Outage | SPIPOWER | V769 | V769 - (CBTS) PRIMARY EQUIPMENT DEFECTS REPAIR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1028530639649.2986111111 | 10285306 | V76958A9 | Child | FALSE | CLN NO.1 66KV FDR AT CBTS (WAS CLN) | 39649.2986 | 39649.6687 | DAILY | 00359488 | SPIMAINT | FTS No1 Line | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058AE39650.2680555556 | X32058AE |  | Parent | FALSE | B1 220/66KV TRANS AT MTS | 39650.2681 | 39650.6361 | DAILY | 00364562 | SPIMAINT | Adjust ROTS No3 Line / B1 Trans CB Trans Side ROI | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028531039650.5020833333 | 10285310 |  | Parent | TRUE | LYPS NO.3 500KV LINE NO.4 BUS CB AT HWTS | 39650.5021 | 39650.525 | DAILY | [12 empty] | 0
_1028545639650.5020833333 | 10285456 | 10285310 | Child | FALSE | HWTS NO.3 500KV LINE AT LYPS | 39650.5021 | 39650.525 | DAILY | 00016088 | SPIMAINT | Rebate for CB outage SP AUS NET GROUP | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027027139651.29375 | 10270271 |  | Parent | FALSE | SYN/COND AT BLTS | 39651.2937 | 39653.6889 | CONT | 00002547 | SPIMAINT | 3 Monthly O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028508539651.3152777778 | 10285085 |  | Parent | FALSE | B2 220/66KV TRANS AT TBTS | 39651.3153 | 39651.509 | DAILY | 00004902 | SPIMAINT | REPAIR/REPLACE FAULTY FAN | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027033339651.3152777778 | 10270333 |  | Parent | FALSE | B5 TRANS NO.2 BUS 220KV CB AT TTS | 39651.3153 | 39652.6465 | CONT | [12 empty] | 0
_1028505439651.3291666667 | 10285054 |  | Parent | FALSE | 22KV/415V S/S TRANS AT FTS | 39651.3292 | 39651.4924 | DAILY | 00004393 | SPIMAINT | REPAIR OIL LEAK | SPIPOWER |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1028484939651.3340277778 | 10284849 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT GNTS | 39651.334 | 39651.6035 | DAILY | [12 empty] | 0
_Z63358D539651.3354166667 | Z63358D5 |  | Parent | FALSE | JLTS NO.2 220KV LINE AT MWTS | 39651.3354 | 39651.7083 | CONT | 00016131 | VEN_AUG | No2 220/66KV TX 22OKV ISOL STRUCTURE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658T539651.3722222222 | X55658T5 |  | Parent | FALSE | TTS 220KV LINE NO.1 BUS CB AT RWTS | 39651.3722 | 39651.5757 | DAILY | [12 empty] | 0
_1028510139651.4173611111 | 10285101 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT MBTS | 39651.4174 | 39651.4292 | DAILY | [12 empty] | 0
_X55658T639651.5756944444 | X55658T6 |  | Parent | FALSE | TTS 220KV LINE NO.2 BUS CB AT RWTS | 39651.5757 | 39651.6576 | DAILY | [12 empty] | 0
_1028539039652.2402777778 | 10285390 |  | Parent | FALSE | NO.3 66KV BUS AT GTS | 39652.2403 | 39652.3771 | DAILY | 00002837 | FAULT | No3 66kV Bus Trip | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1028538039652.2402777778 | 10285380 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 39652.2403 | 39652.8604 | DAILY | 00002829 | FAULT | Fault No3 220/66KV Transformer. | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028539139652.2402777778 | 10285391 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT GTS | 39652.2403 | 39653.5993 | CONT | [12 empty] | 0
_X32058AC39652.2916666667 | X32058AC |  | Parent | FALSE | ROTS NO.1 LINE/B1 TRANS 220KV CB AT MTS | 39652.2917 | 39652.6785 | DAILY | [12 empty] | 0
_X55658T739652.3027777778 | X55658T7 |  | Parent | FALSE | ROTS 220KV LINE NO.1 BUS CB AT RWTS | 39652.3028 | 39652.5521 | DAILY | [12 empty] | 0
_V22858A039652.3097222222 | V22858A0 |  | Parent | FALSE | WMTS NO.2 220KV LINE CB AT FBTS | 39652.3097 | 39653.6458 | CONT | [12 empty] | 0
_1024077639652.3166666667 | 10240776 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT ERTS | 39652.3167 | 39652.4625 | DAILY | 00004373 | SPIMAINT | Conservator oil level low Ageing Other | SPIPOWER |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1028538739652.4826388889 | 10285387 |  | Parent | TRUE | HWTS NO.2 500KV LINE CB AT LYPS | 39652.4826 | 39653.116 | DAILY | [12 empty] | 0
_1028550239652.4826388889 | 10285502 | 10285387 | Child | FALSE | HWTS NO.2 500KV LINE AT LYPS | 39652.4826 | 39653.116 | DAILY | 00016087 | FORCED | LINE REBATE FOR CB OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658T839652.5527777778 | X55658T8 |  | Parent | FALSE | ROTS 220KV LINE NO.2 BUS CB AT RWTS | 39652.5528 | 39652.6285 | DAILY | [12 empty] | 0
_1028541939652.725 | 10285419 |  | Parent | FALSE | LYPS-HWTS 3 500KV G | 39652.725 | 39652.7986 | DAILY | 00020324 | FAULT | Prot trip | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028542139652.8277777778 | 10285421 |  | Parent | FALSE | LYPS NO.3 500KV LINE AT HWTS | 39652.8278 | 39652.8743 | DAILY | 00016236 | FAULT | At HWTS the LYPS No3 Line Off load. | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058AF39653.2909722222 | X32058AF |  | Parent | FALSE | U1 66/22KV TRANS AT MTS | 39653.291 | 39653.5701 | DAILY | 00363343 | SPIMAINT | Earth the metallic ducting in enclosure | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028532039653.3819444444 | 10285320 |  | Parent | FALSE | NO.7 GEN TRANS LINE AT HWPS | 39653.3819 | 39655.7486 | CONT | 00356085 | 3RDPARTY | HVS: No 7 Gen CB Isol'd for PS | GENCO |  |  | Circuits | 3rd Party | 220 | NON AER ELEMENT | EXCLUDED |  | 3
_1028543539653.5701388889 | 10285435 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39653.5701 | 39653.5806 | DAILY | [12 empty] | 0
_X55658U239653.5729166667 | X55658U2 |  | Parent | FALSE | TTS 220KV LINE NO.1 BUS CB AT RWTS | 39653.5729 | 39653.6139 | DAILY | [12 empty] | 0
_1028520939654.2902777778 | 10285209 |  | Parent | FALSE | B1 220/66KV TRANS AT HTS | 39654.2903 | 39654.6285 | DAILY | 00004445 | SPIMAINT | Repair B1 trans fans | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028564239654.3333333333 | 10285642 |  | Parent | TRUE | HWTS NO.2 500KV LINE CB AT LYPS | 39654.3333 | 39654.5396 | DAILY | [12 empty] | 0
_1028564339654.3333333333 | 10285643 | 10285642 | Child | FALSE | HWTS NO.2 500KV LINE AT LYPS | 39654.3333 | 39654.5396 | DAILY | 00016087 | SPIMAINT | LINE REBATE FOR CB OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028489139654.3479166667 | 10284891 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT WOTS | 39654.3479 | 39654.4514 | DAILY | [12 empty] | 0
_1028564439654.5736111111 | 10285644 |  | Parent | TRUE | HWTS NO.2 500KV LINE CB AT LYPS | 39654.5736 | 39654.625 | DAILY | [12 empty] | 0
_1028564539654.5736111111 | 10285645 | 10285644 | Child | FALSE | HWTS NO.2 500KV LINE AT LYPS | 39654.5736 | 39654.625 | DAILY | 00016087 | SPIMAINT | LINE REBATE FOR CB OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028489039654.5826388889 | 10284890 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 39654.5826 | 39654.6562 | DAILY | [12 empty] | 0
_1028548739654.7701388889 | 10285487 |  | Parent | FALSE | NO.1 GEN 220/16.5KV TRANS AT HWPS | 39654.7701 | 39656.809 | CONT | 00009642 | GENCO | Power Station requirements | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_X50858E539655.2513888889 | X50858E5 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 39655.2514 | 39655.6236 | DAILY | 00002830 | SPICAPX | B4 Trans - Install cable tray and conduits | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027032939655.2923611111 | 10270329 |  | Parent | FALSE | B1 TRANS 220KV CB AT TTS | 39655.2924 | 39656.6056 | CONT | [12 empty] | 0
_V60458C039655.3263888889 | V60458C0 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.2 BUS CB LINE SIDE ISOL AT SMTS | 39655.3264 | 39662.5958 | CONT | [12 empty] | 0
_1028209439655.375 | 10282094 | V60458C6 | Child | FALSE | KTS 500KV LINE AT SMTS | 39655.375 | 39655.5222 | DAILY | 00012441 | SPICAPX | child workorder for other end of line | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458C639655.375 | V60458C6 |  | Parent | TRUE | ROTS NO.3 500KV LINE AT SMTS | 39655.375 | 39655.5222 | DAILY | 00012438 | SPICAPX | DEENERGISE LINE FOR HV TESTING | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56958C839656.2916666667 | X56958C8 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39656.2917 | 39656.5993 | DAILY | 00060191 | SPICAPX | Out W/O MSS-DDTS No2 Line OPGW - Run 26 | SPIPOWER | X569 | X569 - (WOTS-T401,JSS LINE,DDTS-MSS) OPGW | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V76958B239656.2972222222 | V76958B2 |  | Parent | TRUE | NO.2 220KV BUS AT CBTS | 39656.2972 | 39656.6215 | DAILY | 00359379 | SPICAPX | No 2 220kv Bus & No3 66kv Bus | SPIPOWER | V769 | V769 - (CBTS) PRIMARY EQUIPMENT DEFECTS REPAIR | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V76958B339656.2972222222 | V76958B3 | V76958B2 | Child | FALSE | B2 220/66KV TRANS AT CBTS | 39656.2972 | 39656.6215 | DAILY | 00353077 | SPICAPX | Tran Rebate for Bus Outage | SPIPOWER | V769 | V769 - (CBTS) PRIMARY EQUIPMENT DEFECTS REPAIR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1027019339657.2993055556 | 10270193 |  | Parent | FALSE | SYN/COND AT FBTS | 39657.2993 | 39660.6389 | CONT | 00002697 | SPIMAINT | 3 Monthly O/HAUL - FBTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028526539657.3020833333 | 10285265 |  | Parent | FALSE | B3 220/66KV TRANS AT RWTS | 39657.3021 | 39657.6333 | DAILY | 00007455 | SPIMAINT | REPAIR FANS,PUMPS & BUSHING OIL LEVELS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028514339657.4548611111 | 10285143 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT BATS | 39657.4549 | 39657.4896 | DAILY | 00006557 | SPIMAINT | Low oil level in No2 S/S Trans at Bats | SPIPOWER |  |  | Other Transformers | Alstom | 22 |  |  |  | 0
_1028550039657.4652777778 | 10285500 |  | Parent | FALSE | SYN/COND TRANS NO.1 BUS 66KV CB AT TSTS | 39657.4653 | 39658.3903 | DAILY | [12 empty] | 0
_1028550139657.4895833333 | 10285501 |  | Parent | FALSE | NO.7 GEN TRANS 220KV CB AT HWPS | 39657.4896 | 39659.2319 | CONT | [12 empty] | 0
_1028516839658.3069444444 | 10285168 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 39658.3069 | 39658.6062 | DAILY | 00022690 | APDALCOA | Scap to PTH | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1028526739658.3159722222 | 10285267 |  | Parent | FALSE | B4 220/66KV TRANS AT RWTS | 39658.316 | 39658.6319 | DAILY | 00007451 | SPIMAINT | REPAIR FANS, PUMPS AND BUSHING OIL LEVELS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z63358E839658.33125 | Z63358E8 |  | Parent | FALSE | MWTS NO.1 220KV LINE AT JLTS | 39658.3313 | 39659.6771 | CONT | 00015947 | VEN_AUG | MWTS 1L 1B CB L/S ISOL RECONNECT | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028488639658.3513888889 | 10284886 |  | Parent | FALSE | R3 TRANS NO.1 BUS 220KV CB AT RCTS | 39658.3514 | 39658.3896 | DAILY | [12 empty] | 0
_1028488739658.45 | 10284887 |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT RCTS | 39658.45 | 39658.4938 | DAILY | [12 empty] | 0
_1028527039659.2986111111 | 10285270 |  | Parent | FALSE | NO.2 CSC NO.3 BUS CB AT ROTS | 39659.2986 | 39660.5889 | CONT | [12 empty] | 0
_1028517139659.3041666667 | 10285171 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39659.3042 | 39659.6319 | DAILY | 00022691 | APDALCOA | Scap to PTH | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1028517039660.3111111111 | 10285170 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 39660.3111 | 39660.6215 | DAILY | 00022690 | APDALCOA | Scap to PTH | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X50858E139660.7486111111 | X50858E1 |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 39660.7486 | 39708.3854 | CONT | [12 empty] | 0
_1028537539661.2958333333 | 10285375 |  | Parent | FALSE | B3 220/66KV TRANS AT SVTS | 39661.2958 | 39661.6007 | DAILY | 00004851 | SPIMAINT | REPAIR OIL PUMP & FAN MOTORS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028517239661.3020833333 | 10285172 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39661.3021 | 39661.5653 | DAILY | 00022691 | APDALCOA | Scap to PTH | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027024539661.3131944445 | 10270245 |  | Parent | FALSE | NO.4 TRANS 66KV CB AT BLTS | 39661.3132 | 39661.6285 | DAILY | [12 empty] | 0
_1027054339661.3152777778 | 10270543 |  | Parent | FALSE | NO.8 22KV/415V S/S TRANS AT SMTS | 39661.3153 | 39661.6076 | DAILY | 00001327 | SPIMAINT | No.8 S/S Transformer | SPIPOWER |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1028564139661.3604166667 | 10285641 |  | Parent | FALSE | 1-4 66KV BUS TIE CB NO.1 BUS SIDE ISOL AT MWTS | 39661.3604 | 39661.6486 | DAILY | [12 empty] | 0
_1028566239661.5611111111 | 10285662 |  | Parent | FALSE | MWTS-LY 1 66KV G | 39661.5611 | 39661.6486 | DAILY | 00020535 | FORCED | Rebate child for bus outage | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028566139661.5618055556 | 10285661 |  | Parent | TRUE | JLTS-MWTS 1 220KV G | 39661.5618 | 39661.6486 | DAILY | 00020468 | FORCED | Rebate child for bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028692839661.5618055556 | 10286928 | 10285661 | Child | FALSE | EX - B1 220/66KV TRANS AT MWTS | 39661.5618 | 39661.6486 | DAILY | 00010265 | FORCED | Avail plant due to bus outage fix 1-4 BT CB isol | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028566639661.9340277778 | 10285666 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39661.934 | 39663.9583 | CONT | 00356084 | GENCO | SCAP for GenCo | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028584339662.2527777778 | 10285843 | V60458B9 | Child | FALSE | KTS 500KV LINE AT SMTS | 39662.2528 | 39662.5958 | DAILY | 00012441 | SPICAPX | child w/o for smts- kts line outgae | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458B939662.2527777778 | V60458B9 |  | Parent | TRUE | ROTS NO.3 500KV LINE AT SMTS | 39662.2528 | 39662.5958 | DAILY | 00012438 | SPICAPX | Restore by-pass in bay "c" | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858E739663.2430555556 | X50858E7 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT GTS | 39663.2431 | 39663.5833 | DAILY | 00002832 | SPICAPX | Decommission No2 Station Service Transformer | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1024916139663.2826388889 | 10249161 |  | Parent | FALSE | B3 TRANS 220KV ISOL AT WMTS | 39663.2826 | 39663.6264 | DAILY | [12 empty] | 0
_X50858E839663.5861111111 | X50858E8 |  | Parent | FALSE | EX - NO.1 22KV/415V S/S TRANS AT GTS | 39663.5861 | 39663.6944 | DAILY | 00002831 | SPICAPX | Decommission No1 Station Service Transformer | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Other Transformers | Alstom | 22 |  |  |  | 0
_1028567539663.9583333333 | 10285675 |  | Parent | FALSE | NO.1 GEN 220/16.5KV TRANS AT HWPS | 39663.9583 | 39665.7604 | CONT | 00009642 | 3RDPARTY | HVS: No 1 Gen at HWPS | GENCO |  |  | Connection Transformers | 3rd Party | 220 | NON SP ASSET | EXCLUDED |  | 3
_1027054739665.2631944444 | 10270547 |  | Parent | FALSE | NO.2 500KV BUS AT SMTS | 39665.2632 | 39676.3368 | CONT | 00001329 | SPIMAINT | O/Haul NO.2 500KV BUS AT SMTS | SPIPOWER |  |  | Bus | Western | 500 |  |  |  | 0
_1028535839665.2930555556 | 10285358 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39665.2931 | 39665.7229 | DAILY | 00319998 | SPIMAINT | Out W/O APD No1 Line outage for conductor sampling | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026938839665.3131944445 | 10269388 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT HTS | 39665.3132 | 39665.4875 | DAILY | 00004449 | SPIMAINT | O/Haul No 2 S/S Trans at HTS | SPIPOWER |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_1028560739665.7291666667 | 10285607 |  | Parent | TRUE | M2 500/275KV TRANS BANK 22KV VT R/PH AT HYTS | 39665.7292 | 39665.8479 | DAILY | [12 empty] | 0
_1028577839665.7291666667 | 10285778 | 10285607 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 39665.7292 | 39665.8479 | DAILY | 00002862 | FORCED | Rebate W/O M2 Trans during 22kV VT replacement | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028565039665.9840277778 | 10285650 |  | Parent | FALSE | NO.2 GEN TRANS 500KV LINE E/SW AT LYPS | 39665.984 | 39671.4326 | CONT | [12 empty] | 0
_1028541239666.2951388889 | 10285412 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39666.2951 | 39666.7361 | REPDAILY | 00319999 | APDALCOA | APD Work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X55658U839666.2986111111 | X55658U8 |  | Parent | FALSE | B1 220/66KV TRANS AT RWTS | 39666.2986 | 39666.7243 | DAILY | 00364702 | SPICAPX | Check Bucholtz | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1027340739666.3194444444 | 10273407 |  | Parent | FALSE | RWTS 220KV LINE NO.4 BUS CB CT R/PH AT ROTS | 39666.3194 | 39666.4479 | DAILY | [12 empty] | 0
_1028580739666.5631944445 | 10285807 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 39666.5632 | 39668.7819 | CONT | [12 empty] | 0
_1028541239667.3041666667 | 10285412 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39667.3042 | 39667.7812 | REPDAILY | 00319999 | APDALCOA | APD Work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1028581539667.3047800926 | 10285815 |  | Parent | FALSE | NO.8 GEN TRANS 220KV CB BUS SIDE ROI AT HWPS | 39667.3048 | 39672.7431 | CONT | [12 empty] | 0
_Z63358F139667.3194444444 | Z63358F1 |  | Parent | FALSE | JLTS NO.2 220KV LINE AT MWTS | 39667.3194 | 39667.6319 | DAILY | 00016131 | VEN_AUG | No2 220/66KV TX 220KV ISOL REBUILD | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358B139668.2604166667 | Z63358B1 |  | Parent | TRUE | EX - NO.1 220KV BUS AT JLTS | 39668.2604 | 39670.7236 | CONT | 00009889 | VEN_AUG | JLTS No 1 220Kv BUS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358B239668.2604166667 | Z63358B2 | Z63358B1 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 39668.2604 | 39670.7236 | CONT | 00015936 | VEN_AUG | Line Rebate for No 1 Bus outage @ JLTS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358F439668.3402777778 | Z63358F4 |  | Parent | FALSE | MWTS NO.2 220KV LINE AT JLTS | 39668.3403 | 39668.6951 | REPDAILY | 00015948 | VEN_AUG | MWTS No2 LINE OUTAGE FOR PROXIMITY DURING BUS OUTA | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028583039668.3826388889 | 10285830 |  | Parent | FALSE | JLGB NO.2 UNIT TRANS DISC CB AT JLGB | 39668.3826 | 39670.7236 | DAILY | [12 empty] | 0
_1028582639668.3826388889 | 10285826 |  | Parent | FALSE | JLGB NO.1 UNIT TRANS DISC CB AT JLGB | 39668.3826 | 39688.375 | CONT | [12 empty] | 0
_1028555339668.6034722222 | 10285553 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 39668.6035 | 39668.6062 | DAILY | [12 empty] | 0
_1028589339668.9180555556 | 10285893 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 39668.9181 | 39672.0569 | CONT | 00356081 | GENCO | GEN-CO Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858F039669.2430555556 | X50858F0 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT GTS | 39669.2431 | 39669.7257 | DAILY | 00002832 | SPICAPX | Decommission No2 Station Service Transformer | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_Z63358F439669.3097222222 | Z63358F4 |  | Parent | FALSE | MWTS NO.2 220KV LINE AT JLTS | 39669.3097 | 39669.6993 | REPDAILY | 00015948 | VEN_AUG | MWTS No2 LINE OUTAGE FOR PROXIMITY DURING BUS OUTA | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028594539670.2118055556 | 10285945 |  | Parent | FALSE | ROTS-SVTS 2 220KV E | 39670.2118 | 39670.2382 | DAILY | 00022756 | FAULT | Rebate Line Outage for B2 Trans Trip | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028594639670.2118055556 | 10285946 |  | Parent | FALSE | SVTS-HTS 2 220KV E | 39670.2118 | 39670.2382 | DAILY | 00022773 | FAULT | Rebate Line Outage for B2 Trans Trip | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028590439670.2125 | 10285904 |  | Parent | FALSE | B2 220/66KV TRANS AT SVTS | 39670.2125 | 39670.5389 | DAILY | 00004850 | FAULT | B2 Transformer tripped on low oil. | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858F139670.2631944444 | X50858F1 |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 39670.2632 | 39670.4986 | DAILY | 00002828 | SPICAPX | decommiss No1 S/S Trans | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V78658A539670.2944444444 | V78658A5 |  | Parent | FALSE | NO.2 66KV BUS AT CBTS | 39670.2944 | 39670.6326 | DAILY | 00359471 | SPIMAINT | Rewire Bus Prot Summation Box | SPIPOWER | V786 | V786 - (CBTS) URGENT REPLACEMENT OF ROTS 4L 500KV CVT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026736339670.3145833333 | 10267363 |  | Parent | TRUE | B3 TRANS Y PROT AT ERTS | 39670.3146 | 39670.4694 | DAILY | [12 empty] | 0
_1028562539670.3145833333 | 10285625 | 10267363 | Child | FALSE | B3 220/66KV TRANS AT ERTS | 39670.3146 | 39670.4694 | DAILY | 00004371 | SPIMAINT | Rebate Trans outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z63358F439670.34375 | Z63358F4 |  | Parent | FALSE | MWTS NO.2 220KV LINE AT JLTS | 39670.3438 | 39670.6486 | REPDAILY | 00015948 | VEN_AUG | MWTS No2 LINE OUTAGE FOR PROXIMITY DURING BUS OUTA | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X32058AH39671.2777777778 | X32058AH |  | Parent | FALSE | B1 220/66KV TRANS AT MTS | 39671.2778 | 39671.6639 | DAILY | 00364562 | SPIMAINT | Inspect Buchholz Relay & adjust as Required | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z53358A539671.2944444444 | Z53358A5 |  | Parent | FALSE | HWPS-ROTS 1 220KV G | 39671.2944 | 39675.6958 | CONT | 00020454 | GEN_AUG | CUT INTO (N) LINE DIVERSION AT TOWERS 4 & 17 | SPIPOWER | Z533 | Z533 - (HWPS-ROTS) LINE 3 HW MINE EXTENSION - ST2 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028343339671.3083333333 | 10283433 |  | Parent | FALSE | EX - FR NO.2 66KV FDR NO.3 BUS CB BUS SIDE CT R/PH AT RTS | 39671.3083 | 39671.4812 | DAILY | [12 empty] | 0
_1027035439671.3125 | 10270354 |  | Parent | FALSE | RWTS 220KV LINE NO.1 BUS CB AT TTS | 39671.3125 | 39672.6521 | CONT | [12 empty] | 0
_1028434339671.3291666667 | 10284343 |  | Parent | TRUE | NO.2A TRANS 22KV CB BUS SIDE ISOL AT RCTS | 39671.3292 | 39671.666 | DAILY | [12 empty] | 0
_1028553739671.3291666667 | 10285537 | 10284343 | Child | FALSE | NO.2 22KV CAPACITOR BANK AT RCTS | 39671.3292 | 39671.666 | DAILY | 00016713 | SPIMAINT | Rebate W/O No2 22kV Cap Bank during bus outage | SPIPOWER |  |  | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028553839671.3291666667 | 10285538 | 10284343 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39671.3292 | 39671.666 | DAILY | 00337584 | SPIMAINT | Perf calc W/O No2 Tr grp | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028343239671.48125 | 10283432 |  | Parent | FALSE | FR NO.2 66KV FDR NO.4 BUS CB BUS SIDE CT R/PH AT RTS | 39671.4812 | 39671.6028 | DAILY | [12 empty] | 0
_X32058AJ39672.2847222222 | X32058AJ |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39672.2847 | 39672.7028 | DAILY | 00363305 | SPIMAINT | Inspect Buchholz Relay & adjust as Required | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028561439672.3145833333 | 10285614 |  | Parent | FALSE | TTS LINE/B1 TRANS 220KV CB AT TSTS | 39672.3146 | 39672.4965 | DAILY | [12 empty] | 0
_1028561539672.4958333333 | 10285615 |  | Parent | FALSE | B1 TRANS NO.1 BUS 220KV CB AT TSTS | 39672.4958 | 39672.6125 | DAILY | [12 empty] | 0
_X32058AK39673.2659722222 | X32058AK |  | Parent | FALSE | U1 66/22KV TRANS AT MTS | 39673.266 | 39673.625 | DAILY | 00363343 | SPIMAINT | Inspect Buchholz Relay & adjust as Required | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_X55658T939673.2805555556 | X55658T9 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT RWTS | 39673.2806 | 39674.7639 | DAILY | 00007458 | SPICAPX | Terminate new No 2 S/S Trans HV Cables | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Other Transformers | Eastern | 22 |  |  |  | 0
_X7E658A039673.3118055556 | X7E658A0 |  | Parent | FALSE | 2-4 66KV BUS TIE CB AT TSTS | 39673.3118 | 39673.4875 | DAILY | [12 empty] | 0
_1028602239673.3916666667 | 10286022 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT HTS | 39673.3917 | 39673.4583 | DAILY | 00004426 | SPIMAINT | cap bank unbalanced | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028602339673.3916666667 | 10286023 | 10286022 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HTS | 39673.3917 | 39673.4583 | DAILY | 00331019 | SPIMAINT | rebate for cap bank outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X32058AG39674.2625 | X32058AG |  | Parent | FALSE | U2 66/22KV TRANS AT MTS | 39674.2625 | 39674.6417 | DAILY | 00363319 | SPIMAINT | Inspect Buchholz Relay | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028620539674.3006944444 | 10286205 |  | Parent | FALSE | B1 220/66KV TRANS AT TBTS | 39674.3007 | 39674.3785 | DAILY | 00004901 | FAULT | Trans rebate for bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028608739674.3006944444 | 10286087 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK CB AT TSTS | 39674.3007 | 39677.6097 | DAILY | [12 empty] | 0
_1028623139674.3006944444 | 10286231 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT TBTS | 39674.3007 | 39677.6097 | CONT | 00351938 | FAULT | Rebate outage for Cap | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1028573339674.3138888889 | 10285733 |  | Parent | FALSE | B1 220/66KV TRANS AT FBTS | 39674.3139 | 39674.7604 | DAILY | 00002726 | SPIMAINT | remove 1 upper and replace 1 upper fan | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z63358F639674.3638888889 | Z63358F6 |  | Parent | FALSE | HWPS NO.2 220KV LINE AT JLTS | 39674.3639 | 39674.6486 | DAILY | 00015937 | VEN_AUG | HWPS NO2 220KV LINE @ JLTS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358B339675.2506944445 | Z63358B3 |  | Parent | TRUE | EX - NO.1 220KV BUS AT JLTS | 39675.2507 | 39677.6528 | CONT | 00009889 | VEN_AUG | JLTS No 1 220Kv BUS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358B439675.2506944445 | Z63358B4 | Z63358B3 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 39675.2507 | 39677.6528 | CONT | 00015936 | VEN_AUG | Line Rebate for No 1 Bus outage @ JLTS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X55658T139675.2916666667 | X55658T1 |  | Parent | FALSE | EX - NO.1 22KV/415V S/S TRANS AT RWTS | 39675.2917 | 39677.6667 | CONT | 00119269 | SPICAPX | Removal of No1 S/S Trans | SPIPOWER | X556 | X556 - (RWTS) REPLACE REYROLLE 66KV CBS AND ASSOCIATED CTS | Other Transformers | Eastern | 22 |  |  |  | 0
_1028573539675.3173611111 | 10285735 |  | Parent | FALSE | B4 220/66KV TRANS AT FBTS | 39675.3174 | 39675.7063 | DAILY | 00002728 | SPIMAINT | replace upper faulty fan | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028607039675.3513888889 | 10286070 |  | Parent | FALSE | SYN/COND AT TSTS | 39675.3514 | 39675.4007 | DAILY | 00007626 | SPIMAINT | REPAIR WATER LEAK SHUT DOWN ONLY NEEDED | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028608439675.3694444444 | 10286084 |  | Parent | FALSE | EX - BAY F 500KV CVT B/PH AT SMTS (O.O.S) | 39675.3694 | 39675.5604 | DAILY | [12 empty] | 0
_1026911739675.6979166667 | 10269117 |  | Parent | FALSE | ROTS NO.2 220KV LINE NO.5 BUS CB AT HWPS | 39675.6979 | 39677.7868 | CONT | [12 empty] | 0
_1029724139675.6979166667 | 10297241 | 10285616 | Child | FALSE | HWPS-ROTS 2 220KV G | 39675.6979 | 39677.7868 | CONT | 00020455 | SPICAPX | CHANGE GLASS TO POLYMERIC INSULATORS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V78658A639676.3055555556 | V78658A6 |  | Parent | FALSE | NO.2 66KV BUS AT CBTS | 39676.3056 | 39676.6153 | DAILY | 00359471 | SPIMAINT | re wire bus prot | SPIPOWER | V786 | V786 - (CBTS) URGENT REPLACEMENT OF ROTS 4L 500KV CVT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1028614439676.3666666667 | 10286144 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 39676.3667 | 39676.6021 | DAILY | 00012436 | SPIMAINT | continuity checks on no.2 500kv bus & assoc equip | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028623339676.4743055556 | 10286233 |  | Parent | FALSE | ROTS-SMTS 3 500KV WT | 39676.4743 | 39676.5819 | DAILY | 00119316 | FAULT | Rebate outage for ROTS-SMTS NO3 500KV LINE | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028623439676.4875 | 10286234 |  | Parent | FALSE | ROTS-RTS 4 220KV E | 39676.4875 | 39676.5035 | DAILY | 00022750 | FORCED | Rebate outage for ROTS-RTS 4 220KV LINE | NEMMCO |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028361739677.2972222222 | 10283617 |  | Parent | TRUE | 1-3 220KV BUS TIE CB NO.3 BUS SIDE ISOL AT SVTS | 39677.2972 | 39677.5583 | DAILY | [12 empty] | 0
_1028361939677.2972222222 | 10283619 | 10283617 | Child | FALSE | B3 220/66KV TRANS AT SVTS | 39677.2972 | 39677.5583 | DAILY | 00004851 | SPIMAINT | Rebate Tran for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028583539677.3555555556 | 10285835 |  | Parent | TRUE | EX - BLTS 220KV LINE CT R/PH AT ATS | 39677.3556 | 39677.4986 | DAILY | [12 empty] | 0
_1028668439677.3555555556 | 10286684 | 10285835 | Child | FALSE | BLTS 220KV LINE AT ATS | 39677.3556 | 39677.4986 | DAILY | 00055536 | SPIMAINT | OUT W/O FOR LINE - sample line ct's | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028583339677.5229166667 | 10285833 |  | Parent | TRUE | EX - KTS 220KV LINE CT B/PH AT ATS | 39677.5229 | 39677.6583 | DAILY | [12 empty] | 0
_1028668239677.5229166667 | 10286682 | 10285833 | Child | FALSE | KTS 220KV LINE AT ATS | 39677.5229 | 39677.6583 | DAILY | 00055535 | SPIMAINT | OUT W/O FOR LINE - sample line ct's | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028607339678.3256944444 | 10286073 |  | Parent | FALSE | LNGS NO.2 GEN TRANS 220KV LINE AT ATS | 39678.3257 | 39681.5 | CONT | 00360129 | GENCO | SCAP to LNGS | GENCO |  |  | Circuits | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027054539679.2597222222 | 10270545 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 39679.2597 | 39682.6028 | CONT | 00001328 | SPIMAINT | O/Haul NO.1 500KV BUS AT SMTS | SPIPOWER |  |  | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1025164439679.2958333333 | 10251644 |  | Parent | TRUE | NO.1 CSC 220/10.5KV TRANS AT ROTS | 39679.2958 | 39680.6326 | CONT | 00004758 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1028643939679.2958333333 | 10286439 | 10251644 | Child | FALSE | NO.1 CSC AT ROTS | 39679.2958 | 39680.6326 | CONT | 00004718 | SPIMAINT | rebate for SVC tran outage | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026828739679.3 | 10268287 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39679.3 | 39679.7028 | REPDAILY | 00016040 | SPIMAINT | O/HAUL Transformer Div Mechanism (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028601439679.3104166667 | 10286014 |  | Parent | FALSE | NO.4 66KV BUS VT AT SVTS | 39679.3104 | 39679.3958 | DAILY | [12 empty] | 0
_1028619539679.3555555556 | 10286195 |  | Parent | FALSE | DC SUPPLY SYSTEMS AT YPS | 39679.3556 | 39679.5951 | DAILY | [12 empty] | 0
_1026828739680.2951388889 | 10268287 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39680.2951 | 39680.7521 | REPDAILY | 00016040 | SPIMAINT | O/HAUL Transformer Div Mechanism (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028591939680.3006944444 | 10285919 |  | Parent | FALSE | B2 220/66KV TRANS AT SVTS | 39680.3007 | 39680.6167 | DAILY | 00004850 | SPIMAINT | Repair oil leak | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z63358D939680.3243055556 | Z63358D9 |  | Parent | TRUE | MWTS NO.2 220KV LINE AT JLTS | 39680.3243 | 39681.6299 | CONT | 00015948 | VEN_AUG | MWTS 2L DROPPERS TO DOUBLE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358F339680.3243055556 | Z63358F3 | Z63358D9 | Child | FALSE | JLTS NO.2 220KV LINE AT MWTS | 39680.3243 | 39681.6299 | CONT | 00016131 | VEN_AUG | No2 220/66KV TX 220KV ISOL RECONNECT | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028503239680.3520833333 | 10285032 |  | Parent | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 39680.3521 | 39680.6111 | DAILY | 00004036 | SPIMAINT | Repair/replace two faulty fans from Trans | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028627939680.5027777778 | 10286279 |  | Parent | FALSE | MSS NO.1 330KV LINE AT DDTS | 39680.5028 | 39680.5104 | CONT | 00012357 | FORCED | Foreign object removal | ALSTOM |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026828739681.29375 | 10268287 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39681.2937 | 39681.6785 | REPDAILY | 00016040 | SPIMAINT | O/HAUL Transformer Div Mechanism (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028629239681.3125 | 10286292 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT SMTS | 39681.3125 | 39681.4285 | DAILY | 00012440 | SPIMAINT | change faulty insulator on tower 96 | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028635439681.3152777778 | 10286354 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB AT KTS | 39681.3153 | 39681.4153 | DAILY | [12 empty] | 0
_1028641039681.3152777778 | 10286410 | 10286354 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 39681.3153 | 39681.4153 | DAILY | 00119824 | FAULT | W/O for KTS 220kV Cap Bank CB Problem | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028591339681.3243055556 | 10285913 |  | Parent | FALSE | B3 TRANS 220KV BUS E/SW AT ATS | 39681.3243 | 39681.641 | DAILY | [12 empty] | 0
_1028632939681.3284722222 | 10286329 |  | Parent | TRUE | NO.3 220KV CAPACITOR BANK CB AT ROTS | 39681.3285 | 39681.3514 | DAILY | [12 empty] | 0
_1028641139681.3284722222 | 10286411 | 10286329 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39681.3285 | 39681.3514 | DAILY | 00112417 | FAULT | ROTS: No 3 220kV Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028635739681.4180555556 | 10286357 |  | Parent | FALSE | SYN/COND AT BLTS | 39681.4181 | 39681.4722 | DAILY | 00002547 | FAULT | W/O For BLTS S/con Trip | SPIPOWER |  |  | Sync Condensers | 3rd Party | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z63358B539682.2604166667 | Z63358B5 |  | Parent | TRUE | EX - NO.1 220KV BUS AT JLTS | 39682.2604 | 39684.6451 | CONT | 00009889 | VEN_AUG | JLTS No 1 220Kv BUS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358B639682.2604166667 | Z63358B6 | Z63358B5 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 39682.2604 | 39684.6451 | CONT | 00015936 | VEN_AUG | Line Rebate for No 1 Bus outage @ JLTS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026828739682.2951388889 | 10268287 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39682.2951 | 39682.6674 | REPDAILY | 00016040 | SPIMAINT | O/HAUL Transformer Div Mechanism (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028591539682.3381944444 | 10285915 |  | Parent | FALSE | B2 220/66KV TRANS AT ATS | 39682.3382 | 39682.6542 | DAILY | 00060871 | SPIMAINT | remove faulty upper fans & invest faulty wti | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028624939682.3423611111 | 10286249 |  | Parent | FALSE | NO.4A 66KV CAPACITOR BANK AT SVTS | 39682.3424 | 39682.4597 | DAILY | 00004825 | SPIMAINT | re-balance cap bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028637939682.6027777778 | 10286379 |  | Parent | FALSE | F2 TRANS NO.1 BUS 500KV CB AT SMTS | 39682.6028 | 39683.2569 | CONT | [12 empty] | 0
_1028634739682.6027777778 | 10286347 |  | Parent | FALSE | NO.1 500KV BUS AT SMTS | 39682.6028 | 39689.7736 | CONT | 00001328 | SPIMAINT | overhaul no.1 500kv bus & associated equip | SPIPOWER |  |  | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1028639039682.9465277778 | 10286390 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39682.9465 | 39684.8951 | CONT | 00356082 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V60458D639683.2569444444 | V60458D6 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 39683.2569 | 39683.7243 | DAILY | 00026099 | SPICAPX | invoke bay f & o/h roi/esw's within bay f bypass | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_V60458D739683.7326388889 | V60458D7 |  | Parent | FALSE | BAY F 500KV LINE AT SMTS (O.O.S) | 39683.7326 | 39708.6389 | CONT | 00012398 | SPICAPX | inject silicon to bay f gis compartments | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1026926939684.2881944444 | 10269269 |  | Parent | TRUE | NO.2 66KV BUS AT RWTS | 39684.2882 | 39684.6306 | DAILY | 00007479 | SPIMAINT | O/Haul NO.2 66KV BUS AT RWTS | SPIPOWER |  |  | Bus | Eastern | 66 |  |  |  | 0
_1028285739684.2881944444 | 10282857 | 10269269 | Child | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39684.2882 | 39684.6306 | DAILY | 00007399 | SPIMAINT | Rebate for bus outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028285839684.2881944444 | 10282858 | 10269269 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39684.2882 | 39684.6306 | DAILY | 00331179 | SPIMAINT | Rebate for bus outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028352539684.2881944444 | 10283525 | 10269269 | Child | FALSE | 2-4 66KV BUS TIE CB CT R/PH AT RWTS | 39684.2882 | 39684.6306 | DAILY | [12 empty] | 0
_1028352639684.2881944444 | 10283526 | 10269269 | Child | FALSE | B3 TRANS 66KV CB CT R/PH AT RWTS | 39684.2882 | 39684.6306 | DAILY | [12 empty] | 0
_1028634239684.3138888889 | 10286342 |  | Parent | FALSE | NO.1 GEN TRANS 500KV LINE E/SW AT LYPS | 39684.3139 | 39684.6104 | DAILY | [12 empty] | 0
_1027330939685.2972222222 | 10273309 |  | Parent | FALSE | EX - WMTS NO.2 220KV LINE CB CT R/PH AT FBTS | 39685.2972 | 39685.484 | DAILY | [12 empty] | 0
_X67058B839685.3125 | X67058B8 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 39685.3125 | 39689.3562 | CONT | 00119824 | SPICAPX | replace faulty ct's | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z56258A239685.3548611111 | Z56258A2 |  | Parent | FALSE | MKPS-BOPS-MBTS 220KV NW | 39685.3549 | 39694.588 | CONT | 00060197 | GEN_AUG | Out W/O MKPS Line replace Xarm & resag | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027077839686.2993055556 | 10270778 |  | Parent | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 39686.2993 | 39686.6896 | REPDAILY | 00329970 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028591939686.3083333333 | 10285919 |  | Parent | FALSE | B2 220/66KV TRANS AT SVTS | 39686.3083 | 39686.6257 | DAILY | 00004850 | SPIMAINT | Repair oil leak | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027329739686.3138888889 | 10273297 |  | Parent | FALSE | FBTS 220KV LINE CB CT R/PH AT BLTS | 39686.3139 | 39686.4167 | DAILY | [12 empty] | 0
_1027330339686.3138888889 | 10273303 |  | Parent | FALSE | EX - BLTS 220KV LINE CB CT R/PH AT FBTS | 39686.3139 | 39686.4167 | DAILY | [12 empty] | 0
_1028643539686.3222222222 | 10286435 |  | Parent | FALSE | SYN/COND AT BLTS | 39686.3222 | 39686.3938 | DAILY | 00002547 | FAULT | Syn Cond trip | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028634339686.3236111111 | 10286343 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39686.3236 | 39686.6868 | DAILY | 00319998 | APDALCOA | APD Work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1026805339686.3819444444 | 10268053 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39686.3819 | 39686.6049 | DAILY | 00017270 | SPIMAINT | 2 Yearly O/Haul - SVC at KGTS | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027077839687.2972222222 | 10270778 |  | Parent | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 39687.2972 | 39687.6944 | REPDAILY | 00329970 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028320339687.2986111111 | 10283203 |  | Parent | TRUE | JLTS NO.3 LINE/AUX TRANS 'C' 220KV CB AT HWPS | 39687.2986 | 39687.7118 | DAILY | [12 empty] | 0
_1028320439687.2986111111 | 10283204 | 10283203 | Child | FALSE | JLTS NO.3 220KV LINE AT HWPS | 39687.2986 | 39687.7118 | DAILY | 00015787 | SPIMAINT | Line outage rebate for Aux Trans C CTs | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028634439687.3125 | 10286344 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39687.3125 | 39687.391 | DAILY | 00319999 | APDALCOA | APD Work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027330739687.3180555556 | 10273307 |  | Parent | FALSE | EX - WMTS NO.1 220KV LINE CB CT R/PH AT FBTS | 39687.3181 | 39687.4521 | DAILY | [12 empty] | 0
_1027260939687.31875 | 10272609 |  | Parent | TRUE | SVC 220KV CB AT KGTS | 39687.3187 | 39687.6486 | DAILY | [12 empty] | 0
_1028581939687.31875 | 10285819 | 10272609 | Child | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39687.3187 | 39687.6486 | DAILY | 00017270 | SPIMAINT | Rebate W/O for SCV during its 220kV CB O/H | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X43258AU39687.33125 | X43258AU |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39687.3313 | 39687.875 | REPDAILY | 00359891 | SPICAPX | Out W/O No1 66kV Cap bank setting changes | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027328539687.5284722222 | 10273285 |  | Parent | TRUE | FBTS NO.1 220KV LINE CB CT R/PH AT WMTS | 39687.5285 | 39687.6153 | DAILY | [12 empty] | 0
_1028649939687.5284722222 | 10286499 | 10273285 | Child | FALSE | FBTS NO.1 220KV LINE AT WMTS | 39687.5285 | 39687.6153 | DAILY | 00025735 | SPIMAINT | out w/o for line - CT OIL SAMPLING | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1027077839688.2916666667 | 10270778 |  | Parent | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 39688.2917 | 39688.7146 | REPDAILY | 00329970 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1025165839688.29375 | 10251658 |  | Parent | TRUE | NO.2 CSC 220/10.5KV TRANS AT ROTS | 39688.2937 | 39689.6319 | CONT | 00004759 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 |  |  |  | 0
_1027900639688.29375 | 10279006 | 10251658 | Child | FALSE | NO.2 CSC AT ROTS | 39688.2937 | 39689.6319 | CONT | 00004716 | SPIMAINT | Rebate For SVC outage | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027262339688.3201388889 | 10272623 |  | Parent | TRUE | NO.1 TRANS 220KV CB AT KGTS | 39688.3201 | 39688.609 | DAILY | [12 empty] | 0
_1028582239688.3201388889 | 10285822 | 10272623 | Child | FALSE | R1 220/66/22KV TRANS AT KGTS | 39688.3201 | 39688.609 | DAILY | 00357301 | SPIMAINT | Perf calc W/O No1 Trans during its 220kV CB O-H | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258AV39688.3305555556 | X43258AV |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 39688.3306 | 39688.6826 | DAILY | 00359892 | SPICAPX | Out W/O No2 66kV Cap bank setting changes | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028655939688.3833333333 | 10286559 |  | Parent | FALSE | HWPS NO.3 LINE/MWTS NO.2 LINE 220KV CB AT JLTS | 39688.3833 | 39688.384 | CONT | [12 empty] | 0
_X43258AU39688.7013888889 | X43258AU |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39688.7014 | 39688.8021 | REPDAILY | 00359891 | SPICAPX | Out W/O No1 66kV Cap bank setting changes | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026926439689.2951388889 | 10269264 |  | Parent | FALSE | B3 220/66KV TRANS AT RWTS | 39689.2951 | 39689.6215 | DAILY | 00007455 | SPIMAINT | O/HAUL Transformer and Trafo Union Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027077839689.3027777778 | 10270778 |  | Parent | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 39689.3028 | 39689.6694 | REPDAILY | 00329970 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028474539689.3138888889 | 10284745 |  | Parent | FALSE | B4 TRANS 220KV CB CT R/PH AT WMTS | 39689.3139 | 39689.4333 | DAILY | [12 empty] | 0
_1027261739689.3270833333 | 10272617 |  | Parent | TRUE | NO.3 TRANS 220KV CB AT KGTS | 39689.3271 | 39689.6778 | DAILY | [12 empty] | 0
_1028582439689.3270833333 | 10285824 | 10272617 | Child | FALSE | R3 220/66/22KV TRANS AT KGTS | 39689.3271 | 39689.6778 | DAILY | 00017375 | SPIMAINT | Perf calc W/O No3 Trans during its 220kV CB O-H | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028650139689.4569444444 | 10286501 |  | Parent | TRUE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39689.4569 | 39689.5396 | DAILY | 00007399 | SPIMAINT | CT Oil Sample | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028650239689.4569444444 | 10286502 | 10286501 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39689.4569 | 39689.5396 | DAILY | 00331179 | SPIMAINT | Rebate for Capbank outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028653839690.275 | 10286538 |  | Parent | FALSE | A1 515/230KV TRANS AT HWTS | 39690.275 | 39690.6896 | DAILY | 00009772 | SPIMAINT | COOLING PUMPs FAULT | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009264039691.2784722222 | 10092640 |  | Parent | TRUE | YPS NO.1 220KV LINE AT HWPS | 39691.2785 | 39691.534 | DAILY | 00015795 | SPIMAINT | O/Haul - YPS No.1 LINE at HWPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009264239691.2784722222 | 10092642 | 10092640 | Child | FALSE | YPS NO.1 220KV LINE NO.6 BUS CB LINE SIDE E/SW AT HWPS | 39691.2785 | 39691.534 | DAILY | [12 empty] | 0
_1009264339691.2784722222 | 10092643 | 10092640 | Child | FALSE | YPS NO.1 220KV LINE E/SW AT HWPS | 39691.2785 | 39691.534 | DAILY | [12 empty] | 0
_1009264539691.2784722222 | 10092645 | 10092640 | Child | FALSE | YPS NO.1 220KV LINE NO.6 BUS CB LINE SIDE ISOL AT HWPS | 39691.2785 | 39691.534 | DAILY | [12 empty] | 0
_1027343339691.2784722222 | 10273433 | 10092640 | Child | TRUE | EX - HWPS NO.1 220KV LINE CB CT R/PH AT YPS | 39691.2785 | 39691.534 | DAILY | [12 empty] | 0
_1028650839691.2784722222 | 10286508 | 10092640 | Child | FALSE | YPS NO.1 220KV LINE NO.6 BUS CB AT HWPS | 39691.2785 | 39691.534 | DAILY | [12 empty] | 0
_1028652439691.2784722222 | 10286524 | 10273433 | Child | FALSE | HWPS NO.1 220KV LINE CB LINE SIDE ISOL AT YPS | 39691.2785 | 39691.534 | DAILY | [12 empty] | 0
_1026927339691.28125 | 10269273 |  | Parent | TRUE | NO.4 66KV BUS AT RWTS | 39691.2812 | 39691.6153 | DAILY | 00007481 | SPIMAINT | O/Haul NO.4 66KV BUS AT RWTS | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1028264539691.28125 | 10282645 | 10269273 | Child | FALSE | B4 220/66KV TRANS AT RWTS | 39691.2812 | 39691.6153 | DAILY | 00007451 | SPIMAINT | Rebate for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028323839691.28125 | 10283238 | 10269273 | Child | FALSE | 2-4 66KV BUS TIE CB AT RWTS | 39691.2812 | 39691.6153 | DAILY | [12 empty] | 0
_1028657139691.5694444444 | 10286571 |  | Parent | FALSE | W1 GEN TRANS NO.1 BUS 220KV CB AT YPS | 39691.5694 | 39773.2278 | CONT | [12 empty] | 0
_1028228039692.2965277778 | 10282280 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39692.2965 | 39692.7583 | REPDAILY | 00002863 | SPIMAINT | (V)M1 Trans S/s cubicle replacement | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028647939692.3076388889 | 10286479 |  | Parent | FALSE | LNGS NO.1 GEN TRANS 220KV LINE AT ATS | 39692.3076 | 39695.625 | CONT | 00360128 | GENCO | SCAP to LNGS | GENCO |  |  | Circuits | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028655739692.9048611111 | 10286557 |  | Parent | FALSE | YWPS NO.4 220KV LINE AT YPS | 39692.9049 | 39700.2431 | CONT | 00016428 | GENCO | SCAP to YWPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028228039693.2923611111 | 10282280 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39693.2924 | 39693.75 | REPDAILY | 00002863 | SPIMAINT | (V)M1 Trans S/s cubicle replacement | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027179339693.2993055556 | 10271793 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT RWTS | 39693.2993 | 39693.6722 | DAILY | 00350529 | SPIMAINT | O/Haul NO.2 220KV CAPACITOR BANK AT RWTS | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028604139693.3020833333 | 10286041 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39693.3021 | 39694.5375 | CONT | 00019243 | SPIMAINT | Out W/O SVC for HV testing of SVC trans | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028698339693.3138888889 | 10286983 | X67058B9 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT KTS | 39693.3139 | 39696.5014 | CONT | 00337022 | SPICAPX | out w/o for 1b cap bank - replace faulty ct's | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X67058B939693.3138888889 | X67058B9 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT KTS | 39693.3139 | 39696.5014 | CONT | 00327947 | SPICAPX | replace faulty ct's | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028639839693.3159722222 | 10286398 |  | Parent | TRUE | KTS NO.2 220KV LINE CB AT TTS | 39693.316 | 39693.6354 | DAILY | [12 empty] | 0
_1028697539693.3159722222 | 10286975 | 10286398 | Child | FALSE | KTS NO.2 220KV LINE AT TTS | 39693.316 | 39693.6354 | DAILY | 00015727 | SPIMAINT | OUT W/O FOR LINE replace leaking pressure switches | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026878639693.3194444444 | 10268786 |  | Parent | FALSE | FUTURE F1 TRANS 500KV LINE AT SMTS | 39693.3194 | 39696.5833 | CONT | 00012391 | SPIMAINT | 500kv SF6 Bushing & Line Entry GDM | SPIPOWER |  |  | Circuits | Western | 500 |  |  |  | 0
_X67058B439693.325 | X67058B4 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 39693.325 | 39696.6674 | CONT | 00112418 | SPICAPX | Replace Cableing between CT and marseling box | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028647139693.4215277778 | 10286471 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.1 BUS CB AT DDTS | 39693.4215 | 39693.4917 | DAILY | [12 empty] | 0
_1027257539694.2923611111 | 10272575 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK AT RWTS | 39694.2924 | 39694.6153 | DAILY | 00356999 | SPIMAINT | O/Haul 22KV CAPACITOR BANK | SPIPOWER |  |  | Capacitors | Eastern | 22 | CONNECTION ASSET | EXCLUDED |  | 0
_1028228039694.2923611111 | 10282280 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39694.2924 | 39694.8264 | REPDAILY | 00002863 | SPIMAINT | (V)M1 Trans S/s cubicle replacement | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028643139694.29375 | 10286431 |  | Parent | FALSE | ROTS 220KV LINE NO.1 BUS CB AT RWTS | 39694.2937 | 39694.5889 | DAILY | [12 empty] | 0
_1027919639694.3131944445 | 10279196 |  | Parent | FALSE | MSS NO.1 LINE/SMTS NO.1 LINE 330KV CB AT DDTS | 39694.3132 | 39694.5896 | DAILY | [12 empty] | 0
_1028668139694.3923611111 | 10286681 |  | Parent | FALSE | B1 220/66KV TRANS AT RWTS | 39694.3924 | 39694.6819 | DAILY | 00364702 | SPIMAINT | Work for SWN SM165a | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1028681139694.7069444444 | 10286811 |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39694.7069 | 39694.7208 | DAILY | 00007452 | FAULT | Rebate W/O for RWTS Bus Trip | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028634939695.2951388889 | 10286349 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39695.2951 | 39695.6486 | REPDAILY | 00354002 | SPIMAINT | TOP UP TRANSFORMER CHECK OIL LEAK | SPIPOWER |  |  | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1027257739695.3034722222 | 10272577 |  | Parent | FALSE | NO.2 22KV CAPACITOR BANK AT RWTS | 39695.3035 | 39695.6458 | DAILY | 00357000 | SPIMAINT | O/Haul 22KV CAPACITOR BANK | SPIPOWER |  |  | Capacitors | Eastern | 22 | CONNECTION ASSET | EXCLUDED |  | 0
_1028228039695.3069444444 | 10282280 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39695.3069 | 39695.7958 | REPDAILY | 00002863 | SPIMAINT | (V)M1 Trans S/s cubicle replacement | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028663239695.3131944445 | 10286632 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB CT R/PH AT RWTS | 39695.3132 | 39695.6868 | DAILY | [12 empty] | 0
_1028665839695.3131944445 | 10286658 | 10286632 | Child | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39695.3132 | 39695.6868 | DAILY | 00007399 | SPIMAINT | Rebate for Capbank Outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028665939695.3131944445 | 10286659 | 10286632 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39695.3132 | 39695.6868 | DAILY | 00331179 | SPIMAINT | Rebate for Capbank Outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027919739695.3145833333 | 10279197 |  | Parent | FALSE | MSS NO.2 LINE/SMTS NO.2 LINE 330KV CB AT DDTS | 39695.3146 | 39695.4951 | DAILY | [12 empty] | 0
_1026928139696.2895833333 | 10269281 |  | Parent | TRUE | L3 TRANS 22KV CB AT RWTS | 39696.2896 | 39696.6389 | DAILY | [12 empty] | 0
_1028265539696.2895833333 | 10282655 | 10269281 | Child | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39696.2896 | 39696.6389 | DAILY | 00007452 | SPIMAINT | REBATE TRANS for CB outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028532939696.2944444444 | 10285329 | Z63358C3 | Child | FALSE | NO.2 220KV BUS X PROT AT JLTS | 39696.2944 | 39700.7181 | CONT | [12 empty] | 0
_Z63358C339696.2944444444 | Z63358C3 |  | Parent | TRUE | EX - NO.2 220KV BUS AT JLTS | 39696.2944 | 39700.7181 | CONT | 00009890 | VEN_AUG | REPLACE BUS INSULATORS & JLGS A ISOL | VENCORP | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358C439696.2944444444 | Z63358C4 | Z63358C3 | Child | FALSE | HWPS NO.2 220KV LINE AT JLTS | 39696.2944 | 39700.7181 | CONT | 00015937 | VEN_AUG | REBATE FOR LINE OUTAGE FOR JLTS No2 BUS OUTAGE | VENCORP | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028228039696.2965277778 | 10282280 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39696.2965 | 39696.7465 | REPDAILY | 00002863 | SPIMAINT | (V)M1 Trans S/s cubicle replacement | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028601439696.3763888889 | 10286014 |  | Parent | FALSE | NO.4 66KV BUS VT AT SVTS | 39696.3764 | 39696.4736 | DAILY | [12 empty] | 0
_1028681339696.4423611111 | 10286813 |  | Parent | FALSE | JLGA NO.4 UNIT TRANS DISC CB AT JLGA | 39696.4424 | 39700.7181 | CONT | [12 empty] | 0
_1028683039696.4423611111 | 10286830 |  | Parent | FALSE | JLGA NO.2 UNIT TRANS DISC CB AT JLGA | 39696.4424 | 39700.7181 | CONT | [12 empty] | 0
_1028683139696.4423611111 | 10286831 |  | Parent | FALSE | JLGA NO.1 UNIT TRANS DISC CB AT JLGA | 39696.4424 | 39700.7181 | CONT | [12 empty] | 0
_1028682939696.4576388889 | 10286829 |  | Parent | FALSE | JLGA NO.3 UNIT TRANS DISC CB AT JLGA | 39696.4576 | 39700.7181 | CONT | [12 empty] | 0
_1028664039696.9145833333 | 10286640 |  | Parent | FALSE | NO.7 GEN TRANS LINE AT HWPS | 39696.9146 | 39741.5694 | CONT | 00356085 | GENCO | SCAP to HWPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z64558A739697.2944444444 | Z64558A7 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39697.2944 | 39697.4458 | REPDAILY | 00026089 | VEN_AUG | Out W/O BATS-HOTS Line OPGW install Runs 1 & 2 | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028228439697.2965277778 | 10282284 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39697.2965 | 39697.6208 | REPDAILY | 00002862 | SPIMAINT | (V)M2 Trans S/S cubicle replacement | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1024067939697.3069444444 | 10240679 | 10283620 | Child | FALSE | B1 220/66KV TRANS 66KV VT R/PH AT SVTS | 39697.3069 | 39697.5507 | DAILY | [12 empty] | 0
_1028362039697.3069444444 | 10283620 |  | Parent | TRUE | 1-3 220KV BUS TIE CB NO.1 BUS SIDE ISOL AT SVTS | 39697.3069 | 39697.5507 | DAILY | [12 empty] | 0
_1028362139697.3069444444 | 10283621 | 10283620 | Child | FALSE | B1 220/66KV TRANS AT SVTS | 39697.3069 | 39697.5507 | DAILY | 00004849 | SPIMAINT | Rebate Tran for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028362239697.3069444444 | 10283622 | 10283620 | Child | FALSE | ROTS NO.1 220KV LINE AT SVTS | 39697.3069 | 39697.5507 | DAILY | 00351700 | SPIMAINT | Rebate Line for Bus Outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028690539697.5868055556 | 10286905 |  | Parent | TRUE | NO.2 66KV BUS AT TGTS | 39697.5868 | 39697.6799 | DAILY | 00364791 | FORCED | Replace insulator on CDN 66kvfdr CB bus side isols | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1028690639697.5868055556 | 10286906 | 10286905 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 39697.5868 | 39697.6799 | DAILY | 00003127 | FORCED | Perf calc W/O B2 Trans during No2 66kV Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028691539697.6305555556 | 10286915 |  | Parent | TRUE | MLTS NO.1 500KV LINE CB AT HYTS | 39697.6306 | 39697.6764 | CONT | [12 empty] | 0
_1028692739697.6305555556 | 10286927 | 10286915 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39697.6306 | 39697.6764 | DAILY | 00002863 | FORCED | Rebate Outage for SF6 top up | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028228439698.2951388889 | 10282284 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39698.2951 | 39698.7424 | REPDAILY | 00002862 | SPIMAINT | (V)M2 Trans S/S cubicle replacement | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028228439699.2916666667 | 10282284 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39699.2917 | 39699.7486 | REPDAILY | 00002862 | SPIMAINT | (V)M2 Trans S/S cubicle replacement | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z64558A739699.2986111111 | Z64558A7 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39699.2986 | 39699.7535 | REPDAILY | 00026089 | VEN_AUG | Out W/O BATS-HOTS Line OPGW install Runs 1 & 2 | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027605439699.3027777778 | 10276054 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT RTS | 39699.3028 | 39699.4715 | DAILY | 00055373 | SPIMAINT | Cap Bank Rebate for CT checks | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028637639699.3069444444 | 10286376 |  | Parent | FALSE | B1 TRANS NO.2 BUS 220KV CB AT RWTS | 39699.3069 | 39699.6417 | DAILY | [12 empty] | 0
_1028638039699.3069444444 | 10286380 |  | Parent | FALSE | B1 TRANS NO.2 BUS 220KV CB AT RWTS | 39699.3069 | 39699.6417 | DAILY | [12 empty] | 0
_X67058B539699.3152777778 | X67058B5 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39699.3153 | 39703.6319 | CONT | 00112417 | SPICAPX | Replace Cableing between CT and marseling box | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028693239699.5763888889 | 10286932 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39699.5764 | 39699.5931 | DAILY | [12 empty] | 0
_1028364539700.29375 | 10283645 |  | Parent | TRUE | TSTS LINE/YPS NO.6 LINE CB TSTS LINE SIDE ISOL AT ROTS | 39700.2937 | 39700.6243 | DAILY | [12 empty] | 0
_1028364639700.29375 | 10283646 | 10283645 | Child | FALSE | TSTS 220KV LINE AT ROTS | 39700.2937 | 39700.6243 | DAILY | 00022678 | SPIMAINT | Rebate LINE for outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028228439700.3020833333 | 10282284 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39700.3021 | 39700.7438 | REPDAILY | 00002862 | SPIMAINT | (V)M2 Trans S/S cubicle replacement | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027305539700.3027777778 | 10273055 |  | Parent | FALSE | A1 515/230KV TRANS AT HWTS | 39700.3028 | 39702.666 | CONT | 00009772 | SPIMAINT | Condition Monitoring Metro Trans 2day Valley Area | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027341739700.3034722222 | 10273417 | X67058B6 | Child | FALSE | JLA NO.2 220KV LINE CB CT R/PH AT TBTS | 39700.3035 | 39700.6076 | DAILY | [12 empty] | 0
_1028535339700.3034722222 | 10285353 |  | Parent | FALSE | JLA NO.2 220KV LINE AT TBTS | 39700.3035 | 39700.6076 | DAILY | 00026919 | SPIMAINT | rebate for Line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028535639700.3034722222 | 10285356 | X67058B6 | Child | FALSE | JLA NO.2 220KV LINE AT TBTS | 39700.3035 | 39700.6076 | DAILY | 00026919 | SPIMAINT | Rebate for Line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X67058B639700.3034722222 | X67058B6 |  | Parent | TRUE | JLA NO.2 220KV LINE CB AT TBTS | 39700.3035 | 39700.6076 | DAILY | [12 empty] | 0
_1027266339700.3166666667 | 10272663 |  | Parent | FALSE | TTS 220KV LINE NO.1 BUS CB AT EPSY | 39700.3167 | 39700.6715 | DAILY | [12 empty] | 0
_1027920039700.3291666667 | 10279200 |  | Parent | FALSE | JINDERA 330KV LINE AT WOTS | 39700.3292 | 39700.75 | DAILY | 00012053 | SPIMAINT | Out W/O Jindera Line for CVT testing by tech serv | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028693639700.41875 | 10286936 |  | Parent | FALSE | SYN/COND TRANS NO.2 BUS 66KV CB AT FBTS | 39700.4187 | 39700.5451 | DAILY | [12 empty] | 0
_1027266539700.6673611111 | 10272665 |  | Parent | FALSE | TTS 220KV LINE NO.2 BUS CB AT EPSY | 39700.6674 | 39701.6799 | CONT | [12 empty] | 0
_1028412239701.2861111111 | 10284122 |  | Parent | TRUE | NO.2 220KV CAPACITOR BANK CB AT RWTS | 39701.2861 | 39701.4625 | DAILY | [12 empty] | 0
_1028664939701.2861111111 | 10286649 | 10284122 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RWTS | 39701.2861 | 39701.4625 | DAILY | 00350529 | SPIMAINT | Cap Bank Rebate for CB outage | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X67058B239701.2958333333 | X67058B2 |  | Parent | TRUE | EX - B1 TRANS 220KV CB CT R/PH AT TBTS | 39701.2958 | 39703.7701 | CONT | [12 empty] | 0
_X67058B739701.2958333333 | X67058B7 | X67058B2 | Child | FALSE | B1 220/66KV TRANS AT TBTS | 39701.2958 | 39703.7701 | DAILY | 00004901 | SPICAPX | Rebate for Tran outage | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027919839701.3145833333 | 10279198 |  | Parent | FALSE | MSS NO.1 330KV LINE AT DDTS | 39701.3146 | 39701.6319 | DAILY | 00012357 | SPIMAINT | Out W/O MSS 1 Line for CVT test by tech services | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028693839701.3993055556 | 10286938 |  | Parent | FALSE | SYN/COND TRANS NO.3 BUS 66KV CB AT FBTS | 39701.3993 | 39701.4896 | DAILY | [12 empty] | 0
_X67058C039701.4541666667 | X67058C0 |  | Parent | FALSE | A1 TRANS/NO.2 CSC CB AT ROTS | 39701.4542 | 39701.5757 | DAILY | [12 empty] | 0
_1028669139701.4694444445 | 10286691 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.1 BUS CB BUS SIDE ROI AT DDTS | 39701.4694 | 39701.4743 | DAILY | [12 empty] | 0
_1028643039701.4777777778 | 10286430 |  | Parent | FALSE | H1 TRANS NO.1 BUS 330KV CB AT DDTS | 39701.4778 | 39701.4944 | DAILY | [12 empty] | 0
_1028705839701.5763888889 | 10287058 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 39701.5764 | 39701.591 | CONT | [12 empty] | 0
_1027267539701.6770833333 | 10272675 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT EPSY | 39701.6771 | 39702.6556 | CONT | [12 empty] | 0
_X32058TT39702.2673611111 | X32058TT |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 39702.2674 | 39702.6125 | DAILY | 00352791 | SPIMAINT | Replace oil pump | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z63358G239702.2854166667 | Z63358G2 | Z63358G1 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 39702.2854 | 39704.7181 | CONT | 00015936 | VEN_AUG | LINE REBATE FOR No1 BUS OUTAGE AT JLTS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358G139702.2854166667 | Z63358G1 |  | Parent | TRUE | EX - NO.1 220KV BUS AT JLTS | 39702.2854 | 39704.7184 | CONT | 00009889 | VEN_AUG | C/O MWTS 1L 1B CB BUS SIDE ROI | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028463339702.3041666667 | 10284633 |  | Parent | TRUE | NO.2 220KV CAPACITOR BANK CB AT ATS | 39702.3042 | 39702.6472 | DAILY | [12 empty] | 0
_1029627739702.3041666667 | 10296277 | 10284633 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ATS | 39702.3042 | 39702.6472 | DAILY | 00350821 | SPIMAINT | out w/o for cap bank HPL - B1GS CB TESTING BY ABB | SPIPOWER |  |  | Capacitors | Western | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1027919939702.3152777778 | 10279199 |  | Parent | FALSE | MSS NO.2 330KV LINE AT DDTS | 39702.3153 | 39702.6194 | DAILY | 00012358 | SPIMAINT | Out W/O MSS 2 Line for CVT test by tech services | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027173339702.3166666667 | 10271733 |  | Parent | FALSE | EX - TTS NO.1 220KV LINE AT KTS | 39702.3167 | 39702.6368 | REPDAILY | 00015989 | SPIMAINT | INSPECTION OF LINE (TTS NO.1 220KV) AT KTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358G439702.3576388889 | Z63358G4 |  | Parent | FALSE | MWTS NO.1 220KV LINE AT JLTS | 39702.3576 | 39702.65 | REPDAILY | 00015947 | VEN_AUG | DAILY DE-ENERGISED FOR BUS PERMIT | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028704339703.2291666667 | 10287043 |  | Parent | TRUE | NO.2 220KV CAPACITOR BANK CB AT RWTS | 39703.2292 | 39703.4944 | DAILY | [12 empty] | 0
_1028704439703.2291666667 | 10287044 | 10287043 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RWTS | 39703.2292 | 39703.4944 | DAILY | 00350529 | SPIMAINT | Cap Bank Rebate for CB outage | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029188739703.2840277778 | 10291887 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT RWTS | 39703.284 | 39703.3479 | DAILY | [12 empty] | 0
_1027173339703.29375 | 10271733 |  | Parent | FALSE | EX - TTS NO.1 220KV LINE AT KTS | 39703.2937 | 39703.6285 | REPDAILY | 00015989 | SPIMAINT | INSPECTION OF LINE (TTS NO.1 220KV) AT KTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358G439703.3326388889 | Z63358G4 |  | Parent | FALSE | MWTS NO.1 220KV LINE AT JLTS | 39703.3326 | 39703.6472 | REPDAILY | 00015947 | VEN_AUG | DAILY DE-ENERGISED FOR BUS PERMIT | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558E139703.3673611111 | X56558E1 |  | Parent | FALSE | B1 TRANS 220KV CB AT GTS | 39703.3674 | 39703.4153 | DAILY | [12 empty] | 0
_X56558E239703.4493055556 | X56558E2 |  | Parent | FALSE | GTS NO.2 220KV LINE NO.2 BUS CB AT MLTS | 39703.4493 | 39703.4903 | DAILY | [12 empty] | 0
_X56558E439703.5347222222 | X56558E4 | X56558E3 | Child | FALSE | BATS NO.2 220KV LINE AT MLTS | 39703.5347 | 39703.5903 | DAILY | 00022969 | SPICAPX | Rebate W/O BATS No2 Line. Proximity of faulty CTs | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558E339703.5347222222 | X56558E3 |  | Parent | TRUE | TGTS 220KV LINE NO.2 BUS CB AT MLTS | 39703.5347 | 39703.5908 | DAILY | [12 empty] | 0
_1029603139703.9201388889 | 10296031 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 39703.9201 | 39705.8764 | CONT | [12 empty] | 0
_1029617439704.2131944444 | 10296174 |  | Parent | TRUE | B3 220/66KV TRANS AT MWTS | 39704.2132 | 39704.2417 | DAILY | 00010267 | FORCED | Forced outage MPS Gas Alarm | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029617539704.2131944444 | 10296175 | 10296174 | Child | FALSE | HWPS-MPS-MWTS 220KV G | 39704.2132 | 39704.2417 | DAILY | 00020448 | FORCED | Rebate outage for Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027304539704.2138888889 | 10273045 |  | Parent | FALSE | NO.2 11/220KV TRANS BANK AT MPS | 39704.2139 | 39709.6931 | CONT | 00001164 | SPIMAINT | Condition Monitoring Metro Trans 3day Valley Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | see note (2) | 0
_Z81058A039704.2965277778 | Z81058A0 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 39704.2965 | 39704.691 | REPDAILY | 00022690 | VEN_AUG | Out W/O GTS-PTH No1 Line raise conductor height | SPIPOWER | Z810 | Z810 - COST EST - (GLN) TOWER HEIGHT ALTERATIONS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358G439704.2979166667 | Z63358G4 |  | Parent | FALSE | MWTS NO.1 220KV LINE AT JLTS | 39704.2979 | 39704.709 | REPDAILY | 00015947 | VEN_AUG | DAILY DE-ENERGISED FOR BUS PERMIT | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V60458D839704.3229166667 | V60458D8 |  | Parent | TRUE | BAY F 500KV LINE AT SMTS (O.O.S) | 39704.3229 | 39704.6146 | DAILY | 00012398 | SPICAPX | hv testing of f2 trans 500kv line entry | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Circuits | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_V60458E039704.3229166667 | V60458E0 | V60458D8 | Child | FALSE | F2 500/330KV TRANS BANK AT SMTS | 39704.3229 | 39704.6146 | DAILY | 00026099 | SPICAPX | out w/o for f2 tr - hv test f2 tr 500kv line entry | SPIPOWER | V604 | V604 - (SMTS) SILICON INJECTION ON LINE ENTRY CO | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1025068139705.2951388889 | 10250681 |  | Parent | TRUE | HWPS-MWTS-MPS 220KV LINE E/SW AT MPS | 39705.2951 | 39705.584 | DAILY | [12 empty] | 0
_1027163939705.2951388889 | 10271639 | 10250681 | Child | TRUE | NO.1 11/220KV TRANS 220KV ISOL AT MPS | 39705.2951 | 39705.584 | DAILY | [12 empty] | 0
_1027164139705.2951388889 | 10271641 | 10250681 | Child | TRUE | NO.2 11/220KV TRANS 220KV ISOL AT MPS | 39705.2951 | 39705.584 | DAILY | [12 empty] | 0
_1027164339705.2951388889 | 10271643 | 10271639 | Child | FALSE | NO.1 11/220KV TRANS 220KV E/SW AT MPS | 39705.2951 | 39705.584 | DAILY | [12 empty] | 0
_1027164539705.2951388889 | 10271645 | 10271641 | Child | FALSE | NO.2 11/220KV TRANS 220KV E/SW AT MPS | 39705.2951 | 39705.584 | DAILY | [12 empty] | 0
_1027304339705.2972222222 | 10273043 |  | Parent | TRUE | NO.1 11/220KV TRANS BANK AT MPS | 39705.2972 | 39709.6931 | CONT | 00001082 | SPIMAINT | Condition Monitoring Metro Trans 3day Valley Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029602839705.2972222222 | 10296028 | 10273043 | Child | FALSE | MPS-MWTS 220KV LINE AT HWPS | 39705.2972 | 39709.6931 | CONT | 00015789 | SPIMAINT | LINE REBATE FOR ISOLS & E/SWS AT MPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027024139705.2979166667 | 10270241 |  | Parent | FALSE | NO.1B 220KV BUS AT BLTS | 39705.2979 | 39705.6264 | DAILY | 00002641 | SPIMAINT | O/Haul NO.1B 220KV BUS AT BLTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028695839705.4166666667 | 10286958 |  | Parent | TRUE | NO.1 220KV BUS CT R/PH AT RTS | 39705.4167 | 39705.5674 | DAILY | [12 empty] | 0
_1028696039705.4166666667 | 10286960 | 10286958 | Child | FALSE | B1 220/66KV TRANS AT RTS | 39705.4167 | 39705.5674 | DAILY | 00007329 | SPIMAINT | Trans Rebate for Bus Outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028696139705.4166666667 | 10286961 | 10286958 | Child | FALSE | ROTS NO.1 220KV LINE AT RTS | 39705.4167 | 39705.5674 | DAILY | 00021385 | SPIMAINT | Line Rebate for Bus Outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027305939706.2923611111 | 10273059 |  | Parent | TRUE | B3 220/66KV TRANS AT MWTS | 39706.2924 | 39708.7292 | CONT | 00010267 | SPIMAINT | Condition Monitoring Metro Trans 2day Valley Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028651239706.2923611111 | 10286512 | 10273059 | Child | FALSE | B3 220/66KV TRANS 66KV BUSHING R/PH AT MWTS | 39706.2924 | 39708.7292 | DAILY | [12 empty] | 0
_1029614239707.2743055556 | 10296142 |  | Parent | FALSE | SYN/COND AT BLTS | 39707.2743 | 39707.3979 | CONT | 00002547 | FORCED | BLTS syn cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z81058A139707.2986111111 | Z81058A1 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39707.2986 | 39707.7236 | REPDAILY | 00022691 | VEN_AUG | Out W/O GTS-PTH No2 Line raise conductor height | SPIPOWER | Z810 | Z810 - COST EST - (GLN) TOWER HEIGHT ALTERATIONS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027341539707.3090277778 | 10273415 | 10286330 | Child | FALSE | JLA NO.1 220KV LINE CB CT R/PH AT TBTS | 39707.309 | 39708.6542 | DAILY | [12 empty] | 0
_1028633039707.3090277778 | 10286330 |  | Parent | TRUE | JLA NO.1 220KV LINE CB AT TBTS | 39707.309 | 39708.6542 | CONT | [12 empty] | 0
_1028633239707.3090277778 | 10286332 | 10286330 | Child | FALSE | JLA NO.1 220KV LINE CB AT TBTS | 39707.309 | 39708.6542 | CONT | [12 empty] | 0
_1028696239707.3111111111 | 10286962 |  | Parent | FALSE | MWTS-MPS LINE 220KV CB AT HWPS | 39707.3111 | 39707.675 | DAILY | [12 empty] | 0
_V71158A439707.3131944445 | V71158A4 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39707.3132 | 39798.6771 | CONT | [12 empty] | 0
_X67058C139707.325 | X67058C1 |  | Parent | FALSE | NO.4 220KV CAPACITOR BANK AT BLTS | 39707.325 | 39710.4243 | CONT | 00327921 | SPICAPX | replace defective ct's | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027241339707.3736111111 | 10272413 |  | Parent | FALSE | R3 220/66/22KV TRANS AT KGTS | 39707.3736 | 39707.6632 | REPDAILY | 00017375 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z64558B339708.2916666667 | Z64558B3 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39708.2917 | 39708.7431 | DAILY | 00026089 | VEN_AUG | Out W/O BATS-HOTS Line OPGW install Run 1 | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858G739708.2951388889 | X50858G7 |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 39708.2951 | 39708.3854 | DAILY | [12 empty] | 0
_1027241339708.3125 | 10272413 |  | Parent | FALSE | R3 220/66/22KV TRANS AT KGTS | 39708.3125 | 39708.7167 | REPDAILY | 00017375 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X43258AZ39708.3166666667 | X43258AZ |  | Parent | FALSE | MLRC 220KV LINE AT RCTS | 39708.3167 | 39708.3361 | REPDAILY | 00352130 | SPICAPX | Out W/O MLRC Line CB & ROI functional checks | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 4
_X50858G839708.4166666667 | X50858G8 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39708.4167 | 39708.566 | DAILY | 00017900 | SPICAPX | KTS 1L CB & KTS 3L 2B CB prox - Bay K CB install | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858G939708.5680555556 | X50858G9 |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 39708.5681 | 39731.6049 | CONT | [12 empty] | 0
_1029620239708.9138888889 | 10296202 |  | Parent | FALSE | YWPS NO.3 220KV LINE AT YPS | 39708.9139 | 39713.9097 | CONT | 00016426 | GENCO | W3 Gen Trans isolated and earthed | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029620339708.9583333333 | 10296203 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 39708.9583 | 39712.9035 | CONT | 00356079 | GENCO | Genco work | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X43258AZ39709.3013888889 | X43258AZ |  | Parent | FALSE | MLRC 220KV LINE AT RCTS | 39709.3014 | 39709.5118 | REPDAILY | 00352130 | SPICAPX | Out W/O MLRC Line CB & ROI functional checks | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 4
_1027241339709.3194444444 | 10272413 |  | Parent | FALSE | R3 220/66/22KV TRANS AT KGTS | 39709.3194 | 39709.6625 | REPDAILY | 00017375 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029629239709.5006944445 | 10296292 |  | Parent | TRUE | B3 220/66KV TRANS AT MWTS | 39709.5007 | 39709.6931 | DAILY | 00010267 | FORCED | B3 Trans at MWTS stranded while MPS L2 Trans out. | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029630739709.5006944445 | 10296307 | 10296292 | Child | FALSE | HWPS-MPS-MWTS 220KV G | 39709.5007 | 39709.6931 | DAILY | 00020448 | FAULT | Rebate workorder | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029645939710.2958333333 | 10296459 |  | Parent | FALSE | BTS 220KV LINE AT RTS | 39710.2958 | 39751.5312 | CONT | 00021222 | SPIMAINT | Rebate outage for Cable | SPIPOWER |  | V796 - (BTS-RTS) CABLE JOINT REPLACEMENTS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028343739710.3118055556 | 10283437 |  | Parent | FALSE | 2B-4 220KV BUS TIE CB NO.4 BUS CT R/PH AT RTS | 39710.3118 | 39710.666 | DAILY | [12 empty] | 0
_X3F258A039710.3861111111 | X3F258A0 |  | Parent | FALSE | NO.1 CSC AT ROTS | 39710.3861 | 39710.5208 | DAILY | 00004718 | SPIMAINT | Inspection of CSC for rebuild | SPIPOWER | X3F2 | X3F2 - (ROTS) REPL THYRISTER & CONTROL CCT - CSC | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029639839710.6548611111 | 10296398 |  | Parent | TRUE | LY NO.1 66KV FDR CB AT MWTS | 39710.6549 | 39710.6625 | DAILY | [12 empty] | 0
_1029663339710.6548611111 | 10296633 | 10296398 | Child | FALSE | LY NO.1 66KV FDR AT MWTS | 39710.6549 | 39710.6625 | DAILY | 00016140 | FORCED | SF6 Top up Sub LY No1 Line 66kV CB | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029638239710.6659722222 | 10296382 |  | Parent | FALSE | 2B-4 220KV BUS TIE CB NO.2B BUS SIDE ISOL AT RTS | 39710.666 | 39710.7799 | DAILY | [12 empty] | 0
_1028623639710.9256944444 | 10286236 |  | Parent | FALSE | NO.4 GEN TRANS 500KV LINE E/SW AT LYPS | 39710.9257 | 39751.4215 | CONT | [12 empty] | 0
_Z64558A939711.29375 | Z64558A9 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39711.2937 | 39711.6521 | REPDAILY | 00026089 | VEN_AUG | Out W/O BATS-HOTS Line OPGW install Runs 3 & 4 | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z64558A939712.2930555556 | Z64558A9 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39712.2931 | 39712.616 | REPDAILY | 00026089 | VEN_AUG | Out W/O BATS-HOTS Line OPGW install Runs 3 & 4 | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010344439712.3256944444 | 10103444 |  | Parent | FALSE | A STH 22KV BUS AT RTS | 39712.3257 | 39712.6035 | DAILY | 00007355 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 22 | NON AER ELEMENT |  |  | 0
_1029640939712.6354166667 | 10296409 |  | Parent | FALSE | SYN/COND AT TSTS | 39712.6354 | 39712.9507 | CONT | 00007626 | FAULT | S/Con auto opening [see SIR 10296410] | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029641139712.6354166667 | 10296411 |  | Parent | FALSE | SYN/COND AT TSTS | 39712.6354 | 39712.9507 | CONT | 00007626 | FAULT | REPLACE DEFECTIVE VT | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V71158A239713.3229166667 | V71158A2 |  | Parent | FALSE | A4 GEN TRANS 500KV CB AT LYPS | 39713.3229 | 39751.4218 | CONT | [12 empty] | 0
_1029642139713.5247106482 | 10296421 |  | Parent | FALSE | LYPS-HWTS 1 500KV G | 39713.5247 | 39714.3814 | CONT | 00020318 | GENCO | Isolations for SCAP on LYA Unit 2 | GENCO |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028600139714.2930555556 | 10286001 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39714.2931 | 39714.6285 | REPDAILY | 00016040 | SPIMAINT | No2 Trans Grp Div Sw Service ops O/Haul | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027303539714.2944444444 | 10273035 |  | Parent | FALSE | A4 500/220KV TRANS BANK AT KTS | 39714.2944 | 39717.5931 | CONT | 00026098 | SPIMAINT | Condition Monitoring Metro Trans 3day West Area | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028867039714.2972222222 | 10288670 | 10288669 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39714.2972 | 39714.6382 | DAILY | 00331179 | SPIMAINT | Rebate for Cap Bank outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027810539715.2923611111 | 10278105 |  | Parent | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 39715.2924 | 39715.6458 | REPDAILY | 00331027 | SPIMAINT | Replace bushing caps Cap Bank | SPIPOWER |  |  | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028600139715.2930555556 | 10286001 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39715.2931 | 39715.6924 | REPDAILY | 00016040 | SPIMAINT | No2 Trans Grp Div Sw Service ops O/Haul | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028364239715.3361111111 | 10283642 |  | Parent | TRUE | RWTS LINE/YPS NO.7 LINE CB YPS NO.7 LINE SIDE ISOL AT ROTS | 39715.3361 | 39715.6104 | DAILY | [12 empty] | 0
_1028364339715.3361111111 | 10283643 | 10283642 | Child | FALSE | YPS NO.7 220KV LINE AT ROTS | 39715.3361 | 39715.6104 | DAILY | 00024013 | SPIMAINT | Rebate LINE for outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028522639715.3597222222 | 10285226 |  | Parent | FALSE | MSS -DDTS 1 330KV NW | 39715.3597 | 39715.8729 | REPDAILY | 00060190 | SPIMAINT | Out W/O for repair of hot joints MSS-DDTS No1 Line | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029631539715.3645833333 | 10296315 |  | Parent | FALSE | NO.8 22KV/415V S/S TRANS AT SMTS | 39715.3646 | 39716.6667 | CONT | 00001327 | DB_AUG | VSCAP to DOC | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1027810539716.2916666667 | 10278105 |  | Parent | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 39716.2917 | 39716.5819 | REPDAILY | 00331027 | SPIMAINT | Replace bushing caps Cap Bank | SPIPOWER |  |  | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028602539716.3611111111 | 10286025 |  | Parent | FALSE | HYTS-SESS 1 275KV WH | 39716.3611 | 39716.7208 | DAILY | 00022795 | ELECTRAN | Electranet Outage | ELECTRAN |  |  | Circuits | Alstom | 275 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029658439716.6284722222 | 10296584 |  | Parent | FALSE | BOPS-MKPS 220KV LINE CB AT MBTS | 39716.6285 | 39716.6764 | CONT | [12 empty] | 0
_1029658839716.6284722222 | 10296588 |  | Parent | FALSE | MKPS-BOPS-MBTS 220KV NW | 39716.6285 | 39716.6764 | DAILY | 00060197 | FAULT | Rebate for line outage | GENCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029658639716.7263888889 | 10296586 |  | Parent | FALSE | GWS 2 - EAST GW A1 GEN TURB. HOUSE WALL to A 1 GEN RACK EAST LEG | 39716.7264 | 39717.3958 | CONT | [12 empty] | 0
_Z64558B039718.2916666667 | Z64558B0 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39718.2917 | 39718.5507 | REPDAILY | 00026089 | VEN_AUG | Out W/O BATS-HOTS Line OPGW install Runs 5 & 6 | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026927139719.26875 | 10269271 |  | Parent | TRUE | NO.3 66KV BUS AT RWTS | 39719.2688 | 39719.6354 | DAILY | 00007480 | SPIMAINT | O/Haul NO.3 66KV BUS AT RWTS | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1028654939719.26875 | 10286549 | 10269271 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 39719.2688 | 39719.6354 | DAILY | 00007450 | SPIMAINT | Rebate for Bus Outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z64558B039719.2951388889 | Z64558B0 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39719.2951 | 39719.5604 | REPDAILY | 00026089 | VEN_AUG | Out W/O BATS-HOTS Line OPGW install Runs 5 & 6 | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z73058D939720.2944444444 | Z73058D9 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT SMTS | 39720.2944 | 39804.5764 | CONT | 00001323 | DB_AUG | excavate for B2 trans slab | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1029647339720.4194444444 | 10296473 |  | Parent | FALSE | MSS -DDTS 1 330KV NW | 39720.4194 | 39720.6708 | DAILY | 00060190 | TRANSGRD | Transgrid Outage | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027337739721.3145833333 | 10273377 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE/A1 TRANS CB CT R/PH AT MLTS | 39721.3146 | 39721.384 | DAILY | [12 empty] | 0
_1027336139721.3881944444 | 10273361 |  | Parent | TRUE | EX - BATS NO.1 220KV LINE NO.1 BUS CB CT R/PH AT MLTS | 39721.3882 | 39721.4729 | DAILY | [12 empty] | 0
_1029630339721.3881944444 | 10296303 | 10273361 | Child | FALSE | 220KV SHUNT REACTOR AT MLTS | 39721.3882 | 39721.4729 | DAILY | 00003011 | SPIMAINT | Rebate W/O 220kV React for prox of its CB CT's | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029663739721.4395833333 | 10296637 |  | Parent | TRUE | NO.2A 66KV CAPACITOR BANK AT BETS | 39721.4396 | 39721.7132 | DAILY | 00350819 | SPIMAINT | Out W/O No2A Cap Bank to replace CB Sf6 aux rly | SPIPOWER |  |  | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1029663839721.4395833333 | 10296638 | 10296637 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 39721.4396 | 39721.7132 | DAILY | 00016274 | SPIMAINT | Rebate W/O No2B Cap Bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027335539721.5048611111 | 10273355 |  | Parent | TRUE | EX - BATS NO.2 220KV LINE CB CT R/PH AT MLTS | 39721.5049 | 39721.55 | DAILY | [12 empty] | 0
_1029630539721.5048611111 | 10296305 | 10273355 | Child | FALSE | BATS NO.2 220KV LINE AT MLTS | 39721.5049 | 39721.55 | DAILY | 00022969 | SPIMAINT | Rebate W/O Bats No2 Line during CB outage. | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z64558A839722.2923611111 | Z64558A8 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39722.2924 | 39723.9333 | CONT | 00026089 | VEN_AUG | Out W/O BATS-HOTS Line erect & cut in T333A | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z74258A139722.2951388889 | Z74258A1 |  | Parent | FALSE | WBE 66KV FDR CB AT ATS | 39722.2951 | 39723.7078 | DAILY | [12 empty] | 0
_1029666739722.3708333333 | 10296667 |  | Parent | FALSE | CBTS NO.4 500KV LINE NO.3 BUS CB AT HWTS | 39722.3708 | 39722.4618 | DAILY | [12 empty] | 0
_1029669839722.4645833333 | 10296698 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 39722.4646 | 39722.525 | DAILY | 00060938 | APDALCOA | Switching for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029671439722.9930555556 | 10296714 |  | Parent | FALSE | NO.8 GEN TRANS 220KV CB BUS SIDE ROI AT HWPS | 39722.9931 | 39728.825 | CONT | [12 empty] | 0
_X43258BA39723.2513888889 | X43258BA |  | Parent | FALSE | R3 220/66/22KV TRANS AT RCTS | 39723.2514 | 39723.7035 | DAILY | 00361128 | SPICAPX | Out W/O No3 Trans to install 220kV CVD's | SPIPOWER | X432 | X432 - (RCTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1028474139723.2951388889 | 10284741 |  | Parent | TRUE | NO.3 220KV CAPACITOR BANK CT R/PH AT TTS | 39723.2951 | 39723.5972 | DAILY | [12 empty] | 0
_1029763939723.2951388889 | 10297639 | 10284741 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT TTS | 39723.2951 | 39723.5972 | DAILY | 00327615 | SPIMAINT | w/o for rebates - NDD REQUEST CT SAMPLES | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028364739723.2965277778 | 10283647 | X7F858A2 | Child | FALSE | A1 TRANS/NO.2 CSC CB CSC SIDE ISOL AT ROTS | 39723.2965 | 39724.6389 | CONT | [12 empty] | 0
_1028705139723.2965277778 | 10287051 | X7F858A2 | Child | FALSE | NO.2 CSC AT ROTS | 39723.2965 | 39724.6389 | CONT | 00004716 | SPIMAINT | REBATE FOR CSC OUTAGE | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X7F858A239723.2965277778 | X7F858A2 |  | Parent | TRUE | NO.2 CSC 220/10.5KV TRANS AT ROTS | 39723.2965 | 39724.6389 | CONT | 00004759 | SPICAPX | Replace Surge Divertors | SPIPOWER | X7F8 | X7F8 - REPLACE AGEING 66KV - 330KV SURGE ARRESTERS | Connection Transformers | Eastern | 220 |  |  |  | 0
_1027335339723.3194444444 | 10273353 |  | Parent | FALSE | EX - A1 TRANS NO.1 BUS 220KV CB CT R/PH AT MLTS | 39723.3194 | 39723.4083 | DAILY | [12 empty] | 0
_1028474339724.2923611111 | 10284743 |  | Parent | TRUE | NO.3 66KV CAPACITOR BANK CB CT R/PH AT WMTS | 39724.2924 | 39724.4271 | DAILY | [12 empty] | 0
_1029646639724.2923611111 | 10296466 | 10284743 | Child | FALSE | NO.3 66KV CAPACITOR BANK AT WMTS | 39724.2924 | 39724.4271 | DAILY | 00003191 | SPIMAINT | out w/o for cap bank-ndd sample/scan b ph cap unit | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029663039724.2958333333 | 10296630 |  | Parent | FALSE | MSS -DDTS 2 330KV NW | 39724.2958 | 39724.5514 | DAILY | 00060191 | TRANSGRD | Transgrid Outage | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029671739724.4263888889 | 10296717 |  | Parent | FALSE | NO.8 22KV/415V S/S TRANS AT SMTS | 39724.4264 | 39724.5931 | DAILY | 00001327 | DB_AUG | VSCAP to DOC | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1029671239724.4263888889 | 10296712 |  | Parent | FALSE | NO.8 22KV/415V S/S TRANS AT SMTS | 39724.4264 | 39727.4049 | DAILY | 00001327 | DB_AUG | VSCAP to DOC | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X49758M539724.5090277778 | X49758M5 |  | Parent | FALSE | BATS 220KV LINE NO.1 BUS CB AT BETS | 39724.509 | 39724.5236 | DAILY | [12 empty] | 0
_X50858G039725.2506944445 | X50858G0 |  | Parent | TRUE | NO.4 66KV BUS AT GTS | 39725.2507 | 39725.616 | DAILY | 00002838 | SPICAPX | Out W/O No4 & 5 66kV Bus to connect temp FDN fdr | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858G139725.2506944445 | X50858G1 | X50858G0 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39725.2507 | 39725.616 | DAILY | 00329879 | SPICAPX | Rebate W/O No4 66 Cap bk during No4 66 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X50858G239725.2506944445 | X50858G2 | X50858G0 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39725.2507 | 39725.616 | DAILY | 00002830 | SPICAPX | Perf calc W/O No4 trans during No4 66 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X71558A639725.2993055556 | X71558A6 |  | Parent | TRUE | MLTS NO.1 500KV LINE CB AT HYTS | 39725.2993 | 39727.0917 | DAILY | [12 empty] | 0
_X71558A739725.2993055556 | X71558A7 | X71558A6 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39725.2993 | 39727.0917 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MLTS 1L 1B CB outage | SPIPOWER | X715 | X715 - (HYTS) REPLACEMENT OF RTU AND HMI | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z64558B139725.3 | Z64558B1 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39725.3 | 39725.584 | DAILY | 00026089 | VEN_AUG | Out W/O BATS-HOTS Line OPGW install Run 7 | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858G639725.5798611111 | X50858G6 |  | Parent | FALSE | EX - FDN 66KV FDR CB AT GTS | 39725.5799 | 39732.2951 | CONT | [12 empty] | 0
_1026910539726.2291666667 | 10269105 |  | Parent | TRUE | NO.3 220KV BUS AT HWPS | 39726.2292 | 39726.6431 | DAILY | 00009660 | SPIMAINT | O/Haul NO.3 220KV BUS AT HWPS | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1028649039726.2291666667 | 10286490 | 10269105 | Child | FALSE | EX - JLTS NO.3 LINE-AUX TRANS 'C' 220KV CB BUS SIDE ISOL AT HWPS | 39726.2292 | 39726.6431 | DAILY | [12 empty] | 0
_1029648139726.2291666667 | 10296481 | 10269105 | Child | FALSE | NO.6 GEN TRANS NO.3 BUS 220KV CB BUS SIDE ROI AT HWPS | 39726.2292 | 39726.6431 | DAILY | [12 empty] | 0
_1026939039726.2909722222 | 10269390 |  | Parent | FALSE | NO.4 220KV BUS AT HTS | 39726.291 | 39726.5583 | DAILY | 00004455 | SPIMAINT | O/Haul NO.4 220KV BUS AT HTS | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1029679639727.1743055556 | 10296796 |  | Parent | FALSE | MBTS-EPS 2 220KV N | 39727.1743 | 39727.7042 | CONT | 00055381 | FORCMAJ | EPS-MBTS No 2 220kv Line Gun shot repair | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_Z64558B239727.2770833333 | Z64558B2 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39727.2771 | 39727.7403 | REPDAILY | 00026089 | VEN_AUG | Out W/O BATS-HOTS Line OPGW install Runs 8 & 9 | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z73058C839727.2791666667 | Z73058C8 |  | Parent | FALSE | EX - TTS NO.2 220KV LINE AT SMTS | 39727.2792 | 39731.625 | CONT | 00013358 | DB_AUG | cutover of line into new 220kv switchyard | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7F858A039727.2916666667 | X7F858A0 |  | Parent | FALSE | B1 220/66KV TRANS AT HTS | 39727.2917 | 39728.6444 | CONT | 00004445 | SPICAPX | Replace Surge Divertors | SPIPOWER | X7F8 | X7F8 - REPLACE AGEING 66KV - 330KV SURGE ARRESTERS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029659339727.3152777778 | 10296593 |  | Parent | FALSE | MSS NO.1 330KV LINE AT DDTS | 39727.3153 | 39727.7109 | REPDAILY | 00012357 | SPIMAINT | Out W/O MSS No1 Line outage for Lines & Prim works | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z64558B239728.275 | Z64558B2 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39728.275 | 39728.7438 | REPDAILY | 00026089 | VEN_AUG | Out W/O BATS-HOTS Line OPGW install Runs 8 & 9 | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029649639728.2965277778 | 10296496 |  | Parent | TRUE | JLA NO.1 220KV LINE CB AT TBTS | 39728.2965 | 39728.6083 | DAILY | [12 empty] | 0
_1029650039728.2965277778 | 10296500 | 10296496 | Child | FALSE | JLA NO.1 220KV LINE AT TBTS | 39728.2965 | 39728.6083 | DAILY | 00018301 | SPIMAINT | rebate for Line outage during plant shut down | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027343939728.3111111111 | 10273439 |  | Parent | TRUE | EX - ROTS NO.7 220KV LINE NO.1 BUS CB CT R/PH AT YPS | 39728.3111 | 39728.3868 | DAILY | [12 empty] | 0
_1029707739728.3111111111 | 10297077 | 10273439 | Child | FALSE | ROTS NO.7 220KV LINE AT YPS | 39728.3111 | 39728.3868 | DAILY | 00016415 | SPIMAINT | LINE REBATE FOR CT OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029659339728.3166666667 | 10296593 |  | Parent | FALSE | MSS NO.1 330KV LINE AT DDTS | 39728.3167 | 39728.7208 | REPDAILY | 00012357 | SPIMAINT | Out W/O MSS No1 Line outage for Lines & Prim works | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358H539728.35625 | Z63358H5 |  | Parent | FALSE | HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 39728.3562 | 39728.6215 | DAILY | [12 empty] | 0
_1027344339728.3923611111 | 10273443 |  | Parent | TRUE | ROTS NO.8 220KV LINE NO.2 BUS CB CT R/PH AT YPS | 39728.3924 | 39728.5132 | DAILY | [12 empty] | 0
_1029707839728.3923611111 | 10297078 | 10273443 | Child | FALSE | ROTS NO.8 220KV LINE AT YPS | 39728.3924 | 39728.5132 | DAILY | 00016416 | SPIMAINT | LINE REBATE FOR CT OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029683939728.5458333333 | 10296839 |  | Parent | FALSE | NO.6 GEN TRANS NO.3 BUS 220KV CB AT HWPS | 39728.5458 | 39728.5833 | DAILY | [12 empty] | 0
_X7F858A139729.2944444444 | X7F858A1 |  | Parent | FALSE | B2 220/66KV TRANS AT HTS | 39729.2944 | 39730.6035 | CONT | 00004446 | SPICAPX | Replace Surge Divertors | SPIPOWER | X7F8 | X7F8 - REPLACE AGEING 66KV - 330KV SURGE ARRESTERS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026930339729.3006944444 | 10269303 |  | Parent | FALSE | WBTS 220KV LINE NO.2 BUS CB AT HOTS | 39729.3007 | 39730.6424 | CONT | [12 empty] | 0
_1028663039729.3340277778 | 10286630 |  | Parent | TRUE | HWTS NO.3 220KV LINE NO.3 BUS CB AT HWPS | 39729.334 | 39729.6299 | DAILY | 00009610 | SPIMAINT | SCAN HOT SPOT BPH BUS CONNECTION | SPIPOWER | [8 empty] | 0 | 10286630 |  | SCAN HOT SPOT BPH BUS CONNECTION | 00009610 | CB |  | HWPS | CB | SPIMAINT | DAILY
_1029614439729.3340277778 | 10296144 | 10286630 | Child | FALSE | HWTS NO.3 220KV LINE NO.3 BUS CB LINE SIDE ISOL AT HWPS | 39729.334 | 39729.6299 | DAILY | [12 empty] | 0
_X49758M639729.4430555556 | X49758M6 |  | Parent | FALSE | BATS 220KV LINE NO.2 BUS CB AT BETS | 39729.4431 | 39729.7799 | DAILY | [12 empty] | 0
_1029690039729.5833333333 | 10296900 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 39729.5833 | 39729.6035 | DAILY | [12 empty] | 0
_1029691039729.9888888889 | 10296910 |  | Parent | FALSE | NO.5 GEN TRANS 220KV CB BUS SIDE ROI AT HWPS | 39729.9889 | 39734.9792 | CONT | [12 empty] | 0
_1029660539730.2361111111 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39730.2361 | 39730.759 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z63358H439730.3243055556 | Z63358H4 |  | Parent | FALSE | MWTS NO.1 220KV LINE NO.1 BUS CB AT JLTS | 39730.3243 | 39730.525 | DAILY | [12 empty] | 0
_1028558739730.3333333333 | 10285587 |  | Parent | FALSE | SMTS NO.2 220KV LINE CB AT TTS | 39730.3333 | 39731.6667 | CONT | [12 empty] | 0
_1028372939730.3354166667 | 10283729 |  | Parent | TRUE | HWTS NO.1 220KV LINE CB LINE SIDE ISOL AT HWPS | 39730.3354 | 39730.5653 | DAILY | [12 empty] | 0
_1029652239730.3354166667 | 10296522 | 10283729 | Child | FALSE | HWTS NO.1 220KV LINE CB AT HWPS | 39730.3354 | 39730.5653 | DAILY | [12 empty] | 0
_1029708039730.3354166667 | 10297080 | 10283729 | Child | FALSE | A1 515/230KV TRANS AT HWTS | 39730.3354 | 39730.5653 | DAILY | 00009772 | SPIMAINT | REBATE FOR No1 MAIN TX @ HWTS | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029660539731.2465277778 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39731.2465 | 39731.7889 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X50858F239731.2520833333 | X50858F2 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 39731.2521 | 39732.2562 | CONT | 00002830 | SPICAPX | Out W/O No4 Transformer for rebuild works | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026781339731.3 | 10267813 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39731.3 | 39731.5542 | DAILY | 00019243 | SPIMAINT | 1 Yearly O/Haul - SVC at HOTS | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027345139731.3138888889 | 10273451 |  | Parent | FALSE | EX - W3 GEN TRANS NO.1 BUS 220KV CB CT R/PH AT YPS | 39731.3139 | 39731.3722 | DAILY | [12 empty] | 0
_Z63358H239731.3333333333 | Z63358H2 |  | Parent | FALSE | MWTS NO.2 220KV LINE NO.1 BUS CB AT JLTS | 39731.3333 | 39731.4799 | DAILY | [12 empty] | 0
_1009450239731.3541666667 | 10094502 |  | Parent | TRUE | EX - NO.2 66KV CAPACITOR BANK CB AT BATS | 39731.3542 | 39737.309 | DAILY | [12 empty] | 0
_1029648739731.3541666667 | 10296487 | 10094502 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39731.3542 | 39737.309 | DAILY | 00331118 | SPIMAINT | Rebate W/O No2 Cap Bank during CB O-H | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029694139731.4930555556 | 10296941 |  | Parent | FALSE | BSS 220KV LINE NO.1 BUS CB AT RCTS | 39731.4931 | 39731.6264 | DAILY | [12 empty] | 0
_1029692639731.6111111111 | 10296926 |  | Parent | FALSE | LYPS NO.2 LINE/ROTS NO.3 LINE 500KV CB AT HWTS | 39731.6111 | 39731.6146 | DAILY | [12 empty] | 0
_1029696639731.6840277778 | 10296966 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT SMTS | 39731.684 | 39731.6993 | CONT | [12 empty] | 0
_1029660539732.2395833333 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39732.2396 | 39732.7632 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1026910739732.2493055556 | 10269107 |  | Parent | TRUE | NO.6 220KV BUS AT HWPS | 39732.2493 | 39732.6431 | DAILY | 00009663 | SPIMAINT | O/Haul NO.6 220KV BUS AT HWPS | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1029620039732.2493055556 | 10296200 | 10269107 | Child | FALSE | YPS NO.2 220KV LINE NO.6 BUS CB AT HWPS | 39732.2493 | 39732.6431 | DAILY | [12 empty] | 0
_1029722039732.2493055556 | 10297220 | 10269107 | Child | FALSE | YPS NO.1 220KV LINE AT HWPS | 39732.2493 | 39732.6431 | DAILY | 00015795 | SPIMAINT | LINE REBATE FOR BUS OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858F339732.25625 | X50858F3 |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 39732.2562 | 39732.7924 | REPDAILY | 00002834 | SPICAPX | Out W/O No2 220kV Bus for rebuild works | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858F439732.25625 | X50858F4 | X50858F3 | Child | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39732.2562 | 39732.7924 | REPDAILY | 00017905 | SPICAPX | Rebate W/O PTH No1 Line during No2 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858F539732.25625 | X50858F5 | X50858F3 | Child | FALSE | EX - MLTS NO.1 220KV LINE AT GTS | 39732.2562 | 39732.7924 | REPDAILY | 00017903 | SPICAPX | Rebate W/O MLTS 1 Line during No2 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858F639732.25625 | X50858F6 | X50858F3 | Child | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39732.2562 | 39732.7924 | REPDAILY | 00017900 | SPICAPX | Rebate W/O KTS No1 Line during No2 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858F739732.25625 | X50858F7 | X50858F3 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39732.2562 | 39732.7924 | REPDAILY | 00002830 | SPICAPX | Perf calc W/O No4 Trans during No2 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858G339732.275 | X50858G3 |  | Parent | TRUE | NO.4 66KV BUS AT GTS | 39732.275 | 39732.8472 | DAILY | 00002838 | SPICAPX | Out W/O No4 & 5 66kV Bus to reconnect FDN fdr | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858G439732.275 | X50858G4 | X50858G3 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39732.275 | 39732.8472 | DAILY | 00329879 | SPICAPX | Rebate W/O No4 66 Cap bk during No4 66 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029697639732.4180555556 | 10296976 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 39732.4181 | 39732.5312 | DAILY | 00026099 | FAULT | F2 500kV CB's Tripped inadvertently by contractor | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X50858F839732.7923611111 | X50858F8 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 39732.7924 | 39733.25 | CONT | 00002830 | SPICAPX | Out W/O No4 Transformer unavailable O'night | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029697139732.7972222222 | 10296971 |  | Parent | FALSE | KTS -ATS 220KV WY | 39732.7972 | 39733.6639 | CONT | 00074402 | SPIMAINT | KTS Line CT replacement | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858F339733.25 | X50858F3 |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 39733.25 | 39733.6431 | REPDAILY | 00002834 | SPICAPX | Out W/O No2 220kV Bus for rebuild works | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858F439733.25 | X50858F4 | X50858F3 | Child | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39733.25 | 39733.6431 | REPDAILY | 00017905 | SPICAPX | Rebate W/O PTH No1 Line during No2 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858F539733.25 | X50858F5 | X50858F3 | Child | FALSE | EX - MLTS NO.1 220KV LINE AT GTS | 39733.25 | 39733.6431 | REPDAILY | 00017903 | SPICAPX | Rebate W/O MLTS 1 Line during No2 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858F639733.25 | X50858F6 | X50858F3 | Child | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39733.25 | 39733.6431 | REPDAILY | 00017900 | SPICAPX | Rebate W/O KTS No1 Line during No2 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858F939733.25 | X50858F9 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 39733.25 | 39734.8736 | CONT | 00002830 | SPICAPX | Out W/O No4 Transformer for rebuild works | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z81058A239733.2986111111 | Z81058A2 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 39733.2986 | 39733.6431 | DAILY | 00022690 | 3RDPARTY | Out W/O GTS-PTH No1 Line raise conductor height | SPIPOWER | Z810 | Z810 - COST EST - (GLN) TOWER HEIGHT ALTERATIONS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026202739733.3048611111 | 10262027 |  | Parent | TRUE | B2 TRANS 66KV CB ISOL AT RTS | 39733.3049 | 39733.4167 | DAILY | [12 empty] | 0
_1028662339733.3048611111 | 10286623 | 10262027 | Child | FALSE | B2 220/66KV TRANS AT RTS | 39733.3049 | 39733.4167 | DAILY | 00007331 | SPIMAINT | Trans Rebate for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028662539733.3048611111 | 10286625 | 10262027 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT RTS | 39733.3049 | 39733.4167 | DAILY | 00055373 | SPIMAINT | Cap Bank Rebate for Bus outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029697239733.3708333333 | 10296972 |  | Parent | FALSE | NO.3 220KV BUS AT ATS | 39733.3708 | 39733.4819 | DAILY | 00356843 | SPICAPX | Bus to be De-Energized daily to allow safe access | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z74258A239733.7277777778 | Z74258A2 |  | Parent | FALSE | WBE 66KV FDR CB AT ATS | 39733.7278 | 39733.7514 | DAILY | [12 empty] | 0
_1029660539734.2388888889 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39734.2389 | 39734.6639 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029660539735.2430555556 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39735.2431 | 39735.7958 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X32058AO39735.2798611111 | X32058AO |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39735.2799 | 39735.3917 | DAILY | 00363305 | SPIMAINT | Clean Bird Droppings | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029182639735.29375 | 10291826 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 39735.2937 | 39735.7833 | DAILY | 00001147 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029653539735.3097222222 | 10296535 |  | Parent | FALSE | HWTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 39735.3097 | 39735.4694 | DAILY | [12 empty] | 0
_1009443839735.3215277778 | 10094438 |  | Parent | TRUE | H1 TRANS NO.1 BUS 330KV CB TRANS SIDE ROI AT DDTS | 39735.3215 | 39735.7236 | REPDAILY | [12 empty] | 0
_1029659439735.3215277778 | 10296594 | 10094438 | Child | FALSE | H1 TRANS NO.1 BUS 330KV CB TRANS SIDE ROI AT DDTS | 39735.3215 | 39735.7236 | REPDAILY | [12 empty] | 0
_1028662939735.4694444445 | 10286629 |  | Parent | FALSE | HWTS NO.2 220KV LINE NO.2 BUS CB AT HWPS | 39735.4694 | 39735.6062 | DAILY | [12 empty] | 0
_1029660539736.2326388889 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39736.2326 | 39736.7625 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029648539736.2944444444 | 10296485 |  | Parent | FALSE | B4 220/66KV TRANS AT RTS | 39736.2944 | 39736.6375 | DAILY | 00007332 | SPIMAINT | INSTALL NEW COOLING FAN | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029182939736.2972222222 | 10291829 |  | Parent | FALSE | B2 220/66KV TRANS AT KTS | 39736.2972 | 39736.6458 | DAILY | 00001148 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009443839736.3 | 10094438 |  | Parent | TRUE | H1 TRANS NO.1 BUS 330KV CB TRANS SIDE ROI AT DDTS | 39736.3 | 39736.6556 | REPDAILY | [12 empty] | 0
_1029659439736.3 | 10296594 | 10094438 | Child | FALSE | H1 TRANS NO.1 BUS 330KV CB TRANS SIDE ROI AT DDTS | 39736.3 | 39736.6556 | REPDAILY | [12 empty] | 0
_1029667739736.3125 | 10296677 |  | Parent | TRUE | MWTS-LY 1 66KV G | 39736.3125 | 39736.6465 | REPDAILY | 00020535 | SPIMAINT | TRAINING - ACCESS & EARTHING | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029669439736.3125 | 10296694 | 10296677 | Child | FALSE | MWTS-LY 2 66KV G | 39736.3125 | 39736.6465 | REPDAILY | 00020536 | SPIMAINT | TRAINING - ACCESS & EARTHING | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009277139736.3125 | 10092771 |  | Parent | FALSE | HWTS NO.2 220KV LINE AT HWPS | 39736.3125 | 39736.6611 | DAILY | 00015766 | SPIMAINT | O/Haul - HWTS No.2 LINE at HWPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027345739736.3125 | 10273457 |  | Parent | TRUE | EX - NO.2 MAIN TRANS 500KV CB CT R/PH AT HWTS | 39736.3125 | 39736.6611 | DAILY | [12 empty] | 0
_1028373539736.3125 | 10283735 | 10273457 | Child | FALSE | EX - NO.2 MAIN TRANS 500KV CB AT HWTS | 39736.3125 | 39736.6611 | DAILY | [12 empty] | 0
_1029614339736.3125 | 10296143 | 10273457 | Child | FALSE | NO.2 MAIN TRANS 220KV ISOL AT HWTS | 39736.3125 | 39736.6611 | DAILY | [12 empty] | 0
_1029721639736.4013888889 | 10297216 |  | Parent | FALSE | MWTS NO.2 66KV FDR NO.1 BUS CB AT LY | 39736.4014 | 39738.3924 | CONT | [12 empty] | 0
_1029684139736.4090277778 | 10296841 |  | Parent | FALSE | BATS 220KV LINE NO.2 BUS CB AT TGTS | 39736.409 | 39736.4583 | DAILY | [12 empty] | 0
_1029684239736.5048611111 | 10296842 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT TGTS | 39736.5049 | 39736.55 | DAILY | [12 empty] | 0
_1029720439736.6458333333 | 10297204 |  | Parent | FALSE | HWTS NO.2 220KV LINE NO.2 BUS CB AT HWPS | 39736.6458 | 39767.2639 | CONT | [12 empty] | 0
_1029660539737.2291666667 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39737.2292 | 39737.8 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1009443139737.2944444444 | 10094431 | 10094443 | Child | FALSE | MSS NO.2 330KV LINE/SMTS NO.2 LINE CB SMTS NO.2 LINE SIDE E/SW AT DDTS | 39737.2944 | 39737.6736 | DAILY | [12 empty] | 0
_1009444339737.2944444444 | 10094443 |  | Parent | TRUE | MSS NO.2 330KV LINE/SMTS NO.2 LINE CB SMTS NO.2 LINE SIDE ROI AT DDTS | 39737.2944 | 39737.6736 | DAILY | [12 empty] | 0
_1029688739737.2944444444 | 10296887 | 10094443 | Child | FALSE | SMTS NO.2 330KV LINE AT DDTS | 39737.2944 | 39737.6736 | DAILY | 00012356 | SPIMAINT | Rebate W/O DDTS-SMTS No2 Line during ROI & Esw OH | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029773539737.2944444444 | 10297735 | 10094443 | Child | FALSE | DDTS NO.2 330KV LINE SERIES CAPACITOR BANK AT SMTS | 39737.2944 | 39737.6736 | DAILY | 00327837 | SPIMAINT | Rebate W/O DDTS-SMTS No2 Line during ROI & Esw OH | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1028790139737.2958333333 | 10287901 | 10287904 | Child | FALSE | NO.1 220KV CAPACITOR BANK CB AT KTS | 39737.2958 | 39737.6514 | DAILY | [12 empty] | 0
_1028790439737.2958333333 | 10287904 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK AT KTS | 39737.2958 | 39737.6514 | DAILY | 00119824 | SPIMAINT | O/Haul NO.1 220KV CAPACITOR BANK AT KTS | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029576339737.2958333333 | 10295763 | 10287904 | Child | FALSE | NO.1 220KV CAPACITOR BANK E/SW AT KTS | 39737.2958 | 39737.6514 | DAILY | [12 empty] | 0
_1029216939737.3006944444 | 10292169 | 10292175 | Child | FALSE | NO.3 220KV CAPACITOR BANK E/SW AT TTS | 39737.3007 | 39737.7035 | DAILY | [12 empty] | 0
_1029217539737.3006944444 | 10292175 |  | Parent | TRUE | NO.3 220KV CAPACITOR BANK AT TTS | 39737.3007 | 39737.7035 | DAILY | 00327615 | SPIMAINT | O/Haul NO.3 220KV CAPACITOR BANK AT TTS | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029293639737.3006944444 | 10292936 | 10292175 | Child | FALSE | NO.3 220KV CAPACITOR BANK CB AT TTS | 39737.3007 | 39737.7035 | DAILY | [12 empty] | 0
_1029701639737.3159722222 | 10297016 |  | Parent | TRUE | EX - NO.2 66KV CAPACITOR BANK CB AT BATS | 39737.316 | 39741.8667 | CONT | [12 empty] | 0
_1029710839737.3159722222 | 10297108 | 10297016 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39737.316 | 39741.8667 | CONT | 00331118 | FORCED | Rebate W/O No2 66kV Cap during CB replace | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029721739737.5416666667 | 10297217 |  | Parent | TRUE | 5-6 220KV BUS TIE CB NO.5 BUS SIDE ISOL AT HWPS | 39737.5417 | 39737.5951 | DAILY | [12 empty] | 0
_1029721839737.5416666667 | 10297218 | 10297217 | Child | FALSE | ROTS NO.1 220KV LINE AT HWPS | 39737.5417 | 39737.5951 | DAILY | 00015790 | SPIMAINT | line rebate for bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029723239737.5416666667 | 10297232 |  | Parent | FALSE | 5-6 220KV BUS TIE CB NO.5 BUS SIDE ISOL AT HWPS | 39737.5417 | 39737.5951 | CONT | [12 empty] | 0
_1029719639737.6125 | 10297196 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39737.6125 | 39737.6361 | DAILY | [12 empty] | 0
_1029660539738.2305555556 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39738.2306 | 39738.7596 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1003842839738.2916666667 | 10038428 | 10263517 | Child | FALSE | S005 LYPS-HWTS 3 500KV | 39738.2917 | 39738.5625 | DAILY | [12 empty] | 0
_1003842939738.2916666667 | 10038429 | 10263517 | Child | FALSE | S005 LYPS-HWTS 3 500KV | 39738.2917 | 39738.5625 | DAILY | [12 empty] | 0
_1003880539738.2916666667 | 10038805 | 10263517 | Child | FALSE | S022 LYPS-HWTS 3 500KV | 39738.2917 | 39738.5625 | DAILY | [12 empty] | 0
_1007386139738.2916666667 | 10073861 | 10263517 | Child | FALSE | S001 LYPS-HWTS 3 500KV | 39738.2917 | 39738.5625 | DAILY | [12 empty] | 0
_1010551739738.2916666667 | 10105517 | 10263517 | Child | FALSE | S010 LYPS-HWTS 3 500KV | 39738.2917 | 39738.5625 | DAILY | [12 empty] | 0
_1026351739738.2916666667 | 10263517 |  | Parent | TRUE | S001 LYPS-HWTS 3 500KV | 39738.2917 | 39738.6042 | DAILY | [12 empty] | 0
_1028249239738.2916666667 | 10282492 |  | Parent | FALSE | HWTS NO.3 500KV LINE CB AT LYPS | 39738.2917 | 39738.6042 | DAILY | [12 empty] | 0
_1026627239738.3034722222 | 10266272 |  | Parent | FALSE | NO.3 220KV BUS AT ATS | 39738.3035 | 39738.7722 | DAILY | 00356843 | SPIMAINT | OVERHAUL OF A 220KV LINE & No 3 220kv Bus | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029722639738.3243055556 | 10297226 |  | Parent | TRUE | MWTS NO.2 66KV FDR NO.1 BUS CB FDR SIDE ISOL AT LY | 39738.3243 | 39738.3924 | DAILY | [12 empty] | 0
_1029762939738.3243055556 | 10297629 | 10297226 | Child | FALSE | MWTS NO.2 66KV FDR AT LY | 39738.3243 | 39738.3924 | DAILY | 00015995 | SPIMAINT | Rebate to FIX ISOLATOR | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358H339738.3583333333 | Z63358H3 |  | Parent | FALSE | HWPS NO.3 LINE/MWTS NO.2 LINE 220KV CB AT JLTS | 39738.3583 | 39738.4882 | DAILY | [12 empty] | 0
_1029682339738.5625 | 10296823 |  | Parent | FALSE | CONTROL GENERAL AT HWPS | 39738.5625 | 39743.4792 | CONT | [12 empty] | 0
_1029726939738.5625 | 10297269 |  | Parent | FALSE | NO.6 GEN TRANS NO.3 BUS 220KV CB BUS SIDE ROI AT HWPS | 39738.5625 | 39743.4792 | CONT | [12 empty] | 0
_1029660539739.2319444444 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39739.2319 | 39739.6847 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X71558B139739.2916666667 | X71558B1 | X71558B0 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39739.2917 | 39740.7181 | CONT | 00002863 | SPICAPX | Rebate W/O M1 Trans during SESS 1-M1 TR CB outage | SPIPOWER | X715 | X715 - (HYTS) REPLACEMENT OF RTU AND HMI | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X71558B039739.2916666667 | X71558B0 |  | Parent | TRUE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 39739.2917 | 39740.7597 | CONT | [12 empty] | 0
_X67058C339739.2979166667 | X67058C3 |  | Parent | FALSE | KTS 220KV LINE AT ATS | 39739.2979 | 39739.6944 | REPDAILY | 00055535 | SPICAPX | replace line side ct's & o/h line side isols & esw | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X67058C639739.33125 | X67058C6 |  | Parent | FALSE | NO.3 220KV BUS AT ATS | 39739.3313 | 39739.4521 | REPDAILY | 00356843 | SPICAPX | Bus to be De-Energized daily to allow safe access | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z73058E239739.5368055556 | Z73058E2 |  | Parent | FALSE | EX - TTS NO.2 220KV LINE AT SMTS | 39739.5368 | 39740.6375 | CONT | 00013358 | DB_AUG | Commissioning of 220kv Switch Yard at SMTS | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029727539739.75 | 10297275 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS SD R/PH AT SMTS | 39739.75 | 39741.7083 | CONT | [12 empty] | 0
_X50858H739740.2291666667 | X50858H7 | X50858H5 | Child | FALSE | EX - MLTS NO.2 220KV LINE AT GTS | 39740.2292 | 39740.7875 | DAILY | 00017904 | SPICAPX | Rebate W/O MLTS 2 Line during No1 220kV Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858H539740.2291666667 | X50858H5 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39740.2292 | 39740.7882 | DAILY | 00002833 | SPICAPX | No1 220kV Bus & MLTS No2 L for GTS rebuild works | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858H639740.2291666667 | X50858H6 | X50858H5 | Child | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39740.2292 | 39740.7882 | DAILY | 00017901 | SPICAPX | Rebate W/O KTS 2 Line during No1 220kV Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858H839740.2291666667 | X50858H8 | X50858H5 | Child | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39740.2292 | 39740.7882 | DAILY | 00017906 | SPICAPX | Rebate W/O PTH 2 Line during No1 220kV Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858H939740.2291666667 | X50858H9 | X50858H5 | Child | FALSE | B3 220/66KV TRANS AT GTS | 39740.2292 | 39740.7882 | DAILY | 00002829 | SPICAPX | Rebate W/O No3 TR during No1 220kV Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029660539740.2305555556 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39740.2306 | 39740.8611 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X67058C339740.2923611111 | X67058C3 |  | Parent | FALSE | KTS 220KV LINE AT ATS | 39740.2924 | 39740.6611 | REPDAILY | 00055535 | SPICAPX | replace line side ct's & o/h line side isols & esw | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z81058A339740.3055555556 | Z81058A3 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39740.3056 | 39740.7882 | DAILY | 00022691 | 3RDPARTY | Out W/O GTS-PTH No2 Line raise conductor height | SPIPOWER | Z810 | Z810 - COST EST - (GLN) TOWER HEIGHT ALTERATIONS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1010344539740.31875 | 10103445 |  | Parent | FALSE | B STH 22KV BUS AT RTS | 39740.3187 | 39740.5965 | DAILY | 00007357 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 22 |  |  |  | 0
_1029727739740.7083333333 | 10297277 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE CB AIR RECEIVER R/PH AT GTS | 39740.7083 | 39760.1979 | CONT | [12 empty] | 0
_X50858I939740.7118055556 | X50858I9 |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 39740.7118 | 39903.6667 | CONT | [12 empty] | 0
_X50858I939740.7534722222 | X50858I9 |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 39740.7535 | 39903.625 | CONT | [12 empty] | 0
_X50858I039740.7875 | X50858I0 |  | Parent | FALSE | EX - MLTS NO.2 220KV LINE AT GTS | 39740.7875 | 39760.1979 | CONT | 00017904 | SPICAPX | MLTS 2 Line for GTS rebuild works | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029660539741.2319444444 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39741.2319 | 39741.791 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X56558F139741.2916666667 | X56558F1 |  | Parent | FALSE | GTS NO.2 LINE/A1 TRANS 220KV CB AT MLTS | 39741.2917 | 39743.3535 | CONT | [12 empty] | 0
_1029721239741.3333333333 | 10297212 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB CT R/PH AT LY | 39741.3333 | 39741.5847 | DAILY | [12 empty] | 0
_1029721339741.3333333333 | 10297213 | 10297212 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT LY | 39741.3333 | 39741.5847 | DAILY | 00009893 | SPIMAINT | scan hotspot CAP BANK | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1003842639741.3451388889 | 10038426 |  | Parent | TRUE | S005 LYPS-HWTS 2 500KV | 39741.3451 | 39741.6146 | DAILY | [12 empty] | 0
_1003880439741.3451388889 | 10038804 | 10038426 | Child | FALSE | S022 LYPS-HWTS 2 500KV | 39741.3451 | 39741.6146 | DAILY | [12 empty] | 0
_1003881339741.3451388889 | 10038813 | 10038426 | Child | FALSE | S037 LYPS-HWTS 2 500KV | 39741.3451 | 39741.6146 | DAILY | [12 empty] | 0
_1003881539741.3451388889 | 10038815 | 10038426 | Child | FALSE | S039 LYPS-HWTS 2 500KV | 39741.3451 | 39741.6146 | DAILY | [12 empty] | 0
_1028249039741.3451388889 | 10282490 |  | Parent | FALSE | HWTS NO.2 500KV LINE CB AT LYPS | 39741.3451 | 39741.6146 | DAILY | [12 empty] | 0
_1029728039741.3597222222 | 10297280 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 39741.3597 | 39742.6882 | CONT | 00022691 | APDALCOA | Outage request from Pt Henry | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029619939741.4263888889 | 10296199 |  | Parent | FALSE | WOTS 330KV LINE NO.2 BUS CB BUS SIDE ROI AT DDTS | 39741.4264 | 39741.5049 | DAILY | [12 empty] | 0
_1029729439741.54375 | 10297294 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 39741.5437 | 39741.6069 | CONT | 00001147 | FORCED | Repair OLTC | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z73058E139741.5659722222 | Z73058E1 |  | Parent | FALSE | EX - TTS NO.2 220KV LINE/H2 TRANS ROI AT SMTS | 39741.566 | 39748.2917 | CONT | [12 empty] | 0
_1029712139741.8111111111 | 10297121 |  | Parent | FALSE | NO.2 66KV BUS AT BATS | 39741.8111 | 39741.8264 | DAILY | 00006561 | SPIMAINT | Out W/O No2 66 Bus de-energ for new Cap CB commiss | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029660539742.2354166667 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39742.2354 | 39742.7722 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X71558B339742.2708333333 | X71558B3 | X71558B2 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 39742.2708 | 39743.6549 | CONT | 00002862 | SPICAPX | Rebate W/O M2 Trans during SESS 2-M2 TR CB outage | SPIPOWER | X715 | X715 - (HYTS) REPLACEMENT OF RTU AND HMI | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X71558B239742.2708333333 | X71558B2 |  | Parent | TRUE | SESS NO.2 275KV LINE/M2 TRANS CB AT HYTS | 39742.2708 | 39743.6965 | CONT | [12 empty] | 0
_1027027339742.2895833333 | 10270273 |  | Parent | FALSE | SYN/COND AT BLTS | 39742.2896 | 39745.7104 | CONT | 00002547 | SPIMAINT | Annual O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029649739742.2972222222 | 10296497 |  | Parent | TRUE | JLA NO.1 220KV LINE CB AT TBTS | 39742.2972 | 39742.6278 | DAILY | [12 empty] | 0
_1029650139742.2972222222 | 10296501 | 10296497 | Child | FALSE | JLA NO.1 220KV LINE AT TBTS | 39742.2972 | 39742.6278 | DAILY | 00018301 | SPIMAINT | rebate for Line outage during plant shut down | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029614539742.3152777778 | 10296145 |  | Parent | TRUE | HWTS NO.4 220KV LINE NO.4 BUS CB LINE SIDE ISOL AT HWPS | 39742.3153 | 39742.6472 | DAILY | [12 empty] | 0
_1029614639742.3152777778 | 10296146 |  | Parent | FALSE | NO.4 MAIN TRANS 220KV ISOL AT HWTS | 39742.3153 | 39742.6472 | DAILY | 00009699 | SPIMAINT | SCAN HOT SPOT R&WPH FIXED & JAW | SPIPOWER | [8 empty] | 0 | 10296146 |  | SCAN HOT SPOT R&WPH FIXED & JAW | 00009699 | SWITCH |  | HWTS | ISOL | SPIMAINT | DAILY
_1029647039742.3152777778 | 10296470 | 10296145 | Child | FALSE | SMTS NO.2 LINE/A4 TRANS 500KV CB TRANS SIDE ROI AT HWTS | 39742.3153 | 39742.6472 | DAILY | [12 empty] | 0
_1029759339742.3152777778 | 10297593 | 10296145 | Child | FALSE | A4 515/230KV TRANS BANK AT HWTS | 39742.3153 | 39742.6472 | DAILY | 00337582 | SPIMAINT | TX REBATE | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029660539743.2305555556 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39743.2306 | 39743.6937 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X56558F239743.2708333333 | X56558F2 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT MLTS | 39743.2708 | 39745.6625 | CONT | 00337580 | SPICAPX | Out W/O A1 Trans to connect & commis new CB CTs | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029657839743.2895833333 | 10296578 |  | Parent | FALSE | ROTS NO.1 220KV LINE CB AT HWPS | 39743.2896 | 39743.684 | DAILY | [12 empty] | 0
_X7F858A339743.29375 | X7F858A3 |  | Parent | FALSE | B3 220/66KV TRANS AT SVTS | 39743.2937 | 39744.5944 | CONT | 00004851 | SPICAPX | Replace Surge Divertors | SPIPOWER | X7F8 | X7F8 - REPLACE AGEING 66KV - 330KV SURGE ARRESTERS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z63358H639743.3027777778 | Z63358H6 |  | Parent | TRUE | B2 220/66KV TRANS 220KV LINE ROI AT MWTS | 39743.3028 | 39743.6632 | REPDAILY | [12 empty] | 0
_Z63368H739743.3027777778 | Z63368H7 | Z63358H6 | Child | FALSE | JLTS NO.2 220KV LINE AT MWTS | 39743.3028 | 39743.6632 | CONT | 00016131 | VEN_AUG | LINE REBATE FOR TX OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028637639743.3083333333 | 10286376 |  | Parent | FALSE | B1 TRANS NO.2 BUS 220KV CB AT RWTS | 39743.3083 | 39743.6236 | DAILY | [12 empty] | 0
_1029725539743.3479166667 | 10297255 | 10297254 | Child | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 39743.3479 | 39743.5528 | DAILY | 00329970 | SPIMAINT | Perf calc W/O No1 Trans grp during 220 CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029725439743.3479166667 | 10297254 |  | Parent | TRUE | B1 TRANS GROUP 220KV CB AT GNTS | 39743.3479 | 39743.5944 | DAILY | [12 empty] | 0
_1029660539744.2361111111 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39744.2361 | 39744.7528 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z63368H739744.2909722222 | Z63368H7 | Z63358H6 | Child | FALSE | JLTS NO.2 220KV LINE AT MWTS | 39744.291 | 39744.6076 | CONT | 00016131 | VEN_AUG | LINE REBATE FOR TX OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358H639744.2909722222 | Z63358H6 |  | Parent | TRUE | B2 220/66KV TRANS 220KV LINE ROI AT MWTS | 39744.291 | 39744.6493 | REPDAILY | [12 empty] | 0
_1029646339744.3069444444 | 10296463 |  | Parent | TRUE | EX - NO.1 MAIN TRANS 500KV CB AT HWTS | 39744.3069 | 39746.4701 | CONT | [12 empty] | 0
_1029734139744.3069444444 | 10297341 | 10296463 | Child | FALSE | A1 515/230KV TRANS AT HWTS | 39744.3069 | 39746.4701 | CONT | 00009772 | SPIMAINT | TX REBATE FOR CB OUTAGE | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_V78258A039744.3729166667 | V78258A0 |  | Parent | FALSE | FBTS 220KV LINE REACTOR CB AT BLTS | 39744.3729 | 39744.4354 | DAILY | [12 empty] | 0
_V78258A139744.3729166667 | V78258A1 |  | Parent | FALSE | NPSD 220KV LINE REACTOR CB AT BLTS | 39744.3729 | 39744.4354 | DAILY | [12 empty] | 0
_1029743239744.4895833333 | 10297432 |  | Parent | FALSE | F2 TRANS 330KV CB AT SMTS | 39744.4896 | 39744.491 | DAILY | [12 empty] | 0
_1029660539745.2347222222 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39745.2347 | 39745.7229 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X32058AS39745.2826388889 | X32058AS |  | Parent | FALSE | U1 66/22KV TRANS AT MTS | 39745.2826 | 39745.3125 | DAILY | 00363343 | SPIMAINT | Install weather shields | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029724339745.3055555556 | 10297243 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT RTS | 39745.3056 | 39745.5139 | DAILY | 00007279 | SPIMAINT | Rebalance cap bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z63358H839745.3506944444 | Z63358H8 |  | Parent | TRUE | B2 220/66KV TRANS 220KV LINE ROI AT MWTS | 39745.3507 | 39745.5125 | DAILY | [12 empty] | 0
_Z63358H939745.3506944444 | Z63358H9 | Z63358H8 | Child | FALSE | JLTS NO.2 220KV LINE AT MWTS | 39745.3507 | 39745.5125 | DAILY | 00016131 | VEN_AUG | LINE REBATE FOR TESTING ROI & E/SWS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V78258A239745.4201388889 | V78258A2 |  | Parent | FALSE | B4 TRANS 220KV CB AT WMTS | 39745.4201 | 39745.4319 | DAILY | [12 empty] | 0
_X50858J039746.2305555556 | X50858J0 |  | Parent | TRUE | NO.2 66KV BUS AT GTS | 39746.2306 | 39746.5611 | DAILY | 00002836 | SPICAPX | Out W/O No2, 5 & 6 66 Bus to connect temp CRO fdr | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858J139746.2305555556 | X50858J1 | X50858J0 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT GTS | 39746.2306 | 39746.5611 | DAILY | 00350421 | SPICAPX | Rebate W/O No1 66 Cap bk during No2 66 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029660539746.2361111111 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39746.2361 | 39746.6354 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029727839746.3006944444 | 10297278 | X74158A0 | Child | FALSE | B3 220/66KV TRANS AT SVTS | 39746.3007 | 39746.7785 | CONT | 00004851 | SPICAPX | Rebate for Bus outage | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X74158A039746.3006944444 | X74158A0 |  | Parent | TRUE | 1-3 220KV BUS TIE CB AT SVTS | 39746.3007 | 39746.7785 | CONT | [12 empty] | 0
_1029739339746.3104166667 | 10297393 |  | Parent | FALSE | NO.1 220KV TRANS BUS CB AT WMTS | 39746.3104 | 39746.3715 | DAILY | [12 empty] | 0
_1027015039746.325 | 10270150 |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 39746.325 | 39746.7218 | REPDAILY | 00002828 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858J639746.5604166667 | X50858J6 |  | Parent | FALSE | EX - CRO 66KV FDR CB AT GTS | 39746.5604 | 39761.1736 | CONT | [12 empty] | 0
_1027015039747.2506944445 | 10270150 |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 39747.2507 | 39747.6014 | REPDAILY | 00002828 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029688439747.2722222222 | 10296884 |  | Parent | FALSE | MSS -DDTS 1 330KV NW | 39747.2722 | 39747.5882 | DAILY | 00060190 | SPIMAINT | Out W/O for repair of hot joints MSS-DDTS No1 Line | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z73058E339748.2090277778 | Z73058E3 |  | Parent | TRUE | EPS-TTS 220KV LINE AT SMTS | 39748.209 | 39748.7389 | DAILY | 00015363 | DB_AUG | modify top plates on eps-tts poles | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028536539748.2513888889 | 10285365 | Z73058E3 | Child | FALSE | H1 330/220KV TRANS BANK AT SMTS | 39748.2514 | 39759.5382 | CONT | 00026101 | SPIMAINT | O/Haul H1 TRANS BANK at smts & assoc gear at tts | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z73058E439748.2513888889 | Z73058E4 |  | Parent | FALSE | EX - TTS NO.1 220KV LINE AT SMTS | 39748.2514 | 39759.5382 | CONT | 00013357 | DB_AUG | w/o for rebates - cutover of smts-tts 1 line | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029660539749.1875 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39749.1875 | 39749.6875 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X56558F739749.2513888889 | X56558F7 | X56558F6 | Child | FALSE | BATS NO.2 220KV LINE AT MLTS | 39749.2514 | 39751.234 | CONT | 00022969 | SPICAPX | Rebate W/O BATS 2 Line for CB CT replacement | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558F639749.2513888889 | X56558F6 |  | Parent | TRUE | BATS NO.2 220KV LINE CB AT MLTS | 39749.2514 | 39751.2465 | CONT | [12 empty] | 0
_1029733139749.2583333333 | 10297331 |  | Parent | FALSE | B1 220/66KV TRANS AT SVTS | 39749.2583 | 39749.6174 | DAILY | 00004849 | SPIMAINT | MODIFY TRANS SD EARTHING | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029672639749.50625 | 10296726 |  | Parent | FALSE | BATS 220KV LINE NO.2 BUS CB AT TGTS | 39749.5062 | 39749.5382 | DAILY | [12 empty] | 0
_1029672439749.5527777778 | 10296724 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT TGTS | 39749.5528 | 39749.5771 | DAILY | [12 empty] | 0
_1029660539750.1902777778 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39750.1903 | 39750.6278 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z63358I039750.275 | Z63358I0 |  | Parent | TRUE | B1 220/66KV TRANS 220KV LINE ROI AT MWTS | 39750.275 | 39750.6132 | REPDAILY | [12 empty] | 0
_Z63358I139750.275 | Z63358I1 | Z63358I0 | Child | FALSE | JLTS NO.1 220KV LINE AT MWTS | 39750.275 | 39750.6132 | CONT | 00016130 | VEN_AUG | LINE REBATE FOR TX OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029747839750.28125 | 10297478 |  | Parent | FALSE | FBTS 220KV LINE CB AT NPSD | 39750.2812 | 39750.5542 | DAILY | [12 empty] | 0
_1029759439750.4131944444 | 10297594 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.2 BUS CB AT LYPS | 39750.4132 | 39750.4444 | DAILY | [12 empty] | 0
_1029671639750.4180555556 | 10296716 |  | Parent | FALSE | BATS 220KV LINE NO.2 BUS CB AT TGTS | 39750.4181 | 39750.6014 | REPDAILY | [12 empty] | 0
_1029671839750.6090277778 | 10296718 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT TGTS | 39750.609 | 39750.6431 | DAILY | [12 empty] | 0
_1029660539751.1902777778 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39751.1903 | 39751.6007 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X56558F839751.2340277778 | X56558F8 |  | Parent | FALSE | BATS NO.2 220KV LINE AT MLTS | 39751.234 | 39751.5764 | DAILY | 00022969 | SPICAPX | Out W/O BATS 2 Line for CT connection to LS Isol | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028561639751.2729166667 | 10285616 |  | Parent | TRUE | EX - ROTS NO.2 220KV LINE NO.1 BUS CB LINE SIDE E/SW AT HWPS | 39751.2729 | 39751.5854 | DAILY | [12 empty] | 0
_1029724139751.2729166667 | 10297241 | 10285616 | Child | FALSE | HWPS-ROTS 2 220KV G | 39751.2729 | 39751.5854 | CONT | 00020455 | SPICAPX | CHANGE GLASS TO POLYMERIC INSULATORS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358I039751.2756944445 | Z63358I0 |  | Parent | TRUE | B1 220/66KV TRANS 220KV LINE ROI AT MWTS | 39751.2757 | 39751.5826 | REPDAILY | [12 empty] | 0
_Z63358I139751.2756944445 | Z63358I1 | Z63358I0 | Child | FALSE | JLTS NO.1 220KV LINE AT MWTS | 39751.2757 | 39751.5826 | CONT | 00016130 | VEN_AUG | LINE REBATE FOR TX OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027417739751.2930555556 | 10274177 |  | Parent | FALSE | B1 220/66KV TRANS AT TGTS | 39751.2931 | 39751.7104 | DAILY | 00363297 | SPIMAINT | O/HAUL Transformer Div Mechanism (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029761239751.3569444444 | 10297612 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 39751.3569 | 39751.4521 | DAILY | 00060938 | APDALCOA | Switching for APD to top up SF6 CB at APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029671639751.4305555556 | 10296716 |  | Parent | FALSE | BATS 220KV LINE NO.2 BUS CB AT TGTS | 39751.4306 | 39751.6194 | REPDAILY | [12 empty] | 0
_1029764739751.7229166667 | 10297647 |  | Parent | FALSE | HOTS-RCTS 220KV | 39751.7229 | 39752.3792 | CONT | 00328509 | BUSHFIRE | HOTS-RCTS 220kV Line Hattah Busfire Outage | SPIPOWER |  |  | Circuits | 3rd Party | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM Event
_1029764839751.8916666667 | 10297648 |  | Parent | FALSE | EPS 220KV LINE AT TTS | 39751.8917 | 39751.8972 | CONT | 00015730 | FAULT | TTS-EPS 220kV Line | SPIPOWER |  |  | Circuits | 3rd Party | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1025319839752.2743055556 | 10253198 |  | Parent | FALSE | NO.2 330KV CAPACITOR BANK AT WOTS | 39752.2743 | 39752.7715 | DAILY | 00354001 | TRANSGRD | Out W/O WOTS #2 330 Cap bank & CB OH for T'grid | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_1029764639752.2868055556 | 10297646 |  | Parent | FALSE | NO.4 GEN TRANS 500KV LINE E/SW AT LYPS | 39752.2868 | 39755.2931 | CONT | [12 empty] | 0
_1027292939752.3048611111 | 10272929 |  | Parent | FALSE | NO.6 GEN TRANS NO.3 BUS 220KV CB AT HWPS | 39752.3049 | 39754.6208 | DAILY | [12 empty] | 0
_Z63358I239752.3125 | Z63358I2 |  | Parent | TRUE | B1 220/66KV TRANS 220KV LINE ROI AT MWTS | 39752.3125 | 39752.4944 | DAILY | [12 empty] | 0
_Z63358I339752.3125 | Z63358I3 | Z63358I2 | Child | FALSE | JLTS NO.1 220KV LINE AT MWTS | 39752.3125 | 39752.4944 | DAILY | 00016130 | VEN_AUG | LINE REBATE FOR TX OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029660539753.1881944445 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39753.1882 | 39753.791 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029751539753.2479166667 | 10297515 |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 39753.2479 | 39753.4389 | DAILY | 00002828 | SPIMAINT | Replace No1 Tr 66kv neutral isolator | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029660539755.1909722222 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39755.191 | 39755.7097 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029769739755.2402777778 | 10297697 |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39755.2403 | 39755.2985 | CONT | 00007452 | FORCED | Delta E/F Alarm | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027155939755.5402777778 | 10271559 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT RCTS | 39755.5403 | 39755.6861 | DAILY | 00016893 | SPIMAINT | OVERHAUL S/S TRANS | SPIPOWER |  |  | Other Transformers | Alstom | 22 |  |  |  | 0
_1029660539756.1909722222 | 10296605 |  | Parent | FALSE | JDSS-WOTS 330KV NW | 39756.191 | 39756.5118 | REPDAILY | 00060188 | TRANSGRD | Transgrid OPGW work | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1027274939756.2680555556 | 10272749 |  | Parent | TRUE | NO.1A TRANS 22KV CB AT RCTS | 39756.2681 | 39756.6868 | DAILY | [12 empty] | 0
_1029731239756.2680555556 | 10297312 | 10272749 | Child | FALSE | NO.1A TRANS AT RCTS | 39756.2681 | 39756.6868 | DAILY | 00016722 | SPIMAINT | Perf calc W/O No1A Trans during 22kV CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029772139756.8006944445 | 10297721 |  | Parent | FALSE | SYN/COND AT BLTS | 39756.8007 | 39756.8521 | CONT | 00002547 | FAULT | Syn Con Trip | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029761939757.2291666667 | 10297619 |  | Parent | FALSE | NO.1 500/220KV TRANS 500KV E/SW AT LYPS | 39757.2292 | 39760.5694 | CONT | [12 empty] | 0
_1027019539757.2347222222 | 10270195 |  | Parent | FALSE | SYN/COND AT FBTS | 39757.2347 | 39759.7104 | CONT | 00002697 | SPIMAINT | 3 Monthly O/HAUL - FBTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z73058E539757.2472222222 | Z73058E5 |  | Parent | FALSE | EPS-TTS 220KV LINE AT SMTS | 39757.2472 | 39757.6785 | REPDAILY | 00015363 | DB_AUG | Modify top plates, O/H line eqpt, replace insul. | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029657839757.2791666667 | 10296578 |  | Parent | FALSE | ROTS NO.1 220KV LINE CB AT HWPS | 39757.2792 | 39757.5292 | DAILY | [12 empty] | 0
_1027332339757.3256944444 | 10273323 |  | Parent | FALSE | H3 TRANS NO.1 BUS 330KV CB CT R/PH AT DDTS | 39757.3257 | 39757.3889 | DAILY | [12 empty] | 0
_Z73058E539758.2319444444 | Z73058E5 |  | Parent | FALSE | EPS-TTS 220KV LINE AT SMTS | 39758.2319 | 39758.6757 | REPDAILY | 00015363 | DB_AUG | Modify top plates, O/H line eqpt, replace insul. | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029732139758.2722222222 | 10297321 |  | Parent | FALSE | NO.1 330KV CAPACITOR BANK AT DDTS | 39758.2722 | 39758.6618 | DAILY | 00352085 | TRANSGRD | Out W/O DDTS #1 330 Cap bank & CB OH for T'grid | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_1029765439758.3263888889 | 10297654 |  | Parent | FALSE | CBTS NO.1 66KV FDR X PROT AT FTS | 39758.3264 | 39758.4417 | DAILY | [12 empty] | 0
_1029731439758.35625 | 10297314 |  | Parent | TRUE | NO.2 22KV BUS AT RCTS | 39758.3562 | 39758.7736 | DAILY | 00016998 | SPIMAINT | Out W/O No2 22kV Bus to repair 2A tr 22CB BS isol | SPIPOWER |  |  | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1029731539758.35625 | 10297315 | 10297314 | Child | FALSE | NO.2 22KV CAPACITOR BANK AT RCTS | 39758.3562 | 39758.7736 | DAILY | 00016713 | SPIMAINT | Rebate W/O No2 22kV Cap Bank during bus outage | SPIPOWER |  |  | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029731639758.35625 | 10297316 | 10297314 | Child | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 39758.3562 | 39758.7736 | DAILY | 00337584 | SPIMAINT | Perf calc W/O No2 Tr grp | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X71558A839758.3576388889 | X71558A8 |  | Parent | TRUE | MLTS NO.2 500KV LINE CB AT HYTS | 39758.3576 | 39758.7854 | DAILY | [12 empty] | 0
_X71558A939758.3576388889 | X71558A9 | X71558A8 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 39758.3576 | 39758.7854 | DAILY | 00002862 | SPICAPX | Rebate W/O M2 Trans during MLTS 2L 2B CB outage | SPIPOWER | X715 | X715 - (HYTS) REPLACEMENT OF RTU AND HMI | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029771339759.0069444444 | 10297713 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 39759.0069 | 39762.0556 | CONT | 00016424 | GENCO | SCAP to YWPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X32058AW39759.24375 | X32058AW |  | Parent | FALSE | U1 66/22KV TRANS AT MTS | 39759.2438 | 39759.3778 | DAILY | 00363343 | SPIMAINT | Install weather shields | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029732239759.2666666667 | 10297322 |  | Parent | FALSE | NO.2 330KV CAPACITOR BANK AT DDTS | 39759.2667 | 39759.5951 | DAILY | 00352093 | TRANSGRD | Out W/O DDTS #2 330 Cap bank & CB OH for T'grid | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_X71558B439759.2722222222 | X71558B4 |  | Parent | TRUE | NO.1 275KV CAPACITOR BANK/SESS NO.1 LINE CB AT HYTS | 39759.2722 | 39759.7972 | DAILY | [12 empty] | 0
_X71558B539759.2722222222 | X71558B5 | X71558B4 | Child | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 39759.2722 | 39759.7972 | DAILY | 00331027 | SPICAPX | Rebate W/O No1 Cap bk during CB outage | SPIPOWER | X715 | X715 - (HYTS) REPLACEMENT OF RTU AND HMI | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029776139759.2902777778 | 10297761 |  | Parent | FALSE | CB CONTROLS/MONITORS AT ROTS | 39759.2903 | 39759.4573 | DAILY | [12 empty] | 0
_1029723039759.3270833333 | 10297230 |  | Parent | FALSE | MLRC 220KV LINE NO.2 BUS CB AT RCTS | 39759.3271 | 39759.3493 | DAILY | [12 empty] | 4
_X32058AT39759.3784722222 | X32058AT |  | Parent | FALSE | U2 66/22KV TRANS AT MTS | 39759.3785 | 39759.4674 | DAILY | 00363319 | SPIMAINT | Install weather shields | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029782239759.5798611111 | 10297822 |  | Parent | FALSE | B3 TRANS 66KV CB BUS SIDE ISOL AT SMTS | 39759.5799 | 39790.25 | CONT | [12 empty] | 0
_1030028739759.5798611111 | 10300287 |  | Parent | FALSE | B1 220/66KV TRANS AT SMTS | 39759.5799 | 39889.3264 | CONT | 00366621 | DB_AUG | Erect new B1 Trans at SMTS | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1029782939759.8479166667 | 10297829 |  | Parent | FALSE | EX - NO.7 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 39759.8479 | 39762.4958 | CONT | [12 empty] | 0
_X50858I239760.2083333333 | X50858I2 | X50858I1 | Child | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39760.2083 | 39760.7028 | DAILY | 00017901 | SPICAPX | Rebate W/O KTS 2 Line during No1 220kV Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858I339760.2083333333 | X50858I3 | X50858I1 | Child | FALSE | EX - MLTS NO.2 220KV LINE AT GTS | 39760.2083 | 39760.7028 | DAILY | 00017904 | SPICAPX | Rebate W/O MLTS 2 Line during No1 220kV Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858I439760.2083333333 | X50858I4 | X50858I1 | Child | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39760.2083 | 39760.7028 | DAILY | 00017906 | SPICAPX | Rebate W/O PTH 2 Line during No1 220kV Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858I539760.2083333333 | X50858I5 | X50858I1 | Child | FALSE | B3 220/66KV TRANS AT GTS | 39760.2083 | 39760.7028 | DAILY | 00002829 | SPICAPX | Rebate W/O No3 TR during No1 220kV Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858I139760.2083333333 | X50858I1 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39760.2083 | 39760.7032 | DAILY | 00002833 | SPICAPX | No1 220kV Bus & MLTS No2 L for GTS rebuild works | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V8C458A039760.2479166667 | V8C458A0 |  | Parent | FALSE | B1 220/66KV TRANS AT CBTS | 39760.2479 | 39760.6278 | DAILY | 00353076 | SPIMAINT | Installation of access hatch | SPIPOWER | V8C4 | V8C4 - (CBTS) RECTIFY CONSTRUCTION DEFECTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_Z63358I539760.2784722222 | Z63358I5 |  | Parent | FALSE | JLTS NO.3 220KV LINE AT HWPS | 39760.2785 | 39760.434 | DAILY | 00015787 | VEN_AUG | ERECT (N) CVTs JLTS 3L AT HWPS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858J839760.6979166667 | X50858J8 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE CB AIR RECEIVER R/PH AT GTS | 39760.6979 | 39872.2083 | CONT | [12 empty] | 0
_X50858I639760.7027777778 | X50858I6 |  | Parent | FALSE | EX - MLTS NO.2 220KV LINE AT GTS | 39760.7028 | 39770.741 | CONT | 00017904 | SPICAPX | MLTS 2 Line for GTS rebuild works | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858J339761.2083333333 | X50858J3 |  | Parent | TRUE | NO.2 66KV BUS AT GTS | 39761.2083 | 39761.5701 | DAILY | 00002836 | SPICAPX | Out W/O No2, 5 & 6 66 Bus to disconn temp CRO fdr | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858J439761.2083333333 | X50858J4 | X50858J3 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT GTS | 39761.2083 | 39761.5701 | DAILY | 00350421 | SPICAPX | Rebate W/O No1 66 Cap bk during No2 66 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X50858J539761.2083333333 | X50858J5 | X50858J3 | Child | FALSE | B1 220/66KV TRANS AT GTS | 39761.2083 | 39761.5701 | DAILY | 00002828 | SPICAPX | Perf calc W/O No1 trans during No2 66 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029708839761.2256944444 | 10297088 |  | Parent | TRUE | 5-6 220KV BUS TIE CB NO.5 BUS SIDE ISOL AT HWPS | 39761.2257 | 39761.5493 | DAILY | [12 empty] | 0
_1029723639761.2256944444 | 10297236 | 10297088 | Child | FALSE | ROTS NO.1 220KV LINE AT HWPS | 39761.2257 | 39761.5493 | DAILY | 00015790 | SPIMAINT | LINE REBATE FOR BUS OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558F939762.2291666667 | X56558F9 |  | Parent | FALSE | GNTS NO.1 220KV LINE AT DDTS | 39762.2292 | 39764.4563 | CONT | 00352475 | SPICAPX | Out W/O GNTS 1 Line for CB CT replacement | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X71558A339763.04375 | X71558A3 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 39763.0437 | 39763.684 | DAILY | 00027386 | SPICAPX | Out W/O HYTS-APD No1 Line CB - SCIMS | SPIPOWER | X715 | X715 - (HYTS) REPLACEMENT OF RTU AND HMI | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029141639763.2347222222 | 10291416 |  | Parent | FALSE | B3 220/66KV TRANS AT FBTS | 39763.2347 | 39763.6139 | REPDAILY | 00002727 | SPIMAINT | O/HAUL Transformer and Trafo Union Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026925439763.2395833333 | 10269254 |  | Parent | FALSE | SYN/COND AT TSTS | 39763.2396 | 39768.5889 | CONT | 00007626 | SPIMAINT | Annual O/HAUL - TSTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029649839763.2472222222 | 10296498 |  | Parent | TRUE | JLA NO.2 220KV LINE CB AT TBTS | 39763.2472 | 39764.5479 | CONT | [12 empty] | 0
_1029650239763.2472222222 | 10296502 | 10296498 | Child | FALSE | JLA NO.2 220KV LINE AT TBTS | 39763.2472 | 39764.5479 | CONT | 00026919 | SPIMAINT | rebate for Line outage during plant shut down | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026921039763.2548611111 | 10269210 |  | Parent | TRUE | JLTS NO.1 220KV LINE LINE ROI AT HWPS | 39763.2549 | 39763.5625 | DAILY | [12 empty] | 0
_1027726739763.2548611111 | 10277267 | 10269210 | Child | FALSE | JLTS NO.1 220KV LINE AT HWPS | 39763.2549 | 39763.5625 | DAILY | 00015784 | SPIMAINT | Rebate for Line Outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029653339763.2548611111 | 10296533 | 10269210 | Child | FALSE | JLTS NO.1 LINE/AUX TRANS 'B' 220KV CB AT HWPS | 39763.2549 | 39763.5625 | DAILY | [12 empty] | 0
_X71558A439764.0472222222 | X71558A4 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 39764.0472 | 39764.691 | DAILY | 00060938 | SPICAPX | Out W/O HYTS-APD No2 Line CB - SCIMS | SPIPOWER | X715 | X715 - (HYTS) REPLACEMENT OF RTU AND HMI | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029141639764.2458333333 | 10291416 |  | Parent | FALSE | B3 220/66KV TRANS AT FBTS | 39764.2458 | 39764.6667 | REPDAILY | 00002727 | SPIMAINT | O/HAUL Transformer and Trafo Union Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X32058AU39764.3027777778 | X32058AU |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 39764.3028 | 39764.6354 | DAILY | 00363305 | SPIMAINT | Clean Bird Droppings | SPIPOWER | X320 | X320 - (MTS) STATION REDEVELOPMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029794239764.6902777778 | 10297942 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT SMTS | 39764.6903 | 39764.7278 | DAILY | [12 empty] | 0
_1029141439765.2236111111 | 10291414 |  | Parent | FALSE | B1 220/66KV TRANS AT FBTS | 39765.2236 | 39765.6354 | CONT | 00002726 | SPIMAINT | O/Haul B1 TRANS AT FBTS | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56558G039765.2326388889 | X56558G0 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT DDTS | 39765.2326 | 39766.4028 | CONT | 00012361 | SPICAPX | Out W/O MBTS 1 Line for CB CT replacement | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X71558B639765.2569444444 | X71558B6 |  | Parent | TRUE | NO.1 275KV CAPACITOR BANK/SESS NO.2 LINE CB AT HYTS | 39765.2569 | 39765.6833 | DAILY | [12 empty] | 0
_X71558B739765.2569444444 | X71558B7 | X71558B6 | Child | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 39765.2569 | 39765.6833 | DAILY | 00331027 | SPICAPX | Rebate W/O No1 Cap bk during CB outage | SPIPOWER | X715 | X715 - (HYTS) REPLACEMENT OF RTU AND HMI | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026816639765.2708333333 | 10268166 |  | Parent | TRUE | ROTS NO.5 220KV LINE AT YPS | 39765.2708 | 39765.5514 | DAILY | 00016413 | SPIMAINT | Overhaul ROTS No 5 220 Kv Line at YPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028652139765.2708333333 | 10286521 | 10268166 | Child | FALSE | ROTS NO.5 220KV LINE NO.2 BUS CB LINE SIDE ROI AT YPS | 39765.2708 | 39765.5514 | DAILY | [12 empty] | 0
_1008872739765.2979166667 | 10088727 |  | Parent | FALSE | BETS 220KV LINE AT KGTS | 39765.2979 | 39765.5111 | REPDAILY | 00017423 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029791239765.5548611111 | 10297912 |  | Parent | FALSE | R2 220/66/22KV TRANS AT KGTS | 39765.5549 | 39765.709 | DAILY | 00017344 | SPIMAINT | NO2 Trans OLTC Mech tight during operation | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029795839766.1236111111 | 10297958 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 39766.1236 | 39770.9535 | CONT | 00356081 | GENCO | Isolation for Generator | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029800739766.2013888889 | 10298007 |  | Parent | FALSE | BATS-BETS 220KV | 39766.2014 | 39766.2028 | DAILY | 00328505 | FAULT | Rebate outage for BATS-BETS Auto | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029791739766.2222222222 | 10297917 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 39766.2222 | 39766.4993 | DAILY | 00017270 | SPIMAINT | Out of balance 5th Harmonic filter replace cap can | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z63358I439766.2722222222 | Z63358I4 |  | Parent | FALSE | JLTS NO.3 220KV LINE AT HWPS | 39766.2722 | 39766.5833 | DAILY | 00015787 | VEN_AUG | CONNECT (N) CVT JLTS 3L AT HWPS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029671939766.3277777778 | 10296719 |  | Parent | FALSE | BATS 220KV LINE NO.2 BUS CB AT TGTS | 39766.3278 | 39766.4958 | DAILY | [12 empty] | 0
_1029796039766.3368055556 | 10297960 |  | Parent | FALSE | JLGA NO.4 UNIT TRANS DISC CB AT JLGA | 39766.3368 | 39766.5299 | CONT | [12 empty] | 0
_1029796939766.4034722222 | 10297969 |  | Parent | FALSE | MBTS NO.2 220KV LINE AT DDTS | 39766.4035 | 39766.4639 | DAILY | 00012363 | SPIMAINT | Outage of MBTS-DDTS No2 line for O/L | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029672039766.5388888889 | 10296720 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT TGTS | 39766.5389 | 39766.6264 | DAILY | [12 empty] | 0
_X50858J939767.2361111111 | X50858J9 |  | Parent | TRUE | NO.4 66KV BUS AT GTS | 39767.2361 | 39767.5833 | DAILY | 00002838 | SPICAPX | Out W/O No4 & No5 66 Bus to connect temp GCY fdr | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858K039767.2361111111 | X50858K0 | X50858J9 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39767.2361 | 39767.5833 | DAILY | 00329879 | SPICAPX | Rebate W/O No4 66 Cap bk during No4 66 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X50858K139767.2361111111 | X50858K1 | X50858J9 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39767.2361 | 39767.5833 | DAILY | 00002830 | SPICAPX | Perf calc W/O B4 trans during No4 66 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029748539767.2430555556 | 10297485 | 10297484 | Child | FALSE | HWPS-HWTS 2 220KV G | 39767.2431 | 39767.5778 | DAILY | 00020331 | SPIMAINT | REBATE FOR TX OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029748439767.2430555556 | 10297484 |  | Parent | TRUE | HWTS NO.2 220KV LINE NO.2 BUS CB LINE SIDE ROI AT HWPS | 39767.2431 | 39767.5784 | DAILY | [12 empty] | 0
_X67058C839767.2506944445 | X67058C8 |  | Parent | FALSE | BLTS 220KV LINE AT ATS | 39767.2507 | 39767.7 | REPDAILY | 00055536 | SPICAPX | replace blts line ct's | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858K639767.5833333333 | X50858K6 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 39767.5833 | 39767.6792 | DAILY | 00002830 | SPICAPX | Out W/O B4 trans VT ratio change | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858K239767.5833333333 | X50858K2 |  | Parent | FALSE | EX - GCY 66KV FDR CB AT GTS | 39767.5833 | 39774.2604 | CONT | [12 empty] | 0
_1026912939768.2458333333 | 10269129 |  | Parent | TRUE | 5-6 220KV BUS TIE CB AT HWPS | 39768.2458 | 39768.409 | DAILY | [12 empty] | 0
_1026915439768.2458333333 | 10269154 | 10269129 | Child | FALSE | 5-6 220KV BUS TIE CB NO.6 BUS SIDE E/SW AT HWPS | 39768.2458 | 39768.409 | DAILY | [12 empty] | 0
_1028373239768.2458333333 | 10283732 | 10269129 | Child | FALSE | 5-6 220KV BUS TIE CB NO.6 BUS SIDE ISOL AT HWPS | 39768.2458 | 39768.409 | DAILY | [12 empty] | 0
_X67058C839768.25 | X67058C8 |  | Parent | FALSE | BLTS 220KV LINE AT ATS | 39768.25 | 39768.6611 | REPDAILY | 00055536 | SPICAPX | replace blts line ct's | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X67058C939769.2305555556 | X67058C9 |  | Parent | FALSE | BLTS 220KV LINE AT ATS | 39769.2306 | 39769.6778 | DAILY | 00055536 | SPICAPX | replace blts line ct's | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029711039769.2611111111 | 10297110 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT ERTS | 39769.2611 | 39769.5639 | DAILY | 00004373 | SPIMAINT | REPAIR EARTHING | SPIPOWER |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1029801939769.7347222222 | 10298019 |  | Parent | FALSE | W1 GEN TRANS NO.2 BUS 220KV CB BUS SIDE ISOL AT YPS | 39769.7347 | 39773.2278 | CONT | [12 empty] | 0
_1029653439770.2708333333 | 10296534 |  | Parent | FALSE | NO.3 GEN TRANS NO.2 BUS 220KV CB AT HWPS | 39770.2708 | 39770.3493 | DAILY | [12 empty] | 0
_X72458A239771.5888888889 | X72458A2 |  | Parent | FALSE | EX - NO.1 66KV REACTOR AT HOTS | 39771.5889 | 39771.6333 | DAILY | 00006935 | SPICAPX | Excavate adjacent to No1 66kv Reactor | SPIPOWER | X724 | X724 - (HOTS) NO.1 SHUNT REACTOR REPLACEMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029808239773.2583333333 | 10298082 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT SVTS | 39773.2583 | 39773.4028 | DAILY | 00004824 | SPIMAINT | Reblance Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029818239773.9673611111 | 10298182 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39773.9674 | 39781.8881 | CONT | 00356082 | GENCO | HWPS No4 Gen Trans Isolations for P/Stn | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029815439774.2013888889 | 10298154 |  | Parent | FALSE | EX - HWTS NO.2 220KV LINE NO.1 BUS CB BUS SIDE ISOL AT HWPS | 39774.2014 | 39776.5139 | CONT | [12 empty] | 0
_X50858K339774.2083333333 | X50858K3 |  | Parent | TRUE | NO.4 66KV BUS AT GTS | 39774.2083 | 39774.7188 | DAILY | 00002838 | SPICAPX | Out W/O No4 & 5 66 Bus to disconnect temp GCY fdr | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858K439774.2083333333 | X50858K4 | X50858K3 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39774.2083 | 39774.7188 | DAILY | 00329879 | SPICAPX | Rebate W/O No4 66 Cap bk during No4 66 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X50858K539774.2083333333 | X50858K5 | X50858K3 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39774.2083 | 39774.7188 | DAILY | 00002830 | SPICAPX | Perf calc W/O B4 trans during No4 66 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026823939774.2291666667 | 10268239 |  | Parent | TRUE | EX - SMTS NO.1 500KV LINE AT HWTS | 39774.2292 | 39774.5514 | REPDAILY | 00016237 | SPIMAINT | Overhaul SMTS No 1 500 Kv Line at HWTS | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029721439774.2291666667 | 10297214 | 10268239 | Child | FALSE | EX - SMTS NO.1 500KV LINE L/TRP R/PH AT HWTS | 39774.2292 | 39774.5514 | DAILY | 00157386 | SPIMAINT | SCAN HOTSPOT LINE TRAPS R&WPH | SPIPOWER |  |  | Reactors | Eastern | 500 |  |  |  | 0
_X74158A139774.2416666667 | X74158A1 |  | Parent | FALSE | 1-3 220KV BUS TIE CB AT SVTS | 39774.2417 | 39775.7729 | DAILY | [12 empty] | 0
_Z63358I639774.25 | Z63358I6 |  | Parent | FALSE | HWPS NO.3 220KV LINE AT JLTS | 39774.25 | 39774.3729 | DAILY | 00015939 | VEN_AUG | UPGRADE EARTHING ON LINE SURGE DIV | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V88158A039774.2576388889 | V88158A0 |  | Parent | FALSE | B1 220/66KV TRANS AT RTS | 39774.2576 | 39775.4583 | CONT | 00007329 | SPIMAINT | Treatment and Regeneration of Appro 60,000 | SPIPOWER | V881 | V881 - (RTS) B1 TRANSFORMER OIL REGENERATION | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027031239774.26875 | 10270312 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT TTS | 39774.2688 | 39774.5938 | DAILY | [12 empty] | 0
_Z63358I739774.3881944444 | Z63358I7 |  | Parent | FALSE | MWTS NO.2 220KV LINE AT JLTS | 39774.3882 | 39774.475 | DAILY | 00015948 | VEN_AUG | UPGRADE EARTHING LINE SURGE DIV | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029857739775.0868055556 | 10298577 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 39775.0868 | 39775.1764 | DAILY | 00002830 | FAULT | B4 Trans tripped on thru fault | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z73058E739775.2777777778 | Z73058E7 |  | Parent | FALSE | H2 330/220/22KV TRANS X PROT AT SMTS | 39775.2778 | 39775.5042 | DAILY | [12 empty] | 0
_X56558E739776.2493055556 | X56558E7 |  | Parent | FALSE | BATS NO.1 LINE/TGTS LINE 220KV CB AT MLTS | 39776.2493 | 39778.2069 | CONT | [12 empty] | 0
_1029822939776.3729166667 | 10298229 |  | Parent | FALSE | JLTS NO.4 220KV LINE NO.3 BUS CB AT HWPS | 39776.3729 | 39776.3778 | CONT | [12 empty] | 0
_1029823039776.3777777778 | 10298230 |  | Parent | FALSE | JLTS NO.4 220KV LINE NO.4 BUS CB AT HWPS | 39776.3778 | 39776.3882 | CONT | [12 empty] | 0
_1029649939777.3173611111 | 10296499 |  | Parent | TRUE | JLA NO.2 220KV LINE CB AT TBTS | 39777.3174 | 39777.5799 | DAILY | [12 empty] | 0
_1029650339777.3173611111 | 10296503 | 10296499 | Child | FALSE | JLA NO.2 220KV LINE AT TBTS | 39777.3174 | 39777.5799 | DAILY | 00026919 | SPIMAINT | rebate for Line outage during plant shut down | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029672239777.5305555556 | 10296722 |  | Parent | FALSE | BATS 220KV LINE NO.1 BUS CB AT BETS | 39777.5306 | 39777.5646 | DAILY | [12 empty] | 0
_1029672139777.5805555556 | 10296721 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT BETS | 39777.5806 | 39777.6 | DAILY | [12 empty] | 0
_X56558E839778.2479166667 | X56558E8 |  | Parent | FALSE | BATS NO.1 220KV LINE AT MLTS | 39778.2479 | 39778.4278 | DAILY | 00022946 | SPICAPX | Out W/O BATS 1 Line to connect CT droppers | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558E939778.4277777778 | X56558E9 |  | Parent | FALSE | BATS NO.1 220KV LINE NO.1 BUS CB AT MLTS | 39778.4278 | 39779.4514 | CONT | [12 empty] | 0
_1029842039778.6604166667 | 10298420 |  | Parent | FALSE | DPS -MBTS 220KV NW | 39778.6604 | 39778.7847 | DAILY | 00060195 | FAULT | Prot Trip of DPS line | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029841339779.2875 | 10298413 |  | Parent | FALSE | R2 220/66/22KV TRANS AT KGTS | 39779.2875 | 39779.5938 | DAILY | 00017344 | SPIMAINT | Investigate No2 Transformer Out of Step | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029813439779.3083333333 | 10298134 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT GNTS | 39779.3083 | 39779.3542 | DAILY | [12 empty] | 0
_1029765239779.3875 | 10297652 |  | Parent | FALSE | CBTS NO.2 66KV FDR X PROT AT FTS | 39779.3875 | 39779.4174 | DAILY | [12 empty] | 0
_1029842539779.3965277778 | 10298425 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 39779.3965 | 39779.4097 | DAILY | 00001147 | SPIMAINT | B1 Trans | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029818839779.3986111111 | 10298188 |  | Parent | FALSE | DDTS NO.1 220KV LINE NO.1 BUS CB AT GNTS | 39779.3986 | 39779.4403 | DAILY | [12 empty] | 0
_1029812339780.3034722222 | 10298123 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT WOTS | 39780.3035 | 39780.3674 | DAILY | [12 empty] | 0
_1029846739780.31875 | 10298467 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 39780.3187 | 39780.3528 | DAILY | [12 empty] | 0
_1029812639780.3972222222 | 10298126 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 39780.3972 | 39780.441 | DAILY | [12 empty] | 0
_X50858K739781.1951388889 | X50858K7 |  | Parent | FALSE | EX - GLE NO.1 66KV FDR CB AT GTS | 39781.1951 | 39781.5181 | DAILY | [12 empty] | 0
_1029771439781.2180555556 | 10297714 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT HOTS | 39781.2181 | 39782.7236 | DAILY | [12 empty] | 0
_1029771539781.2180555556 | 10297715 | 10297714 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HOTS | 39781.2181 | 39782.7236 | DAILY | 00359901 | SPIMAINT | Rebate W/O 1B Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029771639781.2180555556 | 10297716 | 10297714 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT HOTS | 39781.2181 | 39782.7236 | DAILY | 00359898 | SPIMAINT | Rebate W/O 1A Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X56558G139781.2291666667 | X56558G1 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT MLTS | 39781.2292 | 39781.4104 | DAILY | 00337580 | SPICAPX | Out W/O A1 Trans 220kV CVT installation | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027031739781.2486111111 | 10270317 |  | Parent | FALSE | NO.2 220KV BUS AT TTS | 39781.2486 | 39781.6903 | REPDAILY | 00001550 | SPIMAINT | O/Haul NO.2 220KV BUS AT TTS | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_Z63358I839781.2534722222 | Z63358I8 |  | Parent | FALSE | HWPS NO.4 220KV LINE AT JLTS | 39781.2535 | 39781.3826 | DAILY | 00015940 | VEN_AUG | UPGRADE EARTHING LINE SURGE DIV | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V8C458A139781.2569444444 | V8C458A1 |  | Parent | FALSE | B2 220/66KV TRANS AT CBTS | 39781.2569 | 39781.6333 | DAILY | 00353077 | SPIMAINT | Installation of access hatch | SPIPOWER | V8C4 | V8C4 - (CBTS) RECTIFY CONSTRUCTION DEFECTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_Z63358I939781.3930555556 | Z63358I9 |  | Parent | FALSE | MWTS NO.1 220KV LINE AT JLTS | 39781.3931 | 39781.5347 | DAILY | 00015947 | VEN_AUG | UPGRADE EARTHING LINE SURGE DIV | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858K839781.5513888889 | X50858K8 |  | Parent | FALSE | EX - GLE NO.1 66KV FDR CB AT GTS | 39781.5514 | 39788.2021 | CONT | [12 empty] | 0
_1027031739782.2298611111 | 10270317 |  | Parent | FALSE | NO.2 220KV BUS AT TTS | 39782.2299 | 39782.6743 | REPDAILY | 00001550 | SPIMAINT | O/Haul NO.2 220KV BUS AT TTS | SPIPOWER |  |  | Bus | Western | 220 |  |  |  | 0
_Z63358J239782.2340277778 | Z63358J2 |  | Parent | FALSE | HWPS-JLTS 4 220KV G | 39782.234 | 39782.8902 | DAILY | 00020446 | VEN_AUG | CUTOVER NEW PROT | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029811939782.7236111111 | 10298119 |  | Parent | TRUE | NO.1 66KV BUS AT HOTS | 39782.7236 | 39782.7368 | DAILY | 00006940 | SPIMAINT | No1 66kV Bus de-energised for 1AB Cap CB commiss | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029814839782.7236111111 | 10298148 | 10298119 | Child | FALSE | B2 220/66KV TRANS AT HOTS | 39782.7236 | 39782.7368 | DAILY | 00363103 | SPIMAINT | Perf calc W/O B2 Trans during #1 66 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56558G339783.2472222222 | X56558G3 |  | Parent | FALSE | A2 TRANS NO.1 BUS 220KV CB AT MLTS | 39783.2472 | 39785.4118 | CONT | [12 empty] | 0
_1029835339783.2520833333 | 10298353 |  | Parent | FALSE | B3 220/66KV TRANS AT WMTS | 39783.2521 | 39784.5681 | CONT | 00003236 | SPIMAINT | replace faulty transformer mechanism | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z56258A339783.2701388889 | Z56258A3 |  | Parent | FALSE | MKPS-BOPS-MBTS 220KV NW | 39783.2701 | 39783.7771 | REPDAILY | 00060197 | GEN_AUG | Out W/O MKPS Line Install new Xarms | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027344539783.2972222222 | 10273445 |  | Parent | FALSE | EX - W1 GEN TRANS NO.2 BUS 220KV CB CT R/PH AT YPS | 39783.2972 | 39783.4625 | DAILY | [12 empty] | 0
_1027342939783.4743055556 | 10273429 |  | Parent | FALSE | AUX TRANS 'B' 220KV CB CT R/PH AT YPS | 39783.4743 | 39783.5875 | DAILY | [12 empty] | 0
_1029856239783.8236111111 | 10298562 |  | Parent | FALSE | BLTS 220KV LINE AT NPSD | 39783.8236 | 39783.8618 | CONT | 00024005 | GENCO | Works for Power Station | GENCO |  |  | Circuits | 3rd Party | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029856339783.8715277778 | 10298563 |  | Parent | FALSE | FBTS 220KV LINE AT NPSD | 39783.8715 | 39783.884 | CONT | 00024003 | GENCO | Works for Power Station | GENCO |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026896239784.1361111111 | 10268962 | 10273115 | Child | FALSE | AUX TRANS 'C' NO.2 BUS 220KV CB LINE SIDE E/SW AT YPS | 39784.1361 | 39784.6479 | CONT | [12 empty] | 0
_1026896439784.1361111111 | 10268964 | 10273115 | Child | FALSE | AUX TRANS 'C' NO.1 BUS 220KV CB LINE SIDE E/SW AT YPS | 39784.1361 | 39784.6479 | CONT | [12 empty] | 0
_1026897239784.1361111111 | 10268972 | 10273115 | Child | FALSE | AUX TRANS 'C' 220KV E/SW AT YPS | 39784.1361 | 39784.6479 | CONT | [12 empty] | 0
_1026899939784.1361111111 | 10268999 | 10273115 | Child | FALSE | AUX TRANS 'C' NO.2 BUS 220KV CB LINE SIDE ISOL AT YPS | 39784.1361 | 39784.6479 | CONT | [12 empty] | 0
_1026900139784.1361111111 | 10269001 | 10273115 | Child | FALSE | AUX TRANS 'C' NO.1 BUS 220KV CB LINE SIDE ISOL AT YPS | 39784.1361 | 39784.6479 | CONT | [12 empty] | 0
_1027311539784.1361111111 | 10273115 |  | Parent | TRUE | AUX TRANS 'C' 220KV LINE AT YPS | 39784.1361 | 39784.6479 | CONT | 00016421 | SPIMAINT | Overhaul 220KV Line CVT'S | SPIPOWER |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1027342739784.1361111111 | 10273427 | 10273115 | Child | FALSE | AUX TRANS 'C' NO.2 BUS 220KV CB CT R/PH AT YPS | 39784.1361 | 39784.6479 | CONT | [12 empty] | 0
_1027343139784.1361111111 | 10273431 | 10273115 | Child | FALSE | AUX TRANS 'C' NO.1 BUS 220KV CB CT R/PH AT YPS | 39784.1361 | 39784.6479 | CONT | [12 empty] | 0
_Z56258A339784.2486111111 | Z56258A3 |  | Parent | FALSE | MKPS-BOPS-MBTS 220KV NW | 39784.2486 | 39784.7403 | REPDAILY | 00060197 | GEN_AUG | Out W/O MKPS Line Install new Xarms | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029860939784.9666666667 | 10298609 |  | Parent | FALSE | R2 220/66/22KV TRANS AT KGTS | 39784.9667 | 39785.0028 | CONT | 00017344 | FORCED | KGTS No2 Trans OLTC Fault | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56558G439785.2340277778 | X56558G4 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT MLTS | 39785.234 | 39785.4118 | DAILY | 00364782 | SPICAPX | Out W/O A2 Trans to connect new 1B CB Cts | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Main Transformers | Alstom | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_Z56258A339785.2361111111 | Z56258A3 |  | Parent | FALSE | MKPS-BOPS-MBTS 220KV NW | 39785.2361 | 39785.7361 | REPDAILY | 00060197 | GEN_AUG | Out W/O MKPS Line Install new Xarms | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029775539785.25 | 10297755 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK CB AT WMTS | 39785.25 | 39785.3167 | DAILY | [12 empty] | 0
_1009445739785.2590277778 | 10094457 |  | Parent | FALSE | ALQ 66KV FDR CB AT ATS | 39785.259 | 39785.5813 | DAILY | [12 empty] | 0
_1029843139785.2930555556 | 10298431 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39785.2931 | 39785.3125 | DAILY | 00319999 | APDALCOA | APD Work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z63358J339786.2222222222 | Z63358J3 |  | Parent | FALSE | HWPS-JLTS 3 220KV G | 39786.2222 | 39786.8944 | DAILY | 00020445 | VEN_AUG | CUTOVER NEW PROT | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z56258A339786.2333333333 | Z56258A3 |  | Parent | FALSE | MKPS-BOPS-MBTS 220KV NW | 39786.2333 | 39786.7255 | REPDAILY | 00060197 | GEN_AUG | Out W/O MKPS Line Install new Xarms | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029831139786.2465277778 | 10298311 |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39786.2465 | 39786.5806 | DAILY | 00007452 | SPIMAINT | Repair oil leaks | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X56558G539786.2513888889 | X56558G5 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 39786.2514 | 39787.4931 | CONT | 00003011 | SPICAPX | Out W/O 220kV Shunt Reactor to replace its CTs | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029863139786.2583333333 | 10298631 |  | Parent | FALSE | B1 220/66KV TRANS AT WMTS | 39786.2583 | 39786.5785 | DAILY | 00003233 | SPIMAINT | top up 2 off 220kv trans bushings | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029843439786.2923611111 | 10298434 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39786.2924 | 39786.4472 | DAILY | 00319998 | APDALCOA | APD Work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029854239786.3111111111 | 10298542 |  | Parent | FALSE | R2 220/66/22KV TRANS AT KGTS | 39786.3111 | 39786.5312 | DAILY | 00017344 | SPIMAINT | Investigate No2 Transformer Out of Step | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z73058F039786.3479166667 | Z73058F0 |  | Parent | FALSE | B3 220/66KV TRANS X PROT AT SMTS | 39786.3479 | 39790.2917 | CONT | [12 empty] | 0
_1029833639787.2395833333 | 10298336 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39787.2396 | 39787.4153 | DAILY | 00354002 | SPIMAINT | Topped up oil level for OLTC | SPIPOWER |  |  | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1029806539787.2875 | 10298065 |  | Parent | FALSE | B2 TRANS 220KV CB AT GNTS | 39787.2875 | 39787.4729 | DAILY | [12 empty] | 0
_1029811139787.5173611111 | 10298111 |  | Parent | FALSE | DDTS NO.3 220KV LINE/SHTS NO.3 LINE CB CT R/PH AT GNTS | 39787.5174 | 39787.6111 | DAILY | [12 empty] | 0
_1029866239787.6111111111 | 10298662 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 39787.6111 | 39790.0264 | CONT | 00016424 | GENCO | GenCo work | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029867139787.7972222222 | 10298671 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT SMTS | 39787.7972 | 39787.9181 | CONT | [12 empty] | 0
_1029867239787.9416666667 | 10298672 |  | Parent | FALSE | NO.6 GEN 220/16.5KV TRANS AT HWPS | 39787.9417 | 39789.9806 | CONT | 00009647 | GENCO | Power Station requirements | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1029867639788.1305555556 | 10298676 |  | Parent | FALSE | W1A 230/20KV GEN TRANS AT YWPS | 39788.1306 | 39788.1368 | CONT | 00010632 | GENCO | P/Station requirements - W1 Gen to 220 kV System | GENCO |  |  | Connection Transformers | Eastern | 220 |  |  |  | 0
_X50858K939788.2236111111 | X50858K9 |  | Parent | FALSE | EX - GLE NO.1 66KV FDR CB AT GTS | 39788.2236 | 39788.6451 | DAILY | [12 empty] | 0
_X56558G839788.2319444444 | X56558G8 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT MLTS | 39788.2319 | 39788.5882 | DAILY | 00337580 | SPICAPX | Out W/O A1 Trans 220kV CVT installation | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029833239788.2381944445 | 10298332 |  | Parent | TRUE | NO.1B 66KV CAPACITOR BANK CB AT HOTS | 39788.2382 | 39788.8396 | DAILY | [12 empty] | 0
_1029833339788.2381944445 | 10298333 | 10298332 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HOTS | 39788.2382 | 39788.8396 | DAILY | 00359901 | SPIMAINT | Rebate W/O 1B Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029833439788.2381944445 | 10298334 | 10298332 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT HOTS | 39788.2382 | 39788.8396 | DAILY | 00359898 | SPIMAINT | Rebate W/O 1A Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027326939788.25 | 10273269 |  | Parent | FALSE | 1B-3 220KV BUS TIE CB CT R/PH AT BLTS | 39788.25 | 39788.3431 | DAILY | [12 empty] | 0
_1026824239788.25 | 10268242 |  | Parent | TRUE | EX - SMTS NO.2 500KV LINE AT HWTS | 39788.25 | 39788.591 | REPDAILY | 00016238 | SPIMAINT | Overhaul SMTS No 2 500 Kv Line at HWTS | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029646539788.25 | 10296465 | 10268242 | Child | FALSE | EX - SMTS NO.2 500KV LINE NO.4 MAIN TRANS CB AT HWTS | 39788.25 | 39788.591 | DAILY | [12 empty] | 0
_1029864339788.2805555556 | 10298643 |  | Parent | FALSE | DRN NO.2 66KV FDR CB AT SMTS | 39788.2806 | 39788.6819 | CONT | [12 empty] | 0
_1029864239788.28125 | 10298642 |  | Parent | FALSE | DRN NO.1 66KV FDR CB AT SMTS | 39788.2812 | 39789.5781 | CONT | [12 empty] | 0
_1027329539788.3451388889 | 10273295 |  | Parent | FALSE | ATS 220KV LINE NO.4 BUS CB CT R/PH AT BLTS | 39788.3451 | 39788.4035 | DAILY | [12 empty] | 0
_1026824239789.25 | 10268242 |  | Parent | TRUE | EX - SMTS NO.2 500KV LINE AT HWTS | 39789.25 | 39789.6215 | REPDAILY | 00016238 | SPIMAINT | Overhaul SMTS No 2 500 Kv Line at HWTS | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029646539789.25 | 10296465 | 10268242 | Child | FALSE | EX - SMTS NO.2 500KV LINE NO.4 MAIN TRANS CB AT HWTS | 39789.25 | 39789.6215 | DAILY | [12 empty] | 0
_Z73058F339790.2569444444 | Z73058F3 |  | Parent | FALSE | NO.1 220KV BUS AT SMTS | 39790.2569 | 39798.3722 | CONT | 00366543 | DB_AUG | bus out for proximity | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z73058F139790.2569444444 | Z73058F1 |  | Parent | FALSE | NO.2 220KV BUS AT SMTS | 39790.2569 | 39798.6625 | DAILY | 00366542 | DB_AUG | connect 220&66kv droppers/buswork to b3 tr & isol | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7F858A439790.4583333333 | X7F858A4 |  | Parent | FALSE | O.O.S SPARE TRANS BANK AT DDTS | 39790.4583 | 39865.6528 | CONT | 00337559 | SPICAPX | DDTS OOS Trans 220kV & 330kV S/D replacement | SPIPOWER | X7F8 | X7F8 - REPLACE AGEING 66KV - 330KV SURGE ARRESTERS | Main Transformers | Alstom | 330 | NON AER ELEMENT | EXCLUDED |  | 0
_1029870439790.5416666667 | 10298704 |  | Parent | FALSE | NO.3 66KV BUS AT SMTS | 39790.5417 | 39798.6764 | CONT | 00366276 | SPIMAINT | HVS: No 3 66kV Bus | SPIPOWER |  |  | Bus | 3rd Party | 66 |  |  |  | 0
_1029870339790.5416666667 | 10298703 |  | Parent | FALSE | NO.2 66KV BUS AT SMTS | 39790.5417 | 39798.7083 | CONT | 00366275 | SPIMAINT | HVS: No 2 66kV Bus | SPIPOWER |  |  | Bus | 3rd Party | 66 |  |  |  | 0
_1029870239790.5416666667 | 10298702 |  | Parent | FALSE | NO.1 66KV BUS AT SMTS | 39790.5417 | 39798.7127 | CONT | 00366274 | SPIMAINT | HVS: No 1 66kV Bus | SPIPOWER |  |  | Bus | 3rd Party | 66 |  |  |  | 0
_1029870039790.5416666667 | 10298700 |  | Parent | FALSE | DRN NO.1 66KV FDR CB AT SMTS | 39790.5417 | 39799.6507 | CONT | [12 empty] | 0
_1029870139790.5416666667 | 10298701 |  | Parent | FALSE | DRN NO.2 66KV FDR CB AT SMTS | 39790.5417 | 39800.6424 | CONT | [12 empty] | 0
_X67058D039791.1652777778 | X67058D0 |  | Parent | FALSE | NO.4 220KV CAPACITOR BANK AT BLTS | 39791.1653 | 39791.4139 | DAILY | 00327921 | SPICAPX | replace ct stands | SPIPOWER | X670 | X670 - CT REPLACEMENT PROGRAM - STAGE 2 | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029840639791.2513888889 | 10298406 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT RWTS | 39791.2514 | 39791.4229 | REPDAILY | [12 empty] | 0
_1029840739791.2513888889 | 10298407 | 10298406 | Child | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39791.2514 | 39791.4229 | DAILY | 00007399 | SPIMAINT | Rebate for Cb outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029840839791.2513888889 | 10298408 | 10298406 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39791.2514 | 39791.4229 | DAILY | 00331179 | SPIMAINT | Rebate for Cb outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029157139791.2520833333 | 10291571 |  | Parent | FALSE | 1A-2A 220KV BUS TIE CB AT BLTS | 39791.2521 | 39794.6174 | CONT | [12 empty] | 0
_1029826239791.2951388889 | 10298262 |  | Parent | TRUE | B4 TRANS 66KV CB CT R/PH AT SHTS | 39791.2951 | 39791.4437 | DAILY | [12 empty] | 0
_1029833839791.2951388889 | 10298338 | 10298262 | Child | FALSE | B4 220/66KV TRANS AT SHTS | 39791.2951 | 39791.4437 | DAILY | 00350590 | SPIMAINT | Perf calc W/O B4 Trans during its 66kv CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029826339791.4881944445 | 10298263 |  | Parent | TRUE | B2 TRANS 66KV CB CT R/PH AT SHTS | 39791.4882 | 39791.6021 | DAILY | [12 empty] | 0
_1029833939791.4881944445 | 10298339 | 10298263 | Child | FALSE | B2 220/66KV TRANS AT SHTS | 39791.4882 | 39791.6021 | DAILY | 00000841 | SPIMAINT | Perf calc W/O No2 Trans during its 66kv CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029874839791.8697222222 | 10298748 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 39791.8697 | 39793.9556 | CONT | 00356081 | GENCO | HWPS No3 Gen Tran Isol'd from its 220kV Supplies | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029771739792.2326388889 | 10297717 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT HOTS | 39792.2326 | 39792.8431 | DAILY | [12 empty] | 0
_1029771839792.2326388889 | 10297718 | 10297717 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 39792.2326 | 39792.8431 | DAILY | 00359897 | SPIMAINT | Rebate W/O No2 66kV Cap bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X50858N439792.2423611111 | X50858N4 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT GTS | 39792.2424 | 39792.3542 | CONT | 00002832 | SPICAPX | Out W/O Remove No2 S/S Trans redundant cabling | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1029840639792.2451388889 | 10298406 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT RWTS | 39792.2451 | 39792.4187 | REPDAILY | [12 empty] | 0
_1029840739792.2451388889 | 10298407 | 10298406 | Child | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39792.2451 | 39792.4187 | DAILY | 00007399 | SPIMAINT | Rebate for Cb outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029840839792.2451388889 | 10298408 | 10298406 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39792.2451 | 39792.4187 | DAILY | 00331179 | SPIMAINT | Rebate for Cb outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027256939792.26875 | 10272569 |  | Parent | FALSE | NO.3 66KV REACTOR CB AT RCTS | 39792.2688 | 39792.5931 | DAILY | [12 empty] | 0
_1027260139792.26875 | 10272601 |  | Parent | FALSE | NO.3 66KV REACTOR AT RCTS | 39792.2688 | 39792.5931 | DAILY | 00357254 | SPIMAINT | O/Haul - 66kV reactor | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029154239792.2722222222 | 10291542 |  | Parent | FALSE | 2-3 22KV BUS TIE CB AT BLTS | 39792.2722 | 39792.5819 | DAILY | [12 empty] | 0
_1029823339792.5284722222 | 10298233 |  | Parent | FALSE | 2 EXT-4 66KV BUS TIE CB CT R/PH AT SHTS | 39792.5285 | 39792.6174 | DAILY | [12 empty] | 0
_1029831939792.8430555556 | 10298319 |  | Parent | TRUE | NO.2 66KV BUS AT HOTS | 39792.8431 | 39792.85 | DAILY | 00006941 | SPIMAINT | No2 66kV Bus de-energised for No2 Cap CB commiss | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029832039792.8430555556 | 10298320 | 10298319 | Child | FALSE | B2 220/66KV TRANS AT HOTS | 39792.8431 | 39792.85 | DAILY | 00363103 | SPIMAINT | Perf calc W/O B2 Trans during #1 66 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029091239793.2506944445 | 10290912 |  | Parent | FALSE | B2 220/66KV TRANS AT HTS | 39793.2507 | 39793.5604 | DAILY | 00004446 | SPIMAINT | Transformer Div. Switch Overhaul | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028443539793.2659722222 | 10284435 |  | Parent | FALSE | NO.2 66KV REACTOR AT RCTS | 39793.266 | 39793.6278 | DAILY | 00016897 | SPIMAINT | Repair No2 66kv Reactor oil leaks | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029858539793.2722222222 | 10298585 |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT BLTS | 39793.2722 | 39794.6424 | CONT | [12 empty] | 0
_1029823439793.4513888889 | 10298234 |  | Parent | FALSE | 3-4 66KV BUS TIE CB CT R/PH AT SHTS | 39793.4514 | 39793.5674 | DAILY | [12 empty] | 0
_1029874939794.2319444444 | 10298749 |  | Parent | FALSE | NO.2 CSC AT ROTS | 39794.2319 | 39794.4146 | DAILY | 00004716 | SPIMAINT | REPLACE BROKEN INSULATOR | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029826539794.2673611111 | 10298265 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB CT R/PH AT RCTS | 39794.2674 | 39794.3972 | DAILY | [12 empty] | 0
_1029835039794.2673611111 | 10298350 | 10298265 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 39794.2674 | 39794.3972 | DAILY | 00359892 | SPIMAINT | Rebate W/O No2 66kV Cap Bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029825839794.2993055556 | 10298258 |  | Parent | FALSE | B4 TRANS NO.1 BUS 220KV CB CT R/PH AT SHTS | 39794.2993 | 39794.3507 | DAILY | [12 empty] | 0
_1029825939794.4041666667 | 10298259 |  | Parent | FALSE | B4 TRANS NO.2 BUS 220KV CB CT R/PH AT SHTS | 39794.4042 | 39794.5965 | REPDAILY | [12 empty] | 0
_1029879939794.4076388889 | 10298799 |  | Parent | FALSE | EX - TTS NO.2 220KV LINE AT SMTS | 39794.4076 | 39794.4146 | CONT | 00013358 | FAULT | Inadvertent Trip | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358J839795.1895833333 | Z63358J8 |  | Parent | TRUE | NO.2 220KV BUS AT JLTS | 39795.1896 | 39795.6035 | REPDAILY | 00365902 | VEN_AUG | JLTS No2 BUS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358J939795.1895833333 | Z63358J9 | Z63358J8 | Child | FALSE | HWPS NO.2 220KV LINE AT JLTS | 39795.1896 | 39795.6035 | REPDAILY | 00015937 | VEN_AUG | LINE REBATE FOR BUS OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7F858A539795.2305555556 | X7F858A5 |  | Parent | FALSE | H3 330/220KV TRANS AT DDTS | 39795.2306 | 39796.584 | CONT | 00003971 | SPICAPX | DDTS No3 Trans 220kV & 330kV S/D replacement | SPIPOWER | X7F8 | X7F8 - REPLACE AGEING 66KV - 330KV SURGE ARRESTERS | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029871539795.2444444445 | 10298715 |  | Parent | FALSE | NO.6 22KV/415V S/S TRANS W/PH AT SMTS | 39795.2444 | 39795.3708 | DAILY | 00001326 | SPIMAINT | top up transformer conservators | SPIPOWER |  |  | Other Transformers | Western | 22 |  |  |  | 0
_1029826439795.2673611111 | 10298264 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB CT R/PH AT RCTS | 39795.2674 | 39795.3285 | DAILY | [12 empty] | 0
_1029834639795.2673611111 | 10298346 | 10298264 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 39795.2674 | 39795.3285 | DAILY | 00359891 | SPIMAINT | Rebate W/O No1 66kV Cap Bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029878639795.3048611111 | 10298786 |  | Parent | FALSE | DRN NO.1 66KV FDR CB AT SMTS | 39795.3049 | 39795.5764 | DAILY | [12 empty] | 0
_1029878739795.3152777778 | 10298787 |  | Parent | FALSE | DRN NO.2 66KV FDR CB AT SMTS | 39795.3153 | 39795.5764 | DAILY | [12 empty] | 0
_Z63358J839796.1881944445 | Z63358J8 |  | Parent | TRUE | NO.2 220KV BUS AT JLTS | 39796.1882 | 39796.4313 | REPDAILY | 00365902 | VEN_AUG | JLTS No2 BUS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358J939796.1881944445 | Z63358J9 | Z63358J8 | Child | FALSE | HWPS NO.2 220KV LINE AT JLTS | 39796.1882 | 39796.4313 | REPDAILY | 00015937 | VEN_AUG | LINE REBATE FOR BUS OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029859539796.2333333333 | 10298595 | 10298594 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 39796.2333 | 39796.7083 | DAILY | 00016304 | SPIMAINT | Rebate W/O 3B Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029859639796.2333333333 | 10298596 | 10298594 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT BETS | 39796.2333 | 39796.7083 | DAILY | 00350820 | SPIMAINT | Rebate W/O 3A Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1029859439796.2333333333 | 10298594 |  | Parent | TRUE | NO.3 66KV CAPACITOR BANK CB AT BETS | 39796.2333 | 39796.7132 | DAILY | [12 empty] | 0
_1027020139796.2368055556 | 10270201 |  | Parent | TRUE | NO.4 220KV BUS AT BLTS | 39796.2368 | 39796.6104 | DAILY | 00002646 | SPIMAINT | O/Haul NO.4 220KV BUS AT BLTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029886939796.2368055556 | 10298869 | 10270201 | Child | FALSE | ATS 220KV LINE AT BLTS | 39796.2368 | 39796.6104 | DAILY | 00024010 | SPIMAINT | out w/o for ats line on n0.4 bus | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029891039796.2368055556 | 10298910 | 10270201 | Child | FALSE | NPSD 220KV LINE AT BLTS | 39796.2368 | 39796.6104 | DAILY | 00024014 | SPIMAINT | out w/o for npsd line on n0.4 bus | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029893039796.2368055556 | 10298930 | 10270201 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT BLTS | 39796.2368 | 39796.6104 | DAILY | 00327921 | SPIMAINT | out w/o for no.4 cap bank on n0.4 bus | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029818339796.2520833333 | 10298183 |  | Parent | FALSE | ROTS NO.4 220KV LINE AT RTS | 39796.2521 | 39796.5771 | DAILY | 00021338 | SPIMAINT | Repaire hot joints | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028352739796.2791666667 | 10283527 |  | Parent | TRUE | NO.3 220KV BUS CT W/PH AT RTS | 39796.2792 | 39796.5792 | DAILY | [12 empty] | 0
_1029742739796.2791666667 | 10297427 | 10283527 | Child | FALSE | B3 220/66KV TRANS AT RTS | 39796.2792 | 39796.5792 | DAILY | 00329288 | SPIMAINT | trans rebate for bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029742839796.2791666667 | 10297428 | 10283527 | Child | FALSE | L4 220/22KV TRANS AT RTS | 39796.2792 | 39796.5792 | DAILY | 00007333 | SPIMAINT | trans rebate for bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029742939796.2791666667 | 10297429 | 10283527 | Child | FALSE | ROTS NO.4 220KV LINE AT RTS | 39796.2792 | 39796.5792 | DAILY | 00021338 | SPIMAINT | line outage for bus rebate | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029884139796.4819444444 | 10298841 |  | Parent | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 39796.4819 | 39796.8194 | CONT | 00004037 | FAULT | No2 Transf fault on 22kV Cable | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029859039796.7333333333 | 10298590 |  | Parent | TRUE | NO.3 66KV BUS AT BETS | 39796.7333 | 39796.7479 | DAILY | 00016366 | SPIMAINT | No3 66kV Bus de-energised for 3AB Cap CB commiss | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029859139796.7333333333 | 10298591 | 10298590 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39796.7333 | 39796.7479 | DAILY | 00016040 | SPIMAINT | Perf calc W/O No2 Trans during #3 66 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029884039796.7986111111 | 10298840 |  | Parent | FALSE | NO.2 330/66/22KV TRANS CB 22KV CABLE AT WOTS | 39796.7986 | 39803.6056 | DAILY | 00366125 | SPIMAINT | 22 kV Cable Repair | SPIPOWER |  |  | Circuits | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1029876039797.2715277778 | 10298760 |  | Parent | FALSE | B3 220/66KV TRANS AT WMTS | 39797.2715 | 39798.5861 | CONT | 00003236 | SPIMAINT | invest / repair faulty trans mechanism | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028249839797.275 | 10282498 |  | Parent | FALSE | B2 GEN TRANS NO.4 BUS 500KV CB AT LYPS | 39797.275 | 39797.5526 | CONT | [12 empty] | 0
_1029864639797.2770833333 | 10298646 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT SMTS | 39797.2771 | 39798.4778 | CONT | [12 empty] | 0
_1029825939797.36875 | 10298259 |  | Parent | FALSE | B4 TRANS NO.2 BUS 220KV CB CT R/PH AT SHTS | 39797.3688 | 39797.4056 | REPDAILY | [12 empty] | 0
_1029898039798.2604166667 | 10298980 |  | Parent | TRUE | NO.3 220KV CAPACITOR BANK CB AT ROTS | 39798.2604 | 39798.284 | CONT | [12 empty] | 0
_1029920439798.2604166667 | 10299204 | 10298980 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39798.2604 | 39798.284 | CONT | 00112417 | FAULT | Reabate for Tripping of No3 Cap bank | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028248139798.3784722222 | 10282481 |  | Parent | FALSE | A2 GEN TRANS NO.1 BUS 500KV CB AT LYPS | 39798.3785 | 39798.4757 | CONT | [12 empty] | 0
_1029898439798.3895833333 | 10298984 |  | Parent | FALSE | JLGA NO.1 UNIT TRANS DISC CB AT JLGA | 39798.3896 | 39800.6098 | CONT | [12 empty] | 0
_1029849439798.3951388889 | 10298494 |  | Parent | FALSE | RCTS LINE NO.1 BUS CB AT KGTS | 39798.3951 | 39798.4424 | DAILY | [12 empty] | 0
_1029884739798.5763888889 | 10298847 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39798.5764 | 39798.7139 | REPDAILY | 00319999 | APDALCOA | APD Work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z63358K139799.2083333333 | Z63358K1 |  | Parent | TRUE | NO.1 220KV BUS AT JLTS | 39799.2083 | 39799.6458 | REPDAILY | 00365901 | VEN_AUG | BYPOD AND REACTOR No1 BUS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358K239799.2083333333 | Z63358K2 | Z63358K1 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 39799.2083 | 39799.6458 | DAILY | 00015936 | VEN_AUG | REBATE FOR BUS OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029884739799.2819444445 | 10298847 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39799.2819 | 39799.641 | REPDAILY | 00319999 | APDALCOA | APD Work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1028249639799.2875 | 10282496 |  | Parent | FALSE | B2 GEN TRANS NO.3 BUS 500KV CB AT LYPS | 39799.2875 | 39799.5764 | CONT | [12 empty] | 0
_1029857239799.2916666667 | 10298572 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK Y PROT AT ROTS | 39799.2917 | 39799.3139 | DAILY | [12 empty] | 0
_1029898139799.2951388889 | 10298981 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39799.2951 | 39799.4125 | DAILY | 00112417 | SPIMAINT | Repair Cap Bank CB Shooting through | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027013039799.3229166667 | 10270130 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39799.3229 | 39799.6278 | DAILY | 00002862 | SPIMAINT | O/HAUL Transformer Div Mechanism (N) | ELECTRAN |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029787239799.3229166667 | 10297872 |  | Parent | FALSE | HYTS-SESS 2 275KV WH | 39799.3229 | 39799.6389 | DAILY | 00022796 | ELECTRAN | Electranet Outage | ELECTRAN |  |  | Circuits | Alstom | 275 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029903239799.3847222222 | 10299032 |  | Parent | FALSE | EPG NO.2 66KV FDR CB AT SMTS | 39799.3847 | 39799.3854 | CONT | [12 empty] | 0
_1029902939799.3854166667 | 10299029 |  | Parent | FALSE | B1 TRANS 66KV CB AT SMTS | 39799.3854 | 39889.3291 | CONT | [12 empty] | 0
_1029903539799.3854166667 | 10299035 |  | Parent | FALSE | EX - FUTURE KMS 66KV FDR CB AT SMTS | 39799.3854 | 40066.5563 | CONT | [12 empty] | 0
_1029903539799.3854166667 | 10299035 |  | Parent | FALSE | EX - FUTURE KMS 66KV FDR CB AT SMTS | 39799.3854 | 40066.5979 | CONT | [12 empty] | 0
_1029903339799.3854166667 | 10299033 |  | Parent | FALSE | EPG NO.1 66KV FDR CB AT SMTS | 39799.3854 | 40095.5833 | CONT | [12 empty] | 0
_1029903639799.3854166667 | 10299036 |  | Parent | FALSE | EPG NO.2 66KV FDR CB AT SMTS | 39799.3854 | 40095.5833 | CONT | [12 empty] | 0
_1029903139799.3854166667 | 10299031 |  | Parent | FALSE | FUTURE KLO 66KV FDR CB AT SMTS | 39799.3854 | 40235.5 | CONT | [12 empty] | 0
_1030028639799.3868055556 | 10300286 |  | Parent | FALSE | SSS 66KV FDR CB AT SMTS | 39799.3868 | 40095.5833 | CONT | [12 empty] | 0
_1029879739800.1666666667 | 10298797 |  | Parent | TRUE | A3 TRANS 500KV CB AT KTS | 39800.1667 | 39800.3986 | DAILY | [12 empty] | 0
_1029925139800.1666666667 | 10299251 | 10298797 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 39800.1667 | 39800.3986 | DAILY | 00026097 | SPIMAINT | out w/o for a3 trans repair SF6 gas leaking | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z63358K139800.2097222222 | Z63358K1 |  | Parent | TRUE | NO.1 220KV BUS AT JLTS | 39800.2097 | 39800.2292 | REPDAILY | 00365901 | VEN_AUG | BYPOD AND REACTOR No1 BUS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358K239800.2097222222 | Z63358K2 | Z63358K1 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 39800.2097 | 39800.2292 | DAILY | 00015936 | VEN_AUG | REBATE FOR BUS OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029898139800.2798611111 | 10298981 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39800.2799 | 39800.3903 | DAILY | 00112417 | SPIMAINT | Repair Cap Bank CB Shooting through | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028248339800.3381944445 | 10282483 |  | Parent | FALSE | 2-4 500KV BUS TIE CB AT LYPS | 39800.3382 | 39800.5514 | CONT | [12 empty] | 0
_1029905739800.4173611111 | 10299057 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39800.4174 | 39800.6201 | CONT | 00319999 | APDALCOA | HYTS-APD No2 Line De-Energised for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029651639801.2326388889 | 10296516 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 39801.2326 | 39801.4111 | DAILY | [12 empty] | 0
_1029910139801.2409375 | 10299101 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 39801.2409 | 39803.7083 | CONT | [12 empty] | 0
_1029908439801.2555555556 | 10299084 |  | Parent | FALSE | MLTS-TGTS 220KV W | 39801.2556 | 39801.3556 | DAILY | 00022740 | SPIMAINT | Out W/O MLTS-TGTS Line hot joint | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028248539801.2736111111 | 10282485 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.1 BUS CB AT LYPS | 39801.2736 | 39801.4931 | CONT | [12 empty] | 0
_1029915139801.4444444444 | 10299151 |  | Parent | FALSE | SYN/COND AT FBTS | 39801.4444 | 39801.5347 | DAILY | 00002697 | FAULT | Trip SynCon at FBTS | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029915039801.46875 | 10299150 |  | Parent | FALSE | SVTS NO.2 220KV LINE AT ROTS | 39801.4688 | 39801.4764 | DAILY | 00023968 | FORCED | Line de-energised due to burst water main | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027029139803.2298611111 | 10270291 |  | Parent | TRUE | KTS 220KV LINE NO.4 BUS SIDE ISOL AT BLTS | 39803.2299 | 39803.6007 | DAILY | [12 empty] | 0
_1029925539803.2298611111 | 10299255 | 10270291 | Child | FALSE | NPSD 220KV LINE AT BLTS | 39803.2299 | 39803.6007 | DAILY | 00024014 | SPIMAINT | out w/o for kts, ats & npsd isol & esw | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029926539803.2298611111 | 10299265 | 10270291 | Child | FALSE | ATS 220KV LINE AT BLTS | 39803.2299 | 39803.6007 | DAILY | 00024010 | SPIMAINT | out w/o for kts, ats & npsd isol & esw | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029927539803.2298611111 | 10299275 | 10270291 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT BLTS | 39803.2299 | 39803.6007 | DAILY | 00327921 | SPIMAINT | out w/o for kts, ats & npsd isol & esw | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029928539803.2298611111 | 10299285 | 10270291 | Child | FALSE | NO.4 220KV BUS AT BLTS | 39803.2299 | 39803.6007 | DAILY | 00002646 | SPIMAINT | OVERHAUL OF A 220KV ISOLATOR/EARTH SWITCH | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029819839803.2694444445 | 10298198 |  | Parent | FALSE | ROTS NO.4 220KV LINE AT RTS | 39803.2694 | 39803.6806 | DAILY | 00021338 | SPIMAINT | HOT BRIDGE CONNECTION AT S395 ROTS-RTS 4 | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028524939803.2756944445 | 10285249 |  | Parent | TRUE | S008 SMTS-TTS 1 220KV | 39803.2757 | 39803.3542 | DAILY | [12 empty] | 0
_1029925339803.2756944445 | 10299253 | 10285249 | Child | FALSE | EX - TTS NO.1 220KV LINE AT SMTS | 39803.2757 | 39803.3542 | DAILY | 00013357 | FORCED | out w/o for circuit Split pin coming out | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029910539803.3611111111 | 10299105 |  | Parent | FALSE | NO.2 330/66/22KV TRANS 22KV BUS AT WOTS | 39803.3611 | 39803.3889 | DAILY | 00357893 | SPIMAINT | Out W/O High voltage testing of No2 Tr 22kV cable | SPIPOWER |  |  | Bus | Alstom | 22 |  |  |  | 0
_1029904139803.4048611111 | 10299041 |  | Parent | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 39803.4049 | 39803.6854 | DAILY | 00004037 | SPIMAINT | Out W/O for reconnection of No2 Trans 22kV Cable | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029899239804.2493055556 | 10298992 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 39804.2493 | 39804.675 | REPDAILY | 00352791 | SPIMAINT | Replace Pump | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029831139804.2548611111 | 10298311 |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39804.2549 | 39804.5632 | DAILY | 00007452 | SPIMAINT | Repair oil leaks | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029155839804.2625 | 10291558 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT BLTS | 39804.2625 | 39804.5993 | DAILY | [12 empty] | 0
_1029913439804.28125 | 10299134 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39804.2812 | 39804.5951 | DAILY | 00319999 | APDALCOA | APD work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029922239805.2916666667 | 10299222 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39805.2917 | 39805.4181 | DAILY | 00319998 | APDALCOA | APD work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029898139805.3020833333 | 10298981 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39805.3021 | 39805.3806 | DAILY | 00112417 | SPIMAINT | Repair Cap Bank CB Shooting through | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029895839812.3833333333 | 10298958 |  | Parent | FALSE | WOTS 330KV LINE NO.2 BUS CB BUS SIDE ROI AT DDTS | 39812.3833 | 39812.5771 | DAILY | [12 empty] | 0
_1029938739812.4201388889 | 10299387 |  | Parent | FALSE | MWTS NO.2 220KV LINE NO.1 BUS CB AT JLTS | 39812.4201 | 39812.5451 | DAILY | [12 empty] | 0
_1029938839813.3069444445 | 10299388 |  | Parent | FALSE | HWPS NO.3 220KV LINE NO.2 BUS CB AT JLTS | 39813.3069 | 39813.3396 | DAILY | [12 empty] | 0
_1029940139814.6791666667 | 10299401 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 39814.6792 | 39819.7104 | CONT | 00356083 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029940239815.3861111111 | 10299402 |  | Parent | FALSE | WOTS 330KV LINE NO.2 BUS CB AT DDTS | 39815.3861 | 39815.5097 | CONT | [12 empty] | 0
_V77558C639817.3395833333 | V77558C6 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT MLTS | 39817.3396 | 39817.7569 | DAILY | 00360001 | SPIMAINT | Out W/O No1 220 kV Cap bank prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029939639818.375 | 10299396 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 39818.375 | 39818.625 | CONT | [12 empty] | 0
_1029941239818.5555555556 | 10299412 |  | Parent | FALSE | W4 GEN TRANS 220KV CB AT YPS | 39818.5556 | 39823.2778 | CONT | [12 empty] | 0
_1029943139819.3402777778 | 10299431 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39819.3403 | 39819.3417 | DAILY | 00319999 | APDALCOA | APD reactor switching | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029413339820.2361111111 | 10294133 |  | Parent | FALSE | L1 220/22KV TRANS AT BTS | 39820.2361 | 39820.6389 | DAILY | 00360728 | SPIMAINT | O/HAUL Transformer without div sw | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029945239820.3159722222 | 10299452 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 39820.316 | 39820.378 | DAILY | [12 empty] | 0
_1029413639821.2298611111 | 10294136 |  | Parent | FALSE | L2 220/22KV TRANS AT BTS | 39821.2299 | 39821.5972 | DAILY | 00360870 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029943639821.2534722222 | 10299436 |  | Parent | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39821.2535 | 39821.366 | DAILY | 00007399 | SPIMAINT | RE-BALANCE CAP BANK | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029413939822.2493055556 | 10294139 |  | Parent | FALSE | L3 220/22KV TRANS AT BTS | 39822.2493 | 39822.6424 | DAILY | 00360871 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028371639822.28125 | 10283716 |  | Parent | FALSE | W4 GEN TRANS 220KV CB AT YPS | 39822.2812 | 39822.3444 | DAILY | [12 empty] | 0
_1029950939822.40625 | 10299509 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 39822.4062 | 39822.6764 | CONT | 00352121 | FORCED | H2 Trans tripped due to X Diff prot relay fault | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029948439822.85625 | 10299484 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39822.8562 | 39824.3771 | CONT | 00356082 | GENCO | Switching for P/STN HWPS No4 Gen Isols | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z56258A439823.2097222222 | Z56258A4 |  | Parent | TRUE | NO.1 220KV BUS AT MBTS | 39823.2097 | 39823.7278 | DAILY | 00364502 | VEN_AUG | No1 220kV Bus for WKPS L CB BS connection upgrade | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z56258A539823.2097222222 | Z56258A5 | Z56258A4 | Child | FALSE | WKPS 220KV LINE AT MBTS | 39823.2097 | 39823.7278 | DAILY | 00011756 | VEN_AUG | Rebate W/O WKPS Line during No1 220kV Bus outage | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z56258A639823.2097222222 | Z56258A6 | Z56258A4 | Child | FALSE | EPS NO.2 220KV LINE AT MBTS | 39823.2097 | 39823.7278 | DAILY | 00364634 | VEN_AUG | Rebate W/O EPS 2 Line during No1 220kV Bus outage | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z56258A739823.2097222222 | Z56258A7 | Z56258A4 | Child | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 39823.2097 | 39823.7278 | DAILY | 00011755 | VEN_AUG | Rebate W/O MKPS Line during No1 220kV Bus outage | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z56258A839823.2097222222 | Z56258A8 | Z56258A4 | Child | FALSE | DDTS NO.2 220KV LINE AT MBTS | 39823.2097 | 39823.7278 | DAILY | 00364626 | VEN_AUG | Rebate W/O DDTS 2 Line during No1 220kV Bus outage | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z56258A939823.2097222222 | Z56258A9 | Z56258A4 | Child | FALSE | B2 220/66KV TRANS AT MBTS | 39823.2097 | 39823.7278 | DAILY | 00362372 | VEN_AUG | Perf calc W/O B2 Trans during No1 220kV Bus outage | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029763639823.2229166667 | 10297636 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT BETS | 39823.2229 | 39823.8201 | DAILY | [12 empty] | 0
_1029763739823.2229166667 | 10297637 | 10297636 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 39823.2229 | 39823.8201 | DAILY | 00016274 | SPIMAINT | Rebate W/O 2B Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029763839823.2229166667 | 10297638 | 10297636 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT BETS | 39823.2229 | 39823.8201 | DAILY | 00350819 | SPIMAINT | Rebate W/O 2A Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1029944839823.2520833333 | 10299448 |  | Parent | FALSE | RTS 220KV LINE AT BTS | 39823.2521 | 39823.5611 | DAILY | 00015960 | SPIMAINT | REINSTALL STOLEN EARTHING ON LINE POLE | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029951239823.4215277778 | 10299512 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 39823.4215 | 39823.641 | DAILY | 00352121 | SPIMAINT | H2 Trans prot c/o | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029944739823.4472222222 | 10299447 |  | Parent | FALSE | EX - NO.1 22KV/415V S/S TRANS AT WMTS | 39823.4472 | 39824.8123 | DAILY | 00003238 | DBPROX | VSCAP to Citipower | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1029951439823.53125 | 10299514 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 39823.5312 | 39831.7917 | CONT | 00356079 | GENCO | HWPS No1 Gen Trans Isols & Earths for SCAP Issue | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029965939823.5611111111 | 10299659 |  | Parent | TRUE | L2 220/22KV TRANS AT BTS | 39823.5611 | 39823.6813 | DAILY | 00360870 | FAULT | BTS: L2 220/22KV Transf trip on inrush | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029966039823.5611111111 | 10299660 | 10299659 | Child | FALSE | BTS -RTS 220KV W (BTS to Joint Bay 7) (CABLE) | 39823.5611 | 39823.6813 | DAILY | 00310401 | FAULT | BTS: L2 220/22KV Transf trip on inrush | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029951639823.625 | 10299516 |  | Parent | FALSE | SYN/COND COOLING TOWER AT FBTS | 39823.625 | 39823.7646 | DAILY | [12 empty] | 0
_1029819939824.2916666667 | 10298199 |  | Parent | TRUE | S395 ROTS-RTS 1 220KV | 39824.2917 | 39824.6701 | DAILY | [12 empty] | 0
_1029929039824.2916666667 | 10299290 | 10298199 | Child | FALSE | RTS NO.1 220KV LINE AT ROTS | 39824.2917 | 39824.6701 | DAILY | 00023111 | SPIMAINT | out w/o for rts line - HOT BRIDGE CONNECTION | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V77558C739824.3631944445 | V77558C7 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT MLTS | 39824.3632 | 39824.8174 | DAILY | 00350825 | SPIMAINT | Out W/O No2 220 kV Cap bank prot setting change | SPIPOWER | V775 | V775 - ROUTINE PROTECTION & CONTROL DEVICE SETTING AND CONF | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1029476339825.2291666667 | 10294763 |  | Parent | FALSE | B4 220/66KV TRANS AT ATS | 39825.2292 | 39825.6188 | REPDAILY | 00363708 | SPIMAINT | O/HAUL Transformer Div Mechanism (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1026912139825.28125 | 10269121 |  | Parent | FALSE | NO.4 GEN TRANS NO.1 BUS 220KV CB AT HWPS | 39825.2812 | 39827.3681 | CONT | [12 empty] | 0
_1029955239825.4826388889 | 10299552 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39825.4826 | 39825.5 | DAILY | [12 empty] | 0
_1029959039825.6604166667 | 10299590 |  | Parent | FALSE | SMTS-KTS 500KV WT | 39825.6604 | 39825.666 | CONT | 00022650 | FAULT | Current Differential relay scheme malop | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029476339826.2361111111 | 10294763 |  | Parent | FALSE | B4 220/66KV TRANS AT ATS | 39826.2361 | 39826.6056 | REPDAILY | 00363708 | SPIMAINT | O/HAUL Transformer Div Mechanism (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1029909039826.26875 | 10299090 |  | Parent | FALSE | EPG NO.1 66KV FDR CB AT SMTS | 39826.2688 | 39827.4389 | DAILY | [12 empty] | 0
_1029909139826.2916666667 | 10299091 |  | Parent | FALSE | EPG NO.2 66KV FDR CB AT SMTS | 39826.2917 | 39827.475 | DAILY | [12 empty] | 0
_1029957839826.2923611111 | 10299578 |  | Parent | FALSE | H3 330/220KV TRANS AT DDTS | 39826.2924 | 39826.5222 | DAILY | 00003971 | SPIMAINT | Investigate leaking 330kv Bushing | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029909239826.3576388889 | 10299092 |  | Parent | FALSE | SSS 66KV FDR CB AT SMTS | 39826.3576 | 39827.475 | CONT | [12 empty] | 0
_1029381639827.2513888889 | 10293816 |  | Parent | FALSE | B4 TRANS NO.2 BUS 220KV CB AT ATS | 39827.2514 | 39827.5583 | CONT | [12 empty] | 0
_1029905939827.2756944445 | 10299059 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.1 BUS CB AT DDTS | 39827.2757 | 39827.4069 | DAILY | [12 empty] | 0
_1029959739827.2881944444 | 10299597 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB CT R/PH AT HWTS | 39827.2882 | 39827.334 | DAILY | [12 empty] | 0
_1029906039827.4090277778 | 10299060 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.2 BUS CB AT DDTS | 39827.409 | 39827.5243 | DAILY | [12 empty] | 0
_1029909339827.4395833333 | 10299093 |  | Parent | FALSE | EX - FUTURE KMS 66KV FDR CB AT SMTS | 39827.4396 | 39828.591 | DAILY | [12 empty] | 0
_1029909639827.4763888889 | 10299096 |  | Parent | FALSE | FUTURE KLO 66KV FDR CB AT SMTS | 39827.4764 | 39828.5764 | CONT | [12 empty] | 0
_1029909539827.4930555556 | 10299095 |  | Parent | FALSE | ST 66KV FDR CB AT SMTS | 39827.4931 | 39828.5764 | CONT | [12 empty] | 0
_1029963239827.6944444444 | 10299632 |  | Parent | FALSE | NO.2 330KV BUS AT WOTS | 39827.6944 | 39827.7806 | CONT | 00004042 | FAULT | Fault associated with No 2 Trans | SPIPOWER |  |  | Bus | Alstom | 330 | NON AER ELEMENT | EXCLUDED |  | 0
_1029963339827.6944444444 | 10299633 |  | Parent | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 39827.6944 | 39827.8382 | CONT | 00004037 | FAULT | Fault associated with No 2 Trans | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029963439827.6944444444 | 10299634 |  | Parent | FALSE | NO.2 330/66/22KV TRANS CB 22KV CABLE AT WOTS | 39827.6944 | 39829.6424 | CONT | 00366125 | FAULT | Fault associated with No 2 Trans | SPIPOWER |  |  | Circuits | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1029963639828.0701388889 | 10299636 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB AT HWTS | 39828.0701 | 39828.5861 | CONT | [12 empty] | 0
_1029381839828.2493055556 | 10293818 |  | Parent | FALSE | B4 TRANS NO.3 BUS 220KV CB AT ATS | 39828.2493 | 39828.6028 | CONT | [12 empty] | 0
_1029743339828.2708333333 | 10297433 |  | Parent | FALSE | EX - MBTS NO.1 220KV LINE CB CT R/PH AT DDTS | 39828.2708 | 39828.3736 | DAILY | [12 empty] | 0
_1028562739828.3020833333 | 10285627 |  | Parent | FALSE | NO.6 GEN TRANS NO.3 BUS 220KV CB AT HWPS | 39828.3021 | 39828.3368 | DAILY | [12 empty] | 0
_X72458A339828.4236111111 | X72458A3 |  | Parent | FALSE | EX - NO.1 66KV REACTOR AT HOTS | 39828.4236 | 39828.6819 | REPDAILY | 00006935 | SPICAPX | Install No1 66kv Reactor on foundation | SPIPOWER | X724 | X724 - (HOTS) NO.1 SHUNT REACTOR REPLACEMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X72458A339829.2888888889 | X72458A3 |  | Parent | FALSE | EX - NO.1 66KV REACTOR AT HOTS | 39829.2889 | 39829.5139 | REPDAILY | 00006935 | SPICAPX | Install No1 66kv Reactor on foundation | SPIPOWER | X724 | X724 - (HOTS) NO.1 SHUNT REACTOR REPLACEMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029962039829.3402777778 | 10299620 |  | Parent | FALSE | EX - NO.3 MAIN TRANS NO.1 BUS 500KV CB AT HWTS | 39829.3403 | 39829.4139 | DAILY | [12 empty] | 0
_1029972239829.9416666667 | 10299722 |  | Parent | FALSE | A3 GEN TRANS NO.1 BUS 500KV CB AT LYPS | 39829.9417 | 39830.6729 | CONT | [12 empty] | 0
_1029875539830.2298611111 | 10298755 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT KGTS | 39830.2299 | 39830.6611 | DAILY | [12 empty] | 0
_1029875639830.2298611111 | 10298756 | 10298755 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT KGTS | 39830.2299 | 39830.6611 | DAILY | 00359899 | SPIMAINT | Rebate W/O No1 66kV Cap bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029614639830.2305555556 | 10296146 |  | Parent | FALSE | NO.4 MAIN TRANS 220KV ISOL AT HWTS | 39830.2306 | 39830.5972 | DAILY | 00009699 | SPIMAINT | SCAN HOT SPOT R&WPH FIXED & JAW | SPIPOWER | [8 empty] | 0 | 10296146 |  | SCAN HOT SPOT R&WPH FIXED & JAW | 00009699 | SWITCH |  | HWTS | ISOL | SPIMAINT | DAILY
_V81158A239830.3034722222 | V81158A2 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK X PROT AT BATS | 39830.3035 | 39830.534 | DAILY | [12 empty] | 0
_V81158A139830.5368055556 | V81158A1 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK X PROT AT BATS | 39830.5368 | 39830.6454 | DAILY | [12 empty] | 0
_1029972939830.5972222222 | 10299729 |  | Parent | FALSE | EX - NO.4 MAIN TRANS NO.1 BUS 500KV CB AT HWTS | 39830.5972 | 39833.2854 | CONT | [12 empty] | 0
_1029875739830.6534722222 | 10298757 |  | Parent | TRUE | NO.1 66KV BUS AT KGTS | 39830.6535 | 39830.6785 | DAILY | 00357313 | SPIMAINT | No1 66kV Bus de-energised for No1 Cap CB commiss | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029875839830.6534722222 | 10298758 | 10298757 | Child | FALSE | R1 220/66/22KV TRANS AT KGTS | 39830.6535 | 39830.6785 | DAILY | 00357301 | SPIMAINT | Perf calc W/O B1 Trans during #1 66 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029878839831.2291666667 | 10298788 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT KGTS | 39831.2292 | 39831.7021 | DAILY | [12 empty] | 0
_1029878939831.2291666667 | 10298789 | 10298788 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT KGTS | 39831.2292 | 39831.7021 | DAILY | 00359900 | SPIMAINT | Rebate W/O No2 66kV Cap bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029879139831.6923611111 | 10298791 |  | Parent | TRUE | NO.2 66KV BUS AT KGTS | 39831.6924 | 39831.7021 | DAILY | 00357314 | SPIMAINT | No2 66kV Bus de-energised for No2 Cap CB commiss | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029879239831.6923611111 | 10298792 | 10298791 | Child | FALSE | R3 220/66/22KV TRANS AT KGTS | 39831.6924 | 39831.7021 | DAILY | 00017375 | SPIMAINT | Perf calc W/O No3 Trans during #2 66 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029960639832.2722222222 | 10299606 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39832.2722 | 39832.2785 | DAILY | 00319998 | SW_NEM | Reactor Switching for NEMMCO | NEMMCO |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029960739832.2861111111 | 10299607 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39832.2861 | 39832.2972 | DAILY | 00319999 | SW_NEM | Reactor Switching for NEMMCO | NEMMCO |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029142739833.2569444444 | 10291427 |  | Parent | FALSE | 1-3 220KV BUS TIE CB AT FBTS | 39833.2569 | 39834.5924 | CONT | [12 empty] | 0
_V8B758A039834.2534722222 | V8B758A0 |  | Parent | TRUE | NO.1 22KV CAPACITOR BANK CB AT RWTS | 39834.2535 | 39838.4035 | DAILY | [12 empty] | 0
_V8B758A339834.2534722222 | V8B758A3 | V8B758A0 | Child | FALSE | NO.1 22KV CAPACITOR BANK AT RWTS | 39834.2535 | 39838.4035 | DAILY | 00356999 | SPIMAINT | settings checking of cb | SPIPOWER | V8B7 | V8B7 - ABB EDF CB ADJUSTMENT | Capacitors | Eastern | 22 | CONNECTION ASSET | EXCLUDED |  | 0
_1026912539834.2715277778 | 10269125 |  | Parent | FALSE | NO.4 GEN TRANS NO.2 BUS 220KV CB AT HWPS | 39834.2715 | 39836.5824 | CONT | [12 empty] | 0
_1029976339834.2902777778 | 10299763 |  | Parent | TRUE | MLTS NO.2 500KV LINE CB AT HYTS | 39834.2903 | 39834.3243 | DAILY | [12 empty] | 0
_1029983739834.2902777778 | 10299837 | 10299763 | Child | FALSE | MLTS NO.2 500KV LINE CB AT HYTS | 39834.2903 | 39834.3243 | DAILY | [12 empty] | 0
_Z64558C839834.325 | Z64558C8 |  | Parent | FALSE | EX - TGTS 220KV LINE NO.2 TIE CT B/PH AT BATS | 39834.325 | 39835.3097 | CONT | [12 empty] | 0
_1029956739834.3368055556 | 10299567 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT TGTS | 39834.3368 | 39834.5625 | DAILY | [12 empty] | 0
_1029956639834.3986111111 | 10299566 |  | Parent | FALSE | BATS 220KV LINE NO.2 BUS CB AT TGTS | 39834.3986 | 39834.5785 | DAILY | [12 empty] | 0
_1029988039834.4583333333 | 10299880 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 39834.4583 | 39834.4826 | CONT | 00027386 | APDALCOA | De-Energised For APD at their request | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029958839835.3243055556 | 10299588 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT BATS | 39835.3243 | 39835.4 | DAILY | [12 empty] | 0
_1029958939835.40625 | 10299589 |  | Parent | FALSE | BETS 220KV LINE NO.2 BUS CB AT BATS | 39835.4062 | 39835.4354 | DAILY | [12 empty] | 0
_1029996439835.5340277778 | 10299964 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT EPSY | 39835.534 | 39835.7063 | CONT | 00087035 | FAULT | No1 220KV Line tripped auto due to lightning | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1029998739836.4618055556 | 10299987 |  | Parent | FALSE | NO.6 GEN 220/16.5KV TRANS AT HWPS | 39836.4618 | 39838.8771 | CONT | 00009647 | GENCO | HVS: HWPS 6 Gen Isol'd for Gen | GENCO |  |  | Connection Transformers | 3rd Party | 220 | NON SP ASSET | EXCLUDED |  | 0
_X50858L539837.2083333333 | X50858L5 |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 39837.2083 | 39837.7333 | DAILY | 00002834 | SPICAPX | Out W/O No2 220kV Bus in Bays B and C | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858L639837.2083333333 | X50858L6 | X50858L5 | Child | FALSE | KTS NO.1 220KV LINE AT GTS | 39837.2083 | 39837.7333 | DAILY | 00367291 | SPICAPX | Rebate W/O KTS 1 Line during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858L739837.2083333333 | X50858L7 | X50858L5 | Child | FALSE | EX - MLTS NO.1 220KV LINE AT GTS | 39837.2083 | 39837.7333 | DAILY | 00017903 | SPICAPX | Rebate W/O MLTS1 Line during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858L839837.2083333333 | X50858L8 | X50858L5 | Child | FALSE | PT. HENRY NO.1 220KV LINE AT GTS | 39837.2083 | 39837.7333 | DAILY | 00367277 | SPICAPX | Rebate W/O PTH 1 Line during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858L939837.2083333333 | X50858L9 | X50858L5 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39837.2083 | 39837.7333 | DAILY | 00002830 | SPICAPX | Perf calc W/O B4 Trans during No2 220K Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029763339837.21875 | 10297633 |  | Parent | TRUE | NO.3 66KV CAPACITOR BANK CB AT SHTS | 39837.2188 | 39837.7931 | DAILY | [12 empty] | 0
_1029763439837.21875 | 10297634 | 10297633 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT SHTS | 39837.2188 | 39837.7931 | DAILY | 00330780 | SPIMAINT | Rebate W/O 3B Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029763539837.21875 | 10297635 | 10297633 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT SHTS | 39837.2188 | 39837.7931 | DAILY | 00350863 | SPIMAINT | Rebate W/O 3A Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V81158A539837.2979166667 | V81158A5 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 39837.2979 | 39837.5139 | DAILY | 00331109 | SPIMAINT | Out W/O No1 66kV Cap bank prot setting changes | SPIPOWER | V811 | V811 - COST EST - UPGRADE CONFIG CAPBANK IEDS, REF545 | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V81158A639837.5597222222 | V81158A6 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39837.5597 | 39837.8222 | DAILY | 00331118 | SPIMAINT | Out W/O No2 66kV Cap bank prot setting changes | SPIPOWER | V811 | V811 - COST EST - UPGRADE CONFIG CAPBANK IEDS, REF545 | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X50858M239837.7465277778 | X50858M2 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 39837.7465 | 39864.2021 | CONT | 00002829 | SPICAPX | Out W/O Install future B3 Trans equipment | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029880739837.7847222222 | 10298807 |  | Parent | TRUE | NO.3 66KV BUS AT SHTS | 39837.7847 | 39837.7931 | DAILY | 00000848 | SPIMAINT | No3 66kV Bus de-energised for 3AB Cap CB commiss | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029880839837.7847222222 | 10298808 | 10298807 | Child | FALSE | B3 220/66KV TRANS AT SHTS | 39837.7847 | 39837.7931 | DAILY | 00000842 | SPIMAINT | Perf calc W/O B3 Trans during #3 66 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029763039838.2243055556 | 10297630 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT SHTS | 39838.2243 | 39838.6514 | DAILY | [12 empty] | 0
_1029763139838.2243055556 | 10297631 | 10297630 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT SHTS | 39838.2243 | 39838.6514 | DAILY | 00330829 | SPIMAINT | Rebate W/O 2B Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029763239838.2243055556 | 10297632 | 10297630 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT SHTS | 39838.2243 | 39838.6514 | DAILY | 00350862 | SPIMAINT | Rebate W/O 2A Cap bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029961139838.3958333333 | 10299611 |  | Parent | FALSE | NO.1 22KV BUS AT RWTS | 39838.3958 | 39838.4035 | DAILY | 00007482 | SPIMAINT | Commission Cap Bank CB | SPIPOWER |  |  | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1030007039840.6277777778 | 10300070 |  | Parent | FALSE | ROTS 220KV LINE NO.1 BUS CB AT TSTS | 39840.6278 | 39840.6451 | DAILY | [12 empty] | 0
_1030006539841.2118055556 | 10300065 |  | Parent | FALSE | SYN/COND AT FBTS | 39841.2118 | 39841.3299 | DAILY | 00002697 | SPIMAINT | investigate/repair high bearing temps | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V8B758A139841.23125 | V8B758A1 |  | Parent | TRUE | NO.2 22KV CAPACITOR BANK CB AT RWTS | 39841.2312 | 39859.4042 | DAILY | [12 empty] | 0
_V8B758A239841.23125 | V8B758A2 | V8B758A1 | Child | FALSE | NO.2 22KV CAPACITOR BANK AT RWTS | 39841.2312 | 39859.4042 | DAILY | 00357000 | SPIMAINT | settings checking of cb | SPIPOWER | V8B7 | V8B7 - ABB EDF CB ADJUSTMENT | Capacitors | Eastern | 22 | CONNECTION ASSET | EXCLUDED |  | 0
_V81158A739841.2347222222 | V81158A7 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT RWTS | 39841.2347 | 39841.3764 | DAILY | 00350529 | SPIMAINT | Out W/O No2 220kV Cap bank prot setting changes | SPIPOWER | V811 | V811 - COST EST - UPGRADE CONFIG CAPBANK IEDS, REF545 | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029996739841.2409722222 | 10299967 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT HTS | 39841.241 | 39841.4028 | DAILY | 00004426 | SPIMAINT | Reblance Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029997139841.2409722222 | 10299971 | 10299967 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HTS | 39841.241 | 39841.4028 | DAILY | 00331019 | SPIMAINT | Rebate for Cap Bank outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027085539841.3493055556 | 10270855 |  | Parent | TRUE | LY 66/11KV S/S TRANS 'A' X PROT AT LYPA | 39841.3493 | 39841.5333 | CONT | [12 empty] | 0
_1027085739841.3493055556 | 10270857 | 10270855 | Child | FALSE | LY 66/11KV S/S TRANS 'A' Y PROT AT LYPA | 39841.3493 | 39841.5333 | CONT | [12 empty] | 0
_1030014139842.0319444445 | 10300141 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 39842.0319 | 39842.4417 | CONT | [12 empty] | 0
_1030014539842.0777777778 | 10300145 |  | Parent | FALSE | A1 515/230KV TRANS AT HWTS | 39842.0778 | 39842.3681 | CONT | 00009772 | FAULT | A1 515/230KV MAIN TRANS Tertiary Alarm | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030015039842.1423611111 | 10300150 |  | Parent | FALSE | KTS 500KV LINE AT SMTS | 39842.1424 | 39842.4187 | DAILY | 00012441 | FAULT | Remove defective red phase CVT after CAMS Alarm | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027085939842.2861111111 | 10270859 |  | Parent | TRUE | LY 66/11KV S/S TRANS 'B' X PROT AT LYPA | 39842.2861 | 39843.4076 | CONT | [12 empty] | 0
_1027086139842.2861111111 | 10270861 | 10270859 | Child | FALSE | LY 66/11KV S/S TRANS 'B' Y PROT AT LYPA | 39842.2861 | 39843.4076 | CONT | [12 empty] | 0
_1030015239842.3194444444 | 10300152 |  | Parent | FALSE | YPS NO.1 220KV LINE AT HWPS | 39842.3194 | 39842.3375 | DAILY | 00015795 | SW_NEM | NEMMCO reqested HWPS-YPS No1 220kV Line off load | NEMMCO |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1030017839842.5319444445 | 10300178 |  | Parent | FALSE | NO.1 CSC AT ROTS | 39842.5319 | 39842.5563 | DAILY | 00004718 | FAULT | ROTS: No 1 CSC Trip during Heatwave | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030022039842.9909722222 | 10300220 | 10300219 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 39842.991 | 39843.0743 | DAILY | 00015936 | FAULT | CVT Fault at JLGSB HWPS NO.1 220KV LINE AT JLT | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030022139842.9909722222 | 10300221 |  | Parent | FALSE | JLGB 220KV BUS AT JLGB | 39842.991 | 39843.3333 | CONT | 00325273 | FAULT | JLGSB CVT Fault | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030021939843.0173611111 | 10300219 |  | Parent | TRUE | NO.1 220KV BUS AT JLTS | 39843.0174 | 39843.0743 | DAILY | 00365901 | FAULT | CVT Fault at JLGSB NO.1 220KV BUS AT JLTS | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030025739843.4729166667 | 10300257 |  | Parent | FALSE | FBTS 220KV LINE CB AT NPSD | 39843.4729 | 39843.4743 | DAILY | [12 empty] | 0
_1030027439843.5916666667 | 10300274 |  | Parent | FALSE | KTS 500KV LINE AT SMTS | 39843.5917 | 39843.9931 | CONT | 00012441 | FAULT | SMTS-KTS 500KV Line Tripped CVT explosive failure | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030026939843.7090277778 | 10300269 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT SMTS | 39843.709 | 39843.9576 | CONT | 00012440 | FORCED | Outage of SYTS 2 500KV Line Collateral damage | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030026639843.99375 | 10300266 |  | Parent | TRUE | KTS 500KV LINE AT SMTS | 39843.9938 | 39844.6729 | CONT | 00012441 | FAULT | Install By-Pass in Bay "C" ROTS-SMTS-KTS | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030027739843.99375 | 10300277 | 10300266 | Child | FALSE | ROTS NO.3 500KV LINE AT SMTS | 39843.9938 | 39844.6729 | DAILY | 00012438 | FORCED | Bypass outage of SMTS-ROTS 3 Line | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030027839844.4791666667 | 10300278 |  | Parent | FALSE | NO.7 GEN TRANS LINE AT HWPS | 39844.4792 | 39845.4743 | CONT | 00356085 | GENCO | HWPS No7 Gen Trans Isols & SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030028839844.4791666667 | 10300288 |  | Parent | FALSE | NO.7 GEN 220/16.5KV TRANS AT HWPS | 39844.4792 | 39845.6458 | CONT | 00009648 | GENCO | SCAP: Isol'd & Earth'd for PS | GENCO |  |  | Connection Transformers | 3rd Party | 220 | NON SP ASSET | EXCLUDED |  | 0
_1030028439844.6729166667 | 10300284 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 39844.6729 | 39847.5951 | CONT | [12 empty] | 0
_1030029339845.1166666667 | 10300293 |  | Parent | FALSE | 2-4 500KV BUS TIE CB AT LYPS | 39845.1167 | 39845.1792 | CONT | [12 empty] | 0
_1010278939847.3895833333 | 10102789 |  | Parent | FALSE | JLTS NO.4 220KV LINE NO.3 BUS CB AT HWPS | 39847.3896 | 39847.5493 | CONT | [12 empty] | 0
_1027086339847.4076388889 | 10270863 |  | Parent | TRUE | LY 66/11KV S/S TRANS 'C' X PROT AT LYPA | 39847.4076 | 39848.4257 | CONT | [12 empty] | 0
_1027086539847.4076388889 | 10270865 | 10270863 | Child | FALSE | LY 66/11KV S/S TRANS 'C' Y PROT AT LYPA | 39847.4076 | 39848.4257 | CONT | [12 empty] | 0
_1029988439847.43125 | 10299884 |  | Parent | FALSE | NO.2 330KV CAPACITOR BANK AT WOTS | 39847.4313 | 39847.5563 | REPDAILY | 00354001 | SPIMAINT | Rebate W/o N0 2 CAP BANK CB during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_1029918839847.43125 | 10299188 |  | Parent | FALSE | STATION ALARMS AT WOTS | 39847.4313 | 39847.5568 | DAILY | [12 empty] | 0
_1030034839848.08125 | 10300348 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 39848.0813 | 39848.1306 | CONT | [12 empty] | 0
_1030031639848.2083333333 | 10300316 |  | Parent | FALSE | HWTS NO.2 500KV LINE AT SMTS | 39848.2083 | 39848.6931 | DAILY | 00012437 | SPIMAINT | replace damaged blue phase cvt | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X41258H839848.2611111111 | X41258H8 |  | Parent | FALSE | EX - DDTS 220KV LINE NO.1 TIE BUS CT R/PH AT SHTS | 39848.2611 | 39870.2917 | CONT | [12 empty] | 0
_1027054139848.2833333333 | 10270541 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT SMTS | 39848.2833 | 39848.734 | DAILY | 00001323 | SPIMAINT | No.3 S/S Transformer | SPIPOWER |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1026911339848.2944444444 | 10269113 |  | Parent | FALSE | ROTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 39848.2944 | 39848.5215 | CONT | [12 empty] | 0
_1030090439848.3090277778 | 10300904 | 10300358 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39848.309 | 39848.5799 | CONT | 00331118 | FAULT | BATS No2 Cap Bank 66kV CB Failed to Close | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030035839848.3090277778 | 10300358 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT BATS | 39848.309 | 39848.5805 | CONT | [12 empty] | 0
_1030067439848.6041666667 | 10300674 |  | Parent | FALSE | B1 220/66KV TRANS AT MWTS | 39848.6042 | 39848.6236 | CONT | 00351931 | FAULT | SMTS: Trip B3 Trans 66kV CB de-energises 66kV Bus | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1030039739848.6472222222 | 10300397 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT TTS | 39848.6472 | 39863.2708 | CONT | 00001533 | FAULT | B1 220/66KV TRANS AT TTS | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030039839849.2763888889 | 10300398 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 39849.2764 | 39849.7382 | DAILY | 00027386 | SPIMAINT | Replace leaking CVT at HYTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030059539849.3069444445 | 10300595 |  | Parent | FALSE | B1 220/66KV TRANS AT CBTS | 39849.3069 | 39849.3729 | DAILY | 00353076 | FORCED | SF6 Top up Transf 66KV CB | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1030040439849.3486111111 | 10300404 |  | Parent | FALSE | B1 TRANS 66KV CB AT CBTS | 39849.3486 | 39849.3729 | DAILY | [12 empty] | 0
_X72458A439849.5138888889 | X72458A4 |  | Parent | FALSE | EX - NO.1 66KV REACTOR AT HOTS | 39849.5139 | 39849.5474 | DAILY | 00006935 | SPICAPX | Instlla concrete poles adjacent to No1 Reactor | SPIPOWER | X724 | X724 - (HOTS) NO.1 SHUNT REACTOR REPLACEMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X72458A539850.3354166667 | X72458A5 |  | Parent | FALSE | EX - NO.1 66KV REACTOR AT HOTS | 39850.3354 | 39850.4625 | DAILY | 00006935 | SPICAPX | Install concrete poles adjacent to No1 Reactor | SPIPOWER | X724 | X724 - (HOTS) NO.1 SHUNT REACTOR REPLACEMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030044639851.28125 | 10300446 |  | Parent | FALSE | NO.7 GEN TRANS 220KV CB AT HWPS | 39851.2812 | 39857.3299 | CONT | [12 empty] | 0
_1032194139851.6486111111 | 10321941 |  | Parent | FALSE | BLLY 500KV LINE AT LYPS | 39851.6486 | 39851.6611 | DAILY | 00360516 | BUSHFIRE | Basslink trip coincident with Bunyip Bushfire trip | GENCO |  |  | Circuits | Eastern | 500 | CONNECTION ASSET | EXCLUDED |  | 3 | Bushfire tripped Basslink lines
_1030048039851.6493055556 | 10300480 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE AT HWTS | 39851.6493 | 39852.5958 | CONT | 00016237 | BUSHFIRE | Bushfires in Bunyip State Forrest at Labatouche | SPIPOWER |  |  | Circuits | 3rd Party | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3 | Bushfire tripped Basslink lines
_1030048539851.6777777778 | 10300485 |  | Parent | FALSE | EPS -TTS 2 220KV N | 39851.6778 | 39855.3493 | CONT | 00328508 | BUSHFIRE | Kinglake Bushfires EPS-TTS 220kV Line Trip | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM event as per SP AusNet's service performance review
_1030048139851.6798611111 | 10300481 |  | Parent | FALSE | DDTS-SMTS 1 330KV | 39851.6799 | 39856.6722 | CONT | 00328506 | BUSHFIRE | Kinglake Bushfires Failure of T493 at Strathewen | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM event as per SP AusNet's service performance review
_1030048239851.6819444445 | 10300482 |  | Parent | FALSE | SMTS NO.2 330KV LINE AT DDTS | 39851.6819 | 39851.684 | CONT | 00012356 | BUSHFIRE | Kinglake Bushfires Failure of T493 at Strathewen | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM event as per SP AusNet's service performance review
_1030048639851.6819444445 | 10300486 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT SMTS | 39851.6819 | 39852.375 | CONT | 00026101 | FAULT | Trip- SMTS-H1 Trans during 330KV Line trip | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030048339851.6854166667 | 10300483 |  | Parent | FALSE | SMTS NO.2 330KV LINE AT DDTS | 39851.6854 | 39854.8542 | CONT | 00012356 | BUSHFIRE | Kinglake Bushfires Failure of T493 at Strathewen | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM event as per SP AusNet's service performance review
_1030050039851.9868055556 | 10300500 |  | Parent | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 39851.9868 | 39852.475 | CONT | 00329970 | FAULT | Trans Off-Loaded -Loss of DDTS-GNTS Nos 1 & 3 Line | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030050139851.9868055556 | 10300501 |  | Parent | FALSE | DDTS-GNTS 1 220KV NW | 39851.9868 | 39852.475 | CONT | 00060184 | BUSHFIRE | Trip due to Bushfires in Myrtleford area | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM event as per SP AusNet's service performance review
_1030050239851.9868055556 | 10300502 |  | Parent | FALSE | DDTS-GNTS 3 220KV NW | 39851.9868 | 39852.4764 | CONT | 00060186 | BUSHFIRE | Trip due to Bushfire in Myrtleford area | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM event as per SP AusNet's service performance review
_1030049839852.0111111111 | 10300498 |  | Parent | FALSE | DDTS-SHTS 220KV NW | 39852.0111 | 39852.0715 | DAILY | 00352425 | FAULT | DDTS: Prot Trip of SHTS Line at DDTS | SPIPOWER |  |  | Circuits | 3rd Party | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030050339852.0111111111 | 10300503 |  | Parent | FALSE | SHTS 220KV LINE CB AT DDTS | 39852.0111 | 39852.0715 | DAILY | [12 empty] | 0
_1030050439852.4388888889 | 10300504 |  | Parent | FALSE | NO.8 22KV/415V S/S TRANS AT SMTS | 39852.4389 | 39852.7153 | DAILY | 00001327 | DBPROX | VSCAP to DOC | DISTCO |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1030050539852.6104166667 | 10300505 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 39852.6104 | 39857.3125 | CONT | [12 empty] | 0
_1030051139853.0305555556 | 10300511 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT EPSY | 39853.0306 | 39855.775 | CONT | 00087035 | SW_NEM | NEMMCO requested EPS-MBTS No1 220KV Line off load | NEMMCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 3
_1030051539853.2451388889 | 10300515 |  | Parent | FALSE | B4 220/66KV TRANS AT ATS | 39853.2451 | 39870.5743 | CONT | 00363708 | FAULT | Tertiary Bushing failure B4 220/66KV Trans at ATS | SPIPOWER |  |  | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1030045039853.2534722222 | 10300450 |  | Parent | FALSE | BTS 220KV LINE AT RTS | 39853.2535 | 39853.3965 | DAILY | 00021222 | SPIMAINT | Scan for oil leak on Tyree CVT at RTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030051939853.3333333333 | 10300519 |  | Parent | FALSE | DDTS NO.1 330KV LINE NO.1 BUS CB AT SMTS | 39853.3333 | 39853.5312 | DAILY | [12 empty] | 0
_1029988339854.3125 | 10299883 |  | Parent | FALSE | B2 220/66KV TRANS AT HTS | 39854.3125 | 39854.559 | DAILY | 00004446 | SPIMAINT | Repair Pump | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030054239855.2708333333 | 10300542 |  | Parent | FALSE | JLGS B 220KV LINE CT R/PH AT JLTS | 39855.2708 | 39855.5535 | DAILY | [12 empty] | 0
_Z64558D139855.2902777778 | Z64558D1 |  | Parent | FALSE | EX - TGTS 220KV LINE NO.2 TIE CT R/PH AT BATS | 39855.2903 | 39856.4868 | CONT | [12 empty] | 0
_1030043039855.2951388889 | 10300430 |  | Parent | TRUE | NO.4 66KV CAPACITOR BANK CB AT RTS | 39855.2951 | 39855.3271 | DAILY | [12 empty] | 0
_1030044839855.2951388889 | 10300448 | 10300430 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT RTS | 39855.2951 | 39855.3271 | DAILY | 00055373 | SPIMAINT | rebate outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030061639855.2986111111 | 10300616 |  | Parent | FALSE | NO.4 220KV BUS AT FBTS | 39855.2986 | 39855.3264 | CONT | 00002736 | FAULT | Tripping of No4 220kV Bus | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030064739855.2986111111 | 10300647 |  | Parent | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 39855.2986 | 39855.3264 | CONT | 00327661 | FAULT | Tripping of No4 220kV Bus | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030064839855.2986111111 | 10300648 |  | Parent | FALSE | B4 220/66KV TRANS AT FBTS | 39855.2986 | 39855.3264 | CONT | 00002728 | FAULT | Tripping of No4 220kV Bus | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030065239855.2986111111 | 10300652 |  | Parent | FALSE | NPSD 220KV LINE AT FBTS | 39855.2986 | 39855.3264 | CONT | 00002662 | FAULT | Tripping of No4 220kV Bus | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030065439855.2986111111 | 10300654 |  | Parent | FALSE | WMTS-FBTS 1 220KV WY | 39855.2986 | 39855.3264 | CONT | 00022785 | FAULT | Tripping of No4 220kV Bus | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1030037939855.3138888889 | 10300379 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39855.3139 | 39855.3444 | DAILY | 00329879 | SPIMAINT | No4 cap bk CB low oil dashpot | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030059939855.3493055556 | 10300599 |  | Parent | FALSE | EPS 220KV LINE AT TTS | 39855.3493 | 39855.7028 | DAILY | 00015730 | SPIMAINT | Proximity reasons for tower rebuild | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030063839855.6104166667 | 10300638 |  | Parent | FALSE | YPS -ROTS 6 220KV G | 39855.6104 | 39855.7486 | CONT | 00020488 | FAULT | Trip YPS-ROTS No 6 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030066539856.1819444445 | 10300665 |  | Parent | FALSE | ROTS NO.6 220KV LINE AT YPS | 39856.1819 | 39856.3576 | DAILY | 00016414 | FAULT | Trip YPS-ROTS No 6 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030067739856.2729166667 | 10300677 |  | Parent | FALSE | ATS 66KV LINE AT BLTS | 39856.2729 | 39856.659 | CONT | 00017843 | DBPROX | De-energised for PowerCor (Pole fire) | DISTCO |  |  | Circuits | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029783939856.29375 | 10297839 |  | Parent | FALSE | NO.7 GEN TRANS 220KV CB CT R/PH AT HWPS | 39856.2937 | 39856.3465 | DAILY | [12 empty] | 0
_1029721539856.2944444444 | 10297215 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 39856.2944 | 39856.5111 | DAILY | [12 empty] | 0
_1030059739856.3548611111 | 10300597 |  | Parent | FALSE | DDTS NO.2 330KV LINE AT SMTS | 39856.3549 | 39856.6354 | DAILY | 00012750 | BUSHFIRE | Kinglake Bushfires Rebuild of T493 at Strathewen | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM event as per SP AusNet's service performance review
_1030069739856.9833333333 | 10300697 |  | Parent | FALSE | DDTS NO.1 330KV LINE SERIES CAPACITOR BANK AT SMTS | 39856.9833 | 39857.0556 | DAILY | 00327836 | FAULT | SMTS NO1 330KV SERIES CAP Failed Cap Cans | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 4
_1030073539857.2263888889 | 10300735 |  | Parent | FALSE | DDTS NO.1 330KV LINE SERIES CAPACITOR BANK AT SMTS | 39857.2264 | 39993.6368 | CONT | 00327836 | FAULT | SMTS NO1 330KV SERIES CAP Failed Cap Cans | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 4
_1030068339857.2409722222 | 10300683 |  | Parent | FALSE | YWPS NO.3 220KV LINE AT YPS | 39857.241 | 39862.2292 | CONT | 00016426 | GENCO | SCAP to Genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029870639857.2791666667 | 10298706 |  | Parent | FALSE | LYPS NO.2 LINE/ROTS NO.3 LINE 500KV CB AT HWTS | 39857.2792 | 39857.4472 | DAILY | [12 empty] | 0
_1030073839858.2951388889 | 10300738 |  | Parent | FALSE | DDTS NO.1 330KV LINE AT SMTS | 39858.2951 | 39858.6056 | REPDAILY | 00012749 | SPIMAINT | outage for proximity for work on series cap | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030078039858.7465277778 | 10300780 |  | Parent | FALSE | DDTS NO.2 330KV LINE NO.1 BUS CB AT SMTS | 39858.7465 | 39858.7646 | CONT | [12 empty] | 0
_1030200639858.7472222222 | 10302006 |  | Parent | FALSE | H1 330/220KV TRANS R/PH AT SMTS | 39858.7472 | 39858.7535 | DAILY | 00001310 | FORCED | Forced Outage of No 1 330kV Bus/H1 Tr at SMTS | SPIPOWER |  |  | Main Transformers | 3rd Party | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030200739858.7541666667 | 10302007 |  | Parent | FALSE | DDTS NO.1 330KV LINE AT SMTS | 39858.7542 | 39858.759 | DAILY | 00012749 | FORCED | Forced Outage of DDTS-SMTS No 1 330kV Line | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358CB39859.2472222222 | Z51358CB |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39859.2472 | 39859.7493 | CONT | 00007452 | DB_AUG | No 3 220/22kv trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029988739859.2777777778 | 10299887 |  | Parent | FALSE | WD 66KV FDR CB AT TSTS | 39859.2778 | 39859.4806 | DAILY | [12 empty] | 0
_1030073839859.2916666667 | 10300738 |  | Parent | FALSE | DDTS NO.1 330KV LINE AT SMTS | 39859.2917 | 39859.5569 | REPDAILY | 00012749 | SPIMAINT | outage for proximity for work on series cap | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029961239859.3958333333 | 10299612 |  | Parent | FALSE | NO.2 22KV BUS AT RWTS | 39859.3958 | 39859.4042 | DAILY | 00007483 | SPIMAINT | Commission Cap Bank CB | SPIPOWER |  |  | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1030079839860.3625 | 10300798 |  | Parent | FALSE | B1 TRANS 66KV CB AT CBTS | 39860.3625 | 39860.3681 | DAILY | [12 empty] | 0
_1030082639860.3625 | 10300826 |  | Parent | FALSE | B1 220/66KV TRANS AT CBTS | 39860.3625 | 39860.3681 | DAILY | 00353076 | FORCED | Outage of B1 Trans at CBTS for CB SF6 top up | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1030082239860.4173611111 | 10300822 |  | Parent | FALSE | RWTS 220KV LINE AT TTS | 39860.4174 | 39860.5083 | DAILY | 00015734 | FAULT | TTS-RWTS 220kV Line Trip. | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030086839860.4201388889 | 10300868 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39860.4201 | 39860.5667 | DAILY | 00112417 | FAULT | Outage of ROTS No 3 220kV Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X7F858G139861.2576388889 | X7F858G1 |  | Parent | FALSE | B3A 220/66KV TRANS BANK AT BLTS | 39861.2576 | 39861.6493 | DAILY | 00018491 | SPICAPX | replace 66kv trans surge diverters | SPIPOWER | X7F8 | X7F8 - REPLACE AGEING 66KV - 330KV SURGE ARRESTERS | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029870739861.2743055556 | 10298707 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB AT HWTS | 39861.2743 | 39861.6597 | DAILY | [12 empty] | 0
_1030071839861.3041666667 | 10300718 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT HYTS | 39861.3042 | 39861.6181 | DAILY | 00331066 | DBPROX | VSCAP to Powercor | DISTCO |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1030089439861.5118055556 | 10300894 |  | Parent | FALSE | EX - JLGA 220KV BUS CVT R/PH AT JLGA | 39861.5118 | 39861.5174 | DAILY | [12 empty] | 0
_1030174839861.5118055556 | 10301748 |  | Parent | FALSE | HWPS NO.2 220KV LINE AT JLTS | 39861.5118 | 39861.5208 | DAILY | 00015937 | FAULT | TRIP NO2 220KV BUS JLTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030174939861.6215277778 | 10301749 |  | Parent | FALSE | HWPS NO.2 220KV LINE AT JLTS | 39861.6215 | 39861.6229 | DAILY | 00015937 | FORCED | Rebate Bus outage to restore JLGS A Line at JLTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7F858G239862.2513888889 | X7F858G2 |  | Parent | FALSE | B3A 220/66KV TRANS BANK AT BLTS | 39862.2514 | 39862.6465 | DAILY | 00018491 | SPICAPX | replace 66kv surge diverters at the rack structure | SPIPOWER | X7F8 | X7F8 - REPLACE AGEING 66KV - 330KV SURGE ARRESTERS | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029999339862.3083333333 | 10299993 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 39862.3083 | 39862.5479 | DAILY | 00022690 | APDALCOA | SCAP to PTH | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X7F858G439862.3395833333 | X7F858G4 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT BLTS | 39862.3396 | 39862.6229 | DAILY | [12 empty] | 0
_1029870839862.3444444445 | 10298708 |  | Parent | FALSE | LYPS NO.3 500KV LINE NO.4 BUS CB AT HWTS | 39862.3444 | 39862.4688 | DAILY | [12 empty] | 0
_Z64558B939863.2291666667 | Z64558B9 |  | Parent | FALSE | WBTS 220KV LINE NO.1 BUS CB AT HOTS | 39863.2292 | 39867.7688 | CONT | [12 empty] | 0
_V91058A139863.2708333333 | V91058A1 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT TTS | 39863.2708 | 39864.3221 | CONT | 00001533 | SPIMAINT | disconnect trans from all sources of supply | SPIPOWER | V910 | V910 - (TTS) INVESTIGATE & REPAIR - FAIL B1 TRANSFORMER | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029870939863.2798611111 | 10298709 |  | Parent | FALSE | LYPS NO.3 LINE/CBTS NO.4 LINE 500KV CB AT HWTS | 39863.2799 | 39863.2951 | DAILY | [12 empty] | 0
_Z64558D339863.3048611111 | Z64558D3 |  | Parent | FALSE | B1 TRANS 66KV CB LINE SIDE ISOL AT WBTS | 39863.3049 | 39863.4583 | DAILY | [12 empty] | 0
_1030067939863.3131944445 | 10300679 |  | Parent | FALSE | HWPS NO.3 220KV LINE NO.2 BUS CB AT JLTS | 39863.3132 | 39863.4028 | DAILY | [12 empty] | 0
_1030071939863.3243055556 | 10300719 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT HYTS | 39863.3243 | 39863.55 | DAILY | 00331066 | DBPROX | VSCSAP to PowerCor | DISTCO |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1030087039863.5068171296 | 10300870 |  | Parent | FALSE | B1 TRANS 220KV CB AT TTS | 39863.5068 | 39903.5083 | CONT | [12 empty] | 0
_1030068039863.5173611111 | 10300680 |  | Parent | FALSE | LY NO.4 66KV FDR NO.3 BUS CB AT MWTS | 39863.5174 | 39863.5694 | DAILY | [12 empty] | 0
_Z64558C639863.5291666667 | Z64558C6 |  | Parent | FALSE | B2 220/66KV TRANS AT WBTS | 39863.5292 | 39911.6132 | CONT | 00366200 | VEN_AUG | Install and commission future B2 Trans and equip | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1030097639863.6993055556 | 10300976 |  | Parent | TRUE | DPS 220KV LINE CB AT MBTS | 39863.6993 | 39864.4417 | CONT | [12 empty] | 0
_1030169839863.6993055556 | 10301698 | 10300976 | Child | FALSE | DPS -MBTS 220KV NW | 39863.6993 | 39864.4417 | CONT | 00060195 | STHHYDRO | DPS 220kV Line de-energised for P/Stn | STHHYDRO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z64558B739864.2138888889 | Z64558B7 |  | Parent | FALSE | EX - BATS-HOTS 220KV W | 39864.2139 | 39867.7688 | CONT | 00026089 | VEN_AUG | Out W/O BATS-HOTS Line to cut in WBTS | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858M039864.2222222222 | X50858M0 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 39864.2222 | 39865.1875 | CONT | 00002829 | SPICAPX | Out W/O B3 Trans - Install future equipment | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029870539864.275 | 10298705 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 39864.275 | 39864.5271 | DAILY | [12 empty] | 0
_V91058A239864.3225115741 | V91058A2 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT TTS | 39864.3225 | 39903.625 | CONT | 00001533 | SPIMAINT | Maintain Isolations on out of Commisiion B1 Trans | SPIPOWER | V910 | V910 - (TTS) INVESTIGATE & REPAIR - FAIL B1 TRANSFORMER | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029856639865.1875 | 10298566 | X50858M3 | Child | FALSE | B3 220/66KV TRANS AT GTS | 39865.1875 | 39865.7424 | DAILY | 00002829 | SPICAPX | Perf Calc B3 Trans during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858M339865.1875 | X50858M3 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39865.1875 | 39865.7424 | DAILY | 00002833 | SPICAPX | Instal No1 220kv Bus Exten and B3 Trans Conn's | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858M439865.1875 | X50858M4 | X50858M3 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 39865.1875 | 39865.7424 | DAILY | 00366646 | SPICAPX | Rebate W/O MLTS 2 Line during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858M539865.1875 | X50858M5 | X50858M3 | Child | FALSE | KTS NO.2 220KV LINE AT GTS | 39865.1875 | 39865.7424 | DAILY | 00367295 | SPICAPX | Rebate W/O KTS 2 Line during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858M639865.1875 | X50858M6 | X50858M3 | Child | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39865.1875 | 39865.7424 | DAILY | 00017906 | SPICAPX | Rebate W/O PTH 2 Line during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029875139865.2201388889 | 10298751 |  | Parent | TRUE | 66KV CAPACITOR BANK CB AT TGTS | 39865.2201 | 39865.6847 | DAILY | [12 empty] | 0
_1029875239865.2201388889 | 10298752 | 10298751 | Child | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39865.2201 | 39865.6847 | DAILY | 00003104 | SPIMAINT | Rebate W/O No1 66kV Cap bank during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027285739865.2465277778 | 10272857 |  | Parent | TRUE | LY NO.2 66KV FDR CB AT MWTS | 39865.2465 | 39865.4896 | DAILY | [12 empty] | 0
_1030170439865.2465277778 | 10301704 | 10272857 | Child | FALSE | LY NO.2 66KV FDR AT MWTS | 39865.2465 | 39865.4896 | DAILY | 00016141 | SPIMAINT | REBATE FOR CB OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558G939865.25 | X56558G9 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT DDTS | 39865.25 | 39865.5771 | CONT | 00012361 | SPICAPX | Out W/O MBTS 1 Line for CB CT replacement | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358CD39865.2506944445 | Z51358CD |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39865.2507 | 39865.6667 | CONT | 00007452 | DB_AUG | No 3 220/22kv trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027025439865.2597222222 | 10270254 |  | Parent | FALSE | L2 TRANS 22KV CB AT BLTS | 39865.2597 | 39866.4764 | CONT | [12 empty] | 0
_X50858P239865.5333333333 | X50858P2 |  | Parent | FALSE | EX - WPD 66KV FDR CB AT GTS | 39865.5333 | 39872.2083 | CONT | [12 empty] | 0
_1029875339865.6763888889 | 10298753 |  | Parent | TRUE | NO.1 66KV BUS AT TGTS | 39865.6764 | 39865.684 | DAILY | 00364790 | SPIMAINT | No1 66kV Bus de-energised for No1 Cap CB commiss | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029875439865.6763888889 | 10298754 | 10298753 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 39865.6764 | 39865.684 | DAILY | 00363297 | SPIMAINT | Perf calc W/O B1 Trans during #1 66 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030090339865.7423611111 | 10300903 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 39865.7424 | 39866.2083 | CONT | 00002829 | SPICAPX | HVS B3 Trans | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858M739866.2083333333 | X50858M7 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39866.2083 | 39866.6743 | DAILY | 00002833 | SPICAPX | Instal No1 220kv Bus Exten and B3 Trans Conn's | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858M839866.2083333333 | X50858M8 | X50858M7 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 39866.2083 | 39866.6743 | DAILY | 00366646 | SPICAPX | Rebate for MLTS 2 Line during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858M939866.2083333333 | X50858M9 | X50858M7 | Child | FALSE | KTS NO.2 220KV LINE AT GTS | 39866.2083 | 39866.6743 | DAILY | 00367295 | SPICAPX | Rebate for KTS 2 Line during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858N039866.2083333333 | X50858N0 | X50858M7 | Child | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39866.2083 | 39866.6743 | DAILY | 00017906 | SPICAPX | Rebate for PTH 2 Line during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858N139866.2083333333 | X50858N1 | X50858M7 | Child | FALSE | B3 220/66KV TRANS AT GTS | 39866.2083 | 39866.6743 | DAILY | 00002829 | SPICAPX | Perf Calc for B3 Trans during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030097039866.2166666667 | 10300970 |  | Parent | TRUE | EX - NO.1 220KV BUS CVT W/PH AT JLTS | 39866.2167 | 39866.5597 | DAILY | [12 empty] | 0
_1030170539866.2166666667 | 10301705 | 10300970 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 39866.2167 | 39866.5597 | DAILY | 00015936 | SPIMAINT | REBATE FOR BUS OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027285939866.2319444444 | 10272859 |  | Parent | TRUE | LY NO.1 66KV FDR CB AT MWTS | 39866.2319 | 39866.5312 | DAILY | [12 empty] | 0
_1028372339866.2319444444 | 10283723 | 10272859 | Child | FALSE | LY NO.1 66KV FDR CB AT MWTS | 39866.2319 | 39866.5312 | DAILY | [12 empty] | 0
_1030100939866.7395833333 | 10301009 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39866.7396 | 39867.1028 | CONT | 00356082 | GENCO | Isolation for generator | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7F858G339868.2277777778 | X7F858G3 |  | Parent | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 39868.2278 | 39870.6514 | CONT | 00329970 | SPICAPX | GNTS No1Trans bk 220kV & 330kV S/D replacement | SPIPOWER | X7F8 | X7F8 - REPLACE AGEING 66KV - 330KV SURGE ARRESTERS | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030071539868.2583333333 | 10300715 |  | Parent | FALSE | CBTS NO.2 220KV LINE AT TBTS | 39868.2583 | 39868.4146 | DAILY | 00018364 | SPIMAINT | Check CVT oil leak | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030089339868.3125 | 10300893 |  | Parent | FALSE | WD 66KV FDR CB AT TSTS | 39868.3125 | 39868.5799 | DAILY | [12 empty] | 0
_1030101839868.3291666667 | 10301018 |  | Parent | TRUE | B1 TRANS 66KV CB AT CBTS | 39868.3292 | 39868.3604 | DAILY | [12 empty] | 0
_1030102939868.3291666667 | 10301029 | 10301018 | Child | FALSE | B1 220/66KV TRANS AT CBTS | 39868.3292 | 39868.3604 | DAILY | 00353076 | SPIMAINT | Rebate Tran for CB outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1029999639869.2638888889 | 10299996 |  | Parent | FALSE | NO.4 TRANS 66KV CB AT BLTS | 39869.2639 | 39869.6979 | DAILY | [12 empty] | 0
_1030087239869.2708333333 | 10300872 |  | Parent | FALSE | EX - BLTS 220KV LINE NO.2 BUS CB AT KTS | 39869.2708 | 39869.6181 | DAILY | [12 empty] | 0
_1030110539869.8645833333 | 10301105 |  | Parent | FALSE | B2 220/66KV TRANS AT TTS | 39869.8646 | 39870.0674 | DAILY | 00362454 | SPIMAINT | condition monitoring tests | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z73058H039870.2083333333 | Z73058H0 |  | Parent | FALSE | DDTS NO.2 330KV LINE AT SMTS | 39870.2083 | 39870.4306 | DAILY | 00012750 | DB_AUG | auto reclose checks | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030115339870.4215277778 | 10301153 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 39870.4215 | 39870.4382 | DAILY | 00002830 | FAULT | B4 Transf Off Load due to Loss of No4 66kV Bus | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030115439870.4215277778 | 10301154 |  | Parent | FALSE | NO.4 66KV BUS AT GTS | 39870.4215 | 39870.4382 | DAILY | 00002838 | FAULT | Loss of No4 66kV Bus at GTS due to CT cable fault | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030111439871.2111111111 | 10301114 |  | Parent | TRUE | MLTS NO.2 500KV LINE CB AT HYTS | 39871.2111 | 39871.2292 | DAILY | [12 empty] | 0
_1030111539871.2111111111 | 10301115 | 10301114 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 39871.2111 | 39871.2292 | DAILY | 00002862 | SPIMAINT | Rebate W/O M2 Trans during MLTS 2L 2B CB outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030088039871.25 | 10300880 |  | Parent | FALSE | B3 220/66KV TRANS AT FBTS | 39871.25 | 39871.3986 | DAILY | 00002727 | SPIMAINT | replace repaired fan | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030087439871.2555555556 | 10300874 |  | Parent | FALSE | EX - ATS LINE/A2 TRANS 220KV CB AT KTS | 39871.2556 | 39871.625 | DAILY | [12 empty] | 0
_1029896939872.1888888889 | 10298969 | Z56258B0 | Child | FALSE | DDTS NO.1 220KV LINE AT MBTS | 39872.1889 | 39872.7778 | DAILY | 00364622 | VEN_AUG | Rebate W/O DDTS No1 Line during No2 220 Bus outage | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z56258B039872.1888888889 | Z56258B0 |  | Parent | TRUE | NO.2 220KV BUS AT MBTS | 39872.1889 | 39872.7778 | DAILY | 00364503 | VEN_AUG | OUT W/O No2 220kV Bus to connect new bays C & B | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z56258B139872.1888888889 | Z56258B1 | Z56258B0 | Child | FALSE | EPS NO.1 220KV LINE AT MBTS | 39872.1889 | 39872.7778 | DAILY | 00364630 | VEN_AUG | Rebate W/O EPS No1 Line during No2 220 Bus outage | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z56258B239872.1888888889 | Z56258B2 | Z56258B0 | Child | FALSE | DPS 220KV LINE AT MBTS | 39872.1889 | 39872.7778 | DAILY | 00011754 | VEN_AUG | Rebate W/O DPS Line during No2 220 Bus outage | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858P839872.2083333333 | X50858P8 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39872.2083 | 39873.2132 | CONT | 00017900 | SPICAPX | W/O KTS No1 Ln for prep to cut over to new CB | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858O839872.2118055556 | X50858O8 |  | Parent | TRUE | NO.3 66KV BUS AT GTS | 39872.2118 | 39872.6694 | DAILY | 00002837 | SPICAPX | Out WO No3 66kv Bus to connect new BCG Fdr | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858O939872.2118055556 | X50858O9 | X50858O8 | Child | FALSE | B3 220/66KV TRANS AT GTS | 39872.2118 | 39872.6694 | DAILY | 00002829 | SPICAPX | Rebate WO B3 Trans during No3 Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026914439872.2291666667 | 10269144 |  | Parent | FALSE | HWTS NO.3 220KV LINE NO.3 BUS CB AT HWPS | 39872.2292 | 39873.5729 | CONT | 00009610 | SPIMAINT | CL.1 O/HAUL - BTH JW419 & JW420 CB | SPIPOWER | [8 empty] | 0 | 10269144 |  | CL.1 O/HAUL - BTH JW419 & JW420 CB | 00009610 | CB |  | HWPS | CB | SPIMAINT | CONT
_1029904839872.2298611111 | 10299048 | 10296472 | Child | FALSE | HWPS-HWTS 3 220KV G | 39872.2299 | 39872.5368 | DAILY | 00020333 | SPIMAINT | TX REBATE FOR ISOL OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z51358CE39872.2493055556 | Z51358CE |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39872.2493 | 39872.7889 | DAILY | 00007452 | DB_AUG | No 3 220/22kv trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X87058B239872.25625 | X87058B2 |  | Parent | FALSE | MLTS-BATS 1 220KV WY | 39872.2562 | 39872.6917 | REPDAILY | 00022728 | SPICAPX | MLTS-BATS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027329339872.2597222222 | 10273293 |  | Parent | FALSE | 2B-4 220KV BUS TIE CB CT R/PH AT BLTS | 39872.2597 | 39872.3639 | DAILY | [12 empty] | 0
_1027330139872.3875 | 10273301 |  | Parent | FALSE | EX - 3-4 220KV BUS TIE CB CT R/PH AT FBTS | 39872.3875 | 39872.4493 | DAILY | [12 empty] | 0
_1030103539872.78125 | 10301035 |  | Parent | FALSE | WKPS 220KV LINE NO.1 BUS CB AT MBTS | 39872.7812 | 39873.2271 | CONT | [12 empty] | 0
_X50858P339873.2131944445 | X50858P3 |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 39873.2132 | 39873.7299 | DAILY | 00002834 | SPICAPX | Pre comm and test KTS No1 Line equipment | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858P439873.2131944445 | X50858P4 | X50858P3 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39873.2132 | 39873.7299 | DAILY | 00002830 | SPICAPX | Rebate W/O B4 Trans during No2 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858P539873.2131944445 | X50858P5 | X50858P3 | Child | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39873.2132 | 39873.7299 | DAILY | 00017905 | SPICAPX | Rebate W/O PTH No1 Ln for No2 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858P639873.2131944445 | X50858P6 | X50858P3 | Child | FALSE | EX - MLTS NO.1 220KV LINE AT GTS | 39873.2132 | 39873.7299 | DAILY | 00017903 | SPICAPX | Rebate W/O MLTS No1 Ln for No2 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858P739873.2131944445 | X50858P7 | X50858P3 | Child | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39873.2132 | 39873.7299 | DAILY | 00017900 | SPICAPX | Rebate W/O KTS No1 Ln for No2 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z56258B339873.2229166667 | Z56258B3 |  | Parent | FALSE | WKPS 220KV LINE AT MBTS | 39873.2229 | 39873.7083 | DAILY | 00011756 | VEN_AUG | OUT W/O WKPS Line to connect new No2 Bus CB | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058B239873.25 | X87058B2 |  | Parent | FALSE | MLTS-BATS 1 220KV WY | 39873.25 | 39873.6007 | REPDAILY | 00022728 | SPICAPX | MLTS-BATS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858O639873.2708333333 | X50858O6 |  | Parent | FALSE | KTS NO.2 220KV LINE CB AT GTS | 39873.2708 | 39886.25 | CONT | [12 empty] | 0
_V81158A839873.3555555556 | V81158A8 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39873.3556 | 39873.8007 | DAILY | 00003104 | SPIMAINT | Out W/O No1 66kV Cap bank prot setting changes | SPIPOWER | V811 | V811 - COST EST - UPGRADE CONFIG CAPBANK IEDS, REF545 | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z56258B539873.7291666667 | Z56258B5 |  | Parent | FALSE | WKPS 220KV LINE NO.1 BUS CB AT MBTS | 39873.7292 | 39878.559 | CONT | [12 empty] | 0
_X50858O539873.7298611111 | X50858O5 |  | Parent | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39873.7299 | 39874.5938 | CONT | 00017900 | SPICAPX | Pre commiss checks and commission new equip | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030101339875.2583333333 | 10301013 |  | Parent | FALSE | B2 220/66KV TRANS AT KTS | 39875.2583 | 39875.6153 | DAILY | 00001148 | SPIMAINT | replace repaired fan & remove noisy one | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658A239875.2736111111 | X70658A2 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT KTS | 39875.2736 | 39875.3465 | DAILY | 00026096 | SPICAPX | cut away cable tray-outage for vibration | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X87558A139875.2756944445 | X87558A1 |  | Parent | FALSE | NO.4B 66KV BUS AT WMTS | 39875.2757 | 39875.666 | DAILY | 00351982 | SPICAPX | replace / fit new gis inspection windows - day 2 | SPIPOWER | X875 | X875 - (WMTS) INSTALL VIEWING WINDOWS & CAMERAS ON 66KV GIS | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029946639875.2916666667 | 10299466 |  | Parent | FALSE | B2 220/66KV TRANS AT RWTS | 39875.2917 | 39878.5576 | CONT | 00007450 | SPIMAINT | REPAIR OIL LEAKS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030136439875.9430555556 | 10301364 |  | Parent | FALSE | HWPS-JLTS 2 220KV G | 39875.9431 | 39876.0583 | CONT | 00020443 | REM_TRIP | Rem Trip from GENCO for SD failure at JLGS P/Stn | GENCO |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030134939875.9631944445 | 10301349 |  | Parent | FALSE | NO.4 66KV BUS AT MWTS | 39875.9632 | 39876.4514 | CONT | 00010281 | FORCED | No4 66kV Bus Isolated due to pole fire at MWTS | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030135439876.0763888889 | 10301354 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS 220KV SD R/PH AT JLGA | 39876.0764 | 39877.625 | CONT | [12 empty] | 0
_X87558A039876.2541666667 | X87558A0 |  | Parent | FALSE | NO.4B 66KV BUS AT WMTS | 39876.2542 | 39876.6069 | DAILY | 00351982 | SPICAPX | replace / fit new gis inspection windows - day 1 | SPIPOWER | X875 | X875 - (WMTS) INSTALL VIEWING WINDOWS & CAMERAS ON 66KV GIS | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030101739876.2979166667 | 10301017 |  | Parent | FALSE | EX - A2 TRANS NO.2 BUS 220KV CB AT KTS | 39876.2979 | 39876.6271 | DAILY | [12 empty] | 0
_1030145439876.9125 | 10301454 |  | Parent | FALSE | WBTS 220KV LINE AT BATS | 39876.9125 | 39876.9187 | CONT | 00012410 | FAULT | WBTS 220kV Line Tripped incorrect relay setting | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030145339876.9125 | 10301453 |  | Parent | FALSE | B1 220/66KV TRANS AT WBTS | 39876.9125 | 39876.9375 | CONT | 00366199 | FAULT | WBTS B1 Trans Tripped unregulated | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1030145539876.9125 | 10301455 |  | Parent | FALSE | LYPS NO.1 500KV LINE AT HWTS | 39876.9125 | 39877.8715 | CONT | 00016234 | BUSHFIRE | Insul Flashover HWTS due Black Rain from Bushfires | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030118539877.1479166667 | 10301185 |  | Parent | FALSE | LYBPS NO.1 500KV LINE AT LYPS | 39877.1479 | 39880.6458 | CONT | 00023074 | GENCO | SCAP to LYPS B | GENCO |  |  | Circuits | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_X87558A239877.2520833333 | X87558A2 |  | Parent | FALSE | NO.4B 66KV BUS AT WMTS | 39877.2521 | 39877.6264 | DAILY | 00351982 | SPICAPX | replace / fit new gis inspection windows - day 3 | SPIPOWER | X875 | X875 - (WMTS) INSTALL VIEWING WINDOWS & CAMERAS ON 66KV GIS | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030102039877.25625 | 10301020 |  | Parent | FALSE | EX - ATS 220KV LINE NO.1 BUS CB AT KTS | 39877.2562 | 39877.5833 | DAILY | [12 empty] | 0
_1030128339877.2708333333 | 10301283 |  | Parent | TRUE | B1 TRANS 66KV CB AT CBTS | 39877.2708 | 39877.4326 | DAILY | [12 empty] | 0
_1030128439877.2708333333 | 10301284 | 10301283 | Child | FALSE | B1 220/66KV TRANS AT CBTS | 39877.2708 | 39877.4326 | CONT | 00353076 | FORCED | SF6 Top up Transf 66KV CB | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1030099439877.4861111111 | 10300994 |  | Parent | FALSE | WD 66KV FDR CB AT TSTS | 39877.4861 | 39877.5764 | DAILY | [12 empty] | 0
_1030171839877.9534722222 | 10301718 |  | Parent | FALSE | LYPS NO.1 500KV LINE AT HWTS | 39877.9535 | 39878.0382 | CONT | 00016234 | FAULT | LYPS No1 500kV Line CB low oil pressure alarm | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87558A439878.2416666667 | X87558A4 |  | Parent | FALSE | NO.4A 66KV BUS AT WMTS | 39878.2417 | 39878.4715 | DAILY | 00351981 | SPICAPX | replace / fit new gis inspection windows - day 5 | SPIPOWER | X875 | X875 - (WMTS) INSTALL VIEWING WINDOWS & CAMERAS ON 66KV GIS | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1026899739878.2798611111 | 10268997 |  | Parent | FALSE | NO.4 66KV BUS AT MWTS | 39878.2799 | 39878.6014 | DAILY | 00010281 | SPIMAINT | O/Haul NO.4 66KV BUS AT MWTS | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030323339878.4041666667 | 10303233 |  | Parent | FALSE | WKPS 220KV LINE AT MBTS | 39878.4042 | 39878.534 | DAILY | 00011756 | FAULT | Rebate - Trip of line during on load tests. | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030156739878.5888888889 | 10301567 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 39878.5889 | 39878.6257 | DAILY | [12 empty] | 0
_1030157739878.9319444445 | 10301577 |  | Parent | FALSE | LYPS-HWTS 1 500KV G | 39878.9319 | 39879.7076 | CONT | 00020318 | FORCED | NEMMCO directed Line off recurring Y Prot alarms | NEMMCO |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029785539879.2354166667 | 10297855 |  | Parent | FALSE | NO.1 220KV TRANS BUS CB CT R/PH AT WMTS | 39879.2354 | 39879.3257 | DAILY | [12 empty] | 0
_V81158A939879.3020833333 | V81158A9 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT HOTS | 39879.3021 | 39879.9146 | DAILY | 00359898 | SPIMAINT | Out W/O 1A & 1B 66kV Cap bank prot setting changes | SPIPOWER | V811 | V811 - COST EST - UPGRADE CONFIG CAPBANK IEDS, REF545 | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V81158B139879.3020833333 | V81158B1 | V81158A9 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HOTS | 39879.3021 | 39879.9146 | DAILY | 00359901 | SPIMAINT | Out W/O 1A & 1B 66kV Cap bank prot setting changes | SPIPOWER | V811 | V811 - COST EST - UPGRADE CONFIG CAPBANK IEDS, REF545 | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030158239879.8229166667 | 10301582 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39879.8229 | 39881.7458 | CONT | 00356082 | GENCO | Power station request HWPS Gen 4 | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030158439880.3055555556 | 10301584 |  | Parent | TRUE | EX - NO.4A 66KV CAPACITOR BANK AT TTS | 39880.3056 | 39882.4451 | CONT | 00001486 | FAULT | Cap Bank Fault on 4A | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030158539880.3055555556 | 10301585 | 10301584 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT TTS | 39880.3056 | 39882.4451 | CONT | 00337509 | FAULT | Fault on 4A Cap Bank | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V81158B039880.3125 | V81158B0 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 39880.3125 | 39880.8306 | DAILY | 00359897 | SPIMAINT | Out W/O No2 66kV Cap bank prot setting changes | SPIPOWER | V811 | V811 - COST EST - UPGRADE CONFIG CAPBANK IEDS, REF545 | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030146239880.3305555556 | 10301462 |  | Parent | FALSE | NO.4 TRANS 220KV CB AT BETS | 39880.3306 | 39880.3431 | DAILY | [12 empty] | 0
_X87558A639882.2381944445 | X87558A6 |  | Parent | FALSE | NO.4A 66KV BUS AT WMTS | 39882.2382 | 39882.5743 | DAILY | 00351981 | SPICAPX | replace / fit new gis inspection windows - day 7 | SPIPOWER | X875 | X875 - (WMTS) INSTALL VIEWING WINDOWS & CAMERAS ON 66KV GIS | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029543439882.2708333333 | 10295434 |  | Parent | FALSE | 2B-4 220KV BUS TIE CB AT BLTS | 39882.2708 | 39883.6229 | CONT | [12 empty] | 0
_V71158A639882.2770833333 | V71158A6 |  | Parent | FALSE | A2 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 39882.2771 | 39960.6646 | CONT | [12 empty] | 0
_1010278939882.2909722222 | 10102789 |  | Parent | FALSE | JLTS NO.4 220KV LINE NO.3 BUS CB AT HWPS | 39882.291 | 39884.5833 | CONT | [12 empty] | 0
_X72458A639882.4388888889 | X72458A6 |  | Parent | FALSE | EX - NO.1 66KV REACTOR AT HOTS | 39882.4389 | 39882.6979 | REPDAILY | 00006935 | SPICAPX | Install overhead conductors to Fut No1 Reactor | SPIPOWER | X724 | X724 - (HOTS) NO.1 SHUNT REACTOR REPLACEMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030157139882.5618055556 | 10301571 |  | Parent | FALSE | MLRC 220KV LINE NO.2 BUS CB AT RCTS | 39882.5618 | 39882.6375 | DAILY | [12 empty] | 4
_X7F858G539883.2395833333 | X7F858G5 |  | Parent | FALSE | B2 220/66KV TRANS AT GNTS | 39883.2396 | 39885.5764 | CONT | 00000743 | SPICAPX | GNTS No2 Trans 220kV & 66kV S/D replacement | SPIPOWER | X7F8 | X7F8 - REPLACE AGEING 66KV - 330KV SURGE ARRESTERS | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X87558A539883.2402777778 | X87558A5 |  | Parent | FALSE | NO.4A 66KV BUS AT WMTS | 39883.2403 | 39883.5542 | DAILY | 00351981 | SPICAPX | replace / fit new gis inspection windows - day 6 | SPIPOWER | X875 | X875 - (WMTS) INSTALL VIEWING WINDOWS & CAMERAS ON 66KV GIS | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030114439883.2534722222 | 10301144 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 39883.2535 | 39883.5535 | DAILY | 00007456 | SPIMAINT | O/Haul Divetor Switch up on opertional points | SPIPOWER |  |  | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027563639883.28125 | 10275636 |  | Parent | FALSE | NO.2 66KV BUS VT AT RCTS | 39883.2812 | 39883.3924 | DAILY | [12 empty] | 0
_X72458A639883.3666666667 | X72458A6 |  | Parent | FALSE | EX - NO.1 66KV REACTOR AT HOTS | 39883.3667 | 39883.6167 | REPDAILY | 00006935 | SPICAPX | Install overhead conductors to Fut No1 Reactor | SPIPOWER | X724 | X724 - (HOTS) NO.1 SHUNT REACTOR REPLACEMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030112139883.5645833333 | 10301121 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39883.5646 | 39883.6917 | DAILY | 00337581 | SPIMAINT | No1 Trans grp de-energ to run through OLTC range | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030176339883.6888888889 | 10301763 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 39883.6889 | 39885.7153 | CONT | 00356080 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X87558A839884.1291666667 | X87558A8 |  | Parent | FALSE | JA NO.1 66KV FDR CB AT WMTS | 39884.1292 | 39884.284 | DAILY | [12 empty] | 0
_1028472539884.2361111111 | 10284725 | 10288148 | Child | FALSE | B2 TRANS 66KV CB CT R/PH AT ATS | 39884.2361 | 39884.6014 | DAILY | [12 empty] | 0
_1028814839884.2361111111 | 10288148 |  | Parent | TRUE | B2 220/66KV TRANS AT ATS | 39884.2361 | 39884.6014 | DAILY | 00060871 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_U80258A039884.2548611111 | U80258A0 |  | Parent | FALSE | HWTS NO.3 LINE A1 TRANS CB AT ROTS (RTF) | 39884.2549 | 39884.559 | DAILY | [12 empty] | 0
_1028946139885.2472222222 | 10289461 |  | Parent | TRUE | B1 220/66KV TRANS BANK AT BLTS | 39885.2472 | 39885.6785 | DAILY | 00018514 | SPIMAINT | O/HAUL Transformer without Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029155639885.2472222222 | 10291556 | 10289461 | Child | FALSE | NO.1 TRANS 66KV CB AT BLTS | 39885.2472 | 39885.6785 | DAILY | [12 empty] | 0
_1030169539885.2708333333 | 10301695 |  | Parent | FALSE | MLTS-HYTS 1 500KV W | 39885.2708 | 39885.275 | DAILY | 00022630 | SW_NEM | Reactor Switching for NEMMCO | NEMMCO |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1030169739885.2777777778 | 10301697 |  | Parent | FALSE | MLTS-HYTS 2 500KV W | 39885.2778 | 39885.2812 | DAILY | 00022633 | SW_NEM | Reactor Switching for NEMMCO | NEMMCO |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1030181039885.3340277778 | 10301810 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 39885.334 | 39885.3889 | DAILY | 00337581 | SPIMAINT | No1 Trans grp de-energ to run through OLTC range | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030176739885.3395833333 | 10301767 |  | Parent | TRUE | B1 TRANS 66KV CB AT CBTS | 39885.3396 | 39885.3819 | DAILY | [12 empty] | 0
_1030176839885.3395833333 | 10301768 | 10301767 | Child | FALSE | B1 220/66KV TRANS AT CBTS | 39885.3396 | 39885.3819 | CONT | 00353076 | FORCED | SF6 Top up Transf 66KV CB | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X56558G739885.5763888889 | X56558G7 |  | Parent | FALSE | EX - B2 TRANS NO.1 BUS TIE CT R/PH AT GNTS | 39885.5764 | 39889.2472 | CONT | [12 empty] | 0
_1030185439886.1173611111 | 10301854 |  | Parent | FALSE | W2 GEN TRANS 220KV LINE E/SW AT YPS | 39886.1174 | 39890.7 | CONT | [12 empty] | 0
_X50858P939886.2111111111 | X50858P9 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39886.2111 | 39888.8472 | CONT | 00017901 | SPICAPX | KTS No2 Ln for prep to precommissionnew CB | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_U80258A139886.2402777778 | U80258A1 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39886.2403 | 39887.6854 | CONT | 00354002 | SPIMAINT | Replace Bolts on Transformer Connections | SPIPOWER | U802 | U802 - (C-RTF) REPAIR 500KV PRIMARY CONDUCTOR JOINTS | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_X87058C039886.2458333333 | X87058C0 |  | Parent | FALSE | MLTS-BATS 1 220KV WY | 39886.2458 | 39886.4368 | REPDAILY | 00022728 | SPICAPX | MLTS-BATS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358CC39886.2534722222 | Z51358CC |  | Parent | FALSE | L2 220/22KV TRANS BANK AT RWTS | 39886.2535 | 39886.8556 | CONT | 00007447 | DB_AUG | No 2 220/22kv trans | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V79658A239886.2548611111 | V79658A2 |  | Parent | FALSE | BTS 220KV LINE AT RTS | 39886.2549 | 39960.6444 | CONT | 00021222 | SPIMAINT | V796 - (BTS-RTS) CABLE JOINT REPLACEMENTS | SPIPOWER | V796 | V796 - (BTS-RTS) CABLE JOINT REPLACEMENTS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058C039887.2527777778 | X87058C0 |  | Parent | FALSE | MLTS-BATS 1 220KV WY | 39887.2528 | 39887.2993 | REPDAILY | 00022728 | SPICAPX | MLTS-BATS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030175739887.75 | 10301757 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE E/SW AT GTS | 39887.75 | 39889.7257 | CONT | [12 empty] | 0
_Z51358CG39888.5902777778 | Z51358CG |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT RWTS | 39888.5903 | 39888.6458 | DAILY | [12 empty] | 0
_1030135839889.2236111111 | 10301358 | X50858Q3 | Child | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39889.2236 | 39889.7174 | DAILY | 00017906 | SPICAPX | Rebate W/O Pth No2 Line during No1 Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858Q339889.2236111111 | X50858Q3 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39889.2236 | 39889.7174 | DAILY | 00002833 | SPICAPX | Replace Bus Insulators and remove bipods | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858Q439889.2236111111 | X50858Q4 | X50858Q3 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 39889.2236 | 39889.7174 | DAILY | 00366646 | SPICAPX | Rebate W/O MLTS No2 Line during No1 Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858Q539889.2236111111 | X50858Q5 | X50858Q3 | Child | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39889.2236 | 39889.7174 | DAILY | 00017900 | SPICAPX | Rebate W/O KTS No1 Line during No1 Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027303139889.2319444444 | 10273031 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT KTS | 39889.2319 | 39892.6417 | CONT | 00026096 | SPIMAINT | Condition Monitoring Program Transfs Western Area | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1026724339889.2465277778 | 10267243 | 10269258 | Child | FALSE | SYN/COND COOLING SYSTEM AT TSTS | 39889.2465 | 39892.5632 | CONT | [12 empty] | 0
_1026925839889.2465277778 | 10269258 |  | Parent | TRUE | SYN/COND AT TSTS | 39889.2465 | 39892.5632 | CONT | 00007626 | SPIMAINT | 4 Monthly O/HAUL - TSTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X56558H439889.2486111111 | X56558H4 |  | Parent | FALSE | NO.1 220KV BUS AT GNTS | 39889.2486 | 39889.5944 | DAILY | 00000746 | SPICAPX | Replace conn's from Tie Bus CT to Bus Side Isol Sw | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030185339889.2638888889 | 10301853 |  | Parent | FALSE | W2 GEN TRANS NO.2 BUS 220KV CB AT YPS | 39889.2639 | 39889.6264 | DAILY | [12 empty] | 0
_1029316939889.2701388889 | 10293169 |  | Parent | FALSE | 2-3 220KV BUS TIE CB AT WMTS | 39889.2701 | 39890.6556 | CONT | [12 empty] | 0
_1029654839889.2756944445 | 10296548 |  | Parent | TRUE | YPS NO.2 220KV LINE NO.4 BUS CB LINE SIDE ISOL AT HWPS | 39889.2757 | 39889.6153 | DAILY | [12 empty] | 0
_1030182839889.2756944445 | 10301828 | 10296548 | Child | FALSE | YPS NO.2 220KV LINE AT HWPS | 39889.2757 | 39889.6153 | DAILY | 00015796 | SPIMAINT | rebate for isol outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026515939889.3145833333 | 10265159 |  | Parent | FALSE | BETS LINE 220KV E/SW AT KGTS | 39889.3146 | 39889.6139 | REPDAILY | [12 empty] | 0
_Z73058H839889.3263888889 | Z73058H8 |  | Parent | FALSE | B1 220/66KV TRANS AT SMTS | 39889.3264 | 39897.4604 | CONT | 00366621 | DB_AUG | Connect 220 & 66KV connections to Fut B1 Trans | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1030162939889.3423611111 | 10301629 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT BETS | 39889.3424 | 39889.6479 | DAILY | 00016035 | DBPROX | VSCAP to Powercor | DISTCO |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358CJ39889.3708333333 | Z51358CJ |  | Parent | FALSE | 1-2 EXT 66KV BUS TIE CB AT RWTS | 39889.3708 | 39889.4507 | DAILY | [12 empty] | 0
_Z51358CI39889.4625 | Z51358CI |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT RWTS | 39889.4625 | 39889.5139 | DAILY | [12 empty] | 0
_Z51358CH39889.5263888889 | Z51358CH |  | Parent | FALSE | 1-3 66KV BUS TIE CB AT RWTS | 39889.5264 | 39889.566 | DAILY | [12 empty] | 0
_Z51358CK39889.5722222222 | Z51358CK |  | Parent | FALSE | 2-4 66KV BUS TIE CB AT RWTS | 39889.5722 | 39889.6181 | DAILY | [12 empty] | 0
_X50858Q639890.2083333333 | X50858Q6 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39890.2083 | 39890.7764 | DAILY | 00002833 | SPICAPX | Install Bipods to Fut Pth No1 Line CB Bus Side ROI | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858Q739890.2083333333 | X50858Q7 | X50858Q6 | Child | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39890.2083 | 39890.7764 | DAILY | 00017906 | SPICAPX | Rebate WO PTH No2 Line during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858Q839890.2083333333 | X50858Q8 | X50858Q6 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 39890.2083 | 39890.7764 | DAILY | 00366646 | SPICAPX | Rebate WO MLTS 2 Line during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858Q939890.2083333333 | X50858Q9 | X50858Q6 | Child | FALSE | EX - KTS NO.1 220KV LINE AT GTS | 39890.2083 | 39890.7764 | DAILY | 00017900 | SPICAPX | Rebate WO KTS 1 Line during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028434139890.2569444444 | 10284341 |  | Parent | FALSE | DDTS 330KV LINE NO.2 BUS CB AT WOTS | 39890.2569 | 39890.6722 | CONT | [12 empty] | 0
_1009279139890.2729166667 | 10092791 |  | Parent | TRUE | JLTS NO.3 LINE/AUX TRANS 'C' 220KV CB AT HWPS | 39890.2729 | 39892.5604 | CONT | [12 empty] | 0
_1030217939890.2729166667 | 10302179 | 10092791 | Child | FALSE | JLTS NO.3 220KV LINE AT HWPS | 39890.2729 | 39892.5604 | CONT | 00015787 | SPIMAINT | Rebate for CL.1 O/HAUL - BTH JW419 & JW420 CB | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026515939890.2798611111 | 10265159 |  | Parent | FALSE | BETS LINE 220KV E/SW AT KGTS | 39890.2799 | 39890.5889 | REPDAILY | [12 empty] | 0
_1030185639890.2840277778 | 10301856 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 39890.284 | 39890.3056 | DAILY | 00027386 | APDALCOA | HVS: APD-HYTS 1 Line outage for APD | APDALCOA |  |  | Circuits | 3rd Party | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1030198939890.38125 | 10301989 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT BETS | 39890.3812 | 39890.6458 | DAILY | 00016431 | DBPROX | VSCAP to Powercor | DISTCO |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1030199439890.4875 | 10301994 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39890.4875 | 39890.5062 | DAILY | [12 empty] | 0
_X50858R739891.2513888889 | X50858R7 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39891.2514 | 39891.2847 | REPDAILY | 00002833 | SPICAPX | Replace Bus Insulators and Install equip in bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858R839891.2513888889 | X50858R8 | X50858R7 | Child | FALSE | KTS NO.1 220KV LINE AT GTS | 39891.2514 | 39891.2847 | DAILY | 00367291 | SPICAPX | Rebate W/O KTS No1 Line during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858R939891.2513888889 | X50858R9 | X50858R7 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 39891.2514 | 39891.2847 | DAILY | 00366646 | SPICAPX | Rebate W/O MLTS No2 Line during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858S039891.2513888889 | X50858S0 | X50858R7 | Child | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39891.2514 | 39891.2847 | DAILY | 00017906 | SPICAPX | Rebate W/O PTH No2 Line during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030186139891.2902777778 | 10301861 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 39891.2903 | 39891.3056 | DAILY | 00060938 | APDALCOA | HVS: APD-HYTS 2 Line outage for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1026828139891.3020833333 | 10268281 |  | Parent | FALSE | MWTS NO.3 66KV FDR AT LY | 39891.3021 | 39891.5486 | DAILY | 00015996 | SPIMAINT | Overhaul MWTS No 3 66 Kv Fdr at LY | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027258339891.3590277778 | 10272583 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK X & X BACKUP PROT AT RWTS | 39891.359 | 39891.75 | DAILY | [12 empty] | 0
_1030972939891.4506944444 | 10309729 |  | Parent | FALSE | NO.1 220KV BUS AT GTS | 39891.4507 | 39891.65 | DAILY | 00002833 | SPICAPX | Replace bus insulators (ref X50858R7) | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030973039891.4506944444 | 10309730 |  | Parent | FALSE | KTS NO.1 220KV LINE AT GTS | 39891.4507 | 39891.65 | DAILY | 00367291 | SPICAPX | Replace bus insulators (ref X50858R7) | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030973139891.4506944444 | 10309731 |  | Parent | FALSE | MLTS NO.2 220KV LINE AT GTS | 39891.4507 | 39891.65 | DAILY | 00366646 | SPICAPX | Replace bus insulators (ref X50858R7) | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030973239891.4506944444 | 10309732 |  | Parent | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39891.4507 | 39891.65 | DAILY | 00017906 | SPICAPX | Replace bus insulators (ref X50858R7) | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858R739892.2097222222 | X50858R7 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39892.2097 | 39892.6632 | REPDAILY | 00002833 | SPICAPX | Replace Bus Insulators and Install equip in bay K | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858R839892.2097222222 | X50858R8 | X50858R7 | Child | FALSE | KTS NO.1 220KV LINE AT GTS | 39892.2097 | 39892.6632 | DAILY | 00367291 | SPICAPX | Rebate W/O KTS No1 Line during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858R939892.2097222222 | X50858R9 | X50858R7 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 39892.2097 | 39892.6632 | DAILY | 00366646 | SPICAPX | Rebate W/O MLTS No2 Line during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858S039892.2097222222 | X50858S0 | X50858R7 | Child | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39892.2097 | 39892.6632 | DAILY | 00017906 | SPICAPX | Rebate W/O PTH No2 Line during No1 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028044039892.2895833333 | 10280440 |  | Parent | TRUE | NO.3B 66KV CAPACITOR BANK CB AT SHTS | 39892.2896 | 39892.6326 | DAILY | [12 empty] | 0
_1030164939892.2895833333 | 10301649 | 10280440 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT SHTS | 39892.2896 | 39892.6326 | DAILY | 00330780 | SPIMAINT | Rebate W/O 3B Cap Bank durng 3B cap CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030199139892.2979166667 | 10301991 |  | Parent | TRUE | B1 TRANS 66KV CB AT CBTS | 39892.2979 | 39892.3333 | DAILY | [12 empty] | 0
_1030199239892.2979166667 | 10301992 | 10301991 | Child | FALSE | B1 220/66KV TRANS AT CBTS | 39892.2979 | 39892.3333 | CONT | 00353076 | FORCED | SF6 Top Up Transf 66KV CB | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1030208039892.8263888889 | 10302080 |  | Parent | FALSE | NO.8 GEN TRANS 220KV CB AT HWPS | 39892.8264 | 39899.8493 | CONT | [12 empty] | 0
_1026824539893.2097222222 | 10268245 |  | Parent | TRUE | ROTS NO.3 500KV LINE AT HWTS | 39893.2097 | 39893.6104 | REPDAILY | 00016239 | SPIMAINT | Overhaul SMTS No 3 500 Kv Line at HWTS | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026907939893.2097222222 | 10269079 | 10268245 | Child | FALSE | LYPS NO.2 LINE/ROTS NO.3 LINE CB ROTS NO.3 LINE SIDE 500KV E/SW AT HWTS | 39893.2097 | 39893.6104 | DAILY | [12 empty] | 0
_1026908139893.2097222222 | 10269081 | 10268245 | Child | FALSE | ROTS NO.3 500KV LINE E/SW AT HWTS | 39893.2097 | 39893.6104 | DAILY | [12 empty] | 0
_1026908339893.2097222222 | 10269083 | 10268245 | Child | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB LINE SIDE E/SW AT HWTS | 39893.2097 | 39893.6104 | DAILY | [12 empty] | 0
_1026910939893.2097222222 | 10269109 | 10268245 | Child | FALSE | LYPS NO.2 LINE/ROTS NO.3 LINE 500KV CB ROTS NO.3 LINE SIDE ROI AT HWTS | 39893.2097 | 39893.6104 | DAILY | [12 empty] | 0
_1026911139893.2097222222 | 10269111 | 10268245 | Child | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB LINE SIDE ROI AT HWTS | 39893.2097 | 39893.6104 | DAILY | [12 empty] | 0
_X87058B139893.25 | X87058B1 |  | Parent | FALSE | MLTS-BATS 1 220KV WY | 39893.25 | 39893.6194 | REPDAILY | 00022728 | SPICAPX | MLTS-BATS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027258339893.2965277778 | 10272583 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK X & X BACKUP PROT AT RWTS | 39893.2965 | 39893.7213 | DAILY | [12 empty] | 0
_1026824539894.2298611111 | 10268245 |  | Parent | TRUE | ROTS NO.3 500KV LINE AT HWTS | 39894.2299 | 39894.5188 | REPDAILY | 00016239 | SPIMAINT | Overhaul SMTS No 3 500 Kv Line at HWTS | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026907939894.2298611111 | 10269079 | 10268245 | Child | FALSE | LYPS NO.2 LINE/ROTS NO.3 LINE CB ROTS NO.3 LINE SIDE 500KV E/SW AT HWTS | 39894.2299 | 39894.5188 | DAILY | [12 empty] | 0
_1026908139894.2298611111 | 10269081 | 10268245 | Child | FALSE | ROTS NO.3 500KV LINE E/SW AT HWTS | 39894.2299 | 39894.5188 | DAILY | [12 empty] | 0
_1026908339894.2298611111 | 10269083 | 10268245 | Child | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB LINE SIDE E/SW AT HWTS | 39894.2299 | 39894.5188 | DAILY | [12 empty] | 0
_1026910939894.2298611111 | 10269109 | 10268245 | Child | FALSE | LYPS NO.2 LINE/ROTS NO.3 LINE 500KV CB ROTS NO.3 LINE SIDE ROI AT HWTS | 39894.2299 | 39894.5188 | DAILY | [12 empty] | 0
_1026911139894.2298611111 | 10269111 | 10268245 | Child | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB LINE SIDE ROI AT HWTS | 39894.2299 | 39894.5188 | DAILY | [12 empty] | 0
_X87058B139894.25 | X87058B1 |  | Parent | FALSE | MLTS-BATS 1 220KV WY | 39894.25 | 39894.5181 | REPDAILY | 00022728 | SPICAPX | MLTS-BATS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1024910239894.4277777778 | 10249102 |  | Parent | FALSE | L1 220/22KV TRANS AT WMTS | 39894.4278 | 39894.5708 | CONT | 00003234 | SPIMAINT | O/HAUL Transformer Div Mechanism (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858S339895.1881944445 | X50858S3 |  | Parent | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39895.1882 | 39895.7306 | REPDAILY | 00017905 | SPICAPX | Install conductors to PTH No1 Line at first tower | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027027539895.2305555556 | 10270275 |  | Parent | FALSE | SYN/COND AT BLTS | 39895.2306 | 39897.6965 | CONT | 00002547 | SPIMAINT | 3 Monthly O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1009271439895.2715277778 | 10092714 |  | Parent | TRUE | JLTS NO.2 220KV LINE CB AT HWPS | 39895.2715 | 39897.6424 | CONT | [12 empty] | 0
_1030106139895.2715277778 | 10301061 | 10092714 | Child | FALSE | JLTS NO.2 220KV LINE AT HWPS | 39895.2715 | 39897.6424 | CONT | 00015765 | SPIMAINT | rebate for cb outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030200439895.3194444444 | 10302004 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.1 BUS CB CT R/PH AT LYPS | 39895.3194 | 39895.4437 | DAILY | [12 empty] | 0
_1030202339895.3777777778 | 10302023 |  | Parent | TRUE | MLTS NO.1 220KV LINE CB AT BATS | 39895.3778 | 39895.5111 | REPDAILY | [12 empty] | 0
_1030202439895.3777777778 | 10302024 | 10302023 | Child | FALSE | MLTS-BATS 1 220KV WY | 39895.3778 | 39895.5111 | REPDAILY | 00022728 | SPIMAINT | Rebate W/O MLTS 1L CB de-energ for 220 Bus prot wk | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030200539895.4465277778 | 10302005 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.2 BUS CB CT R/PH AT LYPS | 39895.4465 | 39895.5882 | DAILY | [12 empty] | 0
_X72458A739895.4701388889 | X72458A7 |  | Parent | FALSE | EX - NO.1 66KV REACTOR AT HOTS | 39895.4701 | 39940.8187 | CONT | 00006935 | SPICAPX | Connect Overhead Conductors to No1 Reactor | SPIPOWER | X724 | X724 - (HOTS) NO.1 SHUNT REACTOR REPLACEMENT | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030202239895.5236111111 | 10302022 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 39895.5236 | 39895.8 | REPDAILY | 00006554 | SPIMAINT | Out W/O No1 Trans de-energ for 220 Bus prot works | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030202539895.5895833333 | 10302025 |  | Parent | FALSE | BETS 220KV LINE NO.2 BUS CB AT BATS | 39895.5896 | 39895.6285 | REPDAILY | [12 empty] | 0
_1030202639895.6291666667 | 10302026 |  | Parent | FALSE | MLTS NO.2 220KV LINE NO.2 BUS CB AT BATS | 39895.6292 | 39895.6694 | REPDAILY | [12 empty] | 0
_1030202739895.6722222222 | 10302027 |  | Parent | FALSE | WBTS 220KV LINE NO.2 BUS CB AT BATS | 39895.6722 | 39895.7125 | REPDAILY | [12 empty] | 0
_1030200339895.7291666667 | 10302003 |  | Parent | FALSE | PT. HENRY NO.1 220KV LINE CB AT GTS | 39895.7292 | 39896.225 | REPDAILY | [12 empty] | 0
_1030211639895.7409722222 | 10302116 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 39895.741 | 39895.8403 | CONT | 00022690 | FORCED | GTS-PTH No1 220kV Line Outage due to Fault | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858S339896.225 | X50858S3 |  | Parent | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39896.225 | 39896.6687 | REPDAILY | 00017905 | SPICAPX | Install conductors to PTH No1 Line at first tower | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858S139896.2513888889 | X50858S1 |  | Parent | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39896.2514 | 39896.6056 | REPDAILY | 00017901 | SPICAPX | Install SD's and structures KTS No2 Ln in Bay J | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029784339896.2604166667 | 10297843 |  | Parent | FALSE | EX - NO.1 220KV CAPACITOR BANK CB CT R/PH AT KTS | 39896.2604 | 39896.5972 | DAILY | [12 empty] | 0
_1030202239896.375 | 10302022 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 39896.375 | 39896.4236 | REPDAILY | 00006554 | SPIMAINT | Out W/O No1 Trans de-energ for 220 Bus prot works | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030202339896.4381944445 | 10302023 |  | Parent | TRUE | MLTS NO.1 220KV LINE CB AT BATS | 39896.4382 | 39896.4632 | REPDAILY | [12 empty] | 0
_1030202439896.4381944445 | 10302024 | 10302023 | Child | FALSE | MLTS-BATS 1 220KV WY | 39896.4382 | 39896.4632 | REPDAILY | 00022728 | SPIMAINT | Rebate W/O MLTS 1L CB de-energ for 220 Bus prot wk | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030202539896.5138888889 | 10302025 |  | Parent | FALSE | BETS 220KV LINE NO.2 BUS CB AT BATS | 39896.5139 | 39896.5403 | REPDAILY | [12 empty] | 0
_1030202639896.5409722222 | 10302026 |  | Parent | FALSE | MLTS NO.2 220KV LINE NO.2 BUS CB AT BATS | 39896.541 | 39896.5653 | REPDAILY | [12 empty] | 0
_1030202739896.56875 | 10302027 |  | Parent | FALSE | WBTS 220KV LINE NO.2 BUS CB AT BATS | 39896.5687 | 39896.6236 | REPDAILY | [12 empty] | 0
_1030200339896.6694444444 | 10302003 |  | Parent | FALSE | PT. HENRY NO.1 220KV LINE CB AT GTS | 39896.6694 | 39897.1875 | REPDAILY | [12 empty] | 0
_X50858S339897.1875 | X50858S3 |  | Parent | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39897.1875 | 39897.6833 | REPDAILY | 00017905 | SPICAPX | Install conductors to PTH No1 Line at first tower | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029784739897.2590277778 | 10297847 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB CT R/PH AT TTS | 39897.259 | 39897.3444 | DAILY | [12 empty] | 0
_1030249739897.2590277778 | 10302497 | 10297847 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT TTS | 39897.259 | 39897.3444 | DAILY | 00119178 | SPIMAINT | CHILD W/O FOR OUTAGE ON CT OIL SAMPLING | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1027258739897.3555555556 | 10272587 |  | Parent | FALSE | NO.2 22KV CAPACITOR BANK X & X BACKUP PROT AT RWTS | 39897.3556 | 39897.6375 | DAILY | [12 empty] | 0
_1030200339897.6847222222 | 10302003 |  | Parent | FALSE | PT. HENRY NO.1 220KV LINE CB AT GTS | 39897.6847 | 39898.1868 | REPDAILY | [12 empty] | 0
_X50858S539898.1861111111 | X50858S5 |  | Parent | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39898.1861 | 39898.4604 | DAILY | 00017905 | SPICAPX | Instal bridges from PTH No1 Line to harpstrings | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027019939898.2416666667 | 10270199 |  | Parent | FALSE | SYN/COND AT FBTS | 39898.2417 | 39900.616 | CONT | 00002697 | SPIMAINT | 3 Monthly O/HAUL - FBTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1027328739898.2513888889 | 10273287 |  | Parent | FALSE | FBTS NO.2 220KV LINE CB CT R/PH AT WMTS | 39898.2514 | 39898.4722 | DAILY | [12 empty] | 0
_1030125639898.2527777778 | 10301256 |  | Parent | TRUE | TRANS - MBY 66KV FDR CB TRANS SIDE ISOL AT MBTS | 39898.2528 | 39898.4646 | DAILY | [12 empty] | 0
_1030169439898.2527777778 | 10301694 | 10301256 | Child | FALSE | B1 220/66KV TRANS (HOT SPARE) AT MBTS | 39898.2528 | 39898.4646 | DAILY | 00360627 | SPIMAINT | Perf calc W/O B1 Trans during isol repair | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER | NORMALLY OPEN | 0
_1030169639898.2527777778 | 10301696 | 10301256 | Child | FALSE | B2 220/66KV TRANS AT MBTS | 39898.2528 | 39898.4646 | DAILY | 00362372 | SPIMAINT | Perf calc W/O B2 Trans during isol repair | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1026899139898.2805555556 | 10268991 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT MWTS | 39898.2806 | 39898.5611 | DAILY | 00010265 | SPIMAINT | O/HAUL Transformer Div Mechanism (EH) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029871939898.2923611111 | 10298719 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT MLTS | 39898.2924 | 39898.4653 | DAILY | 00360001 | SPIMAINT | No1 220kv Cp bk Bph Ct oil leak | SPIPOWER |  |  | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030197139898.3222222222 | 10301971 |  | Parent | TRUE | NO.1 220KV BUS AT BATS | 39898.3222 | 39898.6722 | DAILY | 00006558 | SPIMAINT | Out W/O No. 1 220kV BUS de-ener for bus prot works | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030197239898.3222222222 | 10301972 | 10301971 | Child | FALSE | BATS-TGTS 220KV WW | 39898.3222 | 39898.6722 | DAILY | 00022665 | SPIMAINT | Rebate W/O TGTS Line during No1 220kV BUS de-ener | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030197339898.3222222222 | 10301973 | 10301971 | Child | FALSE | B1 220/66KV TRANS AT BATS | 39898.3222 | 39898.6722 | DAILY | 00006554 | SPIMAINT | Perf calc W/O #2 Tran during No1 220kV BUS de-ener | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030217839898.3555555556 | 10302178 |  | Parent | FALSE | PT. HENRY NO.2 220KV LINE CB AT GTS | 39898.3556 | 39901.3264 | CONT | [12 empty] | 0
_1030221539898.4236111111 | 10302215 |  | Parent | FALSE | KTS 500KV LINE NO.1 BUS CB BUS SIDE ISOL AT SMTS | 39898.4236 | 39898.5069 | DAILY | [12 empty] | 0
_1030231639898.8951388889 | 10302316 |  | Parent | FALSE | NO.5 GEN 220/16.5KV TRANS AT HWPS | 39898.8951 | 39904.6708 | CONT | 00009646 | GENCO | Power Statio Requirements | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_X50858T039899.1909722222 | X50858T0 |  | Parent | FALSE | EX - PT. HENRY NO.1 220KV LINE AT GTS | 39899.191 | 39899.7118 | DAILY | 00017905 | SPICAPX | Remove redundant Conductors PTH N1 Ln 1st tower | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858N539899.2027777778 | X50858N5 |  | Parent | FALSE | EX - GB 66KV FDR CB AT GTS | 39899.2028 | 39899.5444 | DAILY | [12 empty] | 0
_1026899339899.29375 | 10268993 |  | Parent | TRUE | B2 220/66KV TRANS AT MWTS | 39899.2937 | 39899.5868 | DAILY | 00010266 | SPIMAINT | O/HAUL Transformer Div Mechanism (EH) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030130239899.29375 | 10301302 | 10268993 | Child | FALSE | JLTS NO.2 220KV LINE AT MWTS | 39899.2937 | 39899.5868 | DAILY | 00016131 | SPIMAINT | Rebate Line for Trans outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030264739899.3854166667 | 10302647 | 10284747 | Child | FALSE | BLTS 66KV LINE AT ATS | 39899.3854 | 39899.4632 | DAILY | 00060179 | SPIMAINT | out w/o for NDD REQUEST CT SAMPLES | SPIPOWER |  |  | Circuits | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1028474739899.3854166667 | 10284747 |  | Parent | TRUE | BLTS 66KV LINE CB CT R/PH AT ATS | 39899.3854 | 39899.4637 | DAILY | [12 empty] | 0
_1030223639899.5166666667 | 10302236 |  | Parent | FALSE | EX - A4 TRANS NO.3 BUS 220KV CB AT KTS | 39899.5167 | 39899.5708 | DAILY | [12 empty] | 0
_X50858N639899.5451388889 | X50858N6 |  | Parent | FALSE | EX - GB 66KV FDR CB AT GTS | 39899.5451 | 39900.2326 | CONT | [12 empty] | 0
_1030103039899.5611111111 | 10301030 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB AT HWTS | 39899.5611 | 39899.5618 | DAILY | [12 empty] | 0
_1030228939899.6 | 10302289 |  | Parent | FALSE | NO.2 220KV BUS AT BTS | 39899.6 | 39899.6076 | DAILY | 00000943 | FORCED | RTS Line ROI open but not leaning back | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030230639900.1555555556 | 10302306 |  | Parent | FALSE | H3 TRANS NO.1 BUS 220KV CB AT DDTS | 39900.1556 | 39900.4694 | CONT | [12 empty] | 0
_X50858S839900.2354166667 | X50858S8 |  | Parent | TRUE | NO.3 66KV BUS AT GTS | 39900.2354 | 39900.6715 | DAILY | 00002837 | SPICAPX | Install Sub GB 66kv Fdr CB and connections | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858S939900.2354166667 | X50858S9 | X50858S8 | Child | FALSE | B3 220/66KV TRANS AT GTS | 39900.2354 | 39900.6715 | DAILY | 00002829 | SPICAPX | Rebate W/O B3 Trans during No3 66kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030198239900.2479166667 | 10301982 |  | Parent | TRUE | B1 TRANS 66KV CB AT CBTS | 39900.2479 | 39900.5729 | DAILY | [12 empty] | 0
_1030198339900.2479166667 | 10301983 | 10301982 | Child | FALSE | B1 220/66KV TRANS AT CBTS | 39900.2479 | 39900.5729 | CONT | 00353076 | FORCED | SF6 Top Up Replace CB Bushing | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X87058C339900.2520833333 | X87058C3 |  | Parent | FALSE | MLTS-BATS 1 220KV WY | 39900.2521 | 39900.6833 | REPDAILY | 00022728 | SPICAPX | MLTS-BATS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027172939900.2527777778 | 10271729 |  | Parent | FALSE | JLTS NO.4 220KV LINE AT HWPS | 39900.2528 | 39900.5646 | DAILY | 00015788 | SPIMAINT | Overhaul 220KV Line CVT'S | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V81158B239900.2909722222 | V81158B2 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT RCTS | 39900.291 | 39900.7785 | REPDAILY | 00360382 | SPIMAINT | Out W/O No1 220kV Cap bank prot setting changes | SPIPOWER | V811 | V811 - COST EST - UPGRADE CONFIG CAPBANK IEDS, REF545 | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X50858S739900.6715277778 | X50858S7 |  | Parent | FALSE | EX - GB 66KV FDR CB AT GTS | 39900.6715 | 39902.7812 | CONT | [12 empty] | 0
_1029871139901.2708333333 | 10298711 |  | Parent | FALSE | LYPS NO.1 500KV LINE CB AT HWTS | 39901.2708 | 39901.3542 | DAILY | [12 empty] | 0
_X50858U939901.2715277778 | X50858U9 |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 39901.2715 | 39901.6882 | DAILY | 00002834 | SPICAPX | Replace bus insulators and remove bipods & equip | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858V039901.2715277778 | X50858V0 | X50858U9 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39901.2715 | 39901.6882 | DAILY | 00002830 | SPICAPX | Rebate W/O B4 Trans during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858V139901.2715277778 | X50858V1 | X50858U9 | Child | FALSE | EX - MLTS NO.1 220KV LINE AT GTS | 39901.2715 | 39901.6882 | DAILY | 00017903 | SPICAPX | Rebate W/O MLTS No1 Ln during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858V239901.2715277778 | X50858V2 | X50858U9 | Child | FALSE | EX - KTS NO.2 220KV LINE AT GTS | 39901.2715 | 39901.6882 | DAILY | 00017901 | SPICAPX | Rebate W/O KTS No2 Ln during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | 3rd Party | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058C339901.2916666667 | X87058C3 |  | Parent | FALSE | MLTS-BATS 1 220KV WY | 39901.2917 | 39901.5771 | REPDAILY | 00022728 | SPICAPX | MLTS-BATS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030164739901.3 | 10301647 |  | Parent | FALSE | PR 22KV FDR 130 CB BUS SIDE ISOL AT RTS | 39901.3 | 39901.4993 | DAILY | [12 empty] | 0
_1030070239901.3152777778 | 10300702 |  | Parent | TRUE | NO.1 66KV BUS CVT R/PH AT ERTS | 39901.3153 | 39901.4771 | DAILY | [12 empty] | 0
_1030070939901.3152777778 | 10300709 | 10300702 | Child | FALSE | B1 220/66KV TRANS AT ERTS | 39901.3153 | 39901.4771 | DAILY | 00004370 | SPIMAINT | Rebate Trans for Bus Outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030071139901.3152777778 | 10300711 | 10300702 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT ERTS | 39901.3153 | 39901.4771 | DAILY | 00337043 | SPIMAINT | Rebate CapBank for Bus Outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030071239901.3152777778 | 10300712 | 10300702 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT ERTS | 39901.3153 | 39901.4771 | DAILY | 00004345 | SPIMAINT | Rebate CapBank for Bus Outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029844439901.3513888889 | 10298444 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 39901.3514 | 39901.5819 | DAILY | 00331118 | SPIMAINT | Rebate W/O No2 Cap Bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029837539901.3513888889 | 10298375 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK CB AT BATS | 39901.3514 | 39901.6236 | DAILY | [12 empty] | 0
_1027344139901.3805555556 | 10273441 |  | Parent | FALSE | EX - ROTS NO.7 220KV LINE NO.1 BUS CB CT R/PH AT YPS | 39901.3806 | 39901.4326 | DAILY | [12 empty] | 0
_V81158B439901.3805555556 | V81158B4 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT RCTS | 39901.3806 | 39901.8611 | DAILY | 00360383 | SPIMAINT | Out W/O No2 220kV Cap bank prot setting changes | SPIPOWER | V811 | V811 - COST EST - UPGRADE CONFIG CAPBANK IEDS, REF545 | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030070339901.4826388889 | 10300703 |  | Parent | TRUE | NO.3 66KV BUS CVT R/PH AT ERTS | 39901.4826 | 39901.5799 | DAILY | [12 empty] | 0
_1030070739901.4826388889 | 10300707 | 10300703 | Child | FALSE | B3 220/66KV TRANS AT ERTS | 39901.4826 | 39901.5799 | DAILY | 00004371 | SPIMAINT | Rebate Trans for Bus Outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030070839901.4826388889 | 10300708 | 10300703 | Child | FALSE | NO.3 66KV CAPACITOR BANK AT ERTS | 39901.4826 | 39901.5799 | DAILY | 00087144 | SPIMAINT | Rebate CapBank for Bus Outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030070439901.5875 | 10300704 |  | Parent | FALSE | NO.4 66KV BUS CVT R/PH AT ERTS | 39901.5875 | 39901.7063 | DAILY | [12 empty] | 0
_1030234139901.6666666667 | 10302341 |  | Parent | FALSE | C 66/11KV S/S TRANS NO.2 BUS 66KV CB CABLE SIDE ISOL AT LY | 39901.6667 | 39901.7444 | CONT | [12 empty] | 0
_1030233939901.6979166667 | 10302339 |  | Parent | TRUE | NO.2 66KV BUS AT LY | 39901.6979 | 39901.7708 | CONT | 00009918 | FAULT | Faulty bus VT | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030245839901.6979166667 | 10302458 | 10302339 | Child | FALSE | MWTS NO.4 66KV FDR AT LY | 39901.6979 | 39901.7708 | CONT | 00015997 | FAULT | Isolate 66KV Bus for Faulty bus VT at LY | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030234239901.7708333333 | 10302342 |  | Parent | FALSE | NO.2 66KV BUS VT R/PH AT LY | 39901.7708 | 39903.5625 | CONT | [12 empty] | 0
_1030223139902.3229166667 | 10302231 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39902.3229 | 39902.6861 | DAILY | 00319998 | APDALCOA | Outage for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1030201239902.3784722222 | 10302012 |  | Parent | FALSE | DDTS-SHTS 220KV NW | 39902.3785 | 39903.309 | REPDAILY | 00352425 | SPIMAINT | Repair DDTS Line No1 Bus CB Ln Side E/Sw | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z64558D639902.4361111111 | Z64558D6 |  | Parent | TRUE | RCTS 220KV LINE NO.1 BUS CB LINE SIDE ISOL AT HOTS | 39902.4361 | 39902.5514 | DAILY | [12 empty] | 0
_Z64558D739902.4361111111 | Z64558D7 | Z64558D6 | Child | FALSE | HOTS-RCTS 220KV | 39902.4361 | 39902.5514 | DAILY | 00328509 | VEN_AUG | Rebate W/O for HOTS-RCTS 220kv Line outage | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V81158B939902.7048611111 | V81158B9 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 39902.7049 | 39902.8285 | DAILY | 00359892 | SPIMAINT | Out W/O No2 66kV Cap bank prot setting changes | SPIPOWER | V811 | V811 - COST EST - UPGRADE CONFIG CAPBANK IEDS, REF545 | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1026850839903.2743055556 | 10268508 |  | Parent | FALSE | A3 TRANS 500KV CB AT KTS | 39903.2743 | 39903.6646 | DAILY | [12 empty] | 0
_1028813039903.2916666667 | 10288130 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT WMTS | 39903.2917 | 39903.6535 | DAILY | 00074391 | SPIMAINT | O/Haul NO.2 66KV CAPACITOR BANK AT WMTS | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030197839903.29375 | 10301978 |  | Parent | TRUE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39903.2937 | 39903.466 | DAILY | 00007399 | SPIMAINT | RE-BALANCE CAP BANK | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030197939903.29375 | 10301979 | 10301978 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39903.2937 | 39903.466 | DAILY | 00331179 | SPIMAINT | REBATE FOR CAP BANK OUTAGE | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029544139903.3104166667 | 10295441 |  | Parent | FALSE | DDTS NO.3 LINE/SHTS NO.3 LINE 220KV CB AT GNTS | 39903.3104 | 39904.6993 | CONT | [12 empty] | 0
_1030215039903.3145833333 | 10302150 |  | Parent | FALSE | JLGA NO.4 UNIT TRANS DISC CB AT JLGA | 39903.3146 | 39903.6424 | DAILY | [12 empty] | 0
_1027293539903.3215277778 | 10272935 |  | Parent | TRUE | MWTS-MPS LINE 220KV CB AT HWPS | 39903.3215 | 39903.6125 | DAILY | [12 empty] | 0
_1028562939903.3215277778 | 10285629 | 10272935 | Child | FALSE | MWTS-MPS LINE 220KV CB AT HWPS | 39903.3215 | 39903.6125 | DAILY | [12 empty] | 0
_1030130339903.3215277778 | 10301303 | 10272935 | Child | FALSE | MPS-MWTS 220KV LINE AT HWPS | 39903.3215 | 39903.6125 | DAILY | 00015789 | SPIMAINT | REBATE FOR CB OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027322539903.3361111111 | 10273225 |  | Parent | FALSE | SVTS2/CSC1 220KV CB AUTO CLOSE AT ROTS | 39903.3361 | 39903.5979 | DAILY | [12 empty] | 0
_1030235339903.5256944444 | 10302353 |  | Parent | TRUE | B2 TRANS 220KV CB AT HOTS | 39903.5257 | 39903.5403 | DAILY | [12 empty] | 0
_1030235539903.5256944444 | 10302355 | 10302353 | Child | FALSE | B2 220/66KV TRANS AT HOTS | 39903.5257 | 39903.5403 | DAILY | 00363103 | SPIMAINT | Perf calc W/O B2 Trans during 220kV CB gas top up | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030239339903.5625 | 10302393 |  | Parent | FALSE | NO.2 66KV BUS VT R/PH AT LY | 39903.5625 | 39904.6299 | DAILY | [12 empty] | 0
_1030215139903.6159722222 | 10302151 |  | Parent | FALSE | JLGA NO.3 UNIT TRANS DISC CB AT JLGA | 39903.616 | 39904.5347 | DAILY | [12 empty] | 0
_V91058A439903.625 | V91058A4 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT TTS | 39903.625 | 39909.6458 | CONT | 00001533 | SPIMAINT | Replacement of failed B1 transformer | SPIPOWER | V910 | V910 - (TTS) INVESTIGATE & REPAIR - FAIL B1 TRANSFORMER | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029084739904.2708333333 | 10290847 |  | Parent | FALSE | NO.1 CSC AT ROTS | 39904.2708 | 39925.5174 | CONT | 00004718 | SPIMAINT | Disconnect No.1 CSC at ROTS | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028969539904.2965277778 | 10289695 |  | Parent | TRUE | ROTS NO.6 220KV LINE AT YPS | 39904.2965 | 39904.6306 | DAILY | 00016414 | SPIMAINT | Overhaul ROTS No 6 220 Kv Line at YPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029033339904.2965277778 | 10290333 | 10289695 | Child | FALSE | ROTS NO.6 220KV LINE NO.1 BUS CB LINE SIDE E/SW AT YPS | 39904.2965 | 39904.6306 | DAILY | [12 empty] | 0
_1029020039904.3138888889 | 10290200 |  | Parent | FALSE | MLTS NO.2 220KV LINE AT BATS | 39904.3139 | 39904.7278 | REPDAILY | 00012431 | SPIMAINT | O/Haul MLTS No 2 Line at BATS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030240639904.33125 | 10302406 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 39904.3313 | 39904.65 | CONT | 00027386 | APDALCOA | APD No1 Line De_Energised for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1030220939904.4194444444 | 10302209 |  | Parent | FALSE | SVTS NO.2 220KV LINE NO.4 BUS CB AT ROTS | 39904.4194 | 39904.4208 | DAILY | [12 empty] | 0
_1030242139904.6736111111 | 10302421 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 39904.6736 | 39911.7903 | CONT | 00016423 | GENCO | YWPS No1 220kV Line VSCAP Issue to YWPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029065439905.2923611111 | 10290654 |  | Parent | FALSE | TTS 220KV LINE NO.1 BUS CB AT RWTS | 39905.2924 | 39906.5833 | CONT | [12 empty] | 0
_1029442539905.3090277778 | 10294425 |  | Parent | FALSE | EX - HWPS NO.1 220KV LINE CB CT R/PH AT YPS | 39905.309 | 39905.6139 | DAILY | [12 empty] | 0
_1030190239905.3090277778 | 10301902 |  | Parent | TRUE | YPS NO.1 220KV LINE NO.6 BUS CB AT HWPS | 39905.309 | 39905.6139 | DAILY | [12 empty] | 0
_1030202039905.3090277778 | 10302020 | 10301902 | Child | FALSE | YPS NO.1 220KV LINE AT HWPS | 39905.309 | 39905.6139 | DAILY | 00015795 | SPIMAINT | REBATE FOR CB OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X56558H539905.3090277778 | X56558H5 |  | Parent | FALSE | DDTS 330KV LINE NO.2 BUS CB AT WOTS | 39905.309 | 39908.2917 | CONT | [12 empty] | 0
_X7E458A239905.3131944445 | X7E458A2 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39905.3132 | 39905.6667 | DAILY | 00319998 | SPICAPX | Install OPGW between HYTS and T591 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029215039905.3152777778 | 10292150 |  | Parent | FALSE | DDTS NO.3 220KV LINE NO.1 BUS CB AT GNTS | 39905.3153 | 39906.491 | CONT | [12 empty] | 0
_1029020039905.3409722222 | 10290200 |  | Parent | FALSE | MLTS NO.2 220KV LINE AT BATS | 39905.341 | 39905.7229 | REPDAILY | 00012431 | SPIMAINT | O/Haul MLTS No 2 Line at BATS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030036639905.5666666667 | 10300366 |  | Parent | FALSE | BATS 220KV LINE NO.2 BUS CB AT TGTS | 39905.5667 | 39905.6035 | DAILY | [12 empty] | 0
_1030036739905.60625 | 10300367 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT TGTS | 39905.6062 | 39905.6292 | DAILY | [12 empty] | 0
_1030245939905.8951388889 | 10302459 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 39905.8951 | 39910.9461 | CONT | 00356081 | GENCO | HWPS No3 Gen Trans Isols for P/Stn | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028583139906.2972222222 | 10285831 |  | Parent | FALSE | B1 220/66KV TRANS AT BATS | 39906.2972 | 39906.6083 | DAILY | 00006554 | SPIMAINT | No1 Trans oil Leak at lid rear of trans | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029130839906.3173611111 | 10291308 |  | Parent | TRUE | BATS NO.2 220KV LINE CB AT MLTS | 39906.3174 | 39906.7069 | DAILY | [12 empty] | 0
_1030176939906.3173611111 | 10301769 | 10291308 | Child | FALSE | MLTS-BATS 2 220KV WY | 39906.3174 | 39906.7069 | DAILY | 00022731 | SPIMAINT | Rebate W/O BATS No2 Line during CB outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029442739906.3458333333 | 10294427 |  | Parent | FALSE | ROTS NO.5 220KV LINE NO.1 BUS CB CT R/PH AT YPS | 39906.3458 | 39906.3854 | DAILY | [12 empty] | 0
_V91058A639906.3715277778 | V91058A6 |  | Parent | FALSE | B1 220/66KV TRANS AT TTS | 39906.3715 | 39906.4028 | DAILY | 00367585 | SPIMAINT | hi pot 11kv cable | SPIPOWER | V910 | V910 - (TTS) INVESTIGATE & REPAIR - FAIL B1 TRANSFORMER | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030270139906.4819444444 | 10302701 |  | Parent | FALSE | NO.3 220KV BUS AT BLTS | 39906.4819 | 39906.5333 | CONT | 00002645 | FAULT | BLTS - Loss of No 3 220 kV Bus | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030276539906.4819444444 | 10302765 |  | Parent | FALSE | FBTS-BLTS 220KV WY | 39906.4819 | 39906.5333 | CONT | 00022666 | FAULT | BLTS - Loss of No 3 220 kV Bus | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1030276639906.4819444444 | 10302766 |  | Parent | FALSE | KTS -BLTS 220KV WY | 39906.4819 | 39906.5333 | CONT | 00022716 | FAULT | BLTS - Loss of No 3 220 kV Bus | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030266239906.5236111111 | 10302662 |  | Parent | FALSE | B3A 220/66KV TRANS BANK AT BLTS | 39906.5236 | 39906.7917 | DAILY | 00018491 | FAULT | replace damaged 22kv insulator on neutral bus | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030279039906.7020833333 | 10302790 |  | Parent | FALSE | DDTS 330KV LINE AT WOTS | 39906.7021 | 39906.7104 | DAILY | 00012054 | FAULT | Rebate W/O DDTS 330KV LINE AT WOTS | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030242239907.1305555556 | 10302422 |  | Parent | FALSE | LYBPS NO.2 500KV LINE AT LYPS | 39907.1306 | 39918.0062 | CONT | 00023076 | GENCO | SCAP to LYPSB | GENCO |  |  | Circuits | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1030277139907.3909722222 | 10302771 |  | Parent | FALSE | MLTS NO.2 500KV LINE CB AT HYTS | 39907.391 | 39907.6528 | CONT | [12 empty] | 0
_1030278439907.4326388889 | 10302784 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39907.4326 | 39907.6549 | CONT | 00002862 | FORCED | M2 Transf off loaded to avoid CB blocking SF6 | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030277239907.5979166667 | 10302772 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39907.5979 | 39909.6931 | CONT | 00356084 | GENCO | GenCo work | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X56558H639908.2986111111 | X56558H6 |  | Parent | FALSE | DDTS 330KV LINE AT WOTS | 39908.2986 | 39908.6597 | DAILY | 00012054 | SPICAPX | Out W/O DDTS Line to connect No2 Bus CB new CTs | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030278639908.73125 | 10302786 |  | Parent | FALSE | B2 220/66KV TRANS AT MWTS | 39908.7312 | 39908.7715 | CONT | 00010266 | FAULT | Rebate WO B2 220/66KV TRANS AT MWTS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030278739908.73125 | 10302787 |  | Parent | FALSE | JLTS NO.2 220KV LINE AT MWTS | 39908.7312 | 39908.7715 | CONT | 00016131 | FAULT | Rebate W/O JLTS NO.2 220KV LINE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030278839908.73125 | 10302788 |  | Parent | FALSE | LY NO.2 66KV FDR AT MWTS | 39908.7312 | 39908.7715 | CONT | 00016141 | FAULT | Rebate W/O LY NO.2 66KV LINE | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030277539908.73125 | 10302775 |  | Parent | FALSE | NO.2 66KV BUS AT MWTS | 39908.7312 | 39908.7729 | CONT | 00010279 | FAULT | NO.2 66KV BUS Trip | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X56558H739909.2895833333 | X56558H7 |  | Parent | FALSE | JINDERA 330KV LINE NO.2 BUS CB AT WOTS | 39909.2896 | 39912.4375 | CONT | [12 empty] | 0
_1029065039909.2930555556 | 10290650 |  | Parent | FALSE | TTS 220KV LINE NO.2 BUS CB AT RWTS | 39909.2931 | 39910.4868 | CONT | [12 empty] | 0
_1029286439909.2944444444 | 10292864 |  | Parent | FALSE | WMTS NO.1 220KV LINE AT FBTS | 39909.2944 | 39910.625 | CONT | 00017159 | SPIMAINT | INSPECT LINE AND CHECK SPILL GAP | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1029298839909.30625 | 10292988 |  | Parent | TRUE | NO.2A 66KV CAPACITOR BANK AT BETS | 39909.3063 | 39909.6611 | DAILY | 00350819 | SPIMAINT | O/H CAP BANK & EARTH SW | SPIPOWER |  |  | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1029299239909.30625 | 10292992 | 10292988 | Child | FALSE | NO.2B 66KV CAPACITOR BANK CB AT BETS | 39909.3063 | 39909.6611 | DAILY | [12 empty] | 0
_1030184439909.30625 | 10301844 | 10292988 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 39909.3063 | 39909.6611 | DAILY | 00016274 | SPIMAINT | Rebate W/O 2B Cap Bank during 2B CB & 2A cap OH | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028979139909.3131944445 | 10289791 |  | Parent | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 39909.3132 | 39909.6528 | DAILY | 00015793 | SPIMAINT | Overhaul 220 Kv LINE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030278139909.3166666667 | 10302781 |  | Parent | FALSE | HYTS NO.2/SYTS NO.2 LINE 500KV CB AT MLTS | 39909.3167 | 39909.4076 | DAILY | [12 empty] | 0
_1030280739909.6930555556 | 10302807 |  | Parent | FALSE | NO.6 GEN 220/16.5KV TRANS AT HWPS | 39909.6931 | 39911.5431 | CONT | 00009647 | GENCO | Power Station Requirements | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1029299039910.3020833333 | 10292990 |  | Parent | TRUE | NO.3A 66KV CAPACITOR BANK AT BETS | 39910.3021 | 39910.6458 | DAILY | 00350820 | SPIMAINT | O/H CAP BANK & EARTH SW | SPIPOWER |  |  | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1029299439910.3020833333 | 10292994 | 10292990 | Child | FALSE | NO.3B 66KV CAPACITOR BANK CB AT BETS | 39910.3021 | 39910.6458 | DAILY | [12 empty] | 0
_1030184639910.3020833333 | 10301846 | 10292990 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 39910.3021 | 39910.6458 | DAILY | 00016304 | SPIMAINT | Rebate W/O 3B Cap Bank during 3B CB & 3A cap OH | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458A439910.3104166667 | X7E458A4 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39910.3104 | 39910.741 | DAILY | 00319998 | SPICAPX | Out W/O APD No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030185539910.3201388889 | 10301855 |  | Parent | FALSE | A1 515/230KV TRANS AT HWTS | 39910.3201 | 39910.6097 | DAILY | 00009772 | SPIMAINT | Washdown after Bushfires & disconnect Unit Transf | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009262339910.3347222222 | 10092623 |  | Parent | TRUE | MBTS NO.1 220KV LINE CB AT DDTS | 39910.3347 | 39910.6736 | DAILY | [12 empty] | 0
_1030184839910.3347222222 | 10301848 | 10092623 | Child | FALSE | MBTS NO.1 220KV LINE AT DDTS | 39910.3347 | 39910.6736 | DAILY | 00012361 | SPIMAINT | Rebate W/O MBTS No1 Line during CB outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027333939910.3618055556 | 10273339 |  | Parent | TRUE | EX - APD-MLTS NO.1 500KV LINE CT R/PH AT HYTS | 39910.3618 | 39910.5312 | DAILY | [12 empty] | 0
_1030192039910.3618055556 | 10301920 | 10273339 | Child | FALSE | MLTS-HYTS 1 500KV W | 39910.3618 | 39910.5312 | DAILY | 00022630 | SPIMAINT | Rebate W/O MLTS-HYTS No1 Line during CT sampling | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030192339910.3618055556 | 10301923 | 10273339 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 39910.3618 | 39910.5312 | DAILY | 00003007 | SPIMAINT | Rebate W/O HYTS No1 line React during line outage | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030065939910.3618055556 | 10300659 |  | Parent | TRUE | MLTS NO.1 500KV LINE CB AT HYTS | 39910.3618 | 39910.534 | DAILY | [12 empty] | 0
_1030194639910.3618055556 | 10301946 | 10300659 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39910.3618 | 39910.534 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during MLTS No1 line outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028969339911.2486111111 | 10289693 |  | Parent | TRUE | NO.2 22KV BUS AT BETS | 39911.2486 | 39911.7826 | DAILY | 00016376 | SPIMAINT | O/Haul NO.2 22KV BUS AT BETS | SPIPOWER |  |  | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1030184739911.2486111111 | 10301847 | 10289693 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39911.2486 | 39911.7826 | DAILY | 00016040 | SPIMAINT | Perf W/O No2 Tr GRP during No2 22 Bus overhaul | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1009261839911.3069444444 | 10092618 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT DDTS | 39911.3069 | 39911.7625 | DAILY | 00012361 | SPIMAINT | O/Haul Line End equipment | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027333539911.3472222222 | 10273335 |  | Parent | TRUE | EX - APD-MLTS NO.2 500KV LINE CT R/PH AT HYTS | 39911.3472 | 39911.5188 | DAILY | [12 empty] | 0
_1030192439911.3472222222 | 10301924 | 10273335 | Child | FALSE | MLTS-HYTS 2 500KV W | 39911.3472 | 39911.5188 | DAILY | 00022633 | SPIMAINT | Rebate W/O MLTS-HYTS No2 Line during CT sampling | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030192739911.3472222222 | 10301927 | 10273335 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 39911.3472 | 39911.5188 | DAILY | 00002862 | SPIMAINT | Rebate W/O M2 Trans during CT Sampling MLTS-HYT 2L | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030192839911.3472222222 | 10301928 | 10273335 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 39911.3472 | 39911.5188 | DAILY | 00003008 | SPIMAINT | Rebate W/O HYTS No2 line React during line outage | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030065739911.3472222222 | 10300657 |  | Parent | FALSE | MLTS NO.2 500KV LINE CB AT HYTS | 39911.3472 | 39911.5201 | DAILY | [12 empty] | 0
_1030265739911.3770833333 | 10302657 |  | Parent | FALSE | JLGA NO.3 UNIT TRANS DISC CB AT JLGA | 39911.3771 | 39927.5542 | CONT | [12 empty] | 0
_1030286639911.4597222222 | 10302866 |  | Parent | FALSE | EX - NO.1 MAIN TRANS 500KV CB AT HWTS | 39911.4597 | 39911.6792 | DAILY | [12 empty] | 0
_1030285139911.51875 | 10302851 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39911.5188 | 39911.6687 | DAILY | 00319999 | APDALCOA | SCAP to APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1030288639911.6131944444 | 10302886 |  | Parent | FALSE | B2 TRANS 66KV CB AT WBTS | 39911.6132 | 39925.6667 | CONT | [12 empty] | 0
_1030287439912.4131944444 | 10302874 |  | Parent | FALSE | JLGA NO.2 UNIT TRANS DISC CB AT JLGA | 39912.4132 | 39912.6056 | DAILY | [12 empty] | 0
_1029433339912.4166666667 | 10294333 |  | Parent | TRUE | EX - GNTS NO.1 220KV LINE CB CT R/PH AT DDTS | 39912.4167 | 39912.4826 | DAILY | [12 empty] | 0
_1030184939912.4166666667 | 10301849 | 10294333 | Child | FALSE | GNTS NO.1 220KV LINE AT DDTS | 39912.4167 | 39912.4826 | DAILY | 00352475 | SPIMAINT | Rebate W/O GNTS No1 Line during CB outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030293239912.6458333333 | 10302932 |  | Parent | FALSE | B1 220/66KV TRANS AT TTS | 39912.6458 | 39922.5076 | CONT | 00367585 | SPIMAINT | B1 Transformer Conservator repair | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030294139912.8698842593 | 10302941 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 39912.8699 | 39913.4167 | CONT | [12 empty] | 0
_1030284539913.4166666667 | 10302845 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 39913.4167 | 39940.5628 | CONT | [12 empty] | 0
_1030294639913.4930555556 | 10302946 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 39913.4931 | 39913.5417 | CONT | 00016423 | GENCO | Isolate YWPS Unit 220kV Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030294939914.5916666667 | 10302949 |  | Parent | FALSE | MLRC 220KV LINE NO.2 BUS CB AT RCTS | 39914.5917 | 39914.6333 | CONT | [12 empty] | 4
_1030294039917.3166666667 | 10302940 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39917.3167 | 39917.6576 | REPDAILY | 00319999 | APDALCOA | de-energise for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1030297039918.1784722222 | 10302970 |  | Parent | FALSE | HYTS NO.1 500KV LINE AT MLTS | 39918.1785 | 39918.4597 | CONT | 00022695 | FAULT | Trip MLTS-HYTS No 1 500kV LINE no cause found | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030304939918.1784722222 | 10303049 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39918.1785 | 39918.4597 | CONT | 00319998 | FAULT | Trip HYTS-APD 1 500KV | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030305239918.1784722222 | 10303052 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39918.1785 | 39918.4597 | CONT | 00002863 | FAULT | M1 Transf off loaded by Line fault | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029063139918.2916666667 | 10290631 |  | Parent | TRUE | L3 220/22KV TRANS BANK AT RWTS | 39918.2917 | 39919.7181 | CONT | 00007452 | SPIMAINT | Overhaul Trans | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029066639918.2916666667 | 10290666 | 10290631 | Child | FALSE | L3 TRANS 220KV CB AT RWTS | 39918.2917 | 39919.7181 | CONT | [12 empty] | 0
_1029541339918.2916666667 | 10295413 | 10290631 | Child | FALSE | L3 TRANS 22KV CB AT RWTS | 39918.2917 | 39919.7181 | CONT | [12 empty] | 0
_1029285539918.2930555556 | 10292855 |  | Parent | FALSE | BLTS 220KV LINE AT FBTS | 39918.2931 | 39919.6312 | CONT | 00002660 | SPIMAINT | INSPECT LINE AND CHECK SPILL GAP | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1030186239918.3569444444 | 10301862 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 39918.3569 | 39918.6486 | DAILY | 00337579 | SPIMAINT | WASH DOWN TX AFTER FIRES | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030302539918.6173611111 | 10303025 |  | Parent | FALSE | B2 220/66KV TRANS AT WBTS | 39918.6174 | 39932.75 | CONT | 00366200 | GENCO | De-energised at Acciona request | GENCO |  |  | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1030303439918.9305555556 | 10303034 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 39918.9306 | 39920.9396 | CONT | 00356081 | GENCO | Power Station Requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030306039919.25 | 10303060 |  | Parent | FALSE | HWPS NO.1 220KV LINE AT JLTS | 39919.25 | 39919.3264 | DAILY | 00015936 | REM_TRIP | Remote Trip JLGS B P/Stn Transf fault. | GENCO |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030294039919.3138888889 | 10302940 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39919.3139 | 39919.6417 | REPDAILY | 00319999 | APDALCOA | de-energise for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1030186439919.3229166667 | 10301864 |  | Parent | FALSE | A4 515/230KV TRANS BANK AT HWTS | 39919.3229 | 39919.6826 | DAILY | 00337582 | SPIMAINT | WASH DOWN TX AFTER FIRES | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030305139919.4416666667 | 10303051 |  | Parent | FALSE | JLGA NO.3 UNIT TRANS DISC CB AT JLGA | 39919.4417 | 39919.625 | CONT | [12 empty] | 0
_1029429139920.3006944444 | 10294291 |  | Parent | TRUE | NO.4 220KV CAPACITOR BANK CB CT R/PH AT FBTS | 39920.3007 | 39920.5069 | DAILY | [12 empty] | 0
_1030326839920.3006944444 | 10303268 | 10294291 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 39920.3007 | 39920.5069 | DAILY | 00327661 | SPIMAINT | OUT W/O FOR CT OIL SAMPLING | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030258939920.3173611111 | 10302589 | Z63358L1 | Child | FALSE | JLTS NO.3 220KV LINE AT HWPS | 39920.3174 | 39920.6285 | DAILY | 00015787 | VEN_AUG | LINE REBATE FOR CB OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358L139920.3173611111 | Z63358L1 |  | Parent | TRUE | JLTS NO.3 220KV LINE CVT R/PH AT HWPS | 39920.3174 | 39920.6285 | DAILY | [12 empty] | 0
_1030294039920.3180555556 | 10302940 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39920.3181 | 39920.6528 | REPDAILY | 00319999 | APDALCOA | de-energise for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1030190639920.3493055556 | 10301906 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT GTS | 39920.3493 | 39920.4215 | DAILY | 00350421 | SPIMAINT | Remove weeds and spray inside enclosure | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030309739920.35 | 10303097 |  | Parent | FALSE | B3 220/66KV TRANS AT SMTS | 39920.35 | 39920.6215 | DAILY | 00366622 | SPIMAINT | replace bolts on conserator support structure | SPIPOWER |  |  | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1029427739920.5284722222 | 10294277 |  | Parent | TRUE | EX - NO.4 220KV CAPACITOR BANK CB CT R/PH AT BLTS | 39920.5285 | 39920.5743 | DAILY | [12 empty] | 0
_1030327039920.5284722222 | 10303270 | 10294277 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT BLTS | 39920.5285 | 39920.5743 | DAILY | 00327921 | SPIMAINT | OUT W/O FOR CT OIL SAMPLING | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X50858V539921.2298611111 | X50858V5 |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 39921.2299 | 39921.7215 | DAILY | 00002834 | SPICAPX | Instal Bipods to Fut PTH 2 Ln CB Bus Side ROI | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858V639921.2298611111 | X50858V6 | X50858V5 | Child | FALSE | B4 220/66KV TRANS AT GTS | 39921.2299 | 39921.7215 | DAILY | 00002830 | SPICAPX | Rebate W/O B4 Trans during No2 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858V739921.2298611111 | X50858V7 | X50858V5 | Child | FALSE | EX - MLTS NO.1 220KV LINE AT GTS | 39921.2299 | 39921.7215 | DAILY | 00017903 | SPICAPX | Rebate W/O MLTS No1 Ln during No2 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858V839921.2298611111 | X50858V8 | X50858V5 | Child | FALSE | KTS NO.2 220KV LINE AT GTS | 39921.2299 | 39921.7215 | DAILY | 00367295 | SPICAPX | Rebate W/O KTS No2 Ln during No2 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858V939921.2298611111 | X50858V9 | X50858V5 | Child | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39921.2299 | 39921.7215 | DAILY | 00017906 | SPICAPX | Rebate W/O PTH No2 Ln during No2 220 Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030295939921.2680555556 | 10302959 |  | Parent | FALSE | NO.3 GEN TRANS 500KV LINE E/SW AT LYPS | 39921.2681 | 39926.6708 | CONT | [12 empty] | 0
_X87058B339921.3013888889 | X87058B3 |  | Parent | FALSE | BATS-BETS 220KV | 39921.3014 | 39921.7229 | REPDAILY | 00328505 | SPICAPX | BATS-BETS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030318339921.3145833333 | 10303183 |  | Parent | FALSE | S431 DDTS-SMTS 2 330KV | 39921.3146 | 39921.5306 | DAILY | 00294057 | FORCED | Replace damaged Insulators DDTS-SMTS 2 Line S431 | SPIPOWER | [8 empty] | 0 | 10303183 |  | Replace damaged Insulators DDTS-SMTS 2 Line S431 | 00294057 | SPAN |  | DDTSSMTS2B | SPAN | FORCED | DAILY
_X71558C839921.3333333333 | X71558C8 |  | Parent | TRUE | NO.1 275KV CAPACITOR BANK/SESS NO.2 LINE CB AT HYTS | 39921.3333 | 39921.7285 | REPDAILY | [12 empty] | 0
_X71558C939921.3333333333 | X71558C9 | X71558C8 | Child | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 39921.3333 | 39921.7285 | DAILY | 00331027 | SPICAPX | Rebate W/O No1 Cap bk during CB outage | SPIPOWER | X715 | X715 - (HYTS) REPLACEMENT OF RTU AND HMI | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X50858W139922.2305555556 | X50858W1 |  | Parent | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39922.2306 | 39922.6181 | REPDAILY | 00017906 | SPICAPX | Install Conductors PTH 2 Ln from Rack to 1st Twr | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z51358CL39922.2930555556 | Z51358CL |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT RWTS | 39922.2931 | 39922.3347 | DAILY | [12 empty] | 0
_X87058B339922.2993055556 | X87058B3 |  | Parent | FALSE | BATS-BETS 220KV | 39922.2993 | 39922.7049 | REPDAILY | 00328505 | SPICAPX | BATS-BETS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030291739922.3347222222 | 10302917 |  | Parent | FALSE | NO.1 22KV BUS AT BLTS | 39922.3347 | 39922.484 | DAILY | 00002654 | SPIMAINT | Jemena to replace faulty droppers | SPIPOWER |  |  | Bus | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X71558C839922.3347222222 | X71558C8 |  | Parent | TRUE | NO.1 275KV CAPACITOR BANK/SESS NO.2 LINE CB AT HYTS | 39922.3347 | 39922.6181 | REPDAILY | [12 empty] | 0
_X71558C939922.3347222222 | X71558C9 | X71558C8 | Child | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 39922.3347 | 39922.6181 | DAILY | 00331027 | SPICAPX | Rebate W/O No1 Cap bk during CB outage | SPIPOWER | X715 | X715 - (HYTS) REPLACEMENT OF RTU AND HMI | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030292039922.5173611111 | 10302920 |  | Parent | FALSE | NO.2 22KV BUS AT BLTS | 39922.5174 | 39922.6472 | DAILY | 00002655 | SPIMAINT | Jemena to replace faulty droppers | SPIPOWER |  |  | Bus | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X71558C639922.6180555556 | X71558C6 |  | Parent | TRUE | NO.1 275KV CAPACITOR BANK/SESS NO.1 LINE CB AT HYTS | 39922.6181 | 39922.7243 | DAILY | [12 empty] | 0
_X71558C739922.6180555556 | X71558C7 | X71558C6 | Child | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 39922.6181 | 39922.7243 | DAILY | 00331027 | SPICAPX | Rebate W/O No1 Cap bk during CB outage | SPIPOWER | X715 | X715 - (HYTS) REPLACEMENT OF RTU AND HMI | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X50858W139923.2354166667 | X50858W1 |  | Parent | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39923.2354 | 39923.709 | REPDAILY | 00017906 | SPICAPX | Install Conductors PTH 2 Ln from Rack to 1st Twr | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029410039923.2930555556 | 10294100 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39923.2931 | 39927.4125 | CONT | 00002862 | SPIMAINT | Condition Monitoring Program Transfs Northern Area | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029066239923.2951388889 | 10290662 |  | Parent | FALSE | B3 TRANS 220KV CB AT RWTS | 39923.2951 | 39924.691 | CONT | [12 empty] | 0
_1029045839923.2958333333 | 10290458 |  | Parent | TRUE | NO.1 500KV BUS AT HWTS | 39923.2958 | 39923.684 | DAILY | 00009798 | SPIMAINT | O/Haul NO.1 500KV BUS AT HWTS | SPIPOWER |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1030109439923.2958333333 | 10301094 |  | Parent | FALSE | A3 TRANS NO.1 BUS 500KV CB BUS SIDE ROI AT HWTS | 39923.2958 | 39923.684 | DAILY | [12 empty] | 0
_1030204439923.2958333333 | 10302044 | 10290458 | Child | FALSE | HWPS NO.1 220KV LINE AT HWTS | 39923.2958 | 39923.684 | DAILY | 00016241 | SPIMAINT | REBATE FOR BUS OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029285339923.3020833333 | 10292853 |  | Parent | FALSE | NPSD 220KV LINE AT BLTS | 39923.3021 | 39924.6667 | CONT | 00024014 | SPIMAINT | INSPECTION OF LINE (NPSD 220KV) AT BLTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030010339923.5118055556 | 10300103 |  | Parent | FALSE | WOTS 330KV LINE NO.2 BUS CB LINE SIDE ISOL AT DDTS | 39923.5118 | 39923.5542 | DAILY | [12 empty] | 0
_X50858W239924.2305555556 | X50858W2 |  | Parent | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39924.2306 | 39924.6667 | DAILY | 00017906 | SPICAPX | Install bridges PTH 2 Ln from Rack to harpstrings | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029046339924.3159722222 | 10290463 |  | Parent | TRUE | NO.3 500KV BUS AT HWTS | 39924.316 | 39924.65 | DAILY | 00009800 | SPIMAINT | O/Haul NO.3 500KV BUS AT HWTS | SPIPOWER |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1029681939924.3159722222 | 10296819 |  | Parent | FALSE | CBTS NO.4 500KV LINE NO.3 BUS CB BUS SIDE ROI AT HWTS | 39924.316 | 39924.65 | DAILY | [12 empty] | 0
_1030060539924.3159722222 | 10300605 | 10290463 | Child | FALSE | CBTS NO.4 500KV LINE NO.3 BUS CB AT HWTS | 39924.316 | 39924.65 | DAILY | [12 empty] | 0
_1030060639924.3159722222 | 10300606 | 10290463 | Child | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB AT HWTS | 39924.316 | 39924.65 | DAILY | [12 empty] | 0
_1030322339924.4493055556 | 10303223 |  | Parent | FALSE | JLGA NO.4 UNIT TRANS DISC CB AT JLGA | 39924.4493 | 39927.6514 | CONT | [12 empty] | 0
_X50858W339925.2291666667 | X50858W3 |  | Parent | FALSE | EX - PT. HENRY NO.2 220KV LINE AT GTS | 39925.2292 | 39925.7285 | REPDAILY | 00017906 | SPICAPX | Remove redundant conductors, rack - first tower | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029064639925.2854166667 | 10290646 |  | Parent | FALSE | ROTS 220KV LINE NO.1 BUS CB AT RWTS | 39925.2854 | 39926.5882 | CONT | [12 empty] | 0
_1029285139925.2951388889 | 10292851 |  | Parent | FALSE | FBTS 220KV LINE AT BLTS | 39925.2951 | 39926.7132 | CONT | 00024012 | SPIMAINT | INSPECTION OF LINE (FBTS 220KV) AT BLTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1028434239925.3055555556 | 10284342 |  | Parent | FALSE | JINDERA 330KV LINE NO.1 BUS CB AT WOTS | 39925.3056 | 39948.7167 | DAILY | [12 empty] | 0
_1029046539925.3166666667 | 10290465 |  | Parent | TRUE | NO.4 500KV BUS AT HWTS | 39925.3167 | 39925.6146 | DAILY | 00009801 | SPIMAINT | O/Haul NO.4 500KV BUS AT HWTS | SPIPOWER |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1030060739925.3166666667 | 10300607 | 10290465 | Child | FALSE | LYPS NO.3 500KV LINE NO.4 BUS CB AT HWTS | 39925.3167 | 39925.6146 | DAILY | [12 empty] | 0
_1030061139925.3166666667 | 10300611 | 10290465 | Child | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 39925.3167 | 39925.6146 | DAILY | [12 empty] | 0
_1030109739925.3166666667 | 10301097 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB BUS SIDE ROI AT HWTS | 39925.3167 | 39925.6146 | DAILY | [12 empty] | 0
_1030109839925.3166666667 | 10301098 |  | Parent | FALSE | LYPS NO.3 500KV LINE NO.4 BUS CB BUS SIDE ROI AT HWTS | 39925.3167 | 39925.6146 | DAILY | [12 empty] | 0
_1030323439925.3361111111 | 10303234 |  | Parent | FALSE | EX - FUTURE KMS 66KV FDR CB AT SMTS | 39925.3361 | 40142.3333 | CONT | [12 empty] | 0
_1030297439925.35625 | 10302974 |  | Parent | FALSE | R3 TRANS NO.2 BUS 220KV CB AT RCTS | 39925.3562 | 39925.3965 | DAILY | [12 empty] | 0
_1030225539925.40625 | 10302255 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 39925.4062 | 39925.5972 | REPDAILY | 00119824 | SPIMAINT | carry out ct secondary tests | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X56558I139925.4208333333 | X56558I1 |  | Parent | FALSE | WBTS 220KV LINE NO.1 TIE BUS AT BATS | 39925.4208 | 39930.5146 | CONT | 00362536 | SPICAPX | Out W/O WBTS Line No1 Tie CT replacement | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030297639925.4270833333 | 10302976 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT RCTS | 39925.4271 | 39925.4743 | DAILY | [12 empty] | 0
_1030297539925.5409722222 | 10302975 |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT RCTS | 39925.541 | 39925.5833 | DAILY | [12 empty] | 0
_Z51358CN39926.2944444444 | Z51358CN |  | Parent | FALSE | L2 220/22KV TRANS BANK AT RWTS | 39926.2944 | 39926.5382 | DAILY | 00007447 | DB_AUG | Testing of SCIMS points with Jemena | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030326739926.3347222222 | 10303267 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39926.3347 | 39926.6431 | DAILY | 00319999 | APDALCOA | Outage Requested by APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z51358CO39927.3659722222 | Z51358CO |  | Parent | FALSE | B1 220/66KV TRANS AT RWTS | 39927.366 | 39927.6076 | DAILY | 00364702 | DB_AUG | Testing of SCIMS points with JEMENA | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_Z51358CP39927.6090277778 | Z51358CP |  | Parent | FALSE | B2 220/66KV TRANS AT RWTS | 39927.609 | 39927.7042 | DAILY | 00007450 | DB_AUG | Testing of SCIMS points with Jemena | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858W439928.2506944445 | X50858W4 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39928.2507 | 39928.6271 | DAILY | 00002833 | SPICAPX | Replace Bus Insulators & remove OOS Pth 2 BS ROI | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858W539928.2506944445 | X50858W5 | X50858W4 | Child | FALSE | PT. HENRY NO.1 220KV LINE AT GTS | 39928.2507 | 39928.6271 | DAILY | 00367277 | SPICAPX | Rebate W/O PTH 1 Ln during No1 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858W639928.2506944445 | X50858W6 | X50858W4 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 39928.2507 | 39928.6271 | DAILY | 00366646 | SPICAPX | Rebate W/O MLTS 2 Ln during No1 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858W739928.2506944445 | X50858W7 | X50858W4 | Child | FALSE | KTS NO.1 220KV LINE AT GTS | 39928.2507 | 39928.6271 | DAILY | 00367291 | SPICAPX | Rebate W/O KTS 1 Ln during No1 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058D439928.2506944445 | X87058D4 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 39928.2507 | 39928.6271 | DAILY | 00022702 | SPICAPX | KTS-GTS No1 220kv Line insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058B439928.3034722222 | X87058B4 |  | Parent | FALSE | BATS-BETS 220KV | 39928.3035 | 39928.6542 | REPDAILY | 00328505 | SPICAPX | BATS-BETS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030330139928.6597222222 | 10303301 |  | Parent | FALSE | EX - NO.3 GEN TRANS NO.1 BUS 220KV CB BUS SIDE ISOL AT HWPS | 39928.6597 | 39930.9514 | CONT | [12 empty] | 0
_X87058B439929.3125 | X87058B4 |  | Parent | FALSE | BATS-BETS 220KV | 39929.3125 | 39929.5208 | REPDAILY | 00328505 | SPICAPX | BATS-BETS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030323139930.2520833333 | 10303231 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39930.2521 | 39933.934 | CONT | 00319998 | APDALCOA | Outage Requested by APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1030329139930.3506944444 | 10303291 |  | Parent | FALSE | JLGA NO.2 UNIT TRANS DISC CB AT JLGA | 39930.3507 | 39933.4896 | CONT | [12 empty] | 0
_1030330539930.3583333333 | 10303305 |  | Parent | FALSE | NO.1 CSC AT ROTS | 39930.3583 | 39931.6042 | CONT | 00004718 | FAULT | No1 CSC opened Auto due to thyristor fault | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X56558I239930.4270833333 | X56558I2 |  | Parent | TRUE | NO.1 220KV BUS AT BATS | 39930.4271 | 39930.5146 | DAILY | 00006558 | SPICAPX | Out W/O #1 220 bus de-energ to commiss new tie CTs | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X56558I439930.4270833333 | X56558I4 | X56558I2 | Child | FALSE | B2 220/66KV TRANS AT BATS | 39930.4271 | 39930.5146 | DAILY | 00006555 | SPICAPX | Perf calc W/O #2 Trans during #1 220 Bus de-energ | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858X239931.2465277778 | X50858X2 |  | Parent | FALSE | EX - MLTS NO.1 220KV LINE AT GTS | 39931.2465 | 39956.6667 | CONT | 00017903 | SPICAPX | Remove MLTS 1 Line equipment and Foundations | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027329139931.2916666667 | 10273291 |  | Parent | TRUE | EX - F2 TRANS 330KV CB CT R/PH AT SMTS | 39931.2917 | 39931.4826 | DAILY | [12 empty] | 0
_1030346739931.2916666667 | 10303467 | 10273291 | Child | FALSE | F2 500/330KV TRANS BANK AT SMTS | 39931.2917 | 39931.4826 | DAILY | 00026099 | SPIMAINT | OUT W/O FOR CT OIL SAMPLING | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028872639931.29375 | 10288726 | 10291482 | Child | FALSE | KTS NO.2 220KV LINE AT WMTS | 39931.2937 | 39932.6389 | DAILY | 00025731 | SPIMAINT | OVERHAUL OF A 220KV LINE | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029148239931.29375 | 10291482 |  | Parent | TRUE | KTS NO.2 220KV LINE CB AT WMTS | 39931.2937 | 39932.6389 | CONT | [12 empty] | 0
_1029080239931.2979166667 | 10290802 | 10290818 | Child | FALSE | NO.1 66KV CAPACITOR BANK CB AT SVTS | 39931.2979 | 39931.625 | DAILY | [12 empty] | 0
_1029081839931.2979166667 | 10290818 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK AT SVTS | 39931.2979 | 39931.625 | DAILY | 00004824 | SPIMAINT | Overhaqul Cap Bank & Earth Switch | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030337639931.5881944444 | 10303376 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39931.5882 | 39931.6 | DAILY | [12 empty] | 0
_1030340439931.7138888889 | 10303404 |  | Parent | FALSE | NO.1 CSC AT ROTS | 39931.7139 | 39931.9167 | CONT | 00004718 | FAULT | Failure to reset Power System Stabiliser | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z64558D839932.2756944444 | Z64558D8 |  | Parent | FALSE | WBTS 220KV LINE AT HOTS | 39932.2757 | 39932.8243 | DAILY | 00018717 | VEN_AUG | Out W/O WBTS Line to install LS isol aux sw linkag | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X74158A439932.3180555556 | X74158A4 |  | Parent | TRUE | EX - HWPS NO.1 220KV LINE CB CT R/PH AT YPS | 39932.3181 | 39934.6222 | CONT | [12 empty] | 0
_X74158A539932.3180555556 | X74158A5 | X74158A4 | Child | FALSE | HWPS NO.1 220KV LINE AT YPS | 39932.3181 | 39934.6222 | CONT | 00016409 | SPICAPX | REBATE FOR CB OUTAGE | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z64558E539932.7506944445 | Z64558E5 |  | Parent | FALSE | B2 220/66KV TRANS AT WBTS | 39932.7507 | 39947.5889 | DAILY | 00366200 | VEN_AUG | Out W/O B2 Trans de-energ for AVR testing | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_X50858V439933.2347222222 | X50858V4 |  | Parent | FALSE | NO.6 66KV BUS AT GTS | 39933.2347 | 39933.7951 | CONT | 00002840 | SPICAPX | Install Sub CLC-WIN 66kv Fdr CB and connections | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029125539933.2930555556 | 10291255 |  | Parent | TRUE | FBTS NO.2 220KV LINE CB AT WMTS | 39933.2931 | 39934.6431 | CONT | [12 empty] | 0
_1029286939933.2930555556 | 10292869 | 10291255 | Child | FALSE | FBTS NO.2 220KV LINE AT WMTS | 39933.2931 | 39934.6431 | CONT | 00025736 | SPIMAINT | INSPECTION OF LINE (FBTS NO.2 220KV) AT WMTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1029080539933.2965277778 | 10290805 | 10290812 | Child | FALSE | NO.1 TRANS 66KV CB AT SVTS | 39933.2965 | 39933.5993 | DAILY | [12 empty] | 0
_1029081239933.2965277778 | 10290812 |  | Parent | TRUE | B1 220/66KV TRANS AT SVTS | 39933.2965 | 39933.5993 | DAILY | 00004849 | SPIMAINT | O/HAUL Transformer Div Mechanism (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029081439934.2951388889 | 10290814 |  | Parent | TRUE | B2 220/66KV TRANS AT SVTS | 39934.2951 | 39934.5201 | DAILY | 00004850 | SPIMAINT | O/HAUL Transformer Div Mechanism (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029573039934.2951388889 | 10295730 | 10290814 | Child | FALSE | NO.2 TRANS 66KV CB AT SVTS | 39934.2951 | 39934.5201 | DAILY | [12 empty] | 0
_1030344539934.2965277778 | 10303445 |  | Parent | FALSE | YWPS NO.4 220KV LINE AT YPS | 39934.2965 | 39941.3688 | CONT | 00016428 | GENCO | YWPS No4 Gen Request SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z51358CN39934.3013888889 | Z51358CN |  | Parent | FALSE | L2 220/22KV TRANS BANK AT RWTS | 39934.3014 | 39934.5076 | DAILY | 00007447 | DB_AUG | Testing of SCIMS points with Jemena | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030344339934.3055555556 | 10303443 |  | Parent | FALSE | EX - A4 TRANS NO.1 BUS 500KV CB AT KTS | 39934.3056 | 39934.6167 | DAILY | [12 empty] | 0
_1029865639934.41875 | 10298656 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT CBTS | 39934.4187 | 39934.55 | DAILY | 00359493 | SPIMAINT | CBTS A1 Trans Hydrans | SPIPOWER |  |  | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_Z51358CM39934.5125 | Z51358CM |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 39934.5125 | 39934.7 | DAILY | 00007452 | DB_AUG | Testing of SCIMS points with Jemena | SPIPOWER | Z513 | Z513 - (RWTS) ADD 4TH TRANSFORMER RECON 66KV BUSBAR | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030347239934.5513888889 | 10303472 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT RWTS | 39934.5514 | 39934.6021 | DAILY | [12 empty] | 0
_1030347939934.5513888889 | 10303479 | 10303472 | Child | FALSE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39934.5514 | 39934.6021 | DAILY | 00007399 | SPIMAINT | Rebate for outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030348039934.5513888889 | 10303480 | 10303472 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39934.5514 | 39934.6021 | DAILY | 00331179 | SPIMAINT | rebate 2b Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030349239934.6736111111 | 10303492 |  | Parent | TRUE | EX - NO.1 MAIN TRANS 500KV CB AT HWTS | 39934.6736 | 39934.834 | DAILY | [12 empty] | 0
_1030349339934.6736111111 | 10303493 | 10303492 | Child | FALSE | A1 515/230KV TRANS AT HWTS | 39934.6736 | 39934.834 | DAILY | 00009772 | SPIMAINT | TX REBATE FOR CB OUTAGE | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030361539935.2395833333 | 10303615 | X70658A9 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 39935.2396 | 39935.691 | DAILY | 00026097 | SPICAPX | out w/o bi-pods to from 2bus to fut a3 tr 220kv cb | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X70658A939935.2395833333 | X70658A9 |  | Parent | TRUE | NO.2 220KV BUS AT KTS | 39935.2396 | 39935.691 | DAILY | 00001170 | SPICAPX | bi-pods to from 2 bus to future a3 tr 220kv cb | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030342439935.2395833333 | 10303424 |  | Parent | FALSE | B4 220/66KV TRANS AT KTS | 39935.2396 | 39938.5597 | DAILY | 00001146 | SPIMAINT | investigate high resistance in the mech rotary sw | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z63358L439935.25 | Z63358L4 |  | Parent | TRUE | NO.1 220KV BUS AT JLTS | 39935.25 | 39935.734 | DAILY | 00365901 | VEN_AUG | CHANGE BYPODS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358L539935.25 | Z63358L5 | Z63358L4 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 39935.25 | 39935.734 | DAILY | 00015936 | VEN_AUG | REBATE FOR BUS OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058D039935.2923611111 | X87058D0 |  | Parent | FALSE | BATS-BETS 220KV | 39935.2924 | 39935.7014 | REPDAILY | 00328505 | SPICAPX | BATS-BETS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030350639935.3541666667 | 10303506 |  | Parent | FALSE | NO.1A 66KV CAPACITOR BANK AT HOTS | 39935.3542 | 39935.5938 | DAILY | 00359898 | SPIMAINT | Replacement for No2 Cap Bank work | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030356939935.7215277778 | 10303569 |  | Parent | FALSE | EX - A3 TRANS 220KV CB CVT R/PH AT KTS | 39935.7215 | 39940.4451 | CONT | [12 empty] | 0
_1007159039936.2902777778 | 10071590 |  | Parent | TRUE | S006 SVTS-HTS 2 220KV | 39936.2903 | 39936.7243 | DAILY | [12 empty] | 0
_1030347839936.2902777778 | 10303478 | 10071590 | Child | FALSE | HTS NO.2 220KV LINE AT SVTS | 39936.2903 | 39936.7243 | DAILY | 00351702 | SPIMAINT | Rebate for line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058D039936.29375 | X87058D0 |  | Parent | FALSE | BATS-BETS 220KV | 39936.2937 | 39936.6632 | REPDAILY | 00328505 | SPICAPX | BATS-BETS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7G358A639937.2951388889 | X7G358A6 |  | Parent | FALSE | EX - B1 220/66KV TRANS 66KV SD R/PH AT HTS | 39937.2951 | 39937.6264 | REPDAILY | [12 empty] | 0
_1029386439937.2965277778 | 10293864 |  | Parent | FALSE | LNGS NO.1 GEN TRANS 220KV LINE AT ATS | 39937.2965 | 39938.6944 | CONT | 00360128 | SPIMAINT | OVERHAUL THE 220KV LINE | SPIPOWER |  |  | Circuits | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029411639937.3125 | 10294116 |  | Parent | FALSE | A2 515/230KV TRANS BANK AT HWTS | 39937.3125 | 39941.8618 | CONT | 00337572 | SPIMAINT | Condition Monitoring Metro Trans 3day Valley Area | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030305439937.3243055556 | 10303054 |  | Parent | FALSE | BATS NO.1 LINE/TGTS LINE 220KV CB AT MLTS | 39937.3243 | 39937.3917 | DAILY | [12 empty] | 0
_1030305839937.4166666667 | 10303058 |  | Parent | FALSE | BATS NO.1 220KV LINE NO.1 BUS CB AT MLTS | 39937.4167 | 39937.4542 | DAILY | [12 empty] | 0
_1030305639937.4548611111 | 10303056 |  | Parent | FALSE | TGTS 220KV LINE NO.2 BUS CB AT MLTS | 39937.4549 | 39937.5174 | DAILY | [12 empty] | 0
_1030345739937.5 | 10303457 |  | Parent | FALSE | EPG NO.1 66KV FDR CB AT SMTS | 39937.5 | 39937.6056 | CONT | [12 empty] | 0
_1030357239938.0388888889 | 10303572 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39938.0389 | 39943.7083 | CONT | 00356082 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029131739938.2743055556 | 10291317 |  | Parent | FALSE | GTS NO.1 220KV LINE NO.2 BUS CB AT MLTS | 39938.2743 | 39939.6553 | CONT | [12 empty] | 0
_X7G358A639938.2902777778 | X7G358A6 |  | Parent | FALSE | EX - B1 220/66KV TRANS 66KV SD R/PH AT HTS | 39938.2903 | 39938.6181 | REPDAILY | [12 empty] | 0
_1029113539938.3138888889 | 10291135 |  | Parent | TRUE | SHTS 220KV LINE CB AT DDTS | 39938.3139 | 39940.6708 | CONT | [12 empty] | 0
_1030321539938.3138888889 | 10303215 | 10291135 | Child | FALSE | SHTS 220KV LINE AT DDTS | 39938.3139 | 39940.6708 | CONT | 00012371 | SPIMAINT | Rebate W/O SHTS 220kv Line at DDTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029376739938.33125 | 10293767 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT HOTS | 39938.3313 | 39938.666 | REPDAILY | 00359898 | SPIMAINT | Overhaul of the No 1A 66kv Cap bank | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029377339938.33125 | 10293773 | 10293767 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HOTS | 39938.3313 | 39938.666 | REPDAILY | 00359901 | SPIMAINT | Overhaul of the No1B 66kv Cap Bank | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029090839939.2944444444 | 10290908 | 10290915 | Child | FALSE | NO.3 66KV BUS AT HTS | 39939.2944 | 39939.6292 | DAILY | 00004458 | SPIMAINT | O/Haul NO.3 66KV BUS AT HTS | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029091539939.2944444444 | 10290915 |  | Parent | TRUE | B3 220/66KV TRANS AT HTS | 39939.2944 | 39939.6292 | DAILY | 00004447 | SPIMAINT | O/Haul B3 TRANS AT HTS & No 3 66kv bus & CL 1 cb | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029093539939.2944444444 | 10290935 | 10290915 | Child | FALSE | B3 TRANS 66KV CB AT HTS | 39939.2944 | 39939.6292 | DAILY | [12 empty] | 0
_1029386839939.2958333333 | 10293868 |  | Parent | FALSE | LNGS NO.2 GEN TRANS 220KV LINE AT ATS | 39939.2958 | 39940.6473 | CONT | 00360129 | SPIMAINT | OVERHAUL THE 220KV LINE | SPIPOWER |  |  | Circuits | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z64558E339939.3097222222 | Z64558E3 |  | Parent | FALSE | HOTS-RCTS 220KV | 39939.3097 | 39939.6681 | DAILY | 00328509 | VEN_AUG | Out W/O HOTS-RCTS Line de-energ for anti islanding | SPIPOWER | Z645 | Z645 - (WBTS) WAUBRA WIND FARM GRID CONNECTION | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029376739939.3326388889 | 10293767 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT HOTS | 39939.3326 | 39939.716 | REPDAILY | 00359898 | SPIMAINT | Overhaul of the No 1A 66kv Cap bank | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029377339939.3326388889 | 10293773 | 10293767 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HOTS | 39939.3326 | 39939.716 | REPDAILY | 00359901 | SPIMAINT | Overhaul of the No1B 66kv Cap Bank | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030362239939.6840277778 | 10303622 |  | Parent | FALSE | SYN/COND AT TSTS | 39939.684 | 39940.6667 | CONT | 00007626 | FORCED | Syn Con shutdown. | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7G358B439940.2972222222 | X7G358B4 |  | Parent | FALSE | EX - B3 220/66KV TRANS 66KV SD R/PH AT HTS | 39940.2972 | 39940.5722 | DAILY | [12 empty] | 0
_1029376539940.34375 | 10293765 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT HOTS | 39940.3438 | 39940.6951 | DAILY | 00359897 | SPIMAINT | Overhaul of the No2 66kv Cap Bank | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030363739940.3888888889 | 10303637 |  | Parent | FALSE | H2 TRANS 220KV CB AT DDTS | 39940.3889 | 39940.3958 | CONT | [12 empty] | 0
_1030364439940.3888888889 | 10303644 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 39940.3889 | 39940.3958 | CONT | 00352121 | FORCED | Opening of H2 trans 220kV CB | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X70658C739940.4451388889 | X70658C7 |  | Parent | FALSE | EX - A3 TRANS 220KV CB AT KTS | 39940.4451 | 39942.2049 | CONT | [12 empty] | 0
_1030364639940.5423611111 | 10303646 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39940.5424 | 39940.5667 | DAILY | 00002862 | FAULT | M2 Trans Tripped at HYTS MLTS 2L/2B 500kV CB opene | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029067639941.2951388889 | 10290676 | 10290717 | Child | FALSE | NO.1 66KV CAPACITOR BANK CB AT RTS | 39941.2951 | 39941.4514 | DAILY | [12 empty] | 0
_1029071739941.2951388889 | 10290717 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK AT RTS | 39941.2951 | 39941.4514 | DAILY | 00007279 | SPIMAINT | O/Haul NO.1 66KV CAPACITOR BANK AT RTS | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030348139941.2979166667 | 10303481 |  | Parent | TRUE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 39941.2979 | 39941.4993 | DAILY | 00007399 | SPIMAINT | Rebalance Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030348339941.2979166667 | 10303483 | 10303481 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39941.2979 | 39941.4993 | DAILY | 00331179 | SPIMAINT | rebate 2b Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029317739941.3166666667 | 10293177 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB AT DDTS | 39941.3167 | 39941.6528 | DAILY | [12 empty] | 0
_1030316639941.3166666667 | 10303166 | 10293177 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 39941.3167 | 39941.6528 | DAILY | 00351939 | SPIMAINT | Rebate W/O No1 220kV Cap Bank during CB OH | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1030364039941.3958333333 | 10303640 |  | Parent | TRUE | F2 TRANS 330KV CB AT SMTS | 39941.3958 | 39941.6778 | DAILY | [12 empty] | 0
_1030366239941.3958333333 | 10303662 | 10303640 | Child | FALSE | F2 500/330KV TRANS BANK AT SMTS | 39941.3958 | 39941.6778 | DAILY | 00026099 | SPIMAINT | OUT W/O for replace faulty white phase ct | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030370339941.5194444444 | 10303703 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39941.5194 | 39942.6319 | CONT | 00356082 | GENCO | SCAP: HWPS 4 Isol'd for PS | GENCO |  |  | Circuits | 3rd Party | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030371239942.1215277778 | 10303712 |  | Parent | FALSE | NO.6 GEN 220/16.5KV TRANS AT HWPS | 39942.1215 | 39944.0007 | CONT | 00009647 | GENCO | Unit 6 Isolation | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_X70658B239942.2104166667 | X70658B2 |  | Parent | FALSE | A3 500/220KV TRANS BANK AT KTS | 39942.2104 | 39943.8049 | DAILY | 00026097 | SPICAPX | remove a3 tr 220kv connections | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_V81158C039942.2680555556 | V81158C0 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT KGTS | 39942.2681 | 39942.9042 | DAILY | 00359899 | SPIMAINT | Out W/O No1 66kV Cap bank prot setting changes | SPIPOWER | V811 | V811 - COST EST - UPGRADE CONFIG CAPBANK IEDS, REF545 | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029091739942.2916666667 | 10290917 |  | Parent | TRUE | NO.1 220KV BUS AT HTS | 39942.2917 | 39942.6014 | DAILY | 00004451 | SPIMAINT | O/Haul NO.1 220KV BUS AT HTS | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029692039942.2916666667 | 10296920 | 10290917 | Child | FALSE | SVTS NO.2 220KV LINE AT HTS | 39942.2917 | 39942.6014 | DAILY | 00351698 | SPIMAINT | Rebate Line outage for Bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058D139942.2951388889 | X87058D1 |  | Parent | FALSE | BATS-BETS 220KV | 39942.2951 | 39942.6389 | REPDAILY | 00328505 | SPICAPX | BATS-BETS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029091939943.2909722222 | 10290919 |  | Parent | TRUE | NO.2 220KV BUS AT HTS | 39943.291 | 39943.6062 | DAILY | 00004452 | SPIMAINT | O/Haul NO.2 220KV BUS AT HTS | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029692739943.2909722222 | 10296927 | 10290919 | Child | FALSE | SVTS NO.1 220KV LINE AT HTS | 39943.291 | 39943.6062 | DAILY | 00351699 | SPIMAINT | Rebate Line outage for Bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058D139943.2944444444 | X87058D1 |  | Parent | FALSE | BATS-BETS 220KV | 39943.2944 | 39943.6347 | REPDAILY | 00328505 | SPICAPX | BATS-BETS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030324139943.3229166667 | 10303241 |  | Parent | FALSE | NO.4 TRANS 66KV CB AT ERTS | 39943.3229 | 39943.4722 | DAILY | [12 empty] | 0
_V81158B839943.3430555556 | V81158B8 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT KGTS | 39943.3431 | 39943.7431 | DAILY | 00359900 | SPIMAINT | Out W/O No2 66kV Cap bank prot setting changes | SPIPOWER | V811 | V811 - COST EST - UPGRADE CONFIG CAPBANK IEDS, REF545 | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030328539944.4722222222 | 10303285 |  | Parent | FALSE | JLGB NO.2 UNIT TRANS DISC CB AT JLGB | 39944.4722 | 39953.3611 | CONT | [12 empty] | 0
_Z63658A239945.25 | Z63658A2 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39945.25 | 39946.7278 | CONT | 00002863 | DB_AUG | M1 Trans - disconnect M1 Tr S-S Trans & tert cable | SPIPOWER | Z636 | Z636 - (HYTS) 22KV SUPPLY | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029429739945.2916666667 | 10294297 | 10295738 | Child | FALSE | FBTS NO.1 220KV LINE CB CT R/PH AT WMTS | 39945.2917 | 39948.6271 | DAILY | [12 empty] | 0
_1029573839945.2916666667 | 10295738 |  | Parent | TRUE | FBTS NO.1 220KV LINE CB AT WMTS | 39945.2917 | 39948.6271 | CONT | [12 empty] | 0
_1030387239945.2916666667 | 10303872 | 10295738 | Child | TRUE | FBTS NO.1 220KV LINE AT WMTS | 39945.2917 | 39948.6271 | CONT | 00025735 | SPIMAINT | CL.2 O/HAUL - S&S HPF514P/4F CB | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1030387539945.2916666667 | 10303875 | 10303872 | Child | FALSE | FBTS NO.1 220KV LINE CB CT R/PH AT WMTS | 39945.2917 | 39948.6271 | DAILY | [12 empty] | 0
_1029163239945.2944444444 | 10291632 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT TTS | 39945.2944 | 39945.6292 | DAILY | [12 empty] | 0
_1029129639945.3097222222 | 10291296 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT MLTS | 39945.3097 | 39946.6389 | CONT | [12 empty] | 0
_1029376939945.3597222222 | 10293769 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT KGTS | 39945.3597 | 39945.6667 | DAILY | 00359899 | SPIMAINT | O/Haul 66KV CAPACITOR BANK | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030375839945.3784722222 | 10303758 |  | Parent | TRUE | NO.2B 66KV CAPACITOR BANK CB AT RWTS | 39945.3785 | 39945.75 | DAILY | [12 empty] | 0
_1030388139945.3784722222 | 10303881 | 10303758 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 39945.3785 | 39945.75 | DAILY | 00331179 | FAULT | INVESTIGATE & REPAIR DEFECTIVE CB OPERATION | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030374739945.5027777778 | 10303747 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 39945.5028 | 39947.3486 | CONT | 00337579 | SPIMAINT | ADJUST 220KV BUSHING OIL LEVEL. | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030379339945.9513888889 | 10303793 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 39945.9514 | 39947.9222 | CONT | 00356086 | GENCO | HWPS No8 Gen Isols for Powerstation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029163439946.2986111111 | 10291634 |  | Parent | FALSE | 1-4 66KV BUS TIE CB AT TTS | 39946.2986 | 39946.6584 | DAILY | [12 empty] | 0
_1029556939946.3097222222 | 10295569 |  | Parent | FALSE | 3-4 220KV BUS TIE CB AT SVTS | 39946.3097 | 39946.5104 | DAILY | [12 empty] | 0
_1029377139946.3458333333 | 10293771 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT KGTS | 39946.3458 | 39946.6507 | DAILY | 00359900 | SPIMAINT | O/Haul 66KV CAPACITOR BANK | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029080739947.2909722222 | 10290807 | 10302735 | Child | FALSE | NO.4 TRANS 66KV CB AT SVTS | 39947.291 | 39947.5931 | DAILY | [12 empty] | 0
_1030273539947.2909722222 | 10302735 |  | Parent | TRUE | B4 220/66KV TRANS AT SVTS | 39947.291 | 39947.5931 | DAILY | 00352791 | SPIMAINT | INITIAL O/H | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029022039947.2972222222 | 10290220 |  | Parent | FALSE | JINDERA 330KV LINE AT WOTS | 39947.2972 | 39947.6875 | REPDAILY | 00012053 | SPIMAINT | O/H JINDERA 330KV LINE & EQUIP. | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029132839947.3125 | 10291328 |  | Parent | FALSE | HYTS NO.2 500KV LINE NO.2 BUS CB AT MLTS | 39947.3125 | 39948.5882 | CONT | [12 empty] | 0
_1030374639947.3986111111 | 10303746 |  | Parent | FALSE | A2 515/230KV TRANS W/PH AT HWTS | 39947.3986 | 39947.6354 | DAILY | 00009774 | SPIMAINT | ADJUST 220KV BUSHING OIL LEVEL. | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030382439947.41875 | 10303824 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 39947.4187 | 39947.4222 | CONT | 00002862 | FAULT | SESS NO.2 275KV LINE/M2 TRANS CB,opened auto | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030381539947.5520833333 | 10303815 |  | Parent | FALSE | NO.3 22KV CAPACITOR BANK CB AT BTS | 39947.5521 | 39947.6139 | DAILY | [12 empty] | 0
_1029080939948.2930555556 | 10290809 | 10290820 | Child | FALSE | NO.4 66KV CAPACITOR BANK CB AT SVTS | 39948.2931 | 39948.591 | DAILY | [12 empty] | 0
_1029082039948.2930555556 | 10290820 |  | Parent | TRUE | NO.4A 66KV CAPACITOR BANK AT SVTS | 39948.2931 | 39948.591 | DAILY | 00004825 | SPIMAINT | O/HAUL NO.4A 66KV CAPACITOR BANK AT SVTS | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029252639948.2930555556 | 10292526 | 10290820 | Child | FALSE | NO.4B 66KV CAPACITOR BANK CB AT SVTS | 39948.2931 | 39948.591 | DAILY | [12 empty] | 0
_1029271939948.2930555556 | 10292719 | 10290820 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT SVTS | 39948.2931 | 39948.591 | DAILY | 00329600 | SPIMAINT | O/Haul NO.3B 66KV CAPACITOR BANK AT SVTS | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029022039948.2958333333 | 10290220 |  | Parent | FALSE | JINDERA 330KV LINE AT WOTS | 39948.2958 | 39948.7167 | REPDAILY | 00012053 | SPIMAINT | O/H JINDERA 330KV LINE & EQUIP. | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030381139948.30625 | 10303811 |  | Parent | FALSE | HWTS NO.3 220KV LINE NO.3 BUS CB AT HWPS | 39948.3063 | 39955.6139 | CONT | 00009610 | SPIMAINT | REPLACE BPH BUS SIDE BUSHING | SPIPOWER | [8 empty] | 0 | 10303811 |  | REPLACE BPH BUS SIDE BUSHING | 00009610 | CB |  | HWPS | CB | SPIMAINT | CONT
_1030382539948.9215277778 | 10303825 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 39948.9215 | 39951.7354 | CONT | [12 empty] | 0
_1030388639948.9215277778 | 10303886 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 39948.9215 | 39965.6903 | CONT | 00356082 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030381239949.2055555556 | 10303812 |  | Parent | FALSE | AUX TRANS 'A' 220KV LINE AT YPS | 39949.2056 | 39956.916 | CONT | 00016418 | GENCO | SCAP to Genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V90758A039949.2527777778 | V90758A0 |  | Parent | TRUE | ROTS NO.3 500KV LINE AT SMTS | 39949.2528 | 39949.6597 | DAILY | 00012438 | SPIMAINT | REMOVE BYPASS | SPIPOWER | V907 | V907 - (SMTS) SITE REPAIR - KTS LINE BPH CVT FAILURE 30-1-09 | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V90758L139949.2527777778 | V90758L1 | V90758A0 | Child | FALSE | KTS 500KV LINE AT SMTS | 39949.2528 | 39949.6597 | DAILY | 00012441 | SPIMAINT | REMOVE BYPASS | SPIPOWER | V907 | V907 - (SMTS) SITE REPAIR - KTS LINE BPH CVT FAILURE 30-1-09 | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029061739950.3020833333 | 10290617 |  | Parent | FALSE | NO.2 66KV BUS AT TSTS | 39950.3021 | 39950.6208 | DAILY | 00007674 | SPIMAINT | Overhaul No 2 66kv bus & Isols @ TSTS | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029285839951.3027777778 | 10292858 |  | Parent | FALSE | NPSD 220KV LINE AT FBTS | 39951.3028 | 39952.6368 | CONT | 00002662 | SPIMAINT | INSPECT LINE AND CHECK SPILL GAP | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029440339951.3090277778 | 10294403 |  | Parent | FALSE | EX - 1-3 220KV BUS TIE CB NO.3 BUS CT R/PH AT SVTS | 39951.309 | 39951.3472 | DAILY | [12 empty] | 0
_1029440539951.3479166667 | 10294405 |  | Parent | FALSE | 2-4 220KV BUS TIE CB NO.2 BUS CT R/PH AT SVTS | 39951.3479 | 39951.5062 | DAILY | [12 empty] | 0
_X56558H939951.3993055556 | X56558H9 |  | Parent | FALSE | TGTS 220KV LINE NO.2 TIE BUS AT BATS | 39951.3993 | 39962.55 | CONT | 00362535 | SPICAPX | Out W/O TGTS Line No2 Tie CT replacement | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028945939951.5069444444 | 10289459 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 39951.5069 | 39955.4729 | CONT | 00019243 | SPIMAINT | O/Haul SVC at HOTS | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X7E458A939952.2923611111 | X7E458A9 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39952.2924 | 39952.7875 | DAILY | 00319998 | SPICAPX | Out W/O APD No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1009262439952.3354166667 | 10092624 |  | Parent | TRUE | MBTS NO.2 220KV LINE CB AT DDTS | 39952.3354 | 39952.6556 | DAILY | [12 empty] | 0
_1030323739952.3354166667 | 10303237 | 10092624 | Child | FALSE | MBTS-DDTS 2 220KV NW | 39952.3354 | 39952.6556 | DAILY | 00060194 | SPIMAINT | Rebate W/O MBTS No2 Line during CB OH | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030398839952.6375 | 10303988 |  | Parent | FALSE | WMTS NO.1 220KV LINE CB BUS SIDE ROI AT FBTS | 39952.6375 | 39952.6493 | CONT | [12 empty] | 0
_1030399139952.6375 | 10303991 |  | Parent | FALSE | WMTS-FBTS 1 220KV WY | 39952.6375 | 39952.6493 | CONT | 00022785 | FORCED | FBTS-WMTS No1 Line | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X89258A039953.2916666667 | X89258A0 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39953.2917 | 39953.8028 | DAILY | 00319999 | SPICAPX | Out W/O APD No2 Line - Earth wire replacement | SPIPOWER | X892 | X892 - (HYTS-APD) GROUND WIRE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028871539953.29375 | 10288715 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT KTS | 39953.2937 | 39955.7111 | CONT | 00026096 | SPIMAINT | 500kv English Electric Transformer Bank | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1009261939953.3145833333 | 10092619 |  | Parent | FALSE | MBTS NO.2 220KV LINE AT DDTS | 39953.3146 | 39953.6896 | DAILY | 00012363 | SPIMAINT | O/Haul - LINE & COMP as per E.A.P APPL | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030409039953.8822106481 | 10304090 |  | Parent | FALSE | EX - NO.7 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 39953.8822 | 39957.7465 | CONT | [12 empty] | 0
_1030409639953.9791666667 | 10304096 |  | Parent | FALSE | ROTS-SMTS 3 500KV WT | 39953.9792 | 39953.9931 | CONT | 00119316 | FORCED | Bus Outage to clear 500KV CB Hyd Mech Locked out | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030409539953.9791666667 | 10304095 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.2 BUS CB AT SMTS | 39953.9792 | 39954.3542 | CONT | [12 empty] | 0
_1030398439954.3486111111 | 10303984 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 39954.3486 | 39955.6139 | CONT | 00337579 | SPIMAINT | DLA TEST ON 3TX WPH 220KV BUSHING | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030421739954.9305555556 | 10304217 |  | Parent | FALSE | B2 220/66KV TRANS AT WBTS | 39954.9306 | 39961.6042 | CONT | 00366200 | GENCO | WBTS B2 Trans De-Energised Only for Acciona | GENCO |  |  | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_X50858X339956.2451388889 | X50858X3 |  | Parent | TRUE | EX - NO.4 66KV CAPACITOR BANK CB AT GTS | 39956.2451 | 39956.6382 | CONT | [12 empty] | 0
_X50858X439956.2451388889 | X50858X4 | X50858X3 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39956.2451 | 39956.6382 | CONT | 00329879 | SPICAPX | Rebate W/O No4 66kv Cap Bk during CB outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E558A039956.2923611111 | X7E558A0 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 39956.2924 | 39956.75 | DAILY | 00022640 | SPICAPX | Out W/O SMTS-SYTS No1 Line - OPGW installation | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858X539956.6527777778 | X50858X5 |  | Parent | TRUE | NO.4 66KV CAPACITOR BANK CB AT GTS | 39956.6528 | 39984.2861 | CONT | [12 empty] | 0
_X50858X639956.6527777778 | X50858X6 | X50858X5 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 39956.6528 | 39984.2861 | CONT | 00329879 | SPICAPX | Rebate W/O No4 66 Cap Bk during new CB erection | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X87058C539957.29375 | X87058C5 |  | Parent | FALSE | MLTS-BATS 1 220KV WY | 39957.2937 | 39957.6438 | DAILY | 00022728 | SPICAPX | MLTS-BATS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030349539957.3173611111 | 10303495 |  | Parent | FALSE | NO.1 TRANS 66KV CB AT ERTS | 39957.3174 | 39957.4639 | DAILY | [12 empty] | 0
_1030349739957.4645833333 | 10303497 |  | Parent | FALSE | NO.3 TRANS 66KV CB AT ERTS | 39957.4646 | 39957.741 | DAILY | [12 empty] | 0
_1030394739958.1909722222 | 10303947 |  | Parent | FALSE | AUX TRANS 'B' 220KV LINE AT YPS | 39958.191 | 39969.5333 | CONT | 00016420 | GENCO | SCAP to YWPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E558A139958.2951388889 | X7E558A1 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 39958.2951 | 39958.3458 | DAILY | 00022640 | SPICAPX | Out W/O SMTS-SYTS No1 Line - OPGW installation | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028871839959.2381944444 | 10288718 |  | Parent | FALSE | A3 500/220KV TRANS BANK AT KTS | 39959.2382 | 39961.6722 | CONT | 00026097 | SPIMAINT | 500kv English Electric Transformer Bank | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029443139959.2527777778 | 10294431 | X74158A6 | Child | FALSE | EX - ROTS NO.7 220KV LINE NO.1 BUS CB CT R/PH AT YPS | 39959.2528 | 39962.75 | CONT | [12 empty] | 0
_X74158A639959.2527777778 | X74158A6 |  | Parent | TRUE | EX - ROTS NO.7 220KV LINE NO.1 BUS CB CT R/PH AT YPS | 39959.2528 | 39962.75 | CONT | [12 empty] | 0
_X74158A739959.2527777778 | X74158A7 | X74158A6 | Child | FALSE | ROTS NO.7 220KV LINE AT YPS | 39959.2528 | 39962.75 | CONT | 00016415 | SPICAPX | REBATE FOR CT OUTAGE | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029082739959.25625 | 10290827 |  | Parent | TRUE | NO.3 220KV BUS AT ROTS | 39959.2562 | 39959.6361 | DAILY | 00329013 | SPIMAINT | O/Haul 3 220kv Bus in Bays C D E F G at ROTS | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029689239959.25625 | 10296892 | 10290827 | Child | FALSE | MTS NO.3 220KV LINE AT ROTS | 39959.2562 | 39959.6361 | DAILY | 00023099 | SPIMAINT | Rebate Line outage for Bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029689339959.25625 | 10296893 | 10290827 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 39959.2562 | 39959.6361 | DAILY | 00112417 | SPIMAINT | Rebate CapBank for Bus outage | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030397939959.25625 | 10303979 | 10290827 | Child | FALSE | NO.2 CSC AT ROTS | 39959.2562 | 39959.6361 | DAILY | 00004716 | SPIMAINT | Rebate CSC for Bus outage | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030358039959.2736111111 | 10303580 |  | Parent | FALSE | BATS NO.2 220KV LINE AT MLTS | 39959.2736 | 39959.8299 | REPDAILY | 00022969 | SPIMAINT | OUT W/O BATS No2 Line choke removal | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029587039959.2840277778 | 10295870 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 39959.284 | 39962.6215 | CONT | 00354002 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_X7E458B239959.3034722222 | X7E458B2 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39959.3035 | 39959.7646 | REPDAILY | 00319998 | SPICAPX | Out W/O APD No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029109239959.3145833333 | 10291092 |  | Parent | TRUE | NO.1 66KV BUS AT WOTS | 39959.3146 | 39959.6757 | DAILY | 00004043 | SPIMAINT | O/Haul NO.1 66KV BUS AT WOTS | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030351439959.3145833333 | 10303514 | 10291092 | Child | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 39959.3146 | 39959.6757 | DAILY | 00004036 | SPIMAINT | Perf Calc W/O No1 Trans during no1 66kV Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030358039960.2708333333 | 10303580 |  | Parent | FALSE | BATS NO.2 220KV LINE AT MLTS | 39960.2708 | 39960.6944 | REPDAILY | 00022969 | SPIMAINT | OUT W/O BATS No2 Line choke removal | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E558A239960.2923611111 | X7E558A2 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 39960.2924 | 39961.8063 | DAILY | 00022640 | SPICAPX | Out W/O SMTS-SYTS No1 Line - OPGW installation | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029109439960.3020833333 | 10291094 |  | Parent | TRUE | NO.2 66KV BUS AT WOTS | 39960.3021 | 39960.6438 | DAILY | 00004044 | SPIMAINT | O/Haul NO.2 66KV BUS AT WOTS | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030351539960.3020833333 | 10303515 | 10291094 | Child | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 39960.3021 | 39960.6438 | DAILY | 00004037 | SPIMAINT | Perf Calc W/O No2 Trans during no1 66kV Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458B239960.3152777778 | X7E458B2 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39960.3153 | 39960.7333 | REPDAILY | 00319998 | SPICAPX | Out W/O APD No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029139339961.2951388889 | 10291393 |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 39961.2951 | 39962.5889 | CONT | [12 empty] | 0
_1029111839961.3090277778 | 10291118 |  | Parent | FALSE | DDTS 330KV LINE NO.2 BUS CB AT WOTS | 39961.309 | 39962.6062 | CONT | [12 empty] | 0
_1029442139961.3597222222 | 10294421 |  | Parent | FALSE | AUX TRANS 'B' 220KV CB CT R/PH AT YPS | 39961.3597 | 39961.4597 | DAILY | [12 empty] | 0
_1030190339962.3173611111 | 10301903 |  | Parent | TRUE | HWTS NO.4 220KV LINE NO.3 BUS CB LINE SIDE ISOL AT HWPS | 39962.3174 | 39962.6174 | DAILY | [12 empty] | 0
_1030338239962.3173611111 | 10303382 | 10301903 | Child | FALSE | A4 515/230KV TRANS BANK AT HWTS | 39962.3174 | 39962.6174 | DAILY | 00337582 | SPIMAINT | TX REBATE FOR ISOL OUTAGE | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030446039962.3284722222 | 10304460 |  | Parent | FALSE | CBTS NO.1 220KV LINE X PROT AT ERTS | 39962.3285 | 39962.6521 | DAILY | [12 empty] | 0
_X56558I039962.4027777778 | X56558I0 |  | Parent | FALSE | TGTS 220KV LINE AT BATS | 39962.4028 | 39962.55 | DAILY | 00012435 | SPICAPX | Out W/O TGTS Line to connect new tie CTs | SPIPOWER | X565 | X565 - REPLACE 220KV TYREE CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030454739962.4270833333 | 10304547 |  | Parent | FALSE | YPS -YWPS 3 220KV G | 39962.4271 | 39967.8069 | CONT | 00020520 | GENCO | SCAP to YWPS | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030399539962.6180555556 | 10303995 |  | Parent | TRUE | WMTS NO.1 220KV LINE CB BUS SIDE ROI AT FBTS | 39962.6181 | 39962.6958 | DAILY | [12 empty] | 0
_1030408539962.6180555556 | 10304085 | 10303995 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 39962.6181 | 39962.6958 | CONT | 00327661 | SPIMAINT | NO.4 CAPBANK REBATE CAPTURE W/O | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030408639962.6180555556 | 10304086 | 10303995 | Child | FALSE | NPSD-FBTS 220KV WY | 39962.6181 | 39962.6958 | CONT | 00022738 | SPIMAINT | NPSD LINE REBATE CAPTURE W/O | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030408739962.6180555556 | 10304087 | 10303995 | Child | FALSE | WMTS-FBTS 1 220KV WY | 39962.6181 | 39962.6958 | CONT | 00022785 | SPIMAINT | WMTS No.1LINE REBATES CAPTURE W/O | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1030428039962.8965277778 | 10304280 |  | Parent | FALSE | NO.1 GEN TRANS 500KV LINE E/SW AT LYPS | 39962.8965 | 39969.7222 | CONT | [12 empty] | 0
_1030868639963.1569444445 | 10308686 |  | Parent | FALSE | YPS NO.8 220KV LINE AT ROTS | 39963.1569 | 39963.6271 | CONT | 00024015 | FORCED | YPS No8 220KV Line Sw out by NEMMCO Y prot failure | NEMMCO |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029036239963.2125 | 10290362 |  | Parent | TRUE | NO.1 500KV BUS AT LYPS | 39963.2125 | 39963.6083 | DAILY | 00010023 | SPIMAINT | O/Haul NO.1 500KV BUS AT LYPS | SPIPOWER |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1029215739963.2125 | 10292157 | 10290362 | Child | FALSE | 1-3 500KV BUS TIE ROI AT LYPS | 39963.2125 | 39963.6083 | DAILY | [12 empty] | 0
_1030110239963.2125 | 10301102 | 10290362 | Child | FALSE | HWTS NO.2 500KV LINE NO.1 BUS CB BUS SIDE ROI AT LYPS | 39963.2125 | 39963.6083 | DAILY | [12 empty] | 0
_1030110339963.2125 | 10301103 | 10290362 | Child | FALSE | HWTS NO.2 500KV LINE NO.1 BUS CB LINE SIDE ROI AT LYPS | 39963.2125 | 39963.6083 | DAILY | [12 empty] | 0
_1030116839963.2125 | 10301168 | 10290362 | Child | FALSE | A1 GEN TRANS 500KV CB AT LYPS | 39963.2125 | 39963.6083 | DAILY | [12 empty] | 0
_1030116939963.2125 | 10301169 | 10290362 | Child | FALSE | A2 GEN TRANS NO.1 BUS 500KV CB AT LYPS | 39963.2125 | 39963.6083 | DAILY | [12 empty] | 0
_1030117039963.2125 | 10301170 | 10290362 | Child | FALSE | HWTS NO.1 500KV LINE NO.1 BUS CB AT LYPS | 39963.2125 | 39963.6083 | DAILY | [12 empty] | 0
_1030117239963.2125 | 10301172 | 10290362 | Child | FALSE | HWTS NO.2 500KV LINE CB AT LYPS | 39963.2125 | 39963.6083 | DAILY | [12 empty] | 0
_1030363039963.2125 | 10303630 | 10290362 | Child | FALSE | HWTS NO.2 500KV LINE AT LYPS | 39963.2125 | 39963.6083 | DAILY | 00016087 | SPIMAINT | REBATE FOR BUS OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058D839963.3020833333 | X87058D8 |  | Parent | FALSE | BATS-BETS 220KV | 39963.3021 | 39963.6479 | REPDAILY | 00328505 | SPICAPX | BATS-BETS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030451239963.3194444444 | 10304512 |  | Parent | FALSE | NO.1 500/220KV TRANS 500KV E/SW AT LYPS | 39963.3194 | 39963.4896 | DAILY | [12 empty] | 0
_1028786339964.24375 | 10287863 |  | Parent | TRUE | NO.3 500KV BUS AT LYPS | 39964.2438 | 39964.7292 | DAILY | 00119111 | SPIMAINT | O/Haul NO.3 500KV BUS AT LYPS | SPIPOWER |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1028786539964.24375 | 10287865 | 10287863 | Child | FALSE | B2 GEN TRANS NO.3 BUS 500KV CB BUS SIDE ROI AT LYPS | 39964.2438 | 39964.7292 | DAILY | [12 empty] | 0
_1028786739964.24375 | 10287867 | 10287863 | Child | FALSE | B2 GEN TRANS NO.3 BUS 500KV CB BUS SIDE E/SW AT LYPS | 39964.2438 | 39964.7292 | DAILY | [12 empty] | 0
_X87058D839964.2951388889 | X87058D8 |  | Parent | FALSE | BATS-BETS 220KV | 39964.2951 | 39964.5826 | REPDAILY | 00328505 | SPICAPX | BATS-BETS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858Y239965.2729166667 | X50858Y2 |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 39965.2729 | 39965.7076 | REPDAILY | 00367296 | SPICAPX | Install new footings in Bay L, KTS No3 Line | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029410839965.2958333333 | 10294108 |  | Parent | FALSE | B1 220/66KV TRANS AT SVTS | 39965.2958 | 39966.7257 | CONT | 00004849 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area(W) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030367139965.2993055556 | 10303671 |  | Parent | FALSE | EX - FR NO.2 66KV FDR NO.3 BUS CB AT RTS | 39965.2993 | 39966.9028 | CONT | [12 empty] | 0
_1029131139965.3076388889 | 10291311 |  | Parent | FALSE | GTS NO.2 LINE/A1 TRANS 220KV CB AT MLTS | 39965.3076 | 39966.5042 | CONT | [12 empty] | 0
_1029576739965.3326388889 | 10295767 |  | Parent | FALSE | SHTS NO.1 220KV LINE NO.2 BUS CB AT GNTS | 39965.3326 | 39969.6986 | CONT | [12 empty] | 0
_X50858Y239966.2729166667 | X50858Y2 |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 39966.2729 | 39966.6889 | REPDAILY | 00367296 | SPICAPX | Install new footings in Bay L, KTS No3 Line | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458B339966.2958333333 | X7E458B3 |  | Parent | FALSE | HYTS-APD 1 500KV W | 39966.2958 | 39966.5715 | REPDAILY | 00319998 | SPICAPX | Out W/O APD No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V7A058A139966.3118055556 | V7A058A1 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.2 BUS CB AT SMTS | 39966.3118 | 39969.6639 | CONT | [12 empty] | 0
_1030874639966.5270833333 | 10308746 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 39966.5271 | 39966.5375 | DAILY | [12 empty] | 0
_X50858Y239967.2715277778 | X50858Y2 |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 39967.2715 | 39967.691 | REPDAILY | 00367296 | SPICAPX | Install new footings in Bay L, KTS No3 Line | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030373039967.2756944444 | 10303730 |  | Parent | FALSE | BATS NO.1 220KV LINE AT MLTS | 39967.2757 | 39967.7326 | REPDAILY | 00022946 | SPIMAINT | OUT W/O BATS No1 Line choke removal at MLTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029411039967.29375 | 10294110 |  | Parent | FALSE | B2 220/66KV TRANS AT SVTS | 39967.2937 | 39968.6167 | CONT | 00004850 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area(W) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029070639967.2944444444 | 10290706 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT RTS | 39967.2944 | 39967.5729 | DAILY | [12 empty] | 0
_V8F158A039967.2979166667 | V8F158A0 |  | Parent | FALSE | B1 220/66KV TRANS AT RTS | 39967.2979 | 39968.6375 | CONT | 00007329 | SPIMAINT | Check Oil Leaks | SPIPOWER | V8F1 | V8F1 - REPAIR OF OIL LEAKS IN TERMINAL STNS - STAGE 1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030365739967.3145833333 | 10303657 |  | Parent | TRUE | NO.2 66KV BUS AT GNTS | 39967.3146 | 39967.6694 | DAILY | 00000749 | SPIMAINT | Out W/O No2 66kV BUS for VT NEMMCO metering tests | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030365939967.3145833333 | 10303659 | 10303657 | Child | FALSE | B2 220/66KV TRANS AT GNTS | 39967.3146 | 39967.6694 | DAILY | 00000743 | SPIMAINT | Perf calc W/O No2 Trans during No1 66 BUS outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030880139967.3875 | 10308801 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 39967.3875 | 39967.6667 | DAILY | 00003104 | FAULT | Inspect and replace blown fuses No1 Cap Bk | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030203339967.4236111111 | 10302033 |  | Parent | FALSE | WBTS 220KV LINE NO.1 TIE BUS BUS SIDE ROI AT BATS | 39967.4236 | 39967.5535 | DAILY | [12 empty] | 0
_1030451439967.5715277778 | 10304514 |  | Parent | FALSE | B1 220/66KV TRANS AT TTS | 39967.5715 | 39967.6083 | CONT | 00367585 | SPIMAINT | HV TESTS OF TRANS AFTER REPAIR | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858Y239968.2715277778 | X50858Y2 |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 39968.2715 | 39968.6813 | REPDAILY | 00367296 | SPICAPX | Install new footings in Bay L, KTS No3 Line | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030373039968.2722222222 | 10303730 |  | Parent | FALSE | BATS NO.1 220KV LINE AT MLTS | 39968.2722 | 39968.7125 | REPDAILY | 00022946 | SPIMAINT | OUT W/O BATS No1 Line choke removal at MLTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029070239968.2888888889 | 10290702 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT RTS | 39968.2889 | 39968.4944 | DAILY | [12 empty] | 0
_1030365439968.2979166667 | 10303654 |  | Parent | TRUE | NO.1 66KV BUS AT GNTS | 39968.2979 | 39968.6604 | DAILY | 00000748 | SPIMAINT | Out W/O No1 66kV BUS for VT NEMMCO metering tests | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030365539968.2979166667 | 10303655 | 10303654 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT GNTS | 39968.2979 | 39968.6604 | DAILY | 00329962 | SPIMAINT | Rebate W/O No1 66 Cap bk during No1 66 BUS outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030365639968.2979166667 | 10303656 | 10303654 | Child | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 39968.2979 | 39968.6604 | DAILY | 00329970 | SPIMAINT | Perf calc W/O No1 Tr bk during No1 66 BUS outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030455039968.3652777778 | 10304550 |  | Parent | FALSE | 22KV/415V S/S TRANS AT FTS | 39968.3653 | 39968.6035 | DAILY | 00004393 | DBPROX | VSCAP to Jemena | DISTCO |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858Y239969.2708333333 | X50858Y2 |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 39969.2708 | 39969.691 | REPDAILY | 00367296 | SPICAPX | Install new footings in Bay L, KTS No3 Line | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030887539969.6333333333 | 10308875 |  | Parent | TRUE | NO.3 22KV CAPACITOR BANK CB AT BTS | 39969.6333 | 39969.6396 | DAILY | [12 empty] | 0
_1030887739969.6333333333 | 10308877 | 10308875 | Child | FALSE | NO.3 22KV CAPACITOR BANK AT BTS | 39969.6333 | 39969.6396 | DAILY | 00337011 | SPIMAINT | TOP UP CB WITH SFS | SPIPOWER |  |  | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030887239969.6722222222 | 10308872 |  | Parent | FALSE | MLRC 220KV LINE NO.2 BUS CB AT RCTS | 39969.6722 | 39969.7021 | DAILY | [12 empty] | 4
_1030890839970.1840277778 | 10308908 |  | Parent | TRUE | B3 TRANS 66KV CB AT MWTS | 39970.184 | 39970.1889 | CONT | [12 empty] | 0
_1030905539970.1840277778 | 10309055 | 10308908 | Child | FALSE | HWPS-MPS 220KV LINE AT MWTS | 39970.184 | 39970.1889 | CONT | 00016132 | FAULT | Line rebate for B3 Trans 66kV CB opened auto | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030914739970.1840277778 | 10309147 | 10308908 | Child | FALSE | B3 220/66KV TRANS AT MWTS | 39970.184 | 39970.1889 | CONT | 00010267 | FAULT | B3 Trans 66kV CB opened auto | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030874239970.3229166667 | 10308742 |  | Parent | TRUE | B2 220/66KV TRANS AT RTS | 39970.3229 | 39970.6667 | DAILY | 00007331 | SPIMAINT | De-energised 2A & 2B 220kV Bus | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030874339970.3229166667 | 10308743 | 10308742 | Child | FALSE | BTS 220KV LINE AT RTS | 39970.3229 | 39970.6667 | DAILY | 00021222 | SPIMAINT | Rebate Line outage De-energised 2A & 2B 220kV Bus | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030889939970.3777777778 | 10308899 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 39970.3778 | 39971.8333 | CONT | 00356084 | GENCO | Gen-Co isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030890039971.3881944444 | 10308900 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 39971.3882 | 39977.8771 | CONT | 00356086 | GENCO | Genco work | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030892639973.7284722222 | 10308926 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39973.7285 | 39973.8882 | CONT | 00016040 | FAULT | BETS No2 Trans Group Trip | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030893039974.2118055556 | 10308930 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT KTS | 39974.2118 | 39974.666 | CONT | 00327947 | FAULT | KTS N01A Cap Bank Tripped | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030906639974.2118055556 | 10309066 | 10308930 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT KTS | 39974.2118 | 39974.666 | CONT | 00337022 | FAULT | KTS N01A Cap Bank Tripped | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X49758N339974.2979166667 | X49758N3 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 39974.2979 | 39976.7701 | CONT | 00016040 | SPICAPX | Out W/O No2 Trans grp wiring and functional checks | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030183839974.3208333333 | 10301838 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 39974.3208 | 39974.3903 | DAILY | 00003011 | SPIMAINT | Out W/O 220kV Shunt reactor CB Sf6 sample | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X78558A539974.3527777778 | X78558A5 |  | Parent | FALSE | EX - B4 TRANS NO.1 BUS 220KV CB AT TTS | 39974.3528 | 39974.6507 | DAILY | [12 empty] | 0
_X74158B939974.3569444444 | X74158B9 |  | Parent | FALSE | ROTS 220KV LINE NO.1 BUS CB AT TSTS | 39974.3569 | 39976.4333 | CONT | [12 empty] | 0
_X70758B339974.4048611111 | X70758B3 |  | Parent | FALSE | SYTS NO.1 500KV LINE NO.1 BUS CB AT SMTS | 39974.4049 | 39974.4972 | DAILY | [12 empty] | 0
_X70758A739974.5034722222 | X70758A7 |  | Parent | FALSE | HWTS NO.1 LINE/SYTS NO.1 LINE 500KV CB AT SMTS | 39974.5035 | 39974.5687 | DAILY | [12 empty] | 0
_1030898439974.5291666667 | 10308984 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT TBTS | 39974.5292 | 39976.6722 | DAILY | 00351938 | FAULT | TBTS No1 Cap Bank Tripped | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_Z64558F239974.5305555556 | Z64558F2 |  | Parent | FALSE | WBTS 220KV LINE NO.1 BUS CB AT HOTS | 39974.5306 | 39974.5896 | DAILY | [12 empty] | 0
_X70758A539974.5729166667 | X70758A5 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.2 BUS CB AT SMTS | 39974.5729 | 39974.6083 | DAILY | [12 empty] | 0
_Z64558F339974.6034722222 | Z64558F3 |  | Parent | FALSE | WBTS 220KV LINE NO.2 BUS CB AT HOTS | 39974.6035 | 39974.6896 | DAILY | [12 empty] | 0
_X70758A239974.6270833333 | X70758A2 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT SMTS | 39974.6271 | 39974.7465 | DAILY | [12 empty] | 0
_1030897839974.7048611111 | 10308978 |  | Parent | TRUE | EX - NO.4A 66KV CAPACITOR BANK AT TTS | 39974.7049 | 39975.5826 | CONT | 00001486 | FAULT | TTS No4 Cap Bank Tripped | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030907039974.7048611111 | 10309070 | 10308978 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT TTS | 39974.7049 | 39975.5826 | CONT | 00337509 | FAULT | TTS No4 Cap Bank Tripped | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V8F158A139975.3041666667 | V8F158A1 |  | Parent | FALSE | B4 220/66KV TRANS AT RTS | 39975.3042 | 39976.6118 | CONT | 00007332 | SPIMAINT | Check Oil Leaks | SPIPOWER | V8F1 | V8F1 - REPAIR OF OIL LEAKS IN TERMINAL STNS - STAGE 1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70758A939975.36875 | X70758A9 |  | Parent | FALSE | HWTS NO.2 LINE/SYTS NO.2 LINE 500KV CB AT SMTS | 39975.3688 | 39976.5757 | DAILY | [12 empty] | 0
_1030900139975.5833333333 | 10309001 |  | Parent | TRUE | EX - NO.4A 66KV CAPACITOR BANK AT TTS | 39975.5833 | 39975.6813 | DAILY | 00001486 | SPIMAINT | TTS No4A Cap Bank investigate and rebalance | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030909139975.5833333333 | 10309091 | 10309001 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT TTS | 39975.5833 | 39975.6813 | DAILY | 00337509 | SPIMAINT | TTS No4A Cap Bank investigate and rebalance | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030901139975.8541666667 | 10309011 |  | Parent | FALSE | B STH - C STH 22KV BUS TIE CB B STH BUS SIDE ISOL AT RTS | 39975.8542 | 39976.1722 | CONT | [12 empty] | 0
_V91058A839976.3069444444 | V91058A8 |  | Parent | TRUE | B1 220/66KV TRANS AT TTS | 39976.3069 | 39988.541 | DAILY | 00367585 | SPIMAINT | RECONNECT TRANS | SPIPOWER | V910 | V910 - (TTS) INVESTIGATE & REPAIR - FAIL B1 TRANSFORMER | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X78558B039976.3069444444 | X78558B0 | V91058A8 | Child | FALSE | B1 TRANS 220KV CB AT TTS | 39976.3069 | 39988.541 | DAILY | [12 empty] | 0
_1030897339976.3659722222 | 10308973 | 10308898 | Child | FALSE | HWPS-MPS 220KV LINE AT MWTS | 39976.366 | 39976.5778 | DAILY | 00016132 | SPIMAINT | REBATE FOR CB OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658D839978.2527777778 | X70658D8 |  | Parent | TRUE | NO.1 66KV BUS AT KTS | 39978.2528 | 39978.6118 | DAILY | 00001172 | SPICAPX | REMOVE No.1 66KV BUS VT & ITS ISOL | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658E339978.2527777778 | X70658E3 | X70658D8 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT KTS | 39978.2528 | 39978.6118 | DAILY | 00327947 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658E439978.2527777778 | X70658E4 | X70658D8 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT KTS | 39978.2528 | 39978.6118 | DAILY | 00337022 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029387239978.2944444444 | 10293872 |  | Parent | FALSE | HWTS NO.4 500KV LINE AT CBTS | 39978.2944 | 39978.6854 | DAILY | 00359491 | SPIMAINT | Overhaul 500kV Line at CBTS | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030881839978.3145833333 | 10308818 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT BETS | 39978.3146 | 39978.5729 | DAILY | 00016035 | DBPROX | VSCAP to Powercor | DISTCO |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858Z239979.2520833333 | X50858Z2 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39979.2521 | 39979.7424 | REPDAILY | 00002833 | SPICAPX | Remove Bus Conn's from No1 Trans No1 Bus CB | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858Z339979.2520833333 | X50858Z3 | X50858Z2 | Child | FALSE | PT. HENRY NO.1 220KV LINE AT GTS | 39979.2521 | 39979.7424 | REPDAILY | 00367277 | SPICAPX | Rebate W/O Pth No1 Ln during No1 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858Z439979.2520833333 | X50858Z4 | X50858Z2 | Child | FALSE | KTS NO.1 220KV LINE AT GTS | 39979.2521 | 39979.7424 | REPDAILY | 00367291 | SPICAPX | Rebate W/O KTS No1 Ln during No1 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858Z539979.2520833333 | X50858Z5 | X50858Z2 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 39979.2521 | 39979.7424 | REPDAILY | 00366646 | SPICAPX | Rebate W/O MLTS No2 Ln during No1 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X74158C039979.2916666667 | X74158C0 |  | Parent | FALSE | ROTS 220KV LINE NO.2 BUS CB AT TSTS | 39979.2917 | 39981.4861 | CONT | [12 empty] | 0
_V88258A039979.2944444444 | V88258A0 |  | Parent | FALSE | B2 220/66KV TRANS AT RTS | 39979.2944 | 39991.7181 | CONT | 00007331 | SPIMAINT | Replace PCB Contaminated Oil | SPIPOWER | V882 | V882 - (RTS) B2 TRANSFORMER OIL REGENERATION | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029410439979.2951388889 | 10294104 |  | Parent | FALSE | B3A 220/66KV TRANS BANK AT BLTS | 39979.2951 | 39981.6396 | CONT | 00018491 | SPIMAINT | Condition Monitoring Metro Trans 2 day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X78558A839979.3027777778 | X78558A8 |  | Parent | FALSE | BTS NO.3 220KV LINE CB AT TTS | 39979.3028 | 39979.6354 | DAILY | [12 empty] | 0
_1029130539979.3791666667 | 10291305 |  | Parent | FALSE | BATS NO.1 LINE/TGTS LINE 220KV CB AT MLTS | 39979.3792 | 39981.5924 | CONT | [12 empty] | 0
_X74158E439979.5569444444 | X74158E4 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT TSTS | 39979.5569 | 39979.6583 | DAILY | 00329164 | SPICAPX | Isolate CT for digging up cables | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030914839979.7083333333 | 10309148 |  | Parent | FALSE | B1 TRANS 220KV CB AT GTS | 39979.7083 | 39980.2819 | CONT | [12 empty] | 0
_X50858Z239980.25 | X50858Z2 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39980.25 | 39980.7521 | REPDAILY | 00002833 | SPICAPX | Remove Bus Conn's from No1 Trans No1 Bus CB | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858Z339980.25 | X50858Z3 | X50858Z2 | Child | FALSE | PT. HENRY NO.1 220KV LINE AT GTS | 39980.25 | 39980.7521 | REPDAILY | 00367277 | SPICAPX | Rebate W/O Pth No1 Ln during No1 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858Z439980.25 | X50858Z4 | X50858Z2 | Child | FALSE | KTS NO.1 220KV LINE AT GTS | 39980.25 | 39980.7521 | REPDAILY | 00367291 | SPICAPX | Rebate W/O KTS No1 Ln during No1 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858Z539980.25 | X50858Z5 | X50858Z2 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 39980.25 | 39980.7521 | REPDAILY | 00366646 | SPICAPX | Rebate W/O MLTS No2 Ln during No1 220kv Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558A939980.2916666667 | X78558A9 |  | Parent | FALSE | KTS NO.1 220KV LINE NO.3 BUS CB AT TTS | 39980.2917 | 39980.5868 | DAILY | [12 empty] | 0
_X89258A339980.2958333333 | X89258A3 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39980.2958 | 39980.8063 | REPDAILY | 00319999 | SPICAPX | Out W/O APD No2 Line - Earth wire replacement | SPIPOWER | X892 | X892 - (HYTS-APD) GROUND WIRE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AC39980.2986111111 | X50858AC |  | Parent | FALSE | B2 TRANS NO.1 BUS 220KV CB AT GTS | 39980.2986 | 40406.3403 | CONT | [12 empty] | 0
_X50858AC39980.3402777778 | X50858AC |  | Parent | FALSE | B2 TRANS NO.1 BUS 220KV CB AT GTS | 39980.3403 | 40406.2986 | CONT | [12 empty] | 0
_1030409939980.3506944444 | 10304099 |  | Parent | FALSE | NO.2 66KV BUS VT AT HTS | 39980.3507 | 39980.5861 | DAILY | [12 empty] | 0
_X50858Z839980.7527777778 | X50858Z8 |  | Parent | FALSE | B1 TRANS 220KV CB AT GTS | 39980.7528 | 40007.6708 | CONT | [12 empty] | 0
_X50858AD39981.25 | X50858AD |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39981.25 | 39981.759 | REPDAILY | 00002833 | SPICAPX | Replace Bus Insulators in Bays E,F,G,H,J,K L | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858AE39981.25 | X50858AE | X50858AD | Child | FALSE | PT. HENRY NO.1 220KV LINE AT GTS | 39981.25 | 39981.759 | REPDAILY | 00367277 | SPICAPX | Rebate W/O PTH No1 Ln during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AF39981.25 | X50858AF | X50858AD | Child | FALSE | KTS NO.1 220KV LINE AT GTS | 39981.25 | 39981.759 | REPDAILY | 00367291 | SPICAPX | Rebate W/O KTSNo1 Ln during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AG39981.25 | X50858AG | X50858AD | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 39981.25 | 39981.759 | REPDAILY | 00366646 | SPICAPX | Rebate W/O MLTS No2 Ln during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558A639981.2902777778 | X78558A6 |  | Parent | FALSE | EX - B4 TRANS NO.2 BUS 220KV CB AT TTS | 39981.2903 | 39981.6465 | DAILY | [12 empty] | 0
_1029067939981.2930555556 | 10290679 |  | Parent | FALSE | L4 TRANS 'C' NTH BUS 22KV CB AT RTS | 39981.2931 | 39981.5736 | DAILY | [12 empty] | 0
_X89258A339981.2944444444 | X89258A3 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39981.2944 | 39981.6965 | REPDAILY | 00319999 | SPICAPX | Out W/O APD No2 Line - Earth wire replacement | SPIPOWER | X892 | X892 - (HYTS-APD) GROUND WIRE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029205039981.3013888889 | 10292050 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT SHTS | 39981.3014 | 39981.6521 | DAILY | [12 empty] | 0
_1030410139981.4416666667 | 10304101 |  | Parent | FALSE | NO.3 66KV BUS VT AT HTS | 39981.4417 | 39981.5174 | DAILY | [12 empty] | 0
_X50858AE39982.25 | X50858AE | X50858AD | Child | FALSE | PT. HENRY NO.1 220KV LINE AT GTS | 39982.25 | 39982.7319 | REPDAILY | 00367277 | SPICAPX | Rebate W/O PTH No1 Ln during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AF39982.25 | X50858AF | X50858AD | Child | FALSE | KTS NO.1 220KV LINE AT GTS | 39982.25 | 39982.7319 | REPDAILY | 00367291 | SPICAPX | Rebate W/O KTSNo1 Ln during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AG39982.25 | X50858AG | X50858AD | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 39982.25 | 39982.7319 | REPDAILY | 00366646 | SPICAPX | Rebate W/O MLTS No2 Ln during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AD39982.25 | X50858AD |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39982.25 | 39982.7326 | REPDAILY | 00002833 | SPICAPX | Replace Bus Insulators in Bays E,F,G,H,J,K L | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029068139982.2944444444 | 10290681 |  | Parent | FALSE | L4 TRANS 'C' STH BUS 22KV CB AT RTS | 39982.2944 | 39982.5896 | DAILY | [12 empty] | 0
_X78558A139982.2958333333 | X78558A1 |  | Parent | FALSE | RWTS 220KV LINE NO.1 BUS CB AT TTS | 39982.2958 | 39982.6896 | DAILY | [12 empty] | 0
_1029410639982.2958333333 | 10294106 |  | Parent | FALSE | B4 220/66KV TRANS AT KTS | 39982.2958 | 39983.6542 | CONT | 00001146 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X89258A339982.2979166667 | X89258A3 |  | Parent | FALSE | HYTS-APD 2 500KV W | 39982.2979 | 39982.7465 | REPDAILY | 00319999 | SPICAPX | Out W/O APD No2 Line - Earth wire replacement | SPIPOWER | X892 | X892 - (HYTS-APD) GROUND WIRE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029131439982.3291666667 | 10291314 |  | Parent | FALSE | A2 TRANS NO.1 BUS 220KV CB AT MLTS | 39982.3292 | 39982.6014 | REPDAILY | [12 empty] | 0
_1030925339982.3583333333 | 10309253 |  | Parent | FALSE | B1 220/66KV TRANS AT WBTS | 39982.3583 | 39982.4208 | CONT | 00366199 | FAULT | WBTS B1 & B2 Trans Tripped anti Islanding comm alm | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1030925639982.3583333333 | 10309256 |  | Parent | FALSE | B2 220/66KV TRANS AT WBTS | 39982.3583 | 39982.4208 | CONT | 00366200 | FAULT | WBTS B1 & B2 Trans Tripped anti Islanding comm alm | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1029131439983.3125 | 10291314 |  | Parent | FALSE | A2 TRANS NO.1 BUS 220KV CB AT MLTS | 39983.3125 | 39983.5583 | REPDAILY | [12 empty] | 0
_1029294439983.3180555556 | 10292944 |  | Parent | FALSE | HWTS NO.2 220KV LINE NO.2 BUS CB AT HWPS | 39983.3181 | 39983.5556 | DAILY | [12 empty] | 0
_1030927239983.4819444444 | 10309272 |  | Parent | FALSE | JLGA 220KV BUS AT JLGA | 39983.4819 | 39983.5569 | DAILY | 00325257 | GENCO | SCAP: A 220kV Bus Isolated at JLTS | GENCO |  |  | Bus | 3rd Party | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030931039983.9916666667 | 10309310 |  | Parent | FALSE | NO.3 GEN 220/16.5KV TRANS AT HWPS | 39983.9917 | 39987.3625 | CONT | 00009644 | GENCO | HVS: No3 Gen isol'd for PS | GENCO |  |  | Connection Transformers | 3rd Party | 220 | NON SP ASSET | EXCLUDED |  | 0
_X70658D939984.2736111111 | X70658D9 |  | Parent | FALSE | NO.4 66KV BUS AT KTS | 39984.2736 | 39984.5903 | DAILY | 00001174 | SPICAPX | REMOVE No.4 66KV BUS VT & ITS ISOLS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858X939984.2861111111 | X50858X9 |  | Parent | FALSE | NO.4 66KV BUS AT GTS | 39984.2861 | 39984.5542 | CONT | 00002838 | SPICAPX | SOR De energise No4 66kv Bus, No4 Cap Bk CB Comm | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X87058E739984.2958333333 | X87058E7 |  | Parent | FALSE | BATS-BETS 220KV | 39984.2958 | 39984.5632 | REPDAILY | 00328505 | SPICAPX | BATS-BETS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030925039984.325 | 10309250 |  | Parent | FALSE | B2 220/66KV TRANS AT BATS | 39984.325 | 39984.6465 | DAILY | 00006555 | SPIMAINT | Replace faulty Insulators on 220kv Conn's at rack | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V74658A139984.34375 | V74658A1 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 39984.3438 | 39984.4847 | DAILY | 00002863 | SPICAPX | OUT W/O M1Trans for OLTC funct checks | SPIPOWER | V746 | V746 - (HYTS) MODIFICATION OF TRANSFORMER PARALLEL CONTROL | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z82558A039985.2916666667 | Z82558A0 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT SVTS | 39985.2917 | 39985.7139 | DAILY | 00351700 | VEN_AUG | Ductor all Connections | SPIPOWER | Z825 | Z825 - (ROTS-SVTS) 220KV UPGRADE TO 82 DEGREE C | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058E739985.2979166667 | X87058E7 |  | Parent | FALSE | BATS-BETS 220KV | 39985.2979 | 39985.6417 | REPDAILY | 00328505 | SPICAPX | BATS-BETS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AH39986.2743055556 | X50858AH |  | Parent | FALSE | PT. HENRY NO.1 220KV LINE AT GTS | 39986.2743 | 39986.709 | REPDAILY | 00367277 | SPICAPX | Install Structural Steel & GW Mast to Rack Struct | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X74158C239986.2819444445 | X74158C2 |  | Parent | FALSE | B1 TRANS NO.1 BUS 220KV CB AT TSTS | 39986.2819 | 39988.6444 | CONT | [12 empty] | 0
_X50858AI39987.2708333333 | X50858AI |  | Parent | FALSE | PT. HENRY NO.2 220KV LINE AT GTS | 39987.2708 | 39987.7222 | REPDAILY | 00367278 | SPICAPX | Install Structural Steel & GW Mast to Rack Struct | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558A739987.2923611111 | X78558A7 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT TTS | 39987.2924 | 39987.5465 | DAILY | [12 empty] | 0
_1029409439987.2923611111 | 10294094 |  | Parent | FALSE | B1 220/66KV TRANS AT TSTS | 39987.2924 | 39988.6444 | CONT | 00007657 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V7A058A339987.3277777778 | V7A058A3 |  | Parent | FALSE | ROTS NO.3 LINE/KTS LINE 500KV CB AT SMTS | 39987.3278 | 39990.6528 | CONT | [12 empty] | 0
_1029132339987.3493055556 | 10291323 |  | Parent | FALSE | TGTS 220KV LINE NO.2 BUS CB AT MLTS | 39987.3493 | 39989.6181 | CONT | [12 empty] | 0
_X78558B439987.5138888889 | X78558B4 |  | Parent | FALSE | B1 TRANS 220KV CB AT TTS | 39987.5139 | 39987.6111 | DAILY | [12 empty] | 0
_X50858AJ39988.2708333333 | X50858AJ |  | Parent | FALSE | MLTS NO.2 220KV LINE AT GTS | 39988.2708 | 39988.7042 | REPDAILY | 00366646 | SPICAPX | Install Structural Steel & GW Mast to Rack Struct | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558A439988.3034722222 | X78558A4 |  | Parent | FALSE | B5 TRANS NO.2 BUS 220KV CB AT TTS | 39988.3035 | 39988.5743 | DAILY | [12 empty] | 0
_1029058239988.3131944445 | 10290582 |  | Parent | FALSE | 2-5 220KV BUS TIE CB AT HWPS | 39988.3132 | 39988.625 | DAILY | [12 empty] | 0
_X74158B439988.3138888889 | X74158B4 |  | Parent | TRUE | EX - HWPS NO.1 220KV LINE CB CT R/PH AT YPS | 39988.3139 | 39990.6576 | CONT | [12 empty] | 0
_X74158B539988.3138888889 | X74158B5 | X74158B4 | Child | FALSE | HWPS NO.1 220KV LINE AT YPS | 39988.3139 | 39990.6576 | CONT | 00016409 | SPICAPX | REBATE FOR CT REPLACEMENT | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458C239989.28125 | X7E458C2 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 39989.2812 | 39989.7194 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458C339989.28125 | X7E458C3 | X7E458C2 | Child | FALSE | HYTS-APD 1 500KV W | 39989.2812 | 39989.7194 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458C539989.28125 | X7E458C5 | X7E458C2 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39989.2812 | 39989.7194 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E458C739989.28125 | X7E458C7 | X7E458C2 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 39989.2812 | 39989.7194 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030925739989.28125 | 10309257 |  | Parent | FALSE | APD NO.1/MLTS NO.1 LINE 500KV CB AT HYTS | 39989.2812 | 39989.7208 | REPDAILY | [12 empty] | 0
_X78558B139989.3159722222 | X78558B1 |  | Parent | FALSE | B2 TRANS 220KV CB AT TTS | 39989.316 | 39989.7118 | DAILY | [12 empty] | 0
_1030925139989.3541666667 | 10309251 |  | Parent | FALSE | NO.1 66KV BUS EXTENSION AT TSTS | 39989.3542 | 39989.5271 | DAILY | 00007673 | SPIMAINT | VSCAP CITIPOWER | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030455539989.3583333333 | 10304555 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT MBTS | 39989.3583 | 39989.4104 | DAILY | [12 empty] | 0
_1030940439989.53125 | 10309404 |  | Parent | TRUE | NO.1 220KV BUS AT RTS | 39989.5312 | 39989.5674 | DAILY | 00007347 | FAULT | Rebate loss No1 220KV Bus | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030940539989.53125 | 10309405 | 10309404 | Child | FALSE | B1 220/66KV TRANS AT RTS | 39989.5312 | 39989.5674 | DAILY | 00007329 | FAULT | Rebate loss of B1 220/66KV Transf | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030940939989.53125 | 10309409 | 10309404 | Child | FALSE | ROTS NO.1 220KV LINE AT RTS | 39989.5312 | 39989.5674 | DAILY | 00021385 | FAULT | Rebate loss of ROTS No1 220KV Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030942139989.53125 | 10309421 |  | Parent | FALSE | L1 220/22KV TRANS AT RTS | 39989.5312 | 39989.8201 | DAILY | 00007330 | SPIMAINT | Rebate loss of L1 220/22KV Transformer | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030941739989.8201388889 | 10309417 |  | Parent | FALSE | L1 TRANS 'A' NTH BUS 22KV CB AT RTS | 39989.8201 | 39998.2924 | CONT | [12 empty] | 0
_X7E458C239990.2819444445 | X7E458C2 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 39990.2819 | 39990.6917 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458C339990.2819444445 | X7E458C3 | X7E458C2 | Child | FALSE | HYTS-APD 1 500KV W | 39990.2819 | 39990.6917 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458C539990.2819444445 | X7E458C5 | X7E458C2 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 39990.2819 | 39990.6917 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E458C739990.2819444445 | X7E458C7 | X7E458C2 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 39990.2819 | 39990.6917 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X78558B239990.2972222222 | X78558B2 |  | Parent | FALSE | EX - B3 TRANS 220KV CB AT TTS | 39990.2972 | 39990.5118 | DAILY | [12 empty] | 0
_1029288339990.3166666667 | 10292883 |  | Parent | TRUE | B4 TRANS 66KV CB AT SHTS | 39990.3167 | 39990.5708 | DAILY | [12 empty] | 0
_1030878639990.3166666667 | 10308786 | 10292883 | Child | FALSE | B4 220/66KV TRANS AT SHTS | 39990.3167 | 39990.5708 | DAILY | 00350590 | SPIMAINT | Perf calc W/O B4 Trans during its 66kV CB O/H | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X74158C639990.3326388889 | X74158C6 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT TSTS | 39990.3326 | 39993.6757 | CONT | 00329164 | SPICAPX | Replacement of CT | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X70658E739991.2291666667 | X70658E7 | X70658B0 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 39991.2292 | 39991.8417 | DAILY | 00026097 | SPICAPX | CAPTURE OUTAGE COSTS FOR A3 TRANS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X70658B039991.2291666667 | X70658B0 |  | Parent | TRUE | NO.2 220KV BUS AT KTS | 39991.2292 | 39991.8423 | DAILY | 00001170 | SPICAPX | bi-pods to from 2 bus to future a2 tr 220kv cb roi | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658E139991.2493055556 | X70658E1 |  | Parent | TRUE | NO.1 66KV BUS AT KTS | 39991.2493 | 39991.7451 | DAILY | 00001172 | SPICAPX | CONNECT FUTURE No.1 66KV BUS VT & ITS ISOL | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658E539991.2493055556 | X70658E5 | X70658E1 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT KTS | 39991.2493 | 39991.7451 | DAILY | 00327947 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658E639991.2493055556 | X70658E6 | X70658E1 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT KTS | 39991.2493 | 39991.7451 | DAILY | 00337022 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030910339991.2958333333 | 10309103 |  | Parent | TRUE | T431 RWTS-TTS 220KV | 39991.2958 | 39991.6049 | DAILY | [12 empty] | 0
_1030915839991.2958333333 | 10309158 | 10309103 | Child | FALSE | T431 RWTS-TTS 220KV | 39991.2958 | 39991.6049 | DAILY | [12 empty] | 0
_1030948039991.2958333333 | 10309480 | 10309103 | Child | TRUE | RWTS-TTS 220KV WT | 39991.2958 | 39991.6049 | DAILY | 00119311 | SPIMAINT | Rbate for tree clearing Outage request | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030948139991.2958333333 | 10309481 | 10309480 | Child | FALSE | T431 RWTS-TTS 220KV | 39991.2958 | 39991.6049 | DAILY | [12 empty] | 0
_X70658B139992.2305555556 | X70658B1 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 39992.2306 | 39992.684 | DAILY | 00001169 | SPICAPX | bi-pods from 1 bus to future ats L 220kv cb roi | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658G539992.2305555556 | X70658G5 | X70658B1 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 39992.2306 | 39992.684 | DAILY | 00119824 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z82558A139992.2847222222 | Z82558A1 |  | Parent | FALSE | ROTS NO.2 220KV LINE AT SVTS | 39992.2847 | 39992.6799 | DAILY | 00351701 | VEN_AUG | Ductor all Connections | SPIPOWER | Z825 | Z825 - (ROTS-SVTS) 220KV UPGRADE TO 82 DEGREE C | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V8F158A539992.2986111111 | V8F158A5 |  | Parent | FALSE | B2 220/66KV TRANS AT WMTS | 39992.2986 | 39992.6542 | DAILY | 00003235 | SPIMAINT | Check Oil Leaks | SPIPOWER | V8F1 | V8F1 - REPAIR OF OIL LEAKS IN TERMINAL STNS - STAGE 1 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658G139992.6875 | X70658G1 |  | Parent | FALSE | ATS LINE/A2 TRANS 220KV CB AT KTS | 39992.6875 | 39998.1875 | CONT | [12 empty] | 0
_V8B758A439993.2930555556 | V8B758A4 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT WMTS | 39993.2931 | 39996.9132 | CONT | [12 empty] | 0
_V8B758A639993.2930555556 | V8B758A6 | V8B758A4 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT WMTS | 39993.2931 | 39996.9132 | CONT | 00074391 | SPIMAINT | capture outage costs | SPIPOWER | V8B7 | V8B7 - ABB EDF CB ADJUSTMENT | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029130239993.2944444444 | 10291302 |  | Parent | FALSE | BATS NO.1 220KV LINE NO.1 BUS CB AT MLTS | 39993.2944 | 39995.7257 | CONT | [12 empty] | 0
_X78558A339993.3048611111 | X78558A3 |  | Parent | FALSE | TSTS 220KV LINE NO.3 BUS CB AT TTS | 39993.3049 | 39993.5708 | DAILY | [12 empty] | 0
_X74158C139993.3048611111 | X74158C1 |  | Parent | FALSE | TTS LINE/B1 TRANS 220KV CB AT TSTS | 39993.3049 | 39993.609 | CONT | [12 empty] | 0
_1029050939993.3145833333 | 10290509 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 39993.3146 | 39993.5757 | DAILY | [12 empty] | 0
_1030947939993.3875 | 10309479 |  | Parent | FALSE | HWPS-JLTS 1 220KV G | 39993.3875 | 39993.3979 | CONT | 00020442 | REM_TRIP | Loss of JLTS No1 Bus due to JLGS B Stn Remote Trip | GENCO |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029411239993.4694444445 | 10294112 |  | Parent | FALSE | NO.1B 220/66/22KV TRANS AT RCTS | 39993.4694 | 39996.6118 | CONT | 00016758 | SPIMAINT | Condition Monitoring Country Trans 2day North Area | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030949939993.7173611111 | 10309499 |  | Parent | FALSE | SYN/COND AT BLTS | 39993.7174 | 39993.759 | CONT | 00002547 | FAULT | BLTS Synch Cond Trip | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X78558A039994.2923611111 | X78558A0 |  | Parent | TRUE | ROTS 220KV LINE CB AT TTS | 39994.2924 | 39994.4014 | DAILY | [12 empty] | 0
_X78558C239994.2923611111 | X78558C2 | X78558A0 | Child | FALSE | ROTS 220KV LINE AT TTS | 39994.2924 | 39994.4014 | DAILY | 00015733 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1029051239994.3194444444 | 10290512 |  | Parent | FALSE | LYPS NO.2 LINE/ROTS NO.3 LINE 500KV CB AT HWTS | 39994.3194 | 39994.5722 | DAILY | [12 empty] | 0
_1030949639994.4513888889 | 10309496 |  | Parent | FALSE | 2M BRANCH UNIT (B2) [TTS,77,4ABC,01] | 39994.4514 | 39994.4896 | DAILY | [12 empty] | 0
_1030951139994.4972222222 | 10309511 |  | Parent | FALSE | RWTS 220KV LINE NO.2 BUS CB AT TTS | 39994.4972 | 39994.6944 | DAILY | [12 empty] | 0
_1030891239995.3111111111 | 10308912 |  | Parent | FALSE | MBTS NO.2 220KV LINE AT DDTS | 39995.3111 | 39995.5542 | REPDAILY | 00012363 | SPIMAINT | OUT W/O Inspection of MBTS 2L CB CT's by ABB | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029527439995.3277777778 | 10295274 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT RCTS | 39995.3278 | 39995.5646 | DAILY | 00016892 | SPIMAINT | OVERHAUL S/S TRANS | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1029445139995.3284722222 | 10294451 |  | Parent | FALSE | EX - NO.3 MAIN TRANS NO.1 BUS 500KV CB CT R/PH AT HWTS | 39995.3285 | 39995.4729 | DAILY | [12 empty] | 0
_1031622839995.4118055556 | 10316228 |  | Parent | FALSE | MWTS NO.1 66KV FDR AT LY | 39995.4118 | 39995.5167 | DAILY | 00015994 | FAULT | MWTS No1 Line CB Open at LY end only | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030954439995.4268171296 | 10309544 |  | Parent | FALSE | NO.1 AIR COMPRESSOR AT TTS | 39995.4268 | 39995.5528 | DAILY | [12 empty] | 0
_1029445339995.5430555556 | 10294453 |  | Parent | FALSE | EX - NO.4 MAIN TRANS NO.1 BUS 500KV CB CT R/PH AT HWTS | 39995.5431 | 39995.5972 | DAILY | [12 empty] | 0
_1030957339995.5979166667 | 10309573 |  | Parent | FALSE | MLRC 220KV LINE NO.2 BUS CB AT RCTS | 39995.5979 | 39995.6535 | DAILY | [12 empty] | 4
_X74158C539996.2979166667 | X74158C5 |  | Parent | FALSE | ROTS 220KV LINE NO.1 BUS CB AT TSTS | 39996.2979 | 39998.2882 | CONT | [12 empty] | 0
_1029129939996.30625 | 10291299 |  | Parent | FALSE | A1 TRANS NO.1 BUS 220KV CB AT MLTS | 39996.3063 | 39996.6507 | REPDAILY | [12 empty] | 0
_1030891239996.3145833333 | 10308912 |  | Parent | FALSE | MBTS NO.2 220KV LINE AT DDTS | 39996.3146 | 39996.6667 | REPDAILY | 00012363 | SPIMAINT | OUT W/O Inspection of MBTS 2L CB CT's by ABB | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030900239996.3270833333 | 10309002 | 10309004 | Child | FALSE | CBTS NO.1 220KV LINE X PROT AT ERTS | 39996.3271 | 39996.5056 | DAILY | [12 empty] | 0
_1030900439996.3270833333 | 10309004 |  | Parent | TRUE | CBTS NO.1 220KV LINE AT ERTS | 39996.3271 | 39996.5056 | DAILY | 00012286 | SPIMAINT | REBATE FOR LINE OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030947839996.3590277778 | 10309478 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT HYTS | 39996.359 | 39996.6729 | REPDAILY | 00331066 | DBPROX | VSCAP to PowerCor | DISTCO |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1030900339996.5069444444 | 10309003 | 10309007 | Child | FALSE | CBTS NO.2 220KV LINE X PROT AT ERTS | 39996.5069 | 39996.6521 | DAILY | [12 empty] | 0
_1030900739996.5069444444 | 10309007 |  | Parent | TRUE | CBTS NO.2 220KV LINE AT ERTS | 39996.5069 | 39996.6521 | DAILY | 00012284 | SPIMAINT | REBATE LINE OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030958539996.8333333333 | 10309585 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK CB AT WMTS | 39996.8333 | 39996.8403 | DAILY | [12 empty] | 0
_X50858AK39997.2520833333 | X50858AK |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 39997.2521 | 39997.7674 | DAILY | 00002833 | SPICAPX | Install bipods to fut B1 Trans 220 CB Bus Side ROI | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858AL39997.2520833333 | X50858AL | X50858AK | Child | FALSE | PT. HENRY NO.1 220KV LINE AT GTS | 39997.2521 | 39997.7674 | DAILY | 00367277 | SPICAPX | Rebate W/O PTH No1 Ln during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AM39997.2520833333 | X50858AM | X50858AK | Child | FALSE | KTS NO.1 220KV LINE AT GTS | 39997.2521 | 39997.7674 | DAILY | 00367291 | SPICAPX | Rebate W/O KTSNo1 Ln during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AN39997.2520833333 | X50858AN | X50858AK | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 39997.2521 | 39997.7674 | DAILY | 00366646 | SPICAPX | Rebate W/O MLTS No2 Ln during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029129939997.3395833333 | 10291299 |  | Parent | FALSE | A1 TRANS NO.1 BUS 220KV CB AT MLTS | 39997.3396 | 39997.5164 | REPDAILY | [12 empty] | 0
_1030963039997.3402777778 | 10309630 |  | Parent | FALSE | B4 220/66KV TRANS AT FBTS | 39997.3403 | 39997.3882 | CONT | 00002728 | FAULT | B4 Trans trip No4 66KV Bus | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030957039997.7708333333 | 10309570 |  | Parent | FALSE | B1 TRANS 220KV CB AT GTS | 39997.7708 | 39998.2292 | CONT | [12 empty] | 0
_1030965839997.8743055556 | 10309658 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 39997.8743 | 39999.9243 | CONT | [12 empty] | 0
_1030966339997.9395833333 | 10309663 |  | Parent | FALSE | SMTS NO.2 500KV LINE AT SYTS | 39997.9396 | 39998.0312 | CONT | 00016970 | FAULT | Unplanned opening of SMTS-SYTS No2 Line | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658C839998.1986111111 | X70658C8 |  | Parent | TRUE | EX - ATS 220KV LINE AT KTS | 39998.1986 | 39998.9069 | DAILY | 00015978 | SPICAPX | remove and replace ATS line conductor at KTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658G739998.1986111111 | X70658G7 | X70658C8 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 39998.1986 | 39998.9069 | DAILY | 00119824 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X50858AO39998.2486111111 | X50858AO |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 39998.2486 | 39999.7 | CONT | 00002828 | SPICAPX | Remove bridges & isols and instal new harpstrings | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X74158C439998.2916666667 | X74158C4 |  | Parent | FALSE | ROTS 220KV LINE AT TSTS | 39998.2917 | 39998.9153 | DAILY | 00020107 | SPICAPX | Complete replacement of CT | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030942139998.2923611111 | 10309421 |  | Parent | FALSE | L1 220/22KV TRANS AT RTS | 39998.2924 | 39998.6535 | DAILY | 00007330 | SPIMAINT | Rebate loss of L1 220/22KV Transformer | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658F339998.75 | X70658F3 |  | Parent | FALSE | B1 TRANS 220KV CB AT KTS | 39998.75 | 40026.2292 | CONT | [12 empty] | 0
_X74158E339998.8958333333 | X74158E3 |  | Parent | FALSE | ROTS 220KV LINE NO.2 BUS CB AT TSTS | 39998.8958 | 39999.3104 | CONT | [12 empty] | 0
_1030959839998.9069444445 | 10309598 |  | Parent | FALSE | KTS 220KV LINE AT ATS | 39998.9069 | 39999.2708 | CONT | 00055535 | SPICAPX | KTS - ATS Line hold out HVS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030910539999.2513888889 | 10309105 |  | Parent | TRUE | NO.1 11/220KV TRANS BANK AT MPS | 39999.2514 | 39999.5333 | DAILY | 00001082 | SPIMAINT | ADJUST 220KV BUSHING OIL LEVELS. | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030913639999.2513888889 | 10309136 | 10309105 | Child | FALSE | HWPS-MWTS 220KV LINE AT MPS | 39999.2514 | 39999.5333 | DAILY | 00365925 | SPIMAINT | REBATE FOR TX OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658D039999.2638888889 | X70658D0 |  | Parent | TRUE | EX - ATS 220KV LINE AT KTS | 39999.2639 | 40000.0174 | DAILY | 00015978 | SPICAPX | remove and replace ATS line conductor at KTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658G939999.2638888889 | X70658G9 | X70658D0 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 39999.2639 | 40000.0174 | DAILY | 00119824 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X74158C739999.2909722222 | X74158C7 |  | Parent | FALSE | NO.2 220KV BUS AT TSTS | 39999.291 | 39999.6368 | DAILY | 00007671 | SPICAPX | Replacement of CVT | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X74158C339999.6388888889 | X74158C3 |  | Parent | FALSE | ROTS 220KV LINE NO.2 BUS CB AT TSTS | 39999.6389 | 40001.8493 | CONT | [12 empty] | 0
_X50858AR39999.6597222222 | X50858AR |  | Parent | FALSE | B1 TRANS 220KV CB AT GTS | 39999.6597 | 40004.3125 | CONT | [12 empty] | 0
_1030966639999.6604166667 | 10309666 |  | Parent | FALSE | NO.3 220KV BUS AT ATS | 39999.6604 | 39999.6674 | DAILY | 00356843 | FAULT | Trip No 3 Bus at ATS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E458C840000.2888888889 | X7E458C8 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40000.2889 | 40000.6368 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458C940000.2888888889 | X7E458C9 | X7E458C8 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40000.2889 | 40000.6368 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458D040000.2888888889 | X7E458D0 | X7E458C8 | Child | FALSE | HYTS-APD 1 500KV W | 40000.2889 | 40000.6368 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458D240000.2888888889 | X7E458D2 | X7E458C8 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40000.2889 | 40000.6368 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X50858Y840000.3548611111 | X50858Y8 |  | Parent | FALSE | EX - KTS NO.3 220KV LINE AT GTS | 40000.3549 | 40001.7222 | CONT | 00017902 | SPICAPX | Relocate VT's install connections and remove equip | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z56258B840000.3854166667 | Z56258B8 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 40000.3854 | 40000.8111 | REPDAILY | 00011755 | VEN_AUG | MKPS Line de-energ for BOPS X prot cut over | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030968340000.7305555556 | 10309683 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE AT HWTS | 40000.7306 | 40000.7535 | DAILY | 00016237 | FAULT | SMTS 1 Line 500KV CVT faulty at HWTS | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029347840000.8180555556 | 10293478 |  | Parent | FALSE | A 66/11KV S/S TRANS CABLE AT LY | 40000.8181 | 40003.6868 | DAILY | 00027176 | SPIMAINT | O/H A 66KV S/S TRANS FDR/CABLE AT LY | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030968540000.8555555556 | 10309685 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE AT HWTS | 40000.8556 | 40001.0625 | DAILY | 00016237 | FORCED | REMOVE SMTS 1L BPH LINE CVT | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458C840001.28125 | X7E458C8 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40001.2812 | 40001.7694 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458C940001.28125 | X7E458C9 | X7E458C8 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40001.2812 | 40001.7694 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458D040001.28125 | X7E458D0 | X7E458C8 | Child | FALSE | HYTS-APD 1 500KV W | 40001.2812 | 40001.7694 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458D240001.28125 | X7E458D2 | X7E458C8 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40001.2812 | 40001.7694 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029287740001.2986111111 | 10292877 |  | Parent | FALSE | NO.2 6.6KV BUS AT TSTS | 40001.2986 | 40001.5778 | DAILY | 00007681 | SPIMAINT | O/Haul NO.2 6.6KV BUS AT TSTS | SPIPOWER |  |  | Bus | Eastern | 6.6 | NON AER ELEMENT | EXCLUDED |  | 0
_1029041140001.3340277778 | 10290411 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK CB AT LY | 40001.334 | 40001.3611 | DAILY | [12 empty] | 0
_1029439140001.35625 | 10294391 |  | Parent | FALSE | SHTS NO.3 220KV LINE NO.2 BUS CB CT R/PH AT GNTS | 40001.3562 | 40001.4437 | DAILY | [12 empty] | 0
_1030965940001.3645833333 | 10309659 |  | Parent | FALSE | 22KV/415V S/S TRANS AT FTS | 40001.3646 | 40001.691 | DAILY | 00004393 | DBPROX | VSCAP to Jemena | DISTCO |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_Z56258B840001.3784722222 | Z56258B8 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 40001.3785 | 40002.6965 | REPDAILY | 00011755 | VEN_AUG | MKPS Line de-energ for BOPS X prot cut over | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030968640001.4479166667 | 10309686 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 40001.4479 | 40001.6181 | DAILY | [12 empty] | 0
_X50858Y940002.2513888889 | X50858Y9 |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 40002.2514 | 40002.6562 | REPDAILY | 00367296 | SPICAPX | Demolish old and Install new footings, Bay L East | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X74158D340002.2916666667 | X74158D3 |  | Parent | FALSE | B1 TRANS NO.1 BUS 220KV CB AT TSTS | 40002.2917 | 40006.291 | CONT | [12 empty] | 0
_1030969340002.3069444444 | 10309693 |  | Parent | FALSE | EX - NO.1 22KV/415V S/S TRANS AT ROTS | 40002.3069 | 40002.6326 | DAILY | 00004760 | DBPROX | VSCAP to DB | DISTCO |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1030972340002.3951388889 | 10309723 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 40002.3951 | 40005.2722 | CONT | [12 empty] | 0
_1030957940002.4097222222 | 10309579 |  | Parent | FALSE | MWTS NO.1 66KV FDR AT LY | 40002.4097 | 40002.4646 | DAILY | 00015994 | SPIMAINT | MWTS No1 Line CB Open | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858Y940003.2527777778 | X50858Y9 |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 40003.2528 | 40003.6562 | REPDAILY | 00367296 | SPICAPX | Demolish old and Install new footings, Bay L East | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028874240003.2944444444 | 10288742 |  | Parent | FALSE | RWTS 220KV LINE AT ROTS | 40003.2944 | 40003.6306 | DAILY | 00023949 | SPIMAINT | O/Haul - RWTS Line VT AT ROTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030455240003.35 | 10304552 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT GNTS | 40003.35 | 40003.4549 | REPDAILY | [12 empty] | 0
_1030961440003.3597222222 | 10309614 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40003.3597 | 40003.3951 | DAILY | 00319999 | APDALCOA | Outage Requested by APD to insul wash | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_Z56258B840003.3798611111 | Z56258B8 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 40003.3799 | 40003.6479 | REPDAILY | 00011755 | VEN_AUG | MKPS Line de-energ for BOPS X prot cut over | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030455140003.5291666667 | 10304551 |  | Parent | FALSE | DDTS NO.1 LINE/SHTS NO.1 LINE 220KV CB AT GNTS | 40003.5292 | 40003.6097 | REPDAILY | [12 empty] | 0
_1030976340003.6875 | 10309763 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT KGTS | 40003.6875 | 40009.6514 | CONT | 00359899 | FORCED | Faulty relay | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029348040003.7006944444 | 10293480 |  | Parent | FALSE | B 66/11KV S/S TRANS CABLE AT LY | 40003.7007 | 40004.7083 | DAILY | 00027177 | SPIMAINT | O/H B 66KV S/S TRANS FDR/CABLE AT LY | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030878440003.7006944444 | 10308784 |  | Parent | FALSE | B 66/11KV S/S TRANS AT LYPS | 40003.7007 | 40004.7083 | DAILY | 00325331 | SPIMAINT | SLIGHT OIL LEAK FROM TOP COVER AS PER LYPS | SPIPOWER |  |  | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858Y940004.2576388889 | X50858Y9 |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 40004.2576 | 40004.6667 | REPDAILY | 00367296 | SPICAPX | Demolish old and Install new footings, Bay L East | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AT40004.2777777778 | X50858AT |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 40004.2778 | 40007.7618 | CONT | 00002828 | SPICAPX | Replace B1 Trans VT's & remove conns to harpstring | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030455240004.3527777778 | 10304552 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT GNTS | 40004.3528 | 40004.4507 | REPDAILY | [12 empty] | 0
_Z56258B840004.3777777778 | Z56258B8 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 40004.3778 | 40004.6715 | REPDAILY | 00011755 | VEN_AUG | MKPS Line de-energ for BOPS X prot cut over | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030979540004.3993055556 | 10309795 |  | Parent | FALSE | DC SUPPLY SYSTEMS AT HYTS | 40004.3993 | 40023.6535 | CONT | [12 empty] | 0
_1030455140004.5402777778 | 10304551 |  | Parent | FALSE | DDTS NO.1 LINE/SHTS NO.1 LINE 220KV CB AT GNTS | 40004.5403 | 40004.625 | REPDAILY | [12 empty] | 0
_X70658G340005.1895833333 | X70658G3 |  | Parent | TRUE | A2 500/220KV TRANS BANK AT KTS | 40005.1896 | 40005.6208 | DAILY | 00026096 | SPICAPX | remove a2 tr connections & install new ones | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X70658H440005.1895833333 | X70658H4 | X70658G3 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 40005.1896 | 40005.6208 | DAILY | 00026097 | SPICAPX | capture outage costs | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030977140005.2722222222 | 10309771 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE AT HWTS | 40005.2722 | 40005.6549 | DAILY | 00016237 | SPIMAINT | REPLACE SMTS No1L BPH CVT | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X71158A040005.2965277778 | X71158A0 |  | Parent | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 40005.2965 | 40005.7243 | CONT | 00015793 | SPICAPX | ROTS 2L OUTAGE | SPIPOWER | X711 | X711 - (HWPS) REDEVELOP 220KV SWYD - STAGE 1 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030980640005.6548611111 | 10309806 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 40005.6549 | 40010.6931 | CONT | [12 empty] | 0
_1030980840005.6666666667 | 10309808 |  | Parent | FALSE | A2 TRANS NO.2 BUS 220KV CB AT KTS | 40005.6667 | 40012.375 | CONT | [12 empty] | 0
_X70658G440006.2708333333 | X70658G4 |  | Parent | TRUE | A2 500/220KV TRANS BANK AT KTS | 40006.2708 | 40006.625 | DAILY | 00026096 | SPICAPX | install new a2 tr 220kv droppers | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X70658H540006.2708333333 | X70658H5 | X70658G4 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 40006.2708 | 40006.625 | DAILY | 00026097 | SPICAPX | capture outage costs | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X71158A140006.2916666667 | X71158A1 |  | Parent | FALSE | ROTS NO.2 220KV LINE NO.5 BUS CB AT HWPS | 40006.2917 | 40019.2917 | CONT | [12 empty] | 0
_X74158D540006.2930555556 | X74158D5 |  | Parent | FALSE | B1 220/66KV TRANS AT TSTS | 40006.2931 | 40006.4778 | DAILY | 00007657 | SPICAPX | Replacement of CT | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029348240006.3618055556 | 10293482 |  | Parent | FALSE | C 66/11KV S/S TRANS CABLE AT LY | 40006.3618 | 40009.7194 | DAILY | 00027178 | SPIMAINT | O/H C 66KV S/S TRANS FDR/CABLE AT LY | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1030980740006.3979166667 | 10309807 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 40006.3979 | 40013.4583 | CONT | 00016423 | GENCO | W1 Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X74158D240006.4777777778 | X74158D2 |  | Parent | FALSE | B1 TRANS NO.1 BUS 220KV CB AT TSTS | 40006.4778 | 40007.6222 | DAILY | [12 empty] | 0
_1028911440006.4798611111 | 10289114 | 10290619 | Child | FALSE | SYN/COND COOLING SYSTEM AT TSTS | 40006.4799 | 40006.4806 | CONT | [12 empty] | 0
_1029061940006.4798611111 | 10290619 |  | Parent | TRUE | SYN/COND AT TSTS | 40006.4799 | 40006.4806 | CONT | 00007626 | SPIMAINT | O/Haul Syn Con at TSTS | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030980940006.5979166667 | 10309809 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 40006.5979 | 40008.0278 | CONT | 00356084 | GENCO | Gen 6 isols | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858Y940007.2541666667 | X50858Y9 |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 40007.2542 | 40007.6944 | REPDAILY | 00367296 | SPICAPX | Demolish old and Install new footings, Bay L East | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028911440007.2909722222 | 10289114 | 10290619 | Child | FALSE | SYN/COND COOLING SYSTEM AT TSTS | 40007.291 | 40009.7576 | CONT | [12 empty] | 0
_1029061940007.2909722222 | 10290619 |  | Parent | TRUE | SYN/COND AT TSTS | 40007.291 | 40009.7576 | CONT | 00007626 | SPIMAINT | O/Haul Syn Con at TSTS | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029113940007.3131944445 | 10291139 |  | Parent | FALSE | WOTS 330KV LINE NO.2 BUS CB AT DDTS | 40007.3132 | 40011.6181 | CONT | [12 empty] | 0
_1030980340007.3194444444 | 10309803 |  | Parent | FALSE | EX - FUTURE KMS 66KV FDR CB AT SMTS | 40007.3194 | 40037.625 | DAILY | [12 empty] | 0
_Z56258B940007.3902777778 | Z56258B9 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 40007.3903 | 40007.6979 | REPDAILY | 00011755 | VEN_AUG | MKPS Line de-energ for BOPS Y prot cut over | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030983940007.7486111111 | 10309839 |  | Parent | FALSE | CBTS NO.2 220KV LINE CB AT ERTS | 40007.7486 | 40007.7799 | DAILY | [12 empty] | 0
_1031541340007.7486111111 | 10315413 |  | Parent | FALSE | CBTS NO.2 220KV LINE AT ERTS | 40007.7486 | 40007.7799 | DAILY | 00012284 | FAULT | Rebate outage for SIR | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AW40008.2520833333 | X50858AW |  | Parent | FALSE | EX - KTS NO.3 220KV LINE AT GTS | 40008.2521 | 40008.7625 | DAILY | 00017902 | SPICAPX | Demolish old and Install new footings, Bay L East | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658F440008.2555555556 | X70658F4 |  | Parent | FALSE | NO.3 220KV BUS AT KTS | 40008.2556 | 40008.759 | DAILY | 00001171 | SPICAPX | bi-pods from 3 bus to future B1trans 220kv cb roi | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029426740008.3201388889 | 10294267 |  | Parent | FALSE | BLLY 500KV LINE NO.3 BUS CB AT LYPS | 40008.3201 | 40008.5847 | DAILY | [12 empty] | 0
_V7A058A440008.3277777778 | V7A058A4 |  | Parent | FALSE | ROTS NO.3 LINE/KTS LINE 500KV CB AT SMTS | 40008.3278 | 40011.5875 | CONT | [12 empty] | 0
_Z56258B940008.3763888889 | Z56258B9 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 40008.3764 | 40008.7 | REPDAILY | 00011755 | VEN_AUG | MKPS Line de-energ for BOPS Y prot cut over | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50588AZ40009.2506944445 | X50588AZ |  | Parent | FALSE | KTS NO.2 220KV LINE AT GTS | 40009.2507 | 40009.6451 | DAILY | 00367295 | SPICAPX | Install Structural Steel & GW Mast to Rack Struct | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X74158C940009.2909722222 | X74158C9 |  | Parent | TRUE | NO.2 220KV BUS AT TSTS | 40009.291 | 40009.7167 | DAILY | 00007671 | SPICAPX | Replacement of TTS Line No 2 Bus CB CVT | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X74158D440009.2909722222 | X74158D4 | X74158C9 | Child | FALSE | B3 220/66KV TRANS AT TSTS | 40009.291 | 40009.7167 | DAILY | 00007659 | SPICAPX | TRAN REBATE FOR BUS OUTAGE | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029426940009.3166666667 | 10294269 |  | Parent | FALSE | BLLY 500KV LINE NO.4 BUS CB AT LYPS | 40009.3167 | 40009.6028 | DAILY | [12 empty] | 0
_1029316540009.3208333333 | 10293165 |  | Parent | FALSE | B4 TRANS NO.1 BUS 220KV CB AT SHTS | 40009.3208 | 40009.6319 | DAILY | [12 empty] | 0
_Z56258B940009.3881944444 | Z56258B9 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 40009.3882 | 40009.6646 | REPDAILY | 00011755 | VEN_AUG | MKPS Line de-energ for BOPS Y prot cut over | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031262240009.5458333333 | 10312622 |  | Parent | FALSE | HWPS NO.1 220KV LINE AT JLTS | 40009.5458 | 40009.6292 | CONT | 00015936 | FORCED | Tracking a low CT IR reading | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AY40010.25 | X50858AY |  | Parent | FALSE | KTS NO.1 220KV LINE AT GTS | 40010.25 | 40010.7257 | DAILY | 00367291 | SPICAPX | Install Structural Steel & GW Mast to Rack Struct | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X74158D040010.2930555556 | X74158D0 |  | Parent | FALSE | TTS LINE/B1 TRANS 220KV CB AT TSTS | 40010.2931 | 40012.2542 | CONT | [12 empty] | 0
_X56558I540010.3055555556 | X56558I5 |  | Parent | FALSE | JINDERA 330KV LINE NO.2 BUS CB AT WOTS | 40010.3056 | 40010.5451 | DAILY | [12 empty] | 0
_1029316740010.3229166667 | 10293167 |  | Parent | FALSE | B4 TRANS NO.2 BUS 220KV CB AT SHTS | 40010.3229 | 40010.6444 | DAILY | [12 empty] | 0
_1030982240010.375 | 10309822 |  | Parent | FALSE | LNGS NO.1 GEN TRANS 220KV LINE AT ATS | 40010.375 | 40028.4681 | CONT | 00360128 | GENCO | Outage for GENCO on LNGS 1 GEN 220KV line | GENCO |  |  | Circuits | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030986440010.375 | 10309864 |  | Parent | FALSE | LNGS NO.2 GEN TRANS 220KV LINE AT ATS | 40010.375 | 40028.4681 | CONT | 00360129 | GENCO | outage for genco on lngs 2 gen 220kv line | GENCO |  |  | Circuits | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858AV40010.5152777778 | X50858AV |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT GTS | 40010.5153 | 40010.5153 | DAILY | [12 empty] | 0
_1031548540010.7569444444 | 10315485 |  | Parent | FALSE | CBTS NO.2 220KV LINE AT ERTS | 40010.7569 | 40010.7583 | DAILY | 00012284 | FAULT | Out work order for CBTS - ERTS 2 Line trip | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031545140010.7798611111 | 10315451 |  | Parent | FALSE | ERTS-CBTS 2 220KV E | 40010.7799 | 40010.7806 | DAILY | 00360714 | FAULT | CBTS No 2 Liine CB Trip | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858AX40011.2486111111 | X50858AX |  | Parent | FALSE | MLTS NO.1 220KV LINE AT GTS | 40011.2486 | 40011.691 | DAILY | 00367287 | SPICAPX | Install Structural Steel & GW Mast to Rack Struct | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028958640011.2868055556 | 10289586 |  | Parent | TRUE | B4 TRANS 220KV E/SW AT SHTS | 40011.2868 | 40011.5389 | DAILY | [12 empty] | 0
_1030931340011.2868055556 | 10309313 | 10289586 | Child | FALSE | B4 220/66KV TRANS AT SHTS | 40011.2868 | 40011.5389 | DAILY | 00350590 | SPIMAINT | Perf calc W/O B4 Trans during 220kV E/SW & ROI O-H | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028786040011.3194444444 | 10287860 |  | Parent | TRUE | B2 GEN TRANS NO.4 BUS 500KV CB AT LYPS | 40011.3194 | 40011.6007 | DAILY | [12 empty] | 0
_1030118240011.3194444444 | 10301182 | 10287860 | Child | FALSE | B2 GEN TRANS NO.4 BUS 500KV CB AT LYPS | 40011.3194 | 40011.6007 | DAILY | [12 empty] | 0
_1031547340011.4680555556 | 10315473 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 40011.4681 | 40011.7993 | DAILY | 00352791 | SPIMAINT | Investigate OLTC operation | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031545640011.5833333333 | 10315456 |  | Parent | FALSE | BATS-TGTS 220KV WW | 40011.5833 | 40011.5986 | DAILY | 00022665 | FORCED | De-energisation of 220KV Line to remove Birds Nest | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030924640011.5972222222 | 10309246 |  | Parent | FALSE | B3 TRANS 66KV CB AT MWTS | 40011.5972 | 40011.6087 | DAILY | [12 empty] | 0
_1031548640011.9423611111 | 10315486 |  | Parent | TRUE | ROTS 220KV LINE NO.1 BUS CB AT TSTS | 40011.9424 | 40011.9806 | DAILY | [12 empty] | 0
_1031548840011.9423611111 | 10315488 | 10315486 | Child | FALSE | B1 220/66KV TRANS AT TSTS | 40011.9424 | 40011.9806 | DAILY | 00007657 | FORCED | REBATE TRANS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031549040011.9423611111 | 10315490 | 10315486 | Child | FALSE | B2 220/66KV TRANS AT TSTS | 40011.9424 | 40011.9806 | DAILY | 00007658 | FORCED | REBATE TRANS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031549140011.9423611111 | 10315491 | 10315486 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT TSTS | 40011.9424 | 40011.9806 | DAILY | 00329164 | FORCED | REBATE CAP BANK | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1028651540012 | 10286515 |  | Parent | FALSE | NO.1 66KV BUS 'A' VT B/PH AT MWTS | 40012 | 40012 | DAILY | [12 empty] | 0
_X70658F240012.2173611111 | X70658F2 |  | Parent | FALSE | B3 220/66KV TRANS AT KTS | 40012.2174 | 40026.2292 | CONT | 00350448 | SPICAPX | SECONDARY CABLING AND TERMINATIONS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858BJ40012.25 | X50858BJ |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 40012.25 | 40012.6882 | DAILY | 00002834 | SPICAPX | Replace Bus Insulators Bays E,F,G,H,J,K L No2 Bus | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858BK40012.25 | X50858BK | X50858BJ | Child | FALSE | MLTS NO.1 220KV LINE AT GTS | 40012.25 | 40012.6882 | DAILY | 00367287 | SPICAPX | Rebate W/O MLTS 1 Ln during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858BL40012.25 | X50858BL | X50858BJ | Child | FALSE | KTS NO.2 220KV LINE AT GTS | 40012.25 | 40012.6882 | DAILY | 00367295 | SPICAPX | Rebate W/O KTS 2 Ln during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858BM40012.25 | X50858BM | X50858BJ | Child | FALSE | B4 220/66KV TRANS AT GTS | 40012.25 | 40012.6882 | DAILY | 00002830 | SPICAPX | Perf calc B4 Trans during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858BN40012.25 | X50858BN | X50858BJ | Child | FALSE | PT. HENRY NO.2 220KV LINE AT GTS | 40012.25 | 40012.6882 | DAILY | 00367278 | SPICAPX | Rebate W/O PTH 2 Ln during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X74158D140012.2541666667 | X74158D1 |  | Parent | FALSE | TTS 220KV LINE AT TSTS | 40012.2542 | 40012.5708 | DAILY | 00020098 | SPICAPX | Replacement of CT | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1026899540012.2722222222 | 10268995 |  | Parent | TRUE | NO.1 66KV BUS AT MWTS | 40012.2722 | 40012.5521 | DAILY | 00010278 | SPIMAINT | O/Haul NO.1 66KV BUS AT MWTS | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1028651540012.2722222222 | 10286515 |  | Parent | FALSE | NO.1 66KV BUS 'A' VT B/PH AT MWTS | 40012.2722 | 40012.5521 | DAILY | [12 empty] | 0
_1028651640012.2722222222 | 10286516 | 10268995 | Child | FALSE | MOE 66KV FDR CB BUS SIDE ISOL AT MWTS | 40012.2722 | 40012.5521 | DAILY | [12 empty] | 0
_1029973940012.2722222222 | 10299739 | 10268995 | Child | FALSE | JLTS NO.1 220KV LINE AT MWTS | 40012.2722 | 40012.5521 | DAILY | 00016130 | SPIMAINT | rebate for bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029974040012.2722222222 | 10299740 | 10268995 | Child | FALSE | LY NO.1 66KV FDR AT MWTS | 40012.2722 | 40012.5521 | DAILY | 00016140 | SPIMAINT | rebate for bus outage | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030983040012.2916666667 | 10309830 |  | Parent | FALSE | A4 500/220KV TRANS BANK AT KTS | 40012.2917 | 40012.6118 | DAILY | 00026098 | SPIMAINT | top up 220kv bushings | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X87058G040012.3131944445 | X87058G0 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 40012.3132 | 40012.6854 | REPDAILY | 00060187 | SPICAPX | MBTS-DDTS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658J440012.375 | X70658J4 |  | Parent | FALSE | ATS LINE/A2 TRANS 220KV CB AT KTS | 40012.375 | 40026.2396 | CONT | [12 empty] | 0
_X74158D640012.58125 | X74158D6 |  | Parent | FALSE | TTS LINE/B1 TRANS 220KV CB AT TSTS | 40012.5813 | 40013.5556 | CONT | [12 empty] | 0
_X50858BF40013.2444444444 | X50858BF |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 40013.2444 | 40013.6312 | DAILY | 00002829 | SPICAPX | Install Groundwire & support from B3 Trans to Rack | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031547640013.2951388889 | 10315476 |  | Parent | TRUE | S192 HWTS-SMTS 2 500KV | 40013.2951 | 40013.6646 | DAILY | [12 empty] | 0
_1031549540013.2951388889 | 10315495 | 10315476 | Child | FALSE | EX - SMTS NO.2 500KV LINE AT HWTS | 40013.2951 | 40013.6646 | DAILY | 00016238 | SPIMAINT | rebate for line outage | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031550940013.2958333333 | 10315509 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB AT HWTS | 40013.2958 | 40015.4167 | CONT | [12 empty] | 0
_1031550640013.3111111111 | 10315506 |  | Parent | TRUE | NO.2 500KV BUS AT HWTS | 40013.3111 | 40013.3285 | DAILY | 00009799 | FORCED | De energising of Bus for SMTS 2 Line CB | SPIPOWER |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1031551540013.3118055556 | 10315515 | 10315506 | Child | FALSE | A2 515/230KV TRANS BANK AT HWTS | 40013.3118 | 40013.3278 | DAILY | 00337572 | FORCED | Rebate- De energising of Bus for SMTS 2 Line CB | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031551640013.3131944445 | 10315516 | 10315506 | Child | FALSE | LYPS NO.1 500KV LINE AT HWTS | 40013.3132 | 40013.3271 | DAILY | 00016234 | FORCED | Rebate - De energising of Bus for SMTS 2 Line CB | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058G040013.3159722222 | X87058G0 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 40013.316 | 40013.6819 | REPDAILY | 00060187 | SPICAPX | MBTS-DDTS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028551340013.4027777778 | 10285513 |  | Parent | TRUE | APD NO.2/MLTS NO.2 LINE 500KV CB AT HYTS | 40013.4028 | 40013.7549 | REPDAILY | [12 empty] | 0
_1030925840013.4027777778 | 10309258 | 10285513 | Child | FALSE | HYTS-APD 2 500KV W | 40013.4028 | 40013.7549 | REPDAILY | 00319999 | SPIMAINT | Rebate W/O APD No2 Line during CB outage | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z56258C040014.2597222222 | Z56258C0 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 40014.2597 | 40016.6493 | CONT | 00011755 | VEN_AUG | SP-AusNet Linework for BOPS 220KV Connection | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031551440014.4965277778 | 10315514 |  | Parent | FALSE | W1 GEN TRANS NO.1 BUS 220KV CB AT YPS | 40014.4965 | 40019.7514 | CONT | [12 empty] | 0
_Z63658A340015.25 | Z63658A3 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 40015.25 | 40016.8299 | CONT | 00002863 | DB_AUG | M1 Trans - connect new M1 Tr SS Trans & tert cable | SPIPOWER | Z636 | Z636 - (HYTS) 22KV SUPPLY | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X72758B040015.2743055556 | X72758B0 |  | Parent | FALSE | B2 220/66KV TRANS AT TTS | 40015.2743 | 40016.5 | CONT | 00362454 | SPICAPX | DISCONNECT B2 TRANS & INSTALL RAD BANK | SPIPOWER | X727 | X727 - (TTS) B2 TRANSFORMER REPLACEMENT | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458D340015.2819444445 | X7E458D3 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40015.2819 | 40015.6958 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458D440015.2819444445 | X7E458D4 | X7E458D3 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40015.2819 | 40015.6958 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458D540015.2819444445 | X7E458D5 | X7E458D3 | Child | FALSE | HYTS-APD 1 500KV W | 40015.2819 | 40015.6958 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029416640015.2958333333 | 10294166 |  | Parent | FALSE | TBTS NO.2 220KV LINE NO.1 BUS CB AT CBTS | 40015.2958 | 40015.6264 | DAILY | [12 empty] | 0
_1030949140015.2965277778 | 10309491 |  | Parent | FALSE | NO.1A 66KV CAPACITOR BANK AT HTS | 40015.2965 | 40015.4993 | DAILY | 00004426 | SPIMAINT | Rebalance No1A cap bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029128940015.3013888889 | 10291289 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40015.3014 | 40015.6632 | REPDAILY | 00003011 | SPIMAINT | OVERHAUL OF A 220KV SHUNT REACTOR | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029159440015.3388888889 | 10291594 |  | Parent | FALSE | SYN/COND AT BLTS | 40015.3389 | 40017.6333 | CONT | 00002547 | SPIMAINT | 3 Monthly O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030869840015.3555555556 | 10308698 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT GNTS | 40015.3556 | 40015.475 | REPDAILY | [12 empty] | 0
_1031550840015.4166666667 | 10315508 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB AT HWTS | 40015.4167 | 40015.5771 | DAILY | [12 empty] | 0
_1030869740015.5590277778 | 10308697 |  | Parent | FALSE | DDTS NO.1 LINE/SHTS NO.1 LINE 220KV CB AT GNTS | 40015.559 | 40015.616 | REPDAILY | [12 empty] | 0
_1031555140015.9736111111 | 10315551 |  | Parent | FALSE | NO.7 GEN TRANS 220KV CB AT HWPS | 40015.9736 | 40019.8826 | CONT | [12 empty] | 0
_X7E458D340016.28125 | X7E458D3 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40016.2812 | 40016.616 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458D440016.28125 | X7E458D4 | X7E458D3 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40016.2812 | 40016.616 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458D540016.28125 | X7E458D5 | X7E458D3 | Child | FALSE | HYTS-APD 1 500KV W | 40016.2812 | 40016.616 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029128940016.2916666667 | 10291289 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40016.2917 | 40016.6458 | REPDAILY | 00003011 | SPIMAINT | OVERHAUL OF A 220KV SHUNT REACTOR | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029416040016.2986111111 | 10294160 |  | Parent | FALSE | TBTS NO.1 220KV LINE NO.1 BUS CB AT CBTS | 40016.2986 | 40016.6069 | DAILY | [12 empty] | 0
_1029112440016.3034722222 | 10291124 |  | Parent | TRUE | NO.1 TRANS 66KV CB AT WOTS | 40016.3035 | 40016.6937 | DAILY | [12 empty] | 0
_1030948340016.3034722222 | 10309483 | 10291124 | Child | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 40016.3035 | 40016.6937 | DAILY | 00004036 | SPIMAINT | Perf calc W/O No1 Trans during 66kV CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031540340016.3166666667 | 10315403 |  | Parent | FALSE | HWTS NO.1 LINE/SYTS NO.1 LINE 500KV CB AT SMTS | 40016.3167 | 40016.5757 | DAILY | [12 empty] | 0
_1028785740016.3166666667 | 10287857 |  | Parent | FALSE | B2 GEN TRANS NO.3 BUS 500KV CB AT LYPS | 40016.3167 | 40017.4368 | CONT | [12 empty] | 0
_1030869840016.3534722222 | 10308698 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT GNTS | 40016.3535 | 40016.4486 | REPDAILY | [12 empty] | 0
_1031555440016.3534722222 | 10315554 |  | Parent | FALSE | W2 GEN TRANS 220KV LINE E/SW AT YPS | 40016.3535 | 40018.8542 | CONT | [12 empty] | 0
_1031549240016.3986111111 | 10315492 |  | Parent | FALSE | FUTURE TEMP HYT 11 22KV FDR CB AT HYTS | 40016.3986 | 40016.6 | DAILY | [12 empty] | 0
_1030869740016.5430555556 | 10308697 |  | Parent | FALSE | DDTS NO.1 LINE/SHTS NO.1 LINE 220KV CB AT GNTS | 40016.5431 | 40016.5847 | REPDAILY | [12 empty] | 0
_1029416240017.3034722222 | 10294162 |  | Parent | FALSE | TBTS NO.1 LINE/ERTS NO.1 LINE 220KV CB AT CBTS | 40017.3035 | 40017.6 | DAILY | [12 empty] | 0
_1029128940017.3055555556 | 10291289 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40017.3056 | 40017.7076 | REPDAILY | 00003011 | SPIMAINT | OVERHAUL OF A 220KV SHUNT REACTOR | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031559540017.4555555556 | 10315595 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 40017.4556 | 40019.7819 | CONT | 00356081 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030953140017.5673611111 | 10309531 |  | Parent | FALSE | GNTS NO.1 220KV LINE NO.2 BUS CB AT SHTS | 40017.5674 | 40017.5972 | DAILY | [12 empty] | 0
_1030953240017.6069444444 | 10309532 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT SHTS | 40017.6069 | 40017.6271 | DAILY | [12 empty] | 0
_X70658H940018.2972222222 | X70658H9 |  | Parent | FALSE | NO.3 220KV BUS AT KTS | 40018.2972 | 40018.6111 | DAILY | 00001171 | SPICAPX | trip checks - b3 trans & no.3 bus outage required | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029416440018.2986111111 | 10294164 |  | Parent | FALSE | ERTS NO.1 220KV LINE NO.2 BUS CB AT CBTS | 40018.2986 | 40018.5785 | DAILY | [12 empty] | 0
_1029443940018.3118055556 | 10294439 |  | Parent | FALSE | W2 GEN TRANS NO.2 BUS 220KV CB CT W/PH AT YPS | 40018.3118 | 40018.4167 | DAILY | [12 empty] | 0
_1029022240018.3152777778 | 10290222 |  | Parent | FALSE | HPS 66KV LINE AT WOTS | 40018.3153 | 40018.7611 | DAILY | 00012055 | SPIMAINT | O/H HPS 66KV LINE AT WOTS | SPIPOWER |  |  | Circuits | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031564540018.5618055556 | 10315645 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB AT HWTS | 40018.5618 | 40018.5771 | CONT | [12 empty] | 0
_X71158A240019.2909722222 | X71158A2 |  | Parent | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 40019.291 | 40019.8292 | CONT | 00015793 | SPICAPX | ROTS 2L OUTAGE | SPIPOWER | X711 | X711 - (HWPS) REDEVELOP 220KV SWYD - STAGE 1 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E558A540019.29375 | X7E558A5 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40019.2937 | 40019.4674 | DAILY | 00022640 | SPICAPX | string opgw between tower 50 & 60 | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X74158D740019.2944444444 | X74158D7 |  | Parent | TRUE | NO.1 220KV BUS AT TSTS | 40019.2944 | 40019.6611 | DAILY | 00007670 | SPICAPX | Replacement of ROTS Line No 1 Bus CB CVT | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X74158D840019.2944444444 | X74158D8 | X74158D7 | Child | FALSE | B2 220/66KV TRANS AT TSTS | 40019.2944 | 40019.6611 | DAILY | 00007658 | SPICAPX | TRAN REBATE FOR BUS OUTAGE | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X74158D940019.2944444444 | X74158D9 | X74158D7 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT TSTS | 40019.2944 | 40019.6611 | DAILY | 00329164 | SPICAPX | CAP BANK REBATE FOR BUS OUTAGE | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X74158E940019.3027777778 | X74158E9 |  | Parent | FALSE | WMTS NO.1 220KV LINE AT FBTS | 40019.3028 | 40021.5931 | CONT | 00017159 | SPICAPX | replace 220kv ct's | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1031547440019.3333333333 | 10315474 |  | Parent | TRUE | B2 220/66KV TRANS AT RTS | 40019.3333 | 40019.4299 | DAILY | 00007331 | SPIMAINT | De-energised 2A & 2B 220kV Bus | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031547540019.3333333333 | 10315475 | 10315474 | Child | FALSE | BTS 220KV LINE AT RTS | 40019.3333 | 40019.4299 | DAILY | 00021222 | SPIMAINT | Rebate Line outage De-energised 2A & 2B 220kV Bus | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031566140020.1055555556 | 10315661 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 40020.1056 | 40020.4049 | CONT | 00016423 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X74158E040020.2930555556 | X74158E0 |  | Parent | TRUE | NO.1 220KV BUS AT TSTS | 40020.2931 | 40020.6264 | DAILY | 00007670 | SPICAPX | Replacement of No B1 Trans No1 Bus CVT | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X74158E140020.2930555556 | X74158E1 | X74158E0 | Child | FALSE | B2 220/66KV TRANS AT TSTS | 40020.2931 | 40020.6264 | DAILY | 00007658 | SPICAPX | TRAN REBATE FOR BUS OUTAGE | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X74158E240020.2930555556 | X74158E2 | X74158E0 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT TSTS | 40020.2931 | 40020.6264 | DAILY | 00329164 | SPICAPX | CAP BANK REBATE FOR BUS OUTAGE | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X7E558A640020.3125 | X7E558A6 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40020.3125 | 40020.734 | DAILY | 00022640 | SPICAPX | string opgw between tower 60 & 69 | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031566540020.4013888889 | 10315665 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.4 MAIN TRANS CB AT HWTS | 40020.4014 | 40020.4403 | CONT | [12 empty] | 0
_1029147140021.2708333333 | 10291471 |  | Parent | FALSE | SYN/COND AT FBTS | 40021.2708 | 40025.7312 | CONT | 00002697 | SPIMAINT | 3 Monthly O/HAUL - FBTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029417040021.3027777778 | 10294170 |  | Parent | FALSE | ERTS NO.2 220KV LINE NO.2 BUS CB AT CBTS | 40021.3028 | 40021.6188 | DAILY | [12 empty] | 0
_1030061540021.3152777778 | 10300615 |  | Parent | FALSE | LYPS NO.3 LINE/CBTS NO.4 LINE 500KV CB AT HWTS | 40021.3153 | 40021.4917 | DAILY | [12 empty] | 0
_X72758B240021.3263888889 | X72758B2 |  | Parent | FALSE | NO.3 66KV BUS VT AT TTS | 40021.3264 | 40021.4792 | DAILY | [12 empty] | 0
_1029410240021.3416666667 | 10294102 |  | Parent | FALSE | B3 220/66KV TRANS AT TSTS | 40021.3417 | 40022.6368 | CONT | 00007659 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031567840021.6513888889 | 10315678 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 40021.6514 | 40021.6625 | DAILY | [12 empty] | 0
_X7E458D840022.2833333333 | X7E458D8 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40022.2833 | 40022.6937 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458D940022.2833333333 | X7E458D9 | X7E458D8 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40022.2833 | 40022.6937 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458E040022.2833333333 | X7E458E0 | X7E458D8 | Child | FALSE | HYTS-APD 1 500KV W | 40022.2833 | 40022.6937 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458E240022.2833333333 | X7E458E2 | X7E458D8 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40022.2833 | 40022.6937 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029416840022.3 | 10294168 |  | Parent | FALSE | TBTS NO.2 LINE/ERTS NO.2 LINE 220KV CB AT CBTS | 40022.3 | 40022.5917 | DAILY | [12 empty] | 0
_1031566340022.3236111111 | 10315663 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.4 MAIN TRANS CB AT HWTS | 40022.3236 | 40022.6264 | DAILY | [12 empty] | 0
_X72758B340022.3423611111 | X72758B3 |  | Parent | FALSE | NO.4 66KV BUS VT AT TTS | 40022.3424 | 40022.4514 | DAILY | [12 empty] | 0
_X50858BG40023.25 | X50858BG |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 40023.25 | 40025.7264 | CONT | 00367296 | SPICAPX | Install jumpers from Harpstrings to KTS3 Ln equip | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458D840023.2916666667 | X7E458D8 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40023.2917 | 40023.7917 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458D940023.2916666667 | X7E458D9 | X7E458D8 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40023.2917 | 40023.7917 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458E040023.2916666667 | X7E458E0 | X7E458D8 | Child | FALSE | HYTS-APD 1 500KV W | 40023.2917 | 40023.7917 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458E240023.2916666667 | X7E458E2 | X7E458D8 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40023.2917 | 40023.7917 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031572340023.3125 | 10315723 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 40023.3125 | 40023.4222 | DAILY | 00012436 | SPIMAINT | Replace dislodged clevis pin | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031574540023.3645833333 | 10315745 |  | Parent | FALSE | MKPS-BOPS-MBTS 220KV NW | 40023.3646 | 40023.7166 | DAILY | 00060197 | VEN_AUG | Install Bridges from O/H to PS 220KV U/G at T14 | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X74158F940023.3986111111 | X74158F9 |  | Parent | FALSE | 3-4 220KV BUS TIE CB AT FBTS | 40023.3986 | 40026.3125 | CONT | [12 empty] | 0
_1029410840024.2881944444 | 10294108 |  | Parent | FALSE | B1 220/66KV TRANS AT SVTS | 40024.2882 | 40024.6924 | CONT | 00004849 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area(W) | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458D840024.2916666667 | X7E458D8 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40024.2917 | 40024.8021 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458D940024.2916666667 | X7E458D9 | X7E458D8 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40024.2917 | 40024.8021 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458E040024.2916666667 | X7E458E0 | X7E458D8 | Child | FALSE | HYTS-APD 1 500KV W | 40024.2917 | 40024.8021 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458E240024.2916666667 | X7E458E2 | X7E458D8 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40024.2917 | 40024.8021 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029113040024.3 | 10291130 |  | Parent | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 40024.3 | 40024.7875 | REPDAILY | 00004037 | SPIMAINT | O/H TRANS & OLTC | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029417440024.3006944444 | 10294174 |  | Parent | FALSE | A1 TRANS NO.2 BUS 220KV CB AT CBTS | 40024.3007 | 40024.5764 | DAILY | [12 empty] | 0
_1030455440024.3416666667 | 10304554 |  | Parent | FALSE | RCTS 220KV LINE NO.2 BUS CB AT HOTS | 40024.3417 | 40024.6222 | REPDAILY | [12 empty] | 0
_1030455340024.4277777778 | 10304553 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT HOTS | 40024.4278 | 40024.5785 | REPDAILY | [12 empty] | 0
_1031591640024.7972222222 | 10315916 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 40024.7972 | 40025.7556 | CONT | 00363305 | FAULT | investigate diverter pressure trip | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029417240025.2986111111 | 10294172 |  | Parent | FALSE | A1 TRANS NO.1 BUS 220KV CB AT CBTS | 40025.2986 | 40025.5708 | DAILY | [12 empty] | 0
_1030901740025.3152777778 | 10309017 | X74158B3 | Child | FALSE | ROTS NO.5 220KV LINE AT YPS | 40025.3153 | 40027.7785 | CONT | 00016413 | SPICAPX | Rebate for ROTS 5 220KV Line YPS CT Replacement | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X74158B340025.3152777778 | X74158B3 |  | Parent | TRUE | EX - ROTS NO.5 220KV LINE NO.2 BUS CB CT R/PH AT YPS | 40025.3153 | 40027.7785 | CONT | [12 empty] | 0
_1029113040025.3201388889 | 10291130 |  | Parent | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 40025.3201 | 40025.6646 | REPDAILY | 00004037 | SPIMAINT | O/H TRANS & OLTC | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031570340025.6069444444 | 10315703 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB AT HWTS | 40025.6069 | 40025.6083 | DAILY | [12 empty] | 0
_X50858BH40025.7861111111 | X50858BH |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 40025.7861 | 40028.2757 | CONT | [12 empty] | 0
_1031587640026.0555555556 | 10315876 |  | Parent | FALSE | YWPS NO.4 220KV LINE AT YPS | 40026.0556 | 40029.6931 | CONT | 00016428 | GENCO | SCAP YWPS No4 Gen Trans 220kV Line | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658F840026.23125 | X70658F8 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40026.2312 | 40026.7215 | DAILY | 00001169 | SPICAPX | rem/inst o/head cables from b3 tr to 220 kv racks | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658L140026.23125 | X70658L1 | X70658F8 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40026.2312 | 40026.7215 | DAILY | 00119824 | SPICAPX | rebate outage number for cap bank | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X74158G140026.2833333333 | X74158G1 |  | Parent | FALSE | NO.3 220KV BUS AT FBTS | 40026.2833 | 40026.7465 | CONT | 00002735 | SPICAPX | Install new 220KV CVT for No3 220KV bus | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X87058G340026.2916666667 | X87058G3 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 40026.2917 | 40026.7014 | REPDAILY | 00060187 | SPICAPX | MBTS-DDTS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658K140026.3868055556 | X70658K1 |  | Parent | FALSE | ATS LINE/A2 TRANS 220KV CB AT KTS | 40026.3868 | 40034.7174 | CONT | [12 empty] | 0
_1031590640026.5423611111 | 10315906 |  | Parent | FALSE | MLRC 220KV LINE NO.2 BUS CB AT RCTS | 40026.5424 | 40026.6014 | CONT | [12 empty] | 4
_1029147140026.6527777778 | 10291471 |  | Parent | FALSE | SYN/COND AT FBTS | 40026.6528 | 40026.7076 | CONT | 00002697 | SPIMAINT | 3 Monthly O/HAUL - FBTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X74158G040026.7083333333 | X74158G0 |  | Parent | FALSE | 1-3 220KV BUS TIE CB AT FBTS | 40026.7083 | 40030.7417 | CONT | [12 empty] | 0
_X70658K240026.7152777778 | X70658K2 |  | Parent | FALSE | B1 TRANS 220KV CB AT KTS | 40026.7153 | 40041.2014 | CONT | [12 empty] | 0
_X70658K340026.7152777778 | X70658K3 |  | Parent | FALSE | EX - B3 TRANS 220KV CB AT KTS | 40026.7153 | 40070.2875 | CONT | [12 empty] | 0
_X70658K040026.7222222222 | X70658K0 |  | Parent | FALSE | B3 220/66KV TRANS AT KTS | 40026.7222 | 40027.6208 | CONT | 00350448 | SPICAPX | precommission & commission tests | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031592440026.7451388889 | 10315924 |  | Parent | FALSE | NO.4 220KV BUS AT FBTS | 40026.7451 | 40026.7465 | CONT | 00002736 | FAULT | No4 220kV Bus Tripped | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031592540026.7451388889 | 10315925 |  | Parent | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 40026.7451 | 40026.7465 | CONT | 00327661 | FAULT | No4 220kV bus Trip No4 Cap Bank Rebate W/O | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031592640026.7451388889 | 10315926 |  | Parent | FALSE | WMTS-FBTS 1 220KV WY | 40026.7451 | 40026.7465 | CONT | 00022785 | FAULT | No4 220kV Bus Trip WMTS Line Rebate W/O | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1031592740026.7451388889 | 10315927 |  | Parent | FALSE | NPSD-FBTS 220KV WY | 40026.7451 | 40026.7465 | CONT | 00022738 | FAULT | No4 220kV Bus Trip NPSD Line Rebate W/0 | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031592840026.7451388889 | 10315928 |  | Parent | FALSE | B4 220/66KV TRANS AT FBTS | 40026.7451 | 40026.7465 | CONT | 00002728 | FAULT | No4 220kV BUS Trip B4 Trans Rebate W/O | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031592940026.7451388889 | 10315929 |  | Parent | FALSE | SYN/COND AT FBTS | 40026.7451 | 40026.7472 | CONT | 00002697 | FAULT | No4 220kV Bus Trip SynCon Rebate W/O | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X87058G340027.2916666667 | X87058G3 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 40027.2917 | 40027.5412 | REPDAILY | 00060187 | SPICAPX | MBTS-DDTS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031593240028.1256944445 | 10315932 |  | Parent | FALSE | AUX D 220/22KV TRANS AT YPS | 40028.1257 | 40028.1979 | DAILY | 00356098 | FAULT | AER W/O for Trip AUX 'D' 220/22KV TRANS AT YPS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Owned by SPAusNet | 0
_X50858BS40028.25 | X50858BS |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 40028.25 | 40028.7257 | REPDAILY | 00367296 | SPICAPX | Construct footings and install equipment in Bay L | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031585540028.7013888889 | 10315855 |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 40028.7014 | 40029.2493 | REPDAILY | [12 empty] | 0
_X50858BS40029.25 | X50858BS |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 40029.25 | 40029.6729 | REPDAILY | 00367296 | SPICAPX | Construct footings and install equipment in Bay L | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031574340029.2680555556 | 10315743 |  | Parent | FALSE | EX - SYTS LINE/A4 TRANS 500KV CB AT KTS | 40029.2681 | 40030.6104 | DAILY | [12 empty] | 0
_1030978440029.2798611111 | 10309784 | X78558B7 | Child | FALSE | ROTS 220KV LINE AT TTS | 40029.2799 | 40029.4333 | DAILY | 00015733 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X78558B740029.2798611111 | X78558B7 |  | Parent | TRUE | ROTS 220KV LINE CB AT TTS | 40029.2799 | 40029.4333 | DAILY | [12 empty] | 0
_X7E458E340029.28125 | X7E458E3 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40029.2812 | 40029.741 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458E440029.28125 | X7E458E4 | X7E458E3 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40029.2812 | 40029.741 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458E540029.28125 | X7E458E5 | X7E458E3 | Child | FALSE | HYTS-APD 1 500KV W | 40029.2812 | 40029.741 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458E740029.28125 | X7E458E7 | X7E458E3 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40029.2812 | 40029.741 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029287540029.2965277778 | 10292875 |  | Parent | FALSE | NO.1 6.6KV BUS AT TSTS | 40029.2965 | 40029.5875 | DAILY | 00007678 | SPIMAINT | O/Haul NO.1 6.6KV BUS AT TSTS | SPIPOWER |  |  | Bus | Eastern | 6.6 | NON AER ELEMENT | EXCLUDED |  | 0
_V7A058A540029.3138888889 | V7A058A5 |  | Parent | FALSE | KTS 500KV LINE NO.1 BUS CB AT SMTS | 40029.3139 | 40031.6271 | CONT | [12 empty] | 0
_V71158B340029.3208333333 | V71158B3 |  | Parent | FALSE | 2-4 500KV BUS TIE CB AT LYPS | 40029.3208 | 40049.3021 | CONT | [12 empty] | 0
_1028989840029.33125 | 10289898 |  | Parent | TRUE | NO.2A 66KV CAPACITOR BANK AT SHTS | 40029.3313 | 40029.6444 | REPDAILY | 00350862 | SPIMAINT | O/Haul NO.2A 66KV CAPACITOR BANK AT SHTS | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029207640029.33125 | 10292076 | 10289898 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT SHTS | 40029.3313 | 40029.6444 | REPDAILY | 00330829 | SPIMAINT | O/H 66KV CAP BANK AT SHTS | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029442340029.3423611111 | 10294423 |  | Parent | FALSE | AUX TRANS 'C' NO.1 BUS 220KV CB CT R/PH AT YPS | 40029.3424 | 40029.3819 | DAILY | [12 empty] | 0
_1029441940029.4208333333 | 10294419 |  | Parent | FALSE | AUX TRANS 'C' NO.2 BUS 220KV CB CT R/PH AT YPS | 40029.4208 | 40029.4437 | DAILY | [12 empty] | 0
_1031615540029.5763888889 | 10316155 |  | Parent | FALSE | SYN/COND AT TSTS | 40029.5764 | 40029.5931 | CONT | 00007626 | FAULT | Syn Con Trip during test operation of the Start CB | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031585540029.675 | 10315855 |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 40029.675 | 40030.2479 | REPDAILY | [12 empty] | 0
_X50858BS40030.25 | X50858BS |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 40030.25 | 40030.7729 | REPDAILY | 00367296 | SPICAPX | Construct footings and install equipment in Bay L | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030979040030.2770833333 | 10309790 | X78558B9 | Child | FALSE | BTS NO.3 220KV LINE AT TTS | 40030.2771 | 40030.4271 | DAILY | 00015724 | SPICAPX | capture outage costs | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558B940030.2770833333 | X78558B9 |  | Parent | TRUE | BTS NO.3 220KV LINE CB AT TTS | 40030.2771 | 40030.4271 | DAILY | [12 empty] | 0
_X7E458E340030.2868055556 | X7E458E3 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40030.2868 | 40030.75 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458E440030.2868055556 | X7E458E4 | X7E458E3 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40030.2868 | 40030.75 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458E540030.2868055556 | X7E458E5 | X7E458E3 | Child | FALSE | HYTS-APD 1 500KV W | 40030.2868 | 40030.75 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458E740030.2868055556 | X7E458E7 | X7E458E3 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40030.2868 | 40030.75 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031569140030.3104166667 | 10315691 |  | Parent | FALSE | A1 TRANS NO.1 BUS 220KV CB AT MLTS | 40030.3104 | 40030.6694 | DAILY | [12 empty] | 0
_1030874540030.3722222222 | 10308745 |  | Parent | FALSE | BETS LINE NO.2 BUS CB AT KGTS | 40030.3722 | 40030.4167 | REPDAILY | [12 empty] | 0
_1029441740030.4340277778 | 10294417 |  | Parent | FALSE | 5 GRP TRANS 220KV CB CT R/PH AT YPS | 40030.434 | 40030.4882 | DAILY | [12 empty] | 0
_1030874440030.4708333333 | 10308744 |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT KGTS | 40030.4708 | 40030.5167 | REPDAILY | [12 empty] | 0
_1031585540030.775 | 10315855 |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 40030.775 | 40031.2479 | REPDAILY | [12 empty] | 0
_X50858BS40031.25 | X50858BS |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 40031.25 | 40031.7069 | REPDAILY | 00367296 | SPICAPX | Construct footings and install equipment in Bay L | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558B840031.2972222222 | X78558B8 |  | Parent | FALSE | TSTS 220KV LINE NO.1 BUS CB AT TTS | 40031.2972 | 40031.4611 | DAILY | [12 empty] | 0
_1028990040031.3409722222 | 10289900 |  | Parent | TRUE | NO.3A 66KV CAPACITOR BANK AT SHTS | 40031.341 | 40031.6549 | DAILY | 00350863 | SPIMAINT | O/Haul NO.3A 66KV CAPACITOR BANK AT SHTS | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029207840031.3409722222 | 10292078 | 10289900 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT SHTS | 40031.341 | 40031.6549 | DAILY | 00330780 | SPIMAINT | O/Haul NO.3B 66KV CAPACITOR BANK AT SHTS | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031585540031.7055555556 | 10315855 |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 40031.7056 | 40032.2583 | REPDAILY | [12 empty] | 0
_X50858BS40032.2583333333 | X50858BS |  | Parent | FALSE | KTS NO.3 220KV LINE AT GTS | 40032.2583 | 40032.6507 | REPDAILY | 00367296 | SPICAPX | Construct footings and install equipment in Bay L | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558C040032.2979166667 | X78558C0 |  | Parent | FALSE | KTS NO.1 220KV LINE NO.3 BUS CB AT TTS | 40032.2979 | 40032.4993 | DAILY | [12 empty] | 0
_X71158B540032.4395833333 | X71158B5 |  | Parent | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 40032.4396 | 40032.4563 | DAILY | 00015793 | SPICAPX | HWPS-ROTS 2L DE-ENERG FOR CVT SEC CUB MOVE | SPIPOWER | X711 | X711 - (HWPS) REDEVELOP 220KV SWYD - STAGE 1 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658J740032.4583333333 | X70658J7 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT KTS | 40032.4583 | 40034.7174 | CONT | 00026096 | SPICAPX | remove 220kv connections from a2 trans | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X50858BT40032.6534722222 | X50858BT |  | Parent | FALSE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 40032.6535 | 40045.2451 | CONT | [12 empty] | 0
_X60758J240033.2111111111 | X60758J2 |  | Parent | TRUE | NO.2 220KV BUS AT KTS | 40033.2111 | 40033.7903 | REPDAILY | 00001170 | SPICAPX | remove a2 tr connections & install new ones | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658J340033.2111111111 | X70658J3 | X60758J2 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 40033.2111 | 40033.7903 | DAILY | 00026097 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X74158F440033.3020833333 | X74158F4 |  | Parent | FALSE | NO.2 220KV BUS AT TSTS | 40033.3021 | 40033.6424 | DAILY | 00007671 | SPICAPX | Replacement of CVT Connection | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031620340033.3472222222 | 10316203 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 40033.3472 | 40036.7681 | CONT | 00356082 | GENCO | Unit 4 SCAP Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858BY40033.3583333333 | X50858BY |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 40033.3583 | 40033.3722 | DAILY | 00002830 | SPICAPX | Remove wiring to B4 Trans 66kv Metering CT | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658F740033.6805555556 | X70658F7 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 40033.6806 | 40041.2292 | CONT | 00001147 | SPICAPX | SECONDARY CABLING AND TERMINATIONS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X60758J240034.25 | X60758J2 |  | Parent | TRUE | NO.2 220KV BUS AT KTS | 40034.25 | 40034.7174 | REPDAILY | 00001170 | SPICAPX | remove a2 tr connections & install new ones | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658J340034.25 | X70658J3 | X60758J2 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 40034.25 | 40034.7174 | DAILY | 00026097 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1028891540034.2784722222 | 10288915 |  | Parent | TRUE | FR NO.2 66KV FDR BUS AT RTS | 40034.2785 | 40034.6597 | DAILY | 00022394 | SPIMAINT | Overhaul Sub FR No.2 Fdr Bus @ RTS | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029069340034.2784722222 | 10290693 | 10288915 | Child | FALSE | FR NO.2 66KV FDR NO.4 BUS CB AT RTS | 40034.2785 | 40034.6597 | DAILY | [12 empty] | 0
_1029069640034.2784722222 | 10290696 | 10288915 | Child | FALSE | EX - FR NO.2 66KV FDR NO.3 BUS CB AT RTS | 40034.2785 | 40034.6597 | DAILY | [12 empty] | 0
_X74158F640034.2944444444 | X74158F6 |  | Parent | FALSE | B1 220/66KV TRANS AT TSTS | 40034.2944 | 40034.6424 | DAILY | 00007657 | SPICAPX | Replacement of CVT | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_741758A140034.3263888889 | 741758A1 |  | Parent | FALSE | YPS -ROTS 5 220KV E | 40034.3264 | 40034.7688 | DAILY | 00022789 | DB_AUG | Cut in OPGW at Officer for new ZSS | SPIPOWER | 74176149 | New Zone Substation Officer (OFR) | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031564240035.2895833333 | 10315642 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40035.2896 | 40045.6104 | CONT | 00003011 | SPIMAINT | Out W/O 220kV Sh React works by Wilsons | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029072940035.3722222222 | 10290729 |  | Parent | TRUE | NO.2 220KV BUS AT HOTS | 40035.3722 | 40035.7056 | REPDAILY | 00006939 | SPIMAINT | O/Haul NO.2 220KV BUS AT HOTS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031551140035.3722222222 | 10315511 | 10290729 | Child | FALSE | B3 220/66KV TRANS AT HOTS | 40035.3722 | 40035.7056 | REPDAILY | 00363102 | SPIMAINT | Perf calc W/O B2 Trans during No2 220kV Bus O/H | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458F940036.2923611111 | X7E458F9 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40036.2924 | 40036.7361 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458G040036.2923611111 | X7E458G0 | X7E458F9 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40036.2924 | 40036.7361 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458G140036.2923611111 | X7E458G1 | X7E458F9 | Child | FALSE | HYTS-APD 1 500KV W | 40036.2924 | 40036.7361 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458G340036.2923611111 | X7E458G3 | X7E458F9 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40036.2924 | 40036.7361 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029396640036.2951388889 | 10293966 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT CBTS | 40036.2951 | 40036.6104 | DAILY | [12 empty] | 0
_1029072940036.2972222222 | 10290729 |  | Parent | TRUE | NO.2 220KV BUS AT HOTS | 40036.2972 | 40036.7306 | REPDAILY | 00006939 | SPIMAINT | O/Haul NO.2 220KV BUS AT HOTS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031551140036.2972222222 | 10315511 | 10290729 | Child | FALSE | B3 220/66KV TRANS AT HOTS | 40036.2972 | 40036.7306 | REPDAILY | 00363102 | SPIMAINT | Perf calc W/O B2 Trans during No2 220kV Bus O/H | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031620540036.3055555556 | 10316205 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 40036.3056 | 40036.6201 | DAILY | 00363305 | SPIMAINT | MTS B3 Trans OLTC Low Oil | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458F940037.2826388889 | X7E458F9 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40037.2826 | 40037.7188 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458G040037.2826388889 | X7E458G0 | X7E458F9 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40037.2826 | 40037.7188 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458G140037.2826388889 | X7E458G1 | X7E458F9 | Child | FALSE | HYTS-APD 1 500KV W | 40037.2826 | 40037.7188 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458G340037.2826388889 | X7E458G3 | X7E458F9 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40037.2826 | 40037.7188 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029072740037.2923611111 | 10290727 |  | Parent | TRUE | NO.1 220KV BUS AT HOTS | 40037.2924 | 40037.7528 | REPDAILY | 00006938 | SPIMAINT | O/Haul NO.1 220KV BUS AT HOTS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031551240037.2923611111 | 10315512 | 10290727 | Child | FALSE | STATIC VAR COMPENSATOR AT HOTS | 40037.2924 | 40037.7528 | REPDAILY | 00019243 | SPIMAINT | Rebate W/O for SVC during No1 220kV BUS outage | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031551340037.2923611111 | 10315513 | 10290727 | Child | FALSE | B2 220/66KV TRANS AT HOTS | 40037.2924 | 40037.7528 | REPDAILY | 00363103 | SPIMAINT | Perf calc W/O B2 Trans during No1 220kV BUS outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029396840037.2951388889 | 10293968 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT CBTS | 40037.2951 | 40037.6007 | DAILY | [12 empty] | 0
_V8D258A340037.3548611111 | V8D258A3 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT ROTS | 40037.3549 | 40037.5463 | DAILY | 00004761 | SPIMAINT | Connect new supply to No2 S/S Trans transf Bus | SPIPOWER | V8D2 | V8D2 - (ROTS) REPLACE 220KV BUS DUCT SLIDING SUPPORT | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1031619540037.425 | 10316195 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB AT HWTS | 40037.425 | 40037.4861 | DAILY | [12 empty] | 0
_1031593140037.4597222222 | 10315931 | V8B658A5 | Child | FALSE | AUX 'D' 220/22KV TRANS 220KV CB AT YPS | 40037.4597 | 40038.5097 | DAILY | [12 empty] | 0
_1029072740038.2916666667 | 10290727 |  | Parent | TRUE | NO.1 220KV BUS AT HOTS | 40038.2917 | 40038.7188 | REPDAILY | 00006938 | SPIMAINT | O/Haul NO.1 220KV BUS AT HOTS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031551240038.2916666667 | 10315512 | 10290727 | Child | FALSE | STATIC VAR COMPENSATOR AT HOTS | 40038.2917 | 40038.7188 | REPDAILY | 00019243 | SPIMAINT | Rebate W/O for SVC during No1 220kV BUS outage | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031551340038.2916666667 | 10315513 | 10290727 | Child | FALSE | B2 220/66KV TRANS AT HOTS | 40038.2917 | 40038.7188 | REPDAILY | 00363103 | SPIMAINT | Perf calc W/O B2 Trans during No1 220kV BUS outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z73058K040038.2916666667 | Z73058K0 |  | Parent | FALSE | EX - FUTURE KMS 66KV FDR CB AT SMTS | 40038.2917 | 40046.5944 | CONT | [12 empty] | 0
_1029128540038.3159722222 | 10291285 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 40038.316 | 40038.4819 | DAILY | 00003104 | SPIMAINT | O/Haul 66KV CAPACITOR BANK AT TGTS | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031639040038.5576388889 | 10316390 |  | Parent | FALSE | NO.8 GEN TRANS 220KV CB AT HWPS | 40038.5576 | 40043.7243 | CONT | [12 empty] | 0
_1029072740039.29375 | 10290727 |  | Parent | TRUE | NO.1 220KV BUS AT HOTS | 40039.2937 | 40039.6937 | REPDAILY | 00006938 | SPIMAINT | O/Haul NO.1 220KV BUS AT HOTS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031551240039.29375 | 10315512 | 10290727 | Child | FALSE | STATIC VAR COMPENSATOR AT HOTS | 40039.2937 | 40039.6937 | REPDAILY | 00019243 | SPIMAINT | Rebate W/O for SVC during No1 220kV BUS outage | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031551340039.29375 | 10315513 | 10290727 | Child | FALSE | B2 220/66KV TRANS AT HOTS | 40039.2937 | 40039.6937 | REPDAILY | 00363103 | SPIMAINT | Perf calc W/O B2 Trans during No1 220kV BUS outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658K940039.35 | X70658K9 |  | Parent | FALSE | NO.2 66KV BUS VT R/PH AT KTS | 40039.35 | 40039.6181 | DAILY | [12 empty] | 0
_X70658L040039.35 | X70658L0 |  | Parent | FALSE | NO.4 66KV BUS VT R/PH AT KTS | 40039.35 | 40039.6215 | DAILY | [12 empty] | 0
_V8D258A140039.3611111111 | V8D258A1 |  | Parent | FALSE | SPARE 500KV SF6 BUS DUCTING AT ROTS | 40039.3611 | 40049.3201 | CONT | 00004781 | SPIMAINT | SFT for OOC SF6 Spare Duct | SPIPOWER | V8D2 | V8D2 - (ROTS) REPLACE 220KV BUS DUCT SLIDING SUPPORT | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1031622940039.4326388889 | 10316229 |  | Parent | FALSE | AUX TRANS 'C' NO.2 BUS 220KV CB AT YPS | 40039.4326 | 40039.4611 | DAILY | [12 empty] | 0
_1031619740039.5722222222 | 10316197 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT LY | 40039.5722 | 40039.62 | DAILY | 00009893 | SPIMAINT | OPERATOR TRAINING | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658F540040.21875 | X70658F5 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40040.2188 | 40040.8007 | DAILY | 00001169 | SPICAPX | install bipods from 1 bus to fut b1 tr cb b/s roi | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658L540040.21875 | X70658L5 | X70658F5 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40040.2188 | 40040.8007 | DAILY | 00119824 | SPICAPX | rebate w/o on cap bank for no.1 220kv bus | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X50858BR40040.2493055556 | X50858BR |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 40040.2493 | 40040.5674 | DAILY | 00002828 | SPICAPX | Remove 220kv Bushing Cap Taps and VCU | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V8F158A240040.2923611111 | V8F158A2 |  | Parent | FALSE | L1 220/22KV TRANS AT RTS | 40040.2924 | 40040.6535 | REPDAILY | 00007330 | SPIMAINT | Check Oil Leaks | SPIPOWER | V8F1 | V8F1 - REPAIR OF OIL LEAKS IN TERMINAL STNS - STAGE 1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_741758A240040.3041666667 | 741758A2 |  | Parent | FALSE | YPS -ROTS 5 220KV E | 40040.3042 | 40040.625 | DAILY | 00022789 | DB_AUG | Cut in OPGW at Officer for new ZSS | SPIPOWER | 74176149 | New Zone Substation Officer (OFR) | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031640140040.8 | 10316401 |  | Parent | FALSE | EX - GTS NO.1 220KV LINE NO.1 BUS CB AT KTS | 40040.8 | 40041.2292 | CONT | [12 empty] | 0
_X70658L240041.2375 | X70658L2 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40041.2375 | 40041.625 | DAILY | 00001169 | SPICAPX | CONNECT B1 TRANS IN 220KV BAY I & COMMISSION | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658L640041.2375 | X70658L6 | X70658L2 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40041.2375 | 40041.625 | DAILY | 00119824 | SPICAPX | rebate w/o on cap bank for no.1 220kv bus | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_V8F158A240041.2930555556 | V8F158A2 |  | Parent | FALSE | L1 220/22KV TRANS AT RTS | 40041.2931 | 40041.5889 | REPDAILY | 00007330 | SPIMAINT | Check Oil Leaks | SPIPOWER | V8F1 | V8F1 - REPAIR OF OIL LEAKS IN TERMINAL STNS - STAGE 1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658K740043.2715277778 | X70658K7 |  | Parent | FALSE | EX - GTS NO.1 220KV LINE AT KTS | 40043.2715 | 40044.6208 | CONT | 00015985 | SPICAPX | REMOVE GTS No1 LINE SPAN BETWEEN RACKS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458E940043.28125 | X7E458E9 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40043.2812 | 40043.7611 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458F040043.28125 | X7E458F0 | X7E458E9 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40043.2812 | 40043.7611 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458F140043.28125 | X7E458F1 | X7E458E9 | Child | FALSE | HYTS-APD 1 500KV W | 40043.2812 | 40043.7611 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458F340043.28125 | X7E458F3 | X7E458E9 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40043.2812 | 40043.7611 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031594140043.2840277778 | 10315941 | 10289607 | Child | FALSE | R1 220/66/22KV TRANS AT KGTS | 40043.284 | 40043.659 | DAILY | 00357301 | SPIMAINT | Perf calc W/O No1 Trans during its 22kV CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028960740043.2840277778 | 10289607 |  | Parent | TRUE | NO.1 TRANS 22KV CB AT KGTS | 40043.284 | 40043.6596 | DAILY | [12 empty] | 0
_1031696940043.5819444444 | 10316969 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 40043.5819 | 40057.8824 | CONT | 00356083 | GENCO | SCAP on Unit 5 | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_741758A440044.2958333333 | 741758A4 |  | Parent | FALSE | YPS -ROTS 5 220KV E | 40044.2958 | 40044.7118 | DAILY | 00022789 | DB_AUG | Cut in OPGW at Officer for new ZSS | SPIPOWER | 74176149 | New Zone Substation Officer (OFR) | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029098340044.2965277778 | 10290983 |  | Parent | FALSE | 1-3 66KV BUS TIE CB AT ERTS | 40044.2965 | 40044.5882 | DAILY | [12 empty] | 0
_1027293340044.3145833333 | 10272933 |  | Parent | FALSE | NO.8 GEN TRANS 220KV CB AT HWPS | 40044.3146 | 40044.6347 | DAILY | [12 empty] | 0
_1031734540044.3486111111 | 10317345 |  | Parent | FALSE | H2 330/220KV TRANS BANK AT SMTS | 40044.3486 | 40044.4306 | DAILY | 00026102 | FAULT | H2 Trans Trip | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030870540044.3631944444 | 10308705 |  | Parent | FALSE | RCTS 220KV LINE NO.2 BUS CB AT HOTS | 40044.3632 | 40044.4653 | REPDAILY | [12 empty] | 0
_Z73058K240044.4583333333 | Z73058K2 |  | Parent | FALSE | B3 220/66KV TRANS AT SMTS | 40044.4583 | 40060.566 | CONT | 00366622 | DB_AUG | Pre-commissioning tests on new B3 trans at SMTS | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1030870440044.4791666667 | 10308704 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT HOTS | 40044.4792 | 40044.6292 | REPDAILY | [12 empty] | 0
_X50858BU40045.25 | X50858BU |  | Parent | TRUE | KTS NO.3 220KV LINE NO.1 BUS CB AT GTS | 40045.25 | 40046.4062 | CONT | [12 empty] | 0
_X50858CF40045.25 | X50858CF | X50858BU | Child | FALSE | KTS NO.3 220KV LINE AT GTS | 40045.25 | 40046.4062 | CONT | 00367296 | SPICAPX | Rebate W/O during KTS No3 Line outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658L740045.3020833333 | X70658L7 |  | Parent | FALSE | EX - GTS NO.1 220KV LINE NO.1 BUS CB AT KTS | 40045.3021 | 40048.6215 | CONT | [12 empty] | 0
_1029099040045.3083333333 | 10290990 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT ERTS | 40045.3083 | 40045.5722 | DAILY | [12 empty] | 0
_1030870540045.3451388889 | 10308705 |  | Parent | FALSE | RCTS 220KV LINE NO.2 BUS CB AT HOTS | 40045.3451 | 40045.4222 | REPDAILY | [12 empty] | 0
_1030870440045.3965277778 | 10308704 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT HOTS | 40045.3965 | 40045.5229 | REPDAILY | [12 empty] | 0
_1031666040045.9638888889 | 10316660 |  | Parent | FALSE | EX - NO.1 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 40045.9639 | 40048.8722 | CONT | [12 empty] | 0
_1031665440046.2986111111 | 10316654 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK CB AT TTS | 40046.2986 | 40046.6854 | DAILY | [12 empty] | 0
_1029098540046.3034722222 | 10290985 |  | Parent | FALSE | 1-4 66KV BUS TIE CB AT ERTS | 40046.3035 | 40046.4493 | DAILY | [12 empty] | 0
_1031545940046.3583333333 | 10315459 |  | Parent | TRUE | TRANSFORMER VOLTAGE CONTROL AT SVTS | 40046.3583 | 40046.6292 | DAILY | [12 empty] | 0
_1031660340046.3583333333 | 10316603 | 10315459 | Child | FALSE | B4 220/66KV TRANS AT SVTS | 40046.3583 | 40046.6292 | DAILY | 00352791 | SPIMAINT | Transformer rebates Investigate OLTC operation | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031669040046.4513888889 | 10316690 |  | Parent | FALSE | MLTS NO.2 220KV LINE CB AT GTS | 40046.4514 | 40046.5021 | CONT | [12 empty] | 0
_1031669540046.5236111111 | 10316695 |  | Parent | FALSE | B1 220/66KV TRANS AT SMTS | 40046.5236 | 40046.6438 | CONT | 00366621 | SPIMAINT | B1 Trans Outage to repair connections | SPIPOWER |  |  | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1031647340046.8402777778 | 10316473 |  | Parent | FALSE | NO.4 GEN TRANS 500KV LINE E/SW AT LYPS | 40046.8403 | 40052.7403 | CONT | [12 empty] | 0
_X50858BZ40047.25 | X50858BZ |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 40047.25 | 40047.6674 | REPDAILY | 00002834 | SPICAPX | Replace Bus Insulators BayD E,F,G,H,J,K L No2 Bus | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858CA40047.25 | X50858CA | X50858BZ | Child | FALSE | MLTS NO.1 220KV LINE AT GTS | 40047.25 | 40047.6674 | DAILY | 00367287 | SPICAPX | Rebate W/O MLTS 1 Ln during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858CB40047.25 | X50858CB | X50858BZ | Child | FALSE | KTS NO.2 220KV LINE AT GTS | 40047.25 | 40047.6674 | DAILY | 00367295 | SPICAPX | Rebate W/O KTS 2 Ln during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858CC40047.25 | X50858CC | X50858BZ | Child | FALSE | B4 220/66KV TRANS AT GTS | 40047.25 | 40047.6674 | DAILY | 00002830 | SPICAPX | Perf calc B4 Trans during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858CD40047.25 | X50858CD | X50858BZ | Child | FALSE | PT. HENRY NO.2 220KV LINE AT GTS | 40047.25 | 40047.6674 | DAILY | 00367278 | SPICAPX | Rebate W/O PTH 2 Ln during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029142140047.2701388889 | 10291421 |  | Parent | FALSE | NO.1 220KV BUS AT FBTS | 40047.2701 | 40047.6132 | REPDAILY | 00002734 | SPIMAINT | O/Haul NO.1 220KV BUS AT FBTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_741758A640047.2902777778 | 741758A6 |  | Parent | FALSE | YPS -ROTS 5 220KV E | 40047.2903 | 40047.7118 | DAILY | 00022789 | DB_AUG | Cut in OPGW at Officer for new ZSS | SPIPOWER | 74176149 | New Zone Substation Officer (OFR) | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z63358L440048.2527777778 | Z63358L4 |  | Parent | TRUE | NO.1 220KV BUS AT JLTS | 40048.2528 | 40048.6931 | DAILY | 00365901 | VEN_AUG | CHANGE BYPODS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358L540048.2527777778 | Z63358L5 | Z63358L4 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 40048.2528 | 40048.6931 | DAILY | 00015936 | VEN_AUG | REBATE FOR BUS OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858BZ40048.2569444444 | X50858BZ |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 40048.2569 | 40048.5111 | REPDAILY | 00002834 | SPICAPX | Replace Bus Insulators BayD E,F,G,H,J,K L No2 Bus | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858CA40048.2569444444 | X50858CA | X50858BZ | Child | FALSE | MLTS NO.1 220KV LINE AT GTS | 40048.2569 | 40048.5111 | DAILY | 00367287 | SPICAPX | Rebate W/O MLTS 1 Ln during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858CB40048.2569444444 | X50858CB | X50858BZ | Child | FALSE | KTS NO.2 220KV LINE AT GTS | 40048.2569 | 40048.5111 | DAILY | 00367295 | SPICAPX | Rebate W/O KTS 2 Ln during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858CC40048.2569444444 | X50858CC | X50858BZ | Child | FALSE | B4 220/66KV TRANS AT GTS | 40048.2569 | 40048.5111 | DAILY | 00002830 | SPICAPX | Perf calc B4 Trans during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858CD40048.2569444444 | X50858CD | X50858BZ | Child | FALSE | PT. HENRY NO.2 220KV LINE AT GTS | 40048.2569 | 40048.5111 | DAILY | 00367278 | SPICAPX | Rebate W/O PTH 2 Ln during No2 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029142140048.2736111111 | 10291421 |  | Parent | FALSE | NO.1 220KV BUS AT FBTS | 40048.2736 | 40048.6618 | REPDAILY | 00002734 | SPIMAINT | O/Haul NO.1 220KV BUS AT FBTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V95258B040048.2902777778 | V95258B0 |  | Parent | FALSE | NO.1 66KV REACTOR AT HOTS | 40048.2903 | 40048.7139 | DAILY | 00352148 | SPIMAINT | Out W/O No1 66kV React CB test & adjust by ABB | SPIPOWER | V952 | V952 - ADJUST & COMMISSION 12 - 66KV LTB CBS | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658H740048.5861111111 | X70658H7 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40048.5861 | 40049.0743 | DAILY | 00001169 | SPICAPX | remve bipods from 1 bus to b1 tr cb b/s roi bay h | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658H840048.5861111111 | X70658H8 | X70658H7 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40048.5861 | 40049.0743 | DAILY | 00119824 | SPICAPX | REBATE CAP BANK for Bus outage | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031670340048.8729166667 | 10316703 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 40048.8729 | 40052.3493 | CONT | 00356086 | GENCO | Unit 8 Isolation and earth | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V95258B140049.2916666667 | V95258B1 |  | Parent | FALSE | NO.2 66KV REACTOR AT HOTS | 40049.2917 | 40049.6333 | DAILY | 00357255 | SPIMAINT | Out W/O No2 66kV React CB test & adjust by ABB | SPIPOWER | V952 | V952 - ADJUST & COMMISSION 12 - 66KV LTB CBS | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029035940049.3055555556 | 10290359 | 10290364 | Child | FALSE | A4 GEN TRANS 500KV CB AT LYPS | 40049.3056 | 40049.6604 | DAILY | [12 empty] | 0
_1029036440049.3055555556 | 10290364 |  | Parent | TRUE | NO.2 500KV BUS AT LYPS | 40049.3056 | 40049.6604 | DAILY | 00010024 | SPIMAINT | O/Haul NO.2 500KV BUS AT LYPS | SPIPOWER |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1030117340049.3055555556 | 10301173 | 10290364 | Child | FALSE | A4 GEN TRANS 500KV CB AT LYPS | 40049.3056 | 40049.6604 | DAILY | [12 empty] | 0
_1030117440049.3055555556 | 10301174 | 10290364 | Child | FALSE | A2 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 40049.3056 | 40049.6604 | DAILY | [12 empty] | 0
_1030117740049.3055555556 | 10301177 | 10290364 | Child | FALSE | 2-4 500KV BUS TIE CB AT LYPS | 40049.3056 | 40049.6604 | DAILY | [12 empty] | 0
_1031545940049.3465277778 | 10315459 |  | Parent | TRUE | TRANSFORMER VOLTAGE CONTROL AT SVTS | 40049.3465 | 40049.6222 | DAILY | [12 empty] | 0
_1031660340049.3465277778 | 10316603 | 10315459 | Child | FALSE | B4 220/66KV TRANS AT SVTS | 40049.3465 | 40049.6222 | DAILY | 00352791 | SPIMAINT | Transformer rebates Investigate OLTC operation | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031659040049.3611111111 | 10316590 |  | Parent | TRUE | NO.3 220KV CAPACITOR BANK CB AT ROTS | 40049.3611 | 40049.4097 | DAILY | [12 empty] | 0
_1031708340049.3611111111 | 10317083 | 10316590 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 40049.3611 | 40049.4097 | DAILY | 00112417 | SPIMAINT | REBATES FOR CAPBANK | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031626040049.375 | 10316260 |  | Parent | FALSE | FUTURE F1 TRANS 500KV CB AT SMTS | 40049.375 | 40052.6181 | CONT | [12 empty] | 0
_V7A058A640049.375 | V7A058A6 |  | Parent | FALSE | KTS 500KV LINE NO.1 BUS CB AT SMTS | 40049.375 | 40052.6451 | CONT | [12 empty] | 0
_1028971140050.2958333333 | 10289711 |  | Parent | FALSE | NO.4 TRANS 22KV CB AT BETS | 40050.2958 | 40050.5667 | DAILY | [12 empty] | 0
_1031677840050.3159722222 | 10316778 |  | Parent | FALSE | 2-4 500KV BUS TIE CB AT LYPS | 40050.316 | 40050.4556 | CONT | [12 empty] | 0
_1030394340050.3868055556 | 10303943 |  | Parent | FALSE | A4 GEN TRANS 500KV CB AT LYPS | 40050.3868 | 40050.6924 | DAILY | [12 empty] | 0
_1031678040050.5534722222 | 10316780 |  | Parent | TRUE | NO.1 22KV CAPACITOR BANK CB AT BTS | 40050.5535 | 40051.6042 | DAILY | [12 empty] | 0
_1031678140050.5534722222 | 10316781 | 10316780 | Child | FALSE | NO.1 22KV CAPACITOR BANK AT BTS | 40050.5535 | 40051.6042 | DAILY | 00337002 | SPIMAINT | Rebate Cap Bank | SPIPOWER |  |  | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030972740050.5701388889 | 10309727 |  | Parent | FALSE | BATS NO.1 LINE/TGTS LINE 220KV CB AT MLTS | 40050.5701 | 40050.6514 | DAILY | [12 empty] | 0
_V95258A640051.2888888889 | V95258A6 |  | Parent | TRUE | NO.2B 66KV CAPACITOR BANK AT BETS | 40051.2889 | 40051.7326 | DAILY | 00016274 | SPIMAINT | Out W/O No 2B 66kV Cap CB test & adjust by ABB | SPIPOWER | V952 | V952 - ADJUST & COMMISSION 12 - 66KV LTB CBS | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V95258B340051.2888888889 | V95258B3 | V95258A6 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT BETS | 40051.2889 | 40051.7326 | DAILY | 00350819 | SPIMAINT | Rebate W/O 2A Cap during outage for 2B CB adjust | SPIPOWER | V952 | V952 - ADJUST & COMMISSION 12 - 66KV LTB CBS | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1031614340051.3736111111 | 10316143 |  | Parent | FALSE | SVTS NO.2 220KV LINE/NO.1 CSC CB AT ROTS | 40051.3736 | 40051.6271 | DAILY | [12 empty] | 0
_1030870340051.4145833333 | 10308703 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT MBTS | 40051.4146 | 40051.4854 | DAILY | [12 empty] | 0
_V95258A740052.2923611111 | V95258A7 |  | Parent | TRUE | NO.3B 66KV CAPACITOR BANK AT BETS | 40052.2924 | 40052.666 | DAILY | 00016304 | SPIMAINT | Out W/O No 3B 66kV Cap CB test & adjust by ABB | SPIPOWER | V952 | V952 - ADJUST & COMMISSION 12 - 66KV LTB CBS | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V95258B440052.2923611111 | V95258B4 | V95258A7 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT BETS | 40052.2924 | 40052.666 | DAILY | 00350820 | SPIMAINT | Rebate W/O 3A Cap during outage for 3B CB adjust | SPIPOWER | V952 | V952 - ADJUST & COMMISSION 12 - 66KV LTB CBS | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1031692940052.8722222222 | 10316929 |  | Parent | FALSE | A4 GEN TRANS 500KV CB AT LYPS | 40052.8722 | 40053.462 | CONT | [12 empty] | 0
_X7E458F440053.2944444444 | X7E458F4 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40053.2944 | 40053.7361 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458F540053.2944444444 | X7E458F5 | X7E458F4 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40053.2944 | 40053.7361 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458F640053.2944444444 | X7E458F6 | X7E458F4 | Child | FALSE | HYTS-APD 1 500KV W | 40053.2944 | 40053.7361 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458F840053.2944444444 | X7E458F8 | X7E458F4 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40053.2944 | 40053.7361 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029098140053.2951388889 | 10290981 |  | Parent | FALSE | O.O.S A 66KV FDR CB AT ERTS | 40053.2951 | 40053.616 | DAILY | [12 empty] | 0
_1030969440053.3479166667 | 10309694 |  | Parent | FALSE | SVTS NO.2 220KV LINE/NO.1 CSC CB AT ROTS | 40053.3479 | 40053.6431 | DAILY | [12 empty] | 0
_1031695140053.4270833333 | 10316951 |  | Parent | TRUE | NO.3 22KV CAPACITOR BANK CB AT BTS | 40053.4271 | 40053.5125 | DAILY | [12 empty] | 0
_1031695240053.4270833333 | 10316952 | 10316951 | Child | FALSE | NO.1 22KV CAPACITOR BANK AT BTS | 40053.4271 | 40053.5125 | DAILY | 00337002 | SPIMAINT | Rebate Cap Bank | SPIPOWER |  |  | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031692840053.43125 | 10316928 |  | Parent | FALSE | A4 GEN TRANS 500KV CB AT LYPS | 40053.4313 | 40053.4688 | DAILY | [12 empty] | 0
_1031695540053.4347222222 | 10316955 |  | Parent | FALSE | KTS 500KV LINE NO.1 BUS CB AT SMTS | 40053.4347 | 40053.4938 | DAILY | [12 empty] | 0
_1031692640054.0201388889 | 10316926 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 40054.0201 | 40144.6465 | CONT | 00356080 | GENCO | Gen-Co Major Outage Unit 2 | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658L340054.26875 | X70658L3 |  | Parent | FALSE | NO.2 66KV BUS AT KTS | 40054.2688 | 40054.6903 | DAILY | 00001173 | SPICAPX | install connections-66kv bus to fut bus vt isol | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X87058G840054.2916666667 | X87058G8 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40054.2917 | 40054.5319 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS No2 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E558B240054.2916666667 | X7E558B2 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40054.2917 | 40054.541 | REPDAILY | 00022640 | SPICAPX | install opgw between tower 26 & 39 | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V8F158A340054.2951388889 | V8F158A3 |  | Parent | FALSE | L4 220/22KV TRANS AT RTS | 40054.2951 | 40054.6431 | REPDAILY | 00007333 | SPIMAINT | Check Oil Leaks | SPIPOWER | V8F1 | V8F1 - REPAIR OF OIL LEAKS IN TERMINAL STNS - STAGE 1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V95258A340054.2951388889 | V95258A3 |  | Parent | FALSE | NO.1 66KV REACTOR AT RCTS | 40054.2951 | 40054.6778 | DAILY | 00016895 | SPIMAINT | Out W/O No1 66kV React CB test & adjust by ABB | SPIPOWER | V952 | V952 - ADJUST & COMMISSION 12 - 66KV LTB CBS | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X71158A440054.3513888889 | X71158A4 |  | Parent | FALSE | EX - ROTS NO.2 220KV LINE AT HWPS | 40054.3514 | 40054.7917 | CONT | 00015793 | SPICAPX | ROTS 2L OUTAGE | SPIPOWER | X711 | X711 - (HWPS) REDEVELOP 220KV SWYD - STAGE 1 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X71158A740054.6215277778 | X71158A7 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 40054.6215 | 40121.5153 | CONT | [12 empty] | 0
_X70658L440055.2569444444 | X70658L4 |  | Parent | FALSE | NO.4 66KV BUS AT KTS | 40055.2569 | 40055.616 | DAILY | 00001174 | SPICAPX | install connections-66kv bus to fut bus vt isol | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E558B240055.2923611111 | X7E558B2 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40055.2924 | 40055.7111 | REPDAILY | 00022640 | SPICAPX | install opgw between tower 26 & 39 | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V8F158A340055.2930555556 | V8F158A3 |  | Parent | FALSE | L4 220/22KV TRANS AT RTS | 40055.2931 | 40055.6715 | REPDAILY | 00007333 | SPIMAINT | Check Oil Leaks | SPIPOWER | V8F1 | V8F1 - REPAIR OF OIL LEAKS IN TERMINAL STNS - STAGE 1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V95258A440055.2972222222 | V95258A4 |  | Parent | FALSE | NO.2 66KV REACTOR AT RCTS | 40055.2972 | 40055.6139 | DAILY | 00016897 | SPIMAINT | Out W/O No2 66kV React CB test & adjust by ABB | SPIPOWER | V952 | V952 - ADJUST & COMMISSION 12 - 66KV LTB CBS | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X87058G840055.3027777778 | X87058G8 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40055.3028 | 40055.6743 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS No2 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029349840055.3395833333 | 10293498 |  | Parent | FALSE | B1 TRANS Y PROT AT CBTS | 40055.3396 | 40055.4833 | DAILY | [12 empty] | 0
_V95258A540056.2916666667 | V95258A5 |  | Parent | FALSE | NO.3 66KV REACTOR AT RCTS | 40056.2917 | 40056.6646 | DAILY | 00357254 | SPIMAINT | Out W/O No3 66kV React CB test & adjust by ABB | SPIPOWER | V952 | V952 - ADJUST & COMMISSION 12 - 66KV LTB CBS | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458G440056.3027777778 | X7E458G4 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40056.3028 | 40056.7382 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458G540056.3027777778 | X7E458G5 | X7E458G4 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40056.3028 | 40056.7382 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458G640056.3027777778 | X7E458G6 | X7E458G4 | Child | FALSE | HYTS-APD 1 500KV W | 40056.3028 | 40056.7382 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458G840056.3027777778 | X7E458G8 | X7E458G4 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40056.3028 | 40056.7382 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X74158G240056.3090277778 | X74158G2 |  | Parent | FALSE | DDTS NO.1 330KV LINE NO.1 BUS CB AT SMTS | 40056.309 | 40058.316 | CONT | [12 empty] | 0
_X7E558C140056.3104166667 | X7E558C1 |  | Parent | FALSE | ROTS 220KV LINE AT TTS | 40056.3104 | 40056.8181 | DAILY | 00015733 | SPICAPX | install opwg between towers 16 and tower 17 | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1028872340057.2694444444 | 10288723 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 40057.2694 | 40060.7729 | CONT | 00026099 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029098740057.2923611111 | 10290987 | 10291001 | Child | FALSE | NO.1 66KV CAPACITOR BANK CB AT ERTS | 40057.2924 | 40057.6 | DAILY | [12 empty] | 0
_1029100140057.2923611111 | 10291001 |  | Parent | TRUE | NO.1A 66KV CAPACITOR BANK AT ERTS | 40057.2924 | 40057.6 | DAILY | 00004345 | SPIMAINT | O/Haul NO.1A 66KV CAPACITOR BANK AT ERTS | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031745140057.2923611111 | 10317451 | 10291001 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT ERTS | 40057.2924 | 40057.6 | DAILY | 00337043 | SPIMAINT | Rebate for cap Bank outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V79658A340057.2944444444 | V79658A3 |  | Parent | FALSE | BTS 220KV LINE AT RTS | 40057.2944 | 40057.5868 | CONT | 00021222 | SPIMAINT | V796 - (BTS-RTS) CABLE JOINT REPLACEMENTS | SPIPOWER | V796 | V796 - (BTS-RTS) CABLE JOINT REPLACEMENTS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029134140057.2958333333 | 10291341 |  | Parent | FALSE | NO.1 500KV BUS AT HYTS | 40057.2958 | 40057.8056 | DAILY | 00002866 | SPIMAINT | O/Haul NO.1 500KV BUS AT HYTS | SPIPOWER |  |  | Bus | Alstom | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1031721840057.2958333333 | 10317218 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 40057.2958 | 40057.8056 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during No1 500kv Bus Outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_V96558A040057.3173611111 | V96558A0 |  | Parent | FALSE | JLTS NO.4 220KV LINE NO.4 BUS CB AT HWPS | 40057.3174 | 40066.6174 | CONT | [12 empty] | 0
_V95258B240057.3215277778 | V95258B2 |  | Parent | FALSE | 66KV SHUNT REACTOR AT KGTS | 40057.3215 | 40057.6438 | DAILY | 00354076 | SPIMAINT | Out W/O 66kV Shunt React CB test & adjust by ABB | SPIPOWER | V952 | V952 - ADJUST & COMMISSION 12 - 66KV LTB CBS | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029319440057.3298611111 | 10293194 |  | Parent | FALSE | MLRC 220KV LINE AT RCTS | 40057.3299 | 40057.7667 | DAILY | 00352130 | SPIMAINT | O/H MLRC LINE, CVT'S & SD'S AT RCTS | SPIPOWER |  |  | Circuits | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 4
_1030870240057.3625 | 10308702 |  | Parent | FALSE | GNTS NO.1 220KV LINE NO.2 BUS CB AT SHTS | 40057.3625 | 40057.4611 | DAILY | [12 empty] | 0
_1030869940057.5479166667 | 10308699 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT SHTS | 40057.5479 | 40057.6083 | DAILY | [12 empty] | 0
_1031706540057.5875 | 10317065 |  | Parent | FALSE | BTS 220KV LINE AT RTS | 40057.5875 | 40121.6396 | CONT | 00021222 | SPIMAINT | V796 - (BTS-RTS) CABLE JOINT REPLACEMENTS | SPIPOWER | V796 | V796 - (BTS-RTS) CABLE JOINT REPLACEMENTS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V95258A940058.2902777778 | V95258A9 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT BATS | 40058.2903 | 40058.6215 | DAILY | 00331109 | SPIMAINT | Out W/O No1 66kV Cap CB test & adjust by ABB | SPIPOWER | V952 | V952 - ADJUST & COMMISSION 12 - 66KV LTB CBS | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029099240058.3013888889 | 10290992 | 10290999 | Child | FALSE | NO.4 66KV CAPACITOR BANK CB AT ERTS | 40058.3014 | 40058.5861 | DAILY | [12 empty] | 0
_1029099940058.3013888889 | 10290999 |  | Parent | TRUE | NO.4 66KV CAPACITOR BANK AT ERTS | 40058.3014 | 40058.5861 | DAILY | 00004344 | SPIMAINT | O/Haul NO.4 66KV CAPACITOR BANK AT ERTS | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029318040058.3020833333 | 10293180 |  | Parent | FALSE | MLRC 220KV LINE NO.1 BUS CB AT RCTS | 40058.3021 | 40058.6951 | DAILY | [12 empty] | 4
_1029133740058.3131944445 | 10291337 |  | Parent | TRUE | MLTS NO.1 500KV LINE CB AT HYTS | 40058.3132 | 40058.8021 | REPDAILY | [12 empty] | 0
_1029434140058.3131944445 | 10294341 | 10291337 | Child | FALSE | EX - MLTS NO.1 500KV LINE CB CT R/PH AT HYTS | 40058.3132 | 40058.8021 | REPDAILY | [12 empty] | 0
_1031722040058.3131944445 | 10317220 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 40058.3132 | 40058.8021 | REPDAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during CB Outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031722440058.3131944445 | 10317224 |  | Parent | FALSE | EX - MLTS NO.1 500KV LINE CB CT R/PH AT HYTS | 40058.3132 | 40058.8021 | REPDAILY | [12 empty] | 0
_X74158G340058.3159722222 | X74158G3 |  | Parent | FALSE | DDTS NO.1 330KV LINE NO.2 BUS CB AT SMTS | 40058.316 | 40058.8868 | DAILY | 00329821 | SPICAPX | replace 330kv ct's & conductors between ct & isol | SPIPOWER | X741 | [7 empty] | 0 | X74158G3 |  | replace 330kv ct's & conductors between ct & isol | 00329821 | CB | X741 | SMTS | CB | SPICAPX | DAILY
_X74158G440058.8875 | X74158G4 |  | Parent | FALSE | DDTS NO.1 330KV LINE NO.2 BUS CB AT SMTS | 40058.8875 | 40060.6292 | CONT | [12 empty] | 0
_1029084540059.2722222222 | 10290845 |  | Parent | FALSE | NO.2 CSC AT ROTS | 40059.2722 | 40060.6049 | CONT | 00004716 | SPIMAINT | Yearly O/Haul - No.2 CSC at ROTS | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031732640059.2951388889 | 10317326 | V95258A0 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT TSTS | 40059.2951 | 40059.6243 | DAILY | 00351937 | SPIMAINT | Test and adjust CB - Cap Bank rebate capture WO | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_V95258A040059.2951388889 | V95258A0 |  | Parent | TRUE | EX - NO.1 66KV CAPACITOR BANK CB AT TSTS | 40059.2951 | 40059.6243 | DAILY | [12 empty] | 0
_1029318240059.3180555556 | 10293182 |  | Parent | FALSE | MLRC 220KV LINE NO.2 BUS CB AT RCTS | 40059.3181 | 40059.6792 | DAILY | [12 empty] | 4
_1031574240059.3180555556 | 10315742 |  | Parent | FALSE | MLRC 220KV LINE NO.2 BUS CB AT RCTS | 40059.3181 | 40059.6792 | DAILY | [12 empty] | 4
_1029133740059.3208333333 | 10291337 |  | Parent | TRUE | MLTS NO.1 500KV LINE CB AT HYTS | 40059.3208 | 40059.7021 | REPDAILY | [12 empty] | 0
_1029434140059.3208333333 | 10294341 | 10291337 | Child | FALSE | EX - MLTS NO.1 500KV LINE CB CT R/PH AT HYTS | 40059.3208 | 40059.7021 | REPDAILY | [12 empty] | 0
_1031722040059.3208333333 | 10317220 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 40059.3208 | 40059.7021 | REPDAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during CB Outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031722440059.3208333333 | 10317224 |  | Parent | FALSE | EX - MLTS NO.1 500KV LINE CB CT R/PH AT HYTS | 40059.3208 | 40059.7021 | REPDAILY | [12 empty] | 0
_1028092440059.3222222222 | 10280924 |  | Parent | FALSE | U2 66/22KV TRANS Y PROT AT MTS | 40059.3222 | 40059.6646 | DAILY | [12 empty] | 0
_1030879040059.4104166667 | 10308790 |  | Parent | FALSE | BATS NO.1 LINE/TGTS LINE 220KV CB AT MLTS | 40059.4104 | 40059.459 | DAILY | [12 empty] | 0
_1031732740060.2909722222 | 10317327 | V95258A1 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT TBTS | 40060.291 | 40060.5764 | DAILY | 00351938 | SPIMAINT | Test and adjust CB - Cap Bank rebate capture WO | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_V95258A140060.2909722222 | V95258A1 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK CB AT TBTS | 40060.291 | 40060.5764 | DAILY | [12 empty] | 0
_1029133740060.3138888889 | 10291337 |  | Parent | TRUE | MLTS NO.1 500KV LINE CB AT HYTS | 40060.3139 | 40060.5125 | REPDAILY | [12 empty] | 0
_1029434140060.3138888889 | 10294341 | 10291337 | Child | FALSE | EX - MLTS NO.1 500KV LINE CB CT R/PH AT HYTS | 40060.3139 | 40060.5125 | REPDAILY | [12 empty] | 0
_1031722040060.3138888889 | 10317220 |  | Parent | FALSE | M1 500/275KV TRANS AT HYTS | 40060.3139 | 40060.5125 | REPDAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during CB Outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031722440060.3138888889 | 10317224 |  | Parent | FALSE | EX - MLTS NO.1 500KV LINE CB CT R/PH AT HYTS | 40060.3139 | 40060.5125 | REPDAILY | [12 empty] | 0
_1031639240060.3145833333 | 10316392 |  | Parent | FALSE | U1 66/22KV TRANS AT MTS | 40060.3146 | 40060.5819 | DAILY | 00363343 | SPIMAINT | ROUTINE MAINTENANCE | SPIPOWER |  |  | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028710440060.3180555556 | 10287104 |  | Parent | FALSE | NO.1 22KV CAPACITOR BANK AT RCTS | 40060.3181 | 40060.4958 | DAILY | 00016710 | SPIMAINT | O/Haul NO.1 22KV CAPACITOR BANK AT RCTS | SPIPOWER |  |  | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z82558A540061.2888888889 | Z82558A5 |  | Parent | FALSE | ROTS-SVTS 1 220KV E | 40061.2889 | 40061.7056 | DAILY | 00022752 | VEN_AUG | Replace Cross Arms | SPIPOWER | Z825 | Z825 - (ROTS-SVTS) 220KV UPGRADE TO 82 DEGREE C | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058G940061.2902777778 | X87058G9 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40061.2903 | 40061.5965 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS No2 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V95258A840061.2965277778 | V95258A8 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 40061.2965 | 40061.534 | DAILY | 00329879 | SPIMAINT | Out W/O No 4 66kV Cap CB test & adjust by ABB | SPIPOWER | V952 | V952 - ADJUST & COMMISSION 12 - 66KV LTB CBS | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031584440061.2965277778 | 10315844 |  | Parent | TRUE | B4 220/66KV TRANS AT ERTS | 40061.2965 | 40061.6125 | DAILY | 00004372 | SPIMAINT | Repaire hot joint to trans & ROTS No 2 Line SW | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031743340061.2965277778 | 10317433 | 10315844 | Child | FALSE | CBTS NO.1 220KV LINE AT ERTS | 40061.2965 | 40061.6125 | DAILY | 00012286 | SPIMAINT | REBATE FOR LINE OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031770740061.2965277778 | 10317707 | 10315844 | Child | FALSE | ROTS NO.2 220KV LINE AT ERTS | 40061.2965 | 40061.6125 | DAILY | 00012288 | SPIMAINT | REBATE FOR LINE OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z82558A240062.2888888889 | Z82558A2 |  | Parent | FALSE | ROTS NO.2 220KV LINE AT SVTS | 40062.2889 | 40062.7014 | DAILY | 00351701 | VEN_AUG | Replace Cross arms | SPIPOWER | Z825 | Z825 - (ROTS-SVTS) 220KV UPGRADE TO 82 DEGREE C | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058G940062.2916666667 | X87058G9 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40062.2917 | 40062.641 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS No2 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031562340062.2972222222 | 10315623 |  | Parent | FALSE | B1 220/66KV TRANS AT ERTS | 40062.2972 | 40062.5826 | DAILY | 00004370 | SPIMAINT | Re-tighten transformer connections | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031730040062.8298611111 | 10317300 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 40062.8299 | 40066.3729 | CONT | 00356081 | GENCO | Gen-Co Work | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026810640063.2715277778 | 10268106 |  | Parent | FALSE | SMTS NO.1 500KV LINE AT SYTS | 40063.2715 | 40063.7229 | REPDAILY | 00016971 | SPIMAINT | SYTS-SMTS No.1 Line - VT , Surge Diverters | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V92658A040063.29375 | V92658A0 |  | Parent | FALSE | SYN/COND AT TSTS | 40063.2937 | 40064.8389 | CONT | 00007626 | SPIMAINT | PREPARE AND TEST OF SPARE PRIMARY EQUIPMENT | SPIPOWER | V926 | V926 - PREPARE & TEST SPARE PRIMARY EQPT 2009 | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029412840063.2965277778 | 10294128 |  | Parent | FALSE | B1 220/66KV TRANS AT TBTS | 40063.2965 | 40064.6937 | CONT | 00004901 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458G940063.3013888889 | X7E458G9 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40063.3014 | 40063.5431 | DAILY | 00022630 | SPICAPX | MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458H040063.3013888889 | X7E458H0 | X7E458G9 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40063.3014 | 40063.5431 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458H140063.3013888889 | X7E458H1 | X7E458G9 | Child | FALSE | HYTS-APD 1 500KV W | 40063.3014 | 40063.5431 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458H340063.3013888889 | X7E458H3 | X7E458G9 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40063.3014 | 40063.5431 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X74158G740063.3736111111 | X74158G7 |  | Parent | FALSE | DDTS NO.2 330KV LINE NO.1 BUS CB AT SMTS | 40063.3736 | 40065.2514 | CONT | [12 empty] | 0
_1028967340063.5236111111 | 10289673 |  | Parent | FALSE | NO.2 22KV CAPACITOR BANK AT RCTS | 40063.5236 | 40063.6562 | DAILY | 00016713 | SPIMAINT | O/Haul NO.2 22KV CAPACITOR BANK AT RCTS | SPIPOWER |  |  | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031733640064.0333333333 | 10317336 |  | Parent | FALSE | NO.1 CSC AT ROTS | 40064.0333 | 40064.1271 | DAILY | 00004718 | FAULT | No1 CSC tripped | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031734140064.2152777778 | 10317341 |  | Parent | FALSE | NO.1 CSC AT ROTS | 40064.2153 | 40064.8236 | DAILY | 00004718 | FAULT | No1 CSC tripped due to burnt CT terminal. | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1026810640064.2743055556 | 10268106 |  | Parent | FALSE | SMTS NO.1 500KV LINE AT SYTS | 40064.2743 | 40064.7618 | REPDAILY | 00016971 | SPIMAINT | SYTS-SMTS No.1 Line - VT , Surge Diverters | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029574840064.3138888889 | 10295748 |  | Parent | TRUE | MLTS NO.2 500KV LINE CB AT HYTS | 40064.3139 | 40064.675 | REPDAILY | [12 empty] | 0
_1031744640064.3138888889 | 10317446 | 10295748 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40064.3139 | 40064.675 | REPDAILY | 00002862 | SPIMAINT | Trans Rebate | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029401440064.3243055556 | 10294014 | 10294022 | Child | FALSE | NO.1 220KV CAPACITOR BANK E/SW AT RCTS | 40064.3243 | 40064.6625 | DAILY | [12 empty] | 0
_1029401840064.3243055556 | 10294018 | 10294022 | Child | FALSE | NO.1 220KV CAPACITOR BANK CB AT RCTS | 40064.3243 | 40064.6625 | DAILY | [12 empty] | 0
_1029402240064.3243055556 | 10294022 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK AT RCTS | 40064.3243 | 40064.6625 | DAILY | 00360382 | SPIMAINT | O/Haul 220KV CAPACITOR BANK | SPIPOWER |  |  | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031731740064.3902777778 | 10317317 |  | Parent | FALSE | F2 TRANS 500KV LINE ENTRY BUSHING R/PH AT SMTS | 40064.3903 | 40064.7123 | DAILY | [12 empty] | 0
_1031741640064.5722222222 | 10317416 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 40064.5722 | 40064.7646 | DAILY | 00002829 | FORCED | B3 Trans CT Cable repairs | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X74158G540065.2506944445 | X74158G5 |  | Parent | FALSE | DDTS NO.2 330KV LINE AT SMTS | 40065.2507 | 40065.8382 | DAILY | 00012750 | SPICAPX | replace 330kv ct's & conductors between ct & isol | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031627840065.2583333333 | 10316278 |  | Parent | FALSE | A2 500/220KV TRANS BANK AT KTS | 40065.2583 | 40066.6799 | CONT | 00026096 | SPIMAINT | faulty 415v c/o contactor&replace oil in unit tr | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029553140065.2916666667 | 10295531 |  | Parent | FALSE | B2 220/66KV TRANS AT TBTS | 40065.2917 | 40066.6556 | CONT | 00004902 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029574840065.3125 | 10295748 |  | Parent | TRUE | MLTS NO.2 500KV LINE CB AT HYTS | 40065.3125 | 40065.675 | REPDAILY | [12 empty] | 0
_1031744640065.3125 | 10317446 | 10295748 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40065.3125 | 40065.675 | REPDAILY | 00002862 | SPIMAINT | Trans Rebate | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029401640065.3152777778 | 10294016 | 10294026 | Child | FALSE | NO.2 220KV CAPACITOR BANK E/SW AT RCTS | 40065.3153 | 40065.625 | DAILY | [12 empty] | 0
_1029402040065.3152777778 | 10294020 | 10294026 | Child | FALSE | NO.2 220KV CAPACITOR BANK CB AT RCTS | 40065.3153 | 40065.625 | DAILY | [12 empty] | 0
_1029402640065.3152777778 | 10294026 |  | Parent | TRUE | NO.2 220KV CAPACITOR BANK AT RCTS | 40065.3153 | 40065.625 | DAILY | 00360383 | SPIMAINT | O/Haul 220KV CAPACITOR BANK | SPIPOWER |  |  | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031574240065.4388888889 | 10315742 |  | Parent | FALSE | MLRC 220KV LINE NO.2 BUS CB AT RCTS | 40065.4389 | 40065.5736 | DAILY | [12 empty] | 4
_X74158G640065.9215277778 | X74158G6 |  | Parent | FALSE | DDTS NO.2 330KV LINE NO.2 BUS CB AT SMTS | 40065.9215 | 40067.534 | CONT | [12 empty] | 0
_X7E558B340066.2951388889 | X7E558B3 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40066.2951 | 40066.7049 | DAILY | 00022640 | SPICAPX | install opgw between tower 13 & 26 | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029527240066.3076388889 | 10295272 |  | Parent | FALSE | 1-2 22KV BUS TIE CB AT RCTS | 40066.3076 | 40066.7028 | DAILY | [12 empty] | 0
_1029574840066.3145833333 | 10295748 |  | Parent | TRUE | MLTS NO.2 500KV LINE CB AT HYTS | 40066.3146 | 40066.6229 | REPDAILY | [12 empty] | 0
_1031744640066.3145833333 | 10317446 | 10295748 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40066.3146 | 40066.6229 | REPDAILY | 00002862 | SPIMAINT | Trans Rebate | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z73058K140067.2756944444 | Z73058K1 |  | Parent | FALSE | NO.2 220KV BUS AT SMTS | 40067.2757 | 40083.5125 | CONT | 00366542 | DB_AUG | cut & earth temp bus to existing b3 trans | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z73058L340067.2756944444 | Z73058L3 |  | Parent | FALSE | B3 220/66KV TRANS AT SMTS | 40067.2757 | 40084.5181 | CONT | 00366622 | DB_AUG | 220KV & 66KV CONNS TO FUT B3 TRANS | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_V8B658A340067.2819444445 | V8B658A3 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB BUS SIDE ROI AT ROTS | 40067.2819 | 40067.6646 | DAILY | [12 empty] | 0
_V8B658A640067.2819444445 | V8B658A6 | V8B658A3 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 40067.2819 | 40067.6646 | DAILY | 00354024 | SPICAPX | Repair ROI - Cap Bank Rebate Capture WO | SPIPOWER | V8B6 | V8B6 - REPAIRS TO ABB-HAPAM 220KV DISCONNECTORS | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1026810140067.2944444444 | 10268101 |  | Parent | FALSE | SMTS NO.2 500KV LINE AT SYTS | 40067.2944 | 40067.8153 | DAILY | 00016970 | SPIMAINT | SYTS-SMTS No.2 Line - VT , Surge Diverters | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031713240068.2638888889 | 10317132 | X70658N0 | Child | FALSE | GTS NO.1 220KV LINE AT KTS | 40068.2639 | 40069.7757 | CONT | 00368493 | SPICAPX | w/o for rebates on gts line | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031770040068.2638888889 | 10317700 | X70658N0 | Child | FALSE | B1 220/66KV TRANS AT KTS | 40068.2639 | 40069.7757 | CONT | 00001147 | SPICAPX | w/o for rebates Trans | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031770340068.2638888889 | 10317703 | X70658N0 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40068.2639 | 40069.7757 | CONT | 00119824 | SPICAPX | w/o for rebates Cap Bank | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X70658N040068.2638888889 | X70658N0 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40068.2639 | 40069.7757 | CONT | 00001169 | SPICAPX | Bipod connections - No.1 bus to GTS 1 line X706 - | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z82558A640068.2875 | Z82558A6 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT SVTS | 40068.2875 | 40068.3701 | DAILY | 00351700 | VEN_AUG | Replace Cross Arms | SPIPOWER | Z825 | Z825 - (ROTS-SVTS) 220KV UPGRADE TO 82 DEGREE C | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058H040068.2944444444 | X87058H0 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 40068.2944 | 40068.6708 | REPDAILY | 00060187 | SPICAPX | MBTS-DDTS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z82558A440069.2916666667 | Z82558A4 |  | Parent | FALSE | ROTS NO.2 220KV LINE AT SVTS | 40069.2917 | 40069.7653 | DAILY | 00351701 | VEN_AUG | Replace Cross arms | SPIPOWER | Z825 | Z825 - (ROTS-SVTS) 220KV UPGRADE TO 82 DEGREE C | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058H040069.2944444444 | X87058H0 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 40069.2944 | 40069.7243 | REPDAILY | 00060187 | SPICAPX | MBTS-DDTS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031749040069.800474537 | 10317490 |  | Parent | FALSE | EX - GTS NO.1 220KV LINE NO.3 BUS CB AT KTS | 40069.8005 | 40070.709 | CONT | [12 empty] | 0
_X70658N140070.25 | X70658N1 |  | Parent | FALSE | NO.3 220KV BUS AT KTS | 40070.25 | 40070.709 | DAILY | 00001171 | SPICAPX | bipod connections - no.3 bus to gts 1 line | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E558C240070.2986111111 | X7E558C2 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40070.2986 | 40070.766 | DAILY | 00022640 | SPICAPX | install opgw between tower 50 & 60 | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031756140070.9201388889 | 10317561 |  | Parent | FALSE | NO.8 GEN 220/16.5KV TRANS AT HWPS | 40070.9201 | 40072.9901 | CONT | 00009649 | GENCO | HVS: No 8 Gen Isol'd for PS | GENCO |  |  | Connection Transformers | 3rd Party | 220 | NON SP ASSET | EXCLUDED |  | 0
_1027303340071.2506944445 | 10273033 |  | Parent | FALSE | A3 500/220KV TRANS BANK AT KTS | 40071.2507 | 40074.6743 | CONT | 00026097 | SPIMAINT | Condition Monitoring Metro Trans 3day West Area | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029142340071.2618055556 | 10291423 |  | Parent | FALSE | NO.3 220KV BUS AT FBTS | 40071.2618 | 40071.6507 | REPDAILY | 00002735 | SPIMAINT | O/Haul NO.3 220KV BUS AT FBTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V7A058A740071.2826388889 | V7A058A7 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT SMTS | 40071.2826 | 40075.491 | CONT | [12 empty] | 0
_X7E458B940071.2861111111 | X7E458B9 | X7E458H9 | Child | FALSE | BATS-TGTS 220KV WW | 40071.2861 | 40071.7667 | DAILY | 00022665 | SPICAPX | Rebate W/O BATS-TGTS Line UXing prox | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458H940071.2861111111 | X7E458H9 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40071.2861 | 40071.7667 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458J040071.2861111111 | X7E458J0 | X7E458H9 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40071.2861 | 40071.7667 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458J140071.2861111111 | X7E458J1 | X7E458H9 | Child | FALSE | HYTS-APD 1 500KV W | 40071.2861 | 40071.7667 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458J340071.2861111111 | X7E458J3 | X7E458H9 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40071.2861 | 40071.7667 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E558C340071.2993055556 | X7E558C3 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40071.2993 | 40071.6903 | DAILY | 00022640 | SPICAPX | install opgw between tower 60 & 69 | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031748740071.33125 | 10317487 |  | Parent | FALSE | JLGB NO.1 UNIT TRANS DISC CB AT JLGB | 40071.3313 | 40074.6583 | CONT | [12 empty] | 0
_1031757940071.5583333333 | 10317579 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK X & X BACKUP PROT AT GTS | 40071.5583 | 40071.5681 | DAILY | [12 empty] | 0
_1031758040071.5583333333 | 10317580 | 10317579 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT GTS | 40071.5583 | 40071.5681 | DAILY | 00350421 | SPIMAINT | Rebate W/O No1 66kV Cap Bank during thermo repair | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031699940071.9173611111 | 10316999 |  | Parent | FALSE | NO.2 GEN TRANS 500KV LINE E/SW AT LYPS | 40071.9174 | 40086.3528 | CONT | [12 empty] | 0
_X74158A840072.0493055556 | X74158A8 |  | Parent | FALSE | EX - W1 GEN TRANS NO.1 BUS 220KV CB CT R/PH AT YPS | 40072.0493 | 40073.6597 | CONT | [12 empty] | 0
_1029142340072.2715277778 | 10291423 |  | Parent | FALSE | NO.3 220KV BUS AT FBTS | 40072.2715 | 40072.6424 | REPDAILY | 00002735 | SPIMAINT | O/Haul NO.3 220KV BUS AT FBTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029252840072.2833333333 | 10292528 |  | Parent | TRUE | NO.1 275KV CAPACITOR BANK/SESS NO.1 LINE CB AT HYTS | 40072.2833 | 40072.6813 | REPDAILY | [12 empty] | 0
_1031671540072.2833333333 | 10316715 | 10292528 | Child | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 40072.2833 | 40072.6813 | REPDAILY | 00331027 | SPIMAINT | Rebate W/O: No1 Cap bank during CB & Tie maint | SPIPOWER |  |  | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029376340072.3 | 10293763 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT RCTS | 40072.3 | 40072.7417 | DAILY | 00359892 | SPIMAINT | O/Haul 66KV CAPACITOR BANK | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029422040072.30625 | 10294220 | 10295726 | Child | FALSE | CBTS NO.1 220KV LINE AT TBTS | 40072.3063 | 40072.6847 | DAILY | 00018359 | SPIMAINT | O/Haul TBTS 1 L CVTs at ERTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029572640072.30625 | 10295726 |  | Parent | TRUE | NO.1 220KV BUS AT TBTS | 40072.3063 | 40072.6847 | DAILY | 00004905 | SPIMAINT | O/Haul NO.1 220KV BUS AT TBTS | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031105140072.30625 | 10311051 | 10295726 | Child | FALSE | JLA NO.1 220KV LINE AT TBTS | 40072.3063 | 40072.6847 | DAILY | 00018301 | SPIMAINT | O/Haul JLA 1 Line at TBTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V71158B240072.3111111111 | V71158B2 |  | Parent | FALSE | A2 GEN TRANS NO.1 BUS 500KV CB AT LYPS | 40072.3111 | 40095.4708 | CONT | [12 empty] | 0
_1029556540072.3138888889 | 10295565 |  | Parent | FALSE | WBTS 220KV LINE NO.2 BUS CB AT BATS | 40072.3139 | 40072.6979 | DAILY | [12 empty] | 0
_1031562440072.3631944444 | 10315624 |  | Parent | FALSE | B2 220/66KV TRANS AT SVTS | 40072.3632 | 40072.5271 | DAILY | 00004850 | SPIMAINT | Re-tighten Transformer connections | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031746540072.4270833333 | 10317465 |  | Parent | FALSE | ST 66KV FDR CB AT SMTS | 40072.4271 | 40078.4306 | CONT | [12 empty] | 0
_X7E558B740073.2923611111 | X7E558B7 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40073.2924 | 40073.6806 | DAILY | 00022640 | SPICAPX | install opwg between towers 69 and 81 | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029376140073.3048611111 | 10293761 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT RCTS | 40073.3049 | 40074.6507 | DAILY | 00359891 | SPIMAINT | O/Haul 66KV CAPACITOR BANK | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029252840073.30625 | 10292528 |  | Parent | TRUE | NO.1 275KV CAPACITOR BANK/SESS NO.1 LINE CB AT HYTS | 40073.3063 | 40073.7014 | REPDAILY | [12 empty] | 0
_1031671540073.30625 | 10316715 | 10292528 | Child | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 40073.3063 | 40073.7014 | REPDAILY | 00331027 | SPIMAINT | Rebate W/O: No1 Cap bank during CB & Tie maint | SPIPOWER |  |  | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029142340073.3131944445 | 10291423 |  | Parent | FALSE | NO.3 220KV BUS AT FBTS | 40073.3132 | 40073.6736 | REPDAILY | 00002735 | SPIMAINT | O/Haul NO.3 220KV BUS AT FBTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030028540073.4270833333 | 10300285 |  | Parent | FALSE | ST 66KV FDR CB AT SMTS | 40073.4271 | 40095.5833 | CONT | [12 empty] | 0
_X7E458D640074.2833333333 | X7E458D6 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40074.2833 | 40074.7562 | DAILY | 00022630 | SPICAPX | MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458E140074.2833333333 | X7E458E1 | X7E458D6 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40074.2833 | 40074.7562 | DAILY | 00003007 | SPICAPX | Rebate W/O HYTS 1L SH React - MLTS-HYTS 1L outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458E640074.2833333333 | X7E458E6 | X7E458D6 | Child | FALSE | HYTS-APD 1 500KV W | 40074.2833 | 40074.7562 | DAILY | 00319998 | SPICAPX | Rebate W/O APD 1 Line during MLTS-HYTS 1L outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458F240074.2833333333 | X7E458F2 | X7E458D6 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40074.2833 | 40074.7562 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MLTS-HYTS 1L outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E558C440074.2930555556 | X7E558C4 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40074.2931 | 40074.684 | DAILY | 00022640 | SPICAPX | install opwg between towers 81 and 92 | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031677740074.3236111111 | 10316777 | 10316747 | Child | FALSE | JLTS NO.1 220KV LINE AT HWPS | 40074.3236 | 40074.6424 | DAILY | 00015784 | SPIMAINT | REBATE FOR AUX TX B AT HWPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031674740074.3236111111 | 10316747 |  | Parent | TRUE | AUX B 220KV TRANS LINE AT HWPS | 40074.3236 | 40074.643 | DAILY | 00356087 | SPIMAINT | NEMMCO CT TESTS AUX TRANS B | SPIPOWER |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031748840074.5326388889 | 10317488 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT GNTS | 40074.5326 | 40074.6535 | DAILY | 00000745 | SPIMAINT | Blown surge diverter w phase | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1029123440075.2694444444 | 10291234 |  | Parent | FALSE | NO.1 220KV TRANS BUS AT WMTS | 40075.2694 | 40075.6944 | DAILY | 00003253 | SPIMAINT | O/Haul NO.1 220KV TRANS BUS AT WMTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z82558A740075.2916666667 | Z82558A7 |  | Parent | FALSE | ROTS NO.1 220KV LINE AT SVTS | 40075.2917 | 40075.5319 | DAILY | 00351700 | VEN_AUG | Replace Cross Arms | SPIPOWER | Z825 | Z825 - (ROTS-SVTS) 220KV UPGRADE TO 82 DEGREE C | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058H740075.2916666667 | X87058H7 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40075.2917 | 40075.6701 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS No2 Line ins replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031393340075.3166666667 | 10313933 |  | Parent | TRUE | NO.1 220KV BUS CVT R/PH AT JLTS | 40075.3167 | 40075.5847 | DAILY | [12 empty] | 0
_1031564640075.3166666667 | 10315646 | 10313933 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 40075.3167 | 40075.5847 | DAILY | 00015936 | SPIMAINT | rebate for bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029155040076.2902777778 | 10291550 |  | Parent | TRUE | PHASE ANGLE REGULATOR AT BLTS | 40076.2903 | 40076.6806 | DAILY | 00002624 | SPIMAINT | O/Haul PHASE ANGLE REGULATOR AT BLTS | SPIPOWER |  |  | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1029156140076.2902777778 | 10291561 | 10291550 | Child | FALSE | U1 TRANS-PAR 22KV CB AT BLTS | 40076.2903 | 40076.6806 | DAILY | [12 empty] | 0
_X87058H740076.3125 | X87058H7 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40076.3125 | 40076.6854 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS No2 Line ins replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E558C640077.2958333333 | X7E558C6 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40077.2958 | 40077.7618 | DAILY | 00022640 | SPICAPX | install opwg between towers 92 and rack structure | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V8A358A040077.3055555556 | V8A358A0 |  | Parent | TRUE | NO.4A 66KV CAPACITOR BANK CB AT TTS | 40077.3056 | 40081.6451 | CONT | [12 empty] | 0
_V8A358A340077.3055555556 | V8A358A3 | V8A358A0 | Child | FALSE | EX - NO.4A 66KV CAPACITOR BANK AT TTS | 40077.3056 | 40081.6451 | CONT | 00001486 | SPIMAINT | V8A3 - REFURBISH 4*66KV CAP BANK CBS | SPIPOWER | V8A3 | V8A3 - REFURBISH 4*66KV CAP BANK CBS | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V8A358A640077.3055555556 | V8A358A6 | V8A358A0 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT TTS | 40077.3056 | 40081.6451 | CONT | 00337509 | SPIMAINT | V8A3 - REFURBISH 4*66KV CAP BANK CBS | SPIPOWER | V8A3 | V8A3 - REFURBISH 4*66KV CAP BANK CBS | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029201040077.3125 | 10292010 | 10317396 | Child | FALSE | SLE 66KV FDR Y PROT AT MWTS | 40077.3125 | 40081.6444 | DAILY | [12 empty] | 0
_1031777540077.4375 | 10317775 |  | Parent | FALSE | JLGB NO.3 UNIT TRANS DISC CB AT JLGB | 40077.4375 | 40095.3514 | CONT | [12 empty] | 0
_1031784640077.8368055556 | 10317846 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40077.8368 | 40077.8486 | CONT | 00001169 | FORCED | No1 220kV Bus De-Energised to Isolate faulty CB | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031846740077.8368055556 | 10318467 | 10317846 | Child | FALSE | B1 220/66KV TRANS AT KTS | 40077.8368 | 40077.8486 | CONT | 00001147 | FORCED | No1 220kV Bus De-Energised to Isolate faulty CB | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031784740077.8368055556 | 10317847 |  | Parent | FALSE | KTS -BLTS 220KV WY | 40077.8368 | 40077.8618 | CONT | 00022716 | FORCED | KTS-BLTS 220kV Line De-Energised to Isolate CB | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031784840077.8486111111 | 10317848 |  | Parent | FALSE | EX - BLTS 220KV LINE NO.1 BUS CB AT KTS | 40077.8486 | 40078.6021 | CONT | [12 empty] | 0
_1031608740078.2541666667 | 10316087 |  | Parent | FALSE | NO.1 TRANS/NO.1 NEC 11KV CB AT FVTS | 40078.2542 | 40078.5306 | DAILY | [12 empty] | 0
_1031614240078.2541666667 | 10316142 |  | Parent | FALSE | BETS-FVTS-SHTS 220KV NB | 40078.2542 | 40078.5319 | DAILY | 00026225 | SPIMAINT | Out W/O BETS-FVTS-SHTS Line defect repairs | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031607840078.2611111111 | 10316078 |  | Parent | FALSE | PSV FDR 11KV CB AT FVTS | 40078.2611 | 40078.6306 | DAILY | [12 empty] | 0
_X7E458H440078.2902777778 | X7E458H4 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40078.2903 | 40078.7514 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458H540078.2902777778 | X7E458H5 | X7E458H4 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40078.2903 | 40078.7514 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458H640078.2902777778 | X7E458H6 | X7E458H4 | Child | FALSE | HYTS-APD 1 500KV W | 40078.2903 | 40078.7514 | REPDAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458H840078.2902777778 | X7E458H8 | X7E458H4 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40078.2903 | 40078.7514 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031787140078.375 | 10317871 |  | Parent | FALSE | EX - WMTS NO.2 220KV LINE NO.1 BUS CB AT KTS | 40078.375 | 40079.6632 | CONT | [12 empty] | 0
_1031785540078.3840277778 | 10317855 |  | Parent | FALSE | EX - BLTS 220KV LINE NO.1 BUS CB AT KTS | 40078.384 | 40078.6014 | CONT | [12 empty] | 0
_1031695440078.45625 | 10316954 |  | Parent | FALSE | NO.1 66KV BUS VT AT BLTS | 40078.4563 | 40078.5806 | DAILY | [12 empty] | 0
_1031769740078.6828935185 | 10317697 |  | Parent | FALSE | ST 66KV FDR CB AT SMTS | 40078.6829 | 40095.5833 | CONT | [12 empty] | 0
_1029136740079.29375 | 10291367 |  | Parent | TRUE | SESS NO.2 275KV LINE/M2 TRANS CB LINE SIDE E/SW AT HYTS | 40079.2937 | 40079.7472 | DAILY | [12 empty] | 0
_1031699040079.29375 | 10316990 | 10291367 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40079.2937 | 40079.7472 | REPDAILY | 00002862 | SPIMAINT | Rebate W/O M2 Trans during SESS 2L equip O/H | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031699140079.29375 | 10316991 | 10291367 | Child | FALSE | SESS NO.2 275KV LINE AT HYTS | 40079.2937 | 40079.7472 | REPDAILY | 00026936 | SPIMAINT | Rebate W/O SESS No2 Line during equip O/H | SPIPOWER |  |  | Circuits | Alstom | 275 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031699240079.29375 | 10316992 | 10291367 | Child | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 40079.2937 | 40079.7472 | REPDAILY | 00331027 | SPIMAINT | Rebate W/O No1 Cap bk during SESS 2 L equip O/H | SPIPOWER |  |  | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031777440079.3076388889 | 10317774 |  | Parent | FALSE | EPG NO.1 66KV FDR AT SMTS | 40079.3076 | 40079.6215 | DAILY | 00366226 | DBPROX | VSCAP to DOC | DISTCO |  |  | Circuits | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031777940079.3368055556 | 10317779 |  | Parent | FALSE | WOTS 330KV LINE NO.2 BUS CB AT DDTS | 40079.3368 | 40079.6514 | DAILY | [12 empty] | 0
_1031789940079.3958333333 | 10317899 |  | Parent | FALSE | ROTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 40079.3958 | 40079.6368 | REPDAILY | [12 empty] | 0
_1031695840079.43125 | 10316958 |  | Parent | FALSE | NO.2 66KV BUS VT AT BLTS | 40079.4313 | 40079.5049 | DAILY | [12 empty] | 0
_1031696040079.5541666667 | 10316960 |  | Parent | FALSE | NO.3 66KV BUS VT AT BLTS | 40079.5542 | 40079.6493 | DAILY | [12 empty] | 0
_V96558A240080.1736111111 | V96558A2 |  | Parent | FALSE | NO.6 GEN TRANS NO.4 BUS 220KV CB AT HWPS | 40080.1736 | 40095.5861 | CONT | [12 empty] | 0
_X49758P040080.2493055556 | X49758P0 |  | Parent | FALSE | R4 220/66/22KV TRANS AT BETS | 40080.2493 | 40080.7438 | DAILY | 00016220 | SPICAPX | Out W/O No4 Trans, Wiring checks on 220kv CVT's | SPIPOWER | X497 | X497 - (BETS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458J440080.2875 | X7E458J4 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40080.2875 | 40080.741 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458J540080.2875 | X7E458J5 | X7E458J4 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40080.2875 | 40080.741 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458J640080.2875 | X7E458J6 | X7E458J4 | Child | FALSE | HYTS-APD 1 500KV W | 40080.2875 | 40080.741 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458J840080.2875 | X7E458J8 | X7E458J4 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40080.2875 | 40080.741 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E558C840080.2916666667 | X7E558C8 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40080.2917 | 40080.8514 | DAILY | 00022640 | SPICAPX | INSTALL OPGW BETWEEN SMTS AND TWR 13 | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029093740080.2993055556 | 10290937 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT FTS | 40080.2993 | 40080.6097 | DAILY | [12 empty] | 0
_1031789940080.3125 | 10317899 |  | Parent | FALSE | ROTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 40080.3125 | 40080.5104 | REPDAILY | [12 empty] | 0
_1031738040080.3284722222 | 10317380 |  | Parent | FALSE | KGTS-RCTS 220KV NB | 40080.3285 | 40080.5972 | DAILY | 00026223 | SPIMAINT | Out W/O KGTS-RCTS Line Earth wire & defect repairs | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031786340080.3319444444 | 10317863 | 10317865 | Child | FALSE | NO.2 66KV CAPACITOR BANK Y PROT AT RWTS | 40080.3319 | 40080.6521 | DAILY | [12 empty] | 0
_1031786540080.3319444444 | 10317865 |  | Parent | TRUE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 40080.3319 | 40080.6521 | DAILY | 00007399 | SPIMAINT | REBATE FOR CAP BANK OUTAGE | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031786640080.3319444444 | 10317866 | 10317865 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 40080.3319 | 40080.6521 | DAILY | 00331179 | SPIMAINT | REBATE FOR CAP BANK OUTAGE | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031660340080.3333333333 | 10316603 | 10315459 | Child | FALSE | B4 220/66KV TRANS AT SVTS | 40080.3333 | 40080.5125 | DAILY | 00352791 | SPIMAINT | Transformer rebates Investigate OLTC operation | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031545940080.3333333333 | 10315459 |  | Parent | TRUE | TRANSFORMER VOLTAGE CONTROL AT SVTS | 40080.3333 | 40080.5129 | DAILY | [12 empty] | 0
_1031696140081.4027777778 | 10316961 |  | Parent | FALSE | NO.4 66KV BUS VT R/PH AT BLTS | 40081.4028 | 40081.4826 | DAILY | [12 empty] | 0
_V99158A140084.3111111111 | V99158A1 |  | Parent | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 40084.3111 | 40084.7292 | DAILY | 00004037 | SPICAPX | Remove 22kv Droppers and replace 22kv Potheads | SPIPOWER | V991 | V991 - (WOTS) TRANS #1 & #2 22KV UG CABLE REPAIRS | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_X87058I040084.3368055556 | X87058I0 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 40084.3368 | 40084.7174 | REPDAILY | 00022702 | SPICAPX | KTS-GTS 1 Line insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031794640084.3395833333 | 10317946 |  | Parent | FALSE | NO.1 66KV BUS EXTENSION AT TSTS | 40084.3396 | 40084.6521 | DAILY | 00007673 | DBPROX | VSCAP to DOC | DISTCO |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031792340084.7229166667 | 10317923 |  | Parent | FALSE | NO.2 TRANS RACK BRIDGE | 40084.7229 | 40091.4194 | CONT | [12 empty] | 0
_1029142540085.2708333333 | 10291425 |  | Parent | TRUE | NO.4 220KV BUS AT FBTS | 40085.2708 | 40085.6736 | REPDAILY | 00002736 | SPIMAINT | O/Haul NO.4 220KV BUS AT FBTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029146940085.2708333333 | 10291469 | 10291425 | Child | FALSE | NO.4 220KV BUS E/SW AT FBTS | 40085.2708 | 40085.6736 | DAILY | [12 empty] | 0
_1029150340085.2708333333 | 10291503 | 10291425 | Child | FALSE | 3-4 220KV BUS TIE CB NO.4 BUS SIDE ROI AT FBTS | 40085.2708 | 40085.6736 | DAILY | [12 empty] | 0
_1031762840085.2708333333 | 10317628 | 10291425 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 40085.2708 | 40085.6736 | CONT | 00327661 | SPIMAINT | NO.4 CAPBANK REBATE CAPTURE W/O | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031763040085.2708333333 | 10317630 | 10291425 | Child | FALSE | NPSD-FBTS 220KV WY | 40085.2708 | 40085.6736 | CONT | 00022738 | SPIMAINT | NPSD LINE REBATE CAPTURE W/O | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031854940085.2708333333 | 10318549 | 10291425 | Child | FALSE | WMTS NO.1 220KV LINE AT FBTS | 40085.2708 | 40085.6736 | CONT | 00017159 | SPIMAINT | WMTS LINE REBATE CAPTURE W/O for Bus outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X87058I040085.2916666667 | X87058I0 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 40085.2917 | 40085.6924 | REPDAILY | 00022702 | SPICAPX | KTS-GTS 1 Line insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029412440085.2944444444 | 10294124 |  | Parent | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 40085.2944 | 40088.5569 | CONT | 00004037 | SPIMAINT | Condition Monitoring Country Trans 2day North Area | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029375140085.30625 | 10293751 |  | Parent | TRUE | MLTS NO.1 220KV LINE CB AT GTS | 40085.3063 | 40085.6417 | DAILY | [12 empty] | 0
_1030366040085.30625 | 10303660 | 10293751 | Child | FALSE | MLTS-GTS 1 220KV WY | 40085.3063 | 40085.6417 | DAILY | 00022686 | SPIMAINT | Rebate W/O MLTS No1 Line during CB outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031659040085.3166666667 | 10316590 |  | Parent | TRUE | NO.3 220KV CAPACITOR BANK CB AT ROTS | 40085.3167 | 40085.5722 | DAILY | [12 empty] | 0
_1031708340085.3166666667 | 10317083 | 10316590 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 40085.3167 | 40085.5722 | DAILY | 00112417 | SPIMAINT | REBATES FOR CAPBANK | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_V95858A040085.3215277778 | V95858A0 |  | Parent | TRUE | MBTS NO.1 220KV LINE CB AT DDTS | 40085.3215 | 40085.6833 | DAILY | [12 empty] | 0
_V95858A140085.3215277778 | V95858A1 | V95858A0 | Child | FALSE | MBTS NO.1 220KV LINE AT DDTS | 40085.3215 | 40085.6833 | DAILY | 00012361 | SPIMAINT | Rebate WO MBTS No1 Line during CB outage | SPIPOWER | V958 | V958 - (DDTS) INSPECTION OF ABB IMBP 220KV CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031804040085.4381944445 | 10318040 |  | Parent | FALSE | HYTS NO.2 500KV LINE AT APD | 40085.4382 | 40085.7167 | REPDAILY | 00005922 | APDALCOA | APD - HYTS No2 Line Outage for APD | APDALCOA |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029142540086.2673611111 | 10291425 |  | Parent | TRUE | NO.4 220KV BUS AT FBTS | 40086.2674 | 40086.6701 | REPDAILY | 00002736 | SPIMAINT | O/Haul NO.4 220KV BUS AT FBTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029146940086.2673611111 | 10291469 | 10291425 | Child | FALSE | NO.4 220KV BUS E/SW AT FBTS | 40086.2674 | 40086.6701 | DAILY | [12 empty] | 0
_1029150340086.2673611111 | 10291503 | 10291425 | Child | FALSE | 3-4 220KV BUS TIE CB NO.4 BUS SIDE ROI AT FBTS | 40086.2674 | 40086.6701 | DAILY | [12 empty] | 0
_1031762840086.2673611111 | 10317628 | 10291425 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 40086.2674 | 40086.6701 | CONT | 00327661 | SPIMAINT | NO.4 CAPBANK REBATE CAPTURE W/O | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031763040086.2673611111 | 10317630 | 10291425 | Child | FALSE | NPSD-FBTS 220KV WY | 40086.2674 | 40086.6701 | CONT | 00022738 | SPIMAINT | NPSD LINE REBATE CAPTURE W/O | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031854940086.2673611111 | 10318549 | 10291425 | Child | FALSE | WMTS NO.1 220KV LINE AT FBTS | 40086.2674 | 40086.6701 | CONT | 00017159 | SPIMAINT | WMTS LINE REBATE CAPTURE W/O for Bus outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X87058I140086.2916666667 | X87058I1 |  | Parent | FALSE | KTS -GTS 3 220KV WY | 40086.2917 | 40086.6799 | REPDAILY | 00022709 | SPICAPX | KTS-GTS 3 Line insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031804040086.3020833333 | 10318040 |  | Parent | FALSE | HYTS NO.2 500KV LINE AT APD | 40086.3021 | 40086.6937 | REPDAILY | 00005922 | APDALCOA | APD - HYTS No2 Line Outage for APD | APDALCOA |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029379640086.3034722222 | 10293796 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT MLTS | 40086.3035 | 40086.659 | DAILY | 00360001 | SPIMAINT | O/Haul NO.1 220KV CAPACITOR BANK AT MLTS | SPIPOWER |  |  | Capacitors | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_V95858A240086.3125 | V95858A2 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.1 BUS CB AT DDTS | 40086.3125 | 40086.734 | DAILY | [12 empty] | 0
_1029142540087.2819444445 | 10291425 |  | Parent | TRUE | NO.4 220KV BUS AT FBTS | 40087.2819 | 40087.6639 | REPDAILY | 00002736 | SPIMAINT | O/Haul NO.4 220KV BUS AT FBTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029146940087.2819444445 | 10291469 | 10291425 | Child | FALSE | NO.4 220KV BUS E/SW AT FBTS | 40087.2819 | 40087.6639 | DAILY | [12 empty] | 0
_1029150340087.2819444445 | 10291503 | 10291425 | Child | FALSE | 3-4 220KV BUS TIE CB NO.4 BUS SIDE ROI AT FBTS | 40087.2819 | 40087.6639 | DAILY | [12 empty] | 0
_1031762840087.2819444445 | 10317628 | 10291425 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 40087.2819 | 40087.6639 | CONT | 00327661 | SPIMAINT | NO.4 CAPBANK REBATE CAPTURE W/O | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031763040087.2819444445 | 10317630 | 10291425 | Child | FALSE | NPSD-FBTS 220KV WY | 40087.2819 | 40087.6639 | CONT | 00022738 | SPIMAINT | NPSD LINE REBATE CAPTURE W/O | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031854940087.2819444445 | 10318549 | 10291425 | Child | FALSE | WMTS NO.1 220KV LINE AT FBTS | 40087.2819 | 40087.6639 | CONT | 00017159 | SPIMAINT | WMTS LINE REBATE CAPTURE W/O for Bus outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1029299640087.2972222222 | 10292996 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT MLTS | 40087.2972 | 40087.6951 | DAILY | 00350825 | SPIMAINT | O/Haul NO.2 220KV CAPACITOR BANK AT MLTS | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X87058J140087.3138888889 | X87058J1 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 40087.3139 | 40087.6368 | REPDAILY | 00022702 | SPICAPX | KTS-GTS 1 Line insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031655140087.3145833333 | 10316551 |  | Parent | TRUE | HWTS NO.1 220KV LINE CB LINE SIDE ISOL AT HWPS | 40087.3146 | 40087.6014 | DAILY | [12 empty] | 0
_1031734940087.3145833333 | 10317349 | 10316551 | Child | FALSE | A1 515/230KV TRANS AT HWTS | 40087.3146 | 40087.6014 | DAILY | 00009772 | SPIMAINT | TRANS REBATE FOR ISOL OUTAGE | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029208240087.3145833333 | 10292082 |  | Parent | FALSE | B2 220/66KV TRANS AT GNTS | 40087.3146 | 40087.7049 | CONT | 00000743 | SPIMAINT | O/H TRANSFORMER AT GNTS | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031732040087.3145833333 | 10317320 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT CBTS | 40087.3146 | 40087.7049 | DAILY | 00359493 | SPIMAINT | Rebate WO for Trans outage | SPIPOWER |  |  | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_V95858A340087.3159722222 | V95858A3 |  | Parent | TRUE | MBTS NO.2 220KV LINE CB AT DDTS | 40087.316 | 40087.6458 | DAILY | [12 empty] | 0
_V95858A440087.3159722222 | V95858A4 | V95858A3 | Child | FALSE | MBTS NO.2 220KV LINE AT DDTS | 40087.316 | 40087.6458 | DAILY | 00012363 | SPIMAINT | Rebate WO MBTS No2 Line during CB outage | SPIPOWER | V958 | V958 - (DDTS) INSPECTION OF ABB IMBP 220KV CTS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031817540087.6722222222 | 10318175 |  | Parent | FALSE | EX - NO.1 MAIN TRANS 500KV CB AT HWTS | 40087.6722 | 40087.8347 | DAILY | [12 empty] | 0
_1031819240088.0034722222 | 10318192 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 40088.0035 | 40090.9125 | CONT | 00356083 | GENCO | HWPS No5 Gen SCAP on Isolations | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029142540088.2652777778 | 10291425 |  | Parent | TRUE | NO.4 220KV BUS AT FBTS | 40088.2653 | 40088.6146 | REPDAILY | 00002736 | SPIMAINT | O/Haul NO.4 220KV BUS AT FBTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029146940088.2652777778 | 10291469 | 10291425 | Child | FALSE | NO.4 220KV BUS E/SW AT FBTS | 40088.2653 | 40088.6146 | DAILY | [12 empty] | 0
_1029150340088.2652777778 | 10291503 | 10291425 | Child | FALSE | 3-4 220KV BUS TIE CB NO.4 BUS SIDE ROI AT FBTS | 40088.2653 | 40088.6146 | DAILY | [12 empty] | 0
_1031762840088.2652777778 | 10317628 | 10291425 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 40088.2653 | 40088.6146 | CONT | 00327661 | SPIMAINT | NO.4 CAPBANK REBATE CAPTURE W/O | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031763040088.2652777778 | 10317630 | 10291425 | Child | FALSE | NPSD-FBTS 220KV WY | 40088.2653 | 40088.6146 | CONT | 00022738 | SPIMAINT | NPSD LINE REBATE CAPTURE W/O | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031854940088.2652777778 | 10318549 | 10291425 | Child | FALSE | WMTS NO.1 220KV LINE AT FBTS | 40088.2653 | 40088.6146 | CONT | 00017159 | SPIMAINT | WMTS LINE REBATE CAPTURE W/O for Bus outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X87058J140088.2923611111 | X87058J1 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 40088.2924 | 40088.6007 | REPDAILY | 00022702 | SPICAPX | KTS-GTS 1 Line insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030390340088.2930555556 | 10303903 |  | Parent | FALSE | ERTS NO.2 220KV LINE AT CBTS | 40088.2931 | 40088.5833 | DAILY | 00359469 | SPIMAINT | O/Haul ERTS No 2 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029424940088.3034722222 | 10294249 |  | Parent | FALSE | BLLY 500KV LINE AT LYPS | 40088.3035 | 40091.9556 | CONT | 00360516 | SPIMAINT | Overhaul Basslink Connection Assets at Loy Yang | SPIPOWER |  |  | Circuits | Eastern | 500 | CONNECTION ASSET | EXCLUDED |  | 0
_1031655740088.3145833333 | 10316557 |  | Parent | TRUE | ROTS NO.5 220KV LINE NO.2 BUS CB LINE SIDE ROI AT YPS | 40088.3146 | 40088.5556 | DAILY | [12 empty] | 0
_1031735040088.3145833333 | 10317350 | 10316557 | Child | FALSE | ROTS NO.5 220KV LINE AT YPS | 40088.3146 | 40088.5556 | DAILY | 00016413 | SPIMAINT | LINE REBATE FOR ISOL OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029044440089.25 | 10290444 | Z63358L6 | Child | FALSE | NO.2 220KV BUS E/SW AT JLTS | 40089.25 | 40090.6681 | REPDAILY | [12 empty] | 0
_Z63358L640089.25 | Z63358L6 |  | Parent | TRUE | NO.2 220KV BUS AT JLTS | 40089.25 | 40090.6681 | CONT | 00365902 | VEN_AUG | CHANGE BYPODS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358L740089.25 | Z63358L7 | Z63358L6 | Child | FALSE | HWPS NO.2 220KV LINE AT JLTS | 40089.25 | 40090.6681 | REPDAILY | 00015937 | VEN_AUG | REBATE FOR BUS OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031028640089.2583333333 | 10310286 |  | Parent | TRUE | NO.2 220KV BUS AT ATS | 40089.2583 | 40089.609 | REPDAILY | 00055544 | SPIMAINT | O/Haul NO.2 220KV BUS AT ATS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031855140089.2583333333 | 10318551 | 10310286 | Child | FALSE | ATS -BLTS 220KV WY | 40089.2583 | 40089.609 | REPDAILY | 00074403 | SPIMAINT | capture outage costs | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031861640089.2583333333 | 10318616 | 10310286 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ATS | 40089.2583 | 40089.609 | REPDAILY | 00350821 | SPIMAINT | Bus O/Haul capture outage costs for Cap Bank | SPIPOWER |  |  | Capacitors | Western | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X87058E040089.3006944444 | X87058E0 |  | Parent | FALSE | BATS-BETS 220KV | 40089.3007 | 40089.7097 | REPDAILY | 00328505 | SPICAPX | BATS-BETS 220kv Line insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031028640090.2416666667 | 10310286 |  | Parent | TRUE | NO.2 220KV BUS AT ATS | 40090.2417 | 40090.5875 | REPDAILY | 00055544 | SPIMAINT | O/Haul NO.2 220KV BUS AT ATS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031855140090.2416666667 | 10318551 | 10310286 | Child | FALSE | ATS -BLTS 220KV WY | 40090.2417 | 40090.5875 | REPDAILY | 00074403 | SPIMAINT | capture outage costs | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031861640090.2416666667 | 10318616 | 10310286 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ATS | 40090.2417 | 40090.5875 | REPDAILY | 00350821 | SPIMAINT | Bus O/Haul capture outage costs for Cap Bank | SPIPOWER |  |  | Capacitors | Western | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_X87058E040090.2548611111 | X87058E0 |  | Parent | FALSE | BATS-BETS 220KV | 40090.2549 | 40090.5764 | REPDAILY | 00328505 | SPICAPX | BATS-BETS 220kv Line insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029986640090.2777777778 | 10299866 |  | Parent | FALSE | CBTS NO.4 500KV LINE AT ROTS (RTF) | 40090.2778 | 40090.5736 | DAILY | 00356730 | SPIMAINT | Overhaul 500kV Line @ CBTS and RTF | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458J940091.2520833333 | X7E458J9 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40091.2521 | 40091.7118 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458K040091.2520833333 | X7E458K0 | X7E458J9 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40091.2521 | 40091.7118 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458K140091.2520833333 | X7E458K1 | X7E458J9 | Child | FALSE | HYTS-APD 1 500KV W | 40091.2521 | 40091.7118 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458K340091.2520833333 | X7E458K3 | X7E458J9 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40091.2521 | 40091.7118 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031824740091.3965277778 | 10318247 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 40091.3965 | 40091.4563 | DAILY | [12 empty] | 0
_1030289340091.4493055556 | 10302893 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK CB AT BATS | 40091.4493 | 40091.4833 | DAILY | [12 empty] | 0
_1030289440091.4493055556 | 10302894 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT BATS | 40091.4493 | 40091.4833 | DAILY | 00331118 | SPIMAINT | Rebate W/O No2 Cap Bk during CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V99158A240091.4965277778 | V99158A2 |  | Parent | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 40091.4965 | 40091.6674 | DAILY | 00004037 | SPICAPX | Re Install Droppers to 22kv Bus & 22kv CB cables | SPIPOWER | V991 | V991 - (WOTS) TRANS #1 & #2 22KV UG CABLE REPAIRS | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031827440091.7263888889 | 10318274 |  | Parent | FALSE | EX - GTS NO.2 LINE/A1 TRANS 220KV CB CT B/PH AT MLTS | 40091.7264 | 40093.4361 | CONT | [12 empty] | 0
_1029113340092.25 | 10291133 |  | Parent | TRUE | NO.1 330KV BUS AT DDTS | 40092.25 | 40092.691 | REPDAILY | 00003978 | SPIMAINT | O/Haul NO.1 330KV BUS AT DDTS | SPIPOWER |  |  | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031753440092.25 | 10317534 | 10291133 | Child | FALSE | NO.1 330KV CAPACITOR BANK AT DDTS | 40092.25 | 40092.691 | REPDAILY | 00352085 | SPIMAINT | Rebate W/O #1 330 Cap bk during #1 330 bus outage | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_1027308040092.2506944445 | 10273080 |  | Parent | FALSE | TBTS NO.1 220KV LINE AT CBTS | 40092.2507 | 40092.5868 | DAILY | 00359466 | SPIMAINT | O/H 220KV LINE & EQUIP AS PER E.A.P APPL. | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058J240092.2597222222 | X87058J2 |  | Parent | FALSE | KTS -GTS 3 220KV WY | 40092.2597 | 40092.5667 | REPDAILY | 00022709 | SPICAPX | KTS-GTS 3 Line insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030312740092.3152777778 | 10303127 |  | Parent | TRUE | SMTS NO.2 LINE/A4 TRANS 500KV CB TRANS SIDE ROI AT HWTS | 40092.3153 | 40092.5431 | DAILY | [12 empty] | 0
_1030313340092.3152777778 | 10303133 | 10303127 | Child | FALSE | A4 TRANS NO.1 BUS 500KV CB TRANS SIDE ROI AT HWTS | 40092.3153 | 40092.5431 | DAILY | [12 empty] | 0
_1030315240092.3152777778 | 10303152 | 10303127 | Child | FALSE | A4 515/230KV TRANS BANK AT HWTS | 40092.3153 | 40092.5431 | DAILY | 00337582 | SPIMAINT | TX REBATE FOR ISOL OUTAGE | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031825140092.3555555556 | 10318251 |  | Parent | FALSE | KMS 66KV FDR CB AT SMTS | 40092.3556 | 40124.2424 | CONT | [12 empty] | 0
_1031833540092.8180555556 | 10318335 |  | Parent | FALSE | BLLY 500KV LINE AT LYPS | 40092.8181 | 40092.9111 | CONT | 00360516 | REM_TRIP | Remote Trip from Basslink Converter Station | GENCO |  |  | Circuits | Eastern | 500 | CONNECTION ASSET | EXCLUDED |  | 0
_X7E458K440093.2243055556 | X7E458K4 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40093.2243 | 40093.684 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458K540093.2243055556 | X7E458K5 | X7E458K4 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40093.2243 | 40093.684 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458K640093.2243055556 | X7E458K6 | X7E458K4 | Child | FALSE | HYTS-APD 1 500KV W | 40093.2243 | 40093.684 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458K840093.2243055556 | X7E458K8 | X7E458K4 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40093.2243 | 40093.684 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029113340093.25 | 10291133 |  | Parent | TRUE | NO.1 330KV BUS AT DDTS | 40093.25 | 40093.6868 | REPDAILY | 00003978 | SPIMAINT | O/Haul NO.1 330KV BUS AT DDTS | SPIPOWER |  |  | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031753440093.25 | 10317534 | 10291133 | Child | FALSE | NO.1 330KV CAPACITOR BANK AT DDTS | 40093.25 | 40093.6868 | REPDAILY | 00352085 | SPIMAINT | Rebate W/O #1 330 Cap bk during #1 330 bus outage | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_X87058I340093.2527777778 | X87058I3 | X87058I2 | Child | FALSE | TSTS-TTS 220KV WT | 40093.2528 | 40093.6097 | REPDAILY | 00022783 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030390440093.2555555556 | 10303904 |  | Parent | FALSE | ERTS NO.1 220KV LINE AT CBTS | 40093.2556 | 40093.5993 | DAILY | 00359468 | SPIMAINT | O/Haul ERTS No 1 Line | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031832440093.2708333333 | 10318324 |  | Parent | FALSE | NO.1 220KV BUS AT EPSY | 40093.2708 | 40093.2736 | CONT | 00357773 | STHHYDRO | AGL Hydro requested Bus de-energised | STHHYDRO |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 3
_1031631340093.2715277778 | 10316313 |  | Parent | FALSE | MLRC 220KV LINE NO.2 BUS CB AT RCTS | 40093.2715 | 40093.3975 | CONT | [12 empty] | 4
_1031631140093.2743055556 | 10316311 |  | Parent | FALSE | MLRC 220KV LINE NO.1 BUS CB AT RCTS | 40093.2743 | 40093.5965 | DAILY | [12 empty] | 4
_1031832740093.5833333333 | 10318327 |  | Parent | TRUE | NO.1 220KV BUS AT EPSY | 40093.5833 | 40093.5854 | CONT | 00357773 | STHHYDRO | Bus de-energised at EPS requested by AGL Hydro | STHHYDRO |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 3
_1031855340093.5833333333 | 10318553 | 10318327 | Child | FALSE | MBTS NO.2 220KV LINE AT EPSY | 40093.5833 | 40093.5854 | CONT | 00087036 | STHHYDRO | Bus de-energised at EPS requested by AGL Hydro | STHHYDRO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 3
_1031837840093.9423611111 | 10318378 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 40093.9424 | 40097.2972 | CONT | 00356084 | GENCO | Genco isolation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031715740094.2215277778 | 10317157 | X70658N2 | Child | FALSE | KTS -GTS 2 220KV WY | 40094.2215 | 40094.7667 | DAILY | 00022705 | SPICAPX | W/O FOR REBATE ON GTS NO.2 LINE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658N240094.2215277778 | X70658N2 |  | Parent | TRUE | NO.3 220KV BUS AT KTS | 40094.2215 | 40094.7667 | REPDAILY | 00001171 | SPICAPX | CUT BIPODS FROM No3 BUS TO GTS No2 L No 3 BUS CB | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029417840094.2465277778 | 10294178 |  | Parent | FALSE | HWTS NO.4 L/ROTS NO.4 L 500KV CB AT CBTS | 40094.2465 | 40094.5583 | DAILY | [12 empty] | 0
_1031751840094.2541666667 | 10317518 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT EPSY | 40094.2542 | 40094.5931 | DAILY | 00087035 | SPIMAINT | Out W/O MBTS 1 line for mods to MBTS 1L CB LS ROI | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1029113340094.2597222222 | 10291133 |  | Parent | TRUE | NO.1 330KV BUS AT DDTS | 40094.2597 | 40094.7139 | REPDAILY | 00003978 | SPIMAINT | O/Haul NO.1 330KV BUS AT DDTS | SPIPOWER |  |  | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031753440094.2597222222 | 10317534 | 10291133 | Child | FALSE | NO.1 330KV CAPACITOR BANK AT DDTS | 40094.2597 | 40094.7139 | REPDAILY | 00352085 | SPIMAINT | Rebate W/O #1 330 Cap bk during #1 330 bus outage | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_Z91358A040094.2597222222 | Z91358A0 |  | Parent | FALSE | EX - NO.1 66KV BUS 'B' VT AT MWTS | 40094.2597 | 40094.7833 | DAILY | [12 empty] | 0
_X87058I340094.2826388889 | X87058I3 | X87058I2 | Child | FALSE | TSTS-TTS 220KV WT | 40094.2826 | 40094.5667 | REPDAILY | 00022783 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031851340094.53125 | 10318513 |  | Parent | FALSE | BLLY 500KV LINE AT LYPS | 40094.5312 | 40094.5576 | DAILY | 00360516 | REM_TRIP | Remote Trip from Basslink Converter Station | GENCO |  |  | Circuits | Eastern | 500 | CONNECTION ASSET | EXCLUDED |  | 0
_1031851040094.625 | 10318510 |  | Parent | FALSE | KTS -BLTS 220KV WY | 40094.625 | 40094.6347 | DAILY | 00022716 | FAULT | KTS-BLTS Line Trip | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031850840094.625 | 10318508 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 40094.625 | 40094.7403 | DAILY | 00001147 | FAULT | KTS B1 Trans Trip | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031850940094.6256944445 | 10318509 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 40094.6257 | 40094.7188 | DAILY | 00022702 | FAULT | KTS GTS 1 Line Trip | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031851240094.6402777778 | 10318512 |  | Parent | FALSE | KTS -GTS 3 220KV WY | 40094.6403 | 40094.6785 | DAILY | 00022709 | FAULT | KTS GTS 3 Line Trip | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031851140094.6402777778 | 10318511 |  | Parent | FALSE | B4 220/66KV TRANS AT KTS | 40094.6403 | 40094.7278 | DAILY | 00001146 | FAULT | KTS B4 Trans Trip | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458E840095.2097222222 | X7E458E8 | X7E458M6 | Child | FALSE | HYTS-APD 1 500KV W | 40095.2097 | 40095.6979 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458M640095.2097222222 | X7E458M6 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40095.2097 | 40095.6979 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458M740095.2097222222 | X7E458M7 | X7E458M6 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40095.2097 | 40095.6979 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458M840095.2097222222 | X7E458M8 | X7E458M6 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40095.2097 | 40095.6979 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029418040095.25 | 10294180 |  | Parent | FALSE | ROTS NO.4 500KV LINE NO.1 BUS CB AT CBTS | 40095.25 | 40095.5514 | DAILY | [12 empty] | 0
_1029113340095.2513888889 | 10291133 |  | Parent | TRUE | NO.1 330KV BUS AT DDTS | 40095.2514 | 40095.5618 | REPDAILY | 00003978 | SPIMAINT | O/Haul NO.1 330KV BUS AT DDTS | SPIPOWER |  |  | Bus | Alstom | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031753440095.2513888889 | 10317534 | 10291133 | Child | FALSE | NO.1 330KV CAPACITOR BANK AT DDTS | 40095.2514 | 40095.5618 | REPDAILY | 00352085 | SPIMAINT | Rebate W/O #1 330 Cap bk during #1 330 bus outage | SPIPOWER |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 0
_1031752340095.2520833333 | 10317523 |  | Parent | FALSE | MBTS NO.2 220KV LINE AT EPSY | 40095.2521 | 40095.5236 | DAILY | 00087036 | SPIMAINT | Out W/O MBTS 2 line for mods to MBTS 2L CB LS ROI | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X87058I340095.2854166667 | X87058I3 | X87058I2 | Child | FALSE | TSTS-TTS 220KV WT | 40095.2854 | 40095.5507 | REPDAILY | 00022783 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031781440095.3222222222 | 10317814 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 40095.3222 | 40095.5215 | DAILY | [12 empty] | 0
_1031845040095.3361111111 | 10318450 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40095.3361 | 40095.4896 | CONT | 00119824 | FORCED | KTS No1 220kV Cap Bank | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031781340095.3680555556 | 10317813 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT WOTS | 40095.3681 | 40095.5667 | DAILY | [12 empty] | 0
_1030310640095.3833333333 | 10303106 |  | Parent | FALSE | ROTS NO.8 220KV LINE AT YPS | 40095.3833 | 40095.4444 | DAILY | 00016416 | SPIMAINT | REBATE FOR CB OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031845340095.4895833333 | 10318453 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB CT R/PH AT KTS | 40095.4896 | 40095.5944 | DAILY | [12 empty] | 0
_1031845740095.4895833333 | 10318457 | 10318453 | Child | FALSE | NO.1 220KV CAPACITOR BANK CB AT KTS | 40095.4896 | 40095.5944 | DAILY | [12 empty] | 0
_Z63358M140096.2111111111 | Z63358M1 |  | Parent | TRUE | NO.2 220KV BUS AT JLTS | 40096.2111 | 40096.6681 | DAILY | 00365902 | VEN_AUG | BYPOD CHANGE No2 BUS AT JLTS | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z63358M240096.2111111111 | Z63358M2 | Z63358M1 | Child | FALSE | HWPS NO.2 220KV LINE AT JLTS | 40096.2111 | 40096.6681 | DAILY | 00015937 | VEN_AUG | LINE REBATE FOR BUS OUTAGE | SPIPOWER | Z633 | Z633 - (HWPS,JLTS) SWITCHING RE-ARRANGEMENT & FAULT MIT WKS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z82558A940096.24375 | Z82558A9 |  | Parent | FALSE | SVTS NO.1 220KV LINE AT ROTS | 40096.2438 | 40096.6507 | DAILY | 00350027 | VEN_AUG | REPLACE CROSS ARMS | SPIPOWER | Z825 | Z825 - (ROTS-SVTS) 220KV UPGRADE TO 82 DEGREE C | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458M940097.21875 | X7E458M9 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40097.2188 | 40097.3701 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458N040097.21875 | X7E458N0 | X7E458M9 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40097.2188 | 40097.3701 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458N140097.21875 | X7E458N1 | X7E458M9 | Child | FALSE | HYTS-APD 1 500KV W | 40097.2188 | 40097.3701 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458N240097.21875 | X7E458N2 | X7E458M9 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40097.2188 | 40097.3701 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1027295140097.2270833333 | 10272951 |  | Parent | FALSE | NO.2 220KV BUS AT CBTS | 40097.2271 | 40097.5819 | DAILY | 00359379 | SPIMAINT | O/Haul 220KV BUS AT CBTS | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E458M940098.2194444445 | X7E458M9 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40098.2194 | 40098.3694 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458N040098.2194444445 | X7E458N0 | X7E458M9 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40098.2194 | 40098.3694 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458N140098.2194444445 | X7E458N1 | X7E458M9 | Child | FALSE | HYTS-APD 1 500KV W | 40098.2194 | 40098.3694 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458N240098.2194444445 | X7E458N2 | X7E458M9 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40098.2194 | 40098.3694 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029409840098.25 | 10294098 |  | Parent | FALSE | A4 515/230KV TRANS BANK AT HWTS | 40098.25 | 40102.6222 | CONT | 00337582 | SPIMAINT | Condition Monitoring Metro Trans 3day Valley Area | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X50858CZ40098.2534722222 | X50858CZ |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 40098.2535 | 40100.4653 | CONT | 00329879 | SPICAPX | Reconfigure No4 66kv Cap Bk CB and conn's & Test | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031844840098.3541666667 | 10318448 |  | Parent | FALSE | JLGA NO.4 UNIT TRANS DISC CB AT JLGA | 40098.3542 | 40105.3021 | CONT | [12 empty] | 0
_1029177740099.2305555556 | 10291777 |  | Parent | FALSE | NO.2 500KV BUS AT SYTS | 40099.2306 | 40102.6368 | CONT | 00001390 | SPIMAINT | O/Haul NO.2 500KV BUS AT SYTS | SPIPOWER |  |  | Bus | Western | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1031780440099.2513888889 | 10317804 |  | Parent | TRUE | NO.1 220KV BUS AT EPSY | 40099.2514 | 40099.6521 | REPDAILY | 00357773 | SPIMAINT | Out W/O No1 220kV Bus for mods to ABB ROIs | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031780640099.2513888889 | 10317806 | 10317804 | Child | FALSE | MBTS-EPS 2 220KV N | 40099.2514 | 40099.6521 | REPDAILY | 00055381 | SPIMAINT | Rebate W/O MBTS 2 Line during No1 220kV Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1010344640099.2555555556 | 10103446 |  | Parent | FALSE | C STH 22KV BUS AT RTS | 40099.2556 | 40099.5889 | DAILY | 00007359 | SPIMAINT | O/HAUL - 66kv or 22kv Outdoor Bus (Generic) | SPIPOWER |  |  | Bus | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1029137340099.2715277778 | 10291373 |  | Parent | FALSE | NO.1 66KV BUS AT GTS | 40099.2715 | 40099.6639 | DAILY | 00002835 | SPIMAINT | O/Haul NO.1 66KV BUS AT GTS | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031852640099.48125 | 10318526 |  | Parent | FALSE | W1 GTG/HWPS NO.2 LINE 220KV CB W1 GTG SIDE ISOL AT YPS | 40099.4812 | 40100.2861 | CONT | [12 empty] | 0
_1031858540099.9256944445 | 10318585 |  | Parent | FALSE | NO.7 GEN TRANS LINE AT HWPS | 40099.9257 | 40104.2424 | CONT | 00356085 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E458N340100.2229166667 | X7E458N3 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40100.2229 | 40100.75 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458N440100.2229166667 | X7E458N4 | X7E458N3 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40100.2229 | 40100.75 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458N540100.2229166667 | X7E458N5 | X7E458N3 | Child | FALSE | HYTS-APD 1 500KV W | 40100.2229 | 40100.75 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458N640100.2229166667 | X7E458N6 | X7E458N3 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40100.2229 | 40100.75 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031825340100.2430555556 | 10318253 |  | Parent | FALSE | NO.1 66KV BUS EXTENSION AT ERTS | 40100.2431 | 40100.6458 | DAILY | 00004382 | DBPROX | VSCAP to Jemena (UED) | DISTCO |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031780440100.2506944445 | 10317804 |  | Parent | TRUE | NO.1 220KV BUS AT EPSY | 40100.2507 | 40100.6528 | REPDAILY | 00357773 | SPIMAINT | Out W/O No1 220kV Bus for mods to ABB ROIs | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031780640100.2506944445 | 10317806 | 10317804 | Child | FALSE | MBTS-EPS 2 220KV N | 40100.2507 | 40100.6528 | REPDAILY | 00055381 | SPIMAINT | Rebate W/O MBTS 2 Line during No1 220kV Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1029064440100.2611111111 | 10290644 |  | Parent | TRUE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 40100.2611 | 40100.5972 | DAILY | 00007399 | SPIMAINT | Overhaul Cap Bank & E/Switch | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029252440100.2611111111 | 10292524 | 10290644 | Child | FALSE | NO.2B 66KV CAPACITOR BANK CB AT RWTS | 40100.2611 | 40100.5972 | DAILY | [12 empty] | 0
_1029272340100.2611111111 | 10292723 | 10290644 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 40100.2611 | 40100.5972 | DAILY | 00331179 | SPIMAINT | O/Haul NO.2B 66KV CAPACITOR BANK AT RWTS | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029785940100.2861111111 | 10297859 |  | Parent | FALSE | EX - W1 GTG/HWPS NO.2 LINE 220KV CB CT R/PH AT YPS | 40100.2861 | 40100.6139 | DAILY | [12 empty] | 0
_X50858DB40100.4597222222 | X50858DB |  | Parent | FALSE | NO.4 66KV BUS AT GTS | 40100.4597 | 40100.4757 | DAILY | 00002838 | SPICAPX | SOR - De energisation of No4 66kv Bus | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031858240100.5972222222 | 10318582 |  | Parent | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 40100.5972 | 40100.7312 | CONT | 00331179 | FORCED | HVS for No 2B 66 kV Cap Bank CB Non-availability | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031780740101.25 | 10317807 |  | Parent | TRUE | NO.2 220KV BUS AT EPSY | 40101.25 | 40101.6514 | REPDAILY | 00357774 | SPIMAINT | Out W/O No2 220kV Bus for mods to ABB ROIs | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031780840101.25 | 10317808 | 10317807 | Child | FALSE | MBTS-EPS 1 220KV N | 40101.25 | 40101.6514 | REPDAILY | 00055380 | SPIMAINT | Rebate W/O MBTS 2 Line during No1 220kV Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1029784140101.2673611111 | 10297841 |  | Parent | FALSE | NO.7 GEN TRANS 220KV CB CT R/PH AT HWPS | 40101.2674 | 40101.359 | DAILY | [12 empty] | 0
_Z73058M840101.4104166667 | Z73058M8 |  | Parent | FALSE | B3 220/66KV TRANS AT SMTS | 40101.4104 | 40101.55 | DAILY | 00366622 | DB_AUG | B3 TRANS outage | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X7E458N740102.2201388889 | X7E458N7 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40102.2201 | 40102.7132 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458N840102.2201388889 | X7E458N8 | X7E458N7 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40102.2201 | 40102.7132 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458N940102.2201388889 | X7E458N9 | X7E458N7 | Child | FALSE | HYTS-APD 1 500KV W | 40102.2201 | 40102.7132 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458O040102.2201388889 | X7E458O0 | X7E458N7 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40102.2201 | 40102.7132 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029417640102.2506944445 | 10294176 |  | Parent | FALSE | A1 TRANS/HWTS NO.4 LINE 500KV CB AT CBTS | 40102.2507 | 40102.5222 | DAILY | [12 empty] | 0
_1031780740102.2548611111 | 10317807 |  | Parent | TRUE | NO.2 220KV BUS AT EPSY | 40102.2549 | 40102.4833 | REPDAILY | 00357774 | SPIMAINT | Out W/O No2 220kV Bus for mods to ABB ROIs | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031780840102.2548611111 | 10317808 | 10317807 | Child | FALSE | MBTS-EPS 1 220KV N | 40102.2549 | 40102.4833 | REPDAILY | 00055380 | SPIMAINT | Rebate W/O MBTS 2 Line during No1 220kV Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X70658P240103.2083333333 | X70658P2 |  | Parent | FALSE | NO.3 220KV BUS AT KTS | 40103.2083 | 40103.6458 | CONT | 00001171 | SPICAPX | bipod connections - no.3 bus to gts 1 line | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031817640103.25 | 10318176 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 40103.25 | 40103.4542 | DAILY | 00337579 | SPIMAINT | TOP UP OIL IN WHITE PHASE BUSHHING 220kV TX No 3 | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X87058J540103.2548611111 | X87058J5 |  | Parent | FALSE | HWPS NO.1 220KV LINE AT ROTS | 40103.2549 | 40103.6854 | REPDAILY | 00023990 | SPICAPX | insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X84358A140103.2673611111 | X84358A1 |  | Parent | FALSE | EX - 66KV CAPACITOR BANK AT TGTS | 40103.2674 | 40104.5 | CONT | 00003104 | SPICAPX | Replace Cap Cans TGTS 66kv Cap Bank - ABB | SPIPOWER | X843 | X843 - (RWTS,TGTS,TTS) REPLACE AGEING 66KV CAP BANKS | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1028262740103.26875 | 10282627 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 40103.2688 | 40103.691 | DAILY | 00002830 | SPIMAINT | B4 Trans oil leaks | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027294940104.2131944445 | 10272949 |  | Parent | TRUE | NO.1 220KV BUS AT CBTS | 40104.2132 | 40104.6139 | DAILY | 00359378 | SPIMAINT | O/Haul 220KV BUS AT CBTS | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031781640104.2131944445 | 10317816 | 10272949 | Child | FALSE | B1 220/66KV TRANS AT CBTS | 40104.2132 | 40104.6139 | DAILY | 00353076 | SPIMAINT | TRANS REBATE FOR BUS OUTAGE | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1029137540104.2340277778 | 10291375 |  | Parent | TRUE | NO.2 66KV BUS AT GTS | 40104.234 | 40104.7354 | DAILY | 00002836 | SPIMAINT | O/Haul NO.2 66KV BUS AT GTS | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031781140104.2340277778 | 10317811 | 10291375 | Child | FALSE | B1 220/66KV TRANS AT GTS | 40104.234 | 40104.7354 | DAILY | 00002828 | SPIMAINT | Perf calc W/O B1 Trans during No2 66kV Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X87058J540104.2534722222 | X87058J5 |  | Parent | FALSE | HWPS NO.1 220KV LINE AT ROTS | 40104.2535 | 40104.6597 | REPDAILY | 00023990 | SPICAPX | insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E4580440105.21875 | X7E45804 | X7E458O1 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40105.2188 | 40105.7021 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E458O140105.21875 | X7E458O1 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40105.2188 | 40105.7021 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458O240105.21875 | X7E458O2 | X7E458O1 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40105.2188 | 40105.7021 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458O340105.21875 | X7E458O3 | X7E458O1 | Child | FALSE | HYTS-APD 1 500KV W | 40105.2188 | 40105.7021 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029159840105.2277777778 | 10291598 |  | Parent | FALSE | SYN/COND AT BLTS | 40105.2278 | 40107.5285 | CONT | 00002547 | SPIMAINT | 3 Monthly O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031872440105.2291666667 | 10318724 | X81158A5 | Child | FALSE | EX - H2 TRANS 330KV CB CT R/PH AT SMTS | 40105.2292 | 40107.6458 | CONT | [12 empty] | 0
_1031942040105.2291666667 | 10319420 | X81158A5 | Child | FALSE | H2 330/220KV TRANS BANK AT SMTS | 40105.2292 | 40107.6458 | CONT | 00026102 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X81158A540105.2291666667 | X81158A5 |  | Parent | TRUE | EX - H2 TRANS 330KV CB CT R/PH AT SMTS | 40105.2292 | 40107.6458 | CONT | [12 empty] | 0
_1031852240105.2701388889 | 10318522 | X87058K6 | Child | FALSE | TSTS-TTS 220KV WT | 40105.2701 | 40105.6417 | REPDAILY | 00022783 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029411440105.2868055556 | 10294114 |  | Parent | FALSE | B2 220/66KV TRANS AT TGTS | 40105.2868 | 40107.4903 | CONT | 00003127 | SPIMAINT | Condition Monitoring Country Trans 2day North Area | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031858340105.3069444445 | 10318583 |  | Parent | FALSE | JLGA NO.1 UNIT TRANS DISC CB AT JLGA | 40105.3069 | 40115.4097 | CONT | [12 empty] | 0
_V96558A440105.3618055556 | V96558A4 |  | Parent | FALSE | ROTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 40105.3618 | 40130.5139 | CONT | [12 empty] | 0
_1031871340105.4847222222 | 10318713 |  | Parent | FALSE | EX - NO.2 66KV BUS VT AT GTS | 40105.4847 | 40109.6056 | CONT | [12 empty] | 0
_1031793340105.5048611111 | 10317933 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 40105.5049 | 40105.5389 | DAILY | [12 empty] | 0
_1031793240105.5444444444 | 10317932 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT WOTS | 40105.5444 | 40105.5708 | DAILY | [12 empty] | 0
_1031872040105.7430555556 | 10318720 |  | Parent | FALSE | SYN/COND AT TSTS | 40105.7431 | 40105.8285 | CONT | 00007626 | FORCED | TSTS Synch Cond Bearing Oil Coolers | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031850040106.1145833333 | 10318500 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40106.1146 | 40106.8139 | DAILY | 00319999 | APDALCOA | Outage for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_V96558A140106.2708333333 | V96558A1 |  | Parent | FALSE | HWTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 40106.2708 | 40123.5417 | CONT | [12 empty] | 0
_1031852240106.2756944445 | 10318522 | X87058K6 | Child | FALSE | TSTS-TTS 220KV WT | 40106.2757 | 40106.6507 | REPDAILY | 00022783 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029407540106.4409722222 | 10294075 |  | Parent | FALSE | B1 220/66KV TRANS (HOT SPARE) AT MBTS | 40106.441 | 40109.5771 | CONT | 00360627 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER | NORMALLY OPEN | 0
_1031849840107.1152777778 | 10318498 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40107.1153 | 40107.7958 | DAILY | 00319998 | APDALCOA | Outage for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X7E4580840107.2215277778 | X7E45808 | X7E458O5 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40107.2215 | 40107.6806 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E458O540107.2215277778 | X7E458O5 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40107.2215 | 40107.6806 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458O640107.2215277778 | X7E458O6 | X7E458O5 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40107.2215 | 40107.6806 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029020640107.2506944445 | 10290206 | 10290961 | Child | FALSE | CBTS NO.1 66KV FDR AT FTS | 40107.2507 | 40107.6521 | DAILY | 00012275 | SPIMAINT | O/Haul ERTS 1 CB Fdr Side Isol & SDs at FTS | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029096140107.2506944445 | 10290961 |  | Parent | TRUE | CBTS NO.1 66KV FDR CB AT FTS | 40107.2507 | 40107.6521 | DAILY | [12 empty] | 0
_1028961640107.2666666667 | 10289616 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT KGTS | 40107.2667 | 40108.5194 | CONT | 00017270 | SPIMAINT | O/Haul SVC AT KGTS | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031852240107.2979166667 | 10318522 | X87058K6 | Child | FALSE | TSTS-TTS 220KV WT | 40107.2979 | 40107.75 | REPDAILY | 00022783 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031793440107.3402777778 | 10317934 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.1 BUS CB AT DDTS | 40107.3403 | 40107.3799 | DAILY | [12 empty] | 0
_1031874140107.9416666667 | 10318741 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 40107.9417 | 40111.8799 | CONT | 00356082 | GENCO | Unit 4 Gen-Co Work | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029147340108.23125 | 10291473 |  | Parent | FALSE | SYN/COND AT FBTS | 40108.2312 | 40109.6042 | CONT | 00002697 | SPIMAINT | 3 Monthly O/HAUL - FBTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031942740108.2361111111 | 10319427 | X81158A6 | Child | FALSE | EX - H1 TRANS 330KV CB CT R/PH AT SMTS | 40108.2361 | 40110.4924 | CONT | [12 empty] | 0
_1031951940108.2361111111 | 10319519 | X81158A6 | Child | FALSE | H1 330/220KV TRANS BANK AT SMTS | 40108.2361 | 40110.4924 | CONT | 00026101 | SPICAPX | capture outage costs | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X81158A640108.2361111111 | X81158A6 |  | Parent | TRUE | EX - H1 TRANS 330KV CB CT R/PH AT SMTS | 40108.2361 | 40110.4924 | CONT | [12 empty] | 0
_X70658P940108.2416666667 | X70658P9 |  | Parent | FALSE | GTS NO.1 220KV LINE NO.3 BUS CB AT KTS | 40108.2417 | 40108.366 | DAILY | [12 empty] | 0
_1029020440108.25 | 10290204 | 10290963 | Child | FALSE | CBTS NO.2 66KV FDR AT FTS | 40108.25 | 40108.6021 | DAILY | 00012274 | SPIMAINT | O/Haul CBTS 2 CB Fdr Side Isol & SDs at FTS | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029096340108.25 | 10290963 |  | Parent | TRUE | CBTS NO.2 66KV FDR CB AT FTS | 40108.25 | 40108.6021 | DAILY | [12 empty] | 0
_1029423440108.2631944444 | 10294234 |  | Parent | FALSE | B2 220/66KV TRANS AT MBTS | 40108.2632 | 40108.6438 | REPDAILY | 00362372 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031882140108.3229166667 | 10318821 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 40108.3229 | 40108.5417 | DAILY | [12 empty] | 0
_1031877240108.3333333333 | 10318772 |  | Parent | FALSE | EX - NO.1 66KV BUS 'B' VT AT MWTS | 40108.3333 | 40108.5674 | DAILY | [12 empty] | 0
_1031793540108.3347222222 | 10317935 |  | Parent | FALSE | BATS 220KV LINE NO.1 BUS CB AT BETS | 40108.3347 | 40108.3812 | DAILY | [12 empty] | 0
_1031793640108.3881944444 | 10317936 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT BETS | 40108.3882 | 40108.4132 | DAILY | [12 empty] | 0
_X7E458O940109.2236111111 | X7E458O9 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40109.2236 | 40109.7111 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458P040109.2236111111 | X7E458P0 | X7E458O9 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40109.2236 | 40109.7111 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458P140109.2236111111 | X7E458P1 | X7E458O9 | Child | FALSE | HYTS-APD 1 500KV W | 40109.2236 | 40109.7111 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458P240109.2236111111 | X7E458P2 | X7E458O9 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40109.2236 | 40109.7111 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031829940109.2493055556 | 10318299 |  | Parent | TRUE | L3 TRANS 22KV CB AT RWTS | 40109.2493 | 40109.5646 | DAILY | [12 empty] | 0
_1031833640109.2493055556 | 10318336 | 10318299 | Child | FALSE | L3 220/22KV TRANS BANK AT RWTS | 40109.2493 | 40109.5646 | DAILY | 00007452 | SPIMAINT | Trans Rebate | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029423440109.25625 | 10294234 |  | Parent | FALSE | B2 220/66KV TRANS AT MBTS | 40109.2562 | 40109.5771 | REPDAILY | 00362372 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031852240109.3013888889 | 10318522 | X87058K6 | Child | FALSE | TSTS-TTS 220KV WT | 40109.3014 | 40109.3299 | REPDAILY | 00022783 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031872840109.55625 | 10318728 |  | Parent | TRUE | NO.2 66KV BUS AT GTS | 40109.5563 | 40109.6056 | DAILY | 00002836 | SPIMAINT | Out W/O No2 66kV Bus de-energ for bus VT commiss | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031872940109.55625 | 10318729 | 10318728 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT GTS | 40109.5563 | 40109.6056 | DAILY | 00350421 | SPIMAINT | Rebate W/O No1 66 Cap bk during No2 66 bus outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031873040109.55625 | 10318730 | 10318728 | Child | FALSE | B1 220/66KV TRANS AT GTS | 40109.5563 | 40109.6056 | DAILY | 00002828 | SPIMAINT | Perf calc W/O B1 Trans during No2 66 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031893840110.21875 | 10318938 |  | Parent | FALSE | SYN/COND AT TSTS | 40110.2188 | 40110.6868 | DAILY | 00007626 | SPIMAINT | Syncon Temperature Alarm | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z71958A340110.2333333333 | Z71958A3 |  | Parent | TRUE | NO.2 66KV BUS AT CBTS | 40110.2333 | 40110.7944 | DAILY | 00359471 | DB_AUG | CONNECT ISOL TO 66KV BUS & PRESSURE TEST CB | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z71958A440110.2333333333 | Z71958A4 | Z71958A3 | Child | FALSE | B2 220/66KV TRANS AT CBTS | 40110.2333 | 40110.7944 | DAILY | 00353077 | VEN_AUG | TRANS REBATE FOR BUS OUTAGE | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X7E558D040110.25 | X7E558D0 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40110.25 | 40110.6778 | REPDAILY | 00022640 | SPICAPX | install opgw from twr 106 and SYTS rack structure | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z82558B240110.2555555556 | Z82558B2 |  | Parent | FALSE | SVTS NO.1 220KV LINE AT ROTS | 40110.2556 | 40110.6465 | DAILY | 00350027 | VEN_AUG | REPLACE CROSS ARMS | SPIPOWER | Z825 | Z825 - (ROTS-SVTS) 220KV UPGRADE TO 82 DEGREE C | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X84358A240110.2833333333 | X84358A2 |  | Parent | FALSE | EX - NO.4A 66KV CAPACITOR BANK AT TTS | 40110.2833 | 40111.5111 | CONT | 00001486 | SPICAPX | Replace Cap Cans TTS No.4A 66kv Cap Bank - ABB | SPIPOWER | X843 | X843 - (RWTS,TGTS,TTS) REPLACE AGEING 66KV CAP BANKS | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z71958A940110.7083333333 | Z71958A9 |  | Parent | FALSE | B2 TRANS 66KV CB AT CBTS | 40110.7083 | 40124.2951 | CONT | [12 empty] | 0
_X7E558D040111.2506944445 | X7E558D0 |  | Parent | FALSE | SMTS-SYTS 1 500KV WT | 40111.2507 | 40111.3194 | REPDAILY | 00022640 | SPICAPX | install opgw from twr 106 and SYTS rack structure | SPIPOWER | X7E5 | X7E5 - (SYTS,SMTS) INSTALL & COMMISSION DIGITAL COMMS | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z82558B340111.2506944445 | Z82558B3 |  | Parent | FALSE | SVTS NO.2 220KV LINE AT ROTS | 40111.2507 | 40111.6403 | DAILY | 00023968 | VEN_AUG | REPLACE CROSS ARMS | SPIPOWER | Z825 | Z825 - (ROTS-SVTS) 220KV UPGRADE TO 82 DEGREE C | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031912640112.0104166667 | 10319126 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 40112.0104 | 40113.7021 | CONT | 00356081 | GENCO | GenCo work | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031931440112.2305555556 | 10319314 | X81158A7 | Child | FALSE | EX - F2 TRANS 330KV CB CT R/PH AT SMTS | 40112.2306 | 40114.6236 | CONT | [12 empty] | 0
_1031951540112.2305555556 | 10319515 | X81158A7 | Child | FALSE | F2 500/330KV TRANS BANK AT SMTS | 40112.2306 | 40114.6236 | CONT | 00026099 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X81158A740112.2305555556 | X81158A7 |  | Parent | TRUE | EX - F2 TRANS 330KV CB CT R/PH AT SMTS | 40112.2306 | 40114.6236 | CONT | [12 empty] | 0
_1031926940112.8284722222 | 10319269 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 40112.8285 | 40114.9472 | CONT | 00356086 | GENCO | GenCo work | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E458P340113.2118055556 | X7E458P3 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40113.2118 | 40113.6729 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458P440113.2118055556 | X7E458P4 | X7E458P3 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40113.2118 | 40113.6729 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458P540113.2118055556 | X7E458P5 | X7E458P3 | Child | FALSE | HYTS-APD 1 500KV W | 40113.2118 | 40113.6729 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458P640113.2118055556 | X7E458P6 | X7E458P3 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40113.2118 | 40113.6729 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029572840113.2506944445 | 10295728 |  | Parent | TRUE | NO.2 220KV BUS AT TBTS | 40113.2507 | 40113.5972 | DAILY | 00004906 | SPIMAINT | O/Haul NO.2 220KV BUS AT TBTS | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029995640113.2506944445 | 10299956 | 10295728 | Child | FALSE | CBTS NO.2 220KV LINE AT TBTS | 40113.2507 | 40113.5972 | DAILY | 00018364 | SPIMAINT | Rebate Line outage for Bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031860340113.2506944445 | 10318603 | 10295728 | Child | FALSE | JLA NO.2 220KV LINE AT TBTS | 40113.2507 | 40113.5972 | DAILY | 00026919 | SPIMAINT | Rebate line outage for bus | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031831540113.2916666667 | 10318315 |  | Parent | TRUE | NO.1 220KV BUS AT DDTS | 40113.2917 | 40113.6069 | DAILY | 00003976 | SPIMAINT | Out W/O No1 220 bus for #1 Cap Bk CB BS ROI mods | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031831840113.2916666667 | 10318318 | 10318315 | Child | FALSE | DDTS-GNTS 1 220KV NW | 40113.2917 | 40113.6069 | DAILY | 00060184 | SPIMAINT | Rebate W/O GNTS 1 Line during No1 220 bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031831940113.2916666667 | 10318319 | 10318315 | Child | FALSE | H1 330/220KV TRANS BANK AT DDTS | 40113.2917 | 40113.6069 | DAILY | 00337558 | SPIMAINT | Rebate W/O No1 trans during No1 220 bus outage | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031832140113.2916666667 | 10318321 | 10318315 | Child | FALSE | MBTS-DDTS 1 220KV NW | 40113.2917 | 40113.6069 | DAILY | 00060187 | SPIMAINT | Rebate W/O MBTS 1 Line during No1 220 bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031832240113.2916666667 | 10318322 | 10318315 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 40113.2917 | 40113.6069 | DAILY | 00351939 | SPIMAINT | Rebate W/O 220 Cap Bank during 220 Bus outage | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1031650340114.2840277778 | 10316503 |  | Parent | FALSE | APD NO.1/MLTS NO.1 LINE 500KV CB AT HYTS | 40114.284 | 40114.6035 | DAILY | [12 empty] | 0
_1031655340114.2875 | 10316553 |  | Parent | TRUE | 5-6 220KV BUS TIE CB NO.6 BUS SIDE ISOL AT HWPS | 40114.2875 | 40114.575 | DAILY | [12 empty] | 0
_1031656240114.2875 | 10316562 | 10316553 | Child | FALSE | YPS NO.1 220KV LINE AT HWPS | 40114.2875 | 40114.575 | DAILY | 00015795 | SPIMAINT | LINE REBATE FOR BUS OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031811840114.2875 | 10318118 | 10316553 | Child | FALSE | YPS NO.1 220KV LINE NO.6 BUS CB AT HWPS | 40114.2875 | 40114.575 | DAILY | [12 empty] | 0
_1029541740114.2930555556 | 10295417 |  | Parent | FALSE | JINDERA 330KV LINE NO.1 BUS CB AT WOTS | 40114.2931 | 40115.6361 | CONT | [12 empty] | 0
_1031921840114.3270833333 | 10319218 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK CB AT LY | 40114.3271 | 40114.5417 | DAILY | [12 empty] | 0
_1031756740114.8791666667 | 10317567 | X71158A6 | Child | FALSE | NO.1 BUS 220KV E/SW AT HWPS | 40114.8792 | 40117.7646 | DAILY | [12 empty] | 0
_X71158A540114.8791666667 | X71158A5 |  | Parent | TRUE | NO.1 220KV BUS AT HWPS | 40114.8792 | 40117.7646 | CONT | 00009658 | SPICAPX | BUS 1 OUTAGE | SPIPOWER | X711 | X711 - (HWPS) REDEVELOP 220KV SWYD - STAGE 1 | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X71158B440114.8791666667 | X71158B4 | X71158A5 | Child | FALSE | JLTS NO.1 220KV LINE AT HWPS | 40114.8792 | 40117.7646 | CONT | 00015784 | SPICAPX | LINE REBATE FOR BUS OUTAGE | SPIPOWER | X711 | X711 - (HWPS) REDEVELOP 220KV SWYD - STAGE 1 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031938640114.9902777778 | 10319386 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 40114.9903 | 40118.4404 | CONT | [12 empty] | 0
_1031650540115.2541666667 | 10316505 |  | Parent | FALSE | APD NO.2/MLTS NO.2 LINE 500KV CB AT HYTS | 40115.2542 | 40115.5903 | DAILY | [12 empty] | 0
_X70658Q040115.3520833333 | X70658Q0 |  | Parent | FALSE | B3 220/66KV TRANS AT KTS | 40115.3521 | 40115.625 | DAILY | 00350448 | SPICAPX | B3 TRANS REQUIRED D-ENERGSD TO ERECT BLST WALL | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031932540115.4104166667 | 10319325 |  | Parent | FALSE | JLGA NO.2 UNIT TRANS DISC CB AT JLGA | 40115.4104 | 40135.3889 | CONT | [12 empty] | 0
_1031942340115.7208333333 | 10319423 |  | Parent | TRUE | NO.1 66KV BUS AT RTS | 40115.7208 | 40115.7979 | DAILY | 00022323 | FAULT | No1 66kV Bus trip on CB Fail protection | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031942640115.7208333333 | 10319426 | 10319423 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RTS | 40115.7208 | 40115.7979 | DAILY | 00007279 | FAULT | No1 66kV Cap Bank unavailable while No1 Bus out. | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031943140115.7208333333 | 10319431 |  | Parent | FALSE | B1 220/66KV TRANS AT RTS | 40115.7208 | 40115.7979 | DAILY | 00007329 | FAULT | Rebate B1 220/66KV Trans Trip with No1 66KV Bus | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030238340116.275 | 10302383 |  | Parent | FALSE | DDTS 330KV LINE NO.2 BUS CB AT WOTS | 40116.275 | 40116.609 | DAILY | [12 empty] | 0
_X84358A340117.2451388889 | X84358A3 |  | Parent | TRUE | EX - NO.2A 66KV CAPACITOR BANK AT RWTS | 40117.2451 | 40118.5965 | CONT | 00007399 | SPICAPX | Replace Cap Cans 66kv Cap Bank - ABB | SPIPOWER | X843 | X843 - (RWTS,TGTS,TTS) REPLACE AGEING 66KV CAP BANKS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X84358A440117.2451388889 | X84358A4 | X84358A3 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 40117.2451 | 40118.5965 | CONT | 00331179 | SPICAPX | REBATE FOR CAP BANK OUTAGE | SPIPOWER | X843 | X843 - (RWTS,TGTS,TTS) REPLACE AGEING 66KV CAP BANKS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031871540117.2708333333 | 10318715 |  | Parent | FALSE | B4 220/66KV TRANS AT GTS | 40117.2708 | 40118.6611 | CONT | 00002830 | SPIMAINT | B4 Trans oil leaks | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031944940117.4638888889 | 10319449 |  | Parent | FALSE | F2 TRANS NON AUTO 500KV CB AT SMTS | 40117.4639 | 40117.5646 | CONT | [12 empty] | 0
_1031944040117.7465277778 | 10319440 |  | Parent | TRUE | NO.1 66KV BUS AT RTS | 40117.7465 | 40117.8861 | DAILY | 00022323 | SPIMAINT | Bus outage to repaire CW bus side isols | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031944440117.7465277778 | 10319444 | 10319440 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT RTS | 40117.7465 | 40117.8861 | DAILY | 00007279 | SPIMAINT | Rebate Cap Bank for Bus outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031944540117.7465277778 | 10319445 | 10319440 | Child | FALSE | B1 220/66KV TRANS AT RTS | 40117.7465 | 40117.8861 | DAILY | 00007329 | SPIMAINT | Rebate Trans for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z71958B840118.2555555556 | Z71958B8 |  | Parent | FALSE | B1 220/66KV TRANS AT CBTS | 40118.2556 | 40118.5264 | DAILY | 00353076 | DB_AUG | Install termination gantry for Future B2 66 conn | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X87058K240118.2631944444 | X87058K2 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 40118.2632 | 40118.6764 | DAILY | 00022702 | SPICAPX | KTS-GTS 1 Line insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031937240118.2729166667 | 10319372 |  | Parent | FALSE | BWN/CBTS 66KV FDR AT ERTS | 40118.2729 | 40118.5833 | DAILY | 00012528 | DBPROX | Permit issue on BWN 66KV FDR for DOC | DISTCO |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031561940118.2958333333 | 10315619 |  | Parent | TRUE | 2-3 22KV BUS TIE NO.2 BUS SIDE ISOL AT RWTS | 40118.2958 | 40118.5993 | DAILY | [12 empty] | 0
_1031778740118.2958333333 | 10317787 | 10315619 | Child | FALSE | NO.2 22KV CAPACITOR BANK AT RWTS | 40118.2958 | 40118.5993 | DAILY | 00357000 | SPIMAINT | REBATES FOR BUS OUTAGE | SPIPOWER |  |  | Capacitors | Eastern | 22 | CONNECTION ASSET | EXCLUDED |  | 0
_1031778840118.2958333333 | 10317788 | 10315619 | Child | FALSE | L3 220/22KV TRANS BANK AT RWTS | 40118.2958 | 40118.5993 | DAILY | 00007452 | SPIMAINT | REBATES FOR BUS OUTAGE | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031945840118.5 | 10319458 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 40118.5 | 40123.5299 | CONT | 00016424 | GENCO | Power Station Requirements | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X87058K340119.2569444444 | X87058K3 |  | Parent | FALSE | KTS -GTS 3 220KV WY | 40119.2569 | 40119.6424 | DAILY | 00022709 | SPICAPX | KTS-GTS 3 Line insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031945940119.3298611111 | 10319459 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 40119.3299 | 40122.5563 | CONT | 00356081 | GENCO | Isolated for power station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031949540121.0666666667 | 10319495 |  | Parent | FALSE | CBTS NO.4 500KV LINE NO.3 BUS CB AT HWTS | 40121.0667 | 40121.0715 | CONT | [12 empty] | 0
_1029063340121.2430555556 | 10290633 |  | Parent | FALSE | U1 66/22KV TRANS AT RWTS | 40121.2431 | 40121.5917 | DAILY | 00007456 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Connection Transformers | Eastern | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029868740121.2638888889 | 10298687 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 40121.2639 | 40122.6785 | CONT | 00016040 | SPIMAINT | No2 Trans GRP oil leaks | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031973240121.2715277778 | 10319732 | X81158A8 | Child | FALSE | WMTS-FBTS 2 220KV WY | 40121.2715 | 40123.566 | CONT | 00022787 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X81158A840121.2715277778 | X81158A8 |  | Parent | TRUE | EX - WMTS NO.2 220KV LINE CB CT R/PH AT FBTS | 40121.2715 | 40123.566 | CONT | [12 empty] | 0
_1031948540121.2756944445 | 10319485 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 40121.2757 | 40121.5188 | DAILY | 00027386 | APDALCOA | APD No1 line de-energised for work by Alcoa | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1031932340121.2986111111 | 10319323 |  | Parent | FALSE | MSS NO.1 330KV LINE AT DDTS | 40121.2986 | 40121.6181 | DAILY | 00012357 | TRANSGRD | Outage requested by Transgrid for work at MSS | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X71158C840121.5159722222 | X71158C8 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 40121.516 | 40144.6424 | CONT | [12 empty] | 0
_1031932440122.2951388889 | 10319324 |  | Parent | FALSE | MSS NO.2 330KV LINE AT DDTS | 40122.2951 | 40122.5278 | DAILY | 00012358 | TRANSGRD | Outage requested by Transgrid for work at MSS | TRANSGRD |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1031940840122.3076388889 | 10319408 |  | Parent | FALSE | 22KV/415V S/S TRANS AT FTS | 40122.3076 | 40122.3806 | DAILY | 00004393 | DBPROX | VSCAP to Jemena UED | DISTCO |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1031948640122.3305555556 | 10319486 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 40122.3306 | 40122.4632 | DAILY | 00060938 | APDALCOA | APD No2 Line de-energised for work by Alcoa | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X7E458P740123.1715277778 | X7E458P7 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40123.1715 | 40123.691 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458P840123.1715277778 | X7E458P8 | X7E458P7 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40123.1715 | 40123.691 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458P940123.1715277778 | X7E458P9 | X7E458P7 | Child | FALSE | HYTS-APD 1 500KV W | 40123.1715 | 40123.691 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458Q040123.1715277778 | X7E458Q0 | X7E458P7 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40123.1715 | 40123.691 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029153640123.2395833333 | 10291536 |  | Parent | FALSE | BLTS 220KV LINE CB BUS SIDE ROI AT FBTS | 40123.2396 | 40123.5472 | DAILY | [12 empty] | 0
_1028825140123.2548611111 | 10288251 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT RTS | 40123.2549 | 40123.5472 | DAILY | 00055373 | SPIMAINT | O/H CAP BANK & EARTH SWITCH | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031957740123.2958333333 | 10319577 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 40123.2958 | 40128.7292 | CONT | [12 empty] | 0
_1028970840124.2305555556 | 10289708 |  | Parent | TRUE | CBTS NO.4 500KV LINE AT HWTS | 40124.2306 | 40124.575 | DAILY | 00016240 | SPIMAINT | Overhaul ROTS No 4 500 Kv Line at HWTS | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029770640124.2305555556 | 10297706 | 10289708 | Child | FALSE | S037 HWTS-CBTS 4 500KV | 40124.2306 | 40124.575 | DAILY | [12 empty] | 0
_1030109940124.2305555556 | 10301099 | 10289708 | Child | FALSE | LYPS NO.3 LINE/CBTS NO.4 LINE CB CBTS NO.4 LINE SIDE 500KV ROI AT HWTS | 40124.2306 | 40124.575 | DAILY | [12 empty] | 0
_Z71958A540124.25 | Z71958A5 |  | Parent | FALSE | B2 220/66KV TRANS AT CBTS | 40124.25 | 40124.9826 | DAILY | 00353077 | DB_AUG | COMMISSION NEW B2 TRANS 66KV CB | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1031973340124.25 | 10319733 | X81158A9 | Child | FALSE | FBTS-BLTS 220KV WY | 40124.25 | 40126.5292 | CONT | 00022666 | SPICAPX | BLTS LINE 220KV CB CT REPLACEMENT | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X81158A940124.25 | X81158A9 |  | Parent | TRUE | EX - BLTS 220KV LINE CB CT R/PH AT FBTS | 40124.25 | 40126.5292 | CONT | [12 empty] | 0
_1031960440124.9909722222 | 10319604 |  | Parent | FALSE | F2 TRANS NO.1 BUS 500KV CB AT SMTS | 40124.991 | 40125.4708 | DAILY | [12 empty] | 0
_X70658N440125.2138888889 | X70658N4 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40125.2139 | 40125.6132 | DAILY | 00001169 | SPICAPX | CUT BIPODS FROM No 1 BUS TO GTS No2 L 1B CB ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658N740125.2138888889 | X70658N7 | X70658N4 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40125.2139 | 40125.6132 | DAILY | 00119824 | SPICAPX | CAPTURE OUTAGE COSTS NO1 220KV BUS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X70658Q140125.2138888889 | X70658Q1 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 40125.2139 | 40131.2076 | CONT | 00015976 | SPICAPX | DECOMM GTS No.2 L No1 B CB, ROI, E/SW & CT's | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031956240125.2145833333 | 10319562 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 40125.2146 | 40125.6215 | DAILY | 00001147 | SPIMAINT | TOP UP 220KV BUSHINGS CHECKS ON TEMP INDICATOR | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028892540125.2625 | 10288925 |  | Parent | TRUE | NO.1 22KV BUS PROT AT RWTS | 40125.2625 | 40125.5542 | DAILY | [12 empty] | 0
_1031845940125.2625 | 10318459 | 10288925 | Child | FALSE | NO.1 22KV CAPACITOR BANK AT RWTS | 40125.2625 | 40125.5542 | DAILY | 00356999 | SPIMAINT | Rebate Capbank for Bus outage | SPIPOWER |  |  | Capacitors | Eastern | 22 | CONNECTION ASSET | EXCLUDED |  | 0
_1031961540125.5284722222 | 10319615 |  | Parent | TRUE | NO.3 66KV CAPACITOR BANK CB AT WMTS | 40125.5285 | 40125.5854 | DAILY | [12 empty] | 0
_1031973740125.5284722222 | 10319737 | 10319615 | Child | FALSE | NO.3 66KV CAPACITOR BANK AT WMTS | 40125.5285 | 40125.5854 | DAILY | 00003191 | FAULT | De energised CB for SF6 top up | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031865240126.1986111111 | 10318652 |  | Parent | FALSE | B2 220/66KV TRANS AT KTS | 40126.1986 | 40127.6694 | DAILY | 00001148 | SPIMAINT | top up b2 trans bushings at kts | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658N840126.1986111111 | X70658N8 |  | Parent | FALSE | NO.2 66KV BUS AT KTS | 40126.1986 | 40127.6694 | DAILY | 00001173 | SPICAPX | REMOVE No.1-2 66KV BUS TIE CB | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E458Q140126.2194444445 | X7E458Q1 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40126.2194 | 40126.7257 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458Q240126.2194444445 | X7E458Q2 | X7E458Q1 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40126.2194 | 40126.7257 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458Q340126.2194444445 | X7E458Q3 | X7E458Q1 | Child | FALSE | HYTS-APD 1 500KV W | 40126.2194 | 40126.7257 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458Q440126.2194444445 | X7E458Q4 | X7E458Q1 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40126.2194 | 40126.7257 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029208540126.2597222222 | 10292085 |  | Parent | TRUE | NO.1 66KV BUS AT GNTS | 40126.2597 | 40126.6951 | DAILY | 00000748 | SPIMAINT | O/Haul NO.1 66KV BUS AT GNTS | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031912940126.2597222222 | 10319129 | 10292085 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT GNTS | 40126.2597 | 40126.6951 | DAILY | 00329962 | SPIMAINT | Rebate W/O No1 Cap bk during No1 66kV Bus outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031913040126.2597222222 | 10319130 | 10292085 | Child | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 40126.2597 | 40126.6951 | DAILY | 00329970 | SPIMAINT | Perf calc W/O No1 Trans during No1 66kV Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031966840126.4430555556 | 10319668 |  | Parent | FALSE | A4 500/220KV TRANS BANK AT KTS | 40126.4431 | 40126.4694 | DAILY | 00026098 | FORCED | A4 Trans off loaded due to loss of cooling | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031964140126.5972222222 | 10319641 |  | Parent | FALSE | DDTS 330KV LINE NO.2 BUS CB AT WOTS | 40126.5972 | 40130.8208 | CONT | [12 empty] | 0
_X70658P340126.6694444444 | X70658P3 |  | Parent | FALSE | EX - 1-2 66KV BUS TIE CB AT KTS | 40126.6694 | 40133.2188 | CONT | [12 empty] | 0
_X7E958A040127.2548611111 | X7E958A0 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 40127.2549 | 40127.2778 | CONT | [12 empty] | 0
_1029208740127.2673611111 | 10292087 |  | Parent | TRUE | NO.2 66KV BUS AT GNTS | 40127.2674 | 40127.6271 | DAILY | 00000749 | SPIMAINT | O/Haul NO.2 66KV BUS AT GNTS | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031913240127.2673611111 | 10319132 | 10292087 | Child | FALSE | B2 220/66KV TRANS AT GNTS | 40127.2674 | 40127.6271 | DAILY | 00000743 | SPIMAINT | Perf calc W/O No2 Trans during no2 66kV Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028729740127.2930555556 | 10287297 |  | Parent | TRUE | WMTS NO.2 220KV LINE CB AT FBTS | 40127.2931 | 40127.575 | DAILY | [12 empty] | 0
_1029286140127.2930555556 | 10292861 | 10287297 | Child | FALSE | WMTS NO.2 220KV LINE AT FBTS | 40127.2931 | 40127.575 | CONT | 00017157 | SPIMAINT | INSPECT LINE AND CHECK SPILL GAP | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1029062140127.3076388889 | 10290621 |  | Parent | FALSE | SYN/COND AT TSTS | 40127.3076 | 40131.4576 | CONT | 00007626 | SPIMAINT | O/Haul Syn Con at TSTS | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z91358A140127.3222222222 | Z91358A1 |  | Parent | FALSE | EX - LGA NO.3 66KV FDR CB AT MWTS | 40127.3222 | 40127.7917 | DAILY | [12 empty] | 0
_1031967940127.4659722222 | 10319679 |  | Parent | FALSE | SMTS 500KV LINE NO.2 BUS CB BUS SIDE ROI AT KTS | 40127.466 | 40127.4674 | CONT | [12 empty] | 0
_X50858DA40127.5097222222 | X50858DA |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT GTS | 40127.5097 | 40130.5826 | CONT | 00350421 | SPICAPX | Rewire and Pre commission No1 66kv Cap Bk CB | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031655940128.2729166667 | 10316559 |  | Parent | TRUE | B2 220/66KV TRANS 66KV CB TRANS SIDE ISOL AT MWTS | 40128.2729 | 40128.6278 | DAILY | [12 empty] | 0
_1031845240128.2729166667 | 10318452 | 10316559 | Child | FALSE | B2 220/66KV TRANS COOLING FANS AT MWTS | 40128.2729 | 40128.6278 | DAILY | [12 empty] | 0
_1031866240128.2729166667 | 10318662 | 10316559 | Child | FALSE | JLTS-MWTS 2 220KV G | 40128.2729 | 40128.6278 | DAILY | 00020469 | SPIMAINT | REBATE FOR TRANS 2 CB OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031870840129.1888888889 | 10318708 |  | Parent | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 40129.1889 | 40129.5139 | DAILY | 00327661 | SPICAPX | OUTAGE COSTS No.4 CAP BANK | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031870740129.1888888889 | 10318707 | X81158B0 | Child | FALSE | NPSD-FBTS 220KV WY | 40129.1889 | 40131.4049 | DAILY | 00022738 | SPICAPX | OUTAGE COSTS NPSD LINE | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031969440129.1888888889 | 10319694 | 10319693 | Child | FALSE | EX - NPSD 220KV LINE CB CT R/PH AT FBTS | 40129.1889 | 40131.4049 | DAILY | [12 empty] | 0
_X81158B040129.1888888889 | X81158B0 |  | Parent | TRUE | EX - NPSD 220KV LINE CB CT R/PH AT FBTS | 40129.1889 | 40131.4049 | DAILY | [12 empty] | 0
_X90758A340129.2111111111 | X90758A3 |  | Parent | FALSE | EX - SYTS NO.2 500KV LINE CVT R/PH AT SMTS | 40129.2111 | 40129.4493 | DAILY | 00155375 | SPICAPX | REMOVE REMAINING SECTIONS SYTS 2LINE CVT's | SPIPOWER | X907 | [7 empty] | 0 | X90758A3 |  | REMOVE REMAINING SECTIONS SYTS 2LINE CVT's | 00155375 | CVTCC | X907 | SMTS | INSTRAN | SPICAPX | DAILY
_X7E458Q540129.2333333333 | X7E458Q5 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40129.2333 | 40129.6875 | DAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458Q640129.2333333333 | X7E458Q6 | X7E458Q5 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40129.2333 | 40129.6875 | DAILY | 00003007 | SPICAPX | Rebate W/O Shunt React, MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458Q740129.2333333333 | X7E458Q7 | X7E458Q5 | Child | FALSE | HYTS-APD 1 500KV W | 40129.2333 | 40129.6875 | DAILY | 00319998 | SPICAPX | Rebate HYTS-APD N1 Ln, During MLTS-HYTS 1 Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458Q840129.2333333333 | X7E458Q8 | X7E458Q5 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40129.2333 | 40129.6875 | DAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans , During MLTS-HYTS 1 LN Outage | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029443540129.2715277778 | 10294435 | X87058K7 | Child | FALSE | ROTS NO.8 220KV LINE NO.2 BUS CB CT R/PH AT YPS | 40129.2715 | 40129.6278 | DAILY | [12 empty] | 0
_X87058K740129.2715277778 | X87058K7 |  | Parent | TRUE | ROTS NO.8 220KV LINE AT YPS | 40129.2715 | 40129.6278 | DAILY | 00016416 | SPICAPX | Insulators replacement rots no8 | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031845640129.6388888889 | 10318456 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 40129.6389 | 40129.7965 | DAILY | 00337579 | FORCED | A3 TRANS TOP UP OIL WHITE PH 220KV BUSHING | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E458Q940130.2194444445 | X7E458Q9 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40130.2194 | 40130.6569 | DAILY | 00319998 | SPICAPX | Out W/O AP-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031873440130.23125 | 10318734 |  | Parent | FALSE | EPS -TTS 1 220KV N | 40130.2312 | 40130.4083 | DAILY | 00331826 | SPICAPX | Out W/O EPS-TTS Line OPGW cut - in | SPIPOWER | 80000427 | SCADA Comms to ZSS (Fibre) | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031957140130.2909722222 | 10319571 |  | Parent | TRUE | JLTS NO.1 LINE/AUX TRANS 'B' 220KV CB AT HWPS | 40130.291 | 40130.775 | DAILY | [12 empty] | 0
_1031957340130.2909722222 | 10319573 | 10319571 | Child | FALSE | HWPS-JLTS 1 220KV G | 40130.291 | 40130.775 | DAILY | 00020442 | SPIMAINT | LINE REBATE CB OUTAGE JLTS NO1 | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031976640130.85625 | 10319766 |  | Parent | FALSE | NO.6 GEN 220/16.5KV TRANS AT HWPS | 40130.8562 | 40131.9056 | CONT | 00009647 | GENCO | Power Station requirements | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1031716140131.2076388889 | 10317161 | X70658N3 | Child | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 40131.2076 | 40131.4382 | CONT | 00015976 | SPICAPX | W/O FOR REBATE ON GTS NO.2 LINE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658N340131.2076388889 | X70658N3 |  | Parent | TRUE | NO.3 220KV BUS AT KTS | 40131.2076 | 40131.4382 | REPDAILY | 00001171 | SPICAPX | EST BIPODS FROM No 3 BUS TO FUT GTS No2 L 3B CB | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031977140131.4381944445 | 10319771 |  | Parent | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 40131.4382 | 40132.2562 | CONT | 00015976 | SPICAPX | GTS No2 Line | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_U80358A240132.25 | U80358A2 |  | Parent | FALSE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 40132.25 | 40132.625 | DAILY | 00354002 | SPIMAINT | Replace inverted rupture disc | SPIPOWER | U803 | U803 - (C-RTF) REPLACE A1 TRANS R/PH RUPTURE DISK | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1031716140132.25625 | 10317161 | X70658N3 | Child | FALSE | EX - GTS NO.2 220KV LINE AT KTS | 40132.2562 | 40132.5278 | CONT | 00015976 | SPICAPX | W/O FOR REBATE ON GTS NO.2 LINE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658N340132.25625 | X70658N3 |  | Parent | TRUE | NO.3 220KV BUS AT KTS | 40132.2562 | 40132.5278 | REPDAILY | 00001171 | SPICAPX | EST BIPODS FROM No 3 BUS TO FUT GTS No2 L 3B CB | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658Q840133.1770833333 | X70658Q8 |  | Parent | FALSE | EX - 1-2 66KV BUS TIE CB NO.2 BUS SIDE ISOL AT KTS | 40133.1771 | 40133.4208 | DAILY | [12 empty] | 0
_X7E458R340133.2208333333 | X7E458R3 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40133.2208 | 40133.7056 | REPDAILY | 00319998 | SPICAPX | Out W/O APD-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V99058A140133.2520833333 | V99058A1 |  | Parent | FALSE | B1 220/66KV TRANS AT RTS | 40133.2521 | 40133.625 | REPDAILY | 00007329 | SPIMAINT | Replace Cooling Radiators | SPIPOWER | V990 | V990 - ASEA 150MVA TRANS COOLING SYSTEM OVERHAUL | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031956440133.2736111111 | 10319564 |  | Parent | TRUE | YPS NO.1 220KV LINE NO.6 BUS CB AT HWPS | 40133.2736 | 40133.3847 | DAILY | [12 empty] | 0
_1031993540133.2736111111 | 10319935 | 10319564 | Child | FALSE | YPS NO.1 220KV LINE AT HWPS | 40133.2736 | 40133.3847 | DAILY | 00015795 | SPIMAINT | REBATE LINE OUTAGE YPS NO1 | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031849040133.3333333333 | 10318490 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 40133.3333 | 40133.4271 | REPDAILY | [12 empty] | 0
_1031980740133.3895833333 | 10319807 |  | Parent | FALSE | NO.2 22KV CAPACITOR BANK AT KGTS | 40133.3896 | 40134.3729 | CONT | 00017394 | FAULT | KGTS No2 22kV Cap Bank CB will not close from TOC | SPIPOWER |  |  | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658Q940133.4375 | X70658Q9 |  | Parent | FALSE | EX - 1-2 66KV BUS TIE CB AT KTS | 40133.4375 | 40138.2153 | CONT | [12 empty] | 0
_1031848940133.5 | 10318489 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT WOTS | 40133.5 | 40133.55 | REPDAILY | [12 empty] | 0
_X7E458R340134.2215277778 | X7E458R3 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40134.2215 | 40134.6903 | REPDAILY | 00319998 | SPICAPX | Out W/O APD-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V99058A140134.2479166667 | V99058A1 |  | Parent | FALSE | B1 220/66KV TRANS AT RTS | 40134.2479 | 40134.6292 | REPDAILY | 00007329 | SPIMAINT | Replace Cooling Radiators | SPIPOWER | V990 | V990 - ASEA 150MVA TRANS COOLING SYSTEM OVERHAUL | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031849040134.3333333333 | 10318490 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 40134.3333 | 40134.4444 | REPDAILY | [12 empty] | 0
_1031848940134.5152777778 | 10318489 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT WOTS | 40134.5153 | 40134.5687 | REPDAILY | [12 empty] | 0
_V96558A340135.2104166667 | V96558A3 |  | Parent | FALSE | NO.3 GEN TRANS NO.2 BUS 220KV CB AT HWPS | 40135.2104 | 40149.6132 | CONT | [12 empty] | 0
_X7E458R340135.2201388889 | X7E458R3 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40135.2201 | 40135.8153 | REPDAILY | 00319998 | SPICAPX | Out W/O APD-HYTS No1 Line for OPGW installation | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029347840135.2743055556 | 10293478 |  | Parent | FALSE | A 66/11KV S/S TRANS CABLE AT LY | 40135.2743 | 40135.6486 | DAILY | 00027176 | SPIMAINT | O/H A 66KV S/S TRANS FDR/CABLE AT LY | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031839640135.2819444445 | 10318396 |  | Parent | FALSE | LYPS NO.2 LINE/ROTS NO.3 LINE 500KV CB AT HWTS | 40135.2819 | 40135.5326 | DAILY | [12 empty] | 0
_X89258A140136.225 | X89258A1 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40136.225 | 40136.7528 | REPDAILY | 00319999 | SPICAPX | Out W/O APD No2 Line -Install OHEW from T623-APD | SPIPOWER | X892 | X892 - (HYTS-APD) GROUND WIRE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029348040136.2715277778 | 10293480 |  | Parent | FALSE | B 66/11KV S/S TRANS CABLE AT LY | 40136.2715 | 40136.6326 | DAILY | 00027177 | SPIMAINT | O/H B 66KV S/S TRANS FDR/CABLE AT LY | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031995640136.5263888889 | 10319956 |  | Parent | FALSE | B4 220/66KV TRANS AT KTS | 40136.5264 | 40136.6403 | CONT | 00001146 | FAULT | B4 Transformer Auto Opening | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031994540136.6694444444 | 10319945 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB CT B/PH AT KTS | 40136.6694 | 40136.7 | DAILY | [12 empty] | 0
_1031996840137.0256944445 | 10319968 |  | Parent | FALSE | NO.6 GEN 220/16.5KV TRANS AT HWPS | 40137.0257 | 40139.8047 | CONT | 00009647 | GENCO | HVS: HWPS No 6 Gen Isol'd for PS | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1031976440137.1694444444 | 10319764 |  | Parent | FALSE | EPS -TTS 1 220KV N | 40137.1694 | 40137.2104 | REPDAILY | 00331826 | SPICAPX | Out W/O EPS-TTS Line OPGW cut - in | SPIPOWER | 80000427 | SCADA Comms to ZSS (Fibre) | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029348240137.2701388889 | 10293482 |  | Parent | FALSE | C 66/11KV S/S TRANS CABLE AT LY | 40137.2701 | 40137.634 | DAILY | 00027178 | SPIMAINT | O/H C 66KV S/S TRANS FDR/CABLE AT LY | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031999240137.9763078704 | 10319992 |  | Parent | FALSE | W3 GEN TRANS 220KV LINE E/SW AT YPS | 40137.9763 | 40142.8125 | CONT | [12 empty] | 0
_1031994740138 | 10319947 |  | Parent | TRUE | EX - SMTS 500KV LINE NO.2 BUS CB CT R/PH AT KTS | 40138 | 40138.2139 | DAILY | [12 empty] | 0
_1031995140138 | 10319951 | 10319947 | Child | FALSE | SMTS 500KV LINE AT KTS | 40138 | 40138.2139 | DAILY | 00015991 | SPIMAINT | outage cost capture | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658N940138.1652777778 | X70658N9 |  | Parent | TRUE | NO.1 66KV BUS AT KTS | 40138.1653 | 40138.5764 | DAILY | 00001172 | SPICAPX | REPLACE No.1-2 66KV BUS TIE CB | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658O040138.1652777778 | X70658O0 | X70658N9 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT KTS | 40138.1653 | 40138.5764 | DAILY | 00327947 | SPICAPX | OUTAGE COSTS FOR No1 66KV BUS OUTAGE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031994940138.2138888889 | 10319949 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB CT B/PH AT KTS | 40138.2139 | 40138.391 | DAILY | [12 empty] | 0
_X80458A040138.2201388889 | X80458A0 |  | Parent | FALSE | EX - NO.1 22KV/415V S/S TRANS AT WMTS | 40138.2201 | 40138.8243 | REPDAILY | 00003238 | SPICAPX | REPLACE S/S TRANSFORMER & 415V CABLES | SPIPOWER | X804 | X804 - TERMINAL STATION AC SUPPLY UPGRADES | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1031819640138.2715277778 | 10318196 |  | Parent | FALSE | A2 515/230KV TRANS BANK AT HWTS | 40138.2715 | 40138.4201 | DAILY | 00337572 | SPIMAINT | TOP UP OIL WHITE PHASE 220kV BUSHING TX 2 | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031987440138.4375 | 10319874 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 40138.4375 | 40138.6181 | DAILY | 00337579 | SPIMAINT | A3 TRANS TOP UP OIL WHITE PH 220KV BUSHHING | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z73458A640139.1722222222 | Z73458A6 |  | Parent | FALSE | NO.2 66KV BUS AT KTS | 40139.1722 | 40139.4056 | DAILY | 00001173 | DB_AUG | REMOVE 2-3 BUS TIE CB & 2B ISOLS & 3B DROPPERS | SPIPOWER | Z734 | Z734 - (KTS) 5TH 220/66KV TRANSFORMER | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X90758A440139.2194444445 | X90758A4 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 40139.2194 | 40139.4583 | CONT | 00012436 | SPICAPX | REPLACE 500KV CT'S | SPIPOWER | X907 | X907 - TYREE CVT REPLACEMENT PROGRAM | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027015340139.2486111111 | 10270153 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 40139.2486 | 40139.6451 | DAILY | 00002829 | SPIMAINT | O/HAUL Transformer and Div Sw (N) | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1028652540140.5055555556 | 10286525 |  | Parent | FALSE | W3 GEN TRANS NO.1 BUS 220KV CB LINE SIDE ISOL AT YPS | 40140.5056 | 40141.5729 | DAILY | [12 empty] | 0
_1032001140140.7534722222 | 10320011 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 40140.7535 | 40140.8799 | DAILY | 00337579 | FORCED | A3 TRANS TOP UP OIL WHITE PH 220KV BUSHHING | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029071340141.2666666667 | 10290713 | 10292400 | Child | FALSE | 2B-4 220KV BUS TIE CB NO.4 BUS SIDE E/SW AT RTS | 40141.2667 | 40141.6194 | DAILY | [12 empty] | 0
_1029071540141.2666666667 | 10290715 | 10292400 | Child | FALSE | B4 TRANS 220KV E/SW AT RTS | 40141.2667 | 40141.6194 | DAILY | [12 empty] | 0
_1029240040141.2666666667 | 10292400 |  | Parent | TRUE | NO.4 220KV BUS AT RTS | 40141.2667 | 40141.6194 | DAILY | 00328828 | SPIMAINT | O/Haul NO.4 220KV BUS AT RTS | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029995740141.2666666667 | 10299957 | 10292400 | Child | FALSE | B4 220/66KV TRANS AT RTS | 40141.2667 | 40141.6194 | DAILY | 00007332 | SPIMAINT | TRAN REBATE for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031624740141.2666666667 | 10316247 | 10292400 | Child | FALSE | B4 TRANS 220KV ISOL AT RTS | 40141.2667 | 40141.6194 | DAILY | [12 empty] | 0
_1029035640141.2993055556 | 10290356 |  | Parent | TRUE | A3 GEN TRANS NO.1 BUS 500KV CB AT LYPS | 40141.2993 | 40141.6208 | CONT | [12 empty] | 0
_1030117140141.2993055556 | 10301171 | 10290356 | Child | FALSE | A3 GEN TRANS NO.1 BUS 500KV CB AT LYPS | 40141.2993 | 40141.6208 | DAILY | [12 empty] | 0
_1031849240141.3131944445 | 10318492 |  | Parent | FALSE | BATS 220KV LINE NO.1 BUS CB AT BETS | 40141.3132 | 40141.341 | DAILY | [12 empty] | 0
_1031849340141.3805555556 | 10318493 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT BETS | 40141.3806 | 40141.4118 | DAILY | [12 empty] | 0
_1032002840141.5222222222 | 10320028 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT WMTS | 40141.5222 | 40141.6528 | DAILY | [12 empty] | 0
_1032014240141.5222222222 | 10320142 | 10320028 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT WMTS | 40141.5222 | 40141.6528 | DAILY | 00074391 | FORCED | FAULTY CB GAS DENSITY MONITOR | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031983240142.2097222222 | 10319832 | X7E958A5 | Child | FALSE | SMTS 500KV LINE AT KTS | 40142.2097 | 40142.4167 | CONT | 00015991 | SPICAPX | capture outage costs | SPIPOWER | X7E9 | X7E9 - (KTS) 500KV CT & CB | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E958A540142.2097222222 | X7E958A5 |  | Parent | TRUE | SMTS LINE/A2 TRANS 500KV CB LINE SIDE ROI AT KTS | 40142.2097 | 40142.4167 | DAILY | [12 empty] | 0
_V9A458A640142.2479166667 | V9A458A6 |  | Parent | FALSE | B4 220/66KV TRANS AT SVTS | 40142.2479 | 40142.6035 | DAILY | 00352791 | SPIMAINT | Add NYPASS to Trans | SPIPOWER | V9A4 | V9A4 - TREAT CORROSIVE SULPHUR IN TRANSFMR INSULATING OIL | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V99058A340142.2555555556 | V99058A3 |  | Parent | FALSE | B1 220/66KV TRANS AT RTS | 40142.2556 | 40142.6222 | DAILY | 00007329 | SPIMAINT | Replace Cooling Radiators | SPIPOWER | V990 | V990 - ASEA 150MVA TRANS COOLING SYSTEM OVERHAUL | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030117540142.2645833333 | 10301175 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 40142.2646 | 40142.6333 | DAILY | [12 empty] | 0
_1029112740142.2652777778 | 10291127 |  | Parent | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 40142.2653 | 40142.6396 | REPDAILY | 00004036 | SPIMAINT | O/H NO 1 TRANS & TAP CHANGER & S/S Trans | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031990040142.2909722222 | 10319900 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT GTS | 40142.291 | 40142.6319 | DAILY | 00367360 | DBPROX | VSCAP to PowerCor | DISTCO |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1032015440143.11875 | 10320154 |  | Parent | FALSE | WMTS NO.1 220KV LINE AT FBTS | 40143.1188 | 40143.2146 | CONT | 00017159 | FAULT | Trip No4 220kV Bus loss of WMTS No1 220KV Line | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1032015540143.11875 | 10320155 |  | Parent | FALSE | NO.4 220KV CAPACITOR BANK AT FBTS | 40143.1188 | 40143.2146 | CONT | 00327661 | FAULT | Trip No4 220kV Bus loss of No4 220KV Cap Bank | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1032015240143.11875 | 10320152 |  | Parent | FALSE | NPSD-FBTS 220KV WY | 40143.1188 | 40143.2153 | CONT | 00022738 | FAULT | Trip No4 220kV Bus loss of NPSD 220KV Line | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032015640143.11875 | 10320156 |  | Parent | FALSE | B4 220/66KV TRANS AT FBTS | 40143.1188 | 40143.2153 | CONT | 00002728 | FAULT | Trip No4 220kV Bus loss of B4 220/66KV Transf | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032013340143.11875 | 10320133 |  | Parent | FALSE | SYN/COND AT FBTS | 40143.1188 | 40143.375 | CONT | 00002697 | FAULT | Trip No4 220kV Bus loss of Syn Con at FBTS | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031983440143.1875 | 10319834 | X7E958A6 | Child | FALSE | A2 500/220KV TRANS BANK AT KTS | 40143.1875 | 40143.4181 | DAILY | 00026096 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X7E9 | X7E9 - (KTS) 500KV CT & CB | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E958A640143.1875 | X7E958A6 |  | Parent | TRUE | SMTS LINE/A2 TRANS 500KV CB TRANS SIDE ROI AT KTS | 40143.1875 | 40143.4181 | DAILY | [12 empty] | 0
_1032011940143.2611111111 | 10320119 |  | Parent | TRUE | NO.1 TRANS 66KV CB AT WOTS | 40143.2611 | 40143.5563 | DAILY | [12 empty] | 0
_1032012040143.2611111111 | 10320120 | 10320119 | Child | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 40143.2611 | 40143.5563 | DAILY | 00004036 | SPIMAINT | Perf calc W/O No1 trans 66kV during 66kV CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032015340143.2715277778 | 10320153 |  | Parent | FALSE | NO.1A TRANS AT RCTS | 40143.2715 | 40143.3389 | CONT | 00016722 | FAULT | RCTS No1 22kV Bus Trip Loss of No1A 220/22KV Trans | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031962640143.3270833333 | 10319626 |  | Parent | FALSE | HPS 66KV LINE CB AT WOTS | 40143.3271 | 40143.5444 | DAILY | [12 empty] | 0
_1031936540143.4993055556 | 10319365 |  | Parent | FALSE | BETS 220KV LINE NO.2 BUS CB AT BATS | 40143.4993 | 40143.5944 | DAILY | [12 empty] | 0
_1032016240143.9090277778 | 10320162 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 40143.909 | 40151.9139 | CONT | 00356081 | GENCO | HWPS No3 Gen Trans Isols | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E458S140144.2569444444 | X7E458S1 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40144.2569 | 40144.3333 | DAILY | 00022740 | SPICAPX | Install Prototype earth peaks on MLTS-TGTS Line | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031936340144.3555555556 | 10319363 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT BATS | 40144.3556 | 40144.5667 | DAILY | [12 empty] | 0
_1029432940144.3583333333 | 10294329 |  | Parent | FALSE | H3 TRANS NO.1 BUS 330KV CB CT R/PH AT DDTS | 40144.3583 | 40144.3924 | DAILY | [12 empty] | 0
_1032017140144.5 | 10320171 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT GNTS | 40144.5 | 40144.5312 | DAILY | 00000745 | FORCED | No2 22kV/415V S/S Trans blown SD red phase. | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1032018340144.5534722222 | 10320183 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB AT HWTS | 40144.5535 | 40144.5556 | DAILY | [12 empty] | 0
_Z71958C740145.1875 | Z71958C7 |  | Parent | FALSE | B2 220/66KV TRANS AT CBTS | 40145.1875 | 40145.7097 | DAILY | 00353077 | DB_AUG | Install New B3 Enclosure | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X80458A140145.2173611111 | X80458A1 |  | Parent | FALSE | EX - NO.2 22KV/415V S/S TRANS AT WMTS | 40145.2174 | 40145.7007 | CONT | 00003239 | SPICAPX | REPLACE S/S TRANSFORMER & 415V CABLES | SPIPOWER | X804 | X804 - TERMINAL STATION AC SUPPLY UPGRADES | Other Transformers | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1029137740145.2430555556 | 10291377 |  | Parent | TRUE | NO.4 66KV BUS AT GTS | 40145.2431 | 40145.6472 | DAILY | 00002838 | SPIMAINT | O/Haul NO.4 66KV BUS AT GTS | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031946040145.2430555556 | 10319460 | 10291377 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 40145.2431 | 40145.6472 | DAILY | 00329879 | SPIMAINT | Rebate W/O #4 66 Cap bk during #4 66kV Bus outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031946140145.2430555556 | 10319461 | 10291377 | Child | FALSE | B4 220/66KV TRANS AT GTS | 40145.2431 | 40145.6472 | DAILY | 00002830 | SPIMAINT | Perf calc W/O B4 Trans during No4 66kV Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031786740145.2444444445 | 10317867 | Z91358A2 | Child | FALSE | B2 220/66KV TRANS COOLING FANS AT MWTS | 40145.2444 | 40145.5778 | DAILY | [12 empty] | 0
_1031972440145.2444444445 | 10319724 | Z91358A2 | Child | FALSE | LY NO.2 66KV FDR AT MWTS | 40145.2444 | 40145.5778 | REPDAILY | 00016141 | DB_AUG | LINE REBATE FOR BUS OUTAGE | SPIPOWER | Z913 | Z913 - (MWTS) RE-ARRANGE LGA3 66KV FEEDER | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031973640145.2444444445 | 10319736 | Z91358A2 | Child | FALSE | JLTS NO.2 220KV LINE AT MWTS | 40145.2444 | 40145.5778 | DAILY | 00016131 | DB_AUG | lLINE REBATE FOR BUS OUTAGE | SPIPOWER | Z913 | Z913 - (MWTS) RE-ARRANGE LGA3 66KV FEEDER | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z91358A240145.2444444445 | Z91358A2 |  | Parent | TRUE | NO.2 66KV BUS AT MWTS | 40145.2444 | 40145.5778 | DAILY | 00010279 | DB_AUG | REMOVE OLD LGA 3 CB CONNECTIONS | SPIPOWER | Z913 | Z913 - (MWTS) RE-ARRANGE LGA3 66KV FEEDER | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z56258C240145.25 | Z56258C2 |  | Parent | FALSE | MBTS NO.1 220KV LINE AT DDTS | 40145.25 | 40145.7451 | DAILY | 00012361 | VEN_AUG | Out W/O MBTS No1 Line choke removal | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031994340145.2541666667 | 10319943 |  | Parent | TRUE | ROTS NO.1 220KV LINE CB AT RTS | 40145.2542 | 40145.5694 | DAILY | [12 empty] | 0
_1031995340145.2541666667 | 10319953 | 10319943 | Child | FALSE | ROTS NO.1 220KV LINE AT RTS | 40145.2542 | 40145.5694 | DAILY | 00021385 | SPIMAINT | Rebate Line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032017240145.3145833333 | 10320172 |  | Parent | FALSE | B2 220/66KV TRANS AT MWTS | 40145.3146 | 40145.5451 | DAILY | 00010266 | SPIMAINT | MWTS No2 TRANS COOLING | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032016140145.3715277778 | 10320161 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 40145.3715 | 40145.5014 | DAILY | 00337579 | SPIMAINT | A3 TRANS TOP UP OIL WHITE PH 220KV BUSHHING | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032023340145.51875 | 10320233 |  | Parent | FALSE | YPS -YWPS 1 220KV G | 40145.5188 | 40148.5188 | CONT | 00020517 | GENCO | YWPS No1 Gen Trans Line Isolated for SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032023640145.7208333333 | 10320236 |  | Parent | FALSE | B4 TRANS NO.2 BUS 220KV CB AT SHTS | 40145.7208 | 40147.6306 | CONT | [12 empty] | 0
_Z71958C840146.1798611111 | Z71958C8 |  | Parent | FALSE | B2 220/66KV TRANS AT CBTS | 40146.1799 | 40146.8389 | DAILY | 00353077 | DB_AUG | Install New B3 Enclosure | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X90758B140146.2180555556 | X90758B1 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 40146.2181 | 40146.5194 | CONT | 00012436 | SPICAPX | REPLACE 500KV CT'S | SPIPOWER | X907 | X907 - TYREE CVT REPLACEMENT PROGRAM | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1027015640146.2576388889 | 10270156 |  | Parent | FALSE | NO.3 66KV BUS AT GTS | 40146.2576 | 40146.7028 | DAILY | 00002837 | SPIMAINT | O/Haul NO.3 66KV BUS AT GTS | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1028391540146.2576388889 | 10283915 |  | Parent | FALSE | NO.3 66KV BUS AT GTS | 40146.2576 | 40146.7028 | DAILY | 00002837 | SPIMAINT | O/H No3 66KV Bus bridge connections | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1029631440146.2576388889 | 10296314 |  | Parent | FALSE | NO.3 66KV BUS VT AT GTS | 40146.2576 | 40146.7028 | DAILY | [12 empty] | 0
_1029973540146.2576388889 | 10299735 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 40146.2576 | 40146.7028 | DAILY | 00002829 | SPIMAINT | Perf Calc W/O B3 Trans during No3 66 Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z71958C940147.1798611111 | Z71958C9 |  | Parent | FALSE | B2 220/66KV TRANS AT CBTS | 40147.1799 | 40147.5188 | DAILY | 00353077 | DB_AUG | Install New B3 Enclosure | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1031979240147.2513888889 | 10319792 |  | Parent | TRUE | NO.1 66KV BUS AT TBTS | 40147.2514 | 40147.4208 | DAILY | 00004907 | DB_AUG | TBTS Upgrade DMA No1 &2 Feeder Exit Ratings | SPIPOWER | Z905 | Z905 - (TBTS) UPGRADE DMA 1&2 FEEDER EXIT RATINGS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031979340147.2513888889 | 10319793 | 10319792 | Child | FALSE | B1 220/66KV TRANS AT TBTS | 40147.2514 | 40147.4208 | DAILY | 00004901 | DB_AUG | Rebate Tran for Bus Outage | SPIPOWER | Z905 | Z905 - (TBTS) UPGRADE DMA 1&2 FEEDER EXIT RATINGS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031979440147.2513888889 | 10319794 | 10319792 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT TBTS | 40147.2514 | 40147.4208 | DAILY | 00351938 | DB_AUG | Rebate CapBank for Bus Outage | SPIPOWER | Z905 | Z905 - (TBTS) UPGRADE DMA 1&2 FEEDER EXIT RATINGS | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_V9A658A040147.2548611111 | V9A658A0 |  | Parent | FALSE | KTS NO.1 220KV LINE NO.3 BUS CB AT TTS | 40147.2549 | 40151.6312 | CONT | [12 empty] | 0
_1031980240147.2555555556 | 10319802 |  | Parent | TRUE | B2 TRANS 66KV CB AT RWTS | 40147.2556 | 40147.559 | DAILY | [12 empty] | 0
_1031983340147.2555555556 | 10319833 | 10319802 | Child | FALSE | B2 220/66KV TRANS AT RWTS | 40147.2556 | 40147.559 | DAILY | 00007450 | SPIMAINT | Trans Rebate | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032025640147.3243055556 | 10320256 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 40147.3243 | 40150.7958 | CONT | 00016424 | GENCO | Work by GenCo | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1028964240148.2604166667 | 10289642 |  | Parent | FALSE | NO.2 66KV REACTOR AT RCTS | 40148.2604 | 40148.6 | DAILY | 00016897 | SPIMAINT | O/Haul NO.2 66KV REACTOR AT RCTS | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032025240148.2888888889 | 10320252 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 40148.2889 | 40149.6299 | DAILY | [12 empty] | 0
_1031966540148.3333333333 | 10319665 | Z73058N3 | Child | FALSE | DDTS-SMTS 2 330KV | 40148.3333 | 40148.3965 | DAILY | 00328507 | DB_AUG | CAPTURE OUTAGE COSTS OF DDTS LINE | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z73058N340148.3333333333 | Z73058N3 |  | Parent | TRUE | DDTS NO.2 330KV LINE Y PROT AT SMTS | 40148.3333 | 40148.3965 | DAILY | [12 empty] | 0
_1031947340148.5097222222 | 10319473 |  | Parent | FALSE | BETS 220KV LINE NO.2 BUS CB AT BATS | 40148.5097 | 40148.5639 | REPDAILY | [12 empty] | 0
_1031947240148.5791666667 | 10319472 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT BATS | 40148.5792 | 40148.6181 | REPDAILY | [12 empty] | 0
_1032031640148.9791666667 | 10320316 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 40148.9792 | 40149.8889 | CONT | 00356082 | GENCO | Outage for Generator | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V99058A440149.2513888889 | V99058A4 |  | Parent | FALSE | B1 220/66KV TRANS AT RTS | 40149.2514 | 40150.6681 | REPDAILY | 00007329 | SPIMAINT | Replace Cooling Radiators | SPIPOWER | V990 | V990 - ASEA 150MVA TRANS COOLING SYSTEM OVERHAUL | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458J740149.2680555556 | X7E458J7 |  | Parent | FALSE | MLTS 220KV LINE AT TGTS | 40149.2681 | 40149.5056 | DAILY | 00023131 | SPICAPX | Out W/OTrial installation of earth peaks MLTS-TGTS | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032028540149.2923611111 | 10320285 |  | Parent | FALSE | HYTS NO.1 500KV LINE AT APD | 40149.2924 | 40149.3194 | DAILY | 00005921 | APDALCOA | HVS: APD-HYTS 1 Line outage for APD | APDALCOA |  |  | Circuits | 3rd Party | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1031947240149.3277777778 | 10319472 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT BATS | 40149.3278 | 40149.55 | REPDAILY | [12 empty] | 0
_1031968340150.2465277778 | 10319683 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 40150.2465 | 40150.6514 | REPDAILY | 00337581 | SPIMAINT | Repair oil leaks | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032028640150.2916666667 | 10320286 |  | Parent | FALSE | HYTS NO.2 500KV LINE AT APD | 40150.2917 | 40150.3139 | DAILY | 00005922 | APDALCOA | HVS: APD-HYTS 2 Line outage for APD | APDALCOA |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1031990140150.3444444445 | 10319901 |  | Parent | TRUE | NO.2B 66KV CAPACITOR BANK CB AT RWTS | 40150.3444 | 40150.3597 | DAILY | [12 empty] | 0
_1031992440150.3444444445 | 10319924 | 10319901 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 40150.3444 | 40150.3597 | DAILY | 00331179 | SPIMAINT | Rebate CapBank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032022140150.5194444445 | 10320221 |  | Parent | FALSE | BOPS-MKPS 220KV LINE CB LINE SIDE ROI AT MBTS | 40150.5194 | 40150.591 | DAILY | [12 empty] | 0
_1031873540151.1875 | 10318735 |  | Parent | FALSE | EPS -TTS 1 220KV N | 40151.1875 | 40151.6472 | DAILY | 00331826 | SPICAPX | Out W/O EPS-TTS Line OPGW cut - in | SPIPOWER | 80000427 | SCADA Comms to ZSS (Fibre) | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031968340151.2493055556 | 10319683 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 40151.2493 | 40151.6535 | REPDAILY | 00337581 | SPIMAINT | Repair oil leaks | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z71958A740152.2305555556 | Z71958A7 |  | Parent | TRUE | NO.1 220KV BUS AT CBTS | 40152.2306 | 40152.691 | DAILY | 00359378 | DB_AUG | INSTALL BUS EXTENTION & B1 NEUTRAL REACTOR | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z71958A840152.2305555556 | Z71958A8 | Z71958A7 | Child | FALSE | B1 220/66KV TRANS AT CBTS | 40152.2306 | 40152.691 | DAILY | 00353076 | DB_AUG | TRANS REBATE FOR BUS OUTAGE | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1031968440152.2486111111 | 10319684 |  | Parent | FALSE | R2 220/66/22KV TRANS GROUP AT RCTS | 40152.2486 | 40152.6924 | DAILY | 00337584 | SPIMAINT | Repair oil leaks | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031973440152.2715277778 | 10319734 | X90758A6 | Child | FALSE | SMTS-SYTS 1 500KV WT | 40152.2715 | 40152.4222 | DAILY | 00022640 | SPICAPX | REPLACE X DIST PROT WITH DIGITAL PROT | SPIPOWER | X907 | X907 - TYREE CVT REPLACEMENT PROGRAM | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X90758A640152.2715277778 | X90758A6 |  | Parent | TRUE | EX - SYTS NO.1 500KV LINE X PROT AT SMTS | 40152.2715 | 40152.4227 | DAILY | [12 empty] | 0
_1032040340152.6833333333 | 10320403 |  | Parent | FALSE | EX - NO.7 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 40152.6833 | 40152.8931 | CONT | [12 empty] | 0
_1032040240152.6833333333 | 10320402 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 40152.6833 | 40154.2743 | CONT | 00356082 | GENCO | HWPS No4 Gen Trans Isolated for powerstation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X90758A740153.2083333333 | X90758A7 |  | Parent | FALSE | SYTS NO.1 500KV LINE AT SMTS | 40153.2083 | 40153.6104 | DAILY | 00012439 | SPICAPX | REMOVE SYTS 1LINE 500KV CT'S | SPIPOWER | X907 | X907 - TYREE CVT REPLACEMENT PROGRAM | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031970040153.2229166667 | 10319700 |  | Parent | TRUE | NO.2A TRANS 22KV VT W/PH AT RCTS | 40153.2229 | 40153.6292 | DAILY | [12 empty] | 0
_1031970140153.2229166667 | 10319701 | 10319700 | Child | FALSE | NO.1 22KV CAPACITOR BANK AT RCTS | 40153.2229 | 40153.6292 | DAILY | 00016710 | SPIMAINT | Rebate W/O No1 22kV Cap Bk during #1 22 bus outage | SPIPOWER |  |  | Capacitors | Alstom | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031970240153.2229166667 | 10319702 | 10319700 | Child | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 40153.2229 | 40153.6292 | DAILY | 00337581 | SPIMAINT | Perf calc W/O No1 Tr grp during #1 22kV Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z71958A140153.2284722222 | Z71958A1 |  | Parent | TRUE | NO.1 220KV BUS AT CBTS | 40153.2285 | 40153.6306 | DAILY | 00359378 | DB_AUG | INSTALL BUS EXTENTION | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z71958A240153.2284722222 | Z71958A2 | Z71958A1 | Child | FALSE | B1 220/66KV TRANS AT CBTS | 40153.2285 | 40153.6306 | DAILY | 00353076 | DB_AUG | TRANS REBATE FOR BUS OUTAGE | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_Z56258C340153.25 | Z56258C3 |  | Parent | FALSE | MBTS NO.2 220KV LINE AT DDTS | 40153.25 | 40153.5806 | DAILY | 00012363 | VEN_AUG | Out W/O MBTS No2 Line choke removal | SPIPOWER | Z562 | Z562 - (BOGONG PS) PLANNING ESTIMATE | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z71958B140153.6305555556 | Z71958B1 |  | Parent | FALSE | B3 TRANS NO.1 BUS 220KV CB AT CBTS | 40153.6306 | 40164.3215 | CONT | [12 empty] | 0
_1032015840153.6611111111 | 10320158 | X70658S3 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40153.6611 | 40153.8951 | DAILY | 00119824 | SPICAPX | OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X70658S340153.6611111111 | X70658S3 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40153.6611 | 40153.8951 | DAILY | 00001169 | SPICAPX | EST BIPOD CONNECT FRM No.1 B TO GTS 2 L B/S ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658S740154.8958333333 | X70658S7 |  | Parent | FALSE | GTS NO.2 220KV LINE NO.1 BUS CB AT KTS | 40154.8958 | 40155.2139 | REPDAILY | [12 empty] | 0
_X70658N540155.1666666667 | X70658N5 |  | Parent | FALSE | GTS NO.2 220KV LINE AT KTS | 40155.1667 | 40155.3368 | CONT | 00368492 | SPICAPX | TERM GTS 2L TO GTS 2L 1 BUS CB L/S ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z71958A640155.1805555556 | Z71958A6 |  | Parent | FALSE | B2 220/66KV TRANS AT CBTS | 40155.1806 | 40155.4632 | REPDAILY | 00353077 | DB_AUG | INSTALL OVERHEAD GANTRY TO B3 TRANS | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X7E458J240155.2395833333 | X7E458J2 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40155.2396 | 40155.8035 | DAILY | 00022740 | SPICAPX | Install OPGW between T320 and T332 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658S740155.2708333333 | X70658S7 |  | Parent | FALSE | GTS NO.2 220KV LINE NO.1 BUS CB AT KTS | 40155.2708 | 40156.2257 | REPDAILY | [12 empty] | 0
_1031976440156.1881944445 | 10319764 |  | Parent | FALSE | EPS -TTS 1 220KV N | 40156.1882 | 40156.5903 | REPDAILY | 00331826 | SPICAPX | Out W/O EPS-TTS Line OPGW cut - in | SPIPOWER | 80000427 | SCADA Comms to ZSS (Fibre) | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z71958A640156.1923611111 | Z71958A6 |  | Parent | FALSE | B2 220/66KV TRANS AT CBTS | 40156.1924 | 40156.4132 | REPDAILY | 00353077 | DB_AUG | INSTALL OVERHEAD GANTRY TO B3 TRANS | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X70658N540156.2131944445 | X70658N5 |  | Parent | FALSE | GTS NO.2 220KV LINE AT KTS | 40156.2132 | 40156.6944 | CONT | 00368492 | SPICAPX | TERM GTS 2L TO GTS 2L 1 BUS CB L/S ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032045840156.2381944445 | 10320458 |  | Parent | FALSE | SYN/COND AT BLTS | 40156.2382 | 40156.2819 | DAILY | 00002547 | FAULT | Syn Con trip with BLTS Cap Bank Sw on | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458G740156.2416666667 | X7E458G7 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40156.2417 | 40156.6868 | DAILY | 00022740 | SPICAPX | Install OPGW between T312 and T 320 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X71158C940156.2645833333 | X71158C9 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 40156.2646 | 40165.4306 | DAILY | [12 empty] | 0
_1026911740156.2729166667 | 10269117 |  | Parent | FALSE | ROTS NO.2 220KV LINE NO.5 BUS CB AT HWPS | 40156.2729 | 40158.5333 | CONT | [12 empty] | 0
_V99058A840156.3076388889 | V99058A8 |  | Parent | FALSE | B4 220/66KV TRANS AT RTS | 40156.3076 | 40156.7118 | DAILY | 00007332 | SPIMAINT | Replace Cooling Radiators | SPIPOWER | V990 | V990 - ASEA 150MVA TRANS COOLING SYSTEM OVERHAUL | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031976440157.1881944445 | 10319764 |  | Parent | FALSE | EPS -TTS 1 220KV N | 40157.1882 | 40157.5861 | REPDAILY | 00331826 | SPICAPX | Out W/O EPS-TTS Line OPGW cut - in | SPIPOWER | 80000427 | SCADA Comms to ZSS (Fibre) | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_742058A040157.2451388889 | 742058A0 |  | Parent | FALSE | NO.1 66KV BUS EXTENSION AT TSTS | 40157.2451 | 40157.6903 | DAILY | 00007673 | SPICAPX | Install CVT need SLF & ELM Fdr outages | SPIPOWER | X741 | X741 - (TYREE,GEC FMJL,ASEA IMBA) CT REPLACEMENT | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_V99058A740157.2479166667 | V99058A7 |  | Parent | FALSE | B1 220/66KV TRANS AT RTS | 40157.2479 | 40158.6021 | CONT | 00007329 | SPIMAINT | Replace Cooling Radiators | SPIPOWER | V990 | V990 - ASEA 150MVA TRANS COOLING SYSTEM OVERHAUL | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458H240157.2513888889 | X7E458H2 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40157.2514 | 40157.5743 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T299and T312 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032049540157.3263888889 | 10320495 |  | Parent | FALSE | KTS -GTS 1 220KV WY | 40157.3264 | 40157.4076 | DAILY | 00022702 | FAULT | KTS-GTS No1 220KV line trip from protection | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458H740158.2513888889 | X7E458H7 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40158.2514 | 40158.7604 | DAILY | 00022740 | SPICAPX | Install OPGW between T288 and T299 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031993040158.5013888889 | 10319930 |  | Parent | FALSE | B4 220/66KV TRANS AT KTS | 40158.5014 | 40158.6153 | DAILY | 00001146 | SPIMAINT | IVESTIGATE AND REPAIR OIL LEAKES | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X90758A840159.2131944445 | X90758A8 |  | Parent | FALSE | HWTS NO.2 500KV LINE AT SMTS | 40159.2132 | 40160.5278 | CONT | 00012437 | SPICAPX | REPLACE HWTS 2 LINE 500KV CVT'S | SPIPOWER | X907 | X907 - TYREE CVT REPLACEMENT PROGRAM | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032053740159.2201388889 | 10320537 |  | Parent | FALSE | LYPS NO.1 500KV LINE AT HWTS | 40159.2201 | 40159.2375 | CONT | 00016234 | FORCED | LYPS 1 500KV Line off loaded CB fail to open | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032053840159.2201388889 | 10320538 |  | Parent | FALSE | A2 515/230KV TRANS BANK AT HWTS | 40159.2201 | 40159.2375 | CONT | 00337572 | FORCED | A2 TRANS off Loaded CB Failed to open | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032053940159.2201388889 | 10320539 |  | Parent | FALSE | NO.2 500KV BUS AT HWTS | 40159.2201 | 40159.2375 | CONT | 00009799 | FORCED | 500KV BUS deenergised for CB Fail to open | SPIPOWER |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1032053540159.2201388889 | 10320535 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB AT HWTS | 40159.2201 | 40161.6361 | CONT | [12 empty] | 0
_1032049840159.2784722222 | 10320498 |  | Parent | FALSE | B2 TRANS 66KV CB AT MWTS | 40159.2785 | 40159.3257 | DAILY | [12 empty] | 0
_1032055640159.99375 | 10320556 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT SMTS | 40159.9938 | 40160.1549 | DAILY | 00026101 | FAULT | SMTS: Trip H1 Transformer for CB Failure | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032055740159.99375 | 10320557 |  | Parent | FALSE | H2 330/220KV TRANS BANK AT SMTS | 40159.9938 | 40160.1701 | DAILY | 00026102 | FAULT | SMTS: Trip H2 Transformer for CB Failure | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032054340159.99375 | 10320543 |  | Parent | FALSE | NO.1 220KV BUS AT SMTS | 40159.9938 | 40160.2778 | CONT | 00366543 | FAULT | SMTS: Trip No1 220kV Bus for CB Failure | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032054540159.99375 | 10320545 |  | Parent | FALSE | EX - H2 TRANS NO.1 BUS 220KV CB AT SMTS | 40159.9938 | 40165.511 | CONT | [12 empty] | 0
_1032055940159.9944444445 | 10320559 |  | Parent | FALSE | TTS NO.1 220KV LINE AT SMTS | 40159.9944 | 40160.1549 | DAILY | 00367361 | FAULT | SMTS: Trip TTS 1 Line for CB Failure | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032055840159.9944444445 | 10320558 |  | Parent | FALSE | B1 220/66KV TRANS AT SMTS | 40159.9944 | 40160.2778 | DAILY | 00366621 | FAULT | CB Failure caused Trip of B1 Transf at SMTS | SPIPOWER |  |  | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1032019440160.2972222222 | 10320194 |  | Parent | TRUE | NO.2 66KV BUS AT TSTS | 40160.2972 | 40160.566 | DAILY | 00007674 | SPIMAINT | Bus outage for Secondary Maintance Trip Checks | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032020240160.2972222222 | 10320202 | 10320194 | Child | FALSE | B2 220/66KV TRANS AT TSTS | 40160.2972 | 40160.566 | DAILY | 00007658 | SPIMAINT | Tran Rebate | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032054140160.3256944444 | 10320541 |  | Parent | FALSE | YWPS NO.4 220KV LINE AT YPS | 40160.3257 | 40162.6312 | CONT | 00016428 | GENCO | YWPS NO.4 LINE ISOLATED FOR SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031873240161.1895833333 | 10318732 |  | Parent | FALSE | MBTS-EPS 1 220KV N | 40161.1896 | 40161.6104 | DAILY | 00055380 | SPICAPX | Out W/O MBTS-EPS No1 Line OPGW cut - in | SPIPOWER | 80000427 | SCADA Comms to ZSS (Fibre) | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X7E458S740161.2513888889 | X7E458S7 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40161.2514 | 40161.6806 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T257 and T274 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032049740161.2916666667 | 10320497 |  | Parent | FALSE | 22KV/415V S/S TRANS AT FTS | 40161.2917 | 40161.4896 | DAILY | 00004393 | DBPROX | VSCAP to Jemena UED | DISTCO |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1029444140161.4708333333 | 10294441 |  | Parent | FALSE | EX - W3 GEN TRANS NO.1 BUS 220KV CB CT R/PH AT YPS | 40161.4708 | 40161.5868 | DAILY | [12 empty] | 0
_1032054640161.5604166667 | 10320546 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 40161.5604 | 40162.6296 | CONT | 00016424 | GENCO | W2 Gen Trans Isolated for power station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E458S840162.2743055556 | X7E458S8 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40162.2743 | 40162.6903 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T248 and T257 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032051240162.2923611111 | 10320512 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40162.2924 | 40162.6014 | DAILY | 00319999 | APDALCOA | Outage requested by APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1032046640162.2958333333 | 10320466 |  | Parent | TRUE | SESS NO.1 275KV LINE/M1 TRANS CB AT HYTS | 40162.2958 | 40162.4125 | DAILY | [12 empty] | 0
_1032046740162.2958333333 | 10320467 | 10320466 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40162.2958 | 40162.4125 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during 275kv CB outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031992340163.2784722222 | 10319923 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT MLTS | 40163.2785 | 40163.4306 | DAILY | 00003006 | DBPROX | VSCAP to PowerCor | DISTCO |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1032051340163.2916666667 | 10320513 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40163.2917 | 40163.5111 | DAILY | 00319998 | APDALCOA | Outage requested by APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029786940163.3069444445 | 10297869 |  | Parent | FALSE | W4 GEN TRANS 220KV CB CT R/PH AT YPS | 40163.3069 | 40163.3681 | DAILY | [12 empty] | 0
_X7D958A040164.1909722222 | X7D958A0 |  | Parent | FALSE | SMTS NO.3 500KV LINE AT ROTS (RTF) | 40164.191 | 40164.4292 | DAILY | 00356731 | SPICAPX | Replace X Distance Relay | SPIPOWER | X7D9 | X7D9 - (MLTS,SYTS) REPLACE X PROT ON 3 500KV LINES | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V839511640164.2777777778 | V8395116 |  | Parent | FALSE | EX - JLGB 220KV BUS CVT R/PH AT JLGB | 40164.2778 | 40164.6132 | DAILY | [12 empty] | 0
_Z71958D040164.3208333333 | Z71958D0 |  | Parent | FALSE | B3 220/66KV TRANS AT CBTS | 40164.3208 | 40165.3875 | CONT | 00368875 | SPICAPX | Stability Test on B3 220/66KV TRANS AT CBTS | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1032059740164.33125 | 10320597 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS AT JLGA | 40164.3313 | 40165.6118 | DAILY | 00009820 | GENCO | Gen work | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1032059640164.3368055556 | 10320596 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS AT JLGB | 40164.3368 | 40165.6222 | CONT | 00009830 | GENCO | SCAP for Powerstation Work | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1032063240164.5777777778 | 10320632 |  | Parent | FALSE | HPS 66KV LINE AT WOTS | 40164.5778 | 40165.516 | CONT | 00012055 | FAULT | HPS 66kV Line Tripped | SPIPOWER |  |  | Circuits | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032062240164.6020833333 | 10320622 |  | Parent | FALSE | BATS-BETS 220KV | 40164.6021 | 40164.8847 | DAILY | 00328505 | FAULT | BATS-BETS Line Tripped ARC and tripped to LO | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032061240165.5208333333 | 10320612 |  | Parent | FALSE | EX - H2 TRANS NO.1 BUS 220KV CB AT SMTS | 40165.5208 | 40193.4125 | CONT | [12 empty] | 0
_X72758B840165.625 | X72758B8 |  | Parent | FALSE | B2 220/66KV TRANS AT TTS | 40165.625 | 40170.5514 | CONT | 00362454 | SPICAPX | RECONNECT B2 TRANS | SPIPOWER | X727 | X727 - (TTS) B2 TRANSFORMER REPLACEMENT | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032022440166.1777777778 | 10320224 | Z73458A9 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40166.1778 | 40166.5563 | DAILY | 00119824 | DB_AUG | Outage costs for No1 220KV Bus outage | SPIPOWER | Z734 | Z734 - (KTS) 5TH 220/66KV TRANSFORMER | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_Z73458A940166.1777777778 | Z73458A9 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40166.1778 | 40166.5563 | REPDAILY | 00001169 | DB_AUG | String 220KV conns fut B5 Trans to Rack | SPIPOWER | Z734 | Z734 - (KTS) 5TH 220/66KV TRANSFORMER | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V99058A940166.1777777778 | V99058A9 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 40166.1778 | 40166.5576 | DAILY | 00001147 | SPIMAINT | Upgrade cool fans & their control equip B1 Tr | SPIPOWER | V990 | V990 - ASEA 150MVA TRANS COOLING SYSTEM OVERHAUL | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z71958C040166.21875 | Z71958C0 |  | Parent | TRUE | NO.2 220KV BUS AT CBTS | 40166.2188 | 40166.7812 | REPDAILY | 00359379 | VEN_AUG | Install new Bus connections to new B3 Trans CB ROI | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z71958C140166.21875 | Z71958C1 | Z71958C0 | Child | FALSE | B2 220/66KV TRANS AT CBTS | 40166.2188 | 40166.7812 | DAILY | 00353077 | VEN_AUG | Rebate for Bus outage | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1032065740166.25 | 10320657 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 40166.25 | 40166.4285 | DAILY | 00337579 | SPIMAINT | A3 TRANS TOP UP OIL WHITE PH 220KV BUSHHING | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X89058A340166.28125 | X89058A3 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40166.2812 | 40166.4563 | REPDAILY | 00319999 | SPICAPX | SOR-Erect Lindsay ERS Masts between T591 and T603 | SPIPOWER | X890 | X890 - (HYTS-APD) LINE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X90758A940167.2083333333 | X90758A9 |  | Parent | FALSE | ROTS NO.3 500KV LINE AT SMTS | 40167.2083 | 40167.7215 | DAILY | 00012438 | SPICAPX | REMOVE ROTS 3 LINE 500KV CVT'S | SPIPOWER | X907 | X907 - TYREE CVT REPLACEMENT PROGRAM | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z71958C040167.21875 | Z71958C0 |  | Parent | TRUE | NO.2 220KV BUS AT CBTS | 40167.2188 | 40167.616 | REPDAILY | 00359379 | VEN_AUG | Install new Bus connections to new B3 Trans CB ROI | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z71958C140167.21875 | Z71958C1 | Z71958C0 | Child | FALSE | B2 220/66KV TRANS AT CBTS | 40167.2188 | 40167.616 | DAILY | 00353077 | VEN_AUG | Rebate for Bus outage | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X89058A340167.2291666667 | X89058A3 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40167.2292 | 40167.4347 | REPDAILY | 00319999 | SPICAPX | SOR-Erect Lindsay ERS Masts between T591 and T603 | SPIPOWER | X890 | X890 - (HYTS-APD) LINE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058M140167.275 | X87058M1 |  | Parent | FALSE | TSTS-TTS 220KV WT | 40167.275 | 40167.4187 | DAILY | 00022783 | SPICAPX | TSTS-TTS Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z71958D240167.5819444445 | Z71958D2 |  | Parent | FALSE | B3 220/66KV TRANS AT CBTS | 40167.5819 | 40167.7208 | DAILY | 00368875 | SPICAPX | Commissioning B3 220/66KV TRANS AT CBTS | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X90758B240168.2083333333 | X90758B2 |  | Parent | FALSE | APD NO.1 500KV LINE AT HYTS | 40168.2083 | 40168.65 | REPDAILY | 00027386 | SPICAPX | Out W/O APD No1 Line Wph CVT replacement | SPIPOWER | X907 | X907 - TYREE CVT REPLACEMENT PROGRAM | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V839511740168.2840277778 | V8395117 |  | Parent | FALSE | EX - JLGB 220KV BUS CVT R/PH AT JLGB | 40168.284 | 40168.625 | DAILY | [12 empty] | 0
_1032066140168.3340277778 | 10320661 |  | Parent | FALSE | NO.4 UNIT 230/10.5KV TRANS AT JLGA | 40168.334 | 40168.625 | CONT | 00009819 | GENCO | Isolated for Power Station | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1032066040168.3576388889 | 10320660 |  | Parent | FALSE | NO.2 UNIT 230/10.5KV TRANS AT JLGB | 40168.3576 | 40169.5938 | CONT | 00009831 | GENCO | Power Station requested Isolation | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1031929540169.25 | 10319295 |  | Parent | FALSE | H2 330/220KV TRANS BANK AT SMTS | 40169.25 | 40169.3576 | DAILY | 00026102 | SPIMAINT | REPAIR THERMO FAULT 330KV DROPPER | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031621040169.3932407407 | 10316210 |  | Parent | FALSE | EX - FUTURE KMS 66KV FDR CB AT SMTS | 40169.3932 | 40169.3933 | DAILY | [12 empty] | 0
_1032071740169.4958333333 | 10320717 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 40169.4958 | 40169.5042 | DAILY | [12 empty] | 0
_1032079540170.5986111111 | 10320795 |  | Parent | FALSE | SYN/COND AT FBTS | 40170.5986 | 40170.7153 | DAILY | 00002697 | FAULT | FBTS: SynCon Trip Bearing Oil level | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032023240175.7916666667 | 10320232 |  | Parent | FALSE | NO.2 GEN 220/16.5KV TRANS AT HWPS | 40175.7917 | 40177.816 | CONT | 00009641 | GENCO | HWPS No3 Gen Tran Isolated for Power Station | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1032061340176.2548611111 | 10320613 |  | Parent | FALSE | B2 220/66KV TRANS AT HTS | 40176.2549 | 40176.4882 | DAILY | 00004446 | SPIMAINT | REPLACE DEFECTIVE COOLING FAN | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032086040177.8888888889 | 10320860 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 40177.8889 | 40178.4514 | CONT | [12 empty] | 0
_1032087340178.6256944445 | 10320873 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 40178.6257 | 40179.6222 | CONT | 00356081 | GENCO | HWPS No3 Gen Tran Isolated for Power Station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032087740180.0715277778 | 10320877 |  | Parent | FALSE | DPS -MBTS 220KV NW | 40180.0715 | 40180.3278 | CONT | 00060195 | FAULT | DPS 220KV Line Tripped Auto due to Lightning | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032088240182.2958333333 | 10320882 |  | Parent | FALSE | NO.2 GEN 220/16.5KV TRANS AT HWPS | 40182.2958 | 40183.3424 | CONT | 00009641 | GENCO | No2 Gen Trans isolation for power station | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1032065540183.2465277778 | 10320655 |  | Parent | FALSE | NO.1 66KV BUS EXTENSION AT TSTS | 40183.2465 | 40183.6347 | DAILY | 00007673 | SPIMAINT | BUS OUTAGE FOR SECONDARY WIRING | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032095740183.5881944445 | 10320957 |  | Parent | FALSE | NO.2 GEN 220/16.5KV TRANS AT HWPS | 40183.5882 | 40183.6644 | CONT | 00009641 | GENCO | No2 Gen Trans isolation for power station | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1032095940183.9631944445 | 10320959 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 40183.9632 | 40188.0909 | CONT | 00356086 | GENCO | SCAP for Unit 8 isolation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032100940185.6284722222 | 10321009 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 40185.6285 | 40186.6847 | CONT | 00356080 | GENCO | No2 Gen Trans isolation for power station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032102640186.9673611111 | 10321026 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 40186.9674 | 40189.059 | CONT | 00356081 | GENCO | No3 Gen Trans isolation for power station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032103140187.4895833333 | 10321031 |  | Parent | FALSE | LYPS NO.2 500KV LINE AT HWTS | 40187.4896 | 40187.5042 | CONT | 00016235 | FORCED | HWTS-LYPS No 2 500kv Line to clear CB Lockout | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032103040187.4895833333 | 10321030 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 40187.4896 | 40190.2799 | CONT | [12 empty] | 0
_1032103540187.9861111111 | 10321035 |  | Parent | FALSE | NO.2 330KV BUS AT WOTS | 40187.9861 | 40188.0757 | CONT | 00004042 | FAULT | Trip No2 330KV Bus due to SD Failure on H2 Transf | SPIPOWER |  |  | Bus | Alstom | 330 | NON AER ELEMENT | EXCLUDED |  | 0
_1032103740187.9861111111 | 10321037 |  | Parent | FALSE | NO.2 330KV CAPACITOR BANK CONTROL EQUIPMENT AT WOTS | 40187.9861 | 40188.0757 | CONT | [12 empty] | 0
_1032103640187.9861111111 | 10321036 |  | Parent | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 40187.9861 | 40189.4708 | CONT | 00004037 | FAULT | H2 330/66KV Transformer Surge Diverter Failure | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032103840188.0319444445 | 10321038 |  | Parent | FALSE | EX - NO.2 GEN TRANS 220KV CB AT HWPS | 40188.0319 | 40188.5381 | CONT | [12 empty] | 0
_V8D258A940188.2083333333 | V8D258A9 |  | Parent | FALSE | SMTS NO.3 500KV LINE AT ROTS (RTF) | 40188.2083 | 40188.6632 | DAILY | 00356731 | SPIMAINT | Replace SDs North end Ducting | SPIPOWER | V8D2 | V8D2 - (ROTS) REPLACE 220KV BUS DUCT SLIDING SUPPORT | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032098740188.3131944445 | 10320987 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40188.3132 | 40188.3201 | DAILY | 00022630 | SW_NEM | MLTS reactor Switching for AEMO | VENCORP |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1032098840188.3131944445 | 10320988 | 10320987 | Child | FALSE | HYTS-APD 1 500KV W | 40188.3132 | 40188.3201 | DAILY | 00319998 | SW_NEM | MLTS reactor Switching for AEMO | VENCORP |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1032098940188.3131944445 | 10320989 | 10320987 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40188.3132 | 40188.3201 | DAILY | 00002863 | SW_NEM | MLTS reactor Switching for AEMO | VENCORP |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 3
_1032099040188.3305555556 | 10320990 |  | Parent | TRUE | MLTS-HYTS 2 500KV W | 40188.3306 | 40188.3375 | DAILY | 00022633 | SW_NEM | MLTS reactor Switching or AEMO | VENCORP |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1032099340188.3305555556 | 10320993 | 10320990 | Child | FALSE | HYTS-APD 2 500KV W | 40188.3306 | 40188.3375 | DAILY | 00319999 | SW_NEM | MLTS reactor Switching or AEMO | VENCORP |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1032099640188.3305555556 | 10320996 | 10320990 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40188.3306 | 40188.3375 | DAILY | 00002862 | SW_NEM | MLTS reactor Switching or AEMO | VENCORP |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 3
_1032102740188.3305555556 | 10321027 |  | Parent | FALSE | APD NO.2 500KV LINE AT HYTS | 40188.3306 | 40188.4556 | DAILY | 00060938 | APDALCOA | HVS: Line de-energised for APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029033040189.2680555556 | 10290330 |  | Parent | FALSE | W3 GEN TRANS NO.2 BUS 220KV CB AT YPS | 40189.2681 | 40203.4653 | CONT | [12 empty] | 0
_1032088840190.25 | 10320888 |  | Parent | TRUE | MLTS NO.1 500KV LINE CB AT HYTS | 40190.25 | 40190.3 | DAILY | [12 empty] | 0
_1032094240190.25 | 10320942 | 10320888 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40190.25 | 40190.3 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 TRANS during 500kV CB outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032105240190.2798611111 | 10321052 |  | Parent | FALSE | LYPS NO.2 500KV LINE NO.4 BUS CB AT HWTS | 40190.2799 | 40191.5771 | CONT | [12 empty] | 0
_1032107640190.63125 | 10321076 |  | Parent | FALSE | BETS-KGTS 220KV NB | 40190.6312 | 40196.5944 | CONT | 00026196 | BUSHFIRE | BETS-KGTS 220kV LINE 5 TOWERS DOWN Pyramid Hill | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 1 | FM event and incorrectly entered in outage data base
_X7E458T140191.2395833333 | X7E458T1 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40191.2396 | 40191.6694 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T228and T238 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032088940191.2569444444 | 10320889 |  | Parent | TRUE | MLTS NO.2 500KV LINE CB AT HYTS | 40191.2569 | 40191.2972 | DAILY | [12 empty] | 0
_1032094340191.2569444444 | 10320943 | 10320889 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40191.2569 | 40191.2972 | DAILY | 00002862 | SPIMAINT | Rebate W/O M2 Trans during 500kV CB outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032086740191.2625 | 10320867 |  | Parent | FALSE | B3 220/66KV TRANS AT SVTS | 40191.2625 | 40191.5708 | DAILY | 00004851 | SPIMAINT | REPAIR COOLING OIL PUMP | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032100740191.26875 | 10321007 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 40191.2688 | 40191.4431 | DAILY | 00022690 | APDALCOA | Outage requested by ALCOA for Work at PTH | APDALCOA |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1029435340191.3180555556 | 10294353 |  | Parent | TRUE | SESS NO.2 275KV LINE/M2 TRANS CB CT R/PH AT HYTS | 40191.3181 | 40191.3535 | DAILY | [12 empty] | 0
_1032061740191.3180555556 | 10320617 | 10294353 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40191.3181 | 40191.3535 | DAILY | 00002862 | SPIMAINT | Rebate W/O M2 Trans during 275kV CB outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029152140192.2131944445 | 10291521 |  | Parent | TRUE | NO.5 220KV BUS AT BLTS | 40192.2132 | 40192.5833 | DAILY | 00002647 | SPIMAINT | O/Haul NO.5 220KV BUS AT BLTS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1029428540192.2131944445 | 10294285 | 10291521 | Child | FALSE | 3-5 220KV BUS TIE CB CT R/PH AT BLTS | 40192.2132 | 40192.5833 | DAILY | [12 empty] | 0
_1029428740192.2131944445 | 10294287 | 10291521 | Child | FALSE | 4-5 220KV BUS TIE CB CT R/PH AT BLTS | 40192.2132 | 40192.5833 | DAILY | [12 empty] | 0
_1032112140192.5210300926 | 10321121 |  | Parent | FALSE | NO.7 GEN TRANS LINE AT HWPS | 40192.521 | 40195.076 | CONT | 00356085 | GENCO | Unit 7 isolation for SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032000640192.6881944445 | 10320006 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 40192.6882 | 40195.9847 | CONT | 00337579 | SPIMAINT | A3 TRANS WHITE PH 220KV BUSHING REPLACEMENT | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E458S940193.2402777778 | X7E458S9 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40193.2403 | 40193.6778 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T240 and T241 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032101840193.2583333333 | 10321018 |  | Parent | FALSE | B4 220/66KV TRANS AT RTS | 40193.2583 | 40193.4611 | DAILY | 00007332 | SPIMAINT | REPAIR DEFECTIVE FAN | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z73458A240194.1784722222 | Z73458A2 |  | Parent | FALSE | NO.1 220KV BUS AT KTS | 40194.1785 | 40194.5556 | DAILY | 00001169 | SPICAPX | EST BIPOD CONNTNS FROM No.1 220 BUS TO B5 ROI | SPIPOWER | Z734 | Z734 - (KTS) 5TH 220/66KV TRANSFORMER | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032113540194.2763888889 | 10321135 |  | Parent | FALSE | NO.1 66KV BUS EXTENSION AT ERTS | 40194.2764 | 40194.5 | DAILY | 00004382 | DBPROX | VSCAP to Jemena | DISTCO |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z73458B240194.5347222222 | Z73458B2 |  | Parent | FALSE | B5 220/66KV TRANS AT KTS | 40194.5347 | 40197.5167 | DAILY | 00369184 | SPICAPX | B5 TRANS ITS 220 & 66KV CB'S | SPIPOWER | Z734 | Z734 - (KTS) 5TH 220/66KV TRANSFORMER | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1032081140194.6479166667 | 10320811 | Z71958D4 | Child | FALSE | B2 220/66KV TRANS AT CBTS | 40194.6479 | 40194.6937 | DAILY | 00353077 | VEN_AUG | Rebate for Bus outage to connect new B2 Trans | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_Z71958D440194.6479166667 | Z71958D4 |  | Parent | TRUE | NO.2 220KV BUS AT CBTS | 40194.6479 | 40194.694 | DAILY | 00359379 | VEN_AUG | Connect new B3 Trans No2 Bus 220KV CB Bus ROI | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032114040194.7171064815 | 10321140 |  | Parent | FALSE | B3 TRANS NO.2 BUS 220KV CB AT CBTS | 40194.7171 | 40195.2083 | CONT | [12 empty] | 0
_Z73458A340195.1708333333 | Z73458A3 |  | Parent | FALSE | NO.3 220KV BUS AT KTS | 40195.1708 | 40195.5257 | DAILY | 00001171 | SPICAPX | ESTAB BIPOD CONNTNS FROM No.3 BUS TO B5 ROI | SPIPOWER | Z734 | Z734 - (KTS) 5TH 220/66KV TRANSFORMER | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z71958D540195.23125 | Z71958D5 |  | Parent | FALSE | B3 220/66KV TRANS AT CBTS | 40195.2312 | 40195.7069 | DAILY | 00368875 | VEN_AUG | Connect new B3 Trans No2 Bus 220KV CB Trans ROI | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X7E458T240195.2506944445 | X7E458T2 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40195.2507 | 40195.5875 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T227 and T268 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z73458A440196.1770833333 | Z73458A4 |  | Parent | FALSE | NO.2 66KV BUS AT KTS | 40196.1771 | 40196.6562 | DAILY | 00001173 | SPICAPX | EST CONNTNS FROM No.2 66 BUS TO B5 ROI | SPIPOWER | Z734 | Z734 - (KTS) 5TH 220/66KV TRANSFORMER | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032010440196.3541666667 | 10320104 |  | Parent | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB AT DDTS | 40196.3542 | 40196.4083 | DAILY | [12 empty] | 0
_1032120040196.65625 | 10321200 |  | Parent | FALSE | B5 TRANS NO.2 BUS 66KV CB AT KTS | 40196.6562 | 40197.2778 | CONT | [12 empty] | 0
_X7E458T340197.2645833333 | X7E458T3 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40197.2646 | 40197.684 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T299 and T312 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032010140197.5138888889 | 10320101 |  | Parent | FALSE | BATS 220KV LINE NO.1 BUS CB AT BETS | 40197.5139 | 40197.5979 | REPDAILY | [12 empty] | 0
_Z73458B940197.5173611111 | Z73458B9 |  | Parent | FALSE | B5 220/66KV TRANS AT KTS | 40197.5174 | 40206.2778 | CONT | 00369184 | SPICAPX | EART, PRI CONNECT'S TESTING OF B5 TRANS | SPIPOWER | Z734 | Z734 - (KTS) 5TH 220/66KV TRANSFORMER | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1032010240197.6069444444 | 10320102 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT BETS | 40197.6069 | 40197.6312 | REPDAILY | [12 empty] | 0
_1032010140198.3180555556 | 10320101 |  | Parent | FALSE | BATS 220KV LINE NO.1 BUS CB AT BETS | 40198.3181 | 40198.4014 | REPDAILY | [12 empty] | 0
_1032010240198.4694444445 | 10320102 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT BETS | 40198.4694 | 40198.4965 | REPDAILY | [12 empty] | 0
_X7E458T440199.2541666667 | X7E458T4 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40199.2542 | 40199.7181 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T274 and T288 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032098440199.2708333333 | 10320984 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 40199.2708 | 40199.3667 | DAILY | 00351939 | SPIMAINT | Out W/O No1 220 Cap CB de-en for functional checks | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1032009940199.3194444444 | 10320099 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT BATS | 40199.3194 | 40199.4042 | REPDAILY | [12 empty] | 0
_1032124940199.3715277778 | 10321249 |  | Parent | FALSE | WD 66KV FDR AT TSTS | 40199.3715 | 40199.5833 | DAILY | 00019973 | DBPROX | VSCAP to DISCO TSTS-WD 66kV Fdr | DISTCO |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032010040199.41875 | 10320100 |  | Parent | FALSE | BETS 220KV LINE NO.2 BUS CB AT BATS | 40199.4187 | 40199.5007 | REPDAILY | [12 empty] | 0
_1032126840199.9178935185 | 10321268 |  | Parent | FALSE | NO.8 GEN TRANS 220KV CB AT HWPS | 40199.9179 | 40203.6799 | CONT | [12 empty] | 0
_V9A658A440200.3666666667 | V9A658A4 |  | Parent | FALSE | B1 TRANS 220KV CB AT TTS | 40200.3667 | 40200.6188 | CONT | [12 empty] | 0
_1032123440200.3791666667 | 10321234 |  | Parent | FALSE | SVC COOLING SYSTEM AT KGTS | 40200.3792 | 40200.3847 | DAILY | [12 empty] | 0
_1032129440200.8333333333 | 10321294 |  | Parent | FALSE | HWTS NO.2 220KV LINE NO.2 BUS CB AT HWPS | 40200.8333 | 40200.834 | CONT | [12 empty] | 0
_1032129540200.8333333333 | 10321295 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 40200.8333 | 40209.5694 | CONT | 00356080 | GENCO | No2 Gen Trans isolation for power station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E458T540201.2548611111 | X7E458T5 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40201.2549 | 40201.6875 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T215 and T228 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E958C840201.3159722222 | X7E958C8 |  | Parent | FALSE | SMTS 500KV LINE AT KTS | 40201.316 | 40201.4313 | DAILY | 00015991 | SPICAPX | de-enrgse line as part of SMTS/A2 trans cb commiss | SPIPOWER | X7E9 | X7E9 - (KTS) 500KV CT & CB | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458T640202.2534722222 | X7E458T6 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40202.2535 | 40202.6653 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T202 and T215 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032130440203.7854166667 | 10321304 |  | Parent | FALSE | NO.2 22KV BUS AT BETS | 40203.7854 | 40203.8229 | DAILY | 00016376 | FAULT | BET2 FDR CB 22KV CT Failure (Powercor Asset). | SPIPOWER |  |  | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E458T840205.25 | X7E458T8 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40205.25 | 40205.7132 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T162 and T183 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V9A658A140205.2520833333 | V9A658A1 |  | Parent | FALSE | B1 TRANS 220KV CB AT TTS | 40205.2521 | 40206.6958 | CONT | [12 empty] | 0
_1029438940205.34375 | 10294389 |  | Parent | FALSE | SHTS NO.1 220KV LINE NO.2 BUS CB CT R/PH AT GNTS | 40205.3438 | 40205.5076 | DAILY | [12 empty] | 0
_1030156840206.2638888889 | 10301568 |  | Parent | FALSE | WBTS 220KV LINE NO.2 BUS CB AT HOTS | 40206.2639 | 40206.566 | DAILY | [12 empty] | 0
_Z73458B840206.3263888889 | Z73458B8 |  | Parent | FALSE | B5 TRANS NO.2 BUS 66KV CB AT KTS | 40206.3264 | 40206.4632 | DAILY | [12 empty] | 0
_Z73458C240206.3263888889 | Z73458C2 |  | Parent | FALSE | B5 220/66KV TRANS AT KTS | 40206.3264 | 40207.2986 | CONT | 00369184 | SPICAPX | B5 TRANS ITS 220 & 66KV CB'S | SPIPOWER | Z734 | Z734 - (KTS) 5TH 220/66KV TRANSFORMER | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_Z73458B740206.4722222222 | Z73458B7 |  | Parent | FALSE | B5 TRANS NO.3 BUS 66KV CB AT KTS | 40206.4722 | 40206.6076 | DAILY | [12 empty] | 0
_1032139040206.8951388889 | 10321390 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 40206.8951 | 40207.7965 | CONT | 00356086 | GENCO | Unit 8 220kV isolations & SCAP for P/Stn | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029345640207.2576388889 | 10293456 |  | Parent | TRUE | B5 220/66KV TRANS NO.1 BUS 66KV CABLE AT TTS | 40207.2576 | 40207.6771 | DAILY | 00327888 | SPIMAINT | O/H B5 TRANS NO.1 BUS 66KV CABLE AT TTS | SPIPOWER |  |  | Circuits | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032234740207.2576388889 | 10322347 | 10293456 | Child | FALSE | B5 220/66KV TRANS AT TTS | 40207.2576 | 40207.6771 | DAILY | 00327874 | SPIMAINT | O/H B5 TRANS NO.1 BUS 66KV CABLE AT TTS | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z73458C140207.3006944445 | Z73458C1 |  | Parent | FALSE | B5 220/66KV TRANS AT KTS | 40207.3007 | 40220.5764 | DAILY | 00369184 | SPICAPX | B5 TRANS ITS 220 & 66KV CB'S | SPIPOWER | Z734 | Z734 - (KTS) 5TH 220/66KV TRANSFORMER | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1032139840207.4805555556 | 10321398 |  | Parent | FALSE | KTS NO.1 220KV LINE NO.3 BUS CB AT TTS | 40207.4806 | 40207.65 | DAILY | [12 empty] | 0
_1032142340207.9305555556 | 10321423 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 40207.9306 | 40211.9549 | CONT | [12 empty] | 0
_1027293140208.2333333333 | 10272931 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 40208.2333 | 40208.6007 | DAILY | [12 empty] | 0
_V9A658A340208.2347222222 | V9A658A3 |  | Parent | TRUE | ROTS 220KV LINE CB AT TTS | 40208.2347 | 40211.6208 | CONT | [12 empty] | 0
_V9A658A540208.2347222222 | V9A658A5 | V9A658A3 | Child | FALSE | ROTS 220KV LINE AT TTS | 40208.2347 | 40211.6208 | CONT | 00015733 | SPIMAINT | REPLACE OIL IN 220KV CB BUSHINGS | SPIPOWER | V9A6 | V9A6 - (TTS) REPLACE OIL IN 24 - 220KV BTH BUSHINGS | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X7E458T940208.2583333333 | X7E458T9 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40208.2583 | 40208.6243 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T148 and T162 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032142740209.6555555556 | 10321427 |  | Parent | FALSE | EX - B1 220/66KV TRANS AT MWTS | 40209.6556 | 40284.6486 | CONT | 00010265 | FAULT | MWTS B1 220/66KV TRANS WINDING FAILURE | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032143440209.7215277778 | 10321434 |  | Parent | FALSE | BETS/SHTS LINE 220KV CB AT FVTS | 40209.7215 | 40209.7708 | CONT | [12 empty] | 0
_1032143740209.7402777778 | 10321437 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.1 BUS CB AT LYPS | 40209.7403 | 40211.3847 | CONT | [12 empty] | 0
_1032143540209.7402777778 | 10321435 |  | Parent | TRUE | LYPS NO.1 500KV LINE CB AT HWTS | 40209.7403 | 40212.7583 | CONT | [12 empty] | 0
_1032150540209.7402777778 | 10321505 | 10321435 | Child | FALSE | LYPS NO.1 500KV LINE AT HWTS | 40209.7403 | 40212.7583 | CONT | 00016234 | FORCED | LYPS -HWTS 1 LINE ofloaded by CB Failure at HWTS | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032143340209.7409722222 | 10321433 |  | Parent | FALSE | A2 515/230KV TRANS BANK AT HWTS | 40209.741 | 40209.7625 | CONT | 00337572 | FORCED | HWTS A2 550/220kV Trans Forced out for CB Fault | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E458T040210.2576388889 | X7E458T0 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40210.2576 | 40210.6556 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T148 and T139 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032144240210.2895833333 | 10321442 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 40210.2896 | 40211.1604 | CONT | 00356080 | GENCO | HWPS No2 Gen Trans Isolated for Powersdtation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E458U540211.2527777778 | X7E458U5 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40211.2528 | 40211.6528 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T183 and T202 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V7A058A840211.2888888889 | V7A058A8 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT SMTS | 40211.2889 | 40215.4604 | CONT | [12 empty] | 0
_1032147240211.3847222222 | 10321472 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.1 BUS CB AT LYPS | 40211.3847 | 40211.6417 | DAILY | [12 empty] | 0
_1032151340211.5618055556 | 10321513 |  | Parent | FALSE | B2 220/66KV TRANS AT KTS | 40211.5618 | 40211.5708 | DAILY | 00001148 | FORCED | B2 Trans at KTS offloaded due to loss of cooling | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032151540211.6569444445 | 10321515 |  | Parent | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 40211.6569 | 40212.1312 | CONT | 00004037 | FAULT | WOTS: No2 Trans S/D red phase failed. | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032153040211.9597222222 | 10321530 |  | Parent | FALSE | NO.8 GEN 220/16.5KV TRANS AT HWPS | 40211.9597 | 40215.3404 | CONT | 00009649 | GENCO | Outage Requested by Power Station | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1032137140212.3708333333 | 10321371 |  | Parent | FALSE | WD 66KV FDR AT TSTS | 40212.3708 | 40212.5542 | DAILY | 00019973 | SPIMAINT | VSCAP Required for Live Line Training | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032155340212.5854166667 | 10321553 |  | Parent | TRUE | S457 TSTS-TTS R 220KV | 40212.5854 | 40212.7063 | DAILY | [12 empty] | 0
_1032194540212.5854166667 | 10321945 | 10321553 | Child | FALSE | TSTS 220KV LINE AT TTS | 40212.5854 | 40212.7063 | DAILY | 00015736 | FORCED | TSTS Line forced out to repair broken susp clamp | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032157540212.6701388889 | 10321575 |  | Parent | FALSE | B4 220/66KV TRANS AT RWTS | 40212.6701 | 40212.7729 | DAILY | 00007451 | FORCED | RWTS B4 Trans emergency repair broken Neutral Isol | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458U640213.2444444445 | X7E458U6 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40213.2444 | 40213.6208 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T129 and T139 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V9A658A240213.25625 | V9A658A2 |  | Parent | TRUE | BTS NO.3 220KV LINE CB AT TTS | 40213.2562 | 40215.6403 | CONT | [12 empty] | 0
_V9A658A640213.25625 | V9A658A6 | V9A658A2 | Child | FALSE | BTS NO.3 220KV LINE AT TTS | 40213.2562 | 40215.6403 | CONT | 00015724 | SPIMAINT | REPLACE OIL IN 220KV CB BUSHINGS | SPIPOWER | V9A6 | V9A6 - (TTS) REPLACE OIL IN 24 - 220KV BTH BUSHINGS | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032154740213.3444444445 | 10321547 |  | Parent | FALSE | EX - SMTS LINE/A2 TRANS 500KV CB AT KTS | 40213.3444 | 40213.5396 | DAILY | [12 empty] | 0
_1029553740214.2743055556 | 10295537 |  | Parent | FALSE | MLTS NO.2 220KV LINE NO.1 BUS CB AT BATS | 40214.2743 | 40214.5993 | DAILY | [12 empty] | 0
_1032166140214.9118055556 | 10321661 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 40214.9118 | 40216.7974 | CONT | [12 empty] | 0
_1029046140215.2118055556 | 10290461 |  | Parent | TRUE | NO.2 500KV BUS AT HWTS | 40215.2118 | 40215.6229 | DAILY | 00009799 | SPIMAINT | O/Haul NO.2 500KV BUS AT HWTS | SPIPOWER |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1030061440215.2118055556 | 10300614 | 10290461 | Child | FALSE | LYPS NO.1 500KV LINE CB AT HWTS | 40215.2118 | 40215.6229 | DAILY | [12 empty] | 0
_1030204240215.2118055556 | 10302042 | 10290461 | Child | FALSE | LYPS NO.1 500KV LINE AT HWTS | 40215.2118 | 40215.6229 | DAILY | 00016234 | SPIMAINT | REBATE FOR BUS OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030204340215.2118055556 | 10302043 | 10290461 | Child | FALSE | HWPS NO.2 220KV LINE AT HWTS | 40215.2118 | 40215.6229 | DAILY | 00016243 | SPIMAINT | REBATE FOR BUS OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031839240215.2118055556 | 10318392 |  | Parent | TRUE | LYPS NO.1 500KV LINE CB AT HWTS | 40215.2118 | 40215.6229 | CONT | [12 empty] | 0
_1032225540215.2118055556 | 10322255 | 10318392 | Child | FALSE | LYPS NO.1 500KV LINE CB LINE SIDE ROI AT HWTS | 40215.2118 | 40215.6229 | CONT | [12 empty] | 0
_X7E458U740215.2465277778 | X7E458U7 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40215.2465 | 40215.6326 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T116 and T129 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z73058P240215.2694444445 | Z73058P2 |  | Parent | FALSE | NO.1 220KV BUS AT SMTS | 40215.2694 | 40215.3118 | DAILY | 00366543 | VEN_AUG | FIT MECH INTRLCKS AND ADJUST ROI's | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X87058L840215.2722222222 | X87058L8 |  | Parent | FALSE | KTS -GTS 3 220KV WY | 40215.2722 | 40215.5889 | REPDAILY | 00022709 | SPICAPX | KTS-GTS No3 3 Line Insulator Replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z73058P840215.3208333333 | Z73058P8 |  | Parent | FALSE | NO.2 220KV BUS AT SMTS | 40215.3208 | 40215.3625 | DAILY | 00366542 | VEN_AUG | FIT MECH INTRLCKS AND ADJUST ROI's | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z73058P740215.3868055556 | Z73058P7 |  | Parent | FALSE | H2 330/220KV TRANS BANK AT SMTS | 40215.3868 | 40215.4049 | DAILY | 00026102 | VEN_AUG | FIT MECH INTRLCKS AND ADJUST ROI's | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z73058P440215.4097222222 | Z73058P4 |  | Parent | FALSE | TTS NO.2 220KV LINE AT SMTS | 40215.4097 | 40215.4319 | DAILY | 00367362 | VEN_AUG | FIT MECH INTRLCKS AND ADJUST ROI's | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z73058P340215.4361111111 | Z73058P3 |  | Parent | FALSE | TTS NO.1 220KV LINE AT SMTS | 40215.4361 | 40215.4674 | DAILY | 00367361 | VEN_AUG | FIT MECH INTRLCKS AND ADJUST ROI's | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z73058P540215.4729166667 | Z73058P5 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT SMTS | 40215.4729 | 40215.4972 | DAILY | 00026101 | VEN_AUG | FIT MECH INTRLCKS AND ADJUST ROI's | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031989640216.25 | 10319896 | 10319899 | Child | FALSE | SVTS NO.2 220KV LINE E/SW AT ROTS | 40216.25 | 40216.4896 | DAILY | [12 empty] | 0
_1031989940216.25 | 10319899 |  | Parent | TRUE | SVTS NO.2 220KV LINE AT ROTS | 40216.25 | 40216.4896 | DAILY | 00023968 | SPIMAINT | Repair 220KV Line Side Isolator | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458U840216.25 | X7E458U8 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40216.25 | 40216.65 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T104 and T116 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032161940216.2652777778 | 10321619 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT RWTS (CONNECTED TO RWT11) | 40216.2653 | 40216.5403 | DAILY | 00368934 | DBPROX | VSCAP to DOC Outage Requested by DistCo | DISTCO |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X89058A540217.25 | X89058A5 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40217.25 | 40217.7333 | DAILY | 00319999 | SPICAPX | Connect ERS mast bypass line into T623 and T627 | SPIPOWER | X890 | X890 - (HYTS-APD) LINE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029059340217.2569444444 | 10290593 |  | Parent | FALSE | JLTS NO.4 220KV LINE NO.4 BUS CB AT HWPS | 40217.2569 | 40219.5222 | CONT | 00009614 | SPIMAINT | CL.1 O/HAUL - BTH JW419 & JW420 CB | SPIPOWER | [8 empty] | 0 | 10290593 |  | CL.1 O/HAUL - BTH JW419 & JW420 CB | 00009614 | CB |  | HWPS | CB | SPIMAINT | CONT
_1010283540217.4256944445 | 10102835 |  | Parent | FALSE | WBTS 220KV LINE NO.1 BUS CB AT HOTS | 40217.4257 | 40221.4799 | CONT | [12 empty] | 0
_1032002440218.1756944445 | 10320024 | X70658R3 | Child | FALSE | GTS NO.3 220KV LINE AT KTS | 40218.1757 | 40218.309 | DAILY | 00368494 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658R340218.1756944445 | X70658R3 |  | Parent | TRUE | NO.3 220KV BUS AT KTS | 40218.1757 | 40218.309 | DAILY | 00001171 | SPICAPX | REM BIPODS GTS 3L 3B CB B/S ROI & RMVE 3L CT'S | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032107040218.2673611111 | 10321070 |  | Parent | FALSE | GTS NO.2 LINE/A1 TRANS 220KV CB AT MLTS | 40218.2674 | 40218.5861 | DAILY | [12 empty] | 0
_1029152340218.3055555556 | 10291523 |  | Parent | FALSE | NO.2 22KV BUS AT BLTS | 40218.3056 | 40218.5542 | REPDAILY | 00002655 | SPIMAINT | O/Haul NO.2 22KV BUS AT BLTS | SPIPOWER |  |  | Bus | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658S840218.3395833333 | X70658S8 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE AT KTS | 40218.3396 | 40218.625 | DAILY | 00015986 | SPICAPX | DISCONNECT GTS 3L-3B L/S ROI from GTS 3 LINE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029152340219.2916666667 | 10291523 |  | Parent | FALSE | NO.2 22KV BUS AT BLTS | 40219.2917 | 40219.575 | REPDAILY | 00002655 | SPIMAINT | O/Haul NO.2 22KV BUS AT BLTS | SPIPOWER |  |  | Bus | Western | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1032186340219.575 | 10321863 |  | Parent | FALSE | NO.2 66KV BUS AT BLTS | 40219.575 | 40220.4917 | DAILY | 00002650 | SPIMAINT | REPAIR FAULTY 66KV ISOL | SPIPOWER |  |  | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032287240219.575 | 10322872 |  | Parent | FALSE | U1 66/22KV TRANS AT BLTS | 40219.575 | 40220.4917 | CONT | 00362556 | SPIMAINT | Repair 66kV CB BS Isolator | SPIPOWER |  |  | Connection Transformers | Western | 66 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032187340219.7006944444 | 10321873 |  | Parent | FALSE | B2 220/66KV TRANS AT WBTS | 40219.7007 | 40220.7583 | CONT | 00366200 | FAULT | B2 220/66KV TRANS AT WBTS Tripped | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_X7E958C940220.2923611111 | X7E958C9 |  | Parent | FALSE | EX - SMTS LINE/A2 TRANS 500KV CB AT KTS | 40220.2924 | 40220.4118 | DAILY | [12 empty] | 0
_Z73458C640220.5770833333 | Z73458C6 |  | Parent | FALSE | B5 220/66KV TRANS AT KTS | 40220.5771 | 40222.1597 | DAILY | 00369184 | SPICAPX | INJECTION TESTS ON B5 TR TO VERIFY PROT SCHME | SPIPOWER | Z734 | Z734 - (KTS) 5TH 220/66KV TRANSFORMER | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1032189340220.8916666667 | 10321893 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 40220.8917 | 40223.8278 | CONT | 00356081 | GENCO | HWPS No3 Gen Trans Isolated for Powerstation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032186140221.5451388889 | 10321861 |  | Parent | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB AT HWTS | 40221.5451 | 40221.5465 | DAILY | [12 empty] | 0
_1032192740222.2118055556 | 10321927 |  | Parent | FALSE | NO.5 GEN 220/16.5KV TRANS AT HWPS | 40222.2118 | 40222.4882 | CONT | 00009646 | GENCO | Power Station Requirement | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1029147540222.2118055556 | 10291475 |  | Parent | FALSE | SYN/COND AT FBTS | 40222.2118 | 40223.6097 | CONT | 00002697 | SPIMAINT | Annual O/HAUL - FBTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458U940222.2423611111 | X7E458U9 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40222.2424 | 40222.6646 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T91 andT95 and T95 and T104 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032193340222.2847222222 | 10321933 |  | Parent | FALSE | B5 220/66KV TRANS AT KTS | 40222.2847 | 40223.5437 | CONT | 00369184 | SPICAPX | Commissioning of B5 Trans | SPIPOWER | Z734 | Z734 - (KTS) 5TH 220/66KV TRANSFORMER | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_Z71958E240222.3472222222 | Z71958E2 |  | Parent | FALSE | B1 220/66KV TRANS AT CBTS | 40222.3472 | 40222.625 | DAILY | 00353076 | VEN_AUG | INSTALL GUY WIRES IN 66KV YARD | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_X7E458U040223.2451388889 | X7E458U0 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40223.2451 | 40223.6424 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T78 andT91 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z71958E140223.2527777778 | Z71958E1 |  | Parent | FALSE | B3 220/66KV TRANS AT CBTS | 40223.2528 | 40223.6312 | DAILY | 00368875 | VEN_AUG | INSTALL LIGHTING GANTRY | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1032188140223.2534722222 | 10321881 |  | Parent | TRUE | A2 TRANS Y PROT AT ROTS | 40223.2535 | 40223.6007 | DAILY | [12 empty] | 0
_1032188440223.2534722222 | 10321884 | 10321881 | Child | FALSE | A2 515/220KV TRANS BANK AT ROTS | 40223.2535 | 40223.6007 | DAILY | 00362994 | SPIMAINT | Rebate for A2 Trans outage | SPIPOWER |  |  | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_X70658S940224.2104166667 | X70658S9 |  | Parent | FALSE | NO.3 220KV BUS AT KTS | 40224.2104 | 40224.6417 | DAILY | 00001171 | SPICAPX | REMOVE GTS 3 LINE 3 BUS CB BUS SIDE ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1029163840225.2381944445 | 10291638 |  | Parent | FALSE | EX - B3 220/66KV TRANS AT TTS | 40225.2382 | 40225.5958 | DAILY | 00001544 | SPIMAINT | 220 / 66kv B3 Transformer | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029554940225.2861111111 | 10295549 |  | Parent | FALSE | TGTS 220KV LINE NO.1 BUS CB AT BATS | 40225.2861 | 40225.6347 | DAILY | [12 empty] | 0
_V7A058A940225.40625 | V7A058A9 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT SMTS | 40225.4062 | 40228.4618 | CONT | [12 empty] | 0
_1029163640226.2326388889 | 10291636 |  | Parent | FALSE | B4 220/66KV TRANS AT TTS | 40226.2326 | 40226.675 | DAILY | 00001543 | SPIMAINT | overhaul B4 220/ 66KV Transformer at TTS | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458V140226.2395833333 | X7E458V1 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40226.2396 | 40226.7597 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T60 andT78 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032199440226.9444444444 | 10321994 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 40226.9444 | 40234.8668 | CONT | [12 empty] | 0
_X7E458V240227.2506944445 | X7E458V2 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40227.2507 | 40227.6722 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T48 andT60 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46558A040227.2548611111 | X46558A0 |  | Parent | TRUE | JLA NO.2 220KV LINE AT TBTS | 40227.2549 | 40227.5785 | DAILY | 00026919 | SPICAPX | B1 Trans & JLA No2 Line | SPIPOWER | X465 | X465 - (ATS,HTS,HYTS,MBTS,SVTS,TBTS,YPS) ENV IMPROVEMENT S4 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X46558A140227.2548611111 | X46558A1 | X46558A0 | Child | FALSE | B1 220/66KV TRANS AT TBTS | 40227.2549 | 40227.5785 | DAILY | 00004901 | SPICAPX | Tran Rebate | SPIPOWER | X465 | X465 - (ATS,HTS,HYTS,MBTS,SVTS,TBTS,YPS) ENV IMPROVEMENT S4 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_VA0858A040227.3541666667 | VA0858A0 |  | Parent | FALSE | B1 220/66KV TRANS AT MWTS | 40227.3542 | 40231.2743 | DAILY | 00351931 | SPIMAINT | HV Testing of Country Spare Transformer | SPIPOWER | VA08 | VA08 - (MWTS) SITE REPAIRS - B1 TRANS FAILURE - 31-01-2010 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1032201840227.9069444445 | 10322018 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT TTS | 40227.9069 | 40228.3257 | CONT | 00001485 | FAULT | NO2 66KV Capacitor Bank Tripped on Out of Balance | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029141940228.2743055556 | 10291419 |  | Parent | FALSE | NO.1 11/6.6KV AUX TRANS AT FBTS | 40228.2743 | 40228.5528 | DAILY | 00002730 | SPIMAINT | OVERHAUL OF AN AUXILIARY TRANSFORMER | SPIPOWER |  |  | Other Transformers | Western | 11 | NON AER ELEMENT | EXCLUDED |  | 0
_1032202340228.3263888889 | 10322023 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT TTS | 40228.3264 | 40228.6542 | DAILY | 00001485 | SPIMAINT | INVESTIGATE CAP BANK TRIP AND RECTIFY | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029159640229.2090277778 | 10291596 |  | Parent | FALSE | SYN/COND AT BLTS | 40229.209 | 40230.5264 | CONT | 00002547 | SPIMAINT | Annual O/HAUL - BLTS Syn/Cond | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E458V340229.2534722222 | X7E458V3 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40229.2535 | 40229.4986 | REPDAILY | 00022740 | SPICAPX | Install OPGW betwen T41 andT48 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V79958A540229.2548611111 | V79958A5 |  | Parent | FALSE | A3 500/220KV TRANS BANK AT KTS | 40229.2549 | 40230.4604 | CONT | 00026097 | SPIMAINT | pcb oil removal from unit trans on a3 trans | SPIPOWER | V799 | V799 - (KTS) REPLACE PCB CONTAMINATED INSULATING OIL | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031626340229.2555555556 | 10316263 |  | Parent | TRUE | ROTS NO.1 220KV LINE CB LINE SIDE ISOL AT RTS | 40229.2556 | 40229.6069 | DAILY | [12 empty] | 0
_1031630340229.2555555556 | 10316303 | 10316263 | Child | FALSE | ROTS NO.1 220KV LINE CB AT RTS | 40229.2556 | 40229.6069 | DAILY | [12 empty] | 0
_1032095240229.2555555556 | 10320952 | 10316263 | Child | FALSE | ROTS NO.1 220KV LINE AT RTS | 40229.2556 | 40229.6069 | DAILY | 00021385 | SPIMAINT | Line Rebate | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029692440230.2513888889 | 10296924 |  | Parent | TRUE | RTS NO.4 220KV LINE AT ROTS | 40230.2514 | 40230.5569 | DAILY | 00023969 | SPIMAINT | O/Haul - 220kV Line CVT's | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031624240230.2513888889 | 10316242 | 10296924 | Child | FALSE | ROTS NO.4 220KV LINE CB LINE SIDE ISOL AT RTS | 40230.2514 | 40230.5569 | DAILY | [12 empty] | 0
_X7E458V340230.2569444444 | X7E458V3 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40230.2569 | 40230.6174 | REPDAILY | 00022740 | SPICAPX | Install OPGW betwen T41 andT48 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032207440230.9111111111 | 10322074 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 40230.9111 | 40234.2385 | CONT | 00356084 | GENCO | HWPS No6 Gen Isolated for SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E458V440231.2458333333 | X7E458V4 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40231.2458 | 40231.6042 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T29 andT41 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029083740231.2506944445 | 10290837 |  | Parent | FALSE | TSTS 220KV LINE NO.4 BUS CB AT ROTS | 40231.2507 | 40235.5847 | CONT | [12 empty] | 0
_1032113240231.2611111111 | 10321132 |  | Parent | FALSE | EX - A2 TRANS NO.1 BUS 500KV CB AT KTS | 40231.2611 | 40231.4417 | DAILY | [12 empty] | 0
_Z73058Q140231.2784722222 | Z73058Q1 |  | Parent | FALSE | FUTURE KLO 66KV FDR AT SMTS | 40231.2785 | 40231.434 | DAILY | 00366229 | VEN_AUG | REPLACE FDR VT | SPIPOWER | Z730 | Z730 - (SMTS) ESTABLISH A 220KV SWITCH YARD | Circuits | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032113340231.4430555556 | 10321133 |  | Parent | FALSE | EX - A4 TRANS NO.1 BUS 500KV CB AT KTS | 40231.4431 | 40231.5847 | DAILY | [12 empty] | 0
_X7E458V540232.2458333333 | X7E458V5 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40232.2458 | 40232.7715 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T16 andT29 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X89058A740232.2506944445 | X89058A7 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40232.2507 | 40232.7465 | DAILY | 00319999 | SPICAPX | Remove bridges from temp bypass at T623 and T627 | SPIPOWER | X890 | X890 - (HYTS-APD) LINE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032077340232.2506944445 | 10320773 |  | Parent | FALSE | EX - SYTS LINE/A4 TRANS 500KV CB CT R/PH AT KTS | 40232.2507 | 40233.5028 | DAILY | [12 empty] | 0
_1032219740232.85625 | 10322197 |  | Parent | FALSE | YPS -YWPS 1 220KV G | 40232.8562 | 40235.2986 | CONT | 00020517 | GENCO | Outage Requested by Power Station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032222140233.1958333333 | 10322221 |  | Parent | FALSE | L3 220/22KV TRANS BANK AT RWTS | 40233.1958 | 40233.4708 | CONT | 00007452 | FORCED | RWTS L3 220/22KV TRANS Low Oil Top Up | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032141040233.25 | 10321410 | X81158B3 | Child | FALSE | EX - NPSD 220KV LINE CB CT R/PH AT FBTS | 40233.25 | 40237.6667 | DAILY | [12 empty] | 0
_1032216140233.4604166667 | 10322161 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 40233.4604 | 40233.4743 | DAILY | [12 empty] | 0
_1032077440233.50625 | 10320774 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB CT R/PH AT KTS | 40233.5062 | 40233.5965 | DAILY | [12 empty] | 0
_1032163140234.2125 | 10321631 | X81158B5 | Child | FALSE | EX - NPSD 220KV LINE CB CT R/PH AT FBTS | 40234.2125 | 40234.9465 | DAILY | [12 empty] | 0
_1032163340234.2125 | 10321633 | X81158B6 | Child | FALSE | EX - NPSD 220KV LINE CB CT R/PH AT FBTS | 40234.2125 | 40234.9465 | DAILY | [12 empty] | 0
_X81158B540234.2125 | X81158B5 |  | Parent | TRUE | NO.2 66KV BUS AT TBTS | 40234.2125 | 40234.9465 | DAILY | 00004908 | SPICAPX | 1-2 B/T 66 kv CB & FTS /ByPass CB CT REPLACEMENT | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X81158B640234.2125 | X81158B6 | X81158B5 | Child | TRUE | B2 220/66KV TRANS AT TBTS | 40234.2125 | 40234.9465 | DAILY | 00004902 | SPICAPX | Rebate for Trans outage | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X89058A840234.2472222222 | X89058A8 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40234.2472 | 40234.6674 | DAILY | 00319998 | SPICAPX | Connect temp ERS Line to No1 Circ at T623 and T627 | SPIPOWER | X890 | X890 - (HYTS-APD) LINE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458V840234.2527777778 | X7E458V8 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40234.2528 | 40234.7944 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T02 andT16 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029786140234.2916666667 | 10297861 |  | Parent | FALSE | EX - W1 GTG/HWPS NO.2 LINE 220KV CB CT R/PH AT YPS | 40234.2917 | 40234.3125 | DAILY | [12 empty] | 0
_V9B358A240234.3180555556 | V9B358A2 |  | Parent | FALSE | B1 220/66KV TRANS AT MTS | 40234.3181 | 40234.5743 | DAILY | 00364562 | SPIMAINT | V9B3 - (MTS) REMOVE BIRDS & EXCREMENT FROM B TRS | SPIPOWER | V9B3 | V9B3 - (MTS) REMOVE BIRDS & EXCREMENT FROM B TRS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029444340235.2451388889 | 10294443 |  | Parent | FALSE | EX - W3 GEN TRANS NO.1 BUS 220KV CB CT R/PH AT YPS | 40235.2451 | 40235.3785 | DAILY | [12 empty] | 0
_V9B358A340235.2986111111 | V9B358A3 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 40235.2986 | 40235.5 | DAILY | 00363305 | SPIMAINT | V9B3 - (MTS) REMOVE BIRDS & EXCREMENT FROM B TRS | SPIPOWER | V9B3 | V9B3 - (MTS) REMOVE BIRDS & EXCREMENT FROM B TRS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029542540236.2298611111 | 10295425 |  | Parent | FALSE | L1 220/22KV TRANS AT WMTS | 40236.2299 | 40236.6014 | DAILY | 00003234 | SPIMAINT | O/HAUL Transformer and Div Sw (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E458V940236.23125 | X7E458V9 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40236.2312 | 40236.5993 | DAILY | 00022740 | SPICAPX | Install OPGW betwen T194 andT202 | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029137140236.25 | 10291371 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 40236.25 | 40236.6986 | REPDAILY | 00002833 | SPIMAINT | O/Haul NO.1 220KV BUS AT GTS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032155740236.25 | 10321557 | 10291371 | Child | FALSE | PT. HENRY NO.1 220KV LINE AT GTS | 40236.25 | 40236.6986 | REPDAILY | 00367277 | SPIMAINT | Rebate W/O PTH No1 Line during No1 220 bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032155840236.25 | 10321558 | 10291371 | Child | FALSE | KTS NO.1 220KV LINE AT GTS | 40236.25 | 40236.6986 | REPDAILY | 00367291 | SPIMAINT | Rebate W/O KTS No1 Line during No1 220 bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032155940236.25 | 10321559 | 10291371 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 40236.25 | 40236.6986 | REPDAILY | 00366646 | SPIMAINT | Rebate W/O MLTS No2 Line during No1 220 bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032156040236.25 | 10321560 | 10291371 | Child | FALSE | B1 220/66KV TRANS AT GTS | 40236.25 | 40236.6986 | REPDAILY | 00002828 | SPIMAINT | Perf calc W/O No1 Trans during No1 220 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X87058O540236.2708333333 | X87058O5 |  | Parent | FALSE | TSTS-TTS 220KV WT | 40236.2708 | 40236.359 | DAILY | 00022783 | SPICAPX | INSTALL DAMPERS AT TOWER T444 | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032230140236.3333333333 | 10322301 |  | Parent | FALSE | ROTS NO.2 220KV LINE AT HWPS | 40236.3333 | 40236.6035 | CONT | 00369011 | FAULT | HWPS - ROTS No2 220kV Line Tripped | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028887740236.4666666667 | 10288877 |  | Parent | FALSE | 66/22KV SYN/COND & TRANS Y PROT AT TSTS | 40236.4667 | 40236.509 | REPDAILY | [12 empty] | 0
_1029137140237.25 | 10291371 |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 40237.25 | 40237.684 | REPDAILY | 00002833 | SPIMAINT | O/Haul NO.1 220KV BUS AT GTS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032155740237.25 | 10321557 | 10291371 | Child | FALSE | PT. HENRY NO.1 220KV LINE AT GTS | 40237.25 | 40237.684 | REPDAILY | 00367277 | SPIMAINT | Rebate W/O PTH No1 Line during No1 220 bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032155840237.25 | 10321558 | 10291371 | Child | FALSE | KTS NO.1 220KV LINE AT GTS | 40237.25 | 40237.684 | REPDAILY | 00367291 | SPIMAINT | Rebate W/O KTS No1 Line during No1 220 bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032155940237.25 | 10321559 | 10291371 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 40237.25 | 40237.684 | REPDAILY | 00366646 | SPIMAINT | Rebate W/O MLTS No2 Line during No1 220 bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032156040237.25 | 10321560 | 10291371 | Child | FALSE | B1 220/66KV TRANS AT GTS | 40237.25 | 40237.684 | REPDAILY | 00002828 | SPIMAINT | Perf calc W/O No1 Trans during No1 220 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029428340237.2527777778 | 10294283 |  | Parent | FALSE | 1B-3 220KV BUS TIE CB CT R/PH AT BLTS | 40237.2528 | 40237.4035 | DAILY | [12 empty] | 0
_1029430740237.4027777778 | 10294307 |  | Parent | FALSE | 2B-4 220KV BUS TIE CB CT R/PH AT BLTS | 40237.4028 | 40237.5437 | DAILY | [12 empty] | 0
_1028887740237.4395833333 | 10288877 |  | Parent | FALSE | 66/22KV SYN/COND & TRANS Y PROT AT TSTS | 40237.4396 | 40237.484 | REPDAILY | [12 empty] | 0
_1028882940237.5546643519 | 10288829 |  | Parent | FALSE | NO.3 11/6.6KV AUXILARY TRANS PROT AT TSTS | 40237.5547 | 40237.5547 | DAILY | [12 empty] | 0
_1031987740237.555625 | 10319877 |  | Parent | FALSE | SYN/COND CONTROLS AT TSTS | 40237.5556 | 40237.5557 | DAILY | [12 empty] | 0
_V80558A040238.2666666667 | V80558A0 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40238.2667 | 40248.5576 | CONT | 00003011 | SPIMAINT | Out W/O 220 shunt reactor CB refurb | SPIPOWER | V805 | V805 - (MLTS) REFURBISH DELLE 220KV SHUNT REACTOR CB | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032232340238.4166666667 | 10322323 |  | Parent | FALSE | B4 220/66KV TRANS AT RWTS | 40238.4167 | 40238.5146 | CONT | 00007451 | FORCED | B4 Trans De-Energised due to faulty 66kV CB | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V7A058B040239.2527777778 | V7A058B0 |  | Parent | FALSE | HWTS NO.2 500KV LINE NO.2 BUS CB AT SMTS | 40239.2528 | 40241.6215 | CONT | [12 empty] | 0
_X70658T840239.29375 | X70658T8 |  | Parent | FALSE | B4 220/66KV TRANS AT KTS | 40239.2937 | 40239.6743 | REPDAILY | 00001146 | SPICAPX | DE-ENERGISE B4 TRANS & B4 TR 1B CB & ITS ROI's | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658T840240.25625 | X70658T8 |  | Parent | FALSE | B4 220/66KV TRANS AT KTS | 40240.2562 | 40240.6389 | REPDAILY | 00001146 | SPICAPX | DE-ENERGISE B4 TRANS & B4 TR 1B CB & ITS ROI's | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V9B358A140240.2694444445 | V9B358A1 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 40240.2694 | 40240.6181 | DAILY | 00363305 | SPIMAINT | Clean Down B3 Transformer | SPIPOWER | V9B3 | V9B3 - (MTS) REMOVE BIRDS & EXCREMENT FROM B TRS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032233340240.2770833333 | 10322333 |  | Parent | FALSE | LYPS NO.3 LINE/CBTS NO.4 LINE 500KV CB AT HWTS | 40240.2771 | 40240.6097 | DAILY | [12 empty] | 0
_1032236440240.3138888889 | 10322364 |  | Parent | FALSE | NO.4 66KV BUS AT MWTS | 40240.3139 | 40240.384 | DAILY | 00010281 | SPIMAINT | No4 66KV BUS AT MWTS FOR CRANE | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032241440240.6861111111 | 10322414 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 40240.6861 | 40253.2542 | CONT | [12 empty] | 0
_V9B358A040241.2194444445 | V9B358A0 |  | Parent | FALSE | B1 220/66KV TRANS AT MTS | 40241.2194 | 40241.5278 | DAILY | 00364562 | SPIMAINT | Clean Down Transformer | SPIPOWER | V9B3 | V9B3 - (MTS) REMOVE BIRDS & EXCREMENT FROM B TRS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658T840241.2611111111 | X70658T8 |  | Parent | FALSE | B4 220/66KV TRANS AT KTS | 40241.2611 | 40241.6215 | REPDAILY | 00001146 | SPICAPX | DE-ENERGISE B4 TRANS & B4 TR 1B CB & ITS ROI's | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032242840242.2520833333 | 10322428 |  | Parent | TRUE | YPS NO.1 220KV LINE NO.6 BUS CB AT HWPS | 40242.2521 | 40242.3458 | DAILY | [12 empty] | 0
_1032246740242.2520833333 | 10322467 | 10322428 | Child | FALSE | YPS NO.1 220KV LINE AT HWPS | 40242.2521 | 40242.3458 | DAILY | 00015795 | SPIMAINT | Rebate child | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032233540242.2777777778 | 10322335 |  | Parent | FALSE | CBTS NO.4 500KV LINE NO.3 BUS CB AT HWTS | 40242.2778 | 40242.4368 | DAILY | [12 empty] | 0
_1032247840242.5597222222 | 10322478 |  | Parent | FALSE | EX - W1 GTG/HWPS NO.2 LINE 220KV CB CT B/PH AT YPS | 40242.5597 | 40244.3042 | CONT | [12 empty] | 0
_V70358A140243.2180555556 | V70358A1 |  | Parent | FALSE | KTS -ATS 220KV WY | 40243.2181 | 40243.6528 | REPDAILY | 00074402 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031694640243.2666666667 | 10316946 |  | Parent | FALSE | B1 GEN TRANS 500KV CB AT LYPS | 40243.2667 | 40243.3708 | DAILY | [12 empty] | 0
_1032248740243.5743055556 | 10322487 |  | Parent | FALSE | B5 220/66KV TRANS AT KTS | 40243.5743 | 40244.7028 | CONT | 00369184 | FAULT | B5 Transf tripped from gas prot in storm | SPIPOWER |  |  | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1032248840243.9166666667 | 10322488 |  | Parent | FALSE | HYTS NO.1 500KV LINE AT MLTS | 40243.9167 | 40243.9201 | DAILY | 00022695 | SW_NEM | Reactor Sw on HYTS-MLTS No 1 Line | NEMMCO |  |  | Circuits | 3rd Party | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1032248940243.9215277778 | 10322489 |  | Parent | FALSE | HYTS NO.2 500KV LINE AT MLTS | 40243.9215 | 40243.9257 | DAILY | 00022754 | SW_NEM | Reactor Sw on HYTS-MLTS No 2 Line | NEMMCO |  |  | Circuits | 3rd Party | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_V70358A140244.2131944445 | V70358A1 |  | Parent | FALSE | KTS -ATS 220KV WY | 40244.2132 | 40244.6937 | REPDAILY | 00074402 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z71958C340246.2527777778 | Z71958C3 |  | Parent | FALSE | B3 220/66KV TRANS AT CBTS | 40246.2528 | 40246.4014 | DAILY | 00368875 | VEN_AUG | Measure Concrete Roof | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1032249240246.2986111111 | 10322492 |  | Parent | FALSE | B5 220/66KV TRANS AT KTS | 40246.2986 | 40246.6021 | CONT | 00369184 | SPIMAINT | B5 TRANS TRIP INVESTIGATION | SPIPOWER |  |  | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1029433140246.3659722222 | 10294331 |  | Parent | FALSE | H3 TRANS NO.1 BUS 330KV CB CT R/PH AT DDTS | 40246.366 | 40246.5667 | DAILY | [12 empty] | 0
_1032252540247.29375 | 10322525 |  | Parent | FALSE | DPS -MBTS 220KV NW | 40247.2937 | 40247.5868 | REPDAILY | 00060195 | SPIMAINT | Out W/O DPS-MBTS Line works during AGL outage | GENCO |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032251540247.29375 | 10322515 |  | Parent | FALSE | BSS RCTS (0X1) 220KV (Non SPI circuit) | 40247.2937 | 40247.6062 | DAILY | 00354016 | TRANSGRD | Transgrid Work | TRANSGRD |  |  | Circuits | Alstom | 220 |  |  |  | 3
_1032245040247.38125 | 10322450 |  | Parent | FALSE | R2 220/66/22KV TRANS AT KGTS | 40247.3812 | 40247.5618 | DAILY | 00017344 | SPIMAINT | OLTC Transducer problems at KGTS | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032255540247.5215277778 | 10322555 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT SMTS | 40247.5215 | 40248.5069 | CONT | [12 empty] | 0
_X70658T440248.2083333333 | X70658T4 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE AT KTS | 40248.2083 | 40248.6972 | DAILY | 00015986 | SPICAPX | ESTAB HARPSTRINGS GTS 3 LINE TO GTS 3L 3B L/S ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V99058B040248.2152777778 | V99058B0 |  | Parent | FALSE | B1 220/66KV TRANS AT RTS | 40248.2153 | 40248.4826 | DAILY | 00007329 | SPIMAINT | Install misting spray equipment to B1 Tr cooling | SPIPOWER | V990 | V990 - ASEA 150MVA TRANS COOLING SYSTEM OVERHAUL | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V8D258A640248.2472222222 | V8D258A6 |  | Parent | FALSE | TTS 220KV LINE AT ROTS | 40248.2472 | 40248.7049 | DAILY | 00023972 | SPIMAINT | Move W phase to Spare SF6 Duct and R Phase Back | SPIPOWER | V8D2 | V8D2 - (ROTS) REPLACE 220KV BUS DUCT SLIDING SUPPORT | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1032256640248.3541666667 | 10322566 |  | Parent | FALSE | EX - HWTS NO.1 500KV LINE CVT R/PH AT SMTS | 40248.3542 | 40248.4479 | DAILY | [12 empty] | 0
_1032260640248.3541666667 | 10322606 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 40248.3542 | 40248.4479 | DAILY | 00012436 | FORCED | SMTS: rapid rise in output volts HWTS 1L CVT R PH | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032255940248.5069444444 | 10322559 |  | Parent | FALSE | SYTS NO.2 500KV LINE NO.1 BUS CB AT SMTS | 40248.5069 | 40250.4854 | CONT | [12 empty] | 0
_1032249740248.7291666667 | 10322497 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE AT KTS | 40248.7292 | 40249.2188 | CONT | 00015986 | SPIMAINT | GTS No3 Line Isol'd & Earthed | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031655640248.9444444444 | 10316556 |  | Parent | FALSE | W2 GEN TRANS NO.2 BUS 220KV CB CT R/PH AT YPS | 40248.9444 | 40249.484 | CONT | [12 empty] | 0
_1032254940249.0131944444 | 10322549 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 40249.0132 | 40253.8681 | CONT | 00016424 | GENCO | SCAP for YWPS No2 Generator | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V99058B140249.2041666667 | V99058B1 |  | Parent | FALSE | B4 220/66KV TRANS AT RTS | 40249.2042 | 40249.3361 | DAILY | 00007332 | SPIMAINT | Install misting spray equipment to B4 Tr cooling | SPIPOWER | V990 | V990 - ASEA 150MVA TRANS COOLING SYSTEM OVERHAUL | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658T540249.21875 | X70658T5 |  | Parent | TRUE | NO.3 220KV BUS AT KTS | 40249.2188 | 40249.7014 | DAILY | 00001171 | SPICAPX | BIPODS ON No.3 220KV BUS & CONCT TO GTS 3 L 3B ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658T940249.21875 | X70658T9 | X70658T5 | Child | FALSE | EX - GTS NO.3 220KV LINE AT KTS | 40249.2188 | 40249.7014 | DAILY | 00015986 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032261540249.5201388889 | 10322615 |  | Parent | FALSE | TBTS-JLA 2 220KV E | 40249.5201 | 40249.5257 | CONT | 00022777 | HVCUST | JLA Requirement to switch OOS TR3 trans at JLA | HVCUST |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032239440249.7513888889 | 10322394 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB CT R/PH AT KTS | 40249.7514 | 40249.8313 | DAILY | [12 empty] | 0
_V70358A240250.2083333333 | V70358A2 |  | Parent | FALSE | KTS -ATS 220KV WY | 40250.2083 | 40250.6799 | REPDAILY | 00074402 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E358A140250.2284722222 | X7E358A1 |  | Parent | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 40250.2285 | 40251.5938 | CONT | 00004037 | SPICAPX | No2 Trans outage for X prot replacement | SPIPOWER | X7E3 | X7E3 - (WOTS) UPGRADE TRANSFORMER PROTECTION | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027156140250.2402777778 | 10271561 | X74158B2 | Child | FALSE | HWPS NO.2 220KV LINE AT YPS | 40250.2403 | 40256.425 | DAILY | 00016412 | SPIMAINT | Overhaul HWPS NO2 220 KV Line at YPS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X74158B240250.2402777778 | X74158B2 |  | Parent | TRUE | EX - W1 GTG/HWPS NO.2 LINE 220KV CB CT R/PH AT YPS | 40250.2403 | 40256.425 | CONT | [12 empty] | 0
_V79658A440250.2520833333 | V79658A4 |  | Parent | FALSE | BTS 220KV LINE AT RTS | 40250.2521 | 40299.5576 | CONT | 00021222 | SPIMAINT | V796 - (BTS-RTS) CABLE JOINT REPLACEMENTS | SPIPOWER | V796 | V796 - (BTS-RTS) CABLE JOINT REPLACEMENTS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V70358A240251.2055555556 | V70358A2 |  | Parent | FALSE | KTS -ATS 220KV WY | 40251.2056 | 40251.6431 | REPDAILY | 00074402 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029317140251.2506944445 | 10293171 |  | Parent | FALSE | B4 TRANS 66KV CB AT WMTS | 40251.2507 | 40251.5799 | DAILY | [12 empty] | 0
_X7G358A340251.2583333333 | X7G358A3 |  | Parent | FALSE | EX - B3 220/66KV TRANS 66KV SD R/PH AT ERTS | 40251.2583 | 40251.7528 | DAILY | [12 empty] | 0
_1032262740251.7347222222 | 10322627 |  | Parent | FALSE | NO.3 220KV BUS AT ERTS | 40251.7347 | 40251.7528 | CONT | 00364080 | FORCED | No 3 220kv bus | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V70358A340252.2055555556 | V70358A3 |  | Parent | FALSE | KTS -BLTS 220KV WY | 40252.2056 | 40252.6673 | DAILY | 00022716 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032255240252.2513888889 | 10322552 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40252.2514 | 40255.6521 | CONT | 00319998 | APDALCOA | VSCAP to APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X61058A040252.2534722222 | X61058A0 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40252.2535 | 40252.6444 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line to new Tower for MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X61058A140252.2534722222 | X61058A1 | X61058A0 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40252.2535 | 40252.6444 | REPDAILY | 00002863 | SPICAPX | Out W/O M1 Trans during MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X61058A240252.2534722222 | X61058A2 | X61058A0 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40252.2535 | 40252.6444 | REPDAILY | 00003007 | SPICAPX | Rebate W/O React For Con MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032267340252.8881944444 | 10322673 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 40252.8882 | 40252.95 | CONT | 00356086 | GENCO | No 8 gen trans | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X61058A040253.25 | X61058A0 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40253.25 | 40253.6632 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line to new Tower for MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X61058A140253.25 | X61058A1 | X61058A0 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40253.25 | 40253.6632 | REPDAILY | 00002863 | SPICAPX | Out W/O M1 Trans during MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X61058A240253.25 | X61058A2 | X61058A0 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40253.25 | 40253.6632 | REPDAILY | 00003007 | SPICAPX | Rebate W/O React For Con MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029147940253.2534722222 | 10291479 |  | Parent | TRUE | BLTS 220KV LINE CB AT FBTS | 40253.2535 | 40254.5208 | CONT | [12 empty] | 0
_1032293840253.2534722222 | 10322938 | 10291479 | Child | FALSE | BLTS 220KV LINE AT FBTS | 40253.2535 | 40254.5208 | CONT | 00002660 | SPIMAINT | outage rebate costs | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X7E958B640253.2548611111 | X7E958B6 |  | Parent | FALSE | EX - SYTS 500KV LINE NO.2 BUS CB AT KTS | 40253.2549 | 40303.5938 | CONT | [12 empty] | 0
_X70658T640253.2590277778 | X70658T6 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE AT KTS | 40253.259 | 40253.6667 | REPDAILY | 00015986 | SPICAPX | DE-ENERGISE GTS 3 LINE FOR PROXIMITY | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032186540253.2604166667 | 10321865 |  | Parent | TRUE | MLTS NO.2 220KV LINE NO.1 BUS CB BUS SIDE ROI AT BATS | 40253.2604 | 40253.6361 | DAILY | [12 empty] | 0
_1032194840253.2604166667 | 10321948 | 10321865 | Child | FALSE | TGTS 220KV LINE AT BATS | 40253.2604 | 40253.6361 | DAILY | 00012435 | SPIMAINT | Rebate W/O TGTS Line during No1 220 Bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032194940253.2604166667 | 10321949 | 10321865 | Child | FALSE | B2 220/66KV TRANS AT BATS | 40253.2604 | 40253.6361 | DAILY | 00006555 | SPIMAINT | Perf calc W/O No2 Trans during No1 220 Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658U840253.2631944444 | X70658U8 |  | Parent | FALSE | B4 TRANS NO.1 BUS 220KV CB AT KTS | 40253.2632 | 40253.6681 | REPDAILY | [12 empty] | 0
_1029062340253.2652777778 | 10290623 |  | Parent | FALSE | SYN/COND AT TSTS | 40253.2653 | 40255.6667 | CONT | 00007626 | SPIMAINT | O/Haul Syn Con at TSTS | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V7A058B140253.2680555556 | V7A058B1 |  | Parent | FALSE | HWTS NO.2 500KV LINE NO.2 BUS CB AT SMTS | 40253.2681 | 40255.5889 | CONT | [12 empty] | 0
_X7E358A240253.3027777778 | X7E358A2 |  | Parent | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 40253.3028 | 40254.2847 | CONT | 00004036 | SPICAPX | No1 Trans outage for X prot replacement | SPIPOWER | X7E3 | X7E3 - (WOTS) UPGRADE TRANSFORMER PROTECTION | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032275740254.1854166667 | 10322757 |  | Parent | FALSE | JLA NO.2 220KV LINE AT TBTS | 40254.1854 | 40254.2396 | DAILY | 00026919 | REM_TRIP | JLA NO2 220KV LINE Remote Trip from Customer | HVCUST |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032199540254.25 | 10321995 |  | Parent | TRUE | HYTS NO.1 500KV LINE AT MLTS | 40254.25 | 40254.6056 | REPDAILY | 00022695 | SPICAPX | Out W/O HYTS 1 Line for MOPS&Maint of line & equip | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032199640254.25 | 10321996 | 10321995 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40254.25 | 40254.6056 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MOPS MLTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032199740254.25 | 10321997 | 10321995 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40254.25 | 40254.6056 | REPDAILY | 00003007 | SPICAPX | Out W/O 1L React during MOPS HYTS MLTS 1 Line Out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032273140254.2555555556 | 10322731 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB CT W/PH AT KTS | 40254.2556 | 40254.5861 | DAILY | [12 empty] | 0
_X70658U840254.2645833333 | X70658U8 |  | Parent | FALSE | B4 TRANS NO.1 BUS 220KV CB AT KTS | 40254.2646 | 40254.6653 | REPDAILY | [12 empty] | 0
_1029112740254.2847222222 | 10291127 |  | Parent | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 40254.2847 | 40254.7389 | REPDAILY | 00004036 | SPIMAINT | O/H NO 1 TRANS & TAP CHANGER & S/S Trans | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032272440254.3166666667 | 10322724 |  | Parent | FALSE | NO.1 UNIT 230/10.5KV TRANS AT JLGA | 40254.3167 | 40303.3458 | CONT | 00009820 | GENCO | Power station requirement | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_V70358B840255.2111111111 | V70358B8 |  | Parent | FALSE | KTS -BLTS 220KV WY | 40255.2111 | 40255.6687 | DAILY | 00022716 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032259040255.2486111111 | 10322590 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT TSTS | 40255.2486 | 40255.6111 | DAILY | 00351937 | SPIMAINT | Repair Fire service under Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1032199540255.2486111111 | 10321995 |  | Parent | TRUE | HYTS NO.1 500KV LINE AT MLTS | 40255.2486 | 40255.6833 | REPDAILY | 00022695 | SPICAPX | Out W/O HYTS 1 Line for MOPS&Maint of line & equip | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032199640255.2486111111 | 10321996 | 10321995 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40255.2486 | 40255.6833 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MOPS MLTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032199740255.2486111111 | 10321997 | 10321995 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40255.2486 | 40255.6833 | REPDAILY | 00003007 | SPICAPX | Out W/O 1L React during MOPS HYTS MLTS 1 Line Out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032256440255.2583333333 | 10322564 |  | Parent | FALSE | HWTS NO.1 500KV LINE AT SMTS | 40255.2583 | 40255.5889 | DAILY | 00012436 | SPIMAINT | Remove defective Konkar CVTs | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032281340255.2694444445 | 10322813 |  | Parent | FALSE | B4 220/66KV TRANS AT KTS | 40255.2694 | 40255.5785 | DAILY | 00001146 | SPIMAINT | B4 Trans de-energised | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029112740255.3027777778 | 10291127 |  | Parent | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 40255.3028 | 40255.6924 | REPDAILY | 00004036 | SPIMAINT | O/H NO 1 TRANS & TAP CHANGER & S/S Trans | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032344440256.25 | 10323444 | X61058A3 | Child | FALSE | HYTS-APD 1 500KV W | 40256.25 | 40256.7042 | REPDAILY | 00319998 | SPICAPX | Rebate W/O M1 Trans for MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X61058A340256.25 | X61058A3 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40256.25 | 40256.7042 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line to new Tower for MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X61058A440256.25 | X61058A4 | X61058A3 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40256.25 | 40256.7042 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans For MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X61058A540256.25 | X61058A5 | X61058A3 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40256.25 | 40256.7042 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React For MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658T740256.2506944445 | X70658T7 |  | Parent | FALSE | EX - GTS NO.3 220KV LINE AT KTS | 40256.2507 | 40256.6104 | DAILY | 00015986 | SPICAPX | DE-ENERGISE GTS 3 LINE FOR PROXIMITY | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032116640256.2701388889 | 10321166 |  | Parent | FALSE | EX - NO.1B 66KV CAPACITOR BANK CB AT KTS | 40256.2701 | 40256.4153 | DAILY | [12 empty] | 0
_1029429340256.2895833333 | 10294293 |  | Parent | FALSE | 1-2 220KV BUS TIE CB NO.1 BUS CT R/PH AT WMTS | 40256.2896 | 40256.4271 | DAILY | [12 empty] | 0
_1032200640256.3777777778 | 10322006 | V71158B7 | Child | FALSE | HWTS NO.2 500KV LINE AT LYPS | 40256.3778 | 40259.5924 | CONT | 00016087 | SPIMAINT | REBATE HWTS NO.2 LINE OUTAGE CB OVERHAUL | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V71158B740256.3777777778 | V71158B7 |  | Parent | TRUE | HWTS NO.2 500KV LINE CB AT LYPS | 40256.3778 | 40259.5924 | CONT | [12 empty] | 0
_1029429540256.4347222222 | 10294295 |  | Parent | TRUE | 3-4 220KV BUS TIE CB NO.3 BUS CT R/PH AT WMTS | 40256.4347 | 40256.5569 | DAILY | [12 empty] | 0
_1029437340256.4347222222 | 10294373 | 10294295 | Child | FALSE | 3-4 220KV BUS TIE CB NO.4 BUS CT R/PH AT WMTS | 40256.4347 | 40256.5569 | DAILY | [12 empty] | 0
_V70358A440257.2 | V70358A4 |  | Parent | FALSE | KTS -ATS 220KV WY | 40257.2 | 40257.6493 | DAILY | 00074402 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032344440257.2090277778 | 10323444 | X61058A3 | Child | FALSE | HYTS-APD 1 500KV W | 40257.209 | 40257.7646 | REPDAILY | 00319998 | SPICAPX | Rebate W/O M1 Trans for MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X61058A340257.2090277778 | X61058A3 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40257.209 | 40257.7646 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line to new Tower for MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X61058A440257.2090277778 | X61058A4 | X61058A3 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40257.209 | 40257.7646 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans For MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X61058A540257.2090277778 | X61058A5 | X61058A3 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40257.209 | 40257.7646 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React For MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1029124440257.2395833333 | 10291244 |  | Parent | TRUE | B3 220/66KV TRANS AT WMTS | 40257.2396 | 40257.4222 | DAILY | 00003236 | SPIMAINT | O/HAUL Transformer Div Mechanism (W) | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1029125340257.2395833333 | 10291253 | 10291244 | Child | FALSE | B3 TRANS 66KV CB AT WMTS | 40257.2396 | 40257.4222 | DAILY | [12 empty] | 0
_X7G358A440257.2576388889 | X7G358A4 |  | Parent | FALSE | EX - B4 220/66KV TRANS 66KV SD R/PH AT ERTS | 40257.2576 | 40257.6486 | DAILY | [12 empty] | 0
_1030732340258.2097222222 | 10307323 |  | Parent | FALSE | NO.3 220KV BUS AT ATS | 40258.2097 | 40258.6819 | REPDAILY | 00356843 | SPIMAINT | O/Haul NO.3 220KV BUS AT ATS | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032344440258.2298611111 | 10323444 | X61058A3 | Child | FALSE | HYTS-APD 1 500KV W | 40258.2299 | 40258.7833 | REPDAILY | 00319998 | SPICAPX | Rebate W/O M1 Trans for MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X61058A340258.2298611111 | X61058A3 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40258.2299 | 40258.7833 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line to new Tower for MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X61058A440258.2298611111 | X61058A4 | X61058A3 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40258.2299 | 40258.7833 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans For MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X61058A540258.2298611111 | X61058A5 | X61058A3 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40258.2299 | 40258.7833 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React For MOPS MLTS-HYTS 1 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7G358A240258.2409722222 | X7G358A2 |  | Parent | FALSE | EX - B1 220/66KV TRANS 66KV SD R/PH AT ERTS | 40258.241 | 40258.6299 | DAILY | [12 empty] | 0
_1029216340258.2972222222 | 10292163 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK Y PROT AT TSTS | 40258.2972 | 40258.3986 | DAILY | [12 empty] | 0
_V70358A540259.2090277778 | V70358A5 |  | Parent | FALSE | KTS -BLTS 220KV WY | 40259.209 | 40259.6785 | REPDAILY | 00022716 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030322440259.2729166667 | 10303224 |  | Parent | FALSE | TGTS 220KV LINE AT BATS | 40259.2729 | 40259.6674 | DAILY | 00012435 | SPIMAINT | O/Haul TGTS 220 kv L at BATS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032255340259.2743055556 | 10322553 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40259.2743 | 40262.4868 | CONT | 00319999 | APDALCOA | VSCAP to APD | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1032199840259.2777777778 | 10321998 | 10321999 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40259.2778 | 40259.6979 | REPDAILY | 00002862 | SPICAPX | Out W/O M2 Trans during MOPS HYTMLTS 2 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032199940259.2777777778 | 10321999 |  | Parent | TRUE | HYTS NO.2 500KV LINE AT MLTS | 40259.2778 | 40259.6979 | REPDAILY | 00022754 | SPICAPX | Out W/O HYTS 2 Line for MOPS&maint of line & equip | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032195940259.2777777778 | 10321959 |  | Parent | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 40259.2778 | 40263.7083 | CONT | 00003008 | SPIMAINT | Out W/O HYTS No2 Line React HV Testing (Sel Sol) | SPIPOWER |  |  | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032292040259.6722222222 | 10322920 |  | Parent | FALSE | KTS 220KV LINE AT BLTS | 40259.6722 | 40262.5208 | CONT | 00024011 | FORCED | KTS Line Off loaded to repair failed Mech in CB | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032291840259.6784722222 | 10322918 |  | Parent | FALSE | NO.3 220KV BUS AT BLTS | 40259.6785 | 40259.6868 | CONT | 00002645 | FORCED | No3 220KV BUS stripped to isolate faulty CB | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032296040259.6784722222 | 10322960 |  | Parent | FALSE | B3A 220/66KV TRANS BANK AT BLTS | 40259.6785 | 40259.6868 | CONT | 00018491 | FORCED | B3 Trans Off Loaded when No3 220KV BUS stripped | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032298040259.6784722222 | 10322980 |  | Parent | FALSE | FBTS 220KV LINE AT BLTS | 40259.6785 | 40259.6868 | CONT | 00024012 | FORCED | FBTS LINE Off Loaded when No3 220KV BUS stripped | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1032178140260.25 | 10321781 |  | Parent | FALSE | JLTS NO.1 220KV LINE LINE ROI AT HWPS | 40260.25 | 40260.5625 | DAILY | [12 empty] | 0
_1032199940260.2555555556 | 10321999 |  | Parent | TRUE | HYTS NO.2 500KV LINE AT MLTS | 40260.2556 | 40260.7194 | REPDAILY | 00022754 | SPICAPX | Out W/O HYTS 2 Line for MOPS&maint of line & equip | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X81158B740260.2555555556 | X81158B7 |  | Parent | TRUE | MLTS NO.2 500KV LINE CB AT HYTS | 40260.2556 | 40264.6667 | CONT | [12 empty] | 0
_X81158B840260.2555555556 | X81158B8 | X81158B7 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40260.2556 | 40264.6667 | CONT | 00002862 | SPICAPX | Rebate W/O M2 Trans during 500kV CB outage | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032292740260.3972222222 | 10322927 |  | Parent | FALSE | BLLY 500KV LINE AT LYPS | 40260.3972 | 40260.4042 | DAILY | 00360516 | REM_TRIP | BLLY line Remote Trip from Converter Station | 3RDPARTY |  |  | Circuits | Eastern | 500 | CONNECTION ASSET | EXCLUDED |  | 3
_1029411840260.5201388889 | 10294118 |  | Parent | FALSE | SPARE A 515/230KV TRANS UNIT AT HWTS | 40260.5201 | 40261.6667 | CONT | 00009771 | SPIMAINT | Condition Monitoring Metro Trans 2day Valley Area | SPIPOWER |  |  | Main Transformers | Eastern | 500 |  |  |  | 0
_1032293440260.5395833333 | 10322934 |  | Parent | FALSE | TBTS-JLA 1 220KV E | 40260.5396 | 40260.5431 | DAILY | 00022774 | FAULT | JLA-TBTS No1 220KV Line inadvertent trip by Tests | HVCUST |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029059740260.5659722222 | 10290597 |  | Parent | TRUE | JLTS NO.1 LINE/AUX TRANS 'B' 220KV CB AT HWPS | 40260.566 | 40262.5243 | CONT | [12 empty] | 0
_1030151440260.5659722222 | 10301514 | 10290597 | Child | FALSE | JLTS NO.1 220KV LINE AT HWPS | 40260.566 | 40262.5243 | CONT | 00015784 | SPIMAINT | REBATE FOR CB OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058P140261.21875 | X87058P1 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40261.2188 | 40261.7132 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS 2 Ln ins replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032199940261.2291666667 | 10321999 |  | Parent | TRUE | HYTS NO.2 500KV LINE AT MLTS | 40261.2292 | 40261.7264 | REPDAILY | 00022754 | SPICAPX | Out W/O HYTS 2 Line for MOPS&maint of line & equip | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032294440261.2840277778 | 10322944 |  | Parent | FALSE | WBTS 220KV LINE NO.1 BUS CB AT HOTS | 40261.284 | 40261.4833 | DAILY | [12 empty] | 0
_1032300440261.5534722222 | 10323004 |  | Parent | FALSE | TBTS-JLA 1 220KV E | 40261.5535 | 40261.566 | CONT | 00022774 | FAULT | JLA-TBTS No1 220KV Line inadvertent trip by Tests | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058P140262.2291666667 | X87058P1 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40262.2292 | 40262.7076 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS 2 Ln ins replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032199940262.2340277778 | 10321999 |  | Parent | TRUE | HYTS NO.2 500KV LINE AT MLTS | 40262.234 | 40262.8146 | REPDAILY | 00022754 | SPICAPX | Out W/O HYTS 2 Line for MOPS&maint of line & equip | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031730240262.2513888889 | 10317302 |  | Parent | FALSE | B1 220/66KV TRANS AT CBTS | 40262.2514 | 40262.5903 | DAILY | 00353076 | SPIMAINT | OVERHAUL OF A TRANSFORMER | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_V70358A540262.5208333333 | V70358A5 |  | Parent | FALSE | KTS -BLTS 220KV WY | 40262.5208 | 40262.6 | REPDAILY | 00022716 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032304040262.6090277778 | 10323040 |  | Parent | FALSE | EPS 220KV LINE AT TTS | 40262.609 | 40262.8146 | CONT | 00015730 | FAULT | EPS-TTS 220KV Line Trip no reclose | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V70358A540263.2104166667 | V70358A5 |  | Parent | FALSE | KTS -BLTS 220KV WY | 40263.2104 | 40263.6403 | REPDAILY | 00022716 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058P140263.2291666667 | X87058P1 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40263.2292 | 40263.7069 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS 2 Ln ins replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029784940263.2430555556 | 10297849 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB CT R/PH AT TTS | 40263.2431 | 40263.4347 | DAILY | [12 empty] | 0
_1032338540263.2430555556 | 10323385 | 10297849 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT TTS | 40263.2431 | 40263.4347 | DAILY | 00119178 | SPIMAINT | CAP BANK REBATES | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_V8F158A940263.2430555556 | V8F158A9 |  | Parent | FALSE | B4 220/66KV TRANS AT KTS | 40263.2431 | 40263.6125 | DAILY | 00001146 | SPIMAINT | INVESTIGATE AND DOCUMENT OIL LEAKS | SPIPOWER | V8F1 | V8F1 - REPAIR OF OIL LEAKS IN TERMINAL STNS - STAGE 1 | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032200740263.25 | 10322007 | V71158B0 | Child | FALSE | HWTS NO.2 500KV LINE AT LYPS | 40263.25 | 40265.4569 | CONT | 00016087 | SPIMAINT | REBATE HWTS NO.2 LINE OUTAGE CB OVERHAUL | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V71158B040263.25 | V71158B0 |  | Parent | TRUE | HWTS NO.2 500KV LINE CB AT LYPS | 40263.25 | 40265.4569 | CONT | [12 empty] | 0
_1032199940263.2625 | 10321999 |  | Parent | TRUE | HYTS NO.2 500KV LINE AT MLTS | 40263.2625 | 40263.7083 | REPDAILY | 00022754 | SPICAPX | Out W/O HYTS 2 Line for MOPS&maint of line & equip | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031730540263.2694444445 | 10317305 |  | Parent | FALSE | B2 220/66KV TRANS AT CBTS | 40263.2694 | 40263.6222 | DAILY | 00353077 | SPIMAINT | OVERHAUL OF A TRANSFORMER | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1029785140263.4472222222 | 10297851 |  | Parent | TRUE | NO.3 220KV CAPACITOR BANK CB CT R/PH AT TTS | 40263.4472 | 40263.5472 | DAILY | [12 empty] | 0
_1032338740263.4472222222 | 10323387 | 10297851 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT TTS | 40263.4472 | 40263.5472 | DAILY | 00327615 | SPIMAINT | CAPBANK REBATES | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_V70358A640264.2090277778 | V70358A6 |  | Parent | FALSE | KTS -ATS 220KV WY | 40264.209 | 40264.6889 | REPDAILY | 00074402 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032344640264.2319444444 | 10323446 | X61058A6 | Child | FALSE | HYTS-APD 2 500KV W | 40264.2319 | 40264.6625 | REPDAILY | 00319999 | SPICAPX | Rebate W/O APD Line for MOPS MLTS-HYTS 2 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X61058A640264.2319444444 | X61058A6 |  | Parent | TRUE | MLTS-HYTS 2 500KV W | 40264.2319 | 40264.6625 | REPDAILY | 00022633 | SPICAPX | Out W/O MLTS-HYTS 2 Line to new Tower for MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X61058A840264.2319444444 | X61058A8 | X61058A6 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 40264.2319 | 40264.6625 | REPDAILY | 00003008 | SPICAPX | Rebate W/O Sh React for MOPS MLTS-HYTS 2 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X87058P240264.2333333333 | X87058P2 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 40264.2333 | 40264.6896 | REPDAILY | 00060187 | SPICAPX | MBTS-DDTS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V70358A640265.2118055556 | V70358A6 |  | Parent | FALSE | KTS -ATS 220KV WY | 40265.2118 | 40265.7069 | REPDAILY | 00074402 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058P240265.2305555556 | X87058P2 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 40265.2306 | 40265.6986 | REPDAILY | 00060187 | SPICAPX | MBTS-DDTS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032344640265.2340277778 | 10323446 | X61058A6 | Child | FALSE | HYTS-APD 2 500KV W | 40265.234 | 40265.6583 | REPDAILY | 00319999 | SPICAPX | Rebate W/O APD Line for MOPS MLTS-HYTS 2 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X61058A640265.2340277778 | X61058A6 |  | Parent | TRUE | MLTS-HYTS 2 500KV W | 40265.234 | 40265.6583 | REPDAILY | 00022633 | SPICAPX | Out W/O MLTS-HYTS 2 Line to new Tower for MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X61058A740265.2340277778 | X61058A7 | X61058A6 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40265.234 | 40265.6583 | REPDAILY | 00002862 | SPICAPX | Rebate W/O M2 Trans For MOPS MLTS-HYTS 2 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X61058A840265.2340277778 | X61058A8 | X61058A6 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 40265.234 | 40265.6583 | REPDAILY | 00003008 | SPICAPX | Rebate W/O Sh React for MOPS MLTS-HYTS 2 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V70358CO40266.2166666667 | V70358CO |  | Parent | FALSE | KTS -BLTS 220KV WY | 40266.2167 | 40266.4861 | REPDAILY | 00022716 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X90958A140266.2555555556 | X90958A1 |  | Parent | FALSE | DDTS-SMTS 1 330KV | 40266.2556 | 40267.4944 | CONT | 00328506 | SPICAPX | ERECT NEW TOWER & REMOVE TEMP TOWER | SPIPOWER | X909 | X909 - (DDTS-SMTS#1) REPLACE COLLAPSED TOWER T493 | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V70358CO40267.2118055556 | V70358CO |  | Parent | FALSE | KTS -BLTS 220KV WY | 40267.2118 | 40267.6229 | REPDAILY | 00022716 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029412640267.2493055556 | 10294126 |  | Parent | FALSE | B3 220/66KV TRANS AT FBTS | 40267.2493 | 40268.5799 | CONT | 00002727 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X90958A440267.2541666667 | X90958A4 |  | Parent | FALSE | DDTS-SMTS 2 330KV | 40267.2542 | 40267.4069 | DAILY | 00328507 | SPICAPX | REMVE ERS MASTS FROM UNDER DDTS-SMTS1 PROX | SPIPOWER | X909 | X909 - (DDTS-SMTS#1) REPLACE COLLAPSED TOWER T493 | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E958B740267.41875 | X7E958B7 |  | Parent | FALSE | SYTS 500KV LINE NO.2 BUS CB BUS SIDE ROI AT KTS | 40267.4187 | 40267.5674 | CONT | [12 empty] | 0
_1029434940267.5430555556 | 10294349 |  | Parent | TRUE | EX - SESS NO.1 275KV LINE/M1 TRANS CB CT R/PH AT HYTS | 40267.5431 | 40267.575 | DAILY | [12 empty] | 0
_1032184540267.5430555556 | 10321845 | 10294349 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40267.5431 | 40267.575 | DAILY | 00002863 | SPIMAINT | Rebate W/O M1 Trans during 275kV CB outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_V70358CO40268.2083333333 | V70358CO |  | Parent | FALSE | KTS -BLTS 220KV WY | 40268.2083 | 40268.5465 | REPDAILY | 00022716 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029339840268.2506944445 | 10293398 |  | Parent | TRUE | NO.1 275KV CAPACITOR BANK/SESS NO.2 LINE CB LINE SIDE ROI AT HYTS | 40268.2507 | 40268.6431 | DAILY | [12 empty] | 0
_1032184640268.2506944445 | 10321846 | 10293398 | Child | FALSE | SESS NO.2 275KV LINE AT HYTS | 40268.2507 | 40268.6431 | DAILY | 00026936 | SPIMAINT | Rebate W/O SESS 2 Line during ROI overhaul | SPIPOWER |  |  | Circuits | Alstom | 275 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032184740268.2506944445 | 10321847 | 10293398 | Child | FALSE | NO.1 275KV CAPACITOR BANK AT HYTS | 40268.2507 | 40268.6431 | DAILY | 00331027 | SPIMAINT | Rebate W/O No1 Cap bank during ROI overhaul | SPIPOWER |  |  | Capacitors | Alstom | 275 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1032184840268.2506944445 | 10321848 | 10293398 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40268.2507 | 40268.6431 | DAILY | 00002862 | SPIMAINT | Rebate W/O M2 Trans during ROI overhaul | SPIPOWER |  |  | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031873340268.2513888889 | 10318733 |  | Parent | FALSE | MBTS-EPS 2 220KV N | 40268.2514 | 40268.6618 | DAILY | 00055381 | SPICAPX | Out W/O MBTS-EPS No2 Line OPGW cut - in | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_Z61058A940268.2625 | Z61058A9 |  | Parent | TRUE | MLTS-HYTS 2 500KV W | 40268.2625 | 40268.6292 | DAILY | 00022633 | SPICAPX | Out W/O MLTS-HYTS 2 Line to new Towers at MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058B140268.2625 | Z61058B1 | Z61058A9 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 40268.2625 | 40268.6292 | DAILY | 00003008 | SPICAPX | Rebate W/O Sh React for MOPS MLTS-HYTS 2 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z61058B240268.2625 | Z61058B2 | Z61058A9 | Child | FALSE | HYTS-APD 2 500KV W | 40268.2625 | 40268.6292 | DAILY | 00319999 | SPICAPX | Rebate W/O APD 2L for MOPS MLTS-HYTS 2 Line out | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V8F158B340268.2763888889 | V8F158B3 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 40268.2764 | 40268.6833 | DAILY | 00026099 | SPIMAINT | Check Oil Leaks | SPIPOWER | V8F1 | V8F1 - REPAIR OF OIL LEAKS IN TERMINAL STNS - STAGE 1 | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032332640269.85 | 10323326 |  | Parent | FALSE | NO.3 GEN TRANS NO.2 BUS 220KV CB AT HWPS | 40269.85 | 40276.9056 | CONT | [12 empty] | 0
_1032332340270.1763888889 | 10323323 |  | Parent | FALSE | LYBP-LYPS 2 500KV G | 40270.1764 | 40274.4 | CONT | 00023068 | GENCO | SCAP to LYPB | GENCO |  |  | Circuits | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1030649340274.2763888889 | 10306493 |  | Parent | TRUE | NO.1 330KV BUS AT SMTS | 40274.2764 | 40274.6681 | REPDAILY | 00001330 | SPIMAINT | O/Haul NO.1 330KV BUS AT SMTS | SPIPOWER |  |  | Bus | Western | 330 |  |  |  | 0
_1032286440274.2763888889 | 10322864 | 10306493 | Child | FALSE | H1 330/220KV TRANS BANK AT SMTS | 40274.2764 | 40274.6681 | REPDAILY | 00026101 | SPIMAINT | capture outage costs | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030725040274.2916666667 | 10307250 | 10307255 | Child | FALSE | NO.1 220KV CAPACITOR BANK CB AT ROTS | 40274.2917 | 40274.6167 | CONT | [12 empty] | 0
_1030725540274.2916666667 | 10307255 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK AT ROTS | 40274.2917 | 40274.6167 | CONT | 00354024 | SPIMAINT | O/Haul NO.1 220KV CAPACITOR BANK AT ROTS | SPIPOWER |  |  | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1027299740274.3178703704 | 10272997 |  | Parent | FALSE | LNGS NO.1 GEN TRANS X PROT AT ATS | 40274.3179 | 40274.6493 | REPDAILY | [12 empty] | 0
_1032335740274.4458333333 | 10323357 |  | Parent | FALSE | HWTS NO.2 500KV LINE AT LYPS | 40274.4458 | 40274.4681 | CONT | 00016087 | FAULT | Loss of 500kV Bus & HWTS 2 500KV Line at LYPS | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030649340275.2708333333 | 10306493 |  | Parent | TRUE | NO.1 330KV BUS AT SMTS | 40275.2708 | 40275.7903 | REPDAILY | 00001330 | SPIMAINT | O/Haul NO.1 330KV BUS AT SMTS | SPIPOWER |  |  | Bus | Western | 330 |  |  |  | 0
_1032286440275.2708333333 | 10322864 | 10306493 | Child | FALSE | H1 330/220KV TRANS BANK AT SMTS | 40275.2708 | 40275.7903 | REPDAILY | 00026101 | SPIMAINT | capture outage costs | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X70658V940275.2777777778 | X70658V9 |  | Parent | FALSE | B5 220/66KV TRANS AT KTS | 40275.2778 | 40275.6708 | DAILY | 00369184 | SPICAPX | CARRY OUT FUNCT CHECKS FOR B TRANS CLSE SCHM | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Connection Transformers | Western | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1026316040275.2930555556 | 10263160 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 40275.2931 | 40275.5764 | DAILY | 00112418 | SPIMAINT | Replace Cap Can Caps removed in hail storm | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030626540275.2958333333 | 10306265 |  | Parent | FALSE | H3 330/220KV TRANS AT DDTS | 40275.2958 | 40275.6951 | REPDAILY | 00003971 | SPIMAINT | 4 yr O/H No3 330/220/22KV Trans at DDTS | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030742640275.2986111111 | 10307426 |  | Parent | FALSE | B3 220/66KV TRANS AT RWTS | 40275.2986 | 40276.6778 | CONT | 00007455 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1027299740275.3228587963 | 10272997 |  | Parent | FALSE | LNGS NO.1 GEN TRANS X PROT AT ATS | 40275.3229 | 40275.6465 | REPDAILY | [12 empty] | 0
_1032338940275.9409722222 | 10323389 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 40275.941 | 40277.6736 | CONT | 00356086 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E958B840276.2402777778 | X7E958B8 |  | Parent | TRUE | SYTS 500KV LINE NO.2 BUS CB LINE SIDE ROI AT KTS | 40276.2403 | 40276.4743 | DAILY | [12 empty] | 0
_X7E958D440276.2402777778 | X7E958D4 | X7E958B8 | Child | FALSE | SYTS 500KV LINE AT KTS | 40276.2403 | 40276.4743 | DAILY | 00015990 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X7E9 | X7E9 - (KTS) 500KV CT & CB | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030626540276.2916666667 | 10306265 |  | Parent | FALSE | H3 330/220KV TRANS AT DDTS | 40276.2917 | 40276.7049 | REPDAILY | 00003971 | SPIMAINT | 4 yr O/H No3 330/220/22KV Trans at DDTS | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058B440276.2923611111 | Z61058B4 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40276.2924 | 40276.7035 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line to new Towers at MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058B540276.2923611111 | Z61058B5 | Z61058B4 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40276.2924 | 40276.7035 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058B740276.2923611111 | Z61058B7 | Z61058B4 | Child | FALSE | HYTS-APD 1 500KV W | 40276.2924 | 40276.7035 | REPDAILY | 00319998 | SPICAPX | Rebate W/O APD 1L during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61059B640276.2923611111 | Z61059B6 | Z61058B4 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40276.2924 | 40276.7035 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031204840276.2972222222 | 10312048 |  | Parent | FALSE | NO.2 CSC AT ROTS | 40276.2972 | 40277.6937 | CONT | 00004716 | SPIMAINT | O/Haul No.2 CSC at ROTS | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030649340276.3125 | 10306493 |  | Parent | TRUE | NO.1 330KV BUS AT SMTS | 40276.3125 | 40276.6792 | REPDAILY | 00001330 | SPIMAINT | O/Haul NO.1 330KV BUS AT SMTS | SPIPOWER |  |  | Bus | Western | 330 |  |  |  | 0
_1032286440276.3125 | 10322864 | 10306493 | Child | FALSE | H1 330/220KV TRANS BANK AT SMTS | 40276.3125 | 40276.6792 | REPDAILY | 00026101 | SPIMAINT | capture outage costs | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030585940276.4791666667 | 10305859 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK Y PROT AT LY | 40276.4792 | 40276.5118 | CONT | [12 empty] | 0
_1032340840277.2743055556 | 10323408 |  | Parent | FALSE | B4 220/66KV TRANS AT KTS | 40277.2743 | 40277.7354 | CONT | 00001146 | SPICAPX | B4 Trans holding overnight HVS | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658U340277.2743055556 | X70658U3 |  | Parent | FALSE | GTS NO.3 220KV LINE AT KTS | 40277.2743 | 40277.7354 | DAILY | 00368494 | SPICAPX | CONNECT GTS 3 L TO GTS 3L/B4 TR L/S ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030649340277.275 | 10306493 |  | Parent | TRUE | NO.1 330KV BUS AT SMTS | 40277.275 | 40277.6347 | REPDAILY | 00001330 | SPIMAINT | O/Haul NO.1 330KV BUS AT SMTS | SPIPOWER |  |  | Bus | Western | 330 |  |  |  | 0
_1032286440277.275 | 10322864 | 10306493 | Child | FALSE | H1 330/220KV TRANS BANK AT SMTS | 40277.275 | 40277.6347 | REPDAILY | 00026101 | SPIMAINT | capture outage costs | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058B440277.29375 | Z61058B4 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40277.2937 | 40277.641 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line to new Towers at MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058B540277.29375 | Z61058B5 | Z61058B4 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40277.2937 | 40277.641 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058B740277.29375 | Z61058B7 | Z61058B4 | Child | FALSE | HYTS-APD 1 500KV W | 40277.2937 | 40277.641 | REPDAILY | 00319998 | SPICAPX | Rebate W/O APD 1L during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61059B640277.29375 | Z61059B6 | Z61058B4 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40277.2937 | 40277.641 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032336140277.2972222222 | 10323361 |  | Parent | FALSE | YPS -YWPS 3 220KV G | 40277.2972 | 40328.3882 | CONT | 00020520 | GENCO | SCAP to Genco | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032263640277.3173611111 | 10322636 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK AT ROTS | 40277.3174 | 40277.5979 | DAILY | 00112417 | SPIMAINT | Replace capacitor Can Cap Blown off in hail storm | SPIPOWER |  |  | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1032341940277.9965277778 | 10323419 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 40277.9965 | 40286.5194 | CONT | [12 empty] | 0
_X70658U440278.2125 | X70658U4 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40278.2125 | 40278.7118 | DAILY | 00001169 | SPICAPX | RMVE BIPD CONNS TOB4 TR 1 B CB B/S ROI & RMVE ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658U540278.2125 | X70658U5 | X70658U4 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40278.2125 | 40278.7118 | DAILY | 00119824 | SPICAPX | REBATE COSTS CAPTURE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_V70358A740278.25 | V70358A7 |  | Parent | FALSE | KTS -ATS 220KV WY | 40278.25 | 40278.7194 | REPDAILY | 00074402 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058B440278.2944444444 | Z61058B4 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40278.2944 | 40278.6875 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line to new Towers at MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058B540278.2944444444 | Z61058B5 | Z61058B4 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40278.2944 | 40278.6875 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058B740278.2944444444 | Z61058B7 | Z61058B4 | Child | FALSE | HYTS-APD 1 500KV W | 40278.2944 | 40278.6875 | REPDAILY | 00319998 | SPICAPX | Rebate W/O APD 1L during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61059B640278.2944444444 | Z61059B6 | Z61058B4 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40278.2944 | 40278.6875 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032337940278.3076388889 | 10323379 |  | Parent | FALSE | L3 TRANS NO.3 BUS 22KV CB AT WMTS | 40278.3076 | 40278.4486 | DAILY | [12 empty] | 0
_V70358A740279.2520833333 | V70358A7 |  | Parent | FALSE | KTS -ATS 220KV WY | 40279.2521 | 40279.7229 | REPDAILY | 00074402 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E958D640279.2715277778 | X7E958D6 |  | Parent | FALSE | SYTS 500KV LINE NO.2 BUS CB BUS SIDE ROI AT KTS | 40279.2715 | 40279.4549 | CONT | [12 empty] | 0
_1032336340279.3298611111 | 10323363 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT RWTS (CONNECTED TO RWT21) | 40279.3299 | 40279.6285 | DAILY | 00368935 | DBPROX | VSCAP to DOC | DISTCO |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_1032342140279.4868055556 | 10323421 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 40279.4868 | 40279.6479 | DAILY | [12 empty] | 0
_V70358A840280.2631944444 | V70358A8 |  | Parent | FALSE | ATS -BLTS 220KV WY | 40280.2632 | 40280.6382 | REPDAILY | 00074403 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058B840280.2944444444 | Z61058B8 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40280.2944 | 40280.6806 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line to new Towers at MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058B940280.2944444444 | Z61058B9 | Z61058B8 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40280.2944 | 40280.6806 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058C040280.2944444444 | Z61058C0 | Z61058B8 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40280.2944 | 40280.6806 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z61058C140280.2944444444 | Z61058C1 | Z61058B8 | Child | FALSE | HYTS-APD 1 500KV W | 40280.2944 | 40280.6806 | REPDAILY | 00319998 | SPICAPX | Rebate W/O APD 1L during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032343840280.33125 | 10323438 |  | Parent | FALSE | SESS NO.1 275KV LINE AT HYTS | 40280.3313 | 40280.3326 | DAILY | 00021367 | FAULT | HYTS-SESS 1 275KV line offloaded by AVC | SPIPOWER |  |  | Circuits | Alstom | 275 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032343740280.53125 | 10323437 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 40280.5312 | 40281.4993 | CONT | 00337581 | FORCED | RCTS No1 Trans Grp De-ener due to Gas Alarm | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V70358A840281.2534722222 | V70358A8 |  | Parent | FALSE | ATS -BLTS 220KV WY | 40281.2535 | 40281.7819 | REPDAILY | 00074403 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030606340281.2638888889 | 10306063 |  | Parent | FALSE | DDTS NO.1 330KV LINE AT SMTS | 40281.2639 | 40281.7389 | REPDAILY | 00012749 | SPIMAINT | DDTS No.1 330kv Line Voltage Transformer | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058B840281.2916666667 | Z61058B8 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40281.2917 | 40281.6868 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line to new Towers at MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058B940281.2916666667 | Z61058B9 | Z61058B8 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40281.2917 | 40281.6868 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058C040281.2916666667 | Z61058C0 | Z61058B8 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40281.2917 | 40281.6868 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z61058C140281.2916666667 | Z61058C1 | Z61058B8 | Child | FALSE | HYTS-APD 1 500KV W | 40281.2917 | 40281.6868 | REPDAILY | 00319998 | SPICAPX | Rebate W/O APD 1L during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031419740281.2916666667 | 10314197 |  | Parent | FALSE | A2 TRANS NO.1 BUS 500KV CB AT ROTS | 40281.2917 | 40281.7111 | DAILY | [12 empty] | 0
_X7E858A340281.2958333333 | X7E858A3 |  | Parent | FALSE | A1 515/230KV TRANS AT HWTS | 40281.2958 | 40281.7229 | REPDAILY | 00009772 | SPIMAINT | CONSTRUCTION NEW EQUIPMENT JAMCO NO1 TX @HWTS | 3RDPARTY | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031205440281.3041666667 | 10312054 |  | Parent | FALSE | NO.1 CSC AT ROTS | 40281.3042 | 40282.5931 | CONT | 00004718 | SPIMAINT | O/Haul No.1 CSC at ROTS | SPIPOWER |  |  | SVC & CSC | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1032259140281.3138888889 | 10322591 |  | Parent | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 40281.3139 | 40282.7368 | CONT | 00004036 | SPIMAINT | Out W/O No1 Trans HV testing by Tech services | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032324940281.3229166667 | 10323249 |  | Parent | FALSE | 5 GRP 220/11KV TRANS AT YPS | 40281.3229 | 40281.6729 | REPDAILY | 00010550 | SPIMAINT | Proximity outage for CT replacement | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V70358A840282.2479166667 | V70358A8 |  | Parent | FALSE | ATS -BLTS 220KV WY | 40282.2479 | 40282.8021 | REPDAILY | 00074403 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030606340282.2527777778 | 10306063 |  | Parent | FALSE | DDTS NO.1 330KV LINE AT SMTS | 40282.2528 | 40282.7285 | REPDAILY | 00012749 | SPIMAINT | DDTS No.1 330kv Line Voltage Transformer | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031419540282.2902777778 | 10314195 |  | Parent | FALSE | A2 TRANS NO.2 BUS 500KV CB AT ROTS | 40282.2903 | 40282.6035 | DAILY | [12 empty] | 0
_Z61058B840282.2916666667 | Z61058B8 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40282.2917 | 40282.6993 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line to new Towers at MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058B940282.2916666667 | Z61058B9 | Z61058B8 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40282.2917 | 40282.6993 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058C040282.2916666667 | Z61058C0 | Z61058B8 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40282.2917 | 40282.6993 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z61058C140282.2916666667 | Z61058C1 | Z61058B8 | Child | FALSE | HYTS-APD 1 500KV W | 40282.2917 | 40282.6993 | REPDAILY | 00319998 | SPICAPX | Rebate W/O APD 1L during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E858A340282.2972222222 | X7E858A3 |  | Parent | FALSE | A1 515/230KV TRANS AT HWTS | 40282.2972 | 40282.5257 | REPDAILY | 00009772 | SPIMAINT | CONSTRUCTION NEW EQUIPMENT JAMCO NO1 TX @HWTS | 3RDPARTY | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032324940282.3131944445 | 10323249 |  | Parent | FALSE | 5 GRP 220/11KV TRANS AT YPS | 40282.3132 | 40282.6146 | REPDAILY | 00010550 | SPIMAINT | Proximity outage for CT replacement | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030597740282.5458333333 | 10305977 |  | Parent | FALSE | YWPS AUX TRANS 'A' 220KV LINE X PROT AT YPS | 40282.5458 | 40282.6319 | CONT | [12 empty] | 0
_V70358A840283.25 | V70358A8 |  | Parent | FALSE | ATS -BLTS 220KV WY | 40283.25 | 40283.8028 | REPDAILY | 00074403 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030606340283.2534722222 | 10306063 |  | Parent | FALSE | DDTS NO.1 330KV LINE AT SMTS | 40283.2535 | 40283.7569 | REPDAILY | 00012749 | SPIMAINT | DDTS No.1 330kv Line Voltage Transformer | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058B840283.2986111111 | Z61058B8 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40283.2986 | 40283.6924 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line to new Towers at MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058B940283.2986111111 | Z61058B9 | Z61058B8 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40283.2986 | 40283.6924 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058C040283.2986111111 | Z61058C0 | Z61058B8 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40283.2986 | 40283.6924 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z61058C140283.2986111111 | Z61058C1 | Z61058B8 | Child | FALSE | HYTS-APD 1 500KV W | 40283.2986 | 40283.6924 | REPDAILY | 00319998 | SPICAPX | Rebate W/O APD 1L during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030598140283.3229166667 | 10305981 |  | Parent | FALSE | YWPS AUX TRANS 'B' 220KV LINE X PROT AT YPS | 40283.3229 | 40284.5 | CONT | [12 empty] | 0
_1032351040283.9819444444 | 10323510 |  | Parent | FALSE | EX - NO.5 GEN TRANS 220KV CB AT HWPS | 40283.9819 | 40286.9167 | CONT | [12 empty] | 0
_1030606340284.21875 | 10306063 |  | Parent | FALSE | DDTS NO.1 330KV LINE AT SMTS | 40284.2188 | 40284.741 | REPDAILY | 00012749 | SPIMAINT | DDTS No.1 330kv Line Voltage Transformer | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V70358A840284.2513888889 | V70358A8 |  | Parent | FALSE | ATS -BLTS 220KV WY | 40284.2514 | 40284.6556 | REPDAILY | 00074403 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058C240284.2958333333 | Z61058C2 |  | Parent | TRUE | MLTS-HYTS 2 500KV W | 40284.2958 | 40284.791 | REPDAILY | 00022633 | SPICAPX | Out W/O MLTS-HYTS 2 Line to new Towers at MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058C340284.2958333333 | Z61058C3 | Z61058C2 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40284.2958 | 40284.791 | REPDAILY | 00002862 | SPICAPX | Rebate W/O M2 Trans during MLTS-HYTS 2 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058C440284.2958333333 | Z61058C4 | Z61058C2 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 40284.2958 | 40284.791 | REPDAILY | 00003008 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 2 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z61058C540284.2958333333 | Z61058C5 | Z61058C2 | Child | FALSE | HYTS-APD 2 500KV W | 40284.2958 | 40284.791 | REPDAILY | 00319999 | SPICAPX | Rebate W/O APD 2L during MLTS-HYTS 2 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031467540284.2986111111 | 10314675 |  | Parent | FALSE | CBTS NO.4 500KV LINE NO.2 BUS CB AT ROTS (RTF) | 40284.2986 | 40284.6632 | DAILY | [12 empty] | 0
_1030709940284.3118055556 | 10307099 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT DDTS | 40284.3118 | 40284.65 | DAILY | 00351939 | SPIMAINT | O/Haul NO.1 220KV CAPACITOR BANK AT DDTS | SPIPOWER |  |  | Capacitors | Alstom | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_V70358A940285.2506944445 | V70358A9 |  | Parent | FALSE | KTS -ATS 220KV WY | 40285.2507 | 40285.7285 | REPDAILY | 00074402 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032210840285.2548611111 | 10322108 |  | Parent | TRUE | NO.2 66KV BUS AT CBTS | 40285.2549 | 40285.6778 | DAILY | 00359471 | DB_AUG | Connect new CLN fdr to No 2 66Kv Bus | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032210940285.2548611111 | 10322109 | 10322108 | Child | FALSE | B2 220/66KV TRANS AT CBTS | 40285.2549 | 40285.6778 | DAILY | 00353077 | DB_AUG | tran rebate for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1032212140285.2548611111 | 10322121 | 10322108 | Child | FALSE | FTS NO.2 66KV FDR AT CBTS | 40285.2549 | 40285.6778 | DAILY | 00359486 | DB_AUG | Fdr rebate for Bus outage | SPIPOWER |  |  | Circuits | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_Z61058C240285.2708333333 | Z61058C2 |  | Parent | TRUE | MLTS-HYTS 2 500KV W | 40285.2708 | 40285.7597 | REPDAILY | 00022633 | SPICAPX | Out W/O MLTS-HYTS 2 Line to new Towers at MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058C340285.2708333333 | Z61058C3 | Z61058C2 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40285.2708 | 40285.7597 | REPDAILY | 00002862 | SPICAPX | Rebate W/O M2 Trans during MLTS-HYTS 2 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058C440285.2708333333 | Z61058C4 | Z61058C2 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 40285.2708 | 40285.7597 | REPDAILY | 00003008 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 2 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z61058C540285.2708333333 | Z61058C5 | Z61058C2 | Child | FALSE | HYTS-APD 2 500KV W | 40285.2708 | 40285.7597 | REPDAILY | 00319999 | SPICAPX | Rebate W/O APD 2L during MLTS-HYTS 2 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E858A440285.2715277778 | X7E858A4 |  | Parent | FALSE | LYPS NO.1 500KV LINE AT HWTS | 40285.2715 | 40285.7694 | DAILY | 00016234 | SPIMAINT | CONSTRUCTION OF EQUIPMENT JAMCO ON LYPS NO1 @ HWTS | 3RDPARTY | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029278240285.2840277778 | 10292782 |  | Parent | FALSE | NO.2 11/220KV TRANS BANK AT MPS | 40285.284 | 40286.6125 | CONT | 00001164 | SPIMAINT | Overhaul No2 Trans at MPS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | see note (2) | 0
_X70658W840285.2847222222 | X70658W8 |  | Parent | FALSE | B4 220/66KV TRANS AT KTS | 40285.2847 | 40285.5903 | DAILY | 00001146 | SPICAPX | EXCATVATE AND LAY CONDUITS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032342540285.3118055556 | 10323425 |  | Parent | FALSE | MLRC 220KV LINE AT RCTS | 40285.3118 | 40286.6097 | CONT | 00352130 | HVCUST | SCAP to Murraylink | HVCUST |  |  | Circuits | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 4
_1032362240285.8020833333 | 10323622 |  | Parent | FALSE | NO.3 66KV BUS AT CBTS | 40285.8021 | 40285.8535 | CONT | 00359472 | FORCED | Repair 2-3 66kV B/T isolator | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_V70358A940286.2611111111 | V70358A9 |  | Parent | FALSE | KTS -ATS 220KV WY | 40286.2611 | 40286.7118 | REPDAILY | 00074402 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058C240286.2708333333 | Z61058C2 |  | Parent | TRUE | MLTS-HYTS 2 500KV W | 40286.2708 | 40286.7194 | REPDAILY | 00022633 | SPICAPX | Out W/O MLTS-HYTS 2 Line to new Towers at MOPS | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058C340286.2708333333 | Z61058C3 | Z61058C2 | Child | FALSE | M2 500/275KV TRANS AT HYTS | 40286.2708 | 40286.7194 | REPDAILY | 00002862 | SPICAPX | Rebate W/O M2 Trans during MLTS-HYTS 2 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058C440286.2708333333 | Z61058C4 | Z61058C2 | Child | FALSE | HYTS NO.2 500KV LINE SHUNT REACTOR AT MLTS | 40286.2708 | 40286.7194 | REPDAILY | 00003008 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 2 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z61058C540286.2708333333 | Z61058C5 | Z61058C2 | Child | FALSE | HYTS-APD 2 500KV W | 40286.2708 | 40286.7194 | REPDAILY | 00319999 | SPICAPX | Rebate W/O APD 2L during MLTS-HYTS 2 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058P640286.2916666667 | X87058P6 |  | Parent | FALSE | YPS NO.8 220KV LINE AT ROTS | 40286.2917 | 40286.6653 | DAILY | 00024015 | SPICAPX | YPS-ROTS No 8 220kv Line insulator replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031150740286.3194444444 | 10311507 | 10314687 | Child | FALSE | CBTS NO.4 LINE / SMTS NO.3 LINE CB SMTS NO.3 LINE SIDE E/SW AT ROTS (RTF) | 40286.3194 | 40286.6035 | DAILY | [12 empty] | 0
_1031150940286.3194444444 | 10311509 | 10314687 | Child | FALSE | SMTS NO.3 LINE E/SW AT ROTS (RTF) | 40286.3194 | 40286.6035 | DAILY | [12 empty] | 0
_1031151140286.3194444444 | 10311511 | 10314687 | Child | FALSE | SMTS 500KV NO.3 LINE NO.1 BUS CB LINE SIDE E/SW AT ROTS (RTF) | 40286.3194 | 40286.6035 | DAILY | [12 empty] | 0
_1031206640286.3194444444 | 10312066 | 10314687 | Child | FALSE | CBTS NO.4 LINE / SMTS NO.3 LINE CB SMTS NO.3 LINE SIDE ROI AT ROTS (RTF) | 40286.3194 | 40286.6035 | DAILY | [12 empty] | 0
_1031206840286.3194444444 | 10312068 | 10314687 | Child | FALSE | SMTS NO.3 500KV LINE NO.1 BUS CB LINE SIDE ROI AT ROTS (RTF) | 40286.3194 | 40286.6035 | DAILY | [12 empty] | 0
_1031468740286.3194444444 | 10314687 |  | Parent | TRUE | SMTS NO.3 500KV LINE AT ROTS (RTF) | 40286.3194 | 40286.6035 | DAILY | 00356731 | SPIMAINT | Overhaul 500kV Line End | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031144340287.2520833333 | 10311443 |  | Parent | FALSE | DDTS NO.2 330KV LINE AT SMTS | 40287.2521 | 40287.6903 | REPDAILY | 00012750 | SPIMAINT | DDTS No.2 330kv Line Voltage Transformer | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V70358B040287.2625 | V70358B0 |  | Parent | FALSE | ATS -BLTS 220KV WY | 40287.2625 | 40287.6785 | REPDAILY | 00074403 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030742840287.2944444444 | 10307428 |  | Parent | FALSE | B4 220/66KV TRANS AT RWTS | 40287.2944 | 40288.6056 | CONT | 00007451 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031151340287.2958333333 | 10311513 | 10311515 | Child | FALSE | SMTS 500KV NO.3 LINE NO.1 BUS CB BUS SIDE E/SW AT ROTS (RTF) | 40287.2958 | 40287.684 | DAILY | [12 empty] | 0
_1031151540287.2958333333 | 10311515 |  | Parent | TRUE | NO.1 500KV BUS E/SW (BAY 2) AT ROTS (RTF) | 40287.2958 | 40287.684 | DAILY | [12 empty] | 0
_1031151740287.2958333333 | 10311517 | 10311515 | Child | FALSE | NO.1 500KV BUS E/SW (BAY 3) AT ROTS (RTF) | 40287.2958 | 40287.684 | DAILY | [12 empty] | 0
_1031207040287.2958333333 | 10312070 | 10311515 | Child | FALSE | SMTS 500KV NO.3 LINE NO.1 BUS CB BUS SIDE ROI AT ROTS (RTF) | 40287.2958 | 40287.684 | DAILY | [12 empty] | 0
_1031207840287.2958333333 | 10312078 | 10311515 | Child | FALSE | A1 TRANS NO.1 BUS 500KV CB BUS SIDE E/SW AT ROTS (RTF) | 40287.2958 | 40287.684 | DAILY | [12 empty] | 0
_1031420840287.2958333333 | 10314208 | 10311515 | Child | FALSE | A2 TRANS NO.1 BUS 500KV CB BUS SIDE ROI AT ROTS | 40287.2958 | 40287.684 | DAILY | [12 empty] | 0
_1031421840287.2958333333 | 10314218 | 10311515 | Child | FALSE | A2 TRANS NO.1 BUS 500KV CB BUS SIDE E/SW AT ROTS | 40287.2958 | 40287.684 | DAILY | [12 empty] | 0
_1031467740287.2958333333 | 10314677 | 10311515 | Child | FALSE | A1 TRANS NO.1 BUS 500KV CB BUS SIDE ROI AT ROTS (RTF) | 40287.2958 | 40287.684 | DAILY | [12 empty] | 0
_1031182840287.3180555556 | 10311828 |  | Parent | FALSE | YPS NO.1 220KV LINE NO.6 BUS CB AT HWPS | 40287.3181 | 40290.5764 | CONT | [12 empty] | 0
_1032283540287.3319444444 | 10322835 |  | Parent | FALSE | AEMO METERING AT BLTS | 40287.3319 | 40287.409 | DAILY | [12 empty] | 0
_1032283640287.4118055556 | 10322836 |  | Parent | FALSE | L2 220/22KV TRANS BANK 22KV MET & SYNC VT AT BLTS | 40287.4118 | 40287.491 | DAILY | [12 empty] | 0
_V70358B040288.2513888889 | V70358B0 |  | Parent | FALSE | ATS -BLTS 220KV WY | 40288.2514 | 40288.7403 | REPDAILY | 00074403 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031144340288.2618055556 | 10311443 |  | Parent | FALSE | DDTS NO.2 330KV LINE AT SMTS | 40288.2618 | 40288.6937 | REPDAILY | 00012750 | SPIMAINT | DDTS No.2 330kv Line Voltage Transformer | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030213940288.2993055556 | 10302139 | 10314685 | Child | FALSE | HWTS NO.3 500KV LINE NO.2 BUS CB BUS SIDE ROI AT ROTS (RTF) | 40288.2993 | 40288.6757 | DAILY | [12 empty] | 0
_1031420240288.2993055556 | 10314202 | 10314685 | Child | FALSE | A2 TRANS NO.2 BUS 500KV CB BUS SIDE ROI AT ROTS | 40288.2993 | 40288.6757 | DAILY | [12 empty] | 0
_1031421040288.2993055556 | 10314210 | 10314685 | Child | FALSE | A2 TRANS NO.2 BUS 500KV CB BUS SIDE E/SW AT ROTS | 40288.2993 | 40288.6757 | DAILY | [12 empty] | 0
_1031467940288.2993055556 | 10314679 | 10314685 | Child | FALSE | CBTS NO.4 500KV LINE NO.2 BUS CB BUS SIDE ROI AT ROTS (RTF) | 40288.2993 | 40288.6757 | DAILY | [12 empty] | 0
_1031468140288.2993055556 | 10314681 | 10314685 | Child | FALSE | HWTS NO.3 500KV LINE NO.2 BUS CB BUS SIDE E/SW AT ROTS (RTF) | 40288.2993 | 40288.6757 | DAILY | [12 empty] | 0
_1031468340288.2993055556 | 10314683 | 10314685 | Child | FALSE | CBTS NO.4 500KV LINE NO.2 BUS CB BUS SIDE E/SW AT ROTS (RTF) | 40288.2993 | 40288.6757 | DAILY | [12 empty] | 0
_1031468540288.2993055556 | 10314685 |  | Parent | TRUE | NO.2 500KV BUS E/SW AT ROTS (RTF) | 40288.2993 | 40288.6757 | DAILY | [12 empty] | 0
_X89058B940288.3125 | X89058B9 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40288.3125 | 40288.6924 | REPDAILY | 00319998 | SPICAPX | Erect temp bypass line between T591 and T603 | SPIPOWER | X890 | X890 - (HYTS-APD) LINE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031069640288.3131944445 | 10310696 |  | Parent | FALSE | SYTS NO.1 500KV LINE AT MLTS | 40288.3132 | 40288.7451 | REPDAILY | 00022766 | SPIMAINT | OVERHAUL OF A 500KV LINE | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032284040288.3236111111 | 10322840 |  | Parent | FALSE | L1 TRANS 22KV CB AT BLTS | 40288.3236 | 40288.4639 | DAILY | [12 empty] | 0
_1032284440288.4763888889 | 10322844 |  | Parent | FALSE | L2 TRANS 22KV CB AT BLTS | 40288.4764 | 40288.5903 | DAILY | [12 empty] | 0
_1032370040288.7361342593 | 10323700 |  | Parent | FALSE | W3 GEN TRANS NO.1 BUS 220KV CB AT YPS | 40288.7361 | 40298.1058 | CONT | [12 empty] | 0
_1003377840289.2743055556 | 10033778 |  | Parent | TRUE | S130 MBTS-EPS 1 220KV | 40289.2743 | 40289.6222 | DAILY | [12 empty] | 0
_1032418440289.2743055556 | 10324184 | 10033778 | Child | FALSE | MBTS-EPS 1 220KV N | 40289.2743 | 40289.6222 | DAILY | 00055380 | SPIMAINT | Rebate capture wo | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1031144340289.2756944444 | 10311443 |  | Parent | FALSE | DDTS NO.2 330KV LINE AT SMTS | 40289.2757 | 40289.6868 | REPDAILY | 00012750 | SPIMAINT | DDTS No.2 330kv Line Voltage Transformer | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031206240289.2951388889 | 10312062 | 10323207 | Child | FALSE | A1 TRANS NO.1 BUS 500KV CB TRANS SIDE ROI AT ROTS (RTF) | 40289.2951 | 40289.659 | DAILY | [12 empty] | 0
_1031206440289.2951388889 | 10312064 | 10323207 | Child | FALSE | HWTS NO.3 LINE A1 TRANS 500KV CB TRANS SIDE ROI AT ROTS (RTF) | 40289.2951 | 40289.659 | DAILY | [12 empty] | 0
_1031207240289.2951388889 | 10312072 | 10323207 | Child | FALSE | HWTS NO.3 LINE A1 TRANS 500KV CB TRANS SIDE E/SW AT ROTS (RTF) | 40289.2951 | 40289.659 | DAILY | [12 empty] | 0
_1031207440289.2951388889 | 10312074 | 10323207 | Child | FALSE | A1 TRANS NO.1 BUS 500KV CB TRANS SIDE E/SW AT ROTS (RTF) | 40289.2951 | 40289.659 | DAILY | [12 empty] | 0
_1031207640289.2951388889 | 10312076 | 10323207 | Child | FALSE | A1 TRANS 500KV E/SW AT ROTS (RTF) | 40289.2951 | 40289.659 | DAILY | [12 empty] | 0
_1032320740289.2951388889 | 10323207 |  | Parent | TRUE | A1 515/220KV TRANS BANK AT ROTS (RTF) | 40289.2951 | 40289.659 | DAILY | 00354002 | SPIMAINT | O/H A1 Trans 500kv Isols (Trans Rebate) | SPIPOWER |  |  | Main Transformers | Eastern | 500 | NON SP ASSET | EXCLUDED | Maint by SPAusNet. Owned by RTF | 0
_1031069640289.3 | 10310696 |  | Parent | FALSE | SYTS NO.1 500KV LINE AT MLTS | 40289.3 | 40289.6625 | REPDAILY | 00022766 | SPIMAINT | OVERHAUL OF A 500KV LINE | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032284540289.3194444444 | 10322845 |  | Parent | FALSE | U1 TRANS-PAR 22KV CB AT BLTS | 40289.3194 | 40289.4903 | DAILY | [12 empty] | 0
_X70658T240290.2291666667 | X70658T2 |  | Parent | FALSE | NO.4 66KV BUS AT KTS | 40290.2292 | 40290.6542 | DAILY | 00001174 | SPICAPX | REPLACE B4 TRANS 66KV BUS SIDE ISOL. | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031144340290.2722222222 | 10311443 |  | Parent | FALSE | DDTS NO.2 330KV LINE AT SMTS | 40290.2722 | 40290.6639 | REPDAILY | 00012750 | SPIMAINT | DDTS No.2 330kv Line Voltage Transformer | SPIPOWER |  |  | Circuits | Western | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1029590140290.2854166667 | 10295901 | 10314254 | Child | FALSE | YPS NO.5 220KV LINE NO.1 BUS CB BUS SIDE ROI AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1029591140290.2854166667 | 10295911 | 10314254 | Child | FALSE | YPS NO.5 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1031408540290.2854166667 | 10314085 | 10314254 | Child | FALSE | A2 TRANS NO.1 BUS 220KV CB BUS SIDE ROI AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1031409740290.2854166667 | 10314097 | 10314254 | Child | FALSE | TTS 220KV LINE NO.1 BUS CB BUS SIDE ROI AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1031410940290.2854166667 | 10314109 | 10314254 | Child | FALSE | HWPS NO.1 220KV LINE NO.1 BUS CB BUS SIDE ROI AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1031411940290.2854166667 | 10314119 | 10314254 | Child | FALSE | HWPS NO.2 220KV LINE NO.1 BUS CB BUS SIDE ROI AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1031412540290.2854166667 | 10314125 | 10314254 | Child | FALSE | RTS NO.1 220KV LINE NO.1 BUS CB BUS SIDE ROI AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1031423640290.2854166667 | 10314236 | 10314254 | Child | FALSE | RTS NO.1 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1031425240290.2854166667 | 10314252 | 10314254 | Child | FALSE | HWPS NO.2 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1031425440290.2854166667 | 10314254 |  | Parent | TRUE | NO.1 220KV BUS E/SW AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1031426640290.2854166667 | 10314266 | 10314254 | Child | FALSE | HWPS NO.1 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1031427240290.2854166667 | 10314272 | 10314254 | Child | FALSE | TTS 220KV LINE NO.1 BUS CB BUS SIDE E/SW AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1032308140290.2854166667 | 10323081 | 10314254 | Child | FALSE | NO.1 220KV CAPACITOR BANK CB BUS SIDE ROI AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1032308340290.2854166667 | 10323083 | 10314254 | Child | FALSE | NO.1 220KV CAPACITOR BANK CB BUS SIDE E/SW AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1032308740290.2854166667 | 10323087 | 10314254 | Child | FALSE | NO.1 CSC NO.1 BUS CB BUS SIDE ISOL AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1032308940290.2854166667 | 10323089 | 10314254 | Child | FALSE | NO.1 CSC NO.1 BUS CB NO.1 BUS SIDE E/SW AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1032309540290.2854166667 | 10323095 | 10314254 | Child | FALSE | A2 TRANS NO.1 BUS 220KV CB BUS SIDE E/SW AT ROTS | 40290.2854 | 40291.6264 | CONT | [12 empty] | 0
_1032319540290.2854166667 | 10323195 | 10314254 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 40290.2854 | 40291.6264 | CONT | 00354024 | SPIMAINT | Rebate Cap Bank for Bus outage | SPIPOWER |  |  | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1032328240290.2854166667 | 10323282 | 10314254 | Child | FALSE | NO.1 220KV BUS AT ROTS | 40290.2854 | 40291.6264 | CONT | 00004776 | SPIMAINT | O/Haul NO.1 220KV BUS AT ROTS | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031070440290.2916666667 | 10310704 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT MLTS | 40290.2917 | 40290.7167 | REPDAILY | 00022778 | SPIMAINT | OVERHAUL OF A 500KV LINE | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030722140290.2916666667 | 10307221 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 40290.2917 | 40290.7201 | DAILY | 00352121 | SPIMAINT | 4 Yrly O/H of H2 330/220kv Transformer at DDTS | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029553340290.3034722222 | 10295533 |  | Parent | FALSE | B2 220/66KV TRANS AT RWTS | 40290.3035 | 40291.6312 | CONT | 00007450 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  | Push to 2010 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032284940290.4298611111 | 10322849 |  | Parent | FALSE | SYN/COND START MOTOR TRANS CB AT BLTS | 40290.4299 | 40290.4674 | DAILY | [12 empty] | 0
_1032376240290.6388888889 | 10323762 |  | Parent | FALSE | NO.7 GEN TRANS 220KV CB AT HWPS | 40290.6389 | 40292.9167 | CONT | [12 empty] | 0
_X70658T340290.6569444445 | X70658T3 |  | Parent | FALSE | EX - B4 TRANS 66KV CB AT KTS | 40290.6569 | 40300.309 | CONT | [12 empty] | 0
_1031070440291.2916666667 | 10310704 |  | Parent | FALSE | SYTS NO.2 500KV LINE AT MLTS | 40291.2917 | 40291.6431 | REPDAILY | 00022778 | SPIMAINT | OVERHAUL OF A 500KV LINE | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030626340291.2916666667 | 10306263 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT DDTS | 40291.2917 | 40291.741 | DAILY | 00337558 | SPIMAINT | TRANSFORMER ROUTINE INSP (NO OLTC) | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032384340291.475 | 10323843 |  | Parent | FALSE | SYTS NO.1 500KV LINE AT SMTS | 40291.475 | 40291.5181 | CONT | 00012439 | FAULT | SYTS 1 Line CBs inadvertent trip at SMTS | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030586140291.4756944444 | 10305861 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK Y PROT AT LY | 40291.4757 | 40291.643 | CONT | [12 empty] | 0
_V70358B140292.2743055556 | V70358B1 |  | Parent | FALSE | KTS -ATS 220KV WY | 40292.2743 | 40292.6903 | REPDAILY | 00074402 | SPIMAINT | TOWER PAINTING | SPIPOWER | V703 | V703 - TOWER PAINTING OF TX37 (KTS-ATS) & T36 (ATS-KTS) | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032140840292.2770833333 | 10321408 | X81158B4 | Child | FALSE | EX - NPSD 220KV LINE CB CT R/PH AT FBTS | 40292.2771 | 40292.7542 | DAILY | [12 empty] | 0
_X81158B440292.2770833333 | X81158B4 |  | Parent | TRUE | B1 220/66KV TRANS AT TBTS | 40292.2771 | 40292.7542 | DAILY | 00004901 | SPICAPX | B1 Trans 66 kv CB CT REPLACEMENT | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032384540292.691099537 | 10323845 |  | Parent | FALSE | NO.3 GEN 220/16.5KV TRANS AT HWPS | 40292.6911 | 40293.5243 | CONT | 00009644 | GENCO | Isolation for Gen | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1032140640293.2694444444 | 10321406 | X81158B2 | Child | FALSE | EX - NPSD 220KV LINE CB CT R/PH AT FBTS | 40293.2694 | 40293.6708 | DAILY | [12 empty] | 0
_X81158B240293.2694444444 | X81158B2 |  | Parent | TRUE | B2 220/66KV TRANS AT TBTS | 40293.2694 | 40293.6708 | DAILY | 00004902 | SPICAPX | B2 Trans 66 kv CB CT REPLACEMENT | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032385240294.3766203704 | 10323852 |  | Parent | FALSE | HYTS NO.1 LINE/SYTS NO.1 LINE 500KV CB AT MLTS | 40294.3766 | 40294.4382 | CONT | [12 empty] | 0
_1032388540295.9819444444 | 10323885 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 40295.9819 | 40298.4444 | CONT | 00356081 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030669140296.2930555556 | 10306691 | 10306697 | Child | FALSE | NO.4 220KV CAPACITOR BANK AT BLTS | 40296.2931 | 40297.6139 | DAILY | 00327921 | SPIMAINT | O/Haul NO.4 220KV CAPACITOR BANK AT BLTS | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030669740296.2930555556 | 10306697 |  | Parent | TRUE | NO.4 220KV CAPACITOR BANK CB AT BLTS | 40296.2931 | 40297.6139 | CONT | [12 empty] | 0
_X81158A340296.2944444444 | X81158A3 |  | Parent | FALSE | LYPS NO.3 LINE/CBTS NO.4 LINE 500KV CB AT HWTS | 40296.2944 | 40299.9299 | CONT | [12 empty] | 0
_1031171940296.3229166667 | 10311719 |  | Parent | TRUE | HWPS NO.1 220KV LINE CB AT JLTS | 40296.3229 | 40296.5993 | DAILY | [12 empty] | 0
_1031688340296.3229166667 | 10316883 | 10311719 | Child | FALSE | HWPS NO.1 220KV LINE AT JLTS | 40296.3229 | 40296.5993 | DAILY | 00015936 | SPIMAINT | LINE REBATE FOR CB OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032389840296.5166666667 | 10323898 |  | Parent | FALSE | JLA NO.2 220KV LINE AT TBTS | 40296.5167 | 40296.7132 | DAILY | 00026919 | HVCUST | Line outage requested by Bluescope Steel JLA | HVCUST |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032385540296.5194444444 | 10323855 |  | Parent | FALSE | R1 220/66/22KV TRANS GROUP AT RCTS | 40296.5194 | 40296.7576 | DAILY | 00337581 | SPIMAINT | Test operation of 1A Trans gas relay | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032385940296.658900463 | 10323859 |  | Parent | FALSE | YPS NO.4 220KV LINE AT YWPS | 40296.6589 | 40303.659 | CONT | 00016404 | GENCO | Gen Outage | GENCO |  |  | Circuits | Eastern | 220 |  |  |  | 0
_1032393840296.7131944444 | 10323938 |  | Parent | FALSE | JLA NO.2 220KV LINE AT TBTS | 40296.7132 | 40296.791 | DAILY | 00026919 | FORCED | Rebate outage for CB failure | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058Q040297.2861111111 | X87058Q0 |  | Parent | TRUE | YPS NO.7 220KV LINE AT ROTS | 40297.2861 | 40297.7562 | REPDAILY | 00024013 | SPICAPX | YPS-ROTS 7& 8 Lines | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058Q140297.2861111111 | X87058Q1 | X87058Q0 | Child | FALSE | YPS NO.8 220KV LINE AT ROTS | 40297.2861 | 40297.7562 | REPDAILY | 00024015 | SPICAPX | Rebate 8 Line | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032344540297.3069444444 | 10323445 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT ERTS | 40297.3069 | 40297.5799 | DAILY | 00004344 | SPIMAINT | Re-Balance Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030721940297.3069444444 | 10307219 |  | Parent | FALSE | GNTS NO.3 220KV LINE AT SHTS | 40297.3069 | 40297.7174 | DAILY | 00352426 | SPIMAINT | O/H GNTS NO.3 220KV LINE AT SHTS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058Q040298.2513888889 | X87058Q0 |  | Parent | TRUE | YPS NO.7 220KV LINE AT ROTS | 40298.2514 | 40298.7785 | REPDAILY | 00024013 | SPICAPX | YPS-ROTS 7& 8 Lines | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058Q140298.2513888889 | X87058Q1 | X87058Q0 | Child | FALSE | YPS NO.8 220KV LINE AT ROTS | 40298.2514 | 40298.7785 | REPDAILY | 00024015 | SPICAPX | Rebate 8 Line | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031407540298.2777777778 | 10314075 |  | Parent | FALSE | RTS NO.1 220KV LINE NO.1 BUS CB AT ROTS | 40298.2778 | 40298.6403 | DAILY | [12 empty] | 0
_1032347740298.3027777778 | 10323477 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT RTS | 40298.3028 | 40298.559 | DAILY | 00007279 | SPIMAINT | Re-Balance Cap Bank | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X87058Q040299.2534722222 | X87058Q0 |  | Parent | TRUE | YPS NO.7 220KV LINE AT ROTS | 40299.2535 | 40299.7125 | REPDAILY | 00024013 | SPICAPX | YPS-ROTS 7& 8 Lines | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058Q140299.2534722222 | X87058Q1 | X87058Q0 | Child | FALSE | YPS NO.8 220KV LINE AT ROTS | 40299.2535 | 40299.7125 | REPDAILY | 00024015 | SPICAPX | Rebate 8 Line | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032402640299.8944444444 | 10324026 |  | Parent | FALSE | LYPS NO.3 500KV LINE AT HWTS | 40299.8944 | 40299.9299 | DAILY | 00016236 | SPICAPX | Line de-energised for CT commissioning | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658U640300.2194444445 | X70658U6 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40300.2194 | 40300.7278 | DAILY | 00001169 | SPICAPX | CONNS FROM NO1 BUS TO B4 TR 1B CB B/S ROI. | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658U740300.2194444445 | X70658U7 | X70658U6 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40300.2194 | 40300.7278 | DAILY | 00119824 | SPICAPX | REBATE COSTS CAPTURE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X87058Q040300.2534722222 | X87058Q0 |  | Parent | TRUE | YPS NO.7 220KV LINE AT ROTS | 40300.2535 | 40300.7319 | REPDAILY | 00024013 | SPICAPX | YPS-ROTS 7& 8 Lines | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058Q140300.2534722222 | X87058Q1 | X87058Q0 | Child | FALSE | YPS NO.8 220KV LINE AT ROTS | 40300.2535 | 40300.7319 | REPDAILY | 00024015 | SPICAPX | Rebate 8 Line | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031199040300.3034722222 | 10311990 |  | Parent | FALSE | NO.1 220KV BUS AT SVTS | 40300.3035 | 40300.6417 | DAILY | 00004856 | SPIMAINT | O/Haul NO.1 220KV BUS AT SVTS | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1032365540300.3111111111 | 10323655 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT RWTS (CONNECTED TO RWT11) | 40300.3111 | 40300.6417 | DAILY | 00368934 | DBPROX | VSCAP to DOC | DISTCO |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_X87058Q040301.2520833333 | X87058Q0 |  | Parent | TRUE | YPS NO.7 220KV LINE AT ROTS | 40301.2521 | 40301.7417 | REPDAILY | 00024013 | SPICAPX | YPS-ROTS 7& 8 Lines | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058Q140301.2520833333 | X87058Q1 | X87058Q0 | Child | FALSE | YPS NO.8 220KV LINE AT ROTS | 40301.2521 | 40301.7417 | REPDAILY | 00024015 | SPICAPX | Rebate 8 Line | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058C640301.2923611111 | Z61058C6 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40301.2924 | 40301.7111 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line redundant tower removal | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058C740301.2923611111 | Z61058C7 | Z61058C6 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40301.2924 | 40301.7111 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058C840301.2923611111 | Z61058C8 | Z61058C6 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40301.2924 | 40301.7111 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z61058C940301.2923611111 | Z61058C9 | Z61058C6 | Child | FALSE | HYTS-APD 1 500KV W | 40301.2924 | 40301.7111 | REPDAILY | 00319998 | SPICAPX | Rebate W/O APD 1L during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032326240301.2979166667 | 10323262 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK CB AT SVTS | 40301.2979 | 40301.6528 | DAILY | [12 empty] | 0
_1030682540301.3388888889 | 10306825 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT GNTS | 40301.3389 | 40301.6535 | DAILY | 00000745 | SPIMAINT | O/Haul NO.2 22KV/415V S/S TRANS AT GNTS | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1031455240301.3423611111 | 10314552 |  | Parent | FALSE | MLTS NO.2 220KV LINE NO.2 BUS CB AT BATS | 40301.3424 | 40301.5944 | DAILY | [12 empty] | 0
_1029412040301.4166666667 | 10294120 |  | Parent | FALSE | F2 500/330KV TRANS BANK AT SMTS | 40301.4167 | 40305.5542 | CONT | 00026099 | SPIMAINT | Condition Monitoring Metro Trans 3day West Area | SPIPOWER |  | Push to next year 2010 | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031156740302.2798611111 | 10311567 |  | Parent | TRUE | NO.1 220KV BUS AT YPS | 40302.2799 | 40303.625 | CONT | 00010588 | SPIMAINT | O/Haul NO.1 220KV BUS AT YPS | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1031689140302.2798611111 | 10316891 | 10311567 | Child | FALSE | ROTS NO.7 220KV LINE AT YPS | 40302.2799 | 40303.625 | CONT | 00016415 | SPIMAINT | LINE REBATE FOR BUS OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031689240302.2798611111 | 10316892 | 10311567 | Child | FALSE | HWPS-YPS 1 220KV G | 40302.2799 | 40303.625 | CONT | 00020461 | SPIMAINT | LINE REBATE FOR BUS OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V8B658A240302.2798611111 | V8B658A2 | V8B658A4 | Child | FALSE | AUX 'E' 220/22KV TRANS 220KV CB BUS SIDE ROI AT YPS | 40302.2799 | 40303.625 | DAILY | [12 empty] | 0
_Z61058C640302.2916666667 | Z61058C6 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40302.2917 | 40302.8521 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line redundant tower removal | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058C740302.2916666667 | Z61058C7 | Z61058C6 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40302.2917 | 40302.8521 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058C840302.2916666667 | Z61058C8 | Z61058C6 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40302.2917 | 40302.8521 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z61058C940302.2916666667 | Z61058C9 | Z61058C6 | Child | FALSE | HYTS-APD 1 500KV W | 40302.2917 | 40302.8521 | REPDAILY | 00319998 | SPICAPX | Rebate W/O APD 1L during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031405540302.2965277778 | 10314055 |  | Parent | TRUE | MTS NO.3 220KV LINE CB AT ROTS | 40302.2965 | 40302.6271 | DAILY | [12 empty] | 0
_1032356640302.2965277778 | 10323566 | 10314055 | Child | FALSE | MTS NO.3 220KV LINE AT ROTS | 40302.2965 | 40302.6271 | DAILY | 00023099 | SPIMAINT | Line outage Rebate | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031456240302.3166666667 | 10314562 |  | Parent | TRUE | MLTS NO.1 220KV LINE E/SW AT BATS | 40302.3167 | 40302.6979 | DAILY | [12 empty] | 0
_1032342940302.3166666667 | 10323429 | 10314562 | Child | FALSE | MLTS NO.1 220KV LINE AT BATS | 40302.3167 | 40302.6979 | DAILY | 00012429 | SPIMAINT | Rebate W/O MLTS No1 Line during CB & line equip OH | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032346640302.3305555556 | 10323466 |  | Parent | FALSE | MKPS-BOPS-MBTS 220KV NW | 40302.3306 | 40302.4639 | DAILY | 00060197 | SPIMAINT | Out W/O MKPS-BOPS-MBTS Line - Lines EAP issue | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030660340302.3402777778 | 10306603 |  | Parent | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 40302.3403 | 40302.6417 | DAILY | 00329970 | SPIMAINT | OVERHAUL NO 1 TRANS GROUP | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031518240303.2923611111 | 10315182 |  | Parent | FALSE | MTS NO.1 220KV LINE AT ROTS | 40303.2924 | 40303.6076 | DAILY | 00350667 | SPIMAINT | O/Haul - 220kV Line CVT's | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058C640303.2923611111 | Z61058C6 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40303.2924 | 40303.6924 | REPDAILY | 00022630 | SPICAPX | Out W/O MLTS-HYTS 1 Line redundant tower removal | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058C740303.2923611111 | Z61058C7 | Z61058C6 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40303.2924 | 40303.6924 | REPDAILY | 00002863 | SPICAPX | Rebate W/O M1 Trans during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058C840303.2923611111 | Z61058C8 | Z61058C6 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40303.2924 | 40303.6924 | REPDAILY | 00003007 | SPICAPX | Rebate W/O Sh React during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z61058C940303.2923611111 | Z61058C9 | Z61058C6 | Child | FALSE | HYTS-APD 1 500KV W | 40303.2924 | 40303.6924 | REPDAILY | 00319998 | SPICAPX | Rebate W/O APD 1L during MLTS-HYTS 1 Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031399340303.3173611111 | 10313993 |  | Parent | FALSE | BETS 220KV LINE NO.2 BUS CB AT BATS | 40303.3174 | 40303.5819 | DAILY | [12 empty] | 0
_X7E958E140303.5319444445 | X7E958E1 |  | Parent | FALSE | EX - SMTS 500KV LINE NO.2 BUS CB AT KTS | 40303.5319 | 40334.7882 | CONT | [12 empty] | 0
_1032418140303.7041666667 | 10324181 |  | Parent | FALSE | FVTS/SHTS 220KV LINE AT BETS | 40303.7042 | 40303.7132 | DAILY | 00364420 | FORCED | Removal of foreign object | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032418640303.9493055556 | 10324186 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 40303.9493 | 40308.8958 | CONT | 00356082 | GENCO | Unit 4 outage for power station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1026879140304.2916666667 | 10268791 |  | Parent | FALSE | BETS 220KV LINE AT BATS | 40304.2917 | 40304.6597 | DAILY | 00012434 | SPIMAINT | O/Haul BETS 220 kv L at BATS | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031212540304.2972222222 | 10312125 | 10318394 | Child | FALSE | ROTS NO.3 LINE/B1 TRANS 220KV CB TRANS SIDE E/SW AT MTS | 40304.2972 | 40304.6299 | DAILY | [12 empty] | 0
_1031839440304.2972222222 | 10318394 |  | Parent | TRUE | B1 220/66KV TRANS AT MTS | 40304.2972 | 40304.6299 | DAILY | 00364562 | SPIMAINT | Rebate for Trans outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032259540304.3159722222 | 10322595 |  | Parent | FALSE | HWTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 40304.316 | 40304.45 | DAILY | [12 empty] | 0
_1032402540304.3270833333 | 10324025 |  | Parent | FALSE | JLGB NO.2 UNIT TRANS DISC CB AT JLGB | 40304.3271 | 40312.6666 | CONT | [12 empty] | 0
_1032343240304.4027777778 | 10323432 |  | Parent | TRUE | NO.2 TRANS 66KV CB AT WOTS | 40304.4028 | 40304.4861 | DAILY | [12 empty] | 0
_1032343540304.4027777778 | 10323435 | 10323432 | Child | FALSE | NO.2 330/66/22KV TRANS AT WOTS | 40304.4028 | 40304.4861 | DAILY | 00004037 | SPIMAINT | Perf calc W/O No2 Trans during 66 CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031164140305.25625 | 10311641 |  | Parent | FALSE | HWPS NO.1 220KV LINE CB LINE SIDE ISOL AT YPS | 40305.2562 | 40305.6979 | CONT | [12 empty] | 0
_1031840240305.2944444444 | 10318402 |  | Parent | FALSE | B3 220/66KV TRANS AT MTS | 40305.2944 | 40305.5931 | DAILY | 00363305 | SPIMAINT | Rebate for Tran outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658M340305.2951388889 | X70658M3 |  | Parent | FALSE | EX - WMTS NO.1 220KV LINE AT KTS | 40305.2951 | 40305.616 | DAILY | 00015983 | SPICAPX | Replace WMTS No 1 Line Termination | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031400540305.3048611111 | 10314005 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT BATS | 40305.3049 | 40305.5257 | DAILY | [12 empty] | 0
_1032420540305.3145833333 | 10324205 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.2 BUS CB AT HWTS | 40305.3146 | 40305.6215 | DAILY | [12 empty] | 0
_1032422240305.3590277778 | 10324222 |  | Parent | FALSE | JLGA NO.3 UNIT TRANS DISC CB AT JLGA | 40305.359 | 40305.7569 | DAILY | [12 empty] | 0
_1032423440305.5881944444 | 10324234 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40305.5882 | 40305.6417 | CONT | 00003011 | FAULT | Shunt reactor tripping | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658W140305.6215277778 | X70658W1 |  | Parent | FALSE | EX - TTS NO.1 LINE/WMTS NO.1 LINE 220KV CB AT KTS | 40305.6215 | 40310.2986 | CONT | [12 empty] | 0
_1032424440305.9708333333 | 10324244 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 40305.9708 | 40310.7257 | CONT | 00356084 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658P040306.2520833333 | X70658P0 |  | Parent | FALSE | NO.4 66KV BUS AT KTS | 40306.2521 | 40306.5826 | DAILY | 00001174 | SPICAPX | REMOVE No.3-4 66KV BUS TIE CB | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E858A540306.3138888889 | X7E858A5 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE AT HWTS | 40306.3139 | 40309.6687 | CONT | 00016237 | SPIMAINT | CONSTRUCTION WORKS SMTS NO1 LINE @HWTS JAMCO | 3RDPARTY | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658P440306.5673611111 | X70658P4 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT KTS | 40306.5674 | 40314.3007 | CONT | [12 empty] | 0
_1032334540308.3166666667 | 10323345 |  | Parent | FALSE | LNGS NO.2 GEN TRANS 220KV CB AT ATS | 40308.3167 | 40318.7146 | CONT | [12 empty] | 0
_1032426940308.475 | 10324269 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 40308.475 | 40308.5701 | DAILY | 00011755 | FORCED | MBTS/MKPS/BOPS 220 kV Line De-Energised | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030632240309.2506944445 | 10306322 |  | Parent | TRUE | NO.1 500KV BUS AT MLTS | 40309.2507 | 40309.7667 | REPDAILY | 00003012 | SPIMAINT | O/Haul NO.1 500KV BUS AT MLTS | SPIPOWER |  |  | Bus | Alstom | 500 |  |  |  | 0
_1032316540309.2506944445 | 10323165 | 10306322 | Child | FALSE | A2 500/220KV TRANS BANK AT MLTS | 40309.2507 | 40309.7667 | REPDAILY | 00364782 | SPIMAINT | Rebate W/O A2 Trans during No1 500kV Bus outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_V7A058B240309.2909722222 | V7A058B2 |  | Parent | FALSE | HWTS NO.2 500KV LINE NO.2 BUS CB AT SMTS | 40309.291 | 40312.6048 | CONT | [12 empty] | 0
_1031204440309.2986111111 | 10312044 |  | Parent | FALSE | YPS NO.7 220KV LINE NO.3 BUS CB AT ROTS | 40309.2986 | 40312.6618 | CONT | [12 empty] | 0
_1030696440309.3763888889 | 10306964 | 10306968 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ATS | 40309.3764 | 40310.6153 | DAILY | 00350821 | SPIMAINT | O/Haul NO.2 220KV CAPACITOR BANK AT ATS | SPIPOWER |  |  | Capacitors | Western | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1030696840309.3763888889 | 10306968 |  | Parent | TRUE | NO.2 220KV CAPACITOR BANK CB AT ATS | 40309.3764 | 40310.6153 | DAILY | [12 empty] | 0
_1032366640309.4236111111 | 10323666 |  | Parent | TRUE | MBTS NO.2 220KV LINE CB AT EPSY | 40309.4236 | 40309.5257 | DAILY | [12 empty] | 0
_1032366740309.4236111111 | 10323667 | 10323666 | Child | FALSE | MBTS-EPS 2 220KV N | 40309.4236 | 40309.5257 | DAILY | 00055381 | SPIMAINT | Rebate W/O MBTS No2 Line for CB CT oil sampling | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1032432440310.0166666667 | 10324324 |  | Parent | FALSE | SYN/COND AT BLTS | 40310.0167 | 40310.0861 | DAILY | 00002547 | FAULT | Outage for Syn Cond Auto Trip | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X87058Q540310.2486111111 | X87058Q5 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 40310.2486 | 40310.7562 | DAILY | 00022690 | SPICAPX | Out W/O PT henry No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030632240310.2520833333 | 10306322 |  | Parent | TRUE | NO.1 500KV BUS AT MLTS | 40310.2521 | 40310.7514 | REPDAILY | 00003012 | SPIMAINT | O/Haul NO.1 500KV BUS AT MLTS | SPIPOWER |  |  | Bus | Alstom | 500 |  |  |  | 0
_1032316540310.2520833333 | 10323165 | 10306322 | Child | FALSE | A2 500/220KV TRANS BANK AT MLTS | 40310.2521 | 40310.7514 | REPDAILY | 00364782 | SPIMAINT | Rebate W/O A2 Trans during No1 500kV Bus outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_X87058Q340310.2722222222 | X87058Q3 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40310.2722 | 40310.7347 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS 2 Ln ins replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658W240310.28125 | X70658W2 |  | Parent | FALSE | EX - TTS NO.1 220KV LINE AT KTS | 40310.2812 | 40310.6687 | DAILY | 00015989 | SPICAPX | REMOVE TTS 1 LINE DROPPERS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031472240310.3034722222 | 10314722 |  | Parent | TRUE | GNTS NO.1 220KV LINE E/SW AT SHTS | 40310.3035 | 40310.7215 | DAILY | [12 empty] | 0
_1032366340310.3034722222 | 10323663 | 10314722 | Child | FALSE | GNTS-SHTS 1 220KV NW | 40310.3035 | 40310.7215 | DAILY | 00055388 | SPIMAINT | Rebate W/O GNTS No1 Line during E/SW & ROI maint | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032178540310.3138888889 | 10321785 |  | Parent | TRUE | HWTS NO.3 220KV LINE NO.3 BUS CB LINE SIDE ISOL AT HWPS | 40310.3139 | 40310.6188 | DAILY | [12 empty] | 0
_1032178640310.3138888889 | 10321786 | 10321785 | Child | FALSE | A3 515/230KV TRANS BANK AT HWTS | 40310.3139 | 40310.6188 | DAILY | 00337579 | SPIMAINT | REBATE LINE OUTAGE HWTS NO.3 @ HWPS | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032344840310.3638888889 | 10323448 |  | Parent | TRUE | NO.1A TRANS 22KV CB AT RCTS | 40310.3639 | 40310.7382 | DAILY | [12 empty] | 0
_1032353840310.3638888889 | 10323538 | 10323448 | Child | FALSE | NO.1A TRANS AT RCTS | 40310.3639 | 40310.7382 | DAILY | 00016722 | DBPROX | Perf calc W/O for 1A Trans during 22kV CB outage | DISTCO |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032436240310.7076388889 | 10324362 |  | Parent | FALSE | SHTS NO.1 220KV LINE NO.2 BUS CB AT GNTS | 40310.7076 | 40311.8187 | CONT | [12 empty] | 0
_X71158D740310.9305555556 | X71158D7 |  | Parent | FALSE | NO.1 220KV BUS AT HWPS | 40310.9306 | 40313.75 | CONT | 00009658 | SPICAPX | NO1 BUS OUTAGE @ HWPS JEMENA | SPIPOWER | X711 | X711 - (HWPS) REDEVELOP 220KV SWYD - STAGE 1 | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032436540311.1555555556 | 10324365 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 40311.1556 | 40322.0125 | CONT | 00356084 | GENCO | HWPS Unit 6 Isolated | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032421640311.2111111111 | 10324216 |  | Parent | FALSE | LYBPS NO.1 500KV LINE AT LYPS | 40311.2111 | 40322.7812 | CONT | 00023074 | GENCO | SCAP to Genco | GENCO |  |  | Circuits | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1030632240311.2361111111 | 10306322 |  | Parent | TRUE | NO.1 500KV BUS AT MLTS | 40311.2361 | 40311.7694 | REPDAILY | 00003012 | SPIMAINT | O/Haul NO.1 500KV BUS AT MLTS | SPIPOWER |  |  | Bus | Alstom | 500 |  |  |  | 0
_1032316540311.2361111111 | 10323165 | 10306322 | Child | FALSE | A2 500/220KV TRANS BANK AT MLTS | 40311.2361 | 40311.7694 | REPDAILY | 00364782 | SPIMAINT | Rebate W/O A2 Trans during No1 500kV Bus outage | SPIPOWER |  |  | Main Transformers | Alstom | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_X87058Q640311.2506944445 | X87058Q6 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 40311.2507 | 40311.7201 | DAILY | 00022691 | SPICAPX | Out W/O PT henry No2 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X80458A940311.2631944444 | X80458A9 |  | Parent | FALSE | B4 220/66KV TRANS AT WMTS | 40311.2632 | 40311.6007 | DAILY | 00350829 | SPICAPX | CONNECT FUTURE NO.4 SS TRANS 11KV CABLES | SPIPOWER | X804 | X804 - TERMINAL STATION AC SUPPLY UPGRADES | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X87058Q340311.2736111111 | X87058Q3 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40311.2736 | 40311.7125 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS 2 Ln ins replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031470640311.3013888889 | 10314706 |  | Parent | TRUE | DDTS 220KV LINE E/SW AT SHTS | 40311.3014 | 40311.6264 | DAILY | [12 empty] | 0
_1032366440311.3013888889 | 10323664 | 10314706 | Child | FALSE | DDTS-SHTS 220KV NW | 40311.3014 | 40311.6264 | DAILY | 00352425 | SPIMAINT | Rebate W/O DDTS Line during ROI & E/SW maint | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032396640311.3993055556 | 10323966 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT SHTS | 40311.3993 | 40311.5028 | DAILY | [12 empty] | 0
_1032430940311.4201388889 | 10324309 |  | Parent | FALSE | H1 TRANS NO.1 BUS 330KV CB AT DDTS | 40311.4201 | 40311.4896 | DAILY | [12 empty] | 0
_1032436740311.4458333333 | 10324367 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 40311.4458 | 40314.8854 | CONT | 00356080 | GENCO | Power station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032437540311.6229166667 | 10324375 |  | Parent | FALSE | JLGA NO.1 UNIT TRANS DISC CB AT JLGA | 40311.6229 | 40312.6597 | CONT | [12 empty] | 0
_1032439040312.0895833333 | 10324390 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40312.0896 | 40312.7139 | CONT | 00003011 | FAULT | 220KV SHUNT REACTOR tripping | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X87058Q740312.2513888889 | X87058Q7 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 40312.2514 | 40312.759 | DAILY | 00022690 | SPICAPX | Out W/O PT henry No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058Q340312.2729166667 | X87058Q3 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40312.2729 | 40312.684 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS 2 Ln ins replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1028815040312.3104166667 | 10288150 |  | Parent | FALSE | B1 GEN TRANS 500KV CB AT LYPS | 40312.3104 | 40312.5903 | DAILY | [12 empty] | 0
_1032366540312.3326388889 | 10323665 |  | Parent | FALSE | GTS NO.1 220KV LINE NO.2 BUS CB AT MLTS | 40312.3326 | 40312.5819 | DAILY | [12 empty] | 0
_X7E858A640312.3347222222 | X7E858A6 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE AT HWTS | 40312.3347 | 40314.6438 | CONT | 00016238 | SPIMAINT | CONSTRUCTION WORKS SMTS NO2 LINE @ HWTS JAMCO | 3RDPARTY | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032441040312.6069444444 | 10324410 |  | Parent | FALSE | RCTS LINE NO.1 BUS CB AT KGTS | 40312.6069 | 40312.6243 | DAILY | [12 empty] | 0
_X87058Q840313.2444444444 | X87058Q8 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 40313.2444 | 40313.6896 | DAILY | 00022691 | SPICAPX | Out W/O PT henry No2 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658X640313.2715277778 | X70658X6 |  | Parent | TRUE | NO.2 500KV BUS AT KTS | 40313.2715 | 40313.6292 | DAILY | 00001168 | SPICAPX | INSTALL CB TO ROI PRIMARY CONNECTIONS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 500 |  |  |  | 0
_X70658X840313.2715277778 | X70658X8 | X70658X6 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 40313.2715 | 40313.6292 | DAILY | 00026097 | SPICAPX | CAPTURE REBATE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X87058Q340313.2722222222 | X87058Q3 |  | Parent | FALSE | MBTS-DDTS 2 220KV NW | 40313.2722 | 40313.6854 | REPDAILY | 00060194 | SPICAPX | MBTS-DDTS 2 Ln ins replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658P140314.2520833333 | X70658P1 |  | Parent | FALSE | NO.3 66KV BUS AT KTS | 40314.2521 | 40314.6597 | DAILY | 00350488 | SPICAPX | COMMISSON FUTURE No.3-4 66KV BUS TIE CB | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031199240314.2708333333 | 10311992 |  | Parent | TRUE | NO.2 220KV BUS AT SVTS | 40314.2708 | 40314.6139 | DAILY | 00004857 | SPIMAINT | O/Haul NO.2 220KV BUS AT SVTS | SPIPOWER |  |  | Bus | Eastern | 220 |  |  |  | 0
_1032381040314.2708333333 | 10323810 | 10311992 | Child | FALSE | ROTS NO.2 220KV LINE AT SVTS | 40314.2708 | 40314.6139 | DAILY | 00351701 | SPIMAINT | Rebate Line Outage for Bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032381140314.2708333333 | 10323811 | 10311992 | Child | FALSE | HTS NO.2 220KV LINE AT SVTS | 40314.2708 | 40314.6139 | DAILY | 00351702 | SPIMAINT | Rebate Line Outage for Bus outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058Q440314.2715277778 | X87058Q4 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 40314.2715 | 40314.6403 | REPDAILY | 00060187 | SPICAPX | MBTS-DDTS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032447540314.6020833333 | 10324475 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB AT HWTS | 40314.6021 | 40316.6139 | CONT | [12 empty] | 0
_1032447440314.65 | 10324474 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.2 BUS CB AT HWTS | 40314.65 | 40315.422 | CONT | [12 empty] | 0
_X87058Q440315.2708333333 | X87058Q4 |  | Parent | FALSE | MBTS-DDTS 1 220KV NW | 40315.2708 | 40315.7188 | REPDAILY | 00060187 | SPICAPX | MBTS-DDTS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032393740315.275 | 10323937 |  | Parent | FALSE | A2 515/220KV TRANS BANK AT ROTS | 40315.275 | 40315.6465 | DAILY | 00362994 | SPIMAINT | O/Haul Trans Isol | SPIPOWER |  |  | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1032382240315.3902777778 | 10323822 |  | Parent | FALSE | NO.1 66KV BUS VT AT HTS | 40315.3903 | 40315.4549 | DAILY | [12 empty] | 0
_1032447940315.4208333333 | 10324479 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.2 BUS CB AT HWTS | 40315.4208 | 40315.5764 | DAILY | [12 empty] | 0
_1032382340315.4631944444 | 10323823 |  | Parent | FALSE | NO.2 66KV BUS VT AT HTS | 40315.4632 | 40315.5188 | DAILY | [12 empty] | 0
_1032356140315.4798611111 | 10323561 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 40315.4799 | 40315.4944 | DAILY | [12 empty] | 0
_X71158D640315.4986111111 | X71158D6 |  | Parent | FALSE | NO.1 GEN TRANS 220KV CB AT HWPS | 40315.4986 | 40347.75 | CONT | [12 empty] | 0
_1032451940316.0909722222 | 10324519 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40316.091 | 40316.7014 | CONT | 00003011 | FAULT | Reactor Trip | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z63658B140316.2569444444 | Z63658B1 |  | Parent | FALSE | M2 500/275KV TRANS AT HYTS | 40316.2569 | 40318.809 | CONT | 00002862 | VEN_AUG | M2 Trans disconnect 22kV Cable | SPIPOWER | Z636 | Z636 - (HYTS) 22KV SUPPLY | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032453140316.3493055556 | 10324531 |  | Parent | FALSE | MLTS-HYTS 2 500KV W | 40316.3493 | 40316.3514 | DAILY | 00022633 | FAULT | HYTS - MLTS 2L off load. | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032453240316.3493055556 | 10324532 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40316.3493 | 40316.3514 | DAILY | 00319999 | FAULT | HYTS-APD line off load as a result of trip at MLTS | SPIPOWER |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E858A840317.2736111111 | X7E858A8 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 40317.2736 | 40329.5486 | CONT | [12 empty] | 0
_V22858A140317.2895833333 | V22858A1 |  | Parent | FALSE | NO.3 220KV CAPACITOR BANK CB AT ROTS | 40317.2896 | 40319.5854 | CONT | [12 empty] | 0
_X70658X740317.2916666667 | X70658X7 |  | Parent | FALSE | SMTS 500KV LINE AT KTS | 40317.2917 | 40317.5778 | DAILY | 00015991 | SPICAPX | installation of the CT to ROI Primary connections | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030021840317.3131944445 | 10300218 |  | Parent | FALSE | A1 515/230KV UNIT 22KV/415V TRANS W/PH AT HWTS | 40317.3132 | 40320.5264 | CONT | 00009785 | SPIMAINT | 22KV Unit Transformer disconnected from tertiary | SPIPOWER |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | EXCLUDED | Off A1 Tertiary | 0
_1030591340317.3131944445 | 10305913 |  | Parent | TRUE | HWTS NO.1 220KV LINE AT HWPS | 40317.3132 | 40320.5264 | CONT | 00015794 | SPIMAINT | Overhaul 220 Kv LINE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032178240317.3131944445 | 10321782 | 10305913 | Child | FALSE | HWTS NO.1 220KV LINE CB LINE SIDE ISOL AT HWPS | 40317.3132 | 40320.5264 | DAILY | [12 empty] | 0
_1032280140317.3131944445 | 10322801 | 10305913 | Child | FALSE | HWTS NO.1 220KV LINE CVT R/PH AT HWPS | 40317.3132 | 40320.5264 | DAILY | [12 empty] | 0
_1032461940317.4333333333 | 10324619 |  | Parent | FALSE | SYN/COND AT BLTS | 40317.4333 | 40317.4868 | DAILY | 00002547 | FAULT | BLTS S/C Tripped Automatically | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032397540317.6076388889 | 10323975 |  | Parent | FALSE | DDTS 330KV LINE NO.1 BUS CB AT WOTS | 40317.6076 | 40317.6611 | DAILY | [12 empty] | 0
_1032397840317.6694444444 | 10323978 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT WOTS | 40317.6694 | 40317.7125 | DAILY | [12 empty] | 0
_1030507740318.2743055556 | 10305077 | 10306408 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT TTS | 40318.2743 | 40318.6451 | CONT | 00119178 | SPIMAINT | O/Haul NO.1 220KV CAPACITOR BANK AT TTS | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030640840318.2743055556 | 10306408 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB AT TTS | 40318.2743 | 40318.6451 | REPDAILY | [12 empty] | 0
_X89058C140318.29375 | X89058C1 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40318.2937 | 40318.7361 | DAILY | 00319998 | SPICAPX | Connect temp bypass line at T591 and T603 | SPIPOWER | X890 | X890 - (HYTS-APD) LINE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031467340318.3 | 10314673 |  | Parent | FALSE | HWTS NO.3 500KV LINE NO.2 BUS CB AT ROTS (RTF) | 40318.3 | 40318.6535 | DAILY | [12 empty] | 0
_1030775340318.3298611111 | 10307753 |  | Parent | FALSE | W3 GEN TRANS NO.2 BUS 220KV CB CT R/PH AT YPS | 40318.3299 | 40318.4264 | DAILY | [12 empty] | 0
_1032451840318.3423611111 | 10324518 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40318.3424 | 40318.5903 | DAILY | 00003011 | SPIMAINT | Magnetisation test of CTs after Shunt Reactor trip | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030774140318.4319444444 | 10307741 |  | Parent | FALSE | ROTS NO.6 220KV LINE NO.2 BUS CB CT R/PH AT YPS | 40318.4319 | 40318.4924 | DAILY | [12 empty] | 0
_1032468640318.7833333333 | 10324686 |  | Parent | FALSE | KTS 220KV LINE AT BLTS | 40318.7833 | 40318.834 | DAILY | 00024011 | FORCED | KTS-BLTS 220kV line de-energised | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032469040318.7958333333 | 10324690 |  | Parent | FALSE | NO.2 66KV BUS AT BLTS | 40318.7958 | 40318.8021 | DAILY | 00002650 | FORCED | No2 66kV Bus trip | SPIPOWER |  |  | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032469240318.7958333333 | 10324692 |  | Parent | FALSE | NO.2 66KV BUS AT BLTS | 40318.7958 | 40318.8021 | DAILY | 00002650 | FORCED | No2 66kV Bus trip | SPIPOWER |  |  | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_V8D258A740319.25625 | V8D258A7 |  | Parent | FALSE | TTS 220KV LINE AT ROTS | 40319.2562 | 40319.6479 | DAILY | 00023972 | SPIMAINT | Move B phase to Spare SF6 Duct and W Phase Back | SPIPOWER | V8D2 | V8D2 - (ROTS) REPLACE 220KV BUS DUCT SLIDING SUPPORT | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1030507740319.2888888889 | 10305077 | 10306408 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT TTS | 40319.2889 | 40319.6924 | CONT | 00119178 | SPIMAINT | O/Haul NO.1 220KV CAPACITOR BANK AT TTS | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030640840319.2888888889 | 10306408 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB AT TTS | 40319.2889 | 40319.6924 | REPDAILY | [12 empty] | 0
_1032465440319.3145833333 | 10324654 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.1 BUS CB AT LYPS | 40319.3146 | 40319.4667 | DAILY | [12 empty] | 0
_1032370640321.4215277778 | 10323706 |  | Parent | FALSE | LNGS NO.1 GEN TRANS 220KV CB AT ATS | 40321.4215 | 40328.6556 | CONT | [12 empty] | 0
_V8F158B140322.2930555556 | V8F158B1 |  | Parent | FALSE | B1 220/66KV TRANS AT MTS | 40322.2931 | 40322.3007 | REPDAILY | 00364562 | SPIMAINT | Check Oil Leaks | SPIPOWER | V8F1 | V8F1 - REPAIR OF OIL LEAKS IN TERMINAL STNS - STAGE 1 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032478340322.5347222222 | 10324783 |  | Parent | FALSE | EX - B3 220/66KV TRANS AT TTS | 40322.5347 | 40322.8347 | DAILY | 00001544 | FAULT | Transformer trip | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032478740322.6451388889 | 10324787 |  | Parent | FALSE | HWTS NO.1 LINE/SYTS NO.1 LINE 500KV CB AT SMTS | 40322.6451 | 40323.4569 | CONT | [12 empty] | 0
_1032478540322.6965277778 | 10324785 |  | Parent | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40322.6965 | 40322.8729 | CONT | 00119824 | FORCED | No 1 220kv Cap Bank | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030710340323.2923611111 | 10307103 |  | Parent | TRUE | NO.1 66KV CAPACITOR BANK AT TSTS | 40323.2924 | 40323.6097 | DAILY | 00351937 | SPIMAINT | OVERHAUL CAPACITOR BANK AND E/SW | SPIPOWER |  |  | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1030710940323.2923611111 | 10307109 | 10307103 | Child | FALSE | EX - NO.1 66KV CAPACITOR BANK CB AT TSTS | 40323.2924 | 40323.6097 | DAILY | [12 empty] | 0
_V7A058B340323.3138888889 | V7A058B3 |  | Parent | FALSE | F2 TRANS NON AUTO 500KV CB AT SMTS | 40323.3139 | 40326.3903 | CONT | [12 empty] | 0
_1031178640323.3159722222 | 10311786 |  | Parent | FALSE | A4 TRANS 500KV E/SW AT HWTS | 40323.316 | 40324.5437 | DAILY | [12 empty] | 0
_1030660540323.3430555556 | 10306605 |  | Parent | TRUE | NO.1 220KV BUS AT GNTS | 40323.3431 | 40323.7 | REPDAILY | 00000746 | SPIMAINT | O/Haul NO.1 220KV BUS AT GNTS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032405840323.3430555556 | 10324058 | 10306605 | Child | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 40323.3431 | 40323.7 | REPDAILY | 00329970 | SPIMAINT | Perf calc W/O No1 Trans grp during 220kV Bus maint | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032476640323.4666666667 | 10324766 |  | Parent | FALSE | CBTS NO.4 500KV LINE NO.3 BUS CB AT HWTS | 40323.4667 | 40323.5056 | DAILY | [12 empty] | 0
_1032397940323.5736111111 | 10323979 |  | Parent | FALSE | BATS NO.1 LINE/TGTS LINE 220KV CB AT MLTS | 40323.5736 | 40323.6847 | DAILY | [12 empty] | 0
_X71158D840324.25 | X71158D8 | X87058P3 | Child | FALSE | ROTS NO.2 220KV LINE AT HWPS | 40324.25 | 40324.6694 | DAILY | 00369011 | SPIMAINT | Adjust ROTS No 2 LINE No 1 BUS 220 KV CB LINE SIDE | 3RDPARTY | X711 | X711 - (HWPS) REDEVELOP 220KV SWYD - STAGE 1 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058P340324.25 | X87058P3 |  | Parent | TRUE | HWPS NO.2 220KV LINE AT ROTS | 40324.25 | 40324.6694 | DAILY | 00024004 | SPICAPX | Insulator Replacement HWPS - ROTS No2 Line | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030660540324.2979166667 | 10306605 |  | Parent | TRUE | NO.1 220KV BUS AT GNTS | 40324.2979 | 40324.7521 | REPDAILY | 00000746 | SPIMAINT | O/Haul NO.1 220KV BUS AT GNTS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032405840324.2979166667 | 10324058 | 10306605 | Child | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 40324.2979 | 40324.7521 | REPDAILY | 00329970 | SPIMAINT | Perf calc W/O No1 Trans grp during 220kV Bus maint | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032437440324.3208333333 | 10324374 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 40324.3208 | 40324.6826 | DAILY | 00022691 | HVCUST | Line outage for PTH | HVCUST |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032479940324.34375 | 10324799 |  | Parent | TRUE | MLTS NO.2 220KV LINE CB AT GTS | 40324.3438 | 40324.4715 | DAILY | [12 empty] | 0
_1032481440324.34375 | 10324814 | 10324799 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 40324.3438 | 40324.4715 | DAILY | 00366646 | SPIMAINT | Rebate W/O MLTS No2 Line during CB outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032424040324.3486111111 | 10324240 |  | Parent | TRUE | NO.1A TRANS 22KV CB AT RCTS | 40324.3486 | 40324.7194 | DAILY | [12 empty] | 0
_1032424140324.3486111111 | 10324241 | 10324240 | Child | FALSE | NO.1A TRANS AT RCTS | 40324.3486 | 40324.7194 | DAILY | 00016722 | DBPROX | Perf calc W/O 1A Trans during 22kV CB outage | DISTCO |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032488240324.5465277778 | 10324882 |  | Parent | FALSE | GNTS NO.3 220KV LINE NO.1 BUS CB AT DDTS | 40324.5465 | 40324.5972 | DAILY | [12 empty] | 0
_1030660540325.2930555556 | 10306605 |  | Parent | TRUE | NO.1 220KV BUS AT GNTS | 40325.2931 | 40325.7535 | REPDAILY | 00000746 | SPIMAINT | O/Haul NO.1 220KV BUS AT GNTS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032405840325.2930555556 | 10324058 | 10306605 | Child | FALSE | B1 220/66KV TRANS GROUP AT GNTS | 40325.2931 | 40325.7535 | REPDAILY | 00329970 | SPIMAINT | Perf calc W/O No1 Trans grp during 220kV Bus maint | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7G358B040325.2986111111 | X7G358B0 |  | Parent | FALSE | NO.6 66KV BUS AT HTS | 40325.2986 | 40325.584 | DAILY | 00004460 | SPICAPX | No 6 Bus & NB Fdr & CB plus M-MC Fdr at HTS | SPIPOWER | X7G3 | X7G3 - REPLACE SURGE ARRESTERS AT VARIOUS T/STNS | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031393140325.3048611111 | 10313931 |  | Parent | TRUE | NO.1 TRANS 220KV CB AT BATS | 40325.3049 | 40325.6667 | DAILY | [12 empty] | 0
_1032406440325.3048611111 | 10324064 | 10313931 | Child | FALSE | B1 220/66KV TRANS AT BATS | 40325.3049 | 40325.6667 | DAILY | 00006554 | SPIMAINT | Perf calc W/O No1 Trans during CB maint | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031393440326.3208333333 | 10313934 |  | Parent | TRUE | NO.2 TRANS 220KV CB AT BATS | 40326.3208 | 40326.6028 | DAILY | [12 empty] | 0
_1032406540326.3208333333 | 10324065 | 10313934 | Child | FALSE | B2 220/66KV TRANS AT BATS | 40326.3208 | 40326.6028 | DAILY | 00006555 | SPIMAINT | Perf calc W/O No2 Trans during CB maint | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032481540326.3256944444 | 10324815 |  | Parent | FALSE | ROTS NO.6 220KV LINE CVT R/PH AT YPS | 40326.3257 | 40326.6667 | DAILY | [12 empty] | 0
_1032405740326.3361111111 | 10324057 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT SVTS | 40326.3361 | 40326.5076 | DAILY | 00004824 | SPIMAINT | o/haul CB | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032493640326.4666666667 | 10324936 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK CB AT LY | 40326.4667 | 40326.4924 | DAILY | [12 empty] | 0
_X70658V440327.2423611111 | X70658V4 |  | Parent | FALSE | NO.3 66KV BUS AT KTS | 40327.2424 | 40327.6972 | DAILY | 00350488 | SPICAPX | RMVE/RPLC SA2 66KV CB & IT's FDR SIDE ISOL & SD's | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031517840327.3020833333 | 10315178 |  | Parent | FALSE | RTS NO.1 220KV LINE AT ROTS | 40327.3021 | 40328.6111 | CONT | 00023111 | SPIMAINT | O/Haul - 220kV Line CVT's | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032387740327.3048611111 | 10323877 |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 40327.3049 | 40328.6188 | CONT | 00002828 | SPIMAINT | Out W/O B1 Trans HV testing by Tech services | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658V540327.6972222222 | X70658V5 |  | Parent | FALSE | SA NO.2 66KV FDR CB AT KTS | 40327.6972 | 40351.3801 | DAILY | [12 empty] | 0
_1032497640327.8125 | 10324976 |  | Parent | TRUE | EX - SMTS NO.1 500KV LINE NO.2 BUS CB AT HWTS | 40327.8125 | 40327.8257 | DAILY | [12 empty] | 0
_1032516740327.8125 | 10325167 | 10324976 | Child | FALSE | EX - SMTS NO.1 500KV LINE AT HWTS | 40327.8125 | 40327.8257 | DAILY | 00016237 | FORCED | SMTS No1 500kV line off load | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058E140328.2506944445 | X87058E1 |  | Parent | TRUE | BATS-BETS 220KV | 40328.2507 | 40328.7569 | DAILY | 00328505 | SPICAPX | BETS Line ins replace inc #1 220kV Bus@bats & bets | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058E340328.2506944445 | X87058E3 | X87058E1 | Child | FALSE | B2 220/66KV TRANS AT BATS | 40328.2507 | 40328.7569 | DAILY | 00006555 | SPICAPX | Perf calc W/O #2 Trans during #1 220kV Bus outage | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X87058F240328.2506944445 | X87058F2 | X87058E1 | Child | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 40328.2507 | 40328.7569 | DAILY | 00016040 | SPICAPX | Perf Calc W/O No2 Tr grp during #1 220 bus outage | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032485840328.3777777778 | 10324858 |  | Parent | TRUE | NO.1A TRANS 22KV CB AT RCTS | 40328.3778 | 40328.7069 | DAILY | [12 empty] | 0
_1032485940328.3777777778 | 10324859 | 10324858 | Child | FALSE | NO.1A TRANS AT RCTS | 40328.3778 | 40328.7069 | DAILY | 00016722 | DBPROX | Perf calc W/O 1A Trans during 22kV CB outage | DISTCO |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031187840329.2916666667 | 10311878 |  | Parent | FALSE | 2-4 66KV BUS TIE CB AT TSTS | 40329.2917 | 40329.6354 | DAILY | [12 empty] | 0
_1032455540329.2916666667 | 10324555 |  | Parent | TRUE | BLTS 220KV LINE CB AT FBTS | 40329.2917 | 40329.6687 | DAILY | [12 empty] | 0
_1032489540329.2916666667 | 10324895 | 10324555 | Child | FALSE | BLTS 220KV LINE AT FBTS | 40329.2917 | 40329.6687 | DAILY | 00002660 | SPIMAINT | Rebate for Line outage | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_1030773940329.3138888889 | 10307739 |  | Parent | FALSE | ROTS NO.5 220KV LINE NO.1 BUS CB CT R/PH AT YPS | 40329.3139 | 40329.4257 | DAILY | [12 empty] | 0
_1032435740329.3333333333 | 10324357 |  | Parent | FALSE | B1 TRANS 66KV CB AT HTS | 40329.3333 | 40329.5278 | DAILY | [12 empty] | 0
_X7G358F140329.3652777778 | X7G358F1 |  | Parent | FALSE | EX - LY NO.1 66KV FDR SD R/PH AT MWTS | 40329.3653 | 40329.6458 | DAILY | [12 empty] | 0
_1032426040329.3972222222 | 10324260 |  | Parent | FALSE | H1 TRANS NO.1 BUS 330KV CB AT DDTS | 40329.3972 | 40329.5319 | DAILY | [12 empty] | 0
_1032426340329.5416666667 | 10324263 |  | Parent | FALSE | MSS NO.1 330KV LINE NO.2 BUS CB AT DDTS | 40329.5417 | 40329.6118 | DAILY | [12 empty] | 0
_X7E858B340329.5493055556 | X7E858B3 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.3 MAIN TRANS CB AT HWTS | 40329.5493 | 40329.6056 | DAILY | [12 empty] | 0
_1032505340330.0513888889 | 10325053 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40330.0514 | 40330.3903 | CONT | 00003011 | FAULT | Tripped upon closing | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032490040330.2743055556 | 10324900 |  | Parent | FALSE | NO.3 500KV BUS AT HWTS | 40330.2743 | 40330.6583 | DAILY | 00009800 | SPIMAINT | No3 500kV BUS TO FIX OIL ALARM CBTS 4L3B CB | SPIPOWER |  |  | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1031228940330.2930555556 | 10312289 |  | Parent | FALSE | L1 TRANS NO.1 BUS 22KV CB AT WMTS | 40330.2931 | 40330.6104 | DAILY | [12 empty] | 0
_1031407740330.2986111111 | 10314077 |  | Parent | FALSE | YPS NO.5 220KV LINE NO.1 BUS CB AT ROTS | 40330.2986 | 40330.6354 | DAILY | [12 empty] | 0
_1032425540330.3020833333 | 10324255 |  | Parent | FALSE | HYTS NO.1 LINE/SYTS NO.1 LINE 500KV CB AT MLTS | 40330.3021 | 40367.7146 | CONT | [12 empty] | 0
_1030677940330.3354166667 | 10306779 |  | Parent | FALSE | MSS NO.1 LINE/SMTS NO.1 LINE 330KV CB AT DDTS | 40330.3354 | 40331.6694 | CONT | 00328044 | SPIMAINT | OVERHAUL SIEMENS 330KV 3AQ2EI CB | SPIPOWER | [8 empty] | 0 | 10306779 |  | OVERHAUL SIEMENS 330KV 3AQ2EI CB | 00328044 | CB |  | DDTS | CB | SPIMAINT | CONT
_1032435840330.3395833333 | 10324358 |  | Parent | FALSE | B2 TRANS 66KV CB AT HTS | 40330.3396 | 40330.5806 | DAILY | [12 empty] | 0
_1031229140331.2930555556 | 10312291 |  | Parent | FALSE | L1 TRANS NO.2 BUS 22KV CB AT WMTS | 40331.2931 | 40331.6257 | DAILY | [12 empty] | 0
_1031406740331.29375 | 10314067 |  | Parent | FALSE | ERTS NO.1 220KV LINE NO.2 BUS CB AT ROTS | 40331.2937 | 40331.6153 | DAILY | [12 empty] | 0
_X7E858B140331.3152777778 | X7E858B1 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.4 MAIN TRANS CB AT HWTS | 40331.3153 | 40331.3333 | CONT | [12 empty] | 0
_1032435940331.3201388889 | 10324359 |  | Parent | FALSE | B3 TRANS 66KV CB AT HTS | 40331.3201 | 40331.5493 | DAILY | [12 empty] | 0
_VA0758A640331.3423611111 | VA0758A6 |  | Parent | TRUE | B1 TRANS 66KV CB CT R/PH AT RWTS | 40331.3424 | 40331.4563 | DAILY | [12 empty] | 0
_VA0758A840331.3423611111 | VA0758A8 | VA0758A6 | Child | FALSE | B1 220/66KV TRANS AT RWTS | 40331.3424 | 40331.4563 | DAILY | 00364702 | SPIMAINT | Rebate Tran outage | SPIPOWER | VA07 | VA07 - SAMPLING OF 18 SETS OF ABB IMB CTS | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1032511040331.3832175926 | 10325110 |  | Parent | FALSE | NO.8 GEN TRANS 220KV CB AT HWPS | 40331.3832 | 40338.7257 | CONT | [12 empty] | 0
_1032512440331.6013888889 | 10325124 |  | Parent | TRUE | NO.2 220KV BUS AT BTS | 40331.6014 | 40331.6861 | DAILY | 00000943 | FORCED | Trip Checks | SPIPOWER |  |  | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032527640331.6013888889 | 10325276 | 10325124 | Child | FALSE | BTS -RTS 220KV W (BTS to Joint Bay 7) (CABLE) | 40331.6014 | 40331.6861 | DAILY | 00310401 | FORCED | Trip Checks | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032512940331.7583333333 | 10325129 |  | Parent | TRUE | NO.2 220KV BUS AT JLTS | 40331.7583 | 40331.8243 | CONT | 00365902 | REM_TRIP | No2 220kV Bus Trip | SPIPOWER |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032579540331.7583333333 | 10325795 | 10325129 | Child | FALSE | HWPS NO.2 220KV LINE AT JLTS | 40331.7583 | 40331.8243 | CONT | 00015937 | REM_TRIP | No2 220kV Bus Trip | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030631040332.2743055556 | 10306310 | 10312293 | Child | FALSE | B1 TRANS 66KV CB AT WMTS | 40332.2743 | 40332.6597 | DAILY | [12 empty] | 0
_1031229340332.2743055556 | 10312293 |  | Parent | TRUE | B1 220/66KV TRANS AT WMTS | 40332.2743 | 40332.6597 | DAILY | 00003233 | SPIMAINT | OVERHAUL OF A TRANSFORMER | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031407340332.2951388889 | 10314073 |  | Parent | FALSE | HWPS NO.2 220KV LINE NO.1 BUS CB AT ROTS | 40332.2951 | 40332.6007 | DAILY | [12 empty] | 0
_1031372440332.3340277778 | 10313724 |  | Parent | FALSE | WOTS 330KV LINE/H3 TRANS CB AT DDTS | 40332.334 | 40332.7194 | DAILY | 00351959 | SPIMAINT | OVERHAUL 330KV GEC/ALSTOM FXT15 CB | SPIPOWER | [8 empty] | 0 | 10313724 |  | OVERHAUL 330KV GEC/ALSTOM FXT15 CB | 00351959 | CB |  | DDTS | CB | SPIMAINT | DAILY
_VA0758A540332.3361111111 | VA0758A5 |  | Parent | FALSE | 1-2 66KV BUS TIE CB CT R/PH AT MTS | 40332.3361 | 40332.4743 | DAILY | [12 empty] | 0
_1032514140332.4756944444 | 10325141 |  | Parent | TRUE | B2 TRANS 220KV CB AT TBTS | 40332.4757 | 40332.5 | DAILY | [12 empty] | 0
_1032514440332.4756944444 | 10325144 | 10325141 | Child | FALSE | B2 220/66KV TRANS AT TBTS | 40332.4757 | 40332.5 | DAILY | 00004902 | SPIMAINT | Rebate Trans | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658AH40333.2340277778 | X70658AH |  | Parent | FALSE | SA NO.2 66KV FDR CB AT KTS | 40333.234 | 40333.7604 | DAILY | [12 empty] | 0
_1030708040333.25 | 10307080 |  | Parent | FALSE | B4 220/66KV TRANS AT WMTS | 40333.25 | 40333.6375 | DAILY | 00350829 | SPIMAINT | OVERHAUL OF A TRANSFORMER | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031407140333.2951388889 | 10314071 |  | Parent | FALSE | HWPS NO.1 220KV LINE NO.1 BUS CB AT ROTS | 40333.2951 | 40333.6118 | DAILY | [12 empty] | 0
_1031372640333.3354166667 | 10313726 |  | Parent | FALSE | H1 TRANS NO.2 BUS 330KV CB AT DDTS | 40333.3354 | 40333.6431 | DAILY | 00351960 | SPIMAINT | OVERHAUL 330KV GEC/ALSTOM FXT15 CB | SPIPOWER | [8 empty] | 0 | 10313726 |  | OVERHAUL 330KV GEC/ALSTOM FXT15 CB | 00351960 | CB |  | DDTS | CB | SPIMAINT | DAILY
_1032515940333.3548611111 | 10325159 |  | Parent | FALSE | JLGA NO.2 UNIT TRANS DISC CB AT JLGA | 40333.3549 | 40333.6868 | CONT | [12 empty] | 0
_1032467540333.5243055556 | 10324675 |  | Parent | FALSE | MWTS NO.2 66KV FDR NO.1 BUS CB CT R/PH AT LY | 40333.5243 | 40333.6181 | DAILY | [12 empty] | 0
_1032367840334.2708333333 | 10323678 | X90758C3 | Child | FALSE | S032 SMTS-SYTS 1 500KV | 40334.2708 | 40334.6924 | DAILY | [12 empty] | 0
_X90758C340334.2708333333 | X90758C3 |  | Parent | TRUE | SYTS NO.1 500KV LINE AT SMTS | 40334.2708 | 40334.6924 | DAILY | 00012439 | SPICAPX | REPLACE CVT SYTS 1 LINE | SPIPOWER | X907 | X907 - TYREE CVT REPLACEMENT PROGRAM | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X81158C040334.2881944444 | X81158C0 |  | Parent | TRUE | 4-5 66KV BUS TIE CB AT RTS | 40334.2882 | 40334.7458 | DAILY | [12 empty] | 0
_X81158C340334.2881944444 | X81158C3 | X81158C0 | Child | FALSE | NO.4 66KV CAPACITOR BANK AT RTS | 40334.2882 | 40334.7458 | DAILY | 00055373 | SPICAPX | Rebate Cap Bank for Bus outage | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X81158C440334.2881944444 | X81158C4 | X81158C0 | Child | FALSE | B2 220/66KV TRANS AT RTS | 40334.2882 | 40334.7458 | DAILY | 00007331 | SPICAPX | Rebate trans for Bus outage | SPIPOWER | X811 | X811 - CT REPLACEMENT PROGRAM - STAGE 5 | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032512240334.7409722222 | 10325122 |  | Parent | FALSE | SMTS 500KV LINE AT KTS | 40334.741 | 40334.7576 | DAILY | 00015991 | SPICAPX | Commission SMTS Line 2 Bus CB | SPIPOWER |  |  | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X81158C240334.7465277778 | X81158C2 |  | Parent | FALSE | 4-5 66KV BUS TIE CB AT RTS | 40334.7465 | 40335.2882 | DAILY | [12 empty] | 0
_1032085640335.2743055556 | 10320856 | X90758C4 | Child | FALSE | S004 SMTS-SYTS 2 500KV | 40335.2743 | 40335.7132 | DAILY | [12 empty] | 0
_X90758C440335.2743055556 | X90758C4 |  | Parent | TRUE | SYTS NO.2 500KV LINE AT SMTS | 40335.2743 | 40335.7132 | DAILY | 00012440 | SPICAPX | REPLACE CVT SYTS 2 LINE | SPIPOWER | X907 | X907 - TYREE CVT REPLACEMENT PROGRAM | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X81158C140335.2888888889 | X81158C1 |  | Parent | FALSE | 4-5 66KV BUS TIE CB AT RTS | 40335.2889 | 40335.9688 | DAILY | [12 empty] | 0
_Z61058D040336.30625 | Z61058D0 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40336.3063 | 40336.6958 | REPDAILY | 00022630 | VEN_AUG | Out W/O MLTS-HYTS 1L Dismantle redundant tower | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058D140336.30625 | Z61058D1 | Z61058D0 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40336.3063 | 40336.6958 | REPDAILY | 00002863 | VEN_AUG | Rebate W/O M1 Trans during MLTS-HYTS 1L outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058D340336.30625 | Z61058D3 | Z61058D0 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40336.3063 | 40336.6958 | REPDAILY | 00003007 | VEN_AUG | Rebate W/O HYTS 1Line React during Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032505940336.30625 | 10325059 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40336.3063 | 40336.7 | REPDAILY | 00319998 | APDALCOA | APD Work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_V7A058B440336.3145833333 | V7A058B4 |  | Parent | FALSE | F2 TRANS NON AUTO 500KV CB AT SMTS | 40336.3146 | 40340.5736 | CONT | [12 empty] | 0
_Z61058D040337.3020833333 | Z61058D0 |  | Parent | TRUE | MLTS-HYTS 1 500KV W | 40337.3021 | 40337.6236 | REPDAILY | 00022630 | VEN_AUG | Out W/O MLTS-HYTS 1L Dismantle redundant tower | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z61058D140337.3020833333 | Z61058D1 | Z61058D0 | Child | FALSE | M1 500/275KV TRANS AT HYTS | 40337.3021 | 40337.6236 | REPDAILY | 00002863 | VEN_AUG | Rebate W/O M1 Trans during MLTS-HYTS 1L outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Main Transformers | Alstom | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z61058D340337.3020833333 | Z61058D3 | Z61058D0 | Child | FALSE | HYTS NO.1 500KV LINE SHUNT REACTOR AT MLTS | 40337.3021 | 40337.6236 | REPDAILY | 00003007 | VEN_AUG | Rebate W/O HYTS 1Line React during Line outage | SPIPOWER | Z610 | Z610 - (MOPS) MORTLAKE CONNECTION & SHARED SERVICES | Reactors | Alstom | 500 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032505940337.3020833333 | 10325059 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40337.3021 | 40337.7035 | REPDAILY | 00319998 | APDALCOA | APD Work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1030772740337.3104166667 | 10307727 | 10310440 | Child | FALSE | JLA NO.2 220KV LINE CB CT R/PH AT TBTS | 40337.3104 | 40337.6715 | DAILY | [12 empty] | 0
_1031044040337.3104166667 | 10310440 |  | Parent | TRUE | JLA NO.2 220KV LINE AT TBTS | 40337.3104 | 40337.6715 | DAILY | 00026919 | SPIMAINT | O/Haul JLA 2 Line at TBTS | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031193440337.3104166667 | 10311934 | 10310440 | Child | FALSE | JLA NO.2 220KV LINE CB LINE SIDE E/SW AT TBTS | 40337.3104 | 40337.6715 | DAILY | [12 empty] | 0
_1031194040337.3104166667 | 10311940 | 10310440 | Child | FALSE | JLA NO.2 220KV LINE E/SW AT TBTS | 40337.3104 | 40337.6715 | DAILY | [12 empty] | 0
_X7E958E440337.3416666667 | X7E958E4 |  | Parent | FALSE | NO.1 500KV BUS AT KTS | 40337.3417 | 40377.4417 | CONT | 00001167 | SPICAPX | REPLACE A2 TRANS 1 BUSS 500KV CB | SPIPOWER | X7E9 | X7E9 - (KTS) 500KV CT & CB | Bus | Western | 500 |  |  |  | 0
_1032524340337.3597222222 | 10325243 |  | Parent | FALSE | TTS NO.1 220KV LINE AT KTS | 40337.3597 | 40337.4014 | CONT | 00368497 | SPIMAINT | CB opening at KTS | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032448940337.3819444444 | 10324489 |  | Parent | FALSE | BETS LINE NO.1 BUS CB AT KGTS | 40337.3819 | 40337.5007 | DAILY | [12 empty] | 0
_1032448840337.4513888889 | 10324488 |  | Parent | FALSE | 66KV SHUNT REACTOR AT KGTS | 40337.4514 | 40337.5736 | DAILY | 00354076 | SPIMAINT | Out W/O 66kV Shunt react for CB CT oil samples | SPIPOWER |  |  | Reactors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032449040337.5479166667 | 10324490 |  | Parent | FALSE | NO.2 TRANS NO.2 BUS 220KV CB AT KGTS | 40337.5479 | 40337.6014 | DAILY | [12 empty] | 0
_1032517240338.2395833333 | 10325172 |  | Parent | FALSE | SESS NO.2 275KV LINE/M2 TRANS CB AT HYTS | 40338.2396 | 40338.2812 | DAILY | [12 empty] | 0
_1031405940338.2923611111 | 10314059 |  | Parent | FALSE | A2 TRANS NO.1 BUS 220KV CB AT ROTS | 40338.2924 | 40338.5965 | DAILY | [12 empty] | 0
_1030631240338.2951388889 | 10306312 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT WMTS | 40338.2951 | 40338.6319 | DAILY | [12 empty] | 0
_1031389540338.3263888889 | 10313895 |  | Parent | FALSE | B3 220/66KV TRANS AT ATS | 40338.3264 | 40339.7057 | CONT | 00354003 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030772540338.35625 | 10307725 |  | Parent | TRUE | JLA NO.1 220KV LINE CB CT R/PH AT TBTS | 40338.3562 | 40338.4437 | DAILY | [12 empty] | 0
_1032476540338.35625 | 10324765 | 10307725 | Child | FALSE | JLA NO.1 220KV LINE AT TBTS | 40338.3562 | 40338.4437 | DAILY | 00018301 | SPIMAINT | Rebate for Line outage | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032454240338.3583333333 | 10324542 |  | Parent | FALSE | NO.1A TRANS AT RCTS | 40338.3583 | 40339.6854 | CONT | 00016722 | SPIMAINT | No1 A Trans bleed turrets, bushings. Test gas rly | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032532140338.9472222222 | 10325321 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT GTS | 40338.9472 | 40341.8375 | CONT | 00350421 | FAULT | No1 66kv Cap Bank | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032465140339.0263888889 | 10324651 | X7E858B2 | Child | FALSE | EX - SMTS NO.2 500KV LINE AT HWTS | 40339.0264 | 40339.3 | DAILY | 00016238 | SPICAPX | REBATE LINE OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032465240339.0263888889 | 10324652 | X7E858B2 | Child | FALSE | A4 515/230KV TRANS BANK AT HWTS | 40339.0264 | 40339.3 | DAILY | 00337582 | SPICAPX | TX REBATE | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E858B240339.0263888889 | X7E858B2 |  | Parent | TRUE | EX - SMTS NO.2 500KV LINE NO.4 MAIN TRANS CB AT HWTS | 40339.0264 | 40339.3 | DAILY | [12 empty] | 0
_1031405740339.2902777778 | 10314057 |  | Parent | FALSE | A2 TRANS NO.2 BUS 220KV CB AT ROTS | 40339.2903 | 40339.6021 | DAILY | [12 empty] | 0
_1032532740339.3 | 10325327 |  | Parent | FALSE | A4 515/230KV TRANS BANK AT HWTS | 40339.3 | 40339.909 | DAILY | 00337582 | FORCED | No4 Main Trans isolator failure & False Gas Trip | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030642040339.3055555556 | 10306420 |  | Parent | FALSE | 1-4 66KV BUS TIE CB AT BLTS | 40339.3056 | 40339.6181 | DAILY | [12 empty] | 0
_1032537240340.1020833333 | 10325372 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 40340.1021 | 40343.9611 | CONT | 00356083 | GENCO | Isolated for GenCo | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658W340340.2611111111 | X70658W3 |  | Parent | FALSE | TTS NO.1 220KV LINE AT KTS | 40340.2611 | 40340.7174 | DAILY | 00368497 | SPICAPX | RE CONNECT TTS 1 LINE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032454140340.3243055556 | 10324541 |  | Parent | FALSE | BSS 220KV LINE NO.2 TIE BUS AT RCTS | 40340.3243 | 40340.4764 | DAILY | 00363274 | SPIMAINT | Out W/O BSS Line No2 Tie CT oil samples | SPIPOWER |  |  | Bus | Alstom | 220 |  |  |  | 0
_1030642240340.34375 | 10306422 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT BLTS | 40340.3438 | 40340.6257 | DAILY | [12 empty] | 0
_1032538040340.5430555556 | 10325380 |  | Parent | FALSE | NO.2 220KV BUS AT JLTS | 40340.5431 | 40340.5493 | DAILY | 00365902 | GENCO | Power station requirement | GENCO |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032538140340.6791666667 | 10325381 |  | Parent | FALSE | NO.2 220KV BUS AT JLTS | 40340.6792 | 40340.6826 | DAILY | 00365902 | GENCO | Power station requirement | GENCO |  |  | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032524140340.75 | 10325241 |  | Parent | FALSE | TTS NO.1 LINE/WMTS NO.1 LINE 220KV CB AT KTS | 40340.75 | 40341.2528 | CONT | [12 empty] | 0
_X70658W540341.2534722222 | X70658W5 |  | Parent | FALSE | WMTS NO.1 220KV LINE AT KTS | 40341.2535 | 40341.7903 | DAILY | 00368499 | SPICAPX | REMOVE WMTS 1 LINE DROPPERS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031693240341.2916666667 | 10316932 | X90758C1 | Child | FALSE | ROTS NO.3 500KV LINE NO.3 BUS CB AT HWTS | 40341.2917 | 40342.7639 | DAILY | [12 empty] | 0
_1032348140341.2916666667 | 10323481 | X90758C1 | Child | FALSE | ROTS NO.3 500KV LINE AT HWTS | 40341.2917 | 40342.7639 | CONT | 00016239 | SPICAPX | REBATE FOR LINE OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X90758C140341.2916666667 | X90758C1 |  | Parent | TRUE | EX - ROTS NO.3 500KV LINE CVT R/PH AT HWTS | 40341.2917 | 40342.7639 | CONT | [12 empty] | 0
_X87058R140341.2923611111 | X87058R1 |  | Parent | FALSE | HWPS NO.1 220KV LINE AT ROTS | 40341.2924 | 40341.8201 | DAILY | 00023990 | SPICAPX | Insulator Replacement HWPS - ROTS No1 Line | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058R440342.2916666667 | X87058R4 |  | Parent | FALSE | HWPS NO.2 220KV LINE AT ROTS | 40342.2917 | 40342.8083 | DAILY | 00024004 | SPICAPX | Insulator Replacement HWPS - ROTS No2 Line | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032505440343.3263888889 | 10325054 |  | Parent | FALSE | SCI 66KV FDR CB AT BLTS | 40343.3264 | 40343.7354 | DAILY | [12 empty] | 0
_1030640440344.25 | 10306404 |  | Parent | FALSE | SYN/COND AT FBTS | 40344.25 | 40347.625 | CONT | 00002697 | SPIMAINT | OVERHAUL OF A SYNCHRONOUS CONDENSER | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7E858C640344.2611111111 | X7E858C6 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.4 MAIN TRANS CB AT HWTS | 40344.2611 | 40344.2715 | DAILY | 00009764 | SPIMAINT | COMMISSIONING SMTS NO2 LINE/NO4 TX CB @ HWTS | SPIPOWER | X7E8 | [7 empty] | 0 | X7E858C6 |  | COMMISSIONING SMTS NO2 LINE/NO4 TX CB @ HWTS | 00009764 | CB | X7E8 | HWTS | CB | SPIMAINT | IN-SERV
_1032387940344.3020833333 | 10323879 |  | Parent | FALSE | B3 220/66KV TRANS AT SHTS | 40344.3021 | 40345.784 | CONT | 00000842 | SPIMAINT | Out W/O B3 Trans HV testing by Tech services | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030711840344.30625 | 10307118 |  | Parent | FALSE | ERTS NO.2 LINE/HWPS NO.1 LINE 220KV CB AT ROTS | 40344.3063 | 40344.6299 | DAILY | [12 empty] | 0
_X7E858B940344.3416666667 | X7E858B9 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB AT HWTS | 40344.3417 | 40355.5819 | CONT | [12 empty] | 0
_1032534440344.4270833333 | 10325344 |  | Parent | FALSE | CLN NO.2 66KV FDR CB AT CBTS | 40344.4271 | 40350.6479 | CONT | [12 empty] | 0
_1032546440345.0159722222 | 10325464 |  | Parent | FALSE | SYN/COND AT TSTS | 40345.016 | 40345.0646 | DAILY | 00007626 | FORCED | SYN COND | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031168140345.3215277778 | 10311681 |  | Parent | FALSE | 1-4 66KV BUS TIE CB AT MWTS | 40345.3215 | 40345.5847 | DAILY | [12 empty] | 0
_1031221240345.3361111111 | 10312212 |  | Parent | FALSE | H3 TRANS NO.1 BUS 330KV CB AT DDTS | 40345.3361 | 40346.6243 | CONT | [12 empty] | 0
_1032514540345.6694444444 | 10325145 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT RCTS | 40345.6694 | 40345.6701 | DAILY | [12 empty] | 0
_X70658V140346.23125 | X70658V1 |  | Parent | FALSE | NO.4 66KV BUS EXTENSION AT KTS | 40346.2312 | 40346.7243 | DAILY | 00001175 | SPICAPX | RMVE/RPLC SA1 66KV CB & IT's FDR SIDE ISOL & SD's | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 |  |  |  | 0
_1031204040346.3 | 10312040 |  | Parent | FALSE | RTS NO.4 220KV LINE NO.4 BUS CB AT ROTS | 40346.3 | 40347.6153 | CONT | [12 empty] | 0
_1032547540346.3138888889 | 10325475 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40346.3139 | 40346.6373 | DAILY | 00319999 | APDALCOA | APD No2 Line de-energised for APD isolation | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1032548640346.4270833333 | 10325486 |  | Parent | FALSE | BETS-KGTS 220KV NB | 40346.4271 | 40346.6215 | DAILY | 00026196 | FAULT | KGTS 220kV Line trip to lockout | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658V240346.7270833333 | X70658V2 |  | Parent | FALSE | SA NO.1 66KV FDR CB AT KTS | 40346.7271 | 40353.375 | DAILY | [12 empty] | 0
_1032550640346.7645833333 | 10325506 |  | Parent | FALSE | NO.4 66KV BUS EXTENSION AT KTS | 40346.7646 | 40357.2292 | CONT | 00001175 | SPICAPX | 4-4 Extn 66kV Bus isolator open | SPIPOWER |  |  | Bus | Western | 66 |  |  |  | 0
_1031173240347.34375 | 10311732 |  | Parent | FALSE | NO.3 22KV/415V S/S TRANS AT HWTS | 40347.3438 | 40347.5486 | DAILY | 00009792 | SPIMAINT | Overhaul S/S Trans at HWTS | SPIPOWER |  |  | Other Transformers | Eastern | 22 |  |  |  | 0
_X50858CO40348.2319444444 | X50858CO |  | Parent | TRUE | NO.1 220KV BUS AT GTS | 40348.2319 | 40348.566 | DAILY | 00002833 | SPICAPX | Instal new GW from 220kv Rack to pole in Bay B | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X50858CP40348.2319444444 | X50858CP | X50858CO | Child | FALSE | PT. HENRY NO.1 220KV LINE AT GTS | 40348.2319 | 40348.566 | DAILY | 00367277 | SPICAPX | Rebate W/O PTH No1 Ln during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858CQ40348.2319444444 | X50858CQ | X50858CO | Child | FALSE | KTS NO.1 220KV LINE AT GTS | 40348.2319 | 40348.566 | DAILY | 00367291 | SPICAPX | Rebate W/O KTSNo1 Ln during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858CR40348.2319444444 | X50858CR | X50858CO | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 40348.2319 | 40348.566 | DAILY | 00366646 | SPICAPX | Rebate W/O MLTS No2 Ln during No1 220kv Bus Outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858SC40348.2319444444 | X50858SC | X50858CO | Child | FALSE | B1 220/66KV TRANS AT GTS | 40348.2319 | 40348.566 | DAILY | 00002828 | SPICAPX | Perf calc W/O B1 Trans during No1 220kV Bus outage | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X90758C540348.2708333333 | X90758C5 |  | Parent | FALSE | ROTS NO.3 500KV LINE AT SMTS | 40348.2708 | 40348.6931 | DAILY | 00012438 | SPICAPX | REPLACE CVT ROTS 3 LINE | SPIPOWER | X907 | X907 - TYREE CVT REPLACEMENT PROGRAM | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X50858CT40349.2305555556 | X50858CT | X50858CU | Child | FALSE | B3 220/66KV TRANS AT GTS | 40349.2306 | 40349.7278 | DAILY | 00002829 | SPICAPX | Instal new GW, Pth 1 Ln 1st Twr - B3 Trans rack | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X50858CU40349.2305555556 | X50858CU |  | Parent | TRUE | PT. HENRY NO.1 220KV LINE AT GTS | 40349.2306 | 40349.7278 | DAILY | 00367277 | SPICAPX | Instal new GW, Pth 1 Line 1st Twr - B3 Trans rack | SPIPOWER | X508 | X508 - (GTS) STATION REDEVELOPMENT | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658AT40349.2611111111 | X70658AT |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40349.2611 | 40349.6757 | DAILY | 00001169 | SPICAPX | RMVE CONNS FROM BUS TO WMTS 1L 1B ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658AY40349.2611111111 | X70658AY | X70658AT | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40349.2611 | 40349.6757 | DAILY | 00119824 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1029414240349.2916666667 | 10294142 |  | Parent | FALSE | A1 500/220KV TRANS BANK AT CBTS | 40349.2917 | 40349.5653 | DAILY | 00359493 | SPIMAINT | O/HAUL Transformer and Div Sw (EM) | SPIPOWER |  |  | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_X7E858C140349.3145833333 | X7E858C1 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE AT HWTS | 40349.3146 | 40349.4597 | DAILY | 00016238 | SPIMAINT | CONNECT ROI SMTS NO2 500KV LINE @ HWTS JAMCO | SPIPOWER | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032517440349.46875 | 10325174 | X7E858C2 | Child | FALSE | LYPS NO.1 500KV LINE AT HWTS | 40349.4688 | 40349.5757 | DAILY | 00016234 | SPICAPX | REBATE NO2 BUS OUTAGE @ HWTS JAMCO | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032517540349.46875 | 10325175 | X7E858C2 | Child | FALSE | A2 515/230KV TRANS BANK AT HWTS | 40349.4688 | 40349.5757 | DAILY | 00337572 | SPICAPX | REBATE NO 2 BUS OUTAGE TX NO2 @ HWTS JAMCO | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X7E858C240349.46875 | X7E858C2 |  | Parent | TRUE | NO.2 500KV BUS AT HWTS | 40349.4688 | 40349.5757 | DAILY | 00009799 | SPIMAINT | CONNECT ROI BUS No2 (SMTS No2) @ HWTS JAMCO | 3RDPARTY | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_X87058R740350.25 | X87058R7 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 40350.25 | 40350.6375 | DAILY | 00022691 | SPICAPX | Out W/O PT henry No2 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032537540350.6479166667 | 10325375 |  | Parent | FALSE | CLN NO.2 66KV FDR CB AT CBTS | 40350.6479 | 40359.4674 | CONT | [12 empty] | 0
_X70658J640351.2520833333 | X70658J6 |  | Parent | FALSE | NO.3 220KV BUS AT KTS | 40351.2521 | 40351.7201 | REPDAILY | 00001171 | SPICAPX | REPLACE BUS INSULATORS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V7A058B540351.2881944444 | V7A058B5 |  | Parent | FALSE | F2 TRANS NO.1 BUS 500KV CB AT SMTS | 40351.2882 | 40354.4708 | CONT | [12 empty] | 0
_1031391340351.29375 | 10313913 |  | Parent | FALSE | B1 220/66KV TRANS AT CBTS | 40351.2937 | 40352.6896 | CONT | 00353076 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1030642440351.3013888889 | 10306424 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT BLTS | 40351.3014 | 40351.6743 | DAILY | [12 empty] | 0
_1030752140351.3347222222 | 10307521 |  | Parent | FALSE | HWPS NO.3 LINE/MWTS NO.2 LINE 220KV CB AT JLTS | 40351.3347 | 40351.5604 | DAILY | [12 empty] | 0
_1032555640351.5166666667 | 10325556 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 40351.5167 | 40351.5271 | DAILY | [12 empty] | 0
_1032560440352 | 10325604 |  | Parent | FALSE | CLN NO.2 66KV FDR CB FDR SIDE ISOL AT CBTS | 40352 | 40359.4667 | CONT | [12 empty] | 0
_X70658J640352.25 | X70658J6 |  | Parent | FALSE | NO.3 220KV BUS AT KTS | 40352.25 | 40352.6556 | REPDAILY | 00001171 | SPICAPX | REPLACE BUS INSULATORS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1031257940352.3111111111 | 10312579 |  | Parent | FALSE | SHTS NO.3 220KV LINE NO.2 BUS CB AT GNTS | 40352.3111 | 40353.7151 | CONT | [12 empty] | 0
_1030752540352.3333333333 | 10307525 |  | Parent | FALSE | HWPS NO.4 LINE/MWTS NO.1 LINE 220KV CB AT JLTS | 40352.3333 | 40352.559 | DAILY | [12 empty] | 0
_X70658V340353.2305555556 | X70658V3 |  | Parent | FALSE | NO.4 66KV BUS AT KTS | 40353.2306 | 40353.7951 | DAILY | 00001174 | SPICAPX | REPLACE SA1 FDR CB BUS ISOL & COMM SA1 FDR CB | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031391540353.2916666667 | 10313915 |  | Parent | FALSE | B2 220/66KV TRANS AT CBTS | 40353.2917 | 40354.6722 | CONT | 00353077 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1032506040353.3020833333 | 10325060 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40353.3021 | 40353.6687 | REPDAILY | 00319999 | APDALCOA | APD work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1031396640353.3291666667 | 10313966 |  | Parent | FALSE | MWTS NO.2 220KV LINE NO.1 BUS CB AT JLTS | 40353.3292 | 40353.5646 | DAILY | [12 empty] | 0
_1032506040354.3048611111 | 10325060 |  | Parent | FALSE | HYTS-APD 2 500KV W | 40354.3049 | 40354.5465 | REPDAILY | 00319999 | APDALCOA | APD work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1031416740354.3333333333 | 10314167 |  | Parent | FALSE | HWPS NO.4 220KV LINE NO.2 BUS CB AT JLTS | 40354.3333 | 40354.4722 | DAILY | [12 empty] | 0
_X7E858C740354.5416666667 | X7E858C7 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE AT HWTS | 40354.5417 | 40354.5819 | DAILY | 00016238 | SPIMAINT | COMMISSIONING NEW SMTSNO2/2BUS CB @HWTS JAMCO | SPIPOWER | X7E8 | [7 empty] | 0 | X7E858C7 | NEPH | COMMISSIONING NEW SMTSNO2/2BUS CB @HWTS JAMCO | 00016238 | CIRCUIT | X7E8 | HWTS | CIRCEND | SPIMAINT | DAILY
_1032568240354.8958333333 | 10325682 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 40354.8958 | 40356.3993 | CONT | 00356086 | GENCO | HWPS No8 Gen Isolated for Powerstation | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658Y940355.25 | X70658Y9 |  | Parent | FALSE | NO.1 220KV BUS AT KTS | 40355.25 | 40355.6764 | DAILY | 00001169 | SPICAPX | REMVE BIPOD CONNS FROM No.1 BUS & BLTS L 1B ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X78558D240355.2708333333 | X78558D2 |  | Parent | FALSE | SMTS NO.1 220KV LINE AT TTS | 40355.2708 | 40356.6153 | CONT | 00015732 | SPICAPX | DICONNECT,RELOCATE, RECONNECT SMTS LINE VT'S | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032388040355.2916666667 | 10323880 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 40355.2917 | 40356.6924 | CONT | 00002829 | SPIMAINT | Out W/O B3 Trans HV testing by Tech services | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032569740355.4263888889 | 10325697 | 10325687 | Child | FALSE | 220KV SHUNT REACTOR AT MLTS | 40355.4264 | 40355.4611 | DAILY | 00003011 | SPIMAINT | Shunt reactor CB (Gas Top Up) | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032568740355.4263888889 | 10325687 |  | Parent | TRUE | 220KV SHUNT REACTOR CB AT MLTS | 40355.4264 | 40355.4616 | DAILY | [12 empty] | 0
_X87058R940356.25 | X87058R9 |  | Parent | FALSE | YPS NO.6 220KV LINE AT ROTS | 40356.25 | 40356.5563 | DAILY | 00024009 | SPICAPX | YPS-ROTS No 6 220kv Line Insulator Replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E958B140356.2798611111 | X7E958B1 |  | Parent | TRUE | A4 TRANS NO.1 BUS 500KV CB TRANS SIDE ROI AT KTS | 40356.2799 | 40356.4785 | DAILY | [12 empty] | 0
_X7E958E940356.2798611111 | X7E958E9 | X7E958B1 | Child | FALSE | A4 500/220KV TRANS BANK AT KTS | 40356.2799 | 40356.4785 | DAILY | 00026098 | SPICAPX | OUTAGE REBATE COSTS | SPIPOWER | X7E9 | X7E9 - (KTS) 500KV CT & CB | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X70658Z140357.2291666667 | X70658Z1 |  | Parent | FALSE | SU NO.2 66KV FDR CB AT KTS | 40357.2292 | 40357.7542 | DAILY | [12 empty] | 0
_1031106540357.2791666667 | 10311065 | 10312442 | Child | FALSE | SYN/COND COOLING SYSTEM AT BLTS | 40357.2792 | 40361.6354 | CONT | [12 empty] | 0
_1031107340357.2791666667 | 10311073 | 10312442 | Child | FALSE | SYN/COND TRANS AT BLTS | 40357.2792 | 40361.6354 | CONT | 00017820 | SPIMAINT | OVERHAUL A TRANSFORMER | SPIPOWER |  |  | Connection Transformers | Western | 66 |  |  |  | 0
_1031244240357.2791666667 | 10312442 |  | Parent | TRUE | SYN/COND AT BLTS | 40357.2792 | 40361.6354 | CONT | 00002547 | SPIMAINT | OVERHAUL OF A SYNCHRONOUS CONDENSER | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031408340357.2944444444 | 10314083 |  | Parent | FALSE | A2 TRANS NO.4 BUS 220KV CB AT ROTS | 40357.2944 | 40357.5861 | DAILY | [12 empty] | 0
_1031452440357.3090277778 | 10314524 |  | Parent | FALSE | B3 TRANS 220KV CB AT SHTS | 40357.309 | 40357.6979 | DAILY | [12 empty] | 0
_1032554840357.3090277778 | 10325548 |  | Parent | FALSE | B3 220/66KV TRANS AT SHTS | 40357.309 | 40357.6979 | DAILY | 00000842 | SPIMAINT | Repair cracked gauge glass 220kv bushing | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031416940357.3305555556 | 10314169 |  | Parent | FALSE | HWPS NO.3 220KV LINE NO.2 BUS CB AT JLTS | 40357.3306 | 40357.5514 | DAILY | [12 empty] | 0
_X7E858B640357.33125 | X7E858B6 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE NO.2 BUS CB AT HWTS | 40357.3313 | 40368.2583 | CONT | [12 empty] | 0
_1031230540357.4645833333 | 10312305 |  | Parent | FALSE | NO.2 22KV/415V S/S TRANS AT TGTS | 40357.4646 | 40357.616 | DAILY | 00003129 | SPIMAINT | OVERHAUL OF A STATION SERVICE TRANS | SPIPOWER |  |  | Other Transformers | Alstom | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_X70658Z040357.7708333333 | X70658Z0 |  | Parent | FALSE | SU NO.2 66KV FDR CB AT KTS | 40357.7708 | 40363.3021 | CONT | [12 empty] | 0
_1032387840358.2888888889 | 10323878 |  | Parent | FALSE | B2 220/66KV TRANS AT SHTS | 40358.2889 | 40359.6833 | CONT | 00000841 | SPIMAINT | Out W/O B2 Trans HV testing by Tech services | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032515440358.2902777778 | 10325154 | V8C458A5 | Child | FALSE | B2 220/66KV TRANS AT CBTS | 40358.2903 | 40358.5576 | DAILY | 00353077 | SPIMAINT | Repair oil Pipe Oil Leak & Install hand rails | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1031417140358.3125 | 10314171 |  | Parent | FALSE | MLTS 220KV LINE NO.1 BUS CB AT TGTS | 40358.3125 | 40358.6431 | DAILY | [12 empty] | 0
_1031392940358.3256944444 | 10313929 |  | Parent | FALSE | GNTS NO.1 220KV LINE NO.2 BUS CB AT SHTS | 40358.3257 | 40358.6181 | DAILY | [12 empty] | 0
_1031457240358.3333333333 | 10314572 |  | Parent | FALSE | MWTS NO.1 220KV LINE NO.1 BUS CB AT JLTS | 40358.3333 | 40358.5542 | DAILY | [12 empty] | 0
_1030771140358.4041666667 | 10307711 |  | Parent | FALSE | JINDERA 330KV LINE NO.1 BUS CB CT R/PH AT WOTS | 40358.4042 | 40358.4729 | DAILY | [12 empty] | 0
_1031406140359.2951388889 | 10314061 |  | Parent | FALSE | TTS 220KV LINE NO.1 BUS CB AT ROTS | 40359.2951 | 40359.6299 | DAILY | [12 empty] | 0
_1031392740359.30625 | 10313927 |  | Parent | FALSE | DDTS 220KV LINE NO.2 BUS CB AT SHTS | 40359.3063 | 40359.5854 | DAILY | [12 empty] | 0
_1031417340359.3194444444 | 10314173 |  | Parent | FALSE | MLTS 220KV LINE NO.2 BUS CB AT TGTS | 40359.3194 | 40359.6201 | DAILY | [12 empty] | 0
_1032448440359.4701388889 | 10324484 |  | Parent | FALSE | CLN NO.2 66KV FDR CB AT CBTS | 40359.4701 | 40359.6435 | DAILY | [12 empty] | 0
_1031451640360.3104166667 | 10314516 |  | Parent | FALSE | BATS 220KV LINE NO.1 BUS CB AT TGTS | 40360.3104 | 40360.6424 | DAILY | [12 empty] | 0
_1031452640360.3118055556 | 10314526 |  | Parent | FALSE | FVTS/BETS 220KV LINE NO.1 BUS CB AT SHTS | 40360.3118 | 40360.6444 | DAILY | [12 empty] | 0
_1032466940360.3201388889 | 10324669 |  | Parent | FALSE | MWTS NO.3 66KV FDR NO.1 BUS CB CT R/PH AT LY | 40360.3201 | 40360.4694 | DAILY | [12 empty] | 0
_1031372240360.3277777778 | 10313722 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.2 BUS CB AT LYPS | 40360.3278 | 40360.5632 | DAILY | [12 empty] | 0
_1031392540361.3027777778 | 10313925 |  | Parent | FALSE | FVTS/BETS 220KV LINE NO.2 BUS CB AT SHTS | 40361.3028 | 40361.6174 | DAILY | [12 empty] | 0
_1031451840361.3194444444 | 10314518 |  | Parent | FALSE | BATS 220KV LINE NO.2 BUS CB AT TGTS | 40361.3194 | 40361.5278 | DAILY | [12 empty] | 0
_1032580440361.8034722222 | 10325804 |  | Parent | FALSE | NO.2 GEN TRANS 220KV CB AT HWPS | 40361.8035 | 40365.5035 | CONT | [12 empty] | 0
_X78558D340362.25 | X78558D3 |  | Parent | TRUE | NO.3 220KV BUS AT TTS | 40362.25 | 40362.7528 | DAILY | 00001551 | SPICAPX | O/H OOS CB "B" B/S ISOL & CONN TO NO.3 BUS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Bus | Western | 220 |  |  |  | 0
_X78558D440362.25 | X78558D4 | X78558D3 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT TTS | 40362.25 | 40362.7528 | DAILY | 00327615 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X78558D540362.25 | X78558D5 | X78558D3 | Child | FALSE | SMTS NO.1 220KV LINE AT TTS | 40362.25 | 40362.7528 | DAILY | 00015732 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558D640362.25 | X78558D6 | X78558D3 | Child | FALSE | BTS NO.3 220KV LINE AT TTS | 40362.25 | 40362.7528 | DAILY | 00015724 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X87058R540362.2541666667 | X87058R5 |  | Parent | FALSE | SVTS NO.1 220KV LINE AT HTS | 40362.2542 | 40362.7 | DAILY | 00351699 | SPICAPX | SVTS-HTS No 1 220kv Line Insulator Replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032580740362.6875 | 10325807 |  | Parent | FALSE | TSTS 220KV LINE NO.3 BUS CB LINE SIDE ISOL AT TTS | 40362.6875 | 40369.6347 | CONT | [12 empty] | 0
_1032581240363.18125 | 10325812 |  | Parent | TRUE | 220KV SHUNT REACTOR CB AT MLTS | 40363.1813 | 40363.2097 | CONT | [12 empty] | 0
_1032608040363.18125 | 10326080 | 10325812 | Child | FALSE | 220KV SHUNT REACTOR AT MLTS | 40363.1813 | 40363.2097 | DAILY | 00003011 | FAULT | Rebate child | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658AN40363.2361111111 | X70658AN | X70658Z2 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT KTS | 40363.2361 | 40363.8104 | DAILY | 00327947 | SPICAPX | outage rebate costs | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658BP40363.2361111111 | X70658BP | X70658Z2 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT KTS | 40363.2361 | 40363.8104 | DAILY | 00337022 | SPICAPX | outage rebate costs | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658Z240363.2361111111 | X70658Z2 |  | Parent | TRUE | NO.1 66KV BUS AT KTS | 40363.2361 | 40363.8104 | DAILY | 00001172 | SPICAPX | RPLCE SU 2 FDR CB BUS SIDE ISOL COMM SU 2 CB | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_V8D258A840363.2479166667 | V8D258A8 |  | Parent | FALSE | TTS 220KV LINE AT ROTS | 40363.2479 | 40363.6104 | DAILY | 00023972 | SPIMAINT | Move B phase from Spare SF6 Duct to normal spot | SPIPOWER | V8D2 | V8D2 - (ROTS) REPLACE 220KV BUS DUCT SLIDING SUPPORT | Circuits | Eastern | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X87058R640363.2527777778 | X87058R6 |  | Parent | FALSE | SVTS NO.2 220KV LINE AT HTS | 40363.2528 | 40363.6986 | DAILY | 00351698 | SPICAPX | SVTS-HTS No 2 220kv Line Insulator Replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E958A940363.2729166667 | X7E958A9 |  | Parent | FALSE | A2 TRANS NO.1 BUS 500KV CB BUS SIDE ROI AT KTS | 40363.2729 | 40363.4889 | DAILY | [12 empty] | 0
_X7E858B740363.3361111111 | X7E858B7 |  | Parent | FALSE | EX - SMTS NO.1 500KV LINE AT HWTS | 40363.3361 | 40363.4681 | DAILY | 00016237 | SPIMAINT | CONNECT TO ROI SMTS NO 1 LINE @ HWTS JAMCO | 3RDPARTY | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032516640363.48125 | 10325166 | X7E858B8 | Child | FALSE | A2 515/230KV TRANS BANK AT HWTS | 40363.4812 | 40363.6306 | DAILY | 00337572 | SPICAPX | REBATE BUS OUTAGE | SPIPOWER |  |  | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1032516840363.48125 | 10325168 | X7E858B8 | Child | FALSE | LYPS NO.1 500KV LINE AT HWTS | 40363.4812 | 40363.6306 | DAILY | 00016234 | SPICAPX | REBATE BUS OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E858B840363.48125 | X7E858B8 |  | Parent | TRUE | NO.2 500KV BUS AT HWTS | 40363.4812 | 40363.6306 | DAILY | 00009799 | SPIMAINT | CONNECT ROI BUS No 2 (SMTS NO1) @HWTS JAMCO | 3RDPARTY | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Bus | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1032575740363.6666666667 | 10325757 |  | Parent | FALSE | NO.4 66KV BUS EXTENSION AT KTS | 40363.6667 | 40379.2326 | CONT | 00001175 | SPIMAINT | Holding authority | SPIPOWER |  |  | Bus | Western | 66 |  |  |  | 0
_1030640040365.2833333333 | 10306400 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT FBTS | 40365.2833 | 40365.6382 | DAILY | [12 empty] | 0
_V71158B440365.3145833333 | V71158B4 |  | Parent | FALSE | HWTS NO.1 500KV LINE NO.1 BUS CB AT LYPS | 40365.3146 | 40382.6528 | CONT | [12 empty] | 0
_X78558F940365.4763888889 | X78558F9 |  | Parent | FALSE | NO.3 220KV BUS VT R/PH AT TTS | 40365.4764 | 40370.3056 | CONT | [12 empty] | 0
_1030616240366.2826388889 | 10306162 |  | Parent | FALSE | SYN/COND TRANS NO.1 BUS 66KV CB AT TSTS | 40366.2826 | 40366.2826 | DAILY | [12 empty] | 0
_1030616440366.2826388889 | 10306164 |  | Parent | FALSE | SYN/COND TRANS NO.2 BUS 66KV CB AT TSTS | 40366.2826 | 40366.2826 | DAILY | [12 empty] | 0
_1031064940366.2826388889 | 10310649 | 10311884 | Child | FALSE | NO.3 11/6.6KV AUX TRANS DELUGE SYSTEM AT TSTS | 40366.2826 | 40366.2826 | CONT | [12 empty] | 0
_1031188440366.2826388889 | 10311884 |  | Parent | TRUE | SYN/COND AT TSTS | 40366.2826 | 40366.2826 | CONT | 00007626 | SPIMAINT | 5 yearly O/Haul Syn Con at TSTS | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1030616240366.2833333333 | 10306162 |  | Parent | FALSE | SYN/COND TRANS NO.1 BUS 66KV CB AT TSTS | 40366.2833 | 40388.7125 | DAILY | [12 empty] | 0
_1030616440366.2833333333 | 10306164 |  | Parent | FALSE | SYN/COND TRANS NO.2 BUS 66KV CB AT TSTS | 40366.2833 | 40388.7125 | DAILY | [12 empty] | 0
_1031064940366.2833333333 | 10310649 | 10311884 | Child | FALSE | NO.3 11/6.6KV AUX TRANS DELUGE SYSTEM AT TSTS | 40366.2833 | 40388.7125 | CONT | [12 empty] | 0
_1031188440366.2833333333 | 10311884 |  | Parent | TRUE | SYN/COND AT TSTS | 40366.2833 | 40388.7125 | CONT | 00007626 | SPIMAINT | 5 yearly O/Haul Syn Con at TSTS | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032589840366.3055555556 | 10325898 |  | Parent | FALSE | NO.3 66KV CAPACITOR BANK AT WMTS | 40366.3056 | 40367.3819 | CONT | 00003191 | FAULT | Cap Bank tripped after closing | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032586240366.3319444444 | 10325862 |  | Parent | FALSE | KTS -WMTS 1 220KV WT | 40366.3319 | 40366.3375 | DAILY | 00022718 | FAULT | KTS-WMTS No1 220kV Line off load. | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X81158D240367.30625 | X81158D2 |  | Parent | FALSE | EX - 1-2 66KV BUS TIE CB CT R/PH AT MWTS | 40367.3063 | 40368.7882 | DAILY | [12 empty] | 0
_1032586840367.3826388889 | 10325868 |  | Parent | FALSE | NO.3 66KV CAPACITOR BANK AT WMTS | 40367.3826 | 40367.5958 | DAILY | 00003191 | SPIMAINT | REBALANCE CAP BANK RED PHASE | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032589940367.3875 | 10325899 |  | Parent | FALSE | A2 GEN TRANS NO.1 BUS 500KV CB AT LYPS | 40367.3875 | 40367.5034 | DAILY | [12 empty] | 0
_1032591940368.2326388889 | 10325919 |  | Parent | FALSE | HWTS-SMTS 1 500KV G | 40368.2326 | 40368.2604 | DAILY | 00020191 | SPICAPX | SMTS No1 500kV Line de-energised for commissioning | 3RDPARTY |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z72758A540368.3694444444 | Z72758A5 |  | Parent | FALSE | NO.1 66KV BUS AT GTS | 40368.3694 | 40368.4917 | DAILY | 00002835 | SPICAPX | No1 66kv Bus outage to check connection sleeves | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032593740369.0486111111 | 10325937 |  | Parent | FALSE | YWPS NO.2 220KV LINE AT YPS | 40369.0486 | 40370.8146 | CONT | 00016424 | GENCO | W2 Isolated for power station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658AP40369.2701388889 | X70658AP | X70658Z3 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40369.2701 | 40369.7542 | DAILY | 00119824 | SPICAPX | capture rebate costs | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X70658AQ40369.2701388889 | X70658AQ | X70658Z3 | Child | FALSE | WMTS NO.1 220KV LINE AT KTS | 40369.2701 | 40369.7542 | DAILY | 00368499 | SPICAPX | capture rebate costs | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658Z340369.2701388889 | X70658Z3 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40369.2701 | 40369.7542 | DAILY | 00001169 | SPICAPX | INSTL CONNS FROM BUS TO NEW WMTS 1 L B/S ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032590640369.2736111111 | 10325906 |  | Parent | FALSE | TSTS 220KV LINE AT TTS | 40369.2736 | 40369.6347 | DAILY | 00015736 | SPIMAINT | REPLCE GEARBOX ON No.3 BUS CB LINE SIDE ISOL | SPIPOWER |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032594040369.2784722222 | 10325940 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40369.2785 | 40369.3063 | CONT | 00003011 | FAULT | Tripping of shunt reactor | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032594740370.0895833333 | 10325947 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40370.0896 | 40370.1201 | CONT | 00003011 | FAULT | 220KV SHUNT REACTOR Tripped due to faulty Prot | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658AW40370.25 | X70658AW | X70658Z4 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 40370.25 | 40370.5563 | DAILY | 00026097 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X70658AX40370.25 | X70658AX | X70658Z4 | Child | FALSE | EX - BLTS 220KV LINE AT KTS | 40370.25 | 40370.5563 | DAILY | 00015980 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658Z440370.25 | X70658Z4 |  | Parent | TRUE | NO.2 220KV BUS AT KTS | 40370.25 | 40370.5563 | DAILY | 00001170 | SPICAPX | RMVE BIPODS & CONNS FROM BUS TO TTS 1L 2 B/S ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X78558D740370.2743055556 | X78558D7 |  | Parent | TRUE | NO.3 220KV BUS AT TTS | 40370.2743 | 40370.5174 | DAILY | 00001551 | SPICAPX | RMVE PRI CONNS NO.3 BUS VT ISOL SW TO NO.3 B VT | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Bus | Western | 220 |  |  |  | 0
_X78558D840370.2743055556 | X78558D8 | X78558D7 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT TTS | 40370.2743 | 40370.5174 | DAILY | 00327615 | SPICAPX | OUTAGE REBATE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X78558D940370.2743055556 | X78558D9 | X78558D7 | Child | FALSE | SMTS NO.1 220KV LINE AT TTS | 40370.2743 | 40370.5174 | DAILY | 00015732 | SPICAPX | OUTAGE REBATE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558E040370.2743055556 | X78558E0 | X78558D7 | Child | FALSE | BTS NO.3 220KV LINE AT TTS | 40370.2743 | 40370.5174 | DAILY | 00015724 | SPICAPX | OUTAGE REBATE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032594840370.5569444444 | 10325948 |  | Parent | FALSE | TTS NO.1 220KV LINE NO.2 BUS CB AT KTS | 40370.5569 | 40371.2306 | CONT | [12 empty] | 0
_X70658BN40371.2305555556 | X70658BN |  | Parent | FALSE | TTS NO.1 220KV LINE AT KTS | 40371.2306 | 40371.6361 | DAILY | 00368497 | SPICAPX | REMOVE TEMP CONNS & TTS 1L 2B CB L/S ISOL | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030642940371.2736111111 | 10306429 |  | Parent | TRUE | 4-5 220KV BUS TIE CB AT BLTS | 40371.2736 | 40375.6139 | CONT | [12 empty] | 0
_1030765740371.2736111111 | 10307657 | 10306429 | Child | FALSE | 4-5 220KV BUS TIE CB CT R/PH AT BLTS | 40371.2736 | 40375.6139 | CONT | [12 empty] | 0
_1030659740371.2895833333 | 10306597 |  | Parent | FALSE | B2 220/66KV TRANS AT SHTS | 40371.2896 | 40372.716 | CONT | 00000841 | SPIMAINT | O/H TRANSFORMER & S/S TRANS | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X89058C540371.2958333333 | X89058C5 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40371.2958 | 40371.716 | DAILY | 00319998 | SPICAPX | Commission No1 CCT between T591 and T603 | SPIPOWER | X890 | X890 - (HYTS-APD) LINE REPLACEMENT | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031240840371.3013888889 | 10312408 |  | Parent | FALSE | B3 TRANS NO.2 BUS 220KV CB AT GTS | 40371.3014 | 40372.5736 | CONT | [12 empty] | 0
_V83958B240371.3215277778 | V83958B2 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 40371.3215 | 40371.7715 | DAILY | 00004778 | SPIMAINT | No 2 Bus outage | SPIPOWER | V839 | V839 - URGENT SECONDARY MAINTENANCE WORKS 2008 | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V83958B340371.3215277778 | V83958B3 | V83958B2 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 40371.3215 | 40371.7715 | DAILY | 00112418 | SPIMAINT | Rebate Cap bank for Bus outage | SPIPOWER | V839 | V839 - URGENT SECONDARY MAINTENANCE WORKS 2008 | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1032594940371.3756944445 | 10325949 |  | Parent | FALSE | B2 220/66KV TRANS AT TTS | 40371.3757 | 40371.7417 | REPDAILY | 00362454 | SPICAPX | B2 TRANS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032596340371.3763888889 | 10325963 |  | Parent | TRUE | NO.4B 66KV CAPACITOR BANK CB AT SVTS | 40371.3764 | 40371.4215 | CONT | [12 empty] | 0
_1032605040371.3763888889 | 10326050 | 10325963 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT SVTS | 40371.3764 | 40371.4215 | CONT | 00329600 | FORCED | Foriegn object on Con's to SVTS 4B Cap Bank CB | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032599740371.7708333333 | 10325997 |  | Parent | FALSE | TTS 220KV LINE NO.2 BUS CB AT ROTS | 40371.7708 | 40372.7292 | CONT | [12 empty] | 0
_1032594940372.2486111111 | 10325949 |  | Parent | FALSE | B2 220/66KV TRANS AT TTS | 40372.2486 | 40372.7111 | REPDAILY | 00362454 | SPICAPX | B2 TRANS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032417440372.3125 | 10324174 | VA1258A1 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT KTS | 40372.3125 | 40375.7729 | CONT | 00337022 | SPIMAINT | REBATE FOR CAPBANK OUTAGE | SPIPOWER | VA12 | VA12 - REFURBISH FIVE ABB EDF SKS1-1 CBS | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_VA1258A140372.3125 | VA1258A1 |  | Parent | TRUE | EX - NO.1B 66KV CAPACITOR BANK CB AT KTS | 40372.3125 | 40375.7729 | CONT | [12 empty] | 0
_1032495540372.45625 | 10324955 |  | Parent | FALSE | NO.1 TRANS 66KV CB AT BLTS | 40372.4563 | 40372.575 | DAILY | [12 empty] | 0
_1032495640373.2736111111 | 10324956 |  | Parent | FALSE | NO.2 TRANS 66KV CB AT BLTS | 40373.2736 | 40373.4924 | DAILY | [12 empty] | 0
_1030638340373.3111111111 | 10306383 |  | Parent | FALSE | NO.4 66KV CAPACITOR BANK AT GTS | 40373.3111 | 40373.509 | DAILY | 00329879 | SPIMAINT | O/Haul NO.4 66KV CAPACITOR BANK AT GTS | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032605940374.0979166667 | 10326059 |  | Parent | FALSE | SYN/COND AT BLTS | 40374.0979 | 40374.1569 | CONT | 00002547 | FAULT | BLTS Synch Cond Tripped | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032606240374.1597222222 | 10326062 |  | Parent | FALSE | 220KV SHUNT REACTOR AT MLTS | 40374.1597 | 40374.1847 | CONT | 00003011 | FAULT | MLTS 220kV Shunt Reactor Tripped | SPIPOWER |  |  | Reactors | Alstom | 220 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032495840374.2770833333 | 10324958 |  | Parent | FALSE | NO.4 TRANS 66KV CB AT BLTS | 40374.2771 | 40374.4396 | DAILY | [12 empty] | 0
_1030660040374.2881944444 | 10306600 |  | Parent | FALSE | B3 220/66KV TRANS AT SHTS | 40374.2882 | 40374.675 | CONT | 00000842 | SPIMAINT | O/Haul NO.3 TRANS AT SHTS | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V83958B440375.2923611111 | V83958B4 |  | Parent | TRUE | NO.2 220KV BUS AT ROTS | 40375.2924 | 40375.6944 | DAILY | 00004778 | SPIMAINT | Bus outage No 2 220kv | SPIPOWER | V839 | V839 - URGENT SECONDARY MAINTENANCE WORKS 2008 | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V83958B540375.2923611111 | V83958B5 | V83958B4 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 40375.2924 | 40375.6944 | DAILY | 00112418 | SPIMAINT | Rebate Cap Bank for Bus outage | SPIPOWER | V839 | V839 - URGENT SECONDARY MAINTENANCE WORKS 2008 | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X78558F140376.2298611111 | X78558F1 |  | Parent | FALSE | RWTS 220KV LINE AT TTS | 40376.2299 | 40376.6951 | DAILY | 00015734 | SPICAPX | REMOVE OOC B2 TRANSFORMERUNITS 8 & 9 | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032577240377.2277777778 | 10325772 | X78558E7 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT TTS | 40377.2278 | 40377.6222 | DAILY | 00119178 | SPICAPX | OUTAGE REBATE COSTS NO.1 220KV CAP BANK | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X78558E740377.2277777778 | X78558E7 |  | Parent | TRUE | NO.1 220KV BUS AT TTS | 40377.2278 | 40377.6222 | DAILY | 00001549 | SPICAPX | RMVE OOC B2 TRANS UNITS 6&7 RPLCE INS #1 BUS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Bus | Western | 220 |  |  |  | 0
_X78558E840377.2277777778 | X78558E8 | X78558E7 | Child | FALSE | ROTS 220KV LINE AT TTS | 40377.2278 | 40377.6222 | DAILY | 00015733 | SPICAPX | OUTAGE REBATE COSTS ROTS LINE | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X78558F040377.2277777778 | X78558F0 | X78558E7 | Child | FALSE | SMTS NO.2 220KV LINE AT TTS | 40377.2278 | 40377.6222 | DAILY | 00015729 | SPICAPX | OUTAGE REBATE COSTS SMTS 2 LINE | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032604640378.3090277778 | 10326046 |  | Parent | FALSE | HYTS-APD 1 500KV W | 40378.309 | 40378.5 | DAILY | 00319998 | APDALCOA | APD Work | APDALCOA |  |  | Circuits | Alstom | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1032610540378.5081828704 | 10326105 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 40378.5082 | 40383.4354 | CONT | 00356079 | GENCO | U1 Isol & earthed for power station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658X940379.2326388889 | X70658X9 |  | Parent | FALSE | NO.4 66KV BUS EXTENSION AT KTS | 40379.2326 | 40379.7792 | DAILY | 00001175 | SPICAPX | UPGRADE SU1 FDR EQUIP, FDR AND BUS OUTAGE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 |  |  |  | 0
_X7E958B340379.2527777778 | X7E958B3 |  | Parent | FALSE | EX - SYTS LINE/A4 TRANS 500KV CB AT KTS | 40379.2528 | 40404.3806 | CONT | [12 empty] | 0
_1031390540379.3138888889 | 10313905 |  | Parent | FALSE | B2 220/66KV TRANS AT KTS | 40379.3139 | 40380.7167 | CONT | 00001148 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E858C840379.3138888889 | X7E858C8 |  | Parent | FALSE | EX - NO.3 MAIN TRANS NO.1 BUS 500KV CB AT HWTS | 40379.3139 | 40389.2056 | CONT | [12 empty] | 0
_X70658V740379.7263888889 | X70658V7 |  | Parent | FALSE | SU NO.1 66KV FDR CB AT KTS | 40379.7264 | 40390.2986 | CONT | [12 empty] | 0
_X7G358G040380.28125 | X7G358G0 |  | Parent | FALSE | B4 220/66KV TRANS AT FBTS | 40380.2812 | 40382.641 | CONT | 00002728 | SPIMAINT | Surge Arrestor Replacement | SPIPOWER | X7G3 | X7G3 - REPLACE SURGE ARRESTERS AT VARIOUS T/STNS | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032405540380.3125 | 10324055 |  | Parent | FALSE | HWTS NO.2 220KV LINE NO.1 BUS CB AT HWPS | 40380.3125 | 40381.5021 | CONT | [12 empty] | 0
_VA0758A740380.3319444444 | VA0758A7 |  | Parent | FALSE | TTS 220KV LINE NO.2 BUS CB CT R/PH AT TSTS | 40380.3319 | 40380.4958 | DAILY | [12 empty] | 0
_1032602340380.3472222222 | 10326023 |  | Parent | FALSE | MLRC 220KV LINE NO.2 BUS CB AT RCTS | 40380.3472 | 40380.4153 | DAILY | [12 empty] | 4
_1031314340380.3736111111 | 10313143 |  | Parent | FALSE | NO.4 22KV/415V S/S TRANS AT DDTS | 40380.3736 | 40380.5229 | DAILY | 00003974 | SPIMAINT | O/Haul NO.4 S/S TRANS AT DDTS | SPIPOWER |  |  | Other Transformers | Alstom | 22 |  |  |  | 0
_1032602440380.4166666667 | 10326024 |  | Parent | FALSE | BSS 220KV LINE NO.1 BUS CB AT RCTS | 40380.4167 | 40380.475 | DAILY | [12 empty] | 0
_1031428440380.4298611111 | 10314284 |  | Parent | FALSE | B2 TRANS 220KV CB AT HOTS | 40380.4299 | 40380.6813 | DAILY | [12 empty] | 0
_1032617940380.6770833333 | 10326179 |  | Parent | TRUE | NO.1 22KV CAPACITOR BANK CB AT BTS | 40380.6771 | 40380.7562 | DAILY | [12 empty] | 0
_1032623740380.6770833333 | 10326237 | 10326179 | Child | FALSE | NO.1 22KV CAPACITOR BANK AT BTS | 40380.6771 | 40380.7562 | DAILY | 00337002 | SPIMAINT | capture outage costs | SPIPOWER |  |  | Capacitors | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X78558F440381.2715277778 | X78558F4 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT TTS | 40381.2715 | 40383.6778 | CONT | [12 empty] | 0
_1031390340381.3020833333 | 10313903 |  | Parent | FALSE | B1 220/66KV TRANS AT KTS | 40381.3021 | 40382.6403 | CONT | 00001147 | SPIMAINT | Condition Monitoring Metro Trans 2day West Area | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030573540381.3125 | 10305735 |  | Parent | FALSE | STATIC VAR COMPENSATOR AT HOTS | 40381.3125 | 40381.7118 | DAILY | 00019243 | SPIMAINT | O/Haul SVC at HOTS | SPIPOWER |  |  | SVC & CSC | Alstom | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1032585440381.3173611111 | 10325854 |  | Parent | TRUE | NO.1 66KV BUS AT WOTS | 40381.3174 | 40381.7312 | DAILY | 00004043 | SPIMAINT | No1 66kv bus & No1 Trans 66 CB | SPIPOWER |  |  | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1032602640381.3173611111 | 10326026 | 10325854 | Child | FALSE | NO.1 330/66/22KV TRANS AT WOTS | 40381.3174 | 40381.7312 | DAILY | 00004036 | SPIMAINT | Perf calc W/O No1 Trans works during 66 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 330 | CONNECTION ASSET | TRANSFORMER |  | 0
_X70658AZ40381.8736111111 | X70658AZ | X70658Z5 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40381.8736 | 40382.2625 | DAILY | 00119824 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X70658BA40381.8736111111 | X70658BA | X70658Z5 | Child | FALSE | BLTS 220KV LINE AT KTS | 40381.8736 | 40382.2625 | DAILY | 00368495 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658Z540381.8736111111 | X70658Z5 |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40381.8736 | 40382.2625 | CONT | 00001169 | SPICAPX | INSTL BIPOD CONNS FRM 1BUS TO BLTS L 1BUS CB ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032629240381.9625 | 10326292 |  | Parent | FALSE | EX - NO.7 GEN TRANS 220KV CB BUS SIDE ISOL AT HWPS | 40381.9625 | 40382.9451 | CONT | [12 empty] | 0
_X70658BV40382.2388888889 | X70658BV |  | Parent | FALSE | EX - BLTS 220KV LINE NO.2 BUS CB AT KTS | 40382.2389 | 40383.2951 | DAILY | [12 empty] | 0
_1031324640382.2833333333 | 10313246 |  | Parent | FALSE | NO.4 66KV BUS AT SHTS | 40382.2833 | 40382.7701 | DAILY | 00350053 | SPIMAINT | Overhaul of the No4 66kv Bus and Isols | SPIPOWER |  |  | Bus | Alstom | 66 |  |  |  | 0
_1032530440382.2833333333 | 10325304 |  | Parent | FALSE | B4 220/66KV TRANS AT SHTS | 40382.2833 | 40382.7701 | DAILY | 00350590 | SPIMAINT | Perf Calc W/O B4 Trans during No4 66 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030616040382.2902777778 | 10306160 |  | Parent | TRUE | NO.4 66KV BUS AT TSTS | 40382.2903 | 40382.4319 | DAILY | 00007675 | SPIMAINT | O/Haul NO.4 66KV BUS AT TSTS | SPIPOWER |  |  | Bus | Eastern | 66 |  |  |  | 0
_1032554240382.2902777778 | 10325542 | 10306160 | Child | FALSE | B3 220/66KV TRANS AT TSTS | 40382.2903 | 40382.4319 | DAILY | 00007659 | SPIMAINT | Tran rebate for bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031165140382.3131944445 | 10311651 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT MWTS | 40382.3132 | 40382.5611 | DAILY | [12 empty] | 0
_1031428240382.3256944444 | 10314282 |  | Parent | FALSE | B3 TRANS 220KV CB AT HOTS | 40382.3257 | 40382.3618 | DAILY | [12 empty] | 0
_1032630540382.4 | 10326305 |  | Parent | FALSE | B1 220/66KV TRANS AT WBTS | 40382.4 | 40383.7049 | CONT | 00366199 | FAULT | WBTS B1 Trans Tripped | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_1032631040382.9104166667 | 10326310 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 40382.9104 | 40387.9313 | CONT | 00356086 | GENCO | HWPS No8 Gen Trans Isolated for SCAP | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032630240382.9944444444 | 10326302 |  | Parent | FALSE | W4 GEN TRANS 220KV CB AT YPS | 40382.9944 | 40385.8264 | CONT | [12 empty] | 0
_X78558E440383.2298611111 | X78558E4 |  | Parent | TRUE | NO.1 220KV BUS AT TTS | 40383.2299 | 40383.7368 | DAILY | 00001549 | SPICAPX | RMVE OOC B2 TRANS UNITS 4&5 (SEE LONG DESCRIPT | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Bus | Western | 220 |  |  |  | 0
_X78558E540383.2298611111 | X78558E5 | X78558E4 | Child | FALSE | ROTS 220KV LINE AT TTS | 40383.2299 | 40383.7368 | CONT | 00015733 | SPICAPX | OUTAGE REBATE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X78558E640383.2298611111 | X78558E6 | X78558E4 | Child | FALSE | SMTS NO.2 220KV LINE AT TTS | 40383.2299 | 40383.7368 | CONT | 00015729 | SPICAPX | OUTAGE REBATE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558E940383.2298611111 | X78558E9 | X78558E4 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT TTS | 40383.2299 | 40383.7368 | CONT | 00119178 | SPICAPX | OUTAGE REBATE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031247840383.2479166667 | 10312478 |  | Parent | TRUE | NO.1 66KV BUS AT TTS | 40383.2479 | 40383.7403 | REPDAILY | 00001552 | SPIMAINT | O/Haul NO.1 66KV BUS AT TTS | SPIPOWER |  |  | Bus | Western | 66 |  |  |  | 0
_1032634340383.2479166667 | 10326343 | 10312478 | Child | FALSE | B1 220/66KV TRANS AT TTS | 40383.2479 | 40383.7403 | REPDAILY | 00367585 | SPIMAINT | rebate child | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X87058S040383.25 | X87058S0 |  | Parent | FALSE | MLTS-BATS 1 220KV WY | 40383.25 | 40383.7292 | REPDAILY | 00022728 | SPICAPX | Out W/O MLTS-BATS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658BE40383.2513888889 | X70658BE | X70658Z7 | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 40383.2514 | 40383.6111 | DAILY | 00026097 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X70658Z740383.2513888889 | X70658Z7 |  | Parent | TRUE | NO.2 220KV BUS AT KTS | 40383.2514 | 40383.6111 | DAILY | 00001170 | SPICAPX | REMVE BIPD CONNS NO.2 B & BLTS L 2B B/S ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z72758A240383.2541666667 | Z72758A2 |  | Parent | TRUE | B1 220/66KV TRANS AT GTS | 40383.2542 | 40384.8319 | CONT | 00002828 | SPICAPX | Connect B1 Trans to Future B1 Trans 66kv CB | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z72758A340383.2541666667 | Z72758A3 | Z72758A2 | Child | FALSE | NO.1 66KV CAPACITOR BANK AT GTS | 40383.2542 | 40384.8319 | CONT | 00350421 | SPICAPX | Rebate WO for No1 Cap Bk during No1 66 Bus outage | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X87058S040384.25 | X87058S0 |  | Parent | FALSE | MLTS-BATS 1 220KV WY | 40384.25 | 40384.6271 | REPDAILY | 00022728 | SPICAPX | Out W/O MLTS-BATS No1 Line ins replace | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558F540384.2527777778 | X78558F5 |  | Parent | TRUE | NO.3 220KV BUS AT TTS | 40384.2528 | 40384.6694 | DAILY | 00001551 | SPICAPX | RMVE CONNS FRM NO.3 BUS TO N03 B VT ISOL | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Bus | Western | 220 |  |  |  | 0
_X78558F640384.2527777778 | X78558F6 | X78558F5 | Child | FALSE | NO.3 220KV CAPACITOR BANK AT TTS | 40384.2528 | 40384.6694 | DAILY | 00327615 | SPICAPX | OUTAGE REBATES FOR NO. 220KV CAP BANK | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X78558F740384.2527777778 | X78558F7 | X78558F5 | Child | FALSE | SMTS NO.1 220KV LINE AT TTS | 40384.2528 | 40384.6694 | DAILY | 00015732 | SPICAPX | CAPTURE OUTAGE COSTS SMTS NO.1 LINE | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558F840384.2527777778 | X78558F8 | X78558F5 | Child | FALSE | BTS NO.3 220KV LINE AT TTS | 40384.2528 | 40384.6694 | DAILY | 00015724 | SPICAPX | OUTAGE COSTS BTS NO.3 LINE | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031247840384.2555555556 | 10312478 |  | Parent | TRUE | NO.1 66KV BUS AT TTS | 40384.2556 | 40384.6465 | REPDAILY | 00001552 | SPIMAINT | O/Haul NO.1 66KV BUS AT TTS | SPIPOWER |  |  | Bus | Western | 66 |  |  |  | 0
_1032634340384.2555555556 | 10326343 | 10312478 | Child | FALSE | B1 220/66KV TRANS AT TTS | 40384.2556 | 40384.6465 | REPDAILY | 00367585 | SPIMAINT | rebate child | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E858D140384.3333333333 | X7E858D1 |  | Parent | FALSE | A3 TRANS NO.1 BUS 500KV CB BUS SIDE ROI AT HWTS | 40384.3333 | 40384.4854 | DAILY | [12 empty] | 0
_X7E858C940384.4944444444 | X7E858C9 |  | Parent | FALSE | A3 TRANS NO.1 BUS 500KV CB TRANS SIDE ROI AT HWTS | 40384.4944 | 40384.6438 | DAILY | [12 empty] | 0
_1032631940384.8798611111 | 10326319 |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 40384.8799 | 40386.575 | CONT | 00002828 | FORCED | GTS B1 Trans 22kV Earth Fault Alarm | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X78558F240385.2534722222 | X78558F2 |  | Parent | FALSE | EX - B3 220/66KV TRANS AT TTS | 40385.2535 | 40385.7674 | DAILY | 00001544 | SPICAPX | DECOMMISSION B3 TRANSFORMER | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030665340385.2833333333 | 10306653 |  | Parent | FALSE | DDTS NO.1 330KV LINE SERIES CAPACITOR BANK AT SMTS | 40385.2833 | 40389.6431 | CONT | 00327836 | SPIMAINT | OVERHAUL 330KV SERIES CAP BANK | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 4
_V83958B640385.2930555556 | V83958B6 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 40385.2931 | 40385.7389 | DAILY | 00004776 | SPIMAINT | Bus outage No 1 220kv | SPIPOWER | V839 | V839 - URGENT SECONDARY MAINTENANCE WORKS 2008 | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V83958B740385.2930555556 | V83958B7 | V83958B6 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 40385.2931 | 40385.7389 | DAILY | 00354024 | SPIMAINT | Rebate Cap Bank for Bus outage | SPIPOWER | V839 | V839 - URGENT SECONDARY MAINTENANCE WORKS 2008 | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1031453640385.30625 | 10314536 |  | Parent | FALSE | KGTS 220KV LINE NO.1 BUS CB AT BETS | 40385.3063 | 40385.6618 | DAILY | [12 empty] | 0
_1031159140385.3180555556 | 10311591 |  | Parent | FALSE | AUX TRANS 'C' NO.2 BUS 220KV CB AT YPS | 40385.3181 | 40389.5958 | CONT | [12 empty] | 0
_1032631440385.7340277778 | 10326314 |  | Parent | FALSE | B4 TRANS NO.2 BUS 220KV CB AT SHTS | 40385.734 | 40393.6194 | CONT | [12 empty] | 0
_X78558G040386.2409722222 | X78558G0 |  | Parent | FALSE | NO.3 66KV BUS AT TTS | 40386.241 | 40386.7417 | DAILY | 00001555 | SPICAPX | DISCON & REMVE OOS B3TRANS 66KV BUS SIDE ISOL | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Bus | Western | 66 |  |  |  | 0
_1031469040386.3076388889 | 10314690 |  | Parent | FALSE | 1-3 66KV BUS TIE CB AT RWTS | 40386.3076 | 40386.6278 | DAILY | [12 empty] | 0
_1032635240386.4652777778 | 10326352 |  | Parent | FALSE | NO.1 GEN TRANS 220KV LINE AT HWPS | 40386.4653 | 40386.806 | CONT | 00356079 | GENCO | Power Station Requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032636340386.5770833333 | 10326363 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 40386.5771 | 40386.6951 | DAILY | 00002829 | FORCED | At GTS B3 Trans Forced Outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_VA0758A440387.4576388889 | VA0758A4 |  | Parent | TRUE | B3 TRANS 66KV CB CT R/PH AT MTS | 40387.4576 | 40387.559 | DAILY | [12 empty] | 0
_VA0758A940387.4576388889 | VA0758A9 | VA0758A4 | Child | FALSE | B3 220/66KV TRANS AT MTS | 40387.4576 | 40387.559 | DAILY | 00363305 | SPIMAINT | Rebate Trans outage | SPIPOWER | VA07 | VA07 - SAMPLING OF 18 SETS OF ABB IMB CTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032637540387.5722222222 | 10326375 |  | Parent | FALSE | B1 220/66KV TRANS AT GTS | 40387.5722 | 40387.75 | DAILY | 00002828 | FORCED | Out WO B1 Trans outage for Tert earth flt investig | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_V8C458A340388.2916666667 | V8C458A3 |  | Parent | FALSE | B1 220/66KV TRANS AT CBTS | 40388.2917 | 40389.625 | CONT | 00353076 | SPIMAINT | Install hand rails | SPIPOWER | V8C4 | V8C4 - (CBTS) RECTIFY CONSTRUCTION DEFECTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER | Rolled into RAB 1/4/2008 | 0
_1032650540388.38125 | 10326505 |  | Parent | FALSE | DDTS-SMTS 1 330KV | 40388.3812 | 40388.4299 | DAILY | 00328506 | FAULT | Line rebate | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032643940388.5451388889 | 10326439 |  | Parent | FALSE | B4 220/66KV TRANS AT SHTS | 40388.5451 | 40388.5514 | DAILY | 00350590 | FORCED | B4 Trans de-energised for fault investigation | ALSTOM |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E858D740389.2361111111 | X7E858D7 |  | Parent | FALSE | A3 515/230KV TRANS BANK AT HWTS | 40389.2361 | 40389.2604 | DAILY | 00337579 | SPIMAINT | COMMISSIONING NO3 MAIN TX NO1 BUS CB @ HWTS | SPIPOWER | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_V83958B840389.2756944444 | V83958B8 |  | Parent | TRUE | NO.1 220KV BUS AT ROTS | 40389.2757 | 40389.8444 | DAILY | 00004776 | SPIMAINT | Bus outage No 1 220kv | SPIPOWER | V839 | V839 - URGENT SECONDARY MAINTENANCE WORKS 2008 | Bus | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_V83958B940389.2756944444 | V83958B9 | V83958B8 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT ROTS | 40389.2757 | 40389.8444 | DAILY | 00354024 | SPIMAINT | Rebate Cap Bank for Bus outage | SPIPOWER | V839 | V839 - URGENT SECONDARY MAINTENANCE WORKS 2008 | Capacitors | Eastern | 220 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1032644740389.4652777778 | 10326447 |  | Parent | FALSE | W1 GEN TRANS NO.2 BUS 220KV CB AT YPS | 40389.4653 | 40395.875 | CONT | [12 empty] | 0
_1032647840389.9416666667 | 10326478 |  | Parent | FALSE | NO.3 GEN TRANS LINE AT HWPS | 40389.9417 | 40396.3972 | CONT | 00356081 | GENCO | Power Station requirement | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658Y040390.2388888889 | X70658Y0 |  | Parent | FALSE | NO.2 66KV BUS AT KTS | 40390.2389 | 40390.7201 | DAILY | 00001173 | SPICAPX | UPGRADE FDR EQUIPMENT, FDR AND BUS OUTAGE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_X7E458Y640390.2743055556 | X7E458Y6 |  | Parent | FALSE | BATS-TGTS 220KV WW | 40390.2743 | 40390.8542 | DAILY | 00022665 | SPICAPX | Cut over BATS-TGTS L new prot signalling equip | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E958B540390.2916666667 | X7E958B5 |  | Parent | TRUE | SYTS LINE/A4 TRANS 500KV CB TRANS SIDE ROI AT KTS | 40390.2917 | 40390.6326 | CONT | [12 empty] | 0
_X7E958F540390.2916666667 | X7E958F5 | X7E958B5 | Child | FALSE | A4 500/220KV TRANS BANK AT KTS | 40390.2917 | 40390.6326 | CONT | 00026098 | SPICAPX | OUTAGE REBATE COSTS | SPIPOWER | X7E9 | X7E9 - (KTS) 500KV CT & CB | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1029770140390.2916666667 | 10297701 |  | Parent | FALSE | S191 HWTS-SMTS 1 500KV | 40390.2917 | 40390.6479 | DAILY | [12 empty] | 0
_1032636440390.2916666667 | 10326364 |  | Parent | FALSE | HWTS-SMTS 1 500KV G | 40390.2917 | 40390.6479 | DAILY | 00020191 | SPIMAINT | Broken Strands C phase No.3 spacer Sub Con 1 | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032632740390.6541666667 | 10326327 |  | Parent | FALSE | 1-4 66KV BUS TIE CB NO.1 BUS SIDE ISOL AT KTS | 40390.6542 | 40421.6542 | CONT | [12 empty] | 0
_1032648240390.7118055556 | 10326482 |  | Parent | FALSE | HWTS NO.4 500KV LINE AT CBTS | 40390.7118 | 40390.816 | CONT | 00359491 | FAULT | HWTS NO.4 500KV LINE AT CBTS Tripped | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E458Y740391.2722222222 | X7E458Y7 |  | Parent | FALSE | MLTS-TGTS 220KV W | 40391.2722 | 40391.8222 | DAILY | 00022740 | SPICAPX | Cut over MLTS-TGTS L new prot signalling equip | SPIPOWER | X7E4 | X7E4 - (MLTS,HYTS,APD,TGTS) INSTALL DIGITAL COMMS | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E958B440391.2930555556 | X7E958B4 |  | Parent | TRUE | SYTS LINE/A4 TRANS 500KV CB LINE SIDE ROI AT KTS | 40391.2931 | 40391.5806 | CONT | [12 empty] | 0
_X7E958F440391.2930555556 | X7E958F4 | X7E958B4 | Child | FALSE | SYTS 500KV LINE AT KTS | 40391.2931 | 40391.5806 | DAILY | 00015990 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X7E9 | X7E9 - (KTS) 500KV CT & CB | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032650140392.9930555556 | 10326501 |  | Parent | FALSE | NO.6 GEN TRANS LINE AT HWPS | 40392.9931 | 40396.3799 | CONT | 00356084 | GENCO | Unit 6 Isolated for power station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032571140393.2763888889 | 10325711 |  | Parent | FALSE | SYN/COND AT TSTS | 40393.2764 | 40394.3729 | CONT | 00007626 | SPIMAINT | Re-Gas Syn Con with Hydrogen book to 10311884 | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V7A058B640393.2881944444 | V7A058B6 |  | Parent | FALSE | F2 TRANS NO.1 BUS 500KV CB AT SMTS | 40393.2882 | 40396.525 | CONT | [12 empty] | 0
_1030712740393.2993055556 | 10307127 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT ATS | 40393.2993 | 40393.6507 | DAILY | [12 empty] | 0
_X7E858C340393.3145833333 | X7E858C3 |  | Parent | FALSE | EX - NO.4 MAIN TRANS NO.1 BUS 500KV CB AT HWTS | 40393.3146 | 40407.2365 | CONT | [12 empty] | 0
_1031171640393.3201388889 | 10311716 | 10311724 | Child | FALSE | NO.2 66KV CAPACITOR BANK CB AT LY | 40393.3201 | 40393.5868 | DAILY | [12 empty] | 0
_1031172440393.3201388889 | 10311724 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK AT LY | 40393.3201 | 40393.5868 | DAILY | 00009894 | SPIMAINT | O/Haul NO.2 66KV CAPACITOR BANK AT LY | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031170640393.3229166667 | 10311706 |  | Parent | FALSE | 2-4 500KV BUS TIE CB AT LYPS | 40393.3229 | 40393.5729 | DAILY | [12 empty] | 0
_1032658340393.5916666667 | 10326583 |  | Parent | FALSE | B4 220/66KV TRANS AT SHTS | 40393.5917 | 40393.5931 | CONT | 00350590 | FORCED | Fault finding | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032658440393.6194444444 | 10326584 |  | Parent | FALSE | B4 220/66KV TRANS AT SHTS | 40393.6194 | 40393.6201 | CONT | 00350590 | FORCED | Fault Finding | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032655940393.8145833333 | 10326559 |  | Parent | FALSE | SYN/COND AT FBTS | 40393.8146 | 40396.8006 | CONT | 00002697 | FORCED | Syn Con trip | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031694740394.3138888889 | 10316947 |  | Parent | FALSE | B2 GEN TRANS NO.3 BUS 500KV CB AT LYPS | 40394.3139 | 40394.4708 | DAILY | [12 empty] | 0
_1032655640394.35 | 10326556 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT MWTS | 40394.35 | 40394.7736 | DAILY | [12 empty] | 0
_1031172240394.4034722222 | 10311722 |  | Parent | FALSE | 380V/415V S/S TRANS AT JLTS | 40394.4035 | 40394.6861 | DAILY | 00009888 | SPIMAINT | Overhaul transformer | SPIPOWER |  |  | Other Transformers | Eastern | 6.6 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_1031694840394.5048611111 | 10316948 |  | Parent | FALSE | B2 GEN TRANS NO.4 BUS 500KV CB AT LYPS | 40394.5049 | 40394.6035 | DAILY | [12 empty] | 0
_1030587140395.3013888889 | 10305871 |  | Parent | FALSE | NO.4 22KV BUS AT BETS | 40395.3014 | 40395.7049 | DAILY | 00016373 | SPIMAINT | O/Haul NO.4 22KV BUS AT BETS | SPIPOWER |  |  | Bus | Alstom | 22 | NON AER ELEMENT | EXCLUDED |  | 0
_1031694140395.45 | 10316941 |  | Parent | FALSE | A3 GEN TRANS NO.2 BUS 500KV CB AT LYPS | 40395.45 | 40395.5674 | DAILY | [12 empty] | 0
_X70658BF40396.2513888889 | X70658BF |  | Parent | FALSE | TTS NO.1 220KV LINE AT KTS | 40396.2514 | 40396.6951 | DAILY | 00368497 | SPICAPX | INSTALL CONNS FROM TTS 1L TO TTS 1L 2B CB | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032663740396.6875 | 10326637 |  | Parent | FALSE | TTS NO.1 220KV LINE NO.2 BUS CB AT KTS | 40396.6875 | 40397.25 | CONT | [12 empty] | 0
_1032646040396.9430555556 | 10326460 |  | Parent | FALSE | NO.1 GEN TRANS 500KV LINE E/SW AT LYPS | 40396.9431 | 40403.3611 | CONT | [12 empty] | 0
_X70658AB40397.25 | X70658AB |  | Parent | TRUE | NO.2 220KV BUS AT KTS | 40397.25 | 40397.5979 | DAILY | 00001170 | SPICAPX | INSTL BIPODS FRM NO.2 220KV BUS TO TTS 1L 2B ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658BG40397.25 | X70658BG | X70658AB | Child | FALSE | A3 500/220KV TRANS BANK AT KTS | 40397.25 | 40397.5979 | DAILY | 00026097 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X78558G340397.26875 | X78558G3 |  | Parent | TRUE | NO.1 220KV BUS AT TTS | 40397.2688 | 40397.6069 | DAILY | 00001549 | SPICAPX | RELOCATE OOC B3 TRAN TO NTH OF NO.1 220KV BUS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Bus | Western | 220 |  |  |  | 0
_X78558G440397.26875 | X78558G4 | X78558G3 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT TTS | 40397.2688 | 40397.6069 | DAILY | 00119178 | SPICAPX | OUTAGE REBATE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_X78558G540397.26875 | X78558G5 | X78558G3 | Child | FALSE | ROTS 220KV LINE AT TTS | 40397.2688 | 40397.6069 | DAILY | 00015733 | SPICAPX | OUTAGE REBATE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 0
_X78558G640397.26875 | X78558G6 | X78558G3 | Child | FALSE | SMTS NO.2 220KV LINE AT TTS | 40397.2688 | 40397.6069 | DAILY | 00015729 | SPICAPX | OUTAGE REBATE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X81158D340397.2708333333 | X81158D3 |  | Parent | FALSE | EX - LY NO.1 66KV FDR CB CT R/PH AT MWTS | 40397.2708 | 40397.7556 | DAILY | [12 empty] | 0
_1032662340397.3076388889 | 10326623 |  | Parent | FALSE | YPS NO.1 220KV LINE NO.6 BUS CB AT HWPS | 40397.3076 | 40397.3444 | DAILY | [12 empty] | 0
_U80258A240397.3465277778 | U80258A2 |  | Parent | FALSE | ERTS NO.2 220KV LINE AT ROTS | 40397.3465 | 40397.5979 | DAILY | 00023971 | SPIMAINT | Ergonomic Trial of Earth Sw Handles | SPIPOWER | U802 | U802 - (C-RTF) REPAIR 500KV PRIMARY CONDUCTOR JOINTS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658BY40398.2513888889 | X70658BY |  | Parent | FALSE | EX - WMTS NO.2 220KV LINE AT KTS | 40398.2514 | 40398.6951 | DAILY | 00015982 | SPICAPX | REMOVE CONNS FROM WMTS 2 L TO WMTS 2L CB L/S ISOL | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032664040398.26875 | 10326640 |  | Parent | FALSE | W3 GEN TRANS 220KV LINE E/SW AT YPS | 40398.2688 | 40398.9973 | CONT | [12 empty] | 0
_X7E858C540398.3020833333 | X7E858C5 |  | Parent | FALSE | A4 TRANS NO.1 BUS 500KV CB BUS SIDE ROI AT HWTS | 40398.3021 | 40398.5139 | DAILY | [12 empty] | 0
_1031080640398.3458333333 | 10310806 |  | Parent | FALSE | C NORTH 22KV BUS PROT AT RTS | 40398.3458 | 40398.4944 | DAILY | [12 empty] | 0
_X7E858C440398.53125 | X7E858C4 |  | Parent | FALSE | A4 515/230KV TRANS BANK AT HWTS | 40398.5312 | 40398.7083 | DAILY | 00337582 | SPIMAINT | CONNECT ROI (NO4 MAIN TX) @ HWTS JAMCO | SPIPOWER | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X70658CA40398.6951388889 | X70658CA |  | Parent | FALSE | EX - TTS NO.2 LINE/WMTS NO.2 LINE 220KV CB AT KTS | 40398.6951 | 40405.6401 | DAILY | [12 empty] | 0
_1031260640399.25 | 10312606 |  | Parent | TRUE | DDTS NO.2 330KV LINE SERIES CAPACITOR BANK AT SMTS | 40399.25 | 40403.6111 | CONT | 00327837 | SPIMAINT | OVERHAUL 330KV SERIES CAP BANK | SPIPOWER |  |  | Capacitors | Western | 330 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 4
_1031262540399.25 | 10312625 | 10312606 | Child | FALSE | DDTS NO.2 330KV LINE SERIES CAPACITOR BANK BY-PASS CB AT SMTS | 40399.25 | 40403.6111 | CONT | [12 empty] | 0
_1031452840399.3354166667 | 10314528 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT BETS | 40399.3354 | 40399.6583 | DAILY | [12 empty] | 0
_1032610040399.3354166667 | 10326100 | 10314528 | Child | FALSE | NO.2A 66KV CAPACITOR BANK AT BETS | 40399.3354 | 40399.6583 | DAILY | 00350819 | SPIMAINT | Rebate W/O 2A Cap Bank during 2AB CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1032610140399.3354166667 | 10326101 | 10314528 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT BETS | 40399.3354 | 40399.6583 | DAILY | 00016274 | SPIMAINT | Rebate W/O 2B Cap Bank during 2AB CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032560340399.3402777778 | 10325603 |  | Parent | FALSE | B1A 220/66KV TRANS R/PH AT GNTS | 40399.3403 | 40403.5681 | CONT | 00000741 | SPIMAINT | Out W/O - Cond Mon Tests on B1 Trans Group | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030743740400.2986111111 | 10307437 |  | Parent | FALSE | B2 220/66KV TRANS AT TSTS | 40400.2986 | 40401.7049 | CONT | 00007658 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X81158A040400.3145833333 | X81158A0 |  | Parent | FALSE | AUX TRANS 'A' 220KV CB CT R/PH AT YPS | 40400.3146 | 40402.5639 | CONT | [12 empty] | 0
_1031529640400.3291666667 | 10315296 |  | Parent | TRUE | NO.3 66KV CAPACITOR BANK CB AT BETS | 40400.3292 | 40400.6278 | DAILY | [12 empty] | 0
_1032610240400.3291666667 | 10326102 | 10315296 | Child | FALSE | NO.3A 66KV CAPACITOR BANK AT BETS | 40400.3292 | 40400.6278 | DAILY | 00350820 | SPIMAINT | Rebate W/O 3A Cap Bank during 2AB CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1032610340400.3291666667 | 10326103 | 10315296 | Child | FALSE | NO.3B 66KV CAPACITOR BANK AT BETS | 40400.3292 | 40400.6278 | DAILY | 00016304 | SPIMAINT | Rebate W/O 3B Cap Bank during 2AB CB outage | SPIPOWER |  |  | Capacitors | Alstom | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032678840400.9583333333 | 10326788 |  | Parent | FALSE | NO.4 GEN TRANS LINE AT HWPS | 40400.9583 | 40405.7097 | CONT | 00356082 | GENCO | Genco work | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032528340401.2777777778 | 10325283 |  | Parent | FALSE | B1 220/66KV TRANS AT RWTS | 40401.2778 | 40401.6139 | DAILY | 00364702 | SPIMAINT | Overhaul Trans & Div. Switch | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1030590540401.2930555556 | 10305905 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 40401.2931 | 40401.6778 | REPDAILY | 00016040 | SPIMAINT | O/Haul 2A-2B TRANS GROUP AT BETS | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030590540402.2944444444 | 10305905 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 40402.2944 | 40402.6924 | REPDAILY | 00016040 | SPIMAINT | O/Haul 2A-2B TRANS GROUP AT BETS | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030618140402.2993055556 | 10306181 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT RWTS | 40402.2993 | 40402.6167 | DAILY | [12 empty] | 0
_1031461840402.3236111111 | 10314618 |  | Parent | TRUE | B2 TRANS 66KV CB AT TGTS | 40402.3236 | 40402.6667 | DAILY | [12 empty] | 0
_1032609940402.3236111111 | 10326099 | 10314618 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 40402.3236 | 40402.6667 | DAILY | 00003127 | SPIMAINT | Perf Calc w/O B2 Trans during 66kV CB O/H | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031693640402.3895833333 | 10316936 |  | Parent | FALSE | A1 GEN TRANS 500KV CB AT LYPS | 40402.3896 | 40402.5938 | DAILY | [12 empty] | 0
_1032686440402.4784722222 | 10326864 |  | Parent | FALSE | SYN/COND AT BLTS | 40402.4785 | 40402.5306 | DAILY | 00002547 | FAULT | BLTS Syn Con Tripped | SPIPOWER |  |  | Sync Condensers | Western | 14.5 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032689940402.5951388889 | 10326899 |  | Parent | FALSE | NO.3 66KV CAPACITOR BANK AT WMTS | 40402.5951 | 40402.7625 | CONT | 00003191 | FORCED | No3 Cap Bank trip | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032658940403.2152777778 | 10326589 |  | Parent | TRUE | NPSD-BLTS 220KV WY | 40403.2153 | 40403.8035 | REPDAILY | 00022739 | TPPROX | OUTAGE FOR WORKS ON WESTGATE BRIDGE | 3RDPARTY |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1032659040403.2152777778 | 10326590 | 10326589 | Child | FALSE | FBTS-BLTS 220KV WY | 40403.2153 | 40403.8035 | REPDAILY | 00022666 | TPPROX | OUTAGE FOR WORKS ON WESTGATE BRIDGE | 3RDPARTY |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 3
_1030590540403.2958333333 | 10305905 |  | Parent | FALSE | R2A/2B 220/66/22KV TRANS GROUP AT BETS | 40403.2958 | 40403.65 | REPDAILY | 00016040 | SPIMAINT | O/Haul 2A-2B TRANS GROUP AT BETS | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031507040403.3381944444 | 10315070 |  | Parent | FALSE | 1-2 66KV BUS TIE CB AT TGTS | 40403.3382 | 40403.5458 | DAILY | [12 empty] | 0
_1032658940404.2118055556 | 10326589 |  | Parent | TRUE | NPSD-BLTS 220KV WY | 40404.2118 | 40404.6201 | REPDAILY | 00022739 | TPPROX | OUTAGE FOR WORKS ON WESTGATE BRIDGE | 3RDPARTY |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1032659040404.2118055556 | 10326590 | 10326589 | Child | FALSE | FBTS-BLTS 220KV WY | 40404.2118 | 40404.6201 | REPDAILY | 00022666 | TPPROX | OUTAGE FOR WORKS ON WESTGATE BRIDGE | 3RDPARTY |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 3
_X87058R840404.2659722222 | X87058R8 |  | Parent | FALSE | HWPS NO.1 220KV LINE AT ROTS | 40404.266 | 40404.7556 | DAILY | 00023990 | SPICAPX | HWPS-ROTS No 1 220kv Line Insulator Replacement | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031839340404.28125 | 10318393 | 10318392 | Child | FALSE | LYPS NO.1 500KV LINE CB AT HWTS | 40404.2812 | 40404.2819 | DAILY | [12 empty] | 0
_1031692140404.2826388889 | 10316921 | 10318392 | Child | FALSE | LYPS NO.1 500KV LINE CB AT HWTS | 40404.2826 | 40404.2833 | DAILY | [12 empty] | 0
_1031839240404.2847222222 | 10318392 |  | Parent | TRUE | LYPS NO.1 500KV LINE CB AT HWTS | 40404.2847 | 40405.484 | CONT | [12 empty] | 0
_1032225540404.2847222222 | 10322255 | 10318392 | Child | FALSE | LYPS NO.1 500KV LINE CB LINE SIDE ROI AT HWTS | 40404.2847 | 40405.484 | CONT | [12 empty] | 0
_1032183040404.3131944445 | 10321830 |  | Parent | TRUE | S115 EPS -TTS 1 220KV | 40404.3132 | 40404.3465 | DAILY | [12 empty] | 0
_1032700640404.3131944445 | 10327006 | 10321830 | Child | FALSE | EPS -TTS 1 220KV N | 40404.3132 | 40404.3465 | DAILY | 00331826 | SPIMAINT | Rebate W/O for EPS-TTS Line outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E958D040404.3347222222 | X7E958D0 |  | Parent | FALSE | SYTS 500KV LINE X PROT AT KTS | 40404.3347 | 40404.4597 | DAILY | [12 empty] | 0
_1032658940405.2083333333 | 10326589 |  | Parent | TRUE | NPSD-BLTS 220KV WY | 40405.2083 | 40406.2771 | REPDAILY | 00022739 | TPPROX | OUTAGE FOR WORKS ON WESTGATE BRIDGE | 3RDPARTY |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1032659040405.2083333333 | 10326590 | 10326589 | Child | FALSE | FBTS-BLTS 220KV WY | 40405.2083 | 40406.2771 | REPDAILY | 00022666 | TPPROX | OUTAGE FOR WORKS ON WESTGATE BRIDGE | 3RDPARTY |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 3
_X87058P440405.2506944445 | X87058P4 |  | Parent | FALSE | HWPS NO.2 220KV LINE AT ROTS | 40405.2507 | 40405.7014 | DAILY | 00024004 | SPICAPX | Insulator Replacement HWPS - ROTS No2 Line | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031213840405.2527777778 | 10312138 |  | Parent | TRUE | NO.1 66KV BUS AT HTS | 40405.2528 | 40405.6764 | DAILY | 00004456 | SPIMAINT | O/Haul NO.1 66KV BUS AT HTS | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1031829640405.2527777778 | 10318296 | 10312138 | Child | FALSE | B1 220/66KV TRANS AT HTS | 40405.2528 | 40405.6764 | DAILY | 00004445 | SPIMAINT | Rebate Trans for Bus outage | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031829740405.2527777778 | 10318297 | 10312138 | Child | FALSE | NO.1A 66KV CAPACITOR BANK AT HTS | 40405.2528 | 40405.6764 | DAILY | 00004426 | SPIMAINT | Rebate Cap Bank for Bus outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031829840405.2527777778 | 10318298 | 10312138 | Child | FALSE | NO.1B 66KV CAPACITOR BANK AT HTS | 40405.2528 | 40405.6764 | DAILY | 00331019 | SPIMAINT | Rebate Cap Bank for Bus outage | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658BZ40405.2729166667 | X70658BZ |  | Parent | FALSE | EX - TTS NO.2 220KV LINE AT KTS | 40405.2729 | 40405.6062 | DAILY | 00015987 | SPICAPX | REMVE CONNS FROM TTS 2L TO TTS 2L 2B CBL/S ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032695240405.4506944444 | 10326952 |  | Parent | FALSE | NO.8 GEN TRANS LINE AT HWPS | 40405.4507 | 40408.7819 | CONT | 00356086 | GENCO | Unit 8 isolated (tube leak) | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032659140406.2777777778 | 10326591 |  | Parent | FALSE | NPSD-BLTS 220KV WY | 40406.2778 | 40413.2792 | CONT | 00022739 | TPPROX | OUTAGE FOR WORKS ON WESTGATE BRIDGE | 3RDPARTY |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_X7E858D940407.2083333333 | X7E858D9 |  | Parent | FALSE | A4 515/230KV TRANS BANK AT HWTS | 40407.2083 | 40407.2431 | DAILY | 00337582 | SPIMAINT | COMMISSION No4 TRAN No1 BUS CB @ HWTS JAMCO | SPIPOWER | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_V7A058B740407.2923611111 | V7A058B7 |  | Parent | FALSE | F2 TRANS NO.1 BUS 500KV CB AT SMTS | 40407.2924 | 40410.4285 | CONT | [12 empty] | 0
_1030773340407.2972222222 | 10307733 | 10311663 | Child | FALSE | AUX TRANS 'B' 220KV CB CT R/PH AT YPS | 40407.2972 | 40410.6174 | CONT | [12 empty] | 0
_1031159440407.2972222222 | 10311594 | 10311663 | Child | FALSE | AUX TRANS 'B' 220KV CB AT YPS | 40407.2972 | 40410.6174 | CONT | [12 empty] | 0
_1031160740407.2972222222 | 10311607 | 10311663 | Child | FALSE | AUX TRANS 'B' 220KV CB LINE SIDE E/SW AT YPS | 40407.2972 | 40410.6174 | CONT | [12 empty] | 0
_1031160940407.2972222222 | 10311609 | 10311663 | Child | FALSE | AUX TRANS 'B' 220KV E/SW AT YPS | 40407.2972 | 40410.6174 | CONT | [12 empty] | 0
_1031166340407.2972222222 | 10311663 |  | Parent | TRUE | AUX TRANS 'B' 220KV CB LINE SIDE ISOL AT YPS | 40407.2972 | 40410.6174 | CONT | [12 empty] | 0
_1030752340407.3430555556 | 10307523 |  | Parent | FALSE | 1-2 220KV BUS TIE CB AT MBTS | 40407.3431 | 40407.6771 | DAILY | [12 empty] | 0
_X7E258A140407.3506944444 | X7E258A1 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT TSTS | 40407.3507 | 40407.6257 | DAILY | 00351937 | SPICAPX | Reconnect CTs for new Bus Prot No 1 Cap Bank | SPIPOWER | X7E2 | X7E2 - (TSTS) REPLACE 66KV BUS PROTS | Capacitors | Eastern | 66 | UNREGULATED | EXCLUDED | P703 Never Rolling into RAB | 0
_1032698540407.5958333333 | 10326985 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 40407.5958 | 40407.6083 | DAILY | [12 empty] | 0
_1031501840408.29375 | 10315018 |  | Parent | TRUE | NO.1 220KV BUS AT TGTS | 40408.2937 | 40408.7 | DAILY | 00364788 | SPIMAINT | OVERHAUL 220KV BUS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032639140408.29375 | 10326391 | 10315018 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 40408.2937 | 40408.7 | DAILY | 00003127 | SPIMAINT | Perf cacl W/O B2 Trans during No1 220kV Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030640240408.3055555556 | 10306402 |  | Parent | FALSE | 2EXT-4 66KV BUS TIE CB AT FBTS | 40408.3056 | 40408.5049 | DAILY | [12 empty] | 0
_1032660140409.2805555556 | 10326601 |  | Parent | FALSE | SYN/COND AT TSTS | 40409.2806 | 40412.6618 | CONT | 00007626 | SPIMAINT | Re-Gas Syn Con with Hydrogen book to 10311884 | SPIPOWER |  |  | Sync Condensers | Eastern | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X7G358F640409.2861111111 | X7G358F6 |  | Parent | FALSE | B2 220/66KV TRANS AT SHTS | 40409.2861 | 40409.6924 | CONT | 00000841 | SPICAPX | Surge Arrestor Replacement | SPIPOWER | X7G3 | X7G3 - REPLACE SURGE ARRESTERS AT VARIOUS T/STNS | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030668240409.2895833333 | 10306682 |  | Parent | FALSE | B5 TRANS NO.1 BUS 66KV CB AT TTS | 40409.2896 | 40409.6875 | DAILY | [12 empty] | 0
_1031502040409.2916666667 | 10315020 |  | Parent | TRUE | NO.2 220KV BUS AT TGTS | 40409.2917 | 40409.6389 | DAILY | 00364789 | SPIMAINT | OVERHAUL 220KV BUS | SPIPOWER |  |  | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032644440409.2916666667 | 10326444 | 10315020 | Child | FALSE | B1 220/66KV TRANS AT TGTS | 40409.2917 | 40409.6389 | DAILY | 00363297 | SPIMAINT | Perf cacl W/O B1 Trans during No2 220kV Bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7G358F740410.28125 | X7G358F7 |  | Parent | FALSE | B3 220/66KV TRANS AT SHTS | 40410.2812 | 40410.7 | CONT | 00000842 | SPICAPX | Surge Arrestor Replacement | SPIPOWER | X7G3 | X7G3 - REPLACE SURGE ARRESTERS AT VARIOUS T/STNS | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031450940410.29375 | 10314509 |  | Parent | FALSE | B1 220/66KV TRANS AT TGTS | 40410.2937 | 40410.5306 | DAILY | 00363297 | SPIMAINT | 220kv Transformer | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030668040410.2951388889 | 10306680 |  | Parent | FALSE | B5 TRANS NO.3 BUS 66KV CB AT TTS | 40410.2951 | 40410.5785 | DAILY | [12 empty] | 0
_X78558H140411.2291666667 | X78558H1 |  | Parent | TRUE | NO.2 220KV BUS AT TTS | 40411.2292 | 40411.6986 | DAILY | 00001550 | SPICAPX | RMVE TKE OFF FRM NO.2 B TO OOS 1-2 B/T CB 2B ISOL | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Bus | Western | 220 |  |  |  | 0
_X78558H240411.2291666667 | X78558H2 | X78558H1 | Child | FALSE | BTS NO.1 220KV LINE AT TTS | 40411.2292 | 40411.6986 | DAILY | 00015723 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558H340411.2291666667 | X78558H3 | X78558H1 | Child | FALSE | EPS 220KV LINE AT TTS | 40411.2292 | 40411.6986 | DAILY | 00015730 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558H440411.2291666667 | X78558H4 | X78558H1 | Child | FALSE | KTS NO.2 220KV LINE AT TTS | 40411.2292 | 40411.6986 | CONT | 00015727 | SPICAPX | CAPTURE OUTAGE COSTS | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1030629940411.2958333333 | 10306299 |  | Parent | FALSE | L3 220/22KV TRANS AT WMTS | 40411.2958 | 40411.6431 | DAILY | 00003237 | SPIMAINT | OVERHAUL OF A TRANSFORMER | SPIPOWER |  |  | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X78558H640412.25 | X78558H6 |  | Parent | TRUE | NO.2 220KV BUS AT TTS | 40412.25 | 40412.7243 | DAILY | 00001550 | SPICAPX | INSTL BI PDS & TAKE OFF BUS BAY G RPLCE INS BAY B | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Bus | Western | 220 |  |  |  | 0
_X78558H740412.25 | X78558H7 | X78558H6 | Child | FALSE | BTS NO.1 220KV LINE AT TTS | 40412.25 | 40412.7243 | DAILY | 00015723 | SPICAPX | CAPTURE OUTAGE REBATE BTS 1 LINE | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558H840412.25 | X78558H8 | X78558H6 | Child | FALSE | KTS NO.2 220KV LINE AT TTS | 40412.25 | 40412.7243 | CONT | 00015727 | SPICAPX | CAPTURE OUTAGE REBATE KTS 2 LINE | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X78558H940412.25 | X78558H9 | X78558H6 | Child | FALSE | EPS 220KV LINE AT TTS | 40412.25 | 40412.7243 | CONT | 00015730 | SPICAPX | CAPTURE OUTAGE REBATE EPS LINE | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032644840412.3034722222 | 10326448 |  | Parent | FALSE | B3 220/66KV TRANS AT ERTS | 40412.3035 | 40412.541 | DAILY | 00004371 | SPIMAINT | REPAIR OIL LEAKS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032717140412.3625 | 10327171 |  | Parent | TRUE | LY NO.1 66KV FDR CB AT MWTS | 40412.3625 | 40412.4694 | DAILY | [12 empty] | 0
_1033817540412.3625 | 10338175 | 10327171 | Child | FALSE | LY NO.1 66KV FDR AT MWTS | 40412.3625 | 40412.4694 | DAILY | 00016140 | FORCED | Sub LY No1 66 kV Fdr CB OOS for SF6 Topup | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658DA40412.5951388889 | X70658DA |  | Parent | FALSE | BLTS 220KV LINE NO.2 BUS CB AT KTS | 40412.5951 | 40415.2986 | CONT | [12 empty] | 0
_X78558J140412.7395833333 | X78558J1 |  | Parent | FALSE | B3 TRANS 220KV CB AT TTS | 40412.7396 | 40455.6389 | CONT | [12 empty] | 0
_1032722740413.6993055556 | 10327227 |  | Parent | FALSE | NO.2 GEN TRANS 220KV LINE AT HWPS | 40413.6993 | 40418.9292 | CONT | 00356080 | GENCO | No 2 Gen Trans | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X78558G940414.2263888889 | X78558G9 |  | Parent | FALSE | NO.3 66KV BUS AT TTS | 40414.2264 | 40414.7361 | CONT | 00001555 | SPICAPX | BUILD FUT B3 TR 66KV CB B/S ISOL | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Bus | Western | 66 |  |  |  | 0
_1031504840414.2708333333 | 10315048 |  | Parent | TRUE | NO.1 220KV BUS E/SW AT SHTS | 40414.2708 | 40414.7264 | REPDAILY | [12 empty] | 0
_1032649640414.2708333333 | 10326496 | 10315048 | Child | FALSE | B2 220/66KV TRANS AT SHTS | 40414.2708 | 40414.7264 | REPDAILY | 00000841 | SPIMAINT | Perf calc W/O B2 Trans during No1 220 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1031390940414.2958333333 | 10313909 |  | Parent | FALSE | B3 220/66KV TRANS AT RTS | 40414.2958 | 40415.7271 | CONT | 00329288 | SPIMAINT | Condition Monitoring Metro Trans 2day East Area | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032632240414.3041666667 | 10326322 |  | Parent | FALSE | NO.3A TRANS 66KV CB AT BLTS | 40414.3042 | 40414.5146 | DAILY | [12 empty] | 0
_Z72758B440414.3694444444 | Z72758B4 |  | Parent | FALSE | B2 TRANS NO.1 BUS 220KV CB AT GTS | 40414.3694 | 40415.6486 | CONT | [12 empty] | 0
_X70658CZ40415.2513888889 | X70658CZ |  | Parent | FALSE | BLTS 220KV LINE AT KTS | 40415.2514 | 40415.7542 | DAILY | 00368495 | SPICAPX | INSTL CONNS BLTS HARP STRINGS TO STRUNG BUS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031504840415.2770833333 | 10315048 |  | Parent | TRUE | NO.1 220KV BUS E/SW AT SHTS | 40415.2771 | 40415.6465 | REPDAILY | [12 empty] | 0
_1032649640415.2770833333 | 10326496 | 10315048 | Child | FALSE | B2 220/66KV TRANS AT SHTS | 40415.2771 | 40415.6465 | REPDAILY | 00000841 | SPIMAINT | Perf calc W/O B2 Trans during No1 220 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032724740415.3215277778 | 10327247 |  | Parent | FALSE | NO.8 GEN 220/16.5KV TRANS AT HWPS | 40415.3215 | 40417.2701 | CONT | 00009649 | GENCO | Power Station requirement | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1030724040415.3472222222 | 10307240 |  | Parent | FALSE | EMERGENCY DIESEL GENERATOR PROT AT HWTS | 40415.3472 | 40415.6667 | DAILY | [12 empty] | 0
_X7E258A240415.4215277778 | X7E258A2 |  | Parent | TRUE | B2 TRANS 66KV CB AT TSTS | 40415.4215 | 40415.675 | DAILY | [12 empty] | 0
_X7E258A340415.4215277778 | X7E258A3 | X7E258A2 | Child | FALSE | B2 220/66KV TRANS AT TSTS | 40415.4215 | 40415.675 | DAILY | 00007658 | SPICAPX | Rebate Trans outage | SPIPOWER | X7E2 | X7E2 - (TSTS) REPLACE 66KV BUS PROTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032725640415.5534722222 | 10327256 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT WMTS | 40415.5535 | 40415.5715 | DAILY | [12 empty] | 0
_1033784940415.5534722222 | 10337849 | 10327256 | Child | FALSE | NO.2 66KV CAPACITOR BANK AT WMTS | 40415.5535 | 40415.5715 | DAILY | 00074391 | SPIMAINT | CAPTURE OUTAGE COSTS | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1033759440415.6493055556 | 10337594 |  | Parent | FALSE | B2 TRANS NO.1 BUS 220KV CB AT GTS | 40415.6493 | 40468.7257 | CONT | [12 empty] | 0
_1033760640415.9548611111 | 10337606 |  | Parent | FALSE | BOPS-MKPS 220KV LINE AT MBTS | 40415.9549 | 40416.7535 | CONT | 00011755 | FAULT | MBTS-BOPS/MKPS 220kV Line Tripped | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 1
_1033760940416.0736111111 | 10337609 |  | Parent | FALSE | DPS 220KV LINE AT MBTS | 40416.0736 | 40416.1194 | CONT | 00011754 | FAULT | MBTS-DPS 220kV Line Tripped, Reclosed & Tripped | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 1
_1033761340416.1541666667 | 10337613 |  | Parent | FALSE | DPS 220KV LINE AT MBTS | 40416.1542 | 40417.5736 | CONT | 00011754 | FAULT | MBTS-DPS 220kV Line Tripped, Reclosed & Tripped | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 1
_X7E258A240416.2888888889 | X7E258A2 |  | Parent | TRUE | B2 TRANS 66KV CB AT TSTS | 40416.2889 | 40416.5979 | DAILY | [12 empty] | 0
_X7E258A340416.2888888889 | X7E258A3 | X7E258A2 | Child | FALSE | B2 220/66KV TRANS AT TSTS | 40416.2889 | 40416.5979 | DAILY | 00007658 | SPICAPX | Rebate Trans outage | SPIPOWER | X7E2 | X7E2 - (TSTS) REPLACE 66KV BUS PROTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030620340416.2930555556 | 10306203 |  | Parent | FALSE | A NTH - B NTH 22KV BUS TIE CB AT RTS | 40416.2931 | 40416.5757 | DAILY | [12 empty] | 0
_1030630540416.3201388889 | 10306305 |  | Parent | FALSE | JA NO.3 66KV FDR NO.1 BUS CB AT WMTS | 40416.3201 | 40416.5813 | DAILY | [12 empty] | 0
_X70659DH40417.25 | X70659DH |  | Parent | FALSE | NO.4 66KV BUS EXTENSION AT KTS | 40417.25 | 40417.6062 | DAILY | 00001175 | SPICAPX | NO.1 BUS-4 BUS EXTEN 66KV CB COMMISION TESTS | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 66 |  |  |  | 0
_Z72758B640417.2944444444 | Z72758B6 |  | Parent | FALSE | B2 220/66KV TRANS AT GTS | 40417.2944 | 40417.7083 | DAILY | 00369910 | SPICAPX | Install Future B2 Trans GW Brackets at Rack Struct | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X70658CC40418.2506944445 | X70658CC |  | Parent | FALSE | A4 500/220KV TRANS BANK AT KTS | 40418.2507 | 40418.6424 | DAILY | 00026098 | SPICAPX | DISCONN A4 220KV DRP TO A4 TR3B 220KV CB T/S ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_Z72758A640418.2791666667 | Z72758A6 |  | Parent | TRUE | NO.2 220KV BUS AT GTS | 40418.2792 | 40418.5639 | CONT | 00002834 | SPICAPX | No2 220kV Bus to erect Fut B2 Tr 2 Bus CB ROI | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Bus | Alstom | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_Z72758A740418.2791666667 | Z72758A7 | Z72758A6 | Child | FALSE | B4 220/66KV TRANS AT GTS | 40418.2792 | 40418.5639 | CONT | 00002830 | SPICAPX | Rebate W/O B4 Trans during No2 220kv Bus outage | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z72758A840418.2791666667 | Z72758A8 | Z72758A6 | Child | FALSE | PT. HENRY NO.2 220KV LINE AT GTS | 40418.2792 | 40418.5639 | CONT | 00367278 | SPICAPX | Rebate W/O PTH 2 Ln during No2 220kv Bus outage | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z72758A940418.2791666667 | Z72758A9 | Z72758A6 | Child | FALSE | MLTS NO.1 220KV LINE AT GTS | 40418.2792 | 40418.5639 | CONT | 00367287 | SPICAPX | Rebate W/O MLTS 1 Ln during No2 220kv Bus outage | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z72758B040418.2791666667 | Z72758B0 | Z72758A6 | Child | FALSE | KTS NO.2 220KV LINE AT GTS | 40418.2792 | 40418.5639 | CONT | 00367295 | SPICAPX | Rebate W/O KTS 2 Ln during No2 220kv Bus outage | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032719540418.64375 | 10327195 |  | Parent | FALSE | EX - A4 TRANS/B2 TRANS 220KV CB AT KTS | 40418.6438 | 40463.1875 | CONT | [12 empty] | 0
_X78558H540419.0486111111 | X78558H5 |  | Parent | FALSE | B1 220/66KV TRANS AT TTS | 40419.0486 | 40419.2625 | DAILY | 00367585 | SPICAPX | RMVE GRND WIRE SPANS (SEE LONG DESCRIPTION) | SPIPOWER | X785 | X785 - (TTS) STATION REBUILD | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1033760140419.2375 | 10337601 | X70658CB | Child | FALSE | EX - WMTS NO.2 220KV LINE AT KTS | 40419.2375 | 40419.6903 | DAILY | 00015982 | SPICAPX | OUTAGE REBATE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658CB40419.2375 | X70658CB |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40419.2375 | 40419.6903 | DAILY | 00001169 | SPICAPX | RMVE CONNS FROM NO.1 220KV BUS TO B2 TR 1B CB ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658DH40419.2375 | X70658DH | X70658CB | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40419.2375 | 40419.6903 | DAILY | 00119824 | SPICAPX | OUTAGE REBATE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030596540420.3125 | 10305965 | 10305969 | Child | FALSE | A1 TRANS NO.3 BUS 500KV CB TRANS SIDE ROI AT LYPS | 40420.3125 | 40423.6312 | DAILY | [12 empty] | 0
_1030596940420.3125 | 10305969 |  | Parent | TRUE | NO.1 500/220KV TRANS 500KV E/SW AT LYPS | 40420.3125 | 40423.6312 | CONT | [12 empty] | 0
_1030597140420.3125 | 10305971 | 10305969 | Child | FALSE | LYGS A1 TRANS 500KV CB AT LYPS | 40420.3125 | 40423.6312 | DAILY | [12 empty] | 0
_1032702440420.3361111111 | 10327024 |  | Parent | FALSE | LYGS A1 TRANS 500KV CB CVT W/PH AT LYPS | 40420.3361 | 40424.5743 | CONT | [12 empty] | 0
_X70658DE40421.2527777778 | X70658DE |  | Parent | FALSE | EX - TTS NO.2 220KV LINE AT KTS | 40421.2528 | 40421.7535 | DAILY | 00015987 | SPICAPX | INSTL TEMP DROPPRS TTS 2L TO TTS 2L 2B CB L/S ROI | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031214940421.3416666667 | 10312149 |  | Parent | FALSE | NO.1 22KV/415V S/S TRANS AT ERTS | 40421.3417 | 40421.6181 | DAILY | 00004373 | SPIMAINT | No.1 S/S Trans, S/D & Isol O/H @ ERTS | SPIPOWER |  |  | Other Transformers | Eastern | 22 | NON AER ELEMENT | NON AER ELEMENT |  | 0
_X7E258A440421.40625 | X7E258A4 |  | Parent | TRUE | B1 TRANS 66KV CB AT TSTS | 40421.4062 | 40423.6965 | CONT | [12 empty] | 0
_X7E258A540421.40625 | X7E258A5 | X7E258A4 | Child | FALSE | B1 220/66KV TRANS AT TSTS | 40421.4062 | 40423.6965 | CONT | 00007657 | SPICAPX | Trans Rebate | SPIPOWER | X7E2 | X7E2 - (TSTS) REPLACE 66KV BUS PROTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1033784340421.5368055556 | 10337843 |  | Parent | FALSE | NO.2 66KV CAPACITOR BANK AT TTS | 40421.5368 | 40421.6368 | DAILY | 00001485 | SPIMAINT | REPAIR HOT CONNECTION | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_X70658DJ40421.7433796296 | X70658DJ |  | Parent | FALSE | EX - TTS NO.2 LINE/WMTS NO.2 LINE 220KV CB AT KTS | 40421.7434 | 40436.2882 | CONT | [12 empty] | 0
_1032388140422.2708333333 | 10323881 |  | Parent | FALSE | WOTS 330KV LINE AT DDTS | 40422.2708 | 40422.7743 | REPDAILY | 00012359 | SPIMAINT | OUT W/O for WOTS Line CVT replacement at DDTS | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1033778840422.2902777778 | 10337788 | V8A358E1 | Child | FALSE | NO.4A 66KV CAPACITOR BANK AT TTS | 40422.2903 | 40429.6674 | CONT | 00369405 | SPIMAINT | capture outage costs | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1033778940422.2902777778 | 10337789 | V8A358E1 | Child | FALSE | NO.4B 66KV CAPACITOR BANK AT TTS | 40422.2903 | 40429.6674 | CONT | 00337509 | SPIMAINT | capture outage costs | SPIPOWER |  |  | Capacitors | Western | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_V8A358E140422.2902777778 | V8A358E1 |  | Parent | TRUE | NO.4A 66KV CAPACITOR BANK CB AT TTS | 40422.2903 | 40429.6674 | CONT | [12 empty] | 0
_1031464140422.2916666667 | 10314641 |  | Parent | TRUE | MLTS 220KV LINE E/SW AT TGTS | 40422.2917 | 40422.6618 | DAILY | [12 empty] | 0
_1032669140422.2916666667 | 10326691 | 10314641 | Child | FALSE | MLTS 220KV LINE AT TGTS | 40422.2917 | 40422.6618 | DAILY | 00023131 | SPIMAINT | Rebate W/O MLTS Line during line equip OH | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V79658A540422.2930555556 | V79658A5 |  | Parent | FALSE | BTS 220KV LINE AT RTS | 40422.2931 | 40455.6382 | CONT | 00021222 | SPIMAINT | V796 - (BTS-RTS) CABLE JOINT REPLACEMENTS | SPIPOWER | V796 | V796 - (BTS-RTS) CABLE JOINT REPLACEMENTS | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032667640422.2965277778 | 10326676 | 10326679 | Child | FALSE | 3-6 66KV BUS TIE ISOL AT HTS | 40422.2965 | 40422.5889 | DAILY | [12 empty] | 0
_1032668540422.3159722222 | 10326685 |  | Parent | FALSE | NO.2 330KV CAPACITOR BANK AT WOTS | 40422.316 | 40422.3888 | REPDAILY | 00354001 | TRANSGRD | Overhaul No2 330kV Cap Bank & CB for Transgrid | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_1027304140422.3166666667 | 10273041 |  | Parent | TRUE | B2 220/66KV TRANS AT MWTS | 40422.3167 | 40424.6681 | CONT | 00010266 | SPIMAINT | 73041 B2 220/66KV TRANS AT MWTS Metro Trans | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030118340422.3166666667 | 10301183 | 10273041 | Child | FALSE | JLTS NO.2 220KV LINE AT MWTS | 40422.3167 | 40424.6681 | CONT | 00016131 | SPIMAINT | LINE REBATE FOR TX OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032388140423.2763888889 | 10323881 |  | Parent | FALSE | WOTS 330KV LINE AT DDTS | 40423.2764 | 40423.7222 | REPDAILY | 00012359 | SPIMAINT | OUT W/O for WOTS Line CVT replacement at DDTS | SPIPOWER |  |  | Circuits | Alstom | 330 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1033764740423.2923611111 | 10337647 |  | Parent | FALSE | H1 330/220KV TRANS BANK AT SMTS | 40423.2924 | 40423.5514 | DAILY | 00026101 | SPIMAINT | TOP UP WHITE PHASE DIVERTER SWITCH | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031463940423.3111111111 | 10314639 |  | Parent | TRUE | BATS 220KV LINE E/SW AT TGTS | 40423.3111 | 40423.6681 | DAILY | [12 empty] | 0
_1032669240423.3111111111 | 10326692 | 10314639 | Child | FALSE | BATS 220KV LINE AT TGTS | 40423.3111 | 40423.6681 | DAILY | 00023130 | SPIMAINT | Rebate W/O BATS Line during line equip OH | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031123040423.325 | 10311230 |  | Parent | FALSE | MWTS NO.4 66KV FDR AT LY | 40423.325 | 40423.5799 | DAILY | 00015997 | SPIMAINT | Overhaul MWTS No 4 66 Kv Fdr at LY | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E958C640424.25 | X7E958C6 |  | Parent | FALSE | SYTS 500KV LINE AT KTS | 40424.25 | 40428.6875 | CONT | 00015990 | SPICAPX | REPLACE CVTS AND SURGE DIVERTERS | SPIPOWER | X7E9 | X7E9 - (KTS) 500KV CT & CB | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1033792240424.2729166667 | 10337922 |  | Parent | FALSE | A4 500/220KV TRANS BANK AT KTS | 40424.2729 | 40424.6479 | DAILY | 00026098 | SPIMAINT | TOP UP 220KV BUSHINGS | SPIPOWER |  |  | Main Transformers | Western | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031464940424.2958333333 | 10314649 |  | Parent | TRUE | B2 TRANS 220KV CB AT TGTS | 40424.2958 | 40424.5243 | DAILY | [12 empty] | 0
_1032669340424.2958333333 | 10326693 | 10314649 | Child | FALSE | B2 220/66KV TRANS AT TGTS | 40424.2958 | 40424.5243 | DAILY | 00003127 | SPIMAINT | Perf Cacl W/O B2 Trans during 220kV CB OH | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_X7E258A240424.3479166667 | X7E258A2 |  | Parent | TRUE | B2 TRANS 66KV CB AT TSTS | 40424.3479 | 40424.6285 | DAILY | [12 empty] | 0
_X7E258A340424.3479166667 | X7E258A3 | X7E258A2 | Child | FALSE | B2 220/66KV TRANS AT TSTS | 40424.3479 | 40424.6285 | DAILY | 00007658 | SPICAPX | Rebate Trans outage | SPIPOWER | X7E2 | X7E2 - (TSTS) REPLACE 66KV BUS PROTS | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1033793940424.3590277778 | 10337939 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 40424.359 | 40424.3729 | CONT | 00002829 | FAULT | GTS B3 Trans 66kV CB Opened | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z72758C140424.3673611111 | Z72758C1 |  | Parent | FALSE | NO.1 66KV BUS AT GTS | 40424.3674 | 40424.4035 | DAILY | 00002835 | SPICAPX | Replace blown fuse on No1 66kv Bus VT | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Bus | Alstom | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1033781940424.9375 | 10337819 |  | Parent | FALSE | A4 GEN TRANS 500KV CB AT LYPS | 40424.9375 | 40431.4306 | CONT | [12 empty] | 0
_1033789740425.2993055556 | 10337897 |  | Parent | FALSE | NO.1 11/220KV TRANS BANK AT MPS | 40425.2993 | 40425.4993 | DAILY | 00001082 | SPIMAINT | TOP UP BUSHINGS MPS No1&2 11/220 TXs AT MPS | SPIPOWER |  |  | Connection Transformers | Eastern | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1032669440425.3013888889 | 10326694 |  | Parent | FALSE | B3 220/66KV TRANS AT GTS | 40425.3014 | 40425.566 | DAILY | 00002829 | SPIMAINT | OUT WO Install replacement 220 Bph CVD to B3 Trans | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1033798740426.9298611111 | 10337987 |  | Parent | FALSE | YPS -YWPS 2 220KV G | 40426.9299 | 40427.7111 | CONT | 00020518 | GENCO | YWPS W2 Gen Trans 220kV Line Isolated for PowerSta | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1032701640427.275 | 10327016 |  | Parent | FALSE | A2 515/220KV TRANS BANK AT ROTS | 40427.275 | 40427.6444 | DAILY | 00362994 | SPIMAINT | Rebate Trans outage Over Haul 500kv isols | SPIPOWER |  |  | Main Transformers | Eastern | 500 | UNREGULATED | EXCLUDED | Never Rolling into RAB | 0
_X7E858D240427.3208333333 | X7E858D2 |  | Parent | FALSE | A2 515/230KV TRANS BANK AT HWTS | 40427.3208 | 40429.6486 | CONT | 00337572 | SPIMAINT | CONSTRUCT NEW CB/CT NO2 MAIN TRANS @ HWTS JAMCO | SPIPOWER | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031458040427.3986111111 | 10314580 |  | Parent | TRUE | EPS NO.1 220KV LINE CB AT MBTS | 40427.3986 | 40427.7222 | DAILY | [12 empty] | 0
_1032696640427.3986111111 | 10326966 | 10314580 | Child | FALSE | EPS NO.1 220KV LINE AT MBTS | 40427.3986 | 40427.7222 | DAILY | 00364630 | SPIMAINT | Rebate W/O EPS No1 Line during CB OH | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032695740427.4145833333 | 10326957 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 40427.4146 | 40429.6882 | CONT | 00352121 | SPIMAINT | Out W/O No2 Trans for Tech services HV testing | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031694340427.5340277778 | 10316943 |  | Parent | FALSE | A4 GEN TRANS 500KV CB AT LYPS | 40427.534 | 40428.6146 | DAILY | [12 empty] | 0
_Z72758B940428.25 | Z72758B9 |  | Parent | TRUE | PT. HENRY NO.2 220KV LINE AT GTS | 40428.25 | 40428.7021 | REPDAILY | 00367278 | SPICAPX | Remove GW from Pth No2 Line G Wire mast | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z72758C040428.25 | Z72758C0 | Z72758B9 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 40428.25 | 40428.7021 | REPDAILY | 00366646 | SPICAPX | Rebate WO for MLTS No2 Line outage | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V22858A240428.2958333333 | V22858A2 |  | Parent | FALSE | NO.2 220KV CAPACITOR BANK AT ROTS | 40428.2958 | 40430.5778 | CONT | 00112418 | SPIMAINT | REPLACE CB HEADS | SPIPOWER | V228 | V228 - (VARIOUS) REFURB SPEC 83/302 HPL CB HEADS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1032702640428.3090277778 | 10327026 |  | Parent | FALSE | B2 TRANS 66KV CB AT ATS | 40428.309 | 40428.4951 | DAILY | [12 empty] | 0
_1031232440428.3131944445 | 10312324 |  | Parent | FALSE | A1 TRANS NO.1 BUS 500KV CB AT MLTS | 40428.3132 | 40429.7083 | CONT | [12 empty] | 0
_1031458240428.3222222222 | 10314582 |  | Parent | TRUE | EPS NO.2 220KV LINE CB AT MBTS | 40428.3222 | 40428.6771 | DAILY | [12 empty] | 0
_1032696740428.3222222222 | 10326967 | 10314582 | Child | FALSE | EPS NO.2 220KV LINE AT MBTS | 40428.3222 | 40428.6771 | DAILY | 00364634 | SPIMAINT | Rebate W/O EPS No2 Line during CB OH | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032696140428.3277777778 | 10326961 |  | Parent | FALSE | NO.1 330KV CAPACITOR BANK AT DDTS | 40428.3278 | 40428.7646 | DAILY | 00352085 | TRANSGRD | No1 330kV Cap Bank & CB maint for Transgrid | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_1033806540428.49375 | 10338065 |  | Parent | FALSE | SYN/COND AT FBTS | 40428.4938 | 40428.6104 | DAILY | 00002697 | FAULT | Trip of FBTS Synchronous Condenser | SPIPOWER |  |  | Sync Condensers | Western | 22 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1032702740428.5104166667 | 10327027 |  | Parent | FALSE | Trial Dropper for RADAR | 40428.5104 | 40428.5896 | DAILY | [12 empty] | 0
_Z72758B940429.2506944445 | Z72758B9 |  | Parent | TRUE | PT. HENRY NO.2 220KV LINE AT GTS | 40429.2507 | 40429.609 | REPDAILY | 00367278 | SPICAPX | Remove GW from Pth No2 Line G Wire mast | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_Z72758C040429.2506944445 | Z72758C0 | Z72758B9 | Child | FALSE | MLTS NO.2 220KV LINE AT GTS | 40429.2507 | 40429.609 | REPDAILY | 00366646 | SPICAPX | Rebate WO for MLTS No2 Line outage | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032703540429.2930555556 | 10327035 |  | Parent | FALSE | B3 TRANS 66KV CB AT KTS | 40429.2931 | 40429.5083 | DAILY | [12 empty] | 0
_1030753340429.2979166667 | 10307533 |  | Parent | FALSE | 2-3 66KV BUS TIE CB AT SVTS | 40429.2979 | 40429.5958 | DAILY | [12 empty] | 0
_X7E258A840429.3041666667 | X7E258A8 |  | Parent | FALSE | SYN/COND TRANS NO.1 BUS 66KV CB AT TSTS | 40429.3042 | 40431.5104 | CONT | [12 empty] | 0
_1031158840429.325 | 10311588 |  | Parent | FALSE | AUX TRANS 'C' NO.1 BUS 220KV CB AT YPS | 40429.325 | 40430.4431 | CONT | [12 empty] | 0
_X7E858E240429.3319444444 | X7E858E2 |  | Parent | FALSE | EX - SMTS NO.2 500KV LINE NO.2 BUS CB CT R/PH AT HWTS | 40429.3319 | 40449.6417 | CONT | [12 empty] | 0
_1033811740429.9756944444 | 10338117 |  | Parent | FALSE | NO.5 GEN TRANS LINE AT HWPS | 40429.9757 | 40434.5657 | CONT | 00356083 | GENCO | Isolated for generator | SPIPOWER |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X87058S840430.25 | X87058S8 |  | Parent | FALSE | GTS -PTH 1 220KV WY | 40430.25 | 40430.8028 | DAILY | 00022690 | SPICAPX | GTS-PT Henry No1 Line insulator replace at T86 | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_V8A358A140430.2923611111 | V8A358A1 |  | Parent | TRUE | NO.2 66KV CAPACITOR BANK CB AT RWTS | 40430.2924 | 40436.5354 | CONT | [12 empty] | 0
_V8A358A240430.2923611111 | V8A358A2 | V8A358A1 | Child | FALSE | NO.2 220KV CAPACITOR BANK AT RWTS | 40430.2924 | 40436.5354 | CONT | 00350529 | SPIMAINT | CAPTURE OUTAGE COSTS | SPIPOWER | V8A3 | V8A3 - REFURBISH 4*66KV CAP BANK CBS | Capacitors | Eastern | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_V8A358A840430.2923611111 | V8A358A8 | V8A358A1 | Child | FALSE | NO.2B 66KV CAPACITOR BANK AT RWTS | 40430.2924 | 40436.5354 | CONT | 00331179 | SPIMAINT | CAPTURE OUTAGE COSTS | SPIPOWER | V8A3 | V8A3 - REFURBISH 4*66KV CAP BANK CBS | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_Z72758B840430.3020833333 | Z72758B8 |  | Parent | FALSE | KTS NO.2 220KV LINE AT GTS | 40430.3021 | 40430.5882 | DAILY | 00367295 | SPICAPX | Remove existing GW from first tower GTS-KTS 2 Ln | SPIPOWER | Z727 | Z727 - (GTS) B2 220/66KV TRANSFORMER | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032670540430.3125 | 10326705 | X7E858D8 | Child | FALSE | LYPS NO.1 500KV LINE AT HWTS | 40430.3125 | 40430.4535 | DAILY | 00016234 | SPIMAINT | REBATE FOR BUS NO2 OUTAGE @ HWTS | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E858D840430.3125 | X7E858D8 |  | Parent | TRUE | A2 515/230KV TRANS BANK AT HWTS | 40430.3125 | 40430.4535 | DAILY | 00337572 | SPIMAINT | CONNECT CABLE TO NO2 BUS ROI @ HWTS JAMCO | SPIPOWER | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1031457840430.3194444444 | 10314578 |  | Parent | TRUE | DDTS NO.2 220KV LINE CB AT MBTS | 40430.3194 | 40430.6153 | DAILY | [12 empty] | 0
_1032696840430.3194444444 | 10326968 | 10314578 | Child | FALSE | DDTS NO.2 220KV LINE AT MBTS | 40430.3194 | 40430.6153 | DAILY | 00364626 | SPIMAINT | Rebate W/O DDTS No2 Line during CB OH | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032696340430.3395833333 | 10326963 |  | Parent | FALSE | NO.2 330KV CAPACITOR BANK AT DDTS | 40430.3396 | 40430.7556 | DAILY | 00352093 | TRANSGRD | No2 330kV Cap Bank & CB maint for Transgrid | TRANSGRD |  |  | Capacitors | Alstom | 330 | NON SP ASSET | EXCLUDED | TRANSGRID | 3
_X7E858D340430.45625 | X7E858D3 |  | Parent | FALSE | A2 515/230KV TRANS BANK AT HWTS | 40430.4563 | 40431.8389 | CONT | 00337572 | SPIMAINT | REMOVE OLD CB/CT NO2 MAIN TRANS 500KV @ HWTS JAMCO | SPIPOWER | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1033813640430.51875 | 10338136 |  | Parent | FALSE | SVTS NO.2 220KV LINE/NO.1 CSC CB AT ROTS | 40430.5188 | 40435.4639 | DAILY | [12 empty] | 0
_1032656940430.5826388889 | 10326569 |  | Parent | FALSE | BATS 220KV LINE NO.1 BUS CB AT BETS | 40430.5826 | 40430.6576 | DAILY | [12 empty] | 0
_1032657140430.6645833333 | 10326571 |  | Parent | FALSE | 3-4 66KV BUS TIE CB AT BETS | 40430.6646 | 40430.6868 | DAILY | [12 empty] | 0
_X87058S740431.2479166667 | X87058S7 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 40431.2479 | 40431.5639 | DAILY | 00022691 | SPICAPX | GTS-PT Henry No2 Line insulator replace at T85A | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E958C540431.2506944445 | X7E958C5 |  | Parent | FALSE | SMTS 500KV LINE AT KTS | 40431.2507 | 40435.4132 | CONT | 00015991 | SPICAPX | REPLACE CVTS AND SURGE DIVERTERS | SPIPOWER | X7E9 | X7E9 - (KTS) 500KV CT & CB | Circuits | Western | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031121340431.3444444445 | 10311213 |  | Parent | FALSE | LY NO.3 66KV FDR AT MWTS | 40431.3444 | 40431.6011 | DAILY | 00016142 | SPIMAINT | Overhaul LY No 3 66 Kv LINE at MWTS | SPIPOWER |  |  | Circuits | Eastern | 66 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1033820040433.6833333333 | 10338200 |  | Parent | FALSE | ALQ 66KV FDR CB AT ATS | 40433.6833 | 40433.9979 | DAILY | [12 empty] | 0
_1033820140433.9368055556 | 10338201 |  | Parent | FALSE | NO.3 66KV BUS AT ATS | 40433.9368 | 40433.9951 | DAILY | 00352210 | SPIMAINT | repair alq fdr cb blue phase bus side isolator | SPIPOWER |  |  | Bus | Western | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_VA4858A540434.3236111111 | VA4858A5 | X7E858D4 | Child | FALSE | A1 515/230KV TRANS DELUGE SYSTEM AT HWTS | 40434.3236 | 40435.7875 | CONT | [12 empty] | 0
_X7E858D440434.3236111111 | X7E858D4 |  | Parent | TRUE | A1 515/230KV TRANS AT HWTS | 40434.3236 | 40435.7875 | CONT | 00009772 | SPIMAINT | CONNECTION CB/CT NO1 MAIN TRANS @ HWTS JAMCO | SPIPOWER | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1033822740434.8902777778 | 10338227 |  | Parent | FALSE | NO.3 66KV BUS AT HTS | 40434.8903 | 40434.9632 | DAILY | 00004458 | FAULT | No3 66kV Bus trip | SPIPOWER |  |  | Bus | Eastern | 66 | NON AER ELEMENT | EXCLUDED |  | 0
_1033822940435.0194444444 | 10338229 |  | Parent | FALSE | YWPS NO.1 220KV LINE AT YPS | 40435.0194 | 40437.4319 | CONT | 00016423 | GENCO | W1 GTG Ioslated for power station | GENCO |  |  | Circuits | Eastern | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_1030749840435.3263888889 | 10307498 |  | Parent | FALSE | R3 TRANS NO.1 BUS 220KV CB AT RCTS | 40435.3264 | 40435.6903 | DAILY | [12 empty] | 0
_1032670240435.3333333333 | 10326702 |  | Parent | FALSE | NO.1 66KV CAPACITOR BANK AT SVTS | 40435.3333 | 40435.509 | DAILY | 00004824 | SPIMAINT | Repair thermo Joint | SPIPOWER |  |  | Capacitors | Eastern | 66 | CIRCUIT | EXCLUDED | NON CRITICAL ELEMENT | 0
_1031221540435.3590277778 | 10312215 |  | Parent | FALSE | H3 TRANS NO.1 BUS 220KV CB AT DDTS | 40435.359 | 40436.6521 | CONT | [12 empty] | 0
_V7A058B840435.4152777778 | V7A058B8 |  | Parent | FALSE | F2 TRANS NO.2 BUS 500KV CB AT SMTS | 40435.4153 | 40438.5437 | CONT | [12 empty] | 0
_1031402140435.4645833333 | 10314021 |  | Parent | TRUE | NO.1 220KV BUS E/SW AT BATS | 40435.4646 | 40435.6924 | REPDAILY | [12 empty] | 0
_1032719640435.4645833333 | 10327196 | 10314021 | Child | FALSE | TGTS 220KV LINE AT BATS | 40435.4646 | 40435.6924 | REPDAILY | 00012435 | SPIMAINT | Rebate W/O TGTS Line during No1 220 bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032719740435.4645833333 | 10327197 | 10314021 | Child | FALSE | B2 220/66KV TRANS AT BATS | 40435.4646 | 40435.6924 | REPDAILY | 00006555 | SPIMAINT | Rebate W/O B2 Trans during No1 220 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1033826740435.8159722222 | 10338267 |  | Parent | FALSE | NO.3 GEN 220/16.5KV TRANS AT HWPS | 40435.816 | 40470.8604 | CONT | 00009644 | GENCO | Unit 3 Gen trans | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_X70658DF40436.25 | X70658DF |  | Parent | TRUE | NO.1 220KV BUS AT KTS | 40436.25 | 40436.4958 | DAILY | 00001169 | SPICAPX | RMVE CONN #1 220KV BUS TOWMTS 2L 1B CB B/S ISOL | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Bus | Western | 220 | NON AER ELEMENT | EXCLUDED |  | 0
_X70658DG40436.25 | X70658DG | X70658DF | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40436.25 | 40436.4958 | DAILY | 00119824 | SPICAPX | OUTAGE REBATE | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1031402140436.28125 | 10314021 |  | Parent | TRUE | NO.1 220KV BUS E/SW AT BATS | 40436.2812 | 40436.7604 | REPDAILY | [12 empty] | 0
_1032719640436.28125 | 10327196 | 10314021 | Child | FALSE | TGTS 220KV LINE AT BATS | 40436.2812 | 40436.7604 | REPDAILY | 00012435 | SPIMAINT | Rebate W/O TGTS Line during No1 220 bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032719740436.28125 | 10327197 | 10314021 | Child | FALSE | B2 220/66KV TRANS AT BATS | 40436.2812 | 40436.7604 | REPDAILY | 00006555 | SPIMAINT | Rebate W/O B2 Trans during No1 220 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_Z71958E640436.2923611111 | Z71958E6 |  | Parent | FALSE | B3 220/66KV TRANS AT CBTS | 40436.2924 | 40437.6306 | CONT | 00368875 | VEN_AUG | Enclose Roof | SPIPOWER | Z719 | Z719 - (CBTS) 3RD CONNECTION ASSET TRANSFORMER | Connection Transformers | Eastern | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_X7E858D640436.3125 | X7E858D6 |  | Parent | FALSE | A1 515/230KV TRANS AT HWTS | 40436.3125 | 40436.466 | DAILY | 00009772 | SPIMAINT | CONNECT CABLE TO BUS SIDE ROI @ HWTS JAMCO | SPIPOWER | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030750040436.3194444444 | 10307500 |  | Parent | FALSE | R3 TRANS NO.2 BUS 220KV CB AT RCTS | 40436.3194 | 40436.6465 | DAILY | [12 empty] | 0
_1033824840436.3340277778 | 10338248 |  | Parent | TRUE | CBTS NO.4 LINE Y PROT + EF1002 AT ROTS (RTF) | 40436.334 | 40436.6486 | DAILY | [12 empty] | 0
_1033824940436.3340277778 | 10338249 | 10338248 | Child | FALSE | CBTS NO.4 500KV LINE AT ROTS (RTF) | 40436.334 | 40436.6486 | DAILY | 00356730 | SPIMAINT | Line Rebate | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X70658CD40436.4659722222 | X70658CD |  | Parent | FALSE | EX - WMTS NO.2 220KV LINE AT KTS | 40436.466 | 40436.7569 | DAILY | 00015982 | SPICAPX | RPLC TEMP DRPRS TO WMTS 2L TO WMTS 2L CB L/S ISOL | SPIPOWER | X706 | X706 - (KTS) REBUILD 220/66KV | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X7E858D540436.4666666667 | X7E858D5 |  | Parent | FALSE | A1 515/230KV TRANS AT HWTS | 40436.4667 | 40438.6889 | DAILY | 00009772 | SPIMAINT | REMOVE OLD CB/CT NO1 MAIN TRANS 500KV @HWTS JAMCO | SPIPOWER | X7E8 | X7E8 - (HWTS) 500KV CT & CB | Main Transformers | Eastern | 500 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_X87058T140437.25 | X87058T1 |  | Parent | FALSE | GTS -PTH 2 220KV WY | 40437.25 | 40437.7493 | DAILY | 00022691 | SPICAPX | GTS-PT Henry No2 Line insulator replace at T85A | SPIPOWER | X870 | X870 - 16MM INSULATOR REPLACEMENT PROJECT FY08-10 | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_VA2558A240437.2548611111 | VA2558A2 |  | Parent | FALSE | B1 220/66KV TRANS AT WMTS | 40437.2549 | 40445.6403 | CONT | 00003233 | SPIMAINT | INSTALL STEEL SUPPORT & SITE NEW COOLING UNITS | SPIPOWER | VA25 | VA25 - (KTS,WMTS,RTS,RWTS) ASEA 150MVA TRANS COOLING MODS | Connection Transformers | Western | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1033783940437.2979166667 | 10337839 |  | Parent | TRUE | NO.1 220KV CAPACITOR BANK CB AT KTS | 40437.2979 | 40437.5174 | DAILY | [12 empty] | 0
_1033784140437.2979166667 | 10337841 | 10337839 | Child | FALSE | NO.1 220KV CAPACITOR BANK AT KTS | 40437.2979 | 40437.5174 | DAILY | 00119824 | SPIMAINT | CAPTURE OUTAGE COSTS | SPIPOWER |  |  | Capacitors | Western | 220 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1032720940437.3194444444 | 10327209 | 10307502 | Child | FALSE | R3 220/66/22KV TRANS AT RCTS | 40437.3194 | 40437.6368 | DAILY | 00361128 | SPIMAINT | Perf calc W/O R3 Trans 66 only during 66 CB outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | UNREGULATED | EXCLUDED | Not Rolling into RAB till 2014 | 0
_1030750240437.3194444444 | 10307502 |  | Parent | TRUE | R3 TRANS 66KV CB AT RCTS | 40437.3194 | 40437.6374 | DAILY | [12 empty] | 0
_1033832040437.3361111111 | 10338320 |  | Parent | FALSE | BSS 220KV LINE AT RCTS | 40437.3361 | 40437.6208 | CONT | 00016966 | TRANSGRD | Work for Transgrid | TRANSGRD |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3
_1031221940437.3375 | 10312219 |  | Parent | FALSE | H3 TRANS NO.2 BUS 220KV CB AT DDTS | 40437.3375 | 40438.7368 | CONT | [12 empty] | 0
_1031400340437.35625 | 10314003 |  | Parent | TRUE | NO.2 220KV BUS E/SW AT BATS | 40437.3562 | 40437.4625 | REPDAILY | [12 empty] | 0
_1032695340437.35625 | 10326953 | 10314003 | Child | FALSE | MLTS NO.1 220KV LINE AT BATS | 40437.3562 | 40437.4625 | REPDAILY | 00012429 | SPIMAINT | Rebate W/O MLTS No1 Line during No2 220 bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032695640437.35625 | 10326956 | 10314003 | Child | FALSE | B1 220/66KV TRANS AT BATS | 40437.3562 | 40437.4625 | REPDAILY | 00006554 | SPIMAINT | Perf calc W/O No1 Trans during No2 220 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1033832240437.3916666667 | 10338322 |  | Parent | FALSE | BATS NO.1 LINE/TGTS LINE 220KV CB AT MLTS | 40437.3917 | 40437.5326 | DAILY | [12 empty] | 0
_1032725840437.4069444445 | 10327258 |  | Parent | TRUE | AUTO RECLOSE CONTROL EQUIPMENT AT ROTS | 40437.4069 | 40437.709 | DAILY | [12 empty] | 0
_1033767340437.4069444445 | 10337673 | 10327258 | Child | FALSE | HWTS NO.3 500KV LINE AT ROTS (RTF) | 40437.4069 | 40437.709 | DAILY | 00359383 | SPIMAINT | REBATE FOR LINE OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1031400340438.25 | 10314003 |  | Parent | TRUE | NO.2 220KV BUS E/SW AT BATS | 40438.25 | 40438.7368 | REPDAILY | [12 empty] | 0
_1032695340438.25 | 10326953 | 10314003 | Child | FALSE | MLTS NO.1 220KV LINE AT BATS | 40438.25 | 40438.7368 | REPDAILY | 00012429 | SPIMAINT | Rebate W/O MLTS No1 Line during No2 220 bus outage | SPIPOWER |  |  | Circuits | Alstom | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1032695640438.25 | 10326956 | 10314003 | Child | FALSE | B1 220/66KV TRANS AT BATS | 40438.25 | 40438.7368 | REPDAILY | 00006554 | SPIMAINT | Perf calc W/O No1 Trans during No2 220 bus outage | SPIPOWER |  |  | Connection Transformers | Alstom | 220 | CONNECTION ASSET | TRANSFORMER |  | 0
_1030750540438.3166666667 | 10307505 |  | Parent | FALSE | R3 TRANS 22KV CB AT RCTS | 40438.3167 | 40438.4931 | DAILY | [12 empty] | 0
_1033234140438.3347222222 | 10332341 |  | Parent | FALSE | AUTO RECLOSE CONTROL EQUIPMENT AT CBTS | 40438.3347 | 40438.5139 | DAILY | [12 empty] | 0
_1033815440438.3680555556 | 10338154 | 10338155 | Child | FALSE | HYTS-SESS 1 275KV WH | 40438.3681 | 40439.7278 | CONT | 00022795 | ELECTRAN | Electranet Outage | ELECTRAN |  |  | Circuits | Alstom | 275 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_1033837340438.6555555556 | 10338373 |  | Parent | FALSE | NO.5 GEN 220/16.5KV TRANS AT HWPS | 40438.6556 | 40439.7069 | CONT | 00009646 | GENCO | Unit 5 | GENCO |  |  | Connection Transformers | Eastern | 220 | NON SP ASSET | EXCLUDED |  | 0
_1033837640439.0340277778 | 10338376 |  | Parent | FALSE | CBTS NO.4 500KV LINE NO.3 BUS CB AT HWTS | 40439.034 | 40439.4278 | CONT | [12 empty] | 0
_1033825140439.2083333333 | 10338251 |  | Parent | TRUE | NPSD-BLTS 220KV WY | 40439.2083 | 40441.9056 | CONT | 00022739 | VICROADS | PROXIMITY REASONS FOR WESTGATE BRIDGE WORKS | 3RDPARTY |  |  | Circuits | Western | 220 | CIRCUIT | LINE | CRITICAL ELEMENT | 3 | Vic roads
_1033825940439.2083333333 | 10338259 | 10338251 | Child | FALSE | FBTS-BLTS 220KV WY | 40439.2083 | 40441.9056 | CONT | 00022666 | VICROADS | OUTAGE REBATE FOR WESTGATE BRIDGE WORKS | 3RDPARTY |  |  | Circuits | Western | 220 | CIRCUIT | LINE | NON CRITICAL ELEMENT | 3 | Vic roads
_1031693540439.2527777778 | 10316935 | X90758C2 | Child | FALSE | CBTS NO.4 500KV LINE NO.3 BUS CB AT HWTS | 40439.2528 | 40441.6715 | DAILY | [12 empty] | 0
_1032348240439.2527777778 | 10323482 | X90758C2 | Child | FALSE | CBTS NO.4 500KV LINE AT HWTS | 40439.2528 | 40441.6715 | CONT | 00016240 | SPICAPX | REBATE FOR LINE OUTAGE | SPIPOWER |  |  | Circuits | Eastern | 500 | CIRCUIT | LINE | CRITICAL ELEMENT | 0
_X90758C240439.2527777778 | X90758C2 |  | Parent | TRUE | EX - CBTS NO.4 500KV LINE NO.3 BUS CVT R/PH AT HWTS | 40439.2528 | 40441.6715 | CONT | [12 empty] | 0
_1033827040439.2625 | 10338270 |  | Parent | FALSE | LYBP-LYPS 1 500KV G | 40439.2625 | 40439.759 | CONT | 00023061 | GENCO | genco outage | GENCO |  |  | Circuits | Eastern | 500 | NON AER ELEMENT | EXCLUDED |  | 0
_1032388240439.2715277778 | 10323882 |  | Parent | FALSE | H2 330/220KV TRANS AT DDTS | 40439.2715 | 40439.725 | DAILY | 00352121 | SPIMAINT | OUT W/O for No2 Trans 330 Rph CVT replace at DDTS | SPIPOWER |  |  | Main Transformers | Alstom | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0
_1030648540439.275 | 10306485 |  | Parent | TRUE | NO.2 330KV BUS AT SMTS | 40439.275 | 40439.7535 | REPDAILY | 00001331 | SPIMAINT | O/Haul NO.2 330KV BUS AT SMTS | SPIPOWER |  |  | Bus | Western | 330 | CIRCUIT | EXCLUDED | CRITICAL ELEMENT | 0
_1030649740439.275 | 10306497 |  | Parent | FALSE | H2 TRANS 330KV CB BUS SIDE E/SW AT SMTS | 40439.275 | 40439.7535 | REPDAILY | [12 empty] | 0
_1030649940439.275 | 10306499 |  | Parent | TRUE | NO.2 330KV BUS E/SW AT SMTS | 40439.275 | 40439.7535 | REPDAILY | [12 empty] | 0
_1030650540439.275 | 10306505 | 10306499 | Child | FALSE | F2 TRANS 330KV CB BUS SIDE E/SW AT SMTS | 40439.275 | 40439.7535 | DAILY | [12 empty] | 0
_1030650740439.275 | 10306507 |  | Parent | FALSE | DDTS NO.2 330KV LINE NO.2 BUS CB BUS SIDE ROI AT SMTS | 40439.275 | 40439.7535 | REPDAILY | [12 empty] | 0
_1030650940439.275 | 10306509 |  | Parent | FALSE | F2 TRANS 330KV CB BUS SIDE ROI AT SMTS | 40439.275 | 40439.7535 | REPDAILY | [12 empty] | 0
_1030651340439.275 | 10306513 | 10306499 | Child | FALSE | H2 TRANS 330KV CB BUS SIDE ROI AT SMTS | 40439.275 | 40439.7535 | REPDAILY | [12 empty] | 0
_1030652340439.275 | 10306523 |  | Parent | FALSE | DDTS NO.1 330KV LINE NO.2 BUS CB BUS SIDE E/SW AT SMTS | 40439.275 | 40439.7535 | REPDAILY | [12 empty] | 0
_1030652740439.275 | 10306527 |  | Parent | FALSE | DDTS NO.2 330KV LINE NO.2 BUS CB BUS SIDE E/SW AT SMTS | 40439.275 | 40439.7535 | REPDAILY | [12 empty] | 0
_1030653640439.275 | 10306536 | 10306499 | Child | FALSE | DDTS NO.1 330KV LINE NO.2 BUS CB BUS SIDE ROI AT SMTS | 40439.275 | 40439.7535 | REPDAILY | [12 empty] | 0
_1030767140439.275 | 10307671 | 10306499 | Child | FALSE | EX - F2 TRANS 330KV CB CT R/PH AT SMTS | 40439.275 | 40439.7535 | REPDAILY | [12 empty] | 0
_1033789440439.275 | 10337894 | 10306485 | Child | FALSE | H2 330/220KV TRANS BANK AT SMTS | 40439.275 | 40439.7535 | REPDAILY | 00026102 | SPIMAINT | capture outage costs | SPIPOWER |  |  | Main Transformers | Western | 330 | CIRCUIT | TRANSFORMER | CRITICAL ELEMENT | 0