## TR Line GW C5 Condition
TL_GW_Eq.EQUIPMENT_ID | TL_GW_Eq.OBJECT_TYPE | TL_GW_Eq.FLOC | FLOC_DESCR | SUP_FLOC | TL_GW_Eq.FIREZONE | TL_GW_Eq.CAT_PROFILE | TL_GW_Eq.TECH_IDENT_NO | TL_GW_Eq_Char.Equipment Group Identifier | TL_GW_Eq_Char.Ground Wire Material | TL_GW_Eq_Char.Ground Wire Type | TL_GW_Eq.START_UP_Year | Start up date | Age | TL_GW_Eq.START_UP_Year_Updated-29-11-19 | TL_GW_Eq_Age | TL_GW_Eq_Age_Updated-29-11-19 | TL_GW_Eq_Age_Range | TL_GW_Eq_Age_Range_Updated-29-11-19 | GW_Eq-Criticality.Span Lgth [m] | GW_Eq-Criticality.Span Lgth [km] | TL_Structure_Eq.EQUIPMENT_ID | TL_Structure_Eq.CAT_PROFILE | TL_Structure_Eq.OBJECT_TYPE | TECH_OBJ_TYPE | TL_Structure_Eq_Char.Duty | TL_Structure_Eq_Char.Manufacture Type | TL_Structure_Eq.TECH_IDENT_NO | TL_Structure_Eq.TECH_OBJECT_DESCR | TL_Structure_Floc_Char.Number | TL_Structure_Eq.start Year | Twr_Age | TL_Twr_Age_Range | LATITUDE | LONGITUDE | LOCATION | GW_Eq-Criticality.Twr CA | CCt NAME | CCt NAME-UPDATED | CCt No. | CCt Tag | CCT VOLTAGE [kV] | Allocated CCt No | MP-Allocated | Matched MP | Meas. Position | Meas By | Meas Year | Valuation Code | 20-11-19 Meas Year | 20-11-19 CA | 22-11-19 MP | 22-11-19 CA( Condition Score) | Count GW Eq/twr | Count of CA score/twrEq | Count of GWEq/twrEq | Count of MP-CountGWEq | GW replacement project | GW replacement year | GW Type Updated | GW_Eq-Criticality.Corrosivity Level | GW_Eq-Criticality.Road/Rail Crossing | GW_Eq-Criticality.Urban or Country | Effects Look Up Key | GW_Eq-Criticality.Market Impact Cost (Final) | GW_Eq-Criticality.BushfireEffect | SAFETY_CRITICALITY | Collateral_Damage | Total Effects | Replacement Cost ($/Gwspan) | Ratio | Criticality (Scale1) | Criticality Score (Scale1) | TRR SOW (1/0) | cct check
30114275 | GWSTEEL | TL-TSTXEX-TSTX443-0000360875 | TOWER T443 RWTS-TTS 220KV | TL-TSTXEX-TSTX443 | LBRA | GW_OPGW | MX5-00409244 | GW-19/2 STEEL | Steel | 19/2 STEEL | 2005 | 2005-06-30 | 16.167 | 2005 | 14 | 14 | <20 | <20 | 346.6 | 0.3466 | 30064530 | TOWER | TWRMCCT | STRUCTSUSP | H | ASCOM OB | MX5-00360875 | T443 RWTS-TTS 220KV | T443 | 2005 | 28 | <30 | -37.7136 | 145.0874 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 |  |  |  |  | 2 | 0 | 0 | 180000 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 4 | 1 | Gw-4-1 | 20323388.18 | 4716.498 | 2468415.8044 | 148000 | 22944520.4824 | 100000 | 229.4452 | Cr5 | 5 | 1 | 4
30396683 | GWSTEEL | TL-TSTXEX-TSTX443-0000360875 | TOWER T443 RWTS-TTS 220KV | TL-TSTXEX-TSTX443 | LBRA | GW_OPGW | MX5-00409203 | GW-19/2 STEEL | Steel | 19/2 STEEL | 2005 | 2005-06-30 | 16.167 | 2005 | 14 | 14 | <20 | <20 | 346.6 | 0.3466 | 30064530 | TOWER | TWRMCCT | STRUCTSUSP | H | ASCOM OB | MX5-00360875 | T443 RWTS-TTS 220KV | T443 | 2005 | 28 | <30 | -37.7136 | 145.0874 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 | 180000 |  | JH | 2014 | 2 | 2010 | 5 | 190000 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 4 | 1 | Gw-4-1 | 20323388.18 | 4716.498 | 2468415.8044 | 148000 | 22944520.4824 | 100000 | 229.4452 | Cr5 | 5 | 1 | 4
30171367 | GWSTEEL | TL-SMKXEX-SMKX087-0000058555 | TOWER T055 TTS -KTS 2 220KV | TL-SMKXEX-SMKX087 | LBRA | GW_OPGW | MX5-00410861 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1994 | 1994-06-30 | 27.1677 | 1994 | 25 | 25 | <30 | <30 | 283.7 | 0.2837 | 30298792 | TOWER | TWRMCCT | STRUCTSUSP | L | S | MX5-00058555 | T055 TTS -KTS 2 220KV | T055 | 1994 | 50 | <50 | -37.7343 | 144.8524 | CENTRAL | C1 | TTS -KTS 2 |  | R | 2Steel | 220 | 2 | 190000 | 180010 |  | SQUIN | 2018 | 2 | 2018 | 2 | 190000 | 5 | 2 | 2 | 2 | 0 |  |  |  | 2 | 3 | 1 | Gw-3-1 | 10545.3701 | 0 | 2292990.7141 | 148000 | 2451536.0841 | 20426.4 | 120.018 | Cr5 | 5 | 1 | #N/A
30046225 | GWACSR | TL-HWHWEX-HWHW005-0000084423 | TOWER T005 HWPS-JLTS 3 220KV | TL-HWHWEX-HWHW005 | HBRA | GW_OPGW | MX5-00402041 | GW-GRAPE | ACSR | GRAPE | 1984 | 1984-06-30 | 37.1663 | 1984 | 35 | 35 | <40 | <40 | 430.6 | 0.4306 | 30137209 | TOWER | TWRMCCT | STRUCTSUSP | L |  | MX5-00084423 | T005 HWPS-JLTS 3 220KV | T005 | 1984 | 70 | <70 | -38.2799 | 146.4069 | EAST | C2 | HWPS-JLTS 3 |  | L | 1ACSR | 220 | 1 | 180010 | 180010 |  | DV | 2014 | 2 | 2014 | 5 | 180010 | 5 | 2 | 2 | 2 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 36487.919 | 4692.8839 | 3720.1399 | 25000 | 69900.9428 | 31003.2 | 2.2546 | Cr3 | 3 | 1 | 3
30283651 | GWACSR | TL-HWHWEX-HWHW005-0000084423 | TOWER T005 HWPS-JLTS 3 220KV | TL-HWHWEX-HWHW005 | HBRA | GW_OPGW | MX5-00402032 | GW-GRAPE | ACSR | GRAPE | 1984 | 1984-06-30 | 37.1663 | 1984 | 35 | 35 | <40 | <40 | 430.6 | 0.4306 | 30137209 | TOWER | TWRMCCT | STRUCTSUSP | L |  | MX5-00084423 | T005 HWPS-JLTS 3 220KV | T005 | 1984 | 70 | <70 | -38.2799 | 146.4069 | EAST | C2 | HWPS-JLTS 3 |  | R | 2ACSR | 220 | 2 | 190010 | 190010 |  | DV | 2014 | 2 | 2014 | 5 | 190010 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 36487.919 | 4692.8839 | 3720.1399 | 25000 | 69900.9428 | 31003.2 | 2.2546 | Cr3 | 3 | 1 | 3
30226235 | GWACSR | TL-HWCBEX-HWCB036-0000084997 | TOWER T036 HWTS-ROTS 3 500KV | TL-HWCBEX-HWCB036 | HBRA | GW_OPGW | MX5-00403324 | GW-GRAPE | ACSR | GRAPE | 1981 | 1981-06-30 | 40.167 | 1981 | 38 | 38 | <40 | <40 | 375.5 | 0.3755 | 30110634 | TOWER | TWRSCCT | STRUCTSUSP | L | HA | MX5-00084997 | T036 HWTS-ROTS 3 500KV | T036 | 1981 | 76 | <80 | -38.2947 | 146.2957 | EAST | C2 | HWTS-ROTS 3 |  | L | 1ACSR | 500 | 1 | 180010 | 190010 |  | RK | 2017 | 2 | 2017 | 2 | 180010 | 5 | 1 | 3 | 2 | 1 |  |  |  | 2 | 4 | 0 | Gw-4-0 | 106978625.8637 | 10429.6869 | 2460565.8044 | 25000 | 109474621.355 | 100000 | 1094.7462 | Cr5 | 5 | 1 | 1
30219581 | GWACSR | TL-YPROEX-YPRO320-0000056933 | TOWER T039 HWTS-ROTS 3R500KV | TL-YPROEX-YPRO320 | HBRA | GW_OPGW | MX5-00403218 | GW-GRAPE | ACSR | GRAPE | 1980 | 1980-06-30 | 41.1663 | 1980 | 39 | 39 | <40 | <40 | 341.4 | 0.3414 | 30248364 | TOWER | TWRSCCT | STRUCTSTRN | L | TC | MX5-00056933 | T039 HWTS-ROTS 3R500KV | T039 | 1980 | 78 | <80 | -37.9714 | 145.2851 | CENTRAL | C1 | HWTS-ROTS 3R |  | L | 1ACSR | 500 | 1 | 180010 |  |  |  |  | 2 | 0 | 0 | 180010 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 106978625.8637 | 1189.8017 | 93570.1399 | 550000 | 107623385.8054 | 24580.8 | 4378.3516 | Cr5 | 5 | 1 | #N/A
30220792 | GWACSR | TL-YPROEX-YPRO323-0000056937 | TOWER T041 HWTS-ROTS 3R500KV | TL-YPROEX-YPRO323 | HBRA | GW_OPGW | MX5-00403220 | GW-GRAPE | ACSR | GRAPE | 1980 | 1980-06-30 | 41.1663 | 1980 | 39 | 39 | <40 | <40 | 384 | 0.384 | 30327029 | TOWER | TWRSCCT | STRUCTSUSP | L | TA | MX5-00056937 | T041 HWTS-ROTS 3R500KV | T041 | 1980 | 78 | <80 | -37.9672 | 145.2789 | CENTRAL | C1 | HWTS-ROTS 3R |  | L | 1ACSR | 500 | 1 | 180010 |  |  |  |  | 2 | 0 | 0 | 180010 | 5 | 2 | 0 | 2 | -2 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 106978625.8637 | 1385.1475 | 93570.1399 | 550000 | 107623581.1512 | 27648 | 3892.6353 | Cr5 | 5 | 1 | #N/A
30131115 | GWACSR | TL-YPROEX-YPRO329-0000056949 | TOWER T047 HWTS-ROTS 3R500KV | TL-YPROEX-YPRO329 | HBRA | GW_OPGW | MX5-00403226 | GW-GRAPE | ACSR | GRAPE | 1980 | 1980-06-30 | 41.1663 | 1980 | 39 | 39 | <40 | <40 | 287 | 0.287 | 30124326 | TOWER | TWRSCCT | STRUCTSUSP | L | TA | MX5-00056949 | T047 HWTS-ROTS 3R500KV | T047 | 1980 | 78 | <80 | -37.9547 | 145.2602 | CENTRAL | C1 | HWTS-ROTS 3R |  | L | 1ACSR | 500 | 1 | 180010 |  |  |  |  | 2 | 0 | 0 | 180010 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 106978625.8637 | 1308.0753 | 3720.1399 | 25000 | 107008654.079 | 20664 | 5178.5063 | Cr5 | 5 | 1 | #N/A
30113045 | GWACSR | TL-YPROEX-YPRO322-0000056935 | TOWER T040 HWTS-ROTS 3R500KV | TL-YPROEX-YPRO322 | HBRA | GW_OPGW | MX5-00403219 | GW-GRAPE | ACSR | GRAPE | 1980 | 1980-06-30 | 41.1663 | 1980 | 39 | 39 | <40 | <40 | 374.9 | 0.3749 | 30092865 | TOWER | TWRSCCT | STRUCTSUSP | H | TB | MX5-00056935 | T040 HWTS-ROTS 3R500KV | T040 | 1980 | 78 | <80 | -37.9695 | 145.2821 | CENTRAL | C1 | HWTS-ROTS 3R |  | L | 1ACSR | 500 | 1 | 180010 | 180000 |  | DV | 2019 | 2 | 2019 | 5 | 180010 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 1 | 2 | Gw-1-2 | 106978625.8637 | 1435.1794 | 106635.4606 | 550000 | 107636696.5037 | 26992.8 | 3987.6077 | Cr5 | 5 | 1 | #N/A
30392284 | GWACSR | TL-YPROEX-YPRO328-0000056947 | TOWER T046 HWTS-ROTS 3R500KV | TL-YPROEX-YPRO328 | HBRA | GW_OPGW | MX5-00403225 | GW-GRAPE | ACSR | GRAPE | 1980 | 1980-06-30 | 41.1663 | 1980 | 39 | 39 | <40 | <40 | 447 | 0.447 | 30292947 | TOWER | TWRSCCT | STRUCTSUSP | L | TA | MX5-00056947 | T046 HWTS-ROTS 3R500KV | T046 | 1980 | 78 | <80 | -37.9573 | 145.264 | CENTRAL | C1 | HWTS-ROTS 3R |  | L | 1ACSR | 500 | 1 | 180010 |  |  |  |  | 2 | 0 | 0 | 180010 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 2 | 1 | Gw-2-1 | 106978625.8637 | 1347.7066 | 1583806.0551 | 148000 | 108711779.6254 | 32184 | 3377.8206 | Cr5 | 5 | 1 | #N/A
30177191 | GWACSR | TL-LYHWES-LYHW011-0000084276 | TOWER T011 LYPS-HWTS 2 500KV | TL-LYHWES-LYHW011 | HBRA | GW_OPGW | MX5-00406445 | GW-GRAPE | ACSR | GRAPE | 1984 | 1984-06-30 | 37.1663 | 1984 | 35 | 35 | <40 | <40 | 417 | 0.417 | 30320415 | TOWER | TWRSCCT | STRUCTSTRN | L | HC | MX5-00084276 | T011 LYPS-HWTS 2 500KV | T011 | 1984 | 70 | <70 | -38.2614 | 146.5358 | EAST | C2 | LYPS-HWTS 2 |  | R | 2ACSR | 500 | 2 | 190010 | 190010 |  | CR | 2013 | 2 | 2013 | 5 | 190010 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 200000 | 16606.6393 | 3720.1399 | 25000 | 245326.7792 | 30024 | 8.171 | Cr4 | 4 | 1 | #N/A
30183230 | GWSTEEL | TL-LYHWEN-LYHW019-0000086669 | TOWER T019 MWTS-LY 3 66KV | TL-LYHWEN-LYHW019 | HBRA | GW_OPGW | MX5-00408394 | GW-19/3 STEEL | Steel | STEEL | 1982 | 1982-06-30 | 39.1677 | 1982 | 37 | 37 | <40 | <40 | 350 | 0.35 | 30034655 | TOWER | TWRMCCT | STRUCTSUSP | L | 6A | MX5-00086669 | T019 MWTS-LY 3 66KV | T019 | 1982 | 37 | <40 | -38.2497 | 146.5013 | EAST | C2 | MWTS-LY 3 |  | 1 | 1Steel | 66 | 1 | 180010 | 180000 |  | MB | 2013 | 1 | 2013 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 9016.944 | 22366.7987 | 3720.1399 | 25000 | 60103.8826 | 25200 | 2.3851 | Cr3 | 3 | 1 | 1
30338469 | GWACSR | TL-SMSYEX-SMSY052-0000058897 | TOWER T052 SMTS-SYTS 1 500KV | TL-SMSYEX-SMSY052 | HBRA | GW_OPGW | MX5-00409469 | GW-GRAPE | ACSR | GRAPE | 1983 | 1983-06-30 | 38.1684 | 1983 | 36 | 36 | <40 | <40 | 432.5 | 0.4325 | 30431238 | TOWER | TWRSCCT | STRUCTSUSP | H | HB | MX5-00058897 | T052 SMTS-SYTS 1 500KV | T052 | 1983 | 72 | <80 | -37.5483 | 144.8885 | CENTRAL | C1 | SMTS-SYTS 1 |  | L | 1ACSR | 500 | 1 | 180010 | 190010 |  | JOHNHENDERSO | 2013 | 2 | 2013 | 5 | 180010 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 52534676.3791 | 56267.0851 | 3720.1399 | 25000 | 52619663.6042 | 31140 | 1689.7773 | Cr5 | 5 | 1 | 1
30455961 | GWSTEEL | TL-SMTXEX-SMTX014-0000114253 | TOWER T014 SMTS-TTS 2 220KV | TL-SMTXEX-SMTX014 | LBRA | GW_OPGW | MX5-00409771 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1983 | 1983-06-30 | 38.1684 | 1983 | 36 | 36 | <40 | <40 | 304.8 | 0.3048 | 30144458 | TOWER | TWRMCCT | STRUCTSUSP | L |  | MX5-00114253 | T014 SMTS-TTS 2 220KV | T014 | 1983 | 36 | <40 | -37.6713 | 145.0395 | CENTRAL | C1 | SMTS-TTS 2 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | RDAVIN | 2017 | 1 | 2017 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 100000 | 903.9674 | 93570.1399 | 550000 | 744474.1073 | 21945.6 | 33.9236 | Cr5 | 5 | 1 | 4
30143659 | GWACSR | TL-SYKXEX-SYKX105-0000119782 | TOWER T105 SYTS-KTS 500KV | TL-SYKXEX-SYKX105 | LBRA | GW_OPGW | MX5-00409842 | GW-GRAPE | ACSR | GRAPE | 1981 | 1981-06-30 | 40.167 | 1981 | 38 | 38 | <40 | <40 | 322.6 | 0.3226 | 30384843 | TOWER | TWRSCCT | STRUCTSUSP | H | 0 | MX5-00119782 | T105 SYTS-KTS 500KV | T105 | 1981 | 114 | >80 | -37.6788 | 144.7627 | CENTRAL | C1 | SYTS-KTS |  | R | 2ACSR | 500 | 2 | 190010 |  |  |  |  | 3 | 0 | 0 | 190010 | 5 | 3 | 2 | 3 | -1 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 52534676.3791 | 0 | 3720.1399 | 25000 | 52563396.519 | 23227.2 | 2263.0105 | Cr5 | 5 | 1 | 3
30273851 | GWACSR | TL-SYKXEX-SYKX105-0000119782 | TOWER T105 SYTS-KTS 500KV | TL-SYKXEX-SYKX105 | LBRA | GW_OPGW | MX5-00409871 | GW-GRAPE | ACSR | GRAPE | 1981 | 1981-06-30 | 40.167 | 1981 | 38 | 38 | <40 | <40 | 322.6 | 0.3226 | 30384843 | TOWER | TWRSCCT | STRUCTSUSP | H | 0 | MX5-00119782 | T105 SYTS-KTS 500KV | T105 | 1981 | 114 | >80 | -37.6788 | 144.7627 | CENTRAL | C1 | SYTS-KTS |  | L | 1ACSR | 500 | 1 | 180010 | 180010 |  | SQ | 2013 | 3 | 2007 | 5 | 180010 | 5 | 2 | 2 | 3 | -1 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 52534676.3791 | 0 | 3720.1399 | 25000 | 52563396.519 | 23227.2 | 2263.0105 | Cr5 | 5 | 1 | 3
30403232 | GWACSR | TL-SYMLEX-SYML061-0000058291 | TOWER T061 SYTS-MLTS 1 500KV | TL-SYMLEX-SYML061 | HBRA | GW_OPGW | MX5-00410088 | GW-GRAPE | ACSR | GRAPE | 1981 | 1981-06-30 | 40.167 | 1981 | 38 | 38 | <40 | <40 | 360 | 0.36 | 30222825 | TOWER | TWRSCCT | STRUCTSUSP | L | 5A | MX5-00058291 | T061 SYTS-MLTS 1 500KV | T061 | 1981 | 76 | <80 | -37.7933 | 144.5808 | CENTRAL | C1 | SYTS-MLTS 1 |  | L | 1ACSR | 500 | 1 | 180010 | 190000 |  | RDAVIN | 2017 | 2 | 2017 | 5 | 180010 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 164217796.3207 | 0 | 3720.1399 | 25000 | 164246516.4606 | 25920 | 6336.6712 | Cr5 | 5 | 1 | #N/A
30416394 | GWACSR | TL-SYMLEX-SYML038-0000058558 | TOWER T038 SYTS-MLTS 2 500KV | TL-SYMLEX-SYML038 | HBRA | GW_OPGW | MX5-00410377 | GW-GRAPE | ACSR | GRAPE | 1981 | 1981-06-30 | 40.167 | 1981 | 38 | 38 | <40 | <40 | 380 | 0.38 | 30077923 | TOWER | TWRSCCT | STRUCTSUSP | L | 5A | MX5-00058558 | T038 SYTS-MLTS 2 500KV | T038 | 1981 | 76 | <80 | -37.7787 | 144.6777 | CENTRAL | C1 | SYTS-MLTS 2 |  | L | 1ACSR | 500 | 1 | 180010 | 190010 |  | SQUIN | 2017 | 2 | 2017 | 5 | 180010 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 164217796.3207 | 0 | 3720.1399 | 25000 | 164246516.4606 | 27360 | 6003.1622 | Cr5 | 5 | 1 | #N/A
30078672 | GWACSR | TL-SYMLEX-SYML094-0000058670 | TOWER T094 SYTS-MLTS 2 500KV | TL-SYMLEX-SYML094 | HBRA | GW_OPGW | MX5-00410433 | GW-GRAPE | ACSR | GRAPE | 1981 | 1981-06-30 | 40.167 | 1981 | 38 | 38 | <40 | <40 | 360 | 0.36 | 30063525 | TOWER | TWRSCCT | STRUCTSUSP | L | 5A | MX5-00058670 | T094 SYTS-MLTS 2 500KV | T094 | 1981 | 76 | <80 | -37.8557 | 144.4499 | CENTRAL | C1 | SYTS-MLTS 2 |  | L | 1ACSR | 500 | 1 | 180010 | 190000 |  | DCARABOT | 2017 | 2 | 2017 | 5 | 180010 | 5 | 2 | 3 | 2 | 1 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 164217796.3207 | 1.7345 | 3720.1399 | 25000 | 164246518.1951 | 25920 | 6336.6712 | Cr5 | 5 | 1 | #N/A
30359350 | GWSTEEL | TL-CBJLEX-CBJL083-0000087733 | TOWER T083 CBTS-TBTS 1 220KV | TL-CBJLEX-CBJL083 | HBRA | GW_OPGW | MX5-00398215 | GW-19/3 STEEL | Steel | STEEL | 1976 | 1976-06-30 | 45.1663 | 1976 | 43 | 43 | <50 | <50 | 350 | 0.35 | 30434516 | TOWER | TWRMCCT | STRUCTSUSP | L | W | MX5-00087733 | T083 CBTS-TBTS 1 220KV | T083 | 1976 | 86 | >80 | -38.169 | 145.2547 | CENTRAL | C3 | CBTS-TBTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 190010 |  | DB | 2017 | 2 | 2017 | 5 | 190000 | 5 | 1 | 3 | 2 | 1 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 94913.7965 | 362.0888 | 93570.1399 | 550000 | 738846.0252 | 25200 | 29.3193 | Cr5 | 5 | 1 | #N/A
30185745 | GWSTEEL | TL-YPROEX-YPRO337-0000087640 | TOWER T001 ERTS-ROTS 1 220KV | TL-YPROEX-YPRO337 | LBRA | GW_OPGW | MX5-00401236 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1971 | 1971-06-30 | 50.1684 | 1971 | 48 | 48 | <50 | <50 | 183.79 | 0.18379 | 30057597 | TOWER | TWRMCCT | STRUCTSTRN | H | D | MX5-00087640 | T001 ERTS-ROTS 1 220KV | T001 | 1971 | 192 | >80 | -37.9403 | 145.2355 | CENTRAL | C1 | ERTS-ROTS 1 |  | L | 1Steel | 220 | 1 | 180000 | 180000 |  | DB | 2013 | 4 | 2010 | 4 | 180000 | 5 | 4 | 4 | 4 | 0 |  |  |  | 2 | 4 | 0 | Gw-4-0 | 45221268.066 | 525.0517 | 2460565.8044 | 25000 | 47707358.922 | 100000 | 477.0736 | Cr5 | 5 | 1 | 1
30357230 | GWSTEEL | TL-YPROEX-YPRO337-0000087640 | TOWER T001 ERTS-ROTS 1 220KV | TL-YPROEX-YPRO337 | LBRA | GW_OPGW | MX5-00401228 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1971 | 1971-06-30 | 50.1684 | 1971 | 48 | 48 | <50 | <50 | 183.79 | 0.18379 | 30057597 | TOWER | TWRMCCT | STRUCTSTRN | H | D | MX5-00087640 | T001 ERTS-ROTS 1 220KV | T001 | 1971 | 192 | >80 | -37.9403 | 145.2355 | CENTRAL | C1 | ERTS-ROTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | DB | 2013 | 4 | 2010 | 4 | 190000 | 5 | 1 | 4 | 4 | 0 |  |  |  | 2 | 4 | 0 | Gw-4-0 | 45221268.066 | 525.0517 | 2460565.8044 | 25000 | 47707358.922 | 100000 | 477.0736 | Cr5 | 5 | 1 | 1
30367018 | GWSTEEL | TL-KXBLEX-KXBL036-0000058057 | TOWER T036 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL036 | LBRA | GW_OPGW | MX5-00406094 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1973 | 1973-06-30 | 48.167 | 1973 | 46 | 46 | <50 | <50 | 191.4 | 0.1914 | 30039631 | TOWER | TWRMCCT | STRUCTSTRN | H | D | MX5-00058057 | T036 KTS -BLTS 1 220KV | T036 | 1973 | 138 | >80 | -37.8235 | 144.8205 | CENTRAL | C2 | KTS-BLTS 1 |  | L | 1Steel | 220 | 1 | 180000 | 180010 |  | SQUIN | 2019 | 3 | 2019 | 3 | 180000 | 5 | 2 | 3 | 3 | 0 | XC77 |  |  | 2 | 0 | 1 | Gw-0-1 | 19600.0756 | 0 | 11570.1399 | 148000 | 179170.2155 | 13780.8 | 13.0014 | Cr5 | 5 | 1 | 4
30376253 | GWSTEEL | TL-KXBLEX-KXBL036-0000058057 | TOWER T036 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL036 | LBRA | GW_OPGW | MX5-00406046 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1973 | 1973-06-30 | 48.167 | 1973 | 46 | 46 | <50 | <50 | 191.4 | 0.1914 | 30039631 | TOWER | TWRMCCT | STRUCTSTRN | H | D | MX5-00058057 | T036 KTS -BLTS 1 220KV | T036 | 1973 | 138 | >80 | -37.8235 | 144.8205 | CENTRAL | C2 | KTS-BLTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | SQUIN | 2019 | 3 | 2019 | 5 | 190000 | 5 | 1 | 3 | 3 | 0 | XC77 |  |  | 2 | 0 | 1 | Gw-0-1 | 19600.0756 | 0 | 11570.1399 | 148000 | 179170.2155 | 13780.8 | 13.0014 | Cr5 | 5 | 1 | 4
30038862 | GWSTEEL | TL-KXBLEX-KXBL037-0000058059 | TOWER T037 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL037 | LBRA | GW_OPGW | MX5-00406095 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 270.4 | 0.2704 | 30359206 | TOWER | TWRMCCT | STRUCTSTRN | H | FC2 | MX5-00058059 | T037 KTS -BLTS 1 220KV | T037 | 1969 | 150 | >80 | -37.8247 | 144.8222 | CENTRAL | C2 | KTS-BLTS 1 |  | L | 1Steel | 220 | 1 | 180000 | 180010 |  | RDAVIN | 2019 | 3 | 2019 | 2 | 180000 | 5 | 3 | 4 | 3 | 1 | XC77 |  |  | 2 | 5 | 1 | Gw-5-1 | 19600.0756 | 0 | 9206290.8656 | 148000 | 9373890.9411 | 100000 | 93.7389 | Cr5 | 5 | 1 | 4
30218966 | GWSTEEL | TL-KXBLEX-KXBL040-0000058065 | TOWER T040 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL040 | LBRA | GW_OPGW | MX5-00406098 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 284.4 | 0.2844 | 30133750 | TOWER | TWRMCCT | STRUCTSTRN | L | FC3 | MX5-00058065 | T040 KTS -BLTS 1 220KV | T040 | 1969 | 150 | >80 | -37.8249 | 144.8326 | CENTRAL | C2 | KTS-BLTS 1 |  | L | 1Steel | 220 | 1 | 180000 | 180010 |  | DCARABOT | 2019 | 3 | 2019 | 1 | 180000 | 5 | 3 | 4 | 3 | 1 | XC77 |  |  | 2 | 0 | 2 | Gw-0-2 | 19600.0756 | 0 | 93570.1399 | 550000 | 663170.2155 | 20476.8 | 32.3864 | Cr5 | 5 | 1 | 4
30442094 | GWSTEEL | TL-KXBLEX-KXBL040-0000058065 | TOWER T040 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL040 | LBRA | GW_OPGW | MX5-00406050 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 284.4 | 0.2844 | 30133750 | TOWER | TWRMCCT | STRUCTSTRN | L | FC3 | MX5-00058065 | T040 KTS -BLTS 1 220KV | T040 | 1969 | 150 | >80 | -37.8249 | 144.8326 | CENTRAL | C2 | KTS-BLTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 190010 |  | DCARABOT | 2019 | 3 | 2019 | 2 | 190000 | 5 | 1 | 4 | 3 | 1 | XC77 |  |  | 2 | 0 | 2 | Gw-0-2 | 19600.0756 | 0 | 93570.1399 | 550000 | 663170.2155 | 20476.8 | 32.3864 | Cr5 | 5 | 1 | 4
30020159 | GWSTEEL | TL-KXBLEX-KXBL041-0000058067 | TOWER T041 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL041 | LBRA | GW_OPGW | MX5-00406051 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 357.5 | 0.3575 | 30428168 | TOWER | TWRMCCT | STRUCTSTRN | H | FC2 | MX5-00058067 | T041 KTS -BLTS 1 220KV | T041 | 1969 | 150 | >80 | -37.8249 | 144.8358 | CENTRAL | C2 | KTS-BLTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 180010 |  | SQUIN | 2019 | 3 | 2019 | 2 | 190000 | 5 | 3 | 4 | 3 | 1 | XC77 |  |  | 2 | 0 | 2 | Gw-0-2 | 19600.0756 | 0 | 93570.1399 | 550000 | 663170.2155 | 25740 | 25.7642 | Cr5 | 5 | 1 | 4
30197684 | GWSTEEL | TL-KXBLEX-KXBL044-0000058073 | TOWER T044 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL044 | LBRA | GW_OPGW | MX5-00406102 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 320 | 0.32 | 30055200 | TOWER | TWRMCCT | STRUCTSTRN | L | FC3 | MX5-00058073 | T044 KTS -BLTS 1 220KV | T044 | 1969 | 150 | >80 | -37.8245 | 144.8469 | CENTRAL | C2 | KTS-BLTS 1 |  | L | 1Steel | 220 | 1 | 180000 | 180010 |  | SQUIN | 2019 | 3 | 2019 | 1 | 180000 | 5 | 3 | 4 | 3 | 1 | XC77 |  |  | 2 | 3 | 1 | Gw-3-1 | 19600.0756 | 0 | 2292990.7141 | 148000 | 2460590.7897 | 23040 | 106.7965 | Cr5 | 5 | 1 | 4
30056712 | GWSTEEL | TL-KXBLEX-KXBL045-0000058075 | TOWER T045 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL045 | LBRA | GW_OPGW | MX5-00406055 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 322.5 | 0.3225 | 30253207 | TOWER | TWRMCCT | STRUCTSTRN | H | FC2 | MX5-00058075 | T045 KTS -BLTS 1 220KV | T045 | 1969 | 150 | >80 | -37.8242 | 144.8505 | CENTRAL | C2 | KTS-BLTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 180010 |  | SQUIN | 2019 | 3 | 2019 | 2 | 190000 | 5 | 3 | 4 | 3 | 1 | XC77 |  |  | 2 | 5 | 1 | Gw-5-1 | 19600.0756 | 0 | 9206290.8656 | 148000 | 9373890.9411 | 100000 | 93.7389 | Cr5 | 5 | 1 | 4
30135880 | GWSTEEL | TL-KXBLEX-KXBL046-0000058077 | TOWER T046 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL046 | LBRA | GW_OPGW | MX5-00406104 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 282.2 | 0.2822 | 30017181 | TOWER | TWRMCCT | STRUCTSTRN | L | FC3 | MX5-00058077 | T046 KTS -BLTS 1 220KV | T046 | 1969 | 150 | >80 | -37.825 | 144.854 | CENTRAL | C2 | KTS-BLTS 1 |  | L | 1Steel | 220 | 1 | 180000 |  |  |  |  | 3 | 0 | 0 | 180000 | 5 | 3 | 2 | 3 | -1 | XC77 |  |  | 2 | 0 | 2 | Gw-0-2 | 19600.0756 | 0 | 93570.1399 | 550000 | 663170.2155 | 20318.4 | 32.6389 | Cr5 | 5 | 1 | 4
30316551 | GWSTEEL | TL-KXBLEX-KXBL046-0000058077 | TOWER T046 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL046 | LBRA | GW_OPGW | MX5-00406056 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 282.2 | 0.2822 | 30017181 | TOWER | TWRMCCT | STRUCTSTRN | L | FC3 | MX5-00058077 | T046 KTS -BLTS 1 220KV | T046 | 1969 | 150 | >80 | -37.825 | 144.854 | CENTRAL | C2 | KTS-BLTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 180000 |  | RDAVIN | 2019 | 3 | 2019 | 5 | 190000 | 5 | 2 | 2 | 3 | -1 | XC77 |  |  | 2 | 0 | 2 | Gw-0-2 | 19600.0756 | 0 | 93570.1399 | 550000 | 663170.2155 | 20318.4 | 32.6389 | Cr5 | 5 | 1 | 4
30055331 | GWSTEEL | TL-KXBLEX-KXBL047-0000058079 | TOWER T047 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL047 | LBRA | GW_OPGW | MX5-00406057 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 210 | 0.21 | 30304639 | TOWER | TWRMCCT | STRUCTSTRN | H | FC2 | MX5-00058079 | T047 KTS -BLTS 1 220KV | T047 | 1969 | 150 | >80 | -37.8249 | 144.8573 | CENTRAL | C2 | KTS-BLTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 180000 |  | SQUIN | 2019 | 3 | 2019 | 5 | 190000 | 5 | 2 | 2 | 3 | -1 | XC77 |  |  | 2 | 0 | 2 | Gw-0-2 | 19600.0756 | 0 | 93570.1399 | 550000 | 663170.2155 | 15120 | 43.8605 | Cr5 | 5 | 1 | 4
30364230 | GWSTEEL | TL-KXBLEX-KXBL047-0000058079 | TOWER T047 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL047 | LBRA | GW_OPGW | MX5-00406105 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 210 | 0.21 | 30304639 | TOWER | TWRMCCT | STRUCTSTRN | H | FC2 | MX5-00058079 | T047 KTS -BLTS 1 220KV | T047 | 1969 | 150 | >80 | -37.8249 | 144.8573 | CENTRAL | C2 | KTS-BLTS 1 |  | L | 1Steel | 220 | 1 | 180000 | 190000 |  | SQUIN | 2019 | 3 | 2019 | 5 | 180000 | 5 | 1 | 2 | 3 | -1 | XC77 |  |  | 2 | 0 | 2 | Gw-0-2 | 19600.0756 | 0 | 93570.1399 | 550000 | 663170.2155 | 15120 | 43.8605 | Cr5 | 5 | 1 | 4
30068300 | GWSTEEL | TL-KXBLEX-KXBL048-0000058081 | TOWER T048 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL048 | LBRA | GW_OPGW | MX5-00406106 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 221.3 | 0.2213 | 30015667 | TOWER | TWRMCCT | STRUCTSTRN | H | TF | MX5-00058081 | T048 KTS -BLTS 1 220KV | T048 | 1969 | 150 | >80 | -37.8248 | 144.8596 | CENTRAL | C2 | KTS-BLTS 1 |  | L | 1Steel | 220 | 1 | 180000 |  |  |  |  | 3 | 0 | 0 | 180000 | 5 | 3 | 2 | 3 | -1 | XC77 |  |  | 2 | 0 | 2 | Gw-0-2 | 19600.0756 | 0 | 93570.1399 | 550000 | 663170.2155 | 15933.6 | 41.6209 | Cr5 | 5 | 1 | 4
30265296 | GWSTEEL | TL-KXBLEX-KXBL048-0000058081 | TOWER T048 KTS -BLTS 1 220KV | TL-KXBLEX-KXBL048 | LBRA | GW_OPGW | MX5-00406058 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 221.3 | 0.2213 | 30015667 | TOWER | TWRMCCT | STRUCTSTRN | H | TF | MX5-00058081 | T048 KTS -BLTS 1 220KV | T048 | 1969 | 150 | >80 | -37.8248 | 144.8596 | CENTRAL | C2 | KTS-BLTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 180000 |  | RDAVIN | 2019 | 3 | 2019 | 5 | 190000 | 5 | 2 | 2 | 3 | -1 | XC77 |  |  | 2 | 0 | 2 | Gw-0-2 | 19600.0756 | 0 | 93570.1399 | 550000 | 663170.2155 | 15933.6 | 41.6209 | Cr5 | 5 | 1 | 4
30014308 | GWIRE | TL-SMSYEX-SMSY076-0000059152 | TOWER T076 SMTS-SYTS 2 500KV | TL-SMSYEX-SMSY076 | HBRA | GW_OPGW | MX5-00409599 | GW-BRAHMA | ACSR | BRAHMA | 1969 | 1969-06-30 | 52.167 | 1969 | 50 | 50 | <50 | <50 | 288 | 0.288 | 30406208 | TOWER | TWRSCCT | STRUCTSUSP | L | 5A | MX5-00059152 | T076 SMTS-SYTS 2 500KV | T076 | 1969 | 100 | >80 | -37.5904 | 144.7982 | CENTRAL | C1 | SMTS-SYTS 2 |  | R | 2ACSR | 500 | 2 | 190010 | 190000 |  | RDAVIN | 2019 | 2 | 2019 | 5 | 190010 | 5 | 2 | 3 | 2 | 1 |  |  |  | 2 | 2 | 0 | Gw-2-0 | 52534676.3791 | 33.4174 | 1575956.0551 | 25000 | 54135665.8515 | 20736 | 2610.7092 | Cr5 | 5 | 1 | #N/A
30021555 | GWSTEEL | TL-TXKXEX-TXKX030-0000058390 | TOWER T030 TTS -KTS 1 220KV | TL-TXKXEX-TXKX030 | LBRA | GW_OPGW | MX5-00410773 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1974 | 1974-06-30 | 47.1677 | 1974 | 45 | 45 | <50 | <50 | 223.8 | 0.2238 | 30190961 | TOWER | TWRMCCT | STRUCTSTRN | L | T | MX5-00058390 | T030 TTS -KTS 1 220KV | T030 | 1974 | 90 | >80 | -37.6953 | 144.9147 | CENTRAL | C1 | TTS -KTS 1 |  | 1 | 1Steel | 220 | 1 | 180000 | 180010 |  | BLAWTY | 2018 | 2 | 2018 | 2 | 180010 | 5 | 2 | 2 | 2 | 0 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 10545.3701 | 442.3958 | 93570.1399 | 550000 | 654557.9058 | 16113.6 | 40.6215 | Cr5 | 5 | 1 | #N/A
30003797 | GWSTEEL | TL-YPROEX-YPRO332-0000065650 | TOWER T332 YPS -ROTS 7 220KV | TL-YPROEX-YPRO332 | HBRA | GW_OPGW | MX5-00411637 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1962 | 1962-06-30 | 59.1677 | 1962 | 57 | 57 | <60 | <60 | 174.4 | 0.1744 | 30097224 | TOWER | TWRMCCT | STRUCTSUSP | H | Y +0 | MX5-00065650 | T332 YPS -ROTS 7 220KV | T332 | 1962 | 57 | <60 | -37.9469 | 145.25 | CENTRAL | C1 | YPS -ROTS 7 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | DCARABOT | 2017 | 1 | 2017 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 14883480.4897 | 1889.5112 | 3720.1399 | 25000 | 14914090.1409 | 12556.8 | 1187.7302 | Cr5 | 5 | 1 | 2
30065054 | GWSTEEL | TL-YPROEX-YPRO330-0000065646 | TOWER T330 YPS -ROTS 7 220KV | TL-YPROEX-YPRO330 | HBRA | GW_OPGW | MX5-00411635 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1962 | 1962-06-30 | 59.1677 | 1962 | 57 | 57 | <60 | <60 | 389.3 | 0.3893 | 30225078 | TOWER | TWRMCCT | STRUCTSUSP | H | Y +5 | MX5-00065646 | T330 YPS -ROTS 7 220KV | T330 | 1962 | 57 | <60 | -37.9524 | 145.2583 | CENTRAL | C1 | YPS -ROTS 7 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | DCARABOT | 2017 | 1 | 2017 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 14883480.4897 | 1879.3699 | 3720.1399 | 25000 | 14914079.9996 | 28029.6 | 532.0832 | Cr5 | 5 | 1 | 2
30109702 | GWSTEEL | TL-HWHWEX-HWHW003-0000084371 | TOWER T003 HWPS-HWTS 2 220KV | TL-HWHWEX-HWHW003 | HBRA | GW_OPGW | MX5-00401975 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1968 | 1968-06-30 | 53.1663 | 1968 | 51 | 51 | <60 | <60 | 341.38 | 0.34138 | 30178078 | TOWER | TWRMCCT | STRUCTSTRN | H | KH | MX5-00084371 | T003 HWPS-HWTS 2 220KV | T003 | 1968 | 102 | >80 | -38.2806 | 146.3996 | EAST | C2 | HWPS-HWTS 2 |  | R | 2Steel | 220 | 2 | 190000 | 190010 |  | MB | 2017 | 2 | 2017 | 5 | 190000 | 5 | 1 | 3 | 2 | 1 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 50000 | 8409.9004 | 3720.1399 | 25000 | 87130.0403 | 24579.36 | 3.5448 | Cr4 | 4 | 1 | 4
30145065 | GWSTEEL | TL-HWMWEX-HWMW010-0000084448 | TOWER T010 HWPS-MWTS 220KV | TL-HWMWEX-HWMW010 | HBRA | GW_OPGW | MX5-00402075 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1965 | 1965-06-30 | 56.167 | 1965 | 54 | 54 | <60 | <60 | 168.1 | 0.1681 | 30325253 | TOWER | TWRMCCT | STRUCTSTRN | H | W | MX5-00084448 | T010 HWPS-MWTS 220KV | T010 | 1965 | 108 | >80 | -38.2566 | 146.4108 | EAST | C2 | HWPS-MWTS |  | L | 1Steel | 220 | 1 | 180000 | 190000 |  | RSTIRLING | 2017 | 2 | 2017 | 5 | 180000 | 5 | 2 | 3 | 2 | 1 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 26897.3194 | 5811.0827 | 3720.1399 | 25000 | 61428.542 | 12103.2 | 5.0754 | Cr4 | 4 | 1 | 2
30033487 | GWSTEEL | TL-HWMWEX-HWMW011-0000084449 | TOWER T011 HWPS-MWTS 220KV | TL-HWMWEX-HWMW011 | HBRA | GW_OPGW | MX5-00402060 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1965 | 1965-06-30 | 56.167 | 1965 | 54 | 54 | <60 | <60 | 143 | 0.143 | 30145902 | TOWER | TWRMCCT | STRUCTSTRN | H | W | MX5-00084449 | T011 HWPS-MWTS 220KV | T011 | 1965 | 108 | >80 | -38.2566 | 146.4127 | EAST | C2 | HWPS-MWTS |  | R | 2Steel | 220 | 2 | 190000 | 180010 |  | RSTIRLING | 2017 | 2 | 2017 | 5 | 190000 | 5 | 2 | 3 | 2 | 1 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 26897.3194 | 8872.8614 | 3720.1399 | 25000 | 64490.3208 | 10296 | 6.2636 | Cr4 | 4 | 1 | 2
30072416 | GWSTEEL | TL-YPROEX-YPRO332-0000101043 | TOWER T332 HWPS-ROTS 1 220KV | TL-YPROEX-YPRO332 | HBRA | GW_OPGW | MX5-00402222 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1966 | 1966-06-30 | 55.1677 | 1966 | 53 | 53 | <60 | <60 | 174.3 | 0.1743 | 30058330 | TOWER | TWRMCCT | STRUCTSUSP | H | SSB | MX5-00101043 | T332 HWPS-ROTS 1 220KV | T332 | 1966 | 53 | <60 | -37.9471 | 145.2497 | CENTRAL | C1 | HWPS-ROTS 1 |  | 1 | 1Steel | 220 | 1 | 180000 | 190010 |  | KM AJ | 2017 | 1 | 2017 | 5 | 180000 | 5 | 1 | 3 | 1 | 2 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 14883480.4897 | 1889.5112 | 3720.1399 | 25000 | 14914090.1409 | 12549.6 | 1188.4116 | Cr5 | 5 | 1 | #N/A
30211660 | GWSTEEL | TL-YPROEX-YPRO341-0000101086 | TOWER T341 HWPS-ROTS 1 220KV | TL-YPROEX-YPRO341 | LBRA | GW_OPGW | MX5-00402240 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1963 | 1963-06-30 | 58.1684 | 1963 | 56 | 56 | <60 | <60 | 153.7 | 0.1537 | 30163266 | TOWER | TWRMCCT | STRUCTSUSP | L |  | MX5-00101086 | T341 HWPS-ROTS 1 220KV | T341 | 1963 | 112 | >80 | -37.9308 | 145.2305 | CENTRAL | C1 | HWPS-ROTS 1 |  | L | 1Steel | 220 | 1 | 180000 | 190010 |  | DMOORE | 2014 | 2 | 2014 | 5 | 180000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 14883480.4897 | 552.1646 | 11570.1399 | 148000 | 15043602.7943 | 11066.4 | 1359.3945 | Cr5 | 5 | 1 | #N/A
30449051 | GWSTEEL | TL-HWYPEX-HWYP008-0000085223 | TOWER T008 HWPS-YPS 1 220KV | TL-HWYPEX-HWYP008 | HBRA | GW_OPGW | MX5-00402485 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1964 | 1964-06-30 | 57.1663 | 1964 | 55 | 55 | <60 | <60 | 371.25 | 0.37125 | 30315611 | TOWER | TWRMCCT | STRUCTSTRN | L | K | MX5-00085223 | T008 HWPS-YPS 1 220KV | T008 | 1964 | 110 | >80 | -38.263 | 146.4001 | EAST | C2 | HWPS-YPS 1 |  | L | 1Steel | 220 | 1 | 180000 | 190000 |  | RS | 2014 | 2 | 2014 | 5 | 180000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 63164.135 | 2792.5471 | 3720.1399 | 25000 | 94676.8221 | 26730 | 3.542 | Cr4 | 4 | 1 | 3
30358659 | GWSTEEL | TL-HWYPEX-HWYP012-0000085227 | TOWER T012 HWPS-YPS 1 220KV | TL-HWYPEX-HWYP012 | HBRA | GW_OPGW | MX5-00402466 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1962 | 1962-06-30 | 59.1677 | 1962 | 57 | 57 | <60 | <60 | 368.81 | 0.36881 | 30303744 | TOWER | TWRMCCT | STRUCTSTRN | H | W | MX5-00085227 | T012 HWPS-YPS 1 220KV | T012 | 1962 | 114 | >80 | -38.2536 | 146.4091 | EAST | C2 | HWPS-YPS 1 |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | RS | 2014 | 2 | 2014 | 5 | 190000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 63164.135 | 4676.1543 | 3720.1399 | 25000 | 96560.4292 | 26554.32 | 3.6363 | Cr4 | 4 | 1 | 3
30344690 | GWSTEEL | TL-KXGXEX-KXGX001-0000119401 | TOWER T001AKTS -GTS 1 220KV | TL-KXGXEX-KXGX001 | LBRA | GW_OPGW | MX5-00406135 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1967 | 1967-06-30 | 54.1684 | 1967 | 52 | 52 | <60 | <60 | 69.782 | 0.069782 | 30135144 | TOWER | TWRMCCT | STRUCTSTRN | H |  | MX5-00119401 | T001AKTS -GTS 1 220KV | T001A | 1967 | 104 | >80 | -37.7371 | 144.8464 | CENTRAL | C2 | KTS-GTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 180000 |  | SQUIN | 2019 | 2 | 2019 | 2 | 190000 | 5 | 2 | 2 | 2 | 0 | XC77 |  |  | 2 | 0 | 0 | Gw-0-0 | 21820.9411 | 0 | 3720.1399 | 25000 | 50541.081 | 5024.304 | 10.0593 | Cr5 | 5 | 1 | #N/A
30186409 | GWSTEEL | TL-YPROEX-YPRO328-0000065642 | TOWER T328 YPS -ROTS 7 220KV | TL-YPROEX-YPRO328 | HBRA | GW_OPGW | MX5-00411633 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1962 | 1962-06-30 | 59.1677 | 1962 | 57 | 57 | <60 | <60 | 515 | 0.515 | 30182114 | TOWER | TWRMCCT | STRUCTSUSP | L | X +15 | MX5-00065642 | T328 YPS -ROTS 7 220KV | T328 | 1962 | 57 | <60 | -37.9567 | 145.2646 | CENTRAL | C1 | YPS -ROTS 7 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | DCARABOT | 2017 | 1 | 2017 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 2 | 1 | Gw-2-1 | 14883480.4897 | 1405.2085 | 1583806.0551 | 148000 | 16616691.7533 | 37080 | 448.1308 | Cr5 | 5 | 1 | 2
30169352 | GWSTEEL | TL-YPROEX-YPRO322-0000065630 | TOWER T322 YPS -ROTS 7 220KV | TL-YPROEX-YPRO322 | HBRA | GW_OPGW | MX5-00411627 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1962 | 1962-06-30 | 59.1677 | 1962 | 57 | 57 | <60 | <60 | 259.1 | 0.2591 | 30447976 | TOWER | TWRMCCT | STRUCTSUSP | L | X +0 | MX5-00065630 | T322 YPS -ROTS 7 220KV | T322 | 1962 | 57 | <60 | -37.9682 | 145.2817 | CENTRAL | C1 | YPS -ROTS 7 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | DCARABOT | 2017 | 1 | 2017 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 1 | 2 | Gw-1-2 | 14883480.4897 | 1435.1794 | 106635.4606 | 550000 | 15541551.1297 | 18655.2 | 833.0949 | Cr5 | 5 | 1 | 2
30058733 | GWSTEEL | TL-YPROEX-YPRO168-0000086060 | TOWER T168 YPS -ROTS 7 220KV | TL-YPROEX-YPRO168 | HBRA | GW_OPGW | MX5-00411862 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1962 | 1962-06-30 | 59.1677 | 1962 | 57 | 57 | <60 | <60 | 347.5 | 0.3475 | 30251738 | TOWER | TWRMCCT | STRUCTSTRN | L | K +15 | MX5-00086060 | T168 YPS -ROTS 7 220KV | T168 | 1962 | 57 | <60 | -38.0822 | 145.7702 | EAST | C1 | YPS -ROTS 7 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | DV | 2018 | 1 | 2018 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 14883480.4897 | 942.4152 | 3720.1399 | 25000 | 14913143.0448 | 25020 | 596.0489 | Cr5 | 5 | 1 | 2
30342963 | GWSTEEL | TL-YPROEX-YPRO167-0000086059 | TOWER T167 YPS -ROTS 7 220KV | TL-YPROEX-YPRO167 | HBRA | GW_OPGW | MX5-00411861 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1962 | 1962-06-30 | 59.1677 | 1962 | 57 | 57 | <60 | <60 | 322.8 | 0.3228 | 30110484 | TOWER | TWRMCCT | STRUCTSUSP | H | Y +15 | MX5-00086059 | T167 YPS -ROTS 7 220KV | T167 | 1962 | 57 | <60 | -38.0828 | 145.7738 | EAST | C1 | YPS -ROTS 7 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | DV | 2018 | 1 | 2018 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 3 | 1 | Gw-3-1 | 14883480.4897 | 1225.8994 | 2292990.7141 | 148000 | 17325697.1032 | 23241.6 | 745.4606 | Cr5 | 5 | 1 | 2
30376675 | GWSTEEL | TL-YPROEX-YPRO339-0000065282 | TOWER T339 YPS -ROTS 5 220KV | TL-YPROEX-YPRO339 | LBRA | GW_OPGW | MX5-00411547 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1962 | 1962-06-30 | 59.1677 | 1962 | 57 | 57 | <60 | <60 | 134 | 0.134 | 30368857 | TOWER | TWRMCCT | STRUCTSTRN | H | W +10 | MX5-00065282 | T339 YPS -ROTS 5 220KV | T339 | 1962 | 114 | >80 | -37.9335 | 145.2302 | CENTRAL | C1 | YPS -ROTS 5 |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | GK | 2014 | 2 | 2014 | 5 | 190000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 14883480.4897 | 550.2085 | 11570.1399 | 148000 | 15043600.8381 | 9648 | 1559.2455 | Cr5 | 5 | 1 | #N/A
30395508 | GWSTEEL | TL-RORXEX-RORX381-0000060952 | TOWER T381 ROTS-RTS 1 220KV | TL-RORXEX-RORX381 | LBRA | GW_OPGW | MX5-00408622 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1965 | 1965-06-30 | 56.167 | 1965 | 54 | 54 | <60 | <60 | 262.6 | 0.2626 | 30102845 | TOWER | TWRMCCT | STRUCTSUSP | L | DX +40 | MX5-00060952 | T381 ROTS-RTS 1 220KV | T381 | 1965 | 108 | >80 | -37.8857 | 145.1045 | CENTRAL | C1 | ROTS-RTS 1 |  | L | 1Steel | 220 | 1 | 180000 | 190000 |  | RB | 2015 | 2 | 2015 | 5 | 180000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 9480373.476 | 0 | 11570.1399 | 148000 | 9639943.6159 | 18907.2 | 509.8557 | Cr5 | 5 | 1 | 3
30289371 | GWSTEEL | TL-RORXEX-RORX416-0000060987 | TOWER T416 ROTS-RTS 1 220KV | TL-RORXEX-RORX416 | LBRA | GW_OPGW | MX5-00408569 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1964 | 1964-06-30 | 57.1663 | 1964 | 55 | 55 | <60 | <60 | 298.8 | 0.2988 | 30252938 | TOWER | TWRMCCT | STRUCTSTRN | H | HS +35 | MX5-00060987 | T416 ROTS-RTS 1 220KV | T416 | 1964 | 110 | >80 | -37.8374 | 145.03 | CENTRAL | C1 | ROTS-RTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | RB | 2015 | 2 | 2015 | 5 | 190000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 9480373.476 | 0 | 11570.1399 | 148000 | 9639943.6159 | 21513.6 | 448.086 | Cr5 | 5 | 1 | 3
30426169 | GWSTEEL | TL-ROSVEX-ROSV007-0000061087 | TOWER T007 ROTS-SVTS 1 220KV | TL-ROSVEX-ROSV007 | LBRA | GW_OPGW | MX5-00408952 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1964 | 1964-06-30 | 57.1663 | 1964 | 55 | 55 | <60 | <60 | 257.3 | 0.2573 | 30035881 | TOWER | TWRMCCT | STRUCTSUSP | L | DX | MX5-00061087 | T007 ROTS-SVTS 1 220KV | T007 | 1964 | 110 | >80 | -37.931 | 145.2037 | CENTRAL | C1 | ROTS-SVTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | GK | 2017 | 2 | 2017 | 5 | 190000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 92665206.7412 | 550.2085 | 11570.1399 | 148000 | 92825327.0896 | 18525.6 | 5010.6516 | Cr5 | 5 | 1 | #N/A
30301126 | GWSTEEL | TL-ROSVEX-ROSV009-0000061089 | TOWER T009 ROTS-SVTS 1 220KV | TL-ROSVEX-ROSV009 | LBRA | GW_OPGW | MX5-00408954 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1964 | 1964-06-30 | 57.1663 | 1964 | 55 | 55 | <60 | <60 | 277.5 | 0.2775 | 30043787 | TOWER | TWRMCCT | STRUCTSUSP | L | DX | MX5-00061089 | T009 ROTS-SVTS 1 220KV | T009 | 1964 | 110 | >80 | -37.9307 | 145.1974 | CENTRAL | C1 | ROTS-SVTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | GK | 2017 | 2 | 2017 | 5 | 190000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 92665206.7412 | 550.2085 | 11570.1399 | 148000 | 92825327.0896 | 19980 | 4645.9123 | Cr5 | 5 | 1 | #N/A
30381693 | GWSTEEL | TL-TSTXEX-TSTX445-0000065024 | TOWER T445 TSTS-TTS 220KV | TL-TSTXEX-TSTX445 | LBRA | GW_OPGW | MX5-00410694 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1965 | 1965-06-30 | 56.167 | 1965 | 54 | 54 | <60 | <60 | 360.27 | 0.36027 | 30208885 | TOWER | TWRMCCT | STRUCTSTRN | L | K | MX5-00065024 | T445 TSTS-TTS 220KV | T445 | 1965 | 108 | >80 | -37.7108 | 145.0832 | CENTRAL | C1 | TSTS-TTS |  | L | 1Steel | 220 | 1 | 180000 | 190000 |  | SQUIN | 2016 | 2 | 2016 | 5 | 180000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 1 | 2 | Gw-1-2 | 6131379.2611 | 3039.8395 | 106635.4606 | 550000 | 6791054.5613 | 25939.44 | 261.8042 | Cr5 | 5 | 1 | #N/A
30402156 | GWSTEEL | TL-TSTXEX-TSTX447-0000065028 | TOWER T447 TSTS-TTS 220KV | TL-TSTXEX-TSTX447 | LBRA | GW_OPGW | MX5-00410656 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1965 | 1965-06-30 | 56.167 | 1965 | 54 | 54 | <60 | <60 | 291.39 | 0.29139 | 30207066 | TOWER | TWRMCCT | STRUCTSTRN | H | W | MX5-00065028 | T447 TSTS-TTS 220KV | T447 | 1965 | 108 | >80 | -37.7066 | 145.0775 | CENTRAL | C1 | TSTS-TTS |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | SQUIN | 2016 | 2 | 2016 | 5 | 190000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 6131379.2611 | 1555.7216 | 11570.1399 | 148000 | 6292505.1227 | 20980.08 | 299.9276 | Cr5 | 5 | 1 | #N/A
30207104 | GWSTEEL | TL-TSTXEX-TSTX448-0000065030 | TOWER T448 TSTS-TTS 220KV | TL-TSTXEX-TSTX448 | LBRA | GW_OPGW | MX5-00410657 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1965 | 1965-06-30 | 56.167 | 1965 | 54 | 54 | <60 | <60 | 216.71 | 0.21671 | 30141224 | TOWER | TWRMCCT | STRUCTSUSP | L | X | MX5-00065030 | T448 TSTS-TTS 220KV | T448 | 1965 | 108 | >80 | -37.706 | 145.0744 | CENTRAL | C1 | TSTS-TTS |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | SQUIN | 2016 | 2 | 2016 | 5 | 190000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 6131379.2611 | 2981.7724 | 93570.1399 | 550000 | 6777931.1734 | 15603.12 | 434.3959 | Cr5 | 5 | 1 | #N/A
30348354 | GWSTEEL | TL-TSTXEX-TSTX449-0000065032 | TOWER T449 TSTS-TTS 220KV | TL-TSTXEX-TSTX449 | LBRA | GW_OPGW | MX5-00410658 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1965 | 1965-06-30 | 56.167 | 1965 | 54 | 54 | <60 | <60 | 222.2 | 0.2222 | 30188639 | TOWER | TWRMCCT | STRUCTSUSP | L | X | MX5-00065032 | T449 TSTS-TTS 220KV | T449 | 1965 | 108 | >80 | -37.7055 | 145.072 | CENTRAL | C1 | TSTS-TTS |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | SQUIN | 2016 | 2 | 2016 | 5 | 190000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 6131379.2611 | 3431.4005 | 93570.1399 | 550000 | 6778380.8015 | 15998.4 | 423.6912 | Cr5 | 5 | 1 | #N/A
30142140 | GWSTEEL | TL-TSTXEX-TSTX467-0000065068 | TOWER T467 TSTS-TTS 220KV | TL-TSTXEX-TSTX467 | LBRA | GW_OPGW | MX5-00410674 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1965 | 1965-06-30 | 56.167 | 1965 | 54 | 54 | <60 | <60 | 114.91 | 0.11491 | 30185423 | TOWER | TWRMCCT | STRUCTSTRN | H | W | MX5-00065068 | T467 TSTS-TTS 220KV | T467 | 1965 | 108 | >80 | -37.693 | 145.0125 | CENTRAL | C1 | TSTS-TTS |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | SQUIN | 2016 | 2 | 2016 | 5 | 190000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 4 | 2 | Gw-4-2 | 6131379.2611 | 204.5375 | 2550415.8044 | 550000 | 9231999.603 | 100000 | 92.32 | Cr5 | 5 | 1 | #N/A
30035310 | GWSTEEL | TL-SMKXEX-SMKX066-0000058461 | TOWER T033 TTS -KTS 1 220KV | TL-SMKXEX-SMKX066 | LBRA | GW_OPGW | MX5-00410782 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1966 | 1966-06-30 | 55.1677 | 1966 | 53 | 53 | <60 | <60 | 225 | 0.225 | 30224771 | TOWER | TWRMCCT | STRUCTSTRN | H | W | MX5-00058461 | T033 TTS -KTS 1 220KV | T033 | 1966 | 106 | >80 | -37.6963 | 144.9021 | CENTRAL | C1 | TTS -KTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 180010 |  | SQUIN | 2018 | 2 | 2018 | 2 | 190000 | 5 | 2 | 2 | 2 | 0 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 10545.3701 | 0 | 11570.1399 | 148000 | 170115.51 | 16200 | 10.501 | Cr5 | 5 | 1 | #N/A
30250490 | GWSTEEL | TL-SMKXEX-SMKX067-0000058463 | TOWER T034 TTS -KTS 1 220KV | TL-SMKXEX-SMKX067 | LBRA | GW_OPGW | MX5-00410783 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1966 | 1966-06-30 | 55.1677 | 1966 | 53 | 53 | <60 | <60 | 273.1 | 0.2731 | 30243371 | TOWER | TWRMCCT | STRUCTSUSP | L | X | MX5-00058463 | T034 TTS -KTS 1 220KV | T034 | 1966 | 106 | >80 | -37.6977 | 144.9003 | CENTRAL | C1 | TTS -KTS 1 |  | R | 2Steel | 220 | 2 | 190000 | 190010 |  | BLAWTY | 2018 | 2 | 2018 | 5 | 190000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 10545.3701 | 0 | 11570.1399 | 148000 | 170115.51 | 19663.2 | 8.6515 | Cr4 | 4 | 1 | #N/A
30027840 | GWSTEEL | TL-SMKXEX-SMKX088-0000058507 | TOWER T056 TTS -KTS 1 220KV | TL-SMKXEX-SMKX088 | LBRA | GW_OPGW | MX5-00410805 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1966 | 1966-06-30 | 55.1677 | 1966 | 53 | 53 | <60 | <60 | 340.8 | 0.3408 | 30120819 | TOWER | TWRMCCT | STRUCTSTRN | L | K | MX5-00058507 | T056 TTS -KTS 1 220KV | T056 | 1966 | 53 | <60 | -37.7361 | 144.8503 | CENTRAL | C1 | TTS -KTS 1 |  | R | 1Steel | 220 | 1 | 180000 | 190000 |  | SQUIN | 2018 | 1 | 2018 | 5 | 180000 | 5 | 1 | 2 | 1 | 1 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 10545.3701 | 0 | 11570.1399 | 148000 | 170115.51 | 24537.6 | 6.9329 | Cr4 | 4 | 1 | #N/A
30312179 | GWSTEEL | TL-TXKXEX-TXKX029-0000058388 | TOWER T029 TTS -KTS 1 220KV | TL-TXKXEX-TXKX029 | LBRA | GW_OPGW | MX5-00410772 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1961 | 1961-06-30 | 60.167 | 1961 | 58 | 58 | <60 | <60 | 123.4 | 0.1234 | 30115640 | TOWER | TWRMCCT | STRUCTSTRN | L | L | MX5-00058388 | T029 TTS -KTS 1 220KV | T029 | 1961 | 116 | >80 | -37.6952 | 144.9161 | CENTRAL | C1 | TTS -KTS 1 |  | 1 | 1Steel | 220 | 1 | 180000 | 190010 |  | BLAWTY | 2018 | 2 | 2018 | 5 | 180000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 3 | 2 | Gw-3-2 | 10545.3701 | 442.3958 | 2374990.7141 | 550000 | 2935978.48 | 8884.8 | 330.4496 | Cr5 | 5 | 1 | #N/A
30190158 | GWSTEEL | TL-TXKXEX-TXKX031-0000058392 | TOWER T031 TTS -KTS 1 220KV | TL-TXKXEX-TXKX031 | LBRA | GW_OPGW | MX5-00410774 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1961 | 1961-06-30 | 60.167 | 1961 | 58 | 58 | <60 | <60 | 189.6 | 0.1896 | 30240067 | TOWER | TWRMCCT | STRUCTSUSP | L | S | MX5-00058392 | T031 TTS -KTS 1 220KV | T031 | 1961 | 116 | >80 | -37.6955 | 144.9122 | CENTRAL | C1 | TTS -KTS 1 |  | 1 | 1Steel | 220 | 1 | 180000 | 190010 |  | BLAWTY | 2018 | 2 | 2018 | 5 | 180000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 10545.3701 | 442.3958 | 93570.1399 | 550000 | 654557.9058 | 13651.2 | 47.9487 | Cr5 | 5 | 1 | #N/A
30231195 | GWSTEEL | TL-KXGXEX-KXGX132-0000057567 | TOWER T132 DPTS-GTS 2 220KV | TL-KXGXEX-KXGX132 | HBRA | GW_OPGW | MX5-00406268 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1957 | 1957-06-30 | 64.167 | 1957 | 62 | 62 | <70 | <70 | 414.5 | 0.4145 | 30404463 | TOWER | TWRSCCT | STRUCTSUSP | L | P | MX5-00057567 | T132 DPTS-GTS 2 220KV | T132 | 1957 | 62 | <70 | -37.9614 | 144.3771 | CENTRAL | C2 | DPTS-GTS 2 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | BL | 2013 | 1 | 2009 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 21820.9411 | 13.9528 | 3720.1399 | 25000 | 50555.0338 | 29844 | 1.694 | Cr3 | 3 | 1 | #N/A
30142317 | GWSTEEL | TL-YPROEX-YPRO330-0000065264 | TOWER T330 YPS -ROTS 5 220KV | TL-YPROEX-YPRO330 | HBRA | GW_OPGW | MX5-00411476 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1953 | 1953-06-30 | 68.167 | 1953 | 66 | 66 | <70 | <70 | 376.4 | 0.3764 | 30135352 | TOWER | TWRMCCT | STRUCTSUSP | L | J&W | MX5-00065264 | T330 YPS -ROTS 5 220KV | T330 | 1953 | 66 | <70 | -37.9526 | 145.2581 | CENTRAL | C1 | YPS -ROTS 5 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | SQUIN | 2017 | 1 | 2017 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 14883480.4897 | 1879.3699 | 3720.1399 | 25000 | 14914079.9996 | 27100.8 | 550.3188 | Cr5 | 5 | 1 | #N/A
30319977 | GWSTEEL | TL-YPROEX-YPRO328-0000065260 | TOWER T328 YPS -ROTS 5 220KV | TL-YPROEX-YPRO328 | HBRA | GW_OPGW | MX5-00411474 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1953 | 1953-06-30 | 68.167 | 1953 | 66 | 66 | <70 | <70 | 514.2 | 0.5142 | 30217748 | TOWER | TWRMCCT | STRUCTSUSP | L | J&W | MX5-00065260 | T328 YPS -ROTS 5 220KV | T328 | 1953 | 66 | <70 | -37.9569 | 145.2645 | CENTRAL | C1 | YPS -ROTS 5 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | SQUIN | 2017 | 1 | 2017 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 2 | 1 | Gw-2-1 | 14883480.4897 | 1325.8243 | 1583806.0551 | 148000 | 16616612.3691 | 37022.4 | 448.8259 | Cr5 | 5 | 1 | #N/A
30333159 | GWSTEEL | TL-YPROEX-YPRO326-0000065256 | TOWER T326 YPS -ROTS 5 220KV | TL-YPROEX-YPRO326 | HBRA | GW_OPGW | MX5-00411472 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1953 | 1953-06-30 | 68.167 | 1953 | 66 | 66 | <70 | <70 | 502.3 | 0.5023 | 30205615 | TOWER | TWRMCCT | STRUCTSUSP | L | J&W | MX5-00065256 | T326 YPS -ROTS 5 220KV | T326 | 1953 | 66 | <70 | -37.9609 | 145.2704 | CENTRAL | C1 | YPS -ROTS 5 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | SQUIN | 2017 | 1 | 2017 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 1 | 2 | Gw-1-2 | 14883480.4897 | 1405.8419 | 106635.4606 | 550000 | 15541521.7923 | 36165.6 | 429.7322 | Cr5 | 5 | 1 | #N/A
30447206 | GWSTEEL | TL-YPROEX-YPRO318-0000065240 | TOWER T318 YPS -ROTS 5 220KV | TL-YPROEX-YPRO318 | HBRA | GW_OPGW | MX5-00411464 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1953 | 1953-06-30 | 68.167 | 1953 | 66 | 66 | <70 | <70 | 242.3 | 0.2423 | 30110156 | TOWER | TWRMCCT | STRUCTSUSP | L | J&W | MX5-00065240 | T318 YPS -ROTS 5 220KV | T318 | 1953 | 66 | <70 | -37.9753 | 145.2919 | CENTRAL | C1 | YPS -ROTS 5 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | SQUIN | 2017 | 1 | 2017 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 14883480.4897 | 1241.1555 | 93570.1399 | 550000 | 15528291.7851 | 17445.6 | 890.0979 | Cr5 | 5 | 1 | #N/A
30269655 | GWSTEEL | TL-TSTXEX-TSTX427-0000064895 | TOWER T427 RWTS-TTS 220KV | TL-TSTXEX-TSTX427 | HBRA | GW_OPGW | MX5-00409164 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 323.39 | 0.32339 | 30160369 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, " | MX5-00064895 | T427 RWTS-TTS 220KV | T427 | 1956 | 126 | >80 | -37.7401 | 145.1358 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 |  |  |  |  | 2 | 0 | 0 | 190000 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 3 | 2 | Gw-3-2 | 20323388.18 | 1895.7901 | 2374990.7141 | 550000 | 23250274.6842 | 23284.08 | 998.5481 | Cr5 | 5 | 1 | 4
30441054 | GWSTEEL | TL-TSTXEX-TSTX427-0000064895 | TOWER T427 RWTS-TTS 220KV | TL-TSTXEX-TSTX427 | HBRA | GW_OPGW | MX5-00409205 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 323.39 | 0.32339 | 30160369 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, " | MX5-00064895 | T427 RWTS-TTS 220KV | T427 | 1956 | 126 | >80 | -37.7401 | 145.1358 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 | 180000 |  | DCARABOT | 2016 | 2 | 2016 | 5 | 180000 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 3 | 2 | Gw-3-2 | 20323388.18 | 1895.7901 | 2374990.7141 | 550000 | 23250274.6842 | 23284.08 | 998.5481 | Cr5 | 5 | 1 | 4
30038606 | GWSTEEL | TL-TSTXEX-TSTX428-0000064896 | TOWER T428 RWTS-TTS 220KV | TL-TSTXEX-TSTX428 | LBRA | GW_OPGW | MX5-00409165 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 207.26 | 0.20726 | 30403601 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, " | MX5-00064896 | T428 RWTS-TTS 220KV | T428 | 1956 | 126 | >80 | -37.7393 | 145.1322 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 |  |  |  |  | 2 | 0 | 0 | 190000 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 20323388.18 | 2134.1868 | 93570.1399 | 550000 | 20969092.5067 | 14922.72 | 1405.179 | Cr5 | 5 | 1 | 4
30057153 | GWSTEEL | TL-TSTXEX-TSTX428-0000064896 | TOWER T428 RWTS-TTS 220KV | TL-TSTXEX-TSTX428 | LBRA | GW_OPGW | MX5-00409206 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 207.26 | 0.20726 | 30403601 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, " | MX5-00064896 | T428 RWTS-TTS 220KV | T428 | 1956 | 126 | >80 | -37.7393 | 145.1322 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 | 180000 |  | DCARABOT | 2016 | 2 | 2016 | 5 | 180000 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 20323388.18 | 2134.1868 | 93570.1399 | 550000 | 20969092.5067 | 14922.72 | 1405.179 | Cr5 | 5 | 1 | 4
30196161 | GWSTEEL | TL-TSTXEX-TSTX429-0000064897 | TOWER T429 RWTS-TTS 220KV | TL-TSTXEX-TSTX429 | LBRA | GW_OPGW | MX5-00409166 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 286.51 | 0.28651 | 30022194 | TOWER | TWRMCCT | STRUCTSTRN | L | "J&W, " | MX5-00064897 | T429 RWTS-TTS 220KV | T429 | 1956 | 126 | >80 | -37.7389 | 145.13 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 |  |  |  |  | 2 | 0 | 0 | 190000 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 20323388.18 | 1505.5091 | 93570.1399 | 550000 | 20968463.829 | 20628.72 | 1016.4695 | Cr5 | 5 | 1 | 4
30243509 | GWSTEEL | TL-TSTXEX-TSTX429-0000064897 | TOWER T429 RWTS-TTS 220KV | TL-TSTXEX-TSTX429 | LBRA | GW_OPGW | MX5-00409207 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 286.51 | 0.28651 | 30022194 | TOWER | TWRMCCT | STRUCTSTRN | L | "J&W, " | MX5-00064897 | T429 RWTS-TTS 220KV | T429 | 1956 | 126 | >80 | -37.7389 | 145.13 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 | 180000 |  | DCARABOT | 2016 | 2 | 2016 | 5 | 180000 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 20323388.18 | 1505.5091 | 93570.1399 | 550000 | 20968463.829 | 20628.72 | 1016.4695 | Cr5 | 5 | 1 | 4
30001856 | GWSTEEL | TL-TSTXEX-TSTX430-0000064898 | TOWER T430 RWTS-TTS 220KV | TL-TSTXEX-TSTX430 | LBRA | GW_OPGW | MX5-00409208 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 341.38 | 0.34138 | 30291211 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, " | MX5-00064898 | T430 RWTS-TTS 220KV | T430 | 1956 | 126 | >80 | -37.7382 | 145.1268 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 |  |  |  |  | 2 | 0 | 0 | 180000 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 20323388.18 | 1358.3406 | 93570.1399 | 550000 | 20968316.6605 | 24579.36 | 853.0864 | Cr5 | 5 | 1 | 4
30336856 | GWSTEEL | TL-TSTXEX-TSTX430-0000064898 | TOWER T430 RWTS-TTS 220KV | TL-TSTXEX-TSTX430 | LBRA | GW_OPGW | MX5-00409167 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 341.38 | 0.34138 | 30291211 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, " | MX5-00064898 | T430 RWTS-TTS 220KV | T430 | 1956 | 126 | >80 | -37.7382 | 145.1268 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 | 180000 |  | DCARABOT | 2016 | 2 | 2016 | 5 | 190000 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 20323388.18 | 1358.3406 | 93570.1399 | 550000 | 20968316.6605 | 24579.36 | 853.0864 | Cr5 | 5 | 1 | 4
30078836 | GWSTEEL | TL-TSTXEX-TSTX431-0000064899 | TOWER T431 RWTS-TTS 220KV | TL-TSTXEX-TSTX431 | LBRA | GW_OPGW | MX5-00409168 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 359.66 | 0.35966 | 30001376 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, +10" | MX5-00064899 | T431 RWTS-TTS 220KV | T431 | 1956 | 126 | >80 | -37.7375 | 145.123 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 |  |  |  |  | 2 | 0 | 0 | 190000 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 20323388.18 | 1428.9196 | 93570.1399 | 550000 | 20968387.2395 | 25895.52 | 809.7303 | Cr5 | 5 | 1 | 4
30237432 | GWSTEEL | TL-TSTXEX-TSTX431-0000064899 | TOWER T431 RWTS-TTS 220KV | TL-TSTXEX-TSTX431 | LBRA | GW_OPGW | MX5-00409209 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 359.66 | 0.35966 | 30001376 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, +10" | MX5-00064899 | T431 RWTS-TTS 220KV | T431 | 1956 | 126 | >80 | -37.7375 | 145.123 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 | 180000 |  | DCARABOT | 2016 | 2 | 2016 | 5 | 180000 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 20323388.18 | 1428.9196 | 93570.1399 | 550000 | 20968387.2395 | 25895.52 | 809.7303 | Cr5 | 5 | 1 | 4
30170765 | GWSTEEL | TL-TSTXEX-TSTX433-0000064901 | TOWER T433 RWTS-TTS 220KV | TL-TSTXEX-TSTX433 | LBRA | GW_OPGW | MX5-00409170 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 350.52 | 0.35052 | 30135959 | TOWER | TWRMCCT | STRUCTSUSP | H | "J&W, " | MX5-00064901 | T433 RWTS-TTS 220KV | T433 | 1956 | 126 | >80 | -37.7339 | 145.1149 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 |  |  |  |  | 2 | 0 | 0 | 190000 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 20323388.18 | 1634.5627 | 11570.1399 | 148000 | 20484592.8826 | 25237.44 | 811.6748 | Cr5 | 5 | 1 | 4
30351076 | GWSTEEL | TL-TSTXEX-TSTX433-0000064901 | TOWER T433 RWTS-TTS 220KV | TL-TSTXEX-TSTX433 | LBRA | GW_OPGW | MX5-00409211 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 350.52 | 0.35052 | 30135959 | TOWER | TWRMCCT | STRUCTSUSP | H | "J&W, " | MX5-00064901 | T433 RWTS-TTS 220KV | T433 | 1956 | 126 | >80 | -37.7339 | 145.1149 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 | 180000 |  | DCARABOT | 2016 | 2 | 2016 | 5 | 180000 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 20323388.18 | 1634.5627 | 11570.1399 | 148000 | 20484592.8826 | 25237.44 | 811.6748 | Cr5 | 5 | 1 | 4
30106372 | GWSTEEL | TL-TSTXEX-TSTX434-0000064902 | TOWER T434 RWTS-TTS 220KV | TL-TSTXEX-TSTX434 | LBRA | GW_OPGW | MX5-00409212 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 268.53 | 0.26853 | 30276927 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, +5" | MX5-00064902 | T434 RWTS-TTS 220KV | T434 | 1956 | 126 | >80 | -37.7316 | 145.1121 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 |  |  |  |  | 2 | 0 | 0 | 180000 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 20323388.18 | 1439.011 | 11570.1399 | 148000 | 20484397.3309 | 19334.16 | 1059.4925 | Cr5 | 5 | 1 | 4
30412527 | GWSTEEL | TL-TSTXEX-TSTX434-0000064902 | TOWER T434 RWTS-TTS 220KV | TL-TSTXEX-TSTX434 | LBRA | GW_OPGW | MX5-00409171 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 268.53 | 0.26853 | 30276927 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, +5" | MX5-00064902 | T434 RWTS-TTS 220KV | T434 | 1956 | 126 | >80 | -37.7316 | 145.1121 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | SQUIN | 2016 | 2 | 2016 | 5 | 190000 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 20323388.18 | 1439.011 | 11570.1399 | 148000 | 20484397.3309 | 19334.16 | 1059.4925 | Cr5 | 5 | 1 | 4
30234477 | GWSTEEL | TL-TSTXEX-TSTX445-0000064921 | TOWER T445 RWTS-TTS 220KV | TL-TSTXEX-TSTX445 | LBRA | GW_OPGW | MX5-00409222 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 360.27 | 0.36027 | 30068750 | TOWER | TWRMCCT | STRUCTSTRN | L | "J&W, +10" | MX5-00064921 | T445 RWTS-TTS 220KV | T445 | 1956 | 126 | >80 | -37.7107 | 145.0833 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 |  |  |  |  | 2 | 0 | 0 | 180000 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 1 | 2 | Gw-1-2 | 20323388.18 | 3039.8395 | 106635.4606 | 550000 | 20983063.4801 | 25939.44 | 808.9251 | Cr5 | 5 | 1 | 4
30299338 | GWSTEEL | TL-TSTXEX-TSTX445-0000064921 | TOWER T445 RWTS-TTS 220KV | TL-TSTXEX-TSTX445 | LBRA | GW_OPGW | MX5-00409181 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 360.27 | 0.36027 | 30068750 | TOWER | TWRMCCT | STRUCTSTRN | L | "J&W, +10" | MX5-00064921 | T445 RWTS-TTS 220KV | T445 | 1956 | 126 | >80 | -37.7107 | 145.0833 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 | 180000 |  | DCARABOT | 2016 | 2 | 2016 | 5 | 190000 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 1 | 2 | Gw-1-2 | 20323388.18 | 3039.8395 | 106635.4606 | 550000 | 20983063.4801 | 25939.44 | 808.9251 | Cr5 | 5 | 1 | 4
30100114 | GWSTEEL | TL-TSTXEX-TSTX446-0000064923 | TOWER T446 RWTS-TTS 220KV | TL-TSTXEX-TSTX446 | LBRA | GW_OPGW | MX5-00409223 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 325.22 | 0.32522 | 30392295 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, +10" | MX5-00064923 | T446 RWTS-TTS 220KV | T446 | 1956 | 126 | >80 | -37.7085 | 145.0803 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 |  |  |  |  | 2 | 0 | 0 | 180000 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 20323388.18 | 1320.1279 | 11570.1399 | 148000 | 20484278.4479 | 23415.84 | 874.8043 | Cr5 | 5 | 1 | 4
30295855 | GWSTEEL | TL-TSTXEX-TSTX446-0000064923 | TOWER T446 RWTS-TTS 220KV | TL-TSTXEX-TSTX446 | LBRA | GW_OPGW | MX5-00409182 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 325.22 | 0.32522 | 30392295 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, +10" | MX5-00064923 | T446 RWTS-TTS 220KV | T446 | 1956 | 126 | >80 | -37.7085 | 145.0803 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 | 180000 |  | DCARABOT | 2016 | 2 | 2016 | 5 | 190000 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 20323388.18 | 1320.1279 | 11570.1399 | 148000 | 20484278.4479 | 23415.84 | 874.8043 | Cr5 | 5 | 1 | 4
30211053 | GWSTEEL | TL-TSTXEX-TSTX447-0000064925 | TOWER T447 RWTS-TTS 220KV | TL-TSTXEX-TSTX447 | LBRA | GW_OPGW | MX5-00409183 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 292 | 0.292 | 30401992 | TOWER | TWRMCCT | STRUCTSTRN | H | "J&W, +20" | MX5-00064925 | T447 RWTS-TTS 220KV | T447 | 1956 | 126 | >80 | -37.7065 | 145.0776 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 |  |  |  |  | 2 | 0 | 0 | 190000 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 20323388.18 | 1555.7216 | 11570.1399 | 148000 | 20484514.0415 | 21024 | 974.3395 | Cr5 | 5 | 1 | 4
30212424 | GWSTEEL | TL-TSTXEX-TSTX447-0000064925 | TOWER T447 RWTS-TTS 220KV | TL-TSTXEX-TSTX447 | LBRA | GW_OPGW | MX5-00409224 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 292 | 0.292 | 30401992 | TOWER | TWRMCCT | STRUCTSTRN | H | "J&W, +20" | MX5-00064925 | T447 RWTS-TTS 220KV | T447 | 1956 | 126 | >80 | -37.7065 | 145.0776 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 | 180000 |  | DCARABOT | 2016 | 2 | 2016 | 5 | 180000 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 20323388.18 | 1555.7216 | 11570.1399 | 148000 | 20484514.0415 | 21024 | 974.3395 | Cr5 | 5 | 1 | 4
30147048 | GWSTEEL | TL-TSTXEX-TSTX450-0000064931 | TOWER T450 RWTS-TTS 220KV | TL-TSTXEX-TSTX450 | LBRA | GW_OPGW | MX5-00409227 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 336.19 | 0.33619 | 30256394 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, +10" | MX5-00064931 | T450 RWTS-TTS 220KV | T450 | 1956 | 126 | >80 | -37.7048 | 145.0696 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 |  |  |  |  | 2 | 0 | 0 | 180000 | 5 | 2 | 1 | 2 | -1 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 20323388.18 | 4201.6607 | 93570.1399 | 550000 | 20971159.9806 | 24205.68 | 866.3735 | Cr5 | 5 | 1 | 4
30366688 | GWSTEEL | TL-TSTXEX-TSTX450-0000064931 | TOWER T450 RWTS-TTS 220KV | TL-TSTXEX-TSTX450 | LBRA | GW_OPGW | MX5-00409186 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 336.19 | 0.33619 | 30256394 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, +10" | MX5-00064931 | T450 RWTS-TTS 220KV | T450 | 1956 | 126 | >80 | -37.7048 | 145.0696 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 | 180000 |  | DCARABOT | 2016 | 2 | 2016 | 5 | 190000 | 5 | 1 | 1 | 2 | -1 |  |  |  | 2 | 0 | 2 | Gw-0-2 | 20323388.18 | 4201.6607 | 93570.1399 | 550000 | 20971159.9806 | 24205.68 | 866.3735 | Cr5 | 5 | 1 | 4
30171793 | GWSTEEL | TL-TSTXEX-TSTX466-0000064963 | TOWER T466 RWTS-TTS 220KV | TL-TSTXEX-TSTX466 | LBRA | GW_OPGW | MX5-00409241 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 291.08 | 0.29108 | 30319872 | TOWER | TWRMCCT | STRUCTSUSP | L | "J&W, " | MX5-00064963 | T466 RWTS-TTS 220KV | T466 | 1956 | 126 | >80 | -37.6935 | 145.0157 | CENTRAL | C1 | RWTS-TTS |  | L | 1Steel | 220 | 1 | 180000 | 190000 |  | SQUIN | 2016 | 2 | 2016 | 5 | 180000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 0 | 1 | Gw-0-1 | 20323388.18 | 325.9229 | 11570.1399 | 148000 | 20483284.2428 | 20957.76 | 977.3604 | Cr5 | 5 | 1 | 4
30330379 | GWSTEEL | TL-TSTXEX-TSTX467-0000064965 | TOWER T467 RWTS-TTS 220KV | TL-TSTXEX-TSTX467 | LBRA | GW_OPGW | MX5-00409201 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 145.69 | 0.14569 | 30386104 | TOWER | TWRMCCT | STRUCTSTRN | H | "J&W, +10" | MX5-00064965 | T467 RWTS-TTS 220KV | T467 | 1956 | 126 | >80 | -37.6928 | 145.0125 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | DC | 2016 | 2 | 2016 | 5 | 190000 | 5 | 1 | 2 | 2 | 0 |  |  |  | 2 | 4 | 2 | Gw-4-2 | 20323388.18 | 204.5375 | 2550415.8044 | 550000 | 23424008.5219 | 100000 | 234.2401 | Cr5 | 5 | 1 | 4
30223129 | GWSTEEL | TL-TSTXEX-TSTX468-0000334659 | TOWER T468 RWTS-TTS 220KV | TL-TSTXEX-TSTX468 | LBRA | GW_OPGW | MX5-00409202 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1956 | 1956-06-30 | 65.1663 | 1956 | 63 | 63 | <70 | <70 | 112 | 0.112 | 30320184 | TOWER | TWRMCCT | STRUCTSTRN | H | "J&W, +15" | MX5-00334659 | T468 RWTS-TTS 220KV | T468 | 1956 | 126 | >80 | -37.6926 | 145.0109 | CENTRAL | C1 | RWTS-TTS |  | R | 2Steel | 220 | 2 | 190000 | 190000 |  | RDAVIN | 2016 | 2 | 2016 | 5 | 190000 | 5 | 2 | 4 | 2 | 2 |  |  |  | 2 | 3 | 2 | Gw-3-2 | 20323388.18 | 138.3189 | 2374990.7141 | 550000 | 23248517.213 | 8064 | 2883.0006 | Cr5 | 5 | 1 | 4
30150839 | GWSTEEL | TL-YPROEX-YPRO232-0000085626 | TOWER T232 YPS -ROTS 5 220KV | TL-YPROEX-YPRO232 | HBRA | GW_OPGW | MX5-00411529 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1953 | 1953-06-30 | 68.167 | 1953 | 66 | 66 | <70 | <70 | 261.5 | 0.2615 | 30219484 | TOWER | TWRMCCT | STRUCTSUSP | H | SAE | MX5-00085626 | T232 YPS -ROTS 5 220KV | T232 | 1953 | 66 | <70 | -38.057 | 145.5552 | CENTRAL | C1 | YPS -ROTS 5 |  | 1 | 1Steel | 220 | 1 | 180000 | 190010 |  | DMOORE | 2017 | 1 | 2017 | 5 | 180000 | 5 | 1 | 3 | 1 | 2 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 14883480.4897 | 1483.8558 | 3720.1399 | 25000 | 14913684.4854 | 18828 | 792.1014 | Cr5 | 5 | 1 | #N/A
30329326 | GWSTEEL | TL-YPROEX-YPRO239-0000085633 | TOWER T239 YPS -ROTS 5 220KV | TL-YPROEX-YPRO239 | HBRA | GW_OPGW | MX5-00411536 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1953 | 1953-06-30 | 68.167 | 1953 | 66 | 66 | <70 | <70 | 239.9 | 0.2399 | 30277788 | TOWER | TWRMCCT | STRUCTSUSP | L | SAE | MX5-00085633 | T239 YPS -ROTS 5 220KV | T239 | 1953 | 66 | <70 | -38.0555 | 145.5314 | CENTRAL | C1 | YPS -ROTS 5 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | DCARABOT | 2017 | 1 | 2017 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 2 | 0 | Gw-2-0 | 14883480.4897 | 991.3429 | 1575956.0551 | 25000 | 16485427.8877 | 17272.8 | 954.4155 | Cr5 | 5 | 1 | #N/A
30162952 | GWSTEEL | TL-YPROEX-YPRO240-0000085634 | TOWER T240 YPS -ROTS 5 220KV | TL-YPROEX-YPRO240 | HBRA | GW_OPGW | MX5-00411537 | GW-19/2 STEEL | Steel | 19/2 STEEL | 1953 | 1953-06-30 | 68.167 | 1953 | 66 | 66 | <70 | <70 | 281.9 | 0.2819 | 30044722 | TOWER | TWRMCCT | STRUCTSUSP | L | SAE | MX5-00085634 | T240 YPS -ROTS 5 220KV | T240 | 1953 | 66 | <70 | -38.0553 | 145.5286 | CENTRAL | C1 | YPS -ROTS 5 |  | 1 | 1Steel | 220 | 1 | 180010 | 180000 |  | DCARABOT | 2017 | 1 | 2017 | 5 | 180010 | 5 | 1 | 1 | 1 | 0 |  |  |  | 2 | 0 | 0 | Gw-0-0 | 14883480.4897 | 991.3429 | 3720.1399 | 25000 | 14913191.9726 | 20296.8 | 734.7558 | Cr5 | 5 | 1 | #N/A

## TR Line Conductors C5 condition
FLOC | FLOC_DESCR | TECH_OBJ_TYPE | CAT_PROFILE | LOCATION | EaseSeg_FLOC | LONGITUDE | LATITUDE | TL_Structure_Eq.EQUIPMENT_ID | TL_Structure_Eq.OBJECT_TYPE | TL_Structure_Eq.TECH_OBJECT_DESCR | TL_Structure_Eq.TECH_IDENT_NO | TL_Structure_Eq.CAT_PROFILE | TL_Structure_Eq.START_UP_DATE | Startup date | Age | TL_Structure_Eq.FLOC | TL_Structure_Floc_Char.Tower Name | TL_Structure_Floc_Char.Number | TL_Structure_Eq_Char.1.Duty | TL_Structure_Eq_Char.1.Manufacture Type | TL_Wseg-Floc-Eq.FLOC | TL_Wseg-Floc-Eq.FLOC_DESCR | TL_Wseg_FLOC_Char.Name | TL_Wseg_FLOC_Char.Station Asset? | TL_Wseg-Floc-Eq.TECH_OBJ_TYPE | TL_Wseg-Floc-Eq.FIREZONE | TL_Wseg-Floc-Eq.START_UP_DATE | TL_Wseg-Floc-Eq.SIZE_DIMENSION | TL_Wseg-Floc-Eq.TL_Wseg_Eq.EQUIPMENT_ID | TL_Wseg-Floc-Eq.TL_Wseg_Eq.OBJECT_TYPE | TL_Wseg-Floc-Eq.TL_Wseg_Eq.TECH_OBJECT_DESCR | TL_Wseg-Floc-Eq.TL_Wseg_Eq.TECH_IDENT_NO | TL_Wseg-Floc-Eq.TL_Wseg_Eq.START_UP_DATE | TL_Wseg_Eq_Char.Equipment Group Identifier | TL_Wseg_Eq_Char_SpanLgth.Span Length | Wseg_export2.Wseg_Voltage [kV] | Wseg_export2.TL_Wseg_FLOC_Char.Name | Wseg_export2.CCt No. | Wseg_export2.CCT_No_CA_Allocation | Wseg_export2.Count wseg/tower | Wseg_CAscore_2019-10-23.MEAS_POSITION | Wseg_CAscore_2019-10-23.CCT_No_CA_Allocation | Wseg_CAscore_2019-10-23.MEAS_DATE | Wseg_CAscore_2019-10-23.Year | Wseg_CAscore_2019-10-23.READING_TAKEN_BY | Wseg_CAscore_2019-10-23.VALUATION_CODE | Wseg_CAscore_2019-10-23.status | Wseg_CAscore_2019-10-23.Updated Optimum Meas Date | Wseg_CAscore_2019-10-23.Updated valuation date | Wseg_CAscore_2019-10-23.Final_Meas_Year | Wseg_Cascore_15Nov-Final_Valuation (Condition Score) | Wseg_CAscoreYear_15Nov-Final_MaxYear | Wseg_Criticality_Old-1.NAME | Wseg_Criticality_Old-1.NOMINAL_VOLTAGE_PP | Wseg_Criticality_Old-1.SPAN_LENGTH | Wseg_Criticality_Old-1.Age | Wseg_Criticality_Old-1.Age Range | Wseg_Criticality_Old-1.Corrosivity Level | Wseg_Criticality_Old-1.Rd/Rail Xing Ease Score | Wseg_Criticality_Old-1.Urban Ease Score | Wseg_Criticality_Old-1.Effects Look Up Key | Wseg_Criticality_Old-1.Market Impact Cost_Final | Wseg_Criticality_Old-1.BUSHFIRE_CRITICALITY | Wseg_Criticality_Old-1.Collateral_Damage | Wseg_Criticality_Old-1.MARKET_CRITICALITY | Wseg_Criticality_Old-1.SAFETY_CRITICALITY | Wseg_Criticality_Old-1.THIRD_PARTY_DAMAGE | Wseg_Criticality_Old-1.Total Effect $ | Unit Rate Tag | CTRL Reactive replacement Cost $/span (3ph) | CTRL Reactive replacement Unit Rate $/km (3phase) | CTRL Proactive replacement Cost $/span | CTRL Proactive replacement Unit Rate $/km (3phase) | Wseg_Criticality Criticality Ratio | Wseg_Criticality_Scale2 | Wseg_Criticality_Old-1.Max of CA Final | SOW (1/0) | hn
TL-HYSEEX-HYSE219-0000060110 | TOWER T219 HYTS-SESS 1 275KV | STRUCTSUSP | TOWER | NORTH | TL-HYSEEX-HYSE219 | 141.5744 | -38.1575 | 30349843 | TWRMCCT | T219 HYTS-SESS 1 275KV | MX5-00060110 | TOWER | Thursday, 30 June 1988 | 1988-06-30 | 33.1663 | TL-HYSEEX-HYSE219-0000060110 | T219 HYTS-SESS 1 275KV | T219 |  | DS 2/7 | TL-HYSEEX-HYSE219-2601493672 | WIRE T219 HYTS-SESS 2 275KV T220 | HYTS-SESS NO.2 | NO | WSEGEHV | HBRA |  | 360.992 | 30020770 | CTRACSR | S219 HYTS-SESS 2 275KV | MX5-00292989 | Thursday, 30 June 1988 | SP-OL190 | 362 | 275 | HYTS-SESS NO.2 | 2 | 2 | 2 | 240000 | 2 | Thursday, 16 April 2015 | 2015 | CM | 2 |  |  | 0 | 2015 | 5 | 2010 | HYTS-SESS NO.2 | 275 | 362 | 31 | <=40 | 2 | 0 | 0 | CTRTL-0-0 | 9174000 | 1985.3073 | 50000 | 9174000 | 5070.1399 | 0 | 9231055.4472 | 275-0 | 55144.908 | 152334 | 55144.908 | 152334 | 167.3963 | Cr5 | 2 | 1 | 5
TL-LYHWEN-LYHW009-0000086659 | TOWER T009 MWTS-LY 3 66KV | STRUCTSUSP | TOWER | EAST | TL-LYHWEN-LYHW009 | 146.5415 | -38.252 | 30042336 | TWRMCCT | T009 MWTS-LY 3 66KV | MX5-00086659 | TOWER | Wednesday, 30 June 1982 | 1982-06-30 | 39.1677 | TL-LYHWEN-LYHW009-0000086659 | T009 MWTS-LY 3 66KV | T009 | L | 6A | TL-LYHWEN-LYHW009-9000147340 | WIRE T009 MWTS-LY 4 66KV T010 | MWTS-LY NO.4 | NO | WSEGHV | HBRA |  | 343.303 | 30061460 | CTRACSR | S009 MWTS-LY 4 66KV | MX5-00276707 | Wednesday, 30 June 1982 | SP-MA190 | 345 | 66 | MWTS-LY NO.4 | 4 | 2 | 2 | 240000 | 2 | Monday, 1 July 2013 | 2013 | CR | 5 |  |  | 0 | 2013 | 5 | 2013 | MWTS-LY NO.4 | 66 | 345 | 37 | <=40 | 2 | 0 | 0 | CTRTL-0-0 | 9016.944 | 17288.7653 | 50000 | 9016.944 | 5070.1399 | 0 | 81375.8493 | 66-0 | 21807.7141 | 63210.7654 | 18963.2296 | 54965.883 | 3.7315 | Cr5 | 1 | 1 | 5
TL-HWHWEX-HWHW005-0000084423 | TOWER T005 HWPS-JLTS 3 220KV | STRUCTSUSP | TOWER | EAST | TL-HWHWEX-HWHW005 | 146.4069 | -38.2799 | 30137209 | TWRMCCT | T005 HWPS-JLTS 3 220KV | MX5-00084423 | TOWER | Saturday, 30 June 1984 | 1984-06-30 | 37.1663 | TL-HWHWEX-HWHW005-0000084423 | T005 HWPS-JLTS 3 220KV | T005 | L |  | TL-HWHWEX-HWHW005-2601487258 | WIRE T005 HWPS-JLTS 3 220KV T006 | HWPS-JLTS NO.3 | NO | WSEGEHV | HBRA |  | 428.862 | 30279130 | CTRACSR | S005 HWPS-JLTS 3 220KV | MX5-00274423 | Saturday, 30 June 1984 | SP-PA182 | 430.6 | 220 | HWPS-JLTS NO.3 | 3 | 1 | 2 | 170000 | 1 | Tuesday, 1 July 2014 | 2014 | DV | 5 | Awaiting Info |  | 0 | 2014 | 5 | 2014 | HWPS-JLTS NO.3 | 220 | 430.6 | 35 | <=40 | 2 | 0 | 0 | CTRTL-0-0 | 36487.919 | 4692.8839 | 50000 | 36487.919 | 5070.1399 | 0 | 96250.9428 | 220-0 | 75434.2735 | 175184.1 | 65595.0204 | 152334 | 1.276 | Cr5 | 5 | 1 | 5
TL-LYHWEN-LYHW019-0000086669 | TOWER T019 MWTS-LY 3 66KV | STRUCTSUSP | TOWER | EAST | TL-LYHWEN-LYHW019 | 146.5013 | -38.2497 | 30034655 | TWRMCCT | T019 MWTS-LY 3 66KV | MX5-00086669 | TOWER | Wednesday, 30 June 1982 | 1982-06-30 | 39.1677 | TL-LYHWEN-LYHW019-0000086669 | T019 MWTS-LY 3 66KV | T019 | L | 6A | TL-LYHWEN-LYHW019-9000147311 | WIRE T019 MWTS-LY 3 66KV T020 | MWTS-LY NO.3 | NO | WSEGHV | HBRA |  | 352.727 | 30312638 | CTRACSR | S019 MWTS-LY 3 66KV | MX5-00276669 | Wednesday, 30 June 1982 | SP-MA190 | 350 | 66 | MWTS-LY NO.3 | 3 | 1 | 2 | 170000 | 1 | Monday, 1 July 2013 | 2013 | MB | 5 | Awaiting Info | 0 | 0 | 2013 | 5 | 2013 | MWTS-LY NO.3 | 66 | 350 | 37 | <=40 | 2 | 0 | 0 | CTRTL-0-0 | 9016.944 | 22366.7987 | 50000 | 9016.944 | 5070.1399 | 0 | 86453.8826 | 66-0 | 22123.7679 | 63210.7654 | 19238.059 | 54965.883 | 3.9077 | Cr5 | 1 | 1 | 5
TL-LYHWEN-LYHW019-0000086669 | TOWER T019 MWTS-LY 3 66KV | STRUCTSUSP | TOWER | EAST | TL-LYHWEN-LYHW019 | 146.5013 | -38.2497 | 30034655 | TWRMCCT | T019 MWTS-LY 3 66KV | MX5-00086669 | TOWER | Wednesday, 30 June 1982 | 1982-06-30 | 39.1677 | TL-LYHWEN-LYHW019-0000086669 | T019 MWTS-LY 3 66KV | T019 | L | 6A | TL-LYHWEN-LYHW019-9000147310 | WIRE T019 MWTS-LY 4 66KV T020 | MWTS-LY NO.4 | NO | WSEGHV | HBRA |  | 352.726 | 30420219 | CTRACSR | S019 MWTS-LY 4 66KV | MX5-00276717 | Wednesday, 30 June 1982 | SP-MA190 | 350 | 66 | MWTS-LY NO.4 | 4 | 2 | 2 | 240000 | 2 | Monday, 1 July 2013 | 2013 | MB | 5 | Awaiting Info | 0 | 0 | 2013 | 5 | 2013 | MWTS-LY NO.4 | 66 | 350 | 37 | <=40 | 2 | 0 | 0 | CTRTL-0-0 | 9016.944 | 22366.7987 | 50000 | 9016.944 | 5070.1399 | 0 | 86453.8826 | 66-0 | 22123.7679 | 63210.7654 | 19238.059 | 54965.883 | 3.9077 | Cr5 | 1 | 1 | 5
TL-HWHWEX-HWHW005-0000084423 | TOWER T005 HWPS-JLTS 3 220KV | STRUCTSUSP | TOWER | EAST | TL-HWHWEX-HWHW005 | 146.4069 | -38.2799 | 30137209 | TWRMCCT | T005 HWPS-JLTS 3 220KV | MX5-00084423 | TOWER | Saturday, 30 June 1984 | 1984-06-30 | 37.1663 | TL-HWHWEX-HWHW005-0000084423 | T005 HWPS-JLTS 3 220KV | T005 | L |  | TL-HWHWEX-HWHW005-2601487265 | WIRE T005 HWPS-JLTS 4 220KV T006 | HWPS-JLTS NO.4 | NO | WSEGEHV | HBRA |  | 430.628 | 30200980 | CTRACSR | S005 HWPS-JLTS 4 220KV | MX5-00274433 | Saturday, 30 June 1984 | SP-PA182 | 430.6 | 220 | HWPS-JLTS NO.4 | 4 | 2 | 2 | 240000 | 2 | Tuesday, 1 July 2014 | 2014 | DV | 5 | Awaiting Info |  | 0 | 2014 | 5 | 2014 | HWPS-JLTS NO.4 | 220 | 430.6 | 35 | <=40 | 2 | 0 | 0 | CTRTL-0-0 | 36487.919 | 4692.8839 | 50000 | 36487.919 | 5070.1399 | 0 | 96250.9428 | 220-0 | 75434.2735 | 175184.1 | 65595.0204 | 152334 | 1.276 | Cr5 | 5 | 1 | 5
TL-KXGXEX-KXGX159-0000057290 | TOWER T159 KTS -GTS 1 220KV | STRUCTSUSP | TOWER | CENTRAL | TL-KXGXEX-KXGX159 | 144.3438 | -38.053 | 30132219 | TWRMCCT | T159 KTS -GTS 1 220KV | MX5-00057290 | TOWER | Tuesday, 30 June 1964 | 1964-06-30 | 57.1663 | TL-KXGXEX-KXGX159-0000057290 | T159 KTS -GTS 1 220KV | T159 | L | X | TL-KXGXEX-KXGX159-9000138321 | WIRE T159 KTS -GTS 3 220KV T160 | KTS-GTS NO.3 | NO | WSEGEHV | HBRA |  | 407.012 | 30015162 | CTRACSR | S159 KTS -GTS 3 220KV | MX5-00247953 | Tuesday, 30 June 1964 | SP-CA165 | 407.1 | 220 | KTS-GTS NO.3 | 3 | 2 | 2 | 240000 | 2 | Friday, 1 November 2013 | 2013 | DH | 5 |  |  | 0 | 2013 | 5 | 2013 | KTS-GTS NO.3 | 220 | 407.1 | 55 | <=60 | 2 | 0 | 2 | CTRTL-0-2 | 21820.9411 | 1 | 1100000 | 21820.9411 | 153570.1399 | 0 | 1275391.081 | 220-2 | 73146.0996 | 179676 | 63605.304 | 156240 | 17.4362 | Cr5 | 2 | 1 | 5
TL-TYSMEX-TYSM134-0000083875 | TOWER T134 HWTS-SMTS 2 500KV | STRUCTSUSP | TOWER | EAST | TL-TYSMEX-TYSM134 | 145.8857 | -38.0557 | 30354185 | TWRSCCT | T134 HWTS-SMTS 2 500KV | MX5-00083875 | TOWER | Monday, 30 June 1969 | 1969-06-30 | 52.167 | TL-TYSMEX-TYSM134-0000083875 | T134 HWTS-SMTS 2 500KV | T134 | H | 5B | TL-TYSMEX-TYSM134-2601499505 | WIRE T134 HWTS-SMTS 2 500KV T135 | HWTS-SMTS NO.2 | NO | WSEGEHV | HBRA |  | 553.072 | 30259478 | CTRACSR | S134 HWTS-SMTS 2 500KV | MX5-00273875 | Monday, 30 June 1969 | SP-CA482 | 225.9 | 500 | HWTS-SMTS NO.2 | 2 | 1 | 1 | 170000 | 1 | Saturday, 1 March 2014 | 2014 | DV | 5 | Awaiting Info | 0 | 0 | 2014 | 5 | 2014 | HWTS-SMTS NO.2 | 500 | 225.9 | 50 | <=60 | 2 | 0 | 0 | CTRTL-0-0 | 109975463.4972 | 7070.4499 | 50000 | 109975463.4972 | 5070.1399 | 0 | 110037604.087 | 500-0 | 72315.727 | 320122.74 | 62883.2408 | 278367.6 | 1521.6276 | Cr4 | 1 | 1 | 5
TL-EGPTEX-EGPT079-0000088007 | TOWER T079 GTS -PTH 1 220KV | STRUCTSUSP | TOWER | NORTH | TL-EGPTEX-EGPT079 | 144.4298 | -38.1463 | 30451299 | TWRMCCT | T079 GTS -PTH 1 220KV | MX5-00088007 | TOWER | Sunday, 30 June 1963 | 1963-06-30 | 58.1684 | TL-EGPTEX-EGPT079-0000088007 | T079 GTS -PTH 1 220KV | T079 | L | X | TL-EGPTEX-EGPT079-9000143943 | WIRE T079 GTS -PTH 1 220KV T080 | GTS-PTH NO.2 | NO | WSEGEHV | LBRA |  | 323.334 | 30172051 | CTRACSR | S079 GTS -PTH 2 220KV | MX5-00278181 | Sunday, 30 June 1963 | SP-CA165 | 323.1 | 220 | GTS-PTH NO.2 | 2 | 2 | 2 | 240000 | 2 | Monday, 26 July 2010 | 2010 | KH | 5 |  |  | 0 | 2010 | 5 | 2010 | GTS-PTH NO.2 | 220 | 323.1 | 56 | <=60 | 2 | 1 | 0 | CTRTL-1-0 | 25497.8919 | 1 | 50000 | 25497.8919 | 18135.4606 | 0 | 93633.3525 | 220-0 | 56601.9827 | 175184.1 | 49219.1154 | 152334 | 1.6542 | Cr5 | 2 | 1 | 5
TL-EGPTEX-EGPT079-0000088007 | TOWER T079 GTS -PTH 1 220KV | STRUCTSUSP | TOWER | NORTH | TL-EGPTEX-EGPT079 | 144.4298 | -38.1463 | 30451299 | TWRMCCT | T079 GTS -PTH 1 220KV | MX5-00088007 | TOWER | Sunday, 30 June 1963 | 1963-06-30 | 58.1684 | TL-EGPTEX-EGPT079-0000088007 | T079 GTS -PTH 1 220KV | T079 | L | X | TL-EGPTEX-EGPT079-9000143944 | WIRE T079 GTS -PTH 1 220KV T080 | GTS-PTH NO.1 | NO | WSEGEHV | LBRA |  | 323.335 | 30172601 | CTRACSR | S079 GTS -PTH 1 220KV | MX5-00278007 | Sunday, 30 June 1963 | SP-CA165 | 323.1 | 220 | GTS-PTH NO.1 | 1 | 1 | 2 | 170000 | 1 | Monday, 26 July 2010 | 2010 | KH | 5 |  |  | 0 | 2010 | 5 | 2010 | GTS-PTH NO.1 | 220 | 323.1 | 56 | <=60 | 2 | 1 | 0 | CTRTL-1-0 | 25497.8919 | 1 | 50000 | 25497.8919 | 18135.4606 | 0 | 93633.3525 | 220-0 | 56601.9827 | 175184.1 | 49219.1154 | 152334 | 1.6542 | Cr5 | 5 | 1 | 5
TL-YPROEX-YPRO251-0000065105 | TOWER T251 YPS -ROTS 5 220KV | STRUCTSUSP | TOWER | CENTRAL | TL-YPROEX-YPRO251 | 145.4905 | -38.053 | 30311229 | TWRMCCT | T251 YPS -ROTS 5 220KV | MX5-00065105 | TOWER | Tuesday, 30 June 1953 | 1953-06-30 | 68.167 | TL-YPROEX-YPRO251-0000065105 | T251 YPS -ROTS 5 220KV | T251 | H | SAE | TL-YPROEX-YPRO251-2601489334 | WIRE T251 YPS -ROTS 6 220KV T252 | YPS-ROTS NO.6 | NO | WSEGEHV | HBRA |  | 542.036 | 30398575 | CTRACSR | S251 YPS -ROTS 6 220KV | MX5-00255296 | Tuesday, 30 June 1953 | SP-FI165 | 541 | 220 | YPS-ROTS NO.6 | 6 | 2 | 2 | 240000 | 2 | Monday, 2 June 2014 | 2014 | CL | 5 | Awaiting Info | 2008 | 0 | 2014 | 5 | 2014 | YPS-ROTS NO.6 | 220 | 541 | 66 | <=70 | 2 | 0 | 2 | CTRTL-0-2 | 14883480.4897 | 1287.6655 | 1100000 | 14883480.4897 | 153570.1399 | 0 | 16138338.2951 | 220-2 | 97204.716 | 179676 | 84525.84 | 156240 | 166.0242 | Cr5 | 5 | 1 | 5

## TR Line INSULATOR Failure 16mm
AWB Input
Item | Line Name | Year failed | Age (years) | Age (hours) | Cause | Type | Comments | Failure Age (Hours) | Quantity | Reference ID | Cause | Suspended
4 | EPS-TTS 220 | 1984 | 29 | 254040 | Hook fatigue | 16 mm |  | 254040 | 1 | 4 | Hook fatigue | FALSE
1 | BATS-BETS 220 kV | 1999 | 37 | 324120 | Pin fatigue | 16 mm |  | 324120 | 2 | 1&20 | Pin fatigue | FALSE
20 | YPS-ROTS 5 220 kV | 1993 | 37 | 324120 | Pin fatigue | 16mm |  | 341640 | 2 | 5&8 | Pin fatigue | FALSE
5 | HWPS-ROTS 1 220kV | 2005 | 39 | 341640 | Pin fatigue | 16 mm |  | 367920 | 1 | 6 | Pin fatigue | FALSE
8 | KTS-GTS 1 220KV | 2003 | 39 | 341640 | Pin fatigue | 16 mm |  | 385440 | 1 | 12 | Hook fatigue | FALSE
6 | HWPS-ROTS 1 220kV | 2008 | 42 | 367920 | Pin fatigue | 16 mm |  | 411720 | 1 | 13 | No formal report. | FALSE
12 | MBTS-EPS 1 220kV | 2004 | 44 | 385440 | Hook fatigue | 16mm |  | 429240 | 1 | 21 | Defective LL link | FALSE
13 | MLTS-TGTS 220kV | 2004 | 47 | 411720 | No formal report. | 16mm
21 | YPS-ROTS 7 220 kV | 2005 | 49 | 429240 | Defective LL link | 16mm

## TR Line INSULATOR Failures 20mm
AWB Input
Item | Line Name | Year failed | Age (years) | Age (hours) | Cause | Type | Comments | Failure Age (Hours) | Quantity | Reference ID | Cause | Suspended
16 | ROTS-RTS 4 220kV | 2012 | 28 | 245280 | Flat | 20mm |  | 254040 | 1 | 4 | Hook fatigue | FALSE
19 | SMTS-SYTS 2 500kV | 2008 | 36 | 315360 | Puncture | 20mm |  | 324120 | 2 | 1&20 | Pin fatigue | FALSE
9 | KTS-WMTS 1 220kV | 2001 | 37 | 324120 | Defective shackle | 20mm |  | 341640 | 2 | 5&8 | Pin fatigue | FALSE
7 | KTS-BLTS 220kV | 2007 | 38 | 332880 | Puncture | 20mm |  | 367920 | 1 | 6 | Pin fatigue | FALSE
11 | KTS-WMTS 2 220kV | 2003 | 39 | 341640 | Puncture | 20mm |  | 385440 | 1 | 12 | Hook fatigue | FALSE
10 | KTS-WMTS 1 220kV | 2006 | 42 | 367920 | Puncture | 20mm |  | 411720 | 1 | 13 | No formal report. | FALSE
18 | ROTS-SVTS 2 220kV | 2007 | 43 | 376680 | Puncture | 20mm |  | 429240 | 1 | 21 | Defective LL link | FALSE
3 | CBTS-FTS 1 66kV | 2012 | 44 | 385440 | Flat | 20mm |  | 385440 | 2 | 3&17 | Flat | FALSE
17 | ROTS-RTS 4 220kV | 2012 | 44 | 385440 | Flat | 20mm |  | 420480 | 1 | 14 | Flat | FALSE
14 | ROTS-RTS 1 220kV | 2012 | 48 | 420480 | Flat | 20mm |  | 429240 | 1 | 15 | Flat | FALSE
15 | ROTS-RTS 1 220kV | 2012 | 49 | 429240 | Flat | 20mm |  | 473040 | 1 | 2 | Failed Y-clevis (Manuf defect) | FALSE
2 | BETS-FVTS-SHTS 220kV | 2012 | 54 | 473040 | Failed Y-clevis | 20mm | Manuf defect | 315600 | 1 | 20 | Vibration due to Wind | TRUE
20 | T273 HWTS-ROTS 3 |  | 36.0274 | 315600 | Vibration due to Wind | 20mm | Split pin missing socket clevis | 438312 | 1 | 21 | Vibration due to Wind | TRUE
21 | DDTS-SMTS 1 T202 |  | 50.0356 | 438312 | Vibration due to Wind | 20mm | Split pins missing | 431016 | 1 | 22 | Vibration due to Wind | TRUE
22 | DDTS-SMTS 1 T241 |  | 49.2027 | 431016 | Vibration due to Wind | 20mm | Split pins missing | 429552 | 1 | 23 | Vibration due to Wind | TRUE
23 | DDTS-SMTS 1 T104 |  | 49.0356 | 429552 | Vibration due to Wind | 20mm | Cotter pins missing | 315600 | 1 | 24 | Vibration due to Wind | TRUE
24 | T330 MLTS-TRTS 1 |  | 36.0274 | 315600 | Vibration due to Wind | 20mm | missing w pin hot end socket clevis | 403272 | 1 | 25 | Corrosion | TRUE
25 | CBTS-LYD-ERTS |  | 46.0356 | 403272 | Corrosion | 20mm | Ball Clevis Corrosion