## Analysis
[23 empty] | Current Condition |  | Rectify this Period
FLOC | Equipment | EQUIP_DESCRIPTION | LINE NAME | Line Voltage, kV | Corrosivity Zone | EQUIP_Start-up date | TWR AGE | FLOC_OBJECT TYPE (STRUCTSUSP / STRUCTSTRN) | TWR_DESIGN_TYPE | EQUIPMENT_OBJECT TYPE (TWRMCCT / TWRSCCT) | FLOC_Region | CA Ratings, Structures - CONDITION SCORE | Corr-Cond | V-Rating & Twr Type | SAFETY_CRITICALITY | THIRD_PARTY_DAMAGE | BUSHFIRE_CRITICALITY | Total Collateral Damage | Total Market Criticality ($/h) | Hrs to reinstate using ERS | Total Market Criticality | TOTAL CRITICALITY | Cond-Based Failure Rate | Risk = Cond-based F.R. x Total Criticality | Corr-Cond (replace now, so C1 condition) | Pr(failure), Replace Now [Therefore, C1 condition, same Corrosivity Zone] | Risk = Cond-based F.R. (C1 Cond) x Total Criticality | Annualised Replacement Costs | Benefit (Replace Now) = Current Risk - New Risk | Ratio = Benefit / Cost (Replace Now) | NPV = Benefit - Cost | Remedial Action | Replacement Cost | Comments
TL-HYAPEX-HYAP626-0000056859 | 30307648 | T626 HYTS-APD 1 500KV | HYTS-APD 1 | 500 | Corr3 | 1981-06-30 | 38.811 | STRUCTSUSP | LSU | TWRMCCT | NORTH | C4 | Corr3-C4 | 500KV-TWRMCCT | 1577306 | 100000 | 0 | 95950 | 11119 | 72 | 800568 | 2573824 | 0.021793 | 56092.0867 | Corr3-C1 | 1.2755e-10 | 0.00032829 | 42545.6694 | 56092.0864 | 1.3184 | 13546.417 | Structure replacement | 815000 | Highly Corrosive Env
TL-HYAPEX-HYAP628-0000056863 | 30365768 | T628BHYTS-APD 1 500KV | HYTS-APD 1 | 500 | Corr3 | 1981-06-30 | 38.811 | STRUCTSTRN | LST | TWRSCCT | NORTH | C4 | Corr3-C4 | 500KV-TWRSCCT | 1577306 | 100000 | 0 | 29685 | 11119 | 58 | 644902 | 2351893 | 0.021793 | 51255.4806 | Corr3-C1 | 1.2755e-10 | 0.00029999 | 39152.4565 | 51255.4803 | 1.3091 | 12103.0238 | Structure replacement | 750000 | Highly Corrosive Env
TL-HYAPEX-HYAP628-0000058118 | 30108463 | T628AHYTS-APD 2 500KV | HYTS-APD 2 | 500 | Corr3 | 1981-06-30 | 38.811 | STRUCTSTRN | LST | TWRSCCT | NORTH | C4 | Corr3-C4 | 500KV-TWRSCCT | 1577306 | 100000 | 0 | 29685 | 11119 | 58 | 644902 | 2351893 | 0.021793 | 51255.4806 | Corr3-C1 | 1.2755e-10 | 0.00029999 | 39152.4565 | 51255.4803 | 1.3091 | 12103.0238 | Structure replacement | 750000 | Highly Corrosive Env
TL-HYAPEX-HYAP625-0000056857 | 30157224 | T625 HYTS-APD 1 500KV | HYTS-APD 2 | 500 | Corr3 | 1981-06-30 | 38.811 | STRUCTSUSP | LSU | TWRMCCT | NORTH | C4 | Corr3-C4 | 500KV-TWRMCCT | 1577306 | 100000 | 0 | 95950 | 11119 | 72 | 800568 | 2573824 | 0.021793 | 56092.0867 | Corr3-C1 | 1.2755e-10 | 0.00032829 | 42545.6694 | 56092.0864 | 1.3184 | 13546.417 | Structure replacement | 815000 | Highly Corrosive Env
[24 empty] | Discount Rate | 0.0466
[19 empty] | Corrosivity- Condition | Cond- Based Failure Rate | Eta, η | Beta, β |  | V-rating & Twr Type | Cost ($) per twr-cct | Annualised Replacement Cost (Corr1) | Annualised Replacement Cost (Corr2) | Annualised Replacement Cost (Corr3)
[19 empty] | Corr1-C1 | 9.1144e-07 | 138 | 4.5 |  | 500kV-TWRSCCT | 750000 | 35015.2404 | 36383.7575 | 39152.4565
[19 empty] | Corr1-C2 | 4.2624e-05 | 138 | 4.5 |  | 500kV-TWRMCCT | 815000 | 38049.8945 | 39537.0164 | 42545.6694
[19 empty] | Corr1-C3 | 0.0013199 | 138 | 4.5 |  | 220kV-TWRSCCT | 500000 | 23343.4936 | 24255.8383 | 26101.6377
[19 empty] | Corr1-C4 | 0.011914 | 138 | 4.5 |  | 220kV-TWRMCCT | 575000 | 26845.0176 | 27894.214 | 30016.8833
[19 empty] | Corr1-C5 | 0.018463 | 138 | 4.5 |  | Characteristic Life (yrs) |  | 138 | 71 | 49
[19 empty] | Corr2-C1 | 6.3972e-09 | 71 | 6.5 |  | Beta |  | 4.5 | 6.5 | 8
[19 empty] | Corr2-C2 | 2.6925e-06 | 71 | 6.5
[19 empty] | Corr2-C3 | 0.0005929 | 71 | 6.5
[19 empty] | Corr2-C4 | 0.018814 | 71 | 6.5
[19 empty] | Corr2-C5 | 0.037451 | 71 | 6.5
[19 empty] | Corr3-C1 | 1.2755e-10 | 49 | 8
[19 empty] | Corr3-C2 | 2.7895e-07 | 49 | 8
[19 empty] | Corr3-C3 | 0.00026749 | 49 | 8
[19 empty] | Corr3-C4 | 0.021793 | 49 | 8
[19 empty] | Corr3-C5 | 0.052339 | 49 | 8
Note on M12097: Francis Lirios: Date of CA is 30/05/2017. I thought Cyient was supposed to finish this?
Note on M12108: Francis Lirios: Date of CA is 30/05/2017. I thought Cyient was supposed to finish this?
Note on M12126: Francis Lirios: Date of CA is 01/06/2017. I thought Cyient was supposed to finish this?